## Note
Note to 2017 ETYS Appendix B
Where overhead line circuits are strung on the same transmission towers, their proximity to each other can lead to current and voltage in one circuit inducing current and voltage in the other. This mutual coupling between circuits can affect the Positive Phase Sequence parameters of overhead line circuits. The Positive Phase Sequence values in these tables are taken from PowerFactory models used by National Grid for 2017 ETYS analysis which include these mutual coupling effects.
When using power analysis applications that are not capable of modelling mutual coupling, it may be necessary to adjust overhead line parameters in line with accepted industry assumptions. These adjustments are likely to only have minor impact on power flow but can have material impact on voltages over larger networks. ETYS data users are advised to contact National Grid for advice if intending to use this data in this way.

## Menu
Electricity Ten Year Statement (ETYS) 2017
Appendix B - Supplementary Technical Data
Table | Title
B.1.1a | SHE Transmission Index of Substation Codes
B.1.1b | SPT Index of Substation Codes
B.1.1c | NGET Index of Substation Codes
B.1.1d | OFTO Index of Substation Codes
B.2.1a | SHE Transmission Circuits 2017/18
B.2.1b | SPT Circuits 2017/18
B.2.1c | NGET Circuits 2017/18
B.2.1d | OFTO Circuits 2017/18
B.2.2a | SHE Transmission Circuit Changes 2018/19 to 2026/27
B.2.2b | SPT Transmission Circuit Changes 2018/19 to 2026/27
B.2.2c | NGET Transmission Circuit Changes 2018/19 to 2026/27
B.2.2d | OFTO Circuit Changes 2018/19 to 2026/27
B.3.1a | SHE Transmission Transformers Winter 2017/18
B.3.1b | SPT Transformers Winter 2017/18
B.3.1c | NGET Transformers Winter 2017/18
B.3.1d | OFTO Transformers 2017/18
B.3.2a | SHE Transmission Transformer Changes 2018/19 to 2026/27
B.3.2b | SPT Transformer Changes 2018/19 to 2026/27
B.3.2c | NGET Transformer Changes 2018/19 to 2026/27
B.3.2d | OFTO Transformer Changes 2018/19 to 2026/27
B.4.1a | SHE Transmission Reactive Compensation Equipment Winter 2017/18
B.4.1b | SPT Reactive Compensation Equipment Winter 2017/18
B.4.1c | NGET Reactive Compensation Equipment Winter 2017/18
B.4.1d | OFTO Reactive Compensation Equipment Winter 2017/18
B.4.2a | SHE Transmission Reactive Compensation Equipment Changes 2018/19 to 2026/27
B.4.2b | SPT Reactive Compensation Equipment Changes 2018/19 to 2026/27
B.4.2c | NGET Reactive Compensation Equipment Changes 2018/19 to 2026/27
B.4.2d | OFTO Reactive Compensation Equipment Changes 2018/19 to 2026/27

## B-1-1a
Table B.1.1a - SHE Transmission Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
ABBA | Aberdeen Bay | 132
ABBA | Aberdeen Bay | 33
ABED | Aberarder | 132
ABED | Aberarder | 33
ABNE | Abernethy | 132
ABNE | Abernethy | 33
ACHL | Achlachan | 33
ACHR | A-Cruach | 132
ACHR | A-Cruach | 33
AIGA | Aigas | 132
ALNE | Alness | 132
ALNE | Alness | 33
ALYT | Alyth | 275
AMUL | Amulree | 132
ANSU | An Suidhe | 132
ANSU | An Suidhe | 33
ARBR | Arbroath | 132
ARBR | Arbroath | 33
ARDB | Ardbrecknish | 132
ARDK | Ardkinglas | 132
ARDK | Ardkinglas | 33
ARDR | Ardross | 275
ARMO | Ardmore | 132
ARMO | Ardmore | 33
AULW | Aultmore | 132
AULW | Aultmore | 33
BADA | Bad A Cheo | 33
BASK | Bay of Skaill | 220
BASK | Bay of Skaill | 132
BASK | Bay of Skaill | 33
BEAT | Beatrice Wind | 400
BEAU | Beauly | 400
BEAU | Beauly | 275
BEAU | Beauly | 132
BEAU | Beauly | 33
BEIN | Beinneun | 132
BEIN | Beinneun | 33
BENA | Ben Aketil | 33
BERB | Berryburn | 275
BERB | Berryburn | 33
BETH | Beinn Tharsuinn | 33
BEWF | Beaw Field | 132
BEWF | Beaw Field | 33
BGLA | Beinn Ghlas | 33
BHLA | Bhlaraidh | 132
BHLA | Bhlaraidh | 33
BIHI | Birkhill | 132
BLHI | Blackhillock | 400
BLHI | Blackhillock | 275
BLHI | Blackhillock | 132
BLHI | Blackhillock | 33
BLRH | Blary Hill | 33
BOAG | Boat of Garten | 132
BOAG | Boat of Garten | 33
BOYN | Boyndie | 33
BRCW | Braco West | 275
BRCW | Braco West | 33
BRDU | Braes of Doune Wind | 33
BREC | Brechin | 132
BRID | Bridge of Dun | 132
BRID | Bridge of Dun | 33
BRMO | Braemore Wood | 33
BROA | Broadford | 132
BROA | Broadford | 33
BROR | Brora | 132
BROR | Brora | 33
BTUI | Beinn an Tuirc | 132
BTUI | Beinn an Tuirc | 33
BUMU | Burghmuir | 132
BUMU | Burghmuir | 33
BUWH | Burn of Whilk | 33
CAAD | Carradale | 132
CAAD | Carradale | 33
CAHE | Cantick Head | 33
CAIN | Cairnford | 275
CAIN | Cairnford | 33
CAIR | Cairn Uish Rothes | 33
CAMW | Camster Wind | 33
CASH | Cashlie | 33
CASS | Cashley | 132
CASS | Cashley | 33
CAUS | Causeymire | 33
CEAN | Ceannacroc | 132
CEAN | Ceannacroc | 33
CHAR | Charleston | 132
CHAR | Charleston | 33
CLAC | Clachan | 132
CLAC | Clachan | 33
CLAS | Clashindarroch | 33
CLAY | Clayhills | 132
CLAY | Clayhills | 33
CLUN | Clunie | 132
COGA | Corriegarth | 132
COGA | Corriegarth | 33
COIN | Coire Na Cloiche | 33
CONN | Connagill | 275
CONN | Connagill | 132
CONN | Connagill | 33
CORI | Corriemoillie | 132
CORI | Corriemoillie | 33
COST | Costa Head | 33
COUA | Coupar Angus | 132
COUA | Coupar Angus | 33
COUW | Cour Wind | 33
CRAI | Craigiebuckler | 132
CRAI | Craigiebuckler | 33
CRDH | Creag Dhubh | 275
CRDH | Creag Dhubh | 33
CREA | Creag Riabhach | 132
CREA | Creag Riabhach | 33
CRMY | Corrimony | 33
CROB | Crossburns | 275
CROB | Crossburns | 33
CRSS | Crossaig | 220
CRSS | Crossaig | 132
CRSS | Crossaig | 33
CULL | Culligran | 132
DAAS | Dallas | 275
DAAS | Dallas | 33
DEAN | Deanie | 132
DENS | Denside | 132
DEUC | Deucherin Hill | 33
DORE | Dorenell | 132
DORE | Dorenell | 33
DOUN | Dounreay | 275
DOUN | Dounreay | 220
DOUN | Dounreay | 132
DOUN | Dounreay | 33
DRUL | Druim Lethann | 132
DUBE | Dunbeath | 132
DUBE | Dunbeath | 33
DUCC | Dunmore Cable Compound | 132
DUDH | Dudhope | 132
DUDH | Dudhope | 33
DUGR | Dunvegan | 132
DUGR | Dunvegan | 33
DUNM | Dunmaglass | 132
DUNM | Dunmaglass | 33
DYCE | Dyce | 132
DYCE | Dyce | 33
EDIN | Edinbane | 132
EDIN | Edinbane | 33
EDNT | Edintore | 33
ELCH | Elchies Wind | 132
ELCH | Elchies Wind | 33
ELGI | Elgin | 132
ELGI | Elgin | 33
ERRO | Errochty | 132
FAAR | Farr Windfarm | 132
FAAR | Farr Windfarm | 33
FARI | Farigaig | 275
FARI | Farigaig | 132
FARI | Farigaig | 33
FASN | Fasnakyle | 275
FASN | Fasnakyle | 33
FAUG | Fort Augustus | 400
FAUG | Fort Augustus | 275
FAUG | Fort Augustus | 132
FAUG | Fort Augustus | 33
FAWI | Fairburn Wind | 33
FERO | Fernoch | 132
FERO | Fernoch | 33
FETT | Fetteresso | 275
FETT | Fetteresso | 132
FETT | Fetteresso | 33
FEWI | Fetteresso Wind | 33
FIDD | Fiddes | 132
FIDD | Fiddes | 33
FINL | Finlarig | 132
FINS | Finstown | 33
FOFF | Firth of Forth | 275
FOGG | Foggieton | 132
FOYE | Foyers | 275
FRAS | Fraserburgh | 132
FRAS | Fraserburgh | 33
FRSD | Freasdail | 33
FWIL | Fort William | 132
FWIL | Fort William | 33
FYRI | Fyrish | 275
FYRI | Fyrish | 132
FYRI | Fyrish | 33
GILB | Gills Bay | 132
GILB | Gills Bay | 33
GLAG | Glen Agnes | 132
GLAG | Glen Agnes | 33
GLCA | Glencassley | 33
GLDO | Glendoe Substation | 132
GLEN | Glenmoriston | 132
GLFA | Glenfarclas | 132
GLFA | Glenfarclas | 33
GLKY | Kyllachy | 132
GLKY | Kyllachy | 33
GLNE | Glean Eoghainn | 33
GLNU | Glen Ullinish | 132
GLNU | Glen Ullinish | 33
GLOF | Glens of Foundland | 33
GOHI | Gordonstown Hill | 33
GOLT | Golticlay | 132
GOLT | Golticlay | 33
GORW | Gordonbush Wind | 275
GORW | Gordonbush Wind | 33
GRAR | Gravir | 132
GRFR | Greenford Farm | 33
GRIF | Griffin Wind | 132
GRIF | Griffin Wind | 33
GRUB | Grudie Bridge | 132
GRUB | Grudie Bridge | 33
HALY | Halsary | 33
HEST | Hesta Head | 33
HIGL | Hill of Glaschyle | 33
HITO | Hill of Towie | 33
HUNN | Hunterston North | 220
HYWD | Hywind | 33
INAW | Inverawe | 33
INGA | Invergarry | 132
INNE | Inverness | 132
INNE | Inverness | 33
INRU | Inverugie | 132
INVE | Inveraray | 132
INVR | Inverarnan | 132
INVR | Inverarnan | 33
KEIT | Keith | 275
KEIT | Keith | 132
KEIT | Keith | 33
KIIN | Killin | 132
KIIN | Killin | 33
KILC | Kilchrenan | 132
KILO | Kinlochleven | 132
KILO | Kinlochleven | 33
KINT | Kintore | 400
KINT | Kintore | 275
KINT | Kintore | 132
KINT | Kintore | 33
KINW | Kincardine Wind | 33
KIOR | Kilmorack | 132
KNOC | Knocknagael | 275
KNOC | Knocknagael | 132
KNOC | Knocknagael | 33
LAGG | Laggan | 132
LAIR | Lairg | 132
LAIR | Lairg | 33
LHBR | Lochaber Hydro | 33
LIME | Limekilns | 132
LIME | Limekilns | 33
LOCB | Loch Buidhe | 275
LOCB | Loch Buidhe | 132
LOCB | Loch Buidhe | 33
LOCH | Lochay | 132
LOCH | Lochay | 33
LOCL | Loch Lundie | 132
LOCL | Loch Lundie | 33
LUBR | Lubreoch | 33
LUIC | Luichart | 132
LUMB | Lumbs | 132
LUNA | Lunanhead | 132
LUNA | Lunanhead | 33
LYND | Lyndhurst | 132
LYND | Lyndhurst | 33
MACD | Macduff | 132
MACD | Macduff | 33
MEKL | Meikle | 33
MELG | Melgarve | 400
MELG | Melgarve | 132
MELG | Melgarve | 33
MEYG | Meygen Tidal | 132
MEYG | Meygen Tidal | 33
MIHW | Midhill Wind | 33
MILC | Milton of Craigie | 132
MILC | Milton of Craigie | 33
MILS | Millenium South | 132
MILS | Millenium South | 33
MILW | Millenium Wind | 132
MILW | Millenium Wind | 33
MITA | Milltown Airfield | 33
MORF | Moray Firth Wind | 400
MOSS | Mossford | 132
MOTA | Moultaive | 132
MOYW | Moy Wind | 33
MUAI | Muaithebheal | 132
MYBS | Mybster | 132
MYBS | Mybster | 33
NAIR | Nairn | 132
NAIR | Nairn | 33
NANT | Nant | 132
NANT | Nant | 33
NEDE | New Deer | 400
NOVA | Novar | 33
NOVW | Novar Wind | 33
NWGL | Norwegian Link 2 | 400
ORRI | Orrin | 132
ORRI | Orrin | 33
PAUH | Paul's Hill Aberlour | 33
PEHE | Peterhead | 400
PEHE | Peterhead | 275
PEHE | Peterhead | 132
PEHE | Peterhead | 33
PEHG | Peterhead Grange | 132
PEHG | Peterhead Grange | 33
PERS | Persley | 275
PERS | Persley | 132
PERS | Persley | 33
PITL | Pitlochry Hydro Station | 11
PORA | Port Ann | 132
PORA | Port Ann | 33
QUOI | Quoich | 132
RANN | Rannoch | 132
RANN | Rannoch | 33
REDM | Redmoss | 132
REDM | Redmoss | 33
ROSH | Rosehall | 33
ROTI | Rothienorman | 400
RTHE | Rothes III | 33
SALA | Sallachy | 132
SALA | Sallachy | 33
SFEG | St Fergus Gas Terminal | 132
SFEM | St Fergus Mobil | 132
SFER | St Fergus | 132
SFIL | St Fillians | 132
SFIL | St Fillians | 33
SHET | Shetland | 132
SHIN | Shin | 132
SHIN | Shin | 33
SLKB | Slackbuie | 132
SLOY | Sloy | 132
SONO | Sonachan | 132
SONO | Sonachan | 33
SOUI | Sound of Islay | 33
SPCH | Speyside CHP | 33
SPIT | Spittal | 275
SPIT | Spittal | 132
SPIT | Spittal | 33
SPYW | Speyslaw | 33
STOM | Stoneywood Mills | 33
STRB | Strathbrora Substation | 275
STRB | Strathbrora Substation | 33
STRI | Strichen | 132
STRI | Strichen | 33
STRL | Stronelairg Wind | 132
STRL | Stronelairg Wind | 33
STRS | Stroupster Wind | 33
STRW | Strathy | 132
STRW | Strathy | 33
STWN | Stornoway Wind | 132
TANG | Tangy | 33
TARL | Tarland | 132
TARL | Tarland | 33
TAYN | Taynuilt | 132
TAYN | Taynuilt | 33
TEAL | Tealing | 275
TEAL | Tealing | 132
TEAL | Tealing | 33
THSO | Thurso | 275
THSO | Thurso | 132
THSO | Thurso | 33
TLYM | Tullymurdoch | 33
TOMN | Tom Na Clach | 33
TOMT | Tomatin | 275
TOMT | Tomatin | 132
TOMT | Tomatin | 33
TORA | Torr Achilty | 33
TULL | Tullich | 33
TULW | Tullo 2 | 33
TUMB | Tummel Bridge | 132
TUMB | Tummel Bridge | 33
TUMM | Tummel | 275
TUMM | Tummel | 132
TUMM | Tummel | 33
WATH | Wathegar 2 | 33
WHIB | Whitebridge | 132
WILW | Willow | 132
WILW | Willow | 33
WIOW | Willowdale | 132
WIOW | Willowdale | 33
WISL | West Islay | 132
WISL | West Islay | 33
WOHI | Woodhill | 132
WOHI | Woodhill | 33
WRAY | Westray South | 33

## B-1-1b
Table B.1.1b - SPT Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
AIKE | Aikengall Wind Farm | 33
AIRI | Airies Windfarm | 33
ANDE | Andershaw Wind Farm | 33
ANNA | Annabaglish Wind Farm | 33
AREC | Arecleoch | 132
AREC | Arecleoch | 33
ASVA | Assel Valley Wind Farm | 33
AUCH | Auchencrosh | 275
AUCW | Auchenwynd | 132
AURO | Auchrobert Windfarm | 33
AYR- | Ayr | 275
AYR- | Ayr | 33
BAGA | Bathgate | 132
BAGA | Bathgate | 33
BAGA | Bathgate Rail | 25
BAIN | Bainsford | 132
BAIN | Bainsford | 33
BEQU | Benbrack and Quantans Hill | 132
BEQU | Benbrack and Quantans Hill | 33
BERW | Berwick | 132
BERW | Berwick | 33
BLAH | Blackhill | 132
BLAH | Blackhill | 33
BLCW | Blackcraig | 132
BLCW | Blackcraig | 33
BLKL | Blacklaw Windfarm | 132
BLKL | Blacklaw Windfarm | 33
BLKS | Blackcraig South | 33
BLLX | Blacklaw Extension | 132
BLLX | Blacklaw Extension | 33
BONB | Bonnybridge Border Node | 400
BONB | Bonnybridge Border Node | 275
BONN | Bonnybridge | 275
BONN | Bonnybridge | 132
BONN | Bonnybridge | 33
BONN | Bonnybridge | 25
BOWB | Bowbeat Hill | 33
BPGR | BP Grangemouth | 33
BRAE | Braehead | 132
BRAP | Braehead Park | 132
BRAP | Braehead Park | 33
BRNX | Branxton | 400
BROX | Broxburn | 132
BROX | Broxburn | 33
BUSB | Busby | 275
CAFA | Carsfad | 132
CAFA | Carsfad | 11
CALD | Calder Water | 33
CATY | Carntyne | 132
CATY | Carntyne | 33
CATY | Carntyne | 25
CHAP | Chapelcross | 132
CHAP | Chapelcross | 33
CHAS | Charlotte Street | 275
CHAS | Charlotte Street | 33
CHMO | Chirmorie Wind Farm | 132
CLYM | Clyde's Mill | 275
CLYM | Clyde's Mill | 33
CLYN | Clyde North | 275
CLYN | Clyde North | 33
CLYS | Clyde South | 275
CLYS | Clyde South | 33
COAL | Coalburn | 400
COAL | Coalburn | 132
COAL | Coalburn | 33
COAT | Coatbridge | 275
COAT | Coatbridge | 33
COCK | Cockenzie | 400
COCK | Cockenzie | 275
COCK | Cockenzie | 33
CONO | Coalburn North | 132
COYL | Coylton | 275
COYL | Coylton | 132
COYL | Coylton | 33
COYT | Coylton Tee | 132
COYW | Coylton West | 275
CRDY | Crossdykes Windfarm | 33
CRMH | Cruach Mhor | 33
CROE | Crookedstane Wind Farm | 33
CROO | Crookston | 132
CROO | Crookston | 33
CRUA | Cruachan | 275
CRYR | Crystal Rig | 400
CRYR | Crystal Rig | 132
CRYR | Crystal Rig | 33
CUMB | Cumbernauld | 132
CUMB | Cumbernauld | 33
CUMH | Cumberhead Wind Farm | 33
CUPA | Cupar | 132
CUPA | Cupar | 33
CURR | Currie | 275
CURR | Currie | 132
CURR | Currie | 33
CURR | Currie | 11
DALB | Dalmally Boundary | 275
DALL | Dalmally | 275
DALM | Dalmarnock | 275
DALM | Dalmarnock | 132
DALM | Dalmarnock | 33
DALQ | Dalquhandy Collector | 132
DALQ | Dalquhandy | 33
DALS | Dalswinton | 33
DENN | Denny North | 400
DENN | Denny North | 275
DENN | Denny North | 132
DENN | Denny North | 33
DESA | Dersalloch | 132
DESA | Dersalloch | 33
DEVM | Devol Moor | 400
DEVM | Devol Moor | 132
DEVM | Devol Moor | 33
DEVM | Devol Moor | 25
DEVO | Devonside | 132
DEVO | Devonside | 33
DEWP | Dewar Place | 275
DEWP | Dewar Place | 33
DOWE | Douglas West | 33
DRCR | Drumcross | 132
DRCR | Drumcross | 33
DRUM | Drumchapel | 275
DRUM | Drumchapel | 33
DUMF | Dumfries | 132
DUMF | Dumfries | 33
DUNB | Dunbar | 132
DUNB | Dunbar | 33
DUNE | Dunlaw Extension | 132
DUNE | Dunlaw Extension | 33
DUNF | Dunfermline | 132
DUNF | Dunfermline | 33
DUNH | Dunhill | 132
DUNH | Dunhill | 33
DUNO | Dunoon | 132
DUNO | Dunoon | 33
EARB | Earlsburn | 33
EAST | Earlstoun | 132
EAST | Earlstoun | 11
ECCF | Ecclefechan | 132
ECCF | Ecclefechan | 25
ECCL | Eccles | 400
ECCL | Eccles | 132
ECCL | Eccles | 33
EERH | Easterhouse | 275
EERH | Easterhouse | 33
EKIL | East Kilbride | 275
EKIL | East Kilbride | 33
EKIS | East Kilbride South | 275
EKIS | East Kilbride South | 33
ELDE | Elderslie | 132
ELDE | Elderslie | 33
ELVA | Elvanfoot | 400
ELVA | Elvanfoot | 275
ELVA | Elvanfoot | 132
ELVA | Elvanfoot | 33
ELVA | Elvanfoot | 25
ENHI | Enoch Hill Wind Farm | 132
ENHI | Enoch Hill Wind Farm | 33
ERSK | Erskine | 132
ERSK | Erskine | 33
ESST | Essenside | 132
EWEH | Ewe Hill | 132
EWEH | Ewe Hill | 33
EXON | Exxon mobil | 33
EXON | Exxon mobil | 11
FALL | Fallago | 400
FALL | Fallago | 33
FIFE | Fife Energy | 132
FINN | Finnieston | 132
FINN | Finnieston | 33
GALA | Galashiels | 132
GALA | Galashiels | 33
GARB | Gareloch Boundary | 132
GARE | Gareloch | 132
GAWH | Galawhistle | 132
GAWH | Galawhistle | 33
GIFF | Giffnock | 275
GIFF | Giffnock | 33
GIHI | Gilston Hill Wind Farm | 33
GLAP | Glen App Wind Farm | 33
GLGL | Glenglass | 132
GLGL | Glenglass | 33
GLLE | Glenlee | 132
GLLE | Glenlee | 11
GLLU | Glenluce | 132
GLLU | Glenluce | 33
GLMU | Glenmuckloch | 33
GLNI | Glenniston | 132
GLNI | Glenniston | 33
GLOU | Glenouther Windfarm | 33
GLRB | Glenrothes Boundary | 275
GLRO | Glenrothes | 275
GLRO | Glenrothes | 33
GORG | Gorgie | 132
GORG | Gorgie | 33
GOVA | Govan | 132
GOVA | Govan | 33
GRMO | Grangemouth | 275
GRMO | Grangemouth | 33
GRNA | Gretna | 400
GRNA | Gretna | 132
GRNA | Gretna | 33
HABU | Harry Burn Wind Farm | 33
HADH | Hadyard Hill | 132
HADH | Hadyard Hill | 33
HAGR | Haggs Road | 132
HAGR | Haggs Road | 33
HAKB | Harker Border Node | 400
HAKB | Harker Border Node | 132
HARE | Harestanes | 132
HARE | Harestanes | 33
HARG | Harting Rig Wind Farm | 33
HARH | Harburn Head Wind Farm | 33
HAWI | Hawick | 132
HAWI | Hawick | 33
HELE | Helensburgh | 132
HELE | Helensburgh | 33
HOPR | Hopsrig Wind Farm | 132
HOPR | Hopsrig Wind Farm | 33
HUCS | Hunterston Converter Station | 400
HUER | Hunterston | 400
HUER | Hunterston | 132
HUER | Hunterston | 33
HUNE | Hunterston East | 400
HUNF | Hunterston Farm | 132
HUNF | Hunterston Farm | 33
HUNN | Hunterston North | 400
HUNN | Hunterston North | 220
HUNN | Hunterston North | 33
INKE | Inverkeithing | 132
INKE | Inverkeithing | 33
INVB | Inverarnan | 275
INVR | Inverarnan | 275
INWI | Innerwick | 132
INWI | Innerwick | 25
JOHN | Johnstone | 132
JOHN | Johnstone | 33
JUNA | Junction A | 132
JUNV | Junction V | 132
KAIM | Kaimes | 275
KAIM | Kaimes | 33
KEIH | Keithshill | 33
KENN | Kennoxhead | 132
KENN | Kennoxhead | 33
KEON | Kendoon North | 132
KEOO | Kendoon | 132
KEOO | Kendoon | 11
KIER | Killermont | 132
KIER | Killermont | 33
KILB | Kilbowie | 132
KILB | Kilbowie | 33
KILB | Kilbowie | 11
KILG | Kilgalleoch | 275
KILG | Kilgalleoch | 33
KILS | Kilmarnock South | 400
KILS | Kilmarnock South | 275
KILS | Kilmarnock South | 132
KILS | Kilmarnock South | 33
KILT | Kilmarnock Town | 275
KILT | Kilmarnock Town | 33
KILW | Kilwinning | 132
KILW | Kilwinning | 33
KINB | Kincardine Boundary | 275
KINC | Kincardine | 275
KYPE | Kype Muir | 132
KYPE | Kype Muir | 33
LAMB | Lambhill | 275
LETH | Lethans | 132
LETH | Lethans | 33
LEVE | Leven | 132
LEVE | Leven | 33
LEVT | Leven Tee | 132
LING | Livingston | 132
LING | Livingston | 33
LINM | Linmill | 132
LINM | Linmill | 33
LOAN | Longannet | 275
LOCH | Loch Hill Windfarm 33kV | 33
LONB | Longburn Wind Farm | 132
LOPA | Longpark | 33
LORG | Lorg Wind Farm | 132
LORG | Lorg Wind Farm | 33
MAHI | Mark's Hill | 275
MAHI | Mark's Hill | 132
MAHI | Mark's Hill | 33
MARG | Margree | 132
MARG | Margree | 33
MARM | Marshall Meadows | 25
MAYB | Maybole | 132
MAYB | Maybole | 33
MAYT | Maybole Tee | 132
MEAD | Meadowhead | 132
MEAD | Meadowhead | 11
MIDM | Middle Muir Wind Farm | 132
MIDM | Middle Muir Wind Farm | 33
MINN | Minnygap Wind Farm | 33
MINS | Minsca | 33
MOFF | Moffat | 400
MOFF | Moffat | 132
MOFF | Moffat | 33
MOSH | Mossmorran Shell | 132
MOSH | Mossmorran Shell | 11
MOSM | Mossmorran | 275
MOSM | Mossmorran | 132
MOSM | Mossmorran | 33
NEAR | Newarthill | 275
NEAR | Newarthill | 33
NECU | New Cumnock | 275
NECU | New Cumnock | 132
NECU | New Cumnock | 33
NECU | New Cumnock | 33
NEIL | Neilston | 400
NEIL | Neilston | 275
NEIL | Neilston | 132
NEIL | Neilston | 33
NETS | Newton Stewart | 132
NETS | Newton Stewart | 33
NLEI | North Lowther Energy Initiative | 132
NLEI | North Lowther Energy Initiative | 33
NNGA | Neart na Gaoithe | 220
NNGA | Neart na Gaoithe | 33
NNGB | Neart na Gaoithe | 220
NNGB | Neart na Gaoithe | 33
PAIS | Paisley | 132
PAIS | Paisley | 33
PART | Partick | 132
PART | Partick | 33
PENC | Pencloe | 33
POGB | Pogbie Windfarm | 33
POOB | Portobello | 275
POOB | Portobello | 33
POOB | Portobello | 25
PORD | Port Dundas | 275
PORD | Port Dundas | 33
RAVE | Ravenscraig | 33
REDH | Redhouse | 132
REDH | Redhouse | 33
ROBP | Rothes BioPower | 33
ROBP | Rothes BioPower | 11
SACO | Saltcoats | 132
SACO | Saltcoats | 33
SACO | Saltcoats | 25
SAKN | Sandy Knowe Wind Farm | 132
SANQ | Sanquhar Wind Farm | 132
SANX | St Andrews Cross | 132
SANX | St Andrews Cross | 33
SANX | St Andrews Cross | 25
SHRU | Shrubhill | 275
SHRU | Shrubhill | 33
SIGH | Sighthill | 275
SIGH | Sighthill | 33
SMEA | Smeaton | 400
SMEA | Smeaton | 275
SMEA | Smeaton | 132
SMEA | Smeaton | 33
SNED | Sneddon Law | 33
SOKY | South Kyle | 132
SOKY | South Kyle | 33
SOLW | Solway Bank Wind Farm | 33
SPAV | Spango Valley | 132
SPAV | Spango Valley | 33
STCR | Steven's Croft | 33
STCR | Steven's Croft | 11
STHA | Strathaven | 400
STHA | Strathaven | 275
STHA | Strathaven | 33
STIR | Stirling | 132
STIR | Stirling | 33
STLE | Strathleven | 132
STLE | Strathleven | 33
STLE | Strathleven | 25
STNO | Stranoch Wind Farm | 132
STNO | Stranoch Wind Farm | 33
STVE | Striven | 33
STWB | Stella West Border Node | 400
TELR | Telford Road | 132
TELR | Telford Road | 33
TODD | Toddleburn | 33
TONG | Tongland | 132
TONG | Tongland | 33
TONG | Tongland | 11
TORM | Tormywheel Wind Farm | 33
TORN | Torness | 400
TORN | Torness | 132
TORN | Torness | 33
TRAL | Tralorg Wind Farm | 33
ULZI | Ulzieside | 33
VIRD | Viridor | 33
WEGO | West George Street | 275
WEGO | West George Street | 33
WESE | Westerdod | 132
WFIB | Westfield Boundary | 275
WFIE | Westfield | 275
WFIE | Westfield | 132
WFIE | Westfield | 33
WHBR | Whitelaw Brae Wind Farm | 33
WHHO | Whitehouse | 275
WHHO | Whitehouse | 33
WHLL | Whiteside Hill | 33
WHTB | Whistlefield Boundary | 132
WHTL | Whistlefield | 132
WHTL | Whistlefield | 33
WISH | Wishaw (Gowkthrapple) | 400
WISH | Wishaw (Gowkthrapple) | 275
WISH | Wishaw (Gowkthrapple) | 132
WISH | Wishaw (Gowkthrapple) | 33
WISH | Wishaw (Gowkthrapple) | 25
WIYH | Windyhill | 400
WIYH | Windyhill | 275
WIYH | Windyhill | 132
WIYH | Windyhill | 33
WLEE | Whitelee | 275
WLEE | Whitelee | 33
WLEX | Whitelee Extension | 275
WLEX | Whitelee Extension | 33

## B-1-1c
Table B.1.1c - NGET Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
ABHA | Abham | 400
ABTH | Aberthaw | 275
ABTH | Aberthaw | 132
ABTH | Aberthaw | 132
ACTL | Acton Lane | 22
ALDW | Aldwarke | 275
ALST | Alpha Steel | 33
ALVE | Alverdiscott | 400
AMEM | Amersham | 132
AUST | Aust | 400
AXMI | Axminster | 400
AXMI | Axminster | 132
BACT | Bacton | 400
BAGB | Baglan Bay | 275
BARK | Barking | 400
BARK | Barking | 275
BARK | Barking | 132
BARP | Barking Power | 275
BARW | Barking West | 33
BEDD | Beddington | 400
BEDD | Beddington | 275
BESW | Berkswell | 275
BICF | Bicker Fen | 400
BIRK | Birkenhead | 275
BISW | Bishops Wood | 275
BLYT | Blyth | 400
BLYT | Blyth | 275
BLYT | Blyth | 66
BODE | Bodelwyddan | 400
BOLN | Bolney | 400
BOTW | Botley Wood | 400
BRAI | Braintree | 400
BRAW | Bradford West | 400
BRAW | Bradford West | 275
BRED | Bredbury | 275
BRFO | Bramford | 400
BRIM | Brimsdown | 400
BRIM | Brimsdown | 275
BRIM | Brimsdown | 132
BRIM | Brimsdown | 132
BRIN | Brinsworth | 400
BRIN | Brinsworth | 275
BRIT | Britannia Bridge | 275
BRIW | Bridgewater | 400
BRLE | Bramley | 400
BRWA | Bridgewater | 400
BRWA | Bridgwater | 275
BRWA | Bridgwater | 132
BURW | Burwell | 400
BUSH | Bushbury | 275
BUST | Bustleholm | 400
BUST | Bustleholm | 275
CAMA | Cambridge Arms | 132
CAML | Camblesforth | 66
CANT | Canterbury | 400
CANW | Carnedd Wen | 400
CAPE | Capenhurst | 400
CAPE | Capenhurst | 275
CARE | Cardiff East | 275
CARN | Carnedd Wen | 400
CARR | Carrington | 400
CARR | Carrington | 275
CARR | Carrington | 132
CARR | Carrington | 132
CELL | Cellarhead | 400
CELL | Cellarhead | 132
CELL | Cellarhead | 132
CHIC | Chickerell | 400
CHIL | Chilling | 400
CHSI | Chessington | 275
CHTE | Chesterfield | 275
CILF | Cilfynydd | 400
CILF | Cilfynydd | 275
CITR | City Road | 400
CLEH | Cleve Hill | 400
CONQ | Connahs Quay | 400
COSO | Coryton South | 400
COTT | Cottam | 400
COVE | Coventry | 275
COWL | Cowley | 400
COWT | Cowbridge Tee | 275
CREB | Creyke Beck | 400
CREB | Creyke Beck | 275
CULJ | Culham Jet | 400
DAIN | Daines | 400
DAMC | Damhead Creek | 400
DEES | Deeside | 400
DIDC | Didcot | 400
DINO | Dinorwig | 400
DISS | Diss | 400
DRAK | Drakelow | 400
DRAK | Drakelow | 275
DRAK | Drakelow | 132
DRAK | Drakelow | 132
DRAX | Drax | 400
DRAX | Drax | 132
DRAX | Drax | 132
DUNG | Dungeness | 400
DUNG | Dungeness | 275
EALI | Ealing | 275
EALI | Ealing | 66
EASO | Eaton Socon | 400
ECLA | East Claydon | 400
ECLA | East Claydon | 132
ECLA | East Claydon | 132
EGGB | Eggborough | 400
ELLA | Elland | 275
ELLA | Elland | 132
ELST | Elstree | 400
ELST | Elstree | 275
ELST | Elstree | 132
ENDE | Enderby | 400
EXET | Exeter | 400
EYES | EYE | 400
FAWL | Fawley | 400
FAWL | Fawley | 132
FAWL | Fawley | 132
FECK | Feckenham | 400
FECK | Feckenham | 275
FENW | Fenwick Tee | 400
FERR | Ferrybridge | 400
FERR | Ferrybridge | 275
FERR | Ferrybridge | 132
FERR | Ferrybridge | 132
FFES | Ffestiniog | 275
FIDF | Fiddler's Ferry | 275
FINP | Finsbury Park | 400
FLEE | Fleet | 400
FLIB | Flintshire Bridge WestHVDC | 400
FOUR | Fourstones | 275
FOUX | Four Crosses | 400
FROD | Frodsham | 400
FROD | Frodsham | 275
GART | Garforth | 400
GRAI | Grain | 400
GRAN | Grange | 66
GREN | Grendon | 400
GREN | Grendon | 132
GREN | Grendon | 132
GRIW | Grimsby West | 400
GRSA | Greystones 'A' | 275
GRSB | Greystones 'B' | 275
GRST | Greystones | 275
GRTO | Grangetown | 275
GWYN | Gmynt Y Mor Tee | 400
GYWN | Gmynt Y Mor | 132
HACK | Hackney | 400
HACK | Hackney | 275
HAKB | Harker Border (Node) | 400
HAMB | Hambleton Tee | 400
HAMH | Hams Hall | 400
HAMH | Hams Hall | 275
HAMH | Hams Hall | 132
HARK | Harker | 400
HARK | Harker | 275
HARK | Harker | 132
HARK | Harker | 132
HARM | Hart Moor | 275
HATL | Hartlepool | 275
HAWP | Hawthorn Pit | 400
HAWP | Hawthorn Pit | 275
HEDD | Heddon Tee | 400
HEDN | Hedon | 150
HEDO | Hedon | 275
HEYS | Heysham | 400
HEYS | Heysham | 132
HEYS | Heysham | 132
HIBU | Highbury | 400
HIGM | High Marnham | 400
HIGM | High Marnham | 275
HIKP | Hinckley Point C | 400
HINP | Hinkley Point | 400
HINP | Hinkley Point | 275
HIRN | Hirst North | 400
HUMR | Humber Refinery | 400
HURS | Hurst | 275
HUTT | Hutton | 400
IMPP | Imperial Park | 400
INDQ | Indian Queens | 400
IROA | Iron Acton | 275
IROA | Iron Acton | 132
IROA | Iron Acton | 132
IRON | Ironbridge | 400
IRON | Ironbridge | 132
IRON | Ironbridge | 132
IVER | Iver | 400
IVER | Iver | 275
JORD | Jordanthorpe | 275
KEAD | Keadby | 400
KEAP | Keadby Power | 400
KEAR | Kearsley | 400
KEAR | Kearsley | 275
KEMS | Kemsley | 400
KENG | Kensal Green | 400
KIBY | Kirkby | 275
KILL | Killinghome | 400
KILY | Kings Lynn | 400
KINL | King Lynn | 400
KINO | Kingsnorth | 400
KINO | Kingsnorth | 132
KINO | Kingsnorth | 132
KIRK | Kirkstall | 275
KITW | Kitwell | 275
KNAR | Knaresborough | 275
KNOT | Knottingley | 400
LACK | Lackenby | 400
LACK | Lackenby | 275
LAGA | Langage | 400
LAKE | Lakeside | 400
LALE | Laleham | 275
LAND | Landulph | 400
LEGA | Legacy | 400
LEIB | Leighton Buzzard | 400
LEIS | Leiston | 400
LEMR | Lea Marston | 132
LISD | Lister Drive | 275
LITB | Little Barford | 400
LITD | Little Dunham | 275
LITT | Littlebrook | 400
LITT | Littlebrook | 275
LITT | Littlebrook | 132
LODR | Lodge Road | 66
LOFI | Longfield | 400
LOVE | Lovedean | 400
LOWE | Lowestoft | 400
MACC | Macclesfield | 400
MACC | Macclesfield | 275
MAGA | Margam | 275
MANN | Mannington | 400
MAWO | Marchwood | 400
MEDW | Medway | 400
MEDW | Medway | 400
MELK | Melksham | 400
MELK | Melksham | 275
MELK | Melksham | 132
MELK | Melksham | 132
MIDL | Middleton | 400
MILH | Mill Hill | 275
MILH | Mill Hill | 132
MILH | Mill Hill | 132
MITY | Minety | 400
MIWW | Mid Wales West | 400
MOEL | St Asaph | 400
MONF | Monk Fryston | 400
MONF | Monk Fryston | 275
MUCF | Mucking Flats | 400
MUMB | Mumby | 400
NECH | Nechells | 275
NECT | Necton | 400
NECT | Necton | 400
NEEP | Neepsend | 400
NEEP | Neepsend | 275
NEWF | Newton Flotman | 400
NEWX | New Cross | 275
NFLE | Northfleet East | 400
NHYD | North Hyde | 275
NHYD | North Hyde | 66
NINF | Ninfield | 400
NORL | Norton Lees | 275
NORM | Norwich Main | 400
NORT | Norton | 400
NORT | Norton | 275
NORW | Norwich Main | 400
NURS | Nursling | 400
OCKH | Ocker Hill | 275
OCKH | Ocker Hill | 132
OCKH | Ocker Hill | 132
OFFE | Offerton | 275
OLDB | Oldbury | 400
OLDB | Oldbury | 275
OLDS | Oldbury-on-Severn | 400
OLDS | Oldbury-on-Severn | 132
OSBA | Osbaldwick | 400
OSWE | Oswestry | 400
PADI | Padiham | 400
PADI | Padiham | 132
PADI | Padiham | 132
PAFB | Patford Bridge | 400
PELH | Pelham | 400
PEMB | Pembroke | 400
PEMB | Pembroke | 132
PENE | Penwortham East | 132
PENI | Peniarwaun | 400
PENN | Penn | 400
PENN | Penn | 275
PENT | Pentir | 400
PENW | Penwortham West | 132
PERH | Penrhos | 132
PEWO | Penwortham | 400
PEWO | Penwortham | 275
PITS | Pitsmoor | 275
POPP | Poppleton | 275
PORH | Port Ham | 132
PUDM | Pudding Mill Lane | 400
PURI | Puriton Tee | 400
PYLE | Pyle | 275
QUER | Quernmoor Tee | 400
RAIN | Rainhill | 275
RASS | Rassau | 400
RATS | Ratcliffe-on-Soar | 400
RATS | Ratcliffe-on-Soar | 275
RATS | Ratcliffe-on-Soar | 132
RATS | Ratcliffe-on-Soar | 132
RAYL | Rayleigh | 400
RAYM | Rayleigh Main | 132
REBR | Redbridge | 275
RHIG | Rhigos | 400
RICH | Richborough | 400
ROCH | Rochdale | 400
ROCH | Rochdale | 275
ROCK | Rocksavage | 400
ROWD | Rowdown | 400
RUGE | Rugeley | 400
RUGE | Rugeley | 132
RYEH | Rye House | 400
RYHA | Ryhall | 400
SAEN | Saltend North | 275
SAES | Saltend South | 275
SAFO | Sandford | 400
SALH | Saltholme | 275
SASA | St. Asaph | 132
SBAR | Stoke Bardolph | 400
SEAB | Seabank | 400
SELL | Sellindge | 400
SELT | Sellindge Tee | 400
SELW | Sellindge West | 400
SETW | Sellindge Tee West | 400
SHBA | South Humber Bank | 400
SHEC | Sheffield City | 275
SHRE | Shrewsbury | 400
SING | Singlewell | 400
SIZE | Sizewell | 400
SIZE | Sizewell | 132
SJOW | St Johns Wood | 400
SJOW | St Johns Wood | 275
SKLG | Skelton Grange | 275
SMAN | South Manchester | 275
SPEN | Spennymoor | 400
SPEN | Spennymoor | 275
SPLN | Spalding North | 400
SSHI | South Shields | 275
STAH | Stanah | 400
STAL | Stalybridge | 400
STAL | Stalybridge | 275
STAY | Staythorpe | 400
STAY | Staythorpe | 400
STEN | Stella North | 132
STEN | Stella North | 132
STES | Stella South | 132
STES | Stella South | 132
STEW | Stella West | 400
STEW | Stella West | 275
STOB | Stoke Bardolph | 400
STSB | Stocksbridge | 400
STYC | Staythorpe | 132
SUND | Sundon | 400
SUTB | Sutton Bridge | 400
SWAN | Swansea North | 400
SWAN | Swansea North | 275
TAUN | Taunton | 400
TEMP | Templeborough | 275
THOM | Thorpe Marsh | 400
THOM | Thorpe Marsh | 275
THOM | Thorpe Marsh | 66
THOR | Brine Field | 400
THTO | Thornton | 400
THUR | Thurcroft | 275
TILB | Tilbury | 400
TILB | Tilbury | 275
TINP | Tinsley Park | 275
TOCK | Tockington | 400
TODP | Tod Point | 400
TODP | Tod Point | 275
TOTE | Tottenham East | 275
TOTT | Tottenham | 400
TOTT | Tottenham | 275
TOTW | Tottenham West | 275
TRAW | Trawsfynydd | 400
TRAW | Trawsfynydd | 275
TREM | Tremorfa | 275
TREU | Treuddyn Tee | 400
TYNE | Tynemouth | 275
UPPB | Upper Boat | 275
USKM | Uskmouth | 275
USKM | Uskmouth | 132
WALH | Walham | 400
WALP | Walpole | 400
WALP | Walpole | 132
WALP | Walpole | 132
WALX | Waltham Cross | 400
WALX | Waltham Cross | 275
WARL | Warley | 275
WASF | Washway Farm | 275
WATS | Watford South | 275
WBOL | West Boldon | 275
WBUR | West Burton | 400
WBUR | West Burton | 132
WBUR | West Burton | 132
WEAV | Weaver Junction | 25
WHAM | West Ham | 400
WHGA | Whitegate | 275
WHSO | Whitson | 400
WHSO | Whitson | 275
WIBA | Wincobank | 275
WIEN | Willenhall | 275
WILE | Willington East | 400
WILL | Willington | 275
WILL | Willington | 132
WILL | Willington | 132
WILT | Wilton | 275
WILT | Wilton | 275
WIMB | Wimbledon | 400
WIMB | Wimbledon | 275
WIMC | Wimbledon | 33
WISD | Willesden | 275
WISD | Willesden | 66
WLSD | Willesden | 400
WLSD | Willesden | 400
WMAR | Weston Marsh | 400
WMAR | Weston Marsh | 400
WMEL | West Melton | 275
WTHU | West Thurrock | 400
WWEY | West Weybridge | 400
WWEY | West Weybridge | 275
WYLF | Wylfa | 400
WYLF | Wylfa | 132
WYLF | Wylfa | 132
WYMO | Wymondley | 400

## B-1-1d
Table B1.1d - Sites Relevant to Offshore Transmission |  | Back To Menu
Code | Site
BOSO | Barrow Wind Farm Onshore Site
BOSW | Barrow Offshore Wind Farm
BUBO | Burbo Bank Extension Onshore Substation
BUBW | Burbo Bank Extension Offshore Wind Farm
BURB | Burbo Bank
CLTO | Clacton
DOCO | Docking Shoal Onshore Connection
DOCS | Docking Shoal Offshore Wind Farm
DOGG | Dogger Bank
DUDG | Dudgeon Offshore Wind Farm
DUDO | Dudgeon Onshore Substation
GAOF | Galloper Offshore Substation
GAON | Galloper Onshore
GGON | Greater Gabbard Onshore Substation
GREG | Greater Gabbard Offshore Wind Farm
GUNS | Gunfleet Sands
GWAW | Gwynt-Y-Mor Offshore Wind Farm A
GWBW | Gwynt-Y-Mor Offshore Wind Farm B
GWYO | Gwynt-Y-Mor Onshore Site
GWYW | Gwynt-Y-Mor Offshore Wind Farm
HOEA | Hornsea Offshore Wind Farm
HUMO | Humber Gateway Onshore Site
HUMW | Humber Gateway Offshore Wind Farm
IGOF | Inner Gabbard Offshore
LINO | Lincs Onshore Connection
LINS | Lincs Offshore Wind Farm
LONO | London Array Onshore Site
LONW | London Array Offshore Wind Farm
ORMO | Ormonde Onshore Connection
ORMW | Ormonde Offshore Wind Farm
RABO | Rack Bank Onshore
RACB | Race Bank
RACO | Race Bank Onshore Connection
RACW | Race Bank Offshore Windfarm
RAFO | Rack Bank Offshore
RAMP | Rampion
RORE | Robin Rigg East
RORW | Robin Rigg West
RREW | Robin Rigg East Wind Farm
RRWW | Robin Rigg West Wind Farm
SALL | Sall
SHSW | Sherringham Shoal Offshore Wind Farm
SSAW | Sherringham Shoal Offshore Platform 1
SSBW | Sherringham Shoal Offshore Platform 2
THAW | Thanet Wind Onshore Substation
THOW | Thanet Wind Offshore Substation
TRIM | Trimpell
TWIN | Twineham
WAAO | Walney 1 Onshore Site
WAAW | Walney 1 Offshore Substation
WABO | Walney 2 Onshore Site
WABW | Walney 2 Offshore Substation
WAEN | Walney Extension
WALE | Walney Extension
WDSO | West Of Duddon Sands Onshore Site
WDSW | West Of Duddon Sands Offshore Wind Farm
WDSW | West of Duddon Sands Offshore Wind Farm
WERW | Westermost Rough Wind Farm

## B-2-1a
Table B.2.1a - SHE Transmission Circuits ETYS Yr1 - 2017/18 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 132 | 123 | 106 | 123
ABNE1R | AMUL1G | 28.0986 | 0.001404 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
AIGA1Q | KIOR1Q | 2.7974 | 0.12264 | Composite | 0.264 | 0.594 | 0.66 | 111 | 103 | 89 | 103
ALNE1Q | FYRI1J | 1.2896 | 0.0104 | Composite | 0.06 | 0.28 | 0.07 | 229 | 211 | 183 | 211
ALNE1R | FYRI1K | 1.2896 | 0.0104 | Composite | 0.06 | 0.28 | 0.07 | 229 | 211 | 183 | 211
ALNE3J | BETH3- | 0 | 13.3 | Cable | 6.07 | 13.557 | 1.456 | 47.9 | 46.9 | 43.4 | 46.9
ALNE3J | NOVA3- | 0 | 8.45 | Cable | 13.36 | 25.4 | 0.09 | 22.3 | 21.1 | 18 | 21.1
ALNE3J | NOVW32 | 0 | 13 | Cable | 5.93 | 13.25 | 1.42 | 47.9 | 46.9 | 43.4 | 46.9
ALNE3J | NOVW32 | 0 | 13 | Cable | 5.93 | 13.25 | 1.42 | 47.9 | 46.9 | 43.4 | 46.9
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
ANSU3- | ANSU3W | 0 | 11 | Cable | 2.81 | 5.78 | 0.61 | 39 | 39 | 39 | 39
ARBR1Q | DENS1Q | 14.4 | 0 | OHL | 0.61 | 3.08 | 0.75 | 183 | 160 | 149 | 160
ARBR1R | TEAL1- | 23.2 | 0 | OHL | 0.99 | 4.97 | 1.2 | 183 | 160 | 149 | 160
ARDK1- | INVE1J | 9 | 0 | OHL | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123
ARDK1- | SLOY1T | 10 | 0 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123
ARDK3K | ARDK3- | 0 | 0.03 | Cable | 0.05 | 0.105 | 0 | 22.5 | 21 | 18 | 21
ARDR2Q | FYRI2J | 1.77 | 0 | OHL | 0.0113 | 0.0947 | 0.379 | 702 | 665 | 599 | 665
ARDR2Q | LOCB2K | 32.4 | 0 | OHL | 0.2027 | 1.7046 | 6.818 | 702 | 665 | 599 | 665
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 83 | 77 | 67 | 77
BEAU1J | BEAU1R | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.0078 | 0.0147 | 0.268 | 141 | 136 | 136 | 136
BEAU1J | CULL1Q | 3.542 | 10.458 | Composite | 1.43 | 3.28 | 0.69 | 111 | 103 | 89 | 103
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | BEAU1S | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | KIOR1Q | 1.2402 | 0.0598 | Composite | 0.13 | 0.29 | 0.06 | 111 | 103 | 89 | 103
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117
BEAU1N | BEAU1K | 0 | 0.25 | Cable | 0.0089 | 0.0167 | 0.305 | 141 | 136 | 136 | 136
BEAU1N | FAAR1R | 29.85 | 0 | OHL | 2.953 | 6.7683 | 1.436 | 132 | 123 | 106 | 123
BEAU1P | BEAU1L | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1Q | BEAU1M | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1R | INNE1Q | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1S | INNE1R | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1T | FAAR1Q | 29.88 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BEAU2J | FASN2- | 24.288 | 1.012 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU2J | FYRI2J | 31.73 | 0 | OHL | 0.1983 | 1.6678 | 6.671 | 702 | 665 | 599 | 665
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU2K | FYRI2K | 31.73 | 0 | OHL | 0.1986 | 1.6702 | 6.68 | 702 | 665 | 599 | 665
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU3- | TORA3- | 0 | 1 | Cable | 30.4 | 58.3 | 0 | 17 | 17 | 17 | 17
BEAU4- | FAUG4- | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BERB3- | BERB3W | 0 | 3 | Cable | 1.369 | 3.058 | 0.329 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | BERB3W | 0 | 3 | Cable | 1.369 | 3.058 | 0.329 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | BERB3W | 0 | 3 | Cable | 1.369 | 3.058 | 0.329 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | HIGL31 | 0 | 1.2 | Cable | 0.5472 | 1.223 | 0.132 | 47.9 | 46.9 | 43.4 | 46.9
BLHI2J | BERB2Q | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BLHI2J | KEIT2Q | 0 | 2.4 | Cable | 0.0124 | 0.053 | 7.983 | 349 | 293 | 293 | 293
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2K | KEIT2R | 0 | 2.4 | Cable | 0.0124 | 0.053 | 7.983 | 349 | 293 | 293 | 293
BLHI2L | KINT2J | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2M | PEHERSV1 | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BOAG1Q | FAAR1Q | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOAG1Q | GLFA1- | 33 | 0 | OHL | 3.3496 | 7.6799 | 1.633 | 126 | 117 | 101 | 117
BOAG1R | FAAR1R | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOYN3Q | BOYN3- | 0 | 1 | Cable | 1.17 | 1.12 | 0.08 | 26 | 26 | 26 | 26
BRCW2J | TUMM2K | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
BRCW2K | BONB2J | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BRCW3- | BRDU3J | 0 | 11 | Cable | 3.647 | 10.472 | 1.242 | 49 | 49 | 49 | 49
BRCW3- | BRDU3K | 0 | 11 | Cable | 3.647 | 10.472 | 1.242 | 49 | 49 | 49 | 49
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1Q | FIDD1B | 30.1 | 0 | OHL | 3.54 | 7.26 | 1.48 | 112 | 104 | 90 | 104
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BRID3- | TULW39 | 0 | 10 | Cable | 17 | 35 | 0 | 22.5 | 21 | 18 | 21
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 83 | 77 | 67 | 77
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 83 | 77 | 67 | 77
BROR1- | BROR1Q | 0 | 1.1 | Cable | 0.12 | 0.27 | 0.06 | 111 | 103 | 89 | 103
BROR1Q | DUBE1Q | 38.7224 | 0.077599 | Composite | 3.94 | 9.01 | 1.91 | 126 | 117 | 101 | 117
BROR1Q | LOCB1K | 22.12 | 0 | OHL | 2.2511 | 5.1536 | 1.096 | 126 | 117 | 101 | 117
BUMU1Q | CHAR1- | 38.4999 | 3.7001 | Composite | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
BUMU1R | AMUL1E | 13.9486 | 3.8514 | Composite | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD3- | TANG3- | 0 | 1 | Cable | 36.41 | 76.64 | 0.46 | 22.3 | 21.1 | 18 | 21.1
CAAD3J | BTUI3- | 0 | 1 | Cable | 2.75 | 6.06 | 0.61 | 39.4 | 39.4 | 39.4 | 39.4
CAAD3J | BTUI3K | 0 | 9 | Cable | 4.21 | 8.68 | 0.92 | 47.9 | 43.4 | 43.4 | 43.4
CAAD3J | DEUC3- | 0 | 1 | Cable | 12.08 | 24.84 | 0 | 22.3 | 21.1 | 18 | 21.1
CAIN2- | BLHI2K | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880
CAIN3J | CLAS3K | 0 | 8 | Cable | 1.469 | 3.93 | 1.915 | 107.4 | 97.6 | 97.6 | 97.6
CASH3- | LUBR3- | 0 | 1 | Cable | 9 | 20 | 0 | 24 | 24 | 24 | 24
CASS1Q | LAIR1Q | 28 | 0 | OHL | 2.84 | 6.75 | 1.33 | 111 | 103 | 89 | 103
CEAN1Q | BEIN11 | 2.85 | 0 | OHL | 0.2926 | 0.6622 | 0.139 | 111 | 103 | 89 | 103
CHAR1- | BIHI1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
CHAR1- | CHAR1R | 0 | 1 | Cable | 0 | 0.01 | 0 | 229 | 211 | 183 | 211
CHAR1- | CHAR1S | 0 | 1 | Cable | 0 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1T | 0 | 1 | Cable | 0 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1R | BIHI1Q | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
CHAR1S | GLAG1Q | 1.4983 | 2.2017 | Composite | 0.2 | 0.46 | 4.13 | 126 | 117 | 101 | 117
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 1.4983 | 2.2017 | Composite | 0.2 | 0.46 | 4.13 | 126 | 117 | 101 | 117
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117
CLAC1Q | SLOY1K | 14.2 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
CLAY1Q | WIOW1Q | 2.1 | 0 | OHL | 0.08 | 0.12 | 4.19 | 120 | 100 | 100 | 100
CLAY1S | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1T | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1R | CLUN1T | 0 | 1 | Cable | 0 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 203 | 193 | 176 | 193
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 203 | 193 | 176 | 193
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN5J | CLUN5K | 0 | 1 | Cable | 0 | 25 | 0 | 20 | 20 | 20 | 20
CLUN5J | PITL5J | 0 | 1 | Cable | 33.28 | 15.3 | 0 | 12.2 | 12.2 | 12.2 | 12.2
CLUN5J | PITL5K | 0 | 1 | Cable | 33.28 | 15.3 | 0 | 12.2 | 12.2 | 12.2 | 12.2
COGA1- | COGA1C | 15 | 0 | OHL | 0.7569 | 3.1062 | 0.84 | 162 | 154 | 141 | 154
CONN1C | STRW1C | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 203 | 193 | 176 | 193
CONN1J | CONN1C | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 77.05 | 0 | OHL | 0.4822 | 4.0551 | 16.217 | 702 | 665 | 599 | 665
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211
CORI3- | LOCL3- | 0 | 2.6 | Cable | 0.48 | 1.28 | 0.62 | 107 | 98 | 98 | 98
CORI3K | CORI3J | 0 | 1 | Cable | 0.468 | 0.5 | 0.186 | 67.2 | 65.8 | 61 | 65.8
COUA1Q | BIHI1Q | 14.6 | 0 | OHL | 0.924 | 3.31 | 0.745 | 126 | 117 | 101 | 117
COUA1R | BIHI1R | 14.6 | 0 | OHL | 0.924 | 3.31 | 0.745 | 126 | 117 | 101 | 117
COUA3- | COUA38 | 0 | 24.3 | Cable | 35.9901 | 76.7099 | 0 | 22.3 | 21.1 | 18 | 21.1
COUA3- | COUA39 | 0 | 17.39 | Cable | 23.92 | 52.7901 | 0.01 | 22.3 | 21.1 | 18 | 21.1
COUA3- | TLYM3- | 0 | 19 | Cable | 22.61 | 19.95 | 0 | 24.9 | 22.6 | 22.6 | 22.6
COUW31 | COUW32 | 0 | 4 | Cable | 4.776 | 4.152 | 0.34 | 29.4 | 26.7 | 26.7 | 26.7
COUW31 | FRSD3- | 0 | 9 | Cable | 4.104 | 9.171 | 0.99 | 47.9 | 46.9 | 43.4 | 46.9
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0 | 0.01 | 0 | 145 | 131 | 116 | 131
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | KINT1- | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.91 | 202 | 193 | 176 | 193
CRAI1- | KINT1- | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.91 | 202 | 193 | 176 | 193
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103
DAAS3- | CAIR3W | 0 | 1 | Cable | 1.193 | 3.427 | 0.406 | 49 | 49 | 49 | 49
DAAS3- | CAIR3W | 0 | 1 | Cable | 1.193 | 3.427 | 0.406 | 49 | 49 | 49 | 49
DAAS3- | CAIR3W | 0 | 1 | Cable | 1.193 | 3.427 | 0.406 | 49 | 49 | 49 | 49
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.37 | 1.86 | 0.45 | 183 | 160 | 149 | 160
DOUN1- | THSO1Q | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 132 | 123 | 106 | 123
DOUN1- | THSO1R | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 132 | 123 | 106 | 123
DOUN2- | CONN2J | 10.34 | 0 | OHL | 0.0647 | 0.5443 | 2.177 | 702 | 665 | 599 | 665
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.4621 | 3.1663 | 12.268 | 535 | 490 | 430 | 490
DUBE1Q | MYBS1R | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 117 | 101 | 117
DUBE3- | DUBE3D | 0 | 1 | Cable | 4.55 | 1.13 | 0.216 | 26 | 26 | 26 | 26
DUDH1Q | GLAG1Q | 0 | 1.6 | Cable | 0.036 | 0.0955 | 2.207 | 155 | 129 | 129 | 129
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 0 | 1.6 | Cable | 0.036 | 0.0955 | 2.207 | 155 | 129 | 129 | 129
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 83 | 77 | 67 | 77
DUGR3- | BENA3- | 0 | 5 | Cable | 5.3 | 14.55 | 0 | 34.3 | 32.3 | 29.2 | 32.3
DUNM1- | DUNM1C | 6.5 | 0 | OHL | 0.328 | 1.346 | 0.364 | 162 | 154 | 141 | 154
DYCE1Q | KINT1- | 11.7 | 0 | OHL | 0.83 | 2.65 | 1.82 | 145 | 131 | 116 | 131
DYCE1R | KINT1- | 11.7 | 0 | OHL | 0.83 | 2.65 | 1.82 | 145 | 131 | 116 | 131
DYCE3- | STOM3- | 0 | 1 | Cable | 3.51 | 3.023 | 0 | 24 | 24 | 24 | 24
ELGI1L | NAIR1Q | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1M | NAIR1R | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1Q | ELGI1L | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1Q | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1R | ELGI1M | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1R | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ERRO1A | TUMM1J | 1.33 | 0 | OHL | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280
ERRO1B | TUMM1K | 1.268 | 0.032019 | Composite | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280
ERRO1J | ERRO1A | 0 | 1 | Cable | 0 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1K | ERRO1B | 0 | 1 | Cable | 0 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123
FARI1J | COGA1C | 0 | 4 | Cable | 0.0764 | 0.3258 | 5.798 | 176 | 176 | 176 | 176
FARI1K | DUNM1C | 4 | 0 | OHL | 0.0764 | 0.3258 | 5.798 | 176 | 176 | 176 | 176
FASN2- | FAUG2J | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.005 | 0.012 | 0.002 | 126 | 117 | 101 | 117
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127
FAUG1- | LAGG1Q | 6.4 | 0 | OHL | 0.4635 | 1.455 | 0.321 | 221 | 216 | 208 | 216
FAUG1- | LAGG1R | 6.4 | 0 | OHL | 0.4635 | 1.455 | 0.321 | 221 | 216 | 208 | 216
FAUG1- | LOCL1Q | 8.5 | 0 | OHL | 0.87 | 1.98 | 0.42 | 126 | 117 | 101 | 117
FAUG1- | LOCL1R | 8.5 | 0 | OHL | 0.87 | 1.98 | 0.42 | 126 | 117 | 101 | 117
FAUG1- | LOCL1S | 8.5 | 0 | OHL | 0.8616 | 1.9747 | 0.419 | 111 | 103 | 89 | 103
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FERO1- | FERO1S | 0 | 16.5 | Cable | 1.68 | 3.84 | 0.81 | 132 | 123 | 106 | 123
FETT2P | FETT2R | 0 | 1 | Cable | 0 | 0.01 | 0 | 999 | 999 | 999 | 999
FETT2Q | FETT2R | 0 | 1 | Cable | 0 | 0.01 | 0 | 999 | 999 | 999 | 999
FETT2Q | KINB2J | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT3S | MIHW3- | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 48.6 | 48.6 | 48.6 | 48.6
FETT3S | MIHW3- | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 48.6 | 48.6 | 48.6 | 48.6
FIDD1Q | FOGG1R | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD3- | TULW3- | 0 | 15 | Cable | 11.1 | 14.4 | 1.53 | 38.3 | 38.1 | 34.8 | 38.1
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 132 | 126 | 106 | 126
FOYE2- | FARI2J | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FOYE2- | FARI2K | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FOYE2- | FOYE2J | 0 | 1 | Cable | 0.004 | 0.024 | 6.22 | 400 | 400 | 400 | 400
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 133 | 124 | 107 | 124
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 117 | 101 | 117
FWIL1R | KILO1- | 24.5 | 0 | OHL | 1.7 | 5.55 | 1.25 | 132 | 123 | 106 | 123
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.55 | 8.11 | 1.73 | 126 | 117 | 101 | 117
FYRI2K | LOCB2J | 34.1599 | 0 | OHL | 0.2138 | 1.7981 | 7.191 | 702 | 665 | 599 | 665
GLDO8- | GLDO8J | 0 | 1.2 | Cable | 0.39 | 1.02 | 0.01 | 131 | 131 | 131 | 131
GLEN1Q | BHLA11 | 0 | 7.4 | Cable | 0.0986 | 0.5669 | 10.047 | 220 | 211 | 211 | 211
GLEN1Q | LAGG1Q | 5 | 0 | OHL | 0.3605 | 1.179 | 0.241 | 221 | 216 | 208 | 216
GLFA3- | PAUH3- | 0 | 1 | Cable | 4.193 | 12.043 | 1.428 | 49 | 49 | 49 | 49
GLFA3- | PAUH3- | 0 | 1 | Cable | 4.193 | 12.043 | 1.428 | 49 | 49 | 49 | 49
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0819 | 0.5613 | 2.175 | 535 | 490 | 430 | 490
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211
HYWD30 | HYWD31 | 0 | 1.5 | Cable | 0.58 | 1.41 | 0.17 | 40.6 | 40.6 | 40.6 | 40.6
HYWD31 | HYWD32 | 0 | 26 | Cable | 19.11 | 26.26 | 2.31 | 32.6 | 32.6 | 32.6 | 32.6
INGA1Q | LOCL1R | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
INNE1J | KNOC1J | 4.57 | 0 | OHL | 0.1051 | 0.3818 | 6.326 | 171 | 165 | 165 | 165
INNE1L | KNOC1J | 4.48 | 0 | OHL | 0.1042 | 0.3784 | 6.27 | 171 | 165 | 165 | 165
INNE1Q | NAIR1Q | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1R | INNE1T | 0 | 1 | Cable | 0 | 0.001 | 0 | 126 | 117 | 101 | 117
INNE1T | NAIR1R | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE3- | MOYW3- | 0 | 17.5 | Cable | 3.99 | 8.9 | 3.83 | 95.8 | 93.8 | 86.8 | 93.8
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 142 | 128 | 142
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.18 | 0.41 | 0.09 | 126 | 117 | 101 | 117
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.311 | 1.3664 | 0.317 | 202 | 193 | 176 | 193
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 117 | 101 | 117
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.18 | 0.41 | 0.09 | 126 | 117 | 101 | 117
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.311 | 1.3664 | 0.317 | 202 | 193 | 176 | 193
INRU1S | PEHE1- | 3 | 0 | OHL | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181
INVE1J | ACHR1R | 21.17 | 0 | OHL | 3.002 | 4.9754 | 1.035 | 99 | 92 | 79 | 92
INVE1J | FERO1S | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
INVE1K | ANSU1- | 11.13 | 0 | OHL | 1.578 | 2.615 | 0.544 | 99 | 92 | 79 | 92
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
INVE1K | SLOY1J | 22.6 | 0 | OHL | 2.29 | 5.25 | 1.11 | 126 | 117 | 101 | 117
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126
KEIT1- | GLFA1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117
KEIT1- | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT3- | EDNT3- | 0 | 4.55 | Cable | 5.43 | 4.72 | 0.39 | 29.4 | 26.7 | 26.7 | 26.7
KEIT3- | GLOF3J | 0 | 25.5 | Cable | 62.749 | 83.8449 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KEIT3- | KEIT39 | 0 | 18.6 | Cable | 47.608 | 52.757 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
KEITH3A | HITO3- | 0 | 9 | Cable | 0.73 | 0.97 | 0.11 | 38.3 | 37.5 | 34.8 | 37.5
KEITH3A | HITO3- | 0 | 9 | Cable | 0.73 | 0.97 | 0.11 | 38.3 | 37.5 | 34.8 | 37.5
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 132 | 126 | 106 | 126
KIIN3- | LOCH3- | 0 | 1 | Cable | 3 | 7 | 0 | 24 | 24 | 24 | 24
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99 | 92 | 79 | 92
KILC1Q | TAYN1Q | 7.562 | 0.038 | Composite | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILO3- | KILO3Q | 0 | 1 | Cable | 0.8 | 3.24 | 0.01 | 43 | 41 | 38 | 41
KINT1- | FOGG1Q | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 104 | 90 | 104
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030
KINT2J | TEAL2J | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | FETT2P | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 880 | 760 | 880
KINT2K | FETT2Q | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 885 | 760 | 885
KINT2K | PEHE2Q | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KINT2K | TEAL2K | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT3- | GLOF3K | 0 | 33.7 | Cable | 82.928 | 115.3029 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KINT3- | GOHI3- | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
KNOC2J | BERB2Q | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
KNOC2J | FARI2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.0024 | 0.042 | 8.36 | 930 | 900 | 900 | 900
KNOC2K | DAAS2- | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
KNOC2K | FARI2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
KNOC2M | KNOC2K | 0 | 1.29 | Cable | 0.0021 | 0.037 | 7.336 | 930 | 900 | 900 | 900
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.411 | 1.3441 | 0.275 | 221 | 216 | 208 | 216
LAIR1Q | SHIN1- | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 111 | 103 | 89 | 103
LAIR3- | LAIR3W | 0 | 10 | Cable | 4.564 | 10.193 | 1.095 | 40 | 40 | 40 | 40
LAIR3- | LAIR3W | 0 | 10 | Cable | 4.564 | 10.193 | 1.095 | 40 | 40 | 40 | 40
LOCH3- | LUBR3- | 0 | 1 | Cable | 21 | 45 | 0 | 24 | 24 | 24 | 24
LOCL1S | QUOI1Q | 18.3 | 0 | OHL | 1.91 | 4.54 | 0.9 | 111 | 103 | 89 | 103
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 133 | 124 | 107 | 124
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 133 | 124 | 107 | 124
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
MACD3- | BOYN3Q | 0 | 8 | Cable | 5.95 | 7.71 | 0.82 | 38.3 | 37.5 | 34.8 | 37.5
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILW1S | BEIN11 | 0.85 | 0 | OHL | 0.0874 | 0.1978 | 0.041 | 111 | 103 | 89 | 103
MILW1S | MILW1Q | 0 | 1.3 | Cable | 0.17 | 0.29 | 0.07 | 83 | 77 | 67 | 77
MOSS1Q | MOSS1S | 0 | 0.21 | Cable | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOSS1R | MOSS1T | 0 | 0.21 | Cable | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MYBS1Q | LOCB1J | 81.61 | 0 | OHL | 8.2998 | 19.0008 | 4.028 | 126 | 117 | 101 | 117
MYBS1Q | MYBS1S | 0 | 1 | Cable | 0 | 0.01 | 0 | 999 | 999 | 999 | 999
MYBS1R | MYBS1T | 0 | 1 | Cable | 0 | 0.01 | 0 | 999 | 999 | 999 | 999
MYBS1S | THSO1Q | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 117 | 101 | 117
MYBS1T | THSO1R | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 117 | 101 | 117
MYBS3J | BUWH3- | 0 | 20 | Cable | 2.388 | 20.6999 | 1.7 | 32.6 | 28.8 | 26.7 | 28.8
MYBS3K | CAMW3W | 0 | 12 | Cable | 3.24 | 5.52 | 2.64 | 75.7 | 66.9 | 62.1 | 66.9
MYBS3K | CAUS3J | 0 | 1 | Cable | 0 | 0.01 | 0 | 34 | 34 | 34 | 34
MYBS3K | CAUS3K | 0 | 1 | Cable | 0 | 0.01 | 0 | 34 | 34 | 34 | 34
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1R | ORRI1T | 0 | 1 | Cable | 0 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1S | DUCC1J | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
ORRI1T | DUCC1K | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
ORRI3- | FAWI3W | 0 | 3.5 | Cable | 1.28 | 3.44 | 0.69 | 59.5 | 52.7 | 48.8 | 52.7
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHG3- | HYWD30 | 0 | 0.5 | Cable | 0.19 | 0.47 | 0.06 | 40.6 | 40.6 | 40.6 | 40.6
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PORA1Q | ANSU1- | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99 | 92 | 79 | 92
PORA1Q | CRSS1Q | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
PORA1R | ACHR1R | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
PORA1R | CRSS1R | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
QUOI1- | QUOI1Q | 0 | 1.6 | Cable | 0.12 | 0.28 | 0.05 | 111 | 103 | 89 | 103
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
SFEG1Q | SFEG1S | 0.4 | 0 | OHL | 0.009 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1R | SFEG1T | 0.4 | 0 | OHL | 0.009 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1S | SFEG1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFEM5J | SFEM5K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1L | SFEG1Q | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 117 | 101 | 117
SFER1L | SFEM1Q | 3.1 | 0 | OHL | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1M | SFEG1R | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 117 | 101 | 117
SFER1M | SFEM1R | 3.1 | 0 | OHL | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SHIN1- | LOCB1J | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 117 | 101 | 117
SHIN1- | LOCB1K | 12.18 | 0 | OHL | 1.239 | 2.8364 | 0.604 | 126 | 117 | 101 | 117
SHIN3- | ROSH3- | 0 | 9.5 | Cable | 8.93 | 9.5 | 0.855 | 33.6 | 32 | 30.5 | 32
SLOY1J | GARB1R | 14.1848 | 0.7152 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
SLOY1J | GARB1S | 14.2295 | 0.6705 | Composite | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
SLOY1J | SLOY1N | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 117 | 101 | 117
SLOY1J | SLOY1P | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 117 | 101 | 117
SLOY1J | SLOY1T | 0 | 5.4 | Cable | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123
SLOY1K | GARB1Q | 14.2295 | 0.6705 | Composite | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
SLOY1K | GARB1T | 14.1848 | 0.7152 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
SLOY1K | INVR1- | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126
SLOY1K | SLOY1L | 1.2896 | 0.0104 | Composite | 0.13 | 0.3 | 0.06 | 126 | 117 | 101 | 117
SLOY1K | SLOY1M | 1.2896 | 0.0104 | Composite | 0.13 | 0.3 | 0.06 | 126 | 117 | 101 | 117
STRB2- | LOCB2K | 18.9 | 0 | OHL | 0.1503 | 1.0299 | 3.991 | 535 | 490 | 430 | 490
STRW12 | STRW1C | 0 | 0.35 | Cable | 0.0075 | 0.0631 | 0.48 | 200 | 178 | 178 | 178
TARL1Q | FOGG1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
TARL1R | FOGG1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
TARL3- | TARL3J | 0 | 9.8 | Cable | 15.17 | 32.24 | 0 | 26.5 | 24.7 | 21.3 | 24.7
TARL3J | TARL3K | 0 | 15.3 | Cable | 25.2501 | 50.7999 | 0 | 25.2 | 23.9 | 21.6 | 23.9
TAYN1R | FERO1S | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92
TAYN3- | BGLA3- | 0 | 1 | Cable | 9.88 | 18.92 | 0 | 22.3 | 21.1 | 18 | 21.1
TAYN3- | INAW3Q | 0 | 1 | Cable | 2.04 | 1.59 | 0.05 | 30 | 30 | 30 | 30
TAYN3- | TULL3- | 0 | 1 | Cable | 43.72 | 58.19 | 0 | 17.1 | 16.3 | 13.7 | 16.3
TEAL1- | BIHI1Q | 5.4992 | 0.1008 | Composite | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
TEAL1- | BIHI1R | 5.4992 | 0.1008 | Composite | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
TEAL2J | KINB2K | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
TEAL2J | WFIB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2K | FETT2P | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
TEAL2K | GLRB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
THSO3- | STRS30 | 0 | 27 | Cable | 12.32 | 27.5199 | 2.96 | 47.9 | 43.4 | 43.4 | 43.4
TULL3- | BGLA3- | 0 | 1 | Cable | 20.75 | 39.73 | 0 | 22.3 | 21.1 | 18 | 21.1
TUMM4- | BONB4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670
TUMM4- | FAUG4- | 77.2 | 0 | OHL | 0.1 | 1.478 | 46.678 | 2780 | 2670 | 2480 | 2670
WHIB1A | ERRO1J | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1B | ERRO1K | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1G | GRIF1T | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
WHIB1H | GRIF1S | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
WIOW1Q | WOHI1Q | 3.4 | 0 | OHL | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147
WIOW1R | WOHI1R | 3.4 | 0 | OHL | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147

## B-2-1b
Table B.2.1b - SPT Circuits ETYS Yr1 - 2017/18 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.43633 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.2827 | 40.2207 | 0.73923 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.10903 | 0.83007 | 2.9503 | 825 | 825 | 825 | 825
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 2e-06 | 0.008959 | 0.068205 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.042235 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.042235 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 18.3 | 0 | Composite | 0.72346 | 4.1003 | 0.94648 | 146 | 146 | 146 | 146
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.57893 | 1.4999 | 2.8685 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | Composite | 0.7274 | 4.1221 | 0.95179 | 146 | 146 | 146 | 146
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.57849 | 1.4988 | 2.8607 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.27901 | 1.5909 | 0.45411 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.28257 | 1.61 | 0.68748 | 114 | 114 | 114 | 114
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.9576 | 4.8683 | 1.5223 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.9569 | 4.8645 | 1.4665 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.029369 | 0.20425 | 0.073319 | 352 | 325 | 281 | 325
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.029369 | 0.20425 | 0.073319 | 352 | 325 | 281 | 325
BLAH1- | GLGL1Q | 13.6 | 0 | OHL | 0.51007 | 2.9138 | 0.73138 | 297 | 281 | 258 | 281
BLAH1- | GLGL1R | 13.6 | 0 | OHL | 0.51007 | 2.9138 | 0.73138 | 297 | 281 | 258 | 281
BLCW1- | MARG1- | 1.8 | 0 | OHL | 0.13522 | 0.39606 | 0.094795 | 166 | 159 | 147 | 159
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.65421 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | Composite | 0.053996 | 0.77395 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | Composite | 0.025521 | 0.36581 | 12.2976 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.43048 | 2.4371 | 0.56389 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.43048 | 2.4371 | 0.56389 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 4.04 | 0.3 | Composite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234
BONN1- | STIR1Q | 11.554 | 1.014 | Composite | 0.63316 | 2.6867 | 2.2664 | 183 | 161 | 161 | 161
BONN1- | STIR1R | 11.554 | 1.014 | Composite | 0.63316 | 2.6867 | 2.2664 | 183 | 183 | 183 | 183
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.018312 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.018128 | 0.17091 | 3.8346 | 722 | 647 | 593 | 647
BRAE1G | BRAP1- | 0 | 2.5 | Cable | 0.049788 | 0.20805 | 3.5991 | 250 | 250 | 250 | 250
BRAE1G | GOVA1R | 0 | 3.5 | Cable | 0.152 | 0.239 | 6.934 | 125 | 113 | 110 | 113
BRAE1P | GOVA1Q | 0 | 3.5 | Cable | 0.152 | 0.239 | 6.934 | 125 | 113 | 110 | 113
BRAE1P | PAIS1Q | 4.52 | 0 | OHL | 0.088475 | 0.81418 | 0.28325 | 268 | 268 | 268 | 268
BRAP1- | ERSK1Q | 3.17 | 5.19 | Composite | 0.46169 | 1.3227 | 5.2679 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6 | Composite | 0.47611 | 1.4486 | 6.408 | 102 | 79 | 79 | 79
BRAP1- | PAIS1R | 4.52 | 2.59 | Composite | 0.13891 | 1.0296 | 4.2464 | 274 | 274 | 274 | 274
BROX1Q | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.50503 | 132 | 123 | 106 | 123
BROX1R | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.50503 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.085598 | 0.82668 | 5.625 | 1090 | 1030 | 885 | 1030
BUSB2- | STHA2A | 15.14 | 0 | Composite | 0.06403 | 0.61807 | 4.2097 | 750 | 690 | 630 | 690
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.23373 | 0.52392 | 0.14546 | 132 | 123 | 106 | 123
CAFA5- | CAFA5R | 0 | 0 | Series Reactor | 0.33333 | 21.1544 | 0 | 30 | 30 | 30 | 30
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.30183 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.30183 | 6.1089 | 122 | 107 | 107 | 107
CHAP1- | DUMF1- | 26.9 | 0.17 | Composite | 1.0663 | 6.0851 | 1.9201 | 171 | 171 | 171 | 171
CHAP1- | DUMF1- | 26.9 | 0 | OHL | 1.0626 | 6.0703 | 1.3831 | 171 | 171 | 171 | 171
CHAP1- | ECCF1J | 6.569 | 0.181 | Composite | 0.60032 | 1.5098 | 0.90161 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.126 | Composite | 0.5991 | 1.505 | 0.72789 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.1811 | 3.0837 | 0.98781 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 1.1797 | 3.0784 | 0.93581 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.018976 | 0.17128 | 1.1692 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.019276 | 0.17367 | 1.8402 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 9.17 | 0 | OHL | 0.020719 | 0.32323 | 2.9288 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.02534 | 0.23914 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.02534 | 0.23914 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.22 | 0 | Composite | 0.1223 | 1.9018 | 17.3649 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.058 | 0.079 | 24.356 | 291 | 245 | 245 | 245
COAL1- | GAWH1Q | 0 | 10.5 | Cable | 0.16512 | 0.90393 | 17.3003 | 241 | 241 | 241 | 241
COAL1- | LINM1Q | 8.97 | 0 | OHL | 0.246 | 1.521 | 3.108 | 134 | 123 | 123 | 123
COAL1- | LINM1R | 8.91 | 0 | OHL | 0.244 | 1.516 | 3.055 | 134 | 123 | 123 | 123
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.04674 | 0.50618 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038025 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.044995 | 0.24764 | 17.1398 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.044995 | 0.24764 | 17.1398 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | Composite | 0.083028 | 0.75323 | 5.0595 | 1090 | 1030 | 925 | 1030
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.043169 | 0.39156 | 2.6311 | 1090 | 1030 | 925 | 1030
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.14268 | 1.4132 | 35.4499 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.14266 | 1.4129 | 35.4444 | 1090 | 1030 | 925 | 1030
COYL1- | COYT1T | 4.64 | 0 | OHL | 0.4212 | 1.0554 | 0.23305 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.716 | 0 | Composite | 0.8819 | 2.2528 | 0.47949 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.285 | 0.08 | Composite | 0.005707 | 0.051257 | 0.46302 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.36 | 0 | OHL | 0.005989 | 0.053812 | 0.38896 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.36123 | 2.813 | 10.0797 | 825 | 825 | 825 | 825
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.052942 | 0.57335 | 4.0467 | 1380 | 1310 | 1200 | 1310
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.052942 | 0.57335 | 4.0467 | 1380 | 1310 | 1200 | 1310
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.946 | 0 | Composite | 1.6352 | 4.1661 | 0.89142 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 14.135 | 0 | Composite | 0.062197 | 0.55721 | 4.0537 | 1200 | 1120 | 1020 | 1120
COYW2T | KILS2- | 14.135 | 0 | Composite | 0.062197 | 0.55721 | 4.0537 | 1200 | 1120 | 1020 | 1120
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.49414 | 2.6834 | 0.98398 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.49426 | 2.6844 | 0.99793 | 229 | 211 | 183 | 211
CRUA2Q | CRUA2S | 0 | 0.4 | Cable | 0.0001 | 0.010256 | 2.0513 | 283 | 283 | 283 | 283
CRUA2R | CRUA2T | 0 | 0.4 | Cable | 0.0001 | 0.010256 | 2.0513 | 283 | 283 | 283 | 283
CRUA2S | CRUA2T | 0 | 0 | Cable | 0 | 0 | 0 | 955 | 885 | 760 | 885
CRUA2S | DALL2- | 8.16 | 0 | OHL | 0.034509 | 0.33329 | 2.2691 | 570 | 570 | 570 | 570
CRUA2T | DALL2- | 8.16 | 0 | OHL | 0.034509 | 0.33329 | 2.2691 | 570 | 570 | 570 | 570
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.055895 | 0.34727 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.01824 | 0.27316 | 8.1821 | 2473 | 2349 | 2148 | 2349
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.014288 | 0.21702 | 44.1376 | 935 | 935 | 935 | 935
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2119 | 3.1514 | 0.64519 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2119 | 3.1514 | 0.64519 | 143 | 142 | 128 | 142
CURR1A | GORG1R | 1.49 | 5.78 | Composite | 0.26273 | 0.96133 | 5.0951 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.79262 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123
CURR1B | GORG1Q | 1.49 | 5.8 | Composite | 0.26343 | 0.9635 | 5.1125 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.18 | 0 | OHL | 0.19147 | 1.7367 | 11.6698 | 1090 | 1030 | 920 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.042442 | 0.38498 | 2.5868 | 1090 | 1030 | 925 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.042442 | 0.38498 | 2.5868 | 1090 | 1030 | 925 | 1030
CURR2- | KINC2- | 55.82 | 0 | Composite | 0.25338 | 2.2983 | 15.4435 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.017366 | 0.10338 | 6.0397 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.017184 | 0.10272 | 5.9404 | 120 | 120 | 120 | 120
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.1017 | 0.93586 | 6.1334 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | Composite | 0.35245 | 3.2434 | 21.2562 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.19545 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.16321 | 0.21894 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 32.08 | 0 | OHL | 0.1446 | 1.3051 | 8.9091 | 957 | 881 | 762 | 881
DENN2- | LOAN2- | 21.59 | 0 | Composite | 0.049814 | 0.76944 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.56525 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 123 | 106 | 123
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.69149 | 1.7146 | 0.38601 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.68057 | 1.6869 | 0.38005 | 107 | 107 | 101 | 107
DEVM4- | HUNE4- | 50.471 | 0.167 | Composite | 0.090947 | 0.99844 | 33.1263 | 1316 | 1067 | 1067 | 1067
DEVM4- | WIYH4Q | 28.908 | 0 | Composite | 0.047022 | 0.54436 | 17.7745 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1Q | 8.88 | 0 | OHL | 0.47533 | 2.0513 | 0.44851 | 221 | 219 | 191 | 219
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8818 | 7.1428 | 1.6093 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.015938 | 0.055946 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.016387 | 0.057525 | 7.9728 | 276 | 240 | 240 | 240
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.011288 | 0.10808 | 3.8932 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.011088 | 0.10008 | 0.68318 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNB1Q | INWI1Q | 11.6 | 0 | OHL | 1.0594 | 2.7548 | 0.56399 | 110 | 100 | 90 | 100
DUNB1R | INWI1R | 11.6 | 0 | OHL | 1.0594 | 2.7548 | 0.56399 | 110 | 100 | 90 | 100
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 152 | 122 | 122 | 122
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.69618 | 1.8068 | 0.54442 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1- | 10.46 | 0 | OHL | 0.56015 | 2.4346 | 0.52443 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.69618 | 1.8068 | 0.54442 | 132 | 122 | 106 | 122
DUNF1R | MOSM1- | 10.46 | 0 | OHL | 0.56015 | 2.4346 | 0.52443 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.1 | Cable | 0.005 | 0.011 | 0.082109 | 133 | 133 | 133 | 133
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.35426 | 2.6353 | 0.81689 | 352 | 325 | 281 | 325
DUNH1R | DUNH1T | 0 | 0.1 | Cable | 0.005 | 0.011 | 0.082109 | 133 | 133 | 133 | 133
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.35426 | 2.6353 | 0.81689 | 352 | 325 | 281 | 325
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.2953 | 3.8622 | 0.97647 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.2953 | 3.8622 | 0.97647 | 99 | 92 | 79 | 92
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.15364 | 0.35035 | 0.093986 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | Composite | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | Composite | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.044712 | 0.65435 | 67.6758 | 1165 | 920 | 920 | 920
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.044712 | 0.65435 | 67.6758 | 1165 | 920 | 920 | 920
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.006329 | 0.12087 | 5.1175 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.006329 | 0.12087 | 5.1175 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 46.23 | 0 | Composite | 0.10429 | 1.6221 | 14.8036 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.013751 | 0.18345 | 1.6594 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.021597 | 0.20382 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.014086 | 0.18599 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.021597 | 0.20382 | 1.2722 | 1050 | 965 | 880 | 965
EKIS2- | NEIL2- | 29.58 | 0 | Composite | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030
EKIS2- | STHA2B | 5.8 | 0 | Composite | 0.024529 | 0.23659 | 1.614 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 0 | 2.79 | Cable | 0.12 | 0.559 | 0.684 | 229 | 211 | 183 | 211
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.15168 | 0.82706 | 0.45695 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 0 | 2.79 | Cable | 0.121 | 0.561 | 0.73 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1523 | 0.83189 | 0.52666 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 65.54 | 0 | Composite | 0.11553 | 1.2673 | 38.8356 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.041424 | 0.45436 | 13.9258 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | Composite | 0.084978 | 0.92036 | 29.0717 | 2210 | 2130 | 1980 | 2130
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.071083 | 0.32554 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
ESST1R | KIER1R | 0 | 4.56 | Cable | 0.133 | 0.19 | 8.531 | 100 | 80 | 60 | 80
ESST1R | WIYH1- | 2.089 | 1.376 | Composite | 0.23673 | 0.64971 | 2.5726 | 233 | 200 | 200 | 200
EWEH1Q | GRNA1- | 15.7 | 0.12 | Composite | 1.1828 | 3.4623 | 0.98442 | 122 | 107 | 107 | 107
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.040928 | 0.61294 | 18.3596 | 2473 | 2349 | 2148 | 2349
FIFE1A | WFIE1A | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 100 | 100 | 100
FIFE1B | WFIE1B | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 100 | 100 | 100
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.056344 | 0.15821 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.056985 | 0.16001 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1- | 15.3129 | 0 | Composite | 1.3875 | 3.4126 | 0.78035 | 132 | 123 | 106 | 123
GARB1R | STLE1- | 26.9091 | 0 | Composite | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.0304 | 0 | OHL | 0.45581 | 1.1211 | 0.25635 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.0609 | 0 | OHL | 0.45857 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.21304 | 0.35846 | 0.090638 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.0819 | 0.3304 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.21178 | 0.35635 | 0.090094 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.7398 | 0.1623 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105
GLLE1- | KEOO1- | 7.68 | 0 | Composite | 0.69687 | 1.6787 | 0.405 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLNI1- | MOSM1- | 1.41 | 0.09 | Composite | 0.065707 | 0.25619 | 0.37333 | 171 | 171 | 171 | 171
GLNI1- | MOSM1- | 1.41 | 0.11 | Composite | 0.065976 | 0.25792 | 0.43573 | 130 | 125 | 110 | 125
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.95552 | 2.3056 | 0.55203 | 161 | 156 | 145 | 156
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.35905 | 0.7999 | 0.7252 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.53 | 0 | OHL | 0.065645 | 0.6071 | 3.9361 | 875 | 875 | 760 | 875
GLRO2- | WFIE2- | 11.92 | 0 | OHL | 0.053872 | 0.4987 | 3.2265 | 955 | 885 | 760 | 885
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GOVA1Q | HAGR1Q | 0 | 4.2 | Cable | 0.218 | 0.262 | 6.322 | 70 | 64 | 64 | 64
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.067951 | 0.61748 | 4.1318 | 1050 | 965 | 880 | 965
GRNA1- | HAWI1- | 55.35 | 0 | Composite | 5.0386 | 12.9578 | 2.7219 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.43288 | 1.1257 | 0.23046 | 132 | 123 | 106 | 123
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.003473 | 0.038089 | 1.1674 | 2210 | 2130 | 1980 | 2130
HAKB4- | MOFF4C | 43.79 | 0 | Composite | 0.077189 | 0.84667 | 25.9494 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.304 | 1.375 | 21.563 | 184 | 184 | 184 | 184
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 4.5812 | 11.7697 | 2.4781 | 132 | 123 | 106 | 123
HELE1- | WIYH1- | 24.7994 | 0.182 | Composite | 2.2553 | 5.5462 | 1.6125 | 109 | 105 | 101 | 105
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.000334 | 0.008879 | 7.3943 | 1448 | 1448 | 1448 | 1448
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.000339 | 0.009012 | 7.5055 | 1448 | 1448 | 1448 | 1448
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.000142 | 0.00103 | 0.72634 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.000142 | 0.00103 | 0.72634 | 2770 | 2770 | 2770 | 2770
HUER4- | KILS4- | 59.125 | 0 | Composite | 0.085319 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUER4- | STHA4B | 94.151 | 0 | Composite | 0.15671 | 1.8293 | 56.6371 | 1995 | 1926 | 1787 | 1926
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.000793 | 0.002746 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.000542 | 0.001877 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | NEIL4Q | 35.617 | 0.167 | Composite | 0.071623 | 0.73506 | 23.4602 | 1316 | 1067 | 1067 | 1067
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.60509 | 3.1847 | 6.8629 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.43535 | 2.2253 | 6.6009 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Composite | 0.021179 | 0.10684 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Composite | 0.021625 | 0.10873 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.25075 | 2.3075 | 15.1228 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 110 | 100 | 90 | 100
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 110 | 100 | 90 | 100
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.49088 | 2.779 | 0.64301 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.32177 | 1.8217 | 0.42149 | 151 | 151 | 151 | 151
KAIM2- | SMEA2- | 8.64 | 0 | OHL | 0.039219 | 0.35574 | 2.3904 | 1090 | 1030 | 925 | 1030
KAIM2- | WHHO2Q | 0 | 6.45 | Cable | 0.041451 | 0.1455 | 20.1665 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.22 | Cable | 0.039972 | 0.14031 | 19.4474 | 276 | 240 | 240 | 240
KEOO1- | NECU1R | 30.3 | 0 | Composite | 0.97342 | 5.9268 | 1.7921 | 132 | 132 | 132 | 132
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.38956 | 0.9562 | 7.6124 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14.4 | Cable | 0.073987 | 0.30837 | 55.4911 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.45 | Composite | 0.020655 | 0.15725 | 3.8483 | 280 | 280 | 280 | 280
KILS2- | KILT2R | 3.56 | 0.45 | Composite | 0.020655 | 0.15725 | 3.8483 | 280 | 280 | 280 | 280
KILS4- | STHA4A | 34.948 | 0 | Composite | 0.071231 | 0.71727 | 19.8386 | 1995 | 1926 | 1787 | 1926
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.73902 | 3.212 | 0.69189 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.73902 | 3.212 | 0.69189 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.325 | 0.385 | Composite | 0.046692 | 0.42371 | 7.0632 | 760 | 620 | 620 | 620
KINB2K | KINC2- | 10.71 | 0 | Composite | 0.0483 | 0.43635 | 2.9716 | 910 | 885 | 760 | 885
KINC2- | LOAN2Q | 4.28 | 0.31 | Composite | 0.019175 | 0.19377 | 4.4396 | 760 | 690 | 620 | 690
KINC2- | LOAN2R | 4.28 | 0.17 | Composite | 0.018937 | 0.18985 | 2.8506 | 760 | 690 | 620 | 690
LAMB2- | LAMB2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.018184 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.019184 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.075618 | 0.73029 | 4.9691 | 955 | 885 | 760 | 885
LAMB2T | LOAN2- | 53.67 | 0.225 | Composite | 0.1948 | 2.0807 | 18.1937 | 795 | 620 | 620 | 620
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.075618 | 0.73029 | 4.9691 | 950 | 885 | 760 | 885
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.19726 | 0.51296 | 0.10502 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.20636 | 0.53604 | 0.10999 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7863 | 2.0447 | 0.41862 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | Composite | 1.6003 | 4.4291 | 0.91387 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | MOSM2L | 26.196 | 0.194 | Composite | 0.11862 | 1.0915 | 8.8674 | 760 | 620 | 620 | 620
LOAN2- | WFIE2- | 29.169 | 0.154 | Composite | 0.13193 | 1.2141 | 9.3165 | 760 | 620 | 620 | 620
MARG1- | NECU1Q | 37.3 | 1 | Composite | 1.222 | 7.4801 | 3.8283 | 195 | 180 | 156 | 180
MAYB1- | MAYT1T | 12.92 | 0 | OHL | 1.1799 | 3.068 | 0.62822 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 41 | 40 | 40 | 40
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOSH1Q | MOSM1- | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1- | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | MOSM2L | 5.3 | 0 | OHL | 0.024499 | 0.24192 | 1.3502 | 955 | 885 | 760 | 885
MOSM2- | MOSM2T | 5.3 | 0 | OHL | 0.024499 | 0.24192 | 1.3502 | 955 | 885 | 760 | 885
MOSM2T | WFIE2- | 2.943 | 0 | OHL | 0.013273 | 0.12214 | 0.80047 | 955 | 885 | 760 | 885
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.072609 | 0.66818 | 4.3791 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.072609 | 0.66818 | 4.3791 | 285 | 285 | 285 | 285
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.012571 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.16795 | 1.488 | 0.94835 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.17614 | 1.5029 | 0.78664 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | WIYH2R | 25.453 | 0 | Composite | 0.11087 | 1.0864 | 6.9028 | 957 | 881 | 764 | 881
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.036582 | 0.3302 | 0.11975 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.036582 | 0.3302 | 0.11975 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.033534 | 0.32266 | 2.9788 | 764 | 764 | 764 | 764
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.033534 | 0.32266 | 2.9788 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
RAVE3- | WISH3S | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3S | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3T | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3T | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
REDH1- | WFIE1A | 10.097 | 0 | Composite | 0.81403 | 2.3843 | 0.49526 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 75.76 | 0 | Composite | 0.16472 | 1.546 | 42.9252 | 1390 | 1280 | 1110 | 1280
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.073425 | 1.1026 | 70.0913 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.13442 | 1.2615 | 34.9418 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.023617 | 0.2375 | 6.6189 | 2000 | 1920 | 1790 | 1920
STIR1Q | STIR1S | 2.042 | 0 | OHL | 0.18502 | 0.45954 | 0.10311 | 229 | 211 | 183 | 211
STIR1R | STIR1T | 2.15 | 0 | OHL | 0.19482 | 0.48446 | 0.10847 | 229 | 211 | 183 | 211
STIR1R | WFIE1A | 40.68 | 0 | Composite | 3.3571 | 9.1941 | 2.0578 | 162 | 154 | 141 | 154
STLE1- | WIYH1- | 12.8916 | 0.2908 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.25 | 0 | Composite | 0.10035 | 0.92341 | 6.0518 | 950 | 885 | 760 | 885
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.25997 | 0.43744 | 0.11059 | 100 | 94 | 80 | 94
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.25997 | 0.43744 | 0.11059 | 100 | 94 | 80 | 94
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
Table B.2.1c - NGET Circuits ETYS Yr1 - 2017/18 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
HAKB1 | HARK13 | 8.487 | 0 | OHL | 0.917 | 2.075 | 0.451 | 132 | 122.1 | 105.402 | 122.1
HARK13 | JUNV1* | 16.243 | 0 | OHL | 1.194 | 2.729 | 0.743 | 132 | 122.1 | 105.402 | 122.1
IROA11 | CAMA11 | 1 | 0 | OHL | 0.812 | 5.7488 | 3.3754 | 455 | 420.875 | 363.3175 | 420.875
IROA11 | CAMA12 | 1 | 0 | OHL | 0.812 | 5.7488 | 3.3754 | 455 | 420.875 | 363.3175 | 420.875
IROA11 | OLDS12 | 12.577 | 0 | OHL | 0.297 | 2.361 | 2.693 | 455 | 420.875 | 363.3175 | 420.875
IROA12 | OLDS12 | 12.572 | 0 | OHL | 0.298 | 2.366 | 3.453 | 450 | 416.25 | 359.325 | 416.25
USKM11 | USKM12 |  |  | Series Reactor | 0.25 | 20 | 0 | 90 | 90 | 90 | 90
WALP12 | WALP11 |  |  | Series Reactor | 0.15 | 12 | 0 | 90 | 90 | 90 | 90
WYLF11 | PERH11 | 1 | 0 | OHL | 0.435 | 3.172 | 17.6099 | 330 | 305.25 | 239.55 | 305.25
WYLF12 | PERH11 | 1 | 0 | OHL | 0.435 | 3.177 | 17.772 | 330 | 305.25 | 239.55 | 305.25
ABHA41 | EXET41 | 49.051 | 0 | OHL | 0.1055 | 1.0264 | 26.9062 | 1390 | 1285.75 | 1109.915 | 1285.75
ABHA41 | LAGA41 | 26.121 | 0 | OHL | 0.0559 | 0.5444 | 14.3938 | 1390 | 1285.75 | 1109.915 | 1285.75
ABHA42 | EXET41 | 48.785 | 0 | OHL | 0.1049 | 1.0209 | 26.7606 | 1390 | 1285.75 | 1109.915 | 1285.75
ABHA42 | LAGA41 | 26.121 | 0 | OHL | 0.0559 | 0.5444 | 14.3938 | 1390 | 1285.75 | 1109.915 | 1285.75
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 935 | 864.875 | 746.5975 | 864.875
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 680 | 629 | 542.98 | 629
ABTH21 | UPPB22 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 883.375 | 762.5675 | 883.375
ABTH22 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 935 | 864.875 | 746.5975 | 864.875
ABTH22 | UPPB21 | 27.035 | 1.094 | parallel Composite | 0.124 | 1.1519 | 19.226 | 770 | 712.25 | 614.845 | 712.25
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 625 | 578.125 | 499.0625 | 578.125
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 883.375 | 762.5675 | 883.375
ALVE41 | INDQ41 | 97.176 | 0 | OHL | 0.2123 | 1.9369 | 56.1342 | 1390 | 1285.75 | 1109.915 | 1285.75
ALVE41 | TAUN41 | 73.293 | 0 | OHL | 0.1576 | 1.5337 | 40.2038 | 1390 | 1285.75 | 1109.915 | 1285.75
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2126 | 1.9394 | 56.1987 | 1390 | 1285.75 | 1109.915 | 1285.75
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.1576 | 1.5338 | 40.2065 | 1390 | 1285.75 | 1109.915 | 1285.75
AMEM41 | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 1390 | 1285.75 | 1109.915 | 1285.75
AMEM41 | IVER42 | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 1390 | 1285.75 | 1109.915 | 1285.75
AMEM42 | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2010 | 1859.25 | 1604.985 | 1859.25
AMEM42 | IVER41 | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2010 | 1859.25 | 1604.985 | 1859.25
AXMI41 | CHIC42 | 39.5 | 0 | OHL | 0.0429 | 0.687 | 26.0389 | 2780 | 2571.5 | 2219.83 | 2571.5
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2770 | 2562.25 | 2211.845 | 2562.25
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1200 | 1110 | 958.2 | 1110
BAGB21 | SWAN2A | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1550 | 1433.75 | 1237.675 | 1433.75
BARK21 | BARP22 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 786.25 | 678.725 | 786.25
BARK21 | REBR21 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1130 | 1045.25 | 902.305 | 1045.25
BARK22 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 786.25 | 678.725 | 786.25
BARK22 | REBR22 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1210 | 1119.25 | 966.185 | 1119.25
BARK41 | LAKE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3100 | 2867.5 | 2475.35 | 2867.5
BARK41 | LAKE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 2890 | 2673.25 | 2307.665 | 2673.25
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0176 | 0.1972 | 5.4519 | 2010 | 1859.25 | 1604.985 | 1859.25
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0176 | 0.1977 | 10.2631 | 2010 | 1859.25 | 1604.985 | 1859.25
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2010 | 1859.25 | 1604.985 | 1859.25
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2010 | 1859.25 | 1604.985 | 1859.25
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.0692 | 0.7576 | 7.8243 | 945 | 874.125 | 754.5825 | 874.125
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0412 | 0.3922 | 10.7954 | 1100 | 1017.5 | 878.35 | 1017.5
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0689 | 0.7539 | 6.2735 | 760 | 703 | 606.86 | 703
BEDD23 | WIMB21 | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 1100 | 1017.5 | 878.35 | 1017.5
BEDD4A | ROWD41 | 0 | 11.676 | Cable | 0.0079 | 0.138 | 127.4459 | 1310 | 1211.75 | 1046.035 | 1211.75
BEDD4B | ROWD42 | 0 | 11.676 | Cable | 0.0105 | 0.0957 | 210.168 | 1410 | 1304.25 | 1125.885 | 1304.25
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 883.375 | 762.5675 | 883.375
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 883.375 | 762.5675 | 883.375
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 883.375 | 762.5675 | 883.375
BESW21 | OCKH21 | 56.939 | 0.631 | Composite | 0.2314 | 2.4189 | 22.4142 | 820 | 758.5 | 654.77 | 758.5
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3190 | 2950.75 | 2547.215 | 2950.75
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3330 | 3080.25 | 2659.005 | 3080.25
BICF42 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3160 | 2923 | 2523.26 | 2923
BICF42 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3330 | 3080.25 | 2659.005 | 3080.25
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 883.375 | 762.5675 | 883.375
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 883.375 | 762.5675 | 883.375
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 750 | 693.75 | 598.875 | 693.75
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 883.375 | 762.5675 | 883.375
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 883.375 | 762.5675 | 883.375
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 883.375 | 762.5675 | 883.375
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 962 | 830.44 | 962
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 680 | 629 | 542.98 | 629
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 680 | 629 | 542.98 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1240 | 1147 | 990.14 | 1147
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1240 | 1147 | 990.14 | 1147
BLYT4A | HEDD4A | 26.636 | 0.121 | Composite | 0.0427 | 0.514 | 18.017 | 2200 | 2035 | 1756.7 | 2035
BLYT4B | HEDD4B | 26.636 | 0.49 | Composite | 0.043 | 0.5195 | 24.1166 | 2200 | 2035 | 1756.7 | 2035
BODE41 | GWYN4A | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1060 | 980.5 | 846.41 | 980.5
BODE41 | GWYN4B | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2770 | 2562.25 | 2211.845 | 2562.25
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2770 | 2562.25 | 2211.845 | 2562.25
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2780 | 2571.5 | 2219.83 | 2571.5
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 2780 | 2571.5 | 2219.83 | 2571.5
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 2780 | 2571.5 | 2219.83 | 2571.5
BOTW41 | FAWL41 | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1110 | 1026.75 | 886.335 | 1026.75
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3330 | 3080.25 | 2659.005 | 3080.25
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0451 | 0.8316 | 32.2964 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4A | RAYL41 | 32.993 | 0 | OHL | 0.0358 | 0.5738 | 21.7484 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.065 | 1.1398 | 43.92 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4B | RAYL41 | 33.032 | 0 | OHL | 0.0358 | 0.5745 | 21.774 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 760 | 703 | 606.86 | 703
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 760 | 703 | 606.86 | 703
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.095 | 1.8583 | 16.2816 | 2800 | 2590 | 2235.8 | 2590
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0655 | 1.0887 | 37.4778 | 1000 | 925 | 798.5 | 925
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0895 | 0.8305 | 5.3251 | 950 | 878.75 | 758.575 | 878.75
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.7619 | 850 | 786.25 | 678.725 | 786.25
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0687 | 0.6374 | 4.087 | 1090 | 1008.25 | 870.365 | 1008.25
BRFO41 | LEIS4A | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | LEIS4B | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.1325 | 1.2896 | 35.7771 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.1325 | 1.2896 | 35.7771 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3100 | 2867.5 | 2475.35 | 2867.5
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2571.5 | 2219.83 | 2571.5
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2B | TOTT24 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2C | TOTT22 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2D | TOTT23 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1090 | 1008.25 | 870.365 | 1008.25
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1090 | 1008.25 | 870.365 | 1008.25
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 935 | 864.875 | 746.5975 | 864.875
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 555 | 513.375 | 443.1675 | 513.375
BRIN21 | NORL22 | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 420 | 388.5 | 335.37 | 388.5
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 883.375 | 762.5675 | 883.375
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 883.375 | 762.5675 | 883.375
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1200 | 1110 | 958.2 | 1110
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 625 | 578.125 | 499.0625 | 578.125
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 685 | 633.625 | 546.9725 | 633.625
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 685 | 633.625 | 546.9725 | 633.625
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2550 | 2358.75 | 2036.175 | 2358.75
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2520 | 2331 | 2012.22 | 2331
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2280 | 2109 | 1820.58 | 2109
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8621 | 1390 | 1285.75 | 1109.915 | 1285.75
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8621 | 1390 | 1285.75 | 1109.915 | 1285.75
BRLE41 | WWEY41 | 49.375 | 0 | OHL | 0.0789 | 0.9496 | 29.6904 | 2200 | 2035 | 1756.7 | 2035
BRLE41 | WWEY42 | 49.375 | 0 | OHL | 0.0789 | 0.9496 | 29.6904 | 2200 | 2035 | 1756.7 | 2035
BRWA2A | HINP22 | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 765 | 707.625 | 610.8525 | 707.625
BRWA2B | HINP21 | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 760 | 703 | 606.86 | 703
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3100 | 2867.5 | 2475.35 | 2867.5
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3030 | 2802.75 | 2419.455 | 2802.75
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3100 | 2867.5 | 2475.35 | 2867.5
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3100 | 2867.5 | 2475.35 | 2867.5
BUSH21 | DRAK2A | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 955 | 883.375 | 762.5675 | 883.375
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1040 | 962 | 830.44 | 962
BUSH21 | WIEN21 | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 760 | 703 | 606.86 | 703
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 670.625 | 578.9125 | 670.625
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 670.625 | 578.9125 | 670.625
BUST4A | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1200 | 1110 | 958.2 | 1110
BUST4B | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2570 | 2377.25 | 2052.145 | 2377.25
CANT41 | CLEH41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3100 | 2867.5 | 2475.35 | 2867.5
CANT41 | KEMS4A | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3100 | 2867.5 | 2475.35 | 2867.5
CANT41 | SELL41 | 26.711 | 0.257 | Composite | 0.0417 | 0.5138 | 26.0013 | 2370 | 2192.25 | 1892.445 | 2192.25
CANT41 | SELT4A | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 2960 | 2738 | 2363.56 | 2738
CAPE41 | CONQ42 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 2780 | 2571.5 | 2219.83 | 2571.5
CAPE41 | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2780 | 2571.5 | 2219.83 | 2571.5
CAPE42 | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2780 | 2571.5 | 2219.83 | 2571.5
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 680 | 629 | 542.98 | 629
CARE21 | USKM22 | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 680 | 629 | 542.98 | 629
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 772.375 | 666.7475 | 772.375
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 772.375 | 666.7475 | 772.375
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3100 | 2867.5 | 2475.35 | 2867.5
CARR41 | DAIN41 | 2.545 | 0 | OHL | 0.004 | 0.0488 | 1.5263 | 3100 | 2867.5 | 2475.35 | 2867.5
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2210 | 2044.25 | 1764.685 | 2044.25
CARR41 | PEWO4A | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4403 | 2170 | 2007.25 | 1732.745 | 2007.25
CARR42 | DAIN41 | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 1510 | 1396.75 | 1205.735 | 1396.75
CARR43 | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 750 | 693.75 | 598.875 | 693.75
CELL41 | DAIN41 | 53.412 | 2.31 | parallel Composite | 0.0843 | 1.0314 | 76.88 | 2510 | 2321.75 | 2004.235 | 2321.75
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8657 | 27.0666 | 2180 | 2016.5 | 1740.73 | 2016.5
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4862 | 2180 | 2016.5 | 1740.73 | 2016.5
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0494 | 0.6068 | 18.9766 | 3100 | 2867.5 | 2475.35 | 2867.5
CHIC41 | EXET41 | 75.92 | 0 | OHL | 0.0824 | 1.3205 | 50.0469 | 2780 | 2571.5 | 2219.83 | 2571.5
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3070 | 2839.75 | 2451.395 | 2839.75
CHIC42 | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3070 | 2839.75 | 2451.395 | 2839.75
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1320 | 1221 | 1054.02 | 1221
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1320 | 1221 | 1054.02 | 1221
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1380 | 1276.5 | 1101.93 | 1276.5
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1380 | 1276.5 | 1101.93 | 1276.5
CILF21 | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 750 | 693.75 | 598.875 | 693.75
CILF22 | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 750 | 693.75 | 598.875 | 693.75
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2780 | 2571.5 | 2219.83 | 2571.5
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 2941.5 | 2539.23 | 2941.5
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2780 | 2571.5 | 2219.83 | 2571.5
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1280 | 1184 | 1022.08 | 1184
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1280 | 1184 | 1022.08 | 1184
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1280 | 1184 | 1022.08 | 1184
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1280 | 1184 | 1022.08 | 1184
CLEH41 | KEMS4B | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3100 | 2867.5 | 2475.35 | 2867.5
CONQ41 | CAPE42 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 2780 | 2571.5 | 2219.83 | 2571.5
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3100 | 2867.5 | 2475.35 | 2867.5
CONQ41 | DEES41 | 0 | 0.21 | Cable | 0 | 0 | 0 | 3330 | 3080.25 | 2659.005 | 3080.25
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1940 | 1794.5 | 1549.09 | 1794.5
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 1710 | 1581.75 | 1365.435 | 1581.75
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2400 | 2220 | 1916.4 | 2220
CONQ42 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3100 | 2867.5 | 2475.35 | 2867.5
CONQ42 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1940 | 1794.5 | 1549.09 | 1794.5
CONQ42 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 1710 | 1581.75 | 1365.435 | 1581.75
CONQ42 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2210 | 2044.25 | 1764.685 | 2044.25
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 3070 | 2839.75 | 2451.395 | 2839.75
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 2420 | 2238.5 | 1932.37 | 2238.5
COTT41 | GREN41 | 129.478 | 0 | OHL | 0.2293 | 2.5548 | 75.7188 | 2010 | 1859.25 | 1604.985 | 1859.25
COTT41 | KEAD4A | 34.628 | 0 | OHL | 0.0595 | 0.6862 | 20.1667 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT41 | KEAD4B | 34.479 | 0 | OHL | 0.0592 | 0.6832 | 20.0806 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT41 | RYHA41 | 76.891 | 0 | OHL | 0.0834 | 1.3374 | 50.6872 | 2780 | 2571.5 | 2219.83 | 2571.5
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0506 | 0.5544 | 21.5604 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT42 | RYHA4B | 76.816 | 0 | OHL | 0.0834 | 1.3361 | 50.638 | 2780 | 2571.5 | 2219.83 | 2571.5
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2210 | 2044.25 | 1764.685 | 2044.25
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0096 | 0.1298 | 4.0616 | 3330 | 3080.25 | 2659.005 | 3080.25
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0619 | 1.1211 | 9.699 | 1200 | 1110 | 958.2 | 1110
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 925 | 798.5 | 925
COWL41 | CULJ41 | 6.496 | 0 | OHL | 0.007 | 0.113 | 4.2822 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0125 | 0.2001 | 7.5827 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0394 | 0.6314 | 23.9301 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0543 | 0.9101 | 34.7812 | 2780 | 2571.5 | 2219.83 | 2571.5
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0706 | 1180 | 1091.5 | 942.23 | 1091.5
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1091.5 | 942.23 | 1091.5
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 935 | 864.875 | 746.5975 | 864.875
CREB21 | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1750 | 1618.75 | 1397.375 | 1618.75
CREB22 | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1750 | 1618.75 | 1397.375 | 1618.75
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 2770 | 2562.25 | 2211.845 | 2562.25
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3070 | 2839.75 | 2451.395 | 2839.75
CREB41 | THTO41 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3070 | 2839.75 | 2451.395 | 2839.75
CREB41 | THTO42 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3070 | 2839.75 | 2451.395 | 2839.75
CULJ41 | DIDC41 | 4.898 | 0 | OHL | 0.0053 | 0.0852 | 3.2288 | 2780 | 2571.5 | 2219.83 | 2571.5
DAIN41 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0536 | 0.6516 | 66.7378 | 2400 | 2220 | 1916.4 | 2220
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1600 | 1480 | 1277.6 | 1480
DINO41 | PENT41 | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9578 | 1620 | 1498.5 | 1293.57 | 1498.5
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1000 | 925 | 798.5 | 925
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1320 | 1221 | 1054.02 | 1221
DRAX41 | EGGB43 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2090 | 1933.25 | 1668.865 | 1933.25
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2770 | 2562.25 | 2211.845 | 2562.25
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2970 | 2747.25 | 2371.545 | 2747.25
DRAX42 | THOM42 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2980 | 2756.5 | 2379.53 | 2756.5
DRAX42 | THTO42 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2780 | 2571.5 | 2219.83 | 2571.5
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3070 | 2839.75 | 2451.395 | 2839.75
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3070 | 2839.75 | 2451.395 | 2839.75
DUNG41 | SETW4A | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 1850 | 1711.25 | 1477.225 | 1711.25
DUNG41 | SETW4B | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 1850 | 1711.25 | 1477.225 | 1711.25
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 485.625 | 419.2125 | 485.625
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 485.625 | 419.2125 | 485.625
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 693.75 | 598.875 | 693.75
EASO41 | LITB41 | 0 | 1 | Cable | 0.0024 | 0.033 | 45.76 | 9999 | 9249.075 | 7984.2015 | 9249.075
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2780 | 2571.5 | 2219.83 | 2571.5
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2780 | 2571.5 | 2219.83 | 2571.5
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0147 | 0.2751 | 10.7133 | 2780 | 2571.5 | 2219.83 | 2571.5
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2010 | 1859.25 | 1604.985 | 1859.25
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2010 | 1859.25 | 1604.985 | 1859.25
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1390 | 1285.75 | 1109.915 | 1285.75
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1100 | 1017.5 | 878.35 | 1017.5
EGGB41 | THOM42 | 28.07 | 0.197 | Composite | 0.028 | 0.4883 | 21.9374 | 2220 | 2053.5 | 1772.67 | 2053.5
EGGB42 | FERR41 | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2780 | 2571.5 | 2219.83 | 2571.5
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2780 | 2571.5 | 2219.83 | 2571.5
EGGB43 | STSB41 | 48.084 | 0 | OHL | 0.0458 | 0.8295 | 32.1304 | 2780 | 2571.5 | 2219.83 | 2571.5
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1320 | 1221 | 1054.02 | 1221
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 760 | 703 | 606.86 | 703
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 883.375 | 762.5675 | 883.375
ELST21 | MILH21 | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 525 | 485.625 | 419.2125 | 485.625
ELST21 | MILH22 | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 525 | 485.625 | 419.2125 | 485.625
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 760 | 703 | 606.86 | 703
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 760 | 703 | 606.86 | 703
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 760 | 703 | 606.86 | 703
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 760 | 703 | 606.86 | 703
ELST41 | ELST4A | 0 | 0.1 | Cable | 0 | 0 | 0 | 2000 | 1850 | 1597 | 1850
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1770 | 1637.25 | 1413.345 | 1637.25
ELST42 | SUND42 | 34.706 | 0 | OHL | 0.0749 | 0.6947 | 19.9385 | 1590 | 1470.75 | 1269.615 | 1470.75
ELST4A | ELST41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 1850 | 1597 | 1850
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0752 | 0.6972 | 20.0118 | 1590 | 1470.75 | 1269.615 | 1470.75
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2010 | 1859.25 | 1604.985 | 1859.25
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2010 | 1859.25 | 1604.985 | 1859.25
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2780 | 2571.5 | 2219.83 | 2571.5
ENDE41 | RATS42 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2780 | 2571.5 | 2219.83 | 2571.5
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2010 | 1859.25 | 1604.985 | 1859.25
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2010 | 1859.25 | 1604.985 | 1859.25
FAWL41 | LOVE41 | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1110 | 1026.75 | 886.335 | 1026.75
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2780 | 2571.5 | 2219.83 | 2571.5
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2420 | 2238.5 | 1932.37 | 2238.5
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2010 | 1859.25 | 1604.985 | 1859.25
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2010 | 1859.25 | 1604.985 | 1859.25
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4522 | 1970 | 1822.25 | 1573.045 | 1822.25
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1970 | 1822.25 | 1573.045 | 1822.25
FENW4A | DRAX41 | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 2770 | 2562.25 | 2211.845 | 2562.25
FENW4A | THOM41 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2010 | 1859.25 | 1604.985 | 1859.25
FERR21 | FERR2D | 0 | 0.8161 | Cable | 0.0027 | 0.0204 | 6.0881 | 435 | 402.375 | 347.3475 | 402.375
FERR21 | FERR2F | 0 | 0.70866 | Cable | 0.0065 | 0.0119 | 3.6567 | 183 | 169.275 | 146.1255 | 169.275
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1140 | 1054.5 | 910.29 | 1054.5
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 800.125 | 690.7025 | 800.125
FERR23 | FERR2E | 0 | 0.72603 | Cable | 0.0024 | 0.0182 | 5.4162 | 435 | 402.375 | 347.3475 | 402.375
FERR2A | FERR23 | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1230 | 1137.75 | 982.155 | 1137.75
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1200 | 1110 | 958.2 | 1110
FERR2B | FERR22 | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1030 | 952.75 | 822.455 | 952.75
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 800.125 | 690.7025 | 800.125
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 480 | 444 | 383.28 | 444
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 550 | 508.75 | 439.175 | 508.75
FIDF21 | FIDF23 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 693.75 | 598.875 | 693.75
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1320 | 1221 | 1054.02 | 1221
FIDF22 | FIDF24 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 693.75 | 598.875 | 693.75
FIDF22 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1320 | 1221 | 1054.02 | 1221
FIDF23 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1320 | 1221 | 1054.02 | 1221
FIDF24 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1320 | 1221 | 1054.02 | 1221
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2210 | 2044.25 | 1764.685 | 2044.25
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2210 | 2044.25 | 1764.685 | 2044.25
FOUR21 | HARK21 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 855 | 790.875 | 682.7175 | 790.875
FOUR21 | STEW2A | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 855 | 790.875 | 682.7175 | 790.875
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1017.5 | 878.35 | 1017.5
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3160 | 2923 | 2523.26 | 2923
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3160 | 2923 | 2523.26 | 2923
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2640 | 2442 | 2108.04 | 2442
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2640 | 2442 | 2108.04 | 2442
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3100 | 2867.5 | 2475.35 | 2867.5
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1285.75 | 1109.915 | 1285.75
GRAI41 | TILB41 | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2000 | 1850 | 1597 | 1850
GREN41 | STAY41 | 101.832 | 0 | OHL | 0.1852 | 2.0259 | 59.0223 | 2510 | 2321.75 | 2004.235 | 2321.75
GREN41 | SUND41 | 39.75 | 0 | OHL | 0.0723 | 0.7909 | 23.0368 | 2010 | 1859.25 | 1604.985 | 1859.25
GREN41 | SUND42 | 39.955 | 0 | OHL | 0.0727 | 0.795 | 23.1553 | 2010 | 1859.25 | 1604.985 | 1859.25
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3070 | 2839.75 | 2451.395 | 2839.75
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2645.5 | 2283.71 | 2645.5
GRSA21 | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1180 | 1091.5 | 942.23 | 1091.5
GRSA21 | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1130 | 1045.25 | 902.305 | 1045.25
GRSA21 | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 9999 | 9249.075 | 7984.2015 | 9249.075
GRSA21 | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 9999 | 9249.075 | 7984.2015 | 9249.075
GRSB21 | LACK21 | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1130 | 1045.25 | 902.305 | 1045.25
GRSB21 | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1130 | 1045.25 | 902.305 | 1045.25
GRSB21 | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 9999 | 9249.075 | 7984.2015 | 9249.075
GRSB21 | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 9999 | 9249.075 | 7984.2015 | 9249.075
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2780 | 2571.5 | 2219.83 | 2571.5
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2780 | 2571.5 | 2219.83 | 2571.5
HACK21 | TOTT21 | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 883.375 | 762.5675 | 883.375
HACK22 | TOTT22 | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 883.375 | 762.5675 | 883.375
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 2500 | 2312.5 | 1996.25 | 2312.5
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 2780 | 2571.5 | 2219.83 | 2571.5
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1860 | 1720.5 | 1485.21 | 1720.5
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1860 | 1720.5 | 1485.21 | 1720.5
HAKB4- | HARK41 | 9.857 | 0 | OHL | 0.0179 | 0.2011 | 5.5627 | 2170 | 2007.25 | 1732.745 | 2007.25
HAKB4B | HARK41 | 9.857 | 0 | OHL | 0.0179 | 0.2011 | 5.5627 | 2170 | 2007.25 | 1732.745 | 2007.25
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3330 | 3080.25 | 2659.005 | 3080.25
HAMB4A | PEWO41 | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2470 | 2284.75 | 1972.295 | 2284.75
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 222 | 191.64 | 222
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3330 | 3080.25 | 2659.005 | 3080.25
HAMB4B | PEWO41 | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2470 | 2284.75 | 1972.295 | 2284.75
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 222 | 191.64 | 222
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1360 | 1258 | 1085.96 | 1258
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1206 | 1.5777 | 77.2944 | 2010 | 1859.25 | 1604.985 | 1859.25
HARK22 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 775 | 716.875 | 618.8375 | 716.875
HARK41 | HUTT4A | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 3100 | 2867.5 | 2475.35 | 2867.5
HARK41 | HUTT4B | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 3100 | 2867.5 | 2475.35 | 2867.5
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1110 | 1026.75 | 886.335 | 1026.75
HATL21 | HARM21 | 13.983 | 0 | OHL | 0.0531 | 0.5772 | 3.9082 | 1090 | 1008.25 | 870.365 | 1008.25
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0332 | 0.335 | 2.0887 | 1380 | 1276.5 | 1101.93 | 1276.5
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1150 | 1063.75 | 918.275 | 1063.75
HATL21 | WBOL21 | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 910 | 841.75 | 726.635 | 841.75
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP41 | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2550 | 2358.75 | 2036.175 | 2358.75
HEDD4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3330 | 3080.25 | 2659.005 | 3080.25
HEDD4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3330 | 3080.25 | 2659.005 | 3080.25
HEDD4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3330 | 3080.25 | 2659.005 | 3080.25
HEDD4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3330 | 3080.25 | 2659.005 | 3080.25
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1750 | 1618.75 | 1397.375 | 1618.75
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3070 | 2839.75 | 2451.395 | 2839.75
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3330 | 3080.25 | 2659.005 | 3080.25
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 2500 | 2312.5 | 1996.25 | 2312.5
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 2500 | 2312.5 | 1996.25 | 2312.5
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 625 | 578.125 | 499.0625 | 578.125
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0241 | 0.291 | 17.0214 | 2210 | 2044.25 | 1764.685 | 2044.25
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2150 | 1988.75 | 1716.775 | 1988.75
HINP41 | MELK41 | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2010 | 1859.25 | 1604.985 | 1859.25
HINP41 | MELK41 | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2010 | 1859.25 | 1604.985 | 1859.25
HINP41 | TAUN41 | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | TAUN42 | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2210 | 2044.25 | 1764.685 | 2044.25
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2770 | 2562.25 | 2211.845 | 2562.25
HURS21 | LITT2A | 5.164 | 2.613 | Composite | 0.0288 | 0.2786 | 27.8693 | 865 | 800.125 | 690.7025 | 800.125
HURS21 | LITT2B | 5.14 | 2.659 | Composite | 0.0288 | 0.2786 | 28.329 | 865 | 800.125 | 690.7025 | 800.125
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 823.25 | 710.665 | 823.25
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 823.25 | 710.665 | 823.25
HUTT41 | HUTT4A | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2470 | 2284.75 | 1972.295 | 2284.75
HUTT41 | HUTT4B | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2470 | 2284.75 | 1972.295 | 2284.75
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3100 | 2867.5 | 2475.35 | 2867.5
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3100 | 2867.5 | 2475.35 | 2867.5
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1420 | 1313.5 | 1133.87 | 1313.5
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.1069 | 0.9921 | 28.4755 | 1390 | 1285.75 | 1109.915 | 1285.75
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.1069 | 0.9921 | 28.4755 | 1390 | 1285.75 | 1109.915 | 1285.75
IROA21 | MELK21 | 33.258 | 0.951 | Composite | 0.1854 | 1.7471 | 15.541 | 580 | 536.5 | 463.13 | 536.5
IROA21 | MELK2A | 33.258 | 0.38 | Composite | 0.1838 | 1.7357 | 10.6817 | 580 | 536.5 | 463.13 | 536.5
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 693.75 | 598.875 | 693.75
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 693.75 | 598.875 | 693.75
IRON41 | LEGA4A | 62.073 | 0 | OHL | 0.0992 | 1.1938 | 37.326 | 2400 | 2220 | 1916.4 | 2220
IRON41 | PENN41 | 24.617 | 0 | OHL | 0.049 | 0.4912 | 14.2057 | 1590 | 1470.75 | 1269.615 | 1470.75
IRON41 | PENN42 | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9847 | 1390 | 1285.75 | 1109.915 | 1285.75
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9042 | 1390 | 1285.75 | 1109.915 | 1285.75
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.291 | 9.0974 | 2400 | 2220 | 1916.4 | 2220
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 420 | 388.5 | 335.37 | 388.5
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 888 | 766.56 | 888
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 420 | 388.5 | 335.37 | 388.5
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 775 | 716.875 | 618.8375 | 716.875
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 775 | 716.875 | 618.8375 | 716.875
IVER23 | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 595 | 550.375 | 475.1075 | 550.375
JORD21 | NORL21 | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 420 | 388.5 | 335.37 | 388.5
KEAD41 | GART4B | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3180 | 2941.5 | 2539.23 | 2941.5
KEAD41 | KEAP41 | 0.321 | 0 | OHL | 0.0007 | 0.0066 | 0.179 | 3000 | 2775 | 2395.5 | 2775
KEAD42 | GART4A | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3180 | 2941.5 | 2539.23 | 2941.5
KEAD42 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2830.5 | 2443.41 | 2830.5
KEAD42 | WBUR41 | 28.266 | 0 | OHL | 0.0307 | 0.4916 | 18.6331 | 3330 | 3080.25 | 2659.005 | 3080.25
KEAD43 | FENW4A | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3070 | 2839.75 | 2451.395 | 2839.75
KEAD43 | KEAP42 | 0.433 | 0.42 | Composite | 0.0013 | 0.0151 | 7.1841 | 3000 | 2775 | 2395.5 | 2775
KEAD43 | WBUR42 | 28.425 | 0 | OHL | 0.0308 | 0.4944 | 18.7376 | 2780 | 2571.5 | 2219.83 | 2571.5
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 830 | 767.75 | 662.755 | 767.75
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 772.375 | 666.7475 | 772.375
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0535 | 0.7262 | 24.4122 | 2170 | 2007.25 | 1732.745 | 2007.25
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0721 | 0.7367 | 22.6825 | 1930 | 1785.25 | 1541.105 | 1785.25
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0717 | 0.7289 | 22.3721 | 1930 | 1785.25 | 1541.105 | 1785.25
KENG41 | SJOW41 | 0 | 4.63 | Cable | 0.0021 | 0.0583 | 56.3205 | 1330 | 1230.25 | 1062.005 | 1230.25
KENG41 | SJOW41 | 0 | 4.5 | Cable | 0.002 | 0.0567 | 54.7391 | 2000 | 1850 | 1597 | 1850
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.1304 | 120.0672 | 2000 | 1850 | 1597 | 1850
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.1304 | 120.0672 | 2000 | 1850 | 1597 | 1850
KENG41 | WLSD41 | 0 | 2.892 | Cable | 0.0013 | 0.0372 | 35.179 | 1770 | 1637.25 | 1413.345 | 1637.25
KENG41 | WLSD42 | 0 | 2.892 | Cable | 0.0013 | 0.0372 | 35.179 | 1770 | 1637.25 | 1413.345 | 1637.25
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 760 | 703 | 606.86 | 703
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 760 | 703 | 606.86 | 703
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1420 | 1313.5 | 1133.87 | 1313.5
KIBY21 | WASF22 | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1520 | 1406 | 1213.72 | 1406
KIBY22 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1380 | 1276.5 | 1101.93 | 1276.5
KIBY22 | WASF21 | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1520 | 1406 | 1213.72 | 1406
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2645.5 | 2283.71 | 2645.5
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3100 | 2867.5 | 2475.35 | 2867.5
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2890 | 2673.25 | 2307.665 | 2673.25
KINO41 | TILB41 | 15.4784 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2000 | 1850 | 1597 | 1850
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 760 | 703 | 606.86 | 703
KITW21 | OCKH21 | 13.738 | 0.222 | Composite | 0.0525 | 0.5743 | 6.2479 | 770 | 712.25 | 614.845 | 712.25
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 665 | 615.125 | 531.0025 | 615.125
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 550 | 508.75 | 439.175 | 508.75
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 550 | 508.75 | 439.175 | 508.75
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1150 | 1063.75 | 918.275 | 1063.75
LACK41 | NORT41 | 22.443 | 0.25 | Composite | 0.0404 | 0.4515 | 17.428 | 1830 | 1692.75 | 1461.255 | 1692.75
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2420 | 2238.5 | 1932.37 | 2238.5
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2420 | 2238.5 | 1932.37 | 2238.5
LAGA41 | LAND42 | 21.224 | 0 | OHL | 0.0457 | 0.4249 | 12.1895 | 1390 | 1285.75 | 1109.915 | 1285.75
LAGA41 | LAND42 | 21.355 | 0 | OHL | 0.046 | 0.4275 | 12.2646 | 1390 | 1285.75 | 1109.915 | 1285.75
LAKE4A | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2830 | 2617.75 | 2259.755 | 2617.75
LAKE4A | WTHU42 | 2.4188 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3100 | 2867.5 | 2475.35 | 2867.5
LAKE4B | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2890 | 2673.25 | 2307.665 | 2673.25
LAKE4B | WTHU41 | 2.5806 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 1940 | 1794.5 | 1549.09 | 1794.5
LALE21 | WWEY23 | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 750 | 693.75 | 598.875 | 693.75
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2645.5 | 2283.71 | 2645.5
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2645.5 | 2283.71 | 2645.5
LEGA4B | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2286 | 2000 | 1850 | 1597 | 1850
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0122 | 0.2314 | 9.0239 | 2780 | 2571.5 | 2219.83 | 2571.5
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0122 | 0.2314 | 9.0239 | 2780 | 2571.5 | 2219.83 | 2571.5
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2780 | 2571.5 | 2219.83 | 2571.5
LEIS4B | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2780 | 2571.5 | 2219.83 | 2571.5
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 693.75 | 598.875 | 693.75
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6834 | 1390 | 1285.75 | 1109.915 | 1285.75
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6834 | 1390 | 1285.75 | 1109.915 | 1285.75
LITT41 | WTHU41 | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1940 | 1794.5 | 1549.09 | 1794.5
LITT41 | WTHU42 | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1940 | 1794.5 | 1549.09 | 1794.5
LOFI4A | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3474 | 1590 | 1470.75 | 1269.615 | 1470.75
LOFI4B | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3474 | 1590 | 1470.75 | 1269.615 | 1470.75
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2770 | 2562.25 | 2211.845 | 2562.25
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2780 | 2571.5 | 2219.83 | 2571.5
MACC41 | STAL41 | 31.196 | 0 | OHL | 0.0673 | 0.6244 | 17.9212 | 1710 | 1581.75 | 1365.435 | 1581.75
MAGA21 | PYLE2A | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1200 | 1110 | 958.2 | 1110
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2780 | 2571.5 | 2219.83 | 2571.5
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2420 | 2238.5 | 1932.37 | 2238.5
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2110 | 1951.75 | 1684.835 | 1951.75
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2110 | 1951.75 | 1684.835 | 1951.75
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2550 | 2358.75 | 2036.175 | 2358.75
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3330 | 3080.25 | 2659.005 | 3080.25
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 550 | 508.75 | 439.175 | 508.75
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.0905 | 1.5789 | 56.6993 | 2520 | 2331 | 2012.22 | 2331
NECT4A | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 2520 | 2331 | 2012.22 | 2331
NECT4A | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 2520 | 2331 | 2012.22 | 2331
NECT4B | NECT41 | 0 | 0.198 | parallel Cable | 0 | 0.0006 | 2.1612 | 3190 | 2950.75 | 2547.215 | 2950.75
NECT4B | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3820 | 3533.5 | 3050.27 | 3533.5
NECT4B | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3820 | 3533.5 | 3050.27 | 3533.5
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 420 | 388.5 | 335.37 | 388.5
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 420 | 388.5 | 335.37 | 388.5
NEEP4A | STSB41 | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2780 | 2571.5 | 2219.83 | 2571.5
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 825 | 763.125 | 658.7625 | 763.125
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 820 | 758.5 | 654.77 | 758.5
NFLE41 | KINO41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2890 | 2673.25 | 2307.665 | 2673.25
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2000 | 1850 | 1597 | 1850
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2000 | 1850 | 1597 | 1850
NORL21 | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 420 | 388.5 | 335.37 | 388.5
NORL22 | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 420 | 388.5 | 335.37 | 388.5
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1370 | 1267.25 | 1093.945 | 1267.25
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2010 | 1859.25 | 1604.985 | 1859.25
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2010 | 1859.25 | 1604.985 | 1859.25
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4066 | 12.7287 | 2550 | 2358.75 | 2036.175 | 2358.75
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4066 | 12.7287 | 2550 | 2358.75 | 2036.175 | 2358.75
OCKH21 | WIEN2A | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 670 | 619.75 | 534.995 | 619.75
OCKH2A | WIEN21 | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 955 | 883.375 | 762.5675 | 883.375
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0375 | 0.3474 | 2.2265 | 1090 | 1008.25 | 870.365 | 1008.25
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2780 | 2571.5 | 2219.83 | 2571.5
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2770 | 2562.25 | 2211.845 | 2562.25
PADI41 | PEWO4B | 37.608 | 0 | OHL | 0.0524 | 0.7014 | 23.3846 | 2170 | 2007.25 | 1732.745 | 2007.25
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2780 | 2571.5 | 2219.83 | 2571.5
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2780 | 2571.5 | 2219.83 | 2571.5
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 2941.5 | 2539.23 | 2941.5
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2770 | 2562.25 | 2211.845 | 2562.25
PEMB41 | SWAN41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2780 | 2571.5 | 2219.83 | 2571.5
PEMB41 | SWAN41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2780 | 2571.5 | 2219.83 | 2571.5
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2780 | 2571.5 | 2219.83 | 2571.5
PEMB41 | WALH41 | 217.727 | 5.468 | parallel Composite | 0.2372 | 3.8063 | 207.4152 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0633 | 0.9555 | 131.5497 | 1130 | 1045.25 | 902.305 | 1045.25
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
PEWO21 | WASF21 | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1520 | 1406 | 1213.72 | 1406
PEWO22 | WASF22 | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1520 | 1406 | 1213.72 | 1406
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3100 | 2867.5 | 2475.35 | 2867.5
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3100 | 2867.5 | 2475.35 | 2867.5
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 420 | 388.5 | 335.37 | 388.5
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 440 | 407 | 351.34 | 407
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1280 | 1184 | 1022.08 | 1184
PYLE21 | PYLE2A | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1200 | 1110 | 958.2 | 1110
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2847 | 109.6583 | 2780 | 2571.5 | 2219.83 | 2571.5
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2757 | 2150 | 1988.75 | 1716.775 | 1988.75
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1310 | 1211.75 | 1046.035 | 1211.75
RATS42 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2150 | 1988.75 | 1716.775 | 1988.75
RATS42 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2010 | 1859.25 | 1604.985 | 1859.25
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 2210 | 2044.25 | 1764.685 | 2044.25
REBR21 | TOTT21 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1210 | 1119.25 | 966.185 | 1119.25
REBR22 | TOTT22 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1210 | 1119.25 | 966.185 | 1119.25
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2780 | 2571.5 | 2219.83 | 2571.5
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1320 | 1221 | 1054.02 | 1221
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 840 | 777 | 670.74 | 777
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 905 | 837.125 | 722.6425 | 837.125
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2780 | 2571.5 | 2219.83 | 2571.5
RYEH41 | WALX41 | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2780 | 2571.5 | 2219.83 | 2571.5
RYEH4A | RYEH4C | 0.264 | 0 | OHL | 0.0006 | 0.0053 | 0.1512 | 9999 | 9249.075 | 7984.2015 | 9249.075
RYEH4A | WALX42 | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2780 | 2571.5 | 2219.83 | 2571.5
RYEH4B | RYEH4D | 0.215 | 0 | OHL | 0.0005 | 0.0043 | 0.1232 | 9999 | 9249.075 | 7984.2015 | 9249.075
RYHA41 | EASO41 | 58.95 | 0 | OHL | 0.064 | 1.0253 | 38.8593 | 2780 | 2571.5 | 2219.83 | 2571.5
RYHA4B | EASO41 | 58.769 | 0 | OHL | 0.0638 | 1.0222 | 38.7404 | 2780 | 2571.5 | 2219.83 | 2571.5
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1520 | 1406 | 1213.72 | 1406
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1420 | 1313.5 | 1133.87 | 1313.5
SELL41 | SELT4A | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 1640 | 1517 | 1309.54 | 1517
SELL41 | SELT4A | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 2960 | 2738 | 2363.56 | 2738
SELL41 | SETW4A | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 1640 | 1517 | 1309.54 | 1517
SELL41 | SETW4A | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3300 | 3052.5 | 2635.05 | 3052.5
SELL41 | SETW4B | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3300 | 3052.5 | 2635.05 | 3052.5
SELL41 | SETW4B | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 1640 | 1517 | 1309.54 | 1517
SHRE4A | SHRE4B | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 2170 | 2007.25 | 1732.745 | 2007.25
SJOW21 | TOTT23 | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 870 | 804.75 | 694.695 | 804.75
SJOW21 | TOTT24 | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 870 | 804.75 | 694.695 | 804.75
SJOW41 | SJOW4A | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 240 | 222 | 191.64 | 222
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2284.75 | 1972.295 | 2284.75
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2284.75 | 1972.295 | 2284.75
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3190 | 2950.75 | 2547.215 | 2950.75
SSHI21 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1240 | 1147 | 990.14 | 1147
SSHI21 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1090 | 1008.25 | 870.365 | 1008.25
STAL41 | STSB4A | 28.555 | 5.057 | Composite | 0.0366 | 0.5666 | 94.9484 | 1650 | 1526.25 | 1317.525 | 1526.25
STAL42 | THOM42 | 71.245 | 4.978 | Composite | 0.0738 | 1.299 | 122.495 | 1330 | 1230.25 | 1062.005 | 1230.25
STEW21 | STEW2A | 0 | 0.435 | Cable | 0.0007 | 0.0116 | 2.5837 | 855 | 790.875 | 682.7175 | 790.875
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3050 | 2821.25 | 2435.425 | 2821.25
SUTB41 | WALP41 | 3.85 | 0 | OHL | 0.008 | 0.0773 | 2.2055 | 1450 | 1341.25 | 1157.825 | 1341.25
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3050 | 2821.25 | 2435.425 | 2821.25
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1390 | 1285.75 | 1109.915 | 1285.75
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 420 | 388.5 | 335.37 | 388.5
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 765 | 707.625 | 610.8525 | 707.625
THOM2A | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 883.375 | 762.5675 | 883.375
THUR2A | THUR21 | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 550 | 508.75 | 439.175 | 508.75
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 883.375 | 762.5675 | 883.375
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1180 | 1091.5 | 942.23 | 1091.5
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1120 | 1036 | 894.32 | 1036
TILB41 | TILB4B | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3100 | 2867.5 | 2475.35 | 2867.5
TILB4A | TILB41 | 0.05808 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3100 | 2867.5 | 2475.35 | 2867.5
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1001 | 1.2332 | 38.5742 | 3100 | 2867.5 | 2475.35 | 2867.5
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1001 | 1.2332 | 38.5742 | 3100 | 2867.5 | 2475.35 | 2867.5
TREM21 | USKM23 | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 642.875 | 554.9575 | 642.875
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1090 | 1008.25 | 870.365 | 1008.25
USKM21 | USKM23 | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642.875 | 554.9575 | 642.875
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1010 | 934.25 | 806.485 | 934.25
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1010 | 934.25 | 806.485 | 934.25
USKM22 | USKM21 | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 680 | 629 | 542.98 | 629
USKM22 | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 680 | 629 | 542.98 | 629
USKM23 | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 642.875 | 554.9575 | 642.875
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1387.5 | 1197.75 | 1387.5
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 2780 | 2571.5 | 2219.83 | 2571.5

## B-2-1d
Table B.2.1d - Offshore Transmission Circuits 2017/18 | [11 empty] | Back To Menu
OFTO | Station | Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
Blue Transmission London Array Limited | London Array Offshore Wind Farm | CLEH40 | LONO41 | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
" | " | CLEH40 | LONO42 | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
" | " | LONO11 | LONO1A | 0 | 0.055 | Cable | 0.00121 | 0.0031533 | 0.077765 | 180 | 150
" | " | LONO1A | LONO1B | 0 | 3.048 | Cable | 0.08 | 0.16 | 4.49 | 164.9778 | 150
" | " | LONO1B | LONW1A | 0 | 48.065 | Cable | 1.37 | 2.65 | 64.65 | 158.4826 | 150
" | " | LONW1A | LONW11 | 0 | 1.633 | Cable | 0.04 | 0.09 | 2.41 | 155.8846 | 150
" | " | LONO12 | LONO1C | 0 | 0.105 | Cable | 0.00198 | 0.00516 | 0.12725 | 180 | 150
" | " | LONO1C | LONO1D | 0 | 3.033 | Cable | 0.08 | 0.16 | 4.47 | 164.9778 | 150
" | " | LONO1D | LONW1C | 0 | 48.213 | Cable | 1.37 | 2.66 | 64.85 | 158.4826 | 150
" | " | LONW1C | LONW11 | 0 | 1.913 | Cable | 0.05 | 0.1 | 2.82 | 155.8846 | 150
" | " | LONO13 | LONO1E | 0 | 0.09 | Cable | 0.00209 | 0.0054467 | 0.13432 | 180 | 150
" | " | LONO1E | LONO1F | 0 | 3.102 | Cable | 0.08 | 0.16 | 4.57 | 164.9778 | 150
" | " | LONO1F | LONW1E | 0 | 47.995 | Cable | 1.37 | 2.65 | 64.56 | 158.4826 | 150
" | " | LONW1E | LONW12 | 0 | 1.712 | Cable | 0.04 | 0.09 | 2.52 | 155.8846 | 150
" | " | LONO14 | LONO1G | 0 | 0.115 | Cable | 0.00253 | 0.0065933 | 0.1626 | 180 | 150
" | " | LONO1G | LONO1H | 0 | 3.067 | Cable | 0.08 | 0.16 | 4.52 | 164.9778 | 150
" | " | LONO1H | LONW1G | 0 | 48.785 | Cable | 1.39 | 2.69 | 65.62 | 158.4826 | 150
" | " | LONW1G | LONW12 | 0 | 0.905 | Cable | 0.02 | 0.05 | 1.33 | 155.8846 | 150
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SHSW1B | SSAW10 | 0 | 22.4 | Cable | 0.0061708 | 0.017998 | 0.24522 | 178 | 132
" | " | SHSW1A | SHSW1B | 0 | 0.4 | Cable | 8.2645e-05 | 0.00027548 | 0.0052548 | 178 | 132
" | " | SALL10 | SHSW1A | 0 | 22 | Cable | 0.0039646 | 0.017929 | 0.30224 | 190 | 132
" | " | SHSW1D | SSBW10 | 0 | 20.5 | Cable | 0.0056474 | 0.016472 | 0.22442 | 178 | 132
" | " | SHSW1C | SHSW1D | 0 | 0.4 | Cable | 8.2645e-05 | 0.00027548 | 0.0052548 | 178 | 132
" | " | SALL10 | SHSW1C | 0 | 22 | Cable | 0.0039646 | 0.017929 | 0.30224 | 190 | 132
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAO10 | WAAO1A | 0 |  | Cable | 0.076045 | 0.13688 | 3.5539 |  | 132
" | " | WAAO1A | WAAW10 | 0 |  | Cable | 1.2943 | 2.3298 | 55.0577 |  | 132
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABO10 | WABO1A | 0 |  | Cable | 0.15 | 0.27 | 6.384 |  | 132
" | " | WABO1A | WABW10 | 0 |  | Cable | 1.266 | 2.279 | 53.869 |  | 132
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON11 | GREG11 | 0 | 46 | Cable | 1.9688 | 6.1189 | 59.7739 | 180 | 132
" | " | GGON12 | GREG12 | 0 | 46.15 | Cable | 1.9722 | 6.1291 | 59.7798 | 180 | 132
" | " | GGON13 | GREG13 | 0 | 46 | Cable | 1.9688 | 6.1189 | 59.7739 | 180 | 132
" | " | GREG12 | GAOF10 | 0 | 17 | Cable | 0.36 | 1.07 | 0.6224 | 180 | 132
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | BODE41 | BODE4C | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 400
" | " | BODE41 | BODE4D | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 400
" | " | GWYO1A | GWYO10 | 0 |  | Cable | 0.247 | 1.017 | 14.78 |  | 132
" | " | GWYW10 | GWYO1A | 0 |  | Cable | 0.726 | 1.524 | 22.91 |  | 132
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO10 | BOSO1A | 0 | 2.633 | Cable | 0.00074 | 0.00219 | 0.02292 |  | 132
" | " | BOSO1A | BOSW10 | 0 | 26.9 | Cable | 0.01544 | 0.02161 | 0.22087 |  | 132
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS1A | 0 |  | Cable | 0.0653 | 0.3483 | 4.5678 |  | 132
" | " | GUNS1A | GUNS10 | 0 |  | Cable | 0.2656 | 0.478 | 11.2974 |  | 132
TC Lincs OFTO Limited | Lincs Wind Farm | LINS10 | LINO1A | 0 |  | Cable | 0.21625 | 1.0055 | 15.8882 |  | 132
" | " | LINO1A | LINO10 | 0 |  | Cable | 1.8279 | 3.3691 | 53.6171 |  | 132
" | " | LINS10 | LINO1B | 0 |  | Cable | 0.21625 | 1.0055 | 15.8882 |  | 132
" | " | LINO1B | LINO10 | 0 |  | Cable | 1.8279 | 3.3691 | 53.6171 |  | 132
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMO11 | ORMO1B | 0 | 41.5 | Cable | 0.674 | 2.858 | 43.85 | 789 | 132
" | " | ORMO1B | ORMO1A | 0 | 2.767 | Cable | 0.0583 | 0.246 | 2.83 | 789 | 132
" | " | ORMO1A | TRIM12 | 0 | 0.08 | Cable | 0.00169 | 0.0071 | 0.0818 | 789 | 132
TC Robib Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE10 | RORE1A | 0 | 1.8 | Cable |  |  |  |  | 132
" | " | RORE1A | RREW10 | 0 | 12.5 | Cable |  |  |  |  | 132
" | Robin Rigg West Offshore Wind Farm | RORW10 | RORW1A | 0 | 1.8 | Cable |  |  |  |  | 132
" | " | RORW1A | RRWW10 | 0 | 12.5 | Cable |  |  |  |  | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW10 | THAW1A | 0 | 2.3 | Cable | 0.049 | 0.191 | 3.336 |  | 132
" | " | THAW1A | THAW1B | 0 | 2.26 | Cable | 0.036 | 0.145 | 3.08 |  | 132
" | " | THAW1B | THOW10 | 0 | 24.33 | Cable | 0.846 | 1.703 | 26.23 |  | 132
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | WDSO1A | WDSW11 | 0 | 39.4 | Cable | 0.6396 | 1.8368 | 64.2338 | 209 | 155
" | " | WDSO1B | WDSW12 | 0 | 39.4 | Cable | 0.6396 | 1.8368 | 64.2338 | 209 | 155
" | " | WDSO11 | WDSO1A | 0 | 2.675 | Cable | 0.0234 | 0.161 | 5.1485 | 209 | 155
" | " | WDSO12 | WDSO1B | 0 | 2.675 | Cable | 0.0234 | 0.161 | 5.1485 | 209 | 155
" | " | HEYS40 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
" | " | HEYS40 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
- | Humber Gateway Offshore Wind Farm | HUMO1A | HUMW11 | 0 | 10 | Cable | 0.00396 | 0.007 | 0.10784 | 121.17 | 132
- | " | HUMO1B | HUMW12 | 0 | 10 | Cable | 0.00396 | 0.007 | 0.10784 | 121.17 | 132
- | " | HUMO11 | HUMO1A | 0 | 30 | Cable | 0.01062 | 0.02813 | 0.36456 | 121.17 | 132
- | " | HUMO12 | HUMO1B | 0 | 30 | Cable | 0.01062 | 0.02813 | 0.36456 | 121.17 | 132
- | Westermost Rough Offshore Wind Farm | WERW12 | WERW1C | 0 | 9.6525 | Cable | 0.13835 | 0.50506 | 15.2902 | 214.3413 | 150
- | " | WERW1C | WERW1B | 0 | 1.482 | Cable | 0.016282 | 0.073145 | 2.6692 | 231.7484 | 150
- | " | WERW1B | WERW1A | 0 | 13.9185 | Cable | 0.13374 | 0.85744 | 26.2286 | 229.4101 | 150
- | " | WERW1A | WERW11 | 0 | 0.78055 | Cable | 0.0065636 | 0.046673 | 1.5245 | 140.0623 | 150
- | " | WERW22 | WERW2A | 0 | 0.039 | Cable | 0.00031845 | 0.0012888 | 0.13463 | 256.7809 | 275
- | " | WERW2A | HEDO20 | 0 | 0.29 | Cable | 0.0023679 | 0.0095833 | 1.0011 | 256.7809 | 275
- | " | WERW21 | WERW2B | 0 | 0.103 | Cable | 0.00084102 | 0.0034037 | 0.35556 | 256.7809 | 275
- | " | WERW2B | HEDO20 | 0 | 0.265 | Cable | 0.0021638 | 0.0087572 | 0.9148 | 394.1498 | 275
- | Dudgeon Offshore Wind Farm | DUDO1A | DUDG1* | 0 | 42 | Cable | 1.0968 | 2.9304 | 45.76 |  | 132
- | " | DUDO1B | DUDG1* | 0 | 42 | Cable | 1.0968 | 2.9304 | 45.76 |  | 132
- | " | DUDO1* | DUDO1A | 0 | 47.31 | Cable | 0.7184 | 3.8888 | 64.8609 |  | 132
- | " | DUDO1* | DUDO1B | 0 | 47.31 | Cable | 0.7184 | 3.8888 | 64.8609 |  | 132
- | Burbo Bank Extension Offshore Wind Farm | BODE41 | BURB41 | 0 | 0.621 | Cable | 0.0005 | 0.0078 | 7.8037 |  | 400
- | " | BUBO20 | BUBW20 | 0 | 21.5 | Cable | 0.2265 | 0.5331 | 62.1134 |  | 220
- | " | BURB21 | BUBO20 | 0 | 10.6 | Cable | 0.0701 | 0.311 | 25.9726 |  | 220
- | Race Bank Offshore Wind Farm | WALP41 | RACB41 | 0 | 1 | Cable | 0.0025 | 0.0093 | 21.1035 | 1330 | 400 |  | Missing
- | " | WALP41 | RACB42 | 0 | 1 | Cable | 0.0025 | 0.0093 | 21.1035 | 1330 | 400 |  | Missing
- | " | RABO21 | RAOF2A | 0 | 83 | Cable | 9.6e-05 | 0.001769 | 0.018438 | 1330 | 220
- | " | RABO22 | RAOF2B | 0 | 83 | Cable | 9.6e-05 | 0.001769 | 0.018438 | 1330 | 220
- | " | RAOF21 | RAOF22 | 0 | 77.7 | Cable | 8.8e-05 | 0.001731 | 0.014278 | 1330 | 220
- | " | RAOF2A | RAOF21 | 0 | 1 | Cable | 0 | 0 | 0 |  | 220
- | " | RAOF2B | RAOF22 | 0 | 1 | Cable | 0 | 0 | 0 |  | 220
- | Rampion Offshore Wind Farm | BOLN41 | TWIN4A | 0 | 0.764 | Cable | 1.8e-05 | 6.4e-05 | 0.056068 |  | 400
- | " | BOLN41 | TWIN4B | 0 | 0.602 | Cable | 1.4e-05 | 5e-05 | 0.044179 |  | 400
- | " | TWIN1A | TWIN1C | 0 | 26.586 | Cable | 0.005554 | 0.013707 | 0.43223 |  | 150
- | " | TWIN1B | TWIN1D | 0 | 26.586 | Cable | 0.005554 | 0.013707 | 0.43223 |  | 150
- | " | TWIN1C | RAMP1A | 0 | 1.25 | Cable | 0.000161 | 0.0006 | 0.026065 |  | 150
- | " | TWIN1D | RAMP1B | 0 | 1.25 | Cable | 0.000161 | 0.0006 | 0.026065 |  | 150
- | " | RAMP1A | RAMP1C | 0 | 14.506 | Cable | 0.002321 | 0.007221 | 0.27377 |  | 150
- | " | RAMP1B | RAMP1D | 0 | 14.446 | Cable | 0.002311 | 0.007191 | 0.27264 |  | 150

## B-2-2a
Table B.2.2a - SHE Transmission Circuit Changes 2018/19 to 2026/27 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BEAU1N | KNOC1J | 2018 | Addition | 17.75 | 0 | OHL | 1.7609 | 4.036 | 0.856 | 132 | 123 | 106 | 123
BEAU1T | KNOC1J | 2018 | Addition | 17.78 | 0 | OHL | 1.7609 | 4.036 | 0.856 | 132 | 123 | 106 | 123
BLHI1J | DORE11 | 2018 | Addition | 20 | 0 | OHL | 0.786 | 4.196 | 1.09 | 280 | 270 | 246 | 270
BLHI1K | DORE12 | 2018 | Addition | 20 | 0 | OHL | 0.786 | 4.196 | 1.09 | 280 | 270 | 246 | 270
BOAG1Q | TOMT1K | 2018 | Addition | 14.1 | 0 | OHL | 1.436 | 3.2912 | 0.698 | 132 | 123 | 106 | 123
BOAG1R | TOMT1J | 2018 | Addition | 14.1 | 0 | OHL | 1.436 | 3.2912 | 0.698 | 132 | 123 | 106 | 123
DOUN2- | THSO2J | 2018 | Addition | 15.4 | 0 | OHL | 0.077 | 0.8162 | 3.388 | 965 | 925 | 865 | 925
DOUN2- | THSO2K | 2018 | Addition | 15.4 | 0 | OHL | 0.077 | 0.8162 | 3.388 | 965 | 925 | 865 | 925
DYCE1J | ABBA1- | 2018 | Addition | 0 | 9.5 | Cable | 0.1266 | 0.7277 | 15.712 | 220 | 209 | 209 | 209
DYCE1Q | DYCE1J | 2018 | Addition | 0 | 2.5 | Cable | 0.1774 | 0.5662 | 0.389 | 145 | 131 | 116 | 131
FAAR1Q | TOMT1K | 2018 | Addition | 16 | 0 | OHL | 1.6291 | 3.7338 | 0.792 | 132 | 123 | 106 | 123
FAAR1R | TOMT1J | 2018 | Addition | 16 | 0 | OHL | 1.6291 | 3.7338 | 0.792 | 132 | 123 | 106 | 123
FAUG2K | TUMM2J | 2018 | Addition | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FAUG4- | MELG4J | 2018 | Addition | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
INGA1Q | LOCL1Q | 2018 | Addition | 0 | 2.4 | Cable | 0.2184 | 0.5664 | 0.118 | 111 | 103 | 89 | 103
KNOC2J | TOMT2K | 2018 | Addition | 20 | 0 | OHL | 0.0908 | 0.83 | 5.442 | 955 | 880 | 760 | 880
KNOC2K | TOMT2J | 2018 | Addition | 20 | 0 | OHL | 0.0908 | 0.83 | 5.442 | 955 | 880 | 760 | 880
MELG1J | STRL1- | 2018 | Addition | 0 | 10 | Cable | 0.0707 | 0.387 | 33.8069 | 444 | 403 | 403 | 403
MYBS1Q | SPIT1J | 2018 | Addition | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 2018 | Addition | 0 | 3.99 | Cable | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1S | SPIT1M | 2018 | Addition | 0 | 5 | Cable | 0.1182 | 1.0607 | 0.276 | 464 | 446 | 414 | 446
MYBS1T | SPIT1K | 2018 | Addition | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 464 | 446 | 414 | 446
THSO2J | SPIT2J | 2018 | Addition | 12.1 | 0 | OHL | 0.0605 | 0.6413 | 2.662 | 965 | 925 | 865 | 925
THSO2K | SPIT2K | 2018 | Addition | 12.1 | 0 | OHL | 0.0605 | 0.6413 | 2.662 | 965 | 925 | 865 | 925
TUMM4- | MELG4J | 2018 | Addition | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670
BEAU1N | FAAR1R | 2018 | Removed | 29.85 | 0 | OHL | 2.953 | 6.7683 | 1.436 | 132 | 123 | 106 | 123
BEAU1T | FAAR1Q | 2018 | Removed | 29.88 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOAG1Q | FAAR1Q | 2018 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOAG1R | FAAR1R | 2018 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
DOUN1- | THSO1Q | 2018 | Removed | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 132 | 123 | 106 | 123
DOUN1- | THSO1R | 2018 | Removed | 15.4 | 0 | OHL | 1.57 | 3.6 | 0.76 | 132 | 123 | 106 | 123
FAUG2K | TUMM2J | 2018 | Removed | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
INGA1Q | LOCL1R | 2018 | Removed | 0 | 2.4 | Cable | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
MYBS1S | THSO1Q | 2018 | Removed | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 117 | 101 | 117
MYBS1T | THSO1R | 2018 | Removed | 16.1 | 0 | OHL | 1.64 | 3.75 | 0.79 | 126 | 117 | 101 | 117
TUMM4- | FAUG4- | 2018 | Removed | 77.2 | 0 | OHL | 0.1 | 1.478 | 46.678 | 2780 | 2670 | 2480 | 2670
BLHI1J | KEIT1K | 2020 | Addition | 0 | 4 | Cable | 0.0283 | 0.1548 | 13.523 | 444 | 403 | 403 | 403
BLHI1K | BLHI1M | 2020 | Addition | 0 | 3 | Cable | 0.1675 | 0.6246 | 0.168 | 203 | 193 | 176 | 193
BLHI1K | KEIT1J | 2020 | Addition | 0 | 4 | Cable | 0.0283 | 0.1548 | 13.523 | 444 | 403 | 403 | 403
BLHI1M | GLFA1- | 2020 | Addition | 0 | 39.3 | Cable | 3.995 | 9.157 | 1.947 | 126 | 117 | 101 | 117
FAUG1- | MILS1Q | 2020 | Addition | 0 | 6 | Cable | 0.3036 | 1.2426 | 0.339 | 203 | 193 | 176 | 193
FIDD1Q | FETT1- | 2020 | Addition | 0 | 10 | Cable | 0.558 | 2.082 | 0.559 | 203 | 193 | 176 | 193
FIDD1R | FOGG1R | 2020 | Addition | 0 | 25.4 | Cable | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD1S | FETT1- | 2020 | Addition | 0 | 10 | Cable | 0.558 | 2.082 | 0.559 | 203 | 193 | 176 | 193
KEIT1J | MACD1Q | 2020 | Addition | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1K | MACD1R | 2020 | Addition | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
LOCL1S | MILS1Q | 2020 | Addition | 0 | 2.5 | Cable | 0.1264 | 0.5174 | 0.141 | 203 | 193 | 176 | 193
FAUG1- | LOCL1S | 2020 | Removed | 0 | 8.5 | Cable | 0.43 | 1.76 | 0.48 | 111 | 103 | 89 | 103
FIDD1Q | FOGG1R | 2020 | Removed | 0 | 25.4 | Cable | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
KEIT1- | GLFA1- | 2020 | Removed | 0 | 29.6 | Cable | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117
KEIT1- | MACD1Q | 2020 | Removed | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | MACD1R | 2020 | Removed | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
BEAU4- | FAUG4J | 2021 | Addition | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
DOUN2A | DOUN2B | 2021 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0
DOUN2B | DOUN2C | 2021 | Addition | 0 | 2 | Cable | 0.0226 | 0.0571 | 5.474 | 240 | 240 | 240 | 240
DOUN2C | DOUN2D | 2021 | Addition | 0 | 70 | Cable | 1.2015 | 2.091 | 144.1601 | 240 | 240 | 240 | 240
DOUN2D | BASK2B | 2021 | Addition | 0 | 1 | Cable | 0.0113 | 0.0286 | 2.737 | 240 | 240 | 240 | 240
FAUG1J | LAGG1Q | 2021 | Addition | 6.4 | 0 | OHL | 0.4635 | 1.455 | 0.321 | 221 | 216 | 208 | 216
FAUG1K | LAGG1R | 2021 | Addition | 6.4 | 0 | OHL | 0.4635 | 1.455 | 0.321 | 221 | 216 | 208 | 216
FAUG4J | MELG4J | 2021 | Addition | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
BEAU4- | FAUG4- | 2021 | Removed | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
FAUG1- | LAGG1Q | 2021 | Removed | 6.4 | 0 | OHL | 0.4635 | 1.455 | 0.321 | 221 | 216 | 208 | 216
FAUG1- | LAGG1R | 2021 | Removed | 6.4 | 0 | OHL | 0.4635 | 1.455 | 0.321 | 221 | 216 | 208 | 216
FAUG4- | MELG4J | 2021 | Removed | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
ABED1T | ABED1- | 2023 | Addition | 0 | 5 | Cable | 0.509 | 1.164 | 0.247 | 111 | 103 | 89 | 103
BLHI2L | ROTI2J | 2023 | Addition | 0 | 35.36 | Cable | 0.1824 | 1.5351 | 9.261 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2J | 2023 | Addition | 0 | 35.36 | Cable | 0.1824 | 1.5351 | 9.261 | 1090 | 1030 | 925 | 1030
CAAD1Q | BTUI1G | 2023 | Addition | 0 | 12 | Cable | 1.699 | 2.8214 | 0.584 | 99 | 92 | 79 | 92
CAAD1Q | WISL1- | 2023 | Addition | 0 | 85 | Cable | 2.42 | 5.823 | 92.65 | 150 | 150 | 150 | 150
CASS1Q | SALA1- | 2023 | Addition | 0 | 6 | Cable | 0.61 | 1.4 | 0.3 | 150 | 142 | 128 | 142
DOUN1- | LIME1- | 2023 | Addition | 0 | 4 | Cable | 0.408 | 0.932 | 0.196 | 132 | 123 | 106 | 123
DUGR1J | GLNU1- | 2023 | Addition | 0 | 15 | Cable | 0.838 | 3.123 | 0.84 | 203 | 193 | 176 | 193
DUNM1- | ABED1T | 2023 | Addition | 0 | 3.25 | Cable | 0.164 | 0.673 | 0.182 | 162 | 154 | 141 | 154
DUNM1C | ABED1T | 2023 | Addition | 0 | 3.25 | Cable | 0.164 | 0.673 | 0.182 | 162 | 154 | 141 | 154
FAUG1- | GLNU1- | 2023 | Addition | 0 | 135 | Cable | 7.542 | 28.107 | 7.56 | 203 | 193 | 176 | 193
FERO1S | ARDB1K | 2023 | Addition | 4.98 | 0 | OHL | 0.2541 | 1.0963 | 0.264 | 241 | 230 | 210 | 230
INNE1Q | SLKB1J | 2023 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INNE1T | SLKB1K | 2023 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INVE1J | ARDB1K | 2023 | Addition | 0 | 10.12 | Cable | 0.516 | 2.2257 | 0.536 | 241 | 230 | 210 | 230
INVE1K | ARDB1J | 2023 | Addition | 0 | 10.12 | Cable | 0.516 | 2.2257 | 0.536 | 241 | 230 | 210 | 230
KEIT1J | AULW1S | 2023 | Addition | 0 | 11 | Cable | 1.473 | 2.441 | 0.571 | 83 | 77 | 67 | 77
KILC1Q | ARDB1J | 2023 | Addition | 4.98 | 0 | OHL | 0.2541 | 1.0963 | 0.264 | 241 | 230 | 210 | 230
KILC1Q | TAYN1Q | 2023 | Addition | 7.6 | 0 | OHL | 0.3876 | 1.672 | 0.403 | 241 | 230 | 210 | 230
LAIR1K | LOCB1K | 2023 | Addition | 16 | 0 | OHL | 0.38 | 3.49 | 0.84 | 464 | 446 | 414 | 446
LAIR1Q | CREA1- | 2023 | Addition | 0 | 13 | Cable | 1.32 | 3.03 | 0.64 | 132 | 123 | 106 | 123
LAIR1Q | LOCB1J | 2023 | Addition | 16 | 0 | OHL | 0.38 | 3.49 | 0.84 | 464 | 446 | 414 | 446
NAIR1Q | SLKB1L | 2023 | Addition | 25.87 | 0 | OHL | 1.3194 | 5.7949 | 1.345 | 241 | 230 | 210 | 230
NAIR1R | SLKB1M | 2023 | Addition | 25.87 | 0 | OHL | 1.3194 | 5.7949 | 1.345 | 241 | 230 | 210 | 230
PEHE2Q | NEDE2K | 2023 | Addition | 0 | 23.65 | Cable | 0.1208 | 1.0299 | 6.199 | 1090 | 1030 | 920 | 1030
PEHERSV1 | NEDE2J | 2023 | Addition | 0 | 23.65 | Cable | 0.1201 | 1.0224 | 6.175 | 1090 | 1030 | 920 | 1030
ROTI2J | KINT2J | 2023 | Addition | 23.2 | 0 | OHL | 0.102 | 0.9384 | 6.301 | 1380 | 1320 | 1230 | 1320
ROTI2J | KINT2K | 2023 | Addition | 23.2 | 0 | OHL | 0.102 | 0.9384 | 6.301 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2023 | Addition | 0 | 23.65 | Cable | 0.1201 | 1.0224 | 6.175 | 1090 | 1030 | 925 | 1030
ROTI2J | NEDE2K | 2023 | Addition | 0 | 23.65 | Cable | 0.1201 | 1.0224 | 6.175 | 1090 | 1030 | 925 | 1030
SLKB1J | SLKB1L | 2023 | Addition | 0 | 1.46 | Cable | 0.05 | 0.1 | 1.77 | 146 | 142 | 142 | 142
SLKB1K | SLKB1M | 2023 | Addition | 0 | 1.46 | Cable | 0.05 | 0.1 | 1.77 | 146 | 142 | 142 | 142
THSO1J | GILB1J | 2023 | Addition | 24 | 0 | OHL | 0.9547 | 5.244 | 1.279 | 335 | 320 | 290 | 320
THSO1K | GILB1K | 2023 | Addition | 24 | 0 | OHL | 0.9547 | 5.244 | 1.279 | 335 | 320 | 290 | 320
TOMT1K | GLKY1- | 2023 | Addition | 0 | 3 | Cable | 0.4 | 0.67 | 0.16 | 83 | 77 | 67 | 77
BLHI2L | KINT2J | 2023 | Removed | 0 | 58.6 | Cable | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2M | PEHERS | 2023 | Removed | 0 | 82.72 | Cable | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
DUNM1- | DUNM1C | 2023 | Removed | 0 | 6.5 | Cable | 0.328 | 1.346 | 0.364 | 162 | 154 | 141 | 154
INNE1Q | NAIR1Q | 2023 | Removed | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1T | NAIR1R | 2023 | Removed | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INVE1J | FERO1S | 2023 | Removed | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
INVE1K | KILC1Q | 2023 | Removed | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
KILC1Q | TAYN1Q | 2023 | Removed | 7.562 | 0.038 | Composite | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KINT2K | PEHE2Q | 2023 | Removed | 0 | 70.5 | Cable | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
LAIR1Q | SHIN1- | 2023 | Removed | 0 | 10.5 | Cable | 1.06 | 2.52 | 0.5 | 111 | 103 | 89 | 103
ALYT2 | FETT2P | 2026 | Addition | 67.35 | 0 | OHL | 0.3367 | 2.896 | 17.511 | 1090 | 1030 | 925 | 1030
ALYT2 | FETT2Q | 2026 | Addition | 67.35 | 0 | OHL | 0.3367 | 2.896 | 17.511 | 1090 | 1030 | 925 | 1030
ALYT2 | KINB2J | 2026 | Addition | 69.98 | 0 | OHL | 0.3499 | 3.0091 | 18.195 | 1090 | 1030 | 925 | 1030
ALYT2 | KINB2K | 2026 | Addition | 69.98 | 0 | OHL | 0.3499 | 3.0091 | 18.195 | 1090 | 1030 | 925 | 1030
ALYT2 | TEAL2J | 2026 | Addition | 16.2 | 0 | OHL | 0.0808 | 0.695 | 4.234 | 1090 | 1030 | 925 | 1030
ALYT2 | TEAL2K | 2026 | Addition | 16.2 | 0 | OHL | 0.0808 | 0.695 | 4.234 | 1090 | 1030 | 925 | 1030
ARDB1K | SONO1- | 2026 | Addition | 0 | 1 | Cable | 0.102 | 0.049 | 0.233 | 132 | 123 | 106 | 123
BLHI1J | ELCH1- | 2026 | Addition | 0 | 20 | Cable | 1.0075 | 4.14 | 1.12 | 203 | 193 | 176 | 193
BLHI4- | ROTI4J | 2026 | Addition | 35.4 | 0 | OHL | 0.0758 | 0.6938 | 20.373 | 1590 | 1500 | 1350 | 1500
BLHI4- | ROTI4J | 2026 | Addition | 35.4 | 0 | OHL | 0.0758 | 0.6938 | 20.373 | 1590 | 1500 | 1350 | 1500
BRCW2J | CROB2- | 2026 | Addition | 45.84 | 0 | OHL | 0.1256 | 1.8571 | 13.101 | 1910 | 1830 | 1710 | 1830
CONN1C | CONN1K | 2026 | Addition | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN1J | CONN1D | 2026 | Addition | 0 | 0.66 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178
CRSS1J | WILW1- | 2026 | Addition | 0 | 10 | Cable | 0.91 | 2.16 | 0.54 | 132 | 123 | 106 | 123
DOUN2- | CONN2J | 2026 | Addition | 10.34 | 0 | OHL | 0.0647 | 0.5443 | 2.177 | 702 | 665 | 599 | 665
DOUN2- | CONN2K | 2026 | Addition | 10.34 | 0 | OHL | 0.0647 | 0.5442 | 2.176 | 702 | 665 | 599 | 665
DUBE1Q | MYBS1R | 2026 | Addition | 20.8 | 0 | OHL | 1.0608 | 4.6592 | 1.073 | 195 | 180 | 157 | 180
GOLT1T | GOLT1- | 2026 | Addition | 0 | 3 | Cable | 0.305 | 0.689 | 0.148 | 111 | 103 | 89 | 103
GORW2- | CONN2K | 2026 | Addition | 47.76 | 0 | OHL | 0.2987 | 2.5127 | 10.05 | 702 | 665 | 599 | 665
KINT2A | TEAL2J | 2026 | Addition | 0 | 100.6 | Cable | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2B | TEAL2K | 2026 | Addition | 0 | 100.6 | Cable | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2J | KINT2A | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0
LOCB1J | GOLT1T | 2026 | Addition | 68.5499 | 0 | OHL | 3.4962 | 15.3557 | 3.537 | 195 | 180 | 157 | 180
MYBS1Q | GOLT1T | 2026 | Addition | 13.06 | 0 | OHL | 0.6659 | 2.9249 | 0.674 | 195 | 180 | 157 | 180
PEHE4- | NEDE4J | 2026 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1590 | 1500 | 1350 | 1500
PEHE4- | NEDE4K | 2026 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1590 | 1500 | 1350 | 1500
ROTI4J | KINT4J | 2026 | Addition | 23.2 | 0 | OHL | 0.0496 | 0.4547 | 13.352 | 2002 | 1919 | 1787 | 1919
ROTI4J | KINT4K | 2026 | Addition | 23.2 | 0 | OHL | 0.0496 | 0.4547 | 13.352 | 2002 | 1919 | 1787 | 1919
ROTI4J | NEDE4J | 2026 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1590 | 1500 | 1350 | 1500
ROTI4J | NEDE4K | 2026 | Addition | 23.65 | 0 | OHL | 0.0506 | 0.4635 | 13.611 | 1590 | 1500 | 1350 | 1500
STRW13 | STRW17 | 2026 | Addition | 0 | 0.27 | Cable | 0.0056 | 0.0226 | 0.37 | 200 | 178 | 178 | 178
STRW17 | CONN1D | 2026 | Addition | 0 | 12.12 | Cable | 0.6109 | 2.5094 | 0.679 | 203 | 193 | 176 | 193
TUMM2K | CROB2- | 2026 | Addition | 16.96 | 0 | OHL | 0.0464 | 0.6869 | 4.846 | 1910 | 1830 | 1710 | 1830
BLHI2L | ROTI2J | 2026 | Removed | 0 | 35.36 | Cable | 0.1824 | 1.5351 | 9.261 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2J | 2026 | Removed | 0 | 35.36 | Cable | 0.1824 | 1.5351 | 9.261 | 1090 | 1030 | 925 | 1030
BRCW2J | TUMM2K | 2026 | Removed | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
CONN1J | CONN1C | 2026 | Removed | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
DOUN2- | CONN2J | 2026 | Removed | 10.34 | 0 | OHL | 0.0647 | 0.5443 | 2.177 | 702 | 665 | 599 | 665
DOUN2- | GORW2- | 2026 | Removed | 58.1 | 0 | OHL | 0.3634 | 3.0569 | 12.226 | 535 | 490 | 430 | 490
DUBE1Q | MYBS1R | 2026 | Removed | 20.8 | 0 | OHL | 1.0608 | 4.6592 | 1.073 | 126 | 117 | 101 | 117
FETT2Q | KINB2J | 2026 | Removed | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
KINT2J | TEAL2J | 2026 | Removed | 0 | 100.6 | Cable | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | TEAL2K | 2026 | Removed | 0 | 100.6 | Cable | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
MYBS1Q | LOCB1J | 2026 | Removed | 81.61 | 0 | OHL | 4.1621 | 18.2806 | 4.211 | 126 | 117 | 101 | 117
PEHE2Q | NEDE2K | 2026 | Removed | 0 | 23.65 | Cable | 0.1208 | 1.0299 | 6.199 | 1090 | 1030 | 920 | 1030
PEHERS | NEDE2J | 2026 | Removed | 0 | 23.65 | Cable | 0.1201 | 1.0224 | 6.175 | 1090 | 1030 | 920 | 1030
ROTI2J | KINT2J | 2026 | Removed | 23.2 | 0 | OHL | 0.102 | 0.9384 | 6.301 | 1380 | 1320 | 1230 | 1320
ROTI2J | KINT2K | 2026 | Removed | 23.2 | 0 | OHL | 0.102 | 0.9384 | 6.301 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2026 | Removed | 0 | 23.65 | Cable | 0.1201 | 1.0224 | 6.175 | 1090 | 1030 | 925 | 1030
ROTI2J | NEDE2K | 2026 | Removed | 0 | 23.65 | Cable | 0.1201 | 1.0224 | 6.175 | 1090 | 1030 | 925 | 1030
TEAL2J | KINB2K | 2026 | Removed | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
TEAL2K | FETT2P | 2026 | Removed | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880

## B-2-2b
Table B.2.2b - SPT Circuit Changes 2018/19 to 2026/27 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
BONN1- | STIR1S | 2018 | Addition | 3.35 | 11.2 | Composite | 0.2966 | 1.5164 | 20.0495 | 226.3444 | 209.3686 | 180.736 | 209.3686
BONN1- | STIR1T | 2018 | Addition | 3.35 | 11.2 | Composite | 0.2966 | 1.5164 | 20.0495 | 226.3444 | 209.3686 | 180.736 | 209.3686
COAL1- | KYPE1- | 2018 | Addition | 0 | 17 | Cable | 0.2673 | 1.4635 | 28.01 | 241.2054 | 223.115 | 192.6025 | 223.115
COAL1- | MIDM1- | 2018 | Addition | 0 | 13 | Cable | 0.3671 | 0.8438 | 17.0786 | 121.6315 | 112.5092 | 97.1228 | 112.5092
DEVO1- | STIR1S | 2018 | Addition | 5.858 | 16.5 | Composite | 0.6034 | 2.9019 | 21.0758 | 161.1846 | 149.0958 | 128.7059 | 149.0958
STIR1T | WFIE1A | 2018 | Addition | 37.658 | 5.5 | Composite | 3.2974 | 9.1825 | 8.8047 | 161.1846 | 149.0958 | 128.7059 | 149.0958
DALL2- | INVR2- | 2018 | Change | 22.55 | 0 | OHL | 0.0969 | 0.9581 | 6.1255 | 1371.7842 | 1268.9004 | 1095.3697 | 1268.9004
DALL2- | WIYH2- | 2018 | Change | 78.15 | 0 | OHL | 0.3357 | 3.3206 | 21.2289 | 1371.7843 | 1268.9005 | 1095.3698 | 1268.9005
DEVO1- | WFIE1B | 2018 | Change | 31.8 | 0 | OHL | 2.8876 | 7.3367 | 1.5779 | 161.1846 | 149.0958 | 128.7059 | 149.0958
INVR2- | WIYH2- | 2018 | Change | 55.6 | 0 | OHL | 0.2388 | 2.3624 | 15.1033 | 1371.7842 | 1268.9004 | 1095.3697 | 1268.9004
BONN1- | STIR1Q | 2018 | Removed | 11.554 | 1.014 | Composite | 0.6332 | 2.6866 | 2.2669 | 226.3444 | 209.3686 | 180.736 | 209.3686
BONN1- | STIR1R | 2018 | Removed | 11.554 | 1.014 | Composite | 0.6332 | 2.6866 | 2.2669 | 226.3444 | 209.3686 | 180.736 | 209.3686
DEVO1- | STIR1Q | 2018 | Removed | 8.88 | 0 | OHL | 0.4735 | 1.9965 | 0.4583 | 0 | 0 | 0 | 0
STIR1Q | STIR1S | 2018 | Removed | 2.042 | 0 | OHL | 0.1854 | 0.4711 | 0.1013 | 0 | 0 | 0 | 0
STIR1R | STIR1T | 2018 | Removed | 2.15 | 0 | OHL | 0.1952 | 0.496 | 0.1067 | 0 | 0 | 0 | 0
STIR1R | WFIE1A | 2018 | Removed | 40.68 | 0 | OHL | 3.366 | 9.3357 | 2.0384 | 161.1846 | 149.0958 | 128.7059 | 149.0958
COAL1- | LINM1Q | 2019 | Addition | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 271.025 | 233.9605 | 271.025
COAL1- | LINM1R | 2019 | Addition | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 129.9994 | 120.2495 | 103.8045 | 120.2495
HUER4- | KILS4T | 2019 | Addition | 59.125 | 2e-06 | Composite | 0.0849 | 1.0902 | 37.0252 | 2000 | 1850 | 1597 | 1850
KILS4T | STHA4B | 2019 | Addition | 34.988 | 2e-06 | Composite | 0.071 | 0.7049 | 20.0387 | 2000 | 1850 | 1597 | 1850
COCK2- | KAIM2- | 2019 | Change | 18.29 | 0 | OHL | 0.0786 | 0.7771 | 4.9683 | 1380 | 1276.5 | 1101.93 | 1276.5
COCK2- | SMEA2- | 2019 | Change | 9.51 | 0 | OHL | 0.0408 | 0.4041 | 2.5833 | 1380 | 1276.5 | 1101.93 | 1276.5
COYL2- | COYW2S | 2019 | Change | 1.29 | 0.08 | Composite | 0.0058 | 0.0536 | 0.4557 | 1500 | 1387.5 | 1197.75 | 1387.5
COYL2- | COYW2T | 2019 | Change | 1.32 | 0 | OHL | 0.0059 | 0.0543 | 0.3691 | 1500 | 1387.5 | 1197.75 | 1387.5
COYW2S | KILS2- | 2019 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1387.5 | 1197.75 | 1387.5
COYW2T | KILS2- | 2019 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1387.5 | 1197.75 | 1387.5
KAIM2- | SMEA2- | 2019 | Change | 8.64 | 0 | OHL | 0.0371 | 0.3671 | 2.347 | 1380 | 1276.5 | 1101.93 | 1276.5
KILS4- | STHA4A | 2019 | Change | 34.948 | 0 | OHL | 0.0709 | 0.7041 | 20.0164 | 2000 | 1850 | 1597 | 1850
WFIB2- | WFIE2- | 2019 | Change | 22.48 | 0 | OHL | 0.1026 | 0.9762 | 5.9452 | 950 | 878.75 | 758.575 | 878.75
COAL1- | LINM1Q | 2019 | Removed | 0 | 8.97 | Cable | 0.246 | 1.521 | 3.108 | 0 | 0 | 0 | 0
COAL1- | LINM1R | 2019 | Removed | 0 | 8.91 | Cable | 0.244 | 1.516 | 3.055 | 0 | 0 | 0 | 0
HUER4- | STHA4B | 2019 | Removed | 94.151 | 0 | OHL | 0.1559 | 1.7959 | 57.0851 | 1995.3226 | 1845.6734 | 1593.2651 | 1845.6734
COAL1- | CONO1- | 2020 | Addition | 0 | 0.95 | Cable | 0.0078 | 0.0776 | 1.7691 | 293 | 271.025 | 233.9605 | 271.025
DENN2- | LAMB2T | 2020 | Addition | 32.18 | 0 | OHL | 0.1471 | 1.3621 | 8.7301 | 952.6279 | 881.1808 | 760.6734 | 881.1808
CONO1- | LINM1Q | 2020 | Change | 5.774 | 2.35 | Composite | 0.1565 | 1.4943 | 4.6733 | 293 | 271.025 | 233.9605 | 271.025
CURR2- | GRMO2- | 2020 | Change | 42.18 | 0 | OHL | 0.1812 | 1.7922 | 11.4579 | 1380 | 1276.5 | 1101.93 | 1276.5
CURR2- | KAIM2- | 2020 | Change | 9.35 | 0 | OHL | 0.0402 | 0.3973 | 2.5399 | 1380 | 1276.5 | 1101.93 | 1276.5
CURR2- | KAIM2- | 2020 | Change | 9.35 | 0 | OHL | 0.0402 | 0.3973 | 2.5399 | 1380 | 1276.5 | 1101.93 | 1276.5
CURR2- | KINC2- | 2020 | Change | 57.14 | 0 | OHL | 0.2454 | 2.4279 | 15.5217 | 1380 | 1276.5 | 1101.93 | 1276.5
GRMO2- | KINC2- | 2020 | Change | 14.96 | 0 | OHL | 0.0643 | 0.6356 | 4.0638 | 1380 | 1276.5 | 1101.93 | 1276.5
LAMB2T | LOAN2- | 2020 | Removed | 53.67 | 0.225 | Composite | 0.1978 | 2.1709 | 17.8013 | 819.9983 | 758.4984 | 654.7686 | 758.4984
COAL1- | DALQ1- | 2021 | Addition | 4.1 | 1.3 | Composite | 0.2251 | 0.9841 | 2.3656 | 195.4793 | 180.8183 | 156.0902 | 180.8183
DALB2A | DALL2- | 2021 | Addition | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000.0021 | 925.002 | 798.5017 | 925.002
DALB2B | DALL2- | 2021 | Addition | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000.0021 | 925.002 | 798.5017 | 925.002
DUNB1Q | INWI1Q | 2021 | Addition | 7.8 | 3.7 | Composite | 0.7914 | 2.1559 | 5.5488 | 165 | 152.625 | 131.7525 | 152.625
DUNB1R | INWI1R | 2021 | Addition | 7.8 | 4.3 | Composite | 0.8033 | 2.2103 | 6.3863 | 165 | 152.625 | 131.7525 | 152.625
ENHI1- | NECU1C | 2021 | Addition | 0 | 5 | Cable | 0.1412 | 0.3245 | 6.5687 | 121.6315 | 112.5092 | 97.1228 | 112.5092
ERSK1Q | DEVM1- | 2021 | Addition | 16.5 | 0 | OHL | 0.8764 | 3.51 | 0.9003 | 241 | 222.925 | 192.4385 | 222.925
GLGL1Q | LETH1- | 2021 | Addition | 15 | 0 | OHL | 1.1252 | 3.3032 | 0.789 | 166.9004 | 154.3829 | 133.27 | 154.3829
NECU1C | SOKY1- | 2021 | Addition | 0 | 4.5 | Cable | 0.0292 | 0.2677 | 7.8824 | 242 | 223.85 | 193.237 | 223.85
NNGA2- | NNGA2T | 2021 | Addition | 0 | 12.3 | Cable | 0.093 | 0.447 | 31.794 | 381.0001 | 352.4251 | 304.2286 | 352.4251
NNGA2G | NNGA2T | 2021 | Addition | 0 | 34 | Cable | 0.225 | 0.882 | 87.8859 | 381.0001 | 352.4251 | 304.2286 | 352.4251
NNGB2- | NNGB2T | 2021 | Addition | 0 | 12.3 | Cable | 0.093 | 0.447 | 31.794 | 381.0001 | 352.4251 | 304.2286 | 352.4251
NNGB2G | NNGB2T | 2021 | Addition | 0 | 34 | Cable | 0.225 | 0.882 | 87.8859 | 381.0001 | 352.4251 | 304.2286 | 352.4251
DESA1Q | NECU1C | 2021 | Change | 6.4 | 4.3 | Composite | 0.5762 | 1.7993 | 6.3388 | 132.6 | 122.655 | 105.8811 | 122.655
EWEH1Q | GRNA1- | 2021 | Change | 15.7 | 0.11996 | Composite | 1.1946 | 3.405 | 1.1449 | 243.2631 | 225.0183 | 194.2456 | 225.0183
INWI1Q | TORN1- | 2021 | Change | 0 | 1.15 | Cable | 0.0181 | 0.099 | 1.8948 | 165 | 152.625 | 131.7525 | 152.625
INWI1R | TORN1- | 2021 | Change | 0 | 1.12 | Cable | 0.0176 | 0.0964 | 1.8454 | 165 | 152.625 | 131.7525 | 152.625
LOAN2- | MOSM2L | 2021 | Change | 26.196 | 0.194 | Composite | 0.12 | 1.142 | 8.6702 | 1090 | 1008.25 | 870.365 | 1008.25
LOAN2- | WFIE2- | 2021 | Change | 29.169 | 0.154 | Composite | 0.1335 | 1.2702 | 9.0972 | 1090 | 1008.25 | 870.365 | 1008.25
MOSM2- | MOSM2L | 2021 | Change | 5.3 | 0 | OHL | 0.0242 | 0.2302 | 1.4017 | 1090 | 1008.25 | 870.365 | 1008.25
MOSM2- | MOSM2T | 2021 | Change | 5.3 | 0 | OHL | 0.0242 | 0.2302 | 1.4017 | 1090 | 1008.25 | 870.365 | 1008.25
MOSM2T | WFIE2- | 2021 | Change | 2.943 | 0 | OHL | 0.0134 | 0.1278 | 0.7783 | 1090 | 1008.25 | 870.365 | 1008.25
TORN4- | CRYR4- | 2021 | Change | 9.36 | 2.1 | Composite | 0.0132 | 0.2079 | 28.9878 | 1400 | 1295 | 1117.9 | 1295
DEVM1- | ERSK1Q | 2021 | Removed | 0 | 16.5 | Cable | 1.767 | 3.937 | 0.893 | 0 | 0 | 0 | 0
DUNB1Q | INWI1Q | 2021 | Removed | 11.6 | 0 | OHL | 1.0551 | 2.6772 | 0.5764 | 0 | 0 | 0 | 0
DUNB1R | INWI1R | 2021 | Removed | 11.6 | 0 | OHL | 1.0551 | 2.6772 | 0.5764 | 0 | 0 | 0 | 0
BEQU1- | KEON1- | 2023 | Addition | 3 | 0 | OHL | 0.225 | 0.6606 | 0.1578 | 166 | 153.55 | 132.551 | 153.55
CHMO1- | MAHI1R | 2023 | Addition | 1.01 | 0 | OHL | 0.0758 | 0.2224 | 0.0531 | 166.9004 | 154.3829 | 133.27 | 154.3829
DALQ1- | KENN1- | 2023 | Addition | 13 | 0 | OHL | 0.9752 | 2.8628 | 0.6838 | 166 | 153.55 | 132.551 | 153.55
DENN2- | LOAN2- | 2023 | Addition | 21.59 | 0 | OHL | 0.0507 | 0.8069 | 6.6393 | 1500 | 1387.5 | 1197.75 | 1387.5
DEVM4- | NEIL4R | 2023 | Addition | 28.474 | 0 | OHL | 0.0469 | 0.5373 | 17.5348 | 1385.6406 | 1281.7176 | 1106.434 | 1281.7176
ELVA1- | NLEI1- | 2023 | Addition | 12 | 0 | OHL | 0.6374 | 2.5527 | 0.6547 | 226.3444 | 209.3686 | 180.736 | 209.3686
EWEH1Q | HOPR1- | 2023 | Addition | 6 | 0 | OHL | 0.4501 | 1.3213 | 0.3156 | 166.9004 | 154.3829 | 133.27 | 154.3829
GLGL1- | SAKN1- | 2023 | Addition | 6.5 | 0 | OHL | 0.4876 | 1.4314 | 0.3419 | 166 | 153.55 | 132.551 | 153.55
GLLE1- | TONG1- | 2023 | Addition | 33.1 | 0 | OHL | 2.5495 | 7.6848 | 1.6538 | 166 | 153.55 | 132.551 | 153.55
HUNE4- | NEIL4R | 2023 | Addition | 34.97 | 0 | OHL | 0.0706 | 0.7042 | 20.0047 | 1385.6406 | 1281.7176 | 1106.434 | 1281.7176
KEON1R | LONB1T | 2023 | Addition | 10 | 0 | OHL | 0.5312 | 2.1273 | 0.5456 | 241 | 222.925 | 192.4385 | 222.925
KEOO1- | GLLE1- | 2023 | Addition | 7.68 | 0 | OHL | 0.1977 | 1.4206 | 0.4761 | 352 | 325.6 | 281.072 | 325.6
KEOO1Q | KEOO1S | 2023 | Addition | 2.5 | 0 | OHL | 0.0643 | 0.4624 | 0.155 | 352 | 325.6 | 281.072 | 325.6
KEOO1S | GLLE1- | 2023 | Addition | 7.68 | 0 | OHL | 0.1977 | 1.4206 | 0.4761 | 352 | 325.6 | 281.072 | 325.6
LONB1T | LONB1- | 2023 | Addition | 2 | 0 | OHL | 0.15 | 0.4404 | 0.1052 | 166 | 153.55 | 132.551 | 153.55
LONB1T | LORG1- | 2023 | Addition | 8 | 0 | OHL | 0.6001 | 1.7617 | 0.4208 | 166 | 153.55 | 132.551 | 153.55
MAHI1B | MAHI1X | 2023 | Addition | 0 | 0.5 | Cable | 0.0111 | 0.0498 | 0.536 | 148.61 | 137.4642 | 118.6651 | 137.4642
MAHI1X | MAHI1R | 2023 | Addition | 13.5 | 0 | OHL | 0.6752 | 2.8693 | 0.7375 | 195.4793 | 180.8183 | 156.0902 | 180.8183
SANQ1- | GLGL1- | 2023 | Addition | 1.01 | 0 | OHL | 0.0758 | 0.2224 | 0.0531 | 166 | 153.55 | 132.551 | 153.55
STNO1- | MAHI1R | 2023 | Addition | 7.5 | 0 | OHL | 0.5626 | 1.6516 | 0.3945 | 166 | 153.55 | 132.551 | 153.55
CAFA1Q | KEOO1- | 2023 | Change | 0 | 2.58 | Cable | 0.0574 | 0.2571 | 2.7655 | 132 | 122.1 | 105.402 | 122.1
COYL1- | COYT1T | 2023 | Change | 4.64 | 0 | OHL | 0.3531 | 1.0741 | 0.2298 | 285 | 263.625 | 227.5725 | 263.625
COYL1- | MAYT1T | 2023 | Change | 9.716 | 0 | OHL | 0.7393 | 2.2492 | 0.4812 | 285 | 263.625 | 227.5725 | 263.625
COYT1T | MAYB1- | 2023 | Change | 17.946 | 0 | OHL | 1.3656 | 4.1544 | 0.8889 | 285 | 263.625 | 227.5725 | 263.625
EAST1Q | GLLE1- | 2023 | Change | 0 | 1.69 | Cable | 0.0376 | 0.1684 | 1.8115 | 132 | 122.1 | 105.402 | 122.1
GLLE1- | TONG1- | 2023 | Change | 33.1 | 0 | OHL | 2.5495 | 7.6848 | 1.6538 | 166 | 153.55 | 132.551 | 153.55
GLLU1Q | NETS1- | 2023 | Change | 22 | 0 | OHL | 1.3448 | 5.0188 | 1.1201 | 163.471 | 151.2106 | 130.5316 | 151.2106
GLLU1R | NETS1- | 2023 | Change | 22 | 0 | OHL | 1.3448 | 5.0188 | 1.1201 | 163.471 | 151.2106 | 130.5316 | 151.2106
HUNE4- | NEIL4Q | 2023 | Change | 35.198 | 0 | OHL | 0.0711 | 0.7088 | 20.1355 | 1385.6406 | 1281.7176 | 1106.434 | 1281.7176
KINB2J | KINC2- | 2023 | Change | 10.325 | 0.385 | Composite | 0.0474 | 0.4407 | 6.9969 | 1090 | 1008.25 | 870.365 | 1008.25
KINB2K | KINC2- | 2023 | Change | 10.71 | 0 | OHL | 0.049 | 0.4533 | 2.9052 | 1090 | 1008.25 | 870.365 | 1008.25
MAYB1- | MAYT1T | 2023 | Change | 12.92 | 0 | OHL | 0.9831 | 2.9909 | 0.6399 | 285 | 263.625 | 227.5725 | 263.625
NEIL2- | WIYH2R | 2023 | Change | 25.453 | 0 | OHL | 0.1107 | 1.0835 | 6.9057 | 952.6279 | 881.1808 | 760.6734 | 881.1808
DEVM4- | HUNE4- | 2023 | Removed | 50.471 | 0.167 | Composite | 0.0905 | 0.9798 | 33.476 | 1316.3586 | 1217.6317 | 1051.1124 | 1217.6317
DUMF1- | TONG1Q | 2023 | Removed | 0 | 43.58 | Cable | 4.447 | 10.71 | 2.18 | 0 | 0 | 0 | 0
GLLE1- | KEOO1- | 2023 | Removed | 7.68 | 0 | OHL | 0.697 | 1.6798 | 0.4048 | 132.6058 | 122.6604 | 105.8857 | 122.6604
GALA1- | ECCL1- | 2026 | Addition | 30.5 | 0 | OHL | 2.2947 | 7.1644 | 1.5057 | 166 | 153.55 | 132.551 | 153.55
GALA1- | ECCL1- | 2026 | Addition | 30.5 | 0 | OHL | 2.2947 | 7.1644 | 1.5057 | 166 | 153.55 | 132.551 | 153.55
ECCL1- | GALA1- | 2026 | Removed | 30.94 | 0 | OHL | 2.8142 | 7.133 | 1.538 | 132.6058 | 122.6604 | 105.8857 | 122.6604
ECCL1- | GALA1- | 2026 | Removed | 31.37 | 0 | OHL | 2.848 | 7.3696 | 1.5301 | 132.6058 | 122.6604 | 105.8857 | 122.6604

## B-2-2c
Table B.2.2c - NGET Circuit Changes 2018/19 to 2026/27 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
CANT41 | SELT41 | 2018 | Addition | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3100 | 2867.5 | 2475.35 | 2867.5
CANT42 | RICH41 | 2018 | Addition | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0331 | 2420 | 2238.5 | 1932.37 | 2238.5
CANT42 | RICH41 | 2018 | Addition | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0331 | 2420 | 2238.5 | 1932.37 | 2238.5
EGGB41 | KNOT41 | 2018 | Addition | 5.56 | 0.7 | Composite | 0.0062334 | 0.10038 | 7.7977 | 1100 | 1017.5 | 878.35 | 1017.5
EGGB42 | KNOT41 | 2018 | Addition | 5.56 | 0 | OHL | 0.006 | 0.0967 | 3.6652 | 2780 | 2571.5 | 2219.83 | 2571.5
KNOT41 | FERR41 | 2018 | Addition | 6.304 | 0 | OHL | 0.0068 | 0.1096 | 4.1576 | 2780 | 2571.5 | 2219.83 | 2571.5
KNOT41 | ROCH4A | 2018 | Addition | 79.315 | 0.7 | Composite | 1.0243 | 17.8544 | 56.6592 | 1100 | 1017.5 | 878.35 | 1017.5
SELL41 | SELT41 | 2018 | Addition | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3100 | 2867.5 | 2475.35 | 2867.5
SELL41 | SELT41 | 2018 | Addition | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2370 | 2192.25 | 1892.445 | 2192.25
KENG41 | SJOW41 | 2018 | Change | 0 | 6 | Cable | 0.0027 | 0.0477 | 43.6608 | 2000 | 1850 | 1597 | 1850
KENG41 | SJOW41 | 2018 | Change | 0 | 6 | Cable | 0.0027 | 0.0477 | 43.6608 | 2000 | 1850 | 1597 | 1850
KENG41 | WLSD41 | 2018 | Change | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1637.25 | 1413.345 | 1637.25
KENG41 | WLSD42 | 2018 | Change | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1637.25 | 1413.345 | 1637.25
CANT41 | SELL41 | 2018 | Removed | 26.711 | 0.257 | Composite | 0.0417 | 0.5138 | 26.0013 | 2370 | 2192.25 | 1892.445 | 2192.25
CONQ41 | DEES41 | 2018 | Removed | 0 | 0.21 | Cable | 0 | 0 | 0 | 3330 | 3080.25 | 2659.005 | 3080.25
EGGB41 | ROCH4A | 2018 | Removed | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1100 | 1017.5 | 878.35 | 1017.5
EGGB42 | FERR41 | 2018 | Removed | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2780 | 2571.5 | 2219.83 | 2571.5
WALP12 | WALP11 | 2018 | Removed | 0 | 0 | Series Reactor | 0.15 | 12 | 0 | 90 | 90 | 90 | 90
BOTW41 | CHIL41 | 2019 | Addition | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 693 | 640.8588 | 553.217 | 640.8588
BRFO41 | DISS4A | 2019 | Addition | 30 | 0.1 | Composite | 0.0646 | 0.6289 | 18.4563 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO42 | DISS4B | 2019 | Addition | 30 | 0.1 | Composite | 0.0646 | 0.6289 | 18.4563 | 3070 | 2839.75 | 2451.395 | 2839.75
CHIL41 | FAWL41 | 2019 | Addition | 0 | 7.14 | parallel Cable | 0.0018 | 0.0112 | 109.0992 | 1020 | 1017.4999 | 878.3499 | 1017.4999
CHIL41 | LOVE41 | 2019 | Addition | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 693 | 640.8588 | 553.217 | 640.8588
DISS4A | EYES41 | 2019 | Addition | 5 | 0 | OHL | 0.0044 | 0.0859 | 3.3607 | 1590 | 1470.75 | 1269.615 | 1470.75
DISS4A | NORM41 | 2019 | Addition | 31.576 | 0 | OHL | 0.0679 | 0.6608 | 17.3208 | 3070 | 2839.75 | 2451.395 | 2839.75
DISS4B | EYES41 | 2019 | Addition | 5 | 0 | OHL | 0.0044 | 0.0859 | 3.3607 | 1590 | 1470.75 | 1269.615 | 1470.75
DISS4B | NORM41 | 2019 | Addition | 31.576 | 0 | OHL | 0.0679 | 0.6608 | 17.3208 | 3070 | 2839.75 | 2451.395 | 2839.75
EGGB41 | ROCH4A | 2019 | Addition | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1100 | 1017.5 | 878.35 | 1017.5
EGGB42 | FERR41 | 2019 | Addition | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2780 | 2571.5 | 2219.83 | 2571.5
KINO41 | NFLE41 | 2019 | Change | 23.626 | 0 | OHL | 0.0249 | 0.4177 | 15.452 | 3100 | 2867.5 | 2475.35 | 2867.5
KINO41 | SING41 | 2019 | Change | 17.685 | 0 | OHL | 0.0157 | 0.3038 | 11.8869 | 3820 | 3533.5 | 3050.27 | 3533.5
BOTW41 | FAWL41 | 2019 | Removed | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1110 | 1026.75 | 886.335 | 1026.75
BRFO41 | NORM41 | 2019 | Removed | 61.576 | 0.1 | Composite | 0.1325 | 1.2896 | 35.7771 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO41 | NORM41 | 2019 | Removed | 61.576 | 0.1 | Composite | 0.1325 | 1.2896 | 35.7771 | 1590 | 1470.75 | 1269.615 | 1470.75
EGGB41 | KNOT41 | 2019 | Removed | 5.56 | 0.7 | Composite | 0 | 0 | 0 | 1100 | 1017.5 | 878.35 | 1017.5
EGGB42 | KNOT41 | 2019 | Removed | 5.56 | 0 | OHL | 0.006 | 0.0967 | 3.6652 | 2780 | 2571.5 | 2219.83 | 2571.5
FAWL41 | LOVE41 | 2019 | Removed | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1110 | 1026.75 | 886.335 | 1026.75
KNOT41 | FERR41 | 2019 | Removed | 6.304 | 0 | OHL | 0.0068 | 0.1096 | 4.1576 | 2780 | 2571.5 | 2219.83 | 2571.5
KNOT41 | ROCH4A | 2019 | Removed | 79.315 | 0.7 | Composite | 0 | 0 | 0 | 1100 | 1017.5 | 878.35 | 1017.5
DINO41 | PENI41 | 2020 | Addition | 0 | 8.183 | Cable | 0.0043 | 0.0684 | 123.66 | 1620 | 1498.5 | 1293.57 | 1498.5
FOUX41 | PENI41 | 2020 | Addition | 23.025 | 0 | OHL | 0.0303 | 0.4488 | 13.6563 | 2780 | 2571.5 | 2219.83 | 2571.5
FOUX41 | TRAW41 | 2020 | Addition | 17.53 | 12.286 | parallel Composite | 0.0253 | 0.3827 | 255.5241 | 2780 | 2571.5 | 2219.83 | 2571.5
HATL21 | HAWP21 | 2020 | Addition | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP21 | WBOL21 | 2020 | Addition | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1090 | 1008.25 | 870.365 | 1008.25
PENI41 | PENT41 | 2020 | Addition | 4.545 | 2 | Composite | 0.0049 | 0.0726 | 3.2978 | 2780 | 2571.5 | 2219.83 | 2571.5
SSHI21 | TYNE21 | 2020 | Addition | 6.863 | 0 | OHL | 0.0303 | 0.2915 | 1.8625 | 995 | 920.375 | 794.5075 | 920.375
SSHI21 | WBOL21 | 2020 | Addition | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 955 | 883.375 | 762.5675 | 883.375
HARM21 | HATL21 | 2020 | Change | 13.983 | 0 | OHL | 0.0476 | 0.5708 | 3.9608 | 1090 | 1008.25 | 870.365 | 1008.25
HATL21 | SALH21 | 2020 | Change | 7.794 | 0 | OHL | 0.0331 | 0.3358 | 2.0838 | 1380 | 1276.5 | 1101.93 | 1276.5
HAWP21 | OFFE21 | 2020 | Change | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1090 | 1008.25 | 870.365 | 1008.25
OFFE21 | WBOL21 | 2020 | Change | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1090 | 1008.25 | 870.365 | 1008.25
PENT41 | TRAW41 | 2020 | Change | 45.1 | 6.308 | Composite | 0.0624 | 0.9397 | 174.7909 | 1550 | 1433.75 | 1237.675 | 1433.75
DINO41 | PENT41 | 2020 | Removed | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9578 | 1620 | 1498.5 | 1293.57 | 1498.5
HATL21 | WBOL21 | 2020 | Removed | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1090 | 1008.25 | 870.365 | 1008.25
LISD21 | LISD2A | 2020 | Removed | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 693.75 | 598.875 | 693.75
TILB41 | TILB4B | 2020 | Removed | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3100 | 2867.5 | 2475.35 | 2867.5
TILB4A | TILB41 | 2020 | Removed | 0.05808 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3100 | 2867.5 | 2475.35 | 2867.5
TYNE21 | WBOL21 | 2020 | Removed | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1090 | 1008.25 | 870.365 | 1008.25
NECT4A | KINL41 | 2021 | Addition | 30.347 | 0 | OHL | 0.0269 | 0.5209 | 20.404 | 2520 | 2331 | 2012.22 | 2331
TILB41 | TILB4B | 2021 | Addition | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3100 | 2867.5 | 2475.35 | 2867.5
TILB4A | TILB41 | 2021 | Addition | 0.05808 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3100 | 2867.5 | 2475.35 | 2867.5
WALP41 | KINL41 | 2021 | Addition | 44.319 | 0 | OHL | 0.0393 | 0.7609 | 29.7952 | 2520 | 2331 | 2012.22 | 2331
CARR41 | KEAR41 | 2021 | Change | 13.154 | 0 | OHL | 0.0223 | 0.2572 | 7.7547 | 2210 | 2044.25 | 1764.685 | 2044.25
CARR41 | PEWO41 | 2021 | Change | 56.9 | 0 | OHL | 0.0933 | 1.1043 | 33.7811 | 3100 | 2867.5 | 2475.35 | 2867.5
KEAR41 | PADI41 | 2021 | Change | 39.101 | 0 | OHL | 0.0688 | 0.7651 | 23.0192 | 2170 | 2007.25 | 1732.745 | 2007.25
PADI41 | PEWO41 | 2021 | Change | 37.608 | 0 | OHL | 0.0635 | 0.7283 | 22.3609 | 3100 | 2867.5 | 2475.35 | 2867.5
NECT4A | WALP41 | 2021 | Removed | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 2520 | 2331 | 2012.22 | 2331
BICF41 | WMAR4B | 2023 | Addition | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3190 | 2950.75 | 2547.215 | 2950.75
BICF42 | WMAR4A | 2023 | Addition | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3190 | 2950.75 | 2547.215 | 2950.75
CANW41 | OSWE4A | 2023 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2400 | 2220 | 1916.4 | 2220
CANW41 | OSWE4B | 2023 | Addition | 34.812 | 1 | Composite | 0.0556 | 0.6697 | 20.9333 | 2400 | 2220 | 1916.4 | 2220
DISS4A | NEWF4A | 2023 | Addition | 24.576 | 0 | OHL | 0.0218 | 0.4221 | 16.5186 | 3820 | 3533.5 | 3050.27 | 3533.5
DISS4B | NEWF4B | 2023 | Addition | 24.576 | 0 | OHL | 0.0218 | 0.4221 | 16.5186 | 3820 | 3533.5 | 3050.27 | 3533.5
IRON41 | OSWE4B | 2023 | Addition | 27.261 | 0 | OHL | 0.0436 | 0.5243 | 16.3927 | 3100 | 2867.5 | 2475.35 | 2867.5
KIBY41 | WASF41 | 2023 | Addition | 10.945 | 2 | Composite | 0.0199 | 0.2182 | 6.3427 | 2210 | 2044.25 | 1764.685 | 2044.25
KIBY42 | WASF42 | 2023 | Addition | 11.707 | 0 | OHL | 0.0213 | 0.2329 | 6.783 | 2210 | 2044.25 | 1764.685 | 2044.25
LEGA41 | OSWE4A | 2023 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2000 | 1850 | 1597 | 1850
LEGA41 | OSWE4B | 2023 | Addition | 34.812 | 0 | OHL | 0.0556 | 0.6695 | 20.9333 | 2000 | 1850 | 1597 | 1850
LOWE41 | NEWF4A | 2023 | Addition | 37.195 | 1 | Composite | 0.0326 | 0.6289 | 25.439 | 2780 | 2571.5 | 2219.83 | 2571.5
LOWE41 | NEWF4B | 2023 | Addition | 37.195 | 1 | Composite | 0.0326 | 0.6289 | 25.439 | 2780 | 2571.5 | 2219.83 | 2571.5
NEWF4A | NORM41 | 2023 | Addition | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3820 | 3533.5 | 3050.27 | 3533.5
NEWF4B | NORM41 | 2023 | Addition | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3820 | 3533.5 | 3050.27 | 3533.5
OSWE4A | SHRE4A | 2023 | Addition | 12.132 | 0 | OHL | 0.0194 | 0.2333 | 7.2953 | 3100 | 2867.5 | 2475.35 | 2867.5
PEWO41 | WASF41 | 2023 | Addition | 8 | 2 | Composite | 0.0146 | 0.1596 | 4.6347 | 2210 | 2044.25 | 1764.685 | 2044.25
PEWO41 | WASF42 | 2023 | Addition | 8 | 0 | OHL | 0.0149 | 0.1593 | 4.6296 | 2210 | 2044.25 | 1764.685 | 2044.25
SPLN41 | WMAR4A | 2023 | Addition | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3160 | 2923 | 2523.26 | 2923
SPLN41 | WMAR4B | 2023 | Addition | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3160 | 2923 | 2523.26 | 2923
WALP41 | WMAR4A | 2023 | Addition | 23.475 | 0 | OHL | 0.0208 | 0.4032 | 15.7777 | 3190 | 2950.75 | 2547.215 | 2950.75
WALP41 | WMAR4B | 2023 | Addition | 23.425 | 0 | OHL | 0.0208 | 0.4023 | 15.7443 | 3190 | 2950.75 | 2547.215 | 2950.75
BLYT21 | TYNE21 | 2023 | Change | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1258 | 1085.96 | 1258
BLYT21 | TYNE2A | 2023 | Change | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1258 | 1085.96 | 1258
BRLE41 | FLEE41 | 2023 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3820 | 3533.5 | 3050.27 | 3533.5
BRLE41 | FLEE41 | 2023 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3820 | 3533.5 | 3050.27 | 3533.5
CARR41 | KEAR41 | 2023 | Change | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2210 | 2044.25 | 1764.685 | 2044.25
CARR41 | PEWO41 | 2023 | Change | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4403 | 2170 | 2007.25 | 1732.745 | 2007.25
FLEE41 | LOVE41 | 2023 | Change | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3100 | 2867.5 | 2475.35 | 2867.5
FLEE41 | LOVE41 | 2023 | Change | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3100 | 2867.5 | 2475.35 | 2867.5
HAWP21 | OFFE21 | 2023 | Change | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1180 | 1091.5 | 942.23 | 1091.5
HAWP21 | WBOL21 | 2023 | Change | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1180 | 1091.5 | 942.23 | 1091.5
INDQ41 | LAND41 | 2023 | Change | 49.565 | 0 | OHL | 0.0946 | 0.9615 | 29.5135 | 1930 | 1785.25 | 1541.105 | 1785.25
INDQ41 | LAND42 | 2023 | Change | 49.565 | 0 | OHL | 0.0946 | 0.9615 | 29.5135 | 1930 | 1785.25 | 1541.105 | 1785.25
KEAR41 | PADI41 | 2023 | Change | 39.101 | 0 | OHL | 0.0535 | 0.7262 | 24.4122 | 2170 | 2007.25 | 1732.745 | 2007.25
OFFE21 | WBOL21 | 2023 | Change | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1180 | 1091.5 | 942.23 | 1091.5
PADI41 | PEWO41 | 2023 | Change | 37.608 | 0 | OHL | 0.0524 | 0.7014 | 23.3846 | 2170 | 2007.25 | 1732.745 | 2007.25
PELH41 | RYEH4A | 2023 | Change | 23.015 | 0 | OHL | 0.0359 | 0.4657 | 13.0582 | 3100 | 2867.5 | 2475.35 | 2867.5
PELH41 | RYEH4B | 2023 | Change | 23.439 | 0 | OHL | 0.0366 | 0.4743 | 13.2981 | 3100 | 2867.5 | 2475.35 | 2867.5
RYEH41 | RYEH4B | 2023 | Change | 0.137 | 0 | OHL | 0.0002 | 0.0028 | 0.0777 | 3100 | 2867.5 | 2475.35 | 2867.5
RYEH41 | WALX41 | 2023 | Change | 5.324 | 0 | OHL | 0.0083 | 0.1077 | 3.0209 | 3100 | 2867.5 | 2475.35 | 2867.5
RYEH4A | WALX42 | 2023 | Change | 5.461 | 0 | OHL | 0.0085 | 0.1105 | 3.0987 | 3100 | 2867.5 | 2475.35 | 2867.5
SSHI21 | TYNE21 | 2023 | Change | 6.863 | 0 | OHL | 0.0303 | 0.2915 | 1.8625 | 1180 | 1091.5 | 942.23 | 1091.5
SSHI21 | WBOL21 | 2023 | Change | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1180 | 1091.5 | 942.23 | 1091.5
SSHI22 | TYNE2A | 2023 | Change | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1360 | 1258 | 1085.96 | 1258
SSHI22 | WBOL21 | 2023 | Change | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1180 | 1091.5 | 942.23 | 1091.5
BICF41 | WALP41 | 2023 | Removed | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3190 | 2950.75 | 2547.215 | 2950.75
BICF42 | SPLN41 | 2023 | Removed | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3160 | 2923 | 2523.26 | 2923
DISS4A | NORM41 | 2023 | Removed | 31.576 | 0 | OHL | 0.0679 | 0.6608 | 17.3208 | 3070 | 2839.75 | 2451.395 | 2839.75
DISS4B | NORM41 | 2023 | Removed | 31.576 | 0 | OHL | 0.0679 | 0.6608 | 17.3208 | 3070 | 2839.75 | 2451.395 | 2839.75
IRON41 | LEGA41 | 2023 | Removed | 62.073 | 0 | OHL | 0.0992 | 1.1938 | 37.326 | 2400 | 2220 | 1916.4 | 2220
KIBY21 | WASF22 | 2023 | Removed | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1520 | 1406 | 1213.72 | 1406
KIBY22 | WASF21 | 2023 | Removed | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1520 | 1406 | 1213.72 | 1406
LEGA41 | SHRE4A | 2023 | Removed | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2286 | 2000 | 1850 | 1597 | 1850
PEWO21 | WASF22 | 2023 | Removed | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1520 | 1406 | 1213.72 | 1406
PEWO22 | WASF21 | 2023 | Removed | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1520 | 1406 | 1213.72 | 1406
SHRE4A | SHRE4B | 2023 | Removed | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 9999 | 9249.075 | 7984.2015 | 9249.075
SPLN41 | WALP41 | 2023 | Removed | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3190 | 2950.75 | 2547.215 | 2950.75
BACT41 | NORM41 | 2026 | Addition | 27 | 8 | Composite | 0.0359 | 0.6099 | 117.1358 | 3160 | 2923 | 2523.26 | 2923
BACT41 | NORM41 | 2026 | Addition | 27 | 8 | Composite | 0.0359 | 0.6099 | 117.1358 | 3160 | 2923 | 2523.26 | 2923
BRIW41 | PURI4A | 2026 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 3100 | 2867.5 | 2475.35 | 2867.5
BRIW41 | PURI4B | 2026 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 3100 | 2867.5 | 2475.35 | 2867.5
CELL41 | LEGA41 | 2026 | Addition | 80 | 0 | OHL | 0.0702 | 1.3633 | 53.9622 | 3820 | 3533.5 | 3050.27 | 3533.5
CELL41 | LEGA41 | 2026 | Addition | 80 | 0 | OHL | 0.0702 | 1.3633 | 53.9622 | 3820 | 3533.5 | 3050.27 | 3533.5
EGGB41 | OSBA42 | 2026 | Addition | 33 | 0 | OHL | 0.0431 | 0.6343 | 19.8755 | 2780 | 2571.5 | 2219.83 | 2571.5
EGGB42 | OSBA41 | 2026 | Addition | 33 | 1 | Composite | 0.0431 | 0.6345 | 19.8755 | 2780 | 2571.5 | 2219.83 | 2571.5
HAWP41 | NORT41 | 2026 | Addition | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 2780 | 2571.5 | 2219.83 | 2571.5
HIKP41 | HIKP42 | 2026 | Addition | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2000 | 1850 | 1597 | 1850
HIKP41 | HINP41 | 2026 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 2210 | 2044.25 | 1764.685 | 2044.25
HIKP41 | PURI4B | 2026 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 2867.5 | 2475.35 | 2867.5
HIKP41 | TAUN42 | 2026 | Addition | 27.657 | 0 | OHL | 0.0503 | 0.5503 | 16.0284 | 2210 | 2044.25 | 1764.685 | 2044.25
HIKP42 | HINP41 | 2026 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 2210 | 2044.25 | 1764.685 | 2044.25
HIKP42 | PURI4A | 2026 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 2867.5 | 2475.35 | 2867.5
HIKP42 | TAUN41 | 2026 | Addition | 27.644 | 0 | OHL | 0.0503 | 0.55 | 16.0209 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | SAFO41 | 2026 | Addition | 24.54 | 8.15 | Composite | 0.0376 | 0.5627 | 203.1782 | 3100 | 2867.5 | 2475.35 | 2867.5
HINP41 | SEAB41 | 2026 | Addition | 53.385 | 8.15 | Composite | 0.0697 | 1.1063 | 220.9169 | 3100 | 2867.5 | 2475.35 | 2867.5
MELK41 | PURI4A | 2026 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 3100 | 2867.5 | 2475.35 | 2867.5
MELK41 | PURI4B | 2026 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 3100 | 2867.5 | 2475.35 | 2867.5
PELH41 | WYMO4B | 2026 | Addition | 26.891 | 0 | OHL | 0.0292 | 0.4677 | 17.7269 | 3180 | 2941.5 | 2539.23 | 2941.5
PEMB41 | SWAN41 | 2026 | Addition | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | WYLF4B1 | 2026 | Addition | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
SAFO41 | SEAB41 | 2026 | Addition | 28.845 | 0 | OHL | 0.0322 | 0.5436 | 17.7387 | 3100 | 2867.5 | 2475.35 | 2867.5
SUND42 | WYMO41 | 2026 | Addition | 17.986 | 0 | OHL | 0.0195 | 0.3128 | 11.8566 | 3180 | 2941.5 | 2539.23 | 2941.5
SWAN41 | WALH41 | 2026 | Addition | 133.452 | 5.468 | parallel Composite | 0.1457 | 2.3405 | 151.8607 | 2780 | 2571.5 | 2219.83 | 2571.5
BRAI4B | PELH41 | 2026 | Change | 65.942 | 0 | OHL | 0.0649 | 1.1398 | 43.9222 | 2780 | 2571.5 | 2219.83 | 2571.5
BRLE41 | MELK41 | 2026 | Change | 81.569 | 0 | OHL | 0.1271 | 1.565 | 48.9494 | 1390 | 1285.75 | 1109.915 | 1285.75
BRLE41 | MELK41 | 2026 | Change | 81.569 | 0 | OHL | 0.1271 | 1.565 | 48.9494 | 1390 | 1285.75 | 1109.915 | 1285.75
CELL41 | DRAK41 | 2026 | Change | 45.012 | 0 | OHL | 0.0701 | 0.8636 | 27.0114 | 3100 | 2867.5 | 2475.35 | 2867.5
CELL41 | DRAK41 | 2026 | Change | 45.564 | 0 | OHL | 0.071 | 0.8742 | 27.3416 | 3100 | 2867.5 | 2475.35 | 2867.5
DRAK41 | HAMH41 | 2026 | Change | 29.434 | 0 | OHL | 0.0507 | 0.5785 | 17.2651 | 2010 | 1859.25 | 1604.985 | 1859.25
DRAK41 | OLDB4A | 2026 | Change | 48.818 | 0.5 | Composite | 0.0896 | 0.973 | 36.7062 | 1000 | 925 | 798.5 | 925
FOUX41 | PENI41 | 2026 | Change | 23.025 | 0 | OHL | 0.0204 | 0.3955 | 15.4761 | 3600 | 3330 | 2874.6 | 3330
FOUX41 | TRAW41 | 2026 | Change | 17.53 | 12.286 | parallel Composite | 0.0175 | 0.3385 | 298.9489 | 3600 | 3330 | 2874.6 | 3330
HAWP41 | NORT41 | 2026 | Change | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 2550 | 2358.75 | 2036.175 | 2358.75
IRON41 | OSWE4B | 2026 | Change | 27.261 | 0 | OHL | 0.0425 | 0.523 | 16.3593 | 3100 | 2867.5 | 2475.35 | 2867.5
IRON41 | SHRE4A | 2026 | Change | 15.129 | 0 | OHL | 0.0236 | 0.2903 | 9.0789 | 2400 | 2220 | 1916.4 | 2220
LEGA41 | OSWE4A | 2026 | Change | 34.812 | 0 | OHL | 0.0542 | 0.6679 | 20.8906 | 2000 | 1850 | 1597 | 1850
LEGA41 | OSWE4B | 2026 | Change | 34.812 | 0 | OHL | 0.0542 | 0.6679 | 20.8906 | 2000 | 1850 | 1597 | 1850
NORT41 | OSBA41 | 2026 | Change | 83.839 | 0 | OHL | 0.1204 | 1.6202 | 50.1493 | 2010 | 1859.25 | 1604.985 | 1859.25
NORT41 | OSBA42 | 2026 | Change | 83.839 | 0 | OHL | 0.1204 | 1.6202 | 50.1493 | 2550 | 2358.75 | 2036.175 | 2358.75
OSWE4A | SHRE4A | 2026 | Change | 12.132 | 0 | OHL | 0.0189 | 0.2328 | 7.2804 | 3100 | 2867.5 | 2475.35 | 2867.5
PELH41 | WYMO4A | 2026 | Change | 26.856 | 0 | OHL | 0.0291 | 0.4667 | 17.7225 | 2770 | 2562.25 | 2211.845 | 2562.25
PENI41 | PENT41 | 2026 | Change | 4.545 | 2 | Composite | 0.004 | 0.0785 | 3.0549 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | TRAW41 | 2026 | Change | 45.1 | 12.616 | parallel Composite | 0.042 | 0.8131 | 325.1931 | 3000 | 2775 | 2395.5 | 2775
SUND41 | WYMO41 | 2026 | Change | 18.156 | 0 | OHL | 0.0197 | 0.3152 | 11.9934 | 3050 | 2821.25 | 2435.425 | 2821.25
BRWA2A | HINP22 | 2026 | Removed | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 765 | 707.625 | 610.8525 | 707.625
BRWA2B | HINP2 | 2026 | Removed | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 760 | 703 | 606.86 | 703
HAWP21 | NORT21 | 2026 | Removed | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 910 | 841.75 | 726.635 | 841.75
HINP41 | MELK41 | 2026 | Removed | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2010 | 1859.25 | 1604.985 | 1859.25
HINP41 | MELK41 | 2026 | Removed | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2010 | 1859.25 | 1604.985 | 1859.25
HINP41 | TAUN41 | 2026 | Removed | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | TAUN42 | 2026 | Removed | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2210 | 2044.25 | 1764.685 | 2044.25
PELH41 | SUND42 | 2026 | Removed | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 2941.5 | 2539.23 | 2941.5
PEMB41 | WALH41 | 2026 | Removed | 217.727 | 5.468 | Composite | 0.2372 | 3.8063 | 207.4152 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | WYLF41 | 2026 | Removed | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
PENT41 | WYLF41 | 2026 | Removed | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2780 | 2571.5 | 2219.83 | 2571.5
SJOW21 | TOTT23 | 2026 | Removed | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 870 | 804.75 | 694.695 | 804.75
SJOW21 | TOTT24 | 2026 | Removed | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 870 | 804.75 | 694.695 | 804.75
SWAN42 | SWAN4A | 2026 | Removed | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1390 | 1285.75 | 1109.915 | 1285.75

## B-2-2d
Table B.2.2d - Indicative Offshore Transmission Circuit Changes 2018/19 to 2026/27 | [13 empty] | Back To Menu
OFTO | Site | Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage (kV)
- | Walney extension | WALE11 | WAEN11 | 2018 | Addition | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 0 | 150
- | Walney extension | WALE11 | WAEN11 | 2018 | Addition | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 0 | 150
- | Walney extension | WALE12 | WAEN12 | 2018 | Addition | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 0 | 150
- | Walney extension | WALE12 | WAEN12 | 2018 | Addition | 0 | 50 | Cable | 1.3333 | 2.6667 | 74.2201 | 0 | 150
- | Galloper | GAON11 | LEIS11 | 2018 | Addition | 0 | 0.25 | Cable | 0 | 0 | 0 | 200 | 132
- | Galloper | GAON11 | LEIS11 | 2018 | Addition | 0 | 0.25 | Cable | 0 | 0 | 0 | 200 | 132
- | Galloper | GAON11 | GAOF1A | 2018 | Addition | 0 | 45 | Cable | 1.02 | 3.0599 | 1.776 | 300 | 132
- | Galloper | GAON11 | GAOF1B | 2018 | Addition | 0 | 45.165 | Cable | 1.02 | 3.0599 | 1.776 | 300 | 132
- | Dogger Bank | DOGG4* | CREB41 | 2021 | Addition | 0 | 1.5 | Cable | 0 | 0.0001 | 0 | 2500 | 400
- | Dogger Bank | DOGG4 | LACK41 | 2026 | Addition | 0 | 0.5 | Cable | 0 | 0.0001 | 0 | 2500 | 400

## B-3-1a
Table B.3.1a - SHE Transmission Transformers 2017/18 | [5 empty] | Back To Menu
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
ACHR1R | ACHR3- | 0.36 | 18 | 0 | 90
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.7 | 21 | 0 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU3- | 1.04 | 27.7301 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.7301 | 0 | 45
BEAU2J | BEAU1J | 0.6786 | 12.2312 | -0.0009 | 120
BEAU2J | BEAU1J | 0.6786 | 12.1644 | -0.0009 | 120
BEAU2K | BEAU1K | 0.6786 | 12.1895 | -0.0009 | 120
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.0004 | 1200
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.0004 | 1200
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 0.1486 | 5.3035 | -0.0006 | 360
BLHI2K | BLHI1K | 0.1506 | 5.3034 | -0.0006 | 360
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2L | 0.018 | 1.576 | -0.09 | 1200
BLHI4- | BLHI2M | 0.018 | 1.576 | -0.09 | 1200
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRCW2J | BRCW3- | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 0.42 | 20 | 0 | 120
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 38.9998 | 0 | 30
BROR1- | BROR3- | 0.816 | 27.1211 | 0 | 45
BUMU1Q | BUMU3- | 0.407 | 26.975 | 0 | 90
BUMU1R | BUMU3- | 0.407 | 26.975 | 0 | 90
CAAD1Q | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1Q | CAAD3J | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1R | CAAD3J | 0.5 | 25 | 0 | 90
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120
CASS1Q | CASS3- | 1.518 | 39.8711 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90
CONN2J | CONN1J | 0.143 | 5.3036 | -0.0006 | 360
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
CORI1J | CORI3J | 8.3 | 27.5001 | 0 | 60
COUA1Q | COUA3- | 1.05 | 27.89 | 0 | 45
COUA1R | COUA3- | 1.05 | 27.89 | 0 | 45
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
CRSS1J | COUW31 | 0.3629 | 18.0297 | -0.0123 | 90
CRSS1J | CRSS1Q | 0.073 | 1.875 | 0 | 240
CRSS1K | CRSS1R | 0.073 | 1.875 | 0 | 240
CRSS2A | CRSS1J | 0.2466 | 9.0008 | -0.0005 | 240
CRSS2B | CRSS1K | 0.2459 | 9.0175 | -0.0005 | 240
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DOUN2- | DOUN1- | 0.2112 | 7.7054 | -0.0005 | 240
DOUN2- | DOUN1- | 0.2237 | 7.9135 | -0.0006 | 240
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.7 | 21 | 0 | 60
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120
DYCE1Q | DYCE3- | 1.35 | 26.67 | 0 | 60
DYCE1R | DYCE3- | 1.36 | 26.7299 | 0 | 60
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1J | ERRO1A | 0.04 | 1.942 | 0 | 240
ERRO1K | ERRO1B | 0.04 | 1.942 | 0 | 240
ERRO1T | ERRO1J | 0.068 | 3.73 | 0 | 150
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FARI2J | FARI1J | 0.4989 | 8.2933 | -0.038 | 120
FARI2K | FARI1K | 0.4955 | 8.3186 | -0.038 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1Q | FAUG3- | 2.23 | 64.33 | 0 | 15
FAUG2J | FAUG1- | 0.2606 | 7.7039 | -0.0005 | 240
FAUG2K | FAUG1- | 0.2629 | 7.7038 | -0.0005 | 240
FAUG4- | FAUG1- | 0.3185 | 8.4523 | -0.013 | 240
FAUG4- | FAUG1- | 0.2149 | 8.0138 | -0.013 | 240
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FETT2R | FETT1- | 0.217 | 4.2737 | -0.0006 | 240
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FRAS1Q | FRAS3- | 0.642 | 26.9039 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.9039 | 0 | 45
FWIL1Q | FWIL3- | 0.88 | 27.33 | 0 | 60
FWIL1R | FWIL3- | 0.88 | 27.67 | 0 | 60
FYRI2J | FYRI1J | 0.0967 | 3.8863 | -0.0006 | 480
FYRI2K | FYRI1K | 0.0971 | 3.8738 | -0.0006 | 480
GLAG1Q | GLAG3J | 0.82 | 19.3299 | 0 | 60
GLAG1R | GLAG3K | 0.82 | 19.6 | 0 | 60
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEITH3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEITH3A | 0.499 | 24.995 | 0 | 90
KEIT2Q | KEIT1- | 0.2735 | 8.6123 | -0.0007 | 240
KEIT2R | KEIT1- | 0.3328 | 8.9105 | -0.0389 | 240
KIIN1- | KIIN3- | 0.772 | 24.8769 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.5211 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.7801 | 0 | 45
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT1- | 0.3771 | 10.1929 | -0.018 | 240
KINT2K | KINT1- | 0.6786 | 12.1477 | -0.0009 | 120
KINT2K | KINT1- | 0.3751 | 10.2314 | -0.0147 | 240
KNOC2J | KNOC1J | 0.2216 | 4.311 | -0.0076 | 240
KNOC2K | KNOC1J | 0.2205 | 4.3319 | -0.0006 | 240
LAIR1Q | LAIR3- | 0.425 | 24.674 | 0 | 90
LOCB2J | LOCB1J | 0.2181 | 8.1262 | -0.0007 | 240
LOCB2K | LOCB1K | 0.22 | 8.197 | -0.0007 | 240
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.429 | 25.741 | 0 | 90
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MILC1R | MILC3- | 0.78 | 24.8299 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.1301 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MYBS1Q | MYBS3J | 0.895 | 23.9169 | 0 | 60
MYBS1R | MYBS3J | 1.99 | 32.87 | 0 | 30
MYBS1R | MYBS3J | 1.636 | 33.73 | 0 | 30
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6001 | 0 | 60
NANT1Q | NANT3- | 2.857 | 45.714 | 0 | 35
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
PEHE2Q | PEHE1- | 0.4842 | 9.9549 | -0.0178 | 240
PEHE2R | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240
PEHERSV1 | PEHE1- | 0.2649 | 9.2254 | -0.0005 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.3999 | 0 | 45
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PERS2Q | PERS1Q | 0.3363 | 8.9062 | -0.0412 | 240
PERS2R | PERS1R | 0.3341 | 8.8645 | -0.0419 | 240
PORA1Q | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 1.803 | 29.812 | 0 | 30
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
STRW12 | STRW31 | 0.05 | 18 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.5298 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.7869 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.7869 | 0 | 90
TEAL2J | TEAL1- | 0.5506 | 11.7649 | -0.0008 | 180
TEAL2K | TEAL1- | 0.2564 | 11.7305 | -0.0131 | 180
TEAL2K | TEAL1- | 0.5506 | 11.8761 | -0.0008 | 180
THSO1Q | THSO3- | 0.3837 | 24.98 | 0 | 120
THSO1R | THSO3- | 0.3837 | 24.98 | 0 | 120
TUMB1Q | TUMB3- | 0.499 | 24.995 | 0 | 45
TUMB1R | TUMB3- | 0.499 | 24.995 | 0 | 45
TUMM2J | TUMM1J | 0.259 | 7.7457 | -0.0005 | 240
TUMM2K | TUMM1K | 0.2595 | 7.829 | -0.0005 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.2399 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
Table B.3.1b - SPT Transformers 2017/18 | [5 empty] | Back To Menu
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
AYR-2R | AYR-3- | 0.4326 | 19.1618 | 0 | 120
BAGA1Q | BAGA0J | 0.5559 | 33.3287 | 0 | 18
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA0K | 0.5559 | 33.3287 | 0 | 18
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1Q | MARM0J | 0.933 | 56.0122 | 0 | 10
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BERW1R | MARM0K | 0.933 | 56.0122 | 0 | 10
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN0J | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN0K | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN0L | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY0J | 2.24 | 57.9567 | -0.0633 | 10
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY0K | 2.2 | 57.9583 | -0.0625 | 10
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3- | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3- | 0.4868 | 20.6609 | -0.2478 | 120
CLYM2- | CLYM3- | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3- | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1- | 0.1216 | 9.6242 | -0.0793 | 240
COAL4- | COAL1- | 0.1258 | 9.7909 | -0.0801 | 240
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1718 | 8.665 | -0.0204 | 120
COYL2- | COYL1- | 0.3396 | 12.8288 | -0.2375 | 120
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9194 | 21.9808 | 0 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR1B | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM0J | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM0K | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 160
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 160
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3- | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3- | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCF1J | ECCF0J | 1.4773 | 33.3006 | -0.0896 | 15
ECCF1K | ECCF0K | 0.4481 | 26.8629 | 0 | 18
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EKIL2S | EKIL3- | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3- | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3- | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3- | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA4- | ELVA0J | 0.1612 | 34.0696 | -0.0029 | 80
ELVA4- | ELVA0K | 0.1613 | 34.0696 | -0.0101 | 80
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 0.3119 | 21.8311 | 0 | 60
ERSK1R | ERSK3- | 0.3119 | 21.8311 | 0 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 1.1936 | 28.2415 | 0 | 45
GALA1- | GALA3- | 1.5733 | 28.6235 | 0 | 45
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3- | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3- | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3086 | 27.776 | 0 | 90
GLGL1R | GLGL3- | 0.3086 | 27.776 | 0 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.9167 | 21.8975 | 0 | 60
GORG1R | GORG3- | 0.9111 | 21.9311 | 0 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.5271 | 18.7426 | -0.222 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HAGR1Q | HAGR3- | 0.9806 | 20.7268 | -1.3737 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1- | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1- | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
INWI1Q | INWI0J | 0.917 | 55.0024 | 0 | 10
INWI1R | INWI0K | 0.917 | 55.0024 | 0 | 10
JOHN1Q | JOHN3- | 0.9461 | 21.8128 | 0 | 60
JOHN1R | JOHN3- | 0.9461 | 21.8128 | 0 | 60
KAIM2- | KAIM3A | 0.4819 | 20.2443 | -0.2454 | 120
KAIM2- | KAIM3B | 0.4944 | 20.244 | -0.245 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILT2Q | KILT3- | 0.4927 | 18.4934 | -0.1756 | 120
KILT2R | KILT3- | 0.4976 | 18.4933 | -0.1775 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 38
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 38
MOSM1- | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1- | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1- | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1- | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0312 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0312 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0312 | 240
NECU2- | NECU1Q | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1R | 0.1476 | 8.7488 | -0.1299 | 240
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB0J | 0.5559 | 33.3287 | 0 | 18
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB0K | 0.5559 | 33.3287 | 0 | 18
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.94 | 19.8995 | 0 | 60
REDH1- | REDH3- | 0.6267 | 19.9124 | 0 | 90
SACO1Q | SACO0J | 0.933 | 56.0022 | 0 | 10
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO0K | 0.933 | 56.0022 | 0 | 10
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SANX1Q | SANX0J | 0.558 | 33.4787 | 0 | 18
SANX1Q | SANX3- | 0.8844 | 21.5485 | -0.309 | 60
SANX1R | SANX0K | 0.558 | 33.4787 | 0 | 18
SANX1R | SANX3- | 0.8767 | 21.2319 | -0.3087 | 60
SHRU2Q | SHRU3- | 0.4926 | 19.9939 | -0.2739 | 120
SHRU2R | SHRU3- | 0.4656 | 19.9946 | -0.3204 | 120
SIGH2Q | SIGH3A | 0.2282 | 13.7759 | -0.032 | 90
SIGH2Q | SIGH3B | 0.2282 | 13.7759 | -0.032 | 90
SIGH2R | SIGH3A | 0.2141 | 13.765 | -0.0372 | 90
SIGH2R | SIGH3B | 0.2141 | 13.765 | -0.0372 | 90
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4722 | 20.2445 | -0.1542 | 120
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 120
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1- | STLE0J | 0.958 | 57.502 | 0 | 10
STLE1- | STLE0K | 0.958 | 57.502 | 0 | 10
STLE1- | STLE3S | 0.4217 | 25.741 | -0.028 | 90
STLE1- | STLE3S | 0.4235 | 25.6743 | -0.0254 | 90
TELR1Q | TELR3- | 0.9575 | 20.6778 | 0 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG1R | 0.0267 | 1.3331 | 0 | 90
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30
TONG1Q | TONG1R | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WFIE1A | WFIE3- | 0.9889 | 20.4928 | 0 | 60
WFIE1B | WFIE3- | 0.9528 | 20.5613 | 0 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WISH2- | WISH0J | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH0K | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH2- | WISH3- | 0.4821 | 24.1785 | -0.226 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.1517 | 8.707 | -0.1161 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.231 | 12.258 | 0 | 120
WLEX2- | WLEX3B | 0.231 | 12.275 | 0 | 120
WLEX2- | WLEX3C | 0.232 | 12.292 | 0 | 120

## B-3-1c
Table B.3.1c - NGET Transformers 2017/18 | [5 empty] | Back To Menu
Node 1 | Node 2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA41 | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 240
ABHA42 | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 240
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 240
ABTH21 | ABTH11 | 0.0977 | 8.1994 | -1.7127 | 180
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 180
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 98
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 105
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 105
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 32
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 32
ALVE41 | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 240
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 240
AMEM41 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 240
AMEM42 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 240
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 240
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 240
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 240
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 240
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 100
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 100
BARK22 | BARK11 | 0.1646 | 8.0383 | -0.1808 | 180
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 100
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 100
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 750
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 750
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD21 | BEDD11 | 0.1067 | 8.0868 | -0.034 | 240
BEDD21 | BEDD1B | 0.2264 | 12.2479 | -0.6062 | 120
BEDD22 | BEDD11 | 0.1067 | 8.0868 | -0.034 | 240
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD23 | BEDD1A | 0.2264 | 12.2479 | -0.6062 | 120
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 750
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 750
BEDD4B | BEDD2* | 0.0258 | 2.6799 | -1.2431 | 750
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 750
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 240
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 240
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 240
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BICF42 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 240
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 240
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 240
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 240
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 180
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 120
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 120
BLYT4A | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BLYT4B | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 275
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 275
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 240
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 240
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 240
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 240
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 240
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1000
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 240
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 240
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 240
BRFO41 | BRFO1* | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 265
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 265
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 265
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 265
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 240
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 240
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 240
BRIM2D | BRIM1* | 0.1688 | 8.3316 | -1.1711 | 240
BRIN41 | BRIN2* | 0.0146 | 1.609 | -1.8746 | 1000
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1000
BRLE41 | BRLE1* | 0.1303 | 7.8698 | -0.4285 | 240
BRLE41 | BRLE1* | 0.1303 | 7.8698 | -0.4285 | 240
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 240
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 240
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 240
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 240
BRWA2A | BRWA11 | 0.167 | 7.9774 | -0.2092 | 240
BRWA2B | BRWA11 | 0.167 | 7.9774 | -0.2092 | 240
BURW41 | BURW11 | 0.1372 | 8.0197 | -0.1238 | 240
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 240
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 240
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 240
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 240
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 240
BUST4A | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST4B | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT13 | 0.1509 | 8.2849 | -0.3279 | 240
CANT41 | CANT14 | 0.1658 | 8.426 | -0.2939 | 240
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 180
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 180
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 180
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 240
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 180
CAPE41 | CAPE21 | 0.0185 | 1.614 | -0.5638 | 750
CAPE42 | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 750
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 240
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 240
CARR21 | CARR1* | 0.2847 | 12.2467 | -1.4346 | 120
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 180
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 180
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 120
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 180
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 240
CARR42 | CARR21 | 0.0185 | 1.614 | -0.5638 | 750
CARR43 | CARR21 | 0.0185 | 1.614 | -0.5638 | 750
CELL41 | CELL1* | 0.1658 | 8.4025 | -1.5604 | 240
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 240
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 240
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 240
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 240
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 240
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 240
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 240
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 240
CHSI21 | CHSI1A | 0.2264 | 12.2479 | -0.6062 | 120
CHSI21 | CHSI1B | 0.2264 | 12.2479 | -0.6062 | 120
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 240
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 240
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 240
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 240
CILF41 | CILF21 | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF22 | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 240
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 240
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 240
CITR41 | CITR12 | 0.0997 | 8.0088 | -0.093 | 240
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 240
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 240
CONQ41 | CONQ1* | 0 | 2 | 0 | 600
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 240
CONQ41 | CONQ12 | 0.1057 | 7.9352 | -0.339 | 240
CONQ42 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 240
CONQ42 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 240
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 240
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 240
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 240
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 240
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 240
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 240
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CULJ41 | CULJ31 | 0.069 | 25 | 0 | 90
CULJ41 | CULJ32 | 0.069 | 25 | 0 | 90
CULJ41 | CULJ33 | 0.069 | 25 | 0 | 90
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 240
DRAK41 | DRAK2A | 0.0178 | 1.5995 | -1.2431 | 750
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 240
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 240
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 710
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 710
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EASO41 | EASO1* | 0.103 | 7.9231 | -0.0638 | 240
EASO41 | EASO1* | 0.103 | 7.9231 | -0.0638 | 240
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 240
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 240
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 240
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 240
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 180
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 240
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 180
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST11 | 0.1985 | 8.1167 | -0.4624 | 180
ELST21 | ELST11 | 0.1954 | 8.0796 | -0.2295 | 180
ELST21 | ELST11 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST13 | 0.3567 | 11.136 | -0.7303 | 120
ELST22 | ELST12 | 0.1923 | 8.081 | -1.4418 | 180
ELST22 | ELST12 | 0.1031 | 8.1045 | -0.0494 | 180
ELST22 | ELST14 | 0.3567 | 11.136 | -0.7303 | 120
ELST41 | ELST11 | 0.1039 | 7.8456 | -0.9345 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1100
ELST42 | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1000
ENDE41 | ENDE1* | 0.1303 | 7.8698 | -0.4285 | 240
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 240
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 240
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 240
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 240
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 240
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 240
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 240
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 240
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 120
FECK41 | FECK21 | 0.0211 | 1.6463 | -14.2471 | 1000
FECK41 | FECK6* | 0.1867 | 13.8218 | -0.1803 | 180
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 180
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 180
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 240
FERR2B | FERR12 | 0.2847 | 12.2467 | -1.4346 | 120
FERR2D | FERR11 | 0.1147 | 8.673 | -0.0358 | 240
FERR2D | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR2E | FERR11 | 0.1147 | 8.673 | -0.0358 | 240
FERR2E | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR2F | FERR12 | 0.3732 | 11.6023 | -0.7962 | 120
FERR41 | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR41 | FERR23 | 0.0186 | 1.5729 | -7.729 | 1000
FIDF21 | FIDF12 | 0.1594 | 8.6081 | -0.2215 | 240
FIDF21 | FIDF13 | 0.2847 | 12.2467 | -1.4346 | 120
FIDF22 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 240
FIDF23 | FIDF1* | 0.2847 | 12.2467 | -1.4346 | 120
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 240
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 240
FLIB41 | FLIB4* | 0 | 0.08 | 0 | 3000
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 100
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 40
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 40
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 180
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 240
FROD41 | FROD1* | 0.054 | 4.8906 | -0.1253 | 460
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1000
FROD41 | WEAV7* | 0.3209 | 20.5475 | -0.1224 | 80
FROD41 | WEAV7* | 0.3209 | 20.5475 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 240
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 240
GREN41 | GREN11 | 0.1035 | 7.8472 | -0.0758 | 240
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 240
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 240
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 240
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 240
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 240
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 240
HACK21 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 180
HACK22 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 180
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 240
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 240
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 240
HACK41 | HACK21 | 0.0182 | 1.5763 | -0.0904 | 1100
HACK41 | HACK22 | 0.0182 | 1.5763 | -0.0904 | 1100
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1000
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 240
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 240
HAMH41 | LEMR12 | 0.1118 | 8.3874 | -0.0906 | 240
HAMH41 | LEMR12 | 0.1118 | 8.3874 | -0.0906 | 240
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 120
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 120
HARK22 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 120
HARK22 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 120
HARK22 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK4* | HARK21 | 0.0376 | 2.3797 | -3.9009 | 500
HARK4* | HARK22 | 0.0292 | 2.402 | -0.2732 | 500
HARK41 | HARK21 | 0.0321 | 2.4344 | -0.0528 | 500
HARK41 | HARK22 | 0.0376 | 2.3797 | -3.9009 | 500
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 120
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 120
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 180
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 180
HAWP41 | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1000
HEDO21 | HEDN1* | 0.133 | 8.0758 | -0.2287 | 260
HEDO21 | HEDN1* | 0.133 | 8.0758 | -0.2287 | 260
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 240
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 240
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1000
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2150
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 500
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 500
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 240
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 240
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 240
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 240
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 240
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 240
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 240
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 240
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 240
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 240
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 240
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 180
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 180
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 180
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 240
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 240
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 240
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 240
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 240
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 240
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 240
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 240
IVER22 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 120
IVER41 | IVER21 | 0.0326 | 2.3798 | -3.9003 | 500
IVER41 | IVER23 | 0.0132 | 1.4627 | -2.0624 | 1100
IVER42 | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1000
IVER42 | IVER22 | 0.0326 | 2.3798 | -3.9003 | 500
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 100
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 100
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 240
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 240
KEAD41 | KEAD4A | 0.0002 | 0.4178 | 0 | 2210
KEAD41 | KEAD4B | 0.0002 | 0.2873 | 0 | 2210
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 240
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 240
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 240
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 240
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 240
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1000
KEMS41 | KEMS1* | 0.1621 | 8.0984 | -0.0747 | 230
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 240
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 240
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KIBY21 | KIBY1* | 0.1221 | 8.0467 | -0.0391 | 240
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 240
KIBY21 | KIBY12 | 0.1221 | 8.0467 | -0.0391 | 240
KIBY22 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 240
KIBY22 | KIBY12 | 0.1681 | 8.3396 | -1.4878 | 180
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 240
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 240
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 240
KIRK21 | KIRK11 | 0.1411 | 8.6331 | -0.2264 | 240
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 240
KIRK2A | KIRK21 | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | GRTO61 | 0.1747 | 11.0542 | -0.6256 | 120
LACK21 | GRTO61 | 0.1747 | 11.0542 | -0.6256 | 120
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 120
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 120
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 120
LACK41 | LACK21 | 0.0174 | 1.598 | -0.1503 | 1100
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1000
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1100
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1100
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 180
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 180
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 240
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 240
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 240
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 240
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 240
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 240
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 240
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 240
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 240
LEGA41 | LEGA4A | 0.001 | 0.35 | 0 | 2000
LEGA41 | LEGA4B | 0.001 | 0.35 | 0 | 2000
LEIS4A | LEIS11 | 0.103 | 7.9231 | -0.0638 | 240
LISD21 | LISD1* | 0.1441 | 8.6238 | -0.2707 | 240
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 240
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 240
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 240
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 240
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 240
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 240
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 865
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 950
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 240
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 240
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 240
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 240
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 100
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 100
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 750
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 180
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 180
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 240
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 240
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 240
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 240
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 240
MELK41 | MELK11 | 0.1041 | 7.8535 | -0.0851 | 240
MELK41 | MELK21 | 0 | 1.692 | 0 | 750
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MILH21 | MILH11 | 0.179 | 8.3648 | -4.7616 | 180
MILH21 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 240
MILH22 | MILH11 | 0.179 | 8.3648 | -4.7616 | 180
MILH22 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 240
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 240
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 240
MITY41 | MITY12 | 0.137 | 7.9818 | -0.1471 | 240
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 240
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1000
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 750
NEWX21 | NEWX1* | 0.1053 | 8.0451 | -0.0277 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 180
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 240
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 240
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 240
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 240
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2B | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 180
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 240
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 240
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 240
NINF41 | NINF12 | 0.1509 | 7.9378 | -0.9251 | 240
NORL21 | NORL31 | 0.545 | 19.7925 | -0.1407 | 100
NORL22 | NORL31 | 0.545 | 19.7925 | -0.1407 | 100
NORM41 | NORW1* | 0.1307 | 7.9515 | -0.1098 | 240
NORM41 | NORW12 | 0.1264 | 8.4534 | -0.357 | 240
NORM41 | NORW13 | 0.1509 | 7.9378 | -0.9251 | 240
NORM41 | NORW14 | 0.1118 | 8.3874 | -0.0906 | 240
NORM41 | NORW15 | 0.1509 | 7.9378 | -0.9251 | 240
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 240
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 240
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1000
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1000
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 240
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 240
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 240
OCKH21 | OCKH1* | 0.179 | 8.3648 | -4.7616 | 180
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 240
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 240
OCKH2A | OCKH21 | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 100
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 100
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 240
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 240
OLDB4A | OLDB21 | 0.0175 | 1.5879 | -4.0069 | 1000
OSBA41 | OSBA1* | 0.103 | 7.9231 | -0.0638 | 240
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 240
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 240
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 240
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 240
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 240
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 240
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 240
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 240
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 240
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 240
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 240
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 240
PENN41 | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1000
PENN42 | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1000
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 240
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 240
PEWO21 | PENW11 | 0.1594 | 8.6081 | -0.2215 | 240
PEWO22 | PENW11 | 0.1594 | 8.6081 | -0.2215 | 240
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 240
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 240
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 240
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 240
PEWO41 | PEWO21 | 0.0178 | 1.5995 | -1.2431 | 750
PEWO41 | PEWO21 | 0.0189 | 1.6132 | -0.7226 | 750
PEWO41 | PEWO22 | 0.021 | 1.669 | -12.6082 | 750
PEWO41 | PEWO22 | 0.0175 | 1.5879 | -4.0069 | 1000
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS31 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.4975 | 20.4439 | -0.2606 | 100
PITS21 | PITS32 | 0.4975 | 20.4439 | -0.2606 | 100
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 100
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 120
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 180
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 240
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 180
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 180
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 180
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 180
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 240
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 240
RATS41 | RATS11 | 0.1373 | 8.1976 | -0.1719 | 240
RATS41 | RATS12 | 0.1046 | 7.8493 | -0.0881 | 240
RATS41 | RATS12 | 0.103 | 7.9231 | -0.0638 | 240
RATS42 | RATS11 | 0.1278 | 8.0061 | -0.2276 | 240
RATS42 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1000
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240
RAYL41 | RAYM11 | 0.1759 | 7.9134 | -0.267 | 240
RAYL41 | RAYM12 | 0.1309 | 7.8656 | -0.4549 | 240
RAYL41 | RAYM12 | 0.1303 | 7.8698 | -0.4285 | 240
REBR21 | REBR32 | 0.665 | 28.1922 | -0.151 | 100
REBR22 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 120
REBR22 | REBR31 | 0.665 | 28.1922 | -0.151 | 100
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH12 | 0.2847 | 12.2467 | -1.4346 | 120
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 240
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 240
RYEH41 | RYEH12 | 0.1372 | 8.0197 | -0.1238 | 240
RYEH4C | RYEH13 | 0.1326 | 8.774 | -0.7141 | 240
RYEH4D | RYEH11 | 0.1326 | 8.774 | -0.7141 | 240
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 180
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 180
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 240
SEAB41 | SEAB11 | 0.103 | 7.9231 | -0.0638 | 240
SEAB41 | SEAB11 | 0.1307 | 7.9515 | -0.1098 | 240
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 240
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 240
SELL41 | SELL12 | 0.103 | 7.9231 | -0.0638 | 240
SELL41 | SELL13 | 0.1621 | 8.0984 | -0.0747 | 240
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 100
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 100
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE1* | 0.103 | 7.9231 | -0.0638 | 240
SIZE41 | SIZE1* | 0.103 | 7.9231 | -0.0638 | 240
SIZE41 | SIZE1* | 0.103 | 7.9231 | -0.0638 | 240
SIZE41 | SIZE1* | 0.103 | 7.9231 | -0.0638 | 240
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 180
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 180
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 180
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 240
SJOW21 | SJOW13 | 0.1441 | 8.6238 | -0.2707 | 240
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 750
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 750
SJOW4A | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 240
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 240
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 240
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 240
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 240
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 240
SPEN41 | SPEN1* | 0.1264 | 8.4534 | -0.357 | 240
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 240
SPEN42 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 240
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 100
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 100
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 240
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 180
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 180
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 180
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 240
STAL42 | STAL21 | 0.0146 | 1.609 | -1.8746 | 1000
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 240
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 240
STAY4A | STAY41 | 0.0002 | 0.4178 | -13.831 | 2750
STEW21 | STEN11 | 0.3392 | 11.9012 | -0.7294 | 120
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 240
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 120
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1000
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1000
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STSB4A | STSB41 | 0.0003 | 0.1825 | 0 | 2000
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 240
SUND41 | SUND11 | 0.1303 | 7.8698 | -0.4285 | 240
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 240
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 240
SWAN21 | SWAN1* | 0.1646 | 8.0383 | -0.1808 | 180
SWAN21 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 180
SWAN4* | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 240
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN2A | 0.0182 | 1.5763 | -0.0904 | 1100
SWAN4A | SWAN21 | 0.0178 | 1.5995 | -1.2431 | 750
TAUN42 | TAUN11 | 0.1759 | 7.9134 | -0.267 | 240
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 75
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 75
THOM41 | THOM2A | 0.0152 | 1.6463 | -0.1118 | 955
THOM41 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM41 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM42 | THOM21 | 0.0185 | 1.614 | -0.5638 | 750
THOM42 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 750
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 180
TILB21 | TILB11 | 0.3792 | 12.0524 | -0.3982 | 120
TILB21 | TILB12 | 0.3792 | 12.0524 | -0.3982 | 120
TILB41 | TILB1* | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 240
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 750
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1000
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 100
TINP21 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 120
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 100
TINP22 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 120
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 120
TOTT21 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 240
TOTT22 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 180
TOTT23 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 240
TOTT24 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 240
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 120
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 120
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 965
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 750
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 100
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 120
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 240
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 240
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 222
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 240
UPPB22 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 100
UPPB22 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 100
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 100
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 100
USKM21 | USKM1* | 0.1221 | 8.0467 | -0.0391 | 240
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 240
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 240
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 240
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 240
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 240
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 240
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 240
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 240
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 240
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 240
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 240
WALX41 | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1000
WALX41 | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1000
WALX42 | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1000
WALX42 | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1000
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 240
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 240
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 240
WASF21 | WASF12 | 0.197 | 7.9698 | -0.2553 | 180
WASF22 | WASF11 | 0.197 | 7.9698 | -0.2553 | 180
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 240
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 120
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 120
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 180
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 240
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 120
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 120
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 120
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 240
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 240
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 240
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 240
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 240
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 240
WHAM4A | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHAM4B | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 240
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 240
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 240
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO32 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.5913 | 19.0842 | -0.4269 | 100
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 750
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 100
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 100
WIEN2* | WIEN11 | 0.1594 | 8.6081 | -0.2215 | 240
WIEN21 | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 240
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 240
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 240
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 240
WILE41 | WILL21 | 0.0268 | 2.7989 | -0.3188 | 685
WILL21 | WILL11 | 0.2847 | 12.2467 | -1.4346 | 120
WILL21 | WILL12 | 0.2847 | 12.2467 | -1.4346 | 120
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 180
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 180
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 180
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 180
WIMB21 | WIMB1* | 0.179 | 8.3648 | -4.7616 | 180
WIMB21 | WIMB12 | 0.1845 | 7.8956 | -0.1938 | 240
WIMB21 | WIMB12 | 0.167 | 7.9774 | -0.2092 | 240
WIMB21 | WIMB13 | 0.1845 | 7.8956 | -0.1938 | 240
WIMB21 | WIMB13 | 0.167 | 7.9774 | -0.2092 | 240
WIMB21 | WIMB14 | 0.1923 | 8.081 | -1.4418 | 180
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 240
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 180
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 180
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 180
WLSD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 1100
WLSD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 950
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 120
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 180
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 180
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 180
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4B | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 180
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 240
WWEY22 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 180
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY41 | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY41 | WWEY22 | 0.0185 | 1.614 | -0.5638 | 750
WWEY42 | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 750
WWEY42 | WWEY23 | 0.0178 | 1.5995 | -1.2431 | 750
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 240
WYLF41 | WYLF12 | 0.1509 | 8.2849 | -0.3279 | 240
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 240
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 240

## B-3-1d
Table B.3.1d - Offshore Transmission Transformers 2017/18 | [8 empty] | Back To Menu
OFTO | Site | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | LONO11 | 0.33 | 6.4556 |  | 180/180/90 | 400/150/13.9
" | " | LONO42 | LONO12 | 0.33 | 6.4111 |  | 180/180/90 | 400/150/13.9
" | " | LONO41 | LONO13 | 0.33 | 6.4611 |  | 180/180/90 | 400/150/13.9
" | " | LONO42 | LONO14 | 0.33 | 6.4389 |  | 180/180/90 | 400/150/13.9
" | " | LONW11 | LONW31 | 0.402 | 6.56 |  | 180 | 150/33
" | " | LONW11 | LONW31 | 0.407 | 6.58 |  | 180 | 150/33
" | " | LONW12 | LONW32 | 0.4045 | 6.57 |  | 180 | 150/33
" | " | LONW12 | LONW32 | 0.4045 | 6.57 |  | 180 | 150/33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW10 | SSAW30 | 0.23 | 12.07 |  | 90 | 132/33
" | " | SSBW10 | SSBW30 | 0.23 | 12.07 |  | 90 | 132/33
" | " | SSAW10 | SSAW30 | 0.23 | 12.07 |  | 90 | 132/33
" | " | SSBW10 | SSBW30 | 0.23 | 12.07 |  | 90 | 132/33
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAW10 | WAAW30 | 0.41667 | 8.75 |  | 120 | 132/33
|  | WAAW10 | WAAW30 | 0.41667 | 8.75 |  | 120 | 132/33
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABW10 | WABW30 | 0.41667 | 8.75 |  | 120 | 132/33
|  | WABW10 | WABW30 | 0.41667 | 8.75 |  | 120 | 132/33
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GREG11 | GREG30 | 0.18333 | 11.6667 |  | 180/90/90 | 132/33/33
" | " | GREG12 | GREG30 | 0.18333 | 11.6667 |  | 180/90/90 | 132/33/33
" | " | GREG13 | GREG30 | 0.18333 | 11.6667 |  | 180/90/90 | 132/33/33
" | " | GGON11 | GGON51 | 0.23333 | 11 |  | 90 | 132/13.9
" | " | GGON12 | GGON52 | 0.23333 | 11 |  | 90 | 132/13.9
" | " | GGON13 | GGON53 | 0.23333 | 11 |  | 90 | 132/13.9
" | " | GAOF10 | GAOF30 | 0.41111 | 23.3333 |  | 90 | 132/33
" | " | GAOF10 | GAOF30 | 0.41111 | 23.3333 |  | 90 | 132/33
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | BODE4C | GWYO10 | 0.054688 | 3.7469 |  | 320 | 400/132/13.9
" | " | BODE4D | GWYO10 | 0.054688 | 3.7469 |  | 320 | 400/132/13.9
" | " | GWYW10 | GWBW30 | 0.15625 | 11.25 |  | 160 | 132/33
" | " | GWYW10 | GWAW30 | 0.15625 | 11.25 |  | 160 | 132/33
" | " | GWYW10 | GWBW30 | 0.15625 | 11.25 |  | 160 | 132/33
" | " | GWYW10 | GWAW30 | 0.15625 | 11.25 |  | 160 | 132/33
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW10 | BOSW30 |  | 17 |  | 120 | 132/33
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | GUNS10 | GUNS30 | 0.23333 | 8.575 |  | 120 | 132/33
" | " | GUNS10 | GUNS30 | 0.23333 | 8.575 |  | 120 | 132/33
TC Lincs OFTO Limited | Lincs Wind Farm | LINO40 | LINO10 | 0.036667 | 4.6667 |  | 300 | 400/132/13.9
" | " | LINO40 | LINO10 | 0.036667 | 4.6667 |  | 300 | 400/132/13.9
" | " | LINS10 | LINS30 | 0.091667 | 5 |  | 240 | 132/33
" | " | LINS10 | LINS30 | 0.091667 | 5 |  | 240 | 132/33
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMO11 | ORMO31 | 0 | 14.7059 |  | 85 | 132/33
" | " | ORMO11 | ORMO31 | 0 | 14.7059 |  | 85 | 132/33
" | " | ORMO12 | ORMO32 | 0 | 13.6364 |  | 110 | 132/33
TC Robib Rigg OFTO Limited | Robin Rigg East & West Offshore Wind Farms | RREW10 | RREW30 | 0.3 | 11.36 |  | 100 | 132/33
" | " | RRWW10 | RRWW30 | 0.3 | 11.36 |  | 100 | 132/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW10 | THOW30 | 0.18056 | 12.5556 |  | 180/90/90 | 132/33/33
" | " | THOW10 | THOW30 | 0.18056 | 12.5556 |  | 180/90/90 | 132/33/33
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | WDSO11 | 0.20833 | 5 |  | 240/240/80 | 400/155/13.9
" | " | WDSO42 | WDSO12 | 0.20833 | 5 |  | 240/240/80 | 400/155/13.9
" | " | WDSW11 | WDSW30 | 0.20833 | 5 |  | 240 | 155/34
" | " | WDSW12 | WDSW30 | 0.20833 | 5 |  | 240 | 155/34
- | Humber Gateway Offshore Wind Farm | HEDO20 | HUMO11 | 0.19 | 11.4 |  | 160 | 275/132/33
- | " | HEDO20 | HUMO12 | 0.19 | 11.4 |  | 160 | 275/132/33
- | " | HUMW11 | HUMW31 | 0.23 | 8.57 |  | 140 | 132/33
- | " | HUMW12 | HUMW32 | 0.23 | 8.57 |  | 140 | 132/33
- | Westernost Rough Offshore Wind Farm | WERW21 | WERW11 | 0.003458 | 0.20997 |  | 160 | 275/150/33
- | " | WERW22 | WERW11 | 0.003458 | 0.20997 |  | 160 | 275/150/33
- | " | WERW12 | WERW30 | 0.016 | 0.1592 |  | 140 | 150/33
- | " | WERW12 | WERW30 | 0.016 | 0.1592 |  | 140 | 150/33
- | Dudgeon Offshore Wind Farm | DUDG1* | DUDG3* | 0.1275 | 6.117 | 0 | 200 | 132/33
- | " | DUDG1* | DUDG3* | 0.1275 | 6.117 | 0 | 200 | 132/33
- | " | NECT41 | DUDO1* | 0.1264 | 8.4534 | -0.357 | 240 | 400/132/33
- | " | NECT41 | DUDO1* | 0.1264 | 8.4534 | -0.357 | 240 | 400/132/33
- | Burbo Bank Extension Offshore Wind Farm | BURB41 | BURB21 | 0.1875 | 8.998 | -0.3558 | 200 | 400/220/13
- | " | BURB41 | BURB21 | 0.1875 | 8.998 | -0.3558 | 200 | 400/220/13
- | " | BUBW20 | BUBW30 | 0.246 | 9.7219 | -0.8147 | 200 | 220/33
- | " | BUBW20 | BUBW30 | 0.246 | 9.7219 | -0.8147 | 200 | 220/33
- | Race Bank Offshore Wind Farm | RACB41 | RABO21 | 0.0667 | 3.0548 | -0.8396 | 360 | 400/220
- | " | RACB42 | RABO22 | 0.0667 | 3.0548 | -0.8396 | 360 | 400/220
- | " | RABO21 | RABO31 | 0.1917 | 8.5302 | 0 | 130 | 220/27
- | " | RABO22 | RABO32 | 0.1917 | 8.5302 | 0 | 130 | 220/27
- | " | RAOF21 | RAOF31 | 0.081 | 5.9995 | 0 | 200 | 220/34
- | " | RAOF21 | RAOF32 | 0.081 | 5.9995 | 0 | 200 | 220/34
- | " | RAOF22 | RAOF33 | 0.081 | 5.9995 | 0 | 200 | 220/34
- | " | RAOF22 | RAOF34 | 0.081 | 5.9995 | 0 | 200 | 220/34
- | Rampion Offshore Wind Farm | TWIN4A | TWIN1A | 0.0868 | 4.9992 | -0.144 | 240 | 400/150/33
- | " | TWIN4B | TWIN1B | 0.0868 | 4.9992 | -0.144 | 240 | 400/150/33
- | " | RAMP1C | RAMP31 | 0.0868 | 4.9992 | -0.144 | 240 | 150/33
- | " | RAMP1D | RAMP32 | 0.0868 | 4.9992 | -0.144 | 240 | 150/33

## B-3-2a
Table B.3.2a - SHE Transmission Transformer Changes 2018/19 to 2026/27 | [7 empty] | Back To Menu
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABBA1- | ABBA3- | 2018 | Addition | 0.36 | 18 | 0 | 120
DORE11 | DORE31 | 2018 | Addition | 0.36 | 17.99 | 0 | 120
DORE12 | DORE32 | 2018 | Addition | 0.36 | 17.99 | 0 | 120
FYRI1J | FYRI3J | 2018 | Addition | 0.36 | 18 | 0 | 120
FYRI1K | FYRI3J | 2018 | Addition | 0.36 | 18 | 0 | 120
KINT1B | KINT3B | 2018 | Addition | 1.04 | 27.65 | 0 | 60
KINT1B | KINT3B | 2018 | Addition | 0.456 | 26.107 | 0 | 90
MELG4J | MELG1J | 2018 | Addition | 0.107 | 4.007 | -0.013 | 480
MELG4J | MELG1J | 2018 | Addition | 0.107 | 4.007 | -0.013 | 480
MYBS1S | MYBS3M | 2018 | Addition | 0.2645 | 24.6069 | -0.0229 | 120
MYBS1T | MYBS3N | 2018 | Addition | 0.2578 | 24.757 | -0.0242 | 120
SPIT2J | SPIT1J | 2018 | Addition | 0.2184 | 8.2304 | -0.0007 | 240
SPIT2J | SPIT1J | 2018 | Addition | 0.2184 | 8.1846 | -0.0007 | 240
SPIT2K | SPIT1K | 2018 | Addition | 0.1307 | 4.99 | -0.0006 | 360
SPIT2K | SPIT1M | 2018 | Addition | 0.1287 | 4.99 | -0.0006 | 360
STRL1- | STRL3P | 2018 | Addition | 0.36 | 18 | 0 | 120
STRL1- | STRL3Q | 2018 | Addition | 0.36 | 18 | 0 | 120
STRL1- | STRL3R | 2018 | Addition | 0.36 | 18 | 0 | 120
THSO1J | THSO3- | 2018 | Addition | 0.2621 | 24.6736 | -0.0222 | 120
THSO1K | THSO3- | 2018 | Addition | 0.2614 | 24.7403 | -0.0197 | 120
THSO2J | THSO1J | 2018 | Addition | 0.0985 | 3.9363 | -0.0006 | 480
THSO2K | THSO1K | 2018 | Addition | 0.1 | 3.9362 | -0.0006 | 480
TOMT2J | TOMT1J | 2018 | Addition | 0.0985 | 3.9363 | -0.0005 | 480
TOMT2K | TOMT1K | 2018 | Addition | 0.0985 | 3.9363 | -0.0005 | 480
KINT1- | KINT3- | 2018 | Removed | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 2018 | Removed | 0.456 | 26.107 | 0 | 90
THSO1Q | THSO3- | 2018 | Removed | 0.3837 | 24.98 | 0 | 120
THSO1R | THSO3- | 2018 | Removed | 0.3837 | 24.98 | 0 | 120
CAIN2- | CAIN3J | 2019 | Addition | 0.36 | 18 | 0 | 120
CAIN2- | CAIN3J | 2019 | Removed | 0.36 | 18 | 0 | 120
BLHI2K | BLHI1J | 2020 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
BLHI2K | BLHI1J | 2020 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
FETT2R | FETT1- | 2020 | Addition | 0.2217 | 4.3026 | -0.007 | 240
FIDD1S | FIDD3- | 2020 | Addition | 0.4562 | 26.084 | 0 | 90
MILS1Q | MILS3J | 2020 | Addition | 0.36 | 18.0001 | 0 | 60
MYBS1S | MYBS3J | 2020 | Addition | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3J | 2020 | Addition | 0.5 | 25 | 0 | 120
FIDD1R | FIDD3- | 2020 | Removed | 0.4562 | 26.084 | 0 | 90
MYBS1Q | MYBS3J | 2020 | Removed | 0.895 | 23.9169 | 0 | 60
MYBS1R | MYBS3J | 2020 | Removed | 1.636 | 33.73 | 0 | 30
MYBS1R | MYBS3J | 2020 | Removed | 1.99 | 32.87 | 0 | 30
BASK1A | BASK3A | 2021 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | BASK3A | 2021 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | BASK3B | 2021 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | BASK3B | 2021 | Addition | 0.174 | 16.667 | 0 | 120
BASK1A | FINS3- | 2021 | Addition | 0.499 | 24.995 | 0 | 120
BASK1A | FINS3- | 2021 | Addition | 0.499 | 24.995 | 0 | 120
BASK2A | BASK1A | 2021 | Addition | 0.3422 | 8.8892 | -0.0359 | 240
CAIN2- | CAIN3J | 2021 | Addition | 0.36 | 18 | 0 | 120
DOUN2- | DOUN2A | 2021 | Addition | 0.3422 | 8.8892 | -0.0359 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG4J | FAUG1J | 2021 | Addition | 0.107 | 4.007 | -0.013 | 480
FAUG4K | FAUG1- | 2021 | Addition | 0.3185 | 8.4523 | -0.013 | 240
FAUG4K | FAUG1K | 2021 | Addition | 0.107 | 4.007 | -0.013 | 480
CAIN2- | CAIN3J | 2021 | Removed | 0.36 | 18 | 0 | 120
FAUG4- | FAUG1- | 2021 | Removed | 0.3185 | 8.4523 | -0.013 | 240
FAUG4- | FAUG1- | 2021 | Removed | 0.2149 | 8.0138 | -0.013 | 240
ABED1- | ABED3- | 2023 | Addition | 0.36 | 18.0001 | 0 | 60
AULW1S | AULW3- | 2023 | Addition | 0.5 | 25 | 0 | 90
BTUI1G | BTUI3G | 2023 | Addition | 0.36 | 18 | 0 | 120
CRDH2J | ARDB1J | 2023 | Addition | 0.107 | 4.007 | -0.036 | 480
CRDH2K | ARDB1K | 2023 | Addition | 0.107 | 4.007 | -0.013 | 480
CREA1- | CREA3- | 2023 | Addition | 0.36 | 18 | 0 | 90
DUGR1J | DUGR3- | 2023 | Addition | 0.7 | 21 | 0 | 60
GILB1J | GILB3J | 2023 | Addition | 0.3599 | 17.9964 | 0 | 120
GILB1K | GILB3J | 2023 | Addition | 0.3599 | 17.9964 | 0 | 120
GLKY1- | GLKY3J | 2023 | Addition | 0.36 | 18.0001 | 0 | 60
GLNU1- | GLNU3- | 2023 | Addition | 0.36 | 18.0001 | 0 | 60
LIME1- | LIME3- | 2023 | Addition | 0.36 | 18 | 0 | 120
MEYG1- | MEYG3A | 2023 | Addition | 0.36 | 18 | 0 | 42
SALA1- | SALA3- | 2023 | Addition | 0.36 | 17.99 | 0 | 90
WISL1- | WISL3- | 2023 | Addition | 0.499 | 24.995 | 0 | 120
DUGR1Q | DUGR3- | 2023 | Removed | 0.7 | 21 | 0 | 60
BASK1A | COST3- | 2026 | Addition | 0.36 | 18 | 0 | 45
BASK1A | HEST3- | 2026 | Addition | 0.36 | 18 | 0 | 90
BEWF1- | BEWF3- | 2026 | Addition | 0.36 | 18 | 0 | 90
CONN2K | CONN1K | 2026 | Addition | 0.143 | 5.3036 | -0.0006 | 360
CROB2- | CROB3J | 2026 | Addition | 0.36 | 18 | 0 | 120
ELCH1- | ELCH3- | 2026 | Addition | 0.36 | 17.99 | 0 | 120
GOLT1- | GOLT3- | 2026 | Addition | 0.36 | 18 | 0 | 90
KINT2A | KINT2J | 2026 | Addition | 0.005 | 0.4 | 0 | 1000
KINT2B | KINT2K | 2026 | Addition | 0.005 | 0.4 | 0 | 1000
KINT4J | KINT2J | 2026 | Addition | 0.018 | 1.576 | -0.09 | 1200
KINT4K | KINT2K | 2026 | Addition | 0.018 | 1.576 | -0.09 | 1200
MEYG1- | MEYG3B | 2026 | Addition | 0.18 | 9 | 0 | 96
MEYG1- | MEYG3C | 2026 | Addition | 0.18 | 9 | 0 | 96
PEHE4- | PEHE2Q | 2026 | Addition | 0.018 | 1.576 | -0.09 | 1200
PEHE4- | PEHERSV1 | 2026 | Addition | 0.018 | 1.576 | -0.09 | 1200
SONO1- | SONO3- | 2026 | Addition | 0.36 | 18 | 0 | 90
STRW13 | STRW33 | 2026 | Addition | 0.5 | 25 | 0 | 90
STRW13 | STRW34 | 2026 | Addition | 0.5 | 25 | 0 | 90
STRW1C | STRW35 | 2026 | Addition | 0.36 | 18 | 0 | 120
WILW1- | WILW3- | 2026 | Addition | 0.36 | 18.0001 | 0 | 60
BLHI4- | BLHI2L | 2026 | Removed | 0.018 | 1.576 | -0.09 | 1200
BLHI4- | BLHI2M | 2026 | Removed | 0.018 | 1.576 | -0.09 | 1200

## B-3-2b
Table B.3.2b - SPT Transformer Changes 2018/19 to 2026/27 | [7 empty] | Back To Menu
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
KYPE1- | KYPE3- | 2018 | Addition | 0.1924 | 14.1654 | 0 | 120
MIDM1- | MIDM3- | 2018 | Addition | 0.4722 | 13.325 | 0 | 60
TONG1- | TONG3- | 2018 | Addition | 0.3119 | 21.8311 | 0 | 60
TONG1- | TONG3- | 2018 | Addition | 0.3119 | 21.8311 | 0 | 60
CURR2- | CURR1A | 2018 | Addition | 0.1205 | 8.4741 | -0.084 | 240
GALA1- | GALA3- | 2018 | Change | 0.3635 | 25.4418 | 0 | 90
GALA1- | GALA3- | 2018 | Change | 0.3635 | 25.4418 | 0 | 90
SHRU2R | SHRU3- | 2018 | Change | 0.2917 | 24.5816 | -0.0132 | 120
COAL4- | COAL1- | 2019 | Addition | 0.0733 | 6.6663 | -0.1905 | 360
KILS4T | KILS2- | 2019 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
MARG1- | MARG3-(1) | 2020 | Addition | 0.3635 | 25.4418 | 0 | 90
NEIL1- | NEIL3A | 2020 | Addition | 0.3119 | 21.8311 | 0 | 60
CONO1- | DOWE3G | 2020 | Addition | 0.3119 | 21.8311 | 0 | 60
FALL4- | FALL3C | 2021 | Addition | 0.2564 | 16.6647 | 0 | 120
NECU2- | NECU1C | 2021 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1C | 2021 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
LETH1- | LETH3- | 2021 | Addition | 0.3488 | 24.4142 | 0 | 120
KYPE1- | HARG3- | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
GAWH1Q | CUMH3- | 2021 | Addition | 0.3488 | 24.4142 | 0 | 120
ENHI1- | ENHI3- | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
DUNB1R | DUNB3B | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
DUNB1Q | DUNB3B | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
DALQ1- | DALQ3- | 2021 | Addition | 0.3119 | 21.8311 | 0 | 60
CRYR4- | NNGA2- | 2021 | Addition | 0.1071 | 5.8919 | -0.0108 | 280
SOKY1- | SOKY3- | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
CRYR4- | NNGB2- | 2021 | Addition | 0.1071 | 5.8919 | -0.0108 | 280
SOKY1- | SOKY3- | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
NNGA2G | NNGA3- | 2021 | Addition | 0.1777 | 7.998 | -0.1152 | 250
NNGB2G | NNGB3- | 2021 | Addition | 0.1777 | 7.998 | -0.1152 | 250
HOPR1- | HOPR3- | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
WIYH4Q | WIYH2- | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
STNO1- | STNO3- | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
NLEI1- | NLEI3B | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
NLEI1- | NLEI3A | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
NETS1- | NETS3- | 2023 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
NEIL4R | NEIL2- | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
NECU2- | NECU1B | 2023 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
MAHI2- | MAHI1B | 2023 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
KENN1- | KENN3- | 2023 | Addition | 0.3488 | 24.4142 | 0 | 120
GLLU1R | GLLU3B | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
GLLU1Q | GLLU3B | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
ELVA2R | ELVA1- | 2023 | Addition | 0.0984 | 5.8325 | -0.2121 | 360
ELVA1- | HABU3- | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
BEQU1- | BEQU3- | 2023 | Addition | 0.3635 | 25.4418 | 0 | 90
LORG1- | LORG3- | 2023 | Addition | 0.3119 | 21.8311 | 0 | 60
MAYB1- | MAYB3- | 2023 | Change | 0.3119 | 21.8311 | 0 | 60
MAYB1- | MAYB3- | 2023 | Change | 0.3119 | 21.8311 | 0 | 60
COYL2- | COYL1- | 2023 | Change | 0.1476 | 8.7488 | -0.1299 | 240
COYL2- | COYL1- | 2023 | Change | 0.1476 | 8.7488 | -0.1299 | 240
COYL1- | COYL3- | 2023 | Change | 0.3635 | 25.4418 | 0 | 90
COYL1- | COYL3- | 2023 | Change | 0.3635 | 25.4418 | 0 | 90
TONG1Q | TONG1R | 2023 | Removed | 0.0125 | 2.5 | 0 | 90
TONG1- | TONG1R | 2023 | Removed | 0.0267 | 1.3331 | 0 | 90

## B-3-2c
Table B.3.2c - NGET Transformer Changes 2018/19 to 2026/27 | [7 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
FERR41 | FERR23 | 2018 | Addition | 0.0117 | 1.591 | -4.4806 | 1000
HIBU41 | HIBU11 | 2018 | Addition | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | HIBU11 | 2018 | Addition | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | HIBU11 | 2018 | Addition | 0.1264 | 8.4534 | -0.357 | 240
SJOW41 | LODR62 | 2018 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
WIMB41 | WIMB21 | 2018 | Addition | 0.014 | 2.6567 | -0.1528 | 950
IVER21 | IVER61 | 2018 | Change | 0.2856 | 11.1999 | -2.5672 | 120
IVER22 | IVER61 | 2018 | Change | 0.2856 | 11.1999 | -2.5672 | 180
ELST21 | ELST13 | 2018 | Removed | 0.3567 | 11.136 | -0.7303 | 120
ELST22 | ELST14 | 2018 | Removed | 0.3567 | 11.136 | -0.7303 | 120
SJOW21 | LODR62 | 2018 | Removed | 0.3062 | 11.0235 | -0.4552 | 180
IVER42 | IVER21 | 2019 | Addition | 0.0152 | 1.6463 | -0.1118 | 775
RICH41 | RICH4* | 2019 | Addition | 0 | 0.45 | 0 | 1000
TILB21 | TILB11 | 2019 | Addition | 0.1307 | 7.9515 | -0.1098 | 120
WIMB41 | WIMB11 | 2019 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2019 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
FERR41 | FERR23 | 2019 | Removed | 0.0117 | 1.591 | -4.4806 | 1000
IVER42 | IVER21 | 2019 | Removed | 0.0326 | 2.3798 | -3.9003 | 500
TILB21 | TILB11 | 2019 | Removed | 0.3792 | 12.0524 | -0.3982 | 120
WIMB21 | WIMB11 | 2019 | Removed | 0.1923 | 8.081 | -1.4418 | 180
WIMB21 | WIMB12 | 2019 | Removed | 0.179 | 8.3648 | -4.7616 | 180
LISD2* | LISD21 | 2020 | Addition | 0.002 | 0.9802 | 0 | 760
WIMB41 | WIMB11 | 2020 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2020 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB21 | WIMB11 | 2020 | Removed | 0.1845 | 7.8956 | -0.1938 | 240
WIMB21 | WIMB12 | 2020 | Removed | 0.167 | 7.9774 | -0.2092 | 240
BLYT41 | BLYT21 | 2021 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
BLYT41 | BLYT21 | 2021 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
WIMB41 | WIMB11 | 2021 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2021 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
BLYT41 | BLYT21 | 2021 | Removed | 0.0152 | 1.6463 | -0.1118 | 1100
BLYT41 | BLYT21 | 2021 | Removed | 0.0152 | 1.6463 | -0.1118 | 1100
WIMB21 | WIMB11 | 2021 | Removed | 0.167 | 7.9774 | -0.2092 | 240
WIMB21 | WIMB12 | 2021 | Removed | 0.1845 | 7.8956 | -0.1938 | 240
BICF41 | BICF11 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
BICF41 | BICF11 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
CANW41 | CANW11 | 2023 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW41 | CANW11 | 2023 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW41 | CANW11 | 2023 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW41 | CANW11 | 2023 | Addition | 0.1139 | 8.1036 | -2.059 | 240
CANW41 | CANW11 | 2023 | Addition | 0.1139 | 8.1036 | -2.059 | 240
KIBY41 | KIBY22 | 2023 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
KIBY41 | KIBY22 | 2023 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
KIBY42 | KIBY21 | 2023 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
KIBY42 | KIBY21 | 2023 | Addition | 0.0152 | 1.6463 | -0.1118 | 750
LOVE41 | LOVE4* | 2023 | Addition | 0 | 0.1846 | 0 | 1300
WASF41 | WASF11 | 2023 | Addition | 0.1264 | 8.4534 | -0.357 | 180
WASF42 | WASF12 | 2023 | Addition | 0.1264 | 8.4534 | -0.357 | 180
BICF41 | BICF11 | 2023 | Removed | 0.1307 | 7.9515 | -0.1098 | 240
BICF42 | BICF11 | 2023 | Removed | 0.1307 | 7.9515 | -0.1098 | 240
PEWO41 | PEWO21 | 2023 | Removed | 0.0178 | 1.5995 | -1.2431 | 750
PEWO41 | PEWO22 | 2023 | Removed | 0.0175 | 1.5879 | -4.0069 | 1000
WASF21 | WASF11 | 2023 | Removed | 0.197 | 7.9698 | -0.2553 | 180
WASF22 | WASF12 | 2023 | Removed | 0.197 | 7.9698 | -0.2553 | 180
BRIW41 | BRWA11 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
BRIW41 | BRWA11 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
FOUX41 | FOUX11 | 2026 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HAWP41 | HAWP21 | 2026 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
SAFO41 | SAFO11 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 200
SAFO41 | SAFO12 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
WYMO4A | WYMO41 | 2026 | Addition | 0.001 | 0.35 | 0 | 1410
WYMO4B | WYMO41 | 2026 | Addition | 0.001 | 0.35 | 0 | 1410
BRWA2A | BRWA11 | 2026 | Removed | 0.167 | 7.9774 | -0.2092 | 240
BRWA2B | BRWA11 | 2026 | Removed | 0.167 | 7.9774 | -0.2092 | 240
SEAB41 | SEAB11 | 2026 | Removed | 0.1307 | 7.9515 | -0.1098 | 240
WYLF41 | WYLF12 | 2026 | Removed | 0.1509 | 8.2849 | -0.3279 | 240

## B-3-2d
Table B.3.2d - Indicative Offshore Transmission Transformer Changes 2018/19 to 2026/27 | [10 empty] | Back To Menu
OFTO | Site | Node 1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage Ratio (kV)
- | Walney extension | MIDL41 | WALE11 | 2018 | Addition | 0.1295 | 4.2085 | -1.553 | 380 | 400/150
- | Walney extension | MIDL41 | WALE12 | 2018 | Addition | 0.1295 | 4.2085 | -1.553 | 380 | 400/150
- | Walney extension | WAEN11 | WAEN31 | 2018 | Addition | 0 | 6.6667 | 0 | 180 | 150/33
- | Walney extension | WAEN11 | WAEN31 | 2018 | Addition | 0 | 6.6667 | 0 | 180 | 150/33
- | Walney extension | WAEN12 | WAEN32 | 2018 | Addition | 0 | 6.6667 | 0 | 180 | 150/33
- | Walney extension | WAEN12 | WAEN32 | 2018 | Addition | 0 | 6.6667 | 0 | 180 | 150/33
- | Galloper | GAOF1A | GAOF31/GAOF32 | 2018 | Addition | 0 | 6.6667 | 0 | 180 | 132/33/33
- | Galloper | GAOF1B | GAOF31/GAOF32 | 2018 | Addition | 0 | 6.6667 | 0 | 180 | 132/33/33
- | Galloper | GAON11 | GAON51 | 2018 | Addition | 0.0241 | 11 | 0 | 90 | 132/13.9
- | Galloper | GAON11 | GAON52 | 2018 | Addition | 0.0241 | 11 | 0 | 90 | 132/13.9
- | Dogger Bank | DOGG4* | DOGG2* | 2026 | Addition | 0 | 1.5 | 0 | 1000 | 400/320

## B-4-1a
Table B.4.1a - SHE Transmission Reactive Compensation Equipment, Winter 2017/18 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
BEAULY | BEAU3U | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU3V | 2 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU1K | 1 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1J | 2 | 45 |  | Mechanically Switched Capacitor | 132
CROSSAIG | CRSS3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3W | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Z | 4 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT1- | 1 |  | 200 | Shunt Reactor | 132
TEALING | TEAL3W | 1 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 3 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275
TEALING | TEAL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL1- | 1 |  | 100 | Shunt Reactor | 132

## B-4-1b
Table B.4.1b - SPT Reactive Compensation Equipment, Winter 2017/18 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
COALBURN | COAL3U | 1 |  | 60 | REACTOR | 33
COCKENZIE | COCK2- | 1 | 225 |  | MSCDN | 275
CRYSTAL RIG | CRYR3U | 1 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 1 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 2 |  | 60 | REACTOR | 33
ECCLES | ECCL3V | 1 |  | 60 | REACTOR | 33
ELVANFOOT | ELVA4- | 1 | 225 |  | MSCDN | 400
ELVANFOOT | ELVA3V | 1 |  | 60 | REACTOR | 33
GIFFNOCK | GIFF3- | 1 |  | 60 | REACTOR | 33
Hunterston Converter Station | HUCS4- | 1 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 2 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 3 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 4 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 5 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 6 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 7 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 8 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 1 |  | 200 | REACTOR | 400
Hunterston Converter Station | HUCS4- | 1 | 250 | 382 | STATCOM | 400
HUNTERSTON NORTH | HUNN3W | 1 |  | 60 | REACTOR | 33
HUNTERSTON NORTH | HUNN3X | 1 |  | 60 | REACTOR | 33
KILLGALLIOCH WIND FARM | KILG2- | 1 |  | 60 | REACTOR | 275
KILMARNOCK SOUTH | KILS3U | 1 |  | 60 | REACTOR | 33
LONGANNET | LOAN2- | 1 | 225 |  | MSCDN | 275
LONGANNET | LOAN2- | 2 | 225 |  | MSCDN | 275
MARK'S HILL | MAHI3U | 1 |  | 60 | REACTOR | 33
MOFFAT | MOFF4- | 1 | 225 |  | MSCDN | 400
MOFFAT | MOFF3U | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3U | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3V | 1 |  | 60 | REACTOR | 33
SHRUBHILL | SHRU3- | 1 |  | 60 | REACTOR | 33
SHRUBHILL | SHRU3- | 2 |  | 60 | REACTOR | 33
TORNESS | TORN4- | 1 |  | 150 | REACTOR | 400
TORNESS | TORN4- | 2 |  | 150 | REACTOR | 400
WEST GEORGE STREET | WGEO3- | 1 |  | 60 | REACTOR | 33
WEST GEORGE STREET | WGEO3- | 2 |  | 60 | REACTOR | 33
WINDYHILL | WIYH3W | 3 |  | 60 | REACTOR | 33
WINDYHILL | WIYH2- | 1 | 150 |  | MSCDN | 275
WISHAW | WISH3W | 1 |  | 60 | REACTOR | 33

## B-4-1c
Table B.4.1c - NGET Reactive Compensation Equipment, Winter 2017/18 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
Aberthaw | ABTH12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Aberthaw | ABTH12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Abham | ABHA12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Abham | ABHA11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Alverdiscott | ALVE10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Barking | BARK2 | 2B WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Barking | BARK2 | 2B WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Barking | BARK2 | 4B WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Barking | BARK2 | 4B WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Beddington | BEDD21 | 3B | 150 |  | Mechanically Switched Capacitor | 275
Beddington | BEDD22 | 4B | 150 |  | Mechanically Switched Capacitor | 275
Beddington | BEDD11 | 1B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD11 | 2B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD11 | 3B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD11 | 4B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD21 | 5B |  | 100 | Reactor | 275
Beddington | BEDD22 | 6A |  | 100 | Reactor | 275
Berkswell | BESW20 | 4 | 150 |  | Mechanically Switched Capacitor | 275
Berkswell | BESW10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Berkswell | BESW10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Berkswell | BESW10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Birkenhead | BIRK10 | 4 WDG A |  | 60 | Reactor | Tertiary Connected
Birkenhead | BIRK10 | 4 WDG B |  | 60 | Reactor | Tertiary Connected
Bishops Wood | BISW10 | A | 60 |  | Mechanically Switched Capacitor | 132
Bishops Wood | BISW10 | B | 60 |  | Mechanically Switched Capacitor | 132
Bishops Wood | BISW10 | C | 60 |  | Mechanically Switched Capacitor | 132
Blyth | BLYT21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Blyth | BLYT22 | 2 | 150 |  | Mechanically Switched Capacitor | 275
Bolney | BOLN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | BOLN13 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN14 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN40 | 1 |  | 55 | Reactor | Tertiary Connected
Bolney | BOLN40 | 2 |  | 55 | Reactor | Tertiary Connected
Bradford West | BRAW12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Bradford West | BRAW2 | 3 |  | 60 | Reactor | Tertiary Connected
Bradford West | BRAW2 | 4A |  | 30 | Reactor | Tertiary Connected
Bradford West | BRAW2 | 4B |  | 30 | Reactor | Tertiary Connected
Bramford | BRFO10 | A | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO10 | B | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO10 | C | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO40 | 1 |  | 200 | Reactor | 400
Bredbury | BRED2 | 1 WDG 1 |  | 30 | Reactor | Tertiary Connected
Bredbury | BRED2 | 1 WDG 2 |  | 30 | Reactor | Tertiary Connected
Bredbury | BRED2 | 3 WDG 1 |  | 30 | Reactor | Tertiary Connected
Bredbury | BRED2 | 3 WDG 2 |  | 30 | Reactor | Tertiary Connected
Bridgewater | BRWA10 | 1A | 45 |  | Mechanically Switched Capacitor | 132
Bridgewater | BRWA10 | 1B | 45 |  | Mechanically Switched Capacitor | 132
Bridgewater | BRWA2B |  | 60 |  | SVC | Tertiary Connected
Bushbury | BUSH20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Bushbury | BUSH10 | A | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH10 | B | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH10 | C | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH2 | 3 |  | 60 | Reactor | Tertiary Connected
Bustleholm | BUST2 | 4 | 20 |  | Mechanically Switched Capacitor | Tertiary Connected
Bustleholm | BUST2 | 4 |  | 60 | Reactor | Tertiary Connected
Bustleholm | BUST2 | 1A |  | 30 | Reactor | Tertiary Connected
Bustleholm | BUST2 | 1B |  | 30 | Reactor | Tertiary Connected
Canterbury | CANT40 | 1 |  | 200 | Reactor | 400
Capenhurst | CAPE21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Cellarhead | CELL11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL40 | 7 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | CELL40 | 8 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | CELL11 | 2A | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2B | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2 WDG A |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL11 | 2 WDG B |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL11 | 3 WDG A |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL11 | 3 WDG B |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL40 | 5 | 150 | -75 | SVC | 400
Cellarhead | CELL40 | 6 | 150 | -75 | SVC | 400
Chesterfield | CHTE11 | 1 |  | 60 | Reactor | Tertiary Connected
Chickerell | CHIC42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Chickerell | CHIC10 | 1 |  | 60 | Reactor | Tertiary Connected
Cilfynydd | CILF4 | 1 |  | 60 | Reactor | Tertiary Connected
Cilfynydd | CILF4 | 2 |  | 60 | Reactor | Tertiary Connected
Cilfynydd | CILF40 | 4 |  | 200 | Reactor | 400
Cilfynydd | CILF40 | 6 |  | 200 | Reactor | 400
City Road | CITR12 | 1 | 55 |  | Mechanically Switched Capacitor | Tertiary Connected
City Road | CITR11 | 2 | 55 |  | Mechanically Switched Capacitor | Tertiary Connected
City Road | CITR41 | 1 |  | 200 | Reactor | 400
Connah's Quay | CONQ11 | 1 WDG 1 |  | 30 | Reactor | Tertiary Connected
Connah's Quay | CONQ11 | 1 WDG 2 |  | 30 | Reactor | Tertiary Connected
Coventry | COVE10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE10 | 1 |  | 60 | Reactor | Tertiary Connected
Coventry | COVE20 |  | 60 |  | SVC | Tertiary Connected
Cowley | COWL10 | A | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL10 | B | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL10 | C | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL40 | 2 |  | 200 | Reactor | 400
Cowley | COWL40 | 3 |  | 200 | Reactor | 400
Daines | DAIN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Didcot | DIDC41 | 1 |  | 2640 | Series Reactor (bypassed) | 400
Drakelow | DRAK40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Drakelow | DRAK40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Drakelow | DRAK40 | 4 |  | 200 | Reactor | 400
Drakelow | DRAK40 | 6 |  | 200 | Reactor | 400
Drax | DRAX12 | 1 |  | 60 | Reactor | Tertiary Connected
Drax | DRAX11 | 2 |  | 60 | Reactor | Tertiary Connected
Drax | DRAX41 | 1 |  | 1320 | Series Reactor (bypassed) | 400
East Claydon | ECLA40 | 5 | 225 |  | Mechanically Switched Capacitor | 400
East Claydon | ECLA40 | 7 | 225 |  | Mechanically Switched Capacitor | 400
East Claydon | ECLA10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
East Claydon | ECLA40 | 1 WDG A |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 1 WDG B |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 2 WDG A |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 2 WDG B |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 6 | 150 | -75 | SVC | 400
Elland | ELLA2 | 2 |  | 60 | Reactor | Tertiary Connected
Elstree | ELST40 | 1 |  | 200 | Reactor | 400
Elstree | ELST21 |  | 60 |  | SVC | Tertiary Connected
Elstree | ELST22 |  | 60 |  | SVC | Tertiary Connected
Elstree | ELST4A | 1 |  | 2000 | Series Reactor (bypassed) | 400
Enderby | ENDE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Enderby | ENDE40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Exeter | EXET10 | 1 | 56 |  | Mechanically Switched Capacitor | 132
Exeter | EXET40 | 1/2 | 51 |  | Mechanically Switched Capacitor | Tertiary Connected
Exeter | EXET40 | 3 | 150 | -75 | SVC | 400
Exeter | EXET41 | 5 | 150 | -75 | SVC | 400
Feckenham | FECK40 | 4 WDG A |  | 30 | Reactor | Tertiary Connected
Feckenham | FECK40 | 4 WDG B |  | 30 | Reactor | Tertiary Connected
Feckenham | FECK20 | 6 | 150 | -75 | SVC | 275
Fiddlers Ferry | FIDF21 | 1 |  | 750 | Series Reactor (bypassed) | 275
Fiddlers Ferry | FIDF22 | 2 |  | 750 | Series Reactor (bypassed) | 275
Fleet | FLEE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Fleet | FLEE11 | 2A | 52 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2B | 52 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2C | 52 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 3A WDG 1 |  | 30 | Reactor | Tertiary Connected
Fleet | FLEE12 | 3A WDG 2 |  | 30 | Reactor | Tertiary Connected
Fleet | FLEE11 | 4A WDG 1 |  | 30 | Reactor | Tertiary Connected
Fleet | FLEE12 | 4A WDG 2 |  | 30 | Reactor | Tertiary Connected
Flintshire Bridge | FLIB40 | 1 |  | 235 | Reactor | 400
Flintshire Bridge | FLIB40 | 2 |  | 235 | Reactor | 400
Flintshire Bridge | FLIB40 | 3 |  | 235 | Reactor | 400
Grain | GRAI4 | 1 |  | 200 | Reactor | 400
Grain | GRAI41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Grendon | GREN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN40 | 4 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN12 | 1A | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN12 | 1B | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN12 | 1C | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN40 | 1 |  | 60 | Reactor | Tertiary Connected
Greystones | GRSB20 | 3 |  | 100 | Reactor | 275
Greystones | GRSA20 | 1 |  | 100 | Reactor | 275
Hams Hall | HAMH40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Hams Hall | HAMH40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 1 |  | 200 | Reactor | 400
Hams Hall | HAMH40 |  | 60 |  | SVC | Tertiary Connected
Harker | HARK40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK40 | 3A | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK40 | 3B | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK21 | 7 | 150 | -75 | SVC | 275
Harker | HARK22 | 8 | 150 | -75 | SVC | 275
Hurst | HURS20 | 2B | 150 |  | Mechanically Switched Capacitor | 275
Hurst | HURS2 | 2 |  | 60 | Reactor | Tertiary Connected
Hurst | HURS2 | 3 |  | 60 | Reactor | Tertiary Connected
Hurst | HURS20 | 4 |  | 100 | Reactor | 275
Hurst | HURS20 | 7 |  | 100 | Reactor | 275
Hurst | HURS20 | 1 |  | 100 | Reactor | 275
Hurst | HURS20 | 2A |  | 100 | Reactor | 275
Hutton | HUTT40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Hutton | HUTT41 | 1 |  | 2470 | Series Reactor (bypassed) | 400 (in parallel with series capacitor)
Hutton | HUTT41 | 2 |  | 2470 | Series Reactor (bypassed) | 400 (in parallel with series capacitor)
Indian Queens | INDQ40 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Indian Queens | INDQ10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ40 | 2 |  | 200 | Reactor | 400
Indian Queens | INDQ40 | 1 |  | 60 | Reactor | Tertiary Connected
Iron Acton | IROA1 | 6 | 45 |  | Mechanically Switched Capacitor | 132
Iron Acton | IROA20 |  | 60 |  | SVC | Tertiary Connected
Iron Acton | IROA20 |  | 60 |  | SVC | Tertiary Connected
Ironbridge | IRON40 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Ironbridge | IRON12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Ironbridge | IRON11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Iver | IVER2 | 1A |  | 60 | Reactor | Tertiary Connected
Iver | IVER2 | 3A |  | 60 | Reactor | Tertiary Connected
Iver | IVER4B | 5A |  | 55 | Reactor | Tertiary Connected
Iver | IVER4A | 6B |  | 55 | Reactor | Tertiary Connected
Jordanthorpe | JORD30 | 1 |  | 60 | Reactor | 33
Kearsley | KEAR11 | A | 52 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | B | 52 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | C | 52 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | 1 |  | 60 | Reactor | Tertiary Connected
Killingholme | KILL41 | 1 |  | 2750 | Series Reactor (bypassed) | 400
Kingsnorth | KINO4 | 3 |  | 200 | Reactor | 400
Kingsnorth | KINO4 | 4 |  | 200 | Reactor | 400
Kingsnorth | KINO4 | 1 WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO4 | 1 WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO4 | 2 WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO4 | 2 WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Kirkby | KIBY11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 4 | 45 |  | Mechanically Switched Capacitor | 132
Kirkstall | KIRK20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Kirkstall | KIRK20 | 2 |  | 60 | Reactor | Tertiary Connected
Kirkstall | KIRK20 | 4 |  | 60 | Reactor | Tertiary Connected
Lackenby | LACK2 | A/B/C | 60 |  | Mechanically Switched Capacitor | Tertiary Connected
Lackenby | LACK2 | 1 | 100 |  | Reactor | 275
Laleham | LALE20 | 3 |  | 100 | Reactor | 275
Laleham | LALE20 | 1 |  | 100 | Reactor | 275
Laleham | LALE20 | 2 |  | 100 | Reactor | 275
Landulph | LAND10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Landulph | LAND40 | 1 |  | 200 | Reactor | 400
Landulph | LAND40 | 2 WDG A |  | 30 | Reactor | Tertiary Connected
Landulph | LAND40 | 2 WDG B |  | 30 | Reactor | Tertiary Connected
Landulph | LAND40 |  | 60 |  | SVC | Tertiary Connected
Legacy | LEGA40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Legacy | LEGA40 | 1 |  | 60 | Reactor | Tertiary Connected
Legacy | LEGA40 | 2 |  | 60 | Reactor | Tertiary Connected
Lister Drive | LISD20 | 1 |  | 100 | Reactor | 275
Lister Drive | LISD21 | 1 |  | 750 | Series Reactor | 275 (Birkenhead circuit)
Lovedean | LOVE40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Lovedean | LOVE40 | 3 |  | 60 | Reactor | Tertiary Connected
Lovedean | LOVE40 | 7 |  | 200 | Reactor | 400
Lovedean | LOVE40 | 1 |  | 200 | Reactor | 400
Lovedean | LOVE40 | 1 |  | 60 | Reactor | Tertiary Connected
Lovedean | LOVE40 | 4A | 150 | -75 | SVC | 400
Mannington | MANN10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 5 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 6 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN40 | 1 | 150 | -75 | SVC | 400
Mannington | MANN41 | 2 | 150 | -75 | SVC | 400
Melksham | MELK10 | A | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK10 | B | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK10 | C | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK40 | 5 |  | 60 | Reactor | Tertiary Connected
Melksham | MELK40 | 6 |  | 60 | Reactor | Tertiary Connected
Melksham | MELK40 | 1 |  | 200 | Reactor | 400
Mill Hill | MILH2 | 1 |  | 60 | Reactor | Tertiary Connected
Mill Hill | MILH2 | 2 |  | 60 | Reactor | Tertiary Connected
Monk Fryston | MONF22 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Nechells | NECH2 | 4 |  | 60 | Reactor | Tertiary Connected
Nechells | NECH2 | 1 |  | 60 | Reactor | Tertiary Connected
Newcross | NEWX20 | 5 |  | 100 | Reactor | 275
Newcross | NEWX20 | 6 |  | 100 | Reactor | 275
Ninfield | NINF40 | 6 | 150 | -150 | SVC | 400
Norton | NORT12 | A/B/C | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW10 | A | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW10 | B | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW10 | C | 60 |  | Mechanically Switched Capacitor | 132
Nursling | NURS40 | 2 |  | 60 | Shunt Reactor | Tertiary Connected
Ocker Hill | OCKH20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Oldbury | OLDB10 | 2A/2B |  | 60 | Reactor | Tertiary Connected
Oldbury | OLDB20 |  | 60 |  | SVC | Tertiary Connected
Pelham | PELH11 | 1A/1B |  | 60 | Reactor | Tertiary Connected
Pelham | PELH12 | 2A/2B |  | 60 | Reactor | Tertiary Connected
Pelham | PELH40 | 5 | 150 | -75 | SVC | 400
Pelham | PELH40 | 6 | 150 | -75 | SVC | 400
Pembroke | PEMB4 | 1 |  | 60 | Reactor | Tertiary Connected
Pembroke | PEMB4 | 2 |  | 60 | Reactor | Tertiary Connected
Penn | PENN20 |  | 60 |  | SVC | Tertiary Connected
Pentir | PENT40 | 2 |  | 200 | Reactor | 400
Pentir | PENT40 | 5 |  | 200 | Reactor | 400
Pentir | PENT40 | 1 |  | 200 | Reactor | 400
Penwortham | PEWO4 | 6 |  | 60 | Reactor | Tertiary Connected
Pitsmoor | PITS32 | 1 |  | 60 | Reactor | 33
Pitsmoor | PITS32 | 2 |  | 60 | Reactor | 33
Pyle | PYLE20 |  | 60 |  | SVC | Tertiary Connected
Pyle | PYLE20 |  | 60 |  | SVC | Tertiary Connected
Rainhill | RAIN11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 4 | 45 |  | Mechanically Switched Capacitor | 132
Ratcliffe-On-Soar | RATS40 | 3 |  | 60 | Reactor | Tertiary Connected
Ratcliffe-On-Soar | RATS40 | 2 |  | 200 | Reactor | 400
Rayleigh | RAYL4 | 1 |  | 60 | Reactor | Tertiary Connected
Rochdale | ROCH10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Rochdale | ROCH10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Rochdale | ROCH10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Sellindge | SELL40 | 1 | 150 | -150 | SVC | 400
Sellindge | SELL40 | 2 | 150 | -150 | SVC | 400
Sellindge | SELL41 | 1 |  | 1860 | Series Reactor (bypassed) | 400
Skelton Grange | SKLG10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG10 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG20 | 6 | 150 |  | Mechanically Switched Capacitor | 275
Skelton Grange | SKLG20 | 3 |  | 100 | Reactor | 275
Spennymoor | SPEN40 | 1 |  | 60 | Reactor | Tertiary Connected
St Johns Wood | SJOW11 | A | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW11 | B | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW11 | C | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW40 | 2 |  | 200 | Reactor | 400
St Johns Wood | SJOW40 | 4 |  | 200 | Reactor | 400
St Johns Wood | SJOW20 | 1 |  | 60 | Reactor | Tertiary Connected
St Johns Wood | SJOW40 | 1 |  | 200 | Reactor | 400
St Johns Wood | SJOW20 | 1 | 150 | -106 | SVC | 275
St Johns Wood | SJOW20 | 3 | 150 | -106 | SVC | 275
Staythorpe | STAY41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW2 | 2 | 100 |  | Reactor | 275
Sundon | SUND41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Sundon | SUND42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Sundon | SUND4 | 5 WDG 1 |  | 30 | Reactor | Tertiary Connected
Sundon | SUND4 | 5 WDG 2 |  | 30 | Reactor | Tertiary Connected
Sundon | SUND4 | 8 WDG 1 |  | 30 | Reactor | Tertiary Connected
Sundon | SUND4 | 8 WDG 2 |  | 30 | Reactor | Tertiary Connected
Swansea | SWAN12 | A | 60 |  | Mechanically Switched Capacitor | 132
Swansea | SWAN12 | B | 60 |  | Mechanically Switched Capacitor | 132
Swansea | SWAN12 | C | 60 |  | Mechanically Switched Capacitor | 132
Thorpe Marsh | THOM40 | 2 |  | 200 | Reactor | 400
Thorpe Marsh | THOM40 | 6 |  | 200 | Reactor | 400
Tottenham | TOTT2 | 3 |  | 100 | Reactor | 275
Tottenham | TOTT2 | 5 |  | 100 | Reactor | 275
Tottenham | TOTT2 | 1 |  | 100 | Reactor | 275
Tynemouth | TYNE20 | 1 |  | 60 | Reactor | Tertiary Connected
Uskmouth | USKM10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Walham | WALH40 | 1 | 57 |  | Mechanically Switched Capacitor | Tertiary Connected
Walham | WALH40 | 2 |  | 60 | Reactor | Tertiary Connected
Walham | WALH40 | 3 |  | 60 | Reactor | Tertiary Connected
Walham | WALH40 | 4 |  | 200 | Reactor | 400
Walpole | WALP11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP4 | 1 |  | 60 | Reactor | Tertiary Connected
Walpole | WALP4 | 2 |  | 60 | Reactor | Tertiary Connected
Warley | WARL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Warley | WARL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Warley | WARL10 | 3 | 45 |  | Mechanically Switched Capacitor | 132
West Boldon | WBOL60 | 1 | 50 |  | Mechanically Switched Capacitor | 66
West Burton | WBUR40 | 1 |  | 200 | Reactor | 400
West Burton | WBUR41 | 1 |  | 1500 | Series Reactor (bypassed) | 400
West Ham | WHAM40 | 4 | 225 |  | Mechanically Switched Capacitor | 400
West Ham | WHAM40 | 1 |  | 200 | Reactor | 400
West Melton | WMEL12 | 3A | 45 |  | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3B | 45 |  | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3C | 45 |  | Mechanically Switched Capacitor | 132
West Thurrock | WTHU41 | 1 |  | 2400 | Series Reactor (bypassed) | 400 (Littlebrook-Tilbury circuit)
West Thurrock | WTHU42 | 2 |  | 2400 | Series Reactor (bypassed) | 400 (Littlebrook-Tilbury circuit)
West Weybridge | WWEY2 | 1 |  | 100 | Reactor | 275
Whitegate | WHGA20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Whitegate | WHGA20 | 4A |  | 60 | Reactor | Tertiary Connected
Whitegate | WHGA20 | 4B |  | 60 | Reactor | Tertiary Connected
Willesden | WISD2 | 2B |  | 55 | Reactor | Tertiary Connected
Willesden | WISD2 | 3B WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Willesden | WISD2 | 3B WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Willington | WILE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Willington | WILE40 | 8 | 150 | -75 | SVC | 400
Wimbledon | WIMB20 | 2 |  | 100 | Reactor | 275
Wimbledon | WIMB20 | 4 |  | 100 | Reactor | 275
Wymondley | WYMO40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Wymondley | WYMO40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Wymondley | WYMO40 | 3 | 200 |  | Reactor | 400

## B-4-1d
Table B.4.1d - Offshore Reactive Compensation Equipment, 2017/18 | [8 empty] | Back To Menu
OFTO | Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Tapping
Blue Transmission London Array Limited | London Array Offshore Wind Farm | SGT1A tertiary | SVC PLUS 1A | 50 | 50 | SVC | 13.9
" | " | SGT2A tertiary | SVC PLUS 2A | 50 | 50 | SVC | 13.9
" | " | SGT1B tertiary | SVC PLUS 1B | 50 | 50 | SVC | 13.9
" | " | SGT2B tertiary | SVC PLUS 2B | 50 | 50 | SVC | 13.9
" | " | SGT1A tertiary | MSR 1A | - | 50 | Shunt Reactor | 13.9
" | " | SGT2A tertiary | MSR 2A | - | 50 | Shunt Reactor | 13.9
" | " | SGT1B tertiary | MSR 1B | - | 50 | Shunt Reactor | 13.9
" | " | SGT2B tertiary | MSR 2B | - | 50 | Shunt Reactor | 13.9
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SALL10 | 1 | - | 30 - 60 | Shunt Reactor | 132 | 18 taps from 30 to 60 MVAr
" | " | SALL10 | 2 | - | 30 - 60 | Shunt Reactor | 132 | 18 taps from 30 to 60 MVAr
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAO10 | RCT1 | - | 64 | Shunt Reactor | 132
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABO10 | RCT1 | - | 40-80 | Shunt Reactor | 132
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON51 | 1 | - | 40 | Shunt Reactor | 13.9
" | " | GGON52 | 2 | - | 40 | Shunt Reactor | 13.9
" | " | GGON53 | 3 | - | 40 | Shunt Reactor | 13.9
" | " | GGON51 | 1 | 47.3 | - | MSC | 13.9
" | " | GGON52 | 2 | 47.3 | - | MSC | 13.9
" | " | GGON53 | 3 | 47.3 | - | MSC | 13.9
" | " | GGON51 | 1 | 50 | 50 | SVC | 13.9
" | " | GGON52 | 2 | 50 | 50 | SVC | 13.9
" | " | GGON53 | 3 | 50 | 50 | SVC | 13.9
" | " | GAOF30 | 1 | - | 30 | Shunt Reactor | 33
" | " | GAOF30 | 2 | - | 30 | Shunt Reactor | 33
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | SGT1 tertiary | SVC-1 | 50 | 50 | SVC | 13.9
" | " | SGT2 tertiary | SVC-2 | 50 | 50 | SVC | 13.9
" | " | SGT1 tertiary | MSR1A | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT1 tertiary | MSR1B | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT2 tertiary | MSR2A | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT2 tertiary | MSR2B | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT1 tertiary | MSC1A | 30 | - | MSC | 13.9
" | " | SGT1 tertiary | MSC1B | 30 | - | MSC | 13.9
" | " | SGT2 tertiary | MSC2A | 30 | - | MSC | 13.9
" | " | SGT2 tertiary | MSC2B | 30 | - | MSC | 13.9
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW10 | 1 | - | 24 | Shunt Reactor | 132
" | " | BOSW30 | 1 | 5 | - | MSC | 33
" | " | BOSW30 | 2 | 5 | - | MSC | 33
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | - | - | - | - | - | -
TC Lincs OFTO Limited | Lincs Wind Farm | LINO10 | Reactor 1 | - | 40 | Shunt Reactor | 132
" | " | LINO10 | Reactor 2 | - | 40 | Shunt Reactor | 132
" | " | SGT1A/SGT1B tertiary | SVC Plus 1 | 50 | 50 | SVC | 13.9
" | " | SGT1A/SGT1B tertiary | MSR2 | - | 53.48 | Shunt Reactor | 13.9
" | " | SGT1A/SGT1B tertiary | MSC3 | 31.18 | - | MSC | 13.9
" | " | SGT1A/SGT1B tertiary | MSR4 | - | 53.48 | Shunt Reactor | 13.9
" | " | SGT1A/SGT1B tertiary | MSC5 | 31.18 | - | MSC | 13.9
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMO32 | Reactor 1 | - | 35 | Shunt Reactor | 33
" | " | ORMO32 | Reactor 2 | - | 35 | Shunt Reactor | 33
" | " | ORMO32 | Shunt Capacitor 1 | 15 | - | MSC | 33
" | " | ORMO32 | SVC 1 | 28 | 28 | SVC | 33
TC Robin Rigg OFTO Limited | Robin Rigg East & West Offshore Wind Farms | RORE11 | RREW10_Cap-1 | 18 |  | MSC | 132
" | " | RORE11 | RREW10_Reac-1 |  | 18 | Shunt Reactor | 132
" | " | RORW11 | RRWW10_Cap-1 | 18 |  | MSC | 132
" | " | RORW11 | RRWW10_Reac-1 |  | 18 | Shunt Reactor | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW10 | SVC 1 | 55 | 55 | SVC | 132
" | " | THAW10 | SVC 2 | 55 | 55 | SVC | 132
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | SGT1 tertiary | 13.9kV Reactor 1A | - | 30 | Shunt Reactor | 13.9
" | " | SGT2 tertiary | 13.9kV Reactor 2A | - | 30 | Shunt Reactor | 13.9
" | " | WDSO11 | Shunt Reactor 3 | - | 60 | Shunt Reactor | 155
" | " | WDSO12 | Shunt Reactor 4 | - | 60 | Shunt Reactor | 155
" | " | SGT1 tertiary | SVC1B | 50 | 50 | SVC | 13.9
" | " | SGT2 tertiary | SVC2B | 50 | 50 | SVC | 13.9
- | Humber Gateway Offshore Wind Farm | HUMO11 | SHR1 |  | 28.2 | Shunt Reactor | 132
- | " | SGT1 tertiary | SVC | 24 | 24 | SVC | 33
- | " | SGT1 tertiary | MSR1A |  | 28 | Shunt Reactor | 33
- | " | SGT1 tertiary | MSR1B |  | 28 | Shunt Reactor | 33
- | " | SGT1 tertiary | MSC1 | 25 |  | MSC | 33
- | " | HUMO12 | SHR2 |  | 28.2 | Shunt Reactor | 132
- | " | SGT2 tertiary | SVC | 24 | 24 | SVC | 33
- | " | SGT2 tertiary | MSR2A |  | 28 | Shunt Reactor | 33
- | " | SGT2 tertiary | MSR2B |  | 28 | Shunt Reactor | 33
- | " | SGT2 tertiary | MSC2 | 25 |  | MSC | 33
- | Westermost Rough Offshore Wind Farm | SGT1/SGT2 tertiary | Statcom1 | 25 | 25 | SVC | 33
- | " | SGT1/SGT2 tertiary | Statcom2 | 25 | 25 | SVC | 33
- | " | WERW11 | 1 |  | 50 | Shunt Reactor | 150
- | Dudgeon Offshore Wind Farm | DUDO10 | SHR1 |  | 70 | Shunt Reactor | 132
- | Dudgeon Offshore Wind Farm | DUDO10 | SHR2 |  | 70 | Shunt Reactor | 132
- | Dudgeon Offshore Wind Farm | DUDO31 | SVC1 | 118 | 118 | SVC | 33
- | Dudgeon Offshore Wind Farm | DUDO32 | SVC2 | 118 | 118 | SVC | 33
- | Burbo Bank Extension Offshore Wind Farm | BURB40 | C1 | 60 |  | MSC | 400
- | Burbo Bank Extension Offshore Wind Farm | BURB20 | R1 |  | 125 | Shunt Reactor | 220
- | Burbo Bank Extension Offshore Wind Farm | BURB40 | R2 |  | 67 | Shunt Reactor | 400
- | Burbo Bank Extension Offshore Wind Farm | BURB40 | SVS-9 | 15 | 15 | SVC | 13
- | Race Bank Offshore Wind Farm | RABO31 | STATCOM1 | -100 | -100 | SVC | 27
- | " | RABO32 | STATCOM1 | -100 | -100 | SVC | 27
- | " | RABO21 | SHR1 |  | 200 | Shunt Reactor | 220
- | " | RABO22 | SHR2 |  | 200 | Shunt Reactor | 220
- | " | RAOF2A | SHR1 |  | 90 | Shunt Reactor | 220
- | " | RAOF2B | SHR2 |  | 90 | Shunt Reactor | 220
- | Rampion Offshore Wind Farm | TWIN31 | SVC1 | 75 | 50 | Shunt Reactor | SGT1 33kV tertiary
- | " | TWIN32 | SVC2 | 75 | 50 | Shunt Reactor | SGT2 33kV tertiary
- | " | TWIN1A | SHR1 |  | 64 | Shunt Reactor | 150
- | " | TWIN1B | SHR2 |  | 64 | Shunt Reactor | 150

## B-4-2a
Table B.4.2a - SHE Transmission Reactive Compensation Equipment, 2018/19 to 2026/27 | [8 empty] | Back To Menu
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
MELGARVE | Addition | 2018 | MELG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
MELGARVE | Addition | 2018 | MELG3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
STRONELAIRG | Addition | 2018 | STRL1- | 1 |  | 60 | Shunt Reactor | 132
DOUNREAY | Addition | 2021 | DOUN3Y | 3 |  | 90 | Shunt Reactor - SGT tertiary | 33
ORKNEY | Addition | 2021 | BASK3Y | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
GILLS BAY | Addition | 2022 | GILB3J | 1 |  | 30 | Shunt Reactor | 33
ALYTH | Addition | 2024 | ALYT2 | 1 | 225 | 75 | SVC | 275

## B-4-2b
Table B.4.2b - SPT Reactive Compensation Equipment, 2018/19 to 2026/27 | [8 empty] | Back To Menu
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BONNYBRIDGE | Addition | 2018 | BONN3U | 1 |  | 60 | REACTOR | 33
BONNYBRIDGE | Addition | 2018 | BONN3V | 1 |  | 60 | REACTOR | 33
CURRIE | Addition | 2018 | CURR3W | 1 |  | 60 | REACTOR | 33
CURRIE | Addition | 2018 | CURR3U | 1 |  | 60 | REACTOR | 33
WISHAW | Addition | 2018 | WISH3V | 1 |  | 60 | REACTOR | 33
SHRUBHILL | Deletion | 2018 | SHRU3- | 2 |  | 60 | REACTOR | 33
SMEATON | Addition | 2018 | SMEA3U | 1 |  | 60 | REACTOR | 33
SMEATON | Addition | 2018 | SMEA3V | 1 |  | 60 | REACTOR | 33
WEST GEORGE STREET | Deletion | 2018 | WEGO3- | 1 |  | 60 | REACTOR | 33
WEST GEORGE STREET | Deletion | 2018 | WEGO3- | 2 |  | 60 | REACTOR | 33
NNG OFFSHORE WIND FARM | Addition | 2021 | NNGA2- | 1 |  | 130 | REACTOR | 220
NNG OFFSHORE WIND FARM | Addition | 2021 | NNGB2- | 1 |  | 130 | REACTOR | 220

## B-4-2c
Table B.4.2c - NGET Reactive Compensation Equipment, 2018/19 to 2026/27 | [8 empty] | Back To Menu
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Bolney | Addition | 2018 | BOLN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | Addition | 2018 | BOLN40 | 6 | 75 | 225 | SVC | 400
Ninfield | Addition | 2018 | NINF40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Ninfield | Addition | 2018 | NINF40 | 7 | 75 | 75 | SVC | 400
Richborough | Addition | 2018 | RICH40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Richborough | Addition | 2018 | RICH40 | 1 | 75 | 225 | SVC | 400
Sizewell | Addition | 2018 | SIZE41 | 1 | 66.6667 |  | Series Reactor (bypassed) | 400
Sizewell | Addition | 2018 | SIZE41 | 2 | 66.6667 |  | Series Reactor (bypassed) | 400
Wimbledon | Addition | 2018 | WIMB40 | 2 |  | 225 | Shunt Reactor | 400
Wimbledon | Addition | 2018 | WIMB40 | 4 |  | 225 | Shunt Reactor | 400
Chilling | Addition | 2019 | CHIL40 | 1 |  | 100 | Shunt Reactor | 400
Chickerell | Addition | 2020 | CHIC40 | 1 | 225 | 225 | SVC | 400
Fleet | Addition | 2020 | FLEE41 | 1 | 2470 |  | Series Reactor (bypassed) | 400 (Lovedean 1 circuit)
Fleet | Addition | 2020 | FLEE41 | 2 | 2470 |  | Series Reactor (bypassed) | 400 (Lovedean 2 circuit)
Lovedean | Addition | 2020 | LOVE40 | 4 | 225 | 225 | SVC | 400
Lovedean | Addition | 2020 | LOVE41 | 1 | 2470 |  | Series Reactor (bypassed) | 400 (Fleet 1 circuit)
Lovedean | Addition | 2020 | LOVE41 | 2 | 2470 |  | Series Reactor (bypassed) | 400 (Fleet 2 circuit)
Lister Drive | Removed | 2020 | LISD21 | 1 | 750 |  | Series Reactor | 275 (Birkenhead circuit)
Killingholme | Addition | 2021 | KILL41 | 1 | 2750 |  | Series Reactor (bypassed) | 400
Rayleigh | Addition | 2021 | RAYL41 | 1 | 4000 |  | Series Reactor (bypassed) | 400 (Tilbury circuit)
Rayleigh | Addition | 2021 | RAYL41 | 2 | 4000 |  | Series Reactor (bypassed) | 400 (Coryton circuit)
Wimbledon | Removal | 2021 | WIMB20 | 2 |  | 100 | Shunt Reactor | 275
Wimbledon | Removal | 2021 | WIMB20 | 4 |  | 100 | Shunt Reactor | 275
Sizewell | Removed | 2021 | SIZE41 | 1 | 66.6667 |  | Series Reactor (bypassed) | 400
Sizewell | Removed | 2021 | SIZE41 | 2 | 66.6667 |  | Series Reactor (bypassed) | 400
Carrington | Addition | 2023 | CARR41 | 1 | 2750 |  | Series Reactor (bypassed) | 400
Burwell | Addition | 2026 | BURW40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Burwell | Addition | 2026 | BURW40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Burwell | Addition | 2026 | BURW40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | Addition | 2026 | CELL40 | 9 | 229 |  | Mechanically Switched Capacitor | 400
Drakelow | Addition | 2026 | DRAK40 | 2 | 263 | 263 | SVC | 400
Feckenham | Addition | 2026 | FECK40 | 1 | 229 |  | Mechanically Switched Capacitor | 400
Hinkley Point | Addition | 2026 | HIKP41 | 1 | 2000 |  | Series Reactor (bypassed) | 400
Ironbridge | Addition | 2026 | IRON40 | 9 | 229 |  | Mechanically Switched Capacitor | 400
Legacy | Addition | 2026 | LEGA40 | 2 | 229 |  | Mechanically Switched Capacitor | 400
Pentir | Addition | 2026 | PENT41 | 1 | 1860 |  | Series Reactor (bypassed) | 400
Trawsfynydd | Addition | 2026 | TRAW40 | 9 | 229 |  | Mechanically Switched Capacitor | 400
Bridgwater | Removal | 2026 | BRWA2 |  | 60 | 0 | SVC | Tertiary Connected

## B-4-2d
Table B.4.2d - Indicative Offshore Reactive Compensation Equipment Changes, 2018/19 to 2026/27 | [9 empty] | Back To Menu
OFTO | Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
- | Galloper Onshore | Addition | 2018 |  |  | 50 | 50 | SVC | 13.9
- | Galloper Onshore | Addition | 2018 |  |  | 50 | 50 | SVC | 13.9
- | Galloper Onshore | Addition | 2018 |  |  | 55.1 |  | Mechanically Switched Capacitor | 13.9
- | Galloper Onshore | Addition | 2018 |  |  | 55.1 |  | Mechanically Switched Capacitor | 13.9
- | Galloper Onshore | Addition | 2018 |  |  |  | 85 | Shunt Reactor | 132
- | Galloper Onshore | Addition | 2018 |  |  |  | 85 | Shunt Reactor | 132