## TWR Report 17-04-2026
Project Name | Project Number | Connected Scheme Name | Account Name | Connection Site | Scheme Name | Scheme Description | Mw Effective From
50MW BESS Connagill | PRO-004938 | CS-12181 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12182 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12183 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12184 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12185 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12186 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12187 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-238 |  | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12188 | Cerulisia Ltd | New Connagill 275/132kV Substation | SHET-RI-328 | New 275 kV circuit from Connagill 275/132kV substation | 2031-10-31
50MW BESS Connagill | PRO-004938 | CS-12189 | Cerulisia Ltd | New Connagill 275/132kV Substation | 50MW BESS Connagill Enabling Works | 1. Install 132kV bus bar disconnector (117). 2. Install a 275kV double busbar feeder bay complete with two disconnectors (H34 and H36) and a circuit breaker (H10) at the New Connagill 275/132kV substation. 3. Construct approximately a 1.7km of 275kV OHL from the New Connagill substation to the new 275/132kV substation (New TORI 328). This circuit will comprise of a Circuit breaker (H30) and 2 x disconnectors (H38 and H32) to a 275/132kV Transformer (SGT1) then a circuit breaker (110) and disconnector (113) to a 132kV bus bar | 2031-10-31
Aberarder Wind Farm | PRO-000368 | CS-05446 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2026-08-31
Aberarder Wind Farm | PRO-000368 | CS-05447 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | Aberarder item 2 | Modification of the protection and telecommunication equipment at Farigaig 132kV and Dunmaglass 132kV substations. | 2026-08-31
Aberarder Wind Farm | PRO-000368 | CS-05448 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | Aberarder item 1 | Construction of approximately 5km of 132kV overhead line between Dunmaglass – Farigaig 132kV overhead line, 10km south of Farigaig 275/132kV substation, and the wind farm substation. At the wind farm substation, the 132kV overhead line will terminate onto a new 132kV line disconnector located within the substation compound. | 2026-08-31
Aberarder Wind Farm | PRO-000368 | CS-05449 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | SHET-RI-089 | Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT to facilitate the connection of generation in the area. | 2026-08-31
Aberarder Wind Farm | PRO-000368 | CS-06328 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | SHET-RI-129 | Farigaig SGT1 Upgrade - Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT, to facilitate the connection of generation in the area. | 2026-08-31
Aberthaw (Tertiary) | PRO-000376 | CS-05450 | Aberthaw Green Limited | Aberthaw 275kV Substation | 100649-201328 | Install earthing transformer on 13kV tertiary connection with standard impedance. Install 13kV cable connecting earthing transformer to DCB. Install 72.5kV, 40kA rated DCB to connection assets for Users connection. | 2029-10-31
Aberthaw Energy | PRO-001697 | CS-04589 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 101328-202648 | 1. Works to facilitate the use of Aberthaw 275kV substation’s spare bay for the User’s connection. | 2028-10-30
Aberthaw Energy | PRO-001697 | CS-04590 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-10-30
Aberthaw Energy | PRO-001697 | CS-04591 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2028-10-30
Aberthaw Energy | PRO-001697 | CS-04592 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2028-10-30
Aberthaw Energy | PRO-001697 | CS-04771 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2028-10-30
Aberthaw PV & BESS Generation | PRO-001815 | CS-07150 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 101645-203282 | Extension of the future consolidated South Wales Operational Tripping Scheme (functioning as a commercial operational tripping scheme for this User) | 2029-06-30
Aberthaw PV & BESS Generation | PRO-001815 | CS-07151 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2029-06-30
Aberthaw PV & BESS Generation | PRO-001815 | CS-07152 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2029-06-30
Aberthaw PV & BESS Generation | PRO-001815 | CS-07153 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2029-06-30
Aberthaw PV & BESS Generation | PRO-001815 | CS-07154 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2029-06-30
Achanalt Battery Storage | PRO-004221 | CS-12411 | ADTEK LIMITED | Grudie Bridge GSP | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 2027-10-31
Achanalt Battery Storage | PRO-004221 | CS-12412 | ADTEK LIMITED | Grudie Bridge GSP | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 2027-10-31
Achany Extension Wind Farm | PRO-001555 | CS-06644 | SSE Generation Limited | ACHANY EXTENSION WIND FARM 132/33KV Substation | Achany Extension Enabling Works | The sole use enabling works will include the installation of a 132 kV line disconnector (113) and 132 kV circuit breaker (110) on the 132 kV side of the 132/33 kV transformer at the wind farm site. The line disconnector (113) will connect to the incoming 1.5 km of 132kV underground cable (UGC), followed by 16km of Trident Wood Pole 132 kV overhead line. The 132 kV circuit will be connected to Shin 132 kV substation via a new fully equipped 132 kV double busbar feeder bay, comprising 132 kV line disconnector (303), 132 kV feeder circuit breaker (305) and 132 kV double busbar selection disconnectors (304/306) and associated protection equipment. | 2028-03-30
Achany Extension Wind Farm | PRO-001555 | CS-06645 | SSE Generation Limited | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2028-03-30
Achany Extension Wind Farm | PRO-001555 | CS-06646 | SSE Generation Limited | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2028-03-30
Achany Extension Wind Farm | PRO-001555 | CS-09999 | SSE Generation Limited | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-123 | Shin – Loch Buidhe 132kV Reconductoring | 2028-03-30
Achany Extension Wind Farm | PRO-001555 | CS-10000 | SSE Generation Limited | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2028-03-30
Achany Extension Wind Farm | PRO-001555 | CS-10001 | SSE Generation Limited | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2028-03-30
Acheilidh Wind Farm | PRO-005042 | CS-12075 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | Acheilidh Wind Farm H1 Works | 1. Installation of a 132kV bay at the new 132kV Loch Buidhe Dalchork Collector Substation (to be delivered under SHET-RI-327) consisting of 132kV circuit breakers 107 and 205, 132kV double busbar selector disconnectors 104 and 106 and 132kV line disconnector 203. 2. Installation of all associated protection and control equipment to be housed in a control building. 3. Construction of a 3km 132kV circuit from Loch Buidhe Dalchork Collector Substation to Acheilidh wind farm will consist of 2km OHL and 1km UGC. 4. Installation of a 132kV feeder disconnector 503 at the User’s site. | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12076 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12077 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-138 New Deer 400kV Busbar Extension |  | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12078 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12079 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12080 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-200 (1) |  | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12081 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-230 Dalchork to Loch Buidhe 132kV second Double Circuit |  | 2033-10-31
Acheilidh Wind Farm | PRO-005042 | CS-12082 | ENERGYFARM UK ACHEILIDH LTD | Acheilidh Wind farm 132kV Substation | SHET-RI-327 | 11. Loch Buidhe Dalchork 132kV Collector Substation – Establish a new 132kV double busbar Collector Substation on the OHL between Dalchork 132kV Substation and Loch Buidhe 132kV Substation to accommodate the distribution generation and demand in the area. (SHET-RI-327) | 2033-10-31
Achrugan Wind Farm | PRO-002267 | CS-08253 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2030-07-31
Achrugan Wind Farm | PRO-002267 | CS-08254 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2030-07-31
Achrugan Wind Farm | PRO-002267 | CS-08255 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 2030-07-31
Achrugan Wind Farm | PRO-002267 | CS-08256 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-191 | Strathy Switching Collector Station 132kV - Install 12km approximately of new 275kV double circuit overhead line between Connagill 275/132kV substation and a new 132kV switching collector station at Strathy North Wind Farm substation. The OHL double circuit will be built on steel lattice towers. This reinforcement is dependent upon TORI-106b Connagill 2nd SGT, looking at installing a new 480MVA transformer at Connagill substation (SGT1). If the works of this TORI are progressed, TORI-168 need to be cancelled and the offers issued to the following wind farms need to be amended as follows: -Armadale and Strathy South wind farms to update the TCA, One-off works and sole use works. -Kirkton wind farm to update the TCA and sole use works as per the new network design and double check the protection system configuration if additional devices are needed.(SHET-RI-191) | 2030-07-31
Afan Wind Farm and BESS | PRO-004588 | CS-12553 | TRYDAN GWYRDD CYMRU (Welsh Government) Ltd | SOUTH WALES WEST CONNECTION NODE A 132KV SUBSTATION | 104052-207975 |  | 2036-12-06
Afon Ddaw | PRO-001775 | CS-07033 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 101604-203222 | Works to facilitate the use of Aberthaw 275kV substation’s spare bay for the User’s connection | 2029-10-31
Afon Ddaw | PRO-001775 | CS-07034 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2029-10-31
Afon Ddaw | PRO-001775 | CS-07035 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2029-10-31
Afon Ddaw | PRO-001775 | CS-07036 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2029-10-31
Afon Ddaw | PRO-001775 | CS-07037 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2029-10-31
Afon Ddaw | PRO-001775 | CS-12276 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 103645-207186 (LSBP) |  | 2029-10-31
Afon Ddaw | PRO-001775 | CS-12277 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 103645-207193 |  | 2029-10-31
Afon Ddaw | PRO-001775 | CS-12278 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 103645-207195 |  | 2029-10-31
AGS Calderside Battery Energy Storage System | PRO-002752 | CS-09236 | Advance Grid Solutions Limited | Calderside 275kV Substation | SPT-RI-3557 - Strathaven 275kV Substation Extension |  | 2029-10-31
AGS Calderside Battery Energy Storage System | PRO-002752 | CS-09237 | Advance Grid Solutions Limited | Calderside 275kV Substation | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2029-10-31
AGS Harestonhill BESS | PRO-003656 | CS-09772 | AGS Harestonhill Ltd | AGS Harestonhill BESS 400kV Substation | SPT-RI-3406 | 4. Blacklaw 400kV Collector Substation - To establish a new 400kV collector substation, fed from Wishaw 400kV substation via a single 400kV circuit. The collector substation is to be named Blacklaw 400kV collector substation. The project involves establishing a new 400kV bay at Wishaw 400kV GIS substation, installing approx. 300m of 400kV UGC to the Blacklaw 400kV collector site. | 2030-10-31
AGS Harestonhill BESS | PRO-003656 | CS-09773 | AGS Harestonhill Ltd | AGS Harestonhill BESS 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2030-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11142 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 Cable |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11143 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 OHL |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11144 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 SS |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11145 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 Cable |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11146 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 OHL |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11147 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 SS |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11148 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 Cable |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11149 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 OHL |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11150 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 SS |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11151 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 Cable | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11152 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 SS | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11153 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 OHL | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11154 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11155 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | East Kilbride B (1) 275/33kV Substation H1 Cable |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11156 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | East Kilbride B (1) 275/33kV Substation H1 OHL |  | 2033-10-31
AGS Nerston 2 BESS | PRO-004226 | CS-11157 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | East Kilbride B (1) 275/33kV Substation H1 SS |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11158 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 Cable |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11159 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 OHL |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11160 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 SS |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11161 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 Cable |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11162 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 OHL |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11163 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 SS |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11164 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 Cable |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11165 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 OHL |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11166 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 SS |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11167 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 Cable | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11168 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 SS | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11169 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 OHL | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11170 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11171 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | East Kilbride B (2) 275/33kV Substation H1 Cable |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11172 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | East Kilbride B (2) 275/33kV Substation H1 OHL |  | 2033-10-31
AGS Nerston 3 BESS | PRO-004227 | CS-11173 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | East Kilbride B (2) 275/33kV Substation H1 SS |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11128 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11129 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 Cable |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11130 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 OHL |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11131 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3923 SS |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11132 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 Cable |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11133 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 OHL |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11134 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3924 SS |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11135 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 Cable |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11136 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 OHL |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11137 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3490 SS |  | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11139 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 OHL | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11140 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 SS | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
AGS Nerston BESS | PRO-004216 | CS-11141 | Advance Grid Solutions Limited | East Kilbride B 275/33kV Substation | SPT-RI-3159 Cable | Clydesmill – Strathaven 400kV uprating - Establish a 400kV single circuit between Clydes Mill 400kV (proposed to established under SPT-RI-2083) and Strathaven 400kV. This will be achieved by reconductoring the existing 275kV No2 circuit (east most circuit on ZE route) between Clydes Mill and Strathaven to operate at 400kV. To maintain the second 275kV supply at East Kilbride 275kV the project will also include installation of a 275kV cable connection from Strathaven 275kV to the existing ZE/YZ tee junction near East Kilbride 275kV. The project will also reconductor the No.1 ZE route circuit such that it is rated for 400kV but remain operated at 275kV with a higher rating. This project, originally proposed as the ‘CVUP’ NOA option, is primarily designed to connect the 400kV B5 circuit established initially through wider works scheme DWUP to the existing 400kV circuits between Strathaven and Torness, enhancing the B5 boundary capability, required to enable greater north to south power flows driven by the connection of renewable generation in the north of Scotland. This project will also increase fault infeed headroom at Clydesmill 275kV and Strathaven 275kV to facilitate new connections in this area. (SPT-RI-3159) | 2033-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04897 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04898 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04899 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04900 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101093-202181 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04903 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04904 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04905 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04906 | AL BOUM PHOTO LTD | Norton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04907 | AL BOUM PHOTO LTD | Norton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04908 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04909 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04910 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04911 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04912 | AL BOUM PHOTO LTD | Norton 400kV Substation | 020640-020640 | Reconductor the 2x500mm² sections of the Norton – Osbaldwick 1 400kV circuit with 2x700mm² conductor strung for operation at 90°C | 2031-10-31
Al Boum Photo (Norton) | PRO-001651 | CS-04913 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Alcemi Armadale BESS | PRO-004011 | CS-09180 | ALCEMI STORAGE DEVELOPMENTS 8 LTD | Bathgate 400kV | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2030-10-31
Alcemi Armadale BESS | PRO-004011 | CS-09181 | ALCEMI STORAGE DEVELOPMENTS 8 LTD | Bathgate 400kV | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 2030-10-31
Alcemi Devilla Battery Energy Storage Facility | PRO-001453 | CS-06687 | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Alcemi Devilla Battery Energy Storage Facility | SPT-RI-1879 | Culross 275kV substation turned in Longannet to Mosmorran circuit - A new substation will be established on the Longannet – Mosmorran 275kV circuit (YJ Route) approximately between YJ010 and YJ011. The YJ route (south circuit) will be turned in to the new substation with a 275kV circuit breaker on each side which will be connected to a new 275kV busbar. | 2027-10-30
Alcemi Devilla Battery Energy Storage Facility | PRO-001453 | CS-06688 | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Alcemi Devilla Battery Energy Storage Facility | SPT-RI-1880 | Longannet to Westfield / Mosmorran 275kV circuit uprate - It is proposed to uprate the existing Longannet – Westfield – Mosmorran circuits (both north and south) by reconductoring to accommodate the generation in the area. The following circuits shall be reconductored: Reconductor ~26.5km of the overhead line (on both sides of the towers) between YJ001 to YJ075 with twin Rubus 85C (anticipated; subject to further verification); Reconductor ~3km of the overhead line (on both sides of the towers) between YJ075 to YJ084 with twin Totara 85C (anticipated; subject to further verification); Reconductor ~5.5km of overhead line (on both sides of the towers) between YV001 to YV015 with twin Totara 85C (anticipated; subject to further verification). | 2027-10-30
Alcemi Devilla Battery Energy Storage Facility | PRO-001453 | CS-06689 | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Alcemi Devilla Battery Energy Storage Facility | Alcemi Devilla H1 Works | At a location close to Longannet substation, on YG Route, establish a cable sealing end and install ~4km of 275kV cable circuit (required 554MVA) by tee connect onto YG Route to the Alcemi Devilla site. 2 At the Alcemi Devilla site, install one 275kV disconnector. 3 Provision of communications, alarms, indications and metering from the User site | 2027-10-30
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07158 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07159 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07160 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07161 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07162 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07163 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025d | North East Reinforcement | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07164 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-10-31
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07165 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04310 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | Alcemi Score H1 Works | Installation of a 400kV disconnector at the User’s site, on the Network side of the circuit breaker mentioned above. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04311 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04312 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04313 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04314 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04315 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025d | North East Reinforcement | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04316 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04317 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04318 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04319 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04320 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04321 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04322 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-165 | Alcemi substation 400kV Switchgear - Overhead line works to bring the 400kV circuit to ground, including any required modifications. Design and installation of one 400kV circuit breaker with three 400kV disconnectors and associated protection and control equipment for the circuit. | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04323 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04324 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04325 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2029-10-31
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04326 | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2029-10-31
Allt an Tuir Renewable Energy Park | PRO-001819 | CS-07268 | ALLT AN TUIR RENEWABLE ENERGY PARK LIMITED | Shin GSP | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2031-06-30
Allt an Tuir Renewable Energy Park | PRO-001819 | CS-07269 | ALLT AN TUIR RENEWABLE ENERGY PARK LIMITED | Shin GSP |  |  | 2031-06-30
Alverdiscott | PRO-001344 | CS-04773 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2030-08-30
Alverdiscott | PRO-001344 | CS-04774 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2030-08-30
Alverdiscott | PRO-001344 | CS-04775 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2030-08-30
Alverdiscott | PRO-001344 | CS-04776 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101010-202014 | Works to enable generation connection of 1.8GW for Xlinks at Alverdiscott 400kV substation. | 2030-08-30
Alverdiscott | PRO-001344 | CS-04777 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2030-08-30
Alverdiscott | PRO-001344 | CS-04778 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2030-08-30
Alverdiscott | PRO-001344 | CS-04780 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 100889-201781 | Hotwire Bramley - Melksham 1 & 2 Circuits from 50°C to 75°C | 2030-08-30
Alverdiscott | PRO-001344 | CS-04787 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2030-08-30
Alyth | PRO-001978 | CS-07712 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2029-10-31
Alyth | PRO-001978 | CS-07713 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2029-10-31
Alyth | PRO-001978 | CS-07714 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2029-10-31
Alyth | PRO-001978 | CS-07715 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2029-10-31
Alyth | PRO-001978 | CS-07716 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2029-10-31
Alyth | PRO-001978 | CS-07717 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2029-10-31
Alyth | PRO-001978 | CS-07718 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2029-10-31
Alyth | PRO-001978 | CS-07719 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025d | North East Reinforcement | 2029-10-31
Alyth | PRO-001978 | CS-07720 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-10-31
Alyth | PRO-001978 | CS-07721 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2029-10-31
Alyth | PRO-001978 | CS-07722 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2029-10-31
Alyth | PRO-001978 | CS-07724 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 2029-10-31
Alyth | PRO-001978 | CS-07725 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2029-10-31
Alyth | PRO-001978 | CS-07726 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2029-10-31
Alyth | PRO-001978 | CS-07727 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2029-10-31
Alyth | PRO-001978 | CS-07728 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2029-10-31
Alyth BESS Station | PRO-002466 | CS-09547 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09548 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09549 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09550 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09551 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09552 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09553 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09554 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09555 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09556 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09557 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09558 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09559 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Alyth BESS Station | PRO-002466 | CS-09560 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Amersham | PRO-001770 | CS-11404 | LON Energy 4 Connection Limited | Amersham Main 132kV Substation | 101590-203204 (0) |  | 2037-10-31
Amersham | PRO-001770 | CS-11405 | LON Energy 4 Connection Limited | Amersham Main 132kV Substation | 100917-201919 (Amersham) |  | 2037-10-31
Amersham BESS & Substation | PRO-002354 | CS-11469 | O&G Solar (SPV 31) Limited | Amersham Main 400kV Substation | 102218-204446 |  | 2034-10-31
Amersham Main | PRO-003404 | CS-10256 | Amersham 10 Renewables Limited | London North West Connection Node A 400kV Substation | 103346-206796 (1) |  | 2037-10-31
Amersham Main | PRO-003404 | CS-10257 | Amersham 10 Renewables Limited | London North West Connection Node A 400kV Substation | 103440-206902 |  | 2037-10-31
AMP Eccles BESS | PRO-003836 | CS-09602 | Eccles Grid Stability Limited | Eccles 400/132kV | SPT-RI-151b | In order to provide GBSQSS compliant connections for additional generation requiring to export from Hawick/Galashiels to Eccles, it is proposed to construct a new 132kV double circuit tower line between Galashiels and Eccles, and remove the existing U and AT Routes. | 2029-10-31
AMP Eccles BESS | PRO-003836 | CS-09603 | Eccles Grid Stability Limited | Eccles 400/132kV | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2029-10-31
AMP Eccles BESS | PRO-003836 | CS-09604 | Eccles Grid Stability Limited | Eccles 400/132kV | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 2029-10-31
AMP Eccles BESS | PRO-003836 | CS-09605 | Eccles Grid Stability Limited | Eccles 400/132kV | AMP Eccles | 1. A 132kV disconnector at Eccles 132kV on the Relevant Transmission Licensee’s side of the new 132kV metering circuit breaker. 2. Relevant civil works necessary to accommodate the new 132kV disconnector at Eccles 132kV. | 2029-10-31
Annan Road BESS | PRO-004059 | CS-09791 | SP Distribution plc | Dumfries 132/33kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2028-04-28
Annan Road BESS | PRO-004059 | CS-09792 | SP Distribution plc | Dumfries 132/33kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2028-04-28
Annan Road BESS | PRO-004059 | CS-09793 | SP Distribution plc | Dumfries 132/33kV | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 2028-04-28
Appin Wind Farm | PRO-002661 | CS-11753 | Appin Wind Farm Limited | Glenglass 132kV Substation | SPT-RI-3102 | Glenglass to Cloud Hill 132kV circuit - A new 132kV circuit will be constructed between the Glenglass 132kV substation and the new Cloud Hill 132kV collector substation. At Glenglass 132kV substation, install a new 132kV feeder bay and associated DBB switchgear (circuit breaker, line isolator and DBB disconnector). From here install a new 132kV circuit to the Cloud Hill 132kV collector substation. The collector substation will accommodate the connection of the Cloud Hill 50MW Windfarm and Rowancraig 40MW Windfarm | 2031-10-31
Appin Wind Farm | PRO-002661 | CS-11754 | Appin Wind Farm Limited | Glenglass 132kV Substation | SPT-RI-173 Cable |  | 2031-10-31
Appin Wind Farm | PRO-002661 | CS-11755 | Appin Wind Farm Limited | Glenglass 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2031-10-31
Appin Wind Farm | PRO-002661 | CS-11756 | Appin Wind Farm Limited | Glenglass 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2031-10-31
Appin Wind Farm | PRO-002661 | CS-11757 | Appin Wind Farm Limited | Glenglass 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2031-10-31
Appin Wind Farm | PRO-002661 | CS-11758 | Appin Wind Farm Limited | Glenglass 132kV Substation | Enabling Works - Appin WF | Installation of a 132kV circuit breaker and associated line isolator at Cloud Hill 132kV collector substation. Install approx. 10km of 132kV circuit (UGC/OHL) from Cloud Hill Collector to Appin Windfarm 132kV substation (Pre-fault summer continuous rating – 75MVA) Installation of a 132kV disconnector at Appin Windfarm 132kV substation | 2031-10-31
Aquind Interconnector | PRO-000285 | CS-05455 | Aquind Limited | Lovedean 400kV Substation | 31832-3 | Thermal reinforcement to the South Coast | 2030-12-31
Aquind Interconnector | PRO-000285 | CS-05456 | Aquind Limited | Lovedean 400kV Substation | 31671-2 | Re-conductoring Fleet - Lovedean 1&2 circuits | 2030-12-31
Aquind Interconnector | PRO-000285 | CS-05457 | Aquind Limited | Lovedean 400kV Substation | 33585 | Extend Lovedean 400KV substation to the East and West including connection into Sellindge OTS system | 2030-12-31
Aquind Interconnector | PRO-000285 | CS-05458 | Aquind Limited | Lovedean 400kV Substation | 30752 | Build and install a South West Operational Tripping Scheme (OTS) | 2030-12-31
Aquind Interconnector | PRO-000285 | CS-05459 | Aquind Limited | Lovedean 400kV Substation | 31671-1 | Re-conductoring Bramley - Fleet 1&2 circuits | 2030-12-31
Arbroath Battery Substation | PRO-000950 | CS-04270 | ARBROATH LIMITED | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2022-02-21
Arbroath Battery Substation | PRO-000950 | CS-04271 | ARBROATH LIMITED | Arbroath GSP | Arbroath Enabling | At Arbroath 132/33kV GSP substation, install two 90MVA 132/33kV transformers within the existing substation. Install protection, control, metering and ancillary equipment. The new equipment will be installed to meet current Fire Separation Standards. | 2022-02-21
Arbroath Battery Substation | PRO-000950 | CS-04272 | ARBROATH LIMITED | Arbroath GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2022-02-21
Ardleigh Solar & BESS | PRO-002644 | CS-09336 | Nembus BESS Limited | Hadleigh 400kV Substation | 102774-205610 | Construction of a new 400kV AIS double busbar 400kV substation (Hadleigh 400kV) between Bramford 400kV – Braintree 400kV substations, comprising of 2 feeder bays and 1 bus coupler bay | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09337 | Nembus BESS Limited | Hadleigh 400kV Substation | 102774-205612 | Extend Hadleigh 400kV substation main and reserve 1 busbar for the provision of one User bay. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09338 | Nembus BESS Limited | Hadleigh 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09339 | Nembus BESS Limited | Hadleigh 400kV Substation | 102774-205611 | Provide a single turn in of the 400kV OHL circuit 1 or circuit 2 (TBC after completion of BTNO works) at tower 4YL024 between Bramford 400kV – Braintree 400kV substations to Hadleigh 400kV substation | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09340 | Nembus BESS Limited | Hadleigh 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09341 | Nembus BESS Limited | Hadleigh 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09342 | Nembus BESS Limited | Hadleigh 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09343 | Nembus BESS Limited | Hadleigh 400kV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09344 | Nembus BESS Limited | Hadleigh 400kV Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09345 | Nembus BESS Limited | Hadleigh 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09346 | Nembus BESS Limited | Hadleigh 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09347 | Nembus BESS Limited | Hadleigh 400kV Substation | 101248-204325 | Add a new bus coupler and three new bays at Wymondley 400kV substation to facilitate the turn in of the existing Pelham to Sundon 400kV circuit at Wymondley 400kV substation. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09348 | Nembus BESS Limited | Hadleigh 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09349 | Nembus BESS Limited | Hadleigh 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09350 | Nembus BESS Limited | Hadleigh 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09351 | Nembus BESS Limited | Hadleigh 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09352 | Nembus BESS Limited | Hadleigh 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09353 | Nembus BESS Limited | Hadleigh 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09354 | Nembus BESS Limited | Hadleigh 400kV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09355 | Nembus BESS Limited | Hadleigh 400kV Substation | 100875-201758 | Build a new 400kV substation for the connection of North Falls, Five Estuaries and Tarchon. Part of the South East Anglia Enabling Works Bramford - Tilbury new 400kV OHL route. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09356 | Nembus BESS Limited | Hadleigh 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09357 | Nembus BESS Limited | Hadleigh 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09358 | Nembus BESS Limited | Hadleigh 400kV Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09359 | Nembus BESS Limited | Hadleigh 400kV Substation | 101786-203721 | At Pelham 400 kV Substation: Install 3000MVA QBs on the (Pelham to Rye House 1&2 circuits (PELH4-1 - RYEH4A and PELH4-2 - RYEH4B circuits) | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09360 | Nembus BESS Limited | Hadleigh 400kV Substation | 101955-204070 | Reconductor TILBURY2-WARLEY2-1 (TILB2-WARL2-1) 400kV circuit to achieve a higher MVA (1049) rating summer pre-fault. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09361 | Nembus BESS Limited | Hadleigh 400kV Substation | 101956-204071 | Reconductor TILBURY4-TILBURY4B-1 (TILB4-TILB4B-1) 400kV circuit to achieve a higher MVA (2809) rating summer pre-fault. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09362 | Nembus BESS Limited | Hadleigh 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09363 | Nembus BESS Limited | Hadleigh 400kV Substation | 101883-203859 | Uprating of the Coryton South – Rayleigh Main (A68A) 400kV circuit cables to achieve 3002MVA pre-fault summer rating | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09364 | Nembus BESS Limited | Hadleigh 400kV Substation | 101295-202561 | Power Control Technology on Tilbury to Kingsnorth 400kVA circuit (NOA) | 2032-10-31
Ardleigh Solar & BESS | PRO-002644 | CS-09365 | Nembus BESS Limited | Hadleigh 400kV Substation | 101296-202563 | Power Control Technology on Tilbury to Grain 400kVA circuit (NOA) | 2032-10-31
Ardonald Wind Farm | PRO-003491 | CS-10161 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10162 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-025a Peterhead - Rothienorman 400kV OHL Upgrade |  | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10163 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10164 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-25c |  | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10165 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-25d |  | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10166 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10167 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10168 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10169 | Ardonald Renewables Limited | New North East 275kV Substation | SHELT-RI-105 Rothienorman Substation |  | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10170 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10171 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-136 - Blackhillock Building Extension |  | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10172 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10173 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10174 | Ardonald Renewables Limited | New North East 275kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10175 | Ardonald Renewables Limited | New North East 275kV Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Ardonald Wind Farm | PRO-003491 | CS-10176 | Ardonald Renewables Limited | New North East 275kV Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Arecleoch | PRO-000012 | CS-06707 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | Arecleoch - H1 Works | At Arecleoch Repowering substation install two disconnectors on the HV side of the transformers. At Arecleoch Repowering substation establish a 275kV busbar to which the two disconnectors and a 275kV circuit breaker, to connect the 275kV underground cable, are connected. Install around 9.5km of 275kV underground cable circuit to connect the wind farm substation to Mark Hill substation, continuous summer rating 250MVA. At Arecleoch Repowering substation install a second 275kV CB on the underground circuit to which a 60MVar reactor is connected. At Mark Hill extend the substation to install a 275kV circuit breaker to which the underground 275kV circuit will connect. | 2032-06-15
Arecleoch | PRO-000012 | CS-06708 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2032-06-15
Arecleoch | PRO-000012 | CS-06709 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2032-06-15
Arecleoch Extension Windfarm | PRO-001111 | CS-05460 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | Areceloch Ext H1 Cable | Installation of a 132kV cable system from Mark Hill 132kV circuit breaker to an appropriate location where the 132kV wood pole overhead line will be constructed. | 2026-08-31
Arecleoch Extension Windfarm | PRO-001111 | CS-05461 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | SPT-RI-282 | Markhill SGT4 | 2026-08-31
Arecleoch Extension Windfarm | PRO-001111 | CS-05462 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | Areceloch Ext H1 OHL | Installation of approximately 5km of 132kV wood pole overhead line between Mark Hill and Arecleoch Extension 132kV Substation. | 2026-08-31
Arecleoch Extension Windfarm | PRO-001111 | CS-05463 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | Arecleoch Ext H1 SS | At Mark Hill Substation install a new 132kV switch bay and associated equipment and apparatus | 2026-08-31
Arkwright | PRO-003248 | CS-10286 | ARLINGTON (GROUP SERVICES) LIMITED | Chesterfield 400kV Substation (Not yet constructed) | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 2034-10-30
Arkwright | PRO-003248 | CS-10287 | ARLINGTON (GROUP SERVICES) LIMITED | Chesterfield 400kV Substation (Not yet constructed) | 101812-203717 | A new 400kV route to be established between the Sheffield area and the East Midlands, to aid with North to South flows of generation which consists of rationalisation of existing Chesterfield 275kV to Chesterfield 400kV. The Chesterfield 400kV will have 4x460MVA, 400/132kV SGT along with feeders connecting to Brinsworth and High Marnham | 2034-10-30
Arkwright | PRO-003248 | CS-10288 | ARLINGTON (GROUP SERVICES) LIMITED | Chesterfield 400kV Substation (Not yet constructed) | 102149-204350 (Arkwright) |  | 2034-10-30
Arkwright | PRO-003248 | CS-10289 | ARLINGTON (GROUP SERVICES) LIMITED | Chesterfield 400kV Substation (Not yet constructed) | 103328-206774 |  | 2034-10-30
Artfield Forest Wind Farm | PRO-003578 | CS-08529 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | Artfield Forest Wind Farm H1 Works | 1. At an appropriate location on BT Route (anticipated to be around BT052-053), establish a new 132kV substation and installing a 132kV circuit breaker and associated line disconnectors to tee onto the overhead line. 2. Install a new steel tower and associate downleads. 3. Install approx. 7km of 132kV OHL (minimum of 90MVA required) to Artfield Forest wind farm site. 4. At the wind farm site, install one 132kV disconnector. | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-08530 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-08531 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-08532 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-08534 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-08535 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-2802 | Artfield Tee – Newton Stewart 132kV OHL circuit uprate - In order to alleviate overloads on the 132kV circuit between the proposed tee location and Newton Stewart (on BT Route No.1 side) associated with the connection of the Artfield Forest Windfarm, it is required to uprate the stretch of circuit. It is proposed to uprate the stretch of circuit with 250mm² AAAC (Sycamore), which will provide sufficient headroom to remove any intact overloads seen on the system. (SPT-RI-2802) | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-12408 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-4109 | Newton Stewart – Glenluce (BT Route) Reconductoring -In order to alleviate overloads on the 132kV circuit between Glenluce and Newton Stewart (on BT Route No.1 and No.2 circuits) associated with embedded generation connections into Ladyburn GSP, it is required to uprate both circuits. It is proposed to uprate the stretch of circuit with approximately 22km of 175mm² ACSR HTLS LARK, which will provide sufficient headroom to remove any intact overloads seen on the system | 2030-06-28
Artfield Forest Wind Farm | PRO-003578 | CS-12409 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-4154 | Ladyburn 132/33kV substation –In order to accommodate the connections within the South-West region, it is proposed to establish a new substation called Ladyburn 132/33kV substation within the Ladyburn area, by turning both sides of the existing BT route (approx. 1.5km from Glenluce) connecting into the exiting BT route. | 2030-06-28
ARVEN OFFSHORE WIND FARM | PRO-003288 | CS-09481 | ARVEN OFFSHORE WIND FARM LIMITED | Northern Shetland 400kV Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 2033-10-31
ARVEN OFFSHORE WIND FARM | PRO-003288 | CS-09482 | ARVEN OFFSHORE WIND FARM LIMITED | Northern Shetland 400kV Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 2033-10-31
ARVEN OFFSHORE WIND FARM | PRO-003288 | CS-09483 | ARVEN OFFSHORE WIND FARM LIMITED | Northern Shetland 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
ARVEN OFFSHORE WIND FARM | PRO-003288 | CS-09484 | ARVEN OFFSHORE WIND FARM LIMITED | Northern Shetland 400kV Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
ARVEN OFFSHORE WIND FARM | PRO-003288 | CS-09485 | ARVEN OFFSHORE WIND FARM LIMITED | Northern Shetland 400kV Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Ashbrook Lane BESS | PRO-003534 | CS-11556 | Downing Renewable Developments LLP | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 101248-204325 (Ashbrook) |  | 2031-10-31
Ashbrook Lane BESS | PRO-003534 | CS-11557 | Downing Renewable Developments LLP | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 102020-204175 Ex(8a) |  | 2031-10-31
Ashbrook Lane BESS | PRO-003534 | CS-11558 | Downing Renewable Developments LLP | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 102496-205083 Ex(8a) |  | 2031-10-31
Ashbrook Lane BESS | PRO-003534 | CS-11559 | Downing Renewable Developments LLP | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 102682-205369 Ex(8a) |  | 2031-10-31
Ashbrook Lane BESS | PRO-003534 | CS-11560 | Downing Renewable Developments LLP | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 103043-206459 |  | 2031-10-31
Ashbrook Lane BESS | PRO-003534 | CS-11561 | Downing Renewable Developments LLP | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 103108-206526 (Ashbrook) |  | 2031-10-31
Auchentiber Farm 700MW BESS | PRO-003601 | CS-08544 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2029-10-17
Auchentiber Farm 700MW BESS | PRO-003601 | CS-08545 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2029-10-17
Auchentiber Farm 700MW BESS | PRO-003601 | CS-08546 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2268 | BZ Route No.2 Uprating - Generation connections into the Devol Moor – Erskine 132kV circuit have identified the need to uprate the No.2 side of BZ Route between Erskine and Braehead Park. It has been noted through system studies that an outage on the Erskine to Braehead circuit (BZ No.1) could result in overloads on the No.2 side. In order to alleviate these overloads, it is required to uprate the OHL and cable sections of the circuit. It is proposed to install 1x 280mm² AAAC “Sycamore” conductor on the OHL sections operating at 75℃ with similarly rated cable sections | 2029-10-17
Auchentiber Farm 700MW BESS | PRO-003601 | CS-08547 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2029-10-17
Auchentiber Farm 700MW BESS | PRO-003601 | CS-08548 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2029-10-17
Auchentiber Farm 700MW BESS | PRO-003601 | CS-08549 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2833 | Devol Moor 400kV GIS Substation - At Devol Moor 400kV it is proposed to establish a new indoor GIS Double Busbar substation. The building is proposed to be sized to accommodate 14 bays. The initial GIS substation assets to be installed include the followings (subject to review): ● 5x 400kV Feeder Bays and associated switchgear; SGT1, SGT2, HUNE, WIYH and High Mathernock BESS ● 1x 400kV Bus Coupler ● 1x 400kV Bus Section ● Space to be included with building to accommodate future connections ● Removal of redundant equipment at existing 400kV Devol Moor substation. | 2029-10-17
Auchnasavil Battery Storage | PRO-002127 | CS-07554 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | Intertrip Scheme - Auchnasavil | An intertrip scheme will be installed to facilitate the non-firm connection. The intertrip scheme requires the provision of signals at Carradale 132/33kV GSP Substation, to the host Distribution Network Operator, should either (or both) 33kV metering circuit breakers (3T0 or 4T0) at Carradale Grid Supply Point be opened, resulting in the loss of GT3 or GT4. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07555 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07556 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07557 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07558 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07559 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07560 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07561 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07562 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07563 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2032-10-31
Auchnasavil Battery Storage | PRO-002127 | CS-07564 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 2032-10-31
Auldhouse 200MW BESS | PRO-003825 | CS-12015 | Apatura Project 29 Ltd | Auldhouse 400kV Substation | SPT-RI-3557 |  | 2031-10-31
AULTCRAGGIE BESS | PRO-003228 | CS-10737 | OPDE UK LIMITED | Brora GSP | SHET-RI-109 Loch Buidhe - Spittal 132kV Reconductoring |  | 2034-10-31
AULTCRAGGIE BESS | PRO-003228 | CS-10738 | OPDE UK LIMITED | Brora GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2034-10-31
AULTCRAGGIE BESS | PRO-003228 | CS-10739 | OPDE UK LIMITED | Brora GSP | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2034-10-31
AULTCRAGGIE BESS | PRO-003228 | CS-10740 | OPDE UK LIMITED | Brora GSP | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2034-10-31
AULTCRAGGIE BESS | PRO-003228 | CS-10741 | OPDE UK LIMITED | Brora GSP | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2034-10-31
AULTCRAGGIE BESS | PRO-003228 | CS-10742 | OPDE UK LIMITED | Brora GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2034-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04973 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101604-203228 | Infrastructure works for the generation connection of Aurora Offshore Wind Farm. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04974 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101604-203229 | Extension of the South West OTS to incorporate the Aurora Offshore Wind Farm. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04975 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04976 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04977 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04978 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04979 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04980 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04981 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04982 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04983 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101619-203253 | Reconductoring of the Landulph – Langage 2 circuit to achieve a post-fault Summer rating of 2150MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04984 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04985 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04986 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04987 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04988 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2031-10-31
Aurora Offshore Windfarm | PRO-001774 | CS-04989 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2031-10-31
Awel Y Mor | PRO-000529 | CS-05471 | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 100570-201193 | Extension of the GIS busbar at Bodelwyddan 400kV GIS substation to allow for the connection of the User’s generator bay and the double turn in of the existing CONQ4-BODE/PENT4- 1 & 2 teed circuits. | 2027-04-01
Awel Y Mor | PRO-000529 | CS-05472 | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 100570-201374 | 2. Double turn-in of PENT-BODE-CONQ 1 & 2 circuits - PENT end of circuit 2 to utilise existing OHL between T and BODE s/s (GM line). New OHL to carry CONQ end of (PENT-BODECONQ) circuit 2 turn in, and circuit 1 T. Building of 2 new bays to accommodate additional circuits | 2027-04-01
Awel Y Mor | PRO-000529 | CS-05473 | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 032018-032018 | Reconductor the existing Bodelwyddan - Connah’s Quay Circuits 1 and 2 | 2027-04-01
Axminster | PRO-001017 | CS-04801 | HB825AXM LTD | Axminster 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2024-10-31
Axminster | PRO-001017 | CS-04803 | HB825AXM LTD | Axminster 400kV Substation | 101382-202707 | Expand Axminster 400kV into a 4 Switch Mesh Turn in the Exter - Chickerell onto the Mesh Expansion of Axminster 132kV Install Bus Section Breaker 120 at Axminster 132kV Installation of the 3rd SGT feeding Axminster 132kV | 2024-10-31
Axminster | PRO-001017 | CS-04805 | HB825AXM LTD | Axminster 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2024-10-31
Axminster | PRO-001017 | CS-04806 | HB825AXM LTD | Axminster 400kV Substation | 100805-201625 | 1. Extend Axminster 132kV substation boundary 2. Extend Axminster 132kV main and reserve busbars to provide space for User’s generator bay 3. Works required to connect the User to the Category 2 Melksham Operational Tripping Scheme as described in appendix F3 of the Bilateral Connection Agreement. | 2024-10-31
Axminster | PRO-001017 | CS-04807 | HB825AXM LTD | Axminster 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2024-10-31
Axminster | PRO-001017 | CS-04808 | HB825AXM LTD | Axminster 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2024-10-31
Axminster | PRO-001017 | CS-04809 | HB825AXM LTD | Axminster 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2024-10-31
Axminster | PRO-001017 | CS-04810 | HB825AXM LTD | Axminster 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2024-10-31
Axminster | PRO-001143 | CS-05474 | PIVOTED POWER LLP | Axminster 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2027-10-31
Axminster | PRO-001143 | CS-05475 | PIVOTED POWER LLP | Axminster 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2027-10-31
Axminster | PRO-001143 | CS-05476 | PIVOTED POWER LLP | Axminster 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2027-10-31
Axminster | PRO-001143 | CS-05477 | PIVOTED POWER LLP | Axminster 400kV Substation | 100757-202247 | 1. Substation boundary extension to accommodate the User’s Connection Assets. 2. Install a tertiary cable box or bushing on SGT1. 3. Install a 13kV cable (if required) from tertiary cable box or bushing to earthing transformer. 4. Install an earthing transformer. 5. Install 13kV Disconnector connecting the tertiary connection to Connection Assets. 6. Works required to connect the User to the Melksham Operational Tripping Scheme as described in F3. 7. Works required to connect User to Category 2 intertripping scheme as outline in Appendix F3. | 2027-10-31
Axminster GSP (SEPD) | PRO-002932 | CS-12425 | Southern Electric Power Distribution Plc | West Country Connection Node B 132kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 2038-06-28
Axminster GSP (SEPD) | PRO-002932 | CS-12426 | Southern Electric Power Distribution Plc | West Country Connection Node B 132kV Substation | 102690-205380 |  | 2038-06-28
Axminster GSP (SEPD) | PRO-002932 | CS-12428 | Southern Electric Power Distribution Plc | West Country Connection Node B 132kV Substation | 102690-206879 |  | 2038-06-28
Ayr Farm | PRO-003596 | CS-09913 | Braston New Energy Limited | Ayr Farm Collector Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2028-05-26
Ayr Farm | PRO-003596 | CS-09914 | Braston New Energy Limited | Ayr Farm Collector Substation | SPT-RI-2732 | Busbar Extension and XZ032 Terminal Tower Modifications | 2028-05-26
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08944 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08945 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08946 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08947 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08948 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08949 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08950 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08951 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08952 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 2033-10-31
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08953 | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Ayrshire Grid Services Facility | PRO-001090 | CS-04633 | HUNTERSTON GRID 3 LTD | Hunterston East 400kV substation | SPT-RI-1566 | Hunterston East to Ayrshire Grid 400kV switchgear and cable works - It is proposed to extend the GIS double busbar and install a new 400kV switchbay at Hunterston East 400kV GIS substation, install approximately 900m of 400kV underground cable from the Hunterston East 400kV GIS substation to a new collector substation (Ayrshire Grid 400kV collector substation). At the collector substation, a new outdoor 400kV busbar and three isolators shall be installed. | 2026-03-23
Backmuir Farm BESS | PRO-004485 | CS-11848 | Balance Power Projects Limited | Blackhillock 2 400/33kV GSP Substation | Backmuir Farm BESS 120 MVA Transformer A1 |  | 2033-10-31
Backmuir Farm BESS | PRO-004485 | CS-11849 | Balance Power Projects Limited | Blackhillock 2 400/33kV GSP Substation | Backmuir Farm BESS 33kV switch Bay A1 |  | 2033-10-31
Backmuir Farm BESS | PRO-004485 | CS-11850 | Balance Power Projects Limited | Blackhillock 2 400/33kV GSP Substation | Backmuir Farm BESS AIS Switch Bay A1 |  | 2033-10-31
Backmuir Farm BESS | PRO-004485 | CS-11851 | Balance Power Projects Limited | Blackhillock 2 400/33kV GSP Substation | SHET-RI-136 - Blackhillock Building Extension |  | 2033-10-31
Backmuir Farm BESS | PRO-004485 | CS-11852 | Balance Power Projects Limited | Blackhillock 2 400/33kV GSP Substation | SHET-RI-199 Blackhillock 2 400kV Substation |  | 2033-10-31
Balgonie Solar and BESS | PRO-005047 | CS-12235 | GREENTECH PROJECTS HOLDING UK LIMITED | Abernethy GSP | SHET-RI-255 |  | 2033-10-31
Balgowan Solar and BESS | PRO-004949 | CS-11649 | GREENTECH PROJECTS HOLDING UK LIMITED | Burghmuir GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Balgowan Solar and BESS | PRO-004949 | CS-11650 | GREENTECH PROJECTS HOLDING UK LIMITED | Burghmuir GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Balgowan Solar and BESS | PRO-004949 | CS-11651 | GREENTECH PROJECTS HOLDING UK LIMITED | Burghmuir GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Balgowan Solar and BESS | PRO-004949 | CS-11652 | GREENTECH PROJECTS HOLDING UK LIMITED | Burghmuir GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Balgowan Solar and BESS | PRO-004949 | CS-11653 | GREENTECH PROJECTS HOLDING UK LIMITED | Burghmuir GSP | SHET-RI-311 Burghmuir 400kV Substation | Burghmuir 400kV Substation | 2033-10-31
Balinoe Wind Farm | PRO-004776 | CS-10760 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-304 Shared Double Circuit to Taynuilt |  | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10761 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-263 Taynuilt 132kV Busbar |  | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10762 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10763 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10764 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-046 | Taynuilt – North Argyll Reinforcement - Reinforce the transmission network between Taynuilt and North Argyll substation (established as part of SHET-RI-013). Rebuild approximately 12.5km of existing 132kV double circuit steel tower line between Creag Dhubh and Taynuilt with a heavy duty 132kV | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10765 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10766 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10767 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10768 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10769 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10770 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10771 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bi-pole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10772 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10773 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2034-10-31
Balinoe Wind Farm | PRO-004776 | CS-10774 | RWE Renewables UK Onshore Wind Limited | Balinoe 132kV substation | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08069 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08070 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08071 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08072 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08073 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08074 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08075 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bi-pole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08076 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08077 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08078 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SPT-RI-2347 | Windyhill/Inveranan/Dalmally/Creag Dhubh 275kV Intertripping Scheme - Install new load management schemes at the following locations: Dalmally 275kV, Inverarnan 275kV and Windyhill 275kV. Measure digital and analogue signals of the 275kV circuits between Windyhill – Creag Dhubh, Windyhill – Inverarnan, Inverarnan – Dalmally and Creag Dhubh – Dalmally. These signals shall be shared to SHE Transmission at Creag Dhubh 275kV substation. Relevant signal and communication interface between SP Transmission and SHE Transmission shall be carried out. | 2034-10-31
Balliemeanoch PSH | PRO-001901 | CS-08079 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | Balliemeanoch PSH - 275kV double busbar bay | Installation of a new 275kV double busbar bay at Creag Dhubh 275kV substation, connected to a new 275kV circuit comprised of 7.5km of 275kV tower line and 3km of 275kV cable to the new Balliemeanoch 275kV substation. At the Balliemeanoch 275kV substation, terminate the new 275kV circuit on 1x 275kV line disconnector (L17). | 2034-10-31
Balmachie Farm | PRO-005860 | CS-12496 | GREENTECH PROJECTS HOLDING UK LIMITED | Arbroath GSP | SHET-RI-284 |  | 2033-10-31
Balmachie Farm | PRO-005860 | CS-12497 | GREENTECH PROJECTS HOLDING UK LIMITED | Arbroath GSP | SHET-RI-289 |  | 2033-10-31
Balmeanach Wind Farm | PRO-001438 | CS-06690 | BALMEANACH WIND FARM LIMITED | Edinbane GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2029-11-30
Balmeanach Wind Farm | PRO-001438 | CS-06691 | BALMEANACH WIND FARM LIMITED | Edinbane GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2029-11-30
Balmeanach Wind Farm | PRO-001438 | CS-06692 | BALMEANACH WIND FARM LIMITED | Edinbane GSP | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 2029-11-30
Balmeanach Wind Farm | PRO-001438 | CS-06693 | BALMEANACH WIND FARM LIMITED | Edinbane GSP | Balmeanach Item 1 | Installation of 132kV Disconnector and Circuit breaker, housed indoors with GT2, in addition to 132kV cabling and busbar works to connect new transformer (GT2) | 2029-11-30
Balmeanach Wind Farm | PRO-001438 | CS-06694 | BALMEANACH WIND FARM LIMITED | Edinbane GSP | Balmeanach Item 2 | Replace the existing 33kV Transformer Circuit Breaker 1T0 located within Dunvegan 132/33kV GSP substation compound with the equivalent new equipment rated appropriately. | 2029-11-30
Balmeanach Wind Farm | PRO-001438 | CS-06695 | BALMEANACH WIND FARM LIMITED | Edinbane GSP | Balmeanach Item 3 | Install a new 120MVA transformer and associated switchgear at Dunvegan GSP, extending the 132kV busbar appropriately. Supply and install circuit breaker 2T0, in a location to be provided by the User. | 2029-11-30
Balnacraig Battery Storage | PRO-002244 | CS-08110 | BALNACRAIG BATTERY STORAGE LIMITED | Alness 132/33 kV GSP Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2024-03-31
Balrobert Farm BESS | PRO-004118 | CS-10704 | ELGIN ENERGY ES CO LIMITED | Knocknagael 132kV Substation | SHET-RI-007a Beauly - Blackhillochk 400kV Double Circuit OHL |  | 2032-10-31
Balrobert Farm BESS | PRO-004118 | CS-10705 | ELGIN ENERGY ES CO LIMITED | Knocknagael 132kV Substation | SHET-RI-007b Beauly 400kV Busbar |  | 2032-10-31
Balrobert Farm BESS | PRO-004118 | CS-10706 | ELGIN ENERGY ES CO LIMITED | Knocknagael 132kV Substation | SHET-RI-132 Blackhillock 275kV High Temperature Reconductoring |  | 2032-10-31
Balrobert Farm BESS | PRO-004118 | CS-10707 | ELGIN ENERGY ES CO LIMITED | Knocknagael 132kV Substation | SHET-RI-235 Knocknagael 275kV reserve bus section circuit breaker |  | 2032-10-31
Balrobert Farm BESS | PRO-004118 | CS-10708 | ELGIN ENERGY ES CO LIMITED | Knocknagael 132kV Substation | SHET-RI-292 |  | 2032-10-31
Balvedavist 162 Battery Storage | PRO-002024 | CS-07949 | S4N SPITTAL LTD | Spittal 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2030-10-31
Balvedavist 162 Battery Storage | PRO-002024 | CS-07953 | S4N SPITTAL LTD | Spittal 132kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2030-10-31
Balvedavist 162 Battery Storage | PRO-002024 | CS-12458 | S4N SPITTAL LTD | Spittal 132kV Substation | SHET-RI-109 Loch Buidhe - Spittal 132kV Reconductoring |  | 2030-10-31
Balwyllo BESS | PRO-002352 | CS-08572 | BALWYLLO BESS LIMITED | Bridge of Dun GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-06-30
Balwyllo BESS | PRO-002352 | CS-08573 | BALWYLLO BESS LIMITED | Bridge of Dun GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-06-30
Bankend Rig Extension Wind Farm | PRO-000755 | CS-05383 | SP Distribution plc | Kilmarnock South 275/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2022-10-31
Bankend Rig III Wind Farm | PRO-003451 | CS-08396 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2030-04-30
Bankend Rig III Wind Farm | PRO-003451 | CS-08397 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2030-04-30
Bankend Rig III Wind Farm | PRO-003451 | CS-08398 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 2030-04-30
Bankend Rig III Wind Farm | PRO-003451 | CS-08399 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2826 | Hagshaw Tee to Bankend Rig III Collector Substation -Install a new 132kV trident wood pole circuit between the tee off with Hagshaw Hill Ph3 Wind Farm and the Bankend Rig III collector. The circuit capacity required for this overhead line circuit is 126MVA. The chosen conductor system for the desktop exercise is AAAC UPAS conductor. The circuit length is approximately 18km. At the Hawkwood substation a new 132/33kV substation shall be created with a 132kV circuit breaker and line disconnector being installed alongside a 132/33kV 120MVA transformer . A 33kV 3 Panel board shall be installed with one feeder being captured under this TORI and the remaining two being allocated to Hawkwood WF and Hawkwood Wind Farm. | 2030-04-30
Bankend Rig III Wind Farm | PRO-003451 | CS-08400 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2827 | Redshaw to Hagshaw Tee 132kV Circuit - Construct a new 132kV double busbar bay at Redshaw 132kV substation and from here install a new 132kV cable/OHL circuit to an appropriate point at which a tee off shall be established for the Bankend Rig III Collector substation and Hagshaw Hill Ph3 WF connections. | 2030-04-30
Bankhead BESS | PRO-003236 | CS-09473 | Apatura Project 21 Ltd | Bankhead 400kV Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2033-10-30
Bankhead BESS | PRO-003236 | CS-09474 | Apatura Project 21 Ltd | Bankhead 400kV Substation | SPT-RI-3232 | Bankhead 400kV Substation and 400kV OHL Works - To facilitate the connection of a Battery Storage connection a new 400kV substation will be need to be created and looped into one side of the existing ZA 400kV OHL Route. The 400kV OHL works as well as the creation of this new substation will be established under SPT-RI-3232 which this new Battery Storage connection shall be contingent upon | 2033-10-30
Bankhead BESS | PRO-003236 | CS-12441 | Apatura Project 21 Ltd | Bankhead 400kV Substation | SPT-RI-3802 OHL |  | 2033-10-30
Bankhead BESS | PRO-003236 | CS-12442 | Apatura Project 21 Ltd | Bankhead 400kV Substation | SPT-RI-3802 SS |  | 2033-10-30
Barachander Wind Farm | PRO-003991 | CS-11069 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11070 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-046 | Taynuilt – North Argyll Reinforcement - Reinforce the transmission network between Taynuilt and North Argyll substation (established as part of SHET-RI-013). Rebuild approximately 12.5km of existing 132kV double circuit steel tower line between Creag Dhubh and Taynuilt with a heavy duty 132kV | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11071 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11072 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11073 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11074 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11075 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bi-pole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11076 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-263 Taynuilt 132kV Busbar |  | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11077 | GreenPower (Barachander) Ltd | Taynuilt GSP | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2034-10-31
Barachander Wind Farm | PRO-003991 | CS-11078 | GreenPower (Barachander) Ltd | Taynuilt GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Barking BESS | PRO-003518 | CS-08448 | O&G Solar (SPV 52) Limited | Barking West GSP | 102416 - 204944 | 1. Extend the Substation compound at Barking to accommodate the new SGT. This may require the purchase of additional land and Substation extension. 2. Install and commission a new 275kV Supergrid Transformer (SGT) bay at Barking 275kV substation. This equipment will include the HV side SGT bay disconnectors and circuit breakers. 3. Install 275kV cabling from the new 275kV bay at Barking 275kV to the new SGT. 4. Install and commission a new 120MVA rated 275/33kV SGT 5. Install 33kV cabling from the LV side of the SGTs to the relevant bay at Barking West 33kV substation. 6. At Barking West 33kV substation, modify the current arrangement of SGT 8 to create a 33kV Bay for the new SGT. This equipment will include the LV side SGT bay disconnectors, circuit breakers and busbar selector disconnectors. 7. Install CTs in the Users Generator Bay at Barking West 33kV and link these to the Busbar Protection. Note these will not be for Metering purposes. | 2028-10-31
Bathgate Hygen IDNO GSP | PRO-004673 | CS-10568 | Eclipse Power Networks Limited | Bathgate Hygen IDNO GSP | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2032-06-30
Bathgate Hygen IDNO GSP | PRO-004673 | CS-10569 | Eclipse Power Networks Limited | Bathgate Hygen IDNO GSP | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2032-06-30
Bathgate Hygen IDNO GSP | PRO-004673 | CS-10570 | Eclipse Power Networks Limited | Bathgate Hygen IDNO GSP | SPT-RI-3678 - OHL |  | 2032-06-30
Bathgate Hygen IDNO GSP | PRO-004673 | CS-10571 | Eclipse Power Networks Limited | Bathgate Hygen IDNO GSP | SPT-RI-3678 - SS |  | 2032-06-30
Beaw Field Wind Farm | PRO-000026 | CS-05479 | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 2032-10-29
Beaw Field Wind Farm | PRO-000026 | CS-06456 | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation | SHET-RI-116 | Kergord - Yell 132kV Connection - on Shetland install a new 132kV single circuit between the Kergord 132kV substation (established as part of SHET-RI-053) and a new tee point on Yell, to enable the connection of renewable generation. (SHET-RI-116) | 2032-10-29
Beaw Field Wind Farm | PRO-000026 | CS-06459 | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation | Beaw Field H1 | 1. Installation of a new 132kV circuit breaker (205) and line disconnector (203) connected within the South Yell Switching Station (constructed under TORI SHET-RI-116). 2. Installation of a line disconnector (103) at 132 kV Beaw Field Substation. 3. Establish approximately 1.1 km of 132 kV Underground Cable from the proposed South Yell Switching Station to the 132kV Beaw Field substation on the Isle of Yell. | 2032-10-29
Beinn an Tuirc 1 | PRO-003918 | CS-11182 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11183 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11184 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11185 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11186 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11187 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11188 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SHET-RI-158 Twin Carradale –KilmarnockSouth subsea cable |  | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11189 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11190 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | BAT 1 Feeder Bay | Installation of a new 132kV double busbar feeder bay, consisting of 2x 132kV busbar disconnectors, 1x 132kV circuit breaker and 1x 132kV circuit disconnector, located at the new 132kV double busbar at Carradale substation, installed as part of SHET-RI-158. | 2034-10-31
Beinn an Tuirc 1 | PRO-003918 | CS-11191 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn an Tuirc Substation | BAT 1 - 132kV Circuit | Establishment of a new 132kV single circuit connection between Carradale 132kV substation and the new Beinn an Tuirc 1 132kV substation. This will comprise of approximately 8km of 132kV OHL and 0.5km of 132kV cable. This circuit will terminate onto a new 132kV line disconnector switch and circuit breaker located at the Beinn an Tuirc 1 132kV substation | 2034-10-31
Beinn Mheadhonach | PRO-001506 | CS-06484 | Wind Harvest Limited | Edinbane GSP | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 2029-11-30
Beinn Mheadhonach | PRO-001506 | CS-06485 | Wind Harvest Limited | Edinbane GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2029-11-30
Bellrock Offshore Wind Farm | PRO-001496 | CS-06696 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | Lyra Item 1 | 1. Install 400kV plant and apparatus at Cousland 400kV Substation which will form the connection to the Lyra Offshore Transmission Interface Point, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06697 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06698 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06699 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06700 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06701 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06702 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-1795 | This project will construct a new 400kV double circuit over the boundary from the South East of Scotland and the North West of England | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06703 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06704 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 2032-10-31
Bellrock Offshore Wind Farm | PRO-001496 | CS-06705 | Bellrock Offshore Wind Farm Limited | Hurlie 400kV substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 2032-10-31
Ben Sca | PRO-000907 | CS-03799 | BEN SCA WIND FARM LIMITED | Edinbane GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2028-04-16
Ben Sca | PRO-000907 | CS-03800 | BEN SCA WIND FARM LIMITED | Edinbane GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2028-04-16
Ben Sca | PRO-000907 | CS-04194 | BEN SCA WIND FARM LIMITED | Edinbane GSP | Ben Sca Item 1 | A new 132kV busbar will be created under TORI 61 and two new 132kV Circuit Switcher Bays (115 and 215) will be created to connect to this infrastructure. This will include the associated protection and control infrastructure. | 2028-04-16
Ben Sca | PRO-000907 | CS-04195 | BEN SCA WIND FARM LIMITED | Edinbane GSP | Ben Sca Item 2 | Replace the existing 33kV Transformer Circuit Breaker (1T0) located within Dunvegan 132/33kV GSP substation compound with the equivalent new equipment rated to a minimum of 1250A. | 2028-04-16
Ben Sca | PRO-000907 | CS-04196 | BEN SCA WIND FARM LIMITED | Edinbane GSP | Ben Sca Item 3 | Install an additional 60MVA 132/33kV transformer, a 33kV transformer Circuit Breaker (2T0) within Dunvegan 132/33kV substation, on suitable plinths; along with their associated cabling/metering/protection equipment. The circuit breakers (1T0 and 2T0) will be owned and operated by Relevant Transmission Licensee and will represent the commercial boundary between Relevant Transmission Licensee and the User. | 2028-04-16
Bendle Farm | PRO-002243 | CS-09826 | Balance Power Projects Limited | Gretna 400/132kV | Bendle FarmA1 SS |  | 2031-10-31
Bendle Farm | PRO-002243 | CS-09827 | Balance Power Projects Limited | Gretna 400/132kV | Bendle Farm H1 OHL |  | 2031-10-31
Bendle Farm | PRO-002243 | CS-09828 | Balance Power Projects Limited | Gretna 400/132kV | Bendle Farm H1 SS |  | 2031-10-31
Bendle Farm | PRO-002243 | CS-09829 | Balance Power Projects Limited | Gretna 400/132kV | SPT-RI-231 OHL |  | 2031-10-31
Bendle Farm | PRO-002243 | CS-09830 | Balance Power Projects Limited | Gretna 400/132kV | SPT-RI-2320 OHL |  | 2031-10-31
Bendle Farm | PRO-002243 | CS-09831 | Balance Power Projects Limited | Gretna 400/132kV | SPT-RI-2320 SS |  | 2031-10-31
Bendle Farm 2.0 | PRO-002700 | CS-10133 | Balance Power Projects Limited | BENDLE FARM 2.0 132KV SUBSTATION | SPT-RI-231 |  | 2031-10-31
Bendle Farm 2.0 | PRO-002700 | CS-10134 | Balance Power Projects Limited | BENDLE FARM 2.0 132KV SUBSTATION | SPT-RI-2320 |  | 2031-10-31
Berkswell (Tertiary) | PRO-000516 | CS-04811 | ENSO GREEN HOLDINGS P LIMITED | Berkswell 275kV Substation | 100953-201900 | 1. Install earthing transformer on 13kV tertiary connection 2. Install 13kV Cable from 13kV tertiary connection to the 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection | 2028-05-30
Berkswell (Tertiary) | PRO-000516 | CS-12228 | ENSO GREEN HOLDINGS P LIMITED | Berkswell 275kV Substation | 100953-201900 Infra |  | 2028-05-30
Berkswell (Tertiary) | PRO-000516 | CS-12229 | ENSO GREEN HOLDINGS P LIMITED | Berkswell 275kV Substation | 100953-201901 Conn |  | 2028-05-30
Berkswell (Tertiary) | PRO-000516 | CS-12230 | ENSO GREEN HOLDINGS P LIMITED | Berkswell 275kV Substation | 100953-202125 One Off |  | 2028-05-30
Berkswell Energy Storage | PRO-001788 | CS-05313 | Berkswell Battery Storage Limited | Berkswell 275kV Substation | 101395-202733 | 1. At Berkswell 275KV site, Mesh corner 4 extension to facilitate the transmission works 2. Installation of 275KV disconnector. | 2027-04-30
Berkswell Energy Storage | PRO-001788 | CS-12510 | Berkswell Battery Storage Limited | Berkswell 275kV Substation | 104270-208297 |  | 2027-04-30
Berkswell GSP | PRO-002889 | CS-12664 | National Grid Electricity Distribution (East Midlands) plc | Warwickshire Connection Node C 132kV substation | 102581-205192 -Berkswell |  | 2037-10-30
Berkswell GSP | PRO-002889 | CS-12665 | National Grid Electricity Distribution (East Midlands) plc | Warwickshire Connection Node C 132kV substation | 102581-205193 - Berkswell |  | 2037-10-30
Berkswell GSP | PRO-002889 | CS-12666 | National Grid Electricity Distribution (East Midlands) plc | Warwickshire Connection Node C 132kV substation | 102901-206312-Berkswell |  | 2037-10-30
Berkswell GSP | PRO-002889 | CS-12667 | National Grid Electricity Distribution (East Midlands) plc | Warwickshire Connection Node C 132kV substation | 103022-206431-Berkswell |  | 2037-10-30
Berkswell GSP | PRO-002889 | CS-12668 | National Grid Electricity Distribution (East Midlands) plc | Warwickshire Connection Node C 132kV substation | 103055-206471-Berkswell |  | 2037-10-30
Berkswell GSP | PRO-002889 | CS-12669 | National Grid Electricity Distribution (East Midlands) plc | Warwickshire Connection Node C 132kV substation | 103407-206867-Berkswell |  | 2037-10-30
Berwick Bank Offshore Wind Farm A | PRO-002627 | CS-08401 | BERWICK BANK A LIMITED | Branxton 400kV Substation | Berwick Bank A H1 SS Works | Installation of two 400kV Gas Insulated Switchgear (GIS) bays, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers which will form the transmission interface points for the Berwick Bank “A” Offshore Wind Farm connection (Interfaces A1 and A2). Completion of all associated protection and control works Provision of communications, alarms and indications, as described in Appendix F and Appendix OF of the Bilateral Connection Agreement. All associated miscellaneous and minor works, including provision of Category 2 Intertripping Scheme and Category 4 Intertripping Scheme, as defined in the Grid Code. | 2028-10-31
Berwick Bank Offshore Wind Farm A | PRO-002627 | CS-08402 | BERWICK BANK A LIMITED | Branxton 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2028-10-31
Berwick Bank Offshore Wind Farm A | PRO-002627 | CS-08403 | BERWICK BANK A LIMITED | Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2028-10-31
Berwick Bank Offshore Wind Farm B | PRO-002628 | CS-08404 | Berwick Bank B Limited | Branxton 400kV Substation | Berwick Bank B H1 SS Works | Installation of two 400kV Gas Insulated Switchgear (GIS) bays , including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers which will form the transmission interface points for the Berwick Bank “B” Offshore Wind Farm connection (Interfaces B1 and B2) Completion of all associated protection and control works Provision of communications, alarms and indications, as described in Appendix F and Appendix OF of the Bilateral Connection Agreement All associated miscellaneous and minor works, including provision of Category 2 Intertripping Scheme and Category 4 Intertripping Scheme, as defined in the Grid Code. | 2029-10-31
Berwick Bank Offshore Wind Farm B | PRO-002628 | CS-08406 | Berwick Bank B Limited | Branxton 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2029-10-31
Berwick Bank Offshore Wind Farm B | PRO-002628 | CS-08407 | Berwick Bank B Limited | Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2029-10-31
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07077 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101370-202690 | At Blyth 400kV / 275kV substation: Install 2 new 1100MVA rated interbus transformers. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07078 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07079 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203052 | At Tynemouth 275kV substation: Replace the line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus (101539-203052) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07080 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100927-201853 | 1. At Blyth 400kV Substation: Extend Main and Reserve bar section to accommodate a user bay, install 2 new section breakers in both Main and Reserve busbar and install a generator intertripping scheme. (100927-201853) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07081 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100058-200133 | Tee in the Hartlepool - West Boldon circuit into Hawthorn Pit 275kV Substation (NOA WHTI) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07082 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101369-202689 | Reconductor the Blyth legs of the Blyth – Eccles – Stella West 1 and Blyth – Eccles – Stella West 2 circuits with GAP conductor and replace the cable sections of both circuits. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07083 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07084 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07085 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07086 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07087 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07088 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101385-202713 | Reconductor the Blyth – Stella West 275kV circuits with 1x525mm² Curlew conductor (101385- 202713) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07089 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203053 | At South Shields 275kV substation: Replace the, line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus (101539-203053) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07090 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203054 | At West Boldon 275kV substation: Replace the line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. (101539-203054) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07091 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203055 | At Offerton 275kV substation: Replace the, line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus (101539-203055) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07092 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07093 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 020669-020669 | Lackenby – Norton 1 circuit reconductor the 2x570mm² sections with 2x620mm² GZTACSR conductor. Replace the cable section of the circuit. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07094 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203056 | Reconductor the Blyth – Tynemouth 275kV circuit with 1x525mm² Curlew conductor (101540- 203056) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07095 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203057 | Reconductor the Blyth – South Shields - Tynemouth 275kV circuits with 1x525mm² Curlew conductor (101540-203057) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07096 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203058 | Reconductor the Tynemouth – West Boldon 275kV circuit with 1x525mm² Curlew conductor (101540-203058) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07097 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203059 | Reconductor the South Shields – West Boldon 275kV circuit with 1x525mm² Curlew conductor. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07098 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101430-202806 | Reconductor the Offerton - West Boldon 275kV circuit with 1x525mm² Curlew conductor (101430- 202806) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07099 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07100 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101430-202807 | Reconductor the Hawthorn Pit – Offerton circuit with 1x525mm² Curlew conductor (101430- 202807) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07101 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101430-202808 | Reconductor the Hawthorn Pit – West Boldon circuit with 1x525mm² Curlew conductor (101430- 202808) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07102 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101373-202693 | Reconductor the 2x400mm² section of the Hartlepool – Hawthorn Pit circuit with 2x570mm² conductor (101373-202693) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07103 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033703-033703 | Reconductor Harker - Fourstones - Stella West circuits with 1x525mm² Curlew conductor (033703-033703) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07104 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07105 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101325-202642 | At Thornton 400kV: Establish an additional section switch in place of X224 or X228 and add another section switch in place of X428 or X424. Replace circuit breaker X405 and X805 (In Lackenby - Thornton circuits with 63kA rated breakers. (101325-202642) | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07106 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100110-200299 | Install three new 225MVAr MSCs at Norton, Osbaldwick and Stella West 400kV substations. (NOA NEMS). | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07107 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07108 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07109 | BERWICK BANK C LIMITED | Blyth 400kV Substation | Berwick Bank Offshore Wind Farm C H1 Enabling Works | Modification of Series Compensation Equipment at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits as required. • The final scope of series compensation related works will be subject to a detailed engineering design and studies to be completed by the Series Compensation Equipment original equipment manufacturer | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07110 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2029-11-30
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07111 | BERWICK BANK C LIMITED | Blyth 400kV Substation | Berwick Bank Offshore Wind Farm C H1 Enabling Works | Modification of Series Compensation Equipment at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits as required. • The final scope of series compensation related works will be subject to a detailed engineering design and studies to be completed by the Series Compensation Equipment original equipment manufacturer | 2029-11-30
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09960 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09961 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09962 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | SPT-RI-2963 | Branxton to Eccles Further Uprating – In order to alleviate the overloads identified as part of the system studies conducted it is necessary to reconductor both sides of the Branxton to Eccles circuits with twin HTLS “Curlew” conductor. This conductor shall give a summer pre-fault rating on the circuit of 2590MVA | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09963 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | SPT-RI-2825 SS | Kelloe Mains 400kV Substation | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09964 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | SPT-RI-2825 OHL |  | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09965 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | Berwick - H1 Double busbar transformer bay | At Kelloe Mains, Installation of one new 400kV double busbar transformer bay | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09966 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | Berwick - SGT | At Kelloe Mains, Installation of one 400/132kV 240MVA rated super grid transformer | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09967 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | Berwick - Circuit Breaker | At Kelloe Mains, Installation of one 132kV circuit breaker and associated disconnectors | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09968 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | Berwick - Civils | Relevant civil works necessary to accommodate the new 132kV metering circuit | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09969 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | Berwick - OHL | Installation of approx. 17km of 132kV circuit from Kelloe Mains Substation to Berwick Substation, the majority of wish is routed as an overhead line | 2031-10-31
Berwick Solar Wind and Battery Storage | PRO-003490 | CS-09970 | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV | Berwick - Disconnector | Installation of a line side 132kV disconnector at Berwick 132kV Substation | 2031-10-31
BESS Cilfynydd | PRO-002008 | CS-07950 | REWE 2 LIMITED | Cilfynydd 400kV Substation | 101841-203779 | Double Busbar extension Cilfynydd 400kV Substation to provide space for the User’s generation bay. | 2029-07-12
BESS Cilfynydd | PRO-002008 | CS-07951 | REWE 2 LIMITED | Cilfynydd 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2029-07-12
BESS Cilfynydd | PRO-002008 | CS-07952 | REWE 2 LIMITED | Cilfynydd 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2029-07-12
BESS Harker | PRO-002010 | CS-07770 | REWE 4 LIMITED | Harker 400kV Substation | 101843-203780 | Provision of spare 400kV GIS bay in the new build substation inclusive of required Protection and Control to form a compliant connection. | 2031-05-30
BESS Harker | PRO-002010 | CS-07771 | REWE 4 LIMITED | Harker 400kV Substation | 101268-202511 | The scope of this project is the rebuild of Harker substation and rationalisation to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. | 2031-05-30
BESS North Farm | PRO-002060 | CS-08956 | REWE 5 LIMITED | Chickerell 400kV Substation | 101894-203881 | Extend the Busbar at Chickerell 400kV to make provision for the User to connect their generator bay | 2031-11-01
BESS North Farm | PRO-002060 | CS-08957 | REWE 5 LIMITED | Chickerell 400kV Substation | 101485-202932 | Installation of new circuit breaker to control MSC2 to maintain the substation operability | 2031-11-01
BESS North Farm | PRO-002060 | CS-08958 | REWE 5 LIMITED | Chickerell 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2031-11-01
BESS North Farm | PRO-002060 | CS-08959 | REWE 5 LIMITED | Chickerell 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2031-11-01
BESS North Farm | PRO-002060 | CS-08960 | REWE 5 LIMITED | Chickerell 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2031-11-01
BESS North Farm | PRO-002060 | CS-08961 | REWE 5 LIMITED | Chickerell 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2031-11-01
BESS North Farm | PRO-002060 | CS-08964 | REWE 5 LIMITED | Chickerell 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2031-11-01
BESS North Farm | PRO-002060 | CS-08965 | REWE 5 LIMITED | Chickerell 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2031-11-01
BESS North Farm | PRO-002060 | CS-08968 | REWE 5 LIMITED | Chickerell 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2031-11-01
BESS North Farm | PRO-002060 | CS-08969 | REWE 5 LIMITED | Chickerell 400kV Substation | 101894-203888 | Extension of the Melksham OTS for this connection. | 2031-11-01
BESS Swan | PRO-002009 | CS-08371 | REWE 3 LIMITED | Swansea North 400kV Substation | 101836-203768 | Extension of 400kV busbar at Swansea North 400kV Substation for provision of one generator bay | 2028-10-31
BESS Swan | PRO-002009 | CS-08372 | REWE 3 LIMITED | Swansea North 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2028-10-31
BESS Swan | PRO-002009 | CS-08373 | REWE 3 LIMITED | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-10-31
BESS Swan | PRO-002009 | CS-08374 | REWE 3 LIMITED | Swansea North 400kV Substation | 101841-203778 | Installation of a new commercial Operational Tripping Scheme (via extension of the existing Pembroke OTS) | 2028-10-31
Bettyhill Phase 2 Wind Farm | PRO-002001 | CS-08462 | Bettyhill 2 Wind Ltd | Dounreay 132/33kV | SHET-RI-058 - Bettyhill 2 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement*- This project is to reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2027-11-01
Bettyhill Phase 2 Wind Farm | PRO-002001 | CS-08463 | Bettyhill 2 Wind Ltd | Dounreay 132/33kV | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2027-11-01
BF88 Oakley | PRO-004319 | CS-11522 | BLUEFIELD RENEWABLE DEVELOPMENTS LIMITED | Chiltern Connection Node C 400kV Substation | 102602-205224 (Bluefield) |  | 2038-11-01
BF88 Oakley | PRO-004319 | CS-11523 | BLUEFIELD RENEWABLE DEVELOPMENTS LIMITED | Chiltern Connection Node C 400kV Substation | 103522-207001 |  | 2038-11-01
Bhlaraidh Extension Wind Farm | PRO-000383 | CS-05483 | SSE Generation Limited | Bhlaraidh 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2029-08-17
Bhlaraidh Extension Wind Farm | PRO-000383 | CS-05484 | SSE Generation Limited | Bhlaraidh 132/33kV Substation | Bhlaraidh Extension Enabling | Construct a single circuit 132kV overhead trident line from the 132kV busbar, with a 132kV Circuit Switcher, at the Bhlaraidh Extension Windfarm Substation compound, for a distance of approximately 20 km, to within around 0.5km of the Fort Augustus 400/132kV Substation. The remaining 0.5km distance, to a termination at a new bay on the new 132kV double busbar at the Fort Augustus 400/132kV Substation, should be covered by underground 132kV cable; subject to obtaining the necessary wayleave and consent approvals. The 132kV line/cable will be built using conductors sufficiently rated to accommodate the Bhlaraidh Extension Windfarm | 2029-08-17
Bicker Fen 1 Solar | PRO-001034 | CS-04812 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100891-201788 | 1. Extension of Bicker Fen 400kV substation. 2. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 3. Installation of 13kV cable at the Connection Site. 4. installation of earthing transformer at the Connection Site. 5. Installation of 13kV Disconnector at the Connection Site. 6. Works at the Connection Site to facilitate Category 2 Operational Tripping Scheme (Extension of East Anglia OTS scheme) as described in TOF3. | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08356 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100892-201790 | 1. Installation of tertiary bushings on the 13kV side of SGT2 at the Connection Site.. 2. Installation of earthing transformer at the Connection Site 3. Installation of 13kV Disconnector at the Connection Site. 4. Installation of 13kV busbar to 13kV circuit breaker at the Connection Site. 5. Works at the Connection Site to facilitate Category 2 Operational Tripping Scheme (Extension of East Anglia OTS scheme) as described in Appendix F3 of Bilateral Connection Agreement. | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08357 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08358 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08359 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08360 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08361 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08362 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08363 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08364 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08365 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08366 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08367 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08368 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08369 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-08370 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100798-201612 | At Cottam 400kV Substation: Uprate feeder bay disconnector and circuit breaker on the Cottam - West Burton circuit to provide a post fault summer rating of 3060MVA | 2025-09-26
Bicker Fen 1 Solar | PRO-001034 | CS-12524 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100892-201790 (2) |  | 2025-09-26
Bicker Fen 2 Solar | PRO-001046 | CS-05297 | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 100892-201790 | 1. Installation of tertiary bushings on the 13kV side of SGT2 at the Connection Site.. 2. Installation of earthing transformer at the Connection Site 3. Installation of 13kV Disconnector at the Connection Site. 4. Installation of 13kV busbar to 13kV circuit breaker at the Connection Site. 5. Works at the Connection Site to facilitate Category 2 Operational Tripping Scheme (Extension of East Anglia OTS scheme) as described in Appendix F3 of Bilateral Connection Agreement. | 2026-07-27
Bicker Fen 2 Solar | PRO-001046 | CS-11466 | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 100891-201788 (2) |  | 2026-07-27
Bicker Fen 2 Solar | PRO-001046 | CS-11467 | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 100891-201789 (2) |  | 2026-07-27
Bicker Fen 2 Solar | PRO-001046 | CS-11468 | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 100891-201803 (2) |  | 2026-07-27
Bicker Fenn Energy Park | PRO-001984 | CS-07233 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101716-203424 | 1. Extend Bicker Fenn 400kV substation including 2 Section Breakers Main and Reserve, 1 coupler bay, feeder bay and make provision for the connection of the User’s generation bay. 2. Transpose West Burton Circuit 1 to newly built substation section | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07234 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101651-203292 | 1. Establishment of a new bay on the 400kV bars, including Busbar protection. | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07235 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07236 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07237 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07238 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07239 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07240 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-07241 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-10124 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101651-203292 | 1. Establishment of a new bay on the 400kV bars, including Busbar protection. | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-10125 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101651-203293 |  | 2029-06-01
Bicker Fenn Energy Park | PRO-001984 | CS-10126 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101716-203424 | 1. Extend Bicker Fenn 400kV substation including 2 Section Breakers Main and Reserve, 1 coupler bay, feeder bay and make provision for the connection of the User’s generation bay. 2. Transpose West Burton Circuit 1 to newly built substation section | 2029-06-01
Biggleswade | PRO-003415 | CS-10535 | Biggleswade 10 Renewables Limited | Biggleswade 400kV Substation | 101245-202485 (Biggleswade EX(3)) |  | 2034-10-31
Biggleswade | PRO-003415 | CS-10536 | Biggleswade 10 Renewables Limited | Biggleswade 400kV Substation | 101245-202485 1 |  | 2034-10-31
Biggleswade | PRO-003415 | CS-10537 | Biggleswade 10 Renewables Limited | Biggleswade 400kV Substation | 102903-206314 |  | 2034-10-31
Biggleswade | PRO-003415 | CS-10538 | Biggleswade 10 Renewables Limited | Biggleswade 400kV Substation | 103050-206466 (1) |  | 2034-10-31
Biggleswade BESS | PRO-004279 | CS-11566 | HARMONY BW LTD | Biggleswade 400kV Substation | 101245-202485 (Biggleswade EX(3)) |  | 2034-10-31
Biggleswade BESS | PRO-004279 | CS-11567 | HARMONY BW LTD | Biggleswade 400kV Substation | 102904-206315 |  | 2034-10-31
Biggleswade BESS | PRO-004279 | CS-11568 | HARMONY BW LTD | Biggleswade 400kV Substation | 103049-206465 (Biggleswade EX(3)) |  | 2034-10-31
Biggleswade BESS | PRO-004279 | CS-11569 | HARMONY BW LTD | Biggleswade 400kV Substation | 103050-206466 |  | 2034-10-31
Bilbo Farm | PRO-001301 | CS-09606 | LEL BILBO SOLAR LIMITED | Strichen GSP | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 2024-10-31
Bilbo Farm | PRO-001301 | CS-09607 | LEL BILBO SOLAR LIMITED | Strichen GSP | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 2024-10-31
Bilbo Farm | PRO-001301 | CS-09608 | LEL BILBO SOLAR LIMITED | Strichen GSP | SHET-RI-189 | Strichen-Fraserburgh to St Fergus 132kV OHL Reconductoring - Upgrade a section of the existing Strichen/Fraserburgh to St Fergus Switching Station 132kV SF1/SF2 OHL double circuit (approx. 6.2km) to have a minimum summer pre-fault rating of 231MVA. | 2024-10-31
Birkenhead | PRO-002947 | CS-11892 | SP MANWEB PLC | Birkenhead GSP | 103080-206498 |  | 2037-10-30
Birkenhead | PRO-002947 | CS-11893 | SP MANWEB PLC | Birkenhead GSP | 103080-206607 |  | 2037-10-30
Birkenhead | PRO-002947 | CS-11894 | SP MANWEB PLC | Birkenhead GSP | 104452-208578 Birkenhead |  | 2037-10-30
Birkenhead GSP | PRO-004155 | CS-12113 | SP MANWEB PLC | Birkenhead GSP | 103080-206498 |  | 2037-10-30
Birkenhead GSP | PRO-004155 | CS-12114 | SP MANWEB PLC | Birkenhead GSP | 103080-206607 |  | 2037-10-30
Birkenhead GSP | PRO-004155 | CS-12115 | SP MANWEB PLC | Birkenhead GSP | 104452-208578 Birkenhead |  | 2037-10-30
Bishops Dal Energy Park | PRO-002361 | CS-12443 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2079 OHL |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12444 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2079 SS |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12445 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12446 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2080 Cable |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12447 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2080 OHL |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12448 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2080 SS |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12449 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12450 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-3660 |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12451 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-3736 Cable |  | 2030-10-29
Bishops Dal Energy Park | PRO-002361 | CS-12452 | Renewable Energy Systems Limited | BISHOPS DAL ENERGY PARK 132kV SUBSTATION | SPT-RI-3736 SS |  | 2030-10-29
Blackhill Farm | PRO-005027 | CS-11768 | QAIR RENEWABLES UK LIMITED | Tarland GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
Blackhill Farm | PRO-005027 | CS-11769 | QAIR RENEWABLES UK LIMITED | Tarland GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
Blackhill Farm | PRO-005027 | CS-11770 | QAIR RENEWABLES UK LIMITED | Tarland GSP | SHET-RI-226 |  | 2032-10-31
Blackhillock Battery | PRO-001970 | CS-07336 | BLACKHILLOCK FLEXPOWER LTD | Blackhillock 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2027-10-29
Blackhillock Battery | PRO-001970 | CS-07337 | BLACKHILLOCK FLEXPOWER LTD | Blackhillock 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2027-10-29
Blacklaw | PRO-000036 | CS-06706 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Blacklaw 132/33kV | Blacklaw - H1 Works | Install a new 400kV gas insulated switchgear (GIS) double busbar bay at Wishaw substation. Install a 400kV cable circuit (approx. 700m) between the new GIS switchbay and the location of the new 400/132kV supergrid transformer. Install a new 400kV transformer disconnector. Install a new 400/132kV 360MVA transformer. Civil works to extend the existing Wishaw substation compound. Install a new 132kV circuit breaker at Wishaw substation. Install a new 132kV cable/OHL circuit between Wishaw and Blacklaw WF substation. Install two new 132kV line disconnectors at Blacklaw WF substation | 2032-10-08
Blackpark Battery Storage | PRO-000935 | CS-06686 | BLACKPARK ENERGY STORAGE LIMITED | Nairn GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 2025-12-31
Blaen y Glyn | PRO-001589 | CS-04813 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2027-02-04
Blaen y Glyn | PRO-001589 | CS-04814 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2027-02-04
Blaen y Glyn | PRO-001589 | CS-04815 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2027-02-04
Blaen y Glyn | PRO-001589 | CS-04816 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2027-02-04
Blaen y Glyn | PRO-001589 | CS-04817 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-02-04
Blair Hill Wind Farm | PRO-004994 | CS-11759 | Renewable Energy Systems Limited | Craigenputtlock 400/132 kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Blair Hill Wind Farm | PRO-004994 | CS-11760 | Renewable Energy Systems Limited | Craigenputtlock 400/132 kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Blair Hill Wind Farm | PRO-004994 | CS-11761 | Renewable Energy Systems Limited | Craigenputtlock 400/132 kV Substation | SPT-RI-3657 OHL |  | 2036-10-31
Blairgowrie BESS | PRO-003482 | CS-09420 | WOODSIDE BESS LTD | Blairgowrie BESS 132kV Substation | 132kV Feeder Bay - Blairgowrie BESS | Installation of a new 132kV feeder bay and any associated protection equipment at a new 132kV busbar site (as seen within SHET-RI-237) | 2030-05-30
Blairgowrie BESS | PRO-003482 | CS-09421 | WOODSIDE BESS LTD | Blairgowrie BESS 132kV Substation | 132kV Cable - Blairgowrie | Approximately 2km of 132kV cable will be required as part of this connection. | 2030-05-30
Blairgowrie BESS | PRO-003482 | CS-09422 | WOODSIDE BESS LTD | Blairgowrie BESS 132kV Substation | 132kV Disconnector-Blairgowrie BESS | Additionally, the installation of a new 132kV disconnector switch at Blairgowrie BESS 132kV substation will also be required | 2030-05-30
Blairgowrie BESS | PRO-003482 | CS-09423 | WOODSIDE BESS LTD | Blairgowrie BESS 132kV Substation | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm²) and will operate at 75°C to give a minimum summer pre-fault rating of 176MVA | 2030-05-30
Blairgowrie BESS | PRO-003482 | CS-09424 | WOODSIDE BESS LTD | Blairgowrie BESS 132kV Substation | SHET-RI-237 | Coupar Angus - Clunie 132kV Works - Establish a new 132kV single busbar nearby to the Coupar Angus area. The proposed location for this busbar compound will be next to or underneath the crossing point of the 132kV CCN/CCS circuits and the 275kV YZ1/YZ2 circuits (YZ1/YZ2 proposed to switch to 400kV under SHET-RI-093). For this new 132kV single busbar, 4x new 132kV bays will be required to connect the existing 132kV CCN/CCS circuits as seen from the SLD. A bus section has also been proposed on the busbar. | 2030-05-30
Blarghour Wind | PRO-000398 | CS-06188 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2029-04-01
Blarghour Wind | PRO-000398 | CS-06189 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2029-04-01
Blarghour Wind | PRO-000398 | CS-06190 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2029-04-01
Blarghour Wind | PRO-000398 | CS-06191 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2029-04-01
Blarghour Wind | PRO-000398 | CS-06192 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 2029-04-01
Blarghour Wind | PRO-000398 | CS-06193 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | Blarghour H1 works | H1 132kV AIS Switchgear | 2029-04-01
BLINDWELLS FARM BESS | PRO-002534 | CS-08793 | Opdenergy UK 9 Limited | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-06-30
BLINDWELLS FARM BESS | PRO-002534 | CS-08794 | Opdenergy UK 9 Limited | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-06-30
BLUE PLANET SOLAR | PRO-001703 | CS-04632 | BLUE PLANET SOLAR LIMITED | Dungeness 400kV Substation | 101570-203142 | At Dungeness 400kV double busbar substation: Make provision for connection of generator bay (User Works) Local works to facilitate extension of Sellindge OTS. | 2031-08-31
Blyth GSP (NE) | PRO-002958 | CS-12331 | NORTHERN POWERGRID (NORTHEAST) PLC | Blyth GSP | 101654-203299 |  | 2039-10-30
Bodelwyddan BESS and PV | PRO-001657 | CS-04693 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101568-203131 | At Bodelwyddan 400kV substation extend the site to make provision for a new generator bay. | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04694 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 100570-201374 | 2. Double turn-in of PENT-BODE-CONQ 1 & 2 circuits - PENT end of circuit 2 to utilise existing OHL between T and BODE s/s (GM line). New OHL to carry CONQ end of (PENT-BODECONQ) circuit 2 turn in, and circuit 1 T. Building of 2 new bays to accommodate additional circuits | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04695 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 032281-202001 | 1. Extension of Bodelwyddan 400kV substation. | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04818 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04819 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04820 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04821 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04822 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04823 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04824 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04825 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04826 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04827 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2029-10-31
Bodelwyddan BESS and PV | PRO-001657 | CS-04828 | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 2029-10-31
Bodinglee Wind Farm | PRO-001985 | CS-07389 | Banks Renewables (Bodinglee Wind Farm) Limited | Bodinglee Wind Farm 132kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2029-04-30
Bolney | PRO-001031 | CS-04829 | PIVOTED POWER LLP | Bolney 400kV Substation | 100247-201145 | 1. Site extension to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 3 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer 4. Install an earthing transformer 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets 6. Local works to facilitate the Category 2 with Sellindge Operational Tripping Scheme (OTS) as described in Appendix F3 | 2031-01-31
Bolney | PRO-001031 | CS-04830 | PIVOTED POWER LLP | Bolney 400kV Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 2031-01-31
Bolney | PRO-001031 | CS-04831 | PIVOTED POWER LLP | Bolney 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2031-01-31
Bolney | PRO-001031 | CS-04832 | PIVOTED POWER LLP | Bolney 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2031-01-31
Bolney BESS | PRO-004026 | CS-09234 | CSE45 LIMITED | Bolney 400kV Substation | 102436-204965 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to a new 400kV substation via the Lovedean - Bolney overhead line circuit. • Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. • Construction of 400kV busbar to accommodate the OHL Tee-In connection and the Users Generator Bay. • Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 2037-09-11
Bolney BESS | PRO-004026 | CS-09235 | CSE45 LIMITED | Bolney 400kV Substation | 102695-205389 | • Extension of the 400kV busbars at the new Substation for the User’s bay. • Extension of Sellindge OTS to include this Generator. | 2037-09-11
Bolney Grid Stability Services | PRO-003966 | CS-11477 | WP GRID SERVICES 13 LIMITED | Bolney 400kV Substation | 102436-204965 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to a new 400kV substation via the Lovedean - Bolney overhead line circuit. • Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. • Construction of 400kV busbar to accommodate the OHL Tee-In connection and the Users Generator Bay. • Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 2031-10-31
Bolney Grid Stability Services | PRO-003966 | CS-11478 | WP GRID SERVICES 13 LIMITED | Bolney 400kV Substation | 103490-206968 |  | 2031-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09063 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 102189-204410 | Extension of 400kV main and reserve busbar of Feckenham 400kV substation to accommodate the user’s bay | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09064 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 102092-204283 | Install 400/66kV 180MVA SGT2 and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09065 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 102092-204285 | Install static VAR compensation system and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation. | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09066 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09067 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09068 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09069 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09070 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2033-10-31
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09071 | Wheaten Hill BESS Limited | Feckenham 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2033-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04837 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101555-203096 | 1. Utilise spare bay at Wylfa 400kV to make provision for the User to connect their generator bay | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04838 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04839 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04840 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04841 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04842 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04843 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04844 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04845 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04846 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04847 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04848 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2028-10-31
BOOM Power Llanbabo Generation | PRO-001540 | CS-04849 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 2028-10-31
Boothby Road BESS (PI CS) | PRO-004747 | CS-11125 | Opdenergy UK 11 Limited | Fraserburgh GSP | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 2033-10-31
Boothby Road BESS (PI CS) | PRO-004747 | CS-11126 | Opdenergy UK 11 Limited | Fraserburgh GSP | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 2033-10-31
Boothby Road BESS (PI CS) | PRO-004747 | CS-11127 | Opdenergy UK 11 Limited | Fraserburgh GSP | SHET-RI-189 | Strichen-Fraserburgh to St Fergus 132kV OHL Reconductoring - Upgrade a section of the existing Strichen/Fraserburgh to St Fergus Switching Station 132kV SF1/SF2 OHL double circuit (approx. 6.2km) to have a minimum summer pre-fault rating of 231MVA. | 2033-10-31
Boreham | PRO-005048 | CS-12586 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 033458-033458 (BSR) |  | 2034-10-31
Boreham | PRO-005048 | CS-12588 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 100504-201083-Boreham |  | 2034-10-31
Boreham | PRO-005048 | CS-12589 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 100504-206100-Boreham |  | 2034-10-31
Boreham | PRO-005048 | CS-12590 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 101720-203429 (BSR) n |  | 2034-10-31
Boreham | PRO-005048 | CS-12591 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 104326-208431-Boreham |  | 2034-10-31
Boreland BESS | PRO-004259 | CS-11192 | BORELAND ENERGY LTD | Killin GSP | SHET-RI-243 |  | 2031-10-31
Boreland BESS | PRO-004259 | CS-11193 | BORELAND ENERGY LTD | Killin GSP | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 2031-10-31
Botley West - Cote Solar Power Station | PRO-001587 | CS-04333 | SOLARFIVE LTD | Botley West 400kV Substation | 101420-202783 | 1. Build temporary overhead line to divert the Cowley – Walham circuit and replace suspension tower 4TE037 with a new terminal tower. 2. Construct a new four-bay double busbar Botley West 400kV substation adjacent to tower 4TE037, comprising of two feeder bays, a bus coupler and space for installation of one generator bay. 3. Turn in the new Botley West 400kV substation to the Transmission System, creating Cowley – BotleyWest –Walham circuit. (Substation name, design, and location subject to further engineering assessment during NGET option selection phase) | 2026-10-30
Botley West - Cote Solar Power Station | PRO-001587 | CS-04334 | SOLARFIVE LTD | Botley West 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2026-10-30
Botley West - Cote Solar Power Station | PRO-001587 | CS-04335 | SOLARFIVE LTD | Botley West 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 2026-10-30
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07611 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07612 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07613 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07614 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07615 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-025d | North East Reinforcement | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07616 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07617 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07618 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07619 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07620 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07621 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07622 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07623 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07624 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2035-12-31
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07625 | BOWDUN OFFSHORE WIND FARM LIMITED | Hurlie 400kV substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2035-12-31
Boyndie Solar | PRO-004006 | CS-10019 | GREENTECH PROJECTS HOLDING UK LIMITED | Macduff GSP | SHET-RI-079a | Blackhillock Additional 275/132kV SGT – Reinforce the transmission network at Blackhillock substation by installing an additional new 275/132kv SGT to enable the connection of Elchies WF. The transformer shall be rated at 360MVA | 2029-09-30
Boyndie Solar | PRO-004006 | CS-10020 | GREENTECH PROJECTS HOLDING UK LIMITED | Macduff GSP | SHET-RI-079b | Blackhillock Additional 275/132kV SGT – Reinforce the transmission network at Blackhillock substation by installing an additional new 275/132kV Supergrid Transformer. The transformer shall be rated at 360 MVA | 2029-09-30
Brackenhills Wind | PRO-000592 | CS-06236 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2023-07-20
Brackenhills Wind | PRO-000592 | CS-06237 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 2023-07-20
Brackenhills Wind | PRO-000592 | CS-06238 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2023-07-20
Brackenhills Wind | PRO-000592 | CS-06239 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2023-07-20
Bradford West | PRO-001466 | CS-11886 | Northern Powergrid (Yorkshire) Plc | Bradford West GSP | 103205-206631 2 |  | 2035-10-30
Bradford West | PRO-001466 | CS-11887 | Northern Powergrid (Yorkshire) Plc | Bradford West GSP | 103543-207035 |  | 2035-10-30
Bradford West | PRO-001466 | CS-11888 | Northern Powergrid (Yorkshire) Plc | Bradford West GSP | 103543-207036 |  | 2035-10-30
Bradford West | PRO-001466 | CS-11889 | Northern Powergrid (Yorkshire) Plc | Bradford West GSP | 103572-207084 |  | 2035-10-30
Bradford West 100MW | PRO-001874 | CS-07177 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101744-203464 | Bradford West 275kV substation 1. Extend Mesh Corner 2 and install a Circuit breaker and associated disconnectors to allow connection of the Users generator circuit 2. Modify the mesh corner protection scheme as required, update Substation Control System and database changes | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07178 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101611-203237 | Hotwire the 2x400mm² section of the Rochdale - Whitegate 1 275kV circuit to operate at 65°C. | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07179 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07180 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07181 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101744-203465 | On the Ferrybridge – Skelton Grange 1 275kV circuit, reconductor the 1x700mm² section of the circuit with 1x772mm² Warwick conductor or equivalent. | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07182 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm² sections with 2x620mm² GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07183 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm² sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570mm² strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570mm²should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07184 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101511-202976 | Hotwire the 2x400mm² sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 2027-05-31
Bradford West 100MW | PRO-001874 | CS-07185 | OLD ALLEN ROAD BESS LIMITED | Bradford West 275kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2027-05-31
Bradford West GSP (Yorkshire) | PRO-002971 | CS-12376 | Northern Powergrid (Yorkshire) Plc | Leeds North Connection Node D | 103205-206631 |  | 2039-10-30
Bradford West GSP (Yorkshire) | PRO-002971 | CS-12377 | Northern Powergrid (Yorkshire) Plc | Leeds North Connection Node D | 103543-207036 |  | 2039-10-30
Bradford West GSP (Yorkshire) | PRO-002971 | CS-12378 | Northern Powergrid (Yorkshire) Plc | Leeds North Connection Node D | 103572-207084 |  | 2039-10-30
Bradwell Energy Park | PRO-004004 | CS-09179 | LOW CARBON SOLAR PARK 28 LIMITED | Rayleigh 400kV Substation | 102732-205518 | Extend Rayleigh 400kV substation main and reserve 1 busbars for the provision of one User Bay. | 2032-10-31
Brae WF | PRO-004633 | CS-11710 | WIND 2 LIMITED | Linnmill GSP | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 2032-08-30
Brae WF | PRO-004633 | CS-11711 | WIND 2 LIMITED | Linnmill GSP | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2032-08-30
Brae WF | PRO-004633 | CS-11712 | WIND 2 LIMITED | Linnmill GSP | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2032-08-30
Brae WF | PRO-004633 | CS-11713 | WIND 2 LIMITED | Linnmill GSP | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2032-08-30
Braintree | PRO-001042 | CS-04850 | PIVOTED POWER LLP | Braintree 400kV Substation | 100542-201124 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install 72.5kV, 40kA* Disconnecting Circuit Breaker (DCB) at the 13kV side connecting Tertiary to Connection Assets for Users connection. * Under extreme conditions (G74) the specified 40kA DCB rating is exceeded when both SGTs at Braintree 400/132kV substation are set at identical tap positions, beyond tap position 5 and 13. | 2024-10-30
Braintree | PRO-003406 | CS-10539 | Braintree 10 Renewables Limited | Braintree 400kV Substation | 102637-205303 (2) |  | 2034-10-31
Braintree | PRO-003406 | CS-10540 | Braintree 10 Renewables Limited | Braintree 400kV Substation | 102638-205305 (2) |  | 2034-10-31
Braintree | PRO-003406 | CS-10541 | Braintree 10 Renewables Limited | Braintree 400kV Substation | 102638-205310 | Relocation of NGET’s 400kV Tower 4VB094A, 4VB094B and 4VB094C for installation and connection of new Braintree 400kV substation. | 2034-10-31
Braintree | PRO-003406 | CS-10542 | Braintree 10 Renewables Limited | Braintree 400kV Substation | 102895-206306 |  | 2034-10-31
Bramford BESS | PRO-002071 | CS-08576 | CSE33 LIMITED | Bramford 400kV Substation | 101919-203926 | Extension of Bramford 400kV substation double busbars and establishing separate compound, to provide space for customer bay installation. | 2029-11-30
Bramford BESS | PRO-002071 | CS-08577 | CSE33 LIMITED | Bramford 400kV Substation | 101972-204099 | Extension of the site to accommodate new bay to facilitate a connection | 2029-11-30
Bramford Tertiary | PRO-000397 | CS-04854 | BRAMFORD GREEN LIMITED | Bramford 400kV Substation | 100571 - 201216 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV Cable from Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting the Tertiary connection to Connection Assets for User’s connection 4. Repairment and restoration of the Automatic voltage control (AVC) at Bramford 400/132 kV substation. 5. Repairment and restoration of the auto close scheme at Bramford 400/132kV substation. 6. Extension of substation to facilitate User Connection | 2026-07-16
Bramford Tertiary | PRO-000397 | CS-04855 | BRAMFORD GREEN LIMITED | Bramford 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2026-07-16
Bramford Tertiary | PRO-000397 | CS-04856 | BRAMFORD GREEN LIMITED | Bramford 400kV Substation | 021847-032344 | Bramford – Twinstead 400kV cable sections | 2026-07-16
Bramley (tertiary) | PRO-000396 | CS-05514 | BRAMLEY SOLAR LIMITED | Bramley 400kV Substation | 100605-201257 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer DCB Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection | 2026-08-16
Bramley BESS | PRO-001104 | CS-04857 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 100894-201793 | 1. Extension of Bicker Fen 400kV substation 2. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 3. Installation of 13kV cable at the Connection Site. 4. Installation of earthing transformer at the Connection Site 5. Installation of 13kV Disconnector at the Connection Site. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09134 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2025-09-29
Bramley BESS | PRO-001104 | CS-09135 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09136 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09137 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2025-09-29
Bramley BESS | PRO-001104 | CS-09138 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm² Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm² Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm² Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 2025-09-29
Bramley BESS | PRO-001104 | CS-09139 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 2025-09-29
Bramley BESS | PRO-001104 | CS-09140 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102272-204627 | Construction of a new 400kV double circuit from the Bramley area to the Slough area (route TBC) | 2025-09-29
Bramley BESS | PRO-001104 | CS-09141 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09142 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09143 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2025-09-29
Bramley BESS | PRO-001104 | CS-09144 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09145 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102087-204278 | Uprate A87D Imperial Park – Melksham (future Imperial Park – Folly Farm – Melksham) 400kV circuit cable section (3.9km, with a summer pre-fault rating of 1424MVA) to a summer pre-fault rating of at least 1621MVA | 2025-09-29
Bramley BESS | PRO-001104 | CS-09146 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 2025-09-29
Bramley BESS | PRO-001104 | CS-09147 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 2025-09-29
Bramley BESS | PRO-001104 | CS-09148 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2025-09-29
Branxton Energy Storage Facility | PRO-002076 | CS-07543 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2029-05-13
Branxton Energy Storage Facility | PRO-002076 | CS-07544 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2029-05-13
Branxton Energy Storage Facility | PRO-002076 | CS-07545 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2029-05-13
Branxton Energy Storage Facility | PRO-002076 | CS-07546 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 2029-05-13
Braxbess Branxton BESS | PRO-002208 | CS-08137 | BRAXBESS LTD | Braxbess 400/132kV Collector Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2028-04-30
Braxbess Branxton BESS | PRO-002208 | CS-08138 | BRAXBESS LTD | Braxbess 400/132kV Collector Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2028-04-30
Braxbess Branxton BESS | PRO-002208 | CS-08139 | BRAXBESS LTD | Braxbess 400/132kV Collector Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2028-04-30
Braxbess Branxton BESS | PRO-002208 | CS-08140 | BRAXBESS LTD | Braxbess 400/132kV Collector Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2028-04-30
Braxbess Branxton BESS | PRO-002208 | CS-08141 | BRAXBESS LTD | Braxbess 400/132kV Collector Substation | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 2028-04-30
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07966 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 102099-204292 | Design, construct and commission a new 7 bay Market Harborough 400kV double busbar substation consisting of 2 feeder bays, 1 bus section bay, 1 bus coupler bay, 2 SGT bays and a User generator bay. Modifications to the existing tee point on the Grendon -Market Harborough – Staythorpe and Grendon – Market Harborough – Cottam circuits to facilitate a connection to the new 400kV substation. | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07967 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07968 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07969 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07970 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07971 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07972 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07973 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07974 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07975 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101245-202485 | Reconductor the existing 4x400mm² conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm² 90°C conductor to achieve a pre fault summer rating of 2400 MVA | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07976 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2031-10-31
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07977 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Breakish Windfarm | PRO-002170 | CS-08787 | Asuk Holdco 2 Limited | Breakish 132/33kV | Feeder Bay - Breakish | Install a new 132kV double busbar feeder bay at Broadford collector switching station | 2029-05-31
Breakish Windfarm | PRO-002170 | CS-08788 | Asuk Holdco 2 Limited | Breakish 132/33kV | OHL Circuit - Breakish | Construct approximately 8km of single circuit 132kV overhead line from the Breakish Wind Farm substation to Broadford Collector Switching Station. The end of this line will be coupled to a new underground cable (0.5km approximately) that will connect the 8km single circuit 132kV overhead line to a new bay on the Broadford collector switching station 132kV busbars, via the required 132kV switchgear. | 2029-05-31
Breakish Windfarm | PRO-002170 | CS-08789 | Asuk Holdco 2 Limited | Breakish 132/33kV | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2029-05-31
Breezy Hill Wind Farm | PRO-000475 | CS-06196 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | Breezy Hill H1 Works | 1. At Breezy Hill Wind Farm 132kV Substation, install a 132kV line disconnector. 2. Install ~6.5km of overhead line (wood pole, Poplar conductor) from Clawfin Collector to Breezy Hill Wind Farm 132kV substation. 3. Install a new 132kV circuit breaker bay at the Clawfin Collector substation. | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-06197 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-06198 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-06199 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-06200 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-06201 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-06202 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2028-04-30
Breezy Hill Wind Farm | PRO-000475 | CS-09811 | BROCKWELL ENERGY LIMITED | New Cumnock A 132kV | SPT-RI-2301 | Clawfin Collector Substation – At New Cumnock Board “A” a new 132kV circuit breaker bay will be installed with a new 132kV cable circuit out to Clawfin Collector substation. This is the point where the cable circuit shall transition to an OHL for the Breezy Hill connection. At this same point a new tee off point shall be established for the Dersalloch WF connection to accommodate the requested increase in TEC. The cable circuit shall require a capacity of 182MVA. (SPT-RI-2301) | 2028-04-30
Bridgwater (tertiary) | PRO-000375 | CS-04859 | ENSO GREEN HOLDINGS H LIMITED | Bridgwater 400/132kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2028-08-31
Bridgwater (tertiary) | PRO-000375 | CS-05515 | ENSO GREEN HOLDINGS H LIMITED | Bridgwater 400/132kV Substation | 100653-201333 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer to DCB Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection | 2028-08-31
Bridgwater Energy Park | PRO-004215 | CS-11224 | EXAGEN GROUP LIMITED | Bridgwater GSP | 102798-205759 (Bridgewater) |  | 2037-10-31
Bridgwater Energy Park | PRO-004215 | CS-11225 | EXAGEN GROUP LIMITED | Bridgwater GSP | 102798-205761 (Bridgewater) |  | 2037-10-31
Bridgwater Energy Park | PRO-004215 | CS-11226 | EXAGEN GROUP LIMITED | Bridgwater GSP | 103695-207310 |  | 2037-10-31
Bridgwater Energy Park | PRO-004215 | CS-11227 | EXAGEN GROUP LIMITED | Bridgwater GSP | 103695-207659 |  | 2037-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12248 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-269 |  | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12249 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12250 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12251 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12252 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12253 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12254 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12255 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12256 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12257 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12258 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12259 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12260 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12261 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12262 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SHET-RI-269 |  | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12263 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SPT-RI-004 Cable |  | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12264 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SPT-RI-004 OHL |  | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12265 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SPT-RI-004 SS |  | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12266 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SPT-RI-200 OHL |  | 2033-10-31
Brigton of Ruthven BESS | PRO-004937 | CS-12267 | MORRIS LESLIE LIMITED | Alyth 400kV Substation | SPT-RI-200 SS |  | 2033-10-31
Broadford BESS | PRO-004756 | CS-11297 | FIELD DEVCO LTD | Broadford 132kV Substation | SHET-RI-061 v9 - Skye Overhead Line Reinforcement |  | 2034-10-31
Broadford BESS | PRO-004756 | CS-11298 | FIELD DEVCO LTD | Broadford 132kV Substation | SHET-RI-195 Edinbane to Grudie Bridge 220kV Subsea HVAC Cable Link |  | 2034-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07747 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07748 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-25a |  | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07749 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-25b |  | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07750 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-25c |  | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07751 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-25d |  | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07752 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07753 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07754 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07755 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07756 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07757 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07758 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07759 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07760 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Broadshore Offshore Wind Farm | PRO-002171 | CS-07761 | Broadshore Offshore Wind Farm Limited | Longside 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Brunt Hill Wind Farm | PRO-004322 | CS-12346 | Brunt Hill Limited | Westfield 132/33kV | SHET-RI-314 |  | 2031-10-31
Brunt Hill Wind Farm | PRO-004322 | CS-12347 | Brunt Hill Limited | Westfield 132/33kV | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2031-10-31
Brunt Hill Wind Farm | PRO-004322 | CS-12348 | Brunt Hill Limited | Westfield 132/33kV | SPT-RI-4010 |  | 2031-10-31
Bryn Tilti | PRO-001586 | CS-04700 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2028-07-19
Bryn Tilti | PRO-001586 | CS-04702 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2028-07-19
Bryn Tilti | PRO-001586 | CS-04703 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2028-07-19
Bryn Tilti | PRO-001586 | CS-04704 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2028-07-19
Bryn Tilti | PRO-001586 | CS-04705 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2028-07-19
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06576 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | Two new 400kV feeder bays at New Deer 2 400kV substation | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at New Deer 2 400kV substation. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06577 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06578 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06579 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06580 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06581 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06582 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06583 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06586 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06587 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06588 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06590 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06591 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06592 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06593 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06594 | BUCHAN OFFSHORE WIND LIMITED | Peterhead 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08663 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 101420-202783 | 1. Build temporary overhead line to divert the Cowley – Walham circuit and replace suspension tower 4TE037 with a new terminal tower. 2. Construct a new four-bay double busbar Botley West 400kV substation adjacent to tower 4TE037, comprising of two feeder bays, a bus coupler and space for installation of one generator bay. 3. Turn in the new Botley West 400kV substation to the Transmission System, creating Cowley – BotleyWest –Walham circuit. (Substation name, design, and location subject to further engineering assessment during NGET option selection phase) | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08664 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08665 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08666 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 102386-204875 | Extend the main and reserve busbars at Botley West substation for one additional customer bay. Database update to capture additional generator bay. Design, project management, SAP commissioning resource to facilitate bay extension | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08667 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08668 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2033-10-31
Buckland Marsh Solar Park | PRO-003695 | CS-08669 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm² Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm² Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm² Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 2033-10-31
Builth Wells | PRO-001564 | CS-04721 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2026-10-31
Builth Wells | PRO-001564 | CS-04722 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2026-10-31
Builth Wells | PRO-001564 | CS-04862 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2026-10-31
Builth Wells | PRO-001564 | CS-04863 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2026-10-31
Builth Wells | PRO-001564 | CS-04864 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 2026-10-31
Builth Wells | PRO-001564 | CS-04865 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2026-10-31
Builth Wells | PRO-001564 | CS-04866 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 2026-10-31
Bunloinn Wind Farm BELLA | PRO-004878 | CS-12431 | ENERGYFARM BUNLOINN LLP | Fort Augustus GSP/New Fort Augustus GSP | SHET-RI-211 | Fort Augustus 2 400kV Substation - Construct a new 400kV substation near to Fort Augustus. This new substation will connect to the second Beauly 400kV double circuit overhead line, connecting across the B4 boundary (the first southern connector from Beauly being the Beauly-Denny line). | 2035-10-31
Bunloinn Wind Farm BELLA | PRO-004878 | CS-12432 | ENERGYFARM BUNLOINN LLP | Fort Augustus GSP/New Fort Augustus GSP | SHET-RI-212 | Construct a new 400kV overhead line to run from Beauly, via the Fort Augustus 2 400kV substation, to run across the B4 boundary. | 2035-10-31
Bunloinn Wind Farm BELLA | PRO-004878 | CS-12433 | ENERGYFARM BUNLOINN LLP | Fort Augustus GSP/New Fort Augustus GSP | SPT-RI-2943 | To facilitate the generation connections around Fort Augustus in SSEN area (including ER FA Energy 700MW), in collaboration with SSEN, it is proposed to establish a second Beauly 400kV DC OHL circuit from the proposed SSEN’s ‘Fort Augustus 2 400kV substation’ to terminate into the SPT’s area. The location of the SPT’s new 400kV substation is currently under review, with an initial view that this is to be located at ‘Harburn 400kV substation’ on XJ Route. | 2035-10-31
Bunloinn Wind Farm BELLA | PRO-004878 | CS-12434 | ENERGYFARM BUNLOINN LLP | Fort Augustus GSP/New Fort Augustus GSP | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 2035-10-31
Burgar Hill Renewables Limited | PRO-005121 | CS-12486 | BURGAR HILL RENEWABLES LIMITED | Finstown GSP | SHET-RI-019 | Establish a 220kV HVAC circuit over a distance of approximately 68km between the 275kV GIS substation at Dounreay on the mainland and the new 132kV substation in the vicinity of Finstown on Orkney. The HVAC circuit comprises of approximately 15km of land cable and 53km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Dounreay and Finstown. | 2031-09-30
Burghmuir BESS | PRO-004978 | CS-12286 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | Burghmuir 2 H1 works | 1. Provision of signals to the User for the purposes of Loss of Mains (LOM). 2. Installation of 2x 120 MVA 400/33 kV grid transformers, 2x33 kV metering circuit breakers and 33 kV disconnectors, at the new Burghmuir 2 400/33 kV GSP substation compound including all associated civil, cabling, metering, and protection works. | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12287 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12288 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12289 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12290 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12291 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12292 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12293 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12294 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12295 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12296 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-255 |  | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12297 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SHET-RI-311 Burghmuir 400kV Substation | Burghmuir 400kV Substation | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12298 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SPT-RI-004 Cable |  | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12299 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SPT-RI-004 OHL |  | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12300 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SPT-RI-004 SS |  | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12301 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SPT-RI-2073 Cable |  | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12302 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SPT-RI-2073 OHL |  | 2033-10-31
Burghmuir BESS | PRO-004978 | CS-12303 | YLEM Energy Limited | Burghmuir 2 400/33kV GSP | SPT-RI-2073 SS |  | 2033-10-31
Burwell (Tertiary) | PRO-001109 | CS-04896 | PIVOTED POWER LLP | Burwell Main 400kV Substation | 10756-201150 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install Disconnecting Circuit Breaker (DCB) at the 13kV side connecting tertiary to connection assets for Users connection. | 2029-06-30
Burwell BESS | PRO-003869 | CS-11473 | O&G Solar (SPV 38) Limited | Burwell South 400kV Substation | 102489-205075 |  | 2034-10-30
Burwell BESS | PRO-003869 | CS-11474 | O&G Solar (SPV 38) Limited | Burwell South 400kV Substation | 102489-205076 |  | 2034-10-30
Burwell BESS | PRO-003869 | CS-11475 | O&G Solar (SPV 38) Limited | Burwell South 400kV Substation | 102514-205113 |  | 2034-10-30
Burwell BESS | PRO-003869 | CS-11476 | O&G Solar (SPV 38) Limited | Burwell South 400kV Substation | 102639-205306 |  | 2034-10-30
Bushbury | PRO-003409 | CS-10249 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 101909-203901 | Reconductor the Ironbridge-Rugeley 400kV circuit with 2x620mm² conductor to achieve a pre-fault summer rating of 2490 MVA. | 2037-10-30
Bushbury | PRO-003409 | CS-10250 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 102914-206353 |  | 2037-10-30
Bushbury | PRO-003409 | CS-10251 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 102915-206326 |  | 2037-10-30
Bushbury | PRO-003409 | CS-10252 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 102916-206327 |  | 2037-10-30
Bushbury | PRO-003409 | CS-10253 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 102917-206328 |  | 2037-10-30
Bushbury | PRO-003409 | CS-10254 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 102918-206329 |  | 2037-10-30
Bushbury | PRO-003409 | CS-10255 | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation | 102939-206348 |  | 2037-10-30
Bushbury Green Energy Centre | PRO-001907 | CS-07126 | BUSHBURY GREEN NG LIMITED | Bushbury 275kV Substation | 101730-203440 | Extend Bushbury 275kV Mesh Corner Busbars for the provision of one User Bay | 2028-10-30
Bushbury Green Energy Centre | PRO-001907 | CS-07127 | BUSHBURY GREEN NG LIMITED | Bushbury 275kV Substation | 101731-203442 | Uprating/replacing Bishops wood-Penn-1 circuit to increase capacity above 1000MVA. | 2028-10-30
Bushbury Green Energy Centre | PRO-001907 | CS-07128 | BUSHBURY GREEN NG LIMITED | Bushbury 275kV Substation | 101732-203443 | Uprating/replacing Bushbury - Willenhall-1 circuit to increase capacity above 1000MVA | 2028-10-30
Bushbury GSP | PRO-003018 | CS-12120 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 101909-203901 | Reconductor the Ironbridge-Rugeley 400kV circuit with 2x620mm² conductor to achieve a pre-fault summer rating of 2490 MVA. | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12121 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 102914-206353 Ex1 |  | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12122 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 102915-206326 Ex1 |  | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12123 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 102916-206327 Ex1 |  | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12124 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 102917-206328 Ex1 |  | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12125 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 102918-206329 EX(0) |  | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12126 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 103103-206521 |  | 2037-10-31
Bushbury GSP | PRO-003018 | CS-12127 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node A 400kV Substation | 103104-206522 |  | 2037-10-31
Cairds Hill | PRO-001382 | CS-06651 | EDP RENEWABLES UK LIMITED | Keith 1 132/33kV GSP Substation | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2026-10-01
Cairds Hill | PRO-001382 | CS-06652 | EDP RENEWABLES UK LIMITED | Keith 1 132/33kV GSP Substation | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 2026-10-01
Cairds Hill | PRO-001382 | CS-06653 | EDP RENEWABLES UK LIMITED | Keith 1 132/33kV GSP Substation | Keith - Intertrip facilities | Item 1 - 1. Install intertrip facilities at Keith 132/33kV GSP substation and provide the status of both grid transformers to a new intertripping panel within the 33kV switchroom at Keith substation. The works will include provision of signals from the National Electricity Transmission System to the Host Distribution Network Operator. The intertrip will operate whenever GT1 or GT3 at Keith 132/33kV GSP substation are unavailable due to planned or unplanned outage conditions, reducing the export of Edintore II Wind Farm to 0MW. | 2026-10-01
Cairds Hill | PRO-001382 | CS-06654 | EDP RENEWABLES UK LIMITED | Keith 1 132/33kV GSP Substation | Intertrip scheme to reduce flow | Item 2 - 2. The Host Distribution Network Operator will install an intertrip scheme that will reduce the power flow from Edintore II to 0MW within 120ms upon receipt of an intertrip signal from the Relevant Transmission Licensee. | 2026-10-01
Cairn Duhie Wind Farm | PRO-001743 | CS-06904 | Renewable Energy Systems Limited | Berryburn 275/33kV GSP Substation | SHET-RI-175 | Berryburn 275kV Overhead Line Work | 2027-10-31
Cairn Duhie Wind Farm | PRO-001743 | CS-06905 | Renewable Energy Systems Limited | Berryburn 275/33kV GSP Substation | Cairn Duhie - Switch Bay | Between the new Tee in point and the new 275/33kV GT, install a new 275kV transformer breaker and associated disconnector switch. | 2027-10-31
Cairnbulg BESS | PRO-003961 | CS-12460 | Balance Power Projects Limited | Fraserburgh 132 kV | Cairnbulg BESS - Sole Enabling Works | Installation of 2x new 132kV double busbar switch bays at St Fergus 132kV substation, where each bay shall comprise of 2x 132kV busbar selection switches, 1x 132kV circuit breaker, 1x 132kV line disconnector and any associated protection equipment. Approximately 15km of 132kV double circuit overhead line and 2x 0.5km 132kV cable sections will be required as part of this connection between the proposed location for St Fergus 132kV substation and Fraserburgh 2 132/33kV GSP substation. Installation of a 132kV circuit breaker and 132kV disconnector at the new Fraserburgh 2 132/33kV GSP substation, including the 132kV cabling and works to connect the 132/33kV 120MVA grid transformers. | 2033-10-31
Cairnbulg BESS | PRO-003961 | CS-12462 | Balance Power Projects Limited | Fraserburgh 132 kV | SHET-RI-187 St Fergus 132kV Substation |  | 2033-10-31
Cairnbulg BESS | PRO-003961 | CS-12463 | Balance Power Projects Limited | Fraserburgh 132 kV | SHET-RI-188 St Fergus to New Deer 2 132kV Reinforcement |  | 2033-10-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05526 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05527 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05528 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05529 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05530 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05531 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05532 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2028-05-31
Cairnmore Hill Wind Farm | PRO-001304 | CS-05533 | Cairnmore Hill Energy Limited | Thurso South 132/33kV GSP Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2028-05-31
Cairnstone Estate Solar Wind and Storage | PRO-004746 | CS-11421 | BSR APPLICATIONS LIMITED | Strichen 2 132/33kV Grid Supply Point Substation | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 2033-10-31
Cairnstone Estate Solar Wind and Storage | PRO-004746 | CS-11422 | BSR APPLICATIONS LIMITED | Strichen 2 132/33kV Grid Supply Point Substation | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 2033-10-31
Cairntawie | PRO-004498 | CS-11714 | WIND 2 LIMITED | St Fergus Gas GSP | SHET-RI-150 | Inverguie Tee – Peterhead 132kV Reconductoring – Reconductor approximately 6.7km of 132kV OHL between the Inverguie Tee and Peterhead 132kV substation. The circuit should be reconductored with a conductor capable of a minimum summer pre-fault rating of 226MVA | 2033-10-31
Cairntawie | PRO-004498 | CS-11715 | WIND 2 LIMITED | St Fergus Gas GSP | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Cairntawie | PRO-004498 | CS-11716 | WIND 2 LIMITED | St Fergus Gas GSP | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 2033-10-31
Cairntawie | PRO-004498 | CS-11717 | WIND 2 LIMITED | St Fergus Gas GSP | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Caithness Energy Storage | PRO-004933 | CS-11680 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11681 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11682 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11683 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11684 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11685 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11686 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11687 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11688 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-291a | Thurso South 400kV Substation - Construction of a new 400kV Thurso South Substation, with a double circuit Overhead line connecting to the new Spittal 2 400kV Substation. This TORI has initially been raised ahead of the outcome of HND FUE as part of a holding offer for an application. As such it will likely be subject to change in order to align with the requirements of HND FUE | 2034-10-31
Caithness Energy Storage | PRO-004933 | CS-11689 | BAYWA R.E. UK LIMITED | CAITHNESS ENERGY STORAGE 400KV SUBSTATION | SHET-RI-291b | Thurso - Spittal 400kV double circuit OHL- Install 02 400kV bays at 400kV Thurso substation complete with one circuit breaker, two busbar selector switches and one line isolator. Install 02 400kV bays at 400kV Spittal substation complete with one circuit breaker, two busbar selector switches and one line isolator. Install approximately 12 km of double circuit OHL between these two substations originating and terminating on these bays | 2034-10-31
Calderdale Wind Farm 312MW | PRO-004714 | CS-10882 | CALDERDALE WIND FARM LTD | Leeds North Connection Node B 400kV Substation | 101508-202973 (1) |  | 2035-10-30
Calderdale Wind Farm 312MW | PRO-004714 | CS-10883 | CALDERDALE WIND FARM LTD | Leeds North Connection Node B 400kV Substation | 101661-203312 (1) |  | 2035-10-30
Calderdale Wind Farm 312MW | PRO-004714 | CS-10884 | CALDERDALE WIND FARM LTD | Leeds North Connection Node B 400kV Substation | 103205-206631 2 |  | 2035-10-30
Calderdale Wind Farm 312MW | PRO-004714 | CS-10885 | CALDERDALE WIND FARM LTD | Leeds North Connection Node B 400kV Substation | 103755-207408 |  | 2035-10-30
Callisterhall Wind Farm | PRO-001965 | CS-07498 | E Power Limited | Callisterhall 132kV | Calisterhall Item 1 | At Gretna 132kV substation, install a new 132kV AIS outdoor switchbay. | 2029-04-27
Callisterhall Wind Farm | PRO-001965 | CS-07499 | E Power Limited | Callisterhall 132kV | Callisterhall Item 2 | Install a 132kV cable section to go round the north of the substation and establish a cable sealing end. | 2029-04-27
Callisterhall Wind Farm | PRO-001965 | CS-07500 | E Power Limited | Callisterhall 132kV | Callisterhall Item 3 | Install ~15.5km of 132kV circuit (wood pole OHL) to Callisterhall wind farm site. At the wind farm site, install one 132kV line disconnector. | 2029-04-27
Callisterhall Wind Farm | PRO-001965 | CS-07501 | E Power Limited | Callisterhall 132kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2029-04-27
Callisterhall Wind Farm | PRO-001965 | CS-07502 | E Power Limited | Callisterhall 132kV | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 2029-04-27
Callisterhall Wind Farm | PRO-001965 | CS-07503 | E Power Limited | Callisterhall 132kV | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 2029-04-27
Calon y Gwynt | PRO-004896 | CS-12089 | Wind 2 Project 3 Limited | Mid Wales Connection Node A | 102004-204152 |  | 2037-10-31
Calon y Gwynt | PRO-004896 | CS-12090 | Wind 2 Project 3 Limited | Mid Wales Connection Node A | 103944-207819 (I) |  | 2037-10-31
Calon y Gwynt | PRO-004896 | CS-12091 | Wind 2 Project 3 Limited | Mid Wales Connection Node A | 104224-208203 |  | 2037-10-31
Camblesforth GSP (Yorkshire) | PRO-002792 | CS-08443 | Northern Powergrid (Yorkshire) Plc | Camblesforth 66kV Substation | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2035-10-30
Camblesforth GSP (Yorkshire) | PRO-002792 | CS-12379 | Northern Powergrid (Yorkshire) Plc | Camblesforth 66kV Substation | 100452-201017 Eskamhorn Farm |  | 2035-10-30
Camblesforth GSP (Yorkshire) | PRO-002792 | CS-12380 | Northern Powergrid (Yorkshire) Plc | Camblesforth 66kV Substation | 100452-201222 Eskamhorn Farm |  | 2035-10-30
Camblesforth GSP (Yorkshire) | PRO-002792 | CS-12381 | Northern Powergrid (Yorkshire) Plc | Camblesforth 66kV Substation | 102356-204777 Eskamhorn Farm |  | 2035-10-30
Camblesforth GSP (Yorkshire) | PRO-002792 | CS-12382 | Northern Powergrid (Yorkshire) Plc | Camblesforth 66kV Substation | 103165-206584 Eskamhorn Farm |  | 2035-10-30
Camp Farm | PRO-004990 | CS-11643 | CHINT SOLAR UK MANAGEMENT LTD | Derbyshire Connection Node B 400kV Substation | 102490-205078 2 |  | 2037-10-30
Camp Farm | PRO-004990 | CS-11644 | CHINT SOLAR UK MANAGEMENT LTD | Derbyshire Connection Node B 400kV Substation | 102897-206308 2 |  | 2037-10-30
Camp Farm | PRO-004990 | CS-11645 | CHINT SOLAR UK MANAGEMENT LTD | Derbyshire Connection Node B 400kV Substation | 102898-206309 |  | 2037-10-30
Camp Farm | PRO-004990 | CS-11646 | CHINT SOLAR UK MANAGEMENT LTD | Derbyshire Connection Node B 400kV Substation | 102899-206310 2 |  | 2037-10-30
Camp Farm | PRO-004990 | CS-11647 | CHINT SOLAR UK MANAGEMENT LTD | Derbyshire Connection Node B 400kV Substation | 102900-206311 |  | 2037-10-30
Camp Farm | PRO-004990 | CS-11648 | CHINT SOLAR UK MANAGEMENT LTD | Derbyshire Connection Node B 400kV Substation | 104256-208270 |  | 2037-10-30
Camster 2 Wind Farm | PRO-000963 | CS-05535 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2024-10-31
Camster 2 Wind Farm | PRO-000963 | CS-05536 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | Camster 2 Wind Farm | 1. Install 2 x 132kV transformer circuit breaker bays connected off the Mybster 132kV busbar extension, complete with protection and associated auxiliary equipment. 2. At Mybster 132/33kV substation, the Relevant Transmission Licensee shall replace the existing 2 x 30MVA and 1 x 60MVA 132/33kV transformers with higher rated twin 120MVA 132/33kV transformers within the same substation accommodation. The works will include all associated plinth foundations, transformer protection equipment, and 33kV cabling work associated with the two replacement 120MVA transformers. | 2024-10-31
Camster 2 Wind Farm | PRO-000963 | CS-05537 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-032b | Spittal – Mybster 132kV Reinforcement — This consists of a new higher capacity 132kV OHL and substation works between Spittal and Mybster substation. (SHET-RI-032b) | 2024-10-31
Camster 2 Wind Farm | PRO-000963 | CS-05538 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2024-10-31
Camster 2 Wind Farm | PRO-000963 | CS-05539 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2024-10-31
Camster 2 Wind Farm | PRO-000963 | CS-05540 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2024-10-31
Canterbury North | PRO-001216 | CS-05541 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | Thermal overload relief work. | Thermal overload relief work. | 2021-12-01
Canterbury North | PRO-001216 | CS-05542 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-11642 | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating. | 2021-12-01
Canterbury North | PRO-001216 | CS-05543 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-21588 | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity. | 2021-12-01
Canterbury North | PRO-001216 | CS-05544 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-30967 & NGET-RI-30968 | Construction of a new Sellindge double busbar bypass 400kV Substation. | 2021-12-01
Canterbury North | PRO-001216 | CS-05545 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works. | 2021-12-01
Canterbury North | PRO-003414 | CS-10258 | Canterbury North 10 Renewables Limited | East Kent Connection Node B 400kV Substation | 103499-206976 |  | 2030-10-31
Canterbury North | PRO-003414 | CS-10259 | Canterbury North 10 Renewables Limited | East Kent Connection Node B 400kV Substation | 103499-206977 |  | 2030-10-31
Canterbury Tertiary | PRO-001029 | CS-04914 | ENSO GREEN HOLDINGS L LIMITED | Canterbury North 400kV Substation | 100918-201842 | 1. Install a tertiary cable box or bushings on SGT2 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer 3. Install an earthing transformer 4. Install 13kV Disconnector at the 13kV side connection the tertiary to the Connection Assets. 5. Extension of the Sellindge OTS to include Richborough Energy Park. | 2031-10-31
Canterbury Tertiary | PRO-001029 | CS-04915 | ENSO GREEN HOLDINGS L LIMITED | Canterbury North 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2031-10-31
Canterbury Tertiary | PRO-001029 | CS-04916 | ENSO GREEN HOLDINGS L LIMITED | Canterbury North 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2031-10-31
Canterbury Tertiary | PRO-001029 | CS-04917 | ENSO GREEN HOLDINGS L LIMITED | Canterbury North 400kV Substation | 3187 | 1. Thermal reinforcement to the South Coast, New offshore HVDC link between Suffolk and Kent | 2031-10-31
Caorach | PRO-005026 | CS-11798 | Invenergy Development UK Ltd | Caorach 132 KV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2033-10-31
Caorach | PRO-005026 | CS-11799 | Invenergy Development UK Ltd | Caorach 132 KV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
Caorach | PRO-005026 | CS-11800 | Invenergy Development UK Ltd | Caorach 132 KV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2033-10-31
Caorach | PRO-005026 | CS-11801 | Invenergy Development UK Ltd | Caorach 132 KV Substation | SHET-RI-230 | Loch Buidhe – Dalchork 132 kV Reinforcement- Construction of approximately 17 km 132 kV double circuit between Dalchork - Loch Buidhe substations with same rating OHLs as of existing double circuit i.e. 414 MVA post fault summer ratings. Scope also includes construction of two feeder bays each at Dalchork substation and Loch Buidhe substation | 2033-10-31
Capenhurst GSP | PRO-002949 | CS-12176 | SP MANWEB PLC | Cheshire Connection Node E | 103875-207682 |  | 2037-10-30
Capenhurst GSP | PRO-002949 | CS-12177 | SP MANWEB PLC | Cheshire Connection Node E | 103875-207683 |  | 2037-10-30
Capenhurst GSP | PRO-002949 | CS-12178 | SP MANWEB PLC | Cheshire Connection Node E | 104250-208256 Badgers Energy - 1 |  | 2037-10-30
Capenhurst Tertiary | PRO-002162 | CS-08911 | ENSO GREEN HOLDINGS Q LIMITED | Capenhurst 400kV Substation | 101960-204081 | - Extension of Capenhurst 275KV busbars to make provision for the connection of user. - Replace L45,H40,W10,W20 Breakers at Capenhurst 275kV substation. | 2029-10-30
Capenhurst Tertiary Connection | PRO-001028 | CS-04919 | HD888CAP LIMITED | Capenhurst 275kV Substation | 100533-201152 | 1. Install a tertiary cable box or bushings on SGT2B 2. Install a 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2023-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09187 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-213 | Installation of a new 275kV disconnector switch (L17) at Car Duibh 275kV substation, connecting the new 275kV metering circuit breaker (L10) to a 275kV busbar constructed under the new TORI SHET-RI-213. Car Duibh 275kV Substation and OHL Works - Construction of the new Car Duibh 275kV substation and a 275kV 5km double circuit tower line, connecting into the proposed Creag Dhubh - An Suidhe - Craig Murrail 275kV double circuit tower line in a "turn in" arrangement. This construction arrangement will turn this into a Creag Dhubh - Car Duibh - An Suidhe - Craig Murrail 275kV circuit. (SHET-RI-213) | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09188 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09189 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09190 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-077 | 3rd Subsea Cable Link Kintyre – Hunterston Reinforcement - Establish a third 240MVA 220kV subsea cable circuits between the 132kV substation at Crossaig and the existing 400kV busbar at Hunterston (SPT will make this connection and provide any necessary infrastructure at Hunterston). | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09191 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09192 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09193 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09194 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Car Duibh Wind Farm | PRO-002342 | CS-09195 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bi-pole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 2034-10-31
Carlincraig Wind | PRO-000583 | CS-06640 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2023-09-30
Carlincraig Wind | PRO-000583 | CS-06641 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 2023-09-30
Carlincraig Wind | PRO-000583 | CS-06642 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2023-09-30
Carlincraig Wind | PRO-000583 | CS-06643 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2023-09-30
Carn Fearna Wind Farm | PRO-002231 | CS-08144 | Carn Fearna Wind Farm Limited | Carn Fearna Wind Farm 132/33kV Substation | Carn Fearna Wind Farm H1 SS | 1. Allowance to extend the Corriemoillie Substation 132kV busbars and install a new 132kV feeder bay comprising a line disconnector, a feeder circuit breaker and two busbar selector disconnectors. 2. Construction of 9.4km of single 132kV OHL from the User’s site to Corriemoillie 132kV Substation. 3. Installation of an indoor type 132kV line disconnector within a building at the User’s substation. 4. Associated secondary equipment including protection of the new equipment. | 2030-06-30
Carn Fearna Wind Farm | PRO-002231 | CS-08145 | Carn Fearna Wind Farm Limited | Carn Fearna Wind Farm 132/33kV Substation | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 2030-06-30
Carn Fearna Wind Farm | PRO-002231 | CS-08146 | Carn Fearna Wind Farm Limited | Carn Fearna Wind Farm 132/33kV Substation | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 2030-06-30
Carradale 2 GSP | PRO-003337 | CS-12472 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-013 North Argyll (Ardbrecknish Substation) |  | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12473 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12474 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-086 Craig Murrail Switching Station |  | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12475 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-107 North Argyll - Inveraray Reinforcement |  | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12476 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-130a North Argyll - Craig Murrail 275kV Operation |  | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12477 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-130b Craig Murrail - Crossaig 275kV Operation |  | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12478 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-158 Twin Carradale –KilmarnockSouth subsea cable |  | 2034-10-31
Carradale 2 GSP | PRO-003337 | CS-12479 | Scottish Hydro Electric Power Distribution Plc | Carradale 2 132/33kV GSP Substation | SHET-RI-197 Kintyre to North Wales HVDC Link |  | 2034-10-31
Carrick Wind Farm | PRO-001026 | CS-05549 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | SPT-RI-293 | Carrick 275kV Substation - A new 275kV substation will be installed on the Coylton-Mark Hill 275kV circuit (YY route) approximately 25km northeast of Mark Hill substation. The YY route will be turned in to the new substation with a 275kV circuit breaker on each circuit. The new circuit breakers will maintain the single-phase high-speed auto reclose capability which currently exists on the YY route. (SPT-RI-293) | 2030-04-01
Carrick Wind Farm | PRO-001026 | CS-05550 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2030-04-01
Carrick Wind Farm | PRO-001026 | CS-05551 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2030-04-01
Carrick Wind Farm | PRO-001026 | CS-06676 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | Carrick - H1 Substation | Installation of one 275kV disconnector at Carrick substation. | 2030-04-01
Carrington | PRO-000276 | CS-06104 | Carrington Storage Limited | Carrington 400KV Substation | 33285 | Re-conductor the Carrington to Daines 4 circuit (~2km) with 2 x 620mm² GZTACSR gap-type conductor at 170°C. | 2026-10-30
Carrington | PRO-000276 | CS-06105 | Carrington Storage Limited | Carrington 400KV Substation | 21619 - 11 | Associated substation works for the turn-in including the Penwortham and Daines feeder bays and GIB runs to connect the Penwortham - Daines circuit (ZQ route) to the new 400kV substation. | 2026-10-30
Carrington | PRO-000276 | CS-06106 | Carrington Storage Limited | Carrington 400KV Substation | 21619 - 2 | OHL turn in the Penwortham - Daines circuit into existing Carrington substation. | 2026-10-30
Carrington | PRO-000276 | CS-06107 | Carrington Storage Limited | Carrington 400KV Substation | 33285L | Rephasing of the Carrington - Penwortham circuit. | 2026-10-30
Carrington | PRO-000276 | CS-06108 | Carrington Storage Limited | Carrington 400KV Substation | 21619-1 | Extend the 400kV GIS double busbar substation at Carrington. | 2026-10-30
Carrington | PRO-000276 | CS-06109 | Carrington Storage Limited | Carrington 400KV Substation | 21619-1S | Advance civil works at Carrington substation for Wainstones. | 2026-10-30
Carrington | PRO-000276 | CS-06110 | Carrington Storage Limited | Carrington 400KV Substation | 33285O | Build one skeletal GIS bays for connection of the generation. | 2026-10-30
Carrington | PRO-000276 | CS-06111 | Carrington Storage Limited | Carrington 400KV Substation | 33285S | Scheme Description Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. | 2026-10-30
Carrington GSP (SP Manweb) | PRO-002950 | CS-12361 | SP MANWEB PLC | Carrington GSP (SP Manweb) | 103751-207404 |  | 2037-10-30
Carrington GSP (SP Manweb) | PRO-002950 | CS-12362 | SP MANWEB PLC | Carrington GSP (SP Manweb) | 103069-206486 |  | 2037-10-30
Carrington GSP (SP Manweb) | PRO-002950 | CS-12372 | SP MANWEB PLC | Carrington GSP (SP Manweb) | 103258-206695 |  | 2037-10-30
Carsebank PV | PRO-001169 | CS-06246 | Scottish Hydro Electric Power Distribution Plc | Lunanhead GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2021-11-30
Carseview Road BESS | PRO-003169 | CS-12410 | Vital Energi Solutions Limited | Lunanhead 2 GSP | SHET-RI-315 |  | 2032-10-31
Castlemilk 1 | PRO-003932 | CS-09678 | Queequeg Renewables Ltd | Castlemilk 400kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Castlemilk 1 | PRO-003932 | CS-09679 | Queequeg Renewables Ltd | Castlemilk 400kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Cathkin Energy Storage | PRO-001925 | CS-07166 | CATHKIN ENERGY STORAGE LIMITED | East Kilbride 275/33kV GSP | Cathkin - Bus section reactor & two new 33kV 3-panel switchboards | At East Kilbride GSP, a bus section reactor (30 MVA) shall be installed alongside two new 33kV 3-panel switchboards. | 2024-07-31
Cellarhead | PRO-002161 | CS-08827 | ENSO GREEN HOLDINGS X LIMITED | Cellarhead 400kV Substation | 101976-204101 | At Cellarhead 400 kV substation, busbar extension to create the required space for the User generator bay. | 2033-10-31
Cellarhead 400kV Energy Storage | PRO-001685 | CS-04345 | C & S ENERGY LIMITED | Cellarhead 400kV Substation | 101346-202666 | Extension of the existing Cellarhead 400kV substation busbars to accommodate the User’s bay | 2027-07-16
Cellarhead 400kV Energy Storage | PRO-001685 | CS-04921 | C & S ENERGY LIMITED | Cellarhead 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-07-16
Cellarhead 400kV Energy Storage | PRO-001685 | CS-04922 | C & S ENERGY LIMITED | Cellarhead 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-07-16
Cellarhead Green Energy Centre | PRO-001758 | CS-04738 | S & C ENERGY LIMITED | Cellarhead 400kV Substation | 101357-202677 | Extension of the existing Cellarhead 400kV substation busbars to accommodate the User’s bay | 2028-10-30
Cellarhead Green Energy Centre | PRO-001758 | CS-04923 | S & C ENERGY LIMITED | Cellarhead 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Cellarhead Green Energy Centre | PRO-001758 | CS-04924 | S & C ENERGY LIMITED | Cellarhead 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Cellarhead GSP | PRO-002990 | CS-12644 | National Grid Electricity Distribution (West Midlands) Plc | Manchester South Connection Node B 400kV Substation | 101474-202916 Port Ham |  | 2027-03-31
Cellarhead GSP | PRO-002990 | CS-12645 | National Grid Electricity Distribution (West Midlands) Plc | Manchester South Connection Node B 400kV Substation | 103615-207149 Port Ham |  | 2027-03-31
Cellarhead GSP (SP Manweb) | PRO-001332 | CS-12110 | SP MANWEB PLC | Cellarhead GSP (SP Manweb) | 103296-206735 Maw Green Solar |  | 2037-10-31
Cellarhead GSP (SP Manweb) | PRO-001332 | CS-12111 | SP MANWEB PLC | Cellarhead GSP (SP Manweb) | 103298-206737 |  | 2037-10-31
Cellarhead GSP (SP Manweb) | PRO-001332 | CS-12112 | SP MANWEB PLC | Cellarhead GSP (SP Manweb) | 104384-208491 Maw Green Solar |  | 2037-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07931 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 102053-204223 | Infrastructure works for the generation connection of ESB Celtic Sea Offshore Wind farm | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07932 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07933 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07934 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07935 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07936 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07937 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07938 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07939 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101733-203445 | Extension of the South West OTS to incorporate offshore windfarm | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07940 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101619-203253 | Reconductoring of the Landulph – Langage 2 circuit to achieve a post-fault Summer rating of 2150MVA. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07941 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07942 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07943 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07944 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07945 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07946 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2031-10-31
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07947 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-10-31
CENOS | PRO-001847 | CS-07374 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101699-203398 |  | 2035-10-31
CENOS | PRO-001847 | CS-07375 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101702-203404 |  | 2035-10-31
CENOS | PRO-001847 | CS-07376 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101702-203405 |  | 2035-10-31
CENOS | PRO-001847 | CS-07377 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2035-10-31
CENOS | PRO-001847 | CS-07378 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101699-203399 |  | 2035-10-31
CENOS | PRO-001847 | CS-07379 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2035-10-31
CENOS | PRO-001847 | CS-07380 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101707-203410 |  | 2035-10-31
CENOS | PRO-001847 | CS-07381 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2035-10-31
CENOS | PRO-001847 | CS-07382 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2035-10-31
CENOS | PRO-001847 | CS-07383 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2035-10-31
CENOS | PRO-001847 | CS-07384 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2035-10-31
CENOS | PRO-001847 | CS-07385 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 100481-201052 |  | 2035-10-31
CENOS | PRO-001847 | CS-07386 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2035-10-31
CENOS | PRO-001847 | CS-07387 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101705-203408 | Reconductor the Norton - Lackenby 400kV circuit and uprate the substation cable at the Lackenby substation. | 2035-10-31
CENOS | PRO-001847 | CS-07388 | FLOTATION ENERGY LIMITED | Peterhead 400kV Substation | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm² Araucaria conductor | 2035-10-31
Cerulean Winds INTOG 1 | PRO-004330 | CS-11060 | CERULEAN WINDS LIMITED | Hurlie 400kV substation | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Cerulean Winds INTOG 1 | PRO-004330 | CS-11061 | CERULEAN WINDS LIMITED | Hurlie 400kV substation | INTOG 1 - 2x 400kV AIS Switch Bay |  | 2033-10-31
Challoch Solar Farm | PRO-003041 | CS-09463 | SP Distribution plc | Newton Stewart GSP | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 2028-08-01
Challoch Solar Farm | PRO-003041 | CS-09464 | SP Distribution plc | Newton Stewart GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2028-08-01
Challoch Solar Farm | PRO-003041 | CS-09465 | SP Distribution plc | Newton Stewart GSP | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2028-08-01
Challoch Solar Farm | PRO-003041 | CS-09466 | SP Distribution plc | Newton Stewart GSP | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2028-08-01
Challoch Solar Farm | PRO-003041 | CS-09467 | SP Distribution plc | Newton Stewart GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2028-08-01
Chalmerston Windfarm | PRO-004057 | CS-09766 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | Chalmerston Windfarm H1 works | 1. At the proposed New Cumnock North 400/275kV substation, install a 275kV GIS bay and associated equipment, a new 275/132kV 120MVA SGT and a 132kV disconnector. 2. Install ~6km of 132kV circuit (OHL is anticipated) to the User’s site. 3. At the User’s site, install one 132kV disconnector. | 2033-10-31
Chalmerston Windfarm | PRO-004057 | CS-09767 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-231 |  | 2033-10-31
Chalmerston Windfarm | PRO-004057 | CS-09768 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2033-10-31
Chalmerston Windfarm | PRO-004057 | CS-09769 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2033-10-31
Chalmerston Windfarm | PRO-004057 | CS-09770 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-3309 | New Cumnock North 400kV GIS substation- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new 400kV substation in the vicinity of the existing New Cumnock 275kV substation. This shall be a double busbar GIS ‘New Cumnock North’ 400kV substation. This new substation shall facilitate the development of the NOA WCNC scheme (currently under review) | 2033-10-31
Chalmerston Windfarm | PRO-004057 | CS-09771 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 2033-10-31
Chapelcross Solar PV and Storage | PRO-002031 | CS-08207 | EEB68 LIMITED | Chapelcross 132/33kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2027-10-29
Chapelcross Solar PV and Storage | PRO-002031 | CS-08208 | EEB68 LIMITED | Chapelcross 132/33kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2027-10-29
Chapelcross Solar PV and Storage | PRO-002031 | CS-08209 | EEB68 LIMITED | Chapelcross 132/33kV | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 2027-10-29
Chapelcross Solar PV and Storage | PRO-002031 | CS-08210 | EEB68 LIMITED | Chapelcross 132/33kV | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 2027-10-29
Chesters | PRO-004805 | CS-10783 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-1738 OHL |  | 2033-10-29
Chesters | PRO-004805 | CS-10784 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-1738 SS |  | 2033-10-29
Chesters | PRO-004805 | CS-10785 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-2709 Cable |  | 2033-10-29
Chesters | PRO-004805 | CS-10786 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-2709 OHL |  | 2033-10-29
Chesters | PRO-004805 | CS-10787 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-2378 SS |  | 2033-10-29
Chesters | PRO-004805 | CS-10788 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-3829 OHL |  | 2033-10-29
Chesters | PRO-004805 | CS-10789 | Queequeg Renewables Ltd | Teviot 400/132kV Substation | SPT-RI-3829 SS |  | 2033-10-29
Chickerell Solar PV & BESS | PRO-001598 | CS-05264 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 101485-202932 | Installation of new circuit breaker to control MSC2 to maintain the substation operability | 2027-10-01
Chickerell Solar PV & BESS | PRO-001598 | CS-05265 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 2027-10-01
Chickerell Solar PV & BESS | PRO-001598 | CS-05266 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2027-10-01
Chickerell Solar PV & BESS | PRO-001598 | CS-05267 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2027-10-01
Chickerell Solar PV & BESS | PRO-001598 | CS-05268 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2027-10-01
Chickerell Solar PV & BESS | PRO-001598 | CS-05269 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2027-10-01
Chickerell Solar PV & BESS | PRO-001598 | CS-05270 | CHICKERELL STORAGE LIMITED | Chickerell 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2027-10-01
Chirk iDNO | PRO-001588 | CS-04742 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2029-10-31
Chirk iDNO | PRO-001588 | CS-04743 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2029-10-31
Chirk iDNO | PRO-001588 | CS-04744 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2029-10-31
Chirk iDNO | PRO-001588 | CS-04745 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2029-10-31
Chirmorie Wind Farm | PRO-000094 | CS-04259 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-10-09
Chirmorie Wind Farm | PRO-000094 | CS-05556 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-205 | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | 2026-10-09
Chirmorie Wind Farm | PRO-000094 | CS-05557 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-206 | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | 2026-10-09
Chirmorie Wind Farm | PRO-000094 | CS-05559 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-136 | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation. | 2026-10-09
Chirmorie Wind Farm | PRO-000094 | CS-05560 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2026-10-09
Chirmorie Wind Farm | PRO-000094 | CS-05561 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2026-10-09
Chirmorie Wind Farm | PRO-000094 | CS-06664 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-301 | Mark Hill to Arecleoch Ext Tee 132kV Circuit | 2026-10-09
Chleansaid Wind Farm | PRO-001608 | CS-04471 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | Chleansaid WF - H1 Works | Installation of indoor type line disconnector | 2027-07-31
Chleansaid Wind Farm | PRO-001608 | CS-04472 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 2027-07-31
Chleansaid Wind Farm | PRO-001608 | CS-04473 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2027-07-31
Chleansaid Wind Farm | PRO-001608 | CS-04474 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | SHET-RI-133 Loch Buidhe SGT Upgrade | At Loch Buidhe substation remove the existing two 275/132kV 240MVA SGTs, replace with two new 275/132kV 480MVA SGTs and upgrade the 132kV switchboard | 2027-07-31
Cilfynydd Grid Stability Services | PRO-002540 | CS-08442 | CILFYNYDD GRID SERVICES LIMITED | Cilfynydd 400kV Substation | 102342-204504 | Reserved extension of Cilfynydd 400kV substation to provide space for the reserved pathfinder bay | 2025-07-31
Cilfynydd Grid Stability Services | PRO-002540 | CS-12279 | CILFYNYDD GRID SERVICES LIMITED | Cilfynydd 400kV Substation | 102342-208181 |  | 2025-07-31
Clachaig Glen Wind Farm | PRO-000878 | CS-05562 | RWE Renewables UK Onshore Wind Limited | Carradale 2 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2025-04-30
Clachaig Glen Wind Farm | PRO-000878 | CS-05563 | RWE Renewables UK Onshore Wind Limited | Carradale 2 GSP | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2025-04-30
Clachaig Glen Wind Farm | PRO-000878 | CS-05564 | RWE Renewables UK Onshore Wind Limited | Carradale 2 GSP | SHET-RI-113 | Kintyre-Hunterston Subsea Cable Intertrip Scheme — Between Crossaig substation and Carradale GSP install an intertrip scheme which will monitor the two 220kV Crossaig – Hunterston subsea cables. Following the loss of both subsea cables (N-2) an intertrip signal will be sent to applicable users to switch out. | 2025-04-30
Clash Gour | PRO-001022 | CS-05565 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 3 | On Circuit UH2, it is proposed to install 1 x 275kV line disconnector on the Blackhillock side of the transformer tee, 1 x 275kV line circuit breaker and 1 x 275kV line disconnector on the Knocknagael side of the transformer tee and transformer bay disconnector. | 2029-10-30
Clash Gour | PRO-001022 | CS-05566 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 1 | Two new 275kV Towers will be constructed from the Knocknagael – Blackhillock 275kV double circuit tower line (UH2/CA1) to facilitate the installation of two 275kV tappings from circuit UH2 and circuit CA1, which will include down droppers connecting onto new 275kV switchgear located within the substation compound at the Clash Gour 275/132kV Substation. | 2029-10-30
Clash Gour | PRO-001022 | CS-05567 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 4 | The installation of two 180/360MVA 275/132kV Transformers, associated HV and LV circuit breaker and the creation of a single 132kV busbar including a 132kV bus section circuit breaker. | 2029-10-30
Clash Gour | PRO-001022 | CS-05568 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 2 | On Circuit CA1, it is proposed to install 1 x 275kV line disconnector on the Knocknagael side of the transformer tee, 1 x 275kV line disconnectors and 1 x 275kV line circuit breaker on the Blackhillock side of the transformer tee and transformer bay disconnector | 2029-10-30
Clashindarroch 2 | PRO-000041 | CS-05569 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2026-08-31
Clashindarroch 2 | PRO-000041 | CS-05570 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2026-08-31
Clashindarroch 2 | PRO-000041 | CS-05571 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-025d | North East Reinforcement | 2026-08-31
Clashindarroch 2 | PRO-000041 | CS-05572 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2026-08-31
Clauchrie Windfarm | PRO-001021 | CS-05575 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132/33KV Substation | SPT-RI-282 | Markhill SGT4 | 2033-05-31
Clauchrie Windfarm | PRO-001021 | CS-05576 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132/33KV Substation | Clauchrie H1 OHL/Cable | Installation of approximately 4km of 132kV underground cable or OHL circut between Mark Hill 132kV Substation and Clauchrie 132/33kV Substation. | 2033-05-31
Clauchrie Windfarm | PRO-001021 | CS-05577 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132/33KV Substation | Clauchrie H1 SS | At Mark Hill Substation install a new 132kV switch bay and associated equipment and apparatus | 2033-05-31
Clauchrie Windfarm | PRO-001021 | CS-08434 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132/33KV Substation | Clauchrie WF H1 Isolator | At Clauchrie Wind Farm 132/33kV Substation, install one 132kV line isolator. | 2033-05-31
Clauchrie Windfarm | PRO-001021 | CS-08435 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132/33KV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2033-05-31
Clauchrie Windfarm | PRO-001021 | CS-08436 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132/33KV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2033-05-31
Cleveden Road BESS | PRO-003174 | CS-09940 | Vital Energi Solutions Limited | Killermont 132/33kV | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-06-30
Cleveden Road BESS | PRO-003174 | CS-09941 | Vital Energi Solutions Limited | Killermont 132/33kV | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2031-06-30
Cleveden Road BESS | PRO-003174 | CS-09942 | Vital Energi Solutions Limited | Killermont 132/33kV | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 2031-06-30
Cleveden Road BESS | PRO-003174 | CS-09943 | Vital Energi Solutions Limited | Killermont 132/33kV | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 2031-06-30
Cloich Forest Wind Farm | PRO-001387 | CS-06665 | EDF ENERGY RENEWABLES LIMITED | Cloich 132kV Substation | Cloich Forest H1 Works | 1. Installation of a new 132kV double busbar GIS bay at Currie 132kV substation. 2. Installation of a cable/OHL circuit from Currie 132kV substation to Cloich Forest Wind Farm substation (~25km). 3. Installation of a 132kV line disconnector at Cloich Forest Wind Farm substation. 4. Associated civil, miscellaneous and minor works. 5. Associated protection and control works. 6. Provision of communications, alarms, indications and metering from the User site | 2029-07-31
Cloiche Wind Farm | PRO-000425 | CS-05578 | SSE Generation Limited | Cloich 132kV Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 2028-02-01
Cloiche Wind Farm | PRO-000425 | CS-05579 | SSE Generation Limited | Cloich 132kV Substation | SHET-RI-085a | 2. Melgarve 400/132kV SGT1 – Install a new 400/132kV 480MVA transformer (SGT1) at a new site (Melgarve). This is in order to allow the connection of wind generation in the area. (SHET-RI-085a) | 2028-02-01
Cloiche Wind Farm | PRO-000425 | CS-05580 | SSE Generation Limited | Cloich 132kV Substation | SHET-RI-115 | Melgarve 400-132kV Substation Additional SGTs – At Melgarve substation (established under SHET-RI-085a and SHET-RI-085b), install an additional two 480MVA SGTs to enable the connection of wind generation in the area | 2028-02-01
Cloiche Wind Farm | PRO-000425 | CS-05581 | SSE Generation Limited | Cloich 132kV Substation | SHET-RI-085b | 3. Melgarve 400/132kV Substation – Establish a new 400/132 kV Substation at Melgarve, to allow the connection of wind generation in the area. (SHET-RI-085b) | 2028-02-01
Cloiche Wind Farm | PRO-000425 | CS-05582 | SSE Generation Limited | Cloich 132kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2028-02-01
Cloiche Wind Farm | PRO-000425 | CS-05583 | SSE Generation Limited | Cloich 132kV Substation | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 2028-02-01
Cloud Hill Windfarm | PRO-001938 | CS-07326 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | Cloud Hill - Indoor GIS switchgear and disconnectors |  | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-07327 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | Cloud Hill - OHL & cable circuit |  | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-07328 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | Cloud Hill - 132kV Disconnector |  | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-07329 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-07330 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-07331 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-12140 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-12141 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-12142 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-2862 OHL |  | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-12143 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2030-05-31
Cloud Hill Windfarm | PRO-001938 | CS-12144 | Cloud Hill Windfarm Limited | Glenglass 132/33kV | SPT-RI-3498 - Glenmuckloch 400kV - Dumfries North 400kV | Under the NOA7 Refresh the need was identified to develop a new west coast onshore high?capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. This project is driven by the continued increase in required transfers seen across this boundary due to the need to connect renewable generation in Scotland to achieve UK and Government’s net zero target by 2050 and 2045 respectively. To facilitate generation applications in this area it is proposed to utilise this new west coast onshore corridor. The TORI shall construct a new 400kV double circuit between the proposed Glenmuckloch 400kV substation (established under SPT-RI-236) and the proposed Dumfries North 400kV substation (established under SPT-RI-2862). It is proposed to string both sides of the 400kV corridor with 3x700mm² Araucaria AAAC conductor provisionally rated at 750°C with the capability to uprate the operating temperature to 900°C. | 2030-05-31
Clune Wind Farm | PRO-004620 | CS-11890 | Renewable Energy Systems Limited | Clune 132/33 kV Substation | SHET-RI-177 | 3. Tomatin Additional SGTs - Install a new 275kV indoor GIS double busbar and two additional 275/132kV Super Grid Transformers at the Tomatin 275/132kV Substation | 2030-04-30
Clune Wind Farm | PRO-004620 | CS-11905 | Renewable Energy Systems Limited | Clune 132/33 kV Substation | Clune WF Circuit H1 |  | 2030-04-30
Clune Wind Farm | PRO-004620 | CS-11906 | Renewable Energy Systems Limited | Clune 132/33 kV Substation | Clune WF Switch Bay H1 |  | 2030-04-30
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04593 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | BPUWL 12 Item 1 | The construction of approximately 15 kilometres of 132kV overhead line (12.5km will be wood pole trident line the other 2.5km will be NETS structures) connecting between Crossaig/Carradale overhead line and the Cnoc Buidhe substation. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04594 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | BPUWL 12 Item 2 | At Cnoc Buidhe substation there will be 3x 132kV CB bays installed and a 132kV Disconnector | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04595 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | BPUWL 12 Item 3 | The T point into the RC 2 circuit will comprise of a 132kV bay (1x 132kV Disconnector and 1x 132kV Circuit Breaker). This will be within a compound constructed for the connection | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04596 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-013 and SPT-RI-028 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existing Inveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. Reconfigure Dalmally 275kV substation to a double busbar arrangement to allow the extension of the substation to develop new bays for the connection of renewable generation. (SHET-RI-013 and SPT-RI-028) | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04597 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04598 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04599 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04600 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04601 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04602 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-07983 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-07984 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-07985 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | Cnoc Buidhe Item 4 | Installation of a new 132kV double busbar circuit breaker bay on the new 132kV double busbar to be located at the new Carradale 132kV substation, installed as part of the TORI SHET-RI-158. This will replace the assets required at the T Point onto the RC2 circuit. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-07986 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2030-04-02
Cnoc Buidhe Wind Farm | PRO-001672 | CS-07987 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-077 | 3rd Subsea Cable Link Kintyre – Hunterston Reinforcement - Establish a third 240MVA 220kV subsea cable circuits between the 132kV substation at Crossaig and the existing 400kV busbar at Hunterston (SPT will make this connection and provide any necessary infrastructure at Hunterston). | 2030-04-02
Cnoc Morail Wind Farm | PRO-004212 | CS-10574 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2030-10-30
Cnoc Morail Wind Farm | PRO-004212 | CS-10575 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2030-10-30
Cnoc Morail Wind Farm | PRO-004212 | CS-10576 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-088 Loch Buidhe - Dounreay 275KV Reinforcement |  | 2030-10-30
Cnoc Morail Wind Farm | PRO-004212 | CS-10577 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-140 - Thurso South 275kV Substation Redevelopment |  | 2030-10-30
Cnoc Morail Wind Farm | PRO-004212 | CS-10578 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2030-10-30
Cnoc Morail Wind Farm | PRO-004212 | CS-10579 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2030-10-30
Cnoc Morail Wind Farm | PRO-004212 | CS-10580 | QAIR RENEWABLES UK LIMITED | Mybster 132/33kV Substation | SHET-RI-200 - Loch Buidhe 400-275kV Substation |  | 2030-10-30
Coachford 400MW BESS | PRO-005097 | CS-11729 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11730 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025a Peterhead - Rothienorman 400kV OHL Upgrade |  | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11731 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11732 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025c Peterhead 400kV Busbar |  | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11733 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11734 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11735 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11736 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11737 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11738 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11739 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11740 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11741 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHET-RI-199) | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11742 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11743 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Coachford 400MW BESS | PRO-005097 | CS-11744 | Field Woodhead Ltd | Blackhillock 2 400/33kV GSP Substation | shet-ri-330 | Extend 400kV double busbar to form 3-section busbar, with space provision for a minimum of two additional bays, at Coachford 400kV Substation. | 2033-10-31
Coalburn Battery Energy Storage Facility | PRO-001459 | CS-06655 | ALCEMI STORAGE DEVELOPMENTS 4 LIMITED | Coalburn 400kV Substation | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 2025-10-31
Coalburn Battery Energy Storage Facility | PRO-001459 | CS-06656 | ALCEMI STORAGE DEVELOPMENTS 4 LIMITED | Coalburn 400kV Substation | Alcemi Coalburn 1 (H1) | 1. Installation of a new 400kV double busbar bay at Coalburn including a 400kV circuit breaker and associated equipment. 2. Installation of a new 400kV cable circuit (approx. 2.5km) between Coalburn 400kV substation and the User’s site. 3. Installation of a 400kV line disconnector at the User’s site. | 2025-10-31
Cockenzie BESS | PRO-004217 | CS-09390 | COCKENZIE STORAGE B LTD | Cockenzie 400/132kV | SPT-RI-2907 | Cockenzie 400/132kV Substation - A new 400/132kV substation will be installed via a tee-off with ZA route (No.2 circuit ZA001A Tower). A new 400kV disconnector circuit breaker will be installed at the new substation, along with a 360MVA 400/132kV Super grid transformer. A new 132kV busbar will be established | 2026-07-31
Cockenzie BESS | PRO-004217 | CS-09391 | COCKENZIE STORAGE B LTD | Cockenzie 400/132kV | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 2026-07-31
Cockenzie BESS | PRO-004217 | CS-09392 | COCKENZIE STORAGE B LTD | Cockenzie 400/132kV | Cockenzie BESS Disconnector | Installation of a 132kV disconnector at Cockenzie 400/132kV Substation | 2026-07-31
Cockenzie GSP | PRO-003128 | CS-11640 | SP Distribution plc | Cockenzie 275/33kV | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742)
Cogle Moss Wind Farm | PRO-000973 | CS-06210 | COGLE MOSS RENEWABLES LLP | Mybster 2 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2025-08-31
Cogle Moss Wind Farm | PRO-000973 | CS-06211 | COGLE MOSS RENEWABLES LLP | Mybster 2 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2025-08-31
Cogle Moss Wind Farm | PRO-000973 | CS-06212 | COGLE MOSS RENEWABLES LLP | Mybster 2 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2025-08-31
Coille Beith Wind Farm | PRO-002711 | CS-09277 | COILLE BEITH WIND FARM LIMITED | Oykel Wind Farm 132kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2032-10-31
Coille Beith Wind Farm | PRO-002711 | CS-09278 | COILLE BEITH WIND FARM LIMITED | Oykel Wind Farm 132kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2032-10-31
Coille Beith Wind Farm | PRO-002711 | CS-09279 | COILLE BEITH WIND FARM LIMITED | Oykel Wind Farm 132kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2032-10-31
Coille Beith Wind Farm | PRO-002711 | CS-09280 | COILLE BEITH WIND FARM LIMITED | Oykel Wind Farm 132kV Substation | SHET-RI-230 | Loch Buidhe – Dalchork 132 kV Reinforcement- Construction of approximately 17 km 132 kV double circuit between Dalchork - Loch Buidhe substations with same rating OHLs as of existing double circuit i.e. 414 MVA post fault summer ratings. Scope also includes construction of two feeder bays each at Dalchork substation and Loch Buidhe substation | 2032-10-31
Coille Beith Wind Farm | PRO-002711 | CS-09281 | COILLE BEITH WIND FARM LIMITED | Oykel Wind Farm 132kV Substation | Disconnector - Oykel WF | Installation of a new 132kV line disconnector at User’s site at Oykel Wind Farm 132kV substation. The line disconnector will connect to the incoming 500m 132kV underground cable connected to the 23km 132kV overhead line trident wood pole line coming from Dalchork substation | 2032-10-31
Coille Beith Wind Farm | PRO-002711 | CS-09282 | COILLE BEITH WIND FARM LIMITED | Oykel Wind Farm 132kV Substation | OHL - Oykel WF | The 132kV OHL will be connected to Dalchork substation via a new fully equipped 132kV double busbar feeder bay, comprising 132kV line disconnector, 132kV feeder circuit breaker and 132kV double busbar selection disconnectors and associated protection equipment. | 2032-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-05584 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | Coire Glas Pumped Storage H1 Works Item 2 | Construction of approximately 13km of double circuit 400kV steel tower line from Invergarry to the connection site. | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-05585 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | Coire Glas Pumped Storage H1 Works Item 1 | Installation of 400kV GIS double busbar arrangement and associated bus section circuit breakers/isolators at the connection site. | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-05586 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-068 | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-05587 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-05588 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-06231 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-06232 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-06233 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SPT-RI-003 | Denny-Strathaven 400kV Reinforcement - Construct a new 400kV double circuit overhead line from Bon-nybridge to Newarthill and re-configure associated sites to establish a fourth north to south dou-ble circuit Supergrid route through the Scottish central belt. One side of the new overhead line will oper-ate at 400kV, the other at 275kV. This reinforcement will establish Denny-Bonnybridge, Bonnybridge-Wishaw, Wishaw-Strathaven No.2 and Wishaw-Torness 400kV circuits and a Denny-Newarthill-Easterhouse 275kV circuit. (SPT-RI-003) | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-06234 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 2029-10-31
Coire Glas Pumped Storage | PRO-000073 | CS-06235 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 2029-10-31
Coldstream Solar PV Plant | PRO-003635 | CS-12232 | Conrad Energy (Developments) II Limited | Eccles GSP | SPT-RI-151b Galashiels to Eccles 132kV Cable |  | 2031-07-31
Coldstream Solar PV Plant | PRO-003635 | CS-12233 | Conrad Energy (Developments) II Limited | Eccles GSP | SPT-RI-151b Galashiels to Eccles 132kV OHL |  | 2031-07-31
Coldstream Solar PV Plant | PRO-003635 | CS-12234 | Conrad Energy (Developments) II Limited | Eccles GSP | SPT-RI-3660 |  | 2031-07-31
Cordon Farm BESS | PRO-005011 | CS-10177 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10178 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10179 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10180 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10181 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10182 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10183 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10184 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10185 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10186 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-255 |  | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10187 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 2033-10-31
Cordon Farm BESS | PRO-005011 | CS-10188 | ELGIN ENERGY ES CO LIMITED | Abernethy GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2033-10-31
Cormoran Offshore Wind Farm | PRO-002390 | CS-08156 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 102365-204795 | Infrastructure works for the generation connection of Cormoran Offshore wind farm. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08157 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08158 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08159 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08160 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08161 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08162 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08163 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Cormoran Offshore Wind Farm | PRO-002390 | CS-08164 | South West Wind Holdco Limited | Alverdiscott 400kV Substation |  |  | 2036-12-06
Cornabo Wind | PRO-000659 | CS-03695 | Scottish Hydro Electric Power Distribution Plc | Tarland GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2026-10-31
Cornabo Wind | PRO-000659 | CS-03696 | Scottish Hydro Electric Power Distribution Plc | Tarland GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2026-10-31
Cornharrow Wind Farm | PRO-001741 | CS-08301 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2030-10-31
Cornharrow Wind Farm | PRO-001741 | CS-08302 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2030-10-31
Cornharrow Wind Farm | PRO-001741 | CS-08303 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2030-10-31
Cornharrow Wind Farm | PRO-001741 | CS-08304 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2030-10-31
Cornharrow Wind Farm | PRO-001741 | CS-08305 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-1507 | Holm Hill 132kV substation - At an appropriate point next to the DE route establish a 132kV substation (Holmhill 132kV substation) by teeing into the proposed future New Cumnock to Glenlee 132kV circuit. The substation will consist of a 132kV busbar to which wind farm circuits will connect to. | 2030-10-31
Cornharrow Wind Farm | PRO-001741 | CS-08306 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-2094 | Quantans Hill to Holmhill 132kV Circuit – At the proposed Quantans Hill wind farm site establish a 132kV substation and establish a 132kV busbar to which a 132kV line isolator is connected. Install around 6km of wood pole overhead line with HTLS conductor to connect Quantans Hill substation to Holmhill substation. At Holmhill substation install a 132kV circuit breaker to connect the OHL. | 2030-10-31
Cornharrow Wind Farm | PRO-001741 | CS-12525 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV Substation | SPT-RI-4427 | 4. Wether Hill Tee to Cornharrow 132kV Circuit and associated works - Install ~8.4km of 132kV trident wood pole overhead line with UPAS AAAC conductor (75°C, minimum summer pre-fault rating 176MVA) between Quantans Hill 132kV substation and the proposed tee connection to Cornharrow substation. This overhead line circuit shall be shared by Cornharrow wind farm and Wether Hill Wind Farm. The overhead line circuit shall include an associated 132kV circuit breaker and disconnectors at Quantans Hill 132kV bus bar. At the tee location of the Wether Hill Tee to Cornharrow, establish a 33kV substation and provide a 33kV cable circuit to the indoor two-panel 33kV (metering) switchboard at the customer substation where the customer interface to SPT electrical network is provided. (SPT-RI-4427) | 2030-10-31
Cornwall Energy Park | PRO-002379 | CS-08755 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 102351-204521 | Replacement, or modification, of existing towers and associated OHL works to facilitate a full turn in of the Indian Queens - Landulph #2 (A87B) overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL turn-in and the Users Generator Bay. Local works to facilitate the extension of the Operational Tripping Scheme | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08756 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08757 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101619-203253 | Reconductoring of the Landulph – Langage 2 circuit to achieve a post-fault Summer rating of 2150MVA. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08758 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 100480-201051 | Uprate the cable section of the Seabank -Whitson section of the three-ended Seabank -Whitson - Cilfynydd circuit to a pre-fault rating of 1800MVA | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08759 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08760 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08761 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08762 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101498-202953 | Uprate the double circuits between the Exeter, Axminster & Chickerell substations by reconductoring the 4 x 400mm² Zebra conductor sections with 3 x 700mm² Araucaria conductor at 75°C and hotwiring the existing 3 x 700mm² Araucaria conductor sections at 50°C to 75°C to achieve a pre-fault summer rating of 2790MVA. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08763 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08764 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101833-203761 | Uprate the Chickerell - Mannington double circuit (NASP Code: A851 and A830) by hotwiring the existing 3 x 700mm² Araucaria conductor at 50°C to 90°C to achieve a pre-fault summer rating of 3160MVA | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08765 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08766 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08767 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08768 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101500-202956 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 2 in order to achieve a summer post fault rating of 2850MVA | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08769 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 2036-12-06
Cornwall Energy Park | PRO-002379 | CS-08770 | GREEN ENERGY MAB LTD | Tideford 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Corriegarth 2 Wind Farm | PRO-000420 | CS-05589 | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation | SHET-RI-129 | Farigaig SGT1 Upgrade - Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT, to facilitate the connection of generation in the area. | 2027-07-31
Corriegarth 2 Wind Farm | PRO-000420 | CS-05590 | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation | SHET-RI-089 | Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT to facilitate the connection of generation in the area. | 2027-07-31
Corriegarth 2 Wind Farm | PRO-000420 | CS-06886 | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation | 132kV Disconnector, Trident Line and Cable | From a tee point on the existing Farigaig to Corriegarth 132kV circuit, install a new wood pole overhead line consisting of 3 wood pole structures. This is terminated onto a new 1km section of 132kV underground cable terminating on a new 132kV disconnector (103) within the Corriegarth 2 Wind Farm substation. | 2027-07-31
Corriemoillie BESS | PRO-003992 | CS-09528 | FIELD CORRIEMOILLIE LTD | Corriemoillie 132kV Substation | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 2029-09-30
Corriemoillie BESS | PRO-003992 | CS-09529 | FIELD CORRIEMOILLIE LTD | Corriemoillie 132kV Substation | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 2029-09-30
Cottam | PRO-001502 | CS-04931 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101080-202165 | 1. At Cottam 400kV Substation, extend Main bar 1 and Reserve bar 1/2 to make provision for the User to connect their generator bay (also needs to include site extension) | 2029-10-31
Cottam | PRO-001502 | CS-04932 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2029-10-31
Cottam | PRO-001502 | CS-04933 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2029-10-31
Cottam | PRO-001502 | CS-04934 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101263-202505 | 1. Hotwire 2x620mm² sections of Grendon – Staythorpe circuit to standard operating temperature (170°C) | 2029-10-31
Cottam | PRO-001502 | CS-04935 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2029-10-31
Cottam | PRO-001502 | CS-04936 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2029-10-31
Cottam | PRO-001502 | CS-04937 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2029-10-31
Cottam | PRO-001502 | CS-04938 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm² conductor and uprate the cable section to 3 cores per phase | 2029-10-31
Cottam | PRO-001502 | CS-04939 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2029-10-31
Cottam | PRO-001502 | CS-04940 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2029-10-31
Cottam | PRO-001502 | CS-04941 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2029-10-31
Cottam | PRO-001502 | CS-04942 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2029-10-31
Cottam | PRO-001502 | CS-04943 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2029-10-31
Cottam | PRO-001502 | CS-04944 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101101-202200 | 1. Uprate the Bicker Fen – Walpole, Bicker Fen – Spalding North & Spalding North – Walpole 400kV circuit by reconductoring the 2 x redwood conductor sections to AAAC conductor | 2029-10-31
Cottam | PRO-001502 | CS-04945 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 03305-03305 | 1. Reconductor the 2x400 mm² sections of the Elstree – Sundon circuits with 2x570mm² conductor | 2029-10-31
Cottam | PRO-001502 | CS-04946 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101264-202506 | Cottam-Ryhall reconductoring with 3820MVA post-fault rating during Winter | 2029-10-31
Cottam | PRO-001502 | CS-04947 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101262-202504 | 1. Installation of a power electronics-based power flow control device at Creyke Beck | 2029-10-31
Cottam | PRO-001502 | CS-04948 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101266-202508 | 1. Hotwire the 4x400mm² sections of the Sundon – Wymondley circuit to 75°C | 2029-10-31
Cottam | PRO-001502 | CS-04949 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation |  |  | 2029-10-31
Cottam Solar PV + BESS | PRO-001401 | CS-04730 | COTTAM SOLAR PROJECT LIMITED | Cottam 400kV Substation | 101100- 202198 | Provision of a spare skeletal bay at Cottam 400kV Substation (ex-generator 1 bay). | 2029-09-01
Cottam-Ryhall Solar & BESS | PRO-004100 | CS-11321 | TYLER HILL CONSULTING LIMITED | Trent Valley South Connection Node B 400kV Substation. | 103562-207066 |  | 2034-10-31
Cottam-Ryhall Solar & BESS | PRO-004100 | CS-11322 | TYLER HILL CONSULTING LIMITED | Trent Valley South Connection Node B 400kV Substation. | 104202-208156 |  | 2034-10-31
Cottered | PRO-002173 | CS-07795 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 102003-204155 | 1. Construction of a new 400kV AIS double busbar 400kV substation (Cottered) between Pelham 400kV and Wymondely 400kV substations, comprising a busbar coupler, 2 feeder bays and Users generator bay | 2030-10-30
Cottered | PRO-002173 | CS-07796 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 102003-204147 | 2. Provide a single turn in of the 400kV OHL between Pelham & Wymondely (A602) to the new 400kV (Cottered) substation | 2030-10-30
Cottered | PRO-002173 | CS-07797 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2030-10-30
Cottered | PRO-002173 | CS-07798 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2030-10-30
Cottered | PRO-002173 | CS-07799 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 102011-204165 | 3. At Norwich Main 400kV: Replace circuit breakers X320, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2030-10-30
Cottered | PRO-002173 | CS-07800 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 102012-204166 | 4. At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2030-10-30
Cottered | PRO-002173 | CS-07801 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2030-10-30
Cottered | PRO-002173 | CS-07802 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2030-10-30
Cottered | PRO-002173 | CS-07803 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2030-10-30
Cottered | PRO-002173 | CS-07804 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2030-10-30
Cottered | PRO-002173 | CS-07805 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 2030-10-30
Cottered | PRO-002173 | CS-07806 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2030-10-30
Cottered | PRO-002173 | CS-07807 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2030-10-30
Cottered | PRO-002173 | CS-07808 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2030-10-30
Cottered | PRO-002173 | CS-07809 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2030-10-30
Cottered | PRO-002173 | CS-07810 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 2030-10-30
Cottered | PRO-002173 | CS-07811 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2030-10-30
Cottered | PRO-002173 | CS-07812 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2030-10-30
Cottered | PRO-002173 | CS-07813 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2030-10-30
Cottered | PRO-002173 | CS-07814 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2030-10-30
Cottered | PRO-002173 | CS-07815 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2030-10-30
Cottered | PRO-002173 | CS-07816 | SSE COTTERED SOLAR LIMITED | West Anglia Connection Node D 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2030-10-30
Cottered - PVDP | PRO-003999 | CS-12001 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 101248-204325 (PDVP) |  | 2034-10-31
Cottered - PVDP | PRO-003999 | CS-12002 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 102003-204155 (Cottered) |  | 2034-10-31
Cottered - PVDP | PRO-003999 | CS-12003 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 102003-204147 (Cottered) |  | 2034-10-31
Cottered - PVDP | PRO-003999 | CS-12004 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 102492-205080 (PDVP) |  | 2034-10-31
Cottered - PVDP | PRO-003999 | CS-12005 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 103044-206460 |  | 2034-10-31
Cottered - PVDP | PRO-003999 | CS-12006 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 103154-206574 (PDVP) |  | 2034-10-31
Cottered - PVDP | PRO-003999 | CS-12007 | SolarNine Ltd | West Anglia Connection Node D 400kV Substation | 103633-207169 |  | 2034-10-31
Cowley (Tertiary) | PRO-000407 | CS-05597 | COWLEY BALDON GREEN LIMITED | Cowley 400kV Substation | 100641-201316 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer to DCB Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection Install an auto-close scheme on the section breakers at Cowley 132kV substation to allow a solid running arrangement to be automatically established post fault. | 2025-11-14
Cowley GSP | PRO-001420 | CS-12179 | Southern Electric Power Distribution Plc | Chiltern Connection Node C 132kV Substation | 102602-205224 | 1. New 400kV double busbar (M2/R2) Oakley substation to provide space for User’s generation connection bay in a strategic location between Cowley & East Claydon. (*Substation name, design and location subject to further engineering assessment during the Relevant Transmission Licensee option selection phase). 2. Build temporary overhead line to divert the Cowley – East Claydon 400kV transmission circuit to allow for turning in this circuit and to feed the new 400kV substation. Establish a single turn in connection between Cowley – East Claydon circuit to connect the new substation. 3. Extension of 400 kV busbars to connect user bay. | 2038-11-01
Cowley GSP | PRO-001420 | CS-12180 | Southern Electric Power Distribution Plc | Chiltern Connection Node C 132kV Substation | 104386-208495 |  | 2038-11-01
Cowley GSP Self Build | PRO-002829 | CS-12175 | Southern Electric Power Distribution Plc | Cowley GSP | 102797-205747 EX(14) |  | 2029-10-31
Coylton 275kV Greener Grid Park | PRO-001551 | CS-04304 | COYLTON ENERGY LIMITED | Coylton 275/132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-02-28
Coylton 275kV Greener Grid Park | PRO-001551 | CS-09433 | COYLTON ENERGY LIMITED | Coylton 275/132kV | Coylton 275kV H1 | At Coylton 275kV substation it is required to install a new 275kV disconnector | 2026-02-28
Coylton 275kV Greener Grid Park | PRO-001551 | CS-12413 | COYLTON ENERGY LIMITED | Coylton 275/132kV | SPT-RI-2876 | 3. West Coast Onshore Reinforcement (North Section) - This TORI shall construct a new Killoch 400kV substation to feed a new Killoch 275kV substation via three new 400/275kV SGT’s, diversion and 400kV uprating of the existing XY route between Kilmarnock South and the new Killoch 400kV substations and the 400kV uprating of the WA route between the new Killoch 400kV and New Cumnock North 400kV substations. | 2026-02-28
Coylton 275kV Greener Grid Park | PRO-001551 | CS-12414 | COYLTON ENERGY LIMITED | Coylton 275/132kV | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 2026-02-28
Coylton 275kV Greener Grid Park | PRO-001551 | CS-12415 | COYLTON ENERGY LIMITED | Coylton 275/132kV | SPT-RI-3566 | 1. Killoch 275kV Substation - Establish a new 275kV GIS double busbar system in the vicinity of Killoch 400kV (to be established under SPT-RI-2876) that includes the following: • 1 x 275kV bus coupler • 1 x 275kV bus section • 3 x 275kV feeder bays for connecting to the LV side of the Killoch 400/275kV SGTs • 2 x 275kV feeder bays to connect to Coylton 275kV • Allow space for future connections | 2026-02-28
Coylton Farm | PRO-004230 | CS-09902 | NEW ENERGY PARTNERSHIP LIMITED | Coylton 275/33kV Substation | SPT-RI-3566 | 1. Killoch 275kV Substation - Establish a new 275kV GIS double busbar system in the vicinity of Killoch 400kV (to be established under SPT-RI-2876) that includes the following: • 1 x 275kV bus coupler • 1 x 275kV bus section • 3 x 275kV feeder bays for connecting to the LV side of the Killoch 400/275kV SGTs • 2 x 275kV feeder bays to connect to Coylton 275kV • Allow space for future connections | 2037-10-30
Coylton Farm | PRO-004230 | CS-09903 | NEW ENERGY PARTNERSHIP LIMITED | Coylton 275/33kV Substation | SPT-RI-3567 | 2. Killoch 400/275kV SGT Load Management Scheme - It is proposed to install a LMS at Killoch 275kV to continually monitor the loading of the established SGT1, SGT2 and SGT3. In order to prevent unacceptable overloading of any primary transmission equipment, a trip signal shall be issued to applicable generators as required when sites are in export mode, import mode or both import and export mode of operation. | 2037-10-30
Coylton Farm | PRO-004230 | CS-09904 | NEW ENERGY PARTNERSHIP LIMITED | Coylton 275/33kV Substation | SPT-RI-2876 | 3. West Coast Onshore Reinforcement (North Section) - This TORI shall construct a new Killoch 400kV substation to feed a new Killoch 275kV substation via three new 400/275kV SGT’s, diversion and 400kV uprating of the existing XY route between Kilmarnock South and the new Killoch 400kV substations and the 400kV uprating of the WA route between the new Killoch 400kV and New Cumnock North 400kV substations. | 2037-10-30
Coylton Farm | PRO-004230 | CS-09905 | NEW ENERGY PARTNERSHIP LIMITED | Coylton 275/33kV Substation | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 2037-10-30
Craig Watch Wind Farm | PRO-001877 | CS-05436 | Craig Watch Wind Farm Limited | CRAIG WATCH WIND FARM 132KV SUBSTATION | SHET-RI-176 | Pauls Hill/Glenfarclas Circuit Turn In - Move the existing open point from Keith 132kV Substation to Pauls Hill substation and then turn in the Pauls Hill/Glenfarclas circuit to Blackhillock 132kV Substation andrebuild the circuit from Blackhillock substation to Craig watch Substation. This will include the Tee connection onto the existing circuit. (SHET-RI-176 | 2031-05-15
Craig Watch Wind Farm | PRO-001877 | CS-05437 | Craig Watch Wind Farm Limited | CRAIG WATCH WIND FARM 132KV SUBSTATION | SHET-RI-079 (a & b) | Blackhillock Additional SGTs- Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. The SGTs will be connected to the existing 275kV AIS double busbar and 132kV GIS double busbar at Blackhillock. Two new 275kV AIS transformer circuit breaker bays and two new GIS transformer circuit breaker bays will also be required (SHET-RI-079 (a & b)). | 2031-05-15
Craig Watch Wind Farm | PRO-001877 | CS-05438 | Craig Watch Wind Farm Limited | CRAIG WATCH WIND FARM 132KV SUBSTATION | 0 | 0 | 2031-05-15
Craigdarroch Hybrid Wind and BESS | PRO-005012 | CS-12670 | VOLTALIA UK LTD | Craigdarroch Hybrid Wind & BESS 132kV Substation | SPT-RI-2862 OHL |  | 2037-06-30
Craigdarroch Hybrid Wind and BESS | PRO-005012 | CS-12671 | VOLTALIA UK LTD | Craigdarroch Hybrid Wind & BESS 132kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2037-06-30
Craigdarroch Hybrid Wind and BESS | PRO-005012 | CS-12672 | VOLTALIA UK LTD | Craigdarroch Hybrid Wind & BESS 132kV Substation | SPT-RI-3657 OHL |  | 2037-06-30
Craigdarroch Hybrid Wind and BESS | PRO-005012 | CS-12673 | VOLTALIA UK LTD | Craigdarroch Hybrid Wind & BESS 132kV Substation | SPT-RI-4125 | 8. Craigenputtlock 132kV ‘B’ board – In order to accommodate the connections within the South-West Scotland region, it is proposed to establish a 132kV ‘B’ board at the proposed Craigenputtlock 400/132kV substation in split from the 132kV ‘A’ board within the Craigenputtlock area (near Glenlee) that shall be connected to Dumfries North 400kV. (SPT-RI-4125). | 2037-06-30
Craigdarroch Hybrid Wind and BESS | PRO-005012 | CS-12674 | VOLTALIA UK LTD | Craigdarroch Hybrid Wind & BESS 132kV Substation | Craigdarroch H1s | • At Craigenputtlock install 1 x 132kV double busbar feeder bay. • Install 1 x 132kV OHL (minimum of 170MVA per circuit) to the user’s site. • Install 1 x 132kV line disconnector at Craigdarroch. • All associated protection and control works. • All associated environmental, civil works and miscellaneous works. | 2037-06-30
Craigiebuckler GSP | PRO-003384 | CS-12536 | Scottish Hydro Electric Power Distribution Plc | Craigiebuckler GSP | Craigiebuckler GSP- Sole Enabling Works |  | 2024-09-30
Craigiebuckler GSP | PRO-003384 | CS-12537 | Scottish Hydro Electric Power Distribution Plc | Craigiebuckler GSP | SHET-RI-278-New Craigiebuckler 132kV Substation |  | 2024-09-30
Craigiebuckler GSP | PRO-003384 | CS-12538 | Scottish Hydro Electric Power Distribution Plc | Craigiebuckler GSP | SHET-RI-231-Aberdeen 132kV Protection Works |  | 2024-09-30
Craigneil Wind Farm | PRO-004670 | CS-12093 | ESB ASSET DEVELOPMENT UK LIMITED | Fetteresso GSP | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2030-10-31
Craigo Glenskinno | PRO-004771 | CS-11563 | BSR APPLICATIONS LIMITED | Bridge of Dun 2 132/33kV Grid Supply Point Substation | SHET-RI-185 - TKUP - Kintore - Tealing 400 kV OHL |  | 2033-10-31
Craigo Glenskinno | PRO-004771 | CS-11564 | BSR APPLICATIONS LIMITED | Bridge of Dun 2 132/33kV Grid Supply Point Substation | SHET-RI-205 New Brechin 275kV Substation |  | 2033-10-31
Craigo Glenskinno | PRO-004771 | CS-11565 | BSR APPLICATIONS LIMITED | Bridge of Dun 2 132/33kV Grid Supply Point Substation | SHET-RI-319 |  | 2033-10-31
Cranwell Solar & BESS Farm | PRO-004952 | CS-11458 | TRIO POWER LIMITED | Trent Valley South Connection Node C 400kV Substation | 103342-206819 |  | 2034-10-30
Cranwell Solar & BESS Farm | PRO-004952 | CS-11459 | TRIO POWER LIMITED | Trent Valley South Connection Node C 400kV Substation | 104212-208183 |  | 2034-10-30
Creag Riabhach Wind Farm | PRO-000109 | CS-05599 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2027-07-31
Creag Riabhach Wind Farm | PRO-000109 | CS-05600 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2027-07-31
Creag Riabhach Wind Farm | PRO-000109 | CS-05601 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | Creag Riabhach item 1 | At the new Dalchork 132kV grid substation install a new 132kV double busbar feeder bay complete with 2 x 132kV busbar selection switches (304 and 306), 1 x 132kV circuit breaker (305), 1 x 132kV line disconnector (303) and associated protection equipment. | 2027-07-31
Creag Riabhach Wind Farm | PRO-000109 | CS-05602 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | Creag Riabhach Item 2 | Construct a new 22km 132kV radial circuit (comprising 20.6km of 132kV overhead wood pole line and 1.4km of 132kV underground cable) from Dalchork 132kV substation, terminating on a new 132kV line disconnector (203) installed at the Creag Riabhach 132kV substation location. | 2027-07-31
Creag Riabhach Wind Farm | PRO-000109 | CS-05603 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2027-07-31
Creag Riabhach Wind Farm | PRO-000109 | CS-05604 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 2027-07-31
Creag Riabhach Wind Farm | PRO-000109 | CS-05605 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2027-07-31
CREYKE BECK | PRO-001972 | CS-07572 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101890-203837 | Extend new Creyke Beck 400kV Substation to make provision for the connection of user bay | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07573 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07574 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07575 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07576 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07577 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07578 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 0333496-0333496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07579 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07580 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07581 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07582 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101593-101593 | Uprate the Cottam- Staythorpe circuit 1, to provide winter post fault rating of 3300MVA This includes the cable section. | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07583 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07584 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07585 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07586 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07587 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07588 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2033-05-31
CREYKE BECK | PRO-001972 | CS-07589 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101968-204091 | Turn-in of both Creyke Beck - Thornton 1 & 2 circuits into a new 400kV AIS double busbar substation (Creyke Beck North) with 4 OHL feeder bays, 2 bus coupler bays and 1 bus section bay | 2033-05-31
Creyke Beck Bulk PP | PRO-002712 | CS-08433 | Northern Powergrid (Yorkshire) Plc | Creyke Beck 132kV | 102675-205361 | Construct a new 400kV double busbar substation including all necessary works required to connect it to the Main Interconnected Transmission System. | 2034-10-30
Creyke Beck GSP (Yorkshire) | PRO-002972 | CS-12430 | Northern Powergrid (Yorkshire) Plc | North Humber Connection Node C 132kV Substation | 103340-206790 (EX5) |  | 2039-10-30
Creyke Beck GSP (Yorkshire) | PRO-002972 | CS-12435 | Northern Powergrid (Yorkshire) Plc | North Humber Connection Node C 132kV Substation | 104213-208186(EX5) |  | 2039-10-30
Crookston A & B GSP | PRO-003115 | CS-12675 | SP Distribution plc | Crookston 132/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2028-06-30
Crookston A & B GSP | PRO-003115 | CS-12676 | SP Distribution plc | Crookston 132/33kV | SPT-RI-3788 | 3. Neilston 132kV Uprate to 25kA fault rating | 2028-06-30
Crookston A & B GSP | PRO-003115 | CS-12677 | SP Distribution plc | Crookston 132/33kV | SPT-RI-4261 | Crookston GSP Voltage Control Scheme Upgrades | 2028-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12559 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12560 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12561 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12562 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12563 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12564 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12565 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | SHET-RI-219 Dounreay 2 Tee |  | 2031-06-30
Crosskirk Energy Storage | PRO-004444 | CS-12566 | THE ABBEY GROUP CAMBRIDGESHIRE LIMITED | Dounreay GSP | Crosskirk - Sole Enabling | The sole enabling works will include the installation of two 275kV circuit breaker and two 275kV disconnectors at the new Dounreay 2 275/33kV GSP substation compound, including works to connect the 275/33kV grid transformers | 2031-06-30
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08166 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08167 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-046 | Taynuilt – North Argyll Reinforcement - Reinforce the transmission network between Taynuilt and North Argyll substation (established as part of SHET-RI-013). Rebuild approximately 12.5km of existing 132kV double circuit steel tower line between Creag Dhubh and Taynuilt with a heavy duty 132kV | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08168 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08169 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08170 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08171 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08172 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08173 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bi-pole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08174 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-198 | Beinn Glass Tee 132kV Switching Station - Construct a new 132kV switching station at the site where the Beinn Glass 132kV circuit tees into the Taynuilt to Creag Dhubh 132kV tower line. At the new switching station, install a new 132kV line circuit breaker and associated disconnectors, protection panels, battery systems et | 2034-10-31
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08175 | VOLTALIA UK LTD | Taynuilt GSP | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2034-10-31
Cruachan Expansion | PRO-001889 | CS-06835 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-2321 | Cruachan to Dalmally 275kV circuits uprate - Uprate the overhead line circuits No.1 and No.2 between Cruachan and Dalmally 275kV substations (YX Route) by re-profiling of the existing conductors twin Totara from 39°C to 50°C will be required. (SPT-RI-2321) | 2030-10-31
Cruachan Expansion | PRO-001889 | CS-06836 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2030-10-31
Cruachan Expansion | PRO-001889 | CS-06837 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2030-10-31
Cruachan Expansion | PRO-001889 | CS-06838 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2030-10-31
Cruachan Expansion | PRO-001889 | CS-06839 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 2030-10-31
Cruachan Expansion | PRO-001889 | CS-10506 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-2462 | Cruachan – Dalmally Load Management Scheme - To accommodate a large volume of new renewable generation in the Argyll area whilst being able to operate the Cruachan – Dalmally – Creag Dhubh – Windyhill 275kV network in a safe and efficient manner, it is proposed to install a Load Management Scheme (LMS) at Cruachan and Dalmally 275kV substations to monitor the Dalmally – Inverarnan and Dalmally Creag Dhubh 275kV circuits such that if one circuit is out of service, a signal will be sent to appropriate generator(s) to constrain the (generation) export and (pumping demand) import to prevent any transmission circuits overloads.(SPT-RI-2462) | 2030-10-31
Cruachan U3&4 Replacement | PRO-000113 | CS-07568 | DRAX PUMPED STORAGE LIMITED | Cruachan 275kV Substation | SPT-RI-2321 | Cruachan to Dalmally 275kV circuits uprate - Uprate the overhead line circuits No.1 and No.2 between Cruachan and Dalmally 275kV substations (YX Route) by re-profiling of the existing conductors twin Totara from 39°C to 50°C will be required. (SPT-RI-2321) | 2027-06-01
Cruachan U3&4 Replacement | PRO-000113 | CS-07569 | DRAX PUMPED STORAGE LIMITED | Cruachan 275kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2027-06-01
Cryogenic Battery System (Synchronous) | PRO-000549 | CS-04951 | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation | 101012-202029 | 1. Modifications to the busbar protection scheme and SCS database changes at Carrington 400kV substation. | 2026-05-08
Cryogenic Battery System (Synchronous) | PRO-000549 | CS-04952 | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation | 033285-033285 | 1. Re-conductor the Carrington 400kV to Daines 400kV 4 circuit (~2km) with 2x 620mm² GZTACSR gap type conductor at 170ºC. 2. Installation of a System to Generator intertrip scheme. | 2026-05-08
Cryogenic Battery System (Synchronous) | PRO-000549 | CS-04953 | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation | 033285-033567 | Rephasing of the Carrington – Penwortham circuit. | 2026-05-08
Culham Storage | PRO-001946 | CS-07459 | CULHAM STORAGE LIMITED | Culham Jet 400kV Substation | 101839-203775 | Extension of the 400kV Busbar at Culham Jet 400kV Substation to allow for the connection of a new User bay | 2027-10-29
Culham Storage | PRO-001946 | CS-07460 | CULHAM STORAGE LIMITED | Culham Jet 400kV Substation | 101839-203776 | Connecting the 2nd circuit from Cowley to Didcot into Culham Jet 400kV substation | 2027-10-29
Culham Storage | PRO-001946 | CS-07461 | CULHAM STORAGE LIMITED | Culham Jet 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2027-10-29
Culraven Solar Farm | PRO-001294 | CS-04260 | SP Distribution plc | Tongland 132/11kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2027-08-26
Culraven Solar Farm | PRO-001294 | CS-04261 | SP Distribution plc | Tongland 132/11kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2027-08-26
Culraven Solar Farm | PRO-001294 | CS-04262 | SP Distribution plc | Tongland 132/11kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2027-08-26
Culraven Solar Farm | PRO-001294 | CS-04263 | SP Distribution plc | Tongland 132/11kV | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2027-08-26
Culraven Solar Farm | PRO-001294 | CS-04264 | SP Distribution plc | Tongland 132/11kV | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2027-08-26
Culraven Solar Farm | PRO-001294 | CS-04265 | SP Distribution plc | Tongland 132/11kV | SPT-RI-170 | Tongland 132/33kV GSP Reinforcement | 2027-08-26
Cumberhead West Wind Farm | PRO-000423 | CS-05620 | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead 33kV | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 2025-07-31
Cumberhead West Wind Farm | PRO-000423 | CS-05621 | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead 33kV | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 2025-07-31
Cumberhead West Wind Farm | PRO-000423 | CS-05622 | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead 33kV | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 2025-07-31
Daer Wind Farm | PRO-000565 | CS-04275 | RWE Renewables UK Onshore Wind Limited | Daer Wind Farm 132/33kV | SPT-RI-306 - Moffat 132kV Fault Level Mitigation Bus Section Circuit Breaker | Moffat 132kV substation existing compound extension to accommodate the connection of further generation into the site. The compound shall be extended with the existing 132kV busbars being extended into this area. The installation of a new 132kV bus section circuit breaker will be required in order to alleviate exceeding the fault level design limits at the site. | 2028-08-01
Daer Wind Farm | PRO-000565 | CS-04276 | RWE Renewables UK Onshore Wind Limited | Daer Wind Farm 132/33kV | Daer Wind Farm H1 Works 2 | Installation of a 12km 132kV circuit between Daer Wind Farm substation and Moffat 132kV substation. Indicative desktop studies show a 6km 132kV OHL circuit of trident construction using AAAC “Sycamore” conductor from the wind farm substation to a suitable termination point. From here a further 6km of 132kV underground cable will be installed to Moffat 132kV substation. | 2028-08-01
Daer Wind Farm | PRO-000565 | CS-04277 | RWE Renewables UK Onshore Wind Limited | Daer Wind Farm 132/33kV | Daer Wind Farm H1 Works 1 | Installation of a 132kV line disconnector at Daer Wind Farm substation | 2028-08-01
Daer Wind Farm | PRO-000565 | CS-04278 | RWE Renewables UK Onshore Wind Limited | Daer Wind Farm 132/33kV | SPT-RI-229 - Moffat SGT3 | A new 400/132kV 240MVA transformer, and associated 400kV and 132kV circuit breaker bays, shall be installed at Moffat 400/132kV substation to increase the available generation capacity at the 132kV substation. | 2028-08-01
Daer Wind Farm | PRO-000565 | CS-04279 | RWE Renewables UK Onshore Wind Limited | Daer Wind Farm 132/33kV | Daer Wind Farm H1 Works 3 | Daer Wind Farm 132kV Double busbar feeder bay at Moffat 132kV substation | 2028-08-01
Daines BESS | PRO-002050 | CS-07590 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101929-203942 | At Daines 400kV Substation 1. Extension of Main and Reserve busbar X to facilitate connection of Users generator circuit 2. Extension of the busbar protection scheme and database changes as required | 2028-10-27
Daines BESS | PRO-002050 | CS-07591 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101938-203973 | At Carrington 400kV: 1. Installation of a 2000MVA 80hm series reactor | 2028-10-27
Daines BESS | PRO-002050 | CS-07592 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 2028-10-27
Daines BESS | PRO-002050 | CS-07593 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2028-10-27
Daines BESS | PRO-002050 | CS-07594 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-27
Daines BESS | PRO-002050 | CS-07595 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101948-204012 | 1. Installation of a System to generator scheme to monitor transmission Routes between Daines to Drakelow, Connahs Quay to Ironbridge, and Ironbridge – Rugeley/Feckenham | 2028-10-27
Daines BESS | PRO-002050 | CS-07596 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2028-10-27
Daines BESS | PRO-002050 | CS-07597 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2028-10-27
Daines BESS | PRO-002050 | CS-07598 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-27
Daines BESS | PRO-002050 | CS-07599 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2028-10-27
Daines BESS | PRO-002050 | CS-07600 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2028-10-27
Daines BESS | PRO-002050 | CS-07601 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-27
Daines BESS | PRO-002050 | CS-07602 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-27
Daines BESS | PRO-002050 | CS-07603 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm² conductor | 2028-10-27
Daines BESS | PRO-002050 | CS-07604 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-27
Daines BESS | PRO-002050 | CS-07605 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 2028-10-27
Daines BESS | PRO-002050 | CS-07606 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2028-10-27
Daines BESS | PRO-002050 | CS-07607 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 100478-201049 | Reconductor the Drakelow-Willington East 400kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA | 2028-10-27
Daines BESS | PRO-002050 | CS-07608 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101939-203974 | Reconductor the Drakelow-Rugeley 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA | 2028-10-27
Daines BESS | PRO-002050 | CS-07609 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101943-203988 | 1. Hotwire the 2x500mm² conductor of the Drakelow – Ratcliffe on Soar 400kV circuit to an operating temperature of 90°C | 2028-10-27
Daines BESS | PRO-002050 | CS-07610 | SSE DAINES BESS LIMITED | Daines 400kV Substation | 101697-203383 | Hotwire the 2x400mm² conductor on the Bredbury – South Manchester circuits | 2028-10-27
Daines Green Energy Centre | PRO-001902 | CS-07129 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101727 - 203436 | Extend the Main and Reserve Busbar 1 to make provision for connection of generator bay (User Works). | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07130 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101683-203351 | Hotwire the 2x400mm² conductor on the Carrington – South 1 & 2 circuits to an operating temperature of 65°C | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07131 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07132 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07133 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07134 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07135 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07136 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2030-10-31
Daines Green Energy Centre | PRO-001902 | CS-07137 | DAINES GREEN NG LIMITED | Daines 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2030-10-31
Dalchork Farm - 2 | PRO-005081 | CS-12480 | QAIR RENEWABLES UK LIMITED | Lairg 2 132/33kV Grid Supply Point Substation | SHET-RI-058 Beauly - Loch Buidhe 275kV OHL Reinforcement |  | 2033-10-31
Dalchork Farm - 2 | PRO-005081 | CS-12481 | QAIR RENEWABLES UK LIMITED | Lairg 2 132/33kV Grid Supply Point Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
Dalchork Farm - 2 | PRO-005081 | CS-12482 | QAIR RENEWABLES UK LIMITED | Lairg 2 132/33kV Grid Supply Point Substation | SHET-RI-200 - Loch Buidhe 400-275kV Substation |  | 2033-10-31
Dalchork Farm - 2 | PRO-005081 | CS-12483 | QAIR RENEWABLES UK LIMITED | Lairg 2 132/33kV Grid Supply Point Substation | SHET-RI-230 Dalchork to Loch Buidhe 132kV second Double Circuit |  | 2033-10-31
Dalmarnock Storage BESS | PRO-003737 | CS-09675 | VIRIDISIA LTD | Dalmarnock Storage BESS 132kV Substation | SPT-RI-2957 | Dalmarnock SGT1 & Charlotte Street 1 DCBs – To comply with SQSS circuit complexity as per Appendix B and accommodate a new generation and demand connection within the Dalmarnock area of the network, there is a requirement to replace the H13A disconnector at Dalmarnock 275/132kV substation with a DCB. Additionally, there is also a requirement to replace the H13B disconnector at Dalmarnock 275/132kV substation with a DCB | 2030-04-30
Dalmarnock Storage BESS | PRO-003737 | CS-09676 | VIRIDISIA LTD | Dalmarnock Storage BESS 132kV Substation | SPT-RI-3320 | Gresham House Dalmarnock BESS Collector & YF013 Tee In – In order to accommodate connections in this area, it is proposed to establish a collector substation at the existing Gresham House Dalmarnock BESS substation | 2030-04-30
Dalmarnock Storage BESS | PRO-003737 | CS-09677 | VIRIDISIA LTD | Dalmarnock Storage BESS 132kV Substation | Line Disconnector - Dalmarnock Storage | Installation of 132kV line disconnector | 2030-04-30
Damhead Creek 2 | PRO-001056 | CS-05625 | VPI POWER LIMITED | Kingsnorth 400kV Substation | 020622-031444 |  | 2025-08-31
Dealanach WLC WF | PRO-001722 | CS-07170 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm² Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 2026-12-15
Dealanach WLC WF | PRO-001722 | CS-07171 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2026-12-15
Dealanach WLC WF | PRO-001722 | CS-07172 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2026-12-15
Dealanach WLC WF | PRO-001722 | CS-07173 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 2026-12-15
Dealanach WLC WF | PRO-001722 | CS-07174 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 2026-12-15
Dealanach WLC WF | PRO-001722 | CS-07175 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 2026-12-15
Dealanach WLC WF | PRO-001722 | CS-07176 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-2159 | Hopsrig Substation Grid T1A Transformer - A new 132/33kV 60MVA transformer will be installed at Hopsrig collector substation. This will create a new 33kV busbar to allow new generators to connect. (SPT-RI-2159) | 2026-12-15
Deeside Power Station | PRO-001062 | CS-10525 | DEESIDE POWER (UK) LIMITED | Connah's Quay 400kV Substation | 102129-204352 1 |  | 2026-10-25
Dell Wind Farm | PRO-001012 | CS-05626 | DELL WIND FARM LIMITED | Dell 132kV Substation | SHET-RI-085b | 3. Melgarve 400/132kV Substation – Establish a new 400/132 kV Substation at Melgarve, to allow the connection of wind generation in the area. (SHET-RI-085b) | 2030-04-01
Dell Wind Farm | PRO-001012 | CS-05627 | DELL WIND FARM LIMITED | Dell 132kV Substation | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 2030-04-01
DENFIELD 20MW BESS | PRO-004632 | CS-11423 | SEAHILLS PROPERTIES LIMITED | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
DENFIELD 20MW BESS | PRO-004632 | CS-11424 | SEAHILLS PROPERTIES LIMITED | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
DENFIELD 20MW BESS | PRO-004632 | CS-11425 | SEAHILLS PROPERTIES LIMITED | Arbroath GSP | SHET-RI-234 | Tealing Solar Tee – Tealing 132kV Upgrade – Upgrade the 5.8km of single circuit overhead line between the Tealing Solar tee-point and Tealing 132kV substation. The circuit requires a minimum continuous summer rating of 170MVA | 2032-10-31
DENFIELD 20MW BESS | PRO-004632 | CS-11426 | SEAHILLS PROPERTIES LIMITED | Arbroath GSP | SHET-RI-284 |  | 2032-10-31
Derwent Solar PV Array | PRO-001648 | CS-05417 | ANESCO LIMITED | Thornton 400kV Substation | 101559-203102 | At Thornton 400kV substation extend busbars to make provision for connection of the User’s generator bay | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05418 | ANESCO LIMITED | Thornton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05419 | ANESCO LIMITED | Thornton 400kV Substation | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05420 | ANESCO LIMITED | Thornton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05421 | ANESCO LIMITED | Thornton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05422 | ANESCO LIMITED | Thornton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05423 | ANESCO LIMITED | Thornton 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05424 | ANESCO LIMITED | Thornton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05425 | ANESCO LIMITED | Thornton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05426 | ANESCO LIMITED | Thornton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05427 | ANESCO LIMITED | Thornton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05428 | ANESCO LIMITED | Thornton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05429 | ANESCO LIMITED | Thornton 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05430 | ANESCO LIMITED | Thornton 400kV Substation | 101625-203259 | Uprate the Drax - Eggborough 2 circuit to achieve a post fault summer rating of 2500MVA. | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05431 | ANESCO LIMITED | Thornton 400kV Substation | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2032-05-31
Derwent Solar PV Array | PRO-001648 | CS-05432 | ANESCO LIMITED | Thornton 400kV Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2032-05-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10021 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | Deucheran Hill 2 132kV Wood Pole H1 | Wood Pole | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10022 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10023 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10024 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10025 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10026 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10027 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10028 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10029 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10030 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10775 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | Deucheran Hill 2 AIS Switch Bay H1 |  | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10776 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | Deucheran Hill 2 132kV Cable H1 |  | 2034-10-31
Deucheran Hill 2 Wind Farm | PRO-004208 | CS-10777 | RWE Renewables UK Onshore Wind Limited | DEUCHERAN HILL 2 132KV SUBSTATION | Deucheran Hill 2 32kV Disconnector |  | 2034-10-31
Devol Moor Battery & Solar Project | PRO-004084 | CS-09310 | Sunshine Project 03 Limited | Devol Moor 400/132kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2029-10-17
Devol Moor Battery & Solar Project | PRO-004084 | CS-09311 | Sunshine Project 03 Limited | Devol Moor 400/132kV | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2029-10-17
Devol Moor Battery & Solar Project | PRO-004084 | CS-09312 | Sunshine Project 03 Limited | Devol Moor 400/132kV | SPT-RI-2833 | Devol Moor 400kV GIS Substation - At Devol Moor 400kV it is proposed to establish a new indoor GIS Double Busbar substation. The building is proposed to be sized to accommodate 14 bays. The initial GIS substation assets to be installed include the followings (subject to review): ● 5x 400kV Feeder Bays and associated switchgear; SGT1, SGT2, HUNE, WIYH and High Mathernock BESS ● 1x 400kV Bus Coupler ● 1x 400kV Bus Section ● Space to be included with building to accommodate future connections ● Removal of redundant equipment at existing 400kV Devol Moor substation. | 2029-10-17
Devol Moor GSP | PRO-003133 | CS-11771 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-3419 - Neilston 132kV B board (SS) | It is proposed to establish a new Neilston 132kV B substation to accommodate new load connections into the Neilston 132kV network. The switchboard will be fed via two 400/132kV SGT’s. A 132kV bus section will be installed with corresponding disconnectors on the reserve busbar, a 132kV bus coupler and four 132kV feeder bays (space required within the switchgear housing to accommodate future connections) will also be installed. Two bays will be used to connect the 400/132kV SGT’s with the remaining four bays used to transfer across the Braehead Park/Govan and Crookston 132kV circuits from the existing Neilston 132kV switchboard. Two new 400kV DBB GIS feeder bays with associated switchgear (circuit breaker and DBB disconnectors) will be installed at Neilston 400kV to connect the new 400/132kV 360MVA Super Grid Transformers. | 2031-10-31
Devol Moor GSP | PRO-003133 | CS-11772 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-3419 - Neilston 132kV B board (Cable) | It is proposed to establish a new Neilston 132kV B substation to accommodate new load connections into the Neilston 132kV network. The switchboard will be fed via two 400/132kV SGT’s. A 132kV bus section will be installed with corresponding disconnectors on the reserve busbar, a 132kV bus coupler and four 132kV feeder bays (space required within the switchgear housing to accommodate future connections) will also be installed. Two bays will be used to connect the 400/132kV SGT’s with the remaining four bays used to transfer across the Braehead Park/Govan and Crookston 132kV circuits from the existing Neilston 132kV switchboard. Two new 400kV DBB GIS feeder bays with associated switchgear (circuit breaker and DBB disconnectors) will be installed at Neilston 400kV to connect the new 400/132kV 360MVA Super Grid Transformers. | 2031-10-31
Devol Moor GSP | PRO-003133 | CS-11773 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-3263 | Erskine 132kV Bus Section Circuit Breaker | 2031-10-31
Devol Moor GSP | PRO-003133 | CS-11774 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-2268 | BZ Route No.2 Uprating - Generation connections into the Devol Moor – Erskine 132kV circuit have identified the need to uprate the No.2 side of BZ Route between Erskine and Braehead Park. It has been noted through system studies that an outage on the Erskine to Braehead circuit (BZ No.1) could result in overloads on the No.2 side. In order to alleviate these overloads, it is required to uprate the OHL and cable sections of the circuit. It is proposed to install 1x 280mm² AAAC “Sycamore” conductor on the OHL sections operating at 75℃ with similarly rated cable sections | 2031-10-31
Devol Moor GSP | PRO-003133 | CS-11775 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-3534 - Cable |  | 2031-10-31
Devol Moor GSP | PRO-003133 | CS-11776 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-3534 - SS |  | 2031-10-31
Devol Moor GSP | PRO-003133 | CS-11777 | SP Distribution plc | Devol Moor 132/33kV | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2031-10-31
Devonhill | PRO-004492 | CS-11174 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3474 |  | 2033-10-28
Devonhill | PRO-004492 | CS-11175 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3490 |  | 2033-10-28
Devonhill | PRO-004492 | CS-11176 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3923 Cable |  | 2033-10-28
Devonhill | PRO-004492 | CS-11177 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3923 OHL |  | 2033-10-28
Devonhill | PRO-004492 | CS-11178 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3923 SS |  | 2033-10-28
Devonhill | PRO-004492 | CS-11179 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3924 Cable |  | 2033-10-28
Devonhill | PRO-004492 | CS-11180 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3924 OHL |  | 2033-10-28
Devonhill | PRO-004492 | CS-11181 | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV | SPT-RI-3924 SS |  | 2033-10-28
Dewshill Windfarm | PRO-004115 | CS-09317 | SP Distribution plc | Newarthill 275/33kV | Dewshill Sole Enabling Works | Asset Replacement (Newarthill Fault Level Mitigation) - A bus section reactor will be installed on the SPT side of the GSP, with two new 3-panel 33kV switchboards. | 2026-04-30
Didcot BESS 1 | PRO-003446 | CS-11519 | Downing Renewable Developments LLP | Didcot 400kV Substation | 103454-206921 |  | 2037-10-31
Didcot BESS 1 | PRO-003446 | CS-11520 | Downing Renewable Developments LLP | Didcot 400kV Substation | 102630-205269 |  | 2037-10-31
Didcot BESS 1 | PRO-003446 | CS-11521 | Downing Renewable Developments LLP | Didcot 400kV Substation | 102630-205794 |  | 2037-10-31
Didcot Data Campus | PRO-002199 | CS-12680 | Amazon Data Services UK Limited | Didcot 132kV Substation | 100940-201957 - Didcot Data Campus |  | 2028-07-31
Didcot Data Campus | PRO-002199 | CS-12681 | Amazon Data Services UK Limited | Didcot 132kV Substation | 102219-204484 - Didcot Data Campus |  | 2028-07-31
Didcot Hydrogen | PRO-004336 | CS-10456 | RWE Generation UK Plc | Didcot 132kV Substation | 100940-201957 |  | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10457 | RWE Generation UK Plc | Didcot 132kV Substation | 102219-204484 (1) |  | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10458 | RWE Generation UK Plc | Didcot 132kV Substation | 103541-207033 |  | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10459 | RWE Generation UK Plc | Didcot 132kV Substation | 103609-207136 |  | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10460 | RWE Generation UK Plc | Didcot 132kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10461 | RWE Generation UK Plc | Didcot 132kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10462 | RWE Generation UK Plc | Didcot 132kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10463 | RWE Generation UK Plc | Didcot 132kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 2037-10-31
Didcot Hydrogen | PRO-004336 | CS-10464 | RWE Generation UK Plc | Didcot 132kV Substation |  |  | 2037-10-31
Didcot Road | PRO-002336 | CS-08685 | TBC 001 LIMITED | Didcot 400kV Substation | 102220-204485 | To extend the busbar & construct an additional bay including all necessary equipment at Didcot 400kV main busbar for accommodating user to the connect at Didcot 400kV substation. | 2027-10-31
Didcot Road | PRO-002336 | CS-08686 | TBC 001 LIMITED | Didcot 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2027-10-31
Didcot Road | PRO-002336 | CS-08687 | TBC 001 LIMITED | Didcot 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2027-10-31
Didcot Road | PRO-002336 | CS-08688 | TBC 001 LIMITED | Didcot 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2027-10-31
Didcot Road | PRO-002336 | CS-08689 | TBC 001 LIMITED | Didcot 400kV Substation | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2027-10-31
Divot Hill Wind Farm | PRO-004664 | CS-11015 | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation | Divot Hill Wind Farm H1 Works | 1. At Divot Hill wind farm site, install one 132kV disconnector. 2. Construct a new 132kV wood pole OHL of approx. 8km to Craigenputtlock 400/132kV substation (minimum 70MVA rating is required). 3. At Craigenputtlock substation, install a 132kV line isolator, one new 132kV double busbar switchgear and associated equipment | 2036-10-31
Divot Hill Wind Farm | PRO-004664 | CS-11016 | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation | SPT-RI-2862 OHL |  | 2036-10-31
Divot Hill Wind Farm | PRO-004664 | CS-11017 | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Divot Hill Wind Farm | PRO-004664 | CS-11018 | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Divot Hill Wind Farm | PRO-004664 | CS-11019 | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation | SPT-RI-3657 OHL |  | 2036-10-31
Divot Hill Wind Farm | PRO-004664 | CS-11020 | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation | SPT-RI-3657 SS |  | 2036-10-31
Dog Trap Lane | PRO-001626 | CS-04954 | HB411MIN Limited | Minety 400kV Substation | 101488-202940 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2028-10-31
Dog Trap Lane | PRO-001626 | CS-04955 | HB411MIN Limited | Minety 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2028-10-31
Dog Trap Lane | PRO-001626 | CS-04956 | HB411MIN Limited | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05082 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05083 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05097 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05106 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 101489-202941 | At Hawthorn Pit (New) 400kV Substation: Extend busbars to facilitate the OFTO bay and include the User Bay in the Eastern Link OTS | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05107 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05108 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100058-200133 | Tee in the Hartlepool - West Boldon circuit into Hawthorn Pit 275kV Substation (NOA WHTI) | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05109 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05110 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05111 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05112 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05113 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05114 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05115 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05116 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2031-10-31
Dogger Bank D Offshore Wind Farm | PRO-001675 | CS-05117 | Doggerbank Offshore Wind Farm Project 4 Projco Limited | Birkhill Wood 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Dogger Bank Project C | PRO-000409 | CS-05631 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby 400kV Substation | 031570-031570 | Generation connection for Doggerbank P2 at Lackenby 400kV substation. Extension to the existing GIS building at the Lackenby substation to enable the connection of the Doggerbank connection bay. Transition bay from Alstom T155 and provision of skeleton bay including BB protection etc | 2025-04-01
Dogger Bank Project C | PRO-000409 | CS-07023 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby 400kV Substation | 101243-202472 | Extension of the existing OTS at Lackenby 400kV substation for the connection of new generators | 2025-04-01
Dogger Bank Project C | PRO-000409 | CS-07024 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2025-04-01
Dogger Bank Project C | PRO-000409 | CS-07025 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2025-04-01
Dogger Bank Project C | PRO-000409 | CS-07026 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2025-04-01
Dogger Bank South East | PRO-001375 | CS-04374 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-04386 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-04390 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11210 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 101968-204091 | Turn-in of both Creyke Beck - Thornton 1 & 2 circuits into a new 400kV AIS double busbar substation (Creyke Beck North) with 4 OHL feeder bays, 2 bus coupler bays and 1 bus section bay | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11211 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 100998-201999 |  | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11212 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 101812-203717 | A new 400kV route to be established between the Sheffield area and the East Midlands, to aid with North to South flows of generation which consists of rationalisation of existing Chesterfield 275kV to Chesterfield 400kV. The Chesterfield 400kV will have 4x460MVA, 400/132kV SGT along with feeders connecting to Brinsworth and High Marnham | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11213 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11214 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11215 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11216 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 102757-205560 | At Thornton-Replace X230, X430 & X805 with 63kA rated breakers and suitable X/R ratio. | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11217 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 102775-205613 | Uprate Creyke Beck-Keadby A35A, A35B, A35D as per Creyke Beck Extension SDS which is 2790 MVA summer Prefault including A35E | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11218 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11219 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11220 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2030-10-30
Dogger Bank South East | PRO-001375 | CS-11221 | RWE Renewables UK Dogger Bank South (East) Limited | Birkhill Wood 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11195 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 101968-204091 | Turn-in of both Creyke Beck - Thornton 1 & 2 circuits into a new 400kV AIS double busbar substation (Creyke Beck North) with 4 OHL feeder bays, 2 bus coupler bays and 1 bus section bay | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11196 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 101812-203717 | A new 400kV route to be established between the Sheffield area and the East Midlands, to aid with North to South flows of generation which consists of rationalisation of existing Chesterfield 275kV to Chesterfield 400kV. The Chesterfield 400kV will have 4x460MVA, 400/132kV SGT along with feeders connecting to Brinsworth and High Marnham | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11197 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11198 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11199 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11200 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11201 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11202 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11203 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 102757-205560 | At Thornton-Replace X230, X430 & X805 with 63kA rated breakers and suitable X/R ratio. | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11204 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 102775-205613 | Uprate Creyke Beck-Keadby A35A, A35B, A35D as per Creyke Beck Extension SDS which is 2790 MVA summer Prefault including A35E | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11205 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11206 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11207 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11208 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2030-10-30
Dogger Bank South West | PRO-001386 | CS-11209 | RWE RENEWABLES UK DOGGER BANK SOUTH (WEST) LIMITED | Birkhill Wood 400kV Substation | 101020-202043 | Infrastructure works at Wylfa 400kV substation necessary to connect 1500MW or the RWE R4 offshore wind project. | 2030-10-30
Dolyfardyn | PRO-001584 | CS-04701 | Llyn Lort Energy Park Limited | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2027-02-04
Dolyfardyn | PRO-001584 | CS-04710 | Llyn Lort Energy Park Limited | Chirk GSP | 101323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2027-02-04
Dolyfardyn | PRO-001584 | CS-04712 | Llyn Lort Energy Park Limited | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2027-02-04
Dolyfardyn | PRO-001584 | CS-04713 | Llyn Lort Energy Park Limited | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-02-04
Dolyfardyn | PRO-001584 | CS-04714 | Llyn Lort Energy Park Limited | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2027-02-04
Don Cossack | PRO-003875 | CS-09009 | Don Cossack Ltd | Tynemouth 275kV Substation | 102394-204915 | Make provision for connection of generator bay at Tynemouth 275kV GIS substation. | 2034-06-15
Don Cossack | PRO-003875 | CS-09010 | Don Cossack Ltd | Tynemouth 275kV Substation | 102394-204914 | Construction of a new 275kV double busbar substation of Tynemouth and transposition of circuits from existing single switch mesh. | 2034-06-15
Don Cossack | PRO-003875 | CS-09011 | Don Cossack Ltd | Tynemouth 275kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2034-06-15
Don Cossack | PRO-003875 | CS-09012 | Don Cossack Ltd | Tynemouth 275kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 2034-06-15
Don Cossack | PRO-003875 | CS-09013 | Don Cossack Ltd | Tynemouth 275kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2034-06-15
Don Cossack | PRO-003875 | CS-09014 | Don Cossack Ltd | Tynemouth 275kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2034-06-15
Don Cossack | PRO-003875 | CS-09015 | Don Cossack Ltd | Tynemouth 275kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2034-06-15
Don Cossack | PRO-003875 | CS-09016 | Don Cossack Ltd | Tynemouth 275kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 2034-06-15
Don Cossack | PRO-003875 | CS-09017 | Don Cossack Ltd | Tynemouth 275kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2034-06-15
Don Cossack | PRO-003875 | CS-09018 | Don Cossack Ltd | Tynemouth 275kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2034-06-15
Don Cossack | PRO-003875 | CS-09019 | Don Cossack Ltd | Tynemouth 275kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2034-06-15
Don Cossack | PRO-003875 | CS-09020 | Don Cossack Ltd | Tynemouth 275kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2034-06-15
Don Cossack | PRO-003875 | CS-09021 | Don Cossack Ltd | Tynemouth 275kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2034-06-15
Don Cossack | PRO-003875 | CS-09022 | Don Cossack Ltd | Tynemouth 275kV Substation | 102178-204388 | Replacement of CB's S10, P10, W10, W20, H10 and H20 at Blyth 275kV Substation | 2034-06-15
Don Cossack | PRO-003875 | CS-09023 | Don Cossack Ltd | Tynemouth 275kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2034-06-15
Don Cossack | PRO-003875 | CS-09024 | Don Cossack Ltd | Tynemouth 275kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2034-06-15
Don Cossack | PRO-003875 | CS-09025 | Don Cossack Ltd | Tynemouth 275kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2034-06-15
Dorenell Windfarm Extension | PRO-002415 | CS-08417 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | Dorenell Extension Wind Farm H1 SS | Installation of 2 x new 400kV bays at ‘Blackhillock 2’, comprising line disconnectors, 2 x feeder circuit breakers and 4 x busbar selector disconnectors. Installation of 2 x 400kV line disconnectors at the User’s substation Construction of approximately 21.7km of double circuit line and cable from the User’s site to Blackhillock 2 400kV substation. The line shall comprise 20km double circuit 400kV OHL plus 0.5km and 1.2km 400kV UGC sections. Cable sections are required due to the NETS SQSS stipulation of a maximum OHL length of 20km. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08418 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08419 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08420 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08421 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08422 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08423 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08424 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08425 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08426 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08427 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08428 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08429 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08430 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08431 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Dorenell Windfarm Extension | PRO-002415 | CS-08432 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHET-RI-199) | 2033-10-31
Douglas West Extension | PRO-000422 | CS-05637 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 2025-06-30
Douglas West Extension | PRO-000422 | CS-05638 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-251 | Coalburn to Douglas West 132kV Cable Reinforcement | 2025-06-30
Douglas West Extension | PRO-000422 | CS-05639 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 2025-06-30
Douglas West Extension | PRO-000422 | CS-05640 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-240 | Douglas West Wind Farm 132kV Substation | 2025-06-30
Douglas West Extension | PRO-000422 | CS-05641 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-268 | Coalburn to Douglas North Existing 132kV Cable Rating Enhancement | 2025-06-30
Douglas West Extension | PRO-000422 | CS-09786 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 2025-06-30
Dounreay | PRO-002318 | CS-08498 | Reay Power Limited | Dounreay 132kV Converter | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2026-07-31
Dounreay | PRO-002318 | CS-08499 | Reay Power Limited | Dounreay 132kV Converter | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2026-07-31
Doveryard Energy Centre | PRO-000765 | CS-06772 | SP Distribution plc | Kilmarnock South 275/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2025-05-19
Doveryard Energy Centre | PRO-000765 | CS-06773 | SP Distribution plc | Kilmarnock South 275/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2025-05-19
Drakelow | PRO-000428 | CS-04964 | ENSO GREEN HOLDINGS V LIMITED | Drakelow 132kV Substation | 100582-201204 | 1. Install earthing transformer on 13kV tertiary connection 2. Install 13kV cable connecting earthing transformer to DCB 3. Install 72.5kV, 40kA rated DCB to connection assets for Users connection | 2027-12-01
Drakelow | PRO-000428 | CS-11030 | ENSO GREEN HOLDINGS V LIMITED | Drakelow 132kV Substation | 100582-201938 (One Off) |  | 2027-12-01
Drakelow BESS | PRO-002033 | CS-07355 | HARMONY DL LTD | Drakelow 400kV Substation | 101882-203858 |  | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07356 | HARMONY DL LTD | Drakelow 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07357 | HARMONY DL LTD | Drakelow 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07358 | HARMONY DL LTD | Drakelow 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07359 | HARMONY DL LTD | Drakelow 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07360 | HARMONY DL LTD | Drakelow 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07361 | HARMONY DL LTD | Drakelow 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07362 | HARMONY DL LTD | Drakelow 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07363 | HARMONY DL LTD | Drakelow 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 2029-12-31
Drakelow BESS | PRO-002033 | CS-07364 | HARMONY DL LTD | Drakelow 400kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490 MVA. | 2029-12-31
Drakelow Green Energy Centre | PRO-001693 | CS-04644 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101330-202250 | Extension of the existing Drakelow 400kV substation Main and Reserve Busbars to accommodate the User’s bay | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04958 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04959 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04965 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04966 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04967 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04968 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-04969 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-12606 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 101330-202650 |  | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-12607 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 102085-204275 |  | 2028-04-30
Drakelow Green Energy Centre | PRO-001693 | CS-12608 | DRAKELOW NG LIMITED | Drakelow 400kV Substation | 102086-204276 |  | 2028-04-30
Drax | PRO-001355 | CS-05015 | ENSO GREEN HOLDINGS D LIMITED | Drax 132kV Substation | 101056-202118 | Extend busbars at Drax 132kV Substation to accommodate new bay connection (specifics to be determined in detailed design stage) | 2029-10-30
Drax | PRO-001355 | CS-05016 | ENSO GREEN HOLDINGS D LIMITED | Drax 132kV Substation | 100173-200455 | Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and130) at Drax 132kV Substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required | 2029-10-30
Drax | PRO-001355 | CS-05017 | ENSO GREEN HOLDINGS D LIMITED | Drax 132kV Substation | 101056-202119 |  | 2029-10-30
Drax GSP (Yorkshire) | PRO-002973 | CS-12333 | Northern Powergrid (Yorkshire) Plc | Drax GSP | 101865-203833 Keadby PP |  | 2039-10-30
Drax GSP (Yorkshire) | PRO-002973 | CS-12334 | Northern Powergrid (Yorkshire) Plc | Drax GSP | 103136-206551 Keadby |  | 2039-10-30
Drax GSP (Yorkshire) | PRO-002973 | CS-12336 | Northern Powergrid (Yorkshire) Plc | Drax GSP | 103545-207038 Keadby |  | 2039-10-30
Drax GSP (Yorkshire) | PRO-002973 | CS-12338 | Northern Powergrid (Yorkshire) Plc | Drax GSP | 104286-208320 Keadby |  | 2039-10-30
Drax Solar | PRO-001759 | CS-07044 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101668-203321 | 1. Busbar extensions to provide space within M6 and R4/5/6 at Drax 400kV substation to accommodate a new HV SGT bay 2. Installation of a Section CB on the reserve bar R4/5/6. | 2029-09-30
Drax Solar | PRO-001759 | CS-07045 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101668-203322 | 1. Install and commission a new 400kV Supergrid Transformers (SGT) bay at Drax 400kV substation. 2. Install 400kV switchgear at Drax 400kV substation. This equipment will include the HV side SGT bay disconnectors and circuit breakers 3. Procure, install and commission a new 460MVA rated 400/132kV SGT 4. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. 5. Install 132kV switchgear at Drax 400kV substation on the LV side of the SGT. This equipment will include the HV side SGT bay disconnectors and circuit breaker. | 2029-09-30
Drax Solar | PRO-001759 | CS-07046 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2029-09-30
Drax Solar | PRO-001759 | CS-07047 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2029-09-30
Drax Solar | PRO-001759 | CS-07048 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2029-09-30
Drax Solar | PRO-001759 | CS-07049 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101507-202972 | Make provision for connection of generator bay (User’s Works) at Monk Fryston 275kV double busbar substation. Local works to facilitate extension of Lackenby Operational Tripping Scheme (OTS) at Monk Fryston 275kV double busbar substation. | 2029-09-30
Drax Solar | PRO-001759 | CS-07050 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2029-09-30
Drax Solar | PRO-001759 | CS-07051 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101666-203319 | Uprating/Replacement of the following CBs 130 and 230 at Ferrybridge 132kV substation | 2029-09-30
Drax Solar | PRO-001759 | CS-07052 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 033754-033754 | Uprating/Replacement of the CB L45 at Monk Fryston 275kV substation | 2029-09-30
Drax Solar | PRO-001759 | CS-07053 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101661-203312 | Uprating/Replacement of the CB T10 at Monk Fryston 275kV substation | 2029-09-30
Drax Solar | PRO-001759 | CS-07054 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2029-09-30
Drax Solar | PRO-001759 | CS-07055 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2029-09-30
Drax Solar | PRO-001759 | CS-07056 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2029-09-30
Drax Solar | PRO-001759 | CS-07057 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 2029-09-30
Drax Solar | PRO-001759 | CS-07058 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2029-09-30
Drax Solar | PRO-001759 | CS-07059 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2029-09-30
Drax Solar | PRO-001759 | CS-07060 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101667-203320 | Installation of 2x200 MVAr MSC at Cottam 400kV substation | 2029-09-30
Drax Solar | PRO-001759 | CS-07061 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 101593-203208 & 030613-030613 | Uprate the Cottam – Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2029-09-30
Drax Solar | PRO-001759 | CS-07062 | East Yorkshire Solar Farm Limited | Drax 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2029-09-30
Dronley Solar | PRO-004078 | CS-11576 | GREENTECH PROJECTS HOLDING UK LIMITED | Lyndhurst GSP | Dronley Solar H1 Sole | The construction of a new 132kV GIS double busbar, currently referred to as Lyndhurst 132kV substation. The installation of 4x new 132kV double busbar switch bays will be required as part of this connection. Each switch bay will include 2x 132kV busbar selection switches, 1x 132kV circuit breaker and 1x 132kV line disconnector. 2 of these new 132kV switch bays will be required at Lyndhurst 132kV substation, and the other 2 switch bays will be required at Charleston 132kV substation. In addition to this, any bus couplers or protection equipment required at the new Lyndhurst 132kV substation will also be included. Dismantle the existing 132kV CM1/CM2 double circuit overhead line between Lyndhurst 132/33kV GSP substation and the tee point at Charleston 132kV substation. Approximately 2x 2km of 132kV cable circuits between Lyndhurst 132kV substation and Charleston 132kV substation will be required. | 2031-10-31
Druim Leathann BEGA | PRO-000966 | CS-05642 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | Druim Leathann Wind Farm Enabling works - Items 4-7 | The relevant transmission licensee will install a second 30/60 MVA 132/33 kV transformer (G2) and associated 33 kV transformer circuit breaker/isolator in a new building at Stornoway 132/33 kV Grid Supply Point. Protections and control modifications as required. Associated civil works. Miscellaneous and minor works. | 2027-03-31
Druim Leathann BEGA | PRO-000966 | CS-05643 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 2027-03-31
Druim Leathann BEGA | PRO-000966 | CS-05644 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 2027-03-31
Druim Leathann BEGA | PRO-000966 | CS-05645 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | Druim Leathann Wind Farm enabling works - item 1 | Install 132 kV circuit switcher on the new 132/33 kV transformer (G2) and carry out associated cable and busbar works | 2027-03-31
Drum of Clunas Wind and Solar Park | PRO-003970 | CS-09513 | BROADHAVEN DISTRIBUTION LIMITED | Drum of Clunas 275kV | Drum of Clunas Sole | Installation of a 275kV disconnector at the User’s site, on the Network side of the circuit breaker mentioned in Appendix G of this Bilateral Connection Agreement. | 2031-10-31
Drum of Clunas Wind and Solar Park | PRO-003970 | CS-09514 | BROADHAVEN DISTRIBUTION LIMITED | Drum of Clunas 275kV | SHET-RI-229 | Cawdor Wind Farm substation and OHL Works – Construction of a new 275kV line circuit breaker bay on the 275kV Knocknagael - Blackhillock "CA1" circuit at the future Cawdor 275kV Substation. This construction arrangement will turn this into a Knocknagael - Cawdor - Blackhillock 275kV circuit. | 2031-10-31
Drum of Clunas Wind and Solar Park | PRO-003970 | CS-11723 | BROADHAVEN DISTRIBUTION LIMITED | Drum of Clunas 275kV | SHET-RI-026 Blackhillock 275kV QBs |  | 2031-10-31
Drum of Clunas Wind and Solar Park | PRO-003970 | CS-12439 | BROADHAVEN DISTRIBUTION LIMITED | Drum of Clunas 275kV | SHET-RI-007a Beauly - Blackhillochk 400kV Double Circuit OHL |  | 2031-10-31
Drum of Clunas Wind and Solar Park | PRO-003970 | CS-12440 | BROADHAVEN DISTRIBUTION LIMITED | Drum of Clunas 275kV | SHET-RI-007b Beauly 400kV Busbar |  | 2031-10-31
Drumcross GSP | PRO-003137 | CS-10059 | SP Distribution plc | Drumcross 132/33kV | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 2031-09-30
Drumcross GSP | PRO-003137 | CS-10060 | SP Distribution plc | Drumcross 132/33kV | SPT-RI-2415 - AA Route OHL Uprate |  | 2031-09-30
Drumcross GSP | PRO-003137 | CS-10061 | SP Distribution plc | Drumcross 132/33kV | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2031-09-30
Drumfad Battery Storage System | PRO-002419 | CS-08329 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 132/33kV | SPT-RI-2691 | 1. Windyhill, Strathleven, Helensburgh and Sloy Load Management Scheme - The load management scheme required here shall monitor the two Windyhill to Sloy double circuits. This LMS shall monitor if one of the circuits is out of service and if an overload is detected on the adjacent circuit. Due to the configuration of the circuits in this area it will be required to interface with the 132kV circuit breakers at Sloy substation. The circuits to be monitored are the CK route and CL route. | 2027-10-31
Drumfad Battery Storage System | PRO-002419 | CS-08331 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 132/33kV | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2027-10-31
Drumfad Battery Storage System | PRO-002419 | CS-08334 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 132/33kV | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 2027-10-31
Drumfad Battery Storage System | PRO-002419 | CS-08335 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 132/33kV | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 2027-10-31
Drumlithie Battery Storage | PRO-002299 | CS-07929 | DRUMLITHIE BATTERY LIMITED | Fetteresso GSP | Drumlithie Battery Storage A1 | At Fetteresso 132/33kV GSP substation, install a new HV circuit breaker and associated disconnectors | 2028-10-31
Drumlithie Battery Storage | PRO-002299 | CS-07930 | DRUMLITHIE BATTERY LIMITED | Fetteresso GSP | Drumlithie Battery Storage A1 | At Fetteresso 132/33kV GSP substation, install a new HV circuit breaker and associated disconnectors | 2028-10-31
Drummarnock Wind Farm | PRO-001912 | CS-08464 | Drummarnock Wind Farm Limited | Bonnybridge 132/33kV | SPT-RI-286 | Bonnybridge SGT1 Auto Changeover Scheme - An auto-changeover scheme will be installed on the Bonnybridge 275/132kV transformer SGT1 such that SGT1 will remain disconnected but on hot standby in case of a fault on Bonnybridge SGT2, Denny 275/132kV SGT3, or a double circuit fault on the Bonnybridge-Westfield 132kV circuits. This is required for fault level mitigation on the Bonnybridge 132kV busbar. | 2026-10-01
Drumore Farm | PRO-002397 | CS-09778 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2030-10-31
Drumore Farm | PRO-002397 | CS-09779 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2030-10-31
Drumore Farm | PRO-002397 | CS-09780 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2030-10-31
Drumore Farm | PRO-002397 | CS-09781 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2030-10-31
Drumore Farm | PRO-002397 | CS-09782 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2030-10-31
Drumore Farm | PRO-002397 | CS-09783 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2030-10-31
Drumore Farm | PRO-002397 | CS-09784 | Drumore Battery Storage Limited | Alness 2 275/33 kV GSP Substation | SHET-RI-224 Alness 2 GSP 275kV Reinforcement |  | 2030-10-31
Dunach Wind Farm | PRO-002754 | CS-09368 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09369 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09370 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-046 | Taynuilt – North Argyll Reinforcement - Reinforce the transmission network between Taynuilt and North Argyll substation (established as part of SHET-RI-013). Rebuild approximately 12.5km of existing 132kV double circuit steel tower line between Creag Dhubh and Taynuilt with a heavy duty 132kV | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09371 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09372 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09373 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09374 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09375 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09376 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09377 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bi-pole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09378 | GALILEO 04 LIMITED | Taynuilt GSP | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09379 | GALILEO 04 LIMITED | Taynuilt GSP | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09380 | GALILEO 04 LIMITED | Taynuilt GSP | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09381 | GALILEO 04 LIMITED | Taynuilt GSP | Dunach WF - Disconnector | Installation of 1 x 132kV line disconnector on the Taynuilt side of the metering circuit breaker at Dunach Wind 132kV substation; approximately 11.5km of 132kV circuit between the new Dunach Wind 132kV substation and the existing Taynuilt substation, consisting of 11.2km of overhead line and 0.3km of underground cable | 2034-10-31
Dunach Wind Farm | PRO-002754 | CS-09382 | GALILEO 04 LIMITED | Taynuilt GSP | Dunach WF - Taynuilt Bay | At the Taynuilt substation, installation of a new 132kV bay consisting of 1x 132kV circuit breaker and 2x 132kV disconnectors will also be required, along with an extension to the Taynuilt substation grounds, site platform and control building | 2034-10-31
Dunan Hill | PRO-004433 | CS-10141 | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation | SHET-RI-283 Corrymuckloch 400kV Substation |  | 2036-11-11
Dunan Hill | PRO-004433 | CS-10142 | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation | SHET-RI-134 Beauly-Denny Second Circuit Upgrade from 275kV to 400kV |  | 2036-11-11
Dunan Hill | PRO-004433 | CS-10143 | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation | SHET-RI-212 Second Beauly 400kV Double Circuit OHL Southern Connector |  | 2036-11-11
Dunan Hill | PRO-004433 | CS-10144 | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 2036-11-11
Dunan Hill | PRO-004433 | CS-10145 | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation | SPT-RI-2943 | To facilitate the generation connections around Fort Augustus in SSEN area (including ER FA Energy 700MW), in collaboration with SSEN, it is proposed to establish a second Beauly 400kV DC OHL circuit from the proposed SSEN’s ‘Fort Augustus 2 400kV substation’ to terminate into the SPT’s area. The location of the SPT’s new 400kV substation is currently under review, with an initial view that this is to be located at ‘Harburn 400kV substation’ on XJ Route. | 2036-11-11
Dunan Hill | PRO-004433 | CS-10146 | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation | SPT-RI-3002 Harburn 400kV Substation OHL |  | 2036-11-11
Dunbar Solar PV | PRO-004328 | CS-10079 | SP Distribution plc | Dunbar 132/33kV | SPT-RI-3718 | Torness-Innerwick Dunbar 132kV OHL Replacement | 2029-04-30
Dunbar Solar PV | PRO-004328 | CS-10080 | SP Distribution plc | Dunbar 132/33kV | SPT-RI-3345 | Torness-Innerwick-Dunbar 132kV Cable Replacement. | 2029-04-30
Dungeness Energy Park | PRO-001986 | CS-07242 | SOUTH KENT ENERGY PARK LIMITED | Dungeness 400kV Substation | 101801-203687 | 1. Reconfiguration of Dungeness 400kV Main and Reserve Busbars to accommodate User’s Bay | 2037-10-31
Dungeness Energy Park | PRO-001986 | CS-07243 | SOUTH KENT ENERGY PARK LIMITED | Dungeness 400kV Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 2037-10-31
Dungeness Energy Park | PRO-001986 | CS-07244 | SOUTH KENT ENERGY PARK LIMITED | Dungeness 400kV Substation | 101701-203401 | 1. Uprate the Dungeness – Ninfield OHL circuits to increase capacity. | 2037-10-31
Dungeness Energy Park (Dungeness 400kV) | PRO-005021 | CS-10221 | SOUTH KENT ENERGY PARK LIMITED | East Kent connection node A 400kV Substation | 101801-203687 | 1. Reconfiguration of Dungeness 400kV Main and Reserve Busbars to accommodate User’s Bay | 2033-10-31
Dungeness Energy Park (Dungeness 400kV) | PRO-005021 | CS-12484 | SOUTH KENT ENERGY PARK LIMITED | East Kent connection node A 400kV Substation | 101901-203894 1 |  | 2033-10-31
Dungeness Energy Park (Dungeness 400kV) | PRO-005021 | CS-12485 | SOUTH KENT ENERGY PARK LIMITED | East Kent connection node A 400kV Substation | 103432-206895 1 |  | 2033-10-31
Dunns Farm | PRO-003504 | CS-09538 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2027-10-29
Dunns Farm | PRO-003504 | CS-09539 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2027-10-29
Dunns Farm | PRO-003504 | CS-09540 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2027-10-29
Dunside Wind Farm (Formally Fallago Rig 2 Wind Farm) | PRO-000526 | CS-04266 | EDF ENERGY RENEWABLES LIMITED | Fallago 400/33kV | SPT-RI-125 Thornton Bridge to Torness 400kV Cable Upgrade | it is proposed that the Thornton Bridge / Torness 400kV cable will be uprated. This will be achieved by banking one of the redundant 400kV cables between Branxton / Torness that are to be decommissioned to the existing Thornton Bridge / Torness 400kV cable in order to give a circuit capacity of not less than 1,033MVA (approximately 1,200MVA pre-fault summer rating could be achieved). | 2029-04-30
Dunside Wind Farm (Formally Fallago Rig 2 Wind Farm) | PRO-000526 | CS-04267 | EDF ENERGY RENEWABLES LIMITED | Fallago 400/33kV | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 2029-04-30
Dunside Wind Farm (Formally Fallago Rig 2 Wind Farm) | PRO-000526 | CS-04268 | EDF ENERGY RENEWABLES LIMITED | Fallago 400/33kV | SPT-RI-212 East - West 400kV Upgrade (Strathaven - Torness) | The existing Strathaven-Wishaw, Wishaw-Kaimes and Kaimes-Smeaton 275kV circuits will be reconfigured and uprated to 400kV operation. A second cable per phase will be installed on the Torness-Eccles 400kV circuits. | 2029-04-30
Dyce Battery Storage | PRO-002332 | CS-07957 | Dyce Battery Storage Limited | Dyce 132/33kV GSP | ANM Signals | This scheme requires the Relevant Transmission Licensee to provide signals into an Active Network Management (ANM) scheme to be installed by the Host Distribution Network Operator at Dyce 132/33kV GSP substation. These signals will be provided to the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom. The required measurement points and operation requirements to implement this ANM scheme will be determined through the detailed design phase. | 2025-10-30
Dyce Battery Storage | PRO-002332 | CS-07958 | Dyce Battery Storage Limited | Dyce 132/33kV GSP | Protection Settings - Dyce BESS | Modification to the existing LV Directional Overcurrent (DOC) protection settings at Dyce 132/33kV substation | 2025-10-30
Dyce Battery Storage | PRO-002332 | CS-07959 | Dyce Battery Storage Limited | Dyce 132/33kV GSP | Loss of Mains - Dyce BESS | A loss of mains scheme will be configured at Dyce GSP as requested by the User. | 2025-10-30
Earba PSH | PRO-004030 | CS-09664 | EARBA LIMITED | Earba PSH Powerhouse Substation | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2032-12-31
Earba PSH | PRO-004030 | CS-09665 | EARBA LIMITED | Earba PSH Powerhouse Substation | SHET-RI-172 | Dalwhinnie 400kV Substation - Establish a new 400kV substation on the Beauly-Denny GM1 circuit (between Fort Augustus and Tummel) in the geographical area between Laggan and Dalwhinnie | 2032-12-31
Earba PSH | PRO-004030 | CS-09666 | EARBA LIMITED | Earba PSH Powerhouse Substation | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 2032-12-31
Earba PSH | PRO-004030 | CS-09667 | EARBA LIMITED | Earba PSH Powerhouse Substation | SHET-RI-172 | Dalwhinnie 400kV Substation - Establish a new 400kV substation on the Beauly-Denny GM1 circuit (between Fort Augustus and Tummel) in the geographical area between Laggan and Dalwhinnie | 2032-12-31
Earba PSH | PRO-004030 | CS-09668 | EARBA LIMITED | Earba PSH Powerhouse Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 2032-12-31
Earba PSH | PRO-004030 | CS-09669 | EARBA LIMITED | Earba PSH Powerhouse Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 2032-12-31
Earl Shilton BESS | PRO-001950 | CS-07408 | Exagen Normanton Energy Reserve Limited | Earl Shilton 275kV | 101831-203755 |  | 2029-10-26
Earl Shilton BESS | PRO-001950 | CS-07409 | Exagen Normanton Energy Reserve Limited | Earl Shilton 275kV | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2029-10-26
Earl Shilton BESS | PRO-001950 | CS-07410 | Exagen Normanton Energy Reserve Limited | Earl Shilton 275kV | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2029-10-26
Earl Shilton BESS | PRO-001950 | CS-07411 | Exagen Normanton Energy Reserve Limited | Earl Shilton 275kV | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2029-10-26
Earl Shilton BESS | PRO-001950 | CS-07412 | Exagen Normanton Energy Reserve Limited | Earl Shilton 275kV | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2029-10-26
Earl Shilton BESS | PRO-001950 | CS-07413 | Exagen Normanton Energy Reserve Limited | Earl Shilton 275kV | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2029-10-26
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-04327 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-04328 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-04329 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-04330 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-04331 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | Earraghail H1 Works | The construction of approximately 5.6km of 275kV double circuit overhead line between the Craig Murrail - Crossaig overhead line and the Earraghail 275/33kV substation. At the wind farm substation, the 275kV overhead line will terminate onto a circuit breaker bay. The sole enabling works will include construction of two 275kV AIS line bays with associated line isolators (L13 and L23) and Circuit Breaker isolators (L15 and L25), and a 275kV AIS transformer circuit breaker bay with associated transformer circuit breaker (H10) and transformer circuit breaker isolator (H17). | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-06051 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-06052 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-06053 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2031-04-01
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-06054 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2031-04-01
East Anglia One North | PRO-000269 | CS-05018 | EAST ANGLIA ONE NORTH LIMITED | Friston 400kV Substation | 100911-201829 | At Friston 400kV Substation; Facilitate an OFTO connection in to a spare bay and provide an intertrip facility. | 2029-10-30
East Anglia One North | PRO-000269 | CS-05019 | EAST ANGLIA ONE NORTH LIMITED | Friston 400kV Substation | 100077-200227 | Construct a new 400kV double busbar substation at Friston consisting of four feeder bays, one bus coupler and one section breaker bay. | 2029-10-30
East Anglia One North | PRO-000269 | CS-05021 | EAST ANGLIA ONE NORTH LIMITED | Friston 400kV Substation | 100077-201203 | Connect the new 400kV substation at Friston to the Transmission System by teeing in to the existing two double circuits between Bramford and Sizewell. Construct a new 400kV single-switch mesh busbar switching compound north of the new 400kV substation at Friston and divert the existing Bramford-Leiston-Sizewell 400kV circuit in to the switching compound. | 2029-10-30
East Anglia One North | PRO-000269 | CS-05651 | EAST ANGLIA ONE NORTH LIMITED | Friston 400kV Substation | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 2029-10-30
East Anglia One North | PRO-000269 | CS-05652 | EAST ANGLIA ONE NORTH LIMITED | Friston 400kV Substation | 20834-2A | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit. | 2029-10-30
East Anglia Three | PRO-000270 | CS-06667 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 101238-202465 | At Bramford 400 kV Substation: Phase 1 - Facilitate an OFTO connection in a spare bay and provide an intertrip facility. | 2026-01-31
East Anglia Three | PRO-000270 | CS-06668 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 020834-030647 | At Bramford 400 kV Substation: Phase 1 - To accommodate the additional OFTO bay, the 400kV GIS busbar will be extended to include a fourth busbar section. | 2026-01-31
East Anglia Three | PRO-000270 | CS-06669 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2026-01-31
East Anglia Three | PRO-000270 | CS-06670 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 020315-020315-CLSD | Construct an initial nine bay 400kV GIS substation at Bramford as a two section GIS substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 2026-01-31
East Anglia Three | PRO-000270 | CS-06671 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 020834-021494 | At Bramford 400 kV Substation: Phase 2 - Extend the Phase 1 GIS substation by a further nine bays; comprising of five OHL feeder bays to receive the reconfigured Pelham 1 & 2 circuits, Sizewell 1 & 2 circuits and the Norwich 2 circuit. | 2026-01-31
East Anglia Two | PRO-000134 | CS-05020 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 100077-201203 | Connect the new 400kV substation at Friston to the Transmission System by teeing in to the existing two double circuits between Bramford and Sizewell. Construct a new 400kV single-switch mesh busbar switching compound north of the new 400kV substation at Friston and divert the existing Bramford-Leiston-Sizewell 400kV circuit in to the switching compound. | 2028-03-31
East Anglia Two | PRO-000134 | CS-05022 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 100077-200227 | Construct a new 400kV double busbar substation at Friston consisting of four feeder bays, one bus coupler and one section breaker bay. | 2028-03-31
East Anglia Two | PRO-000134 | CS-05023 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 100077-201239 | Establish a spare bay at the new Friston 400 kV substation, interfacing with the OFTO circuit. | 2028-03-31
East Anglia Two | PRO-000134 | CS-05649 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 2028-03-31
East Anglia Two | PRO-000134 | CS-05650 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 20834-2A | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit. | 2028-03-31
East Claydon Green Energy Centre | PRO-002383 | CS-12595 | EAST CLAYDON GREEN NG LIMITED | East Claydon 400kV Substation | 102023-204178 1 |  | 2034-10-01
East Claydon Green Energy Centre | PRO-002383 | CS-12596 | EAST CLAYDON GREEN NG LIMITED | East Claydon 400kV Substation | 102111-204305 1 |  | 2034-10-01
East Claydon Greener Grid Park | PRO-002314 | CS-09196 | East Claydon Energy Limited | East Claydon 400kV Substation | 102623-205257 | Extension of East Claydon 400kV double busbar (M2/R2) substation to provide space for the User’s generation connection bay | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09197 | East Claydon Energy Limited | East Claydon 400kV Substation | 102112-204306 | Install a bus coupler circuit breaker on busbars M1/R1 | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09198 | East Claydon Energy Limited | East Claydon 400kV Substation | 102023-204178 | The replacement of SGT1, SGT2, SGT3 and SGT4 and any associated assets in order to achieve a rating of 460MVA. The transformers will also have a higher impedance at East Claydon 400/132kV substation to resolve the fault level issues at the tertiary winding of the SGTs | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09199 | East Claydon Energy Limited | East Claydon 400kV Substation | 102624-205258 | Install two bus section circuit breakers on busbars M1 and R1 (one on each bus bar) | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09200 | East Claydon Energy Limited | East Claydon 400kV Substation | 102625-205259 | Transpose the Cowley and Enderby / Patford Bridge 2 circuits on to the East Claydon 400kV M2/R2 busbar extensions | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09201 | East Claydon Energy Limited | East Claydon 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09202 | East Claydon Energy Limited | East Claydon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09203 | East Claydon Energy Limited | East Claydon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09204 | East Claydon Energy Limited | East Claydon 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09205 | East Claydon Energy Limited | East Claydon 400kV Substation | 101592-203207 | Reconductor East Claydon – Amersham Main – Iver 400kV double circuit route (55.5km, 2x500mm² Twin Rubus conductor on L2 Towers at 75°C with a summer pre-fault rating of 1466MVA) to 2x620mm² Twin Matthew Conductor at 170°C to achieve a new summer pre-fault rating of 2490 MVA. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09206 | East Claydon Energy Limited | East Claydon 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09207 | East Claydon Energy Limited | East Claydon 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09208 | East Claydon Energy Limited | East Claydon 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09209 | East Claydon Energy Limited | East Claydon 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09210 | East Claydon Energy Limited | East Claydon 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm² conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm² 90°C conductor to achieve a pre fault summer rating of 2400 MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09211 | East Claydon Energy Limited | East Claydon 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09212 | East Claydon Energy Limited | East Claydon 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09213 | East Claydon Energy Limited | East Claydon 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09214 | East Claydon Energy Limited | East Claydon 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09215 | East Claydon Energy Limited | East Claydon 400kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490 MVA. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09216 | East Claydon Energy Limited | East Claydon 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09217 | East Claydon Energy Limited | East Claydon 400kV Substation | 102108-204302 | Uprate the Iver – Laleham circuit 1 | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09218 | East Claydon Energy Limited | East Claydon 400kV Substation | 102109-204303 | Uprate Iver – West Weybridge circuit. | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09219 | East Claydon Energy Limited | East Claydon 400kV Substation | 102110-204304 | Uprate both Ealing – Laleham circuit 1 and 2 | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09220 | East Claydon Energy Limited | East Claydon 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09221 | East Claydon Energy Limited | East Claydon 400kV Substation | 101978-204103 | Uprate the Drakelow 400kV -to- Ratcliffe On Soar 400kV circuit #1 (DRAK4-RATS4-1) to summer pre-fault rating 2490MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09222 | East Claydon Energy Limited | East Claydon 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09223 | East Claydon Energy Limited | East Claydon 400kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #1 (RATS4-WILE4-1) to summer pre-fault rating 2490 MVA | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-09224 | East Claydon Energy Limited | East Claydon 400kV Substation | 102636-205302 | Upgrade the Cowley – Culham Jet – Didcot circuits | 2034-11-30
East Claydon Greener Grid Park | PRO-002314 | CS-12609 | East Claydon Energy Limited | East Claydon 400kV Substation | 104321-208409 |  | 2034-11-30
East Claydon GSP (NGED EM) | PRO-002893 | CS-12398 | National Grid Electricity Distribution (East Midlands) plc | East Claydon GSP (NGED EM) | 102023-204178 (EX9) |  | 2037-10-31
East Claydon GSP (NGED EM) | PRO-002893 | CS-12399 | National Grid Electricity Distribution (East Midlands) plc | East Claydon GSP (NGED EM) | 104209-208175 |  | 2037-10-31
East Claydon GSP (NGED WM) | PRO-001730 | CS-12640 | National Grid Electricity Distribution (West Midlands) Plc | East Claydon GSP (NGED EM) | 102023-204178 East Claydon |  | 2037-10-30
East Claydon GSP (NGED WM) | PRO-001730 | CS-12642 | National Grid Electricity Distribution (West Midlands) Plc | East Claydon GSP (NGED EM) | 104209-208175 East Claydon |  | 2037-10-30
East Claydon Storage | PRO-001573 | CS-07462 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 101282-202532 | Extension of East Claydon 400kV double busbar substation to provide space for the User’s generation connection bay. | 2026-10-01
East Claydon Storage | PRO-001573 | CS-07463 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 100893-201795 | 1. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT1. 2. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT2. | 2026-10-01
East Claydon Storage | PRO-001573 | CS-07464 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2026-10-01
East Claydon Storage | PRO-001573 | CS-07465 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 2026-10-01
East Claydon Storage | PRO-001573 | CS-07466 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2026-10-01
East Claydon Storage | PRO-001573 | CS-07467 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2026-10-01
East Claydon Storage | PRO-001573 | CS-07468 | EAST CLAYDON STORAGE LIMITED | East Claydon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2026-10-01
East Kilbride GSP (DNO) | PRO-003108 | CS-09816 | SP Distribution plc | East Kilbride 275/33kV GSP | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2026-08-19
East Kilbride GSP (DNO) | PRO-003108 | CS-09817 | SP Distribution plc | East Kilbride 275/33kV GSP | SPT-TOCO-518 | East Kilbride GSP - A bus section reactor will be installed on the SPT side of the GSP, with two new 33kV 3-panel switchboards | 2026-08-19
East Kilbride South GSP | PRO-003142 | CS-11345 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11346 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11347 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11348 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-3490 |  | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11349 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-3924 SS |  | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11350 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-3924 Cable |  | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11351 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-3924 OHL |  | 2033-10-31
East Kilbride South GSP | PRO-003142 | CS-11352 | SP Distribution plc | East Kilbride South 275/33kV |  |  | 2033-10-31
Easterhouse GSP | PRO-003143 | CS-12678 | SP Distribution plc | Easterhouse GSP | SPT-RI-2436 | Easterhouse 275kV fault level mitigation works - To allow a new generation / battery storage connection at Easterhouse 275kV the short circuit rating of Easterhouse 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of all equipment and structures to withstand a fault current of 40kA | 2027-06-30
Eaton Socon PV Storage | PRO-002218 | CS-09298 | CSE37 Limited | Eaton Socon 400kV Substation | 102106-204300 | 1. Make enable/build tertiary connections on the SGT 3. 2. Condition assessment of 13kV cable and other assets to confirm suitability for reuse. 3. Install earthing transformer on 13kV Tertiary connection. 4. Install 13kV Cable (if required) from 13kV Tertiary connection to the 13kV Disconnector. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2029-10-30
Eaton Socon PV Storage | PRO-002218 | CS-09299 | CSE37 Limited | Eaton Socon 400kV Substation | 101428-202800 | 1. The design, procurement and offline construction of a ten bay 400kV GIS substation at Eaton Socon; comprising of three feeder bays, three HV SGT bays, two busbar coupler bays, one busbar section bay and one Third Party bay. 2. The decommissioning and demolition of the existing 400kV substation at Eaton Socon following the completion of the new substation. | 2029-10-30
Eaton Socon Solar | PRO-001513 | CS-05024 | BROCKWELL STORAGE & SOLAR LIMITED | Eaton Socon 400kV Substation | 101215-202437 | Extension of the existing Eaton Socon 400kV Substation Main and Reserve Busbars to accommodate the User’s bay | 2028-10-31
Eaton Socon Solar | PRO-001513 | CS-05025 | BROCKWELL STORAGE & SOLAR LIMITED | Eaton Socon 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm² conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm² 90°C conductor to achieve a pre fault summer rating of 2400 MVA | 2028-10-31
Eaton Socon Solar | PRO-001513 | CS-05026 | BROCKWELL STORAGE & SOLAR LIMITED | Eaton Socon 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2028-10-31
Eaton Socon Solar | PRO-001513 | CS-05027 | BROCKWELL STORAGE & SOLAR LIMITED | Eaton Socon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2028-10-31
Eaton Socon Solar | PRO-001513 | CS-05028 | BROCKWELL STORAGE & SOLAR LIMITED | Eaton Socon 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2028-10-31
Ecclefechan Solar and BESS | PRO-004954 | CS-12236 | GREENTECH PROJECTS HOLDING UK LIMITED | Chapelcross GSP | SPT-RI-227 OHL |  | 2032-10-31
Ecclefechan Solar and BESS | PRO-004954 | CS-12237 | GREENTECH PROJECTS HOLDING UK LIMITED | Chapelcross GSP | SPT-RI-298 OHL |  | 2032-10-31
Ecclefechan Solar and BESS | PRO-004954 | CS-12238 | GREENTECH PROJECTS HOLDING UK LIMITED | Chapelcross GSP | SPT-RI-298 Cable |  | 2032-10-31
Ecclefechan Solar and BESS | PRO-004954 | CS-12239 | GREENTECH PROJECTS HOLDING UK LIMITED | Chapelcross GSP | SPT-RI-298 SS |  | 2032-10-31
Eccles GSP | PRO-003144 | CS-11670 | SP Distribution plc | Eccles GSP | SPT-RI-151b | In order to provide GBSQSS compliant connections for additional generation requiring to export from Hawick/Galashiels to Eccles, it is proposed to construct a new 132kV double circuit tower line between Galashiels and Eccles, and remove the existing U and AT Routes. | 2030-09-30
Eccles GSP | PRO-003144 | CS-11671 | SP Distribution plc | Eccles GSP | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2030-09-30
Eccles GSP | PRO-003144 | CS-11672 | SP Distribution plc | Eccles GSP | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 2030-09-30
Eccles GSP | PRO-003144 | CS-11673 | SP Distribution plc | Eccles GSP | SPT-RI-3660 |  | 2030-09-30
Eclipse at Creyke Beck 400/33kV Substation | PRO-002499 | CS-07732 | Eclipse Power Networks Limited | Creyke Beck IDNO Substation | 100964-201924 | 1. Installation of a new 150MVA rated 400/33kV SGT including HV and LV bays 2. Establish a new single busbar 33kV substation at Creyke Beck to be connected via the new 400/33kV SGT. 3. Installation of an earthing transformer connecting onto the 33kV busbar. 4. Protection and control modification as required 5. Associated civil works. 6. Miscellaneous and minor works. | 2028-06-30
Eclipse at Creyke Beck 400/33kV Substation | PRO-002499 | CS-07733 | Eclipse Power Networks Limited | Creyke Beck IDNO Substation | 100964-201978 | At Creyke Beck 400kV substation: Extend the substation to accommodate anew bay for a 400/33kV SGT HV Bay. | 2028-06-30
Eclipse at Creyke Beck 400/33kV Substation | PRO-002499 | CS-07734 | Eclipse Power Networks Limited | Creyke Beck IDNO Substation | 033837-201012 | At Creyke Beck 400kV Substation: Build a new 400kV double busbar compound with 2 feeders bay, 1 coupler bay, 1 section bay and connect 2 new interconnectors to Creyke Beck 400kV substation | 2028-06-30
Eclipse at Creyke Beck 400/33kV Substation | PRO-002499 | CS-07735 | Eclipse Power Networks Limited | Creyke Beck IDNO Substation | 033837-201648 | At Creyke Beck 400kV Substation: Move Creyke Beck - Thornton 2 circuit and Creyke Beck - Humber Refinery - Keadby circuit to the new GIS Creyke Beck 400kV Compound. | 2028-06-30
EcoKilwinning | PRO-003559 | CS-09971 | Econergy International Limited | Kilwinning 132/33kV | SPT-RI-2709 | CE Route Reconductoring and KILW-HUER Cable Replacement - It is proposed to reconductor the OHL route with 425mm² ‘Totara’ AAAC @ 75°C to achieve a minimum rating of 220MVA per circuit In addition to the OHL works,it is also proposed to replace the existing ~3.2km of 132kV cable between KILW-HUNF and HUNF-HUER to achieve a similar 220MVA rating per circuit. | 2031-10-31
EcoKilwinning | PRO-003559 | CS-09972 | Econergy International Limited | Kilwinning 132/33kV | SPT-RI-3052 - CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Rep. | CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Replacement | 2031-10-31
EcoKilwinning | PRO-003559 | CS-09973 | Econergy International Limited | Kilwinning 132/33kV | SPT-RI-3185 - KILW-HUNF-HUNE No.2 Cable Replacement | KILW-HUNF-HUNE No.2 Cable Replacement | 2031-10-31
EcoKilwinning | PRO-003559 | CS-09974 | Econergy International Limited | Kilwinning 132/33kV | SPT-RI-2710 | BU Route OHL Reconductor - As part of RIIO-T2 asset modernisation a number of assets across the transmission network have been identified for replacement. This TORI captures the asset modernisation work that is scheduled to be carried out on the 132kV OHL BU Route which runs between KILW-HUNF-HUNE at ~13km. The OHL circuit will be reconductored to achieve a minimum of 220MVA per circuit (Reconductor with 425mm² ‘Totara’ AAAC @ 75°C) | 2031-10-31
EcoKilwinning | PRO-003559 | CS-09975 | Econergy International Limited | Kilwinning 132/33kV | SPT-RI-3489 - Kilwinning-Hunterston 132kV DBB | Creation of a new 132/44kV substation around the Giffordland area is proposed to be established on a new portion of land under SPT-RI-3489. | 2031-10-31
EcoKincardine | PRO-003557 | CS-09659 | Econergy International Limited | Kincardine North 400kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2028-07-31
EcoKincardine | PRO-003557 | CS-09660 | Econergy International Limited | Kincardine North 400kV Substation | SPT-RI-2083 | Kincardine North – Wishaw 400kV reinforcement (DWUP)- Establish 400kV infrastructure through the centre of the network following the East Coast 400kV onshore incremental (ECUP) reinforcement, but in advance of the completion of existing Denny to Wishaw 400kV reinforcement (DWNO). The scope of this TORI will be aligned with the ‘DWUP’ option submitted to the 2021/22 Network Options Assessment (NOA) process. It is proposed to reconfigure and update existing 275kV single circuit between the Kincardine and Wishaw to 400kV operation to establish a new Kincardine North – Wishaw 400kV circuit. | 2028-07-31
EcoKincardine | PRO-003557 | CS-09661 | Econergy International Limited | Kincardine North 400kV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 2028-07-31
Edinbane Windfarm | PRO-000135 | CS-07398 | VATTENFALL WIND POWER LTD | Edinbane 132/33kV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2033-04-30
Edinbane Windfarm | PRO-000135 | CS-07399 | VATTENFALL WIND POWER LTD | Edinbane 132/33kV Substation | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 2033-04-30
Eggborough | PRO-002049 | CS-07504 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101821-203734 | Substation Control System database changes and the Relevant Tranmission Licencee’s operations commissioning resource | 2032-06-16
Eggborough | PRO-002049 | CS-07505 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2032-06-16
Eggborough | PRO-002049 | CS-07506 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm² sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570mm² strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570mm²should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 2032-06-16
Eggborough | PRO-002049 | CS-07507 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07508 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2032-06-16
Eggborough | PRO-002049 | CS-07509 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100798-201612 | At Cottam 400kV Substation: Uprate feeder bay disconnector and circuit breaker on the Cottam - West Burton circuit to provide a post fault summer rating of 3060MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07510 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101263-202505 | 1. Hotwire 2x620mm² sections of Grendon – Staythorpe circuit to standard operating temperature (170°C) | 2032-06-16
Eggborough | PRO-002049 | CS-07511 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07512 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101264-202506 | Cottam-Ryhall reconductoring with 3820MVA post-fault rating during Winter | 2032-06-16
Eggborough | PRO-002049 | CS-07513 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2032-06-16
Eggborough | PRO-002049 | CS-07514 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2032-06-16
Eggborough | PRO-002049 | CS-07515 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07516 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 2032-06-16
Eggborough | PRO-002049 | CS-07517 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm² conductor | 2032-06-16
Eggborough | PRO-002049 | CS-07518 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07519 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2032-06-16
Eggborough | PRO-002049 | CS-07520 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07521 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 030613-030613 | Uprate the Cottam - Staythorpe (2) circuit to provide a post-fault summer rating of 2800 MVA | 2032-06-16
Eggborough | PRO-002049 | CS-07522 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 033766-033766 | DRAX4-EGGB4 reconductor for 2250MVA pre-fault rating during Summer | 2032-06-16
Eggborough | PRO-002049 | CS-07523 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101276-202522 | Reconductoring of Ryhall to Eaton Socon line (A484) with 3820MVA postfault rating during Winter | 2032-06-16
Eggborough | PRO-002049 | CS-07524 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2032-06-16
Eggborough | PRO-002049 | CS-07525 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101869-203836 | Reconductoring of Cottam to Eaton Socon line (A481 and A482) with triple araucaria to achieve a 3820MVA post-fault Winter rating | 2032-06-16
Eggborough | PRO-002049 | CS-07526 | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 2032-06-16
Eggborough BESS | PRO-004997 | CS-11517 | Fig Power Limited | Eggborough 400kV Substation | 102501-205096 1 |  | 2035-10-30
Eggborough BESS | PRO-004997 | CS-11518 | Fig Power Limited | Eggborough 400kV Substation | 104217-208190 |  | 2035-10-30
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09639 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100161-200405 | Provision of the required space for the User to connect two of the generator bays at Eggborough 400kV substation. | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09640 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100528-201118 | Uprating of SGT3 (750MVA) at Thorpe Marsh 400kV substation with a 400/275kV 1100 MVA interbus transformer | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09641 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09642 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09643 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09644 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09645 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 102208-204431 | Uprating of OHL double cct from 2TW110 - 2TW169 and 4YR1 - 4YR40 which is part of the current Norton-Osbaldwick double circuit but will become the new Osbaldwick-Overton-Thormanby circuit | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09646 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100987-201984 | Uprate the existing bays in the Creyke Beck – Thornton 1 circuit to achieve a post fault summer rating of 3300MVA. | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09647 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100909-201825 | Uprate the existing bays in the Creyke Beck – Thornton 2 circuit (A323) to achieve a post fault summer rating of 3300MVA. | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09648 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09649 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09650 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09651 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 102173-204381 | Reconductor the Lackenby – Saltholme and Lackenby – Norton 400kV circuit with 2 x 772mm² Warwick conductor as per NOA LNRE | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09652 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm² Araucaria conductor | 2026-10-01
Eggborough CCGT - OCGT - BESS | PRO-000136 | CS-09653 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101775- 203564 | Hotwire the 4 x 400mm² sections of the Drax – Thornton 1 & 2 circuits for operation at 75°C | 2026-10-01
Elchies Wind Farm | PRO-000151 | CS-05654 | ELCHIES WIND LIMITED | Elchies 132/33kV Substation | Elchies Wind Farm H1 Works | The installation of an outdoor AIS 132kV transformer circuit breaker and disconnector at the Elchies 132/33kV Substation. Approximately 24km of 132kV circuit will be required to connect Elchies 132/33kV substation to the a new 132kV bay connected to the 132kV Busbar at Blackhillock 275/132kV substation. Approximately 200m of 132kV underground cable will be required to connect to the Blackhillock 132kV busbar | 2028-11-30
Elchies Wind Farm | PRO-000151 | CS-05655 | ELCHIES WIND LIMITED | Elchies 132/33kV Substation | SHET-RI-079 | Additional 275/132kV SGT’s at Blackhillock - Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. (SHETL- RI-079) | 2028-11-30
Elland Bulk PP | PRO-002778 | CS-08513 | Northern Powergrid (Yorkshire) Plc | Elland 132kV Substation | 102037-204194 | 1. Extension of mesh corner for installation of 240MVA, 275/132kV SGT 5 in Elland 275kV substation. 2. Installation and commissioning of associated equipment and circuit breaker at Elland 275kV substation. 3. Build, connect and commission a new 240MVA, 275/132kV super grid transformer and associated cable work along with 40kA rms breaker rating at Elland substation. 4. Extension the main and reserve busbars at Elland 132kV substation to accommodate the new SGT bay. 5. Extension the main and reserve busbars at Elland 132kV substation to accommodate the new user bay. 6. The auto close scheme to close the selected bus coupler circuit breaker(s) following the loss of an on-load super grid transformer during an outage of another super grid transformer at Elland 132kV substation. Also the scheme to connect the hot standby SGT to the section on outage/loss of an on-load supergrid transformer is observed. | 2036-10-30
Elland Bulk PP | PRO-002778 | CS-08514 | Northern Powergrid (Yorkshire) Plc | Elland 132kV Substation | 102753-205556 | Replacement of L43 and H43 with disconnector circuit breaker (DCB) at Elland 275kV substation. | 2036-10-30
Elmya Bathgate BESS | PRO-004416 | CS-10747 | RPC ELMYA CARNATION BATHGATE LIMITED | Armadale 400kv Substation | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2031-10-31
Elmya Bathgate BESS | PRO-004416 | CS-10748 | RPC ELMYA CARNATION BATHGATE LIMITED | Armadale 400kv Substation | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2031-10-31
Elmya Hunterston | PRO-003182 | CS-11333 | ELMYA RPC UK HUNTERSTON LIMITED | Hunterston 400/132kV | SPT-RI-3485 Cable |  | 2030-10-25
Elmya Hunterston | PRO-003182 | CS-11334 | ELMYA RPC UK HUNTERSTON LIMITED | Hunterston 400/132kV | SPT-RI-3485 SS |  | 2030-10-25
Elmya Hunterston | PRO-003182 | CS-11335 | ELMYA RPC UK HUNTERSTON LIMITED | Hunterston 400/132kV | SPT-RI-3485 OHL |  | 2030-10-25
Elmya Melbourne BESS | PRO-002424 | CS-11977 | ELMYA RPC UK MELBOURNE LIMITED | Thornton 400kV Substation | 101325-202642 5 |  | 2033-10-28
Elmya Melbourne BESS | PRO-002424 | CS-11978 | ELMYA RPC UK MELBOURNE LIMITED | Thornton 400kV Substation | 102197-204416 (Elmya Melbourne) |  | 2033-10-28
Elmya Melbourne BESS | PRO-002424 | CS-11979 | ELMYA RPC UK MELBOURNE LIMITED | Thornton 400kV Substation | 102197-204417 |  | 2033-10-28
Elmya Ryston BESS & PV | PRO-004923 | CS-12519 | ELMYA ENERGY UK 13 LIMITED | North Anglia Connection Node B 400kV Substation | 030447-030447 (Walpole) |  | 2034-10-31
Elmya Ryston BESS & PV | PRO-004923 | CS-12520 | ELMYA ENERGY UK 13 LIMITED | North Anglia Connection Node B 400kV Substation | 102380-204827 (GRETA) |  | 2034-10-31
Elmya Ryston BESS & PV | PRO-004923 | CS-12521 | ELMYA ENERGY UK 13 LIMITED | North Anglia Connection Node B 400kV Substation | 103057-206473 T |  | 2034-10-31
Elmya Ryston BESS & PV | PRO-004923 | CS-12522 | ELMYA ENERGY UK 13 LIMITED | North Anglia Connection Node B 400kV Substation | 103060-206476 |  | 2034-10-31
Elmya Ryston BESS & PV | PRO-004923 | CS-12523 | ELMYA ENERGY UK 13 LIMITED | North Anglia Connection Node B 400kV Substation | 104061-207990 |  | 2034-10-31
Elstree (tertiary) | PRO-000400 | CS-05034 | LON ENERGY 3 CONNECTION LIMITED | Letchmore Heath 132kV Substation | 003606-020741 | 1. Completion of the Elstree 132kV substation GIS transfer | 2037-10-31
Elstree (tertiary) | PRO-000400 | CS-05657 | LON ENERGY 3 CONNECTION LIMITED | Letchmore Heath 132kV Substation | 101379-202702 |  | 2037-10-31
Elstree (tertiary) | PRO-000400 | CS-12593 | LON ENERGY 3 CONNECTION LIMITED | Letchmore Heath 132kV Substation | 101965-208080 (infra) |  | 2037-10-31
Elstree 400MW Demand | PRO-002169 | CS-07695 | Equinix (LD-B) Limited | Letchmore Heath 132kV Substation | 102033-204189 | 1. Installation and commissioning of a fifth 360MVA 275/132kV SGT, including associated assets. 2. Extension of main and reserve busbar to facilitate User feeder bay connections. 3. Extensions of new 132kV GIS hall to accommodate busbar extension for new relevant transmission licensee and User GIS bays. | 2031-01-31
Elstree 400MW Demand | PRO-002169 | CS-07696 | Equinix (LD-B) Limited | Letchmore Heath 132kV Substation | 101826-203749 | 1. Installation and commissioning of a fourth 360MVA 275/132kV SGT, including associated assets. 2. Extension of main and reserve busbar to facilitate User feeder bay Connections 3. Extensions of new 132kV GIS hall to accommodate busbar extension for new relevant transmission licensee and User GIS bays. | 2031-01-31
Elstree 400MW Demand | PRO-002169 | CS-07697 | Equinix (LD-B) Limited | Letchmore Heath 132kV Substation | 101379-202701 | 1. Installation of new towers/modification of existing towers and associated OHL works to facilitate a double circuit turn in of the Elstree – Warley 1 & 2 overhead line circuits. 2. Design, procurement and construction of a 275kV double busbar substation; with associated bus couplers, bus sections, feeder bays and SGT HV bays. 3. Installation and commissioning of three 360MVA 275/132kV SGT, including associated assets. 4. Design, procurement and construction of a 132kV double busbar substation; with associated bus couplers, bus sections, SGT HV bays and skeletal User bays. 5. Works required to establish the new 275/132kV substation, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. | 2031-01-31
Elstree 400MW Demand | PRO-002169 | CS-07698 | Equinix (LD-B) Limited | Letchmore Heath 132kV Substation | 101659-203313 | Reconductoring the existing 2x400mm² conductor on the Tilbury- Warley double circuit with 2x500mm² conductor to achieve a pre- Fault summer rating of 1120MVA | 2031-01-31
Elstree 400MW Demand | PRO-002169 | CS-07699 | Equinix (LD-B) Limited | Letchmore Heath 132kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2031-01-31
Elstree 400MW Demand | PRO-002169 | CS-07700 | Equinix (LD-B) Limited | Letchmore Heath 132kV Substation | 102047-204214 | Reconductor Elstree 275kV – Elstree B 275kV double circuit | 2031-01-31
Elstree Energy Storage | PRO-003205 | CS-11953 | ELSTREE BATTERY STORAGE LIMITED | Elstree 132kV Substation | 101965-207246 |  | 2029-10-01
Elstree Energy Storage | PRO-003205 | CS-11954 | ELSTREE BATTERY STORAGE LIMITED | Elstree 132kV Substation | 101965-207247 |  | 2029-10-01
Elstree Energy Storage | PRO-003205 | CS-11955 | ELSTREE BATTERY STORAGE LIMITED | Elstree 132kV Substation | 101965-207253 |  | 2029-10-01
Elstree Energy Storage | PRO-003205 | CS-11956 | ELSTREE BATTERY STORAGE LIMITED | Elstree 132kV Substation | 101965-208080 | Extension of the existing Elstree 400kV via two interconnecting circuits between the existing Elstree 400kV busbars and the new 400kV busbar extension. Works involving the installation of new towers/modification of existing towers and associated OHL works to facilitate the connections of the Sundon – Borehamwood circuit and the second Elstree – St John Woods cable circuit into Elstree 400kV. | 2029-10-01
Elstree Energy Storage | PRO-003205 | CS-11957 | ELSTREE BATTERY STORAGE LIMITED | Elstree 132kV Substation | 101965-208096 |  | 2029-10-01
Elvanfoot (9.8 MW) Energy Storage | PRO-001721 | CS-04681 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 400/275/33kV | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 2027-04-30
Elvanfoot (9.8 MW) Energy Storage | PRO-001721 | CS-04682 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 400/275/33kV | SPT-RI-1876 | 2. Elvanfoot 132/33kV Grid Transformer - Install a 132/33kV 60MVA transformer at Elvanfoot to accommodate the increased generation connecting at 33kV into the site. (SPT-RI-1876) | 2027-04-30
EMERGE Centre | PRO-001462 | CS-06748 | UNIPER UK LIMITED | Ratcliffe-On-Soar 132kV Substation | 101178-202385 | Busbar protection and database/labelling changes to enable the connection of the User’s power station into the existing spare bay at Ratcliffe-On-Soar 132kV substation. | 2029-06-29
Enderby Tertiary | PRO-000430 | CS-05038 | CLUMP FARM SOLAR LIMITED | Enderby 400kV Substation | 100862-201723 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting Tertiary to User Assets for User’s connection. | 2027-08-01
Energy Isles | PRO-000447 | CS-05658 | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation | SHET-RI-116 | Kergord - Yell 132kV Connection - on Shetland install a new 132kV single circuit between the Kergord 132kV substation (established as part of SHET-RI-053) and a new tee point on Yell, to enable the connection of renewable generation. (SHET-RI-116) | 2032-10-30
Energy Isles | PRO-000447 | CS-05659 | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 2032-10-30
Energy Isles | PRO-000447 | CS-06672 | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation | Energy Isles Enabling Works | 1. Construction of approximately 20.6 km of a new 132 kV single circuit, comprising 2.0 km UGC and 18.6 km OHL. The circuit will run from the proposed South Yell Switching Station (constructed under SHET-RI-116) to the 132kV Energy Isles substation at the North end of Yell, terminating on a new 132 kV disconnector (103) to be installed within the Energy Isles Wind Farm substation building. The 132kV disconnector (103) will be connected to the TCA 132kV metering circuit breaker (105) and 132kV disconnector (107). 2. The 132 kV circuit will connect to the new South Yell 132 kV Switching Station via 132 kV busbar feeder bay, complete with 1 x 132 kV bus disconnector (307), 1 x 132 kV Circuit Breaker (305), 1 x 132 kV line disconnector (303) and associated protection equipment. | 2032-10-30
Enoch Hill | PRO-000152 | CS-05660 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 2025-05-30
Enoch Hill | PRO-000152 | CS-05661 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2025-05-30
Enoch Hill | PRO-000152 | CS-05662 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | SHET-RI-176 | Pauls Hill/Glenfarclas Circuit Turn In - Move the existing open point from Keith 132kV Substation to Pauls Hill substation and then turn in the Pauls Hill/Glenfarclas circuit to Blackhillock 132kV Substation andrebuild the circuit from Blackhillock substation to Craig watch Substation. This will include the Tee connection onto the existing circuit. (SHET-RI-176 | 2025-05-30
Enoch Hill | PRO-000152 | CS-05663 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2025-05-30
Enoch Hill | PRO-000152 | CS-05664 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | Enoch Hill Part 1 | 1. Extend the new 132kV substation compound at New Cumnock collector substation site location Grid Reference E251966, N608134 and install 1 x 132kV feeder bay. 2. Establish new 132/33kV substation compound at Enoch Hill Wind Farm site location, Grid Reference E255430,N608980 including the control /switch room 3. Installation of 0.25km of 132kV underground cable between New Cumnock and Enoch Hill Wind Farm substation. 4. Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 2025-05-30
Enoch Hill | PRO-000152 | CS-05665 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2025-05-30
Enoch Hill | PRO-000152 | CS-05666 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2025-05-30
Enoch Hill 2 Wind Farm | PRO-000478 | CS-05955 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 2 Wind Farm 33kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2027-04-30
Enoch Hill 2 Wind Farm | PRO-000478 | CS-05956 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 2 Wind Farm 33kV Substation | SPT-RI-237 | 3. Enoch Hill Collector 132/33kV Substation and associated 132132kV circuit – Establish a 132/33kV substation adjacent to Enoch Hill wind farm, in East Ayrshire. A new 132kV underground cable circuit will connect this new substation into a new 132kV bay in Board C at New Cumnock 132kV substation. The 132kV circuit will comprise of approximately 4.4km of underground cable (as opposed to OHL), which has been requested by Enoch Hill wind farm. (SPT-RI-237) | 2027-04-30
Enoch Hill 2 Wind Farm | PRO-000478 | CS-05957 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 2 Wind Farm 33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2027-04-30
Enoch Hill 2 Wind Farm | PRO-000478 | CS-06401 | RWE Renewables UK Onshore Wind Limited | Enoch Hill 2 Wind Farm 33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2027-04-30
EPL Suffolk | PRO-003916 | CS-11270 | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation | 020340-020340 (LC West Cam) |  | 2032-10-31
EPL Suffolk | PRO-003916 | CS-11271 | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation | 102226-204464 1 |  | 2032-10-31
EPL Suffolk | PRO-003916 | CS-11272 | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation | 102993-206448 |  | 2032-10-31
EPL Suffolk | PRO-003916 | CS-11273 | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation | 103063-206480 |  | 2032-10-31
EPL Suffolk | PRO-003916 | CS-11274 | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation | 103065-206482 |  | 2032-10-31
EPL Suffolk | PRO-003916 | CS-11275 | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation | 104273-208305 |  | 2032-10-31
Eppynt Common | PRO-001882 | CS-05039 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2026-10-31
Eppynt Common | PRO-001882 | CS-05040 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2026-10-31
Eppynt Common | PRO-001882 | CS-05042 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2026-10-31
Eppynt Common | PRO-001882 | CS-05043 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 2026-10-31
Eppynt Common | PRO-001882 | CS-05044 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2026-10-31
Eppynt Common | PRO-001882 | CS-05045 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2026-10-31
Eppynt Common | PRO-001882 | CS-05046 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 2026-10-31
Equinor Celtic Sea 2 | PRO-004038 | CS-09252 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09253 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09254 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09255 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09256 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09257 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09258 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Equinor Celtic Sea 2 | PRO-004038 | CS-09259 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 102622-205256 | 102622-205256 | 2036-12-06
ER MSM Energy | PRO-003480 | CS-09320 | ER PROJECT DEVELOPMENT CO LIMITED | Er Msm Energy 132kV Substation | ER MSM Energy | 1. Extending the Mossmorran substation compound. 2. Installing a new 400kV circuit breaker at Mossmorran. 3. Installing a new 400/132kV 240MVA SGT at Mossmorran. 4. Installing a new 132kV circuit breaker bay at Mossmorran substation. 5. Installing a new 132kV cable/OHL between Mossmorran and ER MSM Energy substation. This circuit should be capable of 222MVA. 6. Installing a new 132kV line disconnector at the ER MSM Energy substation. | 2030-10-31
ER MSM Energy | PRO-003480 | CS-09321 | ER PROJECT DEVELOPMENT CO LIMITED | Er Msm Energy 132kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2030-10-31
Erebus | PRO-000471 | CS-06300 | Blue Gem Wind Limited | Pembroke 132kV Substation | 100802-201618: | Re-utilise the spare bay at Pembroke 132kV substation to facilitate the connection of a generator bay and extend the Pembroke operational tripping scheme (OTS). | 2028-07-26
Erebus | PRO-000471 | CS-06301 | Blue Gem Wind Limited | Pembroke 132kV Substation | 100838-201680 | Replacement of feeder circuit breakers X105 and X305 of Pembroke - Swansea North 400 kV Circuits 1 and 3 and modification of feeder protection to allow faster operation times. | 2028-07-26
Eredine Wind Farm | PRO-002005 | CS-08465 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08466 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08467 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08468 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08469 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08470 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08471 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-08472 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2029-11-01
Eredine Wind Farm | PRO-002005 | CS-12453 | RWE Renewables UK Onshore Wind Limited | An Suidhe 275/33kV | Eredine Wind Farm-Sole Enabling Works | The sole use enabling works will include the installation of 1 x 275kV line disconnector and 1 x 275kV circuit breaker at the new proposed An Suidhe 275/33kV substation as well as 0.25km of 275kV underground cable to connect the transformer to the 275kV switchgear | 2029-11-01
Essendine | PRO-001643 | CS-04446 | MALLARD PASS SOLAR FARM LIMITED | Ryhall 400kV Substation | 101515-202984 | Facilitate installation of generator bay (Connection Asset) on Mesh Corner 2 at Ryhall 400kV Substation | 2028-01-01
Essendine | PRO-001643 | CS-05041 | MALLARD PASS SOLAR FARM LIMITED | Ryhall 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2028-01-01
Euchanhead Wind Farm | PRO-001011 | CS-05667 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | Euchanhead H1 SS | At Lorg substation, one 132kV line isolator will be installed to tee into the Lorg to Holmhill 132kV circuit. | 2030-10-29
Euchanhead Wind Farm | PRO-001011 | CS-05668 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | SPT-RI-211 | Construct a new 132kV switching station, named Holm Hill, and install a 132kV OHL circuit between the new site and the tee off points to Shepherds Rig and Lorg wind farms. At an appropriate tee-off point on the New Cumnock to Kendoon 132kV circuit, install the new Holm Hill 132kV Switching Station containing one 132kV circuit breaker with two associated disconnectors. Install ~8km of 132kV wood pole overhead line with High Temperature Low Sag (HTLS) EAGLE conductor (190°C, minimum summer pre-fault rating 295MVA) to the tee point between Shepherd’s Rig and Lorg wind farms. | 2030-10-29
Euchanhead Wind Farm | PRO-001011 | CS-05669 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2030-10-29
Euchanhead Wind Farm | PRO-001011 | CS-05670 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | Euchanhead H1 OHL | Installation of approximately 3.5km of 132kV wood pole overhead line from Euchanhead substation to Lorg 132kV substation. | 2030-10-29
Euchanhead Wind Farm | PRO-001011 | CS-05671 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2030-10-29
Ewerby | PRO-002017 | CS-07817 | Leoda Solar Farm Limited | Navenby 400kV Substation | 101687-203362 | Build a new Navenby 400kV Double Busbar Substation with 4 Feeder bays, and 1 Coupler Bay in the vicinity of tower 4ZM508. | 2029-10-30
Ewerby | PRO-002017 | CS-07818 | Leoda Solar Farm Limited | Navenby 400kV Substation | 101777-203568 | Establishment of new generator bay at new Navenby 400kV substation including bus bar extension and associate P&C and SCS modifications | 2029-10-30
Ewerby | PRO-002017 | CS-07819 | Leoda Solar Farm Limited | Navenby 400kV Substation | 101687-203363 | Establish a double turn in connection between the new 400kV substation and the West Burton – Bicker Fen 400kV circuit 1 and 2 | 2029-10-30
Ewerby | PRO-002017 | CS-07820 | Leoda Solar Farm Limited | Navenby 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2029-10-30
Ewerby | PRO-002017 | CS-07821 | Leoda Solar Farm Limited | Navenby 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2029-10-30
Ewerby | PRO-002017 | CS-07822 | Leoda Solar Farm Limited | Navenby 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2029-10-30
Ewerby | PRO-002017 | CS-07823 | Leoda Solar Farm Limited | Navenby 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2029-10-30
Ewerby | PRO-002017 | CS-07824 | Leoda Solar Farm Limited | Navenby 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2029-10-30
Ewerby | PRO-002017 | CS-07825 | Leoda Solar Farm Limited | Navenby 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2029-10-30
Ewerby | PRO-002017 | CS-07826 | Leoda Solar Farm Limited | Navenby 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2029-10-30
Exeter (Tertiary) | PRO-001047 | CS-05047 | PIVOTED POWER LLP | Exeter 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 2028-06-16
Exeter (Tertiary) | PRO-001047 | CS-05048 | PIVOTED POWER LLP | Exeter 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2028-06-16
Exeter (Tertiary) | PRO-001047 | CS-05049 | PIVOTED POWER LLP | Exeter 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2028-06-16
Exeter (Tertiary) | PRO-001047 | CS-06195 | PIVOTED POWER LLP | Exeter 400kV Substation | 100758-201149 | 1. Install earthing transformer on 13kV Tertiary connection 2.Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3.Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection. 4.Installation of a system to generator Category 2 operational intertripping scheme required for the conditions outlined in F3 Schedule 1. 5. Works required to connect the User to the Melksham Operational Tripping Scheme as described in F3 to be constructed by the User under Customer Build agreement | 2028-06-16
Exeter (Tertiary) | PRO-001047 | CS-11464 | PIVOTED POWER LLP | Exeter 400kV Substation | 100758-200691 |  | 2028-06-16
Exeter (Tertiary) | PRO-001047 | CS-11465 | PIVOTED POWER LLP | Exeter 400kV Substation | 100758-201149 | 1. Install earthing transformer on 13kV Tertiary connection 2.Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3.Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection. 4.Installation of a system to generator Category 2 operational intertripping scheme required for the conditions outlined in F3 Schedule 1. 5. Works required to connect the User to the Melksham Operational Tripping Scheme as described in F3 to be constructed by the User under Customer Build agreement | 2028-06-16
Exeter BESS | PRO-001666 | CS-12311 | Exeter Storage Limited | Exeter 400kV Substation | 104626-209312 |  | 2027-08-30
Exeter BESS | PRO-001666 | CS-12312 | Exeter Storage Limited | Exeter 400kV Substation | 104626-209313 |  | 2027-08-30
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-04760 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 101563-203114 | At Exeter Main 400kv substation: 1. Extension of existing Main busbar 2 and Reserve busbar 2 to accommodate the installation of generator bay by the User. 2. Local Works required to connect the User to Category 2 intertripping scheme as outline in Appendix F3. 3. Local Works required to connect the User to the Melksham operational Tripping Scheme as described in F3 | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-04761 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 101564-203118 | Extension of the Exeter Main 400kV substation into Blacklands Larch Plantation to facilitate Generation connections | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05050 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05051 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05052 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05054 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05055 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05056 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2029-12-31
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05057 | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2029-12-31
Exeter Main Tertiary | PRO-000452 | CS-05058 | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation | 100864-201727 | 1. Install earthing transformer on 13kV tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install Disconnector at the 13kV side connecting Tertiary to Connection Assets for User’s connection. 4. Works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. | 2024-05-01
Exeter Main Tertiary | PRO-000452 | CS-05059 | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 2024-05-01
Exeter Main Tertiary | PRO-000452 | CS-05060 | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2024-05-01
Eye Grid Services Facility | PRO-003688 | CS-08652 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102518-205117 | 1. At Yaxley 400kV substation build, connect and commission the new connection bay including but not limited to 400kV circuit breaker, onto the busbars at Yaxley 400kV substation. 2. Associated P & C for a Synch Comp connection. 3. Settlement Metering | 2025-12-31
Eye Grid Services Facility | PRO-003688 | CS-08653 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 032473-032473 | 1.Construction of a new 4 bay indoor GIS double busbar 400kV substation at Yaxley; including two feeder bays, generator bay and bus coupler bay. 2. Replacement of the existing suspension tower with a new terminal tower, tee the new substation to the Bramford – Norwich Main double OHL circuits. 3. Install of cable sealing end compound to provide a duck tee connection underneath OHL. 4. Install an additional circuit breaker on the LV side of SGT3 at Norwich Main to maintain compliance with the SQSS circuit complexity guidance. | 2025-12-31
Eye Grid Services Facility | PRO-003688 | CS-08654 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102333-204493 | Extension of the Main and Reserve busbars at Yaxley 400kV substation to facilitate User connection | 2025-12-31
Eye Grid Services Facility | PRO-003688 | CS-08655 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102516-205115 | Works to facilitate the Category 4 Operational Tripping scheme as described in Appendix F3 of the Bilateral Connection Agreement | 2025-12-31
Eye Grid Services Facility | PRO-003688 | CS-08656 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2025-12-31
Eye Grid Services Facility | PRO-003688 | CS-12580 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102333-204493 | Extension of the Main and Reserve busbars at Yaxley 400kV substation to facilitate User connection | 2025-12-31
Eye Grid Services Facility | PRO-003688 | CS-12581 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 032473-032473 (I) |  | 2025-12-31
FAB Link Interconnector | PRO-000281 | CS-05672 | FAB Link Limited | Exeter 400kV Substation | 32311O | Move SVC 5 isolator/disconnectors and extend substation busbars to the West to provide a skeletal bay to connect the HVDC interconnector. | 2032-09-30
FAB Link Interconnector | PRO-000281 | CS-05673 | FAB Link Limited | Exeter 400kV Substation | 32311SI | Extend the substation busbar to the East to provide a skeletal bay to connect the HVDC interconnector. | 2032-09-30
Fairburn Extension Wind Farm | PRO-004012 | CS-10778 | SSE Renewables Services (UK) Limited | Fairburn Extension 132/33kV Substation | SHET-RI-007a Beauly - Blackhillochk 400kV Double Circuit OHL |  | 2031-10-31
Fairburn Extension Wind Farm | PRO-004012 | CS-10779 | SSE Renewables Services (UK) Limited | Fairburn Extension 132/33kV Substation | SHET-RI-007b Beauly 400kV Busbar |  | 2031-10-31
Fairburn Extension Wind Farm | PRO-004012 | CS-10780 | SSE Renewables Services (UK) Limited | Fairburn Extension 132/33kV Substation | SHET-RI-065a Beauly 132kV Substation Redevelopment |  | 2031-10-31
Fairburn Extension Wind Farm | PRO-004012 | CS-10781 | SSE Renewables Services (UK) Limited | Fairburn Extension 132/33kV Substation | SHET-RI-065b Beauly 3rd SGT Replacement |  | 2031-10-31
Fairburn Extension Wind Farm | PRO-004012 | CS-10782 | SSE Renewables Services (UK) Limited | Fairburn Extension 132/33kV Substation | SHET-RI-273 |  | 2031-10-31
Fall of Warness | PRO-003812 | CS-11058 | THE EUROPEAN MARINE ENERGY CENTRE LIMITED | Eday GSP | SHET-RI-019 Dounreay to North West Orkney 132kV AC Link |  | 2030-05-30
Fall of Warness | PRO-003812 | CS-11059 | THE EUROPEAN MARINE ENERGY CENTRE LIMITED | Eday GSP | SHET-RI-075 - Orkney 132kV Reinforcement for GSP |  | 2030-05-30
Fancott | PRO-002174 | CS-07827 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 102046-204213 | Extend Sundon 400kV substation Main and Reserve 1 busbars for the provision of one User Bay | 2031-10-30
Fancott | PRO-002174 | CS-07828 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Fancott | PRO-002174 | CS-07829 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2031-10-30
Fancott | PRO-002174 | CS-07830 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2031-10-30
Fancott | PRO-002174 | CS-07831 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Fancott | PRO-002174 | CS-07832 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 102011-204165 | 3. At Norwich Main 400kV: Replace circuit breakers X320, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Fancott | PRO-002174 | CS-07833 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 102012-204166 | 4. At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Fancott | PRO-002174 | CS-07834 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Fancott | PRO-002174 | CS-07835 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Fancott | PRO-002174 | CS-07836 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2031-10-30
Fancott | PRO-002174 | CS-07837 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 2031-10-30
Fancott | PRO-002174 | CS-07838 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2031-10-30
Fancott | PRO-002174 | CS-07839 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 00468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2031-10-30
Fancott | PRO-002174 | CS-07850 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2031-10-30
Fancott | PRO-002174 | CS-07855 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2031-10-30
Fancott | PRO-002174 | CS-07859 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2031-10-30
Fancott | PRO-002174 | CS-07860 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2031-10-30
Fancott | PRO-002174 | CS-07861 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2031-10-30
Fancott | PRO-002174 | CS-07862 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2031-10-30
Fancott | PRO-002174 | CS-07863 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2031-10-30
Fancott | PRO-002174 | CS-07864 | KONA ASSET 2 LIMITED | Sundon 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2031-10-30
Fauldielaw | PRO-004503 | CS-11931 | Renewable Energy Systems Limited | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
Fauldielaw | PRO-004503 | CS-11932 | Renewable Energy Systems Limited | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
Fauldielaw | PRO-004503 | CS-11933 | Renewable Energy Systems Limited | Arbroath GSP | SHET-RI-234 | Tealing Solar Tee – Tealing 132kV Upgrade – Upgrade the 5.8km of single circuit overhead line between the Tealing Solar tee-point and Tealing 132kV substation. The circuit requires a minimum continuous summer rating of 170MVA | 2032-10-31
Fauldielaw | PRO-004503 | CS-11934 | Renewable Energy Systems Limited | Arbroath GSP | SHET-RI-284 |  | 2032-10-31
Fauldielaw | PRO-004503 | CS-11935 | Renewable Energy Systems Limited | Arbroath GSP | SHET-RI-289 |  | 2032-10-31
Fauldielaw | PRO-004503 | CS-11936 | Renewable Energy Systems Limited | Arbroath GSP | Fauldielaw Enabling Works | The Enabling Works comprise the following: 1. Installation of 2x 120MVA 132/33kV grid transformers, 2x 33kV metering circuit breakers and 33kV disconnectors on a suitable level platform at the new Arbroath 2 132/33kV GSP substation compound. The transmission connection asset works will also include appropriate 33kV cabling to the existing 33kV switchboard at Arbroath GSP. 2. The 33kV metering circuit breakers and 33kV disconnectors will be owned and operated by the Relevant Transmission Licensee. 3. Installation of 2x 132kV circuit breakers and 132kV disconnectors at the new Arbroath 2 132/33kV GSP substation compound, including 132kV cabling and works to connect the grid transformers. | 2032-10-31
Fawley GSP | PRO-002937 | CS-12367 | Southern Electric Power Distribution Plc | Fawley GSP | 102141-204346 (Fawley 132 Busbar) |  | 2038-10-31
Fawley GSP | PRO-002937 | CS-12368 | Southern Electric Power Distribution Plc | Fawley GSP | 104407-208524 (Fawley 132 Busbar) |  | 2038-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11529 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 100161-200456 (2) |  | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11530 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11531 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11532 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 102500-205094 |  | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11533 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 103145-206565 |  | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11534 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 103166-206585 |  | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11535 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 103338-206788 |  | 2033-10-31
FCC Thurcroft BESS | PRO-003268 | CS-11538 | Downing Renewable Developments LLP | Thorpe Marsh GSP | 103719-207359 |  | 2033-10-31
Fearna PSH 2 | PRO-004391 | CS-09947 | FEARNA PSH LIMITED | Fearna Pump Storage Hydro 2 400/15kV Substation | SHET-RI-211 | Fort Augustus 2 400kV Substation - Construct a new 400kV substation near to Fort Augustus. This new substation will connect to the second Beauly 400kV double circuit overhead line, connecting across the B4 boundary (the first southern connector from Beauly being the Beauly-Denny line). | 2036-11-11
Fearna PSH 2 | PRO-004391 | CS-09948 | FEARNA PSH LIMITED | Fearna Pump Storage Hydro 2 400/15kV Substation | SHET-RI-212 | Construct a new 400kV overhead line to run from Beauly, via the Fort Augustus 2 400kV substation, to run across the B4 boundary. | 2036-11-11
Fearna PSH 2 | PRO-004391 | CS-09949 | FEARNA PSH LIMITED | Fearna Pump Storage Hydro 2 400/15kV Substation | SPT-RI-2943 | To facilitate the generation connections around Fort Augustus in SSEN area (including ER FA Energy 700MW), in collaboration with SSEN, it is proposed to establish a second Beauly 400kV DC OHL circuit from the proposed SSEN’s ‘Fort Augustus 2 400kV substation’ to terminate into the SPT’s area. The location of the SPT’s new 400kV substation is currently under review, with an initial view that this is to be located at ‘Harburn 400kV substation’ on XJ Route. | 2036-11-11
Fearna PSH 2 | PRO-004391 | CS-09950 | FEARNA PSH LIMITED | Fearna Pump Storage Hydro 2 400/15kV Substation | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 2036-11-11
Feckenham | PRO-001600 | CS-04699 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101496-202909 | Extension of the existing Feckenham 400kV Main and Reserve Busbars to accommodate the User's bay. | 2029-07-21
Feckenham | PRO-001600 | CS-05062 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05063 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05064 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05065 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05066 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05067 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05068 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05069 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2029-07-21
Feckenham | PRO-001600 | CS-05070 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-001600 | CS-05071 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2029-07-21
Feckenham | PRO-001600 | CS-05072 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2029-07-21
Feckenham | PRO-001600 | CS-05073 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-07-21
Feckenham | PRO-002189 | CS-08908 | ENSO GREEN HOLDINGS X LIMITED | Feckenham 400kV Substation | 102107-204301 | Extension of 400kV main and reserve busbar of Feckenham 400kV substation to accommodate the user’s new section. | 2036-10-31
Feckenham | PRO-002189 | CS-08909 | ENSO GREEN HOLDINGS X LIMITED | Feckenham 400kV Substation | 102092-204283 | Install 400/66kV 180MVA SGT2 and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation | 2036-10-31
Feckenham | PRO-002189 | CS-08910 | ENSO GREEN HOLDINGS X LIMITED | Feckenham 400kV Substation | 102092-204285 | Install static VAR compensation system and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation. | 2036-10-31
Feckenham Energy Park | PRO-002378 | CS-08862 | GREEN ENERGY MAB LTD | Feckenham 400kV Substation | 102189-204410 | Extension of 400kV main and reserve busbar of Feckenham 400kV substation to accommodate the user’s bay | 2033-10-31
Feckenham Energy Park | PRO-002378 | CS-08863 | GREEN ENERGY MAB LTD | Feckenham 400kV Substation | 102092-204285 | Install static VAR compensation system and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation. | 2033-10-31
Feckenham Energy Park | PRO-002378 | CS-08865 | GREEN ENERGY MAB LTD | Feckenham 400kV Substation | 102092-204283 | Install 400/66kV 180MVA SGT2 and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation | 2033-10-31
Feckenham Green Energy Centre | PRO-001767 | CS-05361 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 101361-202681 | At Feckenham 275 kV substation, a. Extension of Feckenham 275kV substation b. Extension of main and reserve busbar of Feckenham 275 kV substation | 2032-10-30
Feckenham Green Energy Centre | PRO-001767 | CS-05362 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2032-10-30
Feckenham Green Energy Centre | PRO-001767 | CS-05363 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2032-10-30
Feckenham Green Energy Centre | PRO-001767 | CS-05364 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2032-10-30
Feckenham Green Energy Centre | PRO-001767 | CS-05365 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 101431-202809 | Hotwire A842 Cowley-Didcot 400kV circuit (6.496km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA | 2032-10-30
Feckenham Green Energy Centre | PRO-001767 | CS-05366 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 101431-202809 | Hotwire A842 Cowley-Didcot 400kV circuit (6.496km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA | 2032-10-30
Feckenham Green Energy Centre | PRO-001767 | CS-05367 | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation | 101431-202809 | Hotwire A842 Cowley-Didcot 400kV circuit (6.496km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA | 2032-10-30
Fell Wind Farm | PRO-001755 | CS-05258 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-05259 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-05260 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-05261 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-05262 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-05263 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | Fell Wind Farm Enabling Works | At Whiteneuk substation, installation of one 132kV circuit breaker and associated disconnectors and install approximately 5km of 132kV trident wood pole OHL (Poplar) between Whiteneuk and Fell substations. At Fell wind farm substation, install one 132kV line isolator | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-10875 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-274 SS |  | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-12052 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-296 Cable |  | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-12053 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-296 OHL |  | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-12054 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-296 SS |  | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-12055 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-2243 SS |  | 2029-10-31
Fell Wind Farm | PRO-001755 | CS-12056 | ENERGYFARM UK FELL LLP | SPT Margree collector substation | SPT-RI-4212 | 8. Margree 132kV Collector Substation - In order to accommodate the connection of Troston, Glenshimmeroch, Margree and Fell Wind farms via a shared solution as per customer’s request, it is proposed to establish a new 132/33kV collector substation at Margree location (on the New Cumnock / Blackcraig 132kV circuit). The scope of work comprises installation of one 132kV circuit breaker and associated disconnectors, one 132kV busbar and one 132kV circuit breaker and disconnector (on the Blackcraig 132kV circuit). The creation of this new collector substation is noted as part of SPT-TOCO-2143, SPTTOCO-505, SPT-RI-458 & SPT-TOCO-2160. All TOCO Mod-App’s must be accepted to consider this contracted. Upon the acceptance of all 4 Mod-App’s, this TORI will supersede SPT-RI-274 - Glenshimmeroch Collector Substation. In this event, SPT-RI-274 will be withdrawn. Any abortive costs will be detailed in the charging section. (SPT-RI-4212) | 2029-10-31
Fenwick Solar Project | PRO-001915 | CS-07989 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 101679-203342 | Extension of busbars at Thorpe Marsh 400kV DBB substation to provide connection point for Customer's bay including P&C, database updates, Assurance, Operation and Commissioning works. | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07990 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07991 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07992 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07993 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07994 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07995 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 101276-202522 | Reconductoring of Ryhall to Eaton Socon line (A484) with 3820MVA postfault rating during Winter | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07996 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 101264-202506 | Cottam-Ryhall reconductoring with 3820MVA post-fault rating during Winter | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07997 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07998 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-07999 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-08000 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-08001 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-08002 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-08003 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-08004 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2032-04-16
Fenwick Solar Project | PRO-001915 | CS-08005 | FENWICK SOLAR PROJECT LIMITED | Thorpe Marsh 400kV Substation | 100944-201882 | Build a new 400kV Mablethorpe Substation with 6 Bays - 4 Feeder bays, 1 Coupler Bay, 2 Section Breakers Main & Reserve | 2032-04-16
Ferrybridge A GSP (Yorkshire) | PRO-003008 | CS-12363 | Northern Powergrid (Yorkshire) Plc | Ferrybridge A GSP | 102500-205094 |  | 2039-10-30
Ferrybridge A GSP (Yorkshire) | PRO-003008 | CS-12364 | Northern Powergrid (Yorkshire) Plc | Ferrybridge A GSP | 103133-206627 (EX9) |  | 2039-10-30
Ferrybridge A GSP (Yorkshire) | PRO-003008 | CS-12365 | Northern Powergrid (Yorkshire) Plc | Ferrybridge A GSP | 103203-206628 (EX9) |  | 2039-10-30
Ferrybridge A GSP (Yorkshire) | PRO-003008 | CS-12366 | Northern Powergrid (Yorkshire) Plc | Ferrybridge A GSP | 103204-206629 (EX9) |  | 2039-10-30
Ferrybridge D | PRO-001020 | CS-05074 | Keadby Generation Limited | Ferrybridge C 275kV Substation | 100049-200108 | 1. Provision of two skeletal bays for the User to connect at Ferrybridge ‘C’ 275kV substation. 2. To facilitate the User Works within the connection site. 3. SCS database changes and busbar protection modification at Ferrybridge ‘C’ 275kV substation. The existing generator skeletal bay assets are to be transferred to the User, subject to approval from The Authority If the existing disconnected bay assets cannot be transferred to the User, The Relevant Transmission Licensee will revise the construction works accordingly. | 2030-10-04
Ferrymuir Energy Storage | PRO-001352 | CS-06224 | FERRYMUIR ENERGY STORAGE LIMITED | Cupar GSP | SPT-RI-234 | Glenniston 132kV Substation Reinforcement and Associated Works to increase the thermal rating of the equipment: a. Glenniston 132kV T1 LVDOC Relay. b. Glenniston 132kV T2 LVDOC Relay. In addition, replacement of the 132kV disconnectors 124 and 128 and bus section circuit breaker 120 to achieve a minimum rating of 185MVA. | 2022-10-31
Ferrymuir Energy Storage | PRO-001352 | CS-06225 | FERRYMUIR ENERGY STORAGE LIMITED | Cupar GSP | SPT-RI-1577 | Cupar GSP LV Protection Modifications - In order to remain within SPEN policy (PROT-01-107), the existing Alstom/Areva K-series LVDOC relays on the T1 and T2 and Cupar 132/33kV GSP are required to be replaced with a LVDOC relay which utilises a voltage controlled characteristic such that reverse power flow is only limited by the rating of the transformer (including emergency ratings). | 2022-10-31
Fetteresso Wind Farm | PRO-000927 | CS-05692 | FETTERESSO WIND LIMITED | Mid Hill GSP | No Enabling Works | No enabling works | 2026-09-30
Fferm Solar Pentir | PRO-001049 | CS-04646 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 101039-202076 | 1. Install a tertiary cable box or bushings on the SGT 2. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Local works required to connect the User to the Pentir Operational Tripping Scheme as described in F3 to the Bilateral Connection Agreement. | 2027-05-01
Fferm Solar Pentir | PRO-001049 | CS-05053 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 032018-032018 | Reconductor the existing Bodelwyddan - Connah’s Quay Circuits 1 and 2 | 2027-05-01
Fferm Solar Pentir | PRO-001049 | CS-05075 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 032018-032019 | Reconductor the existing Pentir-Bodelwyddan Circuits 1 and 2 Increase Thermal Capability of A220 Pentir-Trawsfynydd circuit; | 2027-05-01
Fferm Solar Pentir | PRO-001049 | CS-05076 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 033711-033711 | Uprating of current cable sections | 2027-05-01
Fferm Solar Pentir | PRO-001049 | CS-05077 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2027-05-01
Fferm Solar Pentir | PRO-001049 | CS-05078 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 033712-033712 | Reconductor existing twin Sorbus OHL section to twin Araucaria. | 2027-05-01
Fiddes Battery Storage | PRO-001831 | CS-07245 | FIDDES BATTERY LIMITED | Fiddes GSP | Fiddes A1 Works | Installation of two new 275kV transformer circuit breakers, and associated disconnectors, connected to the new 275/33kV transformer arrangement. | 2028-10-31
Fiddes Battery Storage | PRO-001831 | CS-07246 | FIDDES BATTERY LIMITED | Fiddes GSP | Fiddes A1 Works | Installation of two new 275kV transformer circuit breakers, and associated disconnectors, connected to the new 275/33kV transformer arrangement. | 2028-10-31
Fiddes Battery Storage | PRO-001831 | CS-07247 | FIDDES BATTERY LIMITED | Fiddes GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2028-10-31
Fiddlers Ferry BESS | PRO-003897 | CS-12500 | FIDDLERS FERRY LTD | Fiddlers Ferry 275kV Substation | 102510-205108 |  | 2027-10-31
Fiddler's Ferry Data Centre | PRO-005020 | CS-12342 | PEEL NRE DEVELOPMENTS ACQUISITIONS NO.1 LIMITED | Manchester North Connection Node C 400kV Substation | 104403-208515 |  | 2037-10-30
Fiddler's Ferry Data Centre | PRO-005020 | CS-12343 | PEEL NRE DEVELOPMENTS ACQUISITIONS NO.1 LIMITED | Manchester North Connection Node C 400kV Substation | 104403-208516 |  | 2037-10-30
Fiddler's Ferry Data Centre | PRO-005020 | CS-12344 | PEEL NRE DEVELOPMENTS ACQUISITIONS NO.1 LIMITED | Manchester North Connection Node C 400kV Substation | 104403-208517 |  | 2037-10-30
Fiddler's Ferry Data Centre | PRO-005020 | CS-12345 | PEEL NRE DEVELOPMENTS ACQUISITIONS NO.1 LIMITED | Manchester North Connection Node C 400kV Substation | 104403-208522 |  | 2037-10-30
Field Auchteraw | PRO-002640 | CS-04400 | FIELD AUCHTERAW LTD. | Fort Augustus GSP | Replacement of the existing 15MVA transformer to a 90MVA transformer | The replacement of the existing 15MVA 132/33kV Transformer with a redeployed 90MVA 132/33kV Transformer at the GSP. The works shall include the foundation and associated compound works to facilitate the new equipment. A new 33kV switchboard will be installed to connect to the Host DNO’s equipment. | 2022-12-31
Field Auchteraw | PRO-002640 | CS-04401 | FIELD AUCHTERAW LTD. | Fort Augustus GSP | Installation of a 132kV Transformer Circuit Breaker and Disconnector at Fort Aug | The installation of a 132kV Transformer Circuit Breaker and Disconnector at Fort Augustus GSP. | 2022-12-31
Fife Grid Services | PRO-000453 | CS-04634 | KINCARDINE GRID 3 LTD | Fife Grid Services Facility 275kV Substation | SPT-RI-1745 | Kincardine to Fife Grid 275kV Switchgear and Cable Works - To facilitate the connection of contracted generation from the Relevant Transmission Licensee’s Fife Grid Services Facility 275kV substation to Kincardine 275kV substation, it is proposed to install a new 275kV busbar and associated 275kV disconnectors and approximately 0.9km of 275kV underground cable circuit to Kincardine 275kV substation. At Kincardine 275kV substation, install a new 275kV GIS switchgear and associated disconnectors and one 275kV line isolator. | 2027-07-30
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06342 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100874-201758 | Build a new 11 bay East Anglia Coastal 400 kV double busbar substation – 2off busbar couplers, 1 Main & Reserve section, 8 feeder bays | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06343 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100879-201769 | Install 2-off 225 Mvar MSCs at Bramford 400 kV substation.Extension of Bramford 400 kV substation to accommodate the new MSCs. | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06344 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100874-201760 | Build a new 400 kV double circuit between Sizewell 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter postfault. Extension of Sizewell 400 kV substation to accommodate 2 feeders from East Anglia Coastal 400 kV. | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06345 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06346 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06347 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100875-201762 | Build a second new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06348 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100596-201227 | Single Bay Extension at East Anglia Coastal 400 kV substation to facilitate the User’s connection. | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06349 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06350 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation |  |  | 2030-10-31
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06351 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2030-10-31
Flash Solar Farm | PRO-001634 | CS-04685 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 101565-203122 | Extend the busbar at Staythorpe 400kV substation to make provision for the User to connect their generator bay. | 2027-05-31
Flash Solar Farm | PRO-001634 | CS-05079 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm² conductor and uprate the cable section to 3 cores per phase | 2027-05-31
Flash Solar Farm | PRO-001634 | CS-05080 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2027-05-31
Flash Solar Farm | PRO-001634 | CS-05084 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2027-05-31
Flash Solar Farm | PRO-001634 | CS-05085 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 033946-033946 | At Keadby 400kV substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2027-05-31
Flash Solar Farm | PRO-001634 | CS-05086 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm² conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm² 90°C conductor to achieve a pre fault summer rating of 2400 MVA | 2027-05-31
Flash Solar Farm | PRO-001634 | CS-05087 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2027-05-31
Flatterton Farm | PRO-003048 | CS-10241 | BIG BATTERY (FLATTERTON FARM) LIMITED | Spango Valley 132/33kV GSP | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2027-05-14
Fleet (Tertiary) | PRO-001087 | CS-05081 | CSE23 LIMITED | Fleet 400kV Substation | 100851-201705 | 1. Extend Mesh Corner 3 at Fleet 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new bus bar, 33kV substation at Fleet to be connected via new 400/33kV SGT. 4. Installation of an earthing transformer connecting onto the 33kV busbar. 5. Installation of new circuit breaker on HV side of SGT3A.* *The exact placement will be confirmed in the detailed design stage. | 2026-10-31
Fleet (Tertiary) | PRO-001087 | CS-05088 | CSE23 LIMITED | Fleet 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2026-10-31
Fleet (Tertiary) | PRO-001087 | CS-05089 | CSE23 LIMITED | Fleet 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2026-10-31
Fleet (Tertiary) | PRO-001087 | CS-11463 | CSE23 LIMITED | Fleet 400kV Substation | 100851-201705 (Fleet) |  | 2026-10-31
Fleet EGH (Tertiary) | PRO-000544 | CS-05090 | FLEET GREEN LIMITED | Fleet 400kV Substation | 100901-201810 | 1. Install earthing transformer 2. Install a tertiary cable box or bushings on the SGT1A 3. Install 13kV cable (if required) from Tertiary cable box or bushings to the earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 to the Bilateral Connection Agreement. | 2027-01-13
Fleet EGH (Tertiary) | PRO-000544 | CS-05092 | FLEET GREEN LIMITED | Fleet 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 2027-01-13
Fleet EGH (Tertiary) | PRO-000544 | CS-05093 | FLEET GREEN LIMITED | Fleet 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2027-01-13
Fleet EGH (Tertiary) | PRO-000544 | CS-05094 | FLEET GREEN LIMITED | Fleet 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2027-01-13
Fleet Solar PV | PRO-002814 | CS-11254 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 100851-201705 (1) |  | 2028-08-07
Fleet Solar PV | PRO-002814 | CS-11255 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 102677-205364 |  | 2028-08-07
Fleet Tertiary | PRO-000429 | CS-05095 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 100851-201705 | 1. Extend Mesh Corner 3 at Fleet 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new bus bar, 33kV substation at Fleet to be connected via new 400/33kV SGT. 4. Installation of an earthing transformer connecting onto the 33kV busbar. 5. Installation of new circuit breaker on HV side of SGT3A.* *The exact placement will be confirmed in the detailed design stage. | 2025-11-30
Fleet Tertiary | PRO-000429 | CS-05096 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 2025-11-30
Fleet Tertiary | PRO-000429 | CS-05098 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2025-11-30
Fleet Tertiary | PRO-000429 | CS-05099 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2025-11-30
Flemyland Battery Storage | PRO-002360 | CS-08262 | Flemyland Battery Storage Limited | Kilwinning 132/33kV | SPT-RI-2709 | CE Route Reconductoring and KILW-HUER Cable Replacement - It is proposed to reconductor the OHL route with 425mm² ‘Totara’ AAAC @ 75°C to achieve a minimum rating of 220MVA per circuit In addition to the OHL works,it is also proposed to replace the existing ~3.2km of 132kV cable between KILW-HUNF and HUNF-HUER to achieve a similar 220MVA rating per circuit. | 2027-10-26
Flemyland Battery Storage | PRO-002360 | CS-08263 | Flemyland Battery Storage Limited | Kilwinning 132/33kV | SPT-RI-2710 | BU Route OHL Reconductor - As part of RIIO-T2 asset modernisation a number of assets across the transmission network have been identified for replacement. This TORI captures the asset modernisation work that is scheduled to be carried out on the 132kV OHL BU Route which runs between KILW-HUNF-HUNE at ~13km. The OHL circuit will be reconductored to achieve a minimum of 220MVA per circuit (Reconductor with 425mm² ‘Totara’ AAAC @ 75°C) | 2027-10-26
Fordtown Battery Storage | PRO-000888 | CS-04469 | SUSI EELPOWER FORDTOWN LIMITED | Kintore GSP | Fordtown Enabling Works | The Relevant Transmission Licensee shall provide status signals to the Host Distribution Network Operator from the 33kV breakers 1TO, 2TO and 3TO, and the 132kV circuit breakers 1310, 110 and 210. This will also include the provision signals for a loss of mains scheme as requested by the Host Distribution Network Operator. | 2022-07-01
Forsa Energy Denny BESS | PRO-004971 | CS-10790 | FORSA ENERGY HOLDINGS LIMITED | FORSA ENERGY DENNY BESS 132KV GRID SUPPLY POINT SUBSTATION | SPT-RI-003 | Denny-Strathaven 400kV Reinforcement - Construct a new 400kV double circuit overhead line from Bon-nybridge to Newarthill and re-configure associated sites to establish a fourth north to south dou-ble circuit Supergrid route through the Scottish central belt. One side of the new overhead line will oper-ate at 400kV, the other at 275kV. This reinforcement will establish Denny-Bonnybridge, Bonnybridge-Wishaw, Wishaw-Strathaven No.2 and Wishaw-Torness 400kV circuits and a Denny-Newarthill-Easterhouse 275kV circuit. (SPT-RI-003) | 2030-10-31
Forsa Energy Denny BESS | PRO-004971 | CS-10791 | FORSA ENERGY HOLDINGS LIMITED | FORSA ENERGY DENNY BESS 132KV GRID SUPPLY POINT SUBSTATION | SPT-RI-2815 | New Denny North 275/123kV Super Grid Transformer- At Denny North substation it is proposed to install a new 275/132kV 240MVA Super Grid Transformer to allow for Stirling 132kV and Devonside 132kV substations to be radially fed via Denny North. Reconfiguration of the existing Denny North – Bonnybridge 132kV (CN Route) high capacity circuit is also proposed to create two 132kV feeder circuits between Denny North and Stirling 132kV/Devonside 132kV. These two circuits will be reinforced to accommodate a pre-fault summer rating of 240MVA on each of these circuits. Normally Open Points will be created at Bonnybridge 132kV and Westfield 132kV substations. The works outlined in this TORI are subject to the works being completed under SPT-RI-2083 (Kincardine North – Wishaw 400kV Reinforcement) | 2030-10-31
Forss BP Wind Turbine | PRO-000639 | CS-05702 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2025-08-31
Forss BP Wind Turbine | PRO-000639 | CS-05703 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2025-08-31
Fragland Solar and BESS | PRO-006072 | CS-12495 | GREENTECH PROJECTS HOLDING UK LIMITED | Abernethy 2 GSP | SHET-RI-255 |  | 2033-10-31
Fraserburgh Energy Plant | PRO-001820 | CS-07440 | FRASERBURGH ENERGY LTD | Fraserburgh 132 kV | Fraserburgh Enabling Works | The Enabling Works Stage 2 comprise the completion of the One Off Works Stage 1 and the following: 1. An additional intertripping scheme is required for the loss of one of the 132kV circuits between St Fergus and Peterhead (VS1, VS2 and VS3). These signals will be provided to the User via a separate relay panel within the 33kV Switchroom from the signals described below. Provision of status signals are required for the following: a. Status signals from the 132kV circuit breakers and disconnectors at St Fergus Switching Station b. Status signals from the 132kV line circuit breakers and disconnectors at the Salamander tee in point. | 2024-09-20
Fraserburgh Energy Plant | PRO-001820 | CS-07441 | FRASERBURGH ENERGY LTD | Fraserburgh 132 kV | Fraserburgh Enabling Works | The Enabling Works Stage 2 comprise the completion of the One Off Works Stage 1 and the following: 1. An additional intertripping scheme is required for the loss of one of the 132kV circuits between St Fergus and Peterhead (VS1, VS2 and VS3). These signals will be provided to the User via a separate relay panel within the 33kV Switchroom from the signals described below. Provision of status signals are required for the following: a. Status signals from the 132kV circuit breakers and disconnectors at St Fergus Switching Station b. Status signals from the 132kV line circuit breakers and disconnectors at the Salamander tee in point. | 2024-09-20
Fraserburgh Energy Storage | PRO-002258 | CS-08859 | FLEXION ENERGY UK STORAGE LTD | Fraserburgh GSP | SHET-RI-150 | Inverguie Tee – Peterhead 132kV Reconductoring – Reconductor approximately 6.7km of 132kV OHL between the Inverguie Tee and Peterhead 132kV substation. The circuit should be reconductored with a conductor capable of a minimum summer pre-fault rating of 226MVA | 2027-10-31
Fraserburgh Energy Storage | PRO-002258 | CS-08860 | FLEXION ENERGY UK STORAGE LTD | Fraserburgh GSP | SHET-RI-189 | Strichen-Fraserburgh to St Fergus 132kV OHL Reconductoring - Upgrade a section of the existing Strichen/Fraserburgh to St Fergus Switching Station 132kV SF1/SF2 OHL double circuit (approx. 6.2km) to have a minimum summer pre-fault rating of 231MVA. | 2027-10-31
Fraserburgh Energy Storage | PRO-002258 | CS-08861 | FLEXION ENERGY UK STORAGE LTD | Fraserburgh GSP | SHET-RI-151 | Peterhead – St Fergus 132kV Line Works – Overhead line works to bring the 132kV circuit to ground, including any required modifications. Design and installation of one 132kV circuit breaker with three 132kV disconnectors and associated protection and control equipment for each of the two circuits. | 2027-10-31
Frodsham GSP | PRO-002953 | CS-12149 | SP MANWEB PLC | Frodsham GSP | 100755-201563 Frodsham 25 |  | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08328 | Frodsham Solar Limited | Frodsham 132kV | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08330 | Frodsham Solar Limited | Frodsham 132kV | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08332 | Frodsham Solar Limited | Frodsham 132kV | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08333 | Frodsham Solar Limited | Frodsham 132kV | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08336 | Frodsham Solar Limited | Frodsham 132kV | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08337 | Frodsham Solar Limited | Frodsham 132kV | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08338 | Frodsham Solar Limited | Frodsham 132kV | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08339 | Frodsham Solar Limited | Frodsham 132kV | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08340 | Frodsham Solar Limited | Frodsham 132kV | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm² conductor | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08341 | Frodsham Solar Limited | Frodsham 132kV | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08342 | Frodsham Solar Limited | Frodsham 132kV | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 2029-04-30
Frodsham Solar Park | PRO-001952 | CS-08343 | Frodsham Solar Limited | Frodsham 132kV | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2029-04-30
Fron Goch | PRO-001563 | CS-04723 | NANT MITHIL ENERGY PARK LIMITED | Pont Abraham 132KV | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2026-10-31
Fron Goch | PRO-001563 | CS-04724 | NANT MITHIL ENERGY PARK LIMITED | Pont Abraham 132KV | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 2026-10-31
Fron Goch | PRO-001563 | CS-04725 | NANT MITHIL ENERGY PARK LIMITED | Pont Abraham 132KV | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2026-10-31
Gaerwen Wind Farm | PRO-001550 | CS-04483 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101269-202512 | 1. Establish a new four bay 400kV double busbar substation1 adjacent to the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. Substation to comprise two feeder bays, a bus coupler bay and a skeletal bay for the User to connect their generator circuit 2. Connect the substation to the Main interconnected system via a turn in of the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. 3. Establish a CUSC Category 4 System to generator intertrip scheme to monitor the circuits between Pentir and Trawsfynydd and Trawsfynydd Gwyddelwern – Connahs Quay and Legacy 400kV substations | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-04484 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05091 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05100 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05101 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05102 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05103 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05104 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-06-01
Gaerwen Wind Farm | PRO-001550 | CS-05105 | RWE Renewables UK Onshore Wind Limited | Gwyddelwern 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2027-06-01
Galileo 09 | PRO-004798 | CS-11470 | GALILEO 09 LIMITED | Oswestry Substation | 102004-204152 |  | 2037-10-31
Galileo 09 | PRO-004798 | CS-11471 | GALILEO 09 LIMITED | Oswestry Substation | 103944-207819 |  | 2037-10-31
Galileo 09 | PRO-004798 | CS-11472 | GALILEO 09 LIMITED | Oswestry Substation | 103946-207821 |  | 2037-10-31
Galileo 10 | PRO-003953 | CS-09976 | GALILEO 10 LIMITED | Armadale 132kV Substation | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2031-10-31
Galileo 10 | PRO-003953 | CS-09977 | GALILEO 10 LIMITED | Armadale 132kV Substation | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2031-10-31
Gallos | PRO-002734 | CS-09267 | Corio Generation Limited | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Gallos | PRO-002734 | CS-09268 | Corio Generation Limited | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
Gallos | PRO-002734 | CS-09269 | Corio Generation Limited | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
Gallos | PRO-002734 | CS-09270 | Corio Generation Limited | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
Gallos | PRO-002734 | CS-09271 | Corio Generation Limited | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Gallos | PRO-002734 | CS-09272 | Corio Generation Limited | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
Gallos | PRO-002734 | CS-09273 | Corio Generation Limited | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Gallos | PRO-002734 | CS-09274 | Corio Generation Limited | Alverdiscott 400kV Substation | 102692-205383 |  | 2036-12-06
Gammidge PV & BESS Park | PRO-001649 | CS-07032 | CS UK HOLDINGS III LIMITED | Grendon 132kV Substation | 101103-202203 | Extension of the existing Grendon 132kV substation Main and Reserve Busbars to accommodate the User’s bay | 2027-10-15
Garbet Wind Farm | PRO-001813 | CS-07694 | GARBET WIND FARM LLP | Keith 2 132/33kV GSP Substation | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2026-10-31
Garlogie B-1 | PRO-004640 | CS-11591 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11592 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11593 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11594 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11595 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11596 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11597 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie B-1 | PRO-004640 | CS-11598 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie B-2 | PRO-004641 | CS-11599 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie B-2 | PRO-004641 | CS-11600 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie B-2 | PRO-004641 | CS-11601 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie B-2 | PRO-004641 | CS-11602 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie B-2 | PRO-004641 | CS-11603 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie B-2 | PRO-004641 | CS-11604 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production B 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11605 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11606 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11607 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11608 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11609 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11610 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11611 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie C-1 | PRO-004642 | CS-11612 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP |  |  | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11613 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11614 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11615 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11616 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11617 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11618 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie C-2 | PRO-004643 | CS-11619 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production C 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie Production A | PRO-003218 | CS-11620 | Eclipse Power Networks Limited | Garlogie Production A 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie Production A | PRO-003218 | CS-11621 | Eclipse Power Networks Limited | Garlogie Production A 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie Production A | PRO-003218 | CS-11622 | Eclipse Power Networks Limited | Garlogie Production A 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie Production A | PRO-003218 | CS-11623 | Eclipse Power Networks Limited | Garlogie Production A 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie Production A | PRO-003218 | CS-11624 | Eclipse Power Networks Limited | Garlogie Production A 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie Production A | PRO-003218 | CS-11625 | Eclipse Power Networks Limited | Garlogie Production A 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11626 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11627 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11628 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11629 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11630 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11631 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie Production B | PRO-003219 | CS-11632 | Eclipse Power Networks Limited | Garlogie Production B 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11633 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11634 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11635 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11636 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11637 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11638 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie Production C | PRO-003220 | CS-11639 | Eclipse Power Networks Limited | Garlogie Production C 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11577 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11578 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11579 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11580 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11581 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11582 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie PV and BESS A-1 | PRO-004636 | CS-11583 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11584 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11585 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11586 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11587 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11588 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SHET-RI-246 - Garlogie 275kV Substation |  | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11589 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Garlogie PV and BESS A-2 | PRO-004637 | CS-11590 | GARLOGIE ENERGY CENTRE LIMITED | Garlogie Production A 275/33kV GSP | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04620 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202058/ 101032-202059/ 101032-202069 | 1. Establish a new 400kV double busbar substation comprising 2 feeder bays, a bus coupler, a MSCDN bay and 4 SGT bays. 2. Establish a new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler,4 SGT bays, an earthing transformer bay and 2 feeder bays. 3. Install a 225MVAr MSCDN at the 400kV substation. 4. Connect an earthing transformer to the 132kV substation 5. Install an earthing transformer at the 132kV substation. 6. Connect the 400kV substation to the 132kV substation via 4 240MVA rated SGT’s 7. Establish a system to generator operational intertripping scheme to perform as per the requirements of the TOF3 8. Connect the 400kV substation to the Legacy – Shrewsbury – Ironbridge and Legacy – Ironbridge circuits via a double tee arrangement. 9. Connect the new Cefn Coch – Lower Frankton 132kV double circuit to Lower Frankton 132kV substation | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04621 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202066 | Establish a new 132kV double circuit route between Lower Frankton and Cefn Coch | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04622 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202061 | 1.Establish a new 132kV substation comprising 4 feeder bays and space for User to connect their generator bay. 2. Connect the new Cefn Coch – Garn Fach 132kV double circuit to Garn Fach 132kV substation 3. Connect the new Garn Fach – Nant y Maen 132kV double circuit to Garn Fach 132kV substation | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04623 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202060 | 1. Establish a new 4 bay new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler, 4 feeder bays, 2 SVC bays. 2. Installation of 2 SVC’s 3. Connect the Cefn Coch – Lower Frankton 132kV double circuit into Cefn Coch substation EdF (Nant Y Maen) ConsAg v1 Ref: A/NANTY/20/0503-1EN(0) Date: August 2020 4. Connect the new Garn Fach – Cefn Coch 132kV double circuit to Cefn Coch 132kV substation | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04624 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202067 | Establish a new 132kV double circuit route between Cefn Coch and Garn Fach | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04625 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202063 | 1. Establish a new 400kV single switch mesh substation 2. Reconnect the HV side of the existing Shrewsbury SGT to Mesh Corner 2 of the newly established mesh substation. 3. Install a circuit intertripping scheme | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-04626 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-12535 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 102004-204152 |  | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-12540 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 103944-207819 (I) |  | 2037-10-31
Garn Fach Wind Farm | PRO-001157 | CS-12541 | EDF ENERGY RENEWABLES LIMITED | MID WALES CONNECTION NODE A 400KV SUBSTATION | 104660-209365 |  | 2037-10-31
Garvary Wind Farm | PRO-001927 | CS-07155 | GARVARY WIND FARM LTD | Garvary 132kV Substation | Garvary Wind Farm Enabling Works | 1. The sole enabling works will include the construction of a new 4km single 132kV circuit 2. Beauly to Loch Buidhe 275kV OHL Reinforcement | 2028-06-30
Garvary Wind Farm | PRO-001927 | CS-07156 | GARVARY WIND FARM LTD | Garvary 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2028-06-30
Garvary Wind Farm | PRO-001927 | CS-07157 | GARVARY WIND FARM LTD | Garvary 132kV Substation | SHET-RI-133 Loch Buidhe SGT Upgrade | At Loch Buidhe substation remove the existing two 275/132kV 240MVA SGTs, replace with two new 275/132kV 480MVA SGTs and upgrade the 132kV switchboard | 2028-06-30
Gateway Energy Centre Power Station | PRO-000045 | CS-05704 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21343-13 | New bus coupler to be installed at Raleigh Main 400kV substation and re-distribution of the ZT circuits such that Bradwell - Rayleigh circuit 1 is re-distributed to the Rayleigh main busbar 1. Involves moving the Rayleigh Main - Coryton South circuit southwards to allow room to extend Rayleigh Main. This work will be conducted at the same time as that associated with works at Rayleigh associated with the connection of a new Rayleigh - Bradwell 400kV double circuit. | 2029-06-30
Gateway Energy Centre Power Station | PRO-000045 | CS-05705 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21343-15 | Replace in situ existing OIBR bus section bay X120, bus coupler X130 and SGT1 and 4 bays X110, X410 respectively. | 2029-06-30
Gateway Energy Centre Power Station | PRO-000045 | CS-05706 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21343-23 | Installation of necessary equipment to provide provision for a generator intertripping scheme at Coryton South 400kV to manage local outage/fault combinations on the circuits connecting the Coryton South - Tilbury - Grain or X205 (at Coryton South) & Rayleigh - Coryton South or X605 (at Rayleigh). | 2029-06-30
Gateway Energy Centre Power Station | PRO-000045 | CS-05707 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21850 | Up-Rating of Rayleigh - Coryton South - Tilbury double circuit. | 2029-06-30
GB-EU MPI | PRO-004398 | CS-10916 | Windgrid | Fiddes 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10917 | Windgrid | Fiddes 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10918 | Windgrid | Fiddes 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10919 | Windgrid | Fiddes 400kV Substation | SHET-RI-093 East Coast Phase 2-400kV Reinforcement |  | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10920 | Windgrid | Fiddes 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10921 | Windgrid | Fiddes 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10922 | Windgrid | Fiddes 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10923 | Windgrid | Fiddes 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10924 | Windgrid | Fiddes 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10925 | Windgrid | Fiddes 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10926 | Windgrid | Fiddes 400kV Substation | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10927 | Windgrid | Fiddes 400kV Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10928 | Windgrid | Fiddes 400kV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10929 | Windgrid | Fiddes 400kV Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10930 | Windgrid | Fiddes 400kV Substation | SHET-RI-202 |  | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10931 | Windgrid | Fiddes 400kV Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10932 | Windgrid | Fiddes 400kV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 2033-10-31
GB-EU MPI | PRO-004398 | CS-10933 | Windgrid | Fiddes 400kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2033-10-31
Geiselittle BESS | PRO-004397 | CS-12684 | The Energy Workshop Limited | Thurso South GSP | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 2033-10-31
Geiselittle BESS | PRO-004397 | CS-12685 | The Energy Workshop Limited | Thurso South GSP | SHET-RI-287 - Thurso 2 GSP 275 kV Reinforcement |  | 2033-10-31
GF SELLINDGE BESS | PRO-004228 | CS-11123 | GF Sellindge Energy Ltd | East Kent connection node A 400kV Substation | 101901-203894 (GF) |  | 2036-10-31
GF SELLINDGE BESS | PRO-004228 | CS-11124 | GF Sellindge Energy Ltd | East Kent connection node A 400kV Substation | 103576-207093 |  | 2036-10-31
GF Upper Boat | PRO-003568 | CS-08524 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 102343-204505 | At Upperboat 275kV substation extend Mesh Corner 1 and install a CB/DCB. Works to include associated P&C. | 2025-05-31
GF Upper Boat | PRO-003568 | CS-08525 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 102344-204506 | At Upperboat 275kV substation extend Mesh Corner 4 and install a CB/DCB. Works to include associate P&C. | 2025-05-31
GF Upper Boat | PRO-003568 | CS-08526 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2025-05-31
GF Upper Boat | PRO-003568 | CS-08527 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2025-05-31
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09072 | GRETNA ENERGY STORAGE LIMITED | Gresham House Gretna 400/132kv Substation | 132kV Disconnector- GH DEVCO Gretna Green BESS | Installation of a 132kV disconnector at Gresham House Gretna BESS 400/132kV substation | 2032-10-30
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09073 | GRETNA ENERGY STORAGE LIMITED | Gresham House Gretna 400/132kv Substation | SPT-RI-231 |  | 2032-10-30
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09074 | GRETNA ENERGY STORAGE LIMITED | Gresham House Gretna 400/132kv Substation | SPT-RI-3022 | Gresham House Gretna 400/132kV substation - A new 400/132kV substation will be installed at the Gresham House Gretna Substation site. An extension of Gretna 400kV substation is required to accommodate a new feeder bay. At Gretna 400kV substation a new 400kV feeder bay and associated DBB switchgear (circuit breaker, line isolator and DBB disconnectors). From here a new 400kV UGC circuit will be laid to the Gresham House Gretna site. A new 400/132kV substation will be established with two 400/132kV 240MVA Super Grid Transformers installed. A new 132kV busbar will be established to accommodate the Gresham House Gretna BESS 400MW and GH DEVCO Gretna Green BESS 56MW | 2032-10-30
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09075 | GRETNA ENERGY STORAGE LIMITED | Gresham House Gretna 400/132kv Substation | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 2032-10-30
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09076 | GRETNA ENERGY STORAGE LIMITED | Gresham House Gretna 400/132kv Substation | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 2032-10-30
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09077 | GRETNA ENERGY STORAGE LIMITED | Gresham House Gretna 400/132kv Substation | NGET 101074 - 202154 | 2. New OHL reinforcement from Teviot Substation to Harker 400kV substation. (NGET 101074 – 202154) | 2032-10-30
GH DEVCO Kincardine BESS | PRO-003173 | CS-09472 | Kincardine Storage Limited | GH DEVCO KINCARDINE BESS 132kV SUBSTATION | SPT-RI-3091 | Kincardine 275kV (Shared) GIS Switchgear - To facilitate the connection of new generation from BESS to Kincardine 275kV substation, it is proposed to install a new 275kV GIS switchgear and associated 275kV equipment at Kincardine 275kV GIS substation | 2029-10-31
Giants Burn Wind Farm | PRO-002232 | CS-09425 | GB WIND FARM LIMITED | Dunoon GSP | Ginats Burn Wind Farm H1 | Installation of two 132kV circuit breakers and associated disconnectors at the new Dunoon GSP to facilitate the connection of GL1 and GL2 circuits. Works shall also include the OHL diversion of GL1 and GL2 to new Dunoon GSP | 2030-05-31
Giants Burn Wind Farm | PRO-002232 | CS-09426 | GB WIND FARM LIMITED | Dunoon GSP | SHET-RI-098 | Dunoon GL1-GL2 OHL Rebuild - Rebuild approximately 18km of double circuit overhead line between Dunoon substation and the SHET – SPT boundary. This project interfaces with Scottish Power Transmission (SPT), and any works required beyond the SHET-SPT boundary will be the responsibility of SPT. (SHET-RI-098) | 2030-05-31
Giants Burn Wind Farm | PRO-002232 | CS-09427 | GB WIND FARM LIMITED | Dunoon GSP | SPT-RI-2935 | CM Route Reinforcement- New generation at The Relevant Transmission Licensee’s New Dunoon 132kV substation necessitates an uprating of the 132kV shared circuit between New Dunoon and the tee into the Sloy-Windyhill circuit. The Relevant Transmission Licensee portion of the circuit runs between tower CM01 and mid span between CM13/14. The circuit presently uses 125mm² ACSR Tiger conductor. It is proposed that SPT uprate the double circuit to Sycamore 280mm² conductor (operated at 90℃) from CM1 to CM12. It is assumed SHETL will uprate over the boundary span between CM14 and CM13, terminating at tower CM12. (SPT?RI-2935) | 2030-05-31
Giants Burn Wind Farm | PRO-002232 | CS-09428 | GB WIND FARM LIMITED | Dunoon GSP | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2030-05-31
Giants Burn Wind Farm | PRO-002232 | CS-09429 | GB WIND FARM LIMITED | Dunoon GSP | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 2030-05-31
Giants Burn Wind Farm | PRO-002232 | CS-09430 | GB WIND FARM LIMITED | Dunoon GSP | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 2030-05-31
Giants Burn Wind Farm | PRO-002232 | CS-09431 | GB WIND FARM LIMITED | Dunoon GSP | SPT-RI-2784 | CL & CK Route Temperature Uprating - To alleviate overloads on the 132kV circuits on CL and CK Routes between Windyhill, Strathleven, Helensburgh and Sloy substations it is required to increase the operating temperature of the circuits from 50℃ to 65℃. This increase in operating temperature provides sufficient headroom to remove any intact overloads seen on the system. (SPT-RI-2784) | 2030-05-31
Giffnock GSP | PRO-003149 | CS-11079 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11080 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11081 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11082 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-3490 |  | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11083 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-3924 Cable |  | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11084 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-3924 OHL |  | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11085 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-3924 SS |  | 2033-10-31
Giffnock GSP | PRO-003149 | CS-11086 | SP Distribution plc | Giffnock 275/33kV |  |  | 2033-10-31
Giffnock GSP | PRO-003149 | CS-12240 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2033-10-31
Giffnock GSP | PRO-003149 | CS-12241 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2033-10-31
Giffnock GSP | PRO-003149 | CS-12242 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2033-10-31
Giffnock GSP | PRO-003149 | CS-12243 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-3490 |  | 2033-10-31
Giffnock GSP | PRO-003149 | CS-12244 | SP Distribution plc | Giffnock 275/33kV | SPT-RI-3924 |  | 2033-10-31
Gilliesfaulds | PRO-003112 | CS-09863 | SP Distribution plc | Cupar GSP | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2031-10-31
Gilliesfaulds | PRO-003112 | CS-09864 | SP Distribution plc | Cupar GSP | SPT-RI-3384 | Glenniston to Westfield 132kV Circuit Uprating | 2031-10-31
Gilliesfaulds | PRO-003112 | CS-09865 | SP Distribution plc | Cupar GSP | SPT-RI-3385 | Glenniston 132kV Substation Works | 2031-10-31
Gilliesfaulds | PRO-003112 | CS-09866 | SP Distribution plc | Cupar GSP | SPT-RI-3386 | Westfield 132kV ‘B’ GIS Substation Works | 2031-10-31
Gilliesfaulds | PRO-003112 | CS-09867 | SP Distribution plc | Cupar GSP | SPT-RI-3420 | Redhouse toWestfield 132kV Circuit Uprating (AG Route) | 2031-10-31
Gilliesfaulds | PRO-003112 | CS-09868 | SP Distribution plc | Cupar GSP | SPT-RI-3420 | Redhouse toWestfield 132kV Circuit Uprating (AG Route) | 2031-10-31
Gilliesfaulds | PRO-003112 | CS-09869 | SP Distribution plc | Cupar GSP | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2031-10-31
Gladsmuir Wind Farm | PRO-005915 | CS-12491 | WIND ESTATE (UK) LIMITED | Harburn 132/33kV Grid Supply Point Substation | SPT-RI-130 XH and XJ route overhead line uprating works (Strathaven Smeaton) |  | 2032-10-29
Gladsmuir Wind Farm | PRO-005915 | CS-12492 | WIND ESTATE (UK) LIMITED | Harburn 132/33kV Grid Supply Point Substation | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2032-10-29
Gladsmuir Wind Farm | PRO-005915 | CS-12493 | WIND ESTATE (UK) LIMITED | Harburn 132/33kV Grid Supply Point Substation | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 2032-10-29
Gladsmuir Wind Farm | PRO-005915 | CS-12494 | WIND ESTATE (UK) LIMITED | Harburn 132/33kV Grid Supply Point Substation | SPT-RI-3168 – Harburn 132kV Substation |  | 2032-10-29
Gleann Eoghainn | PRO-001275 | CS-05711 | Renantis UK Limited | Dunvegan 132/33kV Grid Supply Point Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2029-11-30
Gleann Eoghainn | PRO-001275 | CS-05712 | Renantis UK Limited | Dunvegan 132/33kV Grid Supply Point Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2029-11-30
Gleann Eoghainn | PRO-001275 | CS-05713 | Renantis UK Limited | Dunvegan 132/33kV Grid Supply Point Substation | Gleann Eoghainn item 1 | Replace the existing 33kV transformer circuit breaker 1TO located at Dunvegan 132/33kV GSP substation compound with the equivalent new equipment rated to a minimum of 1250A. This single 33kV circuit breaker will be owned and operated by the Relevant Transmission Licensee and represents the ownership boundary between the Relevant Transmission Licensee and the host Distribution Network Operator. | 2029-11-30
Glen Earrach PSH | PRO-004903 | CS-11751 | GLEN EARRACH ENERGY LIMITED | Glen Earrach PSH 400kV substation | SHET-RI-134 Beauly-Denny Second Circuit Upgrade from 275kV to 400kV |  | 2035-10-31
Glen Earrach PSH | PRO-004903 | CS-11752 | GLEN EARRACH ENERGY LIMITED | Glen Earrach PSH 400kV substation | SHET-RI-134b | Fasnakyle Substation 132kV Reinforcement – The existing Fasnakyle Substation is due to be upgraded from 275kV circuit to 400kV, as part of the Beauly-Denny Second Circuit Upgrade (SHET-RI-134). This document provides additional information on the specific changes required at Fasnakyle Substation, as part of this reinforcement. (SHET-RI-134b). | 2035-10-31
Glen Ullinish Extension | PRO-001346 | CS-06240 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | Glen Ullinish Extension - Enabling Works | 1. Construction of approximately 5km of single circuit 132kV overhead line from the connection site to a new bay on the Edinbane 132kV busbars, via the required 132kV switchgear. | 2027-04-01
Glen Ullinish Extension | PRO-001346 | CS-06241 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2027-04-01
Glen Ullinish Extension | PRO-001346 | CS-06242 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2027-04-01
Glen Ullinish Extension | PRO-001346 | CS-06243 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 2027-04-01
Glen Ullinish Wind Farm | PRO-000298 | CS-05717 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | SHET-RI-125 | Broadford-Dunvegan Reinforcement: Construct a new 132kV double circuit OHL from Broadford to Dunvegan | 2026-10-31
Glen Ullinish Wind Farm | PRO-000298 | CS-05718 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 4 | Modify the tower near the new 132/33kV windfarm substation and erect a new terminal tower and down droppers to the new substation compound. | 2026-10-31
Glen Ullinish Wind Farm | PRO-000298 | CS-05719 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 3 | Install 2 x 132kV line isolating switches (103 and 203) along with associated busbar extensions and support structures within the substation compound. Isolators to be located on either side of the single teed 132kV infeed to the substation. | 2026-10-31
Glen Ullinish Wind Farm | PRO-000298 | CS-05720 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 2 | Install 1 x 132kV transformer circuit breaker (115) along with associated busbar extensions and support structures. | 2026-10-31
Glen Ullinish Wind Farm | PRO-000298 | CS-05721 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 1 | Modify the existing protection and telecommunication equipment's at Fort Augustus and the new 132kV substation near Dunvegan. | 2026-10-31
Glen Ullinish Wind Farm | PRO-000298 | CS-05722 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 2026-10-31
Glen Ullinish Wind Farm | PRO-000298 | CS-05723 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2026-10-31
Glendye Wind Farm | PRO-001389 | CS-07167 | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | Glendye Wind Farm Enabling Works | 1. Installation of a 132kV line disconnector at the User’s substation 2. Construction of approx. 20.75km of single 132kV circuit, comprising 0.75km of underground cable and 20km of overhead line from the User’s site to Fetteresso substation 3. Extension of 132kV busbar at Fetteresso substation and installation of a new 132kV busbar feeder bay 4. Installation of a new 132kV feeder protection and control scheme | 2028-10-31
Glendye Wind Farm | PRO-001389 | CS-07168 | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2028-10-31
Glendye Wind Farm | PRO-001389 | CS-07169 | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2028-10-31
Glengolly | PRO-004326 | CS-10326 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2033-10-31
Glengolly | PRO-004326 | CS-10327 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2033-10-31
Glengolly | PRO-004326 | CS-10328 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 2033-10-31
Glengolly | PRO-004326 | CS-10329 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 2033-10-31
Glengolly | PRO-004326 | CS-10330 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2033-10-31
Glengolly | PRO-004326 | CS-10331 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2033-10-31
Glengolly | PRO-004326 | CS-10332 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
Glengolly | PRO-004326 | CS-10333 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2033-10-31
Glengolly | PRO-004326 | CS-10334 | ECOCEL ENERGY (STORAGE) LTD | Thurso GSP | SHET-RI-287 - Thurso 2 GSP 275 kV Reinforcement |  | 2033-10-31
Glenmore | PRO-004445 | CS-11363 | AEUK WIND PROJECT II LTD | Edinbane 132/33kV Substation | SHET-RI-195 Edinbane to Grudie Bridge 220kV Subsea HVAC Cable Link |  | 2034-10-31
Glenmore | PRO-004445 | CS-11364 | AEUK WIND PROJECT II LTD | Edinbane 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2034-10-31
Glenmore | PRO-004445 | CS-11365 | AEUK WIND PROJECT II LTD | Edinbane 132/33kV Substation | SHET-RI-061 v9 - Skye Overhead Line Reinforcement |  | 2034-10-31
Glenmuckloch Pumped Storage | PRO-000299 | CS-05731 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05732 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05733 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05734 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05735 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05736 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05737 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-05738 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-07396 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-05-18
Glenmuckloch Pumped Storage | PRO-000299 | CS-07397 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2029-05-18
Glenmuckloch Wind Farm | PRO-000300 | CS-05403 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05739 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-007 | New Cumnock 275/132kV Substation | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05740 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05741 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05742 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05743 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05744 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05745 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05746 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05747 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-05748 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-05-31
Glenmuckloch Wind Farm | PRO-000300 | CS-09946 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2029-05-31
Glenmuir Windfarm | PRO-004058 | CS-10193 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | Glenmuir Windfarm H1 SS | 1. Installation of a new DBB feeder bay with associated switchgear (circuit breaker + DBB disconnectors) at Glenmuckloch ‘A’ 132kV substation. 2. Install approx. 8.7km of 132kV circuit (OHL/UGC) between Glenmuckloch 132kV substation and Glenmuir Windfarm substation (Pre-Fault continuous summer rating 89MVA required). 3. Installation of a 132kV line isolator at Glenmuir Windfarm 132kV substation. | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10194 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10195 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10196 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10197 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10198 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10199 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10200 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-2862 OHL |  | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10201 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-06-30
Glenmuir Windfarm | PRO-004058 | CS-10202 | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation | SPT-RI-3498 - Glenmuckloch 400kV - Dumfries North 400kV | Under the NOA7 Refresh the need was identified to develop a new west coast onshore high?capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. This project is driven by the continued increase in required transfers seen across this boundary due to the need to connect renewable generation in Scotland to achieve UK and Government’s net zero target by 2050 and 2045 respectively. To facilitate generation applications in this area it is proposed to utilise this new west coast onshore corridor. The TORI shall construct a new 400kV double circuit between the proposed Glenmuckloch 400kV substation (established under SPT-RI-236) and the proposed Dumfries North 400kV substation (established under SPT-RI-2862). It is proposed to string both sides of the 400kV corridor with 3x700mm² Araucaria AAAC conductor provisionally rated at 750°C with the capability to uprate the operating temperature to 900°C. | 2036-06-30
Glennifer Road BESS | PRO-003600 | CS-08542 | Drax BESS Neilston Limited | Neilston 132kV Substation | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2027-10-30
Glennifer Road BESS | PRO-003600 | CS-08543 | Drax BESS Neilston Limited | Neilston 132kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2027-10-30
Glenshimmeroch Windfarm | PRO-000440 | CS-03720 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | Glenshimmeroch H1 | Installation of a 132kV line isolator connecting onto a 132kV busbar at Glenshimmeroch collector substation. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03721 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03722 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03723 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-274 | Glenshimmeroch Collector Substation - On the New Cumnock / Blackcraig 132kV circuit, installation of a 132kV circuit breaker and associated disconnectors at Glenshimmeroch Collector Substation in South West Scotland. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03724 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03725 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03726 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-03727 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-296 | Glenshimmeroch collector substation 132kV overhead line uprating - Due to an increase in the generation contracted in the area, it is proposed to uprate a section of the overhead line between the proposed Glenshimmeroch collector substation to the cable end on the New Cumnock 132kV circuit. This is approximately 11km. This will be achieved by replacing the existing UPAS conductor with LARK conductor on the existing wood pole system. | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-12058 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-4212 | 8. Margree 132kV Collector Substation - In order to accommodate the connection of Troston, Glenshimmeroch, Margree and Fell Wind farms via a shared solution as per customer’s request, it is proposed to establish a new 132/33kV collector substation at Margree location (on the New Cumnock / Blackcraig 132kV circuit). The scope of work comprises installation of one 132kV circuit breaker and associated disconnectors, one 132kV busbar and one 132kV circuit breaker and disconnector (on the Blackcraig 132kV circuit). The creation of this new collector substation is noted as part of SPT-TOCO-2143, SPTTOCO-505, SPT-RI-458 & SPT-TOCO-2160. All TOCO Mod-App’s must be accepted to consider this contracted. Upon the acceptance of all 4 Mod-App’s, this TORI will supersede SPT-RI-274 - Glenshimmeroch Collector Substation. In this event, SPT-RI-274 will be withdrawn. Any abortive costs will be detailed in the charging section. (SPT-RI-4212) | 2029-10-31
Glenshimmeroch Windfarm | PRO-000440 | CS-12059 | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation | SPT-RI-4205 | 4. Margree substation 132/33kV 120MVA T2 transformer and associated works - In order to accommodate the connection of Troston and Glenshimmeroch Wind farms via a shared solution as per customer’s request, it is proposed to establish a new 132/33kV transformer T2 at Margree 132/33kV collector substation. The scope of work comprises one 132kV circuit breaker and associated line isolator connecting onto a 132kV busbar as well as installation of 132/33kV transformer 120MVA (T2) and one 33kV indoor switchboard. (SPT-RI-4205) | 2029-10-31
Glenside Farm BESS | PRO-004368 | CS-09475 | GPC 1211 Ltd | Denny North 275/132kV | SPT-RI-2083 | Kincardine North – Wishaw 400kV reinforcement (DWUP)- Establish 400kV infrastructure through the centre of the network following the East Coast 400kV onshore incremental (ECUP) reinforcement, but in advance of the completion of existing Denny to Wishaw 400kV reinforcement (DWNO). The scope of this TORI will be aligned with the ‘DWUP’ option submitted to the 2021/22 Network Options Assessment (NOA) process. It is proposed to reconfigure and update existing 275kV single circuit between the Kincardine and Wishaw to 400kV operation to establish a new Kincardine North – Wishaw 400kV circuit. | 2031-10-31
Glentaggart 150MW BESS | PRO-004145 | CS-09957 | BROCKWELL ENERGY LIMITED | Redshaw 400kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2030-10-30
Glentaggart 150MW BESS | PRO-004145 | CS-09958 | BROCKWELL ENERGY LIMITED | Redshaw 400kV | SPT-RI-3060 | Redshaw 132kV “B” Board - Establish a new 132kV double busbar substation, indicatively named Redshaw 132kV “B” board at the new Redshaw 400/132kV substation. The location of the SPT’s new 400kV substation (which this 132kV double busbar site will connect into) will be connected in the existing ZV Route corridor (STHA-ELVA / COAL-ELVA) as well as facilitate the new double circuit from Glenmuckloch under SPT-RI-236. The 400kV substation at Redshaw is being constructed under SPT-RI-2060. The 132kV double busbar substation to be established here will also require installation of two 400/132kV 360MVA transformers. (SPT-RI-3060) | 2030-10-30
Glentaggart 150MW BESS | PRO-004145 | CS-09959 | BROCKWELL ENERGY LIMITED | Redshaw 400kV | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2030-10-30
Glentaggart 42MW BESS | PRO-001595 | CS-04297 | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2027-10-31
Glentaggart 42MW BESS | PRO-001595 | CS-04298 | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2027-10-31
Glentaggart 42MW BESS | PRO-001595 | CS-09803 | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation | SPT-RI-3547 | Redshaw 132kV to Glentaggart / Hare Craig – It is proposed to connect Glentaggart 42MW BESS and Hare Craig WF into Redshaw 132kV GIS substation (‘A’ board) via a shared solution. The shared assets proposed for this solution are covered under this TORI, which entail the following works: • Installation of a new 132kV double busbar bay and associated circuit breaker at Redshaw 132kV GIS (‘A’ board). • Installation of a new 132/33kV 120MVA GT unit at Redshaw 132kV GIS (‘A’ board). • Installation of a 33kV circuit breaker associated with the 3 panel switchboard. (SPT-RI-3547) | 2027-10-31
Golticlay Extension Wind Farm | PRO-000926 | CS-06226 | RWE RENEWABLES UK SWINDON LIMITED | Mybster 2 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2027-09-30
Golticlay Extension Wind Farm | PRO-000926 | CS-06227 | RWE RENEWABLES UK SWINDON LIMITED | Mybster 2 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2027-09-30
Golticlay Extension Wind Farm | PRO-000926 | CS-06228 | RWE RENEWABLES UK SWINDON LIMITED | Mybster 2 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2027-09-30
Golticlay Wind Farm | PRO-000370 | CS-05752 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-037 | Fyrish 275/132kV Substation – Establish a new 275kV/132kV Fyrish substation close to the existing Alness 132kV OHL Teed location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. Two new 132kV underground cables will be installed to link the new 275kV/132kV Fyrish substation with the existing Alness GSP. (SHET-RI-037) | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05753 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05754 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05755 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05756 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-032b | Spittal – Mybster 132kV Reinforcement — This consists of a new higher capacity 132kV OHL and substation works between Spittal and Mybster substation. (SHET-RI-032b) | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05757 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05758 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05759 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-05760 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2026-07-31
Golticlay Wind Farm | PRO-000370 | CS-06657 | RWE Renewables UK Onshore Wind Limited | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2026-07-31
Grangemouth Hybrid BESS & Solar PV | PRO-003254 | CS-11066 | TAGENERGY DEVELOPMENT UK LIMITED | Letham 400/275kV substation | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2032-06-30
Grangemouth Hybrid BESS & Solar PV | PRO-003254 | CS-11067 | TAGENERGY DEVELOPMENT UK LIMITED | Letham 400/275kV substation | SPT-RI-3897 OHL |  | 2032-06-30
Grangemouth Hybrid BESS & Solar PV | PRO-003254 | CS-11068 | TAGENERGY DEVELOPMENT UK LIMITED | Letham 400/275kV substation | SPT-RI-3897 SS |  | 2032-06-30
Grantham Solar Farm - RSL | PRO-005045 | CS-11690 | SOUTH GRANTHAM ENERGY CENTRE LIMITED | Grantham 400KV | 103342-206819 (E) |  | 2034-10-30
Grantham Solar Farm - RSL | PRO-005045 | CS-11691 | SOUTH GRANTHAM ENERGY CENTRE LIMITED | Grantham 400KV | 104222-208201 |  | 2034-10-30
Green Volt Offshore Windfarm | PRO-001469 | CS-04283 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04284 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-025d | North East Reinforcement | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04285 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04286 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04287 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04288 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04289 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04290 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation |  |  | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04291 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04292 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04293 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04294 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04295 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-04296 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2029-03-31
Green Volt Offshore Windfarm | PRO-001469 | CS-09998 | Green Volt Offshore Windfarm Ltd | New Deer 400kV Substation | Green Volt Enabling works | The Sole Enabling Works at New Deer 400kV substation shall comprise of one new 400kV feeder bay complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between SHET and the User will be the User side of the 400kV feeder circuit breaker/isolators at New Deer 400kV substation | 2029-03-31
Greenburn Mixed Technology | PRO-001006 | CS-05767 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2027-10-31
Greenburn Mixed Technology | PRO-001006 | CS-05768 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 1 | At New Cumnock substation on Board C, install a new 132kV switch bay and associated equipment and apparatus. | 2027-10-31
Greenburn Mixed Technology | PRO-001006 | CS-05769 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 3 | Installation of a 132kV cable system from New Cumnock 132kV substation to an appropriate location where the 132kV wood pole overhead line will be constructed. | 2027-10-31
Greenburn Mixed Technology | PRO-001006 | CS-05770 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2027-10-31
Greenburn Mixed Technology | PRO-001006 | CS-05771 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 2 | Installation of approximately 8km of 132kV wood pole overhead line between New Cumnock and Greenburn Mixed Technology 132kV Substation. | 2027-10-31
Greenburn Mixed Technology | PRO-001006 | CS-05772 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 4 | At the Greenburn Mixed Technology Substation, install one 132kV line isolator. | 2027-10-31
Greenburn Mixed Technology | PRO-001006 | CS-05773 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2027-10-31
Greenburn Wind & BESS | PRO-004407 | CS-11937 | HM GB (WIND) LTD | Coupar Angus 2 GSP | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm²) and will operate at 75°C to give a minimum summer pre-fault rating of 176MVA | 2031-10-31
Greenburn Wind & BESS | PRO-004407 | CS-11938 | HM GB (WIND) LTD | Coupar Angus 2 GSP | SHET-RI-184 | Coupar Angus 2 Tee – Establish a new 132kV tee point of the HCS circuit between Coupar Angus GSP and Tealing/Charleston Tee for the connection to a new Coupar Angus 2 132/33kV GSP substation | 2031-10-31
Greenburn Wind & BESS | PRO-004407 | CS-11939 | HM GB (WIND) LTD | Coupar Angus 2 GSP | SHET-RI-264 | Coupar Angus 2 - Birkhill Tee 132kV Upgrade | 2031-10-31
Greentoft Farm | PRO-003640 | CS-12505 | Neven Point Wind Limited | Eday GSP | SHET-RI-019 | Establish a 220kV HVAC circuit over a distance of approximately 68km between the 275kV GIS substation at Dounreay on the mainland and the new 132kV substation in the vicinity of Finstown on Orkney. The HVAC circuit comprises of approximately 15km of land cable and 53km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Dounreay and Finstown. | 2033-10-31
Greentoft Farm | PRO-003640 | CS-12506 | Neven Point Wind Limited | Eday GSP | SHET-RI-075 - Orkney 132kV Reinforcement for GSP v4 |  | 2033-10-31
Grendon Solar & BESS | PRO-001568 | CS-04720 | Green Hill Solar Farm Limited | Grendon 400kV Substation | 101259-202500 | Extension of the existing Grendon 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 2029-07-01
Grendon Solar & BESS | PRO-001568 | CS-05118 | Green Hill Solar Farm Limited | Grendon 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2029-07-01
Grendon Solar & BESS | PRO-001568 | CS-05120 | Green Hill Solar Farm Limited | Grendon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2029-07-01
Grendon Solar & BESS | PRO-001568 | CS-05121 | Green Hill Solar Farm Limited | Grendon 400kV Substation | 030652-030652 | Reconductor and turn in Elstree – Sundon circuit 2 A608 into Elstree. Modify the existing circuit 2 (A608) that run from Sundon 400kV to Elstree 275kV by turning it in at Elstree 400kV. This will create two separate circuits: 1) From Sundon to Elstree 400kV circuit. To this will be added a new series reactor 2) Elstree 400kV to Elstree 275kV substation via existing interbus transformer (F608). No change to this element except connecting into new 400kV bay instead of to A608. | 2029-07-01
Gresham House Cockenzie BESS | PRO-002209 | CS-07744 | COCKENZIE STORAGE LIMITED | Meadowmill 400/132kV Substation | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 2026-07-31
Gresham House Cockenzie BESS | PRO-002209 | CS-07745 | COCKENZIE STORAGE LIMITED | Meadowmill 400/132kV Substation | Gresham House Cockenzie BESS - Tee off | Works to tee off the 400kV OHL tower ZA001A | 2026-07-31
Gresham House Cockenzie BESS | PRO-002209 | CS-07746 | COCKENZIE STORAGE LIMITED | Meadowmill 400/132kV Substation | Gresham House Cockenzie BESS - Disconnector/Circuit Breaker | Installation of 400kV disconnector/circuit breaker | 2026-07-31
Gresham House Connagill BESS | PRO-003434 | CS-09610 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09611 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09612 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09613 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09614 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09615 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09616 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2031-10-31
Gresham House Connagill BESS | PRO-003434 | CS-09617 | ENERGYHUBDEVELOPMENTS LIMITED | New Connagill 275/132kV Substation | SHET-RI-238 |  | 2031-10-31
Gresham House Dalmarnock BESS | PRO-002809 | CS-08550 | ENERGYHUBDEVELOPMENTS LIMITED | Gresham House Dalmarnock Bess 132kv Substation | Suspension Tower - Gresham House Dalmarnock BESS | Installation of 2 x suspension towers | 2030-04-30
Gresham House Dalmarnock BESS | PRO-002809 | CS-08551 | ENERGYHUBDEVELOPMENTS LIMITED | Gresham House Dalmarnock Bess 132kv Substation | Terminal Tower - Gresham House Dalmarnock BESS | Installation of 1 x terminal tower | 2030-04-30
Gresham House Dalmarnock BESS | PRO-002809 | CS-08552 | ENERGYHUBDEVELOPMENTS LIMITED | Gresham House Dalmarnock Bess 132kv Substation | SPT-RI-2957 | Dalmarnock SGT1 & Charlotte Street 1 DCBs – To comply with SQSS circuit complexity as per Appendix B and accommodate a new generation and demand connection within the Dalmarnock area of the network, there is a requirement to replace the H13A disconnector at Dalmarnock 275/132kV substation with a DCB. Additionally, there is also a requirement to replace the H13B disconnector at Dalmarnock 275/132kV substation with a DCB | 2030-04-30
Gresham House Dalmarnock BESS | PRO-002809 | CS-08553 | ENERGYHUBDEVELOPMENTS LIMITED | Gresham House Dalmarnock Bess 132kv Substation | 275kV Line Disconnector - Gresham House Dalmarnock BESS | Installation of 275kV Line Disconnector | 2030-04-30
Gresham House Gretna BESS | PRO-002367 | CS-08211 | ALBUSIA LTD | Gresham House Gretna 400/132kv Substation | SPT-RI-231 |  | 2031-10-31
Gresham House Kincardine BESS | PRO-002368 | CS-11027 | FLAVUSIA LTD | Gresham House Kincardine BESS 275/132kV substation | SPT-RI-3091 | Kincardine 275kV (Shared) GIS Switchgear - To facilitate the connection of new generation from BESS to Kincardine 275kV substation, it is proposed to install a new 275kV GIS switchgear and associated 275kV equipment at Kincardine 275kV GIS substation | 2029-10-31
Gresham House Kincardine BESS | PRO-002368 | CS-11028 | FLAVUSIA LTD | Gresham House Kincardine BESS 275/132kV substation | Gresham House Kincardine BESS Enabling Works | At Gresham House Kincardine BESS 275/132kV substation, install one 132kV disconnector | 2029-10-31
Gresham House Mossmoran BESS | PRO-002395 | CS-08554 | MOSSMORRAN ENERGY STORAGE LIMITED | LOCH GELLY COLLECTOR 132KV SUBSTATION | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2031-10-31
Gresham House Mossmoran BESS | PRO-002395 | CS-11641 | MOSSMORRAN ENERGY STORAGE LIMITED | LOCH GELLY COLLECTOR 132KV SUBSTATION | SPT-RI-3535 CABLE |  | 2031-10-31
Gresham House Mossmoran BESS | PRO-002395 | CS-11642 | MOSSMORRAN ENERGY STORAGE LIMITED | LOCH GELLY COLLECTOR 132KV SUBSTATION | SPT-RI-3535 SS |  | 2031-10-31
Greta III | PRO-001803 | CS-06894 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101615-203248 | Extension of the existing Drakelow 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 2029-10-30
Greta III | PRO-001803 | CS-06895 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-10-30
Greta III | PRO-001803 | CS-06896 | Trent BESS III LIMITED | Drakelow 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-10-30
Greta III | PRO-001803 | CS-06897 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-10-30
Greta III | PRO-001803 | CS-06898 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2029-10-30
Greta III | PRO-001803 | CS-06899 | Trent BESS III LIMITED | Drakelow 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-10-30
Greta III | PRO-001803 | CS-06900 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2029-10-30
Greta III | PRO-001803 | CS-06901 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101616-203249 | Reconductor 400kV Drakelow to Hams Hall line from Rubus 500sqmm to Rubus 500sqmm at 90deg C to have summer pre fault rating of 1660MVA | 2029-10-30
Greta III | PRO-001803 | CS-06902 | Trent BESS III LIMITED | Drakelow 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2029-10-30
Gridlink Interconnector | PRO-000287 | CS-05775 | Gridlink Interconnector Limited | Kingsnorth 400kV Substation | 33748 | Kinsnorth Works, including: - Provide the customer with a spare bay at Kingsnorth 400kV substation (spare bay 3). - Kingsnorth circuit breaker foundation (Xl 05, Xli 0, X140, X205, X21 0 X705 X805 and X1090) updating works - Installation of a new coupler breaker with associated bay works between main busbar 3 and circuit breaker X220. | 2029-03-31
Grimsby West BPP_0523 | PRO-003639 | CS-12391 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 100944-201880 (EX9) |  | 2039-10-30
Grimsby West BPP_0523 | PRO-003639 | CS-12392 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 101669-203323 (1) |  | 2039-10-30
Grimsby West BPP_0523 | PRO-003639 | CS-12393 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 102718-205492 (1) |  | 2039-10-30
Grimsby West BPP_0523 | PRO-003639 | CS-12394 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 103056-206472 (1) |  | 2039-10-30
Grindon Grange | PRO-004028 | CS-10320 | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2035-10-30
Grindon Grange | PRO-004028 | CS-10321 | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-30
Grindon Grange | PRO-004028 | CS-10322 | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 2035-10-30
Grindon Grange | PRO-004028 | CS-10323 | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2035-10-30
Grindon Grange | PRO-004028 | CS-10324 | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2035-10-30
Grindon Grange | PRO-004028 | CS-10325 | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation | 103383-206836 |  | 2035-10-30
GT R4 Wind Farm | PRO-000563 | CS-06361 | GT R4 LIMITED | Weston Marsh 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2030-11-30
GT R4 Wind Farm | PRO-000563 | CS-06362 | GT R4 LIMITED | Weston Marsh 400kV Substation | 100929-201859 | Extend Wylfa 400kV substation in order to facilitate the connection of the GIGL offshore windfarm | 2030-11-30
GT R4 Wind Farm | PRO-000563 | CS-06363 | GT R4 LIMITED | Weston Marsh 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2030-11-30
GT R4 Wind Farm | PRO-000563 | CS-06364 | GT R4 LIMITED | Weston Marsh 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 2030-11-30
Gwynt Alwen WF | PRO-001545 | CS-04728 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101212-202434 | 1. Establish a new four bay 400kV double busbar substation1 adjacent to the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. Substation to comprise two feeder bays, a bus coupler bay and a skeletal bay for the User to connect their generator circuit 2. Connect the substation to the Main interconnected system via a turn in of the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-04729 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05125 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05127 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05130 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05131 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05132 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05133 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-05134 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-12582 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101269-202512 (MOD) |  | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-12583 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 101278-202528 (mod) |  | 2030-06-30
Gwynt Alwen WF | PRO-001545 | CS-12585 | BWLCH GWYN WIND FARM LIMITED | North Wales connection Node A 400kV Substation | 103610-207138 |  | 2030-06-30
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08282 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08283 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08284 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08285 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08286 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08287 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08288 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08289 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 102225-204458 | Infrastructure works for the generation connection of Gwynt Glas offshore wind farm 2. | 2036-12-06
Hagshaw Energy Cluster Western Expansion | PRO-001692 | CS-07434 | Spirebush Ltd | Spirebush 132kV Substation | Spirebush H1 - 132kV AIS feeder bays | Installation of two new 132kV AIS feeder bays at Redshaw 132kV substation | 2028-07-01
Hagshaw Energy Cluster Western Expansion | PRO-001692 | CS-07435 | Spirebush Ltd | Spirebush 132kV Substation | Spirebush H1 - 132kV circuits. Redshaw 132kV - Spirebush 132kV Substations | Installation of two new 132kV circuits between Redshaw 132kV and Spirebush 132kV Substations, circuit length approximately 18km. | 2028-07-01
Hagshaw Energy Cluster Western Expansion | PRO-001692 | CS-07436 | Spirebush Ltd | Spirebush 132kV Substation | Spirebush H1 - Two 132kV line disconnectors at Spirebush 132kV Substation | Installation of two 132kV line disconnectors at Spirebush 132kV Substation. | 2028-07-01
Hagshaw Energy Cluster Western Expansion | PRO-001692 | CS-07437 | Spirebush Ltd | Spirebush 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2028-07-01
Hagshaw Energy Cluster Western Expansion | PRO-001692 | CS-07438 | Spirebush Ltd | Spirebush 132kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2028-07-01
Hagshaw Energy Cluster Western Expansion | PRO-001692 | CS-07439 | Spirebush Ltd | Spirebush 132kV Substation | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 2028-07-01
Hagshaw Repowering Phase 3 | PRO-002306 | CS-07960 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2029-04-26
Hagshaw Repowering Phase 3 | PRO-002306 | CS-07961 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2029-04-26
Hagshaw Repowering Phase 3 | PRO-002306 | CS-07962 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 2029-04-26
Hagshaw Repowering Phase 3 | PRO-002306 | CS-07963 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | AIS Feeder Bay - HPhase 3 | Installation of a new 132kV AIS feeder bay at Redshaw 132kV substation with associated main and reserve busbar disconnectors and line disconnector. | 2029-04-26
Hagshaw Repowering Phase 3 | PRO-002306 | CS-07964 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | 132kV Circuit (OHL/Cable) - HPhase 3 | Installation of a new 132kV circuit between Redshaw 132kV and Hagshaw Repowering Ph3 132kV substation comprising of both 132kV cable and OHL. The indicative length of the circuit is 10km. | 2029-04-26
Hagshaw Repowering Phase 3 | PRO-002306 | CS-07965 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | 132kV Line Disconnector-Hagshaw Wind Farm Repowering 2 | Installation of a 132kV line disconnector at Hagshaw Repowering Ph3 132kV substation. | 2029-04-26
Halfway Energy Park | PRO-004062 | CS-09879 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09880 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-25a |  | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09881 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-25b |  | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09882 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-25c |  | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09883 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-25d |  | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09884 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09885 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09886 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09887 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09888 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09889 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09890 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09891 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09892 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHET-RI-199) | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09893 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09894 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09895 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09896 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SHET-RI-262 | New East Coast 400kV Substation – Establish a new 400kV substation on the east coast between Tealing and Glenrothes/Westfield to facilitate connection of Halfway Energy Park 1000.29MW | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09897 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09898 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2035-10-31
Halfway Energy Park | PRO-004062 | CS-09899 | DALRIADA RENEWABLES LIMITED | New East Coast 400kV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 2035-10-31
Hall Ings Solar Farm (DNO) | PRO-002643 | CS-08447 | Northern Powergrid (Yorkshire) Plc | Creyke Beck GSP | 102675-205361 | Construct a new 400kV double busbar substation including all necessary works required to connect it to the Main Interconnected Transmission System. | 2034-10-30
Hallyburton (2) | PRO-003959 | CS-09995 | Balance Power Projects Limited | Coupar Angus 2 GSP | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm²) and will operate at 75°C to give a minimum summer pre-fault rating of 176MVA | 2029-10-31
Hallyburton (2) | PRO-003959 | CS-09996 | Balance Power Projects Limited | Coupar Angus 2 GSP | SHET-RI-184 | Coupar Angus 2 Tee – Establish a new 132kV tee point of the HCS circuit between Coupar Angus GSP and Tealing/Charleston Tee for the connection to a new Coupar Angus 2 132/33kV GSP substation | 2029-10-31
Hallyburton (2) | PRO-003959 | CS-09997 | Balance Power Projects Limited | Coupar Angus 2 GSP | SHET-RI-264 | Coupar Angus 2 - Birkhill Tee 132kV Upgrade | 2029-10-31
Hare Craig Wind Farm | PRO-000940 | CS-04523 | HARE CRAIG WINDFARM LLP | Hare Craig 33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2028-10-31
Hare Craig Wind Farm | PRO-000940 | CS-04524 | HARE CRAIG WINDFARM LLP | Hare Craig 33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2028-10-31
Hare Craig Wind Farm | PRO-000940 | CS-10793 | HARE CRAIG WINDFARM LLP | Hare Craig 33kV Substation | SPT-RI-3547 SS |  | 2028-10-31
Hare Craig Wind Farm | PRO-000940 | CS-10794 | HARE CRAIG WINDFARM LLP | Hare Craig 33kV Substation | SPT-RI-3547 Cable |  | 2028-10-31
Hare Hill Repowering | PRO-003963 | CS-09149 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2031-10-31
Hare Hill Repowering | PRO-003963 | CS-09150 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2031-10-31
Hare Hill Repowering | PRO-003963 | CS-09151 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2031-10-31
Hare Hill Repowering | PRO-003963 | CS-09152 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2031-10-31
Hare Hill Repowering | PRO-003963 | CS-09153 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | 132kV Line Disconnector - Hare Hill | At Hare Hill Repowering substation install one 132kV line disconnector | 2031-10-31
Hare Hill Repowering | PRO-003963 | CS-09154 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | 132kV AIS Switch Bay - Hare Hill | Installation of a 132kV AIS bay at Glenmuckloch 132kV substation. | 2031-10-31
Hare Hill Repowering | PRO-003963 | CS-09155 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | 132kV OHL - Hare Hill | Installation of a 132kV OHL circuit out to the User’s WF substation. OHL circuit should be capable of 127MVA | 2031-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-05609 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm² Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 2029-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-05610 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2029-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-05611 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 2029-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-06329 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 2029-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-06332 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | NGET-RI-32105 | Reinforce the Junction V to Harker 132kV circuit (from tower AL068 to Harker 132kV substation), to provide a minimum summer pre-fault continuous rating of 202MVA. (NGET-RI-32105 | 2029-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-06333 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-10-31
Hareshaw Rig Wind Farm | PRO-000543 | CS-06334 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | Hareshaw Rig H1 Works | At Hopsrig Collector Substation, install one 132kV line isolator and tee connect onto the Hopsrig – Ewe Hill 132kV circuit. | 2029-10-31
Harestanes West Wind Farm | PRO-001075 | CS-04273 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | Old Forest of Ae H1 SS | Installation of 132kV line disconnector at Old Forest of Ae WF substation | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-04274 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | Old Forest of Ae H1 OHL | Installation of a 20km 132kV OHL circuit using AAAC “Poplar” conductor. | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12401 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12402 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12403 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12404 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | SPT-RI-2741 | Dumfries 132kV – Chapelcross 132kV No.2 Circuit (BR Route) LMS – A Load Management Scheme (LMS) is required at Chapelcross 132kV to monitor the loading through: • Dumfries – Chapelcross 132kV No.2 circuit (BR Route). For the loss of a Dumfries – Chapelcross 132kV No.1 circuit, and a resultant overload on the remaining in-service No.2 circuit, a trip signal shall be issued to SPD for the generators connected to the Dumfries GSP. A current and voltage measurement is required on the Dumfries – Chapelcross 132kV No.2 circuit so the direction, as well as magnitude, of the power flow through the circuit can be determined. | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12405 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | NGET_RI-101268-202511 | NGET-RI - 101268-202511 - The scope of this project is the rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12406 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | NGET-RI-01268-202520 | NGET-RI- 01268-202520 - The scope is the uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. | 2029-09-01
Harestanes West Wind Farm | PRO-001075 | CS-12407 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes West Wind Farm 132/33kV | NGET_RI-101268-202511 | NGET-RI - 101268-202511 - The scope of this project is the rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker | 2029-09-01
Harker Green Energy Centre | PRO-001709 | CS-04739 | Blackdyke BESS Limited | Harker 400kV Substation | 101268-202511 | The scope of this project is the rebuild of Harker substation and rationalisation to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-04740 | Blackdyke BESS Limited | Harker 400kV Substation | 101351-202671 | Extend the Main and Reserve Busbar 3 to make provision for connection of generator bay (User Works). | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-04741 | Blackdyke BESS Limited | Harker 400kV Substation | 100118-200309 | The replacement of the existing four 275/132kV 120MVA SGTs with four 400/132 240MVA SGTs at Harker substation. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05123 | Blackdyke BESS Limited | Harker 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05126 | Blackdyke BESS Limited | Harker 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05128 | Blackdyke BESS Limited | Harker 400kV Substation | 101348-202668 | 1x225MVAR MSC at Carrington 400kV substation | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05129 | Blackdyke BESS Limited | Harker 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05136 | Blackdyke BESS Limited | Harker 400kV Substation | 008645-ON0066 | The offline build and commissioning of a new Harker 132kV GIS substation. The decommissioning and removal of the existing Harker 132kV AIS substation. Develop and commission a new Harker 132kV Auto Close Scheme and a new Harker 132kV Overload Protection Scheme at the Harker substation. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05137 | Blackdyke BESS Limited | Harker 400kV Substation | 101347-202667 | 2x225MVAR MSC at Penwortham 400kV substation | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05138 | Blackdyke BESS Limited | Harker 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05139 | Blackdyke BESS Limited | Harker 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05140 | Blackdyke BESS Limited | Harker 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05141 | Blackdyke BESS Limited | Harker 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Harker Green Energy Centre | PRO-001709 | CS-05142 | Blackdyke BESS Limited | Harker 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2028-10-30
Hartmoor GSP (NE) | PRO-002960 | CS-12383 | NORTHERN POWERGRID (NORTHEAST) PLC | Wearside Connection Node C 400kV Substation | 103361-206817 |  | 2039-10-31
Hartmoor GSP (NE) | PRO-002960 | CS-12384 | NORTHERN POWERGRID (NORTHEAST) PLC | Wearside Connection Node C 400kV Substation | 103553-207048 (EX11) |  | 2039-10-31
Hartmoor GSP (NE) | PRO-002960 | CS-12385 | NORTHERN POWERGRID (NORTHEAST) PLC | Wearside Connection Node C 400kV Substation | 104567-209064 |  | 2039-10-31
Hawkwood Wind Farm | PRO-003450 | CS-08391 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2030-04-30
Hawkwood Wind Farm | PRO-003450 | CS-08392 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 2030-04-30
Hawkwood Wind Farm | PRO-003450 | CS-08393 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 2030-04-30
Hawkwood Wind Farm | PRO-003450 | CS-08394 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2826 | Hagshaw Tee to Bankend Rig III Collector Substation -Install a new 132kV trident wood pole circuit between the tee off with Hagshaw Hill Ph3 Wind Farm and the Bankend Rig III collector. The circuit capacity required for this overhead line circuit is 126MVA. The chosen conductor system for the desktop exercise is AAAC UPAS conductor. The circuit length is approximately 18km. At the Hawkwood substation a new 132/33kV substation shall be created with a 132kV circuit breaker and line disconnector being installed alongside a 132/33kV 120MVA transformer . A 33kV 3 Panel board shall be installed with one feeder being captured under this TORI and the remaining two being allocated to Hawkwood WF and Hawkwood Wind Farm. | 2030-04-30
Hawkwood Wind Farm | PRO-003450 | CS-08395 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2827 | Redshaw to Hagshaw Tee 132kV Circuit - Construct a new 132kV double busbar bay at Redshaw 132kV substation and from here install a new 132kV cable/OHL circuit to an appropriate point at which a tee off shall be established for the Bankend Rig III Collector substation and Hagshaw Hill Ph3 WF connections. | 2030-04-30
Hawthorn Pit Green Energy Centre | PRO-002282 | CS-12617 | HAWTHORN PIT NG LIMITED | Hawthorn Pit 400kV Substation | 030317-030317 (1) |  | 2032-10-31
Hawthorn Pit Green Energy Centre | PRO-002282 | CS-12618 | HAWTHORN PIT NG LIMITED | Hawthorn Pit 400kV Substation | 102121-204322 |  | 2032-10-31
Hawthorn Pit GSP (NE) | PRO-002961 | CS-12360 | NORTHERN POWERGRID (NORTHEAST) PLC | Hawthorn Pit GSP | 102591-205211 |  | 2035-10-30
Heathland Wind Farm | PRO-001156 | CS-06203 | EDF ENERGY RENEWABLES LIMITED | Heathland 132/33kV Substation | Heathland H1 Works | 1. At Wishaw 275/132kV substation, installation of one 132kV circuit breaker and associated disconnectors. This will be teed connect onto the LV side of the supergrid T3 (SGT3) at Wishaw substation. 2. Installation of approximately 18km of 132kV circuit (comprising ~17km of wood pole overhead line and ~1km (sections) of underground cable) from Wishaw substation to Heathland wind farm site. 3. At Heathland wind farm 132kV substation, installation of one 132kV line isolator. | 2028-09-29
Heckington Fen Solar Park | PRO-001903 | CS-12686 | Ecotricity (Heck Fen Solar) Limited | Bicker Fen 400kV Substation | 101716-203424 | 1. Extend Bicker Fenn 400kV substation including 2 Section Breakers Main and Reserve, 1 coupler bay, feeder bay and make provision for the connection of the User’s generation bay. 2. Transpose West Burton Circuit 1 to newly built substation section | 2028-10-01
Heckington Fen Solar Park | PRO-001903 | CS-12687 | Ecotricity (Heck Fen Solar) Limited | Bicker Fen 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2028-10-01
Heckington Fen Solar Park | PRO-001903 | CS-12688 | Ecotricity (Heck Fen Solar) Limited | Bicker Fen 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2028-10-01
Heckington Fen Solar Park | PRO-001903 | CS-12689 | Ecotricity (Heck Fen Solar) Limited | Bicker Fen 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2028-10-01
Heckington Fen Solar Park | PRO-001903 | CS-12690 | Ecotricity (Heck Fen Solar) Limited | Bicker Fen 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2028-10-01
Heights Wind Farm | PRO-000792 | CS-06380 | SP Distribution plc | Bathgate 132/33kV | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 2026-09-30
Helen Street BESS | PRO-003168 | CS-11839 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2028-06-28
Helen Street BESS | PRO-003168 | CS-12150 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2028-06-28
Helen Street BESS | PRO-003168 | CS-12151 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-3263 | Erskine 132kV Bus Section Circuit Breaker | 2028-06-28
Helen Street BESS | PRO-003168 | CS-12152 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-3788 | 3. Neilston 132kV Uprate to 25kA fault rating | 2028-06-28
Helen Street BESS | PRO-003168 | CS-12153 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-3789 | 4. Neilston SGT1 SGT2 SGT3B Load Management Scheme - A transformer load management scheme is required to manage the loadings across SGT1, SGT2 and SGT3B at Neilston 400/275/132kV substation and trip the appropriate non-firm connections to remove any measured overloads. The SPT LMS will be required to transfer the following signals to the User(s): • Stage 1 Signal at 95% of the transformer rating • Stage 2 Signal at 100% of the transformer rating • Stage 3 Signal at 120% of the transformer rating Note: These values will be subject to change following detailed design, User input and optimisation of the system The different stages have the following intended actions: • Stage 1 Signal: Provides an alarm to the connection warning of impending overload condition. • Stage 2 Signal: Will trip connections associated with this TORI as per queue order • Stage 3 Signal: Will trip all connections regardless of queue order (SPT-RI-3789) | 2028-06-28
Helen Street BESS | PRO-003168 | CS-12154 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-3285 | Devol Moor-Erskine-Braehead Park 132kV LMS – BZ Route Monitoring Upgrade –An extension to the existing Devol Moor-Erskine-Braehead Park Load Management Scheme (LMS) is required to manage connections to prevent thermal overloads on the Erskine-Braehead Park Circuit. A new monitoring outstation will be installed at Braehead Park to monitor the loading on the Erskine-Braehead Park 132kV circuit. The measurements will be communicated to Devol Moor 132kV where the IED associated with the existing Devol Moor-Erskine LMS scheme (established under TORI?243) will relay trip signals to relevant non-firm connections as appropriate. | 2028-06-28
Helen Street BESS | PRO-003168 | CS-12155 | Vital Energi Solutions Limited | Govan 132/33kV | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2028-06-28
Heysham Green Energy Centre | PRO-001710 | CS-04643 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101603-203226 |  | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05146 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05147 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101347-202667 | 2x225MVAR MSC at Penwortham 400kV substation | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05148 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101348-202668 | 1x225MVAR MSC at Carrington 400kV substation | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05149 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05150 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05151 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05152 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05153 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05154 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Heysham Green Energy Centre | PRO-001710 | CS-05155 | HEYSHAM GREEN NG LIMITED | Middleton 400KV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2028-10-30
High Constellation Windfarm | PRO-000416 | CS-05793 | HIGH CONSTELLATION WINDFARM LIMITED | High Constellation 132/33kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2027-07-31
High Constellation Windfarm | PRO-000416 | CS-05794 | HIGH CONSTELLATION WINDFARM LIMITED | High Constellation 132/33kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2027-07-31
High Constellation Windfarm | PRO-000416 | CS-05795 | HIGH CONSTELLATION WINDFARM LIMITED | High Constellation 132/33kV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2027-07-31
High Constellation Windfarm | PRO-000416 | CS-06381 | HIGH CONSTELLATION WINDFARM LIMITED | High Constellation 132/33kV Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2027-07-31
High Marnham (Tertiary) | PRO-000531 | CS-06207 | ENSO GREEN HOLDINGS K LIMITED | High Marnham 400kV Substation | 101873-203846 | Construct new High Marnham 400kV substation with 20 bays for network reinforcement. | 2029-10-31
High Marnham (Tertiary) | PRO-000531 | CS-11403 | ENSO GREEN HOLDINGS K LIMITED | High Marnham 400kV Substation | 103534-207019 | Infrastructure works to support Installation of a new 400/33kV SGT including HV and LV bays. a. Establish a new single busbar 33kV substation at High Marnham to be connected via the new 400/33kV SGT. b. Installation of an earthing transformer connecting onto the 33kV busbar. | 2029-10-31
High Marnham 400 | PRO-002194 | CS-08932 | ENSO GREEN HOLDINGS X LIMITED | High Marnham 400kV Substation | 102048-204215 | Extend High Marnham 400kV substation and make provision for the connection of the User’s bay. | 2033-10-31
High Marnham 400 | PRO-002194 | CS-08933 | ENSO GREEN HOLDINGS X LIMITED | High Marnham 400kV Substation | 101873-203846 | Construct new High Marnham 400kV substation with 20 bays for network reinforcement. | 2033-10-31
Highland Wind Farm | PRO-004390 | CS-12487 | HIGHLAND WIND FARM LIMITED | Highland Wind Farm 132/33kV substation | SHET-RI-177 | 3. Tomatin Additional SGTs - Install a new 275kV indoor GIS double busbar and two additional 275/132kV Super Grid Transformers at the Tomatin 275/132kV Substation | 2030-10-31
Highview Hunterston East Cryobattery | PRO-001348 | CS-06639 | HVS SITECO LTD | Hunterston East 400kV | SPT-RI-1857 | Hunterston East to Highview Hunterston 400kV Switchgear and Cable Works | 2027-10-31
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06261 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06262 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-006 | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment. | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06263 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06264 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06265 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-005 | Extend both the 275kV and 132kV busbars and install a second 275/132kV interbus auto-transformer at Dounreay substation. Upgrade the existing 150MVA interbus auto-transformer at Dounreay to 240MVA. | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06266 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06267 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06268 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06269 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06270 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2023-04-30
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06271 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-037 | Fyrish 275/132kV Substation – Establish a new 275kV/132kV Fyrish substation close to the existing Alness 132kV OHL Teed location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. Two new 132kV underground cables will be installed to link the new 275kV/132kV Fyrish substation with the existing Alness GSP. (SHET-RI-037) | 2023-04-30
Hill of Towie 2 Wind Farm | PRO-000938 | CS-05796 | GREENHILLS 1 LIMITED | Keith 2 132/33kV GSP Substation | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2030-06-01
Hill of Towie 2 Wind Farm | PRO-000938 | CS-05797 | GREENHILLS 1 LIMITED | Keith 2 132/33kV GSP Substation | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 2030-06-01
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10341 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 102918-206329 |  | 2037-10-30
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10342 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 102967-206378 |  | 2037-10-30
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10343 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 102917-206328 |  | 2037-10-30
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10344 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 102916-206327 |  | 2037-10-30
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10345 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 101909-203901 | Reconductor the Ironbridge-Rugeley 400kV circuit with 2x620mm² conductor to achieve a pre-fault summer rating of 2490 MVA. | 2037-10-30
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10346 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 102914-206353 |  | 2037-10-30
Hill Street Solar PV/BESS Station | PRO-003744 | CS-10347 | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation | 102915-206326 |  | 2037-10-30
Hinkley Point C | PRO-001674 | CS-10210 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20899 & 20899C | Replacing the 275kV disconnectors, earth switches, post insulators, CVTs and busbars at Bridgwater with 400kV equipment. Replacing the two 275/132kV SGTs at Bridgwater with two 400/275kV SGTs including associated protection. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10211 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20897Q | The work associated with the removal of the existing fluid fill cables at Hinkley Point site between the terminal tower of the VQ route and the Hinkley Point A substation (275kV). | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10212 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20897L4 | Uprating the 275kV Hinkley Point - Bridgwater VQ route to 400kV operation and reconductoring from the tee point to Hinkley Point with GAP equivalent conductor. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10213 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-21535S, NGET-RI-21535C & NGET-RI-21535T1, 21535T2 | A new GSP at Sandford to supply WPD as a consequence of taking over WPD's 132kV 'F' route to construct the new Hinkley Point - Seabank OHL. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10214 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20897L2 | Build a new circuit between the Hinkley Point leg of the broken Hinkley Point - Melksham OHL route and Seabank 400kV substation (~47km). Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors operating at 90°C. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10215 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20897L1 | Breaking into the existing Hinkley Point - Melksham OHL route near M5 motorway and teeing it into the Hinkley Point - Bridgwater circuit by a short (4km) section of new OHL. Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors on the new build section of the OHL, operating at 90°C. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10216 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20832L | Decommissioning the 2 Bridgwater feeder bays at Hinkley Point 275kV substation and re-configure all 6 of the existing 400kV and 275kV feeder circuits at Hinkley Point to facilitate a new connection between Hinkley point and Seabank. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10217 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-21132L | Construction of a short section of new OHL between the line entries of above two circuits at Melksham 400kv substation (approx 800m). | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10218 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20898 | Connecting new Hinkley Point - Seabank 1 circuit to the existing SGT4 bay. Tee-connect new Hinkley Point – Seabank 2 circuit to the existing Seabank – Melksham circuit at very close proximity to Seabank 400kV substation | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10219 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-20832S | Installation of a new 18-bay 400kV GIS double busbar substation at Hinkley Point, consisting of eight feeder bays, two bus couplers, four bus sections, two skeletal generator bays and two skeletal station transformer bays. | 2029-03-31
Hinkley Point C | PRO-001674 | CS-10220 | NNB GENERATION COMPANY (HPC) LIMITED | Shurton 400kV Substation | NGET-RI-21132S | Swaps the Hinkley Point – Melksham 2 circuit and the Bramley Melksham 2 circuit line entries at Melksham 400kV substation. | 2029-03-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-07403 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 101829-203753 |  | 2030-10-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-07404 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 101614-203242 | Extension of South Wales Operational Tripping Scheme | 2030-10-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-07405 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation |  |  | 2030-10-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-07406 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2030-10-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-07407 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2030-10-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-11392 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 103740-207388 |  | 2030-10-31
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-11393 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 101829-207866 |  | 2030-10-31
Holdsworth Road | PRO-002338 | CS-08670 | MAS 002 LIMITED | Bradford West 275kV Substation | 102458-205022 | Make provision for connection of user bay at Bradford West 275kV Substation | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08671 | MAS 002 LIMITED | Bradford West 275kV Substation | 102459-205024 | Construct a new double busbar 275kV Substation at Bradford Wes | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08672 | MAS 002 LIMITED | Bradford West 275kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08673 | MAS 002 LIMITED | Bradford West 275kV Substation | 101939-203974 | Reconductor the Drakelow-Rugeley 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08674 | MAS 002 LIMITED | Bradford West 275kV Substation | 101599-203218 | Reconductor the Padiham-Penwortham 1 circuit to achieve a Summer prefault rating of 2110MVA. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08675 | MAS 002 LIMITED | Bradford West 275kV Substation | 101719-203428 | Uprate the Norton leg of the new Norton- Osbaldwick/ Poppleton 400 kV circuits to provide a pre-fault summer rating of 2350 MVA | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08676 | MAS 002 LIMITED | Bradford West 275kV Substation | 102102-204297 | Reconductor the Carrington – Daines 400kV double circuit achieve a Summer pre fault of 3100MVA (cct 3&4). Reconductor the Carrington - Daines 400kV circuit with 3x700mm² AAAC at 90ºC (3160MVA). L6/5 | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08677 | MAS 002 LIMITED | Bradford West 275kV Substation | 101915-203912 | Uprate Carrington - Penworthham 400kV ZQ OHL Line to 620mm² Matthew Gap conductor. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08678 | MAS 002 LIMITED | Bradford West 275kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08679 | MAS 002 LIMITED | Bradford West 275kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08680 | MAS 002 LIMITED | Bradford West 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08681 | MAS 002 LIMITED | Bradford West 275kV Substation | 102100-204294 | 2x225MVAR MSC at Carrington 400kV substation | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08682 | MAS 002 LIMITED | Bradford West 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08683 | MAS 002 LIMITED | Bradford West 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 2036-10-24
Holdsworth Road | PRO-002338 | CS-08684 | MAS 002 LIMITED | Bradford West 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2036-10-24
Hollandmey Renewable Energy Development | PRO-001094 | CS-05810 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | Hollandmey H1 Works | Establish a new 132kV double busbar GIS feeder bay at the new Gills Bay 132kV switching station, complete with 132kV busbar selector disconnectors, 132kV line circuit breaker and 132kV line disconnector. 2. The Sole Secured Enabling Works also include the installation of approximately 3.5km of 132kV overhead line from the Gills Bay 132kV feeder to the new 132/33kV substation building at the User’s windfarm. At the windfarm substation, the 132kV overhead line will terminate to a new 132kV cable sealing end. Installation of an underground cable to connect the overhead line to a new 132kV AIS switch bay within the windfarm substation building. | 2030-05-31
Hollandmey Renewable Energy Development | PRO-001094 | CS-05811 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 2030-05-31
Hollandmey Renewable Energy Development | PRO-001094 | CS-05812 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2030-05-31
Hollandmey Renewable Energy Development | PRO-001094 | CS-05813 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2030-05-31
Hollandmey Renewable Energy Development | PRO-001094 | CS-05814 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2030-05-31
Holmquarry Road BESS | PRO-004602 | CS-10238 | BIG BATTERY (HOLMQUARRY ROAD) LIMITED | Kilmarnock Town 275/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-04-30
Holmquarry Road BESS | PRO-004602 | CS-10239 | BIG BATTERY (HOLMQUARRY ROAD) LIMITED | Kilmarnock Town 275/33kV Substation | SPT-RI-2249 | Kilmarnock South 275kV Fault Level Uprating - To allow the connection of a battery storage connection at Kilmarnock South 400kV substation, the short circuit rating of Kilmarnock South 275kV substation equipment needs to be increased from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2026-04-30
Holmquarry Road BESS | PRO-004602 | CS-10240 | BIG BATTERY (HOLMQUARRY ROAD) LIMITED | Kilmarnock Town 275/33kV Substation | SPT-TOCO-517 | Kilmarnock Town GSP (Asset Replacement, Fault Level Mitigation) – The existing SGT1 & SGT2 275/33kV 120MVA transformers will be replaced with dual wound 275/33kV 60+60MVA transformers. A new 33kV circuit breaker will be installed to be used temporarily after one SGT is replaced and before the second is replaced. Provision will be made to give OCC visibility and control of the AVC and tap changer for the new SGTs | 2026-04-30
Holmston Farm Battery Energy Storage System | PRO-002359 | CS-08327 | Field Holmston Ltd | Ayr 275/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2025-06-30
Hopsrig Wind Farm | PRO-000318 | CS-05815 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm² Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 2027-10-31
Hopsrig Wind Farm | PRO-000318 | CS-05816 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 2027-10-31
Hopsrig Wind Farm | PRO-000318 | CS-06335 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 2027-10-31
Hopsrig Wind Farm | PRO-000318 | CS-06336 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 2027-10-31
Hopsrig Wind Farm | PRO-000318 | CS-06337 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2027-10-31
Hornsea Power Station 3 | PRO-000434 | CS-05176 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 032452-032452 | Connection of an OFTO bay into existing spare bay. Extension of the existing Norwich Main 400 kV substation on the East side to accommodate a new fully populated bus coupler circuit breaker and reconfiguration of SGT5 bay. | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05177 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 032452-203187 | Extension of the existing 400kV substation for the construction of fully populated main and reserve bus section bays with circuit breakers, one new bus coupler bay and one new feeder bay to accommodate transfer of the Norwich Main – Bramford 1 feeder circuit | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05178 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 030447-030447 (1) |  | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05179 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 100637-201311 | Uprate the existing Rayleigh Main to Tibury 400kV circuit to provide a post fault winter rating of 2210MVA | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05180 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05181 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05182 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05183 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05184 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05185 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05825 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 32452 | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 2026-10-01
Hornsea Power Station 3 | PRO-000434 | CS-05826 | HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 2026-10-01
Hornsea Power Station 4 | PRO-000435 | CS-05186 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-033837 | At Creyke Beck 400kV Substation: Extend Main 1 and Reserve 1 busbars for a Main 3 and Reserve 3 Section Breaker, one Hornsea P4 First Bay and one feeder bay (Interconnector 1 to Creyke Beck 400kV Main and Reserve busbars 4). | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05187 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05188 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05189 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05190 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-201012 | At Creyke Beck 400kV Substation: Build a new 400kV double busbar compound with 2 feeders bay, 1 coupler bay, 1 section bay and connect 2 new interconnectors to Creyke Beck 400kV substation | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05191 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-201648 | At Creyke Beck 400kV Substation: Move Creyke Beck - Thornton 2 circuit and Creyke Beck - Humber Refinery - Keadby circuit to the new GIS Creyke Beck 400kV Compound. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05192 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05193 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-201649 | At Creyke Beck 400kV Substation: Install an 8 Ohm series reactor, utilising the vacated Creyke Beck – Humber Refinery – Keadby feeder bay, with an additional feeder bay to be established by extension of Main and Reserve busbar 3. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05194 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05195 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05196 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05197 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100206-200545 | Installation of a 225MVAr MSC at West Burton 400kV substation | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05198 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05199 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100460-201025 | At Creyke Beck 400kV Substation: Extend Main & Reserve busbars 5 to allow one Hornsea P4 Second Bay. Extend the OTS to include Hornsea P4 Second Bay. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05200 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05201 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05202 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05203 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05204 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05205 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05206 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100909-201825 | Uprate the existing bays in the Creyke Beck – Thornton 2 circuit (A323) to achieve a post fault summer rating of 3300MVA. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05207 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100987-201984 | Uprate the existing bays in the Creyke Beck – Thornton 1 circuit to achieve a post fault summer rating of 3300MVA. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05829 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 33837-3 | Installation of a series reactor at Creyke Beck, utilising the vacated Thornton circuit bay can be used as one of the bay, with an additional bay to be established byextension of Main Bar 2 and Reserve Bar 2. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05830 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 33837-2 | Installation of a new feeder bay on the new bus section and transfer of one of the Thornton circuits into this bay. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05831 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 33837-4 | Provision of a skeletal bay in new bus section at Creyke Beck 400kV substation to allow connection of the offshore transmission cicuit. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-05832 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 33837-1 | Installation of a new section switch in both Main Bar 1 and Reserve busbar 1 at Creyke Beck 400kV substation substation. | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-10743 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-201012 | At Creyke Beck 400kV Substation: Build a new 400kV double busbar compound with 2 feeders bay, 1 coupler bay, 1 section bay and connect 2 new interconnectors to Creyke Beck 400kV substation | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-10744 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-207254 |  | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-10745 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 033837-207255 |  | 2028-10-30
Hornsea Power Station 4 | PRO-000435 | CS-10746 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 100460-201025 | At Creyke Beck 400kV Substation: Extend Main & Reserve busbars 5 to allow one Hornsea P4 Second Bay. Extend the OTS to include Hornsea P4 Second Bay. | 2028-10-30
Househill BESS | PRO-001499 | CS-08111 | HOUSEHILL BESS LIMITED | Nairn GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2027-10-31
Housham PV & BESS | PRO-002254 | CS-07911 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101687-203362 | Build a new Navenby 400kV Double Busbar Substation with 4 Feeder bays, and 1 Coupler Bay in the vicinity of tower 4ZM508. | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07912 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101687-203363 | Establish a double turn in connection between the new 400kV substation and the West Burton – Bicker Fen 400kV circuit 1 and 2 | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07913 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 102070-204246 | Extension of the newly built Navenby 400kV substation busbars to accommodate the User’s bay | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07914 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07915 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07916 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07917 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07918 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07919 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07920 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07921 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07922 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07923 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07924 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07925 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07926 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2033-05-30
Housham PV & BESS | PRO-002254 | CS-07927 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100798-201612 | At Cottam 400kV Substation: Uprate feeder bay disconnector and circuit breaker on the Cottam - West Burton circuit to provide a post fault summer rating of 3060MVA | 2033-05-30
Howmuir PV | PRO-001234 | CS-06245 | Scottish Hydro Electric Power Distribution Plc | Lunanhead GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2021-11-30
Hunterston Battery Storage Facility | PRO-001155 | CS-04308 | FLEXIBLEGRIDPOWER2 LTD | Ayrshire Grid 400kV Substation | SPT-RI-1566 | Hunterston East to Ayrshire Grid 400kV switchgear and cable works - It is proposed to extend the GIS double busbar and install a new 400kV switchbay at Hunterston East 400kV GIS substation, install approximately 900m of 400kV underground cable from the Hunterston East 400kV GIS substation to a new collector substation (Ayrshire Grid 400kV collector substation). At the collector substation, a new outdoor 400kV busbar and three isolators shall be installed. | 2026-03-09
Hunterston Energy Storage Facility | PRO-001644 | CS-04467 | HUNTERSTON GRID 2 LTD | Ayrshire Grid 400kV Substation | SPT-RI-1566 | Hunterston East to Ayrshire Grid 400kV switchgear and cable works - It is proposed to extend the GIS double busbar and install a new 400kV switchbay at Hunterston East 400kV GIS substation, install approximately 900m of 400kV underground cable from the Hunterston East 400kV GIS substation to a new collector substation (Ayrshire Grid 400kV collector substation). At the collector substation, a new outdoor 400kV busbar and three isolators shall be installed. | 2025-08-27
Hunterston Hydrogen | PRO-003957 | CS-11353 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3472 |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11354 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3473 Hunterston – Kilmarnock South 400kV Reinforcement |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11355 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3485 Cable |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11356 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3485 OHL |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11357 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3485 SS |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11358 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3490 |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11359 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3505 H1 OHL |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11360 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3728 |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11361 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3974 OHL |  | 2033-10-31
Hunterston Hydrogen | PRO-003957 | CS-11362 | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV | SPT-RI-3974 SS |  | 2033-10-31
Hunterston Wind Farm | PRO-003165 | CS-09330 | GALILEO 01 LIMITED | Hunterston 400/132kV | SPT-RI-2832 | New Hunterston East 132kV GIS Substation - existing Hunterston 132kV indoor switchboard be replaced with a new GIS building which shall accommodate 11 bays of non-SF6 gas insulated switchgear bays with 2 x SGT transformer bays (SGT1 and SGT2), 3 x Feeder bays (Hunterston Farm1-Kilwinning, Hunterston Farm2-Saltcoats and Kilwinning-Saltcoats), 1 x Bus-coupler bay, 1 x Bus-section bay and future provision for 4 x spare feeder bay | 2033-04-30
Hunterston Wind Farm | PRO-003165 | CS-09331 | GALILEO 01 LIMITED | Hunterston 400/132kV | Hunterston WF Feeder Bay | Installation of a new 132kV GIS DBB feeder bay and associated switchgear (circuit breaker and DBB disconnectors) | 2033-04-30
Hunterston Wind Farm | PRO-003165 | CS-09332 | GALILEO 01 LIMITED | Hunterston 400/132kV | Hunterston WF Circuit | Installation of approx. 5km of 132kV circuit (OHL/UGC) from Hunterston East 132kV substation to Hunterston Windfarm 132k | 2033-04-30
Hunterston Wind Farm | PRO-003165 | CS-09333 | GALILEO 01 LIMITED | Hunterston 400/132kV | Hunterston WF Disconnector | Installation of a 132kV line disconnector at the Hunterston Windfarm substation | 2033-04-30
Hurst BESS | PRO-004249 | CS-10533 | LUMINOUS ENERGY GROUP LIMITED | North Kent Connection Node C 400kV Substation | 103467-206935 (LEGL) |  | 2037-10-31
Hurst BESS | PRO-004249 | CS-10534 | LUMINOUS ENERGY GROUP LIMITED | North Kent Connection Node C 400kV Substation | 103480-206951 |  | 2037-10-31
Icewind Blyth | PRO-001717 | CS-05222 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101548-203088 | At Blyth 400kV Substation: Extend Main and Reserve bar section to accommodate a User bay, install 2 new section breakers in both Main and Reserve busbar, create a new feeder bay and transfer the Blyth-Eccles - Stella West 2 circuit and install a generator intertripping scheme. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05223 | KARI ENERGY LIMITED | Blyth 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05224 | KARI ENERGY LIMITED | Blyth 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05225 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101369-202689 | Reconductor the Blyth legs of the Blyth – Eccles – Stella West 1 and Blyth – Eccles – Stella West 2 circuits with GAP conductor and replace the cable sections of both circuits. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05226 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05227 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05228 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101370-202690 | At Blyth 400kV / 275kV substation: Install 2 new 1100MVA rated interbus transformers. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05229 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101540-203059 | Reconductor the South Shields – West Boldon 275kV circuit with 1x525mm² Curlew conductor. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05230 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05231 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05232 | KARI ENERGY LIMITED | Blyth 400kV Substation | SPT- Icewind Blyth H1 | a. Reconfiguration and/ or replacement of Main Protections at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits. The final scope of protection and control works will be subject to detailed engineering design and studies, the scope of which shall include ‘hardware-in-the-loop’ transient testing, to be performed by real time simulation using relays provided by the Relevant Transmission Licensees, and with a suitable and sufficient representation of the User’s DC Converters and system, their controls, reactive compensation and filter equipment to be provided by the User. b. Modification of Series Compensation Equipment at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits as required. The final scope of series compensation related works will be subject to a detailed engineering design and studies to be completed by the series compensation equipment Original Equipment Manufacturer. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05233 | KARI ENERGY LIMITED | Blyth 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05234 | KARI ENERGY LIMITED | Blyth 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05235 | KARI ENERGY LIMITED | Blyth 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05236 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05237 | KARI ENERGY LIMITED | Blyth 400kV Substation | 100110-200299 | Install three new 225MVAr MSCs at Norton, Osbaldwick and Stella West 400kV substations. (NOA NEMS). | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05238 | KARI ENERGY LIMITED | Blyth 400kV Substation | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05239 | KARI ENERGY LIMITED | Blyth 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05240 | KARI ENERGY LIMITED | Blyth 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05241 | KARI ENERGY LIMITED | Blyth 400kV Substation | 020669-020669 | Lackenby – Norton 1 circuit reconductor the 2x570mm² sections with 2x620mm² GZTACSR conductor. Replace the cable section of the circuit. | 2031-10-31
Icewind Blyth | PRO-001717 | CS-05242 | KARI ENERGY LIMITED | Blyth 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2031-10-31
Imperial Park BESS | PRO-003615 | CS-10526 | KONA ASSET 4 LIMITED | Imperial Park B 400kV Substation | 103491-206969 |  | 2037-10-31
Imperial Park BESS | PRO-003615 | CS-10527 | KONA ASSET 4 LIMITED | Imperial Park B 400kV Substation | 103491-207092 |  | 2037-10-31
Imperial Park BESS | PRO-003615 | CS-10528 | KONA ASSET 4 LIMITED | Imperial Park B 400kV Substation | 101696-203378 (KONA) |  | 2037-10-31
Inch Cape Offshore Wind Farm Platform 1 | PRO-000348 | CS-05838 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | Inch Cape Offshore Wind Farm Platform 1-H1 Shared |  | 2026-02-21
Inch Cape Offshore Wind Farm Platform 1 | PRO-000348 | CS-05839 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | Inch Cape Offshore Wind Farm Platform 1-H1 Sole |  | 2026-02-21
Inch Cape Offshore Wind Farm Platform 1 | PRO-000348 | CS-06247 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | SPT-RI-1742 SS |  | 2026-02-21
Inch Cape Offshore Wind Farm Platform 1 | PRO-000348 | CS-06887 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | Inch Cape Offshore Wind Farm H1 Works Item 3 | Provision of communications, alarms, indications and metering, as described in Appendix F and OF of the relevant Bilateral Connection Agreement. | 2026-02-21
Inch Cape Offshore Wind Farm Platform 2 | PRO-000349 | CS-05840 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | Inch Cape Plat 2 H1 Sole |  | 2026-02-21
Inch Cape Offshore Wind Farm Platform 2 | PRO-000349 | CS-05841 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | Inch Cape Plat 2 H1 Shared |  | 2026-02-21
Inch Cape Offshore Wind Farm Platform 2 | PRO-000349 | CS-06248 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | SPT-RI-1742 SS |  | 2026-02-21
Inch Cape Offshore Wind Farm Platform 2 | PRO-000349 | CS-06888 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV | Inch Cape Offshore Wind Farm H1 Works Item 3 | Provision of communications, alarms, indications and metering, as described in Appendix F and OF of the relevant Bilateral Connection Agreement. | 2026-02-21
Inchbean Energy Park | PRO-002453 | CS-08257 | BROCKWELL STORAGE & SOLAR LIMITED | Kilmarnock Town 275/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2025-06-30
Inchbean Energy Park | PRO-002453 | CS-08258 | BROCKWELL STORAGE & SOLAR LIMITED | Kilmarnock Town 275/33kV | SPT-RI-517 | Kilmarnock Town GSP asset replacement, fault level mitigation | 2025-06-30
Indian Queens Energy Centre | PRO-001371 | CS-05208 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2025-05-31
Indian Queens Energy Centre | PRO-001371 | CS-05209 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 033539- 033539 | Hot wiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating | 2025-05-31
Indian Queens Energy Centre | PRO-001371 | CS-05210 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2025-05-31
Indian Queens Energy Centre | PRO-001371 | CS-05842 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 100443-200993 | Connection | 2025-05-31
Indian Queens Energy Centre | PRO-001371 | CS-05843 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2025-05-31
Innerwick BESS | PRO-002828 | CS-09561 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2028-07-31
Innerwick BESS | PRO-002828 | CS-09562 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2028-07-31
Innerwick BESS | PRO-002828 | CS-09563 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2028-07-31
Innerwick BESS | PRO-002828 | CS-09564 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2028-07-31
Innerwick BESS | PRO-002828 | CS-09565 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | SPT-RI-2963 | Branxton to Eccles Further Uprating – In order to alleviate the overloads identified as part of the system studies conducted it is necessary to reconductor both sides of the Branxton to Eccles circuits with twin HTLS “Curlew” conductor. This conductor shall give a summer pre-fault rating on the circuit of 2590MVA | 2028-07-31
Innerwick BESS | PRO-002828 | CS-09566 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | SPT-RI-3148 | Branxton BESS Collector Substation – Install a new 400kV GIS bay at Branxton substation to accommodate the connection of these two battery storage connections. From here a new 400kV circuit shall be installed out to the new shared substation indicatively named Branxton BESS 400/132kV Collector substation. At this shared substation a 400kV line disconnector shall be installed alongside two 400kV transformer circuit breakers and two 400/132kV 360MVA transformers will be installed with each transformer requiring its own 132kV circuit breaker. This forms the scope of SPT-RI-3148 which this connection shall be contingent on. A 132kV shared busbar will be installed alongside three individual metering circuit breakers for the local connections. | 2028-07-31
Innerwick BESS | PRO-002828 | CS-09567 | Innerwick Storage Ltd | Braxbess 400/132kV Collector Substation | Disconnector - Branxton BESS Collector | Installation of a 132kV line disconnector at Branxton BESS 400/132kV Collector substation for the Innerwick BESS connection | 2028-07-31
Iron Acton | PRO-000455 | CS-06813 | HD000ACT LTD | Iron Acton 275kV Substation | 100810-201635 | 1. Works to facilitate the use of Iron Acton 132kV substation’s spare bay for the User’s connection. 2. Installation of a new Category 2 Operational Tripping Scheme | 2026-04-13
Iron Acton | PRO-000491 | CS-05844 | IRON ACTON GREEN LIMITED | 132kV bay at Iron Acton Substation | 100900-201809 | Attributable | 2026-09-30
Ironbridge | PRO-001629 | CS-04541 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101484-202931 | Extension of the existing Ironbridge 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 2031-04-30
Ironbridge | PRO-001629 | CS-04542 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-04-30
Ironbridge | PRO-001629 | CS-04543 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2031-04-30
Ironbridge | PRO-001629 | CS-04544 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-04-30
Ironbridge | PRO-001629 | CS-04545 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-04-30
Ironbridge | PRO-001629 | CS-04546 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2031-04-30
Ironbridge | PRO-001629 | CS-04547 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-04-30
Ironbridge | PRO-001629 | CS-04548 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2031-04-30
Ironbridge | PRO-001629 | CS-04549 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2031-04-30
Ironbridge | PRO-001629 | CS-11437 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101484-202931 1 |  | 2031-04-30
Isle of Man Offshore Wind Farm | PRO-003698 | CS-08690 | Mooir Vannin Offshore Wind Farm Limited | Penwortham 400kV Substation | 102450-205004 |  | 2037-10-30
iV025 Craigton Energy Storage | PRO-003664 | CS-11840 | FLEXION ENERGY UK STORAGE LTD | Craigiebuckler GSP | SHET-RI-278 New Craigiebuckler 132kV Substation |  | 2027-08-30
Iver | PRO-001141 | CS-05211 | Juniper Energy Limited | Iver 275kV Substation | NGET-RI-100278-200770 (Infra) | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable to motorised disconnector from tertiary connection 3. Install 13kV disconnector connecting tertiary to connection assets for Users connection | 2027-10-29
Jackdaw BESS | PRO-004351 | CS-11546 | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2036-10-31
Jackdaw BESS | PRO-004351 | CS-11547 | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2036-10-31
Jackdaw BESS | PRO-004351 | CS-11548 | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation | 101509-202974-1 |  | 2036-10-31
Jackdaw BESS | PRO-004351 | CS-11549 | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation | 102501-205096 1 |  | 2036-10-31
Jackdaw BESS | PRO-004351 | CS-11550 | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation | 103166-206585 |  | 2036-10-31
Jackdaw BESS | PRO-004351 | CS-11551 | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation | 103588-207106 |  | 2036-10-31
Jamesfield Farm | PRO-006011 | CS-12332 | GREENTECH PROJECTS HOLDING UK LIMITED | Abernethy 2 GSP | SHET-RI-255 Abernethy 400kV Substation | Construct a new 400kV busbar to facilitate the connection of a new 400/33kV GSP at Abernethy. | 2033-10-31
JBM Solar 12 - Shrewsbury Solar | PRO-001146 | CS-06825 | RWE Renewables UK Solar and Storage Limited | Shrewsbury 400/33kV Substation | 100754-201558 | 1. Install a tertiary cable box or bushings on the SGT 3. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2028-09-30
JBM Solar 13 - Melksham | PRO-000495 | CS-07308 | JBM SOLAR PROJECTS 13 LIMITED | Melksham 400kV Substation | 100776 - 201571 |  | 2026-07-17
JBM Solar 13 - Melksham | PRO-000495 | CS-07310 | JBM SOLAR PROJECTS 13 LIMITED | Melksham 400kV Substation | 101305-202589 |  | 2026-07-17
JBM Solar 13 - Melksham | PRO-000495 | CS-12592 | JBM SOLAR PROJECTS 13 LIMITED | Melksham 400kV Substation | 102261-204486 |  | 2026-07-17
JBM Solar -Minety | PRO-000432 | CS-06866 | JBM SOLAR PROJECTS 14 LTD | Minety 400kV Substation | 101488-202944 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish new bus bar, 33kV substation at Minety to be connected via new 400/33kV SGT8B 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2028-11-30
Jersey Farm BESS | PRO-002264 | CS-09366 | CSE39 LIMITED | Jersey Farm 400kV Substation | 102075-204256 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to Jersey Farm via the Exeter – Taunton 2 overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL turn-In connection and the User’s Generator Bay. Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 2032-10-25
JG Pears | PRO-000250 | CS-05845 | JG PEARS GRID CONNECTION LIMITED | High Marnham 275kV Substation | 33237I | Provision of the skeletal bay for the User to connect. The existing SGT1 skeletal bay assets are to be transferred to the User. | 2025-11-30
Keadby GSP (Yorkshire) | PRO-002975 | CS-11844 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103652-207213 |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-11845 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103652-207214 |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-11846 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103652-207216 |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-11847 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104337-208446 Manton Solar Farm |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12030 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 101865-203833 Keadby PP |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12031 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103136-206551 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12032 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103136-206622 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12033 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103545-207038 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12034 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103545-207039 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12035 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104286-208320 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12036 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104286-208321 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12037 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104392-208500 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12038 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104392-208501 Keadby |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12047 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104396-208506 |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12386 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 101865-203833 Crosby Le Moor |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12387 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 103136-206551 Crosby Le Moor |  | 2027-10-31
Keadby GSP (Yorkshire) | PRO-002975 | CS-12388 | Northern Powergrid (Yorkshire) Plc | Keadby GSP | 104286-208320 Crosby Le Moor |  | 2027-10-31
Kearsley | PRO-001064 | CS-05212 | PIVOTED POWER LLP | Kearsley 275kV Substation | 100578-201127 | 1. Extend the Kearsley site as required to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 4 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer 4. Install an earthing transformer 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07306 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101618-203252 |  | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07307 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07309 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101618-203251 |  | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07311 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07312 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07313 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07314 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07315 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07316 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07317 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101347-202667 | 2x225MVAR MSC at Penwortham 400kV substation | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07318 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07319 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2028-10-31
Kearsley North Green Energy Centre | PRO-001793 | CS-07320 | Kearsley North Green NG Limited | Kearsley 275kV Substation | 101627-203263 | Cable uprate on the Kearsley - Whitegate 275 kV circuit 1 to achieve a pre fault summer rating of 400 MVA | 2028-10-31
Kedrum Solar Farm | PRO-003444 | CS-09468 | Rosside Energy Limited | Blackhillock 275kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2030-05-30
Kedrum Solar Farm | PRO-003444 | CS-09469 | Rosside Energy Limited | Blackhillock 275kV Substation | SHET-RI-178 |  | 2030-05-30
Kedrum Solar Farm | PRO-003444 | CS-09470 | Rosside Energy Limited | Blackhillock 275kV Substation | SHET-RI-236 | Blackhillock - Cairnford 275kV Line Works - Establish a new 275kV tee point of the Blackhillock to Cairnford 275kV HCD2 circuit. This will require 3x 275kV line disconnectors and 1x 275kV line circuit breaker. This tee point will be adjacent to that seen from SHET-RI-178, and therefore this new TORI will be dependent on SHET-RI-178 to create the land/compound required for this new switchgear | 2030-05-30
Kedrum Solar Farm | PRO-003444 | CS-09471 | Rosside Energy Limited | Blackhillock 275kV Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2030-05-30
Keith 132 Greener Grid Park | PRO-001129 | CS-04684 | KEITH STORAGE SOLUTIONS LIMITED | Keith 1 132/33kV GSP Substation | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2025-05-31
Keith Battery Storage | PRO-001742 | CS-07121 | Field Keith Ltd | Keith 1 132/33kV GSP Substation | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2026-10-31
Keith BESS | PRO-004399 | CS-11660 | ANESCO LIMITED | Keith GSP | SHET-RI-009 East Coast Onshore 275kV Upgrade |  | 2033-10-31
Keith BESS | PRO-004399 | CS-11661 | ANESCO LIMITED | Keith GSP | SHET-RI-025a Peterhead - Rothienorman 400kV OHL Upgrade |  | 2033-10-31
Keith BESS | PRO-004399 | CS-11662 | ANESCO LIMITED | Keith GSP | SHET-RI-025c Peterhead 400kV Busbar |  | 2033-10-31
Keith BESS | PRO-004399 | CS-11663 | ANESCO LIMITED | Keith GSP | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2033-10-31
Keith BESS | PRO-004399 | CS-11664 | ANESCO LIMITED | Keith GSP | SHET-RI-026 Blackhillock 275kV QBs |  | 2033-10-31
Keith BESS | PRO-004399 | CS-11665 | ANESCO LIMITED | Keith GSP | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
KELL440MW BESS | PRO-003956 | CS-10604 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102501-205096 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10605 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 103582-207099 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10606 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 103583-207100 TCAs |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10607 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10608 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10609 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10610 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10611 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10612 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10613 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10614 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100173-200455 | Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and130) at Drax 132kV Substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10615 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10616 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10617 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10618 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10619 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100479-201050 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10620 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10621 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10622 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10623 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10624 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10625 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10626 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10627 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10628 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101164-202350 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10629 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101164-202350 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10630 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101325-202642 | At Thornton 400kV: Establish an additional section switch in place of X224 or X228 and add another section switch in place of X428 or X424. Replace circuit breaker X405 and X805 (In Lackenby - Thornton circuits with 63kA rated breakers. (101325-202642) | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10631 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10632 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10633 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101386-202716 | LTRE (NOA)Upgrade the existing circuits between Lackenby and Thornton to allow for more capacity | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10634 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101508-202973 (1) |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10635 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10636 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10637 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101625-203259 | Uprate the Drax - Eggborough 2 circuit to achieve a post fault summer rating of 2500MVA. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10638 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101646-203283 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10639 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101661-203312 | Uprating/Replacement of the CB T10 at Monk Fryston 275kV substation | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10640 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10641 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10642 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm² Araucaria conductor | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10643 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101712-203416 | Uprating/Replacement of the following CB at Stella West 275 kV substation: H10, H20, H40, H50, H90, S10 and W10 | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10644 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10645 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10646 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102178-204388 | Replacement of CB's S10, P10, W10, W20, H10 and H20 at Blyth 275kV Substation | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10647 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102197-204417 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10648 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102356-204777 | Uprating/Replacement of the following Circuit breakers for a higher X/R ratio of 25 at Drax 400kV substations: X430, X630, X405. | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10649 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102360-204779 | Uprating/Replacement of the following Circuit breakers at Creyke Beck 400kV substation X510, X130, X420, X430, X520, X620, X330, X1215, X905, X210, X1415, X320 | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10650 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102412-204937 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10651 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102591-205211 |  | 2035-10-30
KELL440MW BESS | PRO-003956 | CS-10652 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP |  |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10653 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102501-205096 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10654 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 103582-207099 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10655 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10656 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10657 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10658 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10659 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10660 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10661 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10662 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100173-200455 | Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and130) at Drax 132kV Substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10663 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10664 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10665 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10666 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10667 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100479-201050 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10668 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10669 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10670 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10671 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10672 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10673 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10674 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10675 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10676 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101164-202350 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10677 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101325-202642 | At Thornton 400kV: Establish an additional section switch in place of X224 or X228 and add another section switch in place of X428 or X424. Replace circuit breaker X405 and X805 (In Lackenby - Thornton circuits with 63kA rated breakers. (101325-202642) | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10678 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10679 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10680 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101386-202716 | LTRE (NOA)Upgrade the existing circuits between Lackenby and Thornton to allow for more capacity | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10681 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101508-202973 (1) |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10682 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10683 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10684 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101625-203259 | Uprate the Drax - Eggborough 2 circuit to achieve a post fault summer rating of 2500MVA. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10685 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101646-203283 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10686 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101661-203312 | Uprating/Replacement of the CB T10 at Monk Fryston 275kV substation | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10687 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10688 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10689 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm² Araucaria conductor | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10690 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101712-203416 | Uprating/Replacement of the following CB at Stella West 275 kV substation: H10, H20, H40, H50, H90, S10 and W10 | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10691 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10692 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10693 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102178-204388 | Replacement of CB's S10, P10, W10, W20, H10 and H20 at Blyth 275kV Substation | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10694 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102197-204417 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10695 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102356-204777 | Uprating/Replacement of the following Circuit breakers for a higher X/R ratio of 25 at Drax 400kV substations: X430, X630, X405. | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10696 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102360-204779 | Uprating/Replacement of the following Circuit breakers at Creyke Beck 400kV substation X510, X130, X420, X430, X520, X620, X330, X1215, X905, X210, X1415, X320 | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10697 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102412-204937 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10698 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP | 102591-205211 |  | 2035-10-30
Kellingley IDNO BESS | PRO-004340 | CS-10699 | CARE POWER (KELLINGLEY) LIMITED | Kellingley IDNO GSP |  |  | 2035-10-30
Kennishead | PRO-004373 | CS-10278 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-2268 Cable |  | 2031-10-31
Kennishead | PRO-004373 | CS-10279 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-2268 OHL |  | 2031-10-31
Kennishead | PRO-004373 | CS-10280 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-2390 OHL |  | 2031-10-31
Kennishead | PRO-004373 | CS-10281 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-2390 SS |  | 2031-10-31
Kennishead | PRO-004373 | CS-10282 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-3534 - Cable |  | 2031-10-31
Kennishead | PRO-004373 | CS-10283 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-3534 - SS |  | 2031-10-31
Kennishead | PRO-004373 | CS-10284 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-3419 - Neilston 132kV B board (SS) | It is proposed to establish a new Neilston 132kV B substation to accommodate new load connections into the Neilston 132kV network. The switchboard will be fed via two 400/132kV SGT’s. A 132kV bus section will be installed with corresponding disconnectors on the reserve busbar, a 132kV bus coupler and four 132kV feeder bays (space required within the switchgear housing to accommodate future connections) will also be installed. Two bays will be used to connect the 400/132kV SGT’s with the remaining four bays used to transfer across the Braehead Park/Govan and Crookston 132kV circuits from the existing Neilston 132kV switchboard. Two new 400kV DBB GIS feeder bays with associated switchgear (circuit breaker and DBB disconnectors) will be installed at Neilston 400kV to connect the new 400/132kV 360MVA Super Grid Transformers. | 2031-10-31
Kennishead | PRO-004373 | CS-10285 | STARLIGHT ENERGY UK LIMITED | Haggs Road GSP | SPT-RI-3419 - Neilston 132kV B board (Cable) | It is proposed to establish a new Neilston 132kV B substation to accommodate new load connections into the Neilston 132kV network. The switchboard will be fed via two 400/132kV SGT’s. A 132kV bus section will be installed with corresponding disconnectors on the reserve busbar, a 132kV bus coupler and four 132kV feeder bays (space required within the switchgear housing to accommodate future connections) will also be installed. Two bays will be used to connect the 400/132kV SGT’s with the remaining four bays used to transfer across the Braehead Park/Govan and Crookston 132kV circuits from the existing Neilston 132kV switchboard. Two new 400kV DBB GIS feeder bays with associated switchgear (circuit breaker and DBB disconnectors) will be installed at Neilston 400kV to connect the new 400/132kV 360MVA Super Grid Transformers. | 2031-10-31
Kennoxhead Wind Farm | PRO-000319 | CS-05857 | ORSTED ONSHORE UK LIMITED | Coalburn 132kV | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 2028-04-28
Kennoxhead Wind Farm | PRO-000319 | CS-05858 | ORSTED ONSHORE UK LIMITED | Coalburn 132kV | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 2028-04-28
Kennoxhead Wind Farm | PRO-000319 | CS-05859 | ORSTED ONSHORE UK LIMITED | Coalburn 132kV | Kennoxhead Wind Farm Sole Enabling Works | 1. Installation of one 132kV line isolator at Kennoxhead wind farm substation. 2. Installation of approximately 2km of 132kV XLPE cable out of Coalburn 132kV substation. 3. Installation of approximately 15.4km 132kV wood pole overhead line between Kennoxhead wind farm substation and Coalburn substation. 4. At Coalburn substation, install a new 132kV bay including circuit breaker, isolator, surge arrester and associated switchgear to connect the new line connecting to Kennoxhead wind farm substation. | 2028-04-28
Killean Wind Farm | PRO-006009 | CS-12464 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-013 North Argyll (Ardbrecknish Substation) |  | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12465 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12466 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-086 Craig Murrail Switching Station |  | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12467 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-107 North Argyll - Inveraray Reinforcement |  | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12468 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-130a North Argyll - Craig Murrail 275kV Operation |  | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12469 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-130b Craig Murrail - Crossaig 275kV Operation |  | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12470 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-158 Twin Carradale –KilmarnockSouth subsea cable |  | 2034-10-31
Killean Wind Farm | PRO-006009 | CS-12471 | Renewable Energy Systems Limited | CARRADALE 3 GSP | SHET-RI-197 Kintyre to North Wales HVDC Link |  | 2034-10-31
Killermont GSP | PRO-003331 | CS-09822 | SP Distribution plc | Killermont GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-06-30
Killermont GSP | PRO-003331 | CS-09823 | SP Distribution plc | Killermont GSP | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 2031-06-30
Killermont GSP | PRO-003331 | CS-09824 | SP Distribution plc | Killermont GSP | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 2031-06-30
Killermont GSP | PRO-003331 | CS-09825 | SP Distribution plc | Killermont GSP | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2031-06-30
Kilmarnock BESS | PRO-001836 | CS-05442 | KILMARNOCK FLEXPOWER LTD | Kilmarnock South 400kV Substation | kilmarnock BESS | Installation of a new 400kV double busbar GIS bay at Kilmarnock South 400kV substation including a 400kV circuit breaker and associated equipment. Installation of a new 400kV cable circuit (approx. 2.6km) between Kilmarnock South 400kV substation and the User’s site. Installation of a 400kV line disconnector at the User’s site. | 2026-10-31
Kilmarnock BESS | PRO-001836 | CS-05443 | KILMARNOCK FLEXPOWER LTD | Kilmarnock South 400kV Substation | SPT-RI-1854 | At Kilmarnock South 400kV GIS substation install a bus coupler to run the substation in double busbar arrangements. (SPT-RI-1854). Protection and control modifications as required. Associated civil works. Miscellaneous and minor works | 2026-10-31
Kilmarnock BESS | PRO-001836 | CS-05444 | KILMARNOCK FLEXPOWER LTD | Kilmarnock South 400kV Substation | SPT-RI-2249 | Kilmarnock South 275kV Fault Level Uprating - To allow the connection of a battery storage connection at Kilmarnock South 400kV substation, the short circuit rating of Kilmarnock South 275kV substation equipment needs to be increased from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2026-10-31
Kilmarnock South Battery Storage | PRO-001809 | CS-05401 | Kilmarnock Energy Centre Limited | Kilmarnock South 400kV Substation | SPT-RI-1854 | At Kilmarnock South 400kV GIS substation install a bus coupler to run the substation in double busbar arrangements. (SPT-RI-1854). Protection and control modifications as required. Associated civil works. Miscellaneous and minor works | 2027-04-30
Kilmarnock South Battery Storage | PRO-001809 | CS-05402 | Kilmarnock Energy Centre Limited | Kilmarnock South 400kV Substation | SPT-RI-2249 | Kilmarnock South 275kV Fault Level Uprating - To allow the connection of a battery storage connection at Kilmarnock South 400kV substation, the short circuit rating of Kilmarnock South 275kV substation equipment needs to be increased from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2027-04-30
Kilmux Farm | PRO-001195 | CS-09763 | SP Distribution plc | Leven GSP | SPT-RI-3384 | Glenniston to Westfield 132kV Circuit Uprating | 2032-05-31
Kilmux Farm | PRO-001195 | CS-09764 | SP Distribution plc | Leven GSP | SPT-RI-3385 | Glenniston 132kV Substation Works | 2032-05-31
Kilmux Farm | PRO-001195 | CS-09765 | SP Distribution plc | Leven GSP | SPT-RI-3420 | Redhouse toWestfield 132kV Circuit Uprating (AG Route) | 2032-05-31
Kincardine Battery Storage Facility | PRO-000856 | CS-04309 | KINCARDINE GRID 1 LTD | Fife Grid Services Facility 275kV Substation | SPT-RI-1745 | Kincardine to Fife Grid 275kV Switchgear and Cable Works - To facilitate the connection of contracted generation from the Relevant Transmission Licensee’s Fife Grid Services Facility 275kV substation to Kincardine 275kV substation, it is proposed to install a new 275kV busbar and associated 275kV disconnectors and approximately 0.9km of 275kV underground cable circuit to Kincardine 275kV substation. At Kincardine 275kV substation, install a new 275kV GIS switchgear and associated disconnectors and one 275kV line isolator. | 2026-03-31
Kincardine Energy Storage Facility | PRO-001653 | CS-04466 | KINCARDINE GRID 2 LTD | Fife Grid Services Facility 275kV Substation | SPT-RI-1745 | Kincardine to Fife Grid 275kV Switchgear and Cable Works - To facilitate the connection of contracted generation from the Relevant Transmission Licensee’s Fife Grid Services Facility 275kV substation to Kincardine 275kV substation, it is proposed to install a new 275kV busbar and associated 275kV disconnectors and approximately 0.9km of 275kV underground cable circuit to Kincardine 275kV substation. At Kincardine 275kV substation, install a new 275kV GIS switchgear and associated disconnectors and one 275kV line isolator. | 2027-07-30
Kinkell IDNO BESS | PRO-004339 | CS-10099 | Eclipse Power Networks Limited | Kinkell IDNO GSP | Kinkell IDNO Sole Enabling Works OHL | 1. At Lambloch Collector substation, install one 275kV feeder bay with the associated switchgear 2. Between Kinkell and Lambloch collector substation, install approx. 8.7km of 275kV circuit. Min required summer pre-fault rating of 296MVA. 3. At Kinkell substation, install one 275kV single busbar with one 275kV feeder bay (one circuit breaker and two disconnectors) 4. At Kinkell substation, install three 275kV disconnectors | 2031-04-30
Kinkell IDNO BESS | PRO-004339 | CS-10100 | Eclipse Power Networks Limited | Kinkell IDNO GSP | Kinkell IDNO Sole Enabling Works - Substation | 1. At Lambloch Collector substation, install one 275kV feeder bay with the associated switchgear 2. Between Kinkell and Lambloch collector substation, install approx. 8.7km of 275kV circuit. Min required summer pre-fault rating of 296MVA. 3. At Kinkell substation, install one 275kV single busbar with one 275kV feeder bay (one circuit breaker and two disconnectors) 4. At Kinkell substation, install three 275kV disconnectors | 2031-04-30
Kinkell IDNO BESS | PRO-004339 | CS-10101 | Eclipse Power Networks Limited | Kinkell IDNO GSP | Kinkell IDNO Sole Enabling Works - Cable | 1. At Lambloch Collector substation, install one 275kV feeder bay with the associated switchgear 2. Between Kinkell and Lambloch collector substation, install approx. 8.7km of 275kV circuit. Min required summer pre-fault rating of 296MVA. 3. At Kinkell substation, install one 275kV single busbar with one 275kV feeder bay (one circuit breaker and two disconnectors) 4. At Kinkell substation, install three 275kV disconnectors | 2031-04-30
Kinkell IDNO BESS | PRO-004339 | CS-10102 | Eclipse Power Networks Limited | Kinkell IDNO GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-04-30
Kinkell IDNO BESS | PRO-004339 | CS-10103 | Eclipse Power Networks Limited | Kinkell IDNO GSP | SPT-RI-3720 - Cable |  | 2031-04-30
Kinkell IDNO BESS | PRO-004339 | CS-10104 | Eclipse Power Networks Limited | Kinkell IDNO GSP | SPT-RI-3720 - SS |  | 2031-04-30
KINKHALL266MW BESS BEGA (Kinkell) | PRO-004268 | CS-10105 | CARE POWER (KINKHALL) LIMITED | Kinkell IDNO GSP | Kinkell IDNO Sole Enabling Works - Cable | 1. At Lambloch Collector substation, install one 275kV feeder bay with the associated switchgear 2. Between Kinkell and Lambloch collector substation, install approx. 8.7km of 275kV circuit. Min required summer pre-fault rating of 296MVA. 3. At Kinkell substation, install one 275kV single busbar with one 275kV feeder bay (one circuit breaker and two disconnectors) 4. At Kinkell substation, install three 275kV disconnectors | 2031-04-30
KINKHALL266MW BESS BEGA (Kinkell) | PRO-004268 | CS-10106 | CARE POWER (KINKHALL) LIMITED | Kinkell IDNO GSP | Kinkell IDNO Sole Enabling Works - Substation | 1. At Lambloch Collector substation, install one 275kV feeder bay with the associated switchgear 2. Between Kinkell and Lambloch collector substation, install approx. 8.7km of 275kV circuit. Min required summer pre-fault rating of 296MVA. 3. At Kinkell substation, install one 275kV single busbar with one 275kV feeder bay (one circuit breaker and two disconnectors) 4. At Kinkell substation, install three 275kV disconnectors | 2031-04-30
KINKHALL266MW BESS BEGA (Kinkell) | PRO-004268 | CS-10107 | CARE POWER (KINKHALL) LIMITED | Kinkell IDNO GSP | Kinkell IDNO Sole Enabling Works OHL | 1. At Lambloch Collector substation, install one 275kV feeder bay with the associated switchgear 2. Between Kinkell and Lambloch collector substation, install approx. 8.7km of 275kV circuit. Min required summer pre-fault rating of 296MVA. 3. At Kinkell substation, install one 275kV single busbar with one 275kV feeder bay (one circuit breaker and two disconnectors) 4. At Kinkell substation, install three 275kV disconnectors | 2031-04-30
KINKHALL266MW BESS BEGA (Kinkell) | PRO-004268 | CS-10108 | CARE POWER (KINKHALL) LIMITED | Kinkell IDNO GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-04-30
KINKHALL266MW BESS BEGA (Kinkell) | PRO-004268 | CS-10109 | CARE POWER (KINKHALL) LIMITED | Kinkell IDNO GSP | SPT-RI-3720 - Cable |  | 2031-04-30
KINKHALL266MW BESS BEGA (Kinkell) | PRO-004268 | CS-10110 | CARE POWER (KINKHALL) LIMITED | Kinkell IDNO GSP | SPT-RI-3720 - SS |  | 2031-04-30
Kinmuck PV and BESS Station | PRO-001700 | CS-04336 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | Kinmuck PV & BESS H1 Works | Installation of 2 x 275kV disconnectors at the User’s site, on the Network side of the circuit breaker. | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04337 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04338 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04339 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04340 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-025d | North East Reinforcement | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04341 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04342 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04343 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2027-05-31
Kinmuck PV and BESS Station | PRO-001700 | CS-04344 | KINMUCK ENERGY STORAGE LIMITED | New Persley Tee 132kV | SHET-RI-155 | Peterhead – Persley Tee 275kV Line Works – Overhead line works to bring the VP 275kV overhead line circuit to ground, including any required tower modifications. Design and installation of one 275kV bus bar including a circuit breaker with four 275kV disconnectors and associated protection and control equipment. | 2027-05-31
Kinnordy Estate Solar -Wind - Battery | PRO-004986 | CS-11797 | BSR APPLICATIONS LIMITED | Lunanhead 2 GSP | SHET-RI-315 |  | 2032-10-31
Kintore BESS | PRO-002518 | CS-09804 | Conrad Energy (Developments) II Limited | Kintore 2 GSP | SHET-RI-245 | Kintore – Craigiebuckler/Tarland Tee Point Upgrade – Kintore to Craigiebuckler-Tarland Tee Point Overhead line 132kV Upgrade | 2031-10-31
Kintore BESS | PRO-002518 | CS-09805 | Conrad Energy (Developments) II Limited | Kintore 2 GSP | Kintore BESS | 1. Installation of an intertrip scheme based on unavailability, due to planned or unplanned outage conditions, of either of the Kintore to Craigiebuckler 132kV XCN/XCS circuits to prevent an overload on the local 132kV network. 2. A loss of mains scheme will be configured at Kintore GSP as requested by the host Distribution Network Operator. 3. Installation of a new 132kV double busbar switch bay at Kintore 132kV substation. The switch bay will include 2x 132kV busbar selection switches, 1x 132kV circuit breaker and 1x 132kV line disconnector. 4. Installation of a 120MVA 132/33kV grid transformer, a 33kV metering circuit breaker and a 33kV disconnector on a suitable level platform at the new Kintore 2 132/33kV GSP substation compound. | 2031-10-31
Kintore Electrolysis | PRO-002094 | CS-11570 | KINTORE HYDROGEN LIMITED | Kintore GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2035-10-31
Kintore Electrolysis | PRO-002094 | CS-11571 | KINTORE HYDROGEN LIMITED | Kintore GSP | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2035-10-31
Kintore Electrolysis | PRO-002094 | CS-11572 | KINTORE HYDROGEN LIMITED | Kintore GSP | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 2035-10-31
Kintore Electrolysis | PRO-002094 | CS-11573 | KINTORE HYDROGEN LIMITED | Kintore GSP | SHET-RI-241 Peterhead - Persley - Kintore 400kV Reinforcement |  | 2035-10-31
Kintore Electrolysis | PRO-002094 | CS-11574 | KINTORE HYDROGEN LIMITED | Kintore GSP | SHET-RI-282 |  | 2035-10-31
Kintore Electrolysis | PRO-002094 | CS-11575 | KINTORE HYDROGEN LIMITED | Kintore GSP |  |  | 2035-10-31
Kirkan Wind Farm | PRO-004401 | CS-12062 | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation | Kirkan Enabling Works | 1. Installation of a 132 kV bay at the new Corriemoillie 2 275/132kV Substation (to be delivered under SHET-RI-272) consisting of a 132 kV circuit breaker 405, 132kV double busbar selector switches 404 and 406 and a 132kV line disconnector 403. 2. Installation of associated protection and control equipment to be housed in a control building established under SHET-RI-272. 3. Construction of a 132kV line from Corriemoillie 2 275/132kV substation to Kirkan Wind Farm 132kV Substation consisting of 5 km single 132kV steel Trident overhead line. 4. Installation of a 132 kV feeder disconnector 103 at the User’s site. | 2033-10-31
Kirkan Wind Farm | PRO-004401 | CS-12063 | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2033-10-31
Kirkan Wind Farm | PRO-004401 | CS-12064 | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2033-10-31
Kirkan Wind Farm | PRO-004401 | CS-12065 | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
Kirkan Wind Farm | PRO-004401 | CS-12066 | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2033-10-31
Kirkan Wind Farm | PRO-004401 | CS-12067 | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation | shet-ri-272 - 275/132kV Corriemoillie 2 Substation |  | 2033-10-31
Kirkby | PRO-001084 | CS-04482 | KIRKBY BATTERY STORAGE LTD | Kirkby 275kV Substation | 100506-201132 | 1. Install a tertiary cable box or bushings on SGT1A 2. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2025-09-30
Kirkby (Tertiary) | PRO-001083 | CS-05214 | PIVOTED POWER LLP | Kirkby 275/33kV Substation | 100763-201870 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install Disconnecting Circuit Breaker (DCB) at the 13kV side connecting tertiary to connection assets for Users connection. | 2027-08-30
Kirkby (Tertiary) | PRO-001083 | CS-10893 | PIVOTED POWER LLP | Kirkby 275/33kV Substation | 100763-200777 |  | 2027-08-30
Kirkby (Tertiary) | PRO-001083 | CS-10894 | PIVOTED POWER LLP | Kirkby 275/33kV Substation | 103992-207878 |  | 2027-08-30
Kirkby (Tertiary) | PRO-001083 | CS-10895 | PIVOTED POWER LLP | Kirkby 275/33kV Substation | 103992-207879 |  | 2027-08-30
Kirkton Solar PV | PRO-001262 | CS-05870 | EEB 19 LIMITED | Peterhead Grange 132kV | Kirkton enabling works item 1 | At Peterhead Grange 132/33kV GSP remove the 2 existing 45 mva transformers and install 2 new 90 mva transformers and ancillary equipment. The transformers will be enclosed within new acoustic enclosures. The works will include metering, protection and control equipment. The Transfromers will be installed within the existing substation location and cabled to the existing 33 kV switchboard | 2024-03-31
Kirkton Wind Farm | PRO-001811 | CS-11899 | Kirkton Wind Farm Ltd | Connagill 275kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2028-10-31
Kirkton Wind Farm | PRO-001811 | CS-11900 | Kirkton Wind Farm Ltd | Connagill 275kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2028-10-31
Kirkton Wind Farm | PRO-001811 | CS-11901 | Kirkton Wind Farm Ltd | Connagill 275kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 2028-10-31
Kirkton Wind Farm | PRO-001811 | CS-11902 | Kirkton Wind Farm Ltd | Connagill 275kV Substation | SHET-RI-191 | Strathy Switching Collector Station 132kV - Install 12km approximately of new 275kV double circuit overhead line between Connagill 275/132kV substation and a new 132kV switching collector station at Strathy North Wind Farm substation. The OHL double circuit will be built on steel lattice towers. This reinforcement is dependent upon TORI-106b Connagill 2nd SGT, looking at installing a new 480MVA transformer at Connagill substation (SGT1). If the works of this TORI are progressed, TORI-168 need to be cancelled and the offers issued to the following wind farms need to be amended as follows: -Armadale and Strathy South wind farms to update the TCA, One-off works and sole use works. -Kirkton wind farm to update the TCA and sole use works as per the new network design and double check the protection system configuration if additional devices are needed.(SHET-RI-191) | 2028-10-31
Kirkton Wind Farm | PRO-001811 | CS-11903 | Kirkton Wind Farm Ltd | Connagill 275kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2028-10-31
Knaresborough GSP (NE) | PRO-002962 | CS-12094 | NORTHERN POWERGRID (NORTHEAST) PLC | Knaresborough GSP | 101740-203455 Lingerfield |  | 2039-10-30
Knarie | PRO-004048 | CS-09944 | Invenergy Development UK Ltd | Narie 400/132kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Knarie | PRO-004048 | CS-09945 | Invenergy Development UK Ltd | Narie 400/132kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Knockcronal Wind Farm | PRO-001801 | CS-07029 | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation | Knockcronal Wind Farm | 1. At Carrick collector substation, installation of one 275kV line isolator connecting onto the Carrick 275kV busbar. Provision of communications, alarms, indications and metering from the User site | 2029-10-30
Knockcronal Wind Farm | PRO-001801 | CS-07030 | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-10-30
Knockcronal Wind Farm | PRO-001801 | CS-07031 | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation | SPT-RI-293 | Carrick 275kV Substation - A new 275kV substation will be installed on the Coylton-Mark Hill 275kV circuit (YY route) approximately 25km northeast of Mark Hill substation. The YY route will be turned in to the new substation with a 275kV circuit breaker on each circuit. The new circuit breakers will maintain the single-phase high-speed auto reclose capability which currently exists on the YY route. (SPT-RI-293) | 2029-10-30
Knockkippen Energy Park | PRO-001826 | CS-05440 | KNOCKKIPPEN WIND ENERGY LIMITED | Ayr GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2028-08-30
Knockodhar Wind Farm | PRO-000483 | CS-05871 | REG KNOCKODHAR LIMITED | Knockodhar Wind Farm 132kV Substation | Knockodhar Enabling Works items 1-4 | 1. At Mark Hill substation install a new 132kV switch bay and associated equipment and apparatus. 2. Installation of a 132kV cable system from Mark Hill 132kV substation to an appropriate location where the 132kV wood pole overhead line will be constructed. 3. Installation of approximately 3km of 132kV wood pole overhead line between Mark Hill and Knockodhar 132kV Substation. 4. At Knockodhar Substation, one 132kV line isolator will be installed. 9. Provision of a Control Scheme to manage the network in South West Scotland. Detailed information shall be provided by The Company in the detailed design phase. | 2028-04-30
Knockodhar Wind Farm | PRO-000483 | CS-06252 | REG KNOCKODHAR LIMITED | Knockodhar Wind Farm 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2028-04-30
Knockodhar Wind Farm | PRO-000483 | CS-06253 | REG KNOCKODHAR LIMITED | Knockodhar Wind Farm 132kV Substation | SPT-RI-282 | Markhill SGT4 | 2028-04-30
Knockodhar Wind Farm | PRO-000483 | CS-06254 | REG KNOCKODHAR LIMITED | Knockodhar Wind Farm 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2028-04-30
Knockton Wind Farm | PRO-003524 | CS-09920 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-237 | Coupar Angus - Clunie 132kV Works - Establish a new 132kV single busbar nearby to the Coupar Angus area. The proposed location for this busbar compound will be next to or underneath the crossing point of the 132kV CCN/CCS circuits and the 275kV YZ1/YZ2 circuits (YZ1/YZ2 proposed to switch to 400kV under SHET-RI-093). For this new 132kV single busbar, 4x new 132kV bays will be required to connect the existing 132kV CCN/CCS circuits as seen from the SLD. A bus section has also been proposed on the busbar. | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09921 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09922 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09923 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09924 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09925 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09926 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09927 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09928 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09929 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09930 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09931 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09932 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09933 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09934 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09935 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SHET-RI-269 |  | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09936 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Knockton Wind Farm | PRO-003524 | CS-09937 | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Kulizumboo Interconnector | PRO-001290 | CS-05872 | KULIZUMBOO LIMITED | Canterbury 400kV GIS Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 2031-04-01
Kulizumboo Interconnector | PRO-001290 | CS-05873 | KULIZUMBOO LIMITED | Canterbury 400kV GIS Substation | 100250-200637 | Provision of 1 bay for Kulizumboo interconnector at Canterbury 400 kV GIS Substation. Extension of Sellindge 400 kV OTS to Kulizumboo connection. | 2031-04-01
Kulizumboo Interconnector | PRO-001290 | CS-05874 | KULIZUMBOO LIMITED | Canterbury 400kV GIS Substation | 020865-020865 | Kemsley to Longfield Tee 400 kV circuit - Reconductor to achieve a 2800MVA post-fault rating. Littlebrook to Longfield Tee 400 kV circuit - Reconductor to achieve a 2800MVA post-fault rating. | 2031-04-01
Kulizumboo Interconnector | PRO-001290 | CS-05875 | KULIZUMBOO LIMITED | Canterbury 400kV GIS Substation | 031339-031339 | South Coast STATCOMS and MSCs. | 2031-04-01
KX Alpha 1 Iron Acton | PRO-003647 | CS-10034 | KXP ALPHA I LIMITED | Severn Connection Node A 400kv Substation | 102179-204389 (KXP) |  | 2037-10-31
KX Alpha 1 Iron Acton | PRO-003647 | CS-10035 | KXP ALPHA I LIMITED | Severn Connection Node A 400kv Substation | 102179-204390 (KXP) |  | 2037-10-31
KX Alpha 1 Iron Acton | PRO-003647 | CS-10036 | KXP ALPHA I LIMITED | Severn Connection Node A 400kv Substation | 103391-206851 |  | 2037-10-31
KXP Alpha 1 Little Horsted | PRO-003776 | CS-10047 | KXP ALPHA I LIMITED | Sussex and Romney Connection Node A 400kV Substation | 103267-206709 | - Replacement, or modification, of existing towers and associated OHL works to facilitate a double turn-in connection into Sussex & Romney Connection Node A via the Bolney – Little Horsted circuit 1 & 2 overhead line circuits (current exiting Bolney – Ninfield circuits 1 & 2) - Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure | 2037-10-31
KXP Alpha 1 Little Horsted | PRO-003776 | CS-10048 | KXP ALPHA I LIMITED | Sussex and Romney Connection Node A 400kV Substation | 103271-206713 |  | 2037-10-31
KXP Alpha 2 Little Horsted | PRO-003777 | CS-10045 | KXP ALPHA II LIMITED | Sussex and Romney Connection Node A 400kV Substation | 103267-206709 | - Replacement, or modification, of existing towers and associated OHL works to facilitate a double turn-in connection into Sussex & Romney Connection Node A via the Bolney – Little Horsted circuit 1 & 2 overhead line circuits (current exiting Bolney – Ninfield circuits 1 & 2) - Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure | 2037-10-31
KXP Alpha 2 Little Horsted | PRO-003777 | CS-10046 | KXP ALPHA II LIMITED | Sussex and Romney Connection Node A 400kV Substation | 103272-206714 |  | 2037-10-31
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10203 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2037-10-30
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10204 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-2876 | 3. West Coast Onshore Reinforcement (North Section) - This TORI shall construct a new Killoch 400kV substation to feed a new Killoch 275kV substation via three new 400/275kV SGT’s, diversion and 400kV uprating of the existing XY route between Kilmarnock South and the new Killoch 400kV substations and the 400kV uprating of the WA route between the new Killoch 400kV and New Cumnock North 400kV substations. | 2037-10-30
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10205 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-3176 - Kilmarnock South to West Coast HVDC Bussing Station | Install a 2GW HVDC link from Kilmarnock South 400kV substation to the South Ayrshire 525kV HVDC bussing station located in southwest Scotland. The DC bussing station to facilitate a multi terminal HVDC arrangement between Kilmarnock South, Machair Wind and a southern converter station located in NGET. | 2037-10-30
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10206 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-3177 - SS Kilmarnock South AIS to GIS Reconfiguration |  | 2037-10-30
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10207 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-3178 - West Coast HVDC Bussing Station to NGET | Install a 4GW HVDC link from the South Ayrshire 525kV HVDC bussing station to a southern converter station within the NGET licensed area. The costs associated with this SPT reinforcement instruction are associated with the installation of the HVDC cable system from the DC bussing station to the Scotland-England maritime boundary. | 2037-10-30
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10208 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-3473 Hunterston – Kilmarnock South 400kV Reinforcement |  | 2037-10-30
KXP ALPHA 3 AYR BESS | PRO-003672 | CS-10209 | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation | SPT-RI-3474 - Kilmarnock South - Strathaven 400kV Reinforcement | It is proposed to re-conductor the 400kV corridor (XV route) from Kilmarnock South 400kV to Strathaven 400kV substations (approx. 35.0km). It is proposed to establish new HTLS conductors (Twin Curlew 525mm² ACCR at 210ºC) along XV route to achieve a Pre-Fault Summer continuous rating of 2690MVA. | 2037-10-30
L48 BESS Glen App | PRO-003058 | CS-09432 | Lower 48 Energy BESS Limited | L48 BESS Glen App | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2028-10-31
Lackenby GSP (NE) | PRO-004039 | CS-12356 | NORTHERN POWERGRID (NORTHEAST) PLC | Lackenby 275kV Substation | 104144-208074 |  | 2039-10-30
Lackenby GSP (NE) | PRO-004039 | CS-12357 | NORTHERN POWERGRID (NORTHEAST) PLC | Lackenby 275kV Substation | 104145-208076 |  | 2039-10-30
Lackenby GSP (NE) | PRO-004039 | CS-12358 | NORTHERN POWERGRID (NORTHEAST) PLC | Lackenby 275kV Substation | 104589-209122 |  | 2039-10-30
Ladyfield Renewable Energy Park | PRO-002002 | CS-10118 | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV | SHET-RI-013 and SPT-RI-028 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existing Inveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. Reconfigure Dalmally 275kV substation to a double busbar arrangement to allow the extension of the substation to develop new bays for the connection of renewable generation. (SHET-RI-013 and SPT-RI-028) | 2029-10-31
Ladyfield Renewable Energy Park | PRO-002002 | CS-10119 | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2029-10-31
Ladyfield Renewable Energy Park | PRO-002002 | CS-10120 | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2029-10-31
Ladyfield Renewable Energy Park | PRO-002002 | CS-10121 | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2029-10-31
Ladyfield Renewable Energy Park | PRO-002002 | CS-10122 | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2029-10-31
Ladyfield Renewable Energy Park | PRO-002002 | CS-10123 | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV | SHET-RI-159 Creag Dhubh Network Management Scheme |  | 2029-10-31
Lairg II Wind Farm | PRO-001434 | CS-04468 | LAIRG II LLP | Dalchork 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2026-10-31
Lairg II Wind Farm | PRO-001434 | CS-04470 | LAIRG II LLP | Dalchork 132kV Substation | Lairg II H1 Works | Construction of a Tee off connection to the Shin 132kV OHL constructing 1.6km of 132kV trident line to the Lairg II windfarm substation | 2026-10-31
Lairg II Wind Farm | PRO-001434 | CS-06679 | LAIRG II LLP | Dalchork 132kV Substation | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 2026-10-31
Laleham | PRO-001063 | CS-05271 | Juniper Energy Limited | Laleham 132kV Substation | 100770-200764 | 1. Extend the existing Laleham 132kV busbar to accommodate a new GIS generator bay to enable connection of User plant. 2. Substation control modification and busbar protection. | 2028-05-30
Laleham | PRO-001063 | CS-12280 | Juniper Energy Limited | Laleham 132kV Substation | 102890-207798 |  | 2028-05-30
Laleham | PRO-001063 | CS-12281 | Juniper Energy Limited | Laleham 132kV Substation | 102890-207882 (EDF) |  | 2028-05-30
Laleham | PRO-001063 | CS-12282 | Juniper Energy Limited | Laleham 132kV Substation | 102890-207796 (EDF) |  | 2028-05-30
Laleham | PRO-001063 | CS-12283 | Juniper Energy Limited | Laleham 132kV Substation | 102890-207799(EDF) |  | 2028-05-30
Laleham | PRO-001063 | CS-12284 | Juniper Energy Limited | Laleham 132kV Substation | 102890-207887 |  | 2028-05-30
Laleham | PRO-001063 | CS-12305 | Juniper Energy Limited | Laleham 132kV Substation | 102890-209360 |  | 2028-05-30
Laleham GSP (SEPD) | PRO-003089 | CS-11921 | Southern Electric Power Distribution Plc | Laleham GSP (SEPD) | 102890-207796 |  | 2026-10-30
Laleham GSP (SEPD) | PRO-003089 | CS-11922 | Southern Electric Power Distribution Plc | Laleham GSP (SEPD) | 102890-207799 EX(8) |  | 2026-10-30
Laleham GSP (SEPD) | PRO-003089 | CS-11923 | Southern Electric Power Distribution Plc | Laleham GSP (SEPD) | 102890-207803 |  | 2026-10-30
Laleham GSP (SEPD) | PRO-003089 | CS-11924 | Southern Electric Power Distribution Plc | Laleham GSP (SEPD) | 102890-207882 EX(8) |  | 2026-10-30
Laleham GSP (SEPD) | PRO-003089 | CS-11925 | Southern Electric Power Distribution Plc | Laleham GSP (SEPD) | 102890-207883 |  | 2026-10-30
Lan Fawr Energy Park | PRO-001609 | CS-06828 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2028-09-11
Lan Fawr Energy Park | PRO-001609 | CS-06829 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2028-09-11
Lan Fawr Energy Park | PRO-001609 | CS-06830 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2028-09-11
Lan Fawr Energy Park | PRO-001609 | CS-06831 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 2028-09-11
Lan Fawr Energy Park | PRO-001609 | CS-06832 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2028-09-11
Lan Fawr Energy Park | PRO-001609 | CS-06833 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-09-11
Lan Fawr Energy Park | PRO-001609 | CS-06834 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 2028-09-11
Lanarkshire BESS | PRO-002183 | CS-08260 | CARLTON POWER LIMITED | Strathaven 400/275kV | SPT-RI-2537 | Strathaven 400kV Compound Extension | 2027-04-30
Lanarkshire BESS | PRO-002183 | CS-08261 | CARLTON POWER LIMITED | Strathaven 400/275kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2027-04-30
Land at Rothienorman | PRO-002073 | CS-07565 | ROTHIENORMAN ENERGY STORAGE LIMITED | Rothienorman 400/33kV Substation | Intertrip Scheme - Land at Rothienorman | This scheme requires an intertrip for the loss of one of the grid transformers at Rothienorman 400/33kV GSP. These signals will be provided to the Host Distribution Network Operator to trip the User via a separate relay panel within the 33kV Switch room from the signals described below | 2024-10-31
Land at Rothienorman | PRO-002073 | CS-07566 | ROTHIENORMAN ENERGY STORAGE LIMITED | Rothienorman 400/33kV Substation | Protection Settings - LoR | Modification to the existing LV Directional Overcurrent (DOC) protection settings at Rothienorman 400/33kV Substation will also be required | 2024-10-31
Land at Rothienorman | PRO-002073 | CS-07567 | ROTHIENORMAN ENERGY STORAGE LIMITED | Rothienorman 400/33kV Substation | Loss of Mains - LoR | A loss of mains scheme will also be configured at Rothienorman GSP as requested by the host Distribution Network Operator | 2024-10-31
Land at Sir William Smith Road | PRO-003802 | CS-11654 | FPC ELECTRIC LAND LIMITED | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
Land at Sir William Smith Road | PRO-003802 | CS-11655 | FPC ELECTRIC LAND LIMITED | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
Land at Sir William Smith Road | PRO-003802 | CS-11656 | FPC ELECTRIC LAND LIMITED | Arbroath GSP | SHET-RI-234 | Tealing Solar Tee – Tealing 132kV Upgrade – Upgrade the 5.8km of single circuit overhead line between the Tealing Solar tee-point and Tealing 132kV substation. The circuit requires a minimum continuous summer rating of 170MVA | 2032-10-31
Land at Sir William Smith Road | PRO-003802 | CS-11657 | FPC ELECTRIC LAND LIMITED | Arbroath GSP | SHET-RI-284 |  | 2032-10-31
Land at Sir William Smith Road | PRO-003802 | CS-11658 | FPC ELECTRIC LAND LIMITED | Arbroath GSP | SHET-RI-289 |  | 2032-10-31
Landulph | PRO-001131 | CS-05272 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-100278-200771 (Infra) | 1. Install earthing transformer on 13 kV tertiary connection 2. Install 13kV disconnector connecting tertiary to connection assets for Users connection 3. Works required to connect the User to the South West Operational Tripping Scheme (OTS), as described in Appendix F3 | 2026-05-18
Landulph | PRO-001131 | CS-05273 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-RI-33539 | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating. | 2026-05-18
Landulph | PRO-001131 | CS-05274 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-31671-2 | 2. Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | 2026-05-18
Landulph | PRO-001131 | CS-05275 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-31671-I | 3. Re-conductor the Bramley - Fleet OHL circuits to increase capacity | 2026-05-18
Landulph | PRO-001131 | CS-05276 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-30752 | 4. Creation of a new South West Operational Tripping Scheme (OTS) at Taunton | 2026-05-18
Landulph | PRO-001131 | CS-12611 | PIVOTED POWER LLP | Landulph 400kV Substation | 100760-202343 (exp) |  | 2026-05-18
Lanehurst Farm BESS | PRO-005083 | CS-12325 | ELGIN ENERGY ES CO LIMITED | Bolney GSP | 104433-208552 |  | 2037-10-31
Langbank Solar and BESS | PRO-003569 | CS-12349 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 2027-10-29
Langbank Solar and BESS | PRO-003569 | CS-12350 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-2268 Cable |  | 2027-10-29
Langbank Solar and BESS | PRO-003569 | CS-12351 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-2268 OHL |  | 2027-10-29
Langbank Solar and BESS | PRO-003569 | CS-12352 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-3285 - Devol Moor-Erskine-Braehead Park 132kV LMS -BZ Route Upgrade |  | 2027-10-29
Langbank Solar and BESS | PRO-003569 | CS-12353 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-3788 | 3. Neilston 132kV Uprate to 25kA fault rating | 2027-10-29
Langbank Solar and BESS | PRO-003569 | CS-12354 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2027-10-29
Langbank Solar and BESS | PRO-003569 | CS-12355 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-3263 | Erskine 132kV Bus Section Circuit Breaker | 2027-10-29
Langlands Business Park | PRO-003476 | CS-09535 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2027-10-30
Langlands Business Park | PRO-003476 | CS-09536 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2027-10-30
Langlands Business Park | PRO-003476 | CS-09537 | SP Distribution plc | East Kilbride South 275/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2027-10-30
Lapwing Fen II | PRO-001995 | CS-07458 | Eclipse Power Networks Limited | Lapwing Fen II (Walpole) IDNO Substation | 100075 - 200225 | 1. Extension of the Gas Insulated Switchgear (GIS) busbars at Walpole 132kV substation. 2. Provision for sufficient space within the GIS hall to allow the User to install a feeder bay at Walpole 132kV substation 3.Substation Control System database changes and the Relevant Transmission Licensee’s operations commissioning resource. | 2029-10-30
Lapwing Fen II | PRO-001995 | CS-12000 | Eclipse Power Networks Limited | Lapwing Fen II (Walpole) IDNO Substation | 103926-207790 |  | 2029-10-30
Larbrax Wind Farm | PRO-000781 | CS-09744 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-3223 | BT Route No.2 Circuit 132kV Uprating | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09745 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-2885 | BT Route 132kV Uprating | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09746 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-3303 | Tee into Newton Stewart-Glenluce 1(2) 132kV Circuits | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09747 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09748 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09749 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09750 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 2029-11-02
Larbrax Wind Farm | PRO-000781 | CS-09751 | SP Distribution plc | Glenluce 132/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-11-02
Lawmoor Energy Storage Glasgow | PRO-004715 | CS-10961 | LAWMOOR DEVELOPMENTS ENERGY STORAGE LIMITED | St. Andrews Cross GSP | No Attributable Works. |  | 2027-07-23
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12641 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 102733-205522 - Lea Marston (EM) |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12643 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 102733-205523 - Lea Marston (EM) |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12646 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 103174-206594 (Lea Marston (EM) |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12647 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 103262-206704 - Lea Marston (EM) |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12649 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 103263-206705 - Lea Marston |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12650 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 103266-206708 lea marston |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12651 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 103804-207487 lea Marston |  | 2037-10-30
Lea Marston GSP (NGED EM) | PRO-001477 | CS-12652 | National Grid Electricity Distribution (East Midlands) plc | Lea Marston (East Midlands) GSP | 103804-207488 lea Marston |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12046 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 102867-206032 |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12629 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 102733-205522 1 |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12630 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 102733-205523 1 |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12631 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 103174-206594 l |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12632 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 103262-206704 l |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12633 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 103263-206705 l |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12634 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 103266-206708 1 |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12635 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 103804-207487 l |  | 2037-10-30
Lea Marston GSP (NGED WM) | PRO-002922 | CS-12636 | National Grid Electricity Distribution (West Midlands) Plc | Warwickshire Connection Node F 400kV Substation | 103804-207488 |  | 2037-10-30
Learielaw Energy Storage | PRO-002531 | CS-08587 | Learielaw Energy Storage Limited | Learlielaw Energy Storage 132kV Substation | SPT-RI-2711 | AP Route 132kV Uprating - The connected and contracted generation at Broxburn GSP has reached a level that will exceed the intact capacity of the existing 132kV OHL AP Route (BROX?CURR) on the No.1 Circuit. It is proposed to reconductor the No.1 Circuit on the AP Route with LARK conductor which will operate at 190°C. The increased rating will provide 191MVA to provide a higher rating to remove the overload under an intact system. Furthermore, the No.1 Circuit of the 132kV cable section entry into Currie 132kV substation will also need replaced to achieve 191MVA loading on this circuit. It is proposed to replace the No.1 Circuit with a single 1600mm AL cable. Additionally, the cost of replacing the existing cable section (130MVA rated) before the end of life will be recovered through TNUoS. | 2028-10-31
Legacy Green Energy Centre | PRO-001662 | CS-04487 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101327-202647 | Works to allow User to connect their generator bay at Legacy 400kV substation. Works to allow User to connect their generator bay at Legacy 400kV substation. | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06844 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06845 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06846 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06847 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06848 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06849 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-06850 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-12025 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 102117-204315 (1) |  | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-12026 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 102119-204317 1 |  | 2027-10-30
Legacy Green Energy Centre | PRO-001662 | CS-12027 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 102118-204316 |  | 2027-10-30
Legacy Tertiary Connection | PRO-001171 | CS-06851 | HD639LEG LIMITED | Legacy 400kV Substation | 100646-201324 | 1. Install a tertiary cable box or bushings on SGT4 2. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2024-08-31
Leithenwater Wind Farm | PRO-001914 | CS-07649 | LEITHENWATER WIND ENERGY HUB LIMITED | Galashiels 132/33kV | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2030-04-02
Leithenwater Wind Farm | PRO-001914 | CS-07650 | LEITHENWATER WIND ENERGY HUB LIMITED | Galashiels 132/33kV | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 2030-04-02
Lessnessock Energy Park | PRO-005033 | CS-12128 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-2876 | 3. West Coast Onshore Reinforcement (North Section) - This TORI shall construct a new Killoch 400kV substation to feed a new Killoch 275kV substation via three new 400/275kV SGT’s, diversion and 400kV uprating of the existing XY route between Kilmarnock South and the new Killoch 400kV substations and the 400kV uprating of the WA route between the new Killoch 400kV and New Cumnock North 400kV substations. | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12129 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3178 - West Coast HVDC Bussing Station to NGET | Install a 4GW HVDC link from the South Ayrshire 525kV HVDC bussing station to a southern converter station within the NGET licensed area. The costs associated with this SPT reinforcement instruction are associated with the installation of the HVDC cable system from the DC bussing station to the Scotland-England maritime boundary. | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12130 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3177 - SS Kilmarnock South AIS to GIS Reconfiguration |  | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12131 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3178 - West Coast HVDC Bussing Station to NGET | Install a 4GW HVDC link from the South Ayrshire 525kV HVDC bussing station to a southern converter station within the NGET licensed area. The costs associated with this SPT reinforcement instruction are associated with the installation of the HVDC cable system from the DC bussing station to the Scotland-England maritime boundary. | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12132 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3473 Hunterston – Kilmarnock South 400kV Reinforcement |  | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12133 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3474 |  | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12134 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3566 | 1. Killoch 275kV Substation - Establish a new 275kV GIS double busbar system in the vicinity of Killoch 400kV (to be established under SPT-RI-2876) that includes the following: • 1 x 275kV bus coupler • 1 x 275kV bus section • 3 x 275kV feeder bays for connecting to the LV side of the Killoch 400/275kV SGTs • 2 x 275kV feeder bays to connect to Coylton 275kV • Allow space for future connections | 2037-10-30
Lessnessock Energy Park | PRO-005033 | CS-12135 | RENEWCO POWER LIMITED | Lessnessock | SPT-RI-3567 | 2. Killoch 400/275kV SGT Load Management Scheme - It is proposed to install a LMS at Killoch 275kV to continually monitor the loading of the established SGT1, SGT2 and SGT3. In order to prevent unacceptable overloading of any primary transmission equipment, a trip signal shall be issued to applicable generators as required when sites are in export mode, import mode or both import and export mode of operation. | 2037-10-30
Letham Farm BESS | PRO-003116 | CS-10057 | BIG BATTERY (LETHAM FARM) LIMITED | Giffnock 275/33kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2027-07-30
Letham Farm BESS | PRO-003116 | CS-10058 | BIG BATTERY (LETHAM FARM) LIMITED | Giffnock 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2027-07-30
Lethans Wind Farm | PRO-001367 | CS-05876 | Lethans Wind Farm Limited | Lethans Collector Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2027-06-30
Lethans Wind Farm | PRO-001367 | CS-05877 | Lethans Wind Farm Limited | Lethans Collector Substation | Lethans WF Enabling Works | 1) Lethans 132kV substation install 132kV line isolator 2) Install c. 3km of cable from Lethans to Glenmucklock Substation 3) at Glenmuckloch substation install 132kV feeder bay 4) Kilmarnock South 400kV and 275kV uprating 5) New Cumnock 275kV Transformers Uprating 6) Glenglass Extension and Glenmuckloch Collector 7) Generation Export Management Scheme (GEMS) 8) Glenglass 132kV Substation | 2027-06-30
Lethans Wind Farm | PRO-001367 | CS-05878 | Lethans Wind Farm Limited | Lethans Collector Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2027-06-30
Lethans Wind Farm | PRO-001367 | CS-05879 | Lethans Wind Farm Limited | Lethans Collector Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2027-06-30
Lethans Wind Farm | PRO-001367 | CS-05880 | Lethans Wind Farm Limited | Lethans Collector Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2027-06-30
Lethans Wind Farm | PRO-001367 | CS-06455 | Lethans Wind Farm Limited | Lethans Collector Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2027-06-30
Lethans Wind Farm Extension | PRO-003553 | CS-08520 | LETHANS EAST WIND FARM LIMITED | Lethans Collector 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2027-10-30
Lethans Wind Farm Extension | PRO-003553 | CS-08521 | LETHANS EAST WIND FARM LIMITED | Lethans Collector 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2027-10-30
Lethans Wind Farm Extension | PRO-003553 | CS-08522 | LETHANS EAST WIND FARM LIMITED | Lethans Collector 132kV Substation | SPT-RI-2792 | Glenmuckloch to Lethans Collector 132kV Circuit | 2027-10-30
Lethans Wind Farm Extension | PRO-003553 | CS-08523 | LETHANS EAST WIND FARM LIMITED | Lethans Collector 132kV Substation | Lethans Extension Wind Farm - enabling works | At Lethans Collector substation install a 132kV line disconnector. | 2027-10-30
Lethen Wind Farm | PRO-002307 | CS-08107 | FRED OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation | SHET-RI-177 | 3. Tomatin Additional SGTs - Install a new 275kV indoor GIS double busbar and two additional 275/132kV Super Grid Transformers at the Tomatin 275/132kV Substation | 2033-12-31
Lethen Wind Farm | PRO-002307 | CS-08108 | FRED OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation | Lethen Wind Farm-132kV GIS Switch BayH1 |  | 2033-12-31
Lethen Wind Farm | PRO-002307 | CS-08109 | FRED OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation | Lethen Wind Farm-132kV AIS Switch BayA1 |  | 2033-12-31
Leven GSP | PRO-003327 | CS-10312 | SP Distribution plc | Leven GSP | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2032-10-31
Leven GSP | PRO-003327 | CS-10313 | SP Distribution plc | Leven GSP | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2032-10-31
Leven GSP | PRO-003327 | CS-10314 | SP Distribution plc | Leven GSP | SPT-RI-3385 | Glenniston 132kV Substation Works | 2032-10-31
Leven GSP | PRO-003327 | CS-10315 | SP Distribution plc | Leven GSP | SPT-RI-3386 | Westfield 132kV ‘B’ GIS Substation Works | 2032-10-31
Leven GSP | PRO-003327 | CS-10316 | SP Distribution plc | Leven GSP | SPT-RI-3420 | Redhouse toWestfield 132kV Circuit Uprating (AG Route) | 2032-10-31
LGB300 | PRO-003907 | CS-09833 | LG-B-300 | LGB300 400KV Substation | SHET-RI-007a | Beauly - Blackhillock 400kV OHL - Establish a new double circuit 400kV overhead line approximately 130km from Beauly to Blackhillock. The new OHL is connected to the Beauly 400kV AIS busbar and the Blackhillock 400kV GIS busbar. | 2031-07-31
LGB300 | PRO-003907 | CS-09834 | LG-B-300 | LGB300 400KV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 2031-07-31
LGB300 | PRO-003907 | CS-09835 | LG-B-300 | LGB300 400KV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2031-07-31
LGB300 | PRO-003907 | CS-09836 | LG-B-300 | LGB300 400KV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2031-07-31
LGB300 | PRO-003907 | CS-09837 | LG-B-300 | LGB300 400KV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2031-07-31
LGB300 | PRO-003907 | CS-09838 | LG-B-300 | LGB300 400KV Substation | SHET-RI-025d | North East Reinforcement | 2031-07-31
LGB300 | PRO-003907 | CS-09839 | LG-B-300 | LGB300 400KV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2031-07-31
LGB300 | PRO-003907 | CS-09840 | LG-B-300 | LGB300 400KV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2031-07-31
LGB300 | PRO-003907 | CS-09841 | LG-B-300 | LGB300 400KV Substation | SHET-RI-134 and SPT-RI-1560 | 9. Beauly – Denny Second Circuit Upgrade from 275kV to 400kV -Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2031-07-31
LGB300 | PRO-003907 | CS-09842 | LG-B-300 | LGB300 400KV Substation | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 2031-07-31
LGB300 | PRO-003907 | CS-09843 | LG-B-300 | LGB300 400KV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2031-07-31
LGB300 | PRO-003907 | CS-09844 | LG-B-300 | LGB300 400KV Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 2031-07-31
LGB300 | PRO-003907 | CS-09845 | LG-B-300 | LGB300 400KV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 2031-07-31
LGB300 | PRO-003907 | CS-09846 | LG-B-300 | LGB300 400KV Substation |  |  | 2031-07-31
Lightsource Middleton | PRO-004817 | CS-10804 | Lightsource Renewable UK Development Limited | Middleton 400KV Substation | 101603-203226 (LSM) |  | 2037-10-30
Lightsource Middleton | PRO-004817 | CS-10805 | Lightsource Renewable UK Development Limited | Middleton 400KV Substation | 102879-206157 (LSM) |  | 2037-10-30
Lightsource Middleton | PRO-004817 | CS-10806 | Lightsource Renewable UK Development Limited | Middleton 400KV Substation | 104039-207941 |  | 2037-10-30
Lightsource Mount Annan BESS | PRO-003034 | CS-09286 | Lightsource Renewable UK Development Limited | Chapelcross 132/33kV | SPT-RI-231 |  | 2031-10-31
Lightsource Mount Annan BESS | PRO-003034 | CS-09287 | Lightsource Renewable UK Development Limited | Chapelcross 132/33kV | SPT-RI-2320 |  | 2031-10-31
Lightsource Mount Annan BESS | PRO-003034 | CS-09288 | Lightsource Renewable UK Development Limited | Chapelcross 132/33kV | 400kV DBB Bay - Mount Annan | Installation of 400kV DBB bay at Wyseby Hill substation, extension to the original compound design may be required | 2031-10-31
Lightsource Mount Annan BESS | PRO-003034 | CS-09289 | Lightsource Renewable UK Development Limited | Chapelcross 132/33kV | Mount Annan - Substation Works | Installation of one 400/132kV 240MVA SGT and one 132kV disconnector | 2031-10-31
Lightsource Mount Annan BESS | PRO-003034 | CS-09290 | Lightsource Renewable UK Development Limited | Chapelcross 132/33kV | Mount Annan - 132kV Disconnector | At Lightsource Mount Annan BESS substation, installation of one 132kV disconnector | 2031-10-31
Lightsourcebp Wakeleys Wind and BESS | PRO-004827 | CS-10822 | Lightsource Renewable UK Development Limited | Derbyshire Connection Node G 400kV | 101884-203860 (3) |  | 2037-10-30
Lightsourcebp Wakeleys Wind and BESS | PRO-004827 | CS-10823 | Lightsource Renewable UK Development Limited | Derbyshire Connection Node G 400kV | 101889-203868 1 |  | 2037-10-30
Lightsourcebp Wakeleys Wind and BESS | PRO-004827 | CS-10824 | Lightsource Renewable UK Development Limited | Derbyshire Connection Node G 400kV | 102643-205312 (I) |  | 2037-10-30
Lightsourcebp Wakeleys Wind and BESS | PRO-004827 | CS-10825 | Lightsource Renewable UK Development Limited | Derbyshire Connection Node G 400kV | 102643-205313 (I) |  | 2037-10-30
Lightsourcebp Wakeleys Wind and BESS | PRO-004827 | CS-10826 | Lightsource Renewable UK Development Limited | Derbyshire Connection Node G 400kV | 103217-206650 |  | 2037-10-30
Lightsourcebp Wakeleys Wind and BESS | PRO-004827 | CS-10827 | Lightsource Renewable UK Development Limited | Derbyshire Connection Node G 400kV | 103976-207857 |  | 2037-10-30
Limekiln | PRO-000515 | CS-03701 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-005 | Extend both the 275kV and 132kV busbars and install a second 275/132kV interbus auto-transformer at Dounreay substation. Upgrade the existing 150MVA interbus auto-transformer at Dounreay to 240MVA. | 2030-12-01
Limekiln | PRO-000515 | CS-05881 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-037 | Fyrish 275/132kV Substation – Establish a new 275kV/132kV Fyrish substation close to the existing Alness 132kV OHL Teed location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. Two new 132kV underground cables will be installed to link the new 275kV/132kV Fyrish substation with the existing Alness GSP. (SHET-RI-037) | 2030-12-01
Limekiln | PRO-000515 | CS-05882 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2030-12-01
Limekiln | PRO-000515 | CS-05883 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2030-12-01
Limekiln | PRO-000515 | CS-05884 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2030-12-01
Limekiln | PRO-000515 | CS-05885 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2030-12-01
Limekiln | PRO-000515 | CS-05886 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 2030-12-01
Limekiln | PRO-000515 | CS-05887 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2030-12-01
Limekiln | PRO-000515 | CS-05888 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-006 | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment. | 2030-12-01
Limekiln | PRO-000515 | CS-05889 | Limekiln Extension Limited | Limekilns 132/33kV substation | Limekilns Item 1 | Construction of a 6km single 132kV circuit from Dounreay 275/132kV substation, comprising 1km 132kV underground cable and 5km of 132kV trident wood pole overhead line (OHL), terminating on an indoor 132kV disconnector (613) installed within the Relevant Transmission Licensee building at Limekiln 132/33kV substation. | 2030-12-01
Limekiln | PRO-000515 | CS-05890 | Limekiln Extension Limited | Limekilns 132/33kV substation | Limekilns Item 2 | The 132kV circuit will be connected to Dounreay 275/132kV substation via a spare 132kV feeder bay, comprising 132kV line disconnector (603), 132kV feeder circuit breaker (605) and 132kV double busbar selector disconnectors (604 and 606). | 2030-12-01
Limekiln | PRO-000515 | CS-05891 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2030-12-01
Limekiln | PRO-000515 | CS-05892 | Limekiln Extension Limited | Limekilns 132/33kV substation | Limekilns Item 3 | The existing protection and telecommunication equipment at Dounreay 275/132 kV substation will be modified for the new connection. | 2030-12-01
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08482 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 102411-204932 | Replace SGT1 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformers and associated circuit breaker with 40kA rms breaker rating. | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08483 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 102411-204933 | Replace SGT2 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformers and associated circuit breaker with 40kA rms breaker rating | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08484 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 102411-204934 | Replace SGT3 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformer and associated circuit breaker with 40kA rms breaker rating. | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08485 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 102411-204935 | Replace SGT4 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformer and associated circuit breaker with 40kA rms breaker rating | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08486 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 102411-204936 | Replacement of CB 250 to have 40kA from existing 20kA | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08487 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08488 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101891-203873 | Uprate the circuit Drakelow 400kV Willington East 400kV to achieve a summer pre-fault rating of 1820MVA | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08489 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08490 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #1 (RATS4-WILE4-1) to summer pre-fault rating 2490 MVA | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08491 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08492 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08493 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101977-204102 | Cable section uprate of the Bishops Wood-Penn 275kV circuit to match the overhead line summer prefault rating of 925MVA | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08494 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101978-204103 | Uprate the Drakelow 400kV -to- Ratcliffe On Soar 400kV circuit #1 (DRAK4-RATS4-1) to summer pre-fault rating 2490MVA | 2033-06-30
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08495 | FPC ELECTRIC LAND LIMITED | Bishops Wood 132kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490 MVA. | 2033-06-30
Lisa's Battery Storage | PRO-003280 | CS-08291 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2030-10-31
Lisa's Battery Storage | PRO-003280 | CS-08292 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2030-10-31
Lisa's Battery Storage | PRO-003280 | CS-08293 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2030-10-31
Lisa's Battery Storage | PRO-003280 | CS-08294 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2030-10-31
Lisa's Battery Storage | PRO-003280 | CS-08295 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2030-10-31
Lister Battery (formerly Lister Drive) | PRO-001088 | CS-05893 | LISTER BATTERY LTD | Lister Drive 275kV Substation | 100787-201590 | Attributable | 2023-10-31
Lister Battery (formerly Lister Drive) | PRO-001088 | CS-05894 | LISTER BATTERY LTD | Lister Drive 275kV Substation | 100787-201589 | Attributable | 2023-10-31
Lister Drive Shaw | PRO-001342 | CS-12050 | Carnegie (BES) Ltd | Lister Drive 275kV Substation | 100859-201716 |  | 2026-09-01
Lister Drive Shaw | PRO-001342 | CS-12051 | Carnegie (BES) Ltd | Lister Drive 275kV Substation | 102191-204411 |  | 2026-09-01
Little Gala Wind Farm | PRO-001478 | CS-06746 | SP Distribution plc | Lesmahagow 132/33kV | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 2027-10-31
Little Gala Wind Farm | PRO-001478 | CS-06747 | SP Distribution plc | Lesmahagow 132/33kV | SPT-TOCO-551 | Lesmahagow GSP - The connection will be provided by installing two new 132kV double busbar feeder bays at Coalburn 132kV. From here two 132kV cable circuits of approximately 4km will be installed to the new Lesmahagow GSP site. At Lesmahagow GSP two new 132kV line disconnectors will be installed along with two 132/33kV 60MVA transformers. The Relevant Transmission Licensee shall install two new 33kV circuit breakers which will form the Point of Connection between the Relevant Transmission Licensee and the User | 2027-10-31
Little Harrowden | PRO-003416 | CS-10267 | Little Harrowden 10 Renewables Limited | West Anglia Connection Node F 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2034-10-31
Little Harrowden | PRO-003416 | CS-10268 | Little Harrowden 10 Renewables Limited | West Anglia Connection Node F 400kV Substation | 101263-202505 | 1. Hotwire 2x620mm² sections of Grendon – Staythorpe circuit to standard operating temperature (170°C) | 2034-10-31
Little Harrowden | PRO-003416 | CS-10269 | Little Harrowden 10 Renewables Limited | West Anglia Connection Node F 400kV Substation | 103048-206464 |  | 2034-10-31
Little Harrowden | PRO-003416 | CS-10270 | Little Harrowden 10 Renewables Limited | West Anglia Connection Node F 400kV Substation | 103148-206568 |  | 2034-10-31
Little Harrowden | PRO-003416 | CS-10271 | Little Harrowden 10 Renewables Limited | West Anglia Connection Node F 400kV Substation | 103153-206573 |  | 2034-10-31
Little Hartfell Wind Farm | PRO-005138 | CS-12217 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-161 | Installation of an Energy Management (Overload Protection) Scheme at Chapelcross 132kV substation. The scheme will issue a signal to SPD and/or SPT to disconnect the appropriate generators if the pre-fault continuous rating of any of the following circuits is exceeded: Chapelcross to Harker 132kV circuit, Chapelcross to Gretna No1 132kV circuit and Chapelcross to Gretna No2 132kV circuit. | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12218 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-168 | Installation of a protection scheme at Gretna 400/132kV substation. The scheme will issue a signal to the Host Distribution Network Operator to disconnect the appropriate generators if either SGT1 or SGT2 is overloaded or if both transformers are out of service (Following planned or unplanned outages). | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12219 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12220 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12221 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-298 Cable |  | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12222 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-298 OHL |  | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12223 | ENERGIEKONTOR UK LTD | Chapelcross GSP | SPT-RI-298 SS |  | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12224 | ENERGIEKONTOR UK LTD | Chapelcross GSP | NGET_RI-101268-202511 | NGET-RI - 101268-202511 - The scope of this project is the rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12225 | ENERGIEKONTOR UK LTD | Chapelcross GSP | NGET-RI-01268-202520 | NGET-RI- 01268-202520 - The scope is the uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12226 | ENERGIEKONTOR UK LTD | Chapelcross GSP | NGET-RI-101074-202154 | NGET-RI- 101074-202154 - CMN3 (NOA) Establish a new 400kV double circuit OHL from Gala North to Carlisle | 2035-07-01
Little Hartfell Wind Farm | PRO-005138 | CS-12227 | ENERGIEKONTOR UK LTD | Chapelcross GSP | NGET-RI-102873-206085 | NGET-RI- 102873-206085 - FSU1 (NOA) – Upgrade Fourstones 275kV network to 400kV and reconductor lines between Harker – Fourstones – Stella West (B37F, B37C and B37E) | 2035-07-01
Little Hill | PRO-001556 | CS-04726 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2026-10-31
Little Hill | PRO-001556 | CS-04727 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2026-10-31
Little Hill | PRO-001556 | CS-06852 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2026-10-31
Little Hill | PRO-001556 | CS-06853 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 2026-10-31
Little Hill | PRO-001556 | CS-06854 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2026-10-31
Little Hill | PRO-001556 | CS-06855 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 2026-10-31
Little Hill | PRO-001556 | CS-06856 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2026-10-31
Little Horsted | PRO-002214 | CS-08936 | CSE34 LIMITED | Little Horsted GSP | 101993-204127 | 1. Install a tertiary cable box or bushing on the SGT2 2. Install 13kV Cable (if required) from tertiary cable box or bushing to earthing transforer 3. Install an earthing transformer 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 2031-10-31
Little Horsted | PRO-002214 | CS-08937 | CSE34 LIMITED | Little Horsted GSP | 033800-033800 | 1. Installation of new towers, and associated OHL works, for the single circuit turn0in of the Bolney – Ninfield, replacing tower 4VM069 2. The construction of new single-swtich mesh 400kV Little Horsted Substation with one section circuit breaker and associated disconnectors 3. The construction of two new feeder circuit bays including associated circuit breakers and disconnectors 4. Construction of two SGT HV circuit breakers and disconnectors 5. Works required to establish Little Horsted 400/132kV Substation, including the installation of the substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure | 2031-10-31
Little Horsted | PRO-002214 | CS-08938 | CSE34 LIMITED | Little Horsted GSP | 033800-200658 | 1. The installation of two 240MVA 400/132kV Super Grid Transformers (SGTs) including associated HV/LV surge arresters and earth switches 2. The installation of 132kV Switchgear on the LV side of the SGTs. This equipment will include the LV side SGT bay disconnector, circuit breaker and line side / cable side disconnectors 3. The installation of HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practive 1 | 2031-10-31
Little Horsted | PRO-002214 | CS-08939 | CSE34 LIMITED | Little Horsted GSP | 033800-204124 | 1. Works required to allow for the onversion of Little Horsted GSP Substation into a double busbar substion with a double circuit turn of the Bolney – Ninfield 400kV transmission circuit | 2031-10-31
Little Horsted Energy Park | PRO-003624 | CS-10222 | ELEMENTS GREEN DEVELOPMENT LTD | Sussex and Romney Connection Node A 400kV Substation | 103267-206709 | - Replacement, or modification, of existing towers and associated OHL works to facilitate a double turn-in connection into Sussex & Romney Connection Node A via the Bolney – Little Horsted circuit 1 & 2 overhead line circuits (current exiting Bolney – Ninfield circuits 1 & 2) - Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure | 2037-10-31
Little Horsted Energy Park | PRO-003624 | CS-10223 | ELEMENTS GREEN DEVELOPMENT LTD | Sussex and Romney Connection Node A 400kV Substation | 103268-206710 | Extension of the 400kV busbars at Sussex & Romney Connection Node A to accommodate the User’s generator bay | 2037-10-31
Llanwern 3 | PRO-004317 | CS-10940 | FUTURE ENERGY LLANWERN LIMITED | South Wales East Connection Node A 275kV Substation | 103344-206793 |  | 2037-10-30
Llanwern 3 | PRO-004317 | CS-10941 | FUTURE ENERGY LLANWERN LIMITED | South Wales East Connection Node A 275kV Substation | 103416-206876 |  | 2037-10-30
Llanwern Phase 1 | PRO-001124 | CS-06857 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100304-200731 | 1. Extension of 33kV busbar and installation of a disconnector to accommodate 33kV generator bay. | 2028-10-01
Llanwern Phase 1 | PRO-001124 | CS-06858 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100304-201748 | Replace the Quad Boosters 1 and 2 at Whitson for larger units | 2028-10-01
Llanwern Phase 1 | PRO-001124 | CS-06859 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100304-201749 | Replacement of Whitson SGT5 for a larger rated unit | 2028-10-01
Llanwern Phase 2 | PRO-001125 | CS-07021 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100414-200951 | Extension of 33 kV busbars on SGTs 3 and 4 and installation of disconnectors to accommodate 33 kV generator bays. | 2028-10-01
Llanwern Phase 2 | PRO-001125 | CS-07022 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100414-200957 | Extension of existing 33 kV cable sealing end compounds. | 2028-10-01
Llwynygog | PRO-001583 | CS-04715 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2027-02-04
Llwynygog | PRO-001583 | CS-04716 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2027-02-04
Llwynygog | PRO-001583 | CS-04717 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-02-04
Llwynygog | PRO-001583 | CS-04718 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2027-02-04
Llwynygog | PRO-001583 | CS-04719 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2027-02-04
Llŷr Floating Wind | PRO-001981 | CS-12164 | Llŷr Floating Wind Limited | Pembroke 400kV Substation | 101575-203161 (1) |  | 2028-10-31
Llŷr Floating Wind | PRO-001981 | CS-12165 | Llŷr Floating Wind Limited | Pembroke 400kV Substation | 101575-207773 | Facilitate the connection of one new GIS user bay, including busbar protection and SCS update. At Pembroke 400kV substation, extend Main Bar 2 and Reserve Bar 1/2 with GIS for: · Two feeder circuits · One section breaker · One busbar coupler | 2028-10-31
Loanhead Farm BESS | PRO-003822 | CS-10795 | Opdenergy UK 18 Limited | Elgin GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2030-10-31
Loanhead Farm BESS | PRO-003822 | CS-10796 | Opdenergy UK 18 Limited | Elgin GSP | SHET-RI-174 | Upgrade of Keith SGTs- Replace the existing 132/275kV 240MVA SGTs at Keith 132kV Substation with larger 480/360MVA units | 2030-10-31
Loanhead Farm BESS | PRO-003822 | CS-10797 | Opdenergy UK 18 Limited | Elgin GSP | Loanhead Farm BESS H1 132kV Double Switch Bay |  | 2030-10-31
Locarno Works - BESS Development | PRO-002591 | CS-12701 | Torridon Developments Limited | Dudhope GSP | SHET-RI-183 New Dundee 132kV Substation |  | 2027-10-31
Loch Fearna Pumped Storage | PRO-002569 | CS-07736 | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 400/18kV Substation | Loch Fearna Item 1 | The installation of a 132kV feeder bay that would be required at the new Loch Lundie 132kV Substation (Part of TORI, SHET-RI-068) to connect the new banked double circuit from the Loch Fearna Pumped Storage 132/18kV Substation. The Loch Fearna Pumped Storage 132/18kV Substation will be connected to the new Loch Lundie 400/132kV Substation by approximately 25km of 132kV banked double circuit. The 25km circuit will consist of 24.5km OHL with the remaining 0.5km section into Loch Lundie 132kV Substation being underground cable. (At this early stage of the process we acknowledge that there may be challenges in obtaining planning consent for the construction of the 24.5km OHL but we will not be in a position to understand any specific planning requirements in advance of your acceptance of this offer. As per the terms of the offer, any changes to the design that are required in order to comply with any planning requirements, and any associated changes in costs, will be dealt with by way of amendments to the terms of the connection agreement.) | 2032-10-28
Loch Fearna Pumped Storage | PRO-002569 | CS-07737 | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 400/18kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 2032-10-28
Loch Fearna Pumped Storage | PRO-002569 | CS-07738 | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 400/18kV Substation | SHET-RI-068 | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | 2032-10-28
Loch Fearna Pumped Storage | PRO-002569 | CS-07739 | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 400/18kV Substation | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 2032-10-28
Loch Fearna Pumped Storage | PRO-002569 | CS-07740 | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 400/18kV Substation | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2032-10-28
Loch Fearna Pumped Storage | PRO-002569 | CS-07741 | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 400/18kV Substation | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 2032-10-28
Loch Fergus Solar | PRO-003808 | CS-09404 | Loch Fergus Solar Ltd | Ayr 275/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-04-30
Loch Fergus Solar | PRO-003808 | CS-11029 | Loch Fergus Solar Ltd | Ayr 275/33kV Substation | SPT-RI-284 SS |  | 2026-04-30
Loch Kemp PSH | PRO-002285 | CS-08475 | LOCH KEMP STORAGE LIMITED | Loch Kemp 275kV Switching Station | SHET-RI-007a | Beauly - Blackhillock 400kV OHL - Establish a new double circuit 400kV overhead line approximately 130km from Beauly to Blackhillock. The new OHL is connected to the Beauly 400kV AIS busbar and the Blackhillock 400kV GIS busbar. | 2030-10-31
Loch Kemp PSH | PRO-002285 | CS-08476 | LOCH KEMP STORAGE LIMITED | Loch Kemp 275kV Switching Station | SHET-RI-201 | Foyers Substation Extension and Connection to Loch Kemp - Extend the existing Foyers 275kV busbar to include a new 275kV bay to connect the new circuit from the Loch Kemp Pumped Storage 275/18kV Substation. Construct a 275kV busbar with three bays at the Loch Kemp 275kV/18kV Substation. The Loch Kemp Pumped Storage 275/18kV Substation will be connected to the existing Foyers 275kV Substation by approximately 10.5km of single circuit 275kV underground cable. | 2030-10-31
Loch Liath Wind Farm | PRO-001671 | CS-09458 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | Loch Liath Wind Farm H1 | 1. Install a new 132kV double busbar feeder bay with associated 132kV Switchgear at the new Fasnakyle 132kV Substation (Part of TORI, SHET-RI 134b). 2. Construct approximately 10.4km of single circuit 132kV overhead line from the Loch Liath Wind Farm 132kV Substation to Fasnakyle 132kV Substation. This 132kV OHL will connect to a new bay on the Fasnakyle 132kV busbars, via the required 132kV switchgear. 3. Installation of a new 132kV disconnector at the Loch Liath Wind Farm 132kV Substation. | 2035-10-31
Loch Liath Wind Farm | PRO-001671 | CS-09459 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2035-10-31
Loch Liath Wind Farm | PRO-001671 | CS-09460 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | SHET-RI-134b | Fasnakyle Substation 132kV Reinforcement – The existing Fasnakyle Substation is due to be upgraded from 275kV circuit to 400kV, as part of the Beauly-Denny Second Circuit Upgrade (SHET-RI-134). This document provides additional information on the specific changes required at Fasnakyle Substation, as part of this reinforcement. (SHET-RI-134b). | 2035-10-31
Loch Liath Wind Farm | PRO-001671 | CS-09461 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | SHET-RI-212 | Construct a new 400kV overhead line to run from Beauly, via the Fort Augustus 2 400kV substation, to run across the B4 boundary. | 2035-10-31
Loch Luichart Extension II | PRO-000487 | CS-03702 | BLUEBELL WIND FARM LIMITED | Loch Luichart Extension II Substation | SHET-RI-065 | Beauly 132kV Reinforcement – Establish a new 132kV GIS double busbar arrangement at Beauly substation, and connect to the existing 275kV busbar via two 480MVA 275/132kV transformers. The Deanie/Aigas (BDN/BDS) 132kV circuits and the Corriemoillie (BM1/BM2) 132kV double circuit will be removed from the existing 132kV busbar at Beauly, and connected to the new 132kV GIS busbar. The existing 132kV busbar will in part be retained, with connectivity to the 275kV busbar maintained via two of the existing 120MVA 275/132kV transformers. The existing 132kV circuits to Elgin/Keith (BIN/BIS) and Boat of Garten (BR1/BR2) and the 132/33kV GTs will remain connected to this busbar. The third 120MVA SGT will be removed. (SHET-RI-065) | 2024-10-31
Loch Luichart Extension II | PRO-000487 | CS-03703 | BLUEBELL WIND FARM LIMITED | Loch Luichart Extension II Substation | SHET-RI-119 | 2. Corriemoillie Transformer Protection Modification - At the existing Corriemoillie substation, install a 3 ended grid transformer differential protection scheme on GT2 to enable the connection of a second generator at Corriemoillie. | 2024-10-31
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-06339 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | Red John - 275kV AIS bays | Extension of the existing Knocknagael 275kV AIS double busbar to create two new 275kV AIS bays to connect the new circuits from Red John 275kV Switching Station. The removal and subsequent replacement of the existing 275kV bus couplers is required to facilitate the connection. | 2029-04-30
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-06340 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | Red John - 275kV underground cable double circuit | Red John 275kV Switching Station will be connected to the existing Knocknagael 275kV by approximately 9km of double circuit 275kV underground cable. The User has requested an underground cable option instead of an overhead line connection. The additional cost of the underground cable compared to the original overhead line solution would be payable by the User as a One-Off Works cost. | 2029-04-30
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-06341 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | Red John - New 4-bay 275kV GIS double busbar Switching Station | At Red John 275kV Switching Station, a new 4-bay 275kV GIS double busbar Switching Station complete with a bus-section and two bus couplers will be constructed. | 2029-04-30
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-10700 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | SHET-RI-286 | SHET-RI-286 - Knocknagael 275kV Extension | 2029-04-30
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-10701 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | SHET-RI-007a | Beauly - Blackhillock 400kV OHL - Establish a new double circuit 400kV overhead line approximately 130km from Beauly to Blackhillock. The new OHL is connected to the Beauly 400kV AIS busbar and the Blackhillock 400kV GIS busbar. | 2029-04-30
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-10702 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-04-30
Loch na Cathrach Pumped Storage Hydro | PRO-000570 | CS-10703 | STATKRAFT HIGHLANDS PSH LIMITED | Knocknagael 275kV | SHET-RI-235 | Knocknagael 275kV - Reserve bus section circuit breaker – Install a reserve bus section circuit breaker at Knocknagael 275kV substation. | 2029-04-30
Lochaber Farm | PRO-004172 | CS-12010 | ECOCEL ENERGY (STORAGE) LTD | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
Lochaber Farm | PRO-004172 | CS-12011 | ECOCEL ENERGY (STORAGE) LTD | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
Lochaber Farm | PRO-004172 | CS-12012 | ECOCEL ENERGY (STORAGE) LTD | Arbroath GSP | SHET-RI-234 | Tealing Solar Tee – Tealing 132kV Upgrade – Upgrade the 5.8km of single circuit overhead line between the Tealing Solar tee-point and Tealing 132kV substation. The circuit requires a minimum continuous summer rating of 170MVA | 2032-10-31
Lochaber Farm | PRO-004172 | CS-12013 | ECOCEL ENERGY (STORAGE) LTD | Arbroath GSP | SHET-RI-284 |  | 2032-10-31
Lochaber Farm | PRO-004172 | CS-12014 | ECOCEL ENERGY (STORAGE) LTD | Arbroath GSP | SHET-RI-289 |  | 2032-10-31
Lochaber Smelter | PRO-001274 | CS-05895 | SIMEC LOCHABER HYDROPOWER 2 LIMITED | Fort William GSP | SHET-RI-045b | 1. Fort Augustus–Fort William 132kV OHL Upgrade Phase 2 - Reconductor one side of the 132kV double circuit OHL between Fort Augustus and Fort William (FFE). The 132kV circuit OHL (FFE) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Replace the existing 132kV cables on FFE & FFW into Fort Augustus with new 132kV cables rated suitably for the increased capacity of the new OHL conductor. Reinstate the permanent connection of the 132kV Kinlochleven circuit (FV1) to FFE following the completion of FFE reconductoring work. (SHET-RI-045b) | 2019-10-31
Lochaber Smelter | PRO-001274 | CS-05896 | SIMEC LOCHABER HYDROPOWER 2 LIMITED | Fort William GSP | SHET-RI-045a | 3. Fort Augustus–Fort William 132kV OHL Upgrade Phase 1 - Reconductor the 132kV double circuit OHL between Fort Augustus and Fort William (FFW). The 132kV double circuit OHL (FFW) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Transfer the connection of Invergarry power station from FFE circuit of the OHL between Fort Augustus and Fort William to the FFW circuit. Temporarily transfer the connection of the Kinlochleven (FV1) 132kV circuit to FFW for the duration of the FFE reconductoring work. (SHET-RI-045a) | 2019-10-31
Locharber | PRO-004283 | CS-09794 | Lochaber Energy Centre Limited | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
Locharber | PRO-004283 | CS-09795 | Lochaber Energy Centre Limited | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
Locharber | PRO-004283 | CS-09796 | Lochaber Energy Centre Limited | Arbroath GSP | SHET-RI-234 | Tealing Solar Tee – Tealing 132kV Upgrade – Upgrade the 5.8km of single circuit overhead line between the Tealing Solar tee-point and Tealing 132kV substation. The circuit requires a minimum continuous summer rating of 170MVA | 2032-10-31
Locharber | PRO-004283 | CS-09797 | Lochaber Energy Centre Limited | Arbroath GSP | Transformers - Arbroath GSP | Installation of 2 x 120MVA transformers within the existing substation | 2032-10-31
Locharber | PRO-004283 | CS-09798 | Lochaber Energy Centre Limited | Arbroath GSP | Arbroath Extension | The TCA asset installation will require an extension of the existing Arbroath GSP substation, and the new equipment will be installed to meet current Fire Separation Standards | 2032-10-31
Locharmoss Solar & Battery | PRO-003477 | CS-09383 | SP Distribution plc | Dumfries 132/33kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2036-10-30
Locharmoss Solar & Battery | PRO-003477 | CS-09384 | SP Distribution plc | Dumfries 132/33kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2036-10-30
Locharmoss Solar & Battery | PRO-003477 | CS-09385 | SP Distribution plc | Dumfries 132/33kV | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 2036-10-30
Lochend Extension | PRO-004665 | CS-11788 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2034-04-30
Lochend Extension | PRO-004665 | CS-11789 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2034-04-30
Lochend Extension | PRO-004665 | CS-11790 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 2034-04-30
Lochend Extension | PRO-004665 | CS-11791 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-140 - Thurso South 275kV Substation Redevelopment |  | 2034-04-30
Lochend Extension | PRO-004665 | CS-11792 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-153 Spittal 2 275 kV Substation |  | 2034-04-30
Lochend Extension | PRO-004665 | CS-11793 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2034-04-30
Lochend Extension | PRO-004665 | CS-11794 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2034-04-30
Lochend Extension | PRO-004665 | CS-11795 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-200 - Loch Buidhe 400-275kV Substation |  | 2034-04-30
Lochend Extension | PRO-004665 | CS-11796 | CWE Lochend Ltd | Thurso South 132/33kV GSP Substation | SHET-RI-287 - Thurso 2 GSP 275 kV Reinforcement |  | 2034-04-30
Lochluichart Battery Storage | PRO-002288 | CS-08205 | Lochluichart Battery Storage Limited | Grudie Bridge GSP | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 2025-10-31
Lochluichart Battery Storage | PRO-002288 | CS-08206 | Lochluichart Battery Storage Limited | Grudie Bridge GSP | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 2025-10-31
Loganhead Windfarm | PRO-000306 | CS-05897 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05898 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm² Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05899 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | 100442-200991 | Chapelcross – Harker 132kV circuit uprating | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05900 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05901 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05902 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05903 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 2027-10-31
Loganhead Windfarm | PRO-000306 | CS-05904 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | 100406-200937 | Reconductor Harker – Gretna – Hawick circuit. Uprate the V route 132kV overload line circuit (between Tower V075 and Harker 132kV substation) to provide a minimum summer pre-fault continuous rating of 170MVA. | 2027-10-31
Long Stratton BESS | PRO-004850 | CS-11037 | Field Long Stratton Ltd | North Anglia Connection Node A 400kV | 103999-207895 |  | 2034-10-31
Long Stratton BESS | PRO-004850 | CS-11038 | Field Long Stratton Ltd | North Anglia Connection Node A 400kV | 103998-207894 |  | 2034-10-31
Long Stratton BESS | PRO-004850 | CS-11039 | Field Long Stratton Ltd | North Anglia Connection Node A 400kV | 102188-204406 (Long Statton) |  | 2034-10-31
Long Stratton PV & BESS Station | PRO-002297 | CS-08828 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 102188-204406 | Installation of a new AIS double busbar 400kV substation between between Bramford 400kV and Norwich Main 400 kV with associated 4 feeder bays, 1 Coupler Bay, 1 section bay. Provide a Double turn in connection of the new substation to the existing 400 kV OHL circuits between Bramford and Norwich Main Substations. Installation of all Circuit Breakers with a higher nominal rating, X/R derating and Initial peak CB rating breakers. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08829 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 102188-204407 | Extension of 400kV main and reserve busbar of newly built Long Stratton 400kV substation to accommodate the User’s Bay. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08834 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100381-200905 | 1. Extension of the Norwich Main 400kV AIS Substation at Main Busbar (M2) and Reserve Busbar (R2) to accommodate an OFTO bay. 2. Extension of the existing East Anglia operational intertripping scheme to include the connection. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08835 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08836 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08837 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08838 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08839 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08840 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08841 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08843 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08844 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08845 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08846 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08847 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101975-204100 | 1. At Kings Lynn 400kV: Ensure circuit break X130 to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08848 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08849 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 021071-021073 | Loop into the new Kings Lynn B 400kV substation with the near side Norwich-Walpole 400kV circuit to form a Walpole- Kings Lynn B and Kings Lynn - Necton - Norwich Main circuit connection. Construction of a new 2.7km double circuit | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08850 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08851 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08852 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08853 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08854 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08855 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08856 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 102122-204324 | Extend Wymondley 400kV substation main and reserve 2 busbars for the provision of one User bay | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08857 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 101248-204325 | Add a new bus coupler and three new bays at Wymondley 400kV substation to facilitate the turn in of the existing Pelham to Sundon 400kV circuit at Wymondley 400kV substation. | 2031-10-30
Long Stratton PV & BESS Station | PRO-002297 | CS-08858 | EAST PYE SOLAR LIMITED | Long Stratton 400kV | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2031-10-30
Longfield Solar | PRO-001053 | CS-06925 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | NGET - 100504-201083 | Construction of a new 6 bay 400kV substation at Porters Wood, including 4x feeder bays, lx coupler bay and provision for lx Generator Bay (User Works) | 2028-10-31
Longfield Solar | PRO-001053 | CS-06926 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | NGET - 100504-201137 (Opex) | Temporary diversion of the Bramford-Braintree-Bulls Lodge 400kV circuit to facilitate the permanent ORL works | 2028-10-31
Longfield Solar | PRO-001053 | CS-06927 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | NGET —10027- 200606 | OHL reconductoring to uprate the new Porters Wood — Rayleigh Main 400 kV circuit. | 2028-10-31
Longfield Solar | PRO-001053 | CS-06928 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2028-10-31
Longfield Solar | PRO-001053 | CS-11983 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 100504-201083 (longfield) |  | 2028-10-31
Longfield Solar | PRO-001053 | CS-11984 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 100504-206099 (Longfield) |  | 2028-10-31
Longfield Solar | PRO-001053 | CS-11985 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 100504-206100 (Longfield) |  | 2028-10-31
Longfield Solar | PRO-001053 | CS-11986 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 100504-207793 |  | 2028-10-31
Longfield Solar | PRO-001053 | CS-11987 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 101720-203429 (Longfield) |  | 2028-10-31
Longmorn Energy Park | PRO-002727 | CS-09241 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | Longmorn 275kV AIS switch bay - A1 |  | 2031-08-15
Longmorn Energy Park | PRO-002727 | CS-09242 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | Longmorn 275kV Line Isolator H1 | Longmorn 275kV Line Isolator H1 | 2031-08-15
Longmorn Energy Park | PRO-002727 | CS-09243 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2031-08-15
Longmorn Energy Park | PRO-002727 | CS-09244 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | SHET-RI-222 | SHET-RI-222 - Longmorn energypark Substation and OHL works | 2031-08-15
Lorg Wind Farm | PRO-000153 | CS-05905 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-211 | Construct a new 132kV switching station, named Holm Hill, and install a 132kV OHL circuit between the new site and the tee off points to Shepherds Rig and Lorg wind farms. At an appropriate tee-off point on the New Cumnock to Kendoon 132kV circuit, install the new Holm Hill 132kV Switching Station containing one 132kV circuit breaker with two associated disconnectors. Install ~8km of 132kV wood pole overhead line with High Temperature Low Sag (HTLS) EAGLE conductor (190°C, minimum summer pre-fault rating 295MVA) to the tee point between Shepherd’s Rig and Lorg wind farms. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-05906 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-05907 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06402 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-007 | New Cumnock 275/132kV Substation | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06403 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm Part 1 | Installation of one disconnector at Lorg Wind Farm. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06404 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-111 | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06405 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06406 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06407 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-292 | Lorg to Shepherds Rig Tee - Install ~10km of 132kV wood pole overhead line with UPAS conductor (75°C, minimum summer pre-fault rating 176MVA) between Lorg 132kV substation and the proposed Shepherds Rig tee connection. The will form part of the Lorg to Holmhill 132kV overhead line. | 2027-04-07
Lorg Wind Farm | PRO-000153 | CS-06408 | RWE Renewables UK Onshore Wind Limited | Lorg Wind Farm 132/32kV | SPT-RI-1507 | Holm Hill 132kV substation - At an appropriate point next to the DE route establish a 132kV substation (Holmhill 132kV substation) by teeing into the proposed future New Cumnock to Glenlee 132kV circuit. The substation will consist of a 132kV busbar to which wind farm circuits will connect to. | 2027-04-07
Lovat Estate BESS | PRO-003062 | CS-10147 | Lovat Estates Limited | Beauly GSP | SHET-RI-065a Beauly 132kV Substation Redevelopment |  | 2026-05-31
Lovat Estate BESS | PRO-003062 | CS-10148 | Lovat Estates Limited | Beauly GSP | SHET-RI-065b Beauly 3rd SGT Replacement |  | 2026-05-31
Lovedean (Tertiary) | PRO-000484 | CS-07122 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 100574-201198 | 1. Site extension to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 2A. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 6. Local works to facilitate the Category 2 with Sellindge Operational Tripping Scheme (OTS) as described in Appendix F3 to the Bilateral Connection Agreement. 7. Local works required to connect the User to the South West Operational Tripping Scheme (OTS), as described in Appendix F3 to the Bilateral Connection Agreement. | 2029-10-30
Lovedean (Tertiary) | PRO-000484 | CS-07123 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2029-10-30
Lovedean (Tertiary) | PRO-000484 | CS-07124 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2029-10-30
Lovedean (Tertiary) | PRO-000484 | CS-07125 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 2029-10-30
Lovedean GSP | PRO-002941 | CS-12429 | Southern Electric Power Distribution Plc | Lovedean GSP | 104492-208869 |  | 2037-10-30
Low Carbon Link | PRO-004262 | CS-11064 | LOW CARBON SOLAR PARK 39 LIMITED | Pembroke GSP | 102596-205218 |  | 2037-10-31
Low Carbon Link | PRO-004262 | CS-11065 | LOW CARBON SOLAR PARK 39 LIMITED | Pembroke GSP | 103509-206990 |  | 2037-10-31
Lunanhead Battery | PRO-000883 | CS-06681 | LUNANHEAD ENERGY STORAGE LIMITED | Lunanhead GSP | Lunanhead TCA Works | Intertrip required for the loss of one of the grid transformers at Lunanhead 132/33kV GSP | 2026-03-01
Lunanhead Solar Park | PRO-001623 | CS-04475 | SUTTIESIDE ENERGY LIMITED | Lunanhead GSP | Lunanhead Solar Park H1 works item 1 | 1. The installation of four new protection bays, two at each of the remote ends between Tealing and Lunanhead. There is also a Requirement to install two new VTs on both circuits at Lunanhead. | 2025-10-31
Lunanhead Solar Park | PRO-001623 | CS-04476 | SUTTIESIDE ENERGY LIMITED | Lunanhead GSP | Lunanhead Solar Park H1 Works item 2 | 2. Replacement or modification of the Battery Systems, LVAC Board and Standby Generator at Lunanhead 132/33kV GSP, along with the upgrade of communication links between Lunanhead 132/33kV GSP substation and Tealing 132kV substation. | 2025-10-31
Lunanhead Solar Park | PRO-001623 | CS-04477 | SUTTIESIDE ENERGY LIMITED | Lunanhead GSP | Lunanhead Solar Park H1 works item 3 | 3. An intertrip is required for the loss of one of the Grid Transformers at Lunanhead 132/33kV GSP. a. These signals shall be provided by the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom from the signals described below. b. Provision of status signals are required for the following: i. 1TO and 2TO 33kV circuit breakers at Lunanhead GSP. ii. 1T7 and 2T7 33kV disconnectors at Lunanhead GSP. iii. 115 and 215 132kV circuit breakers at Lunanhead GSP | 2025-10-31
Lundie Hybrid Energy Park (Ledyatt Farm) | PRO-004883 | CS-12166 | Arm Dev Energy Ltd | Coupar Angus 2 GSP | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm²) and will operate at 75°C to give a minimum summer pre-fault rating of 176MVA | 2031-10-31
Lundie Hybrid Energy Park (Ledyatt Farm) | PRO-004883 | CS-12167 | Arm Dev Energy Ltd | Coupar Angus 2 GSP | SHET-RI-184 | Coupar Angus 2 Tee – Establish a new 132kV tee point of the HCS circuit between Coupar Angus GSP and Tealing/Charleston Tee for the connection to a new Coupar Angus 2 132/33kV GSP substation | 2031-10-31
Lundie Hybrid Energy Park (Ledyatt Farm) | PRO-004883 | CS-12168 | Arm Dev Energy Ltd | Coupar Angus 2 GSP | SHET-RI-264 | Coupar Angus 2 - Birkhill Tee 132kV Upgrade | 2031-10-31
Lundie Hybrid Energy Park (Ledyatt Farm) | PRO-004883 | CS-12170 | Arm Dev Energy Ltd | Coupar Angus 2 GSP | Lundie Enabling Works | Installation of 2x 132kV circuit breakers and 132kV disconnectors at the new Coupar Angus 2 132/33kV GSP substation compound, including 132kV cabling and works to connect the grid transformers. | 2031-10-31
Lurg Hill | PRO-001264 | CS-05911 | LURG HILL WIND FARM LIMITED | Keith 1 132/33kV GSP Substation | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2024-05-01
Lurg Hill | PRO-001264 | CS-05912 | LURG HILL WIND FARM LIMITED | Keith 1 132/33kV GSP Substation | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 2024-05-01
M74 West Wind Farm | PRO-002398 | CS-08142 | RENEWCO POWER LIMITED | M74 West Wind Farm 132kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2029-10-31
M74 West Wind Farm | PRO-002398 | CS-08143 | RENEWCO POWER LIMITED | M74 West Wind Farm 132kV | M74 West Wind Farm Enabling Works | 1. Redshaw 400kV Substation - It is proposed to build a new 400kV GIS substation, building to be sized to accommodate 15 bays. The initial GIS installed to include the following: • 6x 400kV feeder bays: 2x ELVA, 1x STHA, 1x COAL, 2x Glenmuckloch • 1x 400kV bus coupler • 1x 400kV bus section • 2x 400kV SGT bays (SGT2 not proposed but 400kV GIS bay to be installed as part of the initial build) • Space to be included within the building to accommodate a future bus section, future SGT3 and SGT4 400kV GIS bays and 2x future 400kV GIS feeder bays • Installation of a single 400/132kV 360MVA (SGT1) unit at this time | 2029-10-31
Mablethorpe Storage | PRO-001979 | CS-07626 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 101815-203742 | Mablethorpe Storage SEL infrastructure comprising of a substation extension to new Maplethorpe substation including three generator bays, a bus coupler, a feeder bay and section breakers | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07632 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07633 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100944-201882 | Build a new 400kV Mablethorpe Substation with 6 Bays - 4 Feeder bays, 1 Coupler Bay, 2 Section Breakers Main & Reserve | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07634 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07635 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07636 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07639 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07644 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07645 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 101875-203853 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device with the capacity of pushing mode capable of injecting up to +8 ohm in the Creyke Beck-Killingholme-Keadby 400kV circuit | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07646 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 101892-203877 | Reconductoring of the Drax - Keadby - Thorpe Marsh circuit (Drax leg only) to achieve 2750MVA Pre-summer ratings. | 2031-11-30
Mablethorpe Storage | PRO-001979 | CS-07648 | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Lincolnshire Coastal Node 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2031-11-30
Macduff Battery Storage | PRO-002250 | CS-07701 | Macduff Battery Storage Ltd | Macduff GSP | Macduff Battery Storage Intertrip | Intertrip for the loss of one of the Grid Transformers at MacDuff 132/33kV GSP. These signals will be provided to the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom | 2024-04-30
Macduff Battery Storage | PRO-002250 | CS-07702 | Macduff Battery Storage Ltd | Macduff GSP | Macduff Battery Storage - Protection Schemes | Modification to the existing LV Directional Overcurrent (DOC) protection settings at MacDuff 132/33kV substation will also be required. | 2024-04-30
Macduff Battery Storage | PRO-002250 | CS-07703 | Macduff Battery Storage Ltd | Macduff GSP | Macduff Battery Storage - LoM | A loss of mains scheme will also be configured at Macduff GSP as requested by the Host DNO | 2024-04-30
Machair Offshore Wind Farm | PRO-001392 | CS-06352 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Machair 275/66kV Offshore Substation | Machair - H1 Enabling Works |  | 2033-09-16
Maesnant Energy Park | PRO-001919 | CS-08978 | Maesnant Energy Park Limited | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08979 | Maesnant Energy Park Limited | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08980 | Maesnant Energy Park Limited | Chirk GSP | 101323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08981 | Maesnant Energy Park Limited | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08982 | Maesnant Energy Park Limited | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08983 | Maesnant Energy Park Limited | Chirk GSP | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08984 | Maesnant Energy Park Limited | Chirk GSP | 01381-202705 | Establish a new 400kV double circuit from Connahs Quay 400kV substation to the Rugeley 400 kV substation. (This includes circa 90km of L6 tower with 4x400mm² conductor for each circuit plus 2 feeder bays at each Connahs Quay and Rugeley substations) | 2033-11-01
Maesnant Energy Park | PRO-001919 | CS-08985 | Maesnant Energy Park Limited | Chirk GSP | 101905-203903 | nstall power control devices with push and pull capability (up to 8 ohm) at the Rugeley-Drakelow circuit | 2033-11-01
Magwind | PRO-001766 | CS-05384 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | Magwind Item 1 | At New Dounreay 400kV Substation, install two 400 kV feeder bays, with each bay comprising 2 x 400 kV busbar selection switches, 1 x 400 kV circuit breaker, 1 x 400 kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee’s assets and User owned equipment will be the 400kV clamps on the User’s side of the 400kV line disconnectors at the New Dounreay 400kV Substation. | 2033-10-31
Magwind | PRO-001766 | CS-05385 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Magwind | PRO-001766 | CS-05386 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Magwind | PRO-001766 | CS-05387 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Magwind | PRO-001766 | CS-05388 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Magwind | PRO-001766 | CS-05389 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Magwind | PRO-001766 | CS-05390 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Magwind | PRO-001766 | CS-05391 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2033-10-31
Magwind | PRO-001766 | CS-05392 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Magwind | PRO-001766 | CS-05393 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 2033-10-31
Magwind | PRO-001766 | CS-05394 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Magwind | PRO-001766 | CS-05395 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Magwind | PRO-001766 | CS-05396 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Magwind | PRO-001766 | CS-05397 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 2033-10-31
Magwind | PRO-001766 | CS-05398 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Magwind | PRO-001766 | CS-05399 | MAGNORA OFFSHORE WIND N3 LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Mains of Dun Solar | PRO-004007 | CS-10062 | GREENTECH PROJECTS HOLDING UK LIMITED | Bridge of Dun GSP | Mains of Dun Solar Sole Enabling Works | 1. Installation of 2x 132kV circuit breakers and associated disconnectors. 2. Refurbishment of 5km of 132kV double circuit overhead line to facilitate a minimum continuous summer rating of 120MVA. | 2032-06-30
Mains of Dun Solar | PRO-004007 | CS-10063 | GREENTECH PROJECTS HOLDING UK LIMITED | Bridge of Dun GSP | SHET-RI-120 East Coast 132kV Upgrade |  | 2032-06-30
Mains of Dun Solar | PRO-004007 | CS-10064 | GREENTECH PROJECTS HOLDING UK LIMITED | Bridge of Dun GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-06-30
MALTBY DEV. | PRO-003064 | CS-10835 | Firma Vogt Solar Ltd | Thurcroft 275kV Substation | 102149-204350 (Arkwright) |  | 2034-10-31
MALTBY DEV. | PRO-003064 | CS-10836 | Firma Vogt Solar Ltd | Thurcroft 275kV Substation | 101812-203717 (2) |  | 2034-10-31
MALTBY DEV. | PRO-003064 | CS-10837 | Firma Vogt Solar Ltd | Thurcroft 275kV Substation | 103371-206838 |  | 2034-10-31
Mannington | PRO-001091 | CS-05913 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-30752 | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. | 2025-11-30
Mannington | PRO-001091 | CS-05914 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-31671-1 | Re-conductor the Bramley - Fleet OHL circuits to increase capacity. | 2025-11-30
Mannington | PRO-001091 | CS-05915 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-31671-2 | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | 2025-11-30
Mannington | PRO-001091 | CS-05916 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-33539 | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating. | 2025-11-30
Mannington | PRO-001091 | CS-12526 | PIVOTED POWER LLP | Mannington 400kV Substation | 102051-205763 |  | 2025-11-30
Mannington | PRO-001092 | CS-07112 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 100978-201961 | 1. Install a tertiary cable box or bushings on the SGT 4*. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Local works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. * Note: Alternative running arrangements to be discussed and arranged as per Appendix N | 2030-08-30
Mannington | PRO-001092 | CS-07113 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2030-08-30
Mannington | PRO-001092 | CS-07114 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2030-08-30
Mannington | PRO-001092 | CS-07115 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2030-08-30
Mannington | PRO-001092 | CS-12539 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 102051-205763 |  | 2030-08-30
Mannington GSP | PRO-002942 | CS-11666 | Southern Electric Power Distribution Plc | Mannington GSP | 102387-204878-Mannington GSP |  | 2033-10-31
Mannington GSP | PRO-002942 | CS-11667 | Southern Electric Power Distribution Plc | Mannington GSP | 102387-204877 EX5 |  | 2033-10-31
Mannington GSP | PRO-002942 | CS-11668 | Southern Electric Power Distribution Plc | Mannington GSP | 102530-205130 EX5 |  | 2033-10-31
Mannington GSP | PRO-002942 | CS-11669 | Southern Electric Power Distribution Plc | Mannington GSP | 102530-205131 EX5 |  | 2033-10-31
Mannington Tertiary | PRO-000464 | CS-05917 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 102051-204221 | 1. Installation of a new 150MVA-rated 400/33kV SGT including HV and LV bays 2. Establish a new single busbar 33kV substation at Mannington to be connected via the new 400/33kV SGT. 3. Installation of an earthing transformer connecting onto the 33kV busbar 4. Local works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement | 2025-10-30
Mannington Tertiary | PRO-000464 | CS-05918 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2025-10-30
Mannington Tertiary | PRO-000464 | CS-08086 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2025-10-30
Mannington Tertiary | PRO-000464 | CS-08087 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2025-10-30
Manquhill Wind Farm | PRO-004662 | CS-11021 | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation | Manquhill Wind Farm | 1. Installation of one 132kV disconnector at Manquhill wind farm substation. 2. Construction of a new 132kV wood pole OHL of approx. 16.5km to Craigenputtlock 400/132kV substation (minimum 62MVA rating is required). 3. Installation of one 132kV double busbar feeder bay at Craigenputtlock 400/132kV substation. | 2036-10-31
Manquhill Wind Farm | PRO-004662 | CS-11022 | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation | SPT-RI-2862 OHL |  | 2036-10-31
Manquhill Wind Farm | PRO-004662 | CS-11023 | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Manquhill Wind Farm | PRO-004662 | CS-11024 | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Manquhill Wind Farm | PRO-004662 | CS-11025 | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation | SPT-RI-3657 OHL |  | 2036-10-31
Manquhill Wind Farm | PRO-004662 | CS-11026 | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation | SPT-RI-3657 SS |  | 2036-10-31
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07889 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 101996-204131 | 1. Extend the main and reserve busbars at Marchwood 400kV Substation to accommodate the new User bay | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07890 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07891 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07892 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07893 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07894 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07895 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07896 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2028-06-01
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07897 | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2028-06-01
MARES | PRO-000978 | CS-05919 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-30915 | Design, construct and commission a 2.5GW capacity VSC HVDC link from Wylfa to Pembroke comprising of a 2.5GW VSC based HVDC converter station local to the company's owned Wylfa 400kV substation in North Wales, a 2.5GW VSC based HVDC converter station local to the company's owned Pembroke 400kV substation in South Wales and a 2.5GW capacity HVDC linking the converter stations at Wylfa and Pembroke. | 2028-11-30
MARES | PRO-000978 | CS-05920 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32014S1 | Install two new MSCDN's at Ironbridge 400kV substation. | 2028-11-30
MARES | PRO-000978 | CS-05921 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32014S3 | Install two MSCDN's at Legacy 400kV. | 2028-11-30
MARES | PRO-000978 | CS-05922 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32021 | Reconductor the Cellarhead - Drakelow 400kV circuit with 2 x 620mm² GZTACSR. | 2028-11-30
MARES | PRO-000978 | CS-05923 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32022 | Increase the thermal capability of the existing South Manchester - Bredbury 275kV circuit. | 2028-11-30
MARES | PRO-000978 | CS-05924 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32030 | Uprate the two Quad Boosters at Legacy to 2750MVA. | 2028-11-30
MARES | PRO-000978 | CS-05925 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32029 | Reconductor the Legacy legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | 2028-11-30
MARES | PRO-000978 | CS-05926 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32028 | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | 2028-11-30
MARES | PRO-000978 | CS-05927 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-11076 | Reconductor Ironbridge - Rugely circuit with 2 x 570 AAAC conductors. | 2028-11-30
MARES | PRO-000978 | CS-05928 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32014S2 | Install two MSCDN's at Connah's Quay. | 2028-11-30
MARES | PRO-000978 | CS-05929 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32281 | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation. | 2028-11-30
MARES | PRO-000978 | CS-05930 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32372LI | Increase thermal rating of Carrington - South Manchester circuit. | 2028-11-30
MARES | PRO-000978 | CS-05931 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32373LI | Reconductor Connah's Quay - Daines circuit with London. | 2028-11-30
MARES | PRO-000978 | CS-05932 | Maresconnect Limited | Bodelwyddan 400kV Substation | NGET-RI-32374LI | Increase thermal rating of Cellarhead - Daines cable. | 2028-11-30
Margree Wind Farm | PRO-001789 | CS-04779 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-2243 | Glenshimmeroch 132/33kV substation transformer | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-04781 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-04782 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-04783 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-04784 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-04785 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-274 | Glenshimmeroch Collector Substation - On the New Cumnock / Blackcraig 132kV circuit, installation of a 132kV circuit breaker and associated disconnectors at Glenshimmeroch Collector Substation in South West Scotland. | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-04786 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-296 | Glenshimmeroch collector substation 132kV overhead line uprating - Due to an increase in the generation contracted in the area, it is proposed to uprate a section of the overhead line between the proposed Glenshimmeroch collector substation to the cable end on the New Cumnock 132kV circuit. This is approximately 11km. This will be achieved by replacing the existing UPAS conductor with LARK conductor on the existing wood pole system. | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-12060 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-10-31
Margree Wind Farm | PRO-001789 | CS-12061 | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation | SPT-RI-4212 | 8. Margree 132kV Collector Substation - In order to accommodate the connection of Troston, Glenshimmeroch, Margree and Fell Wind farms via a shared solution as per customer’s request, it is proposed to establish a new 132/33kV collector substation at Margree location (on the New Cumnock / Blackcraig 132kV circuit). The scope of work comprises installation of one 132kV circuit breaker and associated disconnectors, one 132kV busbar and one 132kV circuit breaker and disconnector (on the Blackcraig 132kV circuit). The creation of this new collector substation is noted as part of SPT-TOCO-2143, SPTTOCO-505, SPT-RI-458 & SPT-TOCO-2160. All TOCO Mod-App’s must be accepted to consider this contracted. Upon the acceptance of all 4 Mod-App’s, this TORI will supersede SPT-RI-274 - Glenshimmeroch Collector Substation. In this event, SPT-RI-274 will be withdrawn. Any abortive costs will be detailed in the charging section. (SPT-RI-4212) | 2029-10-31
Market Harborough | PRO-003271 | CS-10512 | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation | 100816-201651 (4) |  | 2034-10-31
Market Harborough | PRO-003271 | CS-10513 | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation | 101263-202505 (4) |  | 2034-10-31
Market Harborough | PRO-003271 | CS-10514 | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation | 102381-204829 (4) |  | 2034-10-31
Market Harborough | PRO-003271 | CS-10515 | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation | 102513-205111 (4) |  | 2034-10-31
Market Harborough | PRO-003271 | CS-10516 | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation | 102513-205112 (4) |  | 2034-10-31
Market Harborough | PRO-003271 | CS-10517 | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation | 103121-206538 (4) |  | 2034-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06273 | Marramwind Limited | Longside 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06274 | Marramwind Limited | Longside 400kV Substation | SHET-RI-025d | North East Reinforcement | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06275 | Marramwind Limited | Longside 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06276 | Marramwind Limited | Longside 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06277 | Marramwind Limited | Longside 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06278 | Marramwind Limited | Longside 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06279 | Marramwind Limited | Longside 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06280 | Marramwind Limited | Longside 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06281 | Marramwind Limited | Longside 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06282 | Marramwind Limited | Longside 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06283 | Marramwind Limited | Longside 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06284 | Marramwind Limited | Longside 400kV Substation | OWF3 H1 Works | 400kV GIS Bay | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06285 | Marramwind Limited | Longside 400kV Substation | NGET-RI-30669-1 & SHET-RI-033 | Install a second 2GW HVDC converter station with associated equipment. HVDC cables to be routed between Aberdeenshire and North East England. | 2031-10-31
Marram Wind Offshore Wind Farm | PRO-001406 | CS-06286 | Marramwind Limited | Longside 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2031-10-31
Martindale Farm | PRO-005153 | CS-12488 | BSR APPLICATIONS LIMITED | Hartmoor GSP | 104609-209212 |  | 2039-10-30
MCKRAW99MW BESS BEGA | PRO-004272 | CS-10075 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2032-06-30
MCKRAW99MW BESS BEGA | PRO-004272 | CS-10076 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2032-06-30
MCKRAW99MW BESS BEGA | PRO-004272 | CS-10077 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-3678 - OHL |  | 2032-06-30
MCKRAW99MW BESS BEGA | PRO-004272 | CS-10078 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-3678 - SS |  | 2032-06-30
McQuittiston Farm | PRO-004049 | CS-09265 | SP Distribution plc | Coylton 132/33kV | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 2026-05-29
McQuittiston Farm | PRO-004049 | CS-09266 | SP Distribution plc | Coylton 132/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-05-29
Meadaple Wind Farm | PRO-000677 | CS-05933 | Scottish Hydro Electric Power Distribution Plc | Rothienorman GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2021-06-01
Medway 3 Power Station | PRO-002578 | CS-08556 | MEDWAY POWER LIMITED | Kingsnorth 400kV Substation | 102481-205063 | 1. Facilitate the connection of the generator bay at Kingsnorth 400kV AIS substation. 2. Modification / upgrade to substation control system (SCS) and protection and control systems at the Kingsnorth 400kV substation. | 2030-12-31
Meetlaw BESS | PRO-001966 | CS-07371 | CARRAVINDOON LIMITED | Fiddes GSP | Fiddes SS |  | 2031-10-31
Meetlaw BESS | PRO-001966 | CS-07372 | CARRAVINDOON LIMITED | Fiddes GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2031-10-31
Meetlaw BESS | PRO-001966 | CS-07373 | CARRAVINDOON LIMITED | Fiddes GSP | Fiddes circuit breakers |  | 2031-10-31
Meiklelaught Farm BESS | PRO-003631 | CS-09656 | GPC 1127 Ltd | Saltcoats 132/33kV | SPT-RI-3052 - CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Rep. | CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Replacement | 2028-08-21
Meiklelaught Farm BESS | PRO-003631 | CS-09657 | GPC 1127 Ltd | Saltcoats 132/33kV | SPT-RI-3185 - KILW-HUNF-HUNE No.2 Cable Replacement | KILW-HUNF-HUNE No.2 Cable Replacement | 2028-08-21
Meiklelaught Farm BESS | PRO-003631 | CS-09658 | GPC 1127 Ltd | Saltcoats 132/33kV | SPT-RI-2710 | BU Route OHL Reconductor - As part of RIIO-T2 asset modernisation a number of assets across the transmission network have been identified for replacement. This TORI captures the asset modernisation work that is scheduled to be carried out on the 132kV OHL BU Route which runs between KILW-HUNF-HUNE at ~13km. The OHL circuit will be reconductored to achieve a minimum of 220MVA per circuit (Reconductor with 425mm² ‘Totara’ AAAC @ 75°C) | 2028-08-21
Melksham | PRO-001605 | CS-06860 | LIME DOWN SOLAR PARK LIMITED | Melksham 400kV Substation | 101463-202903 | Double busbar extension at Melksham 400kV Substation to provide space for The User’s Generator Bay. | 2030-07-31
Melksham | PRO-001605 | CS-06861 | LIME DOWN SOLAR PARK LIMITED | Melksham 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 2030-07-31
Melksham | PRO-001605 | CS-06862 | LIME DOWN SOLAR PARK LIMITED | Melksham 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2030-07-31
Melksham | PRO-001605 | CS-06863 | LIME DOWN SOLAR PARK LIMITED | Melksham 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2030-07-31
Melksham | PRO-001605 | CS-06864 | LIME DOWN SOLAR PARK LIMITED | Melksham 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2030-07-31
Melksham (Tertiary) | PRO-000463 | CS-05939 | MELKSHAM CALNE GREEN LIMITED | Melksham 400kV Substation | 100651-201330 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer to Disconnecting Circuit Breaker (DCB) Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection | 2026-06-26
Melksham (Tertiary) | PRO-000463 | CS-06865 | MELKSHAM CALNE GREEN LIMITED | Melksham 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 2026-06-26
Melksham BESS & PV | PRO-002441 | CS-08892 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102270-204632 | Turn in the Minety – Melksham circuit No 1. into the new Melksham B 400kV substation (new substation name to be confirmed) Construction of a new 4 bay 400kV double busbar substation called Melksham B 400kV substation (new substation name to be confirmed) consisting of 2 feeder bays, 1 User bay and 1 bus coupler bay | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08893 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08894 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08895 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08896 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm² Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm² Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm² Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08897 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08898 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08899 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102087-204278 | Uprate A87D Imperial Park – Melksham (future Imperial Park – Folly Farm – Melksham) 400kV circuit cable section (3.9km, with a summer pre-fault rating of 1424MVA) to a summer pre-fault rating of at least 1621MVA | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08900 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 2037-10-15
Melksham BESS & PV | PRO-002441 | CS-08901 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102094-204287 | Installation of a new 200MVAr mechanically switched capacitor bank (MSC) at either Minety 400kV or Melksham 400kV Substation for pre-fault voltage compliance | 2037-10-15
Melksham GSP | PRO-002943 | CS-12171 | Southern Electric Power Distribution Plc | Severn Connection Node B 400kV Substation | 102270-204632 (Melksham) |  | 2037-10-15
Melksham GSP | PRO-002943 | CS-12172 | Southern Electric Power Distribution Plc | Severn Connection Node B 400kV Substation | 102270-204633 (Melksham) |  | 2037-10-15
Melksham GSP | PRO-002943 | CS-12173 | Southern Electric Power Distribution Plc | Severn Connection Node B 400kV Substation | 102270-204634 (Melksham) |  | 2037-10-15
Melksham GSP | PRO-002943 | CS-12174 | Southern Electric Power Distribution Plc | Severn Connection Node B 400kV Substation | 104252-208257 (Melksham) |  | 2037-10-15
Menter Mon Morlais Anglesey Marine Energy | PRO-001134 | CS-04066 | Menter Môn Morlais Limited | Penrhos GSP | 30309 | Install Series Compensation at Pentir 400 kV substation | 2028-03-31
Menter Mon Morlais Anglesey Marine Energy | PRO-001134 | CS-04067 | Menter Môn Morlais Limited | Penrhos GSP | 30310 | Installation of a second Wylfa – Pentir double circuit | 2028-03-31
Menter Mon Morlais Anglesey Marine Energy | PRO-001134 | CS-04068 | Menter Môn Morlais Limited | Penrhos GSP | 30311 | Establish a second Pentir – Trawsfyndd circuit and its associated schemes which includes uprating the overhead line and cable sections, and building of Bryncir substation [30311] Uprating of Pentir – Bodelwyddan – Connah’s Quay double circuit | 2028-03-31
Menter Mon Morlais Anglesey Marine Energy | PRO-001134 | CS-04069 | Menter Môn Morlais Limited | Penrhos GSP | 33642 | Installation of a 400/132 kV Super Grid Transformer (SGT) at Wylfa 132 kV substation, procure land and extend Wylfa 400 kV substation for this new SGT | 2028-03-31
Menter Mon Morlais Anglesey Marine Energy | PRO-001134 | CS-04070 | Menter Môn Morlais Limited | Penrhos GSP | 33815 | Installation of a CAP76 Category 1 and 3 system to generator operational intertrip. Extensions to Reserve Busbar 1 at Wylfa 132 kV Substation. Install equipment on the spare skeletal feeder bay at Wylfa 132 kV Substation to facilitate connection. Busbar protection and substation control system modifications as required at Wylfa 132 kV Substation. Installation of a CAP76 Category 2 system to generator operational intertrip. Installation of a 400/132 kV Super Grid Transformer (SGT) at Wylfa 132 kV substation, procure land and extend Wylfa 400 kV substation for this new SGT | 2028-03-31
Mererid Offshore Wind Farm | PRO-002391 | CS-08147 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 102279-204533 | Infrastructure works for the generation connection of Mererid Offshore wind farm. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08148 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08149 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08150 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08151 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08152 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08153 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08154 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Mererid Offshore Wind Farm | PRO-002391 | CS-08155 | South West Wind Holdco Limited | Alverdiscott 400kV Substation |  |  | 2036-12-06
Merthyr Solar and Battery | PRO-002757 | CS-11552 | EEW RENEWABLES LTD | Cilfynydd 400kV Substation | 101947-203995 (1) |  | 2029-05-12
Merthyr Solar and Battery | PRO-002757 | CS-11553 | EEW RENEWABLES LTD | Cilfynydd 400kV Substation | 102584-205197 (1) |  | 2029-05-12
MeyGen Tidal | PRO-000336 | CS-04447 | Meygrid Limited | Gills Bay GSP | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-05940 | Meygrid Limited | Gills Bay GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-05941 | Meygrid Limited | Gills Bay GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-05942 | Meygrid Limited | Gills Bay GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-05943 | Meygrid Limited | Gills Bay GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-05944 | Meygrid Limited | Gills Bay GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12511 | Meygrid Limited | Gills Bay GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12512 | Meygrid Limited | Gills Bay GSP | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12513 | Meygrid Limited | Gills Bay GSP | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12514 | Meygrid Limited | Gills Bay GSP | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12515 | Meygrid Limited | Gills Bay GSP | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12516 | Meygrid Limited | Gills Bay GSP | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12517 | Meygrid Limited | Gills Bay GSP | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2027-04-01
MeyGen Tidal | PRO-000336 | CS-12518 | Meygrid Limited | Gills Bay GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2027-04-01
Mid Hill | PRO-005000 | CS-11802 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 2034-10-30
Mid Hill | PRO-005000 | CS-11803 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2034-10-30
Mid Hill | PRO-005000 | CS-11804 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | SPT-RI-2417 | Teviot to Gala North Reinforcements - A new 400kV double circuit OHL using L13 towers and triple Araucaria conductor from Teviot 400kV substation to Gala North 400kV substation which is approximately 57km. (SPT-RI-2417) | 2034-10-30
Mid Hill | PRO-005000 | CS-11805 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | SPT-RI-2418 | Under this TORI it is proposed to establish a second 132kV board at Teviot substation. This will require the installation of two 400kV GIS bays as well as two 400/132kV 240MVA transformers and their associated 132kV double busbar bays as well as a 132kV bus coupler. All 132kV switchgear is proposed to be Air Insulated Switchgear (AIS). | 2034-10-30
Mid Hill | PRO-005000 | CS-11806 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 2034-10-30
Mid Hill | PRO-005000 | CS-11807 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | NGET 101074 - 202154 | 2. New OHL reinforcement from Teviot Substation to Harker 400kV substation. (NGET 101074 – 202154) | 2034-10-30
Mid Hill | PRO-005000 | CS-11808 | Invenergy Development UK Ltd | Mid Hill 132kV Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 2034-10-30
Mid Moile Wind Farm | PRO-004036 | CS-09847 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3558 - L48 Glen App Collector Substation | To accommodate generation into Auchencrosh 275kV substation, it is proposed to establish a the L48 Glen App Collector substation. At Auchencrosh substation, install a 275kV feeder bay. From there, install approximately 0.5km of 275kV UGC to the collector substation. At the L48 Glen App Collector substation, install a 275kV single busbar with one 275kV feeder bay. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09848 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3559 - COYL-CARR-MAHI Intertrip Scheme | IED’s will be installed at the Coylton 275kV substation, Carrick 275kV substation and Mark Hill 275kV substation to monitor the status of the 275kV circuit breakers installed along YY Route. Should any of the relevant circuit breakers detailed in the below table open, a trip signal will be sent to relevant generators. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09849 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3560 - COYL-CARR-MAHI-AUCC LMS Scheme | IED’s will be installed at the Carrick 275kV substation and Auchencrosh 275kV substation to monitor the circuit loading along YY Route. Should any of the relevant YY Route circuit sections detailed in the below table be overlaoded, a trip signal will be sent to relevant generators. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09850 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09851 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09852 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09853 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-2876 - West Coast Onshore Reinforcement (North Section | Under the NOA7 Refresh the need was identified to develop a new west coast onshore high?capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. This project is driven by the continued increase in required transfers seen across this boundary due to the need to connect renewable generation in Scotland to achieve UK and Government’s net zero target by 2050 and 2045 respectively. To facilitate generation applications in this area it is proposed to utilise this new west coast onshore corridor. This TORI shall construct a new Killoch 400kV substation to feed a new Killoch 275kV substation via three new 400/275kV SGT’s, diversion and 400kV uprating of the existing XY route between Kilmarnock South and the new Killoch 400kV substations and the 400kV uprating of the WA route between the new Killoch 400kV and New Cumnock North 400kV substations. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09854 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09855 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3176 - Kilmarnock South to West Coast HVDC Bussing Station | Install a 2GW HVDC link from Kilmarnock South 400kV substation to the South Ayrshire 525kV HVDC bussing station located in southwest Scotland. The DC bussing station to facilitate a multi terminal HVDC arrangement between Kilmarnock South, Machair Wind and a southern converter station located in NGET. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09856 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3178 - West Coast HVDC Bussing Station to NGET | Install a 4GW HVDC link from the South Ayrshire 525kV HVDC bussing station to a southern converter station within the NGET licensed area. The costs associated with this SPT reinforcement instruction are associated with the installation of the HVDC cable system from the DC bussing station to the Scotland-England maritime boundary. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09857 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3309 | New Cumnock North 400kV GIS substation- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new 400kV substation in the vicinity of the existing New Cumnock 275kV substation. This shall be a double busbar GIS ‘New Cumnock North’ 400kV substation. This new substation shall facilitate the development of the NOA WCNC scheme (currently under review) | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09858 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09859 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3452 - Mark Hill North - New Cumnock North 400kV Circuit | To alleviate the thermal overloading associated with YY route, it is proposed to reinforce the South West Scotland network by creating 400kV power corridors between New Cumnock and the proposed South Ayrshire HVDC Converter station. As part of these works, a new 400kV double circuit will be established between the Mark Hill North 400kV substation (developed under SPT-RI-3461) and New Cumnock North 400kV substation (developed under SPT-RI?3309). | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09860 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3461 - Mark Hill North 400/275kV Substation | To alleviate the thermal overloading associated with YY route, it is proposed to reinforce the South West Scotland network by creating 400kV power corridors between New Cumnock and the proposed South Ayrshire HVDC Converter station. As part of these works, a new 400/275kV substation will be established within the vicinity of the existing Mark Hill 275kV substation. The new Mark Hill North Substation shall comprise of a 400kV double busbar substation as well as a new 275kV double busbar substation, these will be connected via three 400/275kV Supergrid Transformers. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09861 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3498 - Glenmuckloch 400kV - Dumfries North 400kV | Under the NOA7 Refresh the need was identified to develop a new west coast onshore high?capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. This project is driven by the continued increase in required transfers seen across this boundary due to the need to connect renewable generation in Scotland to achieve UK and Government’s net zero target by 2050 and 2045 respectively. To facilitate generation applications in this area it is proposed to utilise this new west coast onshore corridor. The TORI shall construct a new 400kV double circuit between the proposed Glenmuckloch 400kV substation (established under SPT-RI-236) and the proposed Dumfries North 400kV substation (established under SPT-RI-2862). It is proposed to string both sides of the 400kV corridor with 3x700mm² Araucaria AAAC conductor provisionally rated at 750°C with the capability to uprate the operating temperature to 900°C. | 2031-10-31
Mid Moile Wind Farm | PRO-004036 | CS-09862 | ENERGIEKONTOR UK LTD | Mid Moile Wind Farm 275/132kV Substatio | SPT-RI-3463 - Mark Hill North – South Ayrshire HVDC Bussing Station | It is proposed to establish a new HVDC Converter station at the proposed South Ayrshire HVDC Bussing Station established under SPT-RI-3176 Kilmarnock South – West Coast HVDC Bussing Station. This new converter station will provide an interface between the SPT South-West Ayrshire network and the West Coast HVDC link proposed under HNDFUE. A new 400kV power corridor will be established between the new HVDC converter station and the proposed Mark Hill North substation established under SPT-RI-3461 Mark Hill North 400/275kV substation. | 2031-10-31
Middleton BESS | PRO-002305 | CS-07443 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101603-203226 |  | 2026-11-30
Middleton BESS | PRO-002305 | CS-07444 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2026-11-30
Middleton BESS | PRO-002305 | CS-07445 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07446 | Middleton Energy Storage Limited | Middleton 400KV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07447 | Middleton Energy Storage Limited | Middleton 400KV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07448 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07449 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07450 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07451 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2026-11-30
Middleton BESS | PRO-002305 | CS-07452 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07453 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm² conductor | 2026-11-30
Middleton BESS | PRO-002305 | CS-07454 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 2026-11-30
Middleton BESS | PRO-002305 | CS-07455 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2026-11-30
Middleton Farm BESS | PRO-004120 | CS-10723 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10724 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10725 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-2390 OHL |  | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10726 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-2390 SS |  | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10727 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-3505 H1 OHL |  | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10728 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-3721 OHL |  | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10730 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-3721 SS |  | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10735 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-3722 SS |  | 2033-10-25
Middleton Farm BESS | PRO-004120 | CS-10736 | Bluestone Energy Ltd | Neilston 400kV Substation | SPT-RI-3722 OHL |  | 2033-10-25
Midlands Estate Energy Park | PRO-001945 | CS-07186 | Renewable Energy Systems Limited | West Burton 400kV Substation | 101779-203571 | Extension of 400kV West Burton substation for provision of one user generation bay. | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07187 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07188 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07189 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07190 | Renewable Energy Systems Limited | West Burton 400kV Substation | 030613-030613 | Uprate the Cottam - Staythorpe (2) circuit to provide a post-fault summer rating of 2800 MVA | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07191 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07220 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07221 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07222 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07223 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07224 | Renewable Energy Systems Limited | West Burton 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2029-10-31
Midlands Estate Energy Park | PRO-001945 | CS-07225 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2029-10-31
Mill Hill Tertiary Connection | PRO-000493 | CS-12040 | HB333MIL LTD | Mill Hill 275kV Substation | 102203-204425 |  | 2025-10-24
Mill Hill Tertiary Connection | PRO-000493 | CS-12041 | HB333MIL LTD | Mill Hill 275kV Substation | 102203-204426 |  | 2025-10-24
Mill Rig Wind Farm | PRO-000892 | CS-05946 | Mill Rig Wind Farm LLP | Kilmarnock South 275/33kV | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2024-07-31
Mill Rig Wind Farm | PRO-000892 | CS-05947 | Mill Rig Wind Farm LLP | Kilmarnock South 275/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2024-07-31
Millbrook Power | PRO-000373 | CS-05948 | MILLBROOK POWER LIMITED | Marston Vale 400kV Substation | 100023-200046 | Construct a double busbar 400kV substation in the vicinity of tower ZA378 comprising of 2 feeder bays, 1 busbar coupler bay and space to accommodate the User bay. Establish a double tee connection between the new 400kV substation and the Grendon – Sundon 400kV double circuit. | 2024-06-28
Milligansbush Battery Storage | PRO-003430 | CS-09655 | Milligansbush Battery Storage Ltd | Milligansbush Battery Storage 132kV Substation | SPT-RI-231 |  | 2036-10-30
Millmoor Rig Wind Farm | PRO-001936 | CS-07229 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | Millmoor Rig Wind Farm Enabling Works | 1. Installation of a 132kV line disconnector at the Millmoor Rig Windfarm 132kV substation 2. Installation of a 132kV circuit between Millmoor Rig Windfarm 132kV substation and Hawick 132kV substation. This circuit is approximately 17km in length. 3. Installation of a new 132kV circuit breaker and associated disconnectors at Hawick 132kV substation. 4. Extension of the Hawick 132kV substation platform | 2029-10-30
Millmoor Rig Wind Farm | PRO-001936 | CS-07230 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 2029-10-30
Millmoor Rig Wind Farm | PRO-001936 | CS-07231 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | SPT-RI-288 Hawick to Galashiels 132kV Reconfiguration | Hawick 132/33kV substation is currently supplied via two 132kV circuits from Gretna 400/132kV substation, with a 132kV circuit to Galashiels normally open at CB 205. With the proposed connection of Faw Side wind farm (250MW) it is proposed to reconfigure Hawick 132kV substation such that Hawick can be supplied from Galashiels and establish the Hawick / Galashiels 132kV circuit No.1 and No.2. Works at Galashiels will be required to terminate the double circuit from Hawick post reconfiguration. At Hawick, it is also proposed to install two new 132kV circuit breakers and a fourth 132kV circuit at Hawick with Poplar conductor:. The existing circuit breakers at Galashiels are of 600A and 800A. It is also proposed to replace the 600A circuit breakers 120 and 620 with a standard 2000A circuit breaker. | 2029-10-30
Millmoor Rig Wind Farm | PRO-001936 | CS-07232 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 2029-10-30
Milltown Airfield Solar Farm | PRO-001277 | CS-05952 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2027-02-28
Milltown Airfield Solar Farm | PRO-001277 | CS-05953 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 2027-02-28
Milltown Airfield Solar Farm | PRO-001277 | CS-05954 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2027-02-28
Milltown Airfield Solar Farm | PRO-001277 | CS-09511 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2027-02-28
Milltown Airfield Solar Farm | PRO-001277 | CS-09512 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-174 | Upgrade of Keith SGTs- Replace the existing 132/275kV 240MVA SGTs at Keith 132kV Substation with larger 480/360MVA units | 2027-02-28
Minety | PRO-000454 | CS-04481 | HB411MIN Limited | Minety 400kV Substation | 101488-202944 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish new bus bar, 33kV substation at Minety to be connected via new 400/33kV SGT8B 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2024-10-31
Minnygryle Burn Energy Park | PRO-004204 | CS-10718 | Wind 2 Project 6 Limited | Minnygryle Burn Energy Park 132kV substation | SPT-RI-3657 OHL |  | 2036-10-31
Minnygryle Burn Energy Park | PRO-004204 | CS-10719 | Wind 2 Project 6 Limited | Minnygryle Burn Energy Park 132kV substation | SPT-RI-3657 SS |  | 2036-10-31
Minnygryle Burn Energy Park | PRO-004204 | CS-10720 | Wind 2 Project 6 Limited | Minnygryle Burn Energy Park 132kV substation | SPT-RI-2862 OHL |  | 2036-10-31
Minnygryle Burn Energy Park | PRO-004204 | CS-10721 | Wind 2 Project 6 Limited | Minnygryle Burn Energy Park 132kV substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Minnygryle Burn Energy Park | PRO-004204 | CS-10722 | Wind 2 Project 6 Limited | Minnygryle Burn Energy Park 132kV substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Moel y Llyn | PRO-001585 | CS-04706 | Waun Hesgog Energy Park Limited | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 2027-02-04
Moel y Llyn | PRO-001585 | CS-04707 | Waun Hesgog Energy Park Limited | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 2027-02-04
Moel y Llyn | PRO-001585 | CS-04708 | Waun Hesgog Energy Park Limited | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2027-02-04
Moel y Llyn | PRO-001585 | CS-04709 | Waun Hesgog Energy Park Limited | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2027-02-04
Moel y Llyn | PRO-001585 | CS-04711 | Waun Hesgog Energy Park Limited | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-02-04
Moffat BESS | PRO-004654 | CS-09707 | Conrad Energy (Developments) II Limited | Moffat 400kV Substation | SPT-RI-231 |  | 2031-10-31
Moffat BESS | PRO-004654 | CS-09708 | Conrad Energy (Developments) II Limited | Moffat 400kV Substation | SPT-RI-3423 | Moffat 400kV Single Busbar - Given the connection applications received in the Moffat area it is required to create a new shared 400kV busbar to accommodate two connections in this area. It is proposed to install a new 400kV double busbar bay and extend the substation platform accordingly to accommodate this. From here a new 400kV cable section shall be installed to a location where a new 400kV busbar section shall be created. The contingent connections shall then connect onto this new section of busbar/ | 2031-10-31
Mon Solar Farm | PRO-001480 | CS-06867 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06868 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06869 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06870 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of a new Pentir - Wylfa OHL. | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06871 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06872 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06873 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-06874 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-12085 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 102556-205162 |  | 2029-10-30
Mon Solar Farm | PRO-001480 | CS-12086 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation | 102557-205163 |  | 2029-10-30
Mona Offshore Wind Farm | PRO-001391 | CS-06368 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 102730-205516 |  | 2029-10-31
Mona Offshore Wind Farm | PRO-001391 | CS-06369 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 101292-202001 |  | 2029-10-31
Mona Offshore Wind Farm | PRO-001391 | CS-06370 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 102731-205517 |  | 2029-10-31
Mona Offshore Wind Farm | PRO-001391 | CS-06371 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 101292-201374 BPMona |  | 2029-10-31
Mona Offshore Wind Farm | PRO-001391 | CS-06373 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2029-10-31
Mona Offshore Wind Farm | PRO-001391 | CS-11062 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 101474-202916 | Reconductor the existing Cellarhead-Drakelow 400 kV circuits 1 and 2 to achieve a pre fault summer rating of 2800 MVA | 2029-10-31
Mona Offshore Wind Farm | PRO-001391 | CS-11063 | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 2029-10-31
Monets Garden | PRO-001082 | CS-05990 | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation | 100655-201341 | 1. Install 13kV/33kV earthing transformer on 13kV tertiary connection at Osbaldwick 400/33kV substation. 2. Install 13kV circuit breaker on the 13kV side of the 13kV / 33kV transformer at Osbaldwick 400/33kV substation 3. Install 13kV disconnector on the 13kV side of the 13kV / 33kV transformer at Osbaldwick 400kV/33kV Substation 4. Install an auto-close scheme at Osbaldwick 400/33kV substation. | 2024-10-30
Monets Garden | PRO-001082 | CS-05991 | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation | 100655-201342 | Attributable | 2024-10-30
Monets Garden | PRO-001082 | CS-05992 | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation | 100655-201375 | Attributable | 2024-10-30
Monk Fryston | PRO-001646 | CS-04555 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101561-203104 | At Monk Fryston 275kV AIS Double Busbar Substation: 1) Facilitate the installation of generator bay (User Works). 2) Replace SGT1 400/275kV Interbus Transformer with a higher rated unit. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04556 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 2029-12-31
Monk Fryston | PRO-001646 | CS-04557 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2029-12-31
Monk Fryston | PRO-001646 | CS-04558 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101561-203106 | On the Ferrybridge – Skelton Grange 2 275kV circuit, reconductor the 1x700mm² section of the circuit with 1x772mm² Warwick conductor or equivalent. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04559 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm² sections with 2x620mm² GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 2029-12-31
Monk Fryston | PRO-001646 | CS-04560 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101561-203108 | On the Eggborough leg of the Eggborough – Stalybridge – Stocksbridge 400kV circuit, hotwire the 4x400mm² sections to an operating temperature of 65°C. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04561 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm² sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570mm² strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570mm²should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04562 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101612-203238 | Installation of a second interbus transformer at High Marnham 400/275kV substation | 2029-12-31
Monk Fryston | PRO-001646 | CS-04563 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2029-12-31
Monk Fryston | PRO-001646 | CS-04564 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101511-202976 | Hotwire the 2x400mm² sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 2029-12-31
Monk Fryston | PRO-001646 | CS-04565 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2029-12-31
Monk Fryston | PRO-001646 | CS-04566 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04567 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04568 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04569 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04570 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04571 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2029-12-31
Monk Fryston | PRO-001646 | CS-04572 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04573 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2029-12-31
Monk Fryston | PRO-001646 | CS-04574 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101610-203236 | Reconductor the 2x500mm² sections of the Carrington – Kearsley circuit with 2x620mm² GAP conductor | 2029-12-31
Monk Fryston | PRO-001646 | CS-04575 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2029-12-31
Monk Fryston | PRO-001646 | CS-04576 | Light Valley Solar Limited | Monk Fryston 275kV Substation | 101611-203237 | Hotwire the 2x400mm² section of the Rochdale - Whitegate 1 275kV circuit to operate at 65°C. | 2029-12-31
Monk Fryston | PRO-002159 | CS-08734 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101899-203890 | Make provision for connection of generator bay at Monk Fryston new 400kV substation. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08735 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101899-204096 | Replace circuit breakers L85 and L45 at Monk Fryston 275kV with 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2031-10-31
Monk Fryston | PRO-002159 | CS-08736 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2031-10-31
Monk Fryston | PRO-002159 | CS-08737 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2031-10-31
Monk Fryston | PRO-002159 | CS-08738 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Monk Fryston | PRO-002159 | CS-08739 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101616-203249 | Reconductor 400kV Drakelow to Hams Hall line from Rubus 500sqmm to Rubus 500sqmm at 90deg C to have summer pre fault rating of 1660MVA | 2031-10-31
Monk Fryston | PRO-002159 | CS-08740 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08741 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm² sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570mm² strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570mm²should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08742 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101511-202976 | Hotwire the 2x400mm² sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 2031-10-31
Monk Fryston | PRO-002159 | CS-08743 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101627-203263 | Cable uprate on the Kearsley - Whitegate 275 kV circuit 1 to achieve a pre fault summer rating of 400 MVA | 2031-10-31
Monk Fryston | PRO-002159 | CS-08744 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101610-203236 | Reconductor the 2x500mm² sections of the Carrington – Kearsley circuit with 2x620mm² GAP conductor | 2031-10-31
Monk Fryston | PRO-002159 | CS-08745 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2031-10-31
Monk Fryston | PRO-002159 | CS-08746 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08747 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08748 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08749 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2031-10-31
Monk Fryston | PRO-002159 | CS-08750 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2031-10-31
Monk Fryston | PRO-002159 | CS-08751 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2031-10-31
Monk Fryston | PRO-002159 | CS-08752 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08753 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2031-10-31
Monk Fryston | PRO-002159 | CS-08754 | ENSO GREEN HOLDINGS X LIMITED | Monk Fryston 400kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm² sections with 2x620mm² GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 2031-10-31
Monk Fryston BESS | PRO-001619 | CS-07341 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 101378-202699 |  | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07342 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07343 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07344 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07345 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07346 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07347 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07348 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07349 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07350 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07351 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07352 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm² sections with 2x620mm² GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07353 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm² sections with 2x620mm² GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 2029-10-31
Monk Fryston BESS | PRO-001619 | CS-07354 | HARMONY MF LIMITED | Monk Fryston 275kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2029-10-31
Monk Fryston Energy Park | PRO-002539 | CS-08866 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 102393-204913 | Make provision for connection of generator bay at new Monk Fryston 400kV substation | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08867 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101899-204096 | Replace circuit breakers L85 and L45 at Monk Fryston 275kV with 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08868 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08869 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08870 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 102208-204431 | Uprating of OHL double cct from 2TW110 - 2TW169 and 4YR1 - 4YR40 which is part of the current Norton-Osbaldwick double circuit but will become the new Osbaldwick-Overton-Thormanby circuit | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08871 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08872 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08873 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08874 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101627-203263 | Cable uprate on the Kearsley - Whitegate 275 kV circuit 1 to achieve a pre fault summer rating of 400 MVA | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08875 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101616-203249 | Reconductor 400kV Drakelow to Hams Hall line from Rubus 500sqmm to Rubus 500sqmm at 90deg C to have summer pre fault rating of 1660MVA | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08876 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101610-203236 | Reconductor the 2x500mm² sections of the Carrington – Kearsley circuit with 2x620mm² GAP conductor | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08877 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm² sections with 2x620mm² GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08878 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101511-202976 | Hotwire the 2x400mm² sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08879 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm² sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570mm² strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570mm²should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08880 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08881 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08882 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08883 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08884 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08885 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08886 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08887 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08888 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08889 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08890 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2035-10-24
Monk Fryston Energy Park | PRO-002539 | CS-08891 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2035-10-24
Monk Fryston SSE | PRO-001627 | CS-04731 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101507-202972 | Make provision for connection of generator bay (User’s Works) at Monk Fryston 275kV double busbar substation. Local works to facilitate extension of Lackenby Operational Tripping Scheme (OTS) at Monk Fryston 275kV double busbar substation. | 2025-10-31
Monk Fryston SSE | PRO-001627 | CS-04732 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101507-202972 | Make provision for connection of generator bay (User’s Works) at Monk Fryston 275kV double busbar substation. Local works to facilitate extension of Lackenby Operational Tripping Scheme (OTS) at Monk Fryston 275kV double busbar substation. | 2025-10-31
Monk Fryston SSE | PRO-001627 | CS-04733 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 2025-10-31
Monk Fryston SSE | PRO-001627 | CS-04734 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101561-203104 | At Monk Fryston 275kV AIS Double Busbar Substation: 1) Facilitate the installation of generator bay (User Works). 2) Replace SGT1 400/275kV Interbus Transformer with a higher rated unit. | 2025-10-31
Monk Fryston SSE | PRO-001627 | CS-07064 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101243-202472 | Extension of the existing OTS at Lackenby 400kV substation for the connection of new generators | 2025-10-31
Montreathmont Moor Forest | PRO-001849 | CS-06885 | Montreathmont Energy Centre Limited | Lunanhead GSP | 132kV Protection Works - Montreathmont Moor Forest | The installation of four new protection bays, two at each of the remote ends between Tealing and Lunanhead. There is also a requirement to install two new VTs on both circuits at Lunanhead. Replacement or modification of the Battery Systems, LVAC Board and Standby Generator at Lunanhead 132/33kV GSP, along with the upgrade of communication links between Lunanhead 132/33kV GSP substation and Tealing 132kV substation. | 2029-10-08
Morecambe Offshore Wind Farm | PRO-001450 | CS-04361 | MORECAMBE OFFSHORE WINDFARM LTD | Penwortham 400kV Substation | 101138-202245 |  | 2029-06-30
Morecambe Offshore Wind Farm | PRO-001450 | CS-04362 | MORECAMBE OFFSHORE WINDFARM LTD | Penwortham 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of a new Pentir - Wylfa OHL. | 2029-06-30
Morecambe Offshore Wind Farm | PRO-001450 | CS-04363 | MORECAMBE OFFSHORE WINDFARM LTD | Penwortham 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2029-06-30
Morecambe Offshore Wind Farm | PRO-001450 | CS-04364 | MORECAMBE OFFSHORE WINDFARM LTD | Penwortham 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 2029-06-30
Morecambe Offshore Wind Farm | PRO-001450 | CS-04365 | MORECAMBE OFFSHORE WINDFARM LTD | Penwortham 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2029-06-30
Moreton Estate | PRO-003920 | CS-09085 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 2037-04-28
Moreton Estate | PRO-003920 | CS-09086 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102057-204228 | Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL feeders | 2037-04-28
Moreton Estate | PRO-003920 | CS-09087 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102674-205359 | Extension of the 400kV busbars at the new Substation for the User’s bay and Extension of the South West OTS to include this Generator | 2037-04-28
Moreton Estate | PRO-003920 | CS-09088 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09089 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09090 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09091 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100480-201051 | Uprate the cable section of the Seabank -Whitson section of the three-ended Seabank -Whitson - Cilfynydd circuit to a pre-fault rating of 1800MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09092 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09093 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101833-203761 | Uprate the Chickerell - Mannington double circuit (NASP Code: A851 and A830) by hotwiring the existing 3 x 700mm² Araucaria conductor at 50°C to 90°C to achieve a pre-fault summer rating of 3160MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09094 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09095 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09096 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09097 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101500-202956 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 2 in order to achieve a summer post fault rating of 2850MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09102 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09103 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490 MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09104 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09105 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101978-204103 | Uprate the Drakelow 400kV -to- Ratcliffe On Soar 400kV circuit #1 (DRAK4-RATS4-1) to summer pre-fault rating 2490MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09106 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09107 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #1 (RATS4-WILE4-1) to summer pre-fault rating 2490 MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09108 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101891-203873 | Uprate the circuit Drakelow 400kV Willington East 400kV to achieve a summer pre-fault rating of 1820MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09109 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09110 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09111 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09112 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09113 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09114 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2037-04-28
Moreton Estate | PRO-003920 | CS-09115 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09116 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 2037-04-28
Moreton Estate | PRO-003920 | CS-09117 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2037-04-28
Moreton Estate | PRO-003920 | CS-09118 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2037-04-28
Moreton Estate | PRO-003920 | CS-09119 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102362-204786 | e circuit running from Leighton Buzzard to Sundon 1 (LEIB4A?SUND4-1) will also be reconductored with 4 x 400mm² conductor rating 2870 MVA, 75˚C for winter intact condition. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09120 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09121 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm² zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09122 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101592-203207 | Reconductor East Claydon – Amersham Main – Iver 400kV double circuit route (55.5km, 2x500mm² Twin Rubus conductor on L2 Towers at 75°C with a summer pre-fault rating of 1466MVA) to 2x620mm² Twin Matthew Conductor at 170°C to achieve a new summer pre-fault rating of 2490 MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09123 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2037-04-28
Moreton Estate | PRO-003920 | CS-09124 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09125 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102108-204302 | Uprate the Iver – Laleham circuit 1 | 2037-04-28
Moreton Estate | PRO-003920 | CS-09126 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102109-204303 | Uprate Iver – West Weybridge circuit. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09127 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102110-204304 | Uprate both Ealing – Laleham circuit 1 and 2 | 2037-04-28
Moreton Estate | PRO-003920 | CS-09128 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09129 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102223-204455 | Installation of a 2750MVA quadbooster on the Feckenham-Minety circuit. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09130 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 102224-204456 | Installation of a 2750MVA quadbooster on the Feckenham-Walham circuit. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09131 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09132 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2037-04-28
Moreton Estate | PRO-003920 | CS-09133 | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2037-04-28
Morgan Offshore Wind Farm | PRO-001594 | CS-05029 | Morgan Offshore Wind Limited | Penwortham 400kV Substation | 102712-205484 Morgan AtV |  | 2029-11-30
Morgan Offshore Wind Farm | PRO-001594 | CS-05030 | Morgan Offshore Wind Limited | Penwortham 400kV Substation | 102712-205519 Morgan AtV |  | 2029-11-30
Morgan Offshore Wind Farm | PRO-001594 | CS-05031 | Morgan Offshore Wind Limited | Penwortham 400kV Substation | 101304-202587 | Infrastructure works necessary to connect 1500MW at the Wylfa 400kV substation, for the Project Elizabeth - Yellow One North R4 connection application | 2029-11-30
Morgan Offshore Wind Farm | PRO-001594 | CS-05032 | Morgan Offshore Wind Limited | Penwortham 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 2029-11-30
Morgan Offshore Wind Farm | PRO-001594 | CS-05033 | Morgan Offshore Wind Limited | Penwortham 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 2029-11-30
Morton Manor PV & BESS Station | PRO-003827 | CS-10850 | IB VOGT UK LTD | High Marnham 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10851 | IB VOGT UK LTD | High Marnham 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10852 | IB VOGT UK LTD | High Marnham 400kV Substation | 100459-201024 2 |  | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10853 | IB VOGT UK LTD | High Marnham 400kV Substation | 100681-201437 (Morton Manor) |  | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10854 | IB VOGT UK LTD | High Marnham 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10855 | IB VOGT UK LTD | High Marnham 400kV Substation | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10857 | IB VOGT UK LTD | High Marnham 400kV Substation | 101873-203846 (Morton Manor) |  | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10858 | IB VOGT UK LTD | High Marnham 400kV Substation | 102056-204226 (Morton Manor) |  | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10860 | IB VOGT UK LTD | High Marnham 400kV Substation | 103376-206829 |  | 2037-10-31
Morton Manor PV & BESS Station | PRO-003827 | CS-10863 | IB VOGT UK LTD | High Marnham 400kV Substation | 102149-204350 |  | 2037-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06714 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | Phoenix 1A Item 1 | The Sole Enabling Works at Tealing 400kV substation shall comprise the installation of 2 x new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at Tealing 400kV substation. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06715 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06716 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06717 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06718 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-025d | North East Reinforcement | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06719 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06720 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06721 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06722 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06723 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06724 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06725 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06726 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 2031-10-31
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06727 | Morven Offshore Wind Limited | Hawthorn Pit 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04990 | Morwind Ltd | Alverdiscott 400kV Substation | 101606-203230 | Infrastructure works at the substation for the generation connection of Morwind 300 Offshore Wind Farm. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04991 | Morwind Ltd | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04992 | Morwind Ltd | Alverdiscott 400kV Substation | 101606-203232 | Extension of the South West OTS to incorporate the Morwind 300 Offshore Wind Farm. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04993 | Morwind Ltd | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04994 | Morwind Ltd | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04995 | Morwind Ltd | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04996 | Morwind Ltd | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04997 | Morwind Ltd | Alverdiscott 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2031-10-31
Morwind 300 | PRO-001787 | CS-04998 | Morwind Ltd | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2031-10-31
Morwind 300 | PRO-001787 | CS-04999 | Morwind Ltd | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2031-10-31
Morwind 300 | PRO-001787 | CS-05000 | Morwind Ltd | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2031-10-31
Morwind 300 | PRO-001787 | CS-05001 | Morwind Ltd | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-10-31
Morwind 300 | PRO-001787 | CS-05002 | Morwind Ltd | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2031-10-31
Morwind 300 | PRO-001787 | CS-05003 | Morwind Ltd | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2031-10-31
Morwind 300 | PRO-001787 | CS-05004 | Morwind Ltd | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Mossmorran Storage BESS | PRO-003738 | CS-09670 | RUFUSIA LTD | Mossmorran Storage BESS 132KV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 2031-10-31
Mossmorran Storage BESS | PRO-003738 | CS-09671 | RUFUSIA LTD | Mossmorran Storage BESS 132KV Substation | SPT-RI-148 | Install an auto-close scheme across the three 275/132kV supergrid transformers at WindyHill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. | 2031-10-31
Mossmorran Storage BESS | PRO-003738 | CS-09672 | RUFUSIA LTD | Mossmorran Storage BESS 132KV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 2031-10-31
Mossmorran Storage BESS | PRO-003738 | CS-09673 | RUFUSIA LTD | Mossmorran Storage BESS 132KV Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 2031-10-31
Mossmorran Storage BESS | PRO-003738 | CS-09674 | RUFUSIA LTD | Mossmorran Storage BESS 132KV Substation | Disconnector - Mossmorran Storage | At Gresham House MOSM BESS 132kV collector substation, install one new 132kV disconnector | 2031-10-31
Mosspark Energy Park | PRO-004879 | CS-11762 | REG Power Developments Limited | Dumfries 132/33kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-05-31
Mosspark Energy Park | PRO-004879 | CS-11763 | REG Power Developments Limited | Dumfries 132/33kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 2029-05-31
Mosspark Energy Park | PRO-004879 | CS-11764 | REG Power Developments Limited | Dumfries 132/33kV | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 2029-05-31
Mosspark Energy Park | PRO-004879 | CS-11765 | REG Power Developments Limited | Dumfries 132/33kV | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 2029-05-31
Mosspark Energy Park | PRO-004879 | CS-11766 | REG Power Developments Limited | Dumfries 132/33kV | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 2029-05-31
Mosspark Energy Park | PRO-004879 | CS-11767 | REG Power Developments Limited | Dumfries 132/33kV | SPT-RI-288 |  | 2029-05-31
Mossy Hill Wind Farm | PRO-000461 | CS-05439 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-152 | Shetland ANM Scheme - ANM System on Shetland to manage flows across 600MW HVDC link (established under SHET-RI-053) from Kergord 132kV substation on Shetland to the Scottish mainland at an HVDC convertor station in the vicinity of Noss Head in Caithness. (SHET-RI-152) | 2028-11-30
Mossy Hill Wind Farm | PRO-000461 | CS-06457 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-143 | Kengord to Gremista GSP Infrastructure - Construct a new 132kV 24km circuit between Kergord substation and Gremista GSP, terminated onto new 132kV feeder bays at Kergord and Gremista. Construct a new Tee point for the connection of a wind farm. (SHET-RI-143) | 2028-11-30
Mossy Hill Wind Farm | PRO-000461 | CS-06458 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | Mossy Hill H1 Works | A 132kV feeder disconnector (103) will be installed at the User’s substation as sole use assets. | 2028-11-30
Mossy Hill Wind Farm | PRO-000461 | CS-09752 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-247 | Mossyhill T-connection - Loop In Loop Out Substation will be constructed to accommodate two projects from the same developer (Under different connection applications). Both these projects are hardly 200m away from each other. (SHET-RI-247) | 2028-11-30
Mount Blairy | PRO-002284 | CS-09081 | GREENTECH PROJECTS HOLDING UK LIMITED | Macduff GSP | SHET-RI-207 | Macduff to Blackhillock 132kV OHL – To Rebuild or Reconductor approx. 37.7km of the overhead line between Blackhillock 132kV Substation and Macduff GSP with a conductor capable of a minimum 120MVA Pre Fault rating | 2027-10-31
Mount Farm | PRO-000989 | CS-04305 | SP Distribution plc | Coylton 132/33kV | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 2026-10-31
Mount Farm | PRO-000989 | CS-05963 | SP Distribution plc | Coylton 132/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2026-10-31
Muaitheabhal Wind Farm | PRO-000272 | CS-05964 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | Muaitheabhal Item 1 | The Relevant Transmission Licensee will install a 13km wood pole overhead line between Muaitheabhal Windfarm and the proposed 132kV switching station near Balallan (to be established under SHET-RI-043), with two 132kV circuit switchers at Muaitheabhal Windfarm and a 132kV circuit breaker at Balallan 132kV switching station. | 2030-12-31
Muaitheabhal Wind Farm | PRO-000272 | CS-05965 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 2030-12-31
Muaitheabhal Wind Farm | PRO-000272 | CS-05966 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 2030-12-31
Muaitheabhal Wind Farm | PRO-000272 | CS-05967 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-043 | Lewis Infrastructure - Build a new 132kV single circuit OHL between Arnish substation, and the Muaitheabhal Tee point. Dismantle the existing 132kV single circuit OHL between Stornoway Tee point, and the Muaitheabhal Tee point. | 2030-12-31
Muaitheabhal Wind Farm | PRO-000272 | CS-12436 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-233 Arnish to Balallan 132 kV second Single Circuit |  | 2030-12-31
Muaitheabhal Wind Farm | PRO-000272 | CS-12437 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-193 |  | 2030-12-31
Muaitheabhal Wind Farm | PRO-000272 | CS-12438 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2030-12-31
Muckraw IDNO BESS | PRO-004338 | CS-10071 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-2084 | LCU2 Eastern B5 400kV reinforcement - Establish an eastern 400kV corridor over the B5 transmission system boundary to accommodate the increasing generation connecting in the north of Scotland, following the East Coast 400kV onshore incremental (ECUP) reinforcement, East Coast Onshore 400kV Phase 2 Reinforcement (TKUP), Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘LCU2’ option submitted to the 2020/21 Network Options Assessment (NOA) process. Is it proposed to uprate an existing single 275kV circuit from Kincardine to Cockenzie, via Currie and Smeaton to 400kV operation | 2032-06-30
Muckraw IDNO BESS | PRO-004338 | CS-10072 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2032-06-30
Muckraw IDNO BESS | PRO-004338 | CS-10073 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-3678 - OHL |  | 2032-06-30
Muckraw IDNO BESS | PRO-004338 | CS-10074 | CARE POWER (MUCKRAW) LIMITED | Muckraw IDNO GSP | SPT-RI-3678 - SS |  | 2032-06-30
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04504 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | Cirrus H1 Enabling Works | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at New Deer 2 400kV substation. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04505 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04506 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04507 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04508 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04509 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04510 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04511 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04512 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04513 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04514 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04515 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04516 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04517 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04518 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04519 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Longside 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Murroch BESS | PRO-003610 | CS-09576 | Apatura Battery Ltd | Strathleven GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-05-22
Murroch BESS | PRO-003610 | CS-09577 | Apatura Battery Ltd | Strathleven GSP | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 2031-05-22
Mwdwl Eithin Energy Park | PRO-001511 | CS-06500 | MOEL CHWA ENERGY PARK LIMITED | Gwyddelwern 400kV Substation | 101212-202434 | 1. Establish a new four bay 400kV double busbar substation1 adjacent to the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. Substation to comprise two feeder bays, a bus coupler bay and a skeletal bay for the User to connect their generator circuit 2. Connect the substation to the Main interconnected system via a turn in of the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. | 2030-06-30
Mwdwl Eithin Energy Park | PRO-001511 | CS-06501 | MOEL CHWA ENERGY PARK LIMITED | Gwyddelwern 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2030-06-30
Mybster 2 Battery Storage | PRO-004479 | CS-10709 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-058 Beauly - Loch Buidhe 275kV OHL Reinforcement |  | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10710 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10711 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-128 Caithness - Peterhead Transmission Reinforcement 2250MW HVDC Link |  | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10712 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-140 - Thurso South 275kV Substation Redevelopment |  | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10713 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-153 Spittal 2 275 kV Substation |  | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10714 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10715 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2034-10-31
Mybster 2 Battery Storage | PRO-004479 | CS-10716 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-200 - Loch Buidhe 400-275kV Substation |  | 2034-10-31
Mybster BESS_Ver2 | PRO-004733 | CS-12587 | ANESCO LIMITED | Mybster 1 GSP | SHET-RI-109 Loch Buidhe - Spittal 132kV Reconductoring |  | 2034-10-31
Myreton BESS | PRO-003050 | CS-11724 | GPC 1039 Ltd | Tealing 132kV Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2028-10-31
Myreton BESS | PRO-003050 | CS-11725 | GPC 1039 Ltd | Tealing 132kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2028-10-31
Myreton BESS | PRO-003050 | CS-11726 | GPC 1039 Ltd | Tealing 132kV Substation | SHET-RI-260 |  | 2028-10-31
Myreton BESS | PRO-003050 | CS-11727 | GPC 1039 Ltd | Tealing 132kV Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2028-10-31
Myreton BESS | PRO-003050 | CS-11728 | GPC 1039 Ltd | Tealing 132kV Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2028-10-31
Nairn BESS | PRO-002533 | CS-08582 | ANESCO LIMITED | Nairn GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2026-10-31
Nairn II BESS | PRO-004774 | CS-11991 | ANESCO LIMITED | Nairn GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2028-10-31
Nairn II BESS | PRO-004774 | CS-11992 | ANESCO LIMITED | Nairn GSP | SHET-RI-174 | Upgrade of Keith SGTs- Replace the existing 132/275kV 240MVA SGTs at Keith 132kV Substation with larger 480/360MVA units | 2028-10-31
Nairn II BESS | PRO-004774 | CS-11993 | ANESCO LIMITED | Nairn GSP | SHET-Ri-259 | Protection upgrades for the 132kV circuit (Beauly-Keith) at Nairn – Replacement of the circuit switchers at Nairn (i.e., 403 and 503) with circuit breakers as well as protection relay replacements/additions at Nairn, Elgin, Beauly, and Keith | 2028-10-31
Nant Aman | PRO-001640 | CS-11826 | NANT AMAN ENERGY PARK LIMITED | Rhigos 400kV Substation | 101505-202969 1 |  | 2030-12-13
Nant Aman | PRO-001640 | CS-11827 | NANT AMAN ENERGY PARK LIMITED | Rhigos 400kV Substation | 103009-206412 |  | 2030-12-13
Nant Ceiment Energy Park | PRO-001610 | CS-06875 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2027-09-11
Nant Ceiment Energy Park | PRO-001610 | CS-06876 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2027-09-11
Nant Ceiment Energy Park | PRO-001610 | CS-06877 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 2027-09-11
Nant Ceiment Energy Park | PRO-001610 | CS-06878 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 2027-09-11
Nant Ceiment Energy Park | PRO-001610 | CS-06879 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2027-09-11
Nant Ceiment Energy Park | PRO-001610 | CS-06880 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2027-09-11
Nant Ceiment Energy Park | PRO-001610 | CS-06881 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 2027-09-11
Nant Y Maen Wind Farm | PRO-001158 | CS-04611 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202058/ 101032-202059/ 101032-202069 | 1. Establish a new 400kV double busbar substation comprising 2 feeder bays, a bus coupler, a MSCDN bay and 4 SGT bays. 2. Establish a new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler,4 SGT bays, an earthing transformer bay and 2 feeder bays. 3. Install a 225MVAr MSCDN at the 400kV substation. 4. Connect an earthing transformer to the 132kV substation 5. Install an earthing transformer at the 132kV substation. 6. Connect the 400kV substation to the 132kV substation via 4 240MVA rated SGT’s 7. Establish a system to generator operational intertripping scheme to perform as per the requirements of the TOF3 8. Connect the 400kV substation to the Legacy – Shrewsbury – Ironbridge and Legacy – Ironbridge circuits via a double tee arrangement. 9. Connect the new Cefn Coch – Lower Frankton 132kV double circuit to Lower Frankton 132kV substation | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04612 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202066 | Establish a new 132kV double circuit route between Lower Frankton and Cefn Coch | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04613 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202060 | 1. Establish a new 4 bay new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler, 4 feeder bays, 2 SVC bays. 2. Installation of 2 SVC’s 3. Connect the Cefn Coch – Lower Frankton 132kV double circuit into Cefn Coch substation EdF (Nant Y Maen) ConsAg v1 Ref: A/NANTY/20/0503-1EN(0) Date: August 2020 4. Connect the new Garn Fach – Cefn Coch 132kV double circuit to Cefn Coch 132kV substation | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04614 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202067 | Establish a new 132kV double circuit route between Cefn Coch and Garn Fach | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04615 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202061 | 1.Establish a new 132kV substation comprising 4 feeder bays and space for User to connect their generator bay. 2. Connect the new Cefn Coch – Garn Fach 132kV double circuit to Garn Fach 132kV substation 3. Connect the new Garn Fach – Nant y Maen 132kV double circuit to Garn Fach 132kV substation | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04616 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202062 | Establish a new 132kV substation comprising 2 feeder bays and space for the User to connect their generator bay | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04617 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202068 | Establish a new 132kV double circuit route between Garn Fach and Nant y Maen. | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04618 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202063 | 1. Establish a new 400kV single switch mesh substation 2. Reconnect the HV side of the existing Shrewsbury SGT to Mesh Corner 2 of the newly established mesh substation. 3. Install a circuit intertripping scheme | 2032-05-01
Nant Y Maen Wind Farm | PRO-001158 | CS-04619 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 2032-05-01
Narachan Wind Farm | PRO-001926 | CS-07704 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2030-04-30
Narachan Wind Farm | PRO-001926 | CS-07705 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2030-04-30
Narachan Wind Farm | PRO-001926 | CS-07706 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2030-04-30
Narachan Wind Farm | PRO-001926 | CS-07707 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2030-04-30
Narachan Wind Farm | PRO-001926 | CS-07708 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2030-04-30
Narachan Wind Farm | PRO-001926 | CS-07709 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2030-04-30
Narachan Wind Farm | PRO-001926 | CS-11709 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2030-04-30
NatPower Allington Green Energy Park | PRO-004387 | CS-10908 | COTTOM TO RYHALL ENERGY LIMITED | Trent Valley South Connection Node B 400kV Substation. | 103562-207066 |  | 2034-10-30
NatPower Allington Green Energy Park | PRO-004387 | CS-10909 | COTTOM TO RYHALL ENERGY LIMITED | Trent Valley South Connection Node B 400kV Substation. | 103563-207068 |  | 2034-10-30
NatPower Allington Green Energy Park | PRO-004387 | CS-10910 | COTTOM TO RYHALL ENERGY LIMITED | Trent Valley South Connection Node B 400kV Substation. | 103563-207075 (OF) |  | 2034-10-30
NatPower Connah Quay Green Energy Park | PRO-004797 | CS-11331 | CONNAHS QUAY ENERGY LIMITED | Cheshire Connection Node B 400kV Substation | 102565-205171 2 |  | 2037-10-30
NatPower Connah Quay Green Energy Park | PRO-004797 | CS-11332 | CONNAHS QUAY ENERGY LIMITED | Cheshire Connection Node B 400kV Substation | 104063-207993 |  | 2037-10-30
NatPower Hawthorn Pit Green Energy Park | PRO-004820 | CS-11114 | NP SPV 29 LIMITED | Wearside Connection Node B 400kV Substation | 103299-206738 (II) |  | 2035-10-30
NatPower Hawthorn Pit Green Energy Park | PRO-004820 | CS-11115 | NP SPV 29 LIMITED | Wearside Connection Node B 400kV Substation | 103938-207810 |  | 2035-10-30
NatPower Immingham Green Energy Park | PRO-004566 | CS-10913 | NATPOWER MARINE UK LIMITED | Trent Valley North Connection Node F 400kV Substation | 103626-207161 |  | 2034-10-30
NatPower Immingham Green Energy Park | PRO-004566 | CS-10914 | NATPOWER MARINE UK LIMITED | Trent Valley North Connection Node F 400kV Substation | 103627-207162 |  | 2034-10-30
NatPower Immingham Green Energy Park | PRO-004566 | CS-10915 | NATPOWER MARINE UK LIMITED | Trent Valley North Connection Node F 400kV Substation | 103627-207249 |  | 2034-10-30
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11087 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11088 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11089 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11090 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11091 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-025d | North East Reinforcement | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11092 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11093 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11094 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11095 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11096 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11097 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11098 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11099 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11100 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-180 Second 400kV Peterhead Substation |  | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11101 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHET-RI-199) | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11102 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
NatPower Kintore2 Green Energy Park | PRO-004860 | CS-11103 | NP SPV 41 LIMITED | NATPOWER KINTORE 2 GREEN ENERGY PARK 275KV SUBSTATION | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Nautilus | PRO-000976 | CS-08218 | National Grid Interconnector Holdings Limited | Wallend 400kV Substation | 033694-033694 | Construction of the new Grain West 400 kV GIS double busbar substation consisting of feeder bays, a bus coupler bay Section Breaker and a User bay. | 2029-10-31
Nautilus | PRO-000976 | CS-08219 | National Grid Interconnector Holdings Limited | Wallend 400kV Substation | 101999-204134 | Turn in of the Grain to Kingsnorth 400 kV circuit - Reconductor OHL circuits and reinforce cable circuits to achieve 2350 MVA pre-fault and 3200 post fault rating. | 2029-10-31
Nautilus | PRO-000976 | CS-08221 | National Grid Interconnector Holdings Limited | Wallend 400kV Substation | 033694-201373 | Turn in of the Grain to Tilbury 400 kV circuit - Reconductor OHL circuits and reinforce cable circuits to achieve 2350 MVA pre-fault and 3200 post fault rating. | 2029-10-31
Nautilus | PRO-000976 | CS-08516 | National Grid Interconnector Holdings Limited | Wallend 400kV Substation | 100379-201163 | Make provision for the connection of the Users second bay at Grain West 400kV GIS Substation. | 2029-10-31
NAVAS BESS | PRO-005946 | CS-12542 | OPDE UK LIMITED | Lairg GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2033-10-31
NAVAS BESS | PRO-005946 | CS-12543 | OPDE UK LIMITED | Lairg GSP | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
NAVAS BESS | PRO-005946 | CS-12544 | OPDE UK LIMITED | Lairg GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2033-10-31
NAVAS BESS | PRO-005946 | CS-12545 | OPDE UK LIMITED | Lairg GSP | SHET-RI-230 | Loch Buidhe – Dalchork 132 kV Reinforcement- Construction of approximately 17 km 132 kV double circuit between Dalchork - Loch Buidhe substations with same rating OHLs as of existing double circuit i.e. 414 MVA post fault summer ratings. Scope also includes construction of two feeder bays each at Dalchork substation and Loch Buidhe substation | 2033-10-31
NAVAS BESS | PRO-005946 | CS-12546 | OPDE UK LIMITED | Lairg GSP | Enabling Works - Navas BESS | Installation of a 120MVA 132kV/33kV grid transformer (GT1), 33kV metering circuit breaker (1T0) and 33kV disconnector (1T7), on a suitable level platform at the new Lairg 2 132kV/33kV GSP substation compound (also to be provided as part of TCA Works). The 33kV metering circuit breaker and 33kV disconnector will be owned and operated by the Relevant Transmission Licensee. The User’s boundary between the Relevant Transmission Licensee and the user (the host Distribution Network Operator). | 2033-10-31
Necton Greener Grid Park | PRO-002562 | CS-09488 | Necton Grid Solutions Limited | Necton 400kV Substation | 033804-033804 | At Necton 400kV substation: extend the substation by 5 bays; 1 main and 1 reserve section bay, 1 bus coupler bay and 2 feeder bays | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09489 | Necton Grid Solutions Limited | Necton 400kV Substation | 033804-201295 | At Necton 400kV substation: double turn in of the existing Walpole – Norwich Main OHL circuits | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09490 | Necton Grid Solutions Limited | Necton 400kV Substation | 100926-201852 | At Necton 400kV Substation: Extend the substation by 4 bays; A Main & Reserve Bus Section Bay, One Feeder Bay and one OFTO Bay. Transfer a circuit into the extended busbar section's feeder bay. Extension of the existing East Anglia Operational intertripping scheme. | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09491 | Necton Grid Solutions Limited | Necton 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09492 | Necton Grid Solutions Limited | Necton 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09493 | Necton Grid Solutions Limited | Necton 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09494 | Necton Grid Solutions Limited | Necton 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09495 | Necton Grid Solutions Limited | Necton 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09496 | Necton Grid Solutions Limited | Necton 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09497 | Necton Grid Solutions Limited | Necton 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09498 | Necton Grid Solutions Limited | Necton 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09499 | Necton Grid Solutions Limited | Necton 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09500 | Necton Grid Solutions Limited | Necton 400kV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09501 | Necton Grid Solutions Limited | Necton 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09502 | Necton Grid Solutions Limited | Necton 400kV Substation | 100875-202041 | At Tilbury 400kV Substation: Extension of busbars for the provision of 2 feeder bays for the CLAC-TILB OHL | 2026-10-31
Necton Greener Grid Park | PRO-002562 | CS-09503 | Necton Grid Solutions Limited | Necton 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 2026-10-31
Neilston 400kV Greener Grid Park | PRO-001419 | CS-07248 | Statkraft UK Ltd | Neilston 400kV Substation | Neilston 2 400kV H1 Works | Hunterston East – Neilston 400kV Reinforcements - Modification of the Hunterston East - Devol Moor 400kV circuit to become the Hunterston East - Neilston 400kV double circuit OHL and development of a new 400/275kV supergrid transformer (SGT4) at Neilston 400kV substation. (NOA HNNO) | 2027-05-17
Neilston 400kV Greener Grid Park | PRO-001419 | CS-07249 | Statkraft UK Ltd | Neilston 400kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2027-05-17
Neilston Synchronous Compensation | PRO-001405 | CS-04550 | NEILSTON GRID SERVICES LIMITED | Neilston 400kV Substation | Hunterston Syn Comp (WP) Reinforcement Works | Hunterston East – Hunterston East – Neilston 400kV Reinforcements, protection and control, civils | 2025-06-12
Net Zero Teesside Power Project | PRO-001400 | CS-06460 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 101163-202347 | Install two single switch mesh busbar extensions and (if required (subject to detailed design)) replacement of the existing short bar section at Tod Point 275kV substation. Install two new disconnectors on the new busbar extensions at Tod Point 275kV substation for the User’s connection. | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06461 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 100158-200400 | Extension of the N-1-D Lackenby/Greystones Operational Tripping Scheme (new communications links to a marshalling kiosk at Tod Point 275kV substation) | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06462 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | CTP2 | Additional Power Control Technology along Creyke Beck – Thornton 1 (A319) 400kV Circuit | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06463 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 101164- 202350 | At Lackenby 275kV Substation, replacements of circuit breakers H30, H20 and H10 | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06464 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06465 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | TDP2 | Additional Power Control Technology along the Drax – Thornton 1 (A34C) 400kV Circuit | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06466 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 020640-020640 | Reconductor the 2x500mm² sections of the Norton – Osbaldwick 1 400kV circuit with 2x700mm² conductor strung for operation at 90°C | 2027-07-30
Net Zero Teesside Power Project | PRO-001400 | CS-06467 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2027-07-30
Nether Pitforthie BESS | PRO-003226 | CS-10598 | Opdenergy UK 14 Limited | Fiddes GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-10-31
Nether Pitforthie BESS | PRO-003226 | CS-10599 | Opdenergy UK 14 Limited | Fiddes GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-10-31
Netherton Hub Bess | PRO-004753 | CS-11300 | Field Netherton Ltd | Longside 400kV Substation | SHET-RI-180 Second 400kV Peterhead Substation |  | 2033-10-31
Netherton Hub Bess | PRO-004753 | CS-11302 | Field Netherton Ltd | Longside 400kV Substation | SHET-RI-256 Peterhead 2 400kV Busbar Extension |  | 2033-10-31
NeuConnect Interconnector | PRO-001288 | CS-05970 | Neuconnect Britain Ltd | Grain West 400kV Substation | 33694 | Construction of a new double busbar 400kV substation with two feeder bays, coupler bay and provisions for the connection of the User’s bay. Double tee connection of the new substation to the Grain - Tilbury/Grain - Kingsnorth double over head line circuit and associated works. | 2026-08-01
Newarthill Energy Park | PRO-002532 | CS-10717 | Geocore (Newarthill) Ltd | Newarthill Energy Park 275kV Substation | SPT-RI-3739A SS |  | 2027-10-28
Newchurch | PRO-002056 | CS-07537 | SSE Newchurch Solar Limited | Newchurch 400kV Substation | 101901-203894 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single turn-in connection to Newchurch via the Dungeness – Sellindge 2 overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure Construction of 400kV Busbar to accommodate the OHL Turn-In connection and the Users Generator Bay. | 2031-10-04
Newchurch | PRO-002056 | CS-07538 | SSE Newchurch Solar Limited | Newchurch 400kV Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 2031-10-04
Newchurch | PRO-002056 | CS-07539 | SSE Newchurch Solar Limited | Newchurch 400kV Substation | 101701-203401 | 1. Uprate the Dungeness – Ninfield OHL circuits to increase capacity. | 2031-10-04
Newchurch | PRO-002056 | CS-07540 | SSE Newchurch Solar Limited | Newchurch 400kV Substation | 101701-203403 | Uprate the Dungeness – Sellindge 1& 2 OHL circuits to increase capacity | 2031-10-04
Newchurch | PRO-002056 | CS-07541 | SSE Newchurch Solar Limited | Newchurch 400kV Substation | 101749-203473 | Investigation into Sellindge X305 and X405 infrastructure de-rating, replacing if necessary, to allow higher fault level ratings at Sellindge 400kV (a milestone has been added for this investigation in the Appendix J of this agreement). | 2031-10-04
Newhouse Energy Storage | PRO-001817 | CS-07068 | NEWHOUSE ENERGY STORAGE LIMITED | Burghmuir GSP | SHET-RI-121 | Charleston - Abernethy 132kv reconductoring; approx 25km of 132 kv ohl between abernrethy substation and Charleston. | 2028-10-31
Newlands Hill Wind Energy Hub | PRO-002549 | CS-08588 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2030-04-03
Newlands Hill Wind Energy Hub | PRO-002549 | CS-08589 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2030-04-03
Newlands Hill Wind Energy Hub | PRO-002549 | CS-08590 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | SPT-RI-204 | Wishaw-Smeaton-Torness-Eccles Overload Protection Scheme -An overload protection scheme is proposed to be installed within the Wishaw – Smeaton – Torness – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following system outage conditions as specified in Appendix F of the Bilateral Connection Agreement - | 2030-04-03
Newlands Hill Wind Energy Hub | PRO-002549 | CS-08591 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | Newlands Hill | 1. Installation of a new 400kV double busbar bay at the Fallago Rig substation including a 400kV circuit breaker and associated disconnectors. 2. Installation of a 400/132kV 240MVA transformer at Fallago Rig substation. 3. Installation of a 132kV circuit breaker and associated disconnectors at Fallago Rig substation. 4. Installation of a new 132kV cable and OHL circuit between Fallago Rig and the User’s site. 5. Installation of a 132kV line disconnector at the Newlands Hill Wind Energy Hub site. 6. Installation of two 132kV transformer disconnectors at Newlands Hill Wind Energy Hub site. 7. 400kV GIS substation in Torness Area - A new 400kV double busbar substation, utilising | 2030-04-03
Newtack Farm | PRO-004081 | CS-11809 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Newtack Farm | PRO-004081 | CS-11810 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Newtack Farm | PRO-004081 | CS-11811 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Newtack Farm | PRO-004081 | CS-11812 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Newtack Farm | PRO-004081 | CS-11813 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Newtack Farm | PRO-004081 | CS-11814 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Newtack Farm | PRO-004081 | CS-11815 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Newtack Farm | PRO-004081 | CS-11816 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Newtack Farm | PRO-004081 | CS-11817 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Newtack Farm | PRO-004081 | CS-11818 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Newtack Farm | PRO-004081 | CS-11819 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Newtack Farm | PRO-004081 | CS-11820 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Newtack Farm | PRO-004081 | CS-11821 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHET-RI-199) | 2033-10-31
Newtack Farm | PRO-004081 | CS-11822 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Newtack Farm | PRO-004081 | CS-11823 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Newton of Park BESS 2 | PRO-003562 | CS-10593 | Opdenergy UK 16 Limited | Nairn GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 2028-01-31
Newton of Park BESS 2 | PRO-003562 | CS-10594 | Opdenergy UK 16 Limited | Nairn GSP | SHET-Ri-259 | Protection upgrades for the 132kV circuit (Beauly-Keith) at Nairn – Replacement of the circuit switchers at Nairn (i.e., 403 and 503) with circuit breakers as well as protection relay replacements/additions at Nairn, Elgin, Beauly, and Keith | 2028-01-31
Newton of Park BESS 2 | PRO-003562 | CS-10595 | Opdenergy UK 16 Limited | Nairn GSP | Newton of Park BESS 2 A1 Switch Bay |  | 2028-01-31
Newton of Park BESS 2 | PRO-003562 | CS-10596 | Opdenergy UK 16 Limited | Nairn GSP | Newton of Park Bess 2 A1 Transformer |  | 2028-01-31
Newton of Park BESS 2 | PRO-003562 | CS-10597 | Opdenergy UK 16 Limited | Nairn GSP | Newton of Park BESS H1 |  | 2028-01-31
Ninfield | PRO-001215 | CS-05971 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-11642 | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating. | 2023-12-08
Ninfield | PRO-001215 | CS-05972 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-21588 | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity. | 2023-12-08
Ninfield | PRO-001215 | CS-05973 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-30967 & NGET-RI-30968 | Construction of a new Sellindge double busbar bypass 400kV Substation. | 2023-12-08
Ninfield | PRO-001215 | CS-05974 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works. | 2023-12-08
Ninfield | PRO-003408 | CS-10276 | Ninfield 10 Renewables Limited | Sussex and Romney Connection Node A 400kV Substation | 102060-204231 (1) |  | 2030-10-31
Ninfield | PRO-003408 | CS-10277 | Ninfield 10 Renewables Limited | Sussex and Romney Connection Node A 400kV Substation | 103452-206919 |  | 2030-10-31
Ninfield Greener Grid Park | PRO-001756 | CS-09680 | Ninfield Grid Solutions Limited | Ninfield 400kV Substation | 101572- 203150 | Installation of a new disconnector at a tee point on the HV side of Ninfield SGT4 | 2027-04-30
Ninfield Greener Grid Park | PRO-001756 | CS-09681 | Ninfield Grid Solutions Limited | Ninfield 400kV Substation | 101572-206183 | Extension of Sellindge OTS to include the User’s Battery Energy Storage system connection | 2027-04-30
Ninfield Greener Grid Park | PRO-001756 | CS-09682 | Ninfield Grid Solutions Limited | Ninfield 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 & 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 2027-04-30
Ninfield Greener Grid Park | PRO-001756 | CS-09683 | Ninfield Grid Solutions Limited | Ninfield 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2027-04-30
Norfolk Boreas | PRO-000399 | CS-05493 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05494 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20315L | At Bramford 400kV substation carry out OHL and cable works to enable the turn in of the Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05495 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20315S | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05496 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05497 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20834-3 | Install two switchable series reactors on the Tilbury and Coryton South feeder circuits at Rayleigh main. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05498 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 21847 | Building a new double circuit overhead line between the Bramford, Twinstead Tee and Pelham substation strung with 3x 700mm² AAAC conductor at 750°C (28km), connecting into the new Bramford 400kV GIS substation. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Twinstead Tee -Pelham double circuit and Bramford – Twinstead Tee – Braintree – Rayleigh Main double circuit. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05499 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 30637-1 | Build a new five bay 400kV AIS double busbar substation in the Lowestoft area, including two skeleton generator feeder bays, two feeder bays ad a bus coupler and additional works to enable the connection of 800MW. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05500 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 30637-2 | Tee in the Norwich to Bramford circuit to the new Lowestoft substation. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-05501 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 30641-1 | Cable sealing end work for the new OHL. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-11053 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-11054 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 033804-033804 | At Necton 400kV substation: extend the substation by 5 bays; 1 main and 1 reserve section bay, 1 bus coupler bay and 2 feeder bays | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-11055 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 033804-201295 | At Necton 400kV substation: double turn in of the existing Walpole – Norwich Main OHL circuits | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-11056 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 100926-201852 | At Necton 400kV Substation: Extend the substation by 4 bays; A Main & Reserve Bus Section Bay, One Feeder Bay and one OFTO Bay. Transfer a circuit into the extended busbar section's feeder bay. Extension of the existing East Anglia Operational intertripping scheme. | 2029-10-01
Norfolk Boreas | PRO-000399 | CS-11057 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120 and X320 Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2029-10-01
Norfolk001 | PRO-001996 | CS-08267 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 101872-203844 | Extension of busbar to accommodate new generator bay at Walpole 400kV Substation | 2031-11-30
Norfolk001 | PRO-001996 | CS-08268 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 101872-203845 | Replace circuit breakers X110, X510 with higher ratings fault capability at Walpole 400kV Substation Replace circuit breakers X305, X705 with higher ratings fault capability at Walpole 400kV Substation | 2031-11-30
Norfolk001 | PRO-001996 | CS-08269 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2031-11-30
Norfolk001 | PRO-001996 | CS-08270 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2031-11-30
Norfolk001 | PRO-001996 | CS-08271 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2031-11-30
Norfolk001 | PRO-001996 | CS-08272 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2031-11-30
Norfolk001 | PRO-001996 | CS-08273 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 2031-11-30
Norfolk001 | PRO-001996 | CS-08274 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 101786-203723 | Reconductor BRIMSDOWN-HACKNEY4-1 (BRIM4C-HACK4-1) & BRIMSDOWN-HACKNEY4-2 (BRIM4D-HACK4-2) 400 kV circuit to achieve a higher MVA rating winter pre-fault. | 2031-11-30
Norfolk001 | PRO-001996 | CS-08275 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2031-11-30
Norfolk001 | PRO-001996 | CS-08276 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2031-11-30
Norfolk001 | PRO-001996 | CS-08277 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2031-11-30
Norfolk001 | PRO-001996 | CS-08278 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2031-11-30
Norfolk001 | PRO-001996 | CS-08279 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 2031-11-30
Norfolk001 | PRO-001996 | CS-08280 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 100875-202041 | At Tilbury 400kV Substation: Extension of busbars for the provision of 2 feeder bays for the CLAC-TILB OHL | 2031-11-30
Norfolk001 | PRO-001996 | CS-08281 | EPL NEWCO1 LIMITED | Walpole 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 2031-11-30
North East Offshore Wind Farm | PRO-001436 | CS-06774 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06775 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-025d | North East Reinforcement | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06776 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06777 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06778 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06779 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06780 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06781 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06782 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06783 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06784 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06785 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06786 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06787 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06788 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2031-03-31
North East Offshore Wind Farm | PRO-001436 | CS-06789 | CALEDONIA OFFSHORE WIND FARM LIMITED | Greens 400kV Substation | NEOWF Enabling Works | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at New Deer 2 400kV substation. | 2031-03-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06309 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100874-201758 | Build a new 11 bay East Anglia Coastal 400 kV double busbar substation – 2off busbar couplers, 1 Main & Reserve section, 8 feeder bays | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06310 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100532-201151 | At East Anglia Coastal 400kV Substation: Single Bay Extension to facilitate 100532-201151 the User’s connection. | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06311 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06312 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100875-201762 | Build a second new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06313 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100874-201760 | Build a new 400 kV double circuit between Sizewell 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter postfault. Extension of Sizewell 400 kV substation to accommodate 2 feeders from East Anglia Coastal 400 kV. | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06314 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100879-201769 | Install 2-off 225 Mvar MSCs at Bramford 400 kV substation.Extension of Bramford 400 kV substation to accommodate the new MSCs. | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06315 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06316 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation |  |  | 2030-10-31
North Falls Offshore Wind Farm | PRO-000451 | CS-06317 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2030-10-31
North Killingholme Power Project | PRO-001038 | CS-05975 | UNIPER UK LIMITED | Killingholme 400kV Substation | NGET-RI-30544 | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 2030-09-30
North Killingholme Power Project | PRO-001038 | CS-05976 | UNIPER UK LIMITED | Killingholme 400kV Substation | NGET-RI-21406S | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme 400kV Substation. Extension to the existing South Humber Bank Operational Tripping Scheme | 2030-09-30
North Killingholme Power Project | PRO-001038 | CS-05977 | UNIPER UK LIMITED | Killingholme 400kV Substation | NGET-RI-32278SI | Extend the busbar and a GIS skeletal bay and the associated foundation to provide 490MW CCGT connection. | 2030-09-30
North Lanrigg Battery Storage | PRO-002671 | CS-09182 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Newarthill line works | Replace / reconfigure the downleads from the terminal tower into Newarthill 275kV substation and rebuild the line entry on the Wishaw-Newarthill double circuit overhead line route (XR Route). | 2028-10-30
North Lanrigg Battery Storage | PRO-002671 | CS-09183 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Newarthill Substation Works | Tee off the 275kV busbars at Newarthill 275kV Substation and install a 275kV line disconnector and new “S50” 275kV circuit breaker. | 2028-10-30
North Lanrigg Battery Storage | PRO-002671 | CS-09184 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Line Disconnector - North Lanrigg | Install a 275kV line disconnector on the cable side of the User’s connection | 2028-10-30
North Lanrigg Battery Storage | PRO-002671 | CS-09185 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | 275kV Circuit - North Lanrigg | Install a 275kV cable circuit to the User’s site. As part of the desktop exercise the cable circuit length is circa 2km | 2028-10-30
North Lanrigg Battery Storage | PRO-002671 | CS-09186 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Line Disconnector (User SS) - North Lanrigg | Install a 275kV line disconnector at the North Lanrigg 275kV substation | 2028-10-30
North Lowther Energy Initiative | PRO-000344 | CS-05981 | NLEI LTD | NLEI Windfarm 132/33kV substation | NLEI H1 Sole enabling works | 3. Installation of two 132kV line isolators at NLEI Wind Farm. 2. Installation of approximately 14km overhead line between Elvanfoot 132kV substation and NLEI wind farm. 1. Installation of a 132kV circuit breaker at Elvanfoot substation with transformer and line disconnectors Protection and control modifications as required Associated civil works Miscellaneous and Minor works | 2031-04-30
North Lowther Energy Initiative | PRO-000344 | CS-05982 | NLEI LTD | NLEI Windfarm 132/33kV substation | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 2031-04-30
North Mains Battery Storage Park | PRO-001659 | CS-04478 | SUTTIESIDE BATTERY LIMITED | Lunanhead GSP | North Mains Battery Storage Park H1 Works item 2 | 2. Replacement or modification of the Battery Systems, LVAC Board and Standby Generator at Lunanhead 132/33kV GSP, along with the upgrade of communication links between Lunanhead 132/33kV GSP substation and Tealing 132kV substation. | 2025-10-31
North Mains Battery Storage Park | PRO-001659 | CS-04479 | SUTTIESIDE BATTERY LIMITED | Lunanhead GSP | North Mains Battery Storage Park H1 Works item 1 | 1. The installation of four new protection bays, two at each of the remote ends between Tealing substation and Lunanhead substation. There is also a requirement to install two new VTs on both circuits at Lunanhead substation. | 2025-10-31
North Mains Battery Storage Park | PRO-001659 | CS-04480 | SUTTIESIDE BATTERY LIMITED | Lunanhead GSP | North Mains Battery Storage Park H1 Works item 3 | 3. An intertrip is required for the loss of one of the Grid Transformers at Lunanhead 132/33kV GSP. a. These signals shall be provided by the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom from the signals described below. b. Provision of status signals are required for the following: i. 1TO and 2TO 33kV circuit breakers at Lunanhead GSP. ii. 1T7 and 2T7 33kV disconnectors at Lunanhead GSP. iii. 115 and 215 132kV circuit breakers at Lunanhead GSP. | 2025-10-31
NorthConnect | PRO-001285 | CS-06299 | NORTHCONNECT LIMITED | Peterhead 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2030-03-01
NorthFleet 2 BESS | PRO-002322 | CS-08574 | CSE41 LIMITED | NorthFleet 400kV Substation | 102186-204403 | 1. Extension of the GIS building and busbars at Northfleet 400kV Substation to accommodate User bay. 2. Database updates to capture additional signals from customer populated bay. 3. SAP commissioning resource for bay population. | 2028-10-31
NorthFleet Tertiary | PRO-002038 | CS-08575 | CSE29 LIMITED | Northfleet East 400kV Substation | 101918-203917 | 1. Make connections on the SGT 4. 2. Condition assessment of 13kV cable and other assets to confirm suitability for reuse. 3. Install earthing transformer on 13kV Tertiary connection. 4. Install 13kV Cable (if required) from 13kV Tertiary connection to the 13kV Disconnector. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2028-06-30
Norton | PRO-001537 | CS-06903 | BAYWA R.E. UK LIMITED | Norton 275kV Substation | 101241 -202468 | 1. Extend the Norton site as required to facilitate the transmission works. 2. Install a tertiary cable box or bushings on the SGT 2. 3. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV disconnector at the 13kV side connecting the tertiary winding to the Connection Assets. | 2029-06-01
Norton | PRO-001537 | CS-12039 | BAYWA R.E. UK LIMITED | Norton 275kV Substation | 101241-202562 |  | 2029-06-01
Norton GSP (NE) | PRO-002964 | CS-11841 | NORTHERN POWERGRID (NORTHEAST) PLC | NORTON 132KV SUBSTATION | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2039-10-30
Norton GSP (NE) | PRO-002964 | CS-11842 | NORTHERN POWERGRID (NORTHEAST) PLC | NORTON 132KV SUBSTATION | 102090-204286 |  | 2039-10-30
Norton GSP (NE) | PRO-002964 | CS-11843 | NORTHERN POWERGRID (NORTHEAST) PLC | NORTON 132KV SUBSTATION | 102095-204288 |  | 2039-10-30
Norton GSP (NE) | PRO-002964 | CS-12424 | NORTHERN POWERGRID (NORTHEAST) PLC | NORTON 132KV SUBSTATION | 102090-204281 |  | 2039-10-30
Norton PV and BESS | PRO-001437 | CS-04647 | Darlington Solar 1 Limited | Norton 400kV Substation | 101158-202333 | 1. Extend the Norton site as required to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 1 3. Install a 13kV cable (if required) from the tertiary cable box or bushings to the earthing transformer 4. Install an earthing transformer 5. Install a 13kV disconnector at the 13kV side connecting the tertiary winding to the User’s Assets. | 2027-10-31
Norton Solar Farm | PRO-001875 | CS-07274 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07275 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07276 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07278 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101710-203413 | Busbar extension at Norton East 400kV to provide required space for connection of a new high impedance 240 MW 400/132 kV Supergrid Transformers (SGT) | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07279 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07280 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101712-203416 | Uprating/Replacement of the following CB at Stella West 275 kV substation: H10, H20, H40, H50, H90, S10 and W10 | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07281 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07282 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100035-200062 | Uprating/Replacement of the following Circuit Breakers at Spennymoor 132kV substation: 120 and 130 | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07283 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101714-203420 | Installation of 2x200 MVAr MSC at the new High Marnham 400 kV double busbar substation | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07284 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07285 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07286 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07287 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07288 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07289 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07290 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07291 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07292 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07293 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07294 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07295 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07296 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101667-203320 | Installation of 2x200 MVAr MSC at Cottam 400kV substation | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07297 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07298 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07299 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101717-203426 | Installation of 2x200 MVAr MSC at Thorpe Marsh 400 kV substation | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07300 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07301 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101719-203428 | Uprate the Norton leg of the new Norton- Osbaldwick/ Poppleton 400 kV circuits to provide a pre-fault summer rating of 2350 MVA | 2031-10-31
Norton Solar Farm | PRO-001875 | CS-07302 | RWE Renewables UK Solar and Storage Limited | Norton GSP | 101718-203427 | Installation of 2x200MVAr MSC at West Burton 400kV substation | 2031-10-31
Norwich | PRO-001077 | CS-05277 | PIVOTED POWER LLP | Norwich Main 400kV Substation | 100549-201125 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 72.5kV, 40kA Disconnecting Circuit Breaker (DCB) at 13kV side connecting Tertiary to Connection Assets for User’s connection. | 2025-12-18
Norwich | PRO-001077 | CS-05278 | PIVOTED POWER LLP | Norwich Main 400kV Substation | 033804-201295 | At Necton 400kV substation: double turn in of the existing Walpole – Norwich Main OHL circuits | 2025-12-18
Norwich | PRO-001077 | CS-12087 | PIVOTED POWER LLP | Norwich Main 400kV Substation | 100549-201696 One Off |  | 2025-12-18
Norwich | PRO-001077 | CS-12088 | PIVOTED POWER LLP | Norwich Main 400kV Substation | 104420-208537 |  | 2025-12-18
Norwich 100MW BESS | PRO-002126 | CS-08112 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 102187-204404 | 1. Undertake substation database change to accommodate the tee connection of Norwich 100MW BESS 2. Protection and control modification as a result of Norwich 100MW BESS | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08113 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08114 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08115 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08116 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08117 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101975-204100 | 1. At Kings Lynn 400kV: Ensure circuit break X130 to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08118 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08119 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08120 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08121 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08122 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08123 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08124 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08125 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08126 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08127 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08128 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08129 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08130 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08131 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08132 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08133 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08134 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08135 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 2031-10-31
Norwich 100MW BESS | PRO-002126 | CS-08136 | FLEXION ENERGY SPV 2 LTD | Norwich Main 132kV | 101883-203859 | Uprating of the Coryton South – Rayleigh Main (A68A) 400kV circuit cables to achieve 3002MVA pre-fault summer rating | 2031-10-31
Norwich Green Energy Centre | PRO-001771 | CS-05314 | Norwich NG Limited | Norwich Main 400kW Substation | 101343-202663 | Extension of MBB4 and RBB4 bus of Norwich Main 400kV substation on west side to accommodate the user’s connection. | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05315 | Norwich NG Limited | Norwich Main 400kW Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05316 | Norwich NG Limited | Norwich Main 400kW Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120 and X320 Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05317 | Norwich NG Limited | Norwich Main 400kW Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05319 | Norwich NG Limited | Norwich Main 400kW Substation | 100881-201773 | Install two 225 Mvar MSCs at Norwich Main 400 kV substation. Extension of Norwich Main 400 kV substation to accommodate the new MSCs. | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05320 | Norwich NG Limited | Norwich Main 400kW Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05321 | Norwich NG Limited | Norwich Main 400kW Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05322 | Norwich NG Limited | Norwich Main 400kW Substation | 032452-203187 | Extension of the existing 400kV substation for the construction of fully populated main and reserve bus section bays with circuit breakers, one new bus coupler bay and one new feeder bay to accommodate transfer of the Norwich Main – Bramford 1 feeder circuit | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05323 | Norwich NG Limited | Norwich Main 400kW Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05324 | Norwich NG Limited | Norwich Main 400kW Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05325 | Norwich NG Limited | Norwich Main 400kW Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05326 | Norwich NG Limited | Norwich Main 400kW Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05329 | Norwich NG Limited | Norwich Main 400kW Substation | 021071-021073 | Loop into the new Kings Lynn B 400kV substation with the near side Norwich-Walpole 400kV circuit to form a Walpole- Kings Lynn B and Kings Lynn - Necton - Norwich Main circuit connection. Construction of a new 2.7km double circuit | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05331 | Norwich NG Limited | Norwich Main 400kW Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 2031-04-30
Norwich Green Energy Centre | PRO-001771 | CS-05332 | Norwich NG Limited | Norwich Main 400kW Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2031-04-30
Norwich Main BESS | PRO-003894 | CS-12070 | Tasway Energy Park Limited | North Anglia Connection Node A 400kV | 020340-020340 (Long Stratton) |  | 2032-10-31
Norwich Main BESS | PRO-003894 | CS-12071 | Tasway Energy Park Limited | North Anglia Connection Node A 400kV | 102188-204406 (Long Statton) |  | 2032-10-31
Norwich Main BESS | PRO-003894 | CS-12072 | Tasway Energy Park Limited | North Anglia Connection Node A 400kV | 102547-205150 (Long Stratton) |  | 2032-10-31
Norwich Main BESS | PRO-003894 | CS-12073 | Tasway Energy Park Limited | North Anglia Connection Node A 400kV | 104446-208567 |  | 2032-10-31
Norwich Main BESS | PRO-003894 | CS-12074 | Tasway Energy Park Limited | North Anglia Connection Node A 400kV | 103998-207894 (4) |  | 2032-10-31
Norwich Yare | PRO-001076 | CS-12137 | ASHGREEN ENERGYFARM LIMITED | Norwich GSP | 104419-208536 |  | 2025-12-18
Norwich Yare | PRO-001076 | CS-12138 | ASHGREEN ENERGYFARM LIMITED | Norwich GSP | 100311-200739 Yare |  | 2025-12-18
Norwich Yare | PRO-001076 | CS-12139 | ASHGREEN ENERGYFARM LIMITED | Norwich GSP | 100311-201303 Yare |  | 2025-12-18
Nursling GSP | PRO-002143 | CS-12692 | Southern Electric Power Distribution Plc | Nursling GSP | 101387-202717 SEPD |  | 2037-10-31
Nursling GSP | PRO-002143 | CS-12693 | Southern Electric Power Distribution Plc | Nursling GSP | 101387-202717 SEPD |  | 2037-10-31
Nursling GSP | PRO-002143 | CS-12694 | Southern Electric Power Distribution Plc | Nursling GSP | 102050-204220 SEPD |  | 2037-10-31
Nursling GSP | PRO-002143 | CS-12695 | Southern Electric Power Distribution Plc | Nursling GSP | 102392-204912 SEPD |  | 2037-10-31
Nursling GSP | PRO-002143 | CS-12696 | Southern Electric Power Distribution Plc | Nursling GSP | 103544-207037 |  | 2037-10-31
Oaklands Farm Solar PV | PRO-001004 | CS-05368 | OAKLANDS FARM SOLAR LIMITED. | Drakelow 132kV Substation | 100867-201733 | 1. Asset transfer of spare skeletal bay at Drakelow 132kV substation from the Relevant Transmission Licensee to the User 2. Database changes and protection modifications to facilitate connection of the Users bay | 2027-06-30
Ocker Hill GSP | PRO-002924 | CS-12169 | National Grid Electricity Distribution (West Midlands) Plc | Ocker Hill C 132kV GSP | 101738-203453 EX(11) |  | 2026-05-30
Offerton 200MW BESS | PRO-004910 | CS-11267 | Decerna Limited | Wearside Connection Node B2 400kV substation | 103951-207827 |  | 2035-10-30
Offerton 200MW BESS | PRO-004910 | CS-11268 | Decerna Limited | Wearside Connection Node B2 400kV substation | 103960-207838 |  | 2035-10-30
Old Flatts Farm | PRO-001894 | CS-07321 | Net Zero One Ltd | Brinsworth 400kV Substation | 101713-203417 |  | 2029-10-30
Old Flatts Farm | PRO-001894 | CS-11824 | Net Zero One Ltd | Brinsworth 400kV Substation | 101812-203717 (3) |  | 2029-10-30
Old Flatts Farm | PRO-001894 | CS-11825 | Net Zero One Ltd | Brinsworth 400kV Substation | 102149-204350 (1) |  | 2029-10-30
Old Greenock Road | PRO-000834 | CS-04419 | SP Distribution plc | Erskine 132/33kV | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 2024-10-16
Olivers Forest Wind Farm | PRO-002648 | CS-09434 | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation | Olivers Forest Wind Farm H1 | Installation of a new 132kV feeder bay at Redshaw 132kV substation on the new “B” board. This feeder bay shall include the associated main and reserve busbar disconnectors and line disconnector. Installation of a new 132kV circuit between Redshaw 132kV and Oliver’s Forest Wind Farm 132kV substations comprising of both 132kV cable and OHL. The indicative length of the circuit is 21.9km using an L4 steel tower construction. Installation of a 132kV line disconnector at Oliver’s Forest Wind Farm 132kV substation | 2031-04-30
Olivers Forest Wind Farm | PRO-002648 | CS-09435 | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2031-04-30
Olivers Forest Wind Farm | PRO-002648 | CS-09436 | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation | SPT-RI-3060 | Redshaw 132kV “B” Board - Establish a new 132kV double busbar substation, indicatively named Redshaw 132kV “B” board at the new Redshaw 400/132kV substation. The location of the SPT’s new 400kV substation (which this 132kV double busbar site will connect into) will be connected in the existing ZV Route corridor (STHA-ELVA / COAL-ELVA) as well as facilitate the new double circuit from Glenmuckloch under SPT-RI-236. The 400kV substation at Redshaw is being constructed under SPT-RI-2060. The 132kV double busbar substation to be established here will also require installation of two 400/132kV 360MVA transformers. (SPT-RI-3060) | 2031-04-30
Olrig Mains Wind Farm | PRO-005126 | CS-12095 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-058 Beauly - Loch Buidhe 275kV OHL Reinforcement |  | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12096 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12097 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12098 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12099 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12100 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12101 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12102 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-200 - Loch Buidhe 400-275kV Substation |  | 2033-10-31
Olrig Mains Wind Farm | PRO-005126 | CS-12103 | QAIR RENEWABLES UK LIMITED | Thurso 2 275/33kV Substation | SHET-RI-287 - Thurso 2 GSP 275 kV Reinforcement |  | 2033-10-31
Orkney Finstown Embedded Generation | PRO-000729 | CS-04439 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2023-04-30
Orkney Finstown Embedded Generation | PRO-000729 | CS-04440 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-019 | Establish a 220kV HVAC circuit over a distance of approximately 68km between the 275kV GIS substation at Dounreay on the mainland and the new 132kV substation in the vicinity of Finstown on Orkney. The HVAC circuit comprises of approximately 15km of land cable and 53km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Dounreay and Finstown. | 2023-04-30
Orkney Finstown Embedded Generation | PRO-000729 | CS-04441 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2023-04-30
Orkney Finstown Embedded Generation | PRO-000729 | CS-04442 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2023-04-30
Orkney Finstown Embedded Generation | PRO-000729 | CS-04443 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2023-04-30
Orkney Finstown Embedded Generation | PRO-000729 | CS-04444 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 2023-04-30
Orkney Finstown Embedded Generation | PRO-000729 | CS-04445 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-020 | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in comprise an extension to the 132kV double busbar substation and a 600MW HVDC link from the northwest coast of Orkney to a HVDC switching station located inland in the vicinity of Sinclair’s Bay in Caithness. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections. | 2023-04-30
Osbaldwick GSP (NE) | PRO-002966 | CS-08414 | NORTHERN POWERGRID (NORTHEAST) PLC | Osbaldwick GSP | 101893-203879 | Extension of Mesh Corner at Osbaldwick 400kV substation to facilitate connection of the 4th SGT | 2039-10-31
Osbaldwick GSP (NE) | PRO-002966 | CS-12092 | NORTHERN POWERGRID (NORTHEAST) PLC | Osbaldwick GSP | 101893-203880 |  | 2039-10-31
Osbaldwick GSP (NE) | PRO-002966 | CS-12373 | NORTHERN POWERGRID (NORTHEAST) PLC | Osbaldwick GSP | 102198-204418 |  | 2039-10-31
Osbaldwick GSP (NE) | PRO-002966 | CS-12374 | NORTHERN POWERGRID (NORTHEAST) PLC | Osbaldwick GSP | 104508-208980 |  | 2039-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06762 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SSE Offshore 1 Enabling | Installation of 400kV plant and apparatus at Cousland 400kV Substation which will form the connections to the SSE 1 Offshore 1 Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. Provision of communications, alarms and indications . | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06763 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06764 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06765 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06766 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06767 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06768 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06769 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-1795 | This project will construct a new 400kV double circuit over the boundary from the South East of Scotland and the North West of England | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06770 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 2033-10-31
Ossian 1 Offshore Wind Farm | PRO-001488 | CS-06771 | Ossian Offshore Wind Farm Limited | Brechin 400/275 kV Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 2033-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06749 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SSE Offshore 2 Enabling | Extension of the existing 400kV double busbar and installation of two new 400kV feeder bays at Fetteresso 400kV substation, each completes with 2 x 400kV busbar selection switches, 1 x 400kv metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at Fetteresso 400kV substation. | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06750 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06751 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06752 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06753 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06754 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06755 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025d | North East Reinforcement | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06756 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06757 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06758 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06759 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06760 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2031-10-31
Ossian 2 Offshore Wind Farm | PRO-001491 | CS-06761 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SPT-RI-003 | Denny-Strathaven 400kV Reinforcement - Construct a new 400kV double circuit overhead line from Bon-nybridge to Newarthill and re-configure associated sites to establish a fourth north to south dou-ble circuit Supergrid route through the Scottish central belt. One side of the new overhead line will oper-ate at 400kV, the other at 275kV. This reinforcement will establish Denny-Bonnybridge, Bonnybridge-Wishaw, Wishaw-Strathaven No.2 and Wishaw-Torness 400kV circuits and a Denny-Newarthill-Easterhouse 275kV circuit. (SPT-RI-003) | 2031-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06622 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SSE Offshore 3 Enabling | At New Deer 400kV substation, extend the existing 400kV double busbar and install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at New Deer 400kV substation. | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06623 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06624 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06625 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06626 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06627 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06628 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06629 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06630 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-025d | North East Reinforcement | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06631 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06632 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06633 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06634 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06635 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06636 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Ossian 3 Offshore Wind Farm | PRO-001489 | CS-06637 | Ossian Offshore Wind Farm Limited | Western Marsh 400kV | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07680 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SSE Offshore 4 H1 | 1. Installation of 400kV plant and apparatus at Cousland 400kV Substation which will form the connection to the SSE Offshore 4 Transmission Interface Point, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. 2. Provision of communications, alarms and indications, as described in Appendix OF and Appendix F of the Bilateral Connection agreement | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07681 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07682 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07683 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07684 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07685 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07686 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07687 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07688 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07689 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07690 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07691 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 2033-10-31
Ossian 4 Offshore Wind Farm | PRO-002145 | CS-07692 | Ossian Offshore Wind Farm Limited | Cousland 400kV | SPT-RI-2417 | Teviot to Gala North Reinforcements - A new 400kV double circuit OHL using L13 towers and triple Araucaria conductor from Teviot 400kV substation to Gala North 400kV substation which is approximately 57km. (SPT-RI-2417) | 2033-10-31
Ourack Wind Farm | PRO-001490 | CS-07663 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | Ourack Wind Farm Enabling Works | 1. Installation of a new 132kV double busbar feeder bay comprising of 1 x 132kV line circuit breaker, 1 x 132kV line disconnector and associated protection and control equipment at Clash Gour 275/132kV Collector Substation. 2. Establish a new 132kV single circuit connection between Clash Gour 275/132kV Collector Substation and the Ourack 132/33kV substation at the wind farm site. This will comprise of a 10km section of 132kV overhead steel structure line. The new 132kV circuit will terminate into a new 132kV line disconnector and circuit breaker installed at Ourack 132/33kV substation | 2030-10-31
Ourack Wind Farm | PRO-001490 | CS-07664 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-007a | Beauly - Blackhillock 400kV OHL - Establish a new double circuit 400kV overhead line approximately 130km from Beauly to Blackhillock. The new OHL is connected to the Beauly 400kV AIS busbar and the Blackhillock 400kV GIS busbar. | 2030-10-31
Ourack Wind Farm | PRO-001490 | CS-07665 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 2030-10-31
Ourack Wind Farm | PRO-001490 | CS-07666 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2030-10-31
Ourack Wind Farm | PRO-001490 | CS-07667 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-146 | Clash Gour 275/132kV Collector Substation - The Clash Gour 275/132kV Collector Substation works include establishment of a double 132kV busbar and installation of two 240/480MVA 275/132kV transformers. | 2030-10-31
Ouse Energy Storage | PRO-001861 | CS-06890 | Ouse Energy Limited | Kemsley 400kV Substation | 101685-203354 | 1. Relocation of existing Kemsley 400kV Main and Reserve Busbar disconnectors to accommodate Users Bay 2. Reconfiguration of Kemsley 400kV Main and Reserve Busbars to accommodate Users Bay | 2027-10-27
Ouse Energy Storage | PRO-001861 | CS-06891 | Ouse Energy Limited | Kemsley 400kV Substation | 020865-020865 | Kemsley to Longfield Tee 400 kV circuit - Reconductor to achieve a 2800MVA post-fault rating. Littlebrook to Longfield Tee 400 kV circuit - Reconductor to achieve a 2800MVA post-fault rating. | 2027-10-27
Ouse Energy Storage | PRO-001861 | CS-06892 | Ouse Energy Limited | Kemsley 400kV Substation | 100116-200307 | Uprate Kingsnorth - Tilbury and Grain - Tilbury 400 kV circuits to achieve a 2350 MVA pre-fault and 3200 post fault winter rating | 2027-10-27
Ouse Energy Storage | PRO-001861 | CS-06893 | Ouse Energy Limited | Kemsley 400kV Substation | 100116-200654 | New GRAI - TILB/KINO - TILB tunnel to achieve required 3300 MVA rating (2 cables per phase) | 2027-10-27
Overhill Wind Farm | PRO-000472 | CS-03728 | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation | Overhill H1 | At Overhill 132kV substation install 132kV line isolator. Install approximately 3km underground cable circuit from Overhill 132kV substation to New Cumnock 132kV substation (Board B). At New Cumnock substation on the middle section of Board B install 132kV feeder bay. | 2029-06-06
Overhill Wind Farm | PRO-000472 | CS-03729 | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-06-06
Overhill Wind Farm | PRO-000472 | CS-03730 | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-06-06
Overhill Wind Farm | PRO-000472 | CS-03731 | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-06-06
Overhill Wind Farm | PRO-000472 | CS-06712 | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-06-06
Overhill Wind Farm | PRO-000472 | CS-06713 | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-06-06
Overton Green Energy Centre | PRO-002252 | CS-12556 | OVERTON NG LIMITED | Overton 275kV | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-24
Overton Green Energy Centre | PRO-002252 | CS-12557 | OVERTON NG LIMITED | Overton 275kV | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 2035-10-24
Overton Green Energy Centre | PRO-002252 | CS-12558 | OVERTON NG LIMITED | Overton 275kV | 102080-204270 |  | 2035-10-24
Overton IDNO BESS | PRO-004341 | CS-10962 | Eclipse Power Networks Limited | Overton IDNO GSP |  |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10963 | Eclipse Power Networks Limited | Overton IDNO GSP | 103304-206743 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10964 | Eclipse Power Networks Limited | Overton IDNO GSP | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10965 | Eclipse Power Networks Limited | Overton IDNO GSP | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10966 | Eclipse Power Networks Limited | Overton IDNO GSP | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10967 | Eclipse Power Networks Limited | Overton IDNO GSP | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10968 | Eclipse Power Networks Limited | Overton IDNO GSP | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10969 | Eclipse Power Networks Limited | Overton IDNO GSP | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10970 | Eclipse Power Networks Limited | Overton IDNO GSP | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10971 | Eclipse Power Networks Limited | Overton IDNO GSP | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10972 | Eclipse Power Networks Limited | Overton IDNO GSP | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10973 | Eclipse Power Networks Limited | Overton IDNO GSP | 100173-200455 | Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and130) at Drax 132kV Substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10974 | Eclipse Power Networks Limited | Overton IDNO GSP | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10975 | Eclipse Power Networks Limited | Overton IDNO GSP | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10976 | Eclipse Power Networks Limited | Overton IDNO GSP | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10977 | Eclipse Power Networks Limited | Overton IDNO GSP | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10978 | Eclipse Power Networks Limited | Overton IDNO GSP | 100479-201050 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10979 | Eclipse Power Networks Limited | Overton IDNO GSP | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10980 | Eclipse Power Networks Limited | Overton IDNO GSP | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10981 | Eclipse Power Networks Limited | Overton IDNO GSP | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10982 | Eclipse Power Networks Limited | Overton IDNO GSP | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10983 | Eclipse Power Networks Limited | Overton IDNO GSP | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10984 | Eclipse Power Networks Limited | Overton IDNO GSP | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10985 | Eclipse Power Networks Limited | Overton IDNO GSP | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10986 | Eclipse Power Networks Limited | Overton IDNO GSP | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10987 | Eclipse Power Networks Limited | Overton IDNO GSP | 101164-202350 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10988 | Eclipse Power Networks Limited | Overton IDNO GSP | 101325-202642 | At Thornton 400kV: Establish an additional section switch in place of X224 or X228 and add another section switch in place of X428 or X424. Replace circuit breaker X405 and X805 (In Lackenby - Thornton circuits with 63kA rated breakers. (101325-202642) | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10989 | Eclipse Power Networks Limited | Overton IDNO GSP | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10990 | Eclipse Power Networks Limited | Overton IDNO GSP | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10991 | Eclipse Power Networks Limited | Overton IDNO GSP | 101386-202716 | LTRE (NOA)Upgrade the existing circuits between Lackenby and Thornton to allow for more capacity | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10992 | Eclipse Power Networks Limited | Overton IDNO GSP | 101508-202973 (1) |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10993 | Eclipse Power Networks Limited | Overton IDNO GSP | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10994 | Eclipse Power Networks Limited | Overton IDNO GSP | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10995 | Eclipse Power Networks Limited | Overton IDNO GSP | 101625-203259 | Uprate the Drax - Eggborough 2 circuit to achieve a post fault summer rating of 2500MVA. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10996 | Eclipse Power Networks Limited | Overton IDNO GSP | 101661-203312 | Uprating/Replacement of the CB T10 at Monk Fryston 275kV substation | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10997 | Eclipse Power Networks Limited | Overton IDNO GSP | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10998 | Eclipse Power Networks Limited | Overton IDNO GSP | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm² Araucaria conductor | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-10999 | Eclipse Power Networks Limited | Overton IDNO GSP | 101712-203416 | Uprating/Replacement of the following CB at Stella West 275 kV substation: H10, H20, H40, H50, H90, S10 and W10 | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11000 | Eclipse Power Networks Limited | Overton IDNO GSP | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11001 | Eclipse Power Networks Limited | Overton IDNO GSP | 102178-204388 | Replacement of CB's S10, P10, W10, W20, H10 and H20 at Blyth 275kV Substation | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11002 | Eclipse Power Networks Limited | Overton IDNO GSP | 102197-204417 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11003 | Eclipse Power Networks Limited | Overton IDNO GSP | 102356-204777 | Uprating/Replacement of the following Circuit breakers for a higher X/R ratio of 25 at Drax 400kV substations: X430, X630, X405. | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11004 | Eclipse Power Networks Limited | Overton IDNO GSP | 102360-204779 | Uprating/Replacement of the following Circuit breakers at Creyke Beck 400kV substation X510, X130, X420, X430, X520, X620, X330, X1215, X905, X210, X1415, X320 | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11005 | Eclipse Power Networks Limited | Overton IDNO GSP | 102412-204937 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11006 | Eclipse Power Networks Limited | Overton IDNO GSP | 102591-205211 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11007 | Eclipse Power Networks Limited | Overton IDNO GSP | 103143-206563 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11008 | Eclipse Power Networks Limited | Overton IDNO GSP | 103145-206565 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11009 | Eclipse Power Networks Limited | Overton IDNO GSP | 103165-206584 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11010 | Eclipse Power Networks Limited | Overton IDNO GSP | 103166-206585 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11011 | Eclipse Power Networks Limited | Overton IDNO GSP | 103167-206586 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11012 | Eclipse Power Networks Limited | Overton IDNO GSP | 101074-202154 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11013 | Eclipse Power Networks Limited | Overton IDNO GSP | 103719-207359 |  | 2035-10-30
Overton IDNO BESS | PRO-004341 | CS-11014 | Eclipse Power Networks Limited | Overton IDNO GSP |  |  | 2035-10-30
OWPL Windfarm | PRO-000568 | CS-05993 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | OWPL H1 Enabling | Establishment of two new fully equipped 275kV metering circuit breaker bays and associated disconnectors at the new Spittal 2 275kV substation to connect the OWPL offshore wind farm development. The ownership boundary between the Onshore Transmission Licensee and the User (as OTSDUW User) will be the line side terminal of the 275kV disconnectors (L53, L63, L73, L83 and L93). | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06608 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06609 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06610 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06611 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-025d | North East Reinforcement | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06612 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06613 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06614 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06615 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06616 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06617 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06618 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06619 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06620 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2029-12-31
OWPL Windfarm | PRO-000568 | CS-06621 | OFFSHORE WIND POWER LIMITED | Banniskirk 400kV Substation | no Scheme |  | 2029-12-31
Parkhouse 24MW BESS | PRO-003580 | CS-11971 | GPC 1184 LTD | Crookston 132/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2028-06-28
Parkhouse 24MW BESS | PRO-003580 | CS-11972 | GPC 1184 LTD | Crookston 132/33kV | SPT-RI-3788 | 3. Neilston 132kV Uprate to 25kA fault rating | 2028-06-28
Parkhouse 24MW BESS | PRO-003580 | CS-11973 | GPC 1184 LTD | Crookston 132/33kV | SPT-RI-3263 | Erskine 132kV Bus Section Circuit Breaker | 2028-06-28
Parkhouse 24MW BESS | PRO-003580 | CS-11974 | GPC 1184 LTD | Crookston 132/33kV | SPT-RI-3789 | 4. Neilston SGT1 SGT2 SGT3B Load Management Scheme - A transformer load management scheme is required to manage the loadings across SGT1, SGT2 and SGT3B at Neilston 400/275/132kV substation and trip the appropriate non-firm connections to remove any measured overloads. The SPT LMS will be required to transfer the following signals to the User(s): • Stage 1 Signal at 95% of the transformer rating • Stage 2 Signal at 100% of the transformer rating • Stage 3 Signal at 120% of the transformer rating Note: These values will be subject to change following detailed design, User input and optimisation of the system The different stages have the following intended actions: • Stage 1 Signal: Provides an alarm to the connection warning of impending overload condition. • Stage 2 Signal: Will trip connections associated with this TORI as per queue order • Stage 3 Signal: Will trip all connections regardless of queue order (SPT-RI-3789) | 2028-06-28
Parkhouse 24MW BESS | PRO-003580 | CS-11975 | GPC 1184 LTD | Crookston 132/33kV | SPT-RI-3285 | Devol Moor-Erskine-Braehead Park 132kV LMS – BZ Route Monitoring Upgrade –An extension to the existing Devol Moor-Erskine-Braehead Park Load Management Scheme (LMS) is required to manage connections to prevent thermal overloads on the Erskine-Braehead Park Circuit. A new monitoring outstation will be installed at Braehead Park to monitor the loading on the Erskine-Braehead Park 132kV circuit. The measurements will be communicated to Devol Moor 132kV where the IED associated with the existing Devol Moor-Erskine LMS scheme (established under TORI?243) will relay trip signals to relevant non-firm connections as appropriate. | 2028-06-28
Parkhouse 24MW BESS | PRO-003580 | CS-11976 | GPC 1184 LTD | Crookston 132/33kV | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2028-06-28
Paul's Hill II Wind Farm | PRO-000890 | CS-05994 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2029-06-30
Paul's Hill II Wind Farm | PRO-000890 | CS-05995 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2029-06-30
Paul's Hill II Wind Farm | PRO-000890 | CS-05996 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-015a | Knocknagael – Tomatin 275/132kV Reinforcement - Reinforce the existing 132kV transmission network between Beauly–Farr–Boat of Garten (Circuits BR1/RG1/BR2/RG2). Note that the existing 132kV OHL passes close to Knocknagael substation. Establish a new 275/132kV substation station including a 132kV double busbar arrangement near Tomatin and connected to a new 275kV double circuit OHL from the Knocknagael 275kV busbar via 275/132kV SGTs. | 2029-06-30
Paul's Hill II Wind Farm | PRO-000890 | CS-05997 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-015b | Beauly-Farr-Boat of Garten 132kV OHL Reconfiguration - The existing section of 132kV OHL (BR1 & BR2) between Beauly and Farr will be terminated on the 132kV busbar at Knocknagael Substation. The OHL sections of the existing 132kV OHL will be dismantled between Knocknagael and Farr as part of the 132kV OHL reconfiguration. The existing section of double circuit 132kV OHL (RG1 & RG2) between Farr and Boat of Garten will be reconfigured as radial circuits between Tomatin and Boat of Garten. A normally open (N/O) point will be required at Keith on the circuit (FK) between Glenfarclas and Keith. This arrangement will leave Glenfarclas on a radial circuit fed from Boat of Garten under normal operating conditions. | 2029-06-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11699 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2033-05-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11702 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | Peat Law - AIS Bay | At Gala North 400/132kV Substation, install a 132kV AIS bay. | 2033-05-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11703 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | Peat Law - Circuit Cable | Install a 132kV cable circuit away from GALN to get under ZA Route | 2033-05-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11704 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | Peat Law - OHL | Install a ~10km 132kV OHL circuit heading north to Peat Law. (Circuit capacity required = 280MVA.) | 2033-05-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11705 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | Peat Law - Line Disconnector | At Peat Law, install a new 132kV line disconnector. | 2033-05-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11706 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | Peat Law - GIS Bay | At Gala North 400/132kV Substation, install a 400kV GIS bay. | 2033-05-30
Peat Law Renewable Energy Park | PRO-005030 | CS-11707 | VOLTALIA UK LTD | Peat Law Renewable Energy Park 132kV Substation | Peat Law - SGT | At Gala North 400/132kV Substation, install a 400/132kV 360MVA SGT. | 2033-05-30
Peattie Farm - Coupar Angus | PRO-002989 | CS-09225 | GREENTECH PROJECTS HOLDING UK LIMITED | Coupar Angus 2 GSP | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm²) and will operate at 75°C to give a minimum summer pre-fault rating of 176MVA | 2029-10-31
Peattie Farm - Coupar Angus | PRO-002989 | CS-09226 | GREENTECH PROJECTS HOLDING UK LIMITED | Coupar Angus 2 GSP | SHET-RI-184 | Coupar Angus 2 Tee – Establish a new 132kV tee point of the HCS circuit between Coupar Angus GSP and Tealing/Charleston Tee for the connection to a new Coupar Angus 2 132/33kV GSP substation | 2029-10-31
Peattie Farm - Coupar Angus | PRO-002989 | CS-09227 | GREENTECH PROJECTS HOLDING UK LIMITED | Coupar Angus 2 GSP | Peattie Farm - Coupar Angus 2 Works | Installation of 2 x 132kV circuit breakers and 132kV disconnectors at the new Coupar Angus 2 132/33kV GSP substation compound, including 132kV cabling and works to connect the grid transformers. | 2029-10-31
Pembroke (spare bay) | PRO-000538 | CS-06914 | Pembroke Green Limited | Pembroke 132kV Substation | 100904-201818 | 1. Works to facilitate the connection of User’s plant into a spare bay at Pembroke 132kV substation 2. Extension of Pembroke OTS (Category 2 and Commercial intertripping schemes as explained in F3) | 2028-07-30
Pembroke (spare bay) | PRO-000538 | CS-06915 | Pembroke Green Limited | Pembroke 132kV Substation | 100838-201680 | Replacement of feeder circuit breakers X105 and X305 of Pembroke - Swansea North 400 kV Circuits 1 and 3 and modification of feeder protection to allow faster operation times. | 2028-07-30
Pembroke (spare bay) | PRO-000538 | CS-06916 | Pembroke Green Limited | Pembroke 132kV Substation | 33746 | 1. Thermal uprate of Whitson leg of Tremorfa - Uskmouth – Whitson circuit. 2. Replacement of Cowley – Walham cables. 3. Thermal uprate of Imperial Park – Melksham and Cilfynydd – Whitson – Seabank circuits. 4. Thermal uprate of the Iron Acton – Melksham circuits 1 and 2. 5. Thermal uprate of Iron Acton – Whitson circuits 1 and 2. 6. Replace the Quad boosters 1 and 2 at Whitson for larger units. 7. Replacement of Whitson SGT5 for a larger rated unit. 8. Thermal uprate of Cardiff East – Uskmouth Whitson (Cardiff East leg). 9. Thermal uprate of Cardiff East – Uskmouth – Whitson (Whitson leg). 10. Thermal uprate of Aberthaw – Tremorfa circuit. 11. Thermal uprate of Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit. 12. Thermal uprate of Tremorfa - Uskmouth – Whitson circuit 13. Thermal uprate of Cardiff East – Uskmouth – Whitson (Uskmouth leg). 14. Thermal uprate of Uskmouth – Whitson 2 circuit. | 2028-07-30
Pembroke BESS | PRO-000337 | CS-05945 | RWE Generation UK Plc | Pembroke 400kV Substation | 101575-203161 |  | 2027-10-29
Pembroke BESS | PRO-000337 | CS-10589 | RWE Generation UK Plc | Pembroke 400kV Substation | 101575-207763 |  | 2027-10-29
Pembroke BESS | PRO-000337 | CS-10590 | RWE Generation UK Plc | Pembroke 400kV Substation | 033793-202895 |  | 2027-10-29
Pembroke BESS | PRO-000337 | CS-10591 | RWE Generation UK Plc | Pembroke 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2027-10-29
Pencloe Windfarm | PRO-000323 | CS-05998 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-05999 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-06000 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-116B | Construction of Black Hill 132/33kV Substation including two 132kV circuit breakers (double busbar), two 132/33kV 90MVA transformers and 33kV B switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-06001 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-06002 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-06677 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-06678 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-08224 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-136 | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-08225 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2025-07-01
Pencloe Windfarm | PRO-000323 | CS-08226 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2025-07-01
Penketh Hall Farm | PRO-001932 | CS-07469 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101743-203463 | At Fiddlers Ferry 275kV Substation: 1. Provision of an ex-SSE owned generator bay for the User to connect into – this is subject to SSE agreeing an asset transfer of the bay to The Relevant Transmission Licensee. Specific bay to be confirmed during the development phase of the project. 2. Modifications to protection and control systems / database changes as required. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07470 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07471 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07472 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07473 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07474 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07475 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07476 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07477 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07478 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm² conductor | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07479 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07480 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 2027-09-01
Penketh Hall Farm | PRO-001932 | CS-07481 | Net Zero One Ltd | Fiddlers Ferry 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2027-09-01
Pentland Floating Offshore Wind Farm | PRO-001472 | CS-06496 | HIGHLAND WIND LIMITED | Pentland Floating Offshore Wind Farm 132/66kV substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2027-10-31
Pentland Floating Offshore Wind Farm | PRO-001472 | CS-06497 | HIGHLAND WIND LIMITED | Pentland Floating Offshore Wind Farm 132/66kV substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2027-10-31
Pentland Road | PRO-000361 | CS-06003 | PENTLAND ROAD WINDFARM LIMITED | Stornoway 132/33kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 2027-03-31
Pentland Road | PRO-000361 | CS-06004 | PENTLAND ROAD WINDFARM LIMITED | Stornoway 132/33kV Substation | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 2027-03-31
Penwortham BESS | PRO-001804 | CS-07028 | PENWORTHAM (BES) LTD | Penwortham 400kV Substation | 101607-203231 | Extension Works of the existing fence to provide a 13kV Connection Install Earthing Transformer on 13kV SGT9 Tertiary connection. Install 13kV cable from 13kV SGT9 Tertiary connection to 13 kV Line Disconnector. Install 13 kV Line Disconnector. | 2027-10-30
Penwortham BESS | PRO-001804 | CS-12594 | PENWORTHAM (BES) LTD | Penwortham 400kV Substation | 101607-205823 |  | 2027-10-30
Perry Barr BESS | PRO-004745 | CS-11256 | Perry Barr Limited | Nechells East GSP | 102733-205522 1 |  | 2037-10-30
Perry Barr BESS | PRO-004745 | CS-11257 | Perry Barr Limited | Nechells East GSP | 102733-205523 1 |  | 2037-10-30
Perry Barr BESS | PRO-004745 | CS-11258 | Perry Barr Limited | Nechells East GSP | 103266-206708 1 |  | 2037-10-30
Perry Barr BESS | PRO-004745 | CS-11259 | Perry Barr Limited | Nechells East GSP | 104044-207950 |  | 2037-10-30
Peterhead Battery | PRO-001999 | CS-07254 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07255 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07256 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07257 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07258 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | Peterhead 400 kV Substation | Install one new 400kV feeder bay complete with 2 x 400kV busbar selection switches,1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The construction of approximately 3km of 400kV Circuit between Peterhead 400kV Substation and Peterhead Battery substation. At Peterhead Battery Substation the sole use enabling works will include the construction of a 400kV Line disconnector including all associated civil and protection work. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07259 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07260 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025d | North East Reinforcement | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07261 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07262 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07263 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07264 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07265 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07266 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07267 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07270 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Peterhead Battery | PRO-001999 | CS-07271 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09622 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09623 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09624 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09625 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09626 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-025d | North East Reinforcement | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09627 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09628 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09629 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09630 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09631 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09632 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09633 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09634 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09635 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09636 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Peterhead Carbon Capture | PRO-004529 | CS-09637 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 2033-10-31
Peterhead PV and BESS Station | PRO-002775 | CS-09325 | ETP UK 2 LTD | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07762 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 102155-204359 |  | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07763 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07764 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07765 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07766 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07767 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07768 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07769 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
Petroc Offshore Wind Farm | PRO-001661 | CS-07430 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101460-202897 | Local substation works to enable the generation connection of 300MW Connection Entry Capacity (CEC) for Dewnens Floating Offshore Wind Farm at Alverdiscott substation. Extension of the busbars by 1 bay to enable connection of the generator’s bay. | 2029-03-31
Petroc Offshore Wind Farm | PRO-001661 | CS-07431 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2029-03-31
Petroc Offshore Wind Farm | PRO-001661 | CS-07432 | SCARABEN OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2029-03-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06728 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | Phoenix 1B Item 1 | Installation of 400kV plant and apparatus at Cousland 400kV Substation which will form the connections to the three Phoenix 1B Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06729 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | Phoenix 1B Item 2 | Provision of communications, alarms and indications, as described in Appendix F of the Bilateral Connection Agreement. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06730 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06731 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06732 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06733 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06734 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06735 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06736 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-304 | East Coast B6 onshore reinforcement - Installation of a new 400kV double circuit overhead line, of approximately 185km, between the Torness area (Branxton 400kV substation) in South East Scotland, and Lackenby in North East England. | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06737 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-1795 | This project will construct a new 400kV double circuit over the boundary from the South East of Scotland and the North West of England | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06738 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 2033-10-31
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06739 | Morven Offshore Wind Limited | Near Branxton 400kV Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 2033-10-31
Pines Burn Wind Farm | PRO-000897 | CS-06194 | PINES BURN WIND FARM LLP | Hawick GSP | SPT-RI-151b | In order to provide GBSQSS compliant connections for additional generation requiring to export from Hawick/Galashiels to Eccles, it is proposed to construct a new 132kV double circuit tower line between Galashiels and Eccles, and remove the existing U and AT Routes. | 2023-08-02
Pitkerro Road | PRO-002457 | CS-09598 | Vital Energi Solutions Limited | Milton of Craigie GSP | Pitkerro Road H1 Works | 1. Installation of 2x 120MVA transformers within the existing substation with associated 33kV 2x circuit breakers and 2x disconnectors. 2. Installation of 132kV 2x circuit breakers and 2x disconnectors on the HV side of the new Grid Transformers at Milton of Craigie GSP which have been installed as part of the Transmission Connection Asset Works. | 2033-10-31
Pitkerro Road | PRO-002457 | CS-09599 | Vital Energi Solutions Limited | Milton of Craigie GSP | SHET-RI-183 | New Dundee 132kV Substation – Construction of a new 132kV double busbar substation in Dundee, to replace Dudhope GSP. This busbar will be fed by turning in the current Dudhope/Milton of Craigie 132kV circuits. (SHET-RI-183) | 2033-10-31
Pitkerro Road (DNO) | PRO-003028 | CS-09596 | Scottish Hydro Electric Power Distribution Plc | Milton of Craigie GSP | Pitkerro Road H1 | Installation of 132kV 2x circuit breakers and 2x disconnectors on the HV side of the new Grid Transformers at Milton of Craigie GSP which have been installed as part of the Transmission Connection Asset Works. | 2033-10-31
Pitkerro Road (DNO) | PRO-003028 | CS-09597 | Scottish Hydro Electric Power Distribution Plc | Milton of Craigie GSP | SHET-RI-183 | New Dundee 132kV Substation – Construction of a new 132kV double busbar substation in Dundee, to replace Dudhope GSP. This busbar will be fed by turning in the current Dudhope/Milton of Craigie 132kV circuits. (SHET-RI-183) | 2033-10-31
Plas Power Estate North Tertiary | PRO-001050 | CS-06917 | LIGHTSOURCE SPV 192 LIMITED | Legacy 400kV Substation | 100861-201721 | 1. Install a tertiary cable box or bushings on the SGT 3. 2. Install 13kV Cable from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2028-05-31
PM AB Energy Storage | PRO-002140 | CS-07742 | CBS ENERGY STORAGE ASSETS UK LIMITED | Abernethy GSP | PM AB Energy Storage Item | An intertrip for the loss of one of the Grid Transformers at Abernethy 132/33kV GSP. These signals will be provided to the host Distribution Network Operator via a separate relay panel within the 33kV Switchroom from the signals described below. Provision of status signals are required for the following: Status signals from the 33kV circuit breakers and disconnectors at Abernethy GSP Status signals from 132kV circuit breakers and disconnectors at Abernethy GSP Modification to the existing LV Directional Overcurrent (DOC) protection settings at Abernethy 132/33kV Substation. | 2026-10-31
PM AB Energy Storage | PRO-002140 | CS-07743 | CBS ENERGY STORAGE ASSETS UK LIMITED | Abernethy GSP | SHET-RI-121 | Charleston - Abernethy 132kv reconductoring; approx 25km of 132 kv ohl between abernrethy substation and Charleston. | 2026-10-31
Pond Flexible Energy Park | PRO-003201 | CS-09408 | Pond Flexible Energy Park Limited | Pond Flexible Energy Park 132kV Substation | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 2031-06-30
Pond Flexible Energy Park | PRO-003201 | CS-09480 | Pond Flexible Energy Park Limited | Pond Flexible Energy Park 132kV Substation | SPT-RI-3168 | Harburn 132kV Substation | 2031-06-30
Pond Hill Farm 1 | PRO-001637 | CS-06918 | PD688IRO LTD | Minety 400kV Substation | 101488-202945 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2025-04-30
Pond Hill Farm 1 | PRO-001637 | CS-06919 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2025-04-30
Pond Hill Farm 1 | PRO-001637 | CS-06920 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2025-04-30
Pond Hill Farm 2 BESS | PRO-001635 | CS-06921 | PD688IRO LTD | Minety 400kV Substation | 101488-202945 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2025-05-31
Pond Hill Farm 2 BESS | PRO-001635 | CS-06922 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2025-05-31
Pond Hill Farm 2 BESS | PRO-001635 | CS-06923 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2025-05-31
Pont Abraham iDNO | PRO-001562 | CS-04746 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 2029-10-31
Pont Abraham iDNO | PRO-001562 | CS-04747 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 2029-10-31
Pont Abraham iDNO | PRO-001562 | CS-12245 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202497 (infra sub) |  | 2029-10-31
Pont Abraham iDNO | PRO-001562 | CS-12246 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202607 (infra OHL) |  | 2029-10-31
Pont Abraham iDNO | PRO-001562 | CS-12247 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202608 (conn) |  | 2029-10-31
Poppleton GSP (NE) | PRO-002967 | CS-12104 | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton GSP Northern Powergrid | 102140-204345-Poppleton GSP |  | 2039-10-30
Poppleton GSP (NE) | PRO-002967 | CS-12105 | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton GSP Northern Powergrid | 102145-204347 |  | 2039-10-30
Poppleton GSP (NE) | PRO-002967 | CS-12106 | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton GSP Northern Powergrid | 102147-204348 |  | 2039-10-30
Poppleton GSP (NE) | PRO-002967 | CS-12107 | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton GSP Northern Powergrid | 102148-204349 |  | 2039-10-30
Poppleton GSP (NE) | PRO-002967 | CS-12108 | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton GSP Northern Powergrid | 103097-206515 |  | 2039-10-30
Poppleton GSP (NE) | PRO-002967 | CS-12109 | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton GSP Northern Powergrid | 104458-208584-Poppleton GSP |  | 2039-10-30
Port of Mostyn | PRO-000421 | CS-06924 | MOSTYN SEAPOWER LIMITED | Connah's Quay 400kV Substation | 100534-201153 | Extend the existing GIS busbars at Connah’s Quay 400kV Substation to provide space for a single generator bay. | 2030-12-01
Port of Mostyn | PRO-000421 | CS-11490 | MOSTYN SEAPOWER LIMITED | Connah's Quay 400kV Substation | 100534-201153 | Extend the existing GIS busbars at Connah’s Quay 400kV Substation to provide space for a single generator bay. | 2030-12-01
Priestgill Wind Farm | PRO-000448 | CS-06005 | PRIESTGILL WIND FARM LIMITED | Elvanfoot 400/275/33kV | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 2026-11-30
Priestgill Wind Farm | PRO-000448 | CS-07367 | PRIESTGILL WIND FARM LIMITED | Elvanfoot 400/275/33kV | SPT-RI-1876 | 2. Elvanfoot 132/33kV Grid Transformer - Install a 132/33kV 60MVA transformer at Elvanfoot to accommodate the increased generation connecting at 33kV into the site. (SPT-RI-1876) | 2026-11-30
Progress Power Station | PRO-000274 | CS-06006 | PROGRESS POWER LIMITED | Yaxley 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2024-06-28
Progress Power Station | PRO-000274 | CS-06007 | PROGRESS POWER LIMITED | Yaxley 400kV Substation | 032473-032486 | Installation of a new GIS double busbar 400kV substation at Yaxley with associated two feeder bays, coupler bay and provide double tee connection of the new substation to the Bramford – Norwich Main double OHL circuit. New terminal tower on the Bramford – Norwich Main 1 & 2 circuits and removal of the existing suspension tower(s). Installation of cable circuit to provide a duck tee connection underneath OHL. Install an additional circuit breaker on the LV side of SGT3 at Norwich Main to maintain compliance with the SQSS circuit complexity guidance. Extension of the existing East Anglia Operational Tripping Scheme to include this connection. | 2024-06-28
Project Invicta | PRO-004133 | CS-11237 | PROJECT INVICTA LIMITED | East Kent Connection Node B 400kV Substation | 103499-206977 (Invicta) |  | 2036-10-31
Project Invicta | PRO-004133 | CS-11238 | PROJECT INVICTA LIMITED | East Kent Connection Node B 400kV Substation | 103654-207243 |  | 2036-10-31
PVDP Scarning | PRO-003998 | CS-12042 | SolarFour Ltd | North Anglia Connection Node C 400kV Substation | 030447-030447 1 |  | 2034-10-31
PVDP Scarning | PRO-003998 | CS-12043 | SolarFour Ltd | North Anglia Connection Node C 400kV Substation | 102456-205018 I |  | 2034-10-31
PVDP Scarning | PRO-003998 | CS-12044 | SolarFour Ltd | North Anglia Connection Node C 400kV Substation | 102456-205019 I |  | 2034-10-31
PVDP Scarning | PRO-003998 | CS-12045 | SolarFour Ltd | North Anglia Connection Node C 400kV Substation | 102997-206404 |  | 2034-10-31
PVDP Woodbridge | PRO-004000 | CS-11907 | SolarSeven Ltd | South Anglia Connection Node E 400kV Substation | 100381-200905 2 |  | 2034-10-31
PVDP Woodbridge | PRO-004000 | CS-11908 | SolarSeven Ltd | South Anglia Connection Node E 400kV Substation | 100602-020835 2 |  | 2034-10-31
PVDP Woodbridge | PRO-004000 | CS-11909 | SolarSeven Ltd | South Anglia Connection Node E 400kV Substation | 103040-206457 3 |  | 2034-10-31
PVDP Woodbridge | PRO-004000 | CS-11910 | SolarSeven Ltd | South Anglia Connection Node E 400kV Substation | 103041-206458 3 |  | 2034-10-31
PVDP Woodbridge | PRO-004000 | CS-11911 | SolarSeven Ltd | South Anglia Connection Node E 400kV Substation | 103746-207395 |  | 2034-10-31
Quantans Hill Wind Farm | PRO-001247 | CS-06213 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | Quantans Hill H1 Works | At Quantans Hill substation install one 132kV circuit breaker and associated 132kV disconnector. | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-06214 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-06215 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-06216 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-1507 | Holm Hill 132kV substation - At an appropriate point next to the DE route establish a 132kV substation (Holmhill 132kV substation) by teeing into the proposed future New Cumnock to Glenlee 132kV circuit. The substation will consist of a 132kV busbar to which wind farm circuits will connect to. | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-06217 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-06218 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-08212 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2029-07-02
Quantans Hill Wind Farm | PRO-001247 | CS-08213 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-2094 | Quantans Hill to Holmhill 132kV Circuit – At the proposed Quantans Hill wind farm site establish a 132kV substation and establish a 132kV busbar to which a 132kV line isolator is connected. Install around 6km of wood pole overhead line with HTLS conductor to connect Quantans Hill substation to Holmhill substation. At Holmhill substation install a 132kV circuit breaker to connect the OHL. | 2029-07-02
Rampion Extension Offshore Wind Farm | PRO-000467 | CS-06372 | RAMPION EXTENSION DEVELOPMENT LIMITED | Bolney 400kV Substation | 100732-201514 | AIS Extension of Reserve and Main busbar 2 at Bolney 400kV Substation for the provision of one User Bay. | 2026-08-01
Rampion Extension Offshore Wind Farm | PRO-000467 | CS-06374 | RAMPION EXTENSION DEVELOPMENT LIMITED | Bolney 400kV Substation | 33773 | Thermal upgrade of the Bramley to Fleet 1 & 2 circuits | 2026-08-01
Rampion Extension Offshore Wind Farm | PRO-000467 | CS-06375 | RAMPION EXTENSION DEVELOPMENT LIMITED | Bolney 400kV Substation | 100732-201610 | Extension of the Sellindge Operational Tripping Scheme (OTS) to include Rampion Extension Wind Farm. | 2026-08-01
Rampion Extension Offshore Wind Farm | PRO-000467 | CS-06376 | RAMPION EXTENSION DEVELOPMENT LIMITED | Bolney 400kV Substation | 100298 | Re-Conductor Fleet – Lovedean 1 & 2 circuit | 2026-08-01
Rampion Extension Offshore Wind Farm | PRO-000467 | CS-06377 | RAMPION EXTENSION DEVELOPMENT LIMITED | Bolney 400kV Substation | 33411 | Thermal reinforcement to the South Coast | 2026-08-01
Rassau Stability Services Limited | PRO-003931 | CS-10934 | WP Grid Services 16 Limited | Rassau 400kV Substation | 101947-203995(1) | Replacement of 6 Cilfynydd 400kV circuit breakers X120, X130, X230 and X110, X505 and X305 with new 63kA rated circuit breakers. | 2037-10-31
Rassau Stability Services Limited | PRO-003931 | CS-10935 | WP Grid Services 16 Limited | Rassau 400kV Substation | 102584-205197(1) | Replacement of 5 Cilfynydd 400kV circuit breakers X205, X605, X405, X105, X210 with new 63kA rated circuit breakers. | 2037-10-31
Rassau Stability Services Limited | PRO-003931 | CS-10936 | WP Grid Services 16 Limited | Rassau 400kV Substation | 103449-206913 |  | 2037-10-31
Rat Hall Mod App | PRO-003824 | CS-11828 | Downing Renewable Developments LLP | Burwell South 400kV Substation | 102489-205075 |  | 2032-10-30
Rat Hall Mod App | PRO-003824 | CS-11829 | Downing Renewable Developments LLP | Burwell South 400kV Substation | 102489-205076 |  | 2032-10-30
Rat Hall Mod App | PRO-003824 | CS-11830 | Downing Renewable Developments LLP | Burwell South 400kV Substation | 102489-205077 |  | 2032-10-30
Rat Hall Mod App | PRO-003824 | CS-11831 | Downing Renewable Developments LLP | Burwell South 400kV Substation | 102570-205177 |  | 2032-10-30
Rat Hall Mod App | PRO-003824 | CS-11832 | Downing Renewable Developments LLP | Burwell South 400kV Substation | 103119-206536 |  | 2032-10-30
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-06745 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | Rawhills BESS H1 Works | 1. Installation of a new 400kV double busbar bay at Coalburn North 400kV substation including a 400kV circuit breaker and associated equipment. 2. Installation of a new 400kV cable circuit (approx. 4.5km) between Coalburn North 400kV substation and the User’s site. 3. Installation of a 400kV line disconnector at the User’s site. 4. . Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07651 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07652 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07653 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07654 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07655 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07656 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07657 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07658 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07659 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07660 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07661 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2417 | Teviot to Gala North Reinforcements - A new 400kV double circuit OHL using L13 towers and triple Araucaria conductor from Teviot 400kV substation to Gala North 400kV substation which is approximately 57km. (SPT-RI-2417) | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-07662 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 2027-04-16
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-08290 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2058 | Coalburn North 400kV Substation - construction of a new 400kV substation, indicatively called Coalburn North, to connect into the Strathaven-Elvanfoot 400kV circuit. Construction of a new 400kV double busbar substation with a bus coupler circuit breaker, two feeder bays to connect onto the Strathaven-Elvanfoot 400kV circuit. | 2027-04-16
Rayleigh 1 Tertiary | PRO-000460 | CS-06929 | RAYLEIGH GREEN LIMITED | Rayleigh Main 400kV Substation | 100914 - 201831 | 1. Install earthing transformer 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install a tertiary cable box or bushings on SGT 6. 4. Install a 13kV Disconnector at the 13kV side connecting the tertiary to the Connection Assets for Users connection. | 2028-10-31
Rayleigh 2 Tertiary | PRO-000466 | CS-06930 | ENSO GREEN HOLDINGS J LIMITED | Rayleigh Main 400kV Substation | 100914 - 201845 | 1. Install earthing transformer 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install a tertiary cable box or bushings on SGT 3. 4. Install a 13kV Disconnector at the 13kV side connecting the tertiary to the Connection Assets for Users connection. | 2028-10-31
REBD / MURPHY IDNO PENRHOS REDEVELOPMENT | PRO-002730 | CS-09263 | Eclipse Power Networks Limited | Penrhos GSP | 101557-203099 | Rebuild Penrhos 132kV substation as a double busbar substation to allow for 2 feeder bays and 2 demand bays. | 2027-03-01
REBD / MURPHY IDNO PENRHOS REDEVELOPMENT | PRO-002730 | CS-09264 | Eclipse Power Networks Limited | Penrhos GSP | 101558-203101 | Install a second cable between the OHL from Penrhos and the Wylfa 132kV substation. | 2027-03-01
REBD / MURPHY IDNO PENRHOS REDEVELOPMENT | PRO-002730 | CS-10572 | Eclipse Power Networks Limited | Penrhos GSP | 102742-205536 Recell ATV |  | 2027-03-01
REBD / MURPHY IDNO PENRHOS REDEVELOPMENT | PRO-002730 | CS-10573 | Eclipse Power Networks Limited | Penrhos GSP | 102742-205535 Recell ATV |  | 2027-03-01
Recell at Penrhos (BEGA) | PRO-000330 | CS-05171 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101459-202896 | Infrastructure works for the Orthios Power connection at Penrhos 132kV substation. | 2025-10-30
Recell at Penrhos (BEGA) | PRO-000330 | CS-05172 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101557-203099 | Rebuild Penrhos 132kV substation as a double busbar substation to allow for 2 feeder bays and 2 demand bays. | 2025-10-30
Recell at Penrhos (BEGA) | PRO-000330 | CS-05173 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101458-202894 | Infrastructure works for the Orthios Distribution connection at Penrhos 132kV substation. | 2025-10-30
Recell at Penrhos (BEGA) | PRO-000330 | CS-05174 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101558-203101 | Install a second cable between the OHL from Penrhos and the Wylfa 132kV substation. | 2025-10-30
Recell at Penrhos (BEGA) | PRO-000330 | CS-05175 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101458-203111 | Connection works for Orthios Distribution at Penrhos 132kV substation – Building of 2 generator bays as requested by the customer | 2025-10-30
Red House Farm - Friston 400kV 249MW connection | PRO-003787 | CS-11323 | CAMBRIDGE POWER LIMITED | South Anglia Connection Node E 400kV Substation | 100381-200905 (CPL) |  | 2034-10-31
Red House Farm - Friston 400kV 249MW connection | PRO-003787 | CS-11324 | CAMBRIDGE POWER LIMITED | South Anglia Connection Node E 400kV Substation | 100602-020835 (CPL) |  | 2034-10-31
Red House Farm - Friston 400kV 249MW connection | PRO-003787 | CS-11325 | CAMBRIDGE POWER LIMITED | South Anglia Connection Node E 400kV Substation | 103040-206457 |  | 2034-10-31
Red House Farm - Friston 400kV 249MW connection | PRO-003787 | CS-11326 | CAMBRIDGE POWER LIMITED | South Anglia Connection Node E 400kV Substation | 103041-206458 |  | 2034-10-31
Red House Farm - Friston 400kV 249MW connection | PRO-003787 | CS-11327 | CAMBRIDGE POWER LIMITED | South Anglia Connection Node E 400kV Substation | 103093-206511 |  | 2034-10-31
Red Moss Farm | PRO-002613 | CS-09291 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2030-10-30
Red Moss Farm | PRO-002613 | CS-09292 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2030-10-30
Red Moss Farm | PRO-002613 | CS-09293 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | Red Moss - Redshaw GIS Bay | Installation of a 400kV GIS bay at Redshaw 400kV substation | 2030-10-30
Red Moss Farm | PRO-002613 | CS-09294 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | Red Moss - Redshaw Transformer | Installation of a 400/132kV 360MVA transformer at Redshaw 400/132 substation | 2030-10-30
Red Moss Farm | PRO-002613 | CS-09295 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | Red Moss - AIS Bay at Redshaw | Installation of a 132kV AIS bay at Redshaw 400/132kV substation | 2030-10-30
Red Moss Farm | PRO-002613 | CS-09296 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | Red Moss - 132kV Circuit | Installation of a 132kV circuit between Redshaw 400/132kV substation and Red Moss Farm 132kV substation. As part of the desktop exercise this 132kV circuit shall use two cables per phase to meet the capacity of the connection. The indicative cable route length is 4.7km | 2030-10-30
Red Moss Farm | PRO-002613 | CS-09297 | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation | Red Moss - Line Disconnector | Installation of a 132kV line disconnector at the Red Moss Farm 132kV substation | 2030-10-30
Redshaw Energy Park | PRO-003982 | CS-09741 | Redshaw Energy Park Developments LLP | Linnmill 132/33kV | SPT-RI-231 |  | 2031-10-30
Redshaw Energy Park | PRO-003982 | CS-09742 | Redshaw Energy Park Developments LLP | Linnmill 132/33kV | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2031-10-30
Redshaw Energy Park | PRO-003982 | CS-09743 | Redshaw Energy Park Developments LLP | Linnmill 132/33kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2031-10-30
Redshaw GSP | PRO-003212 | CS-09437 | SP Distribution plc | Linnmill GSP | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 2030-04-30
Redshaw GSP | PRO-003212 | CS-09438 | SP Distribution plc | Linnmill GSP | SPT-RI-3060 | Redshaw 132kV “B” Board - Establish a new 132kV double busbar substation, indicatively named Redshaw 132kV “B” board at the new Redshaw 400/132kV substation. The location of the SPT’s new 400kV substation (which this 132kV double busbar site will connect into) will be connected in the existing ZV Route corridor (STHA-ELVA / COAL-ELVA) as well as facilitate the new double circuit from Glenmuckloch under SPT-RI-236. The 400kV substation at Redshaw is being constructed under SPT-RI-2060. The 132kV double busbar substation to be established here will also require installation of two 400/132kV 360MVA transformers. (SPT-RI-3060) | 2030-04-30
Rhigos BESS | PRO-003613 | CS-10529 | KONA ASSET 4 LIMITED | South Wales West Connection Node A 400kV Substation | 101947-203995 (1) |  | 2037-10-30
Rhigos BESS | PRO-003613 | CS-10530 | KONA ASSET 4 LIMITED | South Wales West Connection Node A 400kV Substation | 102584-205197 (1) |  | 2037-10-30
Rhigos BESS | PRO-003613 | CS-10531 | KONA ASSET 4 LIMITED | South Wales West Connection Node A 400kV Substation | 102736-206768 |  | 2037-10-30
Rhigos BESS | PRO-003613 | CS-10532 | KONA ASSET 4 LIMITED | South Wales West Connection Node A 400kV Substation | 103410-206870 |  | 2037-10-30
Richborough | PRO-001214 | CS-04230 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | NGET-RI-21497-1 | At Richborough construct a new 400kV GIS double busbar substation to provide one HVDC connection and two circuit connection from Richborough to Canterbury North. | 2024-11-22
Richborough | PRO-001214 | CS-04231 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | NGET-RI-21497-2 | Build a new 400kV OHL double circuit from Richborough 400kV GIS substation to the new 400kV double busbar GIS substation at Canterbury North, strung with 2 x 500mm SQ AAAC conductor operating 65°C. | 2024-11-22
Richborough | PRO-001214 | CS-04232 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | NGET-RI-21497-3 | At Canterbury North 400kV substation, construct a new 400kV GIS double busbar substation linked to mesh corners 3 and 4 of the existing substation, consisting of 6 feeder bays, one bus-coupler bay, and one bus-section. In addition, two bays for MSCs or SVCs would be required if there is sufficient space. Turn the Canterbury North – Sellindge 2 and Canterbury - Kemsley 2 into the new 400kV GIS double busbar substation at Canterbury North. | 2024-11-22
Richborough | PRO-001214 | CS-04233 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | Thermal overload relief work. | Thermal overload relief work. | 2024-11-22
Riverside Bungalow Farm | PRO-004082 | CS-11863 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11864 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025a Peterhead - Rothienorman 400kV OHL Upgrade |  | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11865 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11866 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025c Peterhead 400kV Busbar |  | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11867 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-025d North East Reinforcement |  | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11868 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-026 Blackhillock 275kV QBs |  | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11869 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11870 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11871 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11872 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11873 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11874 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11875 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11876 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SHET-RI-199 Blackhillock 2 400kV Substation |  | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11877 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50°C operation to 275kV 65°C operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65°C,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 2033-10-31
Riverside Bungalow Farm | PRO-004082 | CS-11878 | QAIR RENEWABLES UK LIMITED | Blackhillock 2 400/33kV GSP Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 2033-10-31
Rochdale BESS | PRO-001805 | CS-07027 | Rochdale (BES) Ltd | Rochdale 275kV Substation | 101606-203230 | Infrastructure works at the substation for the generation connection of Morwind 300 Offshore Wind Farm. | 2027-07-30
Roger Hill Farm | PRO-003708 | CS-11419 | QAIR RENEWABLES UK LIMITED | Roger Hill Farm 132kV substation | SPT-RI-2058 | Coalburn North 400kV Substation - construction of a new 400kV substation, indicatively called Coalburn North, to connect into the Strathaven-Elvanfoot 400kV circuit. Construction of a new 400kV double busbar substation with a bus coupler circuit breaker, two feeder bays to connect onto the Strathaven-Elvanfoot 400kV circuit. | 2031-10-31
Roger Hill Farm | PRO-003708 | CS-11420 | QAIR RENEWABLES UK LIMITED | Roger Hill Farm 132kV substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 2031-10-31
Rosefield | PRO-001044 | CS-03697 | Rosefield Energyfarm Limited | East Claydon 400kV Substation | 100893-201792 | Extension of the existing East Claydon 400kV Substation Main and Reserve Busbars to accommodate the generator bay. | 2031-10-31
Rosefield | PRO-001044 | CS-03698 | Rosefield Energyfarm Limited | East Claydon 400kV Substation | 100893-201795 | 1. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT1. 2. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT2. | 2031-10-31
Rosefield | PRO-001044 | CS-12551 | Rosefield Energyfarm Limited | East Claydon 400kV Substation | 100893-201792 exp |  | 2031-10-31
Rosefield | PRO-001044 | CS-12552 | Rosefield Energyfarm Limited | East Claydon 400kV Substation | 102023-204178 (Rosefield) |  | 2031-10-31
Rothes III Wind Farm | PRO-000900 | CS-06009 | ROTHES III LIMITED | Dallas GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2028-06-30
Rothienorman 3 BESS | PRO-004236 | CS-11895 | ANESCO LIMITED | Rothienorman GSP | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2030-06-30
Rothienorman 3 BESS | PRO-004236 | CS-11896 | ANESCO LIMITED | Rothienorman GSP | SHET-RI-297 Rothienorman 400kV Busbar Extension |  | 2030-06-30
Rothienorman 3 BESS | PRO-004236 | CS-11898 | ANESCO LIMITED | Rothienorman GSP | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2030-06-30
Rowancraig Wind Farm | PRO-002455 | CS-09228 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV | SPT-RI-3102 | Glenglass to Cloud Hill 132kV circuit - A new 132kV circuit will be constructed between the Glenglass 132kV substation and the new Cloud Hill 132kV collector substation. At Glenglass 132kV substation, install a new 132kV feeder bay and associated DBB switchgear (circuit breaker, line isolator and DBB disconnector). From here install a new 132kV circuit to the Cloud Hill 132kV collector substation. The collector substation will accommodate the connection of the Cloud Hill 50MW Windfarm and Rowancraig 40MW Windfarm | 2028-10-30
Rowancraig Wind Farm | PRO-002455 | CS-09229 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2028-10-30
Rowancraig Wind Farm | PRO-002455 | CS-09230 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2028-10-30
Rowancraig Wind Farm | PRO-002455 | CS-09231 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2028-10-30
Rowancraig Wind Farm | PRO-002455 | CS-09232 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV | Cloud Hill SS Works - Rowancraig | At Cloud Hill substation, extend the substation compound and install one 132kV disconnector | 2028-10-30
Rugeley | PRO-001630 | CS-04577 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101469-202909 | 1. Extension of the existing Rugeley 400kV substation Main and Reserve Busbars to accommodate the User’s bay. 2. Works to facilitate the Category 4 Operational Tripping Scheme as described in the Bilateral Connection Agreement Appendix F3. | 2031-08-30
Rugeley | PRO-001630 | CS-04578 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04579 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04580 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04581 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04582 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2031-08-30
Rugeley | PRO-001630 | CS-04583 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04584 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04585 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-04586 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2031-08-30
Rugeley | PRO-001630 | CS-04587 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2031-08-30
Rugeley | PRO-001630 | CS-04588 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-08-30
Rugeley | PRO-001630 | CS-11435 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101469-202909 (IGP2) |  | 2031-08-30
Rugeley | PRO-001630 | CS-11436 | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation | 101486-202937 |  | 2031-08-30
Rutherend Farm | PRO-004530 | CS-10401 | ECOCEL ENERGY (STORAGE) LTD | East Kilbride 275kV Substation | SPT-RI-3474 - Kilmarnock South - Strathaven 400kV Reinforcement | It is proposed to re-conductor the 400kV corridor (XV route) from Kilmarnock South 400kV to Strathaven 400kV substations (approx. 35.0km). It is proposed to establish new HTLS conductors (Twin Curlew 525mm² ACCR at 210ºC) along XV route to achieve a Pre-Fault Summer continuous rating of 2690MVA. | 2033-10-31
Rutherend Farm | PRO-004530 | CS-10402 | ECOCEL ENERGY (STORAGE) LTD | East Kilbride 275kV Substation | SPT-RI-3826 (OHL) - Rutherend Farm 400kV Substation | Creation of a new Rutherend Farm 400kV substation is proposed to be establish at the customer site of Rutherend Farm (SPT-TOCO-3703) under SPT-RI-3826. The new Rutherend Farm 400kV substation is proposed to tee into both XV route circuits. Rutherend Farm 400kV substation will be a double busbar configuration established with AIS equipment given the number of required bays to facilitate the connection of Rutherend Farm. The required bay allocations are: • 2 x bays towards Kilmarnock South 400kV (XV Route) • 2 x bays towards Strathaven 400kV (XV Route) • 1 x 400kV bus coupler • 1 x bay for Rutherend Farm connection Given the substations location and requirement to only connect a single connection, allocation of spare bays has not been noted at this stage. Due to future fault levels on the 400kV busbars at Strathaven, space should be considered to be allocated at the new Rutherend 400kV substation for either 2 x series reactors or 2 x quad boosters to be installed on the circuits towards Strathaven. Although, this will require further confirmation on specification | 2033-10-31
Rutherend Farm | PRO-004530 | CS-10403 | ECOCEL ENERGY (STORAGE) LTD | East Kilbride 275kV Substation | SPT-RI-3826 (SS) - Rutherend Farm 400kV Substation | Creation of a new Rutherend Farm 400kV substation is proposed to be establish at the customer site of Rutherend Farm (SPT-TOCO-3703) under SPT-RI-3826. The new Rutherend Farm 400kV substation is proposed to tee into both XV route circuits. Rutherend Farm 400kV substation will be a double busbar configuration established with AIS equipment given the number of required bays to facilitate the connection of Rutherend Farm. The required bay allocations are: • 2 x bays towards Kilmarnock South 400kV (XV Route) • 2 x bays towards Strathaven 400kV (XV Route) • 1 x 400kV bus coupler • 1 x bay for Rutherend Farm connection Given the substations location and requirement to only connect a single connection, allocation of spare bays has not been noted at this stage. Due to future fault levels on the 400kV busbars at Strathaven, space should be considered to be allocated at the new Rutherend 400kV substation for either 2 x series reactors or 2 x quad boosters to be installed on the circuits towards Strathaven. Although, this will require further confirmation on specification | 2033-10-31
Rye House | PRO-003413 | CS-10272 | RYE HOUSE 10 RENEWABLES LIMITED | London North East Connection Node A | 102540-205146 (Rye House) |  | 2031-10-31
Rye House | PRO-003413 | CS-10273 | RYE HOUSE 10 RENEWABLES LIMITED | London North East Connection Node A | 103395-206855 (Rye House) |  | 2031-10-31
Rye House | PRO-003413 | CS-10274 | RYE HOUSE 10 RENEWABLES LIMITED | London North East Connection Node A | 103395-206856 (Rye House) |  | 2031-10-31
Rye House | PRO-003413 | CS-10275 | RYE HOUSE 10 RENEWABLES LIMITED | London North East Connection Node A | 103405-206865 |  | 2031-10-31
Rye House (Tertiary) | PRO-000564 | CS-06941 | KD 6A LIMITED | Rye House 400kV Substation | 100961-201916 | 1. Install a tertiary cable box or bushings on Rye House (SGT1). 2. Install a 13 kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13 kV Disconnector at the 13 kV side connecting tertiary to Connection Assets. 5. Extension of Rye House 400 kV substation to accommodate the works required for connection to the SGT1 tertiary. | 2037-10-31
Ryhall PV & BESS | PRO-004379 | CS-11940 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 101276-202522 1 |  | 2034-10-31
Ryhall PV & BESS | PRO-004379 | CS-11941 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 102626-205260 |  | 2034-10-31
Ryhall PV & BESS | PRO-004379 | CS-11942 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 102626-205261 (TICK) |  | 2034-10-31
Ryhall PV & BESS | PRO-004379 | CS-11943 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 102626-205262 |  | 2034-10-31
Ryhall PV & BESS | PRO-004379 | CS-11944 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 102626-205263 |  | 2034-10-31
Ryhall PV & BESS | PRO-004379 | CS-11945 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 103326-206767(I) |  | 2034-10-31
Ryhall PV & BESS | PRO-004379 | CS-11946 | KILNSIDE ENERGY PARK LIMITED | Ryhall 400kV Substation | 103326-206770(I) |  | 2034-10-31
SAE Usk 1 | PRO-003590 | CS-11958 | AFON WYSG ENERGY LIMITED | South Wales East Node A 275kV Substation | 103344-206793 |  | 2037-10-31
SAE Usk 1 | PRO-003590 | CS-11959 | AFON WYSG ENERGY LIMITED | South Wales East Node A 275kV Substation | 103403-206863 |  | 2037-10-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04885 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | Salamander Item 1 | Teeing off the existing 132V overhead lines between Peterhead Grange and St Fergus Substation and constructing a single 2km steel lattice tower 132kV double overhead circuit to the Salamander Offshore Wind Farm 132kV substation. This includes the installation of 2 x 132kV disconnector at the User’s site, on the Transmission Network side of the metering circuit breakers. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04886 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04887 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04888 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04889 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04890 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-025d | North East Reinforcement | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04891 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04892 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-151 | Peterhead – St Fergus 132kV Line Works – Overhead line works to bring the 132kV circuit to ground, including any required modifications. Design and installation of one 132kV circuit breaker with three 132kV disconnectors and associated protection and control equipment for each of the two circuits. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04893 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04894 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2030-03-31
Salamander Offshore Wind Farm | PRO-001512 | CS-04895 | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead 132KV Substation | SHET-RI-150 | Inverguie Tee – Peterhead 132kV Reconductoring – Reconductor approximately 6.7km of 132kV OHL between the Inverguie Tee and Peterhead 132kV substation. The circuit should be reconductored with a conductor capable of a minimum summer pre-fault rating of 226MVA | 2030-03-31
Sallachy Wind Farm | PRO-002137 | CS-07710 | WKN SALLACHY LIMITED | Cassley GSP | Sallachy Wind Farm | The sole use enabling works will include the offline installation of a 132kV Transformer Circuit Breaker, 110 and transformer disconnector,113 at Cassley 132/33kV GSP Substation | 2027-08-31
Sallachy Wind Farm | PRO-002137 | CS-07711 | WKN SALLACHY LIMITED | Cassley GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2027-08-31
Saltend North | PRO-002666 | CS-08415 | Northern Powergrid (Yorkshire) Plc | Saltend North GSP | 102686-205376 | 1. Construct a new Saltend North 275kV GIS substation with a double busbar arrangement to consist of space for 4 SGT bay, 4 feeder bays, 1 bus section and 2 bus couplers. 2. Establish a new 275kV turn-in circuit at the new Saltend North 275kV substation on the Hedon to Saltend South 275kV OHL circuit including all associated OHL droppers including bay population and reconfiguration works. | 2024-05-26
Saltend North BESS & PV | PRO-002236 | CS-10558 | EEB74 LIMITED | Hedon 275kV Substation | 033837-201650 I |  | 2035-10-30
Saltend North BESS & PV | PRO-002236 | CS-10559 | EEB74 LIMITED | Hedon 275kV Substation | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 2035-10-30
Saltend North BESS & PV | PRO-002236 | CS-10560 | EEB74 LIMITED | Hedon 275kV Substation | 102175-204384 |  | 2035-10-30
Saltend North BESS & PV | PRO-002236 | CS-10561 | EEB74 LIMITED | Hedon 275kV Substation | 102360-204779 | Uprating/Replacement of the following Circuit breakers at Creyke Beck 400kV substation X510, X130, X420, X430, X520, X620, X330, X1215, X905, X210, X1415, X320 | 2035-10-30
Saltend North GSP (Yorkshire) | PRO-002979 | CS-12321 | Northern Powergrid (Yorkshire) Plc | North Humber Connection Node B 132kV Substation | 102686-205375 North Humber CNB ex5 |  | 2039-10-31
Saltend North GSP (Yorkshire) | PRO-002979 | CS-12322 | Northern Powergrid (Yorkshire) Plc | North Humber Connection Node B 132kV Substation | 102686-205376 North Humber CNB |  | 2039-10-31
Saltend North GSP (Yorkshire) | PRO-002979 | CS-12323 | Northern Powergrid (Yorkshire) Plc | North Humber Connection Node B 132kV Substation | 104332-208439 |  | 2039-10-31
Saltend North GSP (Yorkshire) | PRO-002979 | CS-12324 | Northern Powergrid (Yorkshire) Plc | North Humber Connection Node B 132kV Substation | 104332-208440 |  | 2039-10-31
Sand Quarry Old Glasgow Road BESS | PRO-002706 | CS-11394 | GPC 1134 Ltd | Giffordland 400/132kV | SPT-RI-3052 - CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Rep. | CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Replacement | 2029-05-07
Sand Quarry Old Glasgow Road BESS | PRO-002706 | CS-11395 | GPC 1134 Ltd | Giffordland 400/132kV | SPT-RI-2710 | BU Route OHL Reconductor - As part of RIIO-T2 asset modernisation a number of assets across the transmission network have been identified for replacement. This TORI captures the asset modernisation work that is scheduled to be carried out on the 132kV OHL BU Route which runs between KILW-HUNF-HUNE at ~13km. The OHL circuit will be reconductored to achieve a minimum of 220MVA per circuit (Reconductor with 425mm² ‘Totara’ AAAC @ 75°C) | 2029-05-07
Sand Quarry Old Glasgow Road BESS | PRO-002706 | CS-11396 | GPC 1134 Ltd | Giffordland 400/132kV | SPT-RI-4122 |  | 2029-05-07
Sandy Knowe Wind Farm | PRO-000345 | CS-03704 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | Sandy Knowe Item 4 | Establish a tee point for the Sandy Knowe circuit into the Blackhill to Glenglass 132kV circuit. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-03705 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | Sandy Knowe Item 5 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-03708 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06016 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | Sandy knowe Item 1 | At Sandy Knowe wind farm 132kV substation, installation of one line isolator to connect to the Sandy Knowe-Glenglass 132kV circuit. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06017 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-007 | New Cumnock 275/132kV Substation | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06018 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06019 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06020 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06021 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | Sandy Knowe Item 2 | Installation of 132kV underground cable (approximately 7km), and an optical fibre, between Glenglass 132/33kV substation and Sandy Knowe wind farm substation. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06022 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | Sandy Knowe Item 3 | Installation of a line isolator in Glenglass substation. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06023 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06024 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-06025 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-07226 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-07227 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2027-10-31
Sandy Knowe Wind Farm | PRO-000345 | CS-07228 | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2027-10-31
Sanquhar II Wind Farm | PRO-000352 | CS-03706 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | Sanquhar II Item 2 | Installation of a 132kV underground cable (approximately 4km), and an optical fibre, betweenSanquhar II 132kV and Glenglass 132kV Substation. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-03707 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | Sanqhuar II Item 3 | At Glenglass substation, install a new 132kV switch bay and associated equipment and apparatus. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-03709 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-03710 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | Sanquhar II Item 1 | At Sanquhar II Substation, install one 132kV line disconnector to connect to the Sanquhar II to Glenglass 132kV circuit. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-03711 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | Sanquhar II Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F to the Bilateral Connection Agreement. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-03712 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-03713 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06026 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06027 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06028 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06029 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06030 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06031 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06032 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | Sandy Knowe Wind Farm H1 Works | At Glenglass 132/33kV substation a new 132kV double switchbay (consisting of five line isolators and two circuit breakers owned by the relevant transmission licensee) and associated apparatus will be installed. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06033 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-06034 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2026-07-31
Sanquhar II Wind Farm | PRO-000352 | CS-12192 | SANQUHAR II COMMUNITY WIND CO LTD | Sanquhar II Wind Farm Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2026-07-31
Sauchentree PV and BESS | PRO-006076 | CS-12509 | GREENTECH PROJECTS HOLDING UK LIMITED | Fraserburgh 2 GSP | SHET-RI-187 St Fergus 132kV Substation |  | 2033-10-30
Scaraben Offshore Wind Farm | PRO-002401 | CS-07840 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07841 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-25a |  | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07842 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-25b |  | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07843 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-25c |  | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07844 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-25d |  | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07845 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07846 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07847 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07848 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07849 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07851 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07852 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07853 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07854 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07856 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07857 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-179 |  | 2033-10-31
Scaraben Offshore Wind Farm | PRO-002401 | CS-07858 | SCARABEN OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 2033-10-31
Scarning | PRO-003275 | CS-11377 | CONNECTID 3 LIMITED | North Anglia Connection Node C 400kV Substation | 030447-030447 1 |  | 2034-10-31
Scarning | PRO-003275 | CS-11378 | CONNECTID 3 LIMITED | North Anglia Connection Node C 400kV Substation | 102456-205018 I |  | 2034-10-31
Scarning | PRO-003275 | CS-11379 | CONNECTID 3 LIMITED | North Anglia Connection Node C 400kV Substation | 102456-205019 I |  | 2034-10-31
Scarning | PRO-003275 | CS-11380 | CONNECTID 3 LIMITED | North Anglia Connection Node C 400kV Substation | 102996-206403 |  | 2034-10-31
Scatsta Greener Grid Park | PRO-001955 | CS-10303 | Statkraft UK Ltd | Scatsta 132kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 2028-10-31
Scatsta Greener Grid Park | PRO-001955 | CS-10304 | Statkraft UK Ltd | Scatsta 132kV Substation | SHET-RI-152 | Shetland ANM Scheme - ANM System on Shetland to manage flows across 600MW HVDC link (established under SHET-RI-053) from Kergord 132kV substation on Shetland to the Scottish mainland at an HVDC convertor station in the vicinity of Noss Head in Caithness. (SHET-RI-152) | 2028-10-31
Scatsta Greener Grid Park | PRO-001955 | CS-10305 | Statkraft UK Ltd | Scatsta 132kV Substation | Double Circuit - Scatsta | The construction of two new 20.35 km double 132 kV circuits, comprising Overhead Line (OHL) and Under Ground Cable (UGC) sections, from Kergord substation terminating on two new indoor 132 kV line disconnectors (1113 / 1213) installed within a Relevant Transmission Licensee’s building at Scatsta 132 kV substation | 2028-10-31
Scatsta Greener Grid Park | PRO-001955 | CS-10306 | Statkraft UK Ltd | Scatsta 132kV Substation | Bays - Scatsta | The double 132 kV circuits will be connected to Kergord substation via two new fully equipped 132 kV feeder circuit breaker bays, each bay comprising 132 kV busbar selection switches (1104 and 1106 / 1204 and 1206), 132 kV circuit breaker (1105 / 1205), 132 kV line disconnector (1103 / 1203) and associated protection equipment. | 2028-10-31
Scatsta1 Greener Grid Park | PRO-002669 | CS-08410 | Statkraft UK Ltd | Scatsta 132kV Substation | Scatsta1 ESS H1 SS Works | The 132 kV circuits will be connected to Kergord substation via two new fully equipped 132 kV feeder circuit breaker bays, complete with 2 x 132 kV busbar selection switches (1104 and 1106 / 1204 and 1206), 1 x 132 kV circuit breaker (1105 / 1205), 1 x 132 kV line disconnector (1103 / 1203) and associated protection equipment | 2028-10-31
Scatsta1 Greener Grid Park | PRO-002669 | CS-08411 | Statkraft UK Ltd | Scatsta 132kV Substation | Scatsta1 ESS H1 SS Works | The 132 kV circuits will be connected to Kergord substation via two new fully equipped 132 kV feeder circuit breaker bays, complete with 2 x 132 kV busbar selection switches (1104 and 1106 / 1204 and 1206), 1 x 132 kV circuit breaker (1105 / 1205), 1 x 132 kV line disconnector (1103 / 1203) and associated protection equipment | 2028-10-31
Scatsta1 Greener Grid Park | PRO-002669 | CS-08412 | Statkraft UK Ltd | Scatsta 132kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 2028-10-31
Scatsta1 Greener Grid Park | PRO-002669 | CS-08413 | Statkraft UK Ltd | Scatsta 132kV Substation | SHET-RI-152 | Shetland ANM Scheme - ANM System on Shetland to manage flows across 600MW HVDC link (established under SHET-RI-053) from Kergord 132kV substation on Shetland to the Scottish mainland at an HVDC convertor station in the vicinity of Noss Head in Caithness. (SHET-RI-152) | 2028-10-31
Scaw Law Wind Farm | PRO-004174 | CS-10065 | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation | SPT-RI-2862 OHL |  | 2036-10-31
Scaw Law Wind Farm | PRO-004174 | CS-10066 | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 2036-10-31
Scaw Law Wind Farm | PRO-004174 | CS-10067 | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 2036-10-31
Scaw Law Wind Farm | PRO-004174 | CS-10068 | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation | SPT-RI-3657 OHL |  | 2036-10-31
Scaw Law Wind Farm | PRO-004174 | CS-10069 | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation | SPT-RI-3657 SS |  | 2036-10-31
Scaw Law Wind Farm | PRO-004174 | CS-10070 | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation | Scaw Law Sole Enabling Works | 1. Install a 132kV double busbar bay at the new Craigenputtlock 400/132kV collector substation and associated switchgear (circuit breaker and DBB disconnectors) 2. Construct a new 132kV circuit between Craigenputtlock 400/132kV Collector Substation and Scaw Law Wind Farm with minimum 67MVA rating. 3. At Scaw Law Wind Farm substation install a 132kV line disconnector. | 2036-10-31
Scira-Dudgeon Extension | PRO-000507 | CS-06378 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 100381-200905 | 1. Extension of the Norwich Main 400kV AIS Substation at Main Busbar (M2) and Reserve Busbar (R2) to accommodate an OFTO bay. 2. Extension of the existing East Anglia operational intertripping scheme to include the connection. | 2030-01-01
Scira-Dudgeon Extension | PRO-000507 | CS-06379 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 100409-200941 | East Anglia NPS mitigation strategies. | 2030-01-01
Scira-Dudgeon Extension | PRO-000507 | CS-08264 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 032452-203187 | Extension of the existing 400kV substation for the construction of fully populated main and reserve bus section bays with circuit breakers, one new bus coupler bay and one new feeder bay to accommodate transfer of the Norwich Main – Bramford 1 feeder circuit | 2030-01-01
Scira-Dudgeon Extension | PRO-000507 | CS-08265 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 100881-201773 | Install two 225 Mvar MSCs at Norwich Main 400 kV substation. Extension of Norwich Main 400 kV substation to accommodate the new MSCs. | 2030-01-01
Scira-Dudgeon Extension | PRO-000507 | CS-08266 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 2030-01-01
Scira-Dudgeon Extension | PRO-000507 | CS-09730 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120 and X320 Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2030-01-01
Scira-Dudgeon Extension | PRO-000507 | CS-09731 | SHERINGHAM SHOAL AND DUDGEON EXTENSIONS PROJCO LIMITED | Norwich Main 400kV Substation | 102875-206098 | At Norwich Main 400kV: Replace circuit breakers X305, X605, X805 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2030-01-01
Sclenteuch Energy Park | PRO-002195 | CS-08477 | SCLENTEUCH ENERGY LIMITED | Sclenteuch Energy Park 132kV | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 2029-10-31
Sclenteuch Energy Park | PRO-002195 | CS-08478 | SCLENTEUCH ENERGY LIMITED | Sclenteuch Energy Park 132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-10-31
Scoop Hill Wind Farm | PRO-000327 | CS-03714 | Community Windpower Limited | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement. | 2027-10-31
Scoop Hill Wind Farm | PRO-000327 | CS-06035 | Community Windpower Limited | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 1 | At Moffat 132kV substation install two 132kV feeder circuit breakers and associated switch bays. | 2027-10-31
Scoop Hill Wind Farm | PRO-000327 | CS-06036 | Community Windpower Limited | Scoop Hill Wind Farm 132kV Substation | SPT-RI-229 - Moffat SGT3 | A new 400/132kV 240MVA transformer, and associated 400kV and 132kV circuit breaker bays, shall be installed at Moffat 400/132kV substation to increase the available generation capacity at the 132kV substation. | 2027-10-31
Scoop Hill Wind Farm | PRO-000327 | CS-06037 | Community Windpower Limited | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 2 | Install two sections of 2000mm² Cu XLPE cable out of Moffat 132kV substation of approximately 300m in length each. | 2027-10-31
Scoop Hill Wind Farm | PRO-000327 | CS-06038 | Community Windpower Limited | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 3 | Establish 2x 132kV circuit, incorporating 10km of underground cable and associated auxiliary cable, between Moffat 132kV Substation and Scoop Hill Wind Farm Substation | 2027-10-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11408 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-003 Cable |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11409 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-003 OHL |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11410 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-003 SS |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11411 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-2083 TBC |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11412 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-2815 Cable |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11413 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-2815 OHL |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11414 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | SPT-RI-2815 SS |  | 2030-07-31
Scottish Water Bonnybridge STW 60MW BESS | PRO-002410 | CS-11415 | Bluestone Energy Ltd | Bonnybridge 275/33kV Substation | Bonnybridge BESS H1 |  | 2030-07-31
Scottish Water Laigh Park STW | PRO-002413 | CS-12156 | Bluestone Energy Ltd | Braehead Park 132/33kV | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 2028-06-28
Scottish Water Laigh Park STW | PRO-002413 | CS-12157 | Bluestone Energy Ltd | Braehead Park 132/33kV | SPT-RI-3263 | Erskine 132kV Bus Section Circuit Breaker | 2028-06-28
Scottish Water Laigh Park STW | PRO-002413 | CS-12158 | Bluestone Energy Ltd | Braehead Park 132/33kV | SPT-RI-3788 | 3. Neilston 132kV Uprate to 25kA fault rating | 2028-06-28
Scottish Water Laigh Park STW | PRO-002413 | CS-12159 | Bluestone Energy Ltd | Braehead Park 132/33kV | SPT-RI-3789 | 4. Neilston SGT1 SGT2 SGT3B Load Management Scheme - A transformer load management scheme is required to manage the loadings across SGT1, SGT2 and SGT3B at Neilston 400/275/132kV substation and trip the appropriate non-firm connections to remove any measured overloads. The SPT LMS will be required to transfer the following signals to the User(s): • Stage 1 Signal at 95% of the transformer rating • Stage 2 Signal at 100% of the transformer rating • Stage 3 Signal at 120% of the transformer rating Note: These values will be subject to change following detailed design, User input and optimisation of the system The different stages have the following intended actions: • Stage 1 Signal: Provides an alarm to the connection warning of impending overload condition. • Stage 2 Signal: Will trip connections associated with this TORI as per queue order • Stage 3 Signal: Will trip all connections regardless of queue order (SPT-RI-3789) | 2028-06-28
Scottish Water Laigh Park STW | PRO-002413 | CS-12160 | Bluestone Energy Ltd | Braehead Park 132/33kV | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm² Lynx ACSR) and earthwire (70mm² Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm² Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 2028-06-28
Seagreen Phase 1A | PRO-000703 | CS-03694 | SEAGREEN 1A LIMITED | Cockenzie 400/275kV | Seagreen 1+ Enabling Works | 1. Installation of 275kV plant and apparatus at Cockenzie 275kV Substation which will form the connection to the transmission interface point, including busbars, disconnectors, earth witches, surge arresters, current and voltage transformers. 2. Modification of existing Bay No.3 at Cockenzie 275kV Substation, including relocation and replacement of existing assets as required. | 2028-04-01
Seagreen Phase 1A | PRO-000703 | CS-04280 | SEAGREEN 1A LIMITED | Cockenzie 400/275kV | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 2028-04-01
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08771 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08772 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08773 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08774 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08775 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08776 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08777 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08778 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08779 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08780 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08781 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08782 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08783 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08784 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08785 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 2033-10-31
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08786 | Shetland Offshore Wind Limited | Northern Shetland 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
SEC 1 BESS | PRO-003198 | CS-09951 | Bluestone Energy Ltd | Finnieston GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-07-17
SEC 1 BESS | PRO-003198 | CS-09952 | Bluestone Energy Ltd | Finnieston GSP | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 2031-07-17
Seggiecrook PV and BESS | PRO-006074 | CS-12507 | GREENTECH PROJECTS HOLDING UK LIMITED | Keith 3 GSP | SHET-RI-136 - Blackhillock Building Extension |  | 2035-10-31
Seggiecrook PV and BESS | PRO-006074 | CS-12508 | GREENTECH PROJECTS HOLDING UK LIMITED | Keith 3 GSP | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHET-RI-199) | 2035-10-31
Sellindge (Tertiary) | PRO-001067 | CS-05284 | PIVOTED POWER LLP | Sellindge 400kV Substation | 100536-201122 | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection. 4. Works required to connect User to the Sellindge Operational Tripping Scheme as described in Appendix F3. | 2028-10-31
Sellindge (Tertiary) | PRO-001067 | CS-05285 | PIVOTED POWER LLP | Sellindge 400kV Substation | 021497-033111 | Installation of Flexible AC Transmission Solutions (FACTS) and MSCs at Bolney, Ninfield and Richborough and associated works | 2028-10-31
Sellindge (Tertiary) | PRO-001067 | CS-05286 | PIVOTED POWER LLP | Sellindge 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 & 2 Circuits to provide a post fault winter rating of 3140MVA. | 2028-10-31
Sellindge (Tertiary) | PRO-001067 | CS-05287 | PIVOTED POWER LLP | Sellindge 400kV Substation | 021497-021497 | The works to establish the new Richborough 400/132kV Grid Supply Point. Including any Connection Asset works required for the Third Party supplied via the Grid Supply Point. | 2028-10-31
Sellindge (Tertiary) | PRO-001067 | CS-05288 | PIVOTED POWER LLP | Sellindge 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 2028-10-31
Sellindge (Tertiary) | PRO-001067 | CS-05289 | PIVOTED POWER LLP | Sellindge 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 2028-10-31
Sellindge (Tertiary) | PRO-001067 | CS-12691 | PIVOTED POWER LLP | Sellindge 400kV Substation | 102283-204612 |  | 2028-10-31
Sellindge Grid Stability Services | PRO-002206 | CS-07063 | SELLINDGE GRID SERVICES LIMITED | Sellindge 400kV Substation | 101670-203325 | GIS building extension and double GIS busbar extension of R3 and M3 at the new Sellindge Compound B 400kV substation to facilitate the connection of The User’s bay with ownership boundary as per CUSC 2.12.1 (f) (ii). | 2026-08-11
Sellindge West | PRO-003412 | CS-10549 | Sellindge West 10 Renewables Limited | East Kent connection node A 400kV Substation | 101901-203894 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single turn-in connection to Newchurch via the Dungeness – Sellindge 2 overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure Construction of 400kV Busbar to accommodate the OHL Turn-In connection and the Users Generator Bay. | 2033-10-31
Sellindge West | PRO-003412 | CS-10550 | Sellindge West 10 Renewables Limited | East Kent connection node A 400kV Substation | 103412-206872 |  | 2033-10-31
Selms Muir Solar & Battery Storage | PRO-001885 | CS-07365 | SP Distribution plc | Livingston East 132/33kV | SPT-RI-2323 |  | 2026-07-31
Selms Muir Solar & Battery Storage | PRO-001885 | CS-07366 | SP Distribution plc | Livingston East 132/33kV | Selms Muir Sole Enabling Works |  | 2026-07-31
SHBEC | PRO-001096 | CS-04748 | EP SHB LIMITED | South Humber Bank 400kV Substation | 101810-203711 | 1. Extend GIS busbar at South Humber Bank 400kV Substation and install the GIS interface point for the new bay 2. Install the Operational Tripping Schemes at South Humber Bank 400kV Substation | 2029-07-01
SHBEC | PRO-001096 | CS-04749 | EP SHB LIMITED | South Humber Bank 400kV Substation | 100711-201483 | Extend GIS Busbar at South Humber Bank 400kV Substation and install the GIS interface point for the new bay. | 2029-07-01
Sheilhill Battery Storage | PRO-002149 | CS-07549 | Sheilhill Battery Storage Limited | St Fergus | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Sheilhill Battery Storage | PRO-002149 | CS-07550 | Sheilhill Battery Storage Limited | St Fergus | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Sheilhill Battery Storage | PRO-002149 | CS-07551 | Sheilhill Battery Storage Limited | St Fergus | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Sheilhill Battery Storage | PRO-002149 | CS-07552 | Sheilhill Battery Storage Limited | St Fergus | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 2033-10-31
Sheilhill Battery Storage | PRO-002149 | CS-07553 | Sheilhill Battery Storage Limited | St Fergus | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 2033-10-31
Sheirdrim Wind Farm | PRO-001066 | CS-06042 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2032-04-01
Sheirdrim Wind Farm | PRO-001066 | CS-06043 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2032-04-01
Sheirdrim Wind Farm | PRO-001066 | CS-06044 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2032-04-01
Sheirdrim Wind Farm | PRO-001066 | CS-06045 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2032-04-01
Shepherds Rig Wind Farm | PRO-000511 | CS-03715 | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2024-07-30
Shepherds Rig Wind Farm | PRO-000511 | CS-03716 | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2024-07-30
Shepherds Rig Wind Farm | PRO-000511 | CS-03717 | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation | SPT-RI-211 | Construct a new 132kV switching station, named Holm Hill, and install a 132kV OHL circuit between the new site and the tee off points to Shepherds Rig and Lorg wind farms. At an appropriate tee-off point on the New Cumnock to Kendoon 132kV circuit, install the new Holm Hill 132kV Switching Station containing one 132kV circuit breaker with two associated disconnectors. Install ~8km of 132kV wood pole overhead line with High Temperature Low Sag (HTLS) EAGLE conductor (190°C, minimum summer pre-fault rating 295MVA) to the tee point between Shepherd’s Rig and Lorg wind farms. | 2024-07-30
Sheriff Faulds 1 | PRO-002783 | CS-10115 | BIG BATTERY (SHERIFF FAULDS FARM 1) LIMITED | Strathaven 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2026-10-30
Sheriff Faulds 1 | PRO-002783 | CS-10116 | BIG BATTERY (SHERIFF FAULDS FARM 1) LIMITED | Strathaven 275/33kV | SPT-TOCO-523 SS | Strathaven GSP (Asset Replacement) – Non Secured | 2026-10-30
Sheriff Faulds 1 | PRO-002783 | CS-10117 | BIG BATTERY (SHERIFF FAULDS FARM 1) LIMITED | Strathaven 275/33kV | SPT-TOCO-523 Cable | Strathaven GSP (Asset Replacement) – Non Secured | 2026-10-30
Shewalton Rd Solar Farm | PRO-002178 | CS-07988 | SP Distribution plc | Kilmarnock South 275/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2024-10-25
Shipley Road BESS | PRO-002553 | CS-09060 | CSE43 LIMITED | Sussex and Romney Connection Node B 400kV Substation | 102436-204965 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to a new 400kV substation via the Lovedean - Bolney overhead line circuit. • Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. • Construction of 400kV busbar to accommodate the OHL Tee-In connection and the Users Generator Bay. • Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 2031-10-21
Shipley Road BESS | PRO-002553 | CS-09061 | CSE43 LIMITED | Sussex and Romney Connection Node B 400kV Substation | 102347-204512 | Installation of a Reserve Busbar Section Circuit Breaker (X160) at Bolney 400kV Substation. | 2031-10-21
Shipley Road BESS | PRO-002553 | CS-09062 | CSE43 LIMITED | Sussex and Romney Connection Node B 400kV Substation | 011642-010177 | Hotwiring of the Bolney – Lovedean – Ninfield circuits to increase their thermal rating. | 2031-10-21
Shrewsbury GSP | PRO-002929 | CS-12637 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206802 Shrewsbery |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12638 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206805 Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12639 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103661-207262 Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12653 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206749 Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12654 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206802 Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12655 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation |  |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12656 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206804 Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12657 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206805- Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12658 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103661-207262 - shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12659 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206803 Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12660 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206802 / Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12661 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206749/Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12662 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206804/Shrewsbury |  | 2037-10-30
Shrewsbury GSP | PRO-002929 | CS-12663 | National Grid Electricity Distribution (West Midlands) Plc | Staffordshire Connection Node D 132kV Substation | 103309-206805 /Shrewsbury |  | 2037-10-30
Sinclair Offshore Wind Farm | PRO-003790 | CS-09709 | SINCLAIR OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Sinclair Offshore Wind Farm | PRO-003790 | CS-09710 | SINCLAIR OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-179 |  | 2033-10-31
Sinclair Offshore Wind Farm | PRO-003790 | CS-09711 | SINCLAIR OFFSHORE WIND FARM LIMITED | Longside 132kV Substation | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 2033-10-31
Sizewell C | PRO-000145 | CS-06046 | Sizewell C Limited | Sizewell 400kV Substation | 20834-4 | Reconductor the two Sizewell – Bramford double circuits | 2035-07-31
Sizewell C | PRO-000145 | CS-06047 | Sizewell C Limited | Sizewell 400kV Substation | 20834-5 | Circuit transfer of 4 Bramford – Sizewell 400kV circuits from the existing Sizewell B GIS substation to the new Sizewell C substation | 2035-07-31
Sizewell C | PRO-000145 | CS-06048 | Sizewell C Limited | Sizewell 400kV Substation | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 2035-07-31
Sizewell C | PRO-000145 | CS-06049 | Sizewell C Limited | Sizewell 400kV Substation | 20315S | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 2035-07-31
Sizewell C | PRO-000145 | CS-06050 | Sizewell C Limited | Sizewell 400kV Substation | NGET-RI-20834-1 | Installation of two 400kV 3000MVA reactors in the existing Sizewell 400kV GIS substation site by utilizing and populating the four spare bays on the existing GIS originally identified for future nuclear generator station and unit transformer connections. | 2035-07-31
Sizing John (Rainhill) | PRO-001581 | CS-06942 | SIZING JOHN LIMITED | Rainhill GSP | 101326-202646 | 1.Replace the 4 x 132kV SGT breakers (180, 280, 380, 480) at Rainhill substation | 2026-09-25
Sizing John (Rainhill) | PRO-001581 | CS-06943 | SIZING JOHN LIMITED | Rainhill GSP | 101326-202643 | 1. Establish a 132kV LV banked connection onto SGT1 to accommodate User’s connection 2. Install a 132kV Disconnector to provide isolation from the User’s circuit | 2026-09-25
Skelton Grange GSP (Yorkshire) | PRO-002980 | CS-11480 | Northern Powergrid (Yorkshire) Plc | Skelton Grange GSP | 102586-205198 |  | 2035-10-24
Skelton Grange GSP (Yorkshire) | PRO-002980 | CS-11481 | Northern Powergrid (Yorkshire) Plc | Skelton Grange GSP | 102586-205199 |  | 2035-10-24
Skelton Grange GSP (Yorkshire) | PRO-002980 | CS-11482 | Northern Powergrid (Yorkshire) Plc | Skelton Grange GSP | 102586-205200 |  | 2035-10-24
Skelton Grange GSP (Yorkshire) | PRO-002980 | CS-11483 | Northern Powergrid (Yorkshire) Plc | Skelton Grange GSP | 102586-205201 |  | 2035-10-24
Skelton Grange GSP (Yorkshire) | PRO-002980 | CS-11484 | Northern Powergrid (Yorkshire) Plc | Skelton Grange GSP | 102586-205202 |  | 2035-10-24
Slickly Wind Farm | PRO-001517 | CS-06523 | Slickly Wind Farm Limited | Slickly Wind Farm 132kV Substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 2029-12-12
Slickly Wind Farm | PRO-001517 | CS-06524 | Slickly Wind Farm Limited | Slickly Wind Farm 132kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2029-12-12
Slickly Wind Farm | PRO-001517 | CS-06525 | Slickly Wind Farm Limited | Slickly Wind Farm 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2029-12-12
Slickly Wind Farm | PRO-001517 | CS-06526 | Slickly Wind Farm Limited | Slickly Wind Farm 132kV Substation | no Scheme |  | 2029-12-12
Slickly Wind Farm | PRO-001517 | CS-06527 | Slickly Wind Farm Limited | Slickly Wind Farm 132kV Substation | Slickly Wind Farm H1 Works | Installation of a 132 kV line disconnector (113) connected to the TCA 132 kV Circuit Breaker (110) at the Slickly wind farm 132 kV substation. The 132 kV line disconnector (113) will connect to the incoming 7.5 km 132 kV circuit (comprising 0.5 km underground cable and 7 km of Trident wood pole overhead line) from Gills Bay 132 kV switching station. The 132 kV OHL will be connected to Gills Bay 132 kV switching station via a new fully equipped 132 kV double busbar feeder bay, comprising 132 kV line disconnector (703), 132 kV feeder circuit breaker (705) and 132 kV double busbar selection disconnectors (704/706). The 7.5 km 132 kV circuit between Gills Bay and Slickly terminates on an outdoor type 132 kV line disconnector (113) at Slickly wind farm 132 kV substation and a CSE structure/compound at Gills Bay. | 2029-12-12
Smeaton BESS | PRO-002635 | CS-09238 | KONA ASSET 3 LIMITED | Smeaton 400/275kV | Smeaton BESS H1 | Installing a new 400kV disconnector at Smeaton 400kV substation to enable a tee off connection from the existing busbars. | 2027-09-30
Smeaton BESS | PRO-002635 | CS-09239 | KONA ASSET 3 LIMITED | Smeaton 400/275kV | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 2027-09-30
Smeaton BESS | PRO-002635 | CS-09240 | KONA ASSET 3 LIMITED | Smeaton 400/275kV | SPT-RI-204 | Wishaw-Smeaton-Torness-Eccles Overload Protection Scheme -An overload protection scheme is proposed to be installed within the Wishaw – Smeaton – Torness – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following system outage conditions as specified in Appendix F of the Bilateral Connection Agreement - | 2027-09-30
Sofia Offshore Wind Farm | PRO-000404 | CS-06057 | SOFIA OFFSHORE WIND FARM LIMITED | Lackenby 400kV Substation | NGET-RI-31571 | Extend Lackenby 400kV substation to make available a single, skeletal OFTO bay for the relevant Transmission Licensee at the interface point. | 2026-01-30
Sofia Offshore Wind Farm | PRO-000404 | CS-06944 | SOFIA OFFSHORE WIND FARM LIMITED | Lackenby 400kV Substation | 031571-031571 | Extend the GIS busbars to the west of Lackenby 400kV substation to Onshore Transmissionprovide the customer’s connection bay. | 2026-01-30
Sofia Offshore Wind Farm | PRO-000404 | CS-06945 | SOFIA OFFSHORE WIND FARM LIMITED | Lackenby 400kV Substation | 100090-200245 | Drax-Thornton 1 circuit – Uprate existing quad zebra conductors to achieve required rating. | 2026-01-30
Somerford | PRO-001631 | CS-06946 | PD688IRO LTD | Minety 400kV Substation | 101488-202944 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish new bus bar, 33kV substation at Minety to be connected via new 400/33kV SGT8B 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2025-06-30
Somerford | PRO-001631 | CS-06947 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2025-06-30
Somerford | PRO-001631 | CS-06948 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2025-06-30
South Brook | PRO-002402 | CS-12648 | JBM Solar Limited | Melksham 400kV Substation | 102261-204486 |  | 2037-06-28
South Esk Solar Farm | PRO-001222 | CS-06058 | Scottish Hydro Electric Power Distribution Plc | Bridge of Dun GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2026-10-31
South Esk Solar Farm | PRO-001222 | CS-06059 | Scottish Hydro Electric Power Distribution Plc | Bridge of Dun GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2026-10-31
South Street BESS | PRO-004924 | CS-11448 | South Street BESS Limited | Partrick GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2031-06-30
South Street BESS | PRO-004924 | CS-11449 | South Street BESS Limited | Partrick GSP | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2031-06-30
South Street BESS | PRO-004924 | CS-11450 | South Street BESS Limited | Partrick GSP | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 2031-06-30
South Street BESS | PRO-004924 | CS-11451 | South Street BESS Limited | Partrick GSP | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 2031-06-30
South Street BESS | PRO-004924 | CS-11452 | South Street BESS Limited | Partrick GSP | SPT-RI-4076 | Partick GSP Voltage Control Scheme Upgrades - The existing AVC relay at Partick GSP is not suitable to accommodate reverse power flow through the Partick Grid Transformers. A T3 scheme will replace the AVC relays at Partick (and many other sites) with modern equivalent relays which can perform adequately with reverse power flow conditions | 2031-06-30
Southern Upland Way Farm | PRO-003838 | CS-10294 | QAIR RENEWABLES UK LIMITED | Galashiels 132/33kV | SPT-RI-151b | In order to provide GBSQSS compliant connections for additional generation requiring to export from Hawick/Galashiels to Eccles, it is proposed to construct a new 132kV double circuit tower line between Galashiels and Eccles, and remove the existing U and AT Routes. | 2031-07-31
Southern Upland Way Farm | PRO-003838 | CS-10295 | QAIR RENEWABLES UK LIMITED | Galashiels 132/33kV | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 2031-07-31
Southern Upland Way Farm | PRO-003838 | CS-10296 | QAIR RENEWABLES UK LIMITED | Galashiels 132/33kV | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 2031-07-31
Southern Upland Way Farm | PRO-003838 | CS-10297 | QAIR RENEWABLES UK LIMITED | Galashiels 132/33kV | SPT-RI-3660 |  | 2031-07-31
Southery | PRO-002172 | CS-07772 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101994-204128 | Installation of a new AIS double busbar 400kV substation between Burwell Main 400 kV and Walpole 400 kV with associated two feeder bays, space for a generation bay and a busbar coupler. Provide a single turn in connection of the new substation to the Burwell Main – Walpole OHL circuit 2 | 2031-10-30
Southery | PRO-002172 | CS-07773 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2031-10-30
Southery | PRO-002172 | CS-07774 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2031-10-30
Southery | PRO-002172 | CS-07775 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 2031-10-30
Southery | PRO-002172 | CS-07776 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Southery | PRO-002172 | CS-07777 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2031-10-30
Southery | PRO-002172 | CS-07778 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2031-10-30
Southery | PRO-002172 | CS-07779 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2031-10-30
Southery | PRO-002172 | CS-07780 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2031-10-30
Southery | PRO-002172 | CS-07781 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2031-10-30
Southery | PRO-002172 | CS-07782 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2031-10-30
Southery | PRO-002172 | CS-07783 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2031-10-30
Southery | PRO-002172 | CS-07784 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2031-10-30
Southery | PRO-002172 | CS-07785 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2031-10-30
Southery | PRO-002172 | CS-07786 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2031-10-30
Southery | PRO-002172 | CS-07787 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2031-10-30
Southery | PRO-002172 | CS-07788 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-30
Southery | PRO-002172 | CS-07789 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2031-10-30
Southery | PRO-002172 | CS-07790 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2031-10-30
Southery | PRO-002172 | CS-07791 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120 and X320 Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Southery | PRO-002172 | CS-07792 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Southery | PRO-002172 | CS-07793 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2031-10-30
Southery | PRO-002172 | CS-07794 | SSE SOUTHERY SOLAR LIMITED | Southery 400kV Substation | 101995-204129 | At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2031-10-30
Southfields | PRO-001632 | CS-06949 | PD688IRO LTD | Minety 400kV Substation | 101488-202940 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2025-06-30
Southfields | PRO-001632 | CS-06950 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2025-06-30
Southfields | PRO-001632 | CS-06951 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2025-06-30
Southfields Farm | PRO-001852 | CS-07338 | PD688IRO LTD | Minety 400kV Substation | 101488-202945 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 2028-10-31
Southfields Farm | PRO-001852 | CS-07339 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2028-10-31
Southfields Farm | PRO-001852 | CS-07340 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-10-31
Spalding Energy Expansion | PRO-000249 | CS-06062 | SPALDING ENERGY EXPANSION LIMITED | Spalding North 400kV Substation | NGET-RI-21339S | • To provide one generator bay. • To modify existing busbar protection to include the new generation connection. • To install ancillary services monitoring equipment. | 2030-10-30
Spalding Energy Expansion | PRO-000249 | CS-06063 | SPALDING ENERGY EXPANSION LIMITED | Spalding North 400kV Substation | NGET-RI-21765-1 | Extend and convert the existing Bicker Fen 400kV substation to a double busbar AIS substation with 4 feeder bays, 2 transformer bays, 1 bus coupler bays and 2 skeleton bus section bays to accommodating the existing 4 circuits and 2 transformers. Build 4 feeder bays, 2 transformer bays and one bus coupler and fully equip these bays. Modify the existing protection scheme to include 4 feeders, 2 transformers and one bus coupler. | 2030-10-30
Spalding PV and BESS Station | PRO-002768 | CS-08579 | ETP UK 1 LTD | Weston Marsh 400kV Substation | 102747-205542 | Extension of main and reverse busbar at Weston Marsh 400kV substation to facilitate connection of users generator bay. | 2033-07-30
Spalding PV and BESS Station | PRO-002768 | CS-08580 | ETP UK 1 LTD | Weston Marsh 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2033-07-30
Spalding PV and BESS Station | PRO-002768 | CS-08581 | ETP UK 1 LTD | Weston Marsh 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2033-07-30
Spennymoor | PRO-002698 | CS-08416 | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP | 101920-203930 | 1. Extend the existing Auto Clock Scheme. 2. Convert MC4 to provide a suitable connection point. 3. Retrofit and install a 400kV line feeder circuit breaker and bay. 4. Substation extension including fence line and cut and fill. 5. P & C modifications. | 2024-11-30
Spennymoor Greener Grid Park | PRO-002041 | CS-09692 | Statkraft UK Ltd | Spennymoor 400kV Substation | 101863-203825 | Extend the Busbar MC2 at Spennymoor 400kV to make provision for the User to connect their equipment | 2027-10-29
Spennymoor GSP (NE) | PRO-002970 | CS-12116 | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP | 101920-203929 Buck Head Farm |  | 2035-10-26
Spennymoor GSP (NE) | PRO-002970 | CS-12117 | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP | 101920-203930 Buck Head Farm |  | 2035-10-26
Spennymoor GSP (NE) | PRO-002970 | CS-12118 | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP | 102640-205307 (1) |  | 2035-10-26
Spennymoor GSP (NE) | PRO-002970 | CS-12119 | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP | 104232-208225 |  | 2035-10-26
Spennymoor PV & BESS | PRO-002035 | CS-09233 | CSE27 LIMITED | Spennymoor 400kV Substation | 101917-203914 | 1. Install Earthing Transformer on 13kV Tertiary Connection 2. Install 13kV Cable from Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting the Tertiary connection to Connection Assets for User’s connection. | 2032-07-30
Spennymoor PV & BESS | PRO-002035 | CS-11692 | CSE27 LIMITED | Spennymoor 400kV Substation | 101917-203915 |  | 2032-07-30
Spennymoor PV & BESS | PRO-002035 | CS-11693 | CSE27 LIMITED | Spennymoor 400kV Substation | 101917-203916 |  | 2032-07-30
Speyslaw Solar | PRO-001278 | CS-06067 | SPEYSLAW SOLAR LIMITED | Elgin GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 2025-06-30
Speyslaw Solar | PRO-001278 | CS-06068 | SPEYSLAW SOLAR LIMITED | Elgin GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 2025-06-30
Speyslaw Solar | PRO-001278 | CS-06069 | SPEYSLAW SOLAR LIMITED | Elgin GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2025-06-30
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04448 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | NPI A H1 Enabling Works | At Dounreay 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User will be the User side of the new 400kV disconnectors (X603/X703) at New Dounreay 400kV substation. | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04449 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04450 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04451 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04452 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04453 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04454 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04455 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04456 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04457 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-025d | North East Reinforcement | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04458 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04459 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04460 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04461 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04462 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04463 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04464 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 2030-12-31
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04465 | SPIORAD NA MARA LIMITED | Arnish Lewis Hub 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2030-12-31
Spittal BESS | PRO-003255 | CS-11675 | Field Spittal Ltd | Spittal 275kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2030-10-31
Spittal BESS | PRO-003255 | CS-11676 | Field Spittal Ltd | Spittal 275kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2030-10-31
Spittal BESS | PRO-003255 | CS-11677 | Field Spittal Ltd | Spittal 275kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2030-10-31
Spittal BESS | PRO-003255 | CS-11678 | Field Spittal Ltd | Spittal 275kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2030-10-31
Spittal BESS | PRO-003255 | CS-11679 | Field Spittal Ltd | Spittal 275kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2030-10-31
Springwell | PRO-001850 | CS-11980 | SPRINGWELL ENERGYFARM LIMITED | Navenby 400kV Substation | 104066-207998 |  | 2029-10-30
Springwell | PRO-001850 | CS-11981 | SPRINGWELL ENERGYFARM LIMITED | Navenby 400kV Substation | 104260-208277 |  | 2029-10-30
Springwell | PRO-001850 | CS-11982 | SPRINGWELL ENERGYFARM LIMITED | Navenby 400kV Substation | 104260-208278 |  | 2029-10-30
SSE Celtic Sea 1 | PRO-002405 | CS-08564 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08565 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08566 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08567 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08568 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08569 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08570 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2036-12-06
SSE Celtic Sea 1 | PRO-002405 | CS-08571 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 102444-204992 | Infrastructure works for the generation connection of SSE Celtic Sea Offshore wind farm. | 2036-12-06
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05408 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101392-202727 | Infrastructure works for the connection of the Fiddlers Ferry Battery Energy Storage at Fiddlers Ferry 275kV substation. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05409 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05410 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05411 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05412 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05413 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05414 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05415 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 2026-10-30
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05416 | SSE FIDDLERS FERRY BATTERY LIMITED | Fiddlers Ferry 275kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
St Asaph GSP | PRO-003005 | CS-12359 | SP MANWEB PLC | St Asaph GSP | 104579-209096 |  | 2037-10-31
St Asaph SSE | PRO-003816 | CS-08918 | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation | 102523-205123 | At Bodelwyddan 400 kV substation: 1. Extend the new busbar sections to make accommodate the Users first Bay | 2037-11-01
St Asaph SSE | PRO-003816 | CS-08919 | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation | 101986-204112 | Infrastructurew works to connect customer via a generator bay at BODE4 substation. This included the creation of a new substation sectiopn including section break (main and reserve) bus couple, a new feeder bay and the transpotition of a cicuit onto the new feeder bay. The circuit will be determined as part of the scheme to turn BODE4 a double turn in substation | 2037-11-01
St Asaph SSE | PRO-003816 | CS-08920 | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 2037-11-01
St Dennis Hendra | PRO-001133 | CS-04750 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 2024-10-31
St Dennis Hendra | PRO-001133 | CS-04751 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 2024-10-31
St Dennis Hendra | PRO-001133 | CS-04752 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 2024-10-31
St Dennis Hendra | PRO-001133 | CS-04753 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 2024-10-31
St Dennis Hendra | PRO-001133 | CS-04754 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 2024-10-31
St Dennis Hendra | PRO-001133 | CS-04755 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 2024-10-31
Stack Hill Solar and Storage | PRO-005105 | CS-12274 | RWE Renewables UK Solar and Storage Limited | Trent Valley South Connection Node B 400kV Substation. | 103562-207066 |  | 2034-10-30
Stack Hill Solar and Storage | PRO-005105 | CS-12275 | RWE Renewables UK Solar and Storage Limited | Trent Valley South Connection Node B 400kV Substation. | 104404-208518 |  | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08176 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 102167-204374 | Infrastructure works for Carbon Free/ Stallingborough 500MW Solar/BESS connection at Grimsby West 400kV busbar extension. This includes 1 x busbar extension and associated P&C, SCS mods and database change. At the time of the offer, it was assumed there would space within NG operational land for additional bay. | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08177 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08178 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08179 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101393-202729 | Extend Operational Tripping Scheme at South Humber Bank 400kV substation | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08180 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08181 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08182 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08183 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 0333496-0333496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08184 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08185 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08186 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08187 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101593-101593 | Uprate the Cottam- Staythorpe circuit 1, to provide winter post fault rating of 3300MVA This includes the cable section. | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08188 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08189 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08190 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08191 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08192 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08193 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08194 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2034-10-30
Stallingborough PV & BESS Station | PRO-003021 | CS-08195 | STALLINGBOROUGH ENERGY PROJECT LIMITED | Grimsby West 400kV Substation | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 2034-10-30
Stalybridge BESS | PRO-002036 | CS-12549 | CSE32 LIMITED | Stalybridge 275kV Substation | 101800-203685 |  | 2036-10-31
Stalybridge BESS | PRO-002036 | CS-12550 | CSE32 LIMITED | Stalybridge 275kV Substation | 104641-209342 |  | 2036-10-31
Staythorpe (BESS and PV) | PRO-001615 | CS-04520 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101368-202688 | Extend the Busbar at Staythorpe 400kV to make provision for the User to connect their generator bay | 2028-09-29
Staythorpe (BESS and PV) | PRO-001615 | CS-04521 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm² conductors to achieve a summer pre fault rating of 2490 MVA | 2028-09-29
Staythorpe (BESS and PV) | PRO-001615 | CS-04522 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm² conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm² 90°C conductor to achieve a pre fault summer rating of 2400 MVA | 2028-09-29
Staythorpe (BESS and PV) | PRO-001615 | CS-08902 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101912-203908 | Extend the Busbar at Staythorpe 400kV to make provision for the User to connect their generator bay | 2028-09-29
Stella North GSP (NE) | PRO-002467 | CS-11479 | NORTHERN POWERGRID (NORTHEAST) PLC | Stella North GSP | 101233-202457 |  | 2035-10-30
Stella South GSP (NE) | PRO-001510 | CS-12328 | NORTHERN POWERGRID (NORTHEAST) PLC | Borders Connection Node B 132 kV Substation | 104187-208129 (EX4) |  | 2039-10-30
Stella South GSP (NE) | PRO-001510 | CS-12329 | NORTHERN POWERGRID (NORTHEAST) PLC | Borders Connection Node B 132 kV Substation | 104188-208130 (EX4) |  | 2039-10-30
Stella South GSP (NE) | PRO-001510 | CS-12330 | NORTHERN POWERGRID (NORTHEAST) PLC | Borders Connection Node B 132 kV Substation | 104188-208142 (EX4) |  | 2039-10-30
Stella South GSP (NE) | PRO-001510 | CS-12389 | NORTHERN POWERGRID (NORTHEAST) PLC | Borders Connection Node B 132 kV Substation | 104188-208130 |  | 2039-10-30
Stella South GSP (NE) | PRO-001510 | CS-12390 | NORTHERN POWERGRID (NORTHEAST) PLC | Borders Connection Node B 132 kV Substation | 104476-208610 |  | 2039-10-30
Stirches Solar PV | PRO-001892 | CS-07323 | SP Distribution plc | Hawick GSP | SPT-RI-288 Hawick to Galashiels 132kV Reconfiguration | Hawick 132/33kV substation is currently supplied via two 132kV circuits from Gretna 400/132kV substation, with a 132kV circuit to Galashiels normally open at CB 205. With the proposed connection of Faw Side wind farm (250MW) it is proposed to reconfigure Hawick 132kV substation such that Hawick can be supplied from Galashiels and establish the Hawick / Galashiels 132kV circuit No.1 and No.2. Works at Galashiels will be required to terminate the double circuit from Hawick post reconfiguration. At Hawick, it is also proposed to install two new 132kV circuit breakers and a fourth 132kV circuit at Hawick with Poplar conductor:. The existing circuit breakers at Galashiels are of 600A and 800A. It is also proposed to replace the 600A circuit breakers 120 and 620 with a standard 2000A circuit breaker. | 2026-12-31
Stirches Solar PV | PRO-001892 | CS-07324 | SP Distribution plc | Hawick GSP | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 2026-12-31
Stirches Solar PV | PRO-001892 | CS-07325 | SP Distribution plc | Hawick GSP | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 2026-12-31
Stockhills Farm | PRO-004323 | CS-11318 | BSR APPLICATIONS LIMITED | Severn Connection Node A 400kv Substation | 102179-204389 (BSR) |  | 2037-10-31
Stockhills Farm | PRO-004323 | CS-11319 | BSR APPLICATIONS LIMITED | Severn Connection Node A 400kv Substation | 102179-204390 (BSR) |  | 2037-10-31
Stockhills Farm | PRO-004323 | CS-11320 | BSR APPLICATIONS LIMITED | Severn Connection Node A 400kv Substation | 103525-207005 |  | 2037-10-31
Stoke Bardolph | PRO-003405 | CS-10551 | Stoke Bardolph 10 Renewables Limited | Trent Valley South Connection Node D 400kV Substation | 100459-201024 (SB10RL) |  | 2034-10-31
Stoke Bardolph | PRO-003405 | CS-10552 | Stoke Bardolph 10 Renewables Limited | Trent Valley South Connection Node D 400kV Substation | 101554-203095 (SB10RL) |  | 2034-10-31
Stoke Bardolph | PRO-003405 | CS-10553 | Stoke Bardolph 10 Renewables Limited | Trent Valley South Connection Node D 400kV Substation | 101812-203717 | A new 400kV route to be established between the Sheffield area and the East Midlands, to aid with North to South flows of generation which consists of rationalisation of existing Chesterfield 275kV to Chesterfield 400kV. The Chesterfield 400kV will have 4x460MVA, 400/132kV SGT along with feeders connecting to Brinsworth and High Marnham | 2034-10-31
Stoke Bardolph | PRO-003405 | CS-10554 | Stoke Bardolph 10 Renewables Limited | Trent Valley South Connection Node D 400kV Substation | 103530-207013 (SB10RL) |  | 2034-10-31
Stoke Bardolph | PRO-003405 | CS-10555 | Stoke Bardolph 10 Renewables Limited | Trent Valley South Connection Node D 400kV Substation | 103531-207014 |  | 2034-10-31
STOR Field 9 BESS | PRO-002528 | CS-09313 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Inverkeithing GSP | SPT-RI-2905 |  | 2029-07-30
Stornoway Wind Farm | PRO-000346 | CS-06070 | STORNOWAY WIND FARM LIMITED | Arnish 275kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 2030-10-31
Stornoway Wind Farm | PRO-000346 | CS-06071 | STORNOWAY WIND FARM LIMITED | Arnish 275kV Substation | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 2030-10-31
Stornoway Wind Farm | PRO-000346 | CS-06072 | STORNOWAY WIND FARM LIMITED | Arnish 275kV Substation | Stornoway Item 1 | The Relevant Transmission Licensee will construct a 5km single circuit 132kV wood pole overhead line from a fully equipped 132kV feeder bay at Arnish 132kV substation to the windfarm site. The new 132kV line will terminate on the Relevant Transmission’s 132kV line isolator at the User’s 132/33kV windfarm substation. | 2030-10-31
Stracathro BESS | PRO-002392 | CS-08408 | Opdenergy UK 8 Limited | Stracathro BESS 275kV Substation | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2032-06-30
Stracathro BESS | PRO-002392 | CS-08409 | Opdenergy UK 8 Limited | Stracathro BESS 275kV Substation | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 2032-06-30
Stranoch Wind Farm | PRO-000127 | CS-06073 | Stranoch Windfarm Limited | Stranoch Wind 132/33kV Substation | SPT-RI-205 | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | 2026-10-09
Stranoch Wind Farm | PRO-000127 | CS-06074 | Stranoch Windfarm Limited | Stranoch Wind 132/33kV Substation | SPT-RI-206 | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | 2026-10-09
Stranoch Wind Farm | PRO-000127 | CS-06075 | Stranoch Windfarm Limited | Stranoch Wind 132/33kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 2026-10-09
Stranoch Wind Farm | PRO-000127 | CS-06076 | Stranoch Windfarm Limited | Stranoch Wind 132/33kV Substation | Stranoch Part 1 Enabling | 1. Installation of approximately 7.5km of 132kV overhead line from the Stranoch Wind Farm site to the Chirmorie Wind Farm tee point. 2. Installation of a 132kV line isolator at Stranoch Wind Farm substation. | 2026-10-09
Stranoch Wind Farm | PRO-000127 | CS-06077 | Stranoch Windfarm Limited | Stranoch Wind 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2026-10-09
Strath Oykel Wind Farm | PRO-004565 | CS-11427 | ENERGYFARM STRATH OYKEL LLP | Shin GSP | Shin 2 132/33kV Substation H1 132kV Double Switch Bay | 1. Installation of a 120 MVA 132/33 kV grid transformer (GT1), 33 kV metering circuit breaker (1T0) and 33 kV disconnector (1T7), on a suitable level platform provided by the user (the host Distribution Network Operator) at the site of the new Shin 2 GSP. 2. The sole enabling works will include the installation of a 132 kV Circuit Breaker (210) and 132kV Disconnector (213) at the new Shin 2 33 kV GSP substation compound, including 132 kV cabling and works to connect the grid transformer (GT1) | 2032-10-31
Strath Oykel Wind Farm | PRO-004565 | CS-11428 | ENERGYFARM STRATH OYKEL LLP | Shin GSP | SHET-RI-123 | Shin – Loch Buidhe 132kV Reconductoring | 2032-10-31
Strath Oykel Wind Farm | PRO-004565 | CS-11429 | ENERGYFARM STRATH OYKEL LLP | Shin GSP | SHET-RI-275 Shin 2 Tee and OHL Works |  | 2032-10-31
Strath Tirry | PRO-001363 | CS-06433 | Strath Tirry Wind Energy 2021 Ltd | Lairg GSP | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 2029-12-19
Strath Tirry | PRO-001363 | CS-06434 | Strath Tirry Wind Energy 2021 Ltd | Lairg GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2029-12-19
Strathaven South Wind Farm | PRO-000815 | CS-04146 | SP Distribution plc | Linnmill GSP | SPT-RI-180 | Coalburn SGTx Overload Protection Scheme: An overload protection scheme will be installed at Coalburn 400/132kV substation such that if SGT1 or SGT2 is overloaded, a trip signal will be issued to SPD at Linnmill GSP, and/or to SPT generation connected directly to Coalburn 132kV substation, to disconnect the appropriate generators to remove the overload. Following completion of Coalburn SGT3 (SPT-RI-144), this transformer will be added to the overload scheme proposed in this TORI (SPT-RI-180). | 2024-10-30
Strathaven South Wind Farm | PRO-000815 | CS-06078 | SP Distribution plc | Linnmill GSP | SPT-RI-178 | Linnmill Grid T1(2) Overload Protection Scheme | 2024-10-30
Strathaven West | PRO-003432 | CS-09654 | Clean Earth Energy Limited | Strathaven 275/33kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 2029-07-23
Strathleven GSP | PRO-003309 | CS-10828 | SP Distribution plc | Strathleven GSP | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 2026-08-10
Strathleven GSP | PRO-003309 | CS-10829 | SP Distribution plc | Strathleven GSP | SPT-RI-2691 | 1. Windyhill, Strathleven, Helensburgh and Sloy Load Management Scheme - The load management scheme required here shall monitor the two Windyhill to Sloy double circuits. This LMS shall monitor if one of the circuits is out of service and if an overload is detected on the adjacent circuit. Due to the configuration of the circuits in this area it will be required to interface with the 132kV circuit breakers at Sloy substation. The circuits to be monitored are the CK route and CL route. | 2026-08-10
Strathleven GSP | PRO-003309 | CS-10830 | SP Distribution plc | Strathleven GSP | SHET-RI-239 SS | Sloy 132kV Cross Boundary LMS – The provision of signals from Sloy switching station to the Relevant Transmission Licensee for inclusion in a Load Management Scheme (LMS) at Windyhill 132kV substation that will monitor if circuits are out of service and if an overload is observed on an adjacent circuit. The LMS requires circuit breaker status signals and analogue outputs from CTs and VTs at Sloy 132kV Switching Station on the Sloy – Strathleven/Windyhill (SWW1/SWW2) 132kV double circuit and the Sloy – Helensburgh/Windyhill (SHE2/SWE1) 132kV double circuit. | 2026-08-10
Strathleven GSP | PRO-003309 | CS-10831 | SP Distribution plc | Strathleven GSP | SHET-RI-239 Cable | Sloy 132kV Cross Boundary LMS – The provision of signals from Sloy switching station to the Relevant Transmission Licensee for inclusion in a Load Management Scheme (LMS) at Windyhill 132kV substation that will monitor if circuits are out of service and if an overload is observed on an adjacent circuit. The LMS requires circuit breaker status signals and analogue outputs from CTs and VTs at Sloy 132kV Switching Station on the Sloy – Strathleven/Windyhill (SWW1/SWW2) 132kV double circuit and the Sloy – Helensburgh/Windyhill (SHE2/SWE1) 132kV double circuit. | 2026-08-10
Strathleven GSP | PRO-003309 | CS-10832 | SP Distribution plc | Strathleven GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2026-08-10
Strathleven GSP | PRO-003309 | CS-10833 | SP Distribution plc | Strathleven GSP | SPT-RI-2784 | CL & CK Route Temperature Uprating - To alleviate overloads on the 132kV circuits on CL and CK Routes between Windyhill, Strathleven, Helensburgh and Sloy substations it is required to increase the operating temperature of the circuits from 50℃ to 65℃. This increase in operating temperature provides sufficient headroom to remove any intact overloads seen on the system. (SPT-RI-2784) | 2026-08-10
Strathleven GSP | PRO-003309 | CS-10834 | SP Distribution plc | Strathleven GSP | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 2026-08-10
Strathy South Wind | PRO-000183 | CS-06079 | SSE Generation Limited | Strathy South 132/33kV Substation | Strathy South | The provision of two 132kV transformer circuit breakers and two 132kV disconnectors on the 132kV side of both 132/33kV transformers at the User’s connection site. The disconnectors will also be coupled to approximately 4.5 km of new 293MVA/132kV single cable per phase underground cable constructed from the site of Strathy South 132/33kV Substation which will be coupled to a 17 km of new 293MVA 132kV single circuit Overhead Line constructed between a sealing end compound in the vicinity of Strathy Wood wind farm substation and Connagill 275/132kV substation (NYG2). The 132kV overhead line will be connected to Connagill 132kV substation via 132kV line disconnector, 132kV feeder circuit breaker and a 132kV busbar disconnector. | 2027-04-25
Strathy South Wind | PRO-000183 | CS-06080 | SSE Generation Limited | Strathy South 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2027-04-25
Strathy South Wind | PRO-000183 | CS-06081 | SSE Generation Limited | Strathy South 132/33kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 2027-04-25
Strathy South Wind | PRO-000183 | CS-06082 | SSE Generation Limited | Strathy South 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2027-04-25
Strathy South Wind | PRO-000183 | CS-06083 | SSE Generation Limited | Strathy South 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2027-04-25
Strathy South Wind | PRO-000183 | CS-10234 | SSE Generation Limited | Strathy South 132/33kV Substation | SHET-RI-191 | Strathy Switching Collector Station 132kV - Install 12km approximately of new 275kV double circuit overhead line between Connagill 275/132kV substation and a new 132kV switching collector station at Strathy North Wind Farm substation. The OHL double circuit will be built on steel lattice towers. This reinforcement is dependent upon TORI-106b Connagill 2nd SGT, looking at installing a new 480MVA transformer at Connagill substation (SGT1). If the works of this TORI are progressed, TORI-168 need to be cancelled and the offers issued to the following wind farms need to be amended as follows: -Armadale and Strathy South wind farms to update the TCA, One-off works and sole use works. -Kirkton wind farm to update the TCA and sole use works as per the new network design and double check the protection system configuration if additional devices are needed.(SHET-RI-191) | 2027-04-25
Strathy Wood | PRO-000154 | CS-06084 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 2026-09-30
Strathy Wood | PRO-000154 | CS-06085 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2026-09-30
Strathy Wood | PRO-000154 | CS-06086 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 2026-09-30
Strathy Wood | PRO-000154 | CS-06087 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 2026-09-30
Strathy Wood | PRO-000154 | CS-06088 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 2026-09-30
Strathy Wood | PRO-000154 | CS-06089 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | Strathy Wood Part 1 | 1. Construct a 132kV wood pole trident line over a distance of 5km between Strathy North 132/33kV substation and the new 132/33kV substation at Strathy Wood. The wood pole line will be coupled off one of the incoming 132kV line circuits at Strathy North 132kV substation, and terminated on a new 132kV transformer disconnector switch at Strathy Wood 132/33kV substation. 2. Provision and installation of a 132kV transformer circuit switcher (115) at Strathy Wood 132/33kV substation, installed on the 132kV side of the 132/33kV transformer unit. | 2026-09-30
Strathy Wood | PRO-000154 | CS-06090 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2026-09-30
Strathy Wood | PRO-000154 | CS-06091 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 2026-09-30
Strathy Wood | PRO-000154 | CS-06400 | RWE Renewables UK Onshore Wind Limited | Strathy Wood 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2026-09-30
Stromar Offshore Windfarm | PRO-001530 | CS-06468 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | Cygnus Item 1 | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at New Deer 2 400kV substation. | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06469 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06470 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06471 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06472 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06473 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06474 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-025d | North East Reinforcement | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06475 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06476 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06477 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06478 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06479 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06480 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06481 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06482 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 2033-10-31
Stromar Offshore Windfarm | PRO-001530 | CS-06483 | Stromar Offshore Wind Farm Limited | Greens 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 2033-10-31
Sulgrave Solar PV | PRO-001572 | CS-06952 | EDF ENERGY RENEWABLES LIMITED | East Claydon GSP (NGED EM) | 100893-201795 | 1. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT1. 2. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT2. | 2026-10-30
Sundhope Wind Farm | PRO-002767 | CS-08970 | Black Knowe Energy Limited | Sundhope 132kV Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 2033-05-30
Sundhope Wind Farm | PRO-002767 | CS-08971 | Black Knowe Energy Limited | Sundhope 132kV Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 2033-05-30
Sundhope Wind Farm | PRO-002767 | CS-08972 | Black Knowe Energy Limited | Sundhope 132kV Substation | SPT-RI-2418 | Under this TORI it is proposed to establish a second 132kV board at Teviot substation. This will require the installation of two 400kV GIS bays as well as two 400/132kV 240MVA transformers and their associated 132kV double busbar bays as well as a 132kV bus coupler. All 132kV switchgear is proposed to be Air Insulated Switchgear (AIS). | 2033-05-30
Sundon | PRO-001132 | CS-06092 | SUNDON BATTERY STORAGE LIMITED | Sundon 400kV Substation | 100306-200734 | 1. Extend Main busbar 1 and Reserve busbar 1 at Sundon 400kV subtation. 2. Installation of a new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish a new single busbar 33kV substation at Sundon to be connected via the new 400/33kV SGT | 2025-09-05
Sundon BESS | PRO-002039 | CS-09260 | CSE30 LIMITED | West Anglia Connection Node A 132kV Substation | 101926-203937 | 1. Extend Sundon 400kV Substation 2. Extend Main 1 and Reserve 1 busbars for the provision of one User Bay | 2037-10-30
Sundon BESS | PRO-002039 | CS-09261 | CSE30 LIMITED | West Anglia Connection Node A 132kV Substation | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2037-10-30
Sutton Courtenay | PRO-004276 | CS-11043 | TBC 004 LIMITED | Didcot 132kV Substation | 100940-201957 (1) |  | 2037-10-31
Sutton Courtenay | PRO-004276 | CS-11044 | TBC 004 LIMITED | Didcot 132kV Substation | 102219-204484 (1) |  | 2037-10-31
Sutton Courtenay | PRO-004276 | CS-11045 | TBC 004 LIMITED | Didcot 132kV Substation | 103541-207033 (1) |  | 2037-10-31
Sutton Courtenay | PRO-004276 | CS-11046 | TBC 004 LIMITED | Didcot 132kV Substation | 103557-207063 (1) |  | 2037-10-31
Sutton Courtenay | PRO-004276 | CS-11047 | TBC 004 LIMITED | Didcot 132kV Substation | 103560-207061 (1) |  | 2037-10-31
Sutton Courtenay | PRO-004276 | CS-11048 | TBC 004 LIMITED | Didcot 132kV Substation | 103560-207062 (1) |  | 2037-10-31
Swansea Greener Grid Park - Connection 1 | PRO-001120 | CS-08926 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 100774-201567 | Installation of a new disconnector at a tee point on the outgoing Swansea North – Rhigos 400kV circuit | 2024-08-31
Swansea Greener Grid Park - Connection 1 | PRO-001120 | CS-08927 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 101614-203242 | Extension of South Wales Operational Tripping Scheme | 2024-08-31
Swansea Greener Grid Park - Connection 1 | PRO-001120 | CS-08928 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2024-08-31
Swansea Greener Grid Park - Connection 1 | PRO-001120 | CS-08929 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2024-08-31
Swansea North Green Energy Centre | PRO-001794 | CS-07277 | SWANSEA NORTH GREEN NG LIMITED | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2028-10-31
Swansea North Green Energy Centre | PRO-001794 | CS-07303 | SWANSEA NORTH GREEN NG LIMITED | Swansea North 400kV Substation | 101614-203241 |  | 2028-10-31
Swansea North Green Energy Centre | PRO-001794 | CS-07304 | SWANSEA NORTH GREEN NG LIMITED | Swansea North 400kV Substation | 101614-203242 | Extension of South Wales Operational Tripping Scheme | 2028-10-31
Swansea North Green Energy Centre | PRO-001794 | CS-07305 | SWANSEA NORTH GREEN NG LIMITED | Swansea North 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2028-10-31
Swansea North Green Energy Centre | PRO-001794 | CS-12682 | SWANSEA NORTH GREEN NG LIMITED | Swansea North 400kV Substation | 103740-207388 |  | 2028-10-31
Sweet Briar Energy Park | PRO-005055 | CS-12083 | SWEET BRIAR 2 ENERGY PARK LIMITED | South Humber Connection Node A | 103626-207161 |  | 2035-10-30
Sweet Briar Energy Park | PRO-005055 | CS-12084 | SWEET BRIAR 2 ENERGY PARK LIMITED | South Humber Connection Node A | 104462-208589 (1) |  | 2035-10-30
Tacher Wind | PRO-002769 | CS-09409 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2025-08-31
Tacher Wind | PRO-002769 | CS-09410 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2025-08-31
Tacher Wind | PRO-002769 | CS-09411 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2025-08-31
Tacher Wind | PRO-002769 | CS-09412 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2025-08-31
Tacher Wind | PRO-002769 | CS-09413 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2025-08-31
Tacher Wind | PRO-002769 | CS-09414 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2025-08-31
Tacher Wind | PRO-002769 | CS-09415 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2025-08-31
Tacher Wind | PRO-002769 | CS-09416 | Clean Earth Energy Limited | Mybster 1 132/33kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2025-08-31
Tangy IV WF | PRO-001408 | CS-06415 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | Tangy IV Enabling Works | Construction of approximately 21.5 kilometres of 132kV OHL line (17.5km will be wood pole trident line the other 4km will be NEST structures) connecting between Crossaig Substation and Carradale GSP overhead line and the Tangy IV substation. This will include all associated Circuit Breakers and disconnectors required for the T point from the Crossaig-Carradale line. A 132kV circuit breaker and a 132kV disconnector will also be installed at Tangy IV 132/33KV substation | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06416 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06417 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06418 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06419 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06420 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06421 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2029-04-30
Tangy IV WF | PRO-001408 | CS-06422 | SSE Renewables Services (UK) Limited | Tangy IV 132KV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2029-04-30
Tarbuckle Hill Wind Farm | PRO-003045 | CS-09595 | ENERGIEKONTOR UK LTD | Cairnford GSP | SHET-RI-232 | Cairnford GSP 275kV tee | 2031-10-31
Tarenni | PRO-001641 | CS-04604 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 101506-202970 | 1. Eastern side GIS extension of Rhigos 400KV substation double busbars including AIS-GIS conversion module for provision of the User’s generator bay. [NOTE 1] 2. Replace AIS bus coupler bay with new GIS bus coupler to facilitate space for new generator bays within existing substation compound (avoiding development of contaminated land) [NOTE 1] 3. Installation of a new Commercial/Category 2 Operational Tripping Scheme at Rhigos 400kV substation. | 2030-12-31
Tarenni | PRO-001641 | CS-04605 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2030-12-31
Tarenni | PRO-001641 | CS-04606 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 033793-202898 | Replacement of the Walham - Cowley circuit 2.092km cable section to increase summer pre-fault rating from existing 877MVA to future requirement of at least 1341MVA | 2030-12-31
Tarenni | PRO-001641 | CS-04607 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2030-12-31
Tarland Battery Storage System | PRO-000922 | CS-04306 | Tarland Limited | Tarland GSP | Tarland BSS H1 Works | 1. At Tarland 132/33kV GSP substation, remove the existing 30MVA transformers and install two new 90MVA 132/33kV transformers and ancillary items. The transformers will be installed within the existing substation and cabled to the existing 33kV switchboard. | 2026-10-31
Tarland Battery Storage System | PRO-000922 | CS-04307 | Tarland Limited | Tarland GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2026-10-31
Tealing Solar & Storage | PRO-001501 | CS-04301 | SIRIUS ECODEV (TEALING) LTD | Tealing IDNO 132/33kV GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2027-10-31
Tealing Solar & Storage | PRO-001501 | CS-04302 | SIRIUS ECODEV (TEALING) LTD | Tealing IDNO 132/33kV GSP | SHET-RI-166 | Tealing – Arbroath 132kV Line Works - Overhead line works to bring the 132kV circuit to ground, including any required modifications. Design and installation of one 132kV circuit breaker with two 132kV disconnectors and associated protection and control equipment. | 2027-10-31
Tealing Solar & Storage | PRO-001501 | CS-04303 | SIRIUS ECODEV (TEALING) LTD | Tealing IDNO 132/33kV GSP | Tealing IDNO H1 Works | - Design and installation of a joint Relevant Transmission Licensee and Host Distribution Network Operator protection system covering the modification of the existing circuit protection to incorporate the new substation - Construction of a substation building large enough to accommodate all the required apparatus and associated metering, protection, batteries etc. - Design and installation of a 132kV transformer circuit breaker bay, including two 132kV disconnector switches, as well as all associated protection and control equipment to be housed in a space provided by the Contestable works substation. | 2027-10-31
Teindland Wind Farm | PRO-001821 | CS-06883 | TEINDLAND WIND FARM LIMITED | Blackhillock substation | Teindland Item 1 | Installation of a new 132kV line disconnector at the Wind Farm substation, connecting a new approximately 15km 132kV circuit comprised of mostly wood pole overhead line but with a short section of 132kV underground cable for entry into Blackhillock substation. This new circuit will be connected to a new 132kV indoor GIS double busbar circuit breaker bay located at Blackhillock substation. The 132kV busbar protection scheme at Blackhillock will also require to be updated | 2029-09-28
Teindland Wind Farm | PRO-001821 | CS-06884 | TEINDLAND WIND FARM LIMITED | Blackhillock substation | SHET-RI-079 | Additional 275/132kV SGT’s at Blackhillock - Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. (SHETL- RI-079) | 2029-09-28
Teindland Wind Farm | PRO-001821 | CS-09832 | TEINDLAND WIND FARM LIMITED | Blackhillock substation | SHET-RI-079 (a & b) | Blackhillock Additional SGTs- Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. The SGTs will be connected to the existing 275kV AIS double busbar and 132kV GIS double busbar at Blackhillock. Two new 275kV AIS transformer circuit breaker bays and two new GIS transformer circuit breaker bays will also be required (SHET-RI-079 (a & b)). | 2029-09-28
Templeton BESS | PRO-002593 | CS-09776 | Templeton Battery Storage Limited | Lyndhurst 132/33kV | SHET-RI-183 | New Dundee 132kV Substation – Construction of a new 132kV double busbar substation in Dundee, to replace Dudhope GSP. This busbar will be fed by turning in the current Dudhope/Milton of Craigie 132kV circuits. (SHET-RI-183) | 2027-10-31
Templeton BESS | PRO-002593 | CS-09777 | Templeton Battery Storage Limited | Lyndhurst 132/33kV | SHET-RI-255 Abernethy 400kV Substation | Construct a new 400kV busbar to facilitate the connection of a new 400/33kV GSP at Abernethy. | 2027-10-31
Teviot Wind Farm | PRO-000855 | CS-06682 | TEVIOT WF LIMITED | Teviot 400/132kV Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 2033-05-30
Teviot Wind Farm | PRO-000855 | CS-06683 | TEVIOT WF LIMITED | Teviot 400/132kV Substation | NGET 101074 - 202154 | 2. New OHL reinforcement from Teviot Substation to Harker 400kV substation. (NGET 101074 – 202154) | 2033-05-30
Teviot Wind Farm | PRO-000855 | CS-06684 | TEVIOT WF LIMITED | Teviot 400/132kV Substation | NGET 101076 - 202156 | 3. Offline rebuild of Harker 400kV Substation to enable the connection of scheme 101074 – 202154. (NGET 101076 – 202156) | 2033-05-30
THE CLEAN FUTURE | PRO-002019 | CS-07482 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101866-203832 | Extend Killingholme 400kV substation at main busbar 5 side and make provision for the connection of user bay. | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07483 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07484 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07485 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07486 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07487 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07488 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 0333496-0333496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07489 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07490 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07491 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07492 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101593-101593 | Uprate the Cottam- Staythorpe circuit 1, to provide winter post fault rating of 3300MVA This includes the cable section. | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07493 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07494 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07495 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07496 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2033-05-31
THE CLEAN FUTURE | PRO-002019 | CS-07497 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2033-05-31
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08795 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 102380-204827 | Installation of a new AIS double busbar 400kV substation (New Swaffham) between Walpole 400kV and Necton 400kV with associated two feeder bays, 1 Coupler Bay, 1 section bay and users generator bay. Provide a single turn in connection of the new substation to the existing 400kV OHL circuit 2 between Walpole 400kV and Necton 400kV. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08796 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100381-200905 | 1. Extension of the Norwich Main 400kV AIS Substation at Main Busbar (M2) and Reserve Busbar (R2) to accommodate an OFTO bay. 2. Extension of the existing East Anglia operational intertripping scheme to include the connection. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08797 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08798 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08799 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100881-201773 | Install two 225 Mvar MSCs at Norwich Main 400 kV substation. Extension of Norwich Main 400 kV substation to accommodate the new MSCs. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08800 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm² AAAC conductors to achieve a postfault winter rating of 3820 MVA | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08801 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08802 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08803 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08804 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08805 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101883-203859 | Uprating of the Coryton South – Rayleigh Main (A68A) 400kV circuit cables to achieve 3002MVA pre-fault summer rating | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08806 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm² AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08807 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08808 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm² AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08809 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08810 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08811 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08812 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100951-201898 | Uprate West Burton - High Marnham (A403) cable section to provide a postfault winter rating of 3100MVA | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08813 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08814 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08815 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm² conductor rating 2870MVA, 75˚C for winter intact condition. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08816 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08817 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08818 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08819 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08820 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08821 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 101975-204100 | 1. At Kings Lynn 400kV: Ensure circuit break X130 to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08822 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08823 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08824 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 102231-204467 | At Weston Marsh 400 kV substation install a 2750 MVA 16 Ohm series reactor between M1/R1 and M2/R2 busbars | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08825 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 2033-10-30
The Droves (formerly Swaffham PV & BESS) | PRO-003754 | CS-08826 | THE DROVES SOLAR FARM LIMITED | Swaffham 400KV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2033-10-30
Thorney Edge | PRO-002327 | CS-08691 | ARL Energy Development Limited | Cellarhead 400kV Substation | 102463-205036 | Extend the 400kV substation compound to facilitate the busbar extension for an additional generator bay. | 2037-11-30
Thorney Edge | PRO-002327 | CS-08692 | ARL Energy Development Limited | Cellarhead 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2037-11-30
Thorney Edge | PRO-002327 | CS-08693 | ARL Energy Development Limited | Cellarhead 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm² conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2037-11-30
Thorney Edge | PRO-002327 | CS-08694 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101474-202916 | Reconductor the existing Cellarhead-Drakelow 400 kV circuits 1 and 2 to achieve a pre fault summer rating of 2800 MVA | 2037-11-30
Thorney Edge | PRO-002327 | CS-08695 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101805-203692 | Install power control devices (8ohms) with push and pull capability on the Cellarhead-Drakelow 400kV circuits 1 and 2 | 2037-11-30
Thorney Edge | PRO-002327 | CS-08696 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 2037-11-30
Thorney Edge | PRO-002327 | CS-08697 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101905-203903 | nstall power control devices with push and pull capability (up to 8 ohm) at the Rugeley-Drakelow circuit | 2037-11-30
Thorney Edge | PRO-002327 | CS-08698 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101910-203902 | Uprating of the Feckenham - Walham 400kV circuit to achieve minimum summer pre-fault rating of 2550MVA | 2037-11-30
Thorney Edge | PRO-002327 | CS-08699 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101908-203900 | Uprate the Feckenham to Hams Hall 400Kv circuit to achieve a pre-fault summer rating of 2490 MVA | 2037-11-30
Thorney Edge | PRO-002327 | CS-08700 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101907-203905 | Reconductor the Drakelow – Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre-fault summer rating of 2490 MVA | 2037-11-30
Thorney Edge | PRO-002327 | CS-08701 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101939-203974 | Reconductor the Drakelow-Rugeley 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA | 2037-11-30
Thorney Edge | PRO-002327 | CS-08702 | ARL Energy Development Limited | Cellarhead 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2037-11-30
Thorney Edge | PRO-002327 | CS-08703 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101909-203901 | Reconductor the Ironbridge-Rugeley 400kV circuit with 2x620mm² conductor to achieve a pre-fault summer rating of 2490 MVA. | 2037-11-30
Thorney Edge | PRO-002327 | CS-08704 | ARL Energy Development Limited | Cellarhead 400kV Substation | 100478-201049 | Reconductor the Drakelow-Willington East 400kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA | 2037-11-30
Thorney Edge | PRO-002327 | CS-08705 | ARL Energy Development Limited | Cellarhead 400kV Substation | 101977-204102 | Cable section uprate of the Bishops Wood-Penn 275kV circuit to match the overhead line summer prefault rating of 925MVA | 2037-11-30
Thornhill BESS | PRO-004763 | CS-12532 | ELGIN ENERGY ES CO LIMITED | Craigiebuckler GSP | Thornhill BESS- Sole Enabling Works |  | 2032-09-30
Thornhill BESS | PRO-004763 | CS-12533 | ELGIN ENERGY ES CO LIMITED | Craigiebuckler GSP | SHET-RI-231-Aberdeen 132kV Protection Works |  | 2032-09-30
Thornhill BESS | PRO-004763 | CS-12534 | ELGIN ENERGY ES CO LIMITED | Craigiebuckler GSP | SHET-RI-278-New Craigiebuckler 132kV Substation |  | 2032-09-30
Thornton | PRO-001647 | CS-04697 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101551-203092 | Thornton 400kV substation extend busbars to make provision for connection of Users generator bay | 2031-10-31
Thornton | PRO-001647 | CS-04698 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2031-10-31
Thornton | PRO-001647 | CS-06953 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101093-202181 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works | 2031-10-31
Thornton | PRO-001647 | CS-06954 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Thornton | PRO-001647 | CS-06955 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2031-10-31
Thornton | PRO-001647 | CS-06956 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Thornton | PRO-001647 | CS-06957 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Thornton | PRO-001647 | CS-06958 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2031-10-31
Thornton | PRO-001647 | CS-06959 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Thornton | PRO-001647 | CS-06960 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2031-10-31
Thornton | PRO-001647 | CS-06961 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Thornton Facility | PRO-001484 | CS-06488 | BALWEN LIMITED | Thornton 400kV Substation | 101191- 202401 | Busbar extensions to provide space for the User’s connection bay | 2025-09-24
Thornton Facility | PRO-001484 | CS-06489 | BALWEN LIMITED | Thornton 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm² at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 2025-09-24
Thornton Facility | PRO-001484 | CS-06490 | BALWEN LIMITED | Thornton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2025-09-24
Thornton Facility | PRO-001484 | CS-06491 | BALWEN LIMITED | Thornton 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm² conductor and uprate the cable section to 3 cores per phase | 2025-09-24
Thornton Facility | PRO-001484 | CS-06492 | BALWEN LIMITED | Thornton 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2025-09-24
Thornton Facility | PRO-001484 | CS-06493 | BALWEN LIMITED | Thornton 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2025-09-24
Thornton Facility | PRO-001484 | CS-06494 | BALWEN LIMITED | Thornton 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2025-09-24
Thornton Facility | PRO-001484 | CS-06495 | BALWEN LIMITED | Thornton 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2025-09-24
Thornton Facility | PRO-001484 | CS-09439 | BALWEN LIMITED | Thornton 400kV Substation | 101191-205618 | Extension to CNI fence, gates and camera system | 2025-09-24
Thornton Facility | PRO-001484 | CS-09440 | BALWEN LIMITED | Thornton 400kV Substation | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2025-09-24
Thornton Facility | PRO-001484 | CS-09441 | BALWEN LIMITED | Thornton 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2025-09-24
Thornton Facility | PRO-001484 | CS-09442 | BALWEN LIMITED | Thornton 400kV Substation | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2025-09-24
Thornton Facility | PRO-001484 | CS-09443 | BALWEN LIMITED | Thornton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2025-09-24
Thornton Facility | PRO-001484 | CS-09444 | BALWEN LIMITED | Thornton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2025-09-24
Thornton Facility | PRO-001484 | CS-09445 | BALWEN LIMITED | Thornton 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 2025-09-24
Thornton Facility | PRO-001484 | CS-09446 | BALWEN LIMITED | Thornton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2025-09-24
Thornton Facility | PRO-001484 | CS-09447 | BALWEN LIMITED | Thornton 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 2025-09-24
Thornton Facility | PRO-001484 | CS-09448 | BALWEN LIMITED | Thornton 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2025-09-24
Thornton Facility | PRO-001484 | CS-09449 | BALWEN LIMITED | Thornton 400kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 2025-09-24
Thornton Facility | PRO-001484 | CS-09450 | BALWEN LIMITED | Thornton 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2025-09-24
Thornton Facility | PRO-001484 | CS-09451 | BALWEN LIMITED | Thornton 400kV Substation | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2025-09-24
Thornton Facility | PRO-001484 | CS-09452 | BALWEN LIMITED | Thornton 400kV Substation | 030613-030613 | Uprate the Cottam - Staythorpe (2) circuit to provide a post-fault summer rating of 2800 MVA | 2025-09-24
Thornton Facility | PRO-001484 | CS-09453 | BALWEN LIMITED | Thornton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2025-09-24
Thornton Facility | PRO-001484 | CS-09454 | BALWEN LIMITED | Thornton 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2025-09-24
Thornton Facility | PRO-001484 | CS-09455 | BALWEN LIMITED | Thornton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2025-09-24
Thornton Facility | PRO-001484 | CS-09456 | BALWEN LIMITED | Thornton 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 2025-09-24
Thornton Facility | PRO-001484 | CS-09457 | BALWEN LIMITED | Thornton 400kV Substation | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 2025-09-24
Thorpe Marsh 1 (Tertiary) | PRO-000470 | CS-06962 | ENSO GREEN HOLDINGS I LIMITED | Thorpe Marsh 400kV Substation | 100954-201902 | 1. Install a tertiary cable box or bushings on SGT 9 2. Install a 13kV cable (if required) from tertiary cable box or bushings to earthing transformer 3. Install an earthing transformer 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 2028-10-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06963 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 101504-202964 | Facilitate connection of Users generator bay on busbar 5 at Thorpe Marsh 400kV B substation | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06964 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06965 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 101504-202966 | Hotwire the 2x400mm² sections of the Bredbury – Stalybridge circuit to an operating temperature of 75°C. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06966 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06967 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06968 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06969 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06970 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06971 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06972 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06973 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-06974 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2027-01-30
Thorpe Marsh Energy Park | PRO-001620 | CS-12400 | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation | 101504-202964 | Facilitate connection of Users generator bay on busbar 5 at Thorpe Marsh 400kV B substation | 2027-01-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05318 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05327 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05328 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 031380-031380 | Hotwire the 4x400mm² sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05330 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101358-202678 | Hotwire the 2x400mm² sections of the conductor on the Bredbury – South Manchester 275kV circuit to an operating temperature of 75°C | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05333 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101571-203146 | At Thorpe Marsh B 400kv Substation: 1) Eastern extension of the 400kV AIS double busbar to a three section arrangement; comprising of 4 circuit feeder bays, 1 transformer bay, 1 bus coupler bay and 2 section breaker bays 2) Install SGT10 400/275kV 1100MVA Interbus transformers. 3) Connect and Commission SGT8 400/66kV 180MVA Transformer. 4) Busbar extension to provide space for Generator bay (User works). Associated OHL and cable works to transfer following circuits to Thorpe Marsh B 400kV substation: 1) Brinsworth 1 400kV circuit. 2) Drax 400kV circuit. 3) Eggborough 400kV circuit. 4) Stalybridge 400kV circuit. 5) West Melton 1 275kV circuit. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05334 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05335 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101571-203148 | Offline replacement of Thorpe Marsh 66kV substation | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05336 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101571-203149 | Establish Yorkshire Operation Tripping Scheme | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05337 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05338 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05339 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm² sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570mm² strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570mm²should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05340 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05341 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05342 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05343 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05344 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101511-202976 | Hotwire the 2x400mm² sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05345 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05346 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05347 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101482-202929 | Uprate Aldwarke to Brinsworth -Thurcroft cct 1 | 2030-10-30
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05348 | THORPE MARSH NG LTD | Thorpe Marsh 400kV Substation | 101359-202679 | Uprate Neepsend - Pitsmoor 275kV cable | 2030-10-30
Three Lochs Hydro | PRO-000716 | CS-04299 | Scottish Hydro Electric Power Distribution Plc | Grudie Bridge GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 2024-06-30
Three Lochs Hydro | PRO-000716 | CS-04300 | Scottish Hydro Electric Power Distribution Plc | Grudie Bridge GSP | SHET-RI-023 | Upgrade section of the Beauly - Grudie Bridge (BFN/BFS) 132kV double circuit line with two circuits of large conductors and increased design capacity. The upgrade conductor will be between the new Corriemoillie 132kV substation (Near Mossford). | 2024-06-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11783 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 103539-207029 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11784 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 103539-207031 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11785 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 103581-207098 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11786 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 104271-208302 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11787 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 104271-208301 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11914 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 102576-205187 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-11915 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 102576-205187 |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-12395 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 103539-207029 (EX3) |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-12396 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 103581-207098 (EX3) |  | 2039-10-30
Thurcroft GSP (Yorkshire) | PRO-002983 | CS-12397 | Northern Powergrid (Yorkshire) Plc | Thurcroft GSP | 104271-208301 (EX3) |  | 2039-10-30
Thurrock Power Station | PRO-000494 | CS-12679 | THURROCK FLEXIBLE GENERATION LIMITED | Tilbury 275kV Substation | 100048-200107 |  | 2025-06-30
Thurso BESS | PRO-001967 | CS-08479 | Stainland BESS Limited | Thurso South GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2027-06-30
Thurso BESS | PRO-001967 | CS-08480 | Stainland BESS Limited | Thurso South GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2027-06-30
Thurso BESS | PRO-001967 | CS-08481 | Stainland BESS Limited | Thurso South GSP | no Scheme |  | 2027-06-30
Thurso South BESS | PRO-003655 | CS-09568 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09569 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09570 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09571 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09572 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09573 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09574 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2030-10-31
Thurso South BESS | PRO-003655 | CS-09575 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2030-10-31
Tillbridge Solar | PRO-001126 | CS-05119 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2028-08-27
Tillbridge Solar | PRO-001126 | CS-05122 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm² conductor and uprate the cable section to 3 cores per phase | 2028-08-27
Tillbridge Solar | PRO-001126 | CS-05124 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2028-08-27
Tillbridge Solar | PRO-001126 | CS-05774 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100842-201687 | Attributable works | 2028-08-27
Tinnisburn Wind Farm | PRO-003997 | CS-09724 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | SPT-RI-231 |  | 2031-10-31
Tinnisburn Wind Farm | PRO-003997 | CS-09725 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | SPT-RI-2320 |  | 2031-10-31
Tinnisburn Wind Farm | PRO-003997 | CS-09726 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | SPT-RI-3434 | Wyseby Hill to Bloch Collector SS 132kV Circuit - Given the number of generation applications in this area and the arrangement at Wyseby Hill, it is proposed to establish a new shared collector substation. It is proposed to install a new 400kV double busbar bay and 400/132kV 240MVA transformer at Wyseby Hill 400kV substation planned to be constructed as part of SPT-RI-2320. From here approx. 9km of 132kV circuit shall be constructed to the Bloch collector substation. At Bloch collector substation, install a single 132kV busbar with a 132kV disconnector. | 2031-10-31
Tinnisburn Wind Farm | PRO-003997 | CS-09727 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | Tinnisburn - Circuit breaker bay | At Bloch Collector substation install a new 132kV circuit breaker bay with associated disconnectors. | 2031-10-31
Tinnisburn Wind Farm | PRO-003997 | CS-09728 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | Tinnisburn - 132kV circuit | Construct a new 132kV circuit from Bloch Collector SS to Tinnisburn Wind Farm. This circuit should be capable of 96MVA | 2031-10-31
Tinnisburn Wind Farm | PRO-003997 | CS-09729 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | Tinnisburn - 132kV line disconnector | At Tinnisburn Wind Farm install a 132kV line disconnector | 2031-10-31
Toftinghall BESS 1 | PRO-000960 | CS-06204 | Toftingall Wind Limited | Mybster 1 GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2025-08-31
Toftinghall BESS 1 | PRO-000960 | CS-06205 | Toftingall Wind Limited | Mybster 1 GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 2025-08-31
Toftinghall BESS 1 | PRO-000960 | CS-06206 | Toftingall Wind Limited | Mybster 1 GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2025-08-31
Tormsdale Windfarm | PRO-001904 | CS-07065 | ASUK HOLDCO 1 LIMITED | Mybster 3 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058) | 2027-06-30
Tormsdale Windfarm | PRO-001904 | CS-07066 | ASUK HOLDCO 1 LIMITED | Mybster 3 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2027-06-30
Tormsdale Windfarm | PRO-001904 | CS-07067 | ASUK HOLDCO 1 LIMITED | Mybster 3 132/33kV Substation | no Scheme |  | 2027-06-30
Tormywheel Extension WF | PRO-002355 | CS-08165 | SP Distribution plc | Bathgate 132/33kV | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 2026-10-29
Torrance Farm Extension 2 | PRO-001835 | CS-05400 | SP Distribution plc | Bathgate 132/33kV | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 2025-09-30
Trafford 2 BESS | PRO-004992 | CS-12597 | FUTURE POINT MANCHESTER LIMITED | Carrington 400KV Substation | 021619-031538 |  | 2038-10-30
Trafford 2 BESS | PRO-004992 | CS-12598 | FUTURE POINT MANCHESTER LIMITED | Carrington 400KV Substation | 104395-208505 |  | 2038-10-30
Trawsfynydd GSP | PRO-002957 | CS-12145 | SP MANWEB PLC | Trawsfynydd GSP | 102004-204152 Galileo |  | 2026-06-30
Trawsfynydd GSP | PRO-002957 | CS-12146 | SP MANWEB PLC | Trawsfynydd GSP | 103944-207819 Galileo |  | 2026-06-30
Trawsfynydd GSP | PRO-002957 | CS-12147 | SP MANWEB PLC | Trawsfynydd GSP | 104300-208340 Galileo |  | 2026-06-30
Trawsfynydd GSP | PRO-002957 | CS-12148 | SP MANWEB PLC | Trawsfynydd GSP | 104301-208341 Galileo |  | 2026-06-30
Troston Wind Farm | PRO-001115 | CS-06119 | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation | Troston Item 1 | Installation of a new 132kV disconnector at a tee point (Glenshimmeroch Collector Substation) on the New Cumnock / Blackcraig 132kV circuit and installation of approximately 5km of 132kV overhead line (POPLAR). | 2029-10-31
Troston Wind Farm | PRO-001115 | CS-06120 | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2029-10-31
Troston Wind Farm | PRO-001115 | CS-06123 | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2029-10-31
Troston Wind Farm | PRO-001115 | CS-12161 | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2029-10-31
Troston Wind Farm | PRO-001115 | CS-12162 | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation | SPT-RI-4205 | 4. Margree substation 132/33kV 120MVA T2 transformer and associated works - In order to accommodate the connection of Troston and Glenshimmeroch Wind farms via a shared solution as per customer’s request, it is proposed to establish a new 132/33kV transformer T2 at Margree 132/33kV collector substation. The scope of work comprises one 132kV circuit breaker and associated line isolator connecting onto a 132kV busbar as well as installation of 132/33kV transformer 120MVA (T2) and one 33kV indoor switchboard. (SPT-RI-4205) | 2029-10-31
Troston Wind Farm | PRO-001115 | CS-12163 | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation | SPT-RI-4212 | 8. Margree 132kV Collector Substation - In order to accommodate the connection of Troston, Glenshimmeroch, Margree and Fell Wind farms via a shared solution as per customer’s request, it is proposed to establish a new 132/33kV collector substation at Margree location (on the New Cumnock / Blackcraig 132kV circuit). The scope of work comprises installation of one 132kV circuit breaker and associated disconnectors, one 132kV busbar and one 132kV circuit breaker and disconnector (on the Blackcraig 132kV circuit). The creation of this new collector substation is noted as part of SPT-TOCO-2143, SPTTOCO-505, SPT-RI-458 & SPT-TOCO-2160. All TOCO Mod-App’s must be accepted to consider this contracted. Upon the acceptance of all 4 Mod-App’s, this TORI will supersede SPT-RI-274 - Glenshimmeroch Collector Substation. In this event, SPT-RI-274 will be withdrawn. Any abortive costs will be detailed in the charging section. (SPT-RI-4212) | 2029-10-31
Tummel Bridge | PRO-000949 | CS-06244 | SSE Generation Limited | Errochty 132/33kV Substation | Tummel Bridge / Errochty GSP Works | The Transmission Connection Asset Works comprise the following: 1. Install two 90MVA 132/33kV transformers; each with a GIS 33kV transformer Circuit Breaker and a 33kV Switch Disconnector, on suitable level platforms at the new site adjacent to the existing Errochty 132kV Substation; along with the associated cabling/metering/protection equipment. The 33kV Circuit Breakers and 33kV Switch Disconnectors will be owned and operated by the Relevant Transmission Licensee. 2. Install a double circuit 132kV underground cable from the 132kV busbar at the new site adjacent to the existing Errochty 132kV Substation compound, via 132kV switchgear, for a distance of approximately 0.2 km to a termination at two new bays on the existing 132kV double busbars at the Errochty 132kV Substation. 3. The User’s busbar side terminal of the 33kV Switch Disconnector will represent the ownership boundary between the Relevant Transmission Licensee and the User. | 2026-08-14
Twyn Hywel Cillfynydd | PRO-001497 | CS-04608 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2027-04-01
Twyn Hywel Cillfynydd | PRO-001497 | CS-04609 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2027-04-01
Twyn Hywel Cillfynydd | PRO-001497 | CS-06505 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 101231-202455 | 1. Double busbar extension of Cilfynydd 400kV substation to provide space for the user’s generator bay. | 2027-04-01
Twyn Hywel Cillfynydd | PRO-001497 | CS-12697 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 102342-204504 T |  | 2027-04-01
Upper Westown BESS Farm | PRO-004985 | CS-11879 | QAIR RENEWABLES UK LIMITED | Fiddes 2 132/33kV GSP Substation | SHET-RI-205 (1) |  | 2033-10-31
Upper Westown BESS Farm | PRO-004985 | CS-11880 | QAIR RENEWABLES UK LIMITED | Fiddes 2 132/33kV GSP Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 2033-10-31
Upper Westown BESS Farm | PRO-004985 | CS-11881 | QAIR RENEWABLES UK LIMITED | Fiddes 2 132/33kV GSP Substation | SHET-RI-319 |  | 2033-10-31
Uskmouth | PRO-000220 | CS-09600 | USKMOUTH ENERGY STORAGE LIMITED | Uskmouth 132kV Substation | 101490-202942 | 1. Extend the main and reserve busbars at Uskmouth 275kV and Uskmouth 132kV Substation by one bay to accommodate a new 240MVA (4th) SGT 2. Install and commission a new SGT Bay each at Uskmouth 275kV and Uskmouth 132kV substations 3. Install and commission a new 240MVA (4th) rated 275/132kV SGT | 2025-03-31
Uskmouth | PRO-000220 | CS-09601 | USKMOUTH ENERGY STORAGE LIMITED | Uskmouth 132kV Substation | 101949-204014 | 1. Extend the main and reserve busbars at Uskmouth 275kV Substation by one bay and main and reserve busbars at Uskmouth 132kV Substation by two bays to accommodate a new 240MVA (5th) SGT 2. Install and commission a new 275kV SGT bay at Uskmouth 275kV substation 3. Install and commission two new 132kV SGT bays at Uskmouth 132kV Substation 4. Install and commission a new 240MVA (5th) rated 275/132kV SGT with suitable cabling arrangements at Uskmouth 132kV Substation to form an SGT swing arrangement circuit | 2025-03-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11276 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101394-202731 | Infrastructure works at Alverdiscott 400kV substation for the generation connection of RWE Celtic offshore wind farm | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11277 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101394-202732 | Extension of the OTS at Alverdiscott to incorporate the RWE Celtic offshore windfarm | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11278 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11279 | Blue Gem Wind Limited | Pembroke 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11280 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11281 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11282 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11283 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11284 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11285 | Blue Gem Wind Limited | Pembroke 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11286 | Blue Gem Wind Limited | Pembroke 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11287 | Blue Gem Wind Limited | Pembroke 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11288 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11289 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 2031-10-31
Valorous Offshore Wind Farm | PRO-001383 | CS-11290 | Blue Gem Wind Limited | Pembroke 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 2031-10-31
Vanguard | PRO-000459 | CS-06132 | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation | 30648-1 | Establish two new feeder bays at Norwich 400kV substation for the connection of the new double circuit from Bacton. | 2025-12-01
Vanguard | PRO-000459 | CS-06133 | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation | 32339LI | Build a new double circuit from the new Bacton 400kV substation to the existing Norwich 400kV substation. | 2025-12-01
Vanguard | PRO-000459 | CS-06134 | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation | 32339SI | Build 400kV AIS double busbar substation in the Bacton area, including one skeleton generator bay, two feeder bays and a bus coupler and additional works to connect 600MW. | 2025-12-01
Vanguard East | PRO-000580 | CS-04397 | Norfolk Vanguard East Ltd | Vanguard East 275/66kV Offshore Substation | 100926-201852 | At Necton 400kV Substation: Extend the substation by 4 bays; A Main & Reserve Bus Section Bay, One Feeder Bay and one OFTO Bay. Transfer a circuit into the extended busbar section's feeder bay. Extension of the existing East Anglia Operational intertripping scheme. | 2028-04-01
Vanguard East | PRO-000580 | CS-11049 | Norfolk Vanguard East Ltd | Vanguard East 275/66kV Offshore Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 2028-04-01
Vanguard East | PRO-000580 | CS-11050 | Norfolk Vanguard East Ltd | Vanguard East 275/66kV Offshore Substation | 033802-033802 Mod App |  | 2028-04-01
Vanguard East | PRO-000580 | CS-11051 | Norfolk Vanguard East Ltd | Vanguard East 275/66kV Offshore Substation | 033804-033804 | At Necton 400kV substation: extend the substation by 5 bays; 1 main and 1 reserve section bay, 1 bus coupler bay and 2 feeder bays | 2028-04-01
Vanguard East | PRO-000580 | CS-11052 | Norfolk Vanguard East Ltd | Vanguard East 275/66kV Offshore Substation | 033804-201295 | At Necton 400kV substation: double turn in of the existing Walpole – Norwich Main OHL circuits | 2028-04-01
VPI Immingham B OCGT | PRO-000854 | CS-06975 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 101040-202081 | Extend Main and Reserve Busbar 1 at Humber Refinery 400kV substation | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06976 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm² conductor and uprate the cable section to 3 cores per phase | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06977 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06978 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06979 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06980 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06981 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06982 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06983 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 033837-201649 | At Creyke Beck 400kV Substation: Install an 8 Ohm series reactor, utilising the vacated Creyke Beck – Humber Refinery – Keadby feeder bay, with an additional feeder bay to be established by extension of Main and Reserve busbar 3. | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06984 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2026-01-16
VPI Immingham B OCGT | PRO-000854 | CS-06985 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 2026-01-16
Wakeleys BESS | PRO-003921 | CS-09098 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205312 | Construction of a new 400kV AIS double busbar substation (Wakeleys 400kV) between Enderby 400kV – Patford Bridge 400kV substations, comprising of 2 feeder bays and 1 bus coupler bay. | 2033-10-30
Wakeleys BESS | PRO-003921 | CS-09099 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205313 | Provide a single turn in of the 400kV OHL circuit 1 between Enderby 400kV – Patford Bridge 400kV–East Claydon 400kV substations to the Wakeleys 400kV substation. | 2033-10-30
Wakeleys BESS | PRO-003921 | CS-09100 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205314 | Extend Wakeleys 400kV substation main and reserve 1 busbar for the provision of one User bay. | 2033-10-30
Wakeleys BESS | PRO-003921 | CS-09101 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205315 | Works to facilitate the Category 4 Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. | 2033-10-30
Walpole | PRO-001114 | CS-05219 | HOLLYGREEN ENERGYFARM LIMITED | Walpole 400kV substations | 100248 – 200635 | 1. Install a tertiary cable box or bushing on SGT5. 2.Install a 13kV cable (if required) from tertiary cable box or bushing to earthing transformer. 3.Install an earthing transformer. 4.Install 13kV Disconnector connecting the tertiary connection to Connection Assets. | 2030-10-30
Walpole | PRO-001114 | CS-11854 | HOLLYGREEN ENERGYFARM LIMITED | Walpole 400kV substations | 030447-030447 (Walpole) |  | 2030-10-30
Walpole | PRO-001114 | CS-11855 | HOLLYGREEN ENERGYFARM LIMITED | Walpole 400kV substations | 100648-201339 (Walpole) |  | 2030-10-30
Walpole | PRO-001114 | CS-11860 | HOLLYGREEN ENERGYFARM LIMITED | Walpole 400kV substations | 101963-204085 (Walpole) |  | 2030-10-30
Walpole | PRO-001114 | CS-11861 | HOLLYGREEN ENERGYFARM LIMITED | Walpole 400kV substations | 103926-207790 |  | 2030-10-30
Walpole | PRO-001114 | CS-11862 | HOLLYGREEN ENERGYFARM LIMITED | Walpole 400kV substations | 104251-208260 |  | 2030-10-30
Walpole 1 (Tertiary) | PRO-000556 | CS-06986 | WALPOLE GREEN LIMITED | Walpole 400kV Substation | 100572-201217 | 1. Install a tertiary cable box or bushings on SGT 4 at Walpole 400/132kV substation. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Install an auto-close scheme on the section breakers at Walpole 132kV substation to allow a solid running arrangement to be automatically established post fault. | 2025-08-01
Walpole 2 (tertiary) | PRO-000505 | CS-06141 | ENSO GREEN HOLDINGS R LIMITED | Walpole 132kV Substation | 100648-201327 (1) |  | 2027-10-31
Walpole Grid Services Facility | PRO-003728 | CS-08792 | Conrad (Walpole) Limited | Walpole 400kV Substation | 102332-204492 | Extension to MBB1 adjacent to SGT5 to provide a suitable connection point. Associated Protection & Control. | 2025-05-30
Walsoken Battery | PRO-002690 | CS-10307 | Walsoken Limited | North Anglia Connection Node D 132kV Substation | No Attributable Works. |  | 2034-10-31
Waltham Cross BESS | PRO-002070 | CS-08657 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 101786-203725 | Construction of new Waltham Cross 400kV GIS Substation | 2033-11-30
Waltham Cross BESS | PRO-002070 | CS-08658 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 102534-205137 | Extend the 400kV substation busbar for an additional bay Database update for generator bay Busbar Protection | 2033-11-30
Waltham Cross BESS | PRO-002070 | CS-08659 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm² and 3M curlew 2x490mm² @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm² conductor | 2033-11-30
Waltham Cross BESS | PRO-002070 | CS-08660 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 033305-033305 | Uprate the ELST4A – SUND4 400kV circuit to achieve 1339 MVA pre-fault summer rating and 1676MVA post-fault winter rating | 2033-11-30
Waltham Cross BESS | PRO-002070 | CS-08661 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm² AAAC 75°C conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 2033-11-30
Waltham Cross BESS | PRO-002070 | CS-08662 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 101786-203721 | At Pelham 400 kV Substation: Install 3000MVA QBs on the (Pelham to Rye House 1&2 circuits (PELH4-1 - RYEH4A and PELH4-2 - RYEH4B circuits) | 2033-11-30
Waltham Cross BESS | PRO-002070 | CS-09084 | KD6B LIMITED | London North East Connection Node A 132kv Substation | 101916-203913 | 1. Install a tertiary cable box or bushings on the SGT1A 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to User Assets. | 2033-11-30
Walton Road Energy Project | PRO-002225 | CS-11951 | Lightsource Renewable UK Development Limited | Drakelow 400kV Substation | 102067-204243 |  | 2029-10-31
Walton Road Energy Project | PRO-002225 | CS-11952 | Lightsource Renewable UK Development Limited | Drakelow 400kV Substation | 104500-208964 |  | 2029-10-31
Warley | PRO-001113 | CS-06987 | WARLEY BATTERY STORAGE LIMITED | Warley 275kV Substation | 100307-200735 | 1. Site extension to facilitate the transmission works. 2.Install a tertiary cable box or bushings on the SGT 4. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2027-08-31
Warley (tertiary) | PRO-000555 | CS-06142 | WARLEY GREEN LIMITED | Warley 275kV Substation | 100654-201335 | Install earthing transformer on 13kV tertiary connection. Install 13kV cable connecting earthing transformer to the disconnecting circuit breaker. Install a 72.5kV, 40kA-rated disconnecting circuit breaker to the connection assets for the User’s connection. | 2023-07-31
Warley 2 | PRO-001848 | CS-07250 | CSE26 LIMITED | New Warley 400/132kV Substation | 101659-203307 | 1. Extend the existing Warley 275kV substation land boundary 2. Design and rebuild existing Warley 275kV four switch mesh corner substation into double bus bar substation to accommodate four overhead line feeder bays, two busbar coupler bays, two busbar section bays and four Supergrid transformer bays | 2036-10-31
Warley Battery Energy Storage | PRO-002321 | CS-08583 | LONDON AND ESSEX ENERGY LIMITED | Warley 275kV Substation | 101659-203307 | 1. Extend the existing Warley 275kV substation land boundary 2. Design and rebuild existing Warley 275kV four switch mesh corner substation into double bus bar substation to accommodate four overhead line feeder bays, two busbar coupler bays, two busbar section bays and four Supergrid transformer bays | 2029-10-31
Warley Battery Energy Storage | PRO-002321 | CS-08584 | LONDON AND ESSEX ENERGY LIMITED | Warley 275kV Substation | 101868-203835 | Provision for accommodating the User’s bay in the rebuilt Warley 275kV double busbar substation | 2029-10-31
Warley Battery Energy Storage | PRO-002321 | CS-08585 | LONDON AND ESSEX ENERGY LIMITED | Warley 275kV Substation | 101659-203313 | Reconductoring the existing 2x400mm² conductor on the Tilbury- Warley double circuit with 2x500mm² conductor to achieve a pre- Fault summer rating of 1120MVA | 2029-10-31
Warley Battery Energy Storage | PRO-002321 | CS-08586 | LONDON AND ESSEX ENERGY LIMITED | Warley 275kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 2029-10-31
Weaver Island 150MW BESS | PRO-002714 | CS-10136 | Weaver Island BESS Ltd | Elton (Merseyside 132kV Substation) | No Attributable Works. |  | 2037-10-30
Weirs Drove | PRO-001655 | CS-06988 | CARE POWER (BURWELL 1) LIMITED | Burwell 132kV Substation | 101462-202902 | Following the conversion of Burwell 400kV substation into a double busbar arrangement, extend main busbar 1 and reserve busbar 1 to accommodate the installation of a new 400/132kV 240MVA rated SGT. | 2028-10-31
Weirs Drove | PRO-001655 | CS-06989 | CARE POWER (BURWELL 1) LIMITED | Burwell 132kV Substation | 101462-202901 | 1. Install and commission a new 400kV Supergrid Transformer (SGT) bay at Burwell 400kV substation. 2. Install and commission switchgear at Burwell to include SGT HV and LV circuit breakers and associated bay assets. 3. Install and commission a new 400/132kV 240MVA rated SGT. 4. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. 5. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 2028-10-31
WELBAR ENERGY STORAGE | PRO-001735 | CS-04610 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101355-202675 | Extension of the existing Hams Hall 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06990 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06991 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm² conductor on the Feckenham-Walham 400 kV circuit with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06992 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06993 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm² conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 1820 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06994 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06995 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06996 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm² conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06997 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm² conductor. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06998 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm² conductor. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-06999 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-07000 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2026-10-30
WELBAR ENERGY STORAGE | PRO-001735 | CS-12459 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101355-202675 2 |  | 2026-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11964 | SolarTen Ltd | High Marnham 400kV Substation | 100451-201016 -SOLARTEN |  | 2034-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11965 | SolarTen Ltd | High Marnham 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2034-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11966 | SolarTen Ltd | High Marnham 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2034-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11967 | SolarTen Ltd | High Marnham 400kV Substation | 101812-203717-SOLARTEN |  | 2034-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11968 | SolarTen Ltd | High Marnham 400kV Substation | 101873-203846 (JGP) |  | 2034-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11969 | SolarTen Ltd | High Marnham 400kV Substation | 103759-207417 |  | 2034-10-30
Welbeck-Newark Solar Farm - PVDP | PRO-004138 | CS-11970 | SolarTen Ltd | High Marnham 400kV Substation | 101481-202928 (JGP) |  | 2034-10-30
West Boldon GSP (NE) | PRO-002618 | CS-08508 | NORTHERN POWERGRID (NORTHEAST) PLC | West Boldon 275/66kV Substation | 102315-204538 | Replacement of the CB S10 and S20 at West Boldon 275kV substation with 40kA nominal rating breaker. | 2024-11-30
West Boldon GSP (NE) | PRO-002618 | CS-08509 | NORTHERN POWERGRID (NORTHEAST) PLC | West Boldon 275/66kV Substation | 101539-203054 | At West Boldon 275kV substation: Replace the line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. (101539-203054) | 2024-11-30
West Botley High Impact Green Energy Hub | PRO-004435 | CS-11381 | TELIS ENERGY UK LIMITED | Botley West 400kV Substation | 101420-202783 Telis |  | 2037-10-31
West Botley High Impact Green Energy Hub | PRO-004435 | CS-11382 | TELIS ENERGY UK LIMITED | Botley West 400kV Substation | 102468-205044 Telis |  | 2037-10-31
West Botley High Impact Green Energy Hub | PRO-004435 | CS-11383 | TELIS ENERGY UK LIMITED | Botley West 400kV Substation | 102468-205043 Telis |  | 2037-10-31
West Botley High Impact Green Energy Hub | PRO-004435 | CS-11384 | TELIS ENERGY UK LIMITED | Botley West 400kV Substation | 103580-207097 Telis |  | 2037-10-31
West Botley High Impact Green Energy Hub | PRO-004435 | CS-11385 | TELIS ENERGY UK LIMITED | Botley West 400kV Substation | 103580-207101 Telis |  | 2037-10-31
West Burton | PRO-001323 | CS-11397 | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation | 101066-202140 |  | 2027-06-30
West Burton | PRO-001323 | CS-11398 | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2027-06-30
West Burton | PRO-001323 | CS-11399 | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2027-06-30
West Burton | PRO-001323 | CS-11400 | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm² conductor and uprate the cable section to 3 cores per phase | 2027-06-30
West Burton | PRO-001323 | CS-11401 | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation | 100816-201651 (1) |  | 2027-06-30
West Burton | PRO-001323 | CS-11402 | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2027-06-30
West Burton Solar Project | PRO-000561 | CS-06840 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100681-201437 | 1. At West Burton 400kV, facilitate the installation of 400kV Gas Insulated Switchgear (User Works), adjacent to banking substation 6 (X690) bay. 2. Modification to the busbar protection and substation control system at West Burton 400kV. 3. Replace circuit breaker X210 at West Burton 400kV with a new 63kA rated circuit breaker | 2028-11-30
West Burton Solar Project | PRO-000561 | CS-06841 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm² conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 2028-11-30
West Burton Solar Project | PRO-000561 | CS-06842 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2028-11-30
West Burton Solar Project | PRO-000561 | CS-06843 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm² conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm² conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 2028-11-30
West Grimsby Farm (DNO) | PRO-002619 | CS-08517 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 2035-10-31
West Grimsby Farm (DNO) | PRO-002619 | CS-08518 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 101669-203323 | Infrastructure works at the Grimsby West 400kV substation for the addition of an SGT transformer to the 132kV substations to enable a customer connection. | 2035-10-31
West Grimsby Farm (DNO) | PRO-002619 | CS-08519 | Northern Powergrid (Yorkshire) Plc | Grimsby West GSP | 102718-205492 | 400kV busbar extension to accommodate new SGT bay Busbar and C Modifications SCS modifications. | 2035-10-31
West Haddon | PRO-003820 | CS-08923 | SSE DE SOLAR HOLDCO LIMITED | West Haddon 400kV Substation | 102603-205227 | 1. Construct a new 400kV double busbar substation. 2. Provide a single turn in of the East Claydon-Partford Bridge- Enderby 400kV circuit 1 for the new substation (Name: West Haddon 400 kV; TBC). | 2039-10-01
West Melton GSP (Yorkshire) | PRO-002984 | CS-11882 | Northern Powergrid (Yorkshire) Plc | West Melton GSP | 102406-204927 |  | 2039-10-31
West Melton GSP (Yorkshire) | PRO-002984 | CS-11883 | Northern Powergrid (Yorkshire) Plc | West Melton GSP | 102408-204929 |  | 2039-10-31
West Melton GSP (Yorkshire) | PRO-002984 | CS-11884 | Northern Powergrid (Yorkshire) Plc | West Melton GSP | 102409-204930 |  | 2039-10-31
West Melton GSP (Yorkshire) | PRO-002984 | CS-11885 | Northern Powergrid (Yorkshire) Plc | West Melton GSP | 102410-204931 |  | 2039-10-31
West Oxfordshire Energy Park | PRO-004296 | CS-10032 | LOW CARBON SOLAR PARK 43 LIMITED | Chiltern Connection Node D 400kV | 103463-206999 | Replacement, or modification, of existing towers and associated OHL works to facilitate a double turn-in connection into Chiltern Connection Node D 400kV substation via the Cowley – Walham circuit 1 & Cowley– Minety circuit 2 overhead line circuits | 2037-10-31
West Oxfordshire Energy Park | PRO-004296 | CS-10033 | LOW CARBON SOLAR PARK 43 LIMITED | Chiltern Connection Node D 400kV | 103463-206932 | Extension of the 400kV Busbars at Chiltern Connection Node D 400kV substation | 2037-10-31
West Pitnacree Solar | PRO-004066 | CS-11430 | GREENTECH PROJECTS HOLDING UK LIMITED | Coupar Angus 2 GSP | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm²) and will operate at 75°C to give a minimum summer pre-fault rating of 176MVA | 2031-10-31
West Pitnacree Solar | PRO-004066 | CS-11431 | GREENTECH PROJECTS HOLDING UK LIMITED | Coupar Angus 2 GSP | SHET-RI-184 | Coupar Angus 2 Tee – Establish a new 132kV tee point of the HCS circuit between Coupar Angus GSP and Tealing/Charleston Tee for the connection to a new Coupar Angus 2 132/33kV GSP substation | 2031-10-31
West Pitnacree Solar | PRO-004066 | CS-11432 | GREENTECH PROJECTS HOLDING UK LIMITED | Coupar Angus 2 GSP | Coupar Angus 2 Bays | Installation of 2x 132kV circuit breakers and 132kV disconnectors at the new Coupar Angus 2 132/33kV GSP substation compound, including 132kV cabling and works to connect the grid transformers. | 2031-10-31
West Torrisdale | PRO-000944 | CS-06255 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2028-05-31
West Torrisdale | PRO-000944 | CS-06256 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 2028-05-31
West Torrisdale | PRO-000944 | CS-06257 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 2028-05-31
West Torrisdale | PRO-000944 | CS-06258 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2028-05-31
West Torrisdale | PRO-000944 | CS-06259 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2028-05-31
West Torrisdale | PRO-000944 | CS-06260 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2028-05-31
West Torrisdale | PRO-000944 | CS-06272 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | West Torrisdale Wind Farm H1 works | 1) replace a Carradale GSP existing 2 x 60MVA 132/33kV Transformers with higher rated 2 x 120MVA 132/33kV 2) replace existing 33kV transformer circuit breaker and cabling | 2028-05-31
West Torrisdale | PRO-000944 | CS-07393 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2028-05-31
West Weybridge | PRO-003410 | CS-10565 | West Weybridge 10 Renewables Limited | London West Connection Node B 400kV Substation | 103278-206719 (1) |  | 2038-10-31
West Weybridge | PRO-003410 | CS-10566 | West Weybridge 10 Renewables Limited | London West Connection Node B 400kV Substation | 103429-206890 |  | 2038-10-31
West Weybridge | PRO-004324 | CS-09870 | EL (WEST WEYBRIDGE) LIMITED | West Weybridge 275kV Substation | 100955-201904 | 1. Install a tertiary cable box or bushings on SGT 2. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2027-10-31
West Weybridge (Tertiary) | PRO-000552 | CS-07001 | EL (WEST WEYBRIDGE) LIMITED | West Weybridge 275kV Substation | 100955-201904 | 1. Install a tertiary cable box or bushings on SGT 2. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 2025-10-31
Wether Hill | PRO-001527 | CS-04352 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-2094 | Quantans Hill to Holmhill 132kV Circuit – At the proposed Quantans Hill wind farm site establish a 132kV substation and establish a 132kV busbar to which a 132kV line isolator is connected. Install around 6km of wood pole overhead line with HTLS conductor to connect Quantans Hill substation to Holmhill substation. At Holmhill substation install a 132kV circuit breaker to connect the OHL. | 2031-09-29
Wether Hill | PRO-001527 | CS-04353 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-1507 | Holm Hill 132kV substation - At an appropriate point next to the DE route establish a 132kV substation (Holmhill 132kV substation) by teeing into the proposed future New Cumnock to Glenlee 132kV circuit. The substation will consist of a 132kV busbar to which wind farm circuits will connect to. | 2031-09-29
Wether Hill | PRO-001527 | CS-04354 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2031-09-29
Wether Hill | PRO-001527 | CS-04355 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 2031-09-29
Wether Hill | PRO-001527 | CS-04356 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 2031-09-29
Wether Hill | PRO-001527 | CS-04357 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2031-09-29
Wether Hill | PRO-001527 | CS-04358 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 2031-09-29
Wether Hill | PRO-001527 | CS-04359 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | Wether Hill H1 Works | At Wether Hill substation install one 132kV line isolator. Installation of around 11km of wood pole OHL with Poplar conductor between Wether Hill substation and Quantans Hill substation. At Quantans Hill extend the substation to install 132kV circuit breaker to connect the OHL. | 2031-09-29
Whitegate Tertiary Connection | PRO-000512 | CS-07002 | HD144WHI LTD | Whitegate 275kV Substation | 10079-201575 | 1. Install a tertiary cable box or bushings on SGT1B. 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 2024-06-30
Whitehill Battery Storage | PRO-002093 | CS-07547 | Whitehill Battery Storage Ltd | Easterhouse 275kV | 275kV Disconnector - Whitehill Battery | At Easterhouse 275kV substation, installation of one new 275kV disconnector and associated equipment. | 2027-06-30
Whitehill Battery Storage | PRO-002093 | CS-07548 | Whitehill Battery Storage Ltd | Easterhouse 275kV | SPT-RI-2436 | Easterhouse 275kV fault level mitigation works - To allow a new generation / battery storage connection at Easterhouse 275kV the short circuit rating of Easterhouse 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of all equipment and structures to withstand a fault current of 40kA | 2027-06-30
WHITEHILL BESS | PRO-004639 | CS-09755 | GPC 1210 Ltd | Whitehill Bess 275/132kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 2029-10-01
WHITEHILL BESS | PRO-004639 | CS-09756 | GPC 1210 Ltd | Whitehill Bess 275/132kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 2029-10-01
WHITEHILL BESS | PRO-004639 | CS-09757 | GPC 1210 Ltd | Whitehill Bess 275/132kV Substation | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 2029-10-01
WHITEHILL BESS | PRO-004639 | CS-09758 | GPC 1210 Ltd | Whitehill Bess 275/132kV Substation | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 2029-10-01
Whitehouse BESS station | PRO-002237 | CS-12567 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12568 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12569 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12570 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12571 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12572 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-196 Whitehouse Substation 275kV Switchgear |  | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12573 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SPT-RI-028 | 7. Dalmally Windyhill 275kV Reconfiguration -As part of its non-load related asset modernisation programme, SPT will replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). As part of its non-load related asset modernisation programme, SPT will uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). As part of a joint SPT/ SHE Transmission project to reinforce the transmission network in north Argyll and accommodate proposed renewable generation schemes, SPT will extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). (SPT-RI-028) | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12574 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12575 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-077 | 3rd Subsea Cable Link Kintyre – Hunterston Reinforcement - Establish a third 240MVA 220kV subsea cable circuits between the 132kV substation at Crossaig and the existing 400kV busbar at Hunterston (SPT will make this connection and provide any necessary infrastructure at Hunterston). | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12576 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12577 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SPT-RI-150 | Installation of one 240MVA 220kV cable circuit from the Kintyre peninsula to Hunterston East 400kV Substation. This circuit will be the third 220kV circuit between the Kintyre peninsula and Hunterston East 400kV Substation. | 2032-07-31
Whitehouse BESS station | PRO-002237 | CS-12578 | IGP INTERNATIONAL PROSPECTING LIMITED | Whitehouse 275kV Substation | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 2032-07-31
Whitelaw Brae BESS | PRO-003247 | CS-09618 | BUK23 Limited | Whitelaw Brae WF 33kV Substation | SPT-RI-3189 | Clyde South to Whitelaw Brae 33kV Works - Following further connection applications in this area it is required to establish a shared 33kV circuit from Clyde South substation to the Whitelaw Brae substation. | 2026-07-31
Whitelee | PRO-000067 | CS-06685 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Whitelee 275/33kV | Whitelee H1 Works | At Whitelee Repowering substation install three disconnector on the HV side of the transformers. Establish a 275kV busbar to which the three disconnectors are connected. Install around 12km of 275kV underground cable circuit to connect the new wind farm substation to Busby substation, continuous summer rating 450MVA. | 2031-05-02
Wick Moor Drove | PRO-004788 | CS-11491 | BSR APPLICATIONS LIMITED | West Country Connection Node D 400kV Substation | 103442-206904 |  | 2037-10-31
Wick Moor Drove | PRO-004788 | CS-11492 | BSR APPLICATIONS LIMITED | West Country Connection Node D 400kV Substation | 103844-207598 |  | 2037-10-31
Willington BESS Station | PRO-003727 | CS-10876 | IBV WILLINGTON ENERGY PARK LIMITED | Derbyshire Connection Node D 400kV Substation | 101879-203856 (4) |  | 2033-10-31
Willington BESS Station | PRO-003727 | CS-10877 | IBV WILLINGTON ENERGY PARK LIMITED | Derbyshire Connection Node D 400kV Substation | 101880-203857 Derbyshire |  | 2033-10-31
Willington BESS Station | PRO-003727 | CS-10878 | IBV WILLINGTON ENERGY PARK LIMITED | Derbyshire Connection Node D 400kV Substation | 102925-206331 |  | 2033-10-31
Willington BESS Station | PRO-003727 | CS-10879 | IBV WILLINGTON ENERGY PARK LIMITED | Derbyshire Connection Node D 400kV Substation | 102926-206332 |  | 2033-10-31
Willington BESS Station | PRO-003727 | CS-10880 | IBV WILLINGTON ENERGY PARK LIMITED | Derbyshire Connection Node D 400kV Substation | 102927-206333 |  | 2033-10-31
Willington BESS Station | PRO-003727 | CS-10881 | IBV WILLINGTON ENERGY PARK LIMITED | Derbyshire Connection Node D 400kV Substation | 102929-206339 |  | 2033-10-31
Willington East 2 (Tertiary) | PRO-000548 | CS-07004 | ENSO GREEN HOLDINGS SS LIMITED | Willington 400kV Substation | 100945-201885 | 1. Install a tertiary cable box or bushings on the SGT2. 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV disconnector at the 13kV side connecting tertiary to connection assets. | 2028-07-30
Willington East 2 (Tertiary) | PRO-000548 | CS-12489 | ENSO GREEN HOLDINGS SS LIMITED | Willington 400kV Substation | 104117-208052 |  | 2028-07-30
Willington Energy Park | PRO-001964 | CS-07116 | BROCKWELL STORAGE & SOLAR LIMITED | Willington 400kV Substation | 101778-203570 | Extension of the existing Willington East 400kV substation main and reserve busbars to accommodate the User’s bay | 2028-03-30
Willington Energy Park | PRO-001964 | CS-07117 | BROCKWELL STORAGE & SOLAR LIMITED | Willington 400kV Substation | 100477-201048 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4- WILE4-2) to summer pre-fault rating 1400MVA | 2028-03-30
Willington Energy Park | PRO-001964 | CS-07118 | BROCKWELL STORAGE & SOLAR LIMITED | Willington 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-03-30
Willington Energy Park | PRO-001964 | CS-07119 | BROCKWELL STORAGE & SOLAR LIMITED | Willington 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2028-03-30
Willington Energy Park | PRO-001964 | CS-07120 | BROCKWELL STORAGE & SOLAR LIMITED | Willington 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 2028-03-30
Willington Green Energy Centre | PRO-001797 | CS-07038 | WILLINGTON NG LIMITED | Willington 400kV Substation | 101595-203210 | Substation Busbar extension works to facilitate the use of the existing generator bays (for the decommissioned generators) for connection of Willington Green Energy | 2028-10-30
Willington Green Energy Centre | PRO-001797 | CS-07039 | WILLINGTON NG LIMITED | Willington 400kV Substation | 100477-201048 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4- WILE4-2) to summer pre-fault rating 1400MVA | 2028-10-30
Willington Green Energy Centre | PRO-001797 | CS-07040 | WILLINGTON NG LIMITED | Willington 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm² conductor on the Feckenham-Minety 400 kV circuit with 2x620mm² conductor to achieve a pre fault summer rating of 2490 MVA. | 2028-10-30
Willington Green Energy Centre | PRO-001797 | CS-07041 | WILLINGTON NG LIMITED | Willington 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm² conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm² conductor to achieve a pre-fault Summer rating of 2490 MVA. | 2028-10-30
Willington Green Energy Centre | PRO-001797 | CS-07042 | WILLINGTON NG LIMITED | Willington 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2028-10-30
Willington Green Energy Centre | PRO-001797 | CS-12308 | WILLINGTON NG LIMITED | Willington 400kV Substation | 101228-202967 I |  | 2028-10-30
Willington Green Energy Centre | PRO-001797 | CS-12309 | WILLINGTON NG LIMITED | Willington 400kV Substation | 101595-203210 I |  | 2028-10-30
Wilton Hydrogen | PRO-003587 | CS-10404 | RWE Generation UK Plc | Teeside Connection Node B | 103359-206815 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10405 | RWE Generation UK Plc | Teeside Connection Node B | 103318-206759 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10406 | RWE Generation UK Plc | Teeside Connection Node B | 101646-203283 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10407 | RWE Generation UK Plc | Teeside Connection Node B | 101164-202350 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10408 | RWE Generation UK Plc | Teeside Connection Node B | 102197-204417 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10409 | RWE Generation UK Plc | Teeside Connection Node B | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10410 | RWE Generation UK Plc | Teeside Connection Node B | 101325-202642 | At Thornton 400kV: Establish an additional section switch in place of X224 or X228 and add another section switch in place of X428 or X424. Replace circuit breaker X405 and X805 (In Lackenby - Thornton circuits with 63kA rated breakers. (101325-202642) | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10411 | RWE Generation UK Plc | Teeside Connection Node B | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10412 | RWE Generation UK Plc | Teeside Connection Node B | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10413 | RWE Generation UK Plc | Teeside Connection Node B | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10414 | RWE Generation UK Plc | Teeside Connection Node B | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10415 | RWE Generation UK Plc | Teeside Connection Node B | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10416 | RWE Generation UK Plc | Teeside Connection Node B | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10417 | RWE Generation UK Plc | Teeside Connection Node B | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10418 | RWE Generation UK Plc | Teeside Connection Node B | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10419 | RWE Generation UK Plc | Teeside Connection Node B | 100173-200455 | Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and130) at Drax 132kV Substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10420 | RWE Generation UK Plc | Teeside Connection Node B | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10421 | RWE Generation UK Plc | Teeside Connection Node B | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm² AAAC sections of the circuits with 2×591mm² ACCR conductor and the 2x700mm² AAAC sections with 3x700mm² AAAC conductor | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10422 | RWE Generation UK Plc | Teeside Connection Node B | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10423 | RWE Generation UK Plc | Teeside Connection Node B | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10424 | RWE Generation UK Plc | Teeside Connection Node B | 100479-201050 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10425 | RWE Generation UK Plc | Teeside Connection Node B | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10426 | RWE Generation UK Plc | Teeside Connection Node B | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10427 | RWE Generation UK Plc | Teeside Connection Node B | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10428 | RWE Generation UK Plc | Teeside Connection Node B | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10429 | RWE Generation UK Plc | Teeside Connection Node B | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10430 | RWE Generation UK Plc | Teeside Connection Node B | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10431 | RWE Generation UK Plc | Teeside Connection Node B | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10432 | RWE Generation UK Plc | Teeside Connection Node B | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10433 | RWE Generation UK Plc | Teeside Connection Node B | 101386-202715 | Reconductor the 2x700mm² sections of the Lackenby-Thornton 1+2 circuit with 2x850mm² conductor. Reconductor the 4x400mm² sections with 2x850mm² conductor. Uprate the cable section of this circuit. (2850MVA). | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10434 | RWE Generation UK Plc | Teeside Connection Node B | 101386-202716 | LTRE (NOA)Upgrade the existing circuits between Lackenby and Thornton to allow for more capacity | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10435 | RWE Generation UK Plc | Teeside Connection Node B | 101508-202973 (1) |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10436 | RWE Generation UK Plc | Teeside Connection Node B | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10437 | RWE Generation UK Plc | Teeside Connection Node B | 101625-203259 | Uprate the Drax - Eggborough 2 circuit to achieve a post fault summer rating of 2500MVA. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10438 | RWE Generation UK Plc | Teeside Connection Node B | 101661-203312 | Uprating/Replacement of the CB T10 at Monk Fryston 275kV substation | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10439 | RWE Generation UK Plc | Teeside Connection Node B | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10440 | RWE Generation UK Plc | Teeside Connection Node B | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10441 | RWE Generation UK Plc | Teeside Connection Node B | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm² Araucaria conductor | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10442 | RWE Generation UK Plc | Teeside Connection Node B | 101712-203416 (II) |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10443 | RWE Generation UK Plc | Teeside Connection Node B | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10444 | RWE Generation UK Plc | Teeside Connection Node B | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10445 | RWE Generation UK Plc | Teeside Connection Node B | 102178-204388 | Replacement of CB's S10, P10, W10, W20, H10 and H20 at Blyth 275kV Substation | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10446 | RWE Generation UK Plc | Teeside Connection Node B | 102356-204777 | Uprating/Replacement of the following Circuit breakers for a higher X/R ratio of 25 at Drax 400kV substations: X430, X630, X405. | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10447 | RWE Generation UK Plc | Teeside Connection Node B | 102360-204779 | Uprating/Replacement of the following Circuit breakers at Creyke Beck 400kV substation X510, X130, X420, X430, X520, X620, X330, X1215, X905, X210, X1415, X320 | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10448 | RWE Generation UK Plc | Teeside Connection Node B | 102412-204937 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10449 | RWE Generation UK Plc | Teeside Connection Node B | 102591-205211 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10450 | RWE Generation UK Plc | Teeside Connection Node B | 103143-206563 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10451 | RWE Generation UK Plc | Teeside Connection Node B | 103145-206565 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10452 | RWE Generation UK Plc | Teeside Connection Node B | 103165-206584 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10453 | RWE Generation UK Plc | Teeside Connection Node B | 103166-206585 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10454 | RWE Generation UK Plc | Teeside Connection Node B | 103167-206586 |  | 2035-10-30
Wilton Hydrogen | PRO-003587 | CS-10455 | RWE Generation UK Plc | Teeside Connection Node B |  |  | 2035-10-30
Windburn | PRO-004768 | CS-12498 | WINDBURN WIND FARM LIMITED | Braco West GSP | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2035-10-31
Windburn | PRO-004768 | CS-12499 | WINDBURN WIND FARM LIMITED | Braco West GSP | SHET-RI-134a Braco West Substation 400kV Reinforcement |  | 2035-10-31
Windy Standard III Wind Farm | PRO-000359 | CS-05433 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-05434 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-05435 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-06150 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-007 | New Cumnock 275/132kV Substation | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-06151 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-145 | Construction of Dun Hill 132/33kV Substation including three 33kV circuit breakers, two 132/33kV 90MVA transformers and 33kV switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-06152 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPT-RI-284) | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-06153 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-06154 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 2026-06-01
Windy Standard III Wind Farm | PRO-000359 | CS-06155 | Windy Standard III Limited | Dun Hill 132/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 2026-06-01
WindyHill BESS2 Facility | PRO-002032 | CS-07272 | Windyhill Grid 2 Ltd | Windyhill 275/132kV | SPT-RI-148 | Install an auto-close scheme across the three 275/132kV supergrid transformers at WindyHill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. | 2025-07-27
WindyHill BESS2 Facility | PRO-002032 | CS-07273 | Windyhill Grid 2 Ltd | Windyhill 275/132kV |  |  | 2025-07-27
WindyHill Energy Storage Facility | PRO-001696 | CS-04503 | Windyhill Grid 1 LTD | Windyhill 132kV | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 2025-08-27
Womblehill BESS Farm | PRO-002197 | CS-07978 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2029-12-31
Womblehill BESS Farm | PRO-002197 | CS-07979 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 2029-12-31
Womblehill BESS Farm | PRO-002197 | CS-07980 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-025d | North East Reinforcement | 2029-12-31
Womblehill BESS Farm | PRO-002197 | CS-07981 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2029-12-31
Womblehill BESS Farm | PRO-002197 | CS-07982 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 2029-12-31
Woodcock Faulds Battery Storage | PRO-002663 | CS-10016 | Woodcock Faulds Battery Storage Limited | GARTCLASH COLLECTOR 275KV SUBSTATION | Woodcock Faulds H1 | At Gartclash Collector substation, install one 275kV disconnector | 2029-10-31
Woodcock Faulds Battery Storage | PRO-002663 | CS-10017 | Woodcock Faulds Battery Storage Limited | GARTCLASH COLLECTOR 275KV SUBSTATION | SPT-RI-3615 | Gartclash Farm BESS 275kV Collector Substation – It is proposed to establish a collector substation at the Gartclash Farm BESS site to accommodate generation through shared solutions in the Denny North 275kV area. At the Gartclash Collector substation, a 275kV single busbar shall be installed along with a 275kV feeder bay. From there, install approximately 1.3km of 275kV circuit to Denny North 275kV substation where a double busbar bay shall be installed | 2029-10-31
Woodcock Faulds Battery Storage | PRO-002663 | CS-10018 | Woodcock Faulds Battery Storage Limited | GARTCLASH COLLECTOR 275KV SUBSTATION | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 2029-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10002 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | Woodcock Hill - Circuit Breaker and Disconnector | Installation of 275kV circuit breaker and 275kV bus disconnector at the Woodcock Hill 275/33kV Substation | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10003 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10004 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90°C to increase the continuous current rating of the circuit | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10005 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10006 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10007 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10008 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10009 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 2032-10-31
Woodcock Hill Wind Farm | PRO-004282 | CS-10010 | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation | SHET-RI-267 | Turn-in/out connection of 275kV Dounreay – Loch Buidhe circuit Turn In-Out substation will be constructed to accommodate the connection of Woodcock Hill Wind Farm. The new generation site is approximately 0.5 km from the Turn In-Out connection point | 2032-10-31
Woolfords Wind Farm | PRO-004151 | CS-10111 | SP Distribution plc | Bathgate 132/33kV | SPT-RI-2415 - AA Route OHL Uprate |  | 2031-08-29
Woolfords Wind Farm | PRO-004151 | CS-10113 | SP Distribution plc | Bathgate 132/33kV | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 2031-08-29
Woolfords Wind Farm | PRO-004151 | CS-10114 | SP Distribution plc | Bathgate 132/33kV | SPT-RI-3383 | Armadale 275/132kV Substation – It is proposed to establish a new 275/132kV substation, indicatively named Armadale substation, which would connect into XM Route and then connect to Bathgate Hygen via the existing AA Route as well as lifting Bathgate and Drumcross into this substation. | 2031-08-29
WORSET LANE BESS | PRO-003650 | CS-08578 | FIELD HARTMOOR LTD | Hartmoor 275kV Substation | 102573-205181 | Hartmoor 275kV substation: extend mesh corner 4 and install a CB/DCB | 2026-10-25
Worset PV & BESS Park | PRO-001055 | CS-06156 | Worcestershire Solar 1 Limited | Hartmoor 275kV Substation | 100788-201592 | Reconfigure the bars around SGT2 and provide a banked 66kV User connection point consisting of a disconnector and cable sealing end at Hartmoor 275/66kV substation | 2024-06-07
Wright Street BESS | PRO-003083 | CS-08555 | P3P PARTNERS LLP | Braehead Park 132/33kV | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 2025-07-16
Wull Muir Wind Farm | PRO-005854 | CS-12326 | ENERGIEKONTOR UK LTD | Kaimes GSP | SPT-RI-4378 | 1. Interface to SPT-RI-4378 Kaimes GSP SGT1(2) LMS. 2. Kaimes GSP SGT1(2) LMS – (SPT-RI-4378). | 2029-10-01
Wull Muir Wind Farm | PRO-005854 | CS-12327 | ENERGIEKONTOR UK LTD | Kaimes GSP | SPT-RI-4370 | Kaimes GSP Loss of Mains - (SPT-RI-4370). | 2029-10-01
Wylfa Substation | PRO-000506 | CS-06157 | WYLFA GREEN LIMITED | Wylfa 132kV Substation | 100647-201326 | Provision of existing Skeleton bay to enable User to connect to that bay Substation control modification and bus bar protection | 2029-06-30
Wymondley | PRO-001245 | CS-05215 | Priory Generation Limited | Wymondley 400kV Substation | 100589-201123 | 1. Install a tertiary cable box or bushing on the SGT 1. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to User Assets. | 2025-10-31
Wymondley Farm | PRO-002552 | CS-12527 | Wymondley 10 Renewables Ltd | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 101248-202488 2 |  | 2032-10-30
Wymondley Farm | PRO-002552 | CS-12528 | Wymondley 10 Renewables Ltd | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 102496-205083 2 |  | 2032-10-30
Wymondley Farm | PRO-002552 | CS-12529 | Wymondley 10 Renewables Ltd | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 104621-209305 |  | 2032-10-30
Wymondley Farm | PRO-002552 | CS-12530 | Wymondley 10 Renewables Ltd | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 102682-205369 2 |  | 2032-10-30
Wymondley Farm | PRO-002552 | CS-12531 | Wymondley 10 Renewables Ltd | WEST ANGLIA CONNECTION NODE B 400KV SUBSTATION | 103043-206459 2 |  | 2032-10-30
Wymondley Solar Farm | PRO-001105 | CS-05296 | AGR SOLAR 4 LIMITED | Wymondley 400kV Substation | 100895-201796 | 1. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 2. Installation of 13kV cable at the Connection Site. 3. Installation of earthing transformer at the Connection Site. 4. Installation of 13kV Disconnector at the Connection Site. | 2025-10-31
Wyseby Hill Energy Farm | PRO-001884 | CS-07332 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | SPT-RI-231 |  | 2031-10-31
Wyseby Hill Energy Farm | PRO-001884 | CS-07333 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | SPT-RI-2320 |  | 2031-10-31
Wyseby Hill Energy Farm | PRO-001884 | CS-07334 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 2031-10-31
Wyseby Hill Energy Farm | PRO-001884 | CS-07335 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 2031-10-31
YAMAL BESS | PRO-005918 | CS-12547 | OPDE UK LIMITED | Macduff GSP | SHET-RI-079a | Blackhillock Additional 275/132kV SGT – Reinforce the transmission network at Blackhillock substation by installing an additional new 275/132kv SGT to enable the connection of Elchies WF. The transformer shall be rated at 360MVA | 2033-10-31
YAMAL BESS | PRO-005918 | CS-12548 | OPDE UK LIMITED | Macduff GSP | SHET-RI-079b | Blackhillock Additional 275/132kV SGT – Reinforce the transmission network at Blackhillock substation by installing an additional new 275/132kV Supergrid Transformer. The transformer shall be rated at 360 MVA | 2033-10-31
Yaxley | PRO-003272 | CS-10507 | CONNECTID 2 LIMITED | North Anglia Connection Node E 400kV Substation | 020340-020340 (Yax) |  | 2034-10-31
Yaxley | PRO-003272 | CS-10508 | CONNECTID 2 LIMITED | North Anglia Connection Node E 400kV Substation | 102226-204464 (C2) |  | 2034-10-31
Yaxley | PRO-003272 | CS-10509 | CONNECTID 2 LIMITED | North Anglia Connection Node E 400kV Substation | 103003-206409 |  | 2034-10-31
Yaxley | PRO-003272 | CS-10510 | CONNECTID 2 LIMITED | North Anglia Connection Node E 400kV Substation | 103063-206480 (C2) |  | 2034-10-31
Yaxley | PRO-003272 | CS-10511 | CONNECTID 2 LIMITED | North Anglia Connection Node E 400kV Substation | 103065-206482 (C2) |  | 2034-10-31
Yorkshire Reactive Power Limited | PRO-005960 | CS-12683 | YORKSHIRE REACTIVE POWER LIMITED | Neepsend 275kV Substation | 104572-209072 |  | 2028-10-30
Zenobe Blackhillock 300 MW | PRO-001624 | CS-06647 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2026-04-01
Zenobe Blackhillock 300 MW | PRO-001624 | CS-06648 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2026-04-01
Zenobe Blackhillock 300 MW | PRO-001624 | CS-06649 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-025d | North East Reinforcement | 2026-04-01
Zenobe Blackhillock 300 MW | PRO-001624 | CS-06650 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 2026-04-01
Zenobe Coalburn Battery Storage | PRO-001780 | CS-07442 | Zenobe Coalburn Limited | Coalburn North 400kV Substation | SPT-RI-2058 | Coalburn North 400kV Substation - construction of a new 400kV substation, indicatively called Coalburn North, to connect into the Strathaven-Elvanfoot 400kV circuit. Construction of a new 400kV double busbar substation with a bus coupler circuit breaker, two feeder bays to connect onto the Strathaven-Elvanfoot 400kV circuit. | 2027-08-31
Zenobe Hartmoor BESS | PRO-003696 | CS-11485 | Zenobe Energy Limited | Wearside Connection Node A 275kV Substation | 030317-030317 1 |  | 2035-10-30
Zenobe Hartmoor BESS | PRO-003696 | CS-11486 | Zenobe Energy Limited | Wearside Connection Node A 275kV Substation | 102591-205211 3 |  | 2035-10-30
Zenobe Hartmoor BESS | PRO-003696 | CS-11487 | Zenobe Energy Limited | Wearside Connection Node A 275kV Substation | 103143-206563 |  | 2035-10-30
Zenobe Hartmoor BESS | PRO-003696 | CS-11488 | Zenobe Energy Limited | Wearside Connection Node A 275kV Substation | 103206-206637 |  | 2035-10-30
Zenobe Hartmoor BESS | PRO-003696 | CS-11489 | Zenobe Energy Limited | Wearside Connection Node A 275kV Substation | 103209-206638 |  | 2035-10-30
Zenobe Kilmarnock South | PRO-001687 | CS-04488 | ZENOBE KILMARNOCK SOUTH LIMITED | Kilmarnock South 400kV Substation | SPT-RI-1854 | At Kilmarnock South 400kV GIS substation install a bus coupler to run the substation in double busbar arrangements. (SPT-RI-1854). Protection and control modifications as required. Associated civil works. Miscellaneous and minor works | 2025-08-29
Zenobe New Deer Battery Storage | PRO-001778 | CS-06805 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65°C, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06806 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06807 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-025d | North East Reinforcement | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06808 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06809 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06810 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06811 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 2029-10-31
Zenobe New Deer Battery Storage | PRO-001778 | CS-06812 | Zenobe Energy Limited | New Deer 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 2029-10-31
Zenobe Norton | PRO-001691 | CS-07005 | Zenobe Energy Limited | Norton East 400kV Substation | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07006 | Zenobe Energy Limited | Norton East 400kV Substation | 101331-202651 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07007 | Zenobe Energy Limited | Norton East 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07008 | Zenobe Energy Limited | Norton East 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07009 | Zenobe Energy Limited | Norton East 400kV Substation | 101093-202181 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07010 | Zenobe Energy Limited | Norton East 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07011 | Zenobe Energy Limited | Norton East 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07012 | Zenobe Energy Limited | Norton East 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07013 | Zenobe Energy Limited | Norton East 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm² strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07014 | Zenobe Energy Limited | Norton East 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07015 | Zenobe Energy Limited | Norton East 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07016 | Zenobe Energy Limited | Norton East 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm² conductor | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07017 | Zenobe Energy Limited | Norton East 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07018 | Zenobe Energy Limited | Norton East 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm² conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm² conductor to achieve a post-fault winter rating of 3100MVA. | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07019 | Zenobe Energy Limited | Norton East 400kV Substation | 020640-020640/101576-203163 | 1. Uprate the Norton - Osbaldwick 1 and 2 400kV circuits | 2031-10-31
Zenobe Norton | PRO-001691 | CS-07020 | Zenobe Energy Limited | Norton East 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm² cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm² cable. | 2031-10-31
Zenobe Stalybridge Project | PRO-001940 | CS-12700 | ZENOBE STALYBRIDGE LIMITED | Stalybridge 275kV Substation | 101800-203685 |  | 2027-09-30
Zenobe Yaxley BESS | PRO-004088 | CS-11504 | Zenobe Energy Limited | North Anglia Connection Node E 400kV Substation | 020340-020340 1 |  | 2034-10-31
Zenobe Yaxley BESS | PRO-004088 | CS-11505 | Zenobe Energy Limited | North Anglia Connection Node E 400kV Substation | 102226-204464 1 |  | 2034-10-31
Zenobe Yaxley BESS | PRO-004088 | CS-11506 | Zenobe Energy Limited | North Anglia Connection Node E 400kV Substation | 103002-206408 |  | 2034-10-31
Zenobe Yaxley BESS | PRO-004088 | CS-11507 | Zenobe Energy Limited | North Anglia Connection Node E 400kV Substation | 103063-206480 1 |  | 2034-10-31
Zenobe Yaxley BESS | PRO-004088 | CS-11508 | Zenobe Energy Limited | North Anglia Connection Node E 400kV Substation | 103065-206482 1 |  | 2034-10-31