## Discussion Points
GC0079 - Frequency Changes During System Disturbances - Workgroup Issue Tracker
NGET Owner: | Richard Woodward
Action/Risk Management:
Line No. | Meeting Date | Meeting No. | Agenda Item | Topic | Workgroup Discussion Point | Category | Raised by | Status | Owner | Target Completion Date | Updates
1 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | Solar proliferation has continued as projected in Ecofys' 2014/15 analysis. At least 50% of sub-5MW distribution-connected generation is thought to be Solar PV and this growth is expected to continue. | Point to note | MD
2 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | Whilst concern was expressed at the impact rapid PV growth had on the generators in scope for a GC0079 protection settings change, GS's previous analysis had shown that PV sensitivity to the CBA numbers made little difference | Point to note | Workgroup
3 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | MK did not consider that Adam Dysko's previous study work needed to be updated to reflect the revised Solar PV figures, but again, it was an important point to note that increased distributed generation increased the islanding risk in general | Point to note | JR
4 | 2016-05-17 | 41 | Ecofys Update | Solar PV generation volumes | The Ecofys study work needs to be supplemented with a distribution of individual site volume, and a monthly trend on growth rather than just yearly. This will then be finalised with their previous study work and published. | Action | GS | Active | MD/GS | 2016-06-27
5 | 2016-05-17 | 41 | Ecofys Update | DG generation volumes | A previous action remains with the DNO reps to provide GS their sub-5MW generation figures (removing domestic schemes). GS has circulated an email explaining what he needs. DNO reps should submit their information as soon as possible | Action | Workgroup | Active | DNO Reps/GS | 2016-06-27
6 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | The Transmission Charging Methodology Forum (TCMF) provided feedback to GS during a presentation on potential funding options (including BSUoS). - Not convinced on justification for funding through BSUoS - particularly as some parties incurring the short-term cost may not be around to realise the long-term benefit - Seek further guidance from Ofgem, particularly as this is a networks issue not just a commercial one - Concern over the management cost - this could be a blank cheque (GS estimated £10m for the work, £33m/year recurring benefit of complete GC0035 + GC0079 changes) - GC0079 cannot change charging regimes (though an SO charging review is in progress) | Point to note | GS
7 | 2016-05-17 | 41 | TCMF Update | Phase 1 compliance | The success rate of achieving compliance needs to be factored into the GC0079 recommendation. This is still a moving target for GC0035, which is due to give an update at the DCRP on 02/06/16 | Point to note | CMD
8 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | Need to ensure that benefits and costs from Phase 1/2(/3) are properly set out in the workgroup report and not double-counted. GS confirmed these would be disaggregated in the workgroup report | Point to note | JD
9 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | Workgroup members are requested to consider their preference on the funding options set out, consider potential other options, and the DNO reps requested to consider managing the work within their own organisations | Action | Workgroup | Resolved
10 | 2016-05-17 | 41 | TCMF Update | Commercial Considerations | MK and GS to resume discussions with Ofgem on the funding route and what should be included in the WG report. | Action | Workgroup | Active | GS/MK
11 | 2016-05-17 | 41 | Workgroup Report | Costs | The table of costs on page 14 needs to be updated to include site visit admin and test witnessing costs | Action | IK | Active | GS | 2016-06-27
12 | 2016-05-17 | 41 | Workgroup Report | Vector Shift | Workgroup consideration of Vector Shift needs to be added. Section 5.24 in particular needs to be adjusted to reflect workgroup thinking on this topic. It was also noted that VS is not allowed in Ireland for synchronous machines as it cannot detect islanding (need to confirm this in writing) Vector Shift is part of the consideration for GC0079 Phase 3 | Action | ML | Active | GS/MK/ML | 2016-06-27
13 | 2016-05-17 | 41 | Workgroup Report | Voltage Control v Power Factor mode | Scottish DNOs get generation to operate in Voltage Control mode - this will impact the GC0079 recommendation and needs to be checked against a previous discussion between MK with GM and AMPS (details were circulated at the time). Also note there is a meeting on 28/06 at ENA with ML/MK on use of Voltage Control for DG. For more info, contact MK, ML or RJW | Action | JD | Active | MK | 2016-06-27
14 | 2016-05-17 | 41 | Workgroup Report | LoMP | DNOs were requested to provide their own view of the ratio of Loss of Mains Protection being RoCoF or not (excluding domestic). The current workgroup report assumption is 50/50. | Action | ST | Active | DNO Reps | 2016-06-27
15 | 2016-05-17 | 41 | Workgroup Report | Site visits | The workgroup report needs to clarify whether generator owners can facilitate their own settings change, and how/if this is funded | Point to note | Workgroup
16 | 2016-05-17 | 41 | Workgroup Report | Exemptions | Phase 1 provided for generation exemptions for compliance - would the same wording be used in the workgroup report for Phase 2? Would such a process be needed? | Action | GM | Active | MK/GS | 2016-06-27 | Check with GM on this action on 29/06
17 | 2016-05-17 | 41 | AOB | Meeting Dates | RJW to provide the meeting dates and venues for the remainder of 2016 | Action | Workgroup | Active | RJW | ASAP
18 | 2015-10-22 | 35 |  | Enhanced Frequency Response | NGET to provide more details on the Enhanced Frequency Response tender exercise currently on-going by NGET, particularly re. obtaining response from batteries and storage devices | Action | JD/GE | Active | GS/RJW | When tender results published | http://www2.nationalgrid.com/Enhanced-Frequency-Response.aspx
19 | 2015-11-23 | 36 |  | Over-frequency | Recommend resetting of protection on sub 5MW generators as part of the intended recommendations (from previous G59/1 change of over-frequency to 51.5hz) - placeholder action to note for WG report | Action | ML | Active | MK/GS | TBC
20 | 2016-02-24 | 39 |  | Risk Assessment | JA to update his risk assessment paper and to recirculate for workgroup comment | Action | JA | Active | JA | ASAP
21 | 2016-03-23 | 40 |  | Workgroup Terms of Reference | Circulate agreed Terms of Reference following Grid Code and Distribution Code Review Panel approvals | Action | Workgroup | Active | RJW | ASAP
22 | 2016-04-20 | 40A |  | Dead Times | Write up general propostion re longer dead times for individual risk mitigation | Action | MK | Resolved | AD | ASAP
23 | 2016-04-20 | 40A |  |  | Confirm tripping time wording OK | Action | MK | Resolved
24 | 2016-04-20 | 40A |  | RoCoF Protection | Re. RoCoF protection requirements - stability type testing machines <50kW was a defacto ride through requirement. SB to seek out where misinformation was arising, and to use the offices of the DNOs to try to resolve. Discuss RoCoF ridethrough and escalate to GS/MK if required. | Action | SB/CMD | Active
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40

## Decision Tracker
GC0048-C EU Coordination Group - Decision Tracker
Owner | Richard Woodward
Meeting Date | Meeting No. | Decision Point
Workgroup Preference:
Name | Organisation | Vote
Mike Kay | ENA
Richard Woodward | NGET SO
Greg Middleton | Deepsea Electronics
John Ruddock | Deepsea Electronics
Graham Stein | NGET SO
Miguel Bernardo | UKPN
Joe Duddy | RES
Campbell McDonald | SSE Generation
Jacob Allinson | RWE
Sam Turner | NPG
Michael Doering | Ecofys
Ioannis Koutsokeras | SP Energy Networks
Martin Lee | SSE Distribution
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0

## Sheet1 (hidden)
Active | Point to note | Yes
On Hold | Risk | No
Urgent | Action | Abstain
Resolved | Decision

## Attendance Tracker
GC0048-C EU Coordination Group - Workgroup Attendance Tracker
Owner: | Richard Woodward
Name | Organisation | Role | Meeting 41 - 17-05-16
Mike Kay | ENA | Chair | Y
Richard Woodward | NGET SO | Technical Secretary | Y
Greg Middleton | Deepsea Electronics | WG Member | Y
John Ruddock | Deepsea Electronics | WG Member | Y
Graham Stein | NGET SO | WG Member | Y
Miguel Bernardo | UKPN | WG Member | Y
Joe Duddy | RES | WG Member | Y
Campbell McDonald | SSE Generation | WG Member | Y
Jacob Allinson | RWE | WG Member | Y
Sam Turner | NPG | WG Member | Y
Michael Doering | Ecofys | Presenter | Y
Ioannis Koutsokeras | SP Energy Networks | WG Member | Y
Martin Lee | SSE Distribution | WG Member | Y