## SOGL
| SOGL EIF date : |  |  |  |  | 2017-09-14
S O G L
GROUP | [9 empty] | Obligation On | [12 empty] | NGET Workstream
Row Order # | Title | Chapter | Section | Article | Paragraph | Article Text | Applicable date | EIF offset in months | EIF offset in code | SO | TO | I/C | OFTO | DBEIS | Ofgem | All TSOs | ENTSO-E | RSC | DSOs | BSPs | BRPs | Elexon | Data Exchange | Operational Practices | Planning and RSC | Operational Agreements | Common Grid Model | Reserve Providers | information transparency | General Compliance | WG Comments relative to GB regulation and code modifications if necessary | Is a mod required? | Grid Code Reference | D Code Reference
1543 | 2 | 0 | 0 | 40 | 0 | Article 40 - Organisation, roles, responsibilities and quality of data exchange | 2017-09-14
1544 | 2 | 0 | 0 | 40 | 1 | 1. The exchange and provision of data and information pursuant to this Title shall reflect, to the extent possible, the real and forecasted situation of the transmission system. | 2017-09-14 | [15 empty] | X | [8 empty] | No | Context setting requirement - does not need to be literally transposed | Context setting requirement - does not need to be literally transposed
1545 | 2 | 0 | 0 | 40 | 2 | 2. Each TSO shall be responsible for providing and using high quality data and information. | 2017-09-14 |  |  | ü | ü | ü | ü | [9 empty] | X | [8 empty] | No | Context setting requirement - does not need to be literally transposed | Context setting requirement - does not need to be literally transposed
1546 | 2 | 0 | 0 | 40 | 3 | 3. Each TSO shall gather the following information about its observability area and shall exchange this data with all other TSOs to the extent that it is necessary for carrying out the operational security analysis in accordance with Article 72: | 2018-09-14 | 12 | EIF+12months | ü | [12 empty] | X | [7 empty] | Just GB - don't have observability areas for other EU countries (based on what we currently have). Uncertain how extensive EU observability areas will be on GB. Will have to see when we get the methodology. KORRR - exchange should be TSO to TSO. | No | Grid Code OC1,2 BC1
1547 | 2 | 0 | 0 | 40 | 3(a) | (a) generation; | 2018-09-14 | 12 | EIF+12months | [13 empty] | X | [8 empty] | No | Grid Code OC1,2 BC2 | Context setting requirement - does not need to be literally transposed (DOC1,2)
1548 | 2 | 0 | 0 | 40 | 3(b) | (b) consumption; | 2018-09-14 | 12 | EIF+12months | [13 empty] | X | [8 empty] | No | Grid Code OC1,2 BC3 | Context setting requirement - does not need to be literally transposed (DOC1,2)
1549 | 2 | 0 | 0 | 40 | 3(c ) | (c) schedules; | 2018-09-14 | 12 | EIF+12months | [13 empty] | X | [8 empty] | No | Grid Code OC1,2 BC4 | Context setting requirement - does not need to be literally transposed (DOC1,2)
1550 | 2 | 0 | 0 | 40 | 3(d) | (d) balance positions; | 2018-09-14 | 12 | EIF+12months | [13 empty] | X | [8 empty] | No | Grid Code OC1,2 BC5 | Context setting requirement - does not need to be literally transposed (DOC1,2)
1551 | 2 | 0 | 0 | 40 | 3(e ) | (e) planned outages and substation topologies; and | 2018-09-14 | 12 | EIF+12months | [13 empty] | X | [8 empty] | No | Grid Code OC1,2 BC6 | Context setting requirement - does not need to be literally transposed (DOC1,2)
1552 | 2 | 0 | 0 | 40 | 3(f) | (f) forecasts. | 2018-09-14 | 12 | EIF+12months | [13 empty] | X | [8 empty] | No | Grid Code OC1,2 BC7 | Context setting requirement - does not need to be literally transposed (DOC1,2)
1553 | 2 | 0 | 0 | 40 | 4 | 4. Each TSO shall represent the information in paragraph (3) as injections and withdrawals at each node of the TSO’s individual grid model referred to in Article 64. | 2018-09-14 | 12 | EIF+12months | ü | [12 empty] | X |  |  |  | X |  |  |  |  | No | Context setting requirement - does not need to be literally transposed | Context setting requirement - does not need to be literally transposed
1554 | 2 | 0 | 0 | 40 | 5 | 5. In coordination with the DSOs and SGUs, each TSO shall determine the applicability and scope of the data exchange based on the following categories: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | To be determined in GB via normal governance
1555 | 2 | 0 | 0 | 40 | 5(a) | (a) structural data in accordance with Article 48; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | To be determined in GB via normal governance | To be determined in GB via normal governance
1556 | 2 | 0 | 0 | 40 | 5(b) | (b) scheduling and forecast data in accordance with Article 49; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | To be determined in GB via normal governance | To be determined in GB via normal governance
1557 | 2 | 0 | 0 | 40 | 5(c ) | (c) real-time data in accordance with Article 44, Article 47 and Article 50; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | To be determined in GB via normal governance | To be determined in GB via normal governance
1558 | 2 | 0 | 0 | 40 | 5(d) | (d) provisions in accordance with Article 47, 51, Article 52 and Article 53. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | To be determined in GB via normal governance | To be determined in GB via normal governance
1559 | 2 | 0 | 0 | 40 | 6 | 6. By 6 months after entry into force of this Regulation, all TSOs shall jointly agree on key organisational requirements, roles and responsibilities in relation to data exchange. Those organisational requirements, roles and responsibilities shall take into account and complement where necessary the operational conditions of the generation and load data methodology developed in accordance with Article 16 of Regulation (EU) No 2015/1222. They shall apply to all data exchange provisions in this Title and shall include organisational requirements, roles and responsibilities for the following elements: | 2018-03-14 | 6 | EIF+6months | ü | [12 empty] | X | [9 empty] | All TSO obligation to agree on KORRR methodology | TSO obligation
1560 | 2 | 0 | 0 | 40 | 6(a) | (a) obligations for TSOs to communicate without delay to all neighbouring TSOs any changes in the protection settings, thermal limits and technical capacities at the interconnectors between their control areas; | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | Obligation only on SO | TSO obligation
1561 | 2 | 0 | 0 | 40 | 6(b) | (b) obligations for DSOs directly connected to the transmission system to inform the TSOs they are connected to, within the agreed timescales, of any changes in the data and information pursuant to this Title; | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | CUSC Obligations, Grid Code PCA.1.2b | CUSC obligation DRC5.3
1562 | 2 | 0 | 0 | 40 | 6 (c ) | (c) obligations for the adjacent DSOs and/or between the downstream DSO and upstream DSO to inform each other within agreed timescales of any changes in the data and information pursuant to this Title; | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | CUSC Obligations, Grid Code PC | DPC8.2.2
1563 | 2 | 0 | 0 | 40 | 6(d) | (d) obligations for SGUs to inform their TSO or DSO, within agreed timescales, about any relevant changes in the data and information established pursuant to this Title; | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | PCA.1.2, OC2 | DPC8.2.2
1564 | 2 | 0 | 0 | 40 | 6(e ) | (e) detailed contents of the data and information established pursuant to this Title, including main principles, type of data, communication means, format and standards to be applied, timing and responsibilities; | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | Context setting requirement - does not need to be literally transposed | Context setting requirement - does not need to be literally transposed
1565 | 2 | 0 | 0 | 40 | 6(f) | (f) the time stamping and frequency of delivery of the data and information to be provided by DSOs and SGUs, to be used by TSOs in the different timescales. The frequency of information exchanges for real-time data, scheduled data and update of structural data shall be defined; and | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | Context setting requirement - does not need to be literally transposed - but effected through GB governance | Context setting requirement - does not need to be literally transposed - but effected through GB governance
1566 | 2 | 0 | 0 | 40 | 6(g) | (g) the format for the reporting of the data and information established pursuant to this Title. | 2018-03-14 | 6 | EIF+6months | [13 empty] | X | [9 empty] | Context setting requirement - does not need to be literally transposed - but effected through GB governance | Context setting requirement - does not need to be literally transposed - but effected through GB governance
1567 | 2 | 0 | 0 | 40 | 6(g) | The organisational requirements, roles and responsibilities shall be published by ENTSO for Electricity. | 2017-09-14 | [15 empty] | X | [9 empty] | TSO to TSO format as per OPDE and TSO to DSO/SGU as per existing national formats | TSO obligation
1568 | 2 | 0 | 0 | 40 | 7 | 7. By 18 months after entry into force of this Regulation, each TSO shall agree with the relevant DSOs on effective, efficient and proportional processes for providing and managing data exchanges between them, including, where required for efficient network operation, the provision of data related to distribution systems and SGUs. Without prejudice to the provisions of paragraph 6(g), each TSO shall agree with the relevant DSOs on the format for the data exchange. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | As of today, TSO gets all data that is officially needed hence we are currently compliant. If that changes, TSO will need to raise a mod to change the GC to force DNOs/SGUs to provide different data which will be actioned through existing code governance | TSO obligation
1569 | 2 | 0 | 0 | 40 | 8 | 8. Transmission-connected SGUs shall have access to the data related to their commissioned network installations at the connection point. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | GG - what is the procedure and format of the data? - this needs to be set out through GC0106. TJ - 1.PCA8 in GC (parties that do modelling) 2. OC2 outage information 3. DRC schedule 9 pg. 54 - data NG has to provide to end parties | No | Grid Code PCA8, OC2 , DRC schedule 9 | TSO obligation
1570 | 2 | 0 | 0 | 40 | 9 | 9. Each TSO shall agree with the transmission-connected DSOs on the scope of additional information to be exchanged between them concerning commissioned network installations. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [7 empty] | Similar to above point - GG, need to have the format methodoloy about how SGUs access that data - this should be covered in KORRR amendments (each TSO should decide on the format). If already an existing format as specified in the GC, this will be used. Is the realtime data allowed between TSOs/DSOs? We supply network data to TOs under the STC, with confidential bit stripped out (costs etc.). Also see PC88 of Grid Code. | No | Grid Code PCA8 (Data provided by NG to user), PCA6 (Data required from NG for more detail transmission modelling studies) | TSO obligation
1571 | 2 | 0 | 0 | 40 | 10 | 10. DSOs with a connection point to a transmission system shall be entitled to receive the relevant structural, scheduled and real-time information from the relevant TSOs and to gather the relevant structural, scheduled and real-time information from the neighbouring DSOs. Neighbouring DSOs shall determine, in a coordinated manner, the scope of information that may be exchanged. | 2019-03-14 | 18 | EIF+18months | [9 empty] | X |  |  |  | X | [8 empty] | No | Grid Code planning code week 42 process | Data exchanged via NG's existing processes
1572 | 2 | 0 | 0 | 41 | 0 | Article 41 - Structural and forecast data exchange | 2017-09-14 | [15 empty] | X | [8 empty] | No | Context setting requirement - does not need to be literally transposed - but confirm exchange of third party data. Obligation on SO, TO, OFTO and I/C
1573 | 2 | 0 | 0 | 41 | 1 | 1. Neighbouring TSOs shall exchange at least the following structural information related to the observability area: | 2019-03-14 | 18 | EIF+18months | ü | ü | ü | ü | [9 empty] | X | [10 empty] | TSO obligation
1574 | 2 | 0 | 0 | 41 | 1(a) | (a) the regular topology of substations and other relevant data, by voltage level; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1575 | 2 | 0 | 0 | 41 | 1(b) | (b) technical data on transmission lines; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1576 | 2 | 0 | 0 | 41 | 1(c ) | (c) technical data on transformers connecting the DSOs, SGUs which are demand facilities and generators’ block-transformers of SGUs which are power generating facilities; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1577 | 2 | 0 | 0 | 41 | 1(d) | (d) the maximum and minimum active and reactive power of SGUs which are power generating modules; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | PCA3.2.2.f(i)- Synchronous generating units, PCA3.2.2.f(ii)- Power park modules | TSO obligation
1578 | 2 | 0 | 0 | 41 | 1(e ) | (e) technical data on phase-shifting transformers; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1579 | 2 | 0 | 0 | 41 | 1(f) | (f) technical data on HVDC systems; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1580 | 2 | 0 | 0 | 41 | 1(g) | (g) technical data on reactors, capacitors and static volt-ampere reactive (VAR) compensators; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1581 | 2 | 0 | 0 | 41 | 1(h) | (h) operational security limits defined by each TSO according to Article 25. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | SQSS | TSO obligation
1582 | 2 | 0 | 0 | 41 | 2 | 2. To coordinate the protection of their transmission systems, neighbouring TSOs shall exchange the protection setpoints of the lines for which the contingencies are included as external contingencies in their contingency lists. | 2019-03-14 | 18 | EIF+18months | ü | ü | ü | ü | [9 empty] | X | [8 empty] | No | STCP12-1 | TSO obligation
1583 | 2 | 0 | 0 | 41 | 3 | 3. To coordinate their operational security analysis and to establish the common grid model in accordance with Article 67, Article 68, Article 69 and Article 70, each TSO shall exchange, with at least all other TSOs from the same synchronous area, at least the following data: | 2019-03-14 | 18 | EIF+18months | ü | ü | ü | ü | [9 empty] | X |  |  |  | X |  |  |  |  | No |  | TSO obligation
1584 | 2 | 0 | 0 | 41 | 3(a) | (a) the topology of the 220 kV and higher voltage transmission systems within its control area; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X |  |  |  | X |  |  |  |  | No | TSO data provided through Individual Grid Model for all GB synchronous area | TSO obligation
1585 | 2 | 0 | 0 | 41 | 3(b) | (b) a model or an equivalent of the transmission system with voltage below 220 kV with significant impact on its own transmission system; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X |  |  |  | X |  |  |  |  | No | TSO data provided through Individual Grid Model | TSO obligation
1586 | 2 | 0 | 0 | 41 | 3(c ) | (c) the thermal limits of the transmission system elements; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X |  |  |  | X |  |  |  |  | No | TSO data provided through Individual Grid Model for all GB synchronous area | TSO obligation
1587 | 2 | 0 | 0 | 41 | 3(d) | (d) a realistic and accurate forecasted aggregate amount of injection and withdrawal, per primary energy source, at each node of the transmission system, for different time-frames. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X |  |  |  | X |  |  |  |  | No | TSO data provided through Individual Grid Model for all GB synchronous area | TSO obligation
1588 | 2 | 0 | 0 | 41 | 4 | 4. To coordinate the dynamic stability assessments pursuant to Article 38(2) and (4), and to carry them out, each TSO shall exchange with the other TSOs of the same synchronous area or of its relevant part the following data: | 2019-03-14 | 18 | EIF+18months | ü | ü | ü | ü | [9 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1589 | 2 | 0 | 0 | 41 | 4(a) | (a) data concerning SGUs which are power generating modules relating to, but not limited to: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No |  | TSO obligation
1590 | 2 | 0 | 0 | 41 | 4(a)(i) | (i) electrical parameters of the alternator suitable for the dynamic stability assessment, including total inertia; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1591 | 2 | 0 | 0 | 41 | 4(a)(ii) | (ii) protection models; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1592 | 2 | 0 | 0 | 41 | 4(a)(iii) | (iii) alternator and prime mover; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1593 | 2 | 0 | 0 | 41 | 4(a)(iv) | (iv) step-up transformer description; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1594 | 2 | 0 | 0 | 41 | 4(a)(v) | (v) minimum and maximum reactive power; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1595 | 2 | 0 | 0 | 41 | 4(a)(vi) | (vi) voltage models and speed controller models; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1596 | 2 | 0 | 0 | 41 | 4(a)(vii) | (vii) prime movers models and excitation system models suitable for large disturbances; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1597 | 2 | 0 | 0 | 41 | 4(b) | (b) the data on type of regulation and voltage regulation range concerning tap changers, including the description of existing on-load tap changers, and the data on type of regulation and voltage regulation range concerning step-up and network transformers; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1598 | 2 | 0 | 0 | 41 | 4(c ) | (c) the data concerning HVDC systems and FACTS devices on the dynamic models of the system or the device and its associated regulation suitable for large disturbances. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP22-1 | TSO obligation
1599 | 2 | 0 | 0 | 42 | 0 | Article 42 - Real-time data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | NG to think about should it be codified (as it's other people's data) somewhere - if answer is no because it's national TSO agreement, how does National Grid prove compliance? OPDE? - 2. is this sufficient to prove compliance Action: feedback next time (Ofgem will want to know compliance before we get revised observability area) |  | Grid Code CC.6.5.6 (Operation metering) | TSO obligation
1600 | 2 | 0 | 0 | 42 | 1 | 1. In accordance with Articles 18 and 19, each TSO shall exchange with the other TSOs of the same synchronous area the following data on the system state of its transmission system using the IT tool for real-time data exchange at pan-European level as provided by ENTSO for Electricity: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [7 empty] | OPDE is the IT tool for real-time and storage. Do TOs need to use the IT tool or another one? (Graeme Vincent) currently exchanged through STC. |  | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1601 | 2 | 0 | 0 | 42 | 1(a) | (a) frequency; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1602 | 2 | 0 | 0 | 42 | 1(b) | (b) frequency restoration control error; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1603 | 2 | 0 | 0 | 42 | 1(c ) | (c) measured active power interchanges between LFC areas; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1604 | 2 | 0 | 0 | 42 | 1(d) | (d) aggregated generation infeed; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1605 | 2 | 0 | 0 | 42 | 1(e ) | (e) system state in accordance with Article 18; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1606 | 2 | 0 | 0 | 42 | 1(f) | (f) setpoint of the load-frequency controller; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1607 | 2 | 0 | 0 | 42 | 1(g) | (g) power exchange (interexchange?) via virtual tie-lines. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Only applies for SO, GB data already exchanged through OPDE. | TSO obligation
1608 | 2 | 0 | 0 | 42 | 2 | 2. Each TSO shall exchange with the other TSOs in its observability area the following data about its transmission system using real-time data exchanges between the TSOs' supervisory control and data acquisition (SCADA) systems and energy management systems: | 2019-03-14 | 18 | EIF+18months | ü | ü | ü | ü | [9 empty] | X | [8 empty] | No |  | TSO obligation
1609 | 2 | 0 | 0 | 42 | 2(a) | (a) actual substation topology; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1610 | 2 | 0 | 0 | 42 | 2(b) | (b) active and reactive power in line bay, including transmission, distribution and lines connecting SGUs; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1611 | 2 | 0 | 0 | 42 | 2(c ) | (c) active and reactive power in transformer bay, including transmission, distribution and SGUs connecting transformers; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1612 | 2 | 0 | 0 | 42 | 2(d) | (d) active and reactive power in power generating facility bay; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1613 | 2 | 0 | 0 | 42 | 2(e ) | (e) regulating positions of transformers, including phase-shifting transformers; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1614 | 2 | 0 | 0 | 42 | 2(f) | (f) measured or estimated busbar voltage; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1615 | 2 | 0 | 0 | 42 | 2(g) | (g) reactive power in reactor and capacitor bay or from a static VAR compensator; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1616 | 2 | 0 | 0 | 42 | 2(h) | (h) restrictions on active and reactive power supply capabilities with respect to the observability area. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | STCP4 | TSO obligation
1617 | 2 | 0 | 0 | 42 | 3 | 3. Each TSO shall have the right to request the TSOs from its observability area to provide real-time snapshots of state estimated data from that TSO’s control area if that is relevant for the operational security of the transmission system of the requesting TSO. | 2019-03-14 | 18 | EIF+18months | ü | ü | ü | ü | [9 empty] | X | [8 empty] | No | State estimator already in place for SO, no relevance for TOs | TSO obligation
1618 | 2 | 0 | 0 | 43 | 0 | Article 43 - Structural data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Grid Code Planning Code; Week24 covered in PC.A.2, PC.A.3, PC.A.4 and OC.6
1619 | 2 | 0 | 0 | 43 | 1 | 1. Each TSO shall determine the observability area of the transmission-connected distribution systems which is needed for the TSO to determine the system state accurately and efficiently, based on the methodology developed in accordance with Article 75. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Grid Code Planning Code; Observability is defined by NG through the Grid Code, subject to changes in Art 75) | TSO obligation - For Grid Code implementation
1620 | 2 | 0 | 0 | 43 | 2 | 2. If a TSO considers that a non-transmission-connected distribution system has a significant influence in terms of voltage, power flows or other electrical parameters for the representation of the transmission system's behaviour, such distribution system shall be defined by the TSO as being part of the observability area in accordance with Article 75. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Significant IDNO etc networks would be visible if connected at subtransmission level through normal WK24 data exchange - and probably through JPTL. If there is generation >SoW threshold on the IDNO development this should trigger SoW. | Significant IDNO etc networks would be visible if connected at subtransmission level through normal WK24 data exchange - and probably through JPTL. If there is generation >SoW threshold on the IDNO development this should trigger SoW.
1621 | 2 | 0 | 0 | 43 | 3 | 3. The structural information related to the observability area referred to in paragraphs 1 and 2 provided by each DSO to the TSO shall include at least: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No
1622 | 2 | 0 | 0 | 43 | 3(a) | (a) substations by voltage; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PCA2.2, DRC Schedule 5 | TSO obligation - For Grid Code implementation
1623 | 2 | 0 | 0 | 43 | 3(b) | (b) lines that connect the substations referred to in point (a); | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PCA2.2, DRC Schedule 5 | TSO obligation - For Grid Code implementation
1624 | 2 | 0 | 0 | 43 | 3(c ) | (c) transformers from the substations referred to in point (a); | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PCA2.2, DRC Schedule 5 | TSO obligation - For Grid Code implementation
1625 | 2 | 0 | 0 | 43 | 3(d) | (d) SGUs; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PCA2.2, DRC Schedule 5 | TSO obligation - For Grid Code implementation
1626 | 2 | 0 | 0 | 43 | 3(e ) | (e) reactors and capacitors connected to the substations referred to in point (a). | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PCA2.3,PCA2.4, DRC Schedule 5 | TSO obligation - For Grid Code implementation
1627 | 2 | 0 | 0 | 43 | 4 | 4. Each transmission-connected DSO shall provide the TSO with an update of the structural information in accordance with paragraph 3 at least every six months. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | New requirement - this absolutely justifies GC0106 change | Yes | NEW (PC.A.1.2(A) (iii) | TSO obligation - For Grid Code implementation
1628 | 2 | 0 | 0 | 43 | 5 | 5. At least once a year, each transmission-connected DSO shall provide the TSO, per primary energy sources, the total aggregated generating capacity of the type A power generating modules subject to requirements of Commission Regulation No (EU) 2016/631 and the best possible estimates of generating capacity of type A power generating modules not subject to or derogated from Commission Regulation No (EU) 2016/631, connected to its distribution system, and the related information concerning their frequency behaviour. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Alan Creighton/Mike Kay have a different take: Grid Code and SOGL are the same here but Alan doesn't think that NG are asking for domestic PV for example as only asking for 1MW or above for 24weeks. Mike Kay thinks the Grid Code does ask for it though. Joaquin is confident that guidance note asks for it. Action: to make sure all DNOs have the same understanding, if all in agreement with JJ (down to 1MW site by site, below that agregated) JJ to send info to Mike Kay to circulate to DNOs. For the DNOs that don't agree, put in touch with SM/JJ. (PCA3E14 in Grid Code - less that what's already in the Grid Code - also look at schedule 11 of data registration code to see what's provided). Should a change be that NG should collect it from us - check whether a mod needs to be raised 1MW plus?? (estimated to best of our ability - check wording with lawyers "best endeavours/reasonable endeavors) | Yes | NEW TBC?:::PCA.3.1.4 | DPC7.3 and DDRC 5b EREC G83 5.1.1 and appendix A3
1629 | 2 | 0 | 0 | 44 | 0 | Article 44 - Real-time data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | The Grid Code, Connection Conditions, CC.6.5.6, Operational Metering
1630 | 2 | 0 | 0 | 44 | 1 | Unless otherwise provided by the TSO, each DSO shall provide its TSO, in real-time, the information related to the observability area of the TSO as referred to in Article 43(1) and (2), including: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1631 | 2 | 0 | 0 | 44 | (a) | (a) the actual substation topology; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1632 | 2 | 0 | 0 | 44 | (b) | (b) the active and reactive power in line bay; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1633 | 2 | 0 | 0 | 44 | (c ) | (c) the active and reactive power in transformer bay; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1634 | 2 | 0 | 0 | 44 | (d) | (d) the active and reactive power injection in power generating facility bay; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1635 | 2 | 0 | 0 | 44 | (e ) | (e) the tap positions of transformers connected to the transmission system; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1636 | 2 | 0 | 0 | 44 | (f) | (f) the busbar voltages; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1637 | 2 | 0 | 0 | 44 | (g) | (g) the reactive power in reactor and capacitor bay; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1638 | 2 | 0 | 0 | 44 | (h) | (h) the best available data for aggregated generation per primary energy source in the DSO area; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1639 | 2 | 0 | 0 | 44 | (h)(i) | (i) the best available data for aggregated consumption in the DSO area. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation - NG are NOT going to ask for this data in G Code (ie using flexibility)
1640 | 2 | 0 | 0 | 45 | 0 | Article 45 - Structural data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X
1641 | 2 | 0 | 0 | 45 | 1 | 1. Each SGU which is a power generating facility owner of a type D power generating module connected to the transmission system shall provide the TSO with at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.2 | TSO obligation - For Grid Code implementation
1642 | 2 | 0 | 0 | 45 | 1(a) | (a) general data of the power generating module, including installed capacity and primary energy source; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.3.2.2(a) | TSO obligation - For Grid Code implementation
1643 | 2 | 0 | 0 | 45 | 1(b) | (b) turbine and power generating facility data including time for cold and warm start; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code - Planning Code, PC.A.2 , Data Registration Code DRC.6.1.2 | TSO obligation - For Grid Code implementation
1644 | 2 | 0 | 0 | 45 | 1(c ) | (c) data for short-circuit current calculation; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code - Planning Code, PC.A.2, Data Registration Code | TSO obligation - For Grid Code implementation
1645 | 2 | 0 | 0 | 45 | 1(d) | (d) power generating facility transformer data; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code - Planning Code, PART 1 - STANDARD PLANNING DATA, PC.A.2 , Data Registration Code | TSO obligation - For Grid Code implementation
1646 | 2 | 0 | 0 | 45 | 1(e ) | (e) FCR data of power generating modules offering or providing that service, in accordance with Article 154; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Not in grid code but whenever we have a contract, it's already exchanged through existing contract until pre-qual process is confirmed (defined through C16). Article 154 - NG interpretation - current arrangements for freq response will remain as mandatory. Alastair thinks current interpretaton doesn't work. Project TERRE consultation mentions Art 154 aswell. | No | Maintain existing data exchange through contracts subject to changes from SOGL Article 154 | TSO obligation - For Grid Code implementation
1647 | 2 | 0 | 0 | 45 | 1(f) | (f) FRR data of power generating modules offering or providing that service, in accordance with Article 158; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | See above | No | Maintain existing data exchange through contracts subject to changes from Article 158 | TSO obligation - For Grid Code implementation
1648 | 2 | 0 | 0 | 45 | 1(g) | (g) RR data of power generating modules that offer or provide that service in accordance with Article 161; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | See above | No | Maintain existing data exchange through contracts subject to changes from Article 161 | TSO obligation - For Grid Code implementation
1649 | 2 | 0 | 0 | 45 | 1(h) | (h) data necessary for restoration of the transmission system; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code, Operating Codes, OC9 Contingency Planning, OC10, OC10.1 - OC10.4, OC12, OC12.1 - OC12.4 | TSO obligation - For Grid Code implementation
1650 | 2 | 0 | 0 | 45 | 1(h)(i) | (i) data and models necessary for performing dynamic simulation; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code, PC.A.2, PC.A.3, PC.A.4, PC.A.5, PC.A.5.7, DRC.6.1.16 | TSO obligation - For Grid Code implementation
1651 | 2 | 0 | 0 | 45 | 1(h)(i) | (j) protection data; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code, PC.A.6.6, DRC.6 | TSO obligation - For Grid Code implementation
1652 | 2 | 0 | 0 | 45 | 1(k) | (k) data necessary for determining the costs of remedial actions in accordance with Article 78(1)(b); where a TSO makes use of market based mechanisms in line with Article 4(2)(d), the provision of prices to be paid by the TSO shall be considered sufficient; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Isn't covered in GC. But covered in scenario where don't use a market based mechanism. If use a market based mechanism then need it. SM to research and provide clarity on (Tim Truscott, BSC perspective) | No | BSC Section 4 | TSO obligation - For Grid Code implementation
1653 | 2 | 0 | 0 | 45 | 1(l) | (l) voltage and reactive power control capability. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6, 7, BC2 PC.A.2.4 | TSO obligation - For Grid Code implementation
1654 | 2 | 0 | 0 | 45 | 2 | 2. Each SGU which is a power generating facility owner of a type B or a type C power generating module connected to the transmission system shall provide the TSO with at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | CC.6.3.2, CC6.3, CC.6.3.8, APPENDIX 6 , 7 , BC2 | TSO obligation - For Grid Code implementation
1655 | 2 | 0 | 0 | 45 | 1(a) | (a) general data of the power generating module, including installed capacity and primary energy source; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 , 7 , BC2 | TSO obligation - For Grid Code implementation
1656 | 2 | 0 | 0 | 45 | 2(b) | (b) data for short-circuit current calculation; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1657 | 2 | 0 | 0 | 45 | 2(c ) | (c) FCR data according to the definition and requirements of the Article 173 for power generating modules offering or providing that service; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | CC6.3, CC.6.3.2, CC6.3, CC.6.3.8, APPENDIX 6, 7 , BC2, | TSO obligation - For Grid Code implementation
1658 | 2 | 0 | 0 | 45 | 2(d) | (d) FRR data for power generating modules that offer or provide that service; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1659 | 2 | 0 | 0 | 45 | 2(e ) | (e) RR data for power generating modules that offer or provide that service; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1660 | 2 | 0 | 0 | 45 | 2(f) | (f) protection data; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1661 | 2 | 0 | 0 | 45 | 2(g) | (g) reactive power control capability; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1662 | 2 | 0 | 0 | 45 | 2(h) | (h) data necessary for determining the costs of remedial actions in accordance with Article 78(1)(b); where a TSO makes use of market based mechanisms in line with Article 4 (2) d), the provision of prices to be paid by the TSO shall be considered sufficient; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1663 | 2 | 0 | 0 | 45 | 2(h)(i) | (i) data necessary for performing dynamic stability assessment according to Article 38. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13 | TSO obligation - For Grid Code implementation
1664 | 2 | 0 | 0 | 45 | 3 | 3. A TSO may request the power generating facility owner of a power generating module connected to the transmission system to provide further data where appropriate for operational security analysis in accordance with Title 2 of Part III. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | PC.A.6.1.3, PC.A.7 | TSO obligation - For Grid Code implementation
1665 | 2 | 0 | 0 | 45 | 4 | 4. Each HVDC system owner or interconnector owner shall provide the TSO with the following data regarding the HVDC system or interconnector: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1666 | 2 | 0 | 0 | 45 | 4(a) | (a) nameplate data of the installation; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1667 | 2 | 0 | 0 | 45 | 4(b) | (b) transformers data; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.3.2.2(a) | TSO obligation - For Grid Code implementation
1668 | 2 | 0 | 0 | 45 | 4(c ) | (c) data on filters and filter banks; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1669 | 2 | 0 | 0 | 45 | 4(d) | (d) reactive power compensation data; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1670 | 2 | 0 | 0 | 45 | 4(e ) | (e) active power control capability; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1671 | 2 | 0 | 0 | 45 | 4(f) | (f) reactive power and voltage control capability; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1672 | 2 | 0 | 0 | 45 | 4(g) | (g) active or reactive operational mode prioritization, if existing; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1673 | 2 | 0 | 0 | 45 | 4(h) | (h) frequency response capability; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1674 | 2 | 0 | 0 | 45 | 4(h)(i) | (i) dynamic models for dynamic simulation; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1675 | 2 | 0 | 0 | 45 | 4(h)(i) | (j) protection data; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1676 | 2 | 0 | 0 | 45 | 4(k) | (k) fault-ride-through capability. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Grid Code PC.A.5.4.3 | TSO obligation - For Grid Code implementation
1677 | 2 | 0 | 0 | 45 | 5 | 5. Each AC interconnector owner shall provide the TSO with at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | N/A in GB | TSO obligation - For Grid Code implementation
1678 | 2 | 0 | 0 | 45 | 5(a) | (a) nameplate data of the installation; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | N/A in GB | TSO obligation - For Grid Code implementation
1679 | 2 | 0 | 0 | 45 | 5(b) | (b) electrical parameters; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | N/A in GB | TSO obligation - For Grid Code implementation
1680 | 2 | 0 | 0 | 45 | 5(c ) | (c) associated protections. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | N/A in GB | TSO obligation - For Grid Code implementation
1681 | 2 | 0 | 0 | 46 | 0 | Article 46 - Scheduled data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No |  | TSO obligation - For Grid Code implementation
1682 | 2 | 0 | 0 | 46 | 1 | 1. Each SGU which is a power generating facility owner of a type B, C or D power generating module connected to the transmission system shall provide the TSO with at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Same as we are now - covered in PN submissions | No | Grid Code BC1.A.1.1, OC.1,2 | TSO obligation - For Grid Code implementation
1683 | 2 | 0 | 0 | 46 | 1(a) | (a) active power output and active power reserves amount and availability, on a day-ahead and intra-day basis; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Same as we are now - covered in PN submissions | No | Grid Code BC1.A.1.1, OC.1,2 | TSO obligation - For Grid Code implementation
1684 | 2 | 0 | 0 | 46 | 1(b) | (b) without any delay, any scheduled unavailability or active power restriction; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Same as we are now - covered in PN submissions | No | Grid Code BC1.A.1.1, OC.1,2 | TSO obligation - For Grid Code implementation
1685 | 2 | 0 | 0 | 46 | 1(c ) | (c) any forecasted restriction in the reactive power control capability; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Same as we are now - covered in PN submissions | No | Grid Code BC1.A.1.1, OC.1,2 | TSO obligation - For Grid Code implementation
1686 | 2 | 0 | 0 | 46 | 1(d) | (d) as an exception to points (a) and (b), in regions with a central dispatch system, data requested by the TSO for the preparation of its active power output schedule. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | N/A in GB | TSO obligation - For Grid Code implementation
1687 | 2 | 0 | 0 | 46 | 2 | 2. Each HVDC system operator shall provide the TSOs with at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No |  | TSO obligation - For Grid Code implementation
1688 | 2 | 0 | 0 | 46 | 2(a) | (a) active power schedule and availability on a day-ahead and intra-day basis; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | static generation data in PCA5.4.3, running regime PCA.3.2.2, Data submission done under BC1 (BM) | TSO obligation - For Grid Code implementation
1689 | 2 | 0 | 0 | 46 | 2(b) | (b) without delay its scheduled unavailability or active power restriction; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | static generation data in PCA5.4.3, running regime PCA.3.2.2, Data submission done under BC1 (BM) | TSO obligation - For Grid Code implementation
1690 | 2 | 0 | 0 | 46 | 2(c ) | (c) any forecast restriction in the reactive power or voltage control capability. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | static generation data in PCA5.4.3, running regime PCA.3.2.2, Data submission done under BC1 (BM) | TSO obligation - For Grid Code implementation
1691 | 2 | 0 | 0 | 46 | 3 | 3. Each AC interconnector or line operator shall provide its scheduled unavailability or active power restriction data to the TSOs. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | N/A in GB | TSO obligation - For Grid Code implementation
1692 | 2 | 0 | 0 | 47 | 0 | Article 47 - Real-time data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1693 | 2 | 0 | 0 | 47 | 1 | 1. Unless otherwise provided by the TSO, each significant grid user which is a power generating facility owner of type B, C or D power generating module shall provide the TSO, in real-time, at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements (CC) | TSO obligation - For Grid Code implementation
1694 | 2 | 0 | 0 | 47 | 1(a) | (a) position of the circuit breakers at the connection point or another point of interaction agreed with the TSO; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. (CC6.3) | TSO obligation - For Grid Code implementation
1695 | 2 | 0 | 0 | 47 | 1(b) | (b) active and reactive power at the connection point or another point of interaction agreed with the TSO; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1696 | 2 | 0 | 0 | 47 | 1(c ) | (c) in the case of power generating facility with consumption other than auxiliary consumption net active and reactive power. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Does this depend on where it's metered? Based on GC0106, not going to change anything that's not in the Grid Code so not proposing any change. GG big problem with this - Type A 800watts - pre-text was because 800watt generator could have an impact but from a data point of view they are being ignored. NG get it anyway in the baseline, not asking for anything more. | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1697 | 2 | 0 | 0 | 47 | 2 | 2. Each HVDC system or AC interconnector owner shall provide, in real-time, at least the following data regarding the connection point of the HVDC system or AC interconnector to the TSOs: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1698 | 2 | 0 | 0 | 47 | 2(a) | (a) position of the circuit breakers; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1699 | 2 | 0 | 0 | 47 | 2(b) | (b) operational status; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1700 | 2 | 0 | 0 | 47 | 2(c ) | (c) active and reactive power. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1701 | 2 | 0 | 0 | 48 | 0 | Article 48 - Structural data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | TSO obligation - For Grid Code implementation
1702 | 2 | 0 | 0 | 48 | 1 | 1. Unless otherwise provided by the TSO, each power generating facility owner of a power generating module which is a SGU pursuant to Article 2(1)(a) and by aggregation of the SGUs pursuant to Article 2(1)(e) connected to the distribution system shall provide at least the following data to the TSO and to the DSO to which it has a connection point: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements (CC).
1703 | 2 | 0 | 0 | 48 | 1(a) | (a) general data of the power generating module, including installed capacity and primary energy source or fuel type; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | DDRC 5b and 5c
1704 | 2 | 0 | 0 | 48 | 1(b) | (b) FCR data according to the definition and requirements of Article 173 for power generating facilities offering or providing the FCR service; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | To be determined by NG what this actually means - but is flexible so may not be required
1705 | 2 | 0 | 0 | 48 | 1(c ) | (c) FRR data for power generating facilities offering or providing the FRR service; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | To be determined by NG what this actually means - but is flexible so may not be required
1706 | 2 | 0 | 0 | 48 | 1(d) | (d) RR data for power generating modules offering or providing the RR service; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | To be determined by NG what this actually means - but is flexible so may not be required
1707 | 2 | 0 | 0 | 48 | 1(e ) | (e) protection data; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | DCP7.4.3 and DDRC 5b & 5c
1708 | 2 | 0 | 0 | 48 | 1(f) | (f) reactive power control capability; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | DDRC 5b and 5c
1709 | 2 | 0 | 0 | 48 | 1(g) | (g) capability of remote access to the circuit breaker; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Probably better if NG do not want this. DPC 6.7.4 sort of applies - but this data is not codified. It will be obvious/available from DNOs' control systems
1710 | 2 | 0 | 0 | 48 | 1(h) | (h) data necessary for performing dynamic simulation according to the provisions in Commission Regulation No (EU) 2016/631; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | DDRC 5b and 5c. G99 Annexes B4 and C7
1711 | 2 | 0 | 0 | 48 | 1(h)(i) | (i) voltage level and location of each power generating module. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Check D Code matches G Code - Mike Kay to check | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | DDCR 5a
1712 | 2 | 0 | 0 | 48 | 2 | 2. Each power generating facility owner of a power generating module which is a SGU in accordance with Article 2(1)(a) and 2(1)(e) shall inform the TSO and the DSO to which it has a connection point, within the agreed time and not later than the first commissioning or any changes to the existing installation, about any change in the scope and the contents of the data listed in paragraph 1. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Included in connexion agreements as well as D Code DPC 8.2.2 and DDRC 5.3
1713 | 2 | 0 | 0 | 49 | 0 | Article 49 - Scheduled data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1714 | 2 | 0 | 0 | 49 | 1 | Unless otherwise provided by the TSO, each power generating facility owner of a power generating module which is a SGU in accordance with Article 2(1)(a) and 2(1)(e) connected to the distribution system shall provide the TSO and the DSO to which it has the connection point, with at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1715 | 2 | 0 | 0 | 49 | (a) | (a) its scheduled unavailability, scheduled active power restriction and its forecasted scheduled active power output at the connection point; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements (OC1,OC2). | DOC2 for unavailability and DOC1 for sheduled output. DDRC Schedule 7
1716 | 2 | 0 | 0 | 49 | (b) | (b) any forecasted restriction in the reactive power control capability; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements (OC1,OC2). | DOC1.4.2 and DDRC Schedule 7 - although these probably should be rewritten to be more precise
1717 | 2 | 0 | 0 | 49 | (c ) | (c) as an exception to paragraphs (a) and (b), in regions with a central dispatch system, data requested by the TSO for the preparation of its active power output schedule. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements (OC1,OC2, BC1). | TSO obligation - For Grid Code implementation
1718 | 2 | 0 | 0 | 50 | 0 | Article 50 - Real-time data exchange | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1719 | 2 | 0 | 0 | 50 | 1 | 1. Unless otherwise provided by the TSO, each power generating facility owner of a power generating module which is a SGU in accordance with Article 2(1)(a) and 2(1)(e) connected to the distribution system shall provide the TSO and the DSO to which it has the connection point, in real-time, at least the following data: | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Not a current G Code requirement - NG will, under the flexibility of Art 40-5 not currently ask for it for small power stations.
1720 | 2 | 0 | 0 | 50 | 1(a) | (a) status of the switching devices and circuit breakers at the connection point; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Not a current G Code requirement - NG will, under the flexibility of Art 40-5 not currently ask for it for small power stations DPC6.7.4
1721 | 2 | 0 | 0 | 50 | 1(b) | (b) active and reactive power flows, current, and voltage at the connection point. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Not a current G Code requirement - NG will, under the flexibility of Art 40-5 not currently ask for it for small power stations DPC6.7.3
1722 | 2 | 0 | 0 | 50 | 2 | 2. Each TSO shall define in coordination with the responsible DSOs which SGUs may be exempted from providing the real-time data listed in paragraph 1 directly to the TSO. In such cases, the responsible TSOs and DSOs shall agree on the aggregated real-time data of the SGUs concerned to be delivered to the TSO. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Not a current G Code requirement - NG will, under the flexibility of Art 40-5 not currently ask for it for small power stations.
1723 | 2 | 0 | 0 | 51 | 0 | Article 51 - Data exchange between TSOs and DSOs concerning significant power generating modules | 2019-03-14 | 18 | EIF+18months | [13 empty] | X
1724 | 2 | 0 | 0 | 51 | 1 | 1. Unless otherwise provided by the TSO, each DSO shall provide to its TSO the information specified in Articles 48, 49 and 50 with the frequency and level of detail requested by the TSO. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Not a current G Code requirement - NG will, under the flexibility of Art 40-5 not currently ask for it for small power stations.
1725 | 2 | 0 | 0 | 51 | 2 | 2. Each TSO shall make available to the DSO, to whose distribution system SGUs are connected, the information specified in Articles 48, 49 and 50 as requested by the DSO. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
1726 | 2 | 0 | 0 | 51 | 3 | 3. A TSO may request further data from a power generating facility owner of a power generating module which is a SGU in accordance with Article 2(1)(a) and 2(1)(e) connected to the distribution system, if it is necessary for the operational security analysis and for the validation of models. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements. | Not a current G Code requirement - NG will, under the flexibility of Art 40-5 not currently ask for it for small power stations. But NG can always ask for more data under current Grid Code provisions
1727 | 2 | 0 | 0 | 52 | 0 | Article 52 - Data exchange between TSOs and transmission-connected demand facilities | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [9 empty] | Aligned to Demand Connection Code | TSO obligation - For Grid Code implementation
1728 | 2 | 0 | 0 | 52 | 1 | 1. Unless otherwise provided by the TSO, each transmission-connected demand facility owner shall provide the following structural data to the TSO: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [9 empty] | DRC.6.2 | TSO obligation - For Grid Code implementation
1729 | 2 | 0 | 0 | 52 | 1(a) | (a) electrical data of the transformers connected to the transmission system; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1730 | 2 | 0 | 0 | 52 | 1(b) | (b) characteristics of the load of the demand facility; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1731 | 2 | 0 | 0 | 52 | 1(c ) | (c) characteristics of the reactive power control. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1732 | 2 | 0 | 0 | 52 | 2 | 2. Unless otherwise provided by the TSO, each transmission-connected demand facility owner shall provide the following data to the TSO: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1733 | 2 | 0 | 0 | 52 | 2(a) | (a) scheduled active and forecasted reactive power consumption on a day-ahead and intraday basis, including any changes of those schedules or forecast; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1734 | 2 | 0 | 0 | 52 | 2(b) | (b) any forecasted restriction in the reactive power control capability; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1735 | 2 | 0 | 0 | 52 | 2(c ) | (c) in case of participation in demand response, a schedule of its structural minimum and maximum power range to be curtailed; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1736 | 2 | 0 | 0 | 52 | 2(d) | (d) by exception to point (a), in regions with a central dispatch system, the data requested by the TSO for the preparation of its active power output schedule. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1737 | 2 | 0 | 0 | 52 | 3 | 3. Unless otherwise provided by the TSO, each transmission-connected demand facility owner shall provide the following data to the TSO in real-time: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1738 | 2 | 0 | 0 | 52 | 3(a) | (a) active and reactive power at the connection point; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1739 | 2 | 0 | 0 | 52 | 3(b) | (b) the minimum and maximum power range to be curtailed. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | DRC.6.2 | TSO obligation - For Grid Code implementation
1740 | 2 | 0 | 0 | 52 | 4 | 4. Each transmission-connected demand facility owner shall describe to its TSO its behaviour at the voltage ranges referred to in Article 27. | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [7 empty] | Uncertainty - how do customers know they are compliant? NG should be able to say on behalf of all our customers that they are compliant | No | Schedule 7 of DRC, PCA.4.7 | TSO obligation - For Grid Code implementation
1741 | 2 | 0 | 0 | 53 | 0 | Article 53 - Data exchange between TSOs and distribution-connected demand facilities or third parties participating in demand response | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [7 empty] | Demand response isn't covered in Grid Code at the moment, it's done through commercial contract arrangements, but any party connected to transmission should provide appropriate data. As long as contracts are compliant with this, there's no problem. Tony: issue needs to be raised with Adam Simms. Can GC0104 be used as the vehicle to cover this off? Premature to resolve 53 without prior discussion with GC0104 (23/01/18) |  | Flexible but also handled in collaboration with GC0104 and new Demand Side addition to Grid Code
1742 | 2 | 0 | 0 | 53 | 1 | 1. Unless otherwise provided by the TSO, each SGU which is a distribution-connected demand facility and which participates in demand response other than through a third party shall provide the following scheduled and real-time data to the TSO and to the DSO: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1743 | 2 | 0 | 0 | 53 | 1(a) | (a) structural minimum and maximum active power available for demand response and the maximum and minimum duration of any potential usage of this power for demand response; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1744 | 2 | 0 | 0 | 53 | 1(b) | (b) a forecast of unrestricted active power available for demand response and any planned demand response; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1745 | 2 | 0 | 0 | 53 | 1(c ) | (c) real-time active and reactive power at the connection point; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1746 | 2 | 0 | 0 | 53 | 1(d) | (d) a confirmation that the estimations of the actual values of demand response are applied. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1747 | 2 | 0 | 0 | 53 | 2 | 2. Unless otherwise provided by the TSO, each SGU which is a third party participating in demand response as defined in Article 27 of Commission Regulation No (EU) 2016/1388, shall provide the TSO and the DSO at the day-ahead and close to real-time and on behalf of all of its distribution-connected demand facilities, with the following data: | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1748 | 2 | 0 | 0 | 53 | 2(a) | (a) structural minimum and maximum active power available for demand response and the maximum and minimum duration of any potential activation of demand response in a specific geographical area defined by the TSO and DSO; | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1749 | 2 | 0 | 0 | 53 | 2(b) | (b) a forecast of unrestricted active power available for the demand response and any planned level of demand response in a specific geographical area defined by the TSO and DSO; | 2019-03-14 | 18 | EIF+18months | ü | [12 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1750 | 2 | 0 | 0 | 53 | 2(c ) | (c) real-time active and reactive power; and | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
1751 | 2 | 0 | 0 | 53 | 2(d) | (d) a confirmation that the estimations of the actual values of demand response are applied. | 2019-03-14 | 18 | EIF+18months | [13 empty] | X | [8 empty] | No | Flexible as per Article 40.5- Maintain existing data exchange through contract framework. Future mods will be raised based on changes to system operational requirements. | Needs further discussion - but suggest that we use the flexibility to not codify this and deal with it contractually
Formulas:
Applicable date = DATE(YEAR(G1), MONTH(G1)+[EIF offset in months], DAY(G1))
Note on A3: Grouping details (from left) 1-Work Streams(WS) 2-TITLES 3-CHAPTERS(IONDEX VIEW) 4-SECTIONS 5-ARTICLES(ALL OPEN VIEW)
Note on A4: *****PLEASE DO NOT CHANGE***** This column is used to re-order the ROWS if the filter function is used on this document and the original order has been changed.
Note on C4: ZERO("0") is allcated for TITLES row.
Note on D4: ZERO("0") is allcated for TITLES row.
Note on E4: ZERO("0") is allcated for TITLES row.
Note on F4: ZERO("0") is allcated for TITLES row.

## Project Gantt (hidden)
Project EU Elec - Work Stream Plan
| Key: |  | Mandated manually filled cells |  | Current Month |  | Proposal Development/ Consultation | - | Completed Task
|  | NOT BOLDED | AUTOMATED fill - please do not edit |  | Task Schedule |  | NRA Approval/Approval | EIF | CONFIRMED EIF Dates | CONFIRMED EIF Dates
|  | BOLDED | Information needs to be entered manually |  | SUB Task Schedule |  | Implementation | EIF | FCA CONFIRMED EIF Dates | FCA CONFIRMED EIF Dates
|  |  | Sub Sub Tasks |  | SUB SUB Task Schedule |  | Other Tasks |  | CODE MODs | CODE MODs
[13 empty] | 2013 | [11 empty] | 2014 | [11 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022 | [11 empty] | 2023
[13 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half
ID Tasks # | Work stream | Lead & Resource | IS Lead | Dependencies | Articles | EIF | Start | End | Cal. Days | % Done | Work Weeks | Work Days | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
0.0.1 | Regional design of long-term transmission rights | TBC |  | [ID #] | FCA 31(2) |  | 2016-08-01 | 2017-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 9: TSO; 2nd Half 10: Consultation; 1st Half 2: NRA Approval
0.0.2 | Nomination procedures for physical transmission rights | TBC |  | [ID #] | FCA 36(2) |  | 2016-08-01 | 2018-01-31 | 549 | 25% | 78.6 | 393 | 2nd Half 9: TSOs develop first report; 1st Half 4: Consultation; 2nd Half 8: NRA Approval
0.0.3 | Fallback | TBC |  | [ID #] | FCA 42(2) |  | 2016-08-01 | 2017-07-31 | 365 | 80% | 52.2 | 261 | 2nd Half 9: TSOs develop - Timing unclear in FCA
0.0.4 | SAP estabilshment (Single Allocation Platform) | TBC |  | 3.6.5 | FCA 48(2) |  | 2017-08-01 | 2019-07-31 | 730 | 0% | 104.4 | 522 | 2nd Half 10: EIF; 2nd Half 8: TSOs Develop
0.0.5 | SAP requirements | TBC |  | [ID #] | FCA 49(1) |  | 2017-08-01 | 2018-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 8: TSOs Develop; 1st Half 2: NRA Approval
0.0.6 | Hermonised Allocation Rules(HAR) | TBC |  | [ID #] | FCA 51(1) |  | 2017-08-01 | 2018-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 8: TSOs Dev; 2nd Half 10: Consultation; 1st Half 2: NRA Approval
0.0.7 | SAP costs | TBC |  | [ID #] | FCA 59 |  | 2017-08-01 | 2018-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 8: TSOs Develop; 1st Half 2: NRA Approval
1 | System Operation (TSOG & ER) | John Young | Stefan D'alessandro (IS PM) |  |  |  | 2016-06-01 | 2020-07-31 |  | 0.6973%
1.1 | GENERAL PROVISIONS | John Young |  | [ID #] |  |  | 2016-11-14 | 2018-07-31 |  | 0% | bar: 2nd Half 11 to 2nd Half 7
1.1.1 | GENERAL PROVISIONS |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval
1.1.2 | Modification Approval (GB code) |  |  | 4.1.1 | [Articles] |  | 2016-11-14 | 2018-07-31 | 625 | 0% | 89.4 | 447 | 2nd Half 11: Mod Assessment; 1st Half 2: Mod Approval
1.2 | Data Exchange | John Young |  | [ID #] |  |  | 2016-09-07 | 2018-08-31 |  | 4.167% |  |  | 2nd Half 9: 4.167%
1.2.1 | Ref Art 72 - Exchange data with all other TSOs to the extent that it is necessary for carrying out the operational security analysis |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-04-30 | 454 | 0% | 64.8 | 324 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: IMP
1.2.2 | Agree on key organisational requirements, roles and responsibilities in relation to data exchange [EIF+6m] |  |  | [ID #] | [Articles] |  | 2016-09-07 | 2017-01-31 | 147 | 25% | 21 | 105 | 1st Half 1: EIF; 1st Half 2: Consultation; 1st Half 4: -; 1st Half 5: -; 1st Half 6: -; 2nd Half 8: ("Rreport to Authority" folloby "Modification Approval", Then "All TSOs shall define a harmonised data format for data exchange")
1.2.3 | Define Data Exchange Scope [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 8: (Modification change & approval)
1.2.4 | Scheduled & Structural Data Exchange [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 8: (Modification change & approval)
1.2.5 | Real time Data Exchange [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 8: (Modification change & approval)
1.2.6 | Modification Approval (GB code) |  |  | 4.2.1/4.2.2/4.2.3/4.2.4/4.2.5 | [Articles] |  | 2017-06-01 | 2018-08-31 | 457 | 0% | 65.4 | 327 | 1st Half 1: EIF; 1st Half 6: Mod Assessment; 1st Half 2: Mod Approval
1.3 | Reserve Providers | John Young |  | [ID #] |  |  | 2016-09-07 | 2018-04-30 |  | 0% | bar: 2nd Half 9 to 1st Half 4
1.3.1 | Define reserve technical requirements [EIF+12m] |  |  | [ID #] | [Articles] |  | 2016-09-07 | 2017-09-06 | 365 | 0% | 52.2 | 261 | 2nd Half 9: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.3.2 | Pre-Qualification of Reserves Process (JY??) [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.3.3 | Modification Approval (GB code) |  |  | 4.3.1/4.3.2 | [Articles] |  | 2017-03-01 | 2018-04-30 | 426 | 0% | 60.8 | 304 | 1st Half 1: EIF; 1st Half 3: Mod Assessment; 2nd Half 11: Mod Approval
1.4 | Planning & Scheduling | John Young |  | [ID #] |  |  | 2017-02-01 | 2018-11-30 |  | 0% | bar: 1st Half 1 to 2nd Half 11
1.4.1 | OP Contingency analysis and handling (=6months NRA Approval) [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.2 | Operational security analysis [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.3 | Methodology for assessing relevance of assets. [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.4 | Availability Plans [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.5 | Regional Security Coordination(NRA Approval 75 +3months) [EIF+19m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-08-31 | 577 | 0% | 82.6 | 413 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 9: (Modification change & approval)
1.4.6 | Proposal for Regional Operational Security Coordination [EIF+21] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.7 | Com Grid Model building [EIF+21m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.8 | Lists of relevant generating modules and relevant facilities [EIF+21] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.9 | Lists of relevant grid elements [EIF+21] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.10 | Year Ahead Availability plans [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.11 | Procedure for handling forced outages [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.12 | Adequacy Analysis [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.13 | ENTSO-E Operational Planning Data Environment [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.14 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Mod Assessment; 1st Half 4: Mod Approval
1.5 | LFCR | John Young |  | [ID #] |  |  | 2016-06-01 | 2018-12-31 |  | 0% | bar: 1st Half 1 to 2nd Half 12
1.5.1 | LFCR TITLE 2 - Frequency Quality Parameters |  |  | [ID #] | [Articles] |  | 2017-01-02 | 2018-08-31 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP
1.5.2 | Process Structure [EIF+4m] (Check with JY Code Mapping) |  |  | [ID #] | [Articles] |  | 2017-01-02 | 2017-04-13 | 102 | 0% | 14.8 | 74 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 4: -; 1st Half 5: -; 1st Half 6: ("Rreport to Authority" folloby "Modification Approval")
1.5.3 | LFCR - Opearational Agreement [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.5.4 | Automatic and manual frequency restoration process implementation [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-12-31 | 699 | 0% | 99.8 | 499 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: Implementation & Testing; 1st Half 1: (Modification Approval)
1.5.5 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2016-06-01 | 2017-07-31 | 426 | 0% | 60.8 | 304 | 1st Half 1: EIF; 1st Half 6: Mod Assessment; 1st Half 2: Mod Approval
1.6 | Operational Practices (TBC) | John Young |  | [ID #] |  |  | 2017-02-01 | 2018-12-31 |  | 0.7143% |  |  | 1st Half 2: 0.7143%
1.6.1 | Operational Security |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 5% | 47.6 | 238 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.6.1.1 | Modification Approval | [5 empty] | 2017-09-01 | 2018-07-31 | 334 | 5% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.1 | OS TITLE 1 - Operational Security Requirements |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.2 | OS TITLE 3 - Compliance |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.3 | OP TITLE 3 - Procedure for handling forced outages |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.4 | OP TITLE 5 - Ancillary Services |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.5 | OP TITLE 6 - Scheduling |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 25% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.2 | OS - Business continuity plan [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 4: IMP; 2nd Half 8: (Modification change & approval); 2nd Half 9: (Modification change & approval)
1.6.3 | Training plan [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Training Plan; 2nd Half 7: Resource Identification; 1st Half 1: Communication; 2nd Half 8: (IMP)
1.6.4 | Dynamic stability study [EIF+24m] |  |  | [ID #] | [Articles] |  | 2018-01-01 | 2018-12-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 1: Proposal Development; 1st Half 4: NRA Approval; 2nd Half 10: IMP
1.6.5 | Updates of year-ahead individual and comgrid models [EIF+18m] |  |  | [ID #] | [Articles] |  | 2018-01-01 | 2018-12-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 1: Proposal Development; 1st Half 4: NRA Approval; 2nd Half 10: IMP
1.6.6 | Define minimum required inertia by 6months following study in Art 39a [EIF+30m] |  |  | [ID #] | [Articles] |  | 2018-01-01 | 2018-12-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 1: Proposal Development; 1st Half 4: NRA Approval; 2nd Half 10: IMP
1.6.7 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2018-02-01 | 2018-08-03 | 184 | 0% | 26.4 | 132 | 1st Half 1: EIF; 1st Half 2: Mod Assessment; 2nd Half 10: Mod Approval
1.7 | Emergency Restoration(TBC) | John Young |  | [ID #] |  |  | 2017-05-01 | 2020-07-31 |  | 0% | bar: 1st Half 5 to 2nd Half 7
1.7.1 | Emergency Restoration [EIF+12] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2018-04-30 | 365 | 0% | 52.2 | 261 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 8: NRA Approval; 2nd Half 11: Compliance Testing; 1st Half 2: Monitoring
1.7.2 | Restoration Plan [EIF+12] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2018-04-30 | 365 | 0% | 52.2 | 261 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 11: NRA Approval
1.7.3 | System Defence Plan [EIF+12] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2018-04-30 | 365 | 0% | 52.2 | 261 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 11: NRA Approval
1.7.4 | Defence System Implementation [EIF+24] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2019-04-30 | 730 | 0% | 104.4 | 522 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 11: NRA Approval; 1st Half 5: Compliance Testing; 2nd Half 11: Monitoring
1.7.5 | Automatic under-frequency control scheme [EIF+60] |  |  | [ID #] | [Articles] |  | 2019-05-01 | 2020-04-30 | 366 | 0% | 52.4 | 262 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: IMP
1.7.6 | Tools and Communication [EIF+60] |  |  | [ID #] | [Articles] |  | 2019-05-01 | 2020-04-30 | 366 | 0% | 52.4 | 262 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: IMP
1.7.7 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2019-05-01 | 2020-07-31 | 458 | 0% | 65.6 | 328 | 1st Half 4: EIF; 1st Half 6: Mod Assessment; 1st Half 2: Mod Approval
Article 57 - Performing operational tests and analysis
Article 57 Performing operational tests and analysis
Formulas:
EIF = IF([Completed Task]=0,[Proposal Development/ Consultation],[Proposal Development/ Consultation]+[Completed Task]-1)
EIF = MAX([EIF, row below],I21,I28,I32,I47,I53,I67)
Proposal Development/ Consultation = MIN([Proposal Development/ Consultation, row below],H21,H28,H32,H47,H53,H67)
Proposal Development/ Consultation = MIN([Proposal Development/ Consultation, row below],H20)
Note on A9: ID - Task Number Level 1: 1, 2, 3, ... Level 2: 1.1, 1.2, 1.3, ... Level 3: 1.1.1, 1.1.2, 1.1.3, … The WBS uses a formula to control the numbering, but the formulas are different for different levels. When you add rows, you need to use th etemaplte located at the bottom of this document.
Note on B9: Work stream - Task Name Enter the name of each task and sub-task. Use indents for sub-tasks.
Note on C9: Task Lead Enter the name of the Task Lead in this column. Preferbly with the percetage allocation
Note on E9: Dependencies Insert Task ID number which has dependencies against.
Note on F9: Articles: Articles against the document. Article Number(section) XX(Y) ie. 12(3)
Note on H9: Task Start Date
Note on I9: Task End Date
Note on J9: Manual Input - How Many days(including weekends). This will determin the END DATE.
Note on K9: % Completed This is a manual input. Once you enter the percentage progressed/completed, the GREY bar will appear.
Note on L9: Calculation for number of Working Weeks from "Cal.Days"
Note on M9: Calculation for number of Working Days from "Cal.Days". (Excluding Weekends)

## EIF Dates (hidden)
Work Stream | EIF Dates | Officaly confirmed? | When was it confirmed? | Success Criteria | NOTE
Balancing | 2017-04-01 | No | No
Common Grid Model (CGM) | TBC | No | No
Capacity Calculation (CACM) | 2015-08-14 | Yes | 2015 | Complete proposal
Capacity Calculation (FCA) | 2016-10-17 | Yes | 2016-10-01 | Complete proposal
System Operation (TSOG) | 2017-01-01 | No | No
System Operation (ER) | 2016-04-01 | No | No
Grid Connection Code (RfG) | 2016-05-17 | Yes | 2016 | Complete Implementation | Generation 800w and above
Grid Connection Code (HVDC) | 2016-09-15 | Yes | 2016 | Complete Implementation | to be confirmed by WS leads
Grid Connection Code (DCC) | 2016-09-06 | Yes | 2016 | Complete Implementation | to be confirmed by WS leads

## KORRR
[6 empty] | Obligation On | [10 empty] | NGET Workstream
Title | Chapter | Article | Paragraph | Article Text | Applicable date | SO | TO | I/C | OFTO | DBEIS | Ofgem | All TSOs | ENTSO-E | DSOs | Generators | Demand Faclities | Data Exchange | Operational Practices | Planning and RSC | Operational Agreements | Common Grid Model | Reserve Providers | information transparency | General Compliance | WG Comments relative to GB regulation and code modifications if necessary | Is a mod required? | Grid Code Reference | D Code Reference
0 | 0 | Whereas | 1 | This document is a common proposal developed by all Transmission System Operators (hereinafter referred to as “TSOs”) regarding the key organisational requirements, roles and responsibilities relating to data exchange (hereinafter referred to as "KORRR"). | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 2 | The KORRR takes into account the general principles and goals set in Commission Regulation (EU) 2017/1485 establishing a guideline on electricity transmission system operation (hereinafter referred to as “SO GL”), Commission Regulation (EU) 2015/1222 establishing a guideline on capacity allocation and congestion management, (hereinafter referred to as “CACM”), as well as, Commission Regulation (EU) 2017/2195 establishing a guideline on electricity balancing (hereinafter referred to as “EB GL” ). The purpose of the SO GL is to safeguard operational security, frequency quality and the efficient use of the interconnected system and resources. To achieve these goals, it is necessary that each party of the electric system has the necessary observability of the network elements and services that impact their activities. Especially relevant is the global demand-generation balance through the procurement of balancing services and activation of balancing energy bids, where EG BL assigns the responsibility to the TSO in the EB GL. The KORRR addresses in particular the key roles, requirements and responsibilities of the TSOs, the distribution system operators (hereinafter referred to as “DSOs”), the closed distribution system operators (hereinafter referred to as “CDSOs”) and the significant grid users (hereinafter referred to as “SGUs”) in relation to the data exchange necessary to ensure that observability. | 2019-03-14 | [21 empty] | Real time data: The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) CUSC bilateral connection agreement Static data: Grid Code - Data Registration Code (various schedules) STCP 12-1 Data Exchange Mechanism | Context setting - no GB documentation required
0 | 0 | Whereas | 3 | The KORRR takes into account and complements where necessary the operational conditions and requirements set out in the generation and load data provision methodology (hereinafter referred to as “GLDPM”) developed in accordance with article 16 of CACM. While the GLDPM establishes which data has to be provided by whom and when to prepare the common grid model, the KORRR addresses who must exchange data as well as, how and when to perform the tasks defined in the SO GL. Furthermore, the GLDPM only refers to data exchange up to the day ahead, while KORRR also includes data exchange up to real time. | 2019-03-14 | [21 empty] | Real time data: The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) CUSC bilateral connection agreement Static data: Grid Code - Data Registration Code (various schedules) STCP 12-1 Data Exchange Mechanism | Context setting - no GB documentation required
0 | 0 | Whereas | 4 | Article 40(6) of the SO GL establishes the legal basis for the KORRR and lists the elements to be covered by the KORRR: By 6 months after entry into force of this Regulation, all TSOs shall jointly agree on key organisational requirements, roles and responsibilities in relation to data exchange. Those organisational requirements, roles and responsibilities shall take into account and complement where necessary the operational conditions of the generation and load data methodology developed in accordance with Article 16 of Regulation (EU) No 2015/1222. They shall apply to all data exchange provisions in this Title and shall include organisational requirements, roles and responsibilities for the following elements: | 2019-03-14 | [21 empty] | STCP 12-1 Data Exchange Mechanism The Grid Code, Data Registration Code, DRC Schedule 8 - Data Supplied by BM The Grid Code, Connection Codes, CC.6.5.8 Electronic Data Communication Facilities | Context setting - no GB documentation required
0 | 0 | Whereas | 4 (a) | obligations for TSOs to communicate without delay to all neighbouring TSOs any changes in the protection settings, thermal limits and technical capacities at the interconnectors between their control areas; | 2019-03-14 | [21 empty] | SO Obligation; NGET is sole System Operator for GB. No shared control area with other TSOs. | Context setting - no GB documentation required
0 | 0 | Whereas | 4 (b) | obligations for DSOs directly connected to the transmission system to inform their TSOs, within the agreed timescales, of any changes in the data and information pursuant to this Title; | 2019-03-14 | [21 empty] | CUSC Obligations, Grid Code PCA.1.2b | Context setting - no GB documentation required
0 | 0 | Whereas | 4 (c ) | obligations for the adjacent DSOs and/or between the downstream DSO and upstream DSO to inform each other within agreed timescales of any change in the data and information established in accordance with this Title; | 2019-03-14 | [21 empty] | CUSC Obligations, Grid Code PC | Context setting - no GB documentation required
0 | 0 | Whereas | 4 (d) | obligations for SGUs to inform their TSO or DSO, within agreed timescales, about any relevant change in the data and information established in accordance with this Title; | 2019-03-14 | [21 empty] | Grid Code PCA.1.2, OC2 | Context setting - no GB documentation required
0 | 0 | Whereas | 4 ( e ) | detailed contents of the data and information established in accordance with this Title, including main principles, type of data, communication means, format and standards to be applied, timing and responsibilities; | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 4 (f) | the time stamping and frequency of delivery of the data and information to be provided by DSOs and SGUs, to be used by TSOs in the different timescales. The frequency of information exchanges for real-time data, scheduled data and update of structural data shall be defined; and | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 4 (g) | the format for the reporting of the data and information established in accordance with this Title. The organizational requirements, roles and responsibilities shall be published by ENTSO for Electricity. | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other Transmission SOs. Exchange with GB TO as per STC and with DSO/SGU as per existing GB formats | Context setting - no GB documentation required
0 | 0 | Whereas | 5 | Article 40(5) of the SO GL specifies that TSO shall determine, in coordination with DSOs and SGUs, data exchange applicability and scope based on the a) to d) categories in article 40(5) referring to specific articles in Title II of the SO GL. Applicability is therefore to be determined at national level and is subject to approval by the competent authority (National Regulatory Authority or another entity designated by the Member State). | 2019-03-14 | [21 empty] | To be determined in GB via normal governance | Context setting - no GB documentation required
0 | 0 | Whereas | 6 | Article 40(7) of the SO GL specifies the TSOs’ obligation to agree with relevant DSOs on the process for exchanging information between them, including the format of data exchanges. | 2019-03-14 | [21 empty] | As of today, TSO gets all data that is officially needed hence we are currently compliant. If that changes, TSO will need to raise a mod to change the GC to request DNOs/SGUs to provide different data which will be actioned through existing code governance | Context setting - no GB documentation required
0 | 0 | Whereas | 7 | The KORRR shall ensure the provision of data necessary to perform the security analysis in accordance with article 75 of the SO GL which specifies the obligation of TSOs to develop a methodology for coordinating operational security analysis. | 2019-03-14 | [21 empty] | Article 75 is being developed separately, no changes to existing observability areas are expected. | Context setting - no GB documentation required
0 | 0 | Whereas | 8 | Article 40(10) of the SO GL entitles DSOs with a connection point to a transmission system to receive relevant structural, scheduled and real-time information from relevant TSOs and to gather relevant structural, scheduled and real-time information from neighbouring DSOs. It also specifies the obligation of neighbouring DSOs to determine in a coordinated manner the scope of information exchanged between them and with the relevant TSO. | 2019-03-14 | [21 empty] | Grid Code planning code week 42 process; PC.4.2.5, PC.4.3.2, PC.A.1.3, PC.A.8 | Context setting - no GB documentation required
0 | 0 | Whereas | 9 | Article 6(6) of the SO GL requires a proposed implementation time scale and a description of the expected impact of the KORRR on the objectives of the SO GL. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 10 | The KORRR further establishes a common framework for data exchange for all TSOs in the interconnected system, in line with the requirement of article 4(1) (a) of the SO GL. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 11 | With the aim of determining common operational planning principles as required in article 4(1) (b) of the SO GL, the KORRR allows for the receipt of data required to prepare scenarios to perform operational security analysis in the planning stage. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 12 | The KORRR includes the organisation to exchange, among other, real time data, and the provision of services to determine common load-frequency control processes and control structures as required in article 4(1) (c) of the SO GL. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 13 | To ensure the conditions for maintaining operational security throughout the Union as specified in article 4(1) (d) of the SO GL, TSOs need to have good observability of the system in order to perform reliable security analysis. The KORRR aims to set the framework for the TSOs to access necessary data for their respective observability area and prepare accurate scenarios. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 14 | Data exchanges on capabilities and active power production are necessary for TSOs to follow processes to maintain a frequency quality level for all synchronous areas throughout the Union as defined in article 4(1) (e) of the SO GL. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 15 | The KORRR takes into account the exchange of structural and scheduled data between TSOs and DSOs to perform security analysis before and in real time to promote the coordination of system operation and operational planning as defined in article 4(1) (f) of the SO GL. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 16 | Article 4(1) (g) of the SO GL aims at ensuring and enhancing the transparency and reliability of information about transmission system operation. The KORRR establishes the framework to regulate necessary information among different parties in the electric system to ensure operational security. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 | 0 | Whereas | 17 | The KORRR will contribute to the efficient operation and development of the electricity transmission system and the electricity sector in the Union while having good observability of the system to perform reliable security analysis which help to identify improvements in the transmission system. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
0 |  | Whereas | 18 | The KORRR contributes to the general objectives of the SO GL to the benefit of all TSOs, DSOs, SGUs, consumers, market participants, the Agency and regulatory authorities. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
1 | 0 |  |  | General Provisions | 2019-03-14 | [21 empty] | Context setting - no GB documentation required
1 | 0 | 1 |  | Subject matter and scope | 2019-03-14 | [21 empty] | Context setting - no GB documentation required
| 0 | 1 | 1 | The KORRR as defined in the present document shall be considered the common proposal of all TSOs in accordance with article 40(6) of the SO GL and shall include organisational requirements, roles and responsibilities for data exchange according to Title II of this regulation. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
1 | 0 | 1 | 2 | The KORRR shall apply to all transmission systems, distribution systems and interconnections in the Union, in the area referred to in article 2(2) of the SO GL. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
1 | 0 | 1 | 3 | The KORRR shall apply to SGUs as referred to in Article 2(1) of the SO GL. SGUs that provide services to the system individually or through an aggregator shall comply with prequalification rules defined at a national level. The roles and responsibilities of an aggregator shall be defined in the respective service provision agreements in observance of national prequalification rules. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
1 | 0 | 1 | 4 | The KORRR shall apply to: | 2019-03-14
1 | 0 | 1 | 4 (a) | CDSOs in their roles as relevant system operators. For the purposes of KORRR, CDSOs shall be considered as DSOs, as stated in article 3 (1) of the Commission Regulation (EC) 1388/2016 establishing a Network Code on Demand Connection (hereinafter referred to as “NC DCC”), and the requirements and responsibilities described shall apply accordingly. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | Context setting - no GB documentation required
1 | 0 | 1 | 4 (b) | Transmission-connected CDSOs in their roles as SGUs in accordance with article 2(1) of the SO GL and, if determined at a national level within the applicability and scope of data exchanges subject to KORRR. | 2019-03-14 | [21 empty] | Context setting - no GB documentation required | CDSOs, IDNOs and DNOs all treated equally in the GB D Code.
1 | 0 | 1 | 5 | When applying the KORRR, system operators shall: | 2019-03-14
1 | 0 | 1 | 5 (a) | apply the principles of proportionality and non-discrimination; | 2019-03-14 | [21 empty] | General GB code governance | LC21.4
1 | 0 | 1 | 5 (b) | ensure transparency; | 2019-03-14 | [21 empty] | General GB code governance | LC21
1 | 0 | 1 | 5 (c ) | apply the principle of optimisation between the highest overall efficiency and lowest total costs for all parties involved; | 2019-03-14 | [21 empty] | General GB code governance | LC21.4
1 | 0 | 1 | 5 (d) | respect the responsibility assigned to the relevant TSO to ensure system security, as required by national legislation; | 2019-03-14 | [21 empty] | General GB code governance | LC20.1
1 | 0 | 1 | 5 (e ) | consult with relevant DSOs and take account of potential impacts on their system; and | 2019-03-14 | [21 empty] | General GB code governance | DGC4.5
1 | 0 | 1 | 5 (f) | follow take into consideration agreed European standards and technical specifications. | 2019-03-14 | [21 empty] | General GB code governance | DPC4.4
1 | 0 | 1 | 6 | TSOs from jurisdictions outside the area referred to in article 2(2) of the SO GL may adopt the KORRR on a voluntary basis, provided that | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 | 6 (a) | For them to do so is technically feasible and compatible with the requirements of SO GL; | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 | 6 (b) | They agree that they shall have the same rights and responsibilities with respect to the data exchange process as the TSOs referred to in paragraph 2, in particular, they shall accept that the KORRR applies to the relevant parties in their control area as well; | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 | 6 (c ) | They accept any other legally feasible conditions related to the voluntary nature of their participation in the data exchange process that the TSOs may set; | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 | 6 (d) | The TSOs referred to in paragraph 2 have concluded an agreement governing the terms of the voluntary participation with the TSOs referred to in this paragraph; | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 | 6 (e ) | Once TSOs participating in the data exchange process on a voluntary basis have demonstrated objective compliance with the requirements set out in (a), (b), (c) and (d), of this paragraph, the TSOs referred to in paragraph 1, after checking that the criteria in (a), (b), (c) and (d) are met, have approved an application from the TSO wishing to join the KORRR process in accordance with the procedure set out in Article 5(3) of the SO GL. | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 | 7 | The TSOs referred to in paragraph 2 shall monitor whether those TSOs participating in the data | 2019-03-14 | [21 empty] | Not relevant | Not relevant
1 | 0 | 1 |  | exchange process on a voluntary basis pursuant to paragraph 6 respect their obligations. If a TSO | 2019-03-14
1 | 0 | 1 |  | participating in the data exchange process pursuant to paragraph 6 neglects its essential obligations | 2019-03-14
1 | 0 | 1 |  | in a way that significantly endangers the implementation and operation of the SO GL, the TSOs | 2019-03-14
1 | 0 | 1 |  | referred to in paragraph 2 shall terminate that TSO’s voluntary participation in the data exchange | 2019-03-14
1 | 0 | 1 |  | process in accordance with the procedure set out in Article 5(3) of the SO GL. | 2019-03-14
1 | 0 | 2 |  | Definitions | 2019-03-14
1 | 0 | 2 | 1 | For the purposes of the KORRR, terms used in this document shall have the meaning of the definitions included in article 3 of the SO GL , article 2 of CACM, article 2 of the EB GL, article 2 of Regulation (EC) 714/2009 on conditions for access to the network for cross-border exchanges in electricity, article 2 of Commission Regulation (EU) 543/2013 on submission and publication of data in electricity markets, article 2 of Commission Regulation (EC) 631/2016 establishing a network code on requirements for grid connection of generators (hereinafter referred to as “NC RfG”), article 2 of NC DCC, article 2 of the Commission Regulation (EC) 1447/2016 establishing a network code on requirements for grid connection of high voltage direct current systems and direct currentconnected power park modules (hereinafter referred to as “NC HVDC”), as well as article 2 of the Directive 2009/72/EC of the European Parliament and of the Council concerning common rules for the internal market in electricity and the other items of legislation referenced therein. | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 2 | The KORRR shall be binding upon all TSOs, their permitted successors and assigns- and irrespective of any change in the TSOs’ names- as well as upon any other entities covered by the SO GL including DSOs and SGUs. | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 3 | In the KORRR, unless the context requires otherwise: | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 3 (a) | The singular indicates the plural and vice versa; | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 3 (b) | The table of contents, headings and examples are inserted for convenience only and do not affect the interpretation of the KORRR; | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 3 (c ) | Any reference to legislation, regulations, directive, order, instrument, network code or any other enactment shall include any modification, extension or re-enactment of it then in force. | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 4 | A modification in a network element, power generating module or demand facility is considered significant for the purpose of the KORRR when it is also considered significant in the NC RfG, the NC DCC or the NC HVDC. In this context, national specificities in the implementation process concerning the definition of the term “significant” need to be taken into account. | 2019-03-14 | [21 empty] | Significant will be as defined for substantial modification in RfG, DCC and HVDC. | Context setting - not for direct implementation in GB documentation
1 | 0 | 2 | 5 | For the purpose of the KORRR, real time data means a representation of the actual state of the power generating modules, demand facilities or network elements when the data is measured. | 2019-03-14 | [21 empty] | Context setting - not for direct implementation in GB documentation | Context setting - not for direct implementation in GB documentation
1 | 0 | 3 |  | General responsibilities | 2019-03-14
1 | 0 | 3 | 1 | Each TSO, DSO or SGU shall be responsible for the quality of the information they provide regarding their power generating modules, demand facilities or services to other parties. | 2019-03-14 | [21 empty] | Data Registration code. Grid code sets requirements to be followed | Existing D Code obligation to provide data; DDRC5.4.1 specifies responsibility for quality; DPC1.6 envisages that data may need to be improved over time.
1 | 0 | 3 | 2 | On the basis of articles 48 to 50 and 53 of the SO GL, the KORRR renders the provision of data both to TSOs and DSOs as the default option. Pursuant to article 40 (5) of the SO GL, this approach can be revised at a national level in order to allow SGUs the provision of data only to the TSO or to the DSO to which they are connected unless otherwise required to provide services to the system. In those cases where an SGU only provides data to a TSO or to a DSO to which they are connected, the TSO and the DSO shall exchange between them the data related to that SGU according to the processes agreed according to the article 40(7) of the SO GL. | 2019-03-14 | [21 empty] | The default position in GB is that data is provided to the SO with whom there is the connection agreement. The exceptions to this are for Large Embedded parties who provide it direct to NG. This is well established practice, within the scope of the KORRR, so needs no further attention. | The default position in GB is that data is provided to the SO with whom there is the connexion agreement. The exceptions to this are for Large Embedded parties who provide it direct to NG. This is well established practice, within the scope of the KORRR, so needs no further attention.
1 | 0 | 3 | 3 | Subject to approval by the competent regulatory authority or by the entity designated by the Member State, in line with article 40 (5) of the SO GL each TSO, in coordination with the DSOs in its control area, shall define whether distribution connected SGUs in its control area shall provide the structural, scheduled and real-time data to the TSO directly or through its connecting DSO or to both. The decision for each type of information and SGU may be independent. When the data is provided directly to the TSO, after request of the DSO to whose network the SGU is connected, the TSO shall make it available to the DSO. When the data is provided to the DSO, the DSO shall provide the data to the TSO. The quality and granularity of the data shall be maintained or improved. | 2019-03-14 | [21 empty] | The default position in GB is that data is provided to the SO with whom there is the connection agreement. The exceptions to this are for Large Embedded parties who provide it direct to NG. This is well established practice, within the scope of the KORRR, so needs no further attention. | As above
1 | 0 | 3 | 4 | When the TSO or the DSO receives the data directly from the SGU, the TSO or DSO shall check that the data complies with the quality requirements specified by TSOs or when applicable by DSOs according to the KORRR before sharing it with another entity. | 2019-03-14 | [21 empty] | Requirements as defined in Grid Code schedules and DRC. | Quality requirements, if any, to be specified by NG.
1 | 0 | 3 | 5 | Adjacent DSOs and/or between the downstream DSO and upstream DSO shall inform each other on the processes and formats of any change in the data and information between them according to article 40(6) of the SO GL | 2019-03-14 | [21 empty] | DSO obligation | DOC1, DOC2 and DDRC all apply to downstream DNOs.
1 | 0 | 3 | 6 | DSOs shall be responsible for the installation, configuration, security and maintenance of communication links for data exchange with the TSO up to the communication interface point agreed with the TSO. | 2019-03-14 | [21 empty] | CC.6.5, CC.7.7 | Grid Code, not D Code requirement
1 | 0 | 3 | 7 | SGUs providing scheduled data to the TSO and SGUs providing real time data according to article 6(5) of KORRR shall be responsible for the installation, configuration, security and maintenance of the communication links to exchange data up to the communication interface point with the TSO or with the DSO when the data is provided to the DSO, unless explicitly otherwise agreed with the TSO or DSO. | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) CUSC bilateral connection agreement | DNOs generally provide the SCADA - so no need to specify this detail to Users.
1 | 0 | 3 | 8 | The TSO, or the DSO when data is directly provided to the DSO according to article 3(3) of KORRR, shall define the communication interface point for the exchange of scheduled data and real-time data with SGUs. | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) CUSC bilateral connection agreement | As above
1 | 0 | 3 | 9 | Subject to the agreement of the TSO or the DSO in case of SGUs providing directly data to a DSO, parties required to provide data under the KORRR shall be allowed to delegate all tasks or parts hereof assigned to it under the SO GL to one or more third parties, in case the third party can carry out the respective function at least as effectively as the delegating entity. The delegating entity shall remain responsible for ensuring compliance with the obligations under the SO GL, including ensuring access to information necessary for monitoring by the regulatory authority. | 2019-03-14 | [21 empty] | No requirment to replicate this in GB documentation. | Statement of the obvious. No need to replicate this in GB documentation.
1 | 0 | 4 | 0 | Confidentiality | 2019-03-14
1 | 0 | 4 | 1 | Unless otherwise explicitly stated, all data affected by the KORRR shall be confidential. In accordance with article 12 of the SO GL, each party receiving data according to the KORRR shall implement appropriate technical and organizational measures to ensure that data is not disclosed to any other person or authority, without prejudice to cases covered by national law, other provisions of the SO GL or other relevant Union legislation. | 2019-03-14 | [21 empty] | SO GL obligation in force from Mar-19 | LC31.B and UA(2000) 105
1 | 0 | 4 | 2 | Subject to the confidentiality obligations set out in article 12 of the SO GL, TSOs may share the data obtained with all other TSOs that have fully implemented the requirements set out in the KORRR. | 2019-03-14 | [21 empty] | SO GL obligation in force from Mar-19 | TSO obligation
1 | 0 | 5 |  | Access to information | 2019-03-14
1 | 0 | 5 | 1 | Each power generating module, demand facility or CDSO considered as a SGU according to article 2(1) of the SO GL shall have access to the structural information referring to its facilities stored by the TSO or DSO. | 2019-03-14 | [21 empty] | PCA.8 | Gap in D code - a new para in DPC8 has been drafted to discharge this.
1 | 0 | 5 | 2 | Each DSO shall have access to the structural, scheduled and real-time information of the SGUs connected to its distribution network. | 2019-03-14 | [21 empty] | DSO obligation | Main purpose of DDRC and DPC8; DPC6.7 for real time data
1 | 0 | 5 | 3 | According to article 40(10) of the SO GL, DSOs shall have access to the structural, scheduled and real-time information of the commissioned network elements of the transmission network in their connection point. Upon justification of the need for information for operational security reasons, reliable dynamic simulations of their grids, they may request further structural or real-time information from commissioned network elements of the transmission system of the control area they are connected. When the request of information comes from a CDSO, it shall not include the connection point of other CDSOs or SGUs. TSOs may give positive or justified negative answers to such requests. | 2019-03-14 | [21 empty] | Grid Code planning code PC.4.2.5, PC.4.3.2, PCA.1.3, PC.A.1.4, PC.A.8 | TSO obligation
1 | 0 | 5 | 4 | SGUs shall have access to the structural, scheduled and real-time information of the commissioned facilities of the transmission system or distribution system in their connection point. It shall not include the connection point of other SGUs. | 2019-03-14 | [21 empty] | PCA.8 | As 5.1 above.
1 | 0 | 5 | 5 | Competent national regulatory authorities shall have access to all information exchanged subject to the KORRR upon request. | 2019-03-14 | [21 empty] | Ofgem already have this right in the licences | Ofgem already have this right in the licences
1 | 0 | 5 | 6 | The TSOs may share structural information of DSOs or SGU with a third party to comply with the responsibilities defined in the SO GL, subject to the formalization of confidentiality and a limitation of use agreement. | 2019-03-14 | [21 empty] | SO GL obligation in force from Mar-19 | TSO obligation
2 | 0 |  |  | Key Organisational Requirements, Roles and Responsibilities | 2019-03-14
2 | 1 | 0 | 0 | Responsibilities of TSOs | 2019-03-14
2 | 1 | 6 | 0 | General Responsibilities | 2019-03-14
2 | 1 | 6 | 1 | Each TSO shall communicate to the relevant TSOs, the elements of their transmission system identified as part of its observability area according to the methodology of article 75 of the SO GL. | 2019-03-14 | [21 empty] | No requirement to share with neigbouring EU TSOs. For GB this is covered in STCP22-1 | TSO obligation
2 | 1 | 6 | 2 | Each TSO shall communicate to the relevant DSOs of its control area, the elements of their distribution network identified as part of its observability area according to the methodology of article 75 of the SO GL. | 2019-03-14 | [21 empty] | Grid Code planning code week 42 process; PC.4.2.5, PC.4.3.2, PC1.3 | TSO obligation
2 | 1 | 6 | 3 | Each TSO shall provide updated information of the network elements in its transmission system that is part of the observability area of other TSO to those TSOs in accordance with article 41 and 42 (2) of the SO GL. | 2019-03-14 | [21 empty] | No requirement to share with neigbouring EU TSOs. STCP22-1, STCP12-1 , CC.6.5.6 , PCA3.2.2.f(i) | TSO obligation
2 | 1 | 6 | 4 | Each TSO shall exchange real-time data with the other TSOs of the same synchronous area in accordance with article 42 (1) of the SOGL. | 2019-03-14 | [21 empty] | No requirement for GB SO to share with neigbouring EU TSOs. | TSO obligation
2 | 1 | 6 | 5 | Subject to approval of the competent regulatory authority or approval of the entity designated by the Member State in accordance with article 40 (5) of SO GL, each TSO, in coordination with the DSOs and SGUs, shall define the SGUs in its control area which shall provide real time data. | 2019-03-14 | [21 empty] | No proposed changes to Real time data exchange. Maintain GC and CUSC bilateral connection agreement | TSO obligation
2 | 1 | 6 | 6 | Each TSO shall provide updated information of DSO network of its control area that is part of the observability area of other TSO to those TSOs. | 2019-03-14 | [21 empty] | Currently not applicable in GB as obserbaility areas are not shared with neighbouring countries. | TSO obligation
2 | 1 | 6 | 7 | Each TSO may provide updated information of the neighbouring TSO networks which have an impact on the distribution networks of its own control area to the DSOs operating those distribution networks. | 2019-03-14 | [21 empty] | Currently not applicable in GB as obserbaility areas are not shared with neighbouring countries. | TSO obligation
2 | 1 | 6 | 8 | All transmission and distribution data to be exchanged between TSO control areas shall be exchanged only through TSOs unless otherwise required by national legislation or specific agreements. | 2019-03-14 | [21 empty] | Currently not applicable in GB as obserbaility areas are not shared with neighbouring countries. | TSO obligation
2 | 1 | 6 | 9 | TSOs shall use the operational planning data environment platform for the exchange of structural and scheduled information with other TSOs for data required in accordance with articles 114, 115, 116 and 117 of the SO GL. All TSOs shall use the harmonized data format for data exchange among them in accordance with article 114 (2) of the SO GL. | 2019-03-14 | [21 empty] | TSO to TSO format already in use as per Operational Planning Data Environmen (OPDE) | TSO obligation
2 | 1 | 6 | 10 | Each TSO shall electronically store the information needed for its processes for the duration defined by national legislation. | 2019-03-14 | [21 empty] | National rules to store data for 7 years are in place. | TSO obligation
2 | 1 | 7 |  | Structural data used by TSOs | 2019-03-14
2 | 1 | 7 | 1 | In agreement with relevant DSOs, each TSO shall specify the format and may publish templates for the structural data that DSOs shall provide. The format or template has to include the detailed content of the structural data that have to be provided | 2019-03-14 | [21 empty] | No requirements to exchange data with other Transmission SO's. Exchange with GB TO's is through ETYS. Data exchange with DNOs as per PC.A.2.1 to PC.A.2.5, DRC Schedule 5 | TSO obligation
2 | 1 | 7 | 2 | Each TSO shall specify the format and may publish templates for the structural data that transmission connected SGUs and distribution connected SGUs that exchanges data directly with the TSO shall provide. The format or template has to include the detailed content of the structural data that have to be provided. | 2019-03-14 | [21 empty] | No requirements to exchange data with other Transmission SO's. Exchange with GB TO's is through ETYS. Grid Code - DRC Schedules 1,13, 18 | TSO obligation
2 | 1 | 8 | 0 | Notification of changes | 2019-03-14
2 | 1 | 8 | 1 | Each TSO shall review the structural information it shares with other TSOs at least every 6 months and provide updated information of the observability area to the neighbouring TSO in the following situations: | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. | TSO obligation
2 | 1 | 8 | 1 (a) | At least 6 months before the planned commissioning of a new network element, power generating module or demand facility; | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. | TSO obligation
2 | 1 | 8 | 1 (b) | At least 6 months before the planned final removal from service of the network element, power generating module or demand facility; | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. | TSO obligation
2 | 1 | 8 | 1 (c ) | At least 6 months before the planned significant modifications in the network element, power generating module or demand facility; | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. | TSO obligation
2 | 1 | 8 | 1 (d) | As soon as possible in case there is a change in the observability area; | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. | TSO obligation
2 | 1 | 8 | 1 (e ) | As soon as an error in the data set transmitted earlier is detected. | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. | TSO obligation
2 | 1 | 8 | 2 | According to articles 5(3) and 5(4), DSOs and SGUs may request an update of the structural data from its TSO. | 2019-03-14 | [21 empty] | PC.4.2.5, PC.4.3.2, PC.1.3, PC.A.8 | TSO obligation
2 | 1 | 9 | 0 | Scheduled data, Responsibilities of TSOs | 2019-03-14
2 | 1 | 9 | 1 | Each TSO shall be capable of exchanging scheduled data with TSOs and with SGUs, DSOs or third parties within its control area to whom the exchange of scheduled information may have been delegated. Scheduled data shall at least include generation and consumption schedules between two days ahead and close to real time, unavailability or limitations to active power production or consumption of SGUs and unavailability of network elements in the TSO’s observability area. | 2019-03-14 | [21 empty] | There's no requirement as GB observability is not shared with other Transmission SOs. Grid Code Operating Code OC2.3, OC2.4.1, OC2.4.2 for exchange with SGUs and DSOs | TSO obligation
2 | 1 | 9 | 2 | In agreement with DSOs within the TSOs’ control area, each TSO shall specify the format and may publish templates to exchange the scheduled data between them. | 2019-03-14 | [21 empty] | There's no requirement for TSO exchange as GB observability is not shared with other Transmission SOs. Grid Code - PC.A.4, Data Registration Code schedules 10A, 10B,10C, 11, 11C for DSO | TSO obligation
2 | 1 | 9 | 3 | In coordination with SGUs or third parties within TSOs´ control area, each TSO shall define and publish the format of the information for the exchange of scheduled data. | 2019-03-14 | [21 empty] | There's no requirement for TSO exchange as GB observability is not shared with other Transmission SOs. Grid Code BC1.A.1.1, BC1.4.2 for SGUs | TSO obligation
2 | 1 | 9 | 4 | Each TSO shall define and publish the technical requirements, including time stamping, for the exchange of scheduled data with SGUs, DSOs or third parties with in its control area. The technical requirements should where possible, be in accordance with an international standard recommended by all TSOs and with current technologies to guarantee the security, confidentiality and redundancy of the communications. | 2019-03-14 | [21 empty] | PC.A.4, DRC Schedule 10, 11 Grid Code applies to all users irrespective of transmission area they're in | TSO obligation
2 | 1 | 9 | 5 | Each TSO shall communicate to the DSOs connected to the transmission system their planned and unplanned unavailability of network elements in their connection point. For planned unavailability, they shall agree on the necessary level of coordination and communication between them. For unplanned unavailability, the TSO shall communicate to them as soon as possible. | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. Exchange with DSOs are covered in OC2.4 | TSO obligation
2 | 1 | 10 | 0 | Format of Real Time Information | 2019-03-14
2 | 1 | 10 | 1 | Each TSO, in agreement with the DSOs in its control area, shall specify the detailed content of and publish the format for real-time data exchange between them related to the distribution network observability area within its control area. | 2019-03-14 | [21 empty] | There is no requirement to share real time data with neighbouring EU TSOs. Currently in GB real time data is obtained from NG’s own systems, so NG does not have to specify any real time data exchange requirements with SGUs until future mods are raised based on system requirements. | TSO obligation
2 | 1 | 10 | 2 | Each TSO, in coordination with SGUs and DSOs, shall specify the detailed content of and publish the format for real time data exchange related to SGUs within its control area. | 2019-03-14 | [21 empty] | There is no requirement to share real time data with neighbouring EU TSOs. Currently in GB real time data is obtained from NG’s own systems, so NG does not have to specify any real time data exchange requirements with SGUs until future mods are raised based on system requirements. | TSO obligation
2 | 1 | 10 | 3 | Each TSO shall specify the technical requirements, including time stamping, for real time data exchange related to the distribution network observability area and to the SGUs with in its control area. The technical requirements should where possible, be in accordance with an international standard recommended by all TSOs and with current technologies to guarantee security, confidentiality and redundancy of the communications. | 2019-03-14 | [21 empty] | The GB SO is responsible for following the all TSO practices for data exchange with other Transmission System Operators in the EU. There's no requirement to exchange the data with other Transmission Sos in EU. | TSO obligation
2 | 1 | 10 | 4 | Each TSO, when exchanging real time information with other TSOs, shall follow and fulfil all the rules and obligations according to the current all TSOs practices in terms of: | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 4 (a) | Logical connections between parties and protocols used; | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 4 (b) | Network architecture including redundancy; | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 4 (c ) | Network security rules; | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 4 (d) | Identification code (ID) and/or naming convention and data quality; | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 4 (e ) | Data transmission parameters and performance; | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 4 (f) | Rules of conduct in the case of planned outages and disturbances of communication equipment. | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 1 | 10 | 5 | Each TSO shall define the refresh rate for the real-time data exchanges in its control area. It shall not be longer than 1 minute. | 2019-03-14 | [21 empty] | There's no requirement for GB to exchange this data with other TSOs. | TSO obligation
2 | 2 | 0 | 0 | Responsibilities of DSOs | 2019-03-14
2 | 2 | 11 | 1 | Each DSO shall review the structural information of network elements in the observability area and power generating modules and demand facilities in the control area it shares with the TSOs at least every 6 months and, in agreement with the TSO, provide updated information to the TSO in the following situations: | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code PC.A.1.2 and DRC Schedule 5 - notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. | G Code requirement to implement SOGL requirement for six monthly structural data.
2 | 2 | 11 | 1 (a) | At least 6 months before the planned commissioning of a new network element, power generating module or demand facility. | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. Maintain same data as existing week 24 schedule requirements. | For Generation the SoW process picks this up. For generation and demand DNOs already have the necessary details from DNO system users - to be forwarded to NG in line with G Code requirements.
2 | 2 | 11 | 1 (b) | At least 6 months before the planned final removal from service of the network element, power generating module or demand facility. | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. Maintain same data as existing week 24 schedule requirements. | To be passed on to NG as soon as a DNO is aware
2 | 2 | 11 | 1 (c ) | At least 6 months before the planned significant modifications in the network element, power generating module or demand facility. | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. Maintain same data as existing week 24 schedule requirements. | For Generation the SoW procoess picks this up. For generation and demand DNOs already have the necessary details from DNO system users - to be forwarded to NG in line with G Code requirements.
2 | 2 | 11 | 1 (d) | As soon as possible in case there is a change in the Observability Area; | 2019-03-14 | [21 empty] | Existing Grid Code practice PC.A.2.1.4, PC.A.6. TSO in agreement with DSOs can propose changes to the observability areas at any time. Any change to observability areas in accordance with Article 75 will go through existing code governance process | No D Code wording needed - to be done upon NG's notification of Observability Area change
2 | 2 | 11 | 1 (e ) | As soon as an error in the data set transmitted earlier is detected. | 2019-03-14 | [21 empty] | Existing Grid Code practice PC.A.1.2 | DDRC 5.3 and 5.4
2 | 2 | 11 | 2 | Each DSO, in coordination with its TSO, shall specify the format and may publish templates for the structural data that distribution connected SGUs that exchanges directly data with the DSO shall provide. The format or template has to include the detailed content of the structural data to be provided. | 2019-03-14 | [21 empty] | Grid Code - Data Registration Code Schedule 5 Demand response providers submitted through DRSC which links back to ancillary services agreement and standard contract terms | DDRC Schedule 5
2 | 2 | 11 | 3 | According to article 5(4), SGUs connected at the distribution level may request the update of the structural data from its DSO. | 2019-03-14 | [21 empty] | DSO obligation | As per Art 5(4)
2 | 2 | 12 | 0 | Scheduled data, Rights and responsibilities of DSOs | 2019-03-14
2 | 2 | 12 | 1 | All DSOs within the observability area of the relevant TSO shall provide their planned unavailability of network elements to the TSO, at least in D-2 and D-1 and their unplanned unavailability as soon as possible. For planned unavailability, they shall agree on the necessary level of coordination and communication between them. Transmission connected DSOs shall provide data directly to the TSO. Non-transmission connected DSOs may provide data directly to the TSO or through its connecting DSO or to both, as defined in article 3(3). The frequency of delivery of scheduled data shall be defined at a national level. | 2019-03-14 | [21 empty] | Grid Code OC2.4.1.2.4 Only those elements with significant influence on the transmission system are to be included. D-2 and D-1 time requirements are in line with Capacity Allocation Congestion Management Regulation. | Grid Code obligation. If there are IDNOs in the observability area, existing DOC provisions should be sufficient.
2 | 2 | 12 | 2 | Each DSO shall have access to the scheduled data of SGUs connected to its network. DSOs shall comply with the requirements defined by the relevant TSO to exchange scheduled data | 2019-03-14 | [21 empty] | DSO obligation | DOC2
2 | 2 | 13 | 0 | Real Time Data provided by DSOs | 2019-03-14 | [21 empty] | CC.6.5.6,
2 | 2 | 13 | 1 | Each DSO shall provide to its TSO real time data from the observability area defined by the TSO according to article 44 of SO GL. | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6, Operational Metering Currently in GB real time data is obtained from NG’s own systems and there is no proposal to change the existing practice. NG does not have to specify real time data exchange requirements until future mods are raised. | For NG to specify - assumed that most data from FMS will be sufficient.
2 | 2 | 13 | 2 | Each DSO shall fulfil the requirements defined by the TSO in terms of: | 2019-03-14
2 | 2 | 13 | 2 (a) | Logical connections between parties and protocols used; | 2019-03-14 | [21 empty] | Grid Code CC6.5.6 SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET is not requesting new real time connections as part of GC0106. Future modification may be raised when system needs change. | As 13.1
2 | 2 | 13 | 2 (b) | Network Architecture including redundancy; | 2019-03-14 | [21 empty] | Grid Code CC6.5.6 SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET is not requesting new real time connections as part of GC0106. Future modification may be raised when system needs change. | As 13.1
2 | 2 | 13 | 2 (c ) | Network security rules; | 2019-03-14 | [21 empty] | Grid Code CC6.5.6 SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET is not requesting new real time connections as part of GC0106. Future modification may be raised when system needs change. | As 13.1
2 | 2 | 13 | 2 (d) | Identification code (ID) and/or naming convention and data quality; | 2019-03-14 | [21 empty] | Grid Code CC6.5.6 SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET is not requesting new real time connections as part of GC0106. Future modification may be raised when system needs change. | As 13.1
2 | 2 | 13 | 2 (e ) | Data transmission parameters and performance; | 2019-03-14 | [21 empty] | Grid Code CC6.5.6 SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET is not requesting new real time connections as part of GC0106. Future modification may be raised when system needs change. | As 13.1
2 | 2 | 13 | 2 (f) | Rules of conduct in the case of planned outages and disturbances of communication equipment. | 2019-03-14 | [21 empty] | Grid Code CC6.5.6 SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET is not requesting new real time connections as part of GC0106. Future modification may be raised when system needs change. | As 13.1
2 | 2 | 13 | 3 | Each DSO, in coordination with its TSO and SGUs, shall specify the detailed content of and the requirements for real-time data exchange related to distribution connected SGUs that exchanges data directly with the DSO. The technical requirements should where possible, be in accordance with an international standard recommended by all TSOs and with current technologies to guarantee security, confidentiality and redundancy of the communications. Each DSO shall provide the templates and formats to the SGUs for real time data exchange. | 2019-03-14 | [21 empty] | Grid Code CC6.5.6. SOGL flexibility allows for TSO to determine real time data exchange scope and applicability. NGET has already specified data exchange requirements for relevant embedded generators in CC6.5.6. Future modification may be raised when system needs change | Generally real time data is sourced from the DNO's own SCADA
2 | 3 | 0 | 0 | Responsibilities of SGUs | 2019-03-14
2 | 3 | 14 | 0 | Structural Data provided by SGUs | 2019-03-14
2 | 3 | 14 | 1 | Each SGU connected to the transmission system shall provide to its TSO the structural data according to articles 45 and 52(1) of SO GL in the format specified by its TSO. | 2019-03-14 | [21 empty] | Grid Code - Planning Code, PC.A.2, PC.A.3.2.2(a), PC.A.5.4.3 , PC.A.6.1.3, PC.A.7 Data Registration Code DRC.6.1.2, DRC.6.1.13, DRC.6.2, DRC Schedule 1 CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , BSC Section 4 | G Code
2 | 3 | 14 | 2 | Each SGU connected to the distribution system shall provide directly to the TSO or through its connecting DSO or to both, as defined in article 3(3), the structural data according to articles 48 and 53 of the SO GL in the format specified by its TSO or DSO. | 2019-03-14 | [21 empty] | Grid Code - Planning Code PC.4, DRC Schedule 5 | DDRC Schedule 5
2 | 3 | 15 |  | Notification of changes | 2019-03-14
2 | 3 | 15 | 1 | Each SGU shall review the structural information it shares with the DSOs or TSOs of the control area of SGU belongs to, at least every 6 months and provide updated information to the TSO and DSO in the following situations: | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. | DDRC5.3 requires this continuously -which is better than every six months. No change proposed.
2 | 3 | 15 | 1 (a) | At least 6 months, before the planned commissioning of a new network element, power generating module or demand facility. | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. | DDRC 5.3 expects this data to be submitted as soon as it is known - not six months in advance
2 | 3 | 15 | 1 (b) | At least 6 months before the planned final removal from service of the network element, power generating module or demand facility. | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. | DDRC 5.3 expects this data to be submitted as soon as it is known - not six months in advance
2 | 3 | 15 | 1 (c ) | At least 6 months before the planned significant modifications in the network element, power generating module or demand facility. | 2019-03-14 | [21 empty] | Currently 12 months in GC Planning Code notifications are sent well before 6 months, GC0106 proposes to have a 6month update in week 50 for any substantial changes following week 24 submission. Network elements and SGU data will be updated through this process for structural information in TSOs observability area. | DDRC 5.3 expects this data to be submitted as soon as it is known - not six months in advance
2 | 3 | 15 | 1 (d) | As soon as an error in the data set transmitted earlier is detected. | 2019-03-14 | [21 empty] | Existing Grid Code practice | DDRC 5.3
2 | 3 | 15 | 1 (e ) | In case of an unforeseeable modification within the period of 6 months before the date of entry into force of the new situation described in points a, b and c, the SGU shall inform the TSO without delay. | 2019-03-14 | [21 empty] | Existing Grid Code practice | DDCR 5.3
2 | 3 | 16 | 0 | Scheduled Data provided by SGUs | 2019-03-14
2 | 3 | 16 | 1 | All SGUs within the control area of the TSO shall provide scheduled data to the TSO. Transmission connected SGUs shall provide data directly to the TSO. Distribution connected SGUs shall provide data directly to the TSO or through its connecting DSO or to both, as defined in article 3(3). | 2019-03-14 | [21 empty] | Grid Code BC1.A.1.1, OC.1,2 and DRC shedule 5 | DDRC shedule 5
2 | 3 | 16 | 2 | SGUs shall comply with the requirements defined by the relevant TSO or by the DSO when the data is exchanged trough the DSO, to exchange scheduled data. The frequency of delivery of scheduled data shall be defined at a national level. | 2019-03-14 | [21 empty] | Grid Code BC1.A.1.1, OC.1,2 and DRC shedule 5
2 | 3 | 17 | 0 | Real Time Data provided by SGUs | 2019-03-14
2 | 3 | 17 | 1 | Subject to article 6(5) of KORRR, all concerned SGUs connected to the transmission system shall provide the real-time data directly to the TSO. Subject to article 6(5) of KORRR, all concerned distribution connected SGUs shall provide the real-time data to the TSO directly or through its connecting DSO or to both, as defined in article 3(3). All SGUs which are power generating modules not subject to the NC RfG, or which are HVDC systems not subject to the NC HVDC, or which are demand facilities not subject to the NC DCC, shall inform to the TSO about their technical capabilities for real time data provision. The evaluation process to exempt particular SGUs, in case of non-compliance with the requirement to provide real time data, shall be defined at national level. | 2019-03-14 | [21 empty] | TSO not proposing changes to existing real time data provided by SGUs. Maintain flexibility and existing rules for real time data according CUSC agreements: Data provision from large and medium power stations excluding small. The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | Existing GB arrangements to apply - ie real time data from DNO connected customers is provided by the DNO from the DNO's own telemetry
2 | 3 | 17 | 2 | Each SGU providing data directly to the TSO or the DSO when the data is directly provided to the DSO shall fulfil the requirements defined by the TSO in terms of: | 2019-03-14 | [22 empty] | NG to specify
2 | 3 | 17 | 2 (a) | Logical connections between parties and protocols used; | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | NG to specify
2 | 3 | 17 | 2 (b) | Network architecture including redundancy; | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | NG to specify
2 | 3 | 17 | 2 (c ) | Network security rules; | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | NG to specify
2 | 3 | 17 | 2 (d) | Identification code (ID) and/or naming convention and data quality; | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | NG to specify
2 | 3 | 17 | 2 (e ) | Data transmission parameters and performance; | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | NG to specify
2 | 3 | 17 | 2 (f) | Rules of conduct in the case of planned outages and disturbances of communication equipment. | 2019-03-14 | [21 empty] | The Grid Code, Connection Conditions, CC.6.5.6 (Operational metering) / Bilateral agreement The Grid Code, Connection Conditions, CC6.4.4 (Operational metering) / Bilateral agreement for LEEMPS | NG to specify
3 | 0 | 0 | 0 | Final provisions | 2019-03-14
3 | 0 | 18 | 0 | Implementation date of the KORRR | 2019-03-14
3 | 0 | 18 | 1 | Upon approval of the KORRR each TSO shall publish it on the internet in accordance with article 8(1) of the SO GL. | 2019-03-14 | [21 empty] | NGET to comply with SO GL | NG responsibility
3 | 0 | 18 | 2 | By 18 months after entry into force of the SO GL, and in accordance with article 192 of the SO GL, TSOs shall apply the KORRR as described in Title 2 as soon as all regulatory authorities have approved the KORRR or a decision has been taken by the Agency in accordance with article 6(8) and 7(3) of the SO GL. | 2019-03-14 | [21 empty] | NGET to comply with SO GL | Context setting, but sets a compliance date too.
3 | 0 | 19 | 0 | Language | 2019-03-14
3 | 0 | 19 | 0 | The reference language for the KORRR shall be English. For the avoidance of doubt, where TSOs need to translate the KORRR into their national language(s), in the event of inconsistencies between the English version published by TSOs in accordance with article 8 (1) of the SO GL and any version in another language, the relevant TSOs shall, in accordance with national legislation, provide the relevant national regulatory authorities with an updated translation of the KORRR. | 2019-03-14 | [21 empty] | N/A