## Document Control
Project | Power Potential
DER customer
Content | DER_Interface_ScheduleV2.3.2
File Description | DER Interface Schedule spreadsheet (updated). The file provides further explanation of the signals between the UKPN RTU and DER controller, including an additional tab with further information on how to set up the DNP3 Protocol configuration for each signal. There is a reduction in the overall number of signals, including some new optional and mandatory signals. (The DER Technical Requirements and DER Test Specification will be updated accordingly).
Note on aggregator solution | This file describes the signal schedule for direct interface between an RTU and DER controller. Similar signals would be required to be sent between an aggregator and a DER controller, but this file is not a schedule for an aggregator interface. An IT assessment is currently being conducted to determine a specification for a potential future aggregator interface, in consultation with potential aggregator customers.
Version | Date | Author | Approved by | Description
2.2 | 2019-01-04 | Dr Sima Davarzani | Tim Manandhar / Rita Shaw | Standard DER interface schedule Version 2.2
2.2.2 | 2019-01-11 | Dr Sima Davarzani | Dr Rita Shaw | No change to signals relative to v2.2. Includes description in the file (cell B11 above), and note on aggregator solution (cell B14 above).
2.2.3 | 2019-01-24 | Dr Sima Davarzani | Dr Rita Shaw | - The mandatory "Failsafe2" signal has been broken down to two separate mandatory failsafe signals: "Failsafe2" and "Failsafe3". - Two Mandatory signals including "Measured Customer PF" (for DER operating under PF mode as default) and "Customer mode of operation" have been added. - One optional signal "Readback Failsafe3" has been added. - "Measured active power @POC" and "Measured reactive power @POC" have been replaced by "Measured Customer active power" and "Measured Customer reactive power".
2.2.4 | 2019-01-28 | Dr Sima Davarzani | Dr Rita Shaw | Typographical changes - refer to Power Potential in capital letters, and refer to "Power Potential DER Framework Agreement" and "Variation Agreement relating to a Connection Agreement". Minor clarification to text describing signals 28, 29 and 30. Update file description.
2.2.5 | 2019-01-31 | Dr Sima Davarzani | Dr Rita Shaw | - 6 digital breach signals including "Active power, reactive Power and Power factor upper and lower limits breach) have been removed. ' One column ("note") has been added to explain the signals which are not needed for DER operating in "V mode" as default. - Two column ("min range" and "max range") in the "DNP3 Protocol configuration" tab have been modified. - One column ("Source") has been added in the "DNP3 Protocol configuration" tab.
2.2.6 | 2019-03-19 | Dr Sima Davarzani | Dr Rita Shaw | -ALL digital limit enable signals ("P, Q and V upper/lower limit enable") are combined in one single integer as "DER mode of operation command". - All digital "failsafe action 1-4" signals are combined in one single integer as "Failsafe Action" (this applies for both the command from UKPN RTU to DER and the readback from DER to UKPN RTU). -All digital "V upper and lower limit Breach" signals are combined in one single integer as "Limit Breach". - One integer signal "readback DER mode of operation command" is added. _A column "Format" is added to indicated the format of data. -One tab "additional information" is added to explain the new integer signals. -IP address and the subnet mask are specified in "additional Information" tab.
2.2.7 | 2019-03-21 |  | Dr Rita Shaw | Typographical changes - and clarify that Failsafe 3 applies to all DER and is not related to active power service.
2.2.8 | 2019-06-12 | Dr Sima Davarzani |  | - Typographical changes - The "DER current mode of operation" has been renamed to "DER services" and also it has also changed from digital to integer. - All analogue floats have been changed to integer. - Description of signals are updated. - The single integer signal "DER mode of operation command" has changed to digital signals as "P service enable", "V service enable", "contractual mode enable" and "disable mode enable". - The single integer signal "readback DER mode of operation command" changed to 4 optional digital signals as "readback P service enable", "readback V service enable", "readback contractual mode enable" and "readback disable mode enable". - The index for all points are updated in the “DNP3 protocol configuration” tab. - A new column called "scaling" and a column with some example of scaling called "Example Raw DNP3 Value / Scaled Value" are added in the “DNP3 protocol configuration” tab. - In the “DNP3 protocol configuration” tab, DNP object number and variation number for digital command and readback has been corrected and updated. - "Additional information" tab updated based on the changes in signals. An example of data exchange and handshaking are also provided. - A separate tab is produced to include TCP-IP configuration required. - A separate tab is produced to include scaling calculation for converting integer to float at DER side.
2.2.9 | 2019-06-21 | Dr Sima Davarzani |  | - In the “DNP3 protocol configuration” tab, DNP object number for digital command have been changed from 10 to 12. - In the “DNP3 protocol configuration” tab, the bits description in columns "unit/value" and "note" for all integers have been updated. - In the “DNP3 protocol configuration” tab, the scaling for DER measurements and analogue readback have been updated.
2.2.10 | 2019-07-02 | Dr Sima Davarzani |  | - In the "DNP3 Configuration tab", the integer signal "DER services" description has been change as: Bit 0 : P Mode Bit 1 : Q mode Bit 2 : V mode Bit 3 : PF mode Accordingly, the picture in the "additional Information" tab has been updated.
2.2.11 | 2019-07-19 | Dr Sima Davarzani |  | -In the "DNP3 Protocol Configuration" tab, the analogue readback signals have been added to Obj 30,V2. - The Control version has been added to all pages in the spreadsheet.
2.2.12 | 2019-08-13 | Dr Sima Davarzani |  | - In the "DNP3 Protocol Configuration" tab: • In column "Note" at DER services signal, “V service =2” changed to “V service =4” (Typo). • The analogue readback signals categorised as obj 40 are removed as these signals are now mapped as Obj 30. - In "Additional Information tab": figures are updated for highlighting the difference between “Disable service” and “contractual mode enable”, and also for typo (V service =4).
2.2.13 | 2019-12-10 | Dr Sima Davarzani | Dr Rita Shaw | - In the "DNP3 Protocol Configuration" tab: • The data type for setpoints and limit changes from integer to float as: - Obj 30, V2 changes to Obj 30, V5 - Obj 41, V2 changes to Obj 41, V3 • Column L (Scaling) has been removed due to changes from integer to float data type - In the "Data Exchange" tab: • All analogue setpoints/limits/measurements and readbacks updated to float. • Decouple Alarm has changed to Digital rather than analogue (Typo). - In the "Additional tab": • The sequence diagram have been updated. - The tab "Analogue Scaling" has been removed.
2.3 | 2019-12-24 | Dr Sima Davarzani |  | - In the "DNP3 Protocol Configuration" tab: • Column Q (Example Raw DER DNP3 Value / Scaled Value) has been removed due to changes from integer to float data type. • The "data table" has been rearranged to better reflect and clarify the different data types based on the DNP3 group and Variation. - In the "Additional information" tab, clarify that Failsafe 3 is not being implemented as part of the Power Potential trial, but is included here should it be required in future. - Typographical changes
2.3.1 | 2019-03-19 | Dr Sima Davarzani |  | -The "DER Services" data format has changed from "Integer" to "Float" data type. -The "DER Services" DNP3 variation has changed from variation "2" to variation "5". - All the units are changed from MW, MVAr and kV to kW, kVAr and V. - DER services definition is updated to reflect that this is a mirror and readback of P or V service enable signals. All the changes have been reflected in "Data Exchange" , "DNP3 Protocol Configuration" and "Additional Information" tabs.
2.3.2 | 2020-06-09 | Dr Sima Davarzani |  | - In the "Data Exchange" tab : • The following data points are now defined as Mandatory signals: -Reactive Power Upper Limit - Reactive Power Lower Limit - DER Link Counter - Readback Active Power Upper Limit - Readback Active Power Lower Limit - Readback Voltage Upper Limit - Readback Voltage Lower Limit - Readback Reactive Power Upper Limit - Readback Reactive Power Lower Limit - Readback Active power setpoint - Readback Voltage setpoint • A footnote is added to clarify that the following signals are only required if DER is providing Active Power service: - Setpoint Active Power - Readback Setpoint Active Power - P service Enable - In the "DNP3 Protocol Configuration" tab: • A note is added at Colum M For DER link counter to clarify that the Default value being issued to DER is 60 (means 60seconds)

## Data Exchange
| Protocol |  |  | DNP3 over TCP/IP
UKPN RTU
| DER Control system (PPC) |  |  | 2
Ramp up rate
Ramp down rate
No | Alias - Data Points between UKPN RTU and DER control system | Points Group or Location in Logic | Generic Description | Type | Format | Required | Source | Destination | Function | Note
1 | Active Power Upper Limit | Effective Operating Limits | Limit input to Comparator 1 | Analogue | Float | Mandatory | UKPN RTU | DER Control System | Maximum kW limit; To control output active power of the DER to maintain within the appropriate statutory limit. The DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode) and keep the exported active power output to the level equal to or lower than this level.
2 | Active Power Lower Limit |  |  | Analogue | Float | Mandatory | UKPN RTU | DER Control System | Minimum kW limit; To control output active power of the DER to maintain within the appropriate statutory limit. The DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode) and keep the exported active power output to the level equal to or upper than this level.
3 | Reactive Power Upper Limit |  |  | Analogue | Float | Mandatory | UKPN RTU | DER Control System | Maximum kVAr limit; To control output reactive power of the DER to maintain within the appropriate statutory limit. The DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode) and keep the exported reactive power output to the level equal to or lower than this level.
4 | Reactive Power Lower Limit |  |  | Analogue | Float | Mandatory | UKPN RTU | DER Control System | Minimum kVAr limit; To control output reactive power of the DER to maintain within the appropriate statutory limit. The DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode) and keep the exported reactive power output to the level equal to or upper than this level.
5 | Voltage Upper Limit |  |  | Analogue | Float | Mandatory | UKPN RTU | DER Control System | Maximum Voltage limit; To control output voltage of the DER to maintain within the appropriate statutory limit. This is an important signal which is used by UKPN to actively manage the voltage level at DER site. The DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode)
6 | Voltage Lower Limit |  |  | Analogue | Float | Mandatory | UKPN RTU | DER Control System | Minimum Voltage limit; To control output voltage of the DER to maintain within the appropriate statutory limit. This is an important signal which is used by UKPN to actively manage the voltage level at DER site. The DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode) and maintain the voltage at the level equal or upper than this level.
7 | Power Factor Upper limit (Lagging) |  |  | Analogue | Float | Optional, used based on specific scheme requirement | UKPN RTU | DER Control System | Power factor upper limit which the DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode).This refers to lagging power factor. | This is not required for DERs operating in the V mode as default
8 | Power Factor lower limit (Leading) |  |  | Analogue | Float | Optional, used based on specific scheme requirement | UKPN RTU | DER Control System | Power factor lower limit which the DER Control system must comply with the limits received from UKPN (if they are providing any services for Power Potential) or with their contractual settings indicated in the "DER Framework Agreement and Connection Agreement" (if they are in contractual mode). This refers to leading power factor. | This is not required for DERs operating in the V mode as default
9 | Setpoint Active Power |  |  | Analogue | Float | Mandatory* | UKPN RTU | DER Control System | This is the target active power value requested to the DER which provides active power service, to control the active power output of the DER to maintain an appropriate export. This is an important signal, which is used by UKPN to actively manage the export from site. | This is not required for DERs providing only reactive power service.
10 | Setpoint Voltage |  |  | Analogue | Float | Mandatory | UKPN RTU | DER Control System | This is the target voltage value requested to the DER which provides reactive power service.
11 | DER Link Counter |  |  | Analogue | Integer | Mandatory | UKPN RTU | DER Control System | This signal is used by DER to monitor communications health to UKPN. If the loss of link is detected by DER, it must mitigate the risk and take safety action by reverting back to "DER Framework Agreement and Connection Agreement".
12 | V Service Enable |  |  | Digital | Boolean | Mandatory | UKPN RTU | DER Control System | This is an instruction to DER to enable V mode. DER should go to V mode (if they are in PF mode as default) and provide reactive power services by responding appropriately to the receiving limits and voltage setpoint. | Please refer to tab "additional information" page for explanation of each service/mode
13 | P Service Enable |  |  | Digital | Boolean | Mandatory* | UKPN RTU | DER Control System | This is an instruction to DER to enable P mode. DER should go to P mode (no need to change their current mode) and provide active power services by responding appropriately to the receiving limits and active power setpoints. | Please refer to tab "additional information" page for explanation of each service/mode
14 | Contractual Mode Enable |  |  | Digital | Boolean | Mandatory | UKPN RTU | DER Control System | This is an instruction to DER to instruct them to revert back to their contractual mode and settings as indicated in the "DER Framework Agreement and Connection Agreement". The DER operational limits will still be monitored by UKPN RTU in comparison with their contractual settings and failsafe actions may execute if required. | Please refer to tab "additional information" page for explanation of each service/mode
15 | Disable Mode Enable |  |  | Digital | Boolean | Mandatory | UKPN RTU | DER Control System | This is an instruction to DER to instruct them to revert back to their contractual mode and settings as indicated in the "DER Framework Agreement and Connection Agreement". The DER will then be out of the scope of Power Potential project and be considered as disconnected. | Please refer to tab "additional information" page for explanation of each service/mode
16 | Limit breach |  |  | Analogue | Integer | Optional, used based on specific scheme requirement | UKPN RTU | DER Control System | This is a notification signal for DER informing them that one or more of the limits has breached".
17 | Failsafe Action |  |  | Analogue | Integer | Mandatory | UKPN RTU | DER Control System | This is an alarm/instruction for failsafe actions carried out by UK Power Networks, should the DER fail to provide an output which respects the limit. Failsafe actions will also be triggered due to any non-compliancy status or any risk for the network. | Please refer to tab "additional information" page for explanation of each failsafe.
18 | Decouple Alarm |  |  | Analogue | Boolean | Optional, used based on specific scheme requirement | UKPN RTU | DER Control System | This is a notification signal to inform DER that it has lost its communication with UKPN RTU due to lack of receiving acknowledgment or response from DER. It is assumed that DER operates under safety condition by reverting back to its original contracted setting mode as indicated in "DER Framework Agreement and Connection Agreement" if it lost its connection with UKPN.
19 | Readback Active Power Upper Limit |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the feedback of the received "Active Power Upper Limit" (signal 1) by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
20 | Readback Active Power Lower Limit |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the Readback of the received "Active Power Lower Limit" (signal 2) by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
21 | Readback Voltage Upper Limit |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the Readback of the received "Voltage Upper Limit" (signal 3) by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
22 | Readback Voltage Lower Limit |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the Readback of the received "Voltage Lower Limit" (signal 4) by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
23 | Readback Reactive Power Upper Limit |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the Readback of the received "Reactive Power Upper Limit" (signal 5) by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
24 | Readback Reactive Power Lower Limit |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the Readback of the received "Reactive Power Lower Limit" (signal 6) by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
25 | Readback Active power setpoint |  |  | Analogue | Float | Mandatory* | DER Control System | UKPN RTU | This is the Readback of the received "Active Power setpoint" by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER. | This is not required for DERs providing only reactive power service.
26 | Readback Voltage setpoint |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the Readback of the received "voltage setpoint" by DER control system to UKPN RTU confirming acknowledgement of the action. This is required to check integrity of the DER control system and the comms link between UKPN RTU and DER.
27 | MW Capacity in Service |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | DER Controller's indication of percentage of MW capacity in service, relative to total plant rating at commissioning. | This is not required for DERs providing only reactive power service.
28 | Measured Customer Voltage |  |  | Analogue | Float | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | Customer's own voltage measurement at generator terminal, for comparison with UKPN measurement at point of connection.
29 | Measured Customer Active Power |  |  | Analogue | Float | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | Customer's own active power measurement at generator terminal, for comparison with UKPN measurement at point of connection.
30 | Measured Customer Reactive Power |  |  | Analogue | Float | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | Customer's own reactive power measurement at generator terminal, for comparison with UKPN measurement at point of connection.
31 | Measured Customer Power factor |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | Customer's own power factor measurement at generator terminal, for comparison with UKPN measurement at point of connection. | This is not required for DERs operating in the V mode as default
32 | Readback failsafe |  |  | Analogue | Integer | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | This is the feedback of the received "Failsafe" by DER control system to UKPN RTU confirming acknowledgement of the action. This confirmation will be used to detect abnormal behaviour between UKPN RTU and DER. | Please refer to tab "additional information" page for explanation of each failsafe.
33 | Readback V Service Enable |  |  | Digital | Boolean | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | This is the feedback (mirror) of the received V services enable by DER control system to UKPN RTU confirming acknowledgement of the action. This confirmation will be used to detect abnormal behaviour between UKPN RTU and DER.
34 | Readback P Service Enable |  |  | Digital | Boolean | Optional, used based on specific scheme requirement * | DER Control System | UKPN RTU | This is the feedback (mirror) of the received P services enable by DER control system to UKPN RTU confirming acknowledgement of the action. This confirmation will be used to detect abnormal behaviour between UKPN RTU and DER.
35 | Readback Contractual Mode Enable |  |  | Digital | Boolean | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | This is the feedback (mirror) of the received Contractual mode enable by DER control system to UKPN RTU confirming acknowledgement of the action. This confirmation will be used to detect abnormal behaviour between UKPN RTU and DER.
36 | Readback Disable Mode Enable |  |  | Digital | Boolean | Optional, used based on specific scheme requirement | DER Control System | UKPN RTU | This is the feedback (mirror) of the received Disable enable by DER control system to UKPN RTU confirming acknowledgement of the action. This confirmation will be used to detect abnormal behaviour between UKPN RTU and DER.
33 | DER Services |  |  | Analogue | Float | Mandatory | DER Control System | UKPN RTU | This is the feedback (mirror) of the received "Service Enable" signal (signals 12 and 13) by DER control system to UKPN RTU confirming acknowledgement of the action. This confirmation will be used to detect abnormal behaviour between UKPN RTU and DER. Therefore, if the DER is issued P or V service enable commands as digital points, they need to send back the DER services signal as readback signal in a Float format. Otherwise the DER service will be 0.
* This signal is only applicable to DER participating in the Active power service.

## DNP3 Protocol Configuration
Detailed DNP3 configuration to be followed
16-Bit Analogue Input
Object | Variation | Index | Class | Source | Destination | Signal | Type | Format | Unit | Min Range | Max Range | Notes | Address in PPC2 | Test OK
30 | 2 | 33 | 2 | DER Control System | UKPN RTU | Readback Failsafe | Analogue | Integer | Bit 0: Failsafe 1 action Bit 1 : Failsafe 2 action Bit 2 : Failsafe 3 action Bit 3 : Failsafe 4 action (Future Consideration) | - | - | Value 1: Failsafe 1 Value 2: failsafe 2 Value 4: Failsafe 3 Value 8: Failsafe 4 (Future Consideration) | 33
Short Floating Point Analouge Input
Object | Variation | Index | Class | Source | Destination | Signal | Type | Format | Unit/Value | Min Range | Max Range | Notes | Address in PPC 2 | Test OK
30 | 5 | 14 | 2 | DER Control System | UKPN RTU | Measured Customer Voltage | Analogue | Float | V | 0 | TBC1 |  | N/A3
|  | 15 | 2 | DER Control System | UKPN RTU | MW Capacity in Service | Analogue | Float | KW | 0 | TBC1 | This is not required for DERs providing only reactive power service. | N/A3
|  | 16 | 2 | DER Control System | UKPN RTU | Measured Customer Active Power | Analogue | Float | KW | 0 | TBC1 |  | N/A3
|  | 17 | 2 | DER Control System | UKPN RTU | Measured Customer Reactive Power | Analogue | Float | KVAr | TBC1 | TBC1 |  | N/A3
|  | 18 | 2 | DER Control System | UKPN RTU | Measured Customer Power Factor | Analogue | Float | - | -1 | 1 | This is not required for DERs operating in the V mode as default | N/A3
|  | 21 | 2 | DER Control System | UKPN RTU | Readback Active power setpoint | Analogue | Float | KW | 0 | TBC1 | This is not required for DERs providing only reactive power service. | 21
|  | 23 | 2 | DER Control System | UKPN RTU | Readback Voltage setpoint | Analogue | Float | V | 0 | TBC1 |  | 23
|  | 25 | 2 | DER Control System | UKPN RTU | Readback Active Power Upper Limit | Analogue | Float | KW | 0 | TBC1 |  | 25
|  | 26 | 2 | DER Control System | UKPN RTU | Readback Active Power Lower Limit | Analogue | Float | KW | 0 | TBC1 |  | 26
|  | 27 | 2 | DER Control System | UKPN RTU | Readback Reactive Power Upper Limit | Analogue | Float | KVAr | TBC1 | TBC1 |  | 27
|  | 28 | 2 | DER Control System | UKPN RTU | Readback Reactive Power Lower Limit | Analogue | Float | KVAr | TBC1 | TBC1 |  | 28
|  | 29 | 2 | DER Control System | UKPN RTU | Readback Voltage Upper Limit | Analogue | Float | V | 0 | TBC1 |  | 29
|  | 30 | 2 | DER Control System | UKPN RTU | Readback Voltage Lower Limit | Analogue | Float | V | 0 | TBC1 |  | 30
|  | 19 | 2 | DER Control System | UKPN RTU | DER Services | Analogue | Float | Bit 0 : P Service Bit 1: spare Bit 2 V Service Bit 3: spare | - | - | Value 0: No Service Value 1: P Service Value 4: V Service Value 5: P and V Services | N/A3
Binary Input with Status (Readback)
Object | Variation | Index | Class | Source | Destination | Signal | Type | Format | Unit | Min Range | Max Range | Notes | Address in PPC2 | Test OK
1 | 2 | 9 | 1 | DER Control System | UKPN RTU | Readback V service Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 9
|  | 10 | 1 | DER Control System | UKPN RTU | Readback P service Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable, This is not required for DERs providing only reactive power service. | 10
|  | 11 | 1 | DER Control System | UKPN RTU | Readback Contractual Mode Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 11
|  | 12 | 1 | DER Control System | UKPN RTU | Readback Disable Mode Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 12
Binary Output Status (Command)
Object | Variation | Index | Class | Source | Destination | Signal | Type | Format | Unit | Min Range | Max Range | Notes | Address in PPC2 | Test OK
12 | 2 | 7 | N/A | UKPN RTU | DER Control System | Decouple alarm | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 7
|  | 9 | N/A | UKPN RTU | DER Control System | V service Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 9
|  | 10 | N/A | UKPN RTU | DER Control System | P service Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable, This is not required for DERs providing only reactive power service. | 10
|  | 11 | N/A | UKPN RTU | DER Control System | Contractual Mode Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 11
|  | 12 | N/A | UKPN RTU | DER Control System | Disable Mode Enable | Digital | Boolean | Latch ON/OFF | N/A3 | N/A3 | 1=Enable, 0=Disable | 12
16-Bit Analogue outputs Block
Object | Variation | Index | Class | Source | Destination | Signal | Type | Format | Unit | Min Range | Max Range | Notes | Address in PPC2 | Test OK
41 | 2 | 18 | N/A | UKPN RTU | DER Control System | Limit Breach | Analogue | Integer | Bit 0: P upper limit Breach Bit 1: P Lower limit Breach Bit 2: Q upper limit Breach Bit 3: Q Lower limit Breach Bit 4: V upper limit Breach Bit 5: V Lower limit Breach Bit 6: PF upper limit Breach Bit 7: PF Lower limit Breach | - | - | I.e. : Value 0: No breach Value 16: V Upper limit Breach Value 32: V Lower Limit Breach Value 48: V upper limit and V lower Limit Breach | 18
|  | 19 | N/A | UKPN RTU | DER Control System | DER Link Counter | Analogue | Integer | - | 0 | 1000 | step=1, Default value being issued to DER is 60 (means 60seconds) | 19
|  | 20 | N/A | UKPN RTU | DER Control System | Failsafe Action | Analogue | Integer | Bit 0: Failsafe 1 action Bit 1: Failsafe 2 action Bit 2: Failsafe 3 action Bit 3: Failsafe 4 action (Future Consideration) | - | - | Value 1: Failsafe 1 Value 2: failsafe 2 Value 4: Failsafe 3 Value 8: Failsafe 4 (Future Consideration) | 20
Short Floating Point Analog Output Block
Object | Variation | Index | Class | Source | Destination | Signal | Type | Format | Unit | Min Range | Max Range | Notes | Address in PPC2 | Test OK
41 | 3 | 1 | N/A | UKPN RTU | DER Control System | Setpoint Active Power | Analogue | Float | KW | 0 | TBC1 | This is not required for DERs providing only reactive power service. | 1
|  | 3 | N/A | UKPN RTU | DER Control System | Setpoint Voltage | Analogue | Float | V | 0 | TBC1 |  | 3
|  | 5 | N/A | UKPN RTU | DER Control System | Active Power Upper Limit | Analogue | Float | KW | 0 | TBC1 |  | 5
|  | 6 | N/A | UKPN RTU | DER Control System | Active Power Lower Limit | Analogue | Float | KW | 0 | TBC1 |  | 6
|  | 7 | N/A | UKPN RTU | DER Control System | Reactive Power Upper Limit | Analogue | Float | KVAr | TBC1 | TBC1 |  | 7
|  | 8 | N/A | UKPN RTU | DER Control System | Reactive Power Lower Limit | Analogue | Float | KVAr | TBC1 | TBC1 |  | 8
|  | 9 | N/A | UKPN RTU | DER Control System | Voltage Upper Limit | Analogue | Float | V | 0 | TBC1 |  | 9
|  | 10 | N/A | UKPN RTU | DER Control System | Voltage Lower Limit | Analogue | Float | V | 0 | TBC1 |  | 10
|  | 11 | N/A | UKPN RTU | DER Control System | Power Factor Upper Limit (lagging) | Analogue | Float | - | -1 | 1 | This is not required for DERs operating in the V mode as default | 11
|  | 12 | N/A | UKPN RTU | DER Control System | Power Factor Lower Limit (leading) | Analogue | Float | - | -1 | 1 | This is not required for DERs operating in the V mode as default | 12
Note:
1 TBC: to be confirmed with customer according to DER P/Q characteristics, DER Framework Agreement and DER Connection Agreement
2 PPC: Power Plant Controller
3 N/A: Not applicable

## Additional Information
DER mode of operation Command
Definition | Function | Description
P Service Enable * = 0 and V Service Enable = 1 | DER Providing only Q service | Arm DER and request reactive power service with 4% droop, dedicated VUpper limit, VLower limit, QUpper Limit, QLower Limit, PUpper Limit, PLower Limit and a VSetpoint. *The DER should be armed (in V mode) and active power mode should be disable (only provide reactive power).
P Service Enable = 1 and V service Enable = 0 | DER Providing only P service | Request active power service with a PSetpoint under their default contractual agreement. *DER should be in their default mode and only provide P service.
P Service Enable = 1 and V service Enable = 1 | DER Providing both P and Q services | V mode: Arm DER and request reactive power service with 4% droop, dedicated VUpper limit, VLower limit, QUpper Limit, QLower Limit, PUpper Limit, PLower Limit and a VSetpoint. P mode: Request active power service with a P Setpoint under V mode defined on line above.
Contractual mode Enable = 1 | DER should behave as in the "DER Connection Agreement" but still monitored and controlled by UKPN RTU . | Disarm DER to revert back to its default mode and operate within P/Q characteristic as in "DER connection agreement" setting.
Disable (disarm) DER mode Enable = 1 | DER should behave as in the "DER Connection Agreement" and will be disable/disconnected from power potential trials. | Disarm DER to revert back to its default mode and operate within P/Q characteristic as in "DER connection agreement" setting and disable the active power mode.
* For DER operating in Voltage mode (V mode) as default (as in the "DER contractual agreement"), DER does not need to change its mode while receiving "V service enable" instruction but this signal arms the DER to start participating in Power Potential and provides reactive power service.
Failsafe Actions
Failsafe 1: This is the first failsafe action carried out by UK Power Networks, should the DER fail to provide an output which respects the limit as per Signal 1-8 (as appropriate). This failsafe action will also be triggered due to any non-compliancy status or any risk for the network. When this signal is HIGH(1) DER is instructed to operate within its P/Q characteristics as stated in "Power Potential DER Framework Agreement" and "Variation Agreement relating to a Connection Agreement.
Failsafe 2: The second failsafe action carried out by UK Power Networks, as the DER has failed to provide an output which respects the limit as per failsafe1 (signal expired). This failsafe action will also be triggered due to non-compliancy status or any risk for the network. When this signal is HIGH(1) DER is instructed to revert back to its default mode when not delivering the Power Potential service (PF or V mode) as in the customer's original "Connection Agreement" prior to the "Variation Agreement relating to a Connection Agreement".
Failsafe 3:The third failsafe action carried out by UK Power Networks, as the DER has failed to provide an output which respects the limit as per Failsafe3 (signal expired). This failsafe action will also be triggered due to non-compliancy status or any risk for the network. When this signal is HIGH(1) DER is instructed to go to 0 MW. It should be noted that the Failsafe 3 (0MW Request) is not being implemented as part of the Power Potential trial, but is included here should it be required in future.
Failsafe 4: This is a notification signal that the forth failsafe action has been carried out by UK Power Networks, informing the DER that it has been disconnected from the network and UKPN has opened the circuit breaker. This is due to failure to respect failsafe within the configured deadline. This failsafe action will also be triggered due to non-compliancy with the "Power Potential DER Framework Agreement" or "Variation Agreement relating to a Connection Agreement" or any risk for the network. It should be noted that the Failsafe 4 (opening the circuit breaker) is not being implemented as part of the Power Potential trial, but is included here should it be required in future.
Example of Signal exchange for Enabling V Service to Provide Reactive Power
Example of Signal exchange for Contractual mode Enable

## DNP TCP-IP Configuration
TCP/IP configuration
Physical Medium | TBC* | Ethernet Interfaces: | DER control system
Chosen Protocol | DNP3 over TCP/IP | IP Address: | 192.168.35.9
DNP3 Client (Master) | UKPN RTU | Mask: | 255.255.255.0
DNP3 Server (Slave) | DER control system | Def.GW.: | 192.168.35.1
DER DNP type | Listening to the end point | Target IP: | 192.168.35.127
DNP3 port | 20000 | DNP Address: | 2
*TBC: To be Confirmed with DER