## Project Gantt (hidden)
Project EU Elec - Work Stream Plan
| Key: |  | Mandated manually filled cells |  | Current Month |  | Proposal Development/ Consultation | - | Completed Task
|  | NOT BOLDED | AUTOMATED fill - please do not edit |  | Task Schedule |  | NRA Approval/Approval | EIF | CONFIRMED EIF Dates | CONFIRMED EIF Dates
|  | BOLDED | Information needs to be entered manually |  | SUB Task Schedule |  | Implementation | EIF | FCA CONFIRMED EIF Dates | FCA CONFIRMED EIF Dates
|  |  | Sub Sub Tasks |  | SUB SUB Task Schedule |  | Other Tasks |  | CODE MODs | CODE MODs
[13 empty] | 2013 | [11 empty] | 2014 | [11 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022 | [11 empty] | 2023
[13 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half | [5 empty] | 1st Half | [5 empty] | 2nd Half
ID Tasks # | Work stream | Lead & Resource | IS Lead | Dependencies | Articles | EIF | Start | End | Cal. Days | % Done | Work Weeks | Work Days | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
0.0.1 | Regional design of long-term transmission rights | TBC |  | [ID #] | FCA 31(2) |  | 2016-08-01 | 2017-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 9: TSO; 2nd Half 10: Consultation; 1st Half 2: NRA Approval
0.0.2 | Nomination procedures for physical transmission rights | TBC |  | [ID #] | FCA 36(2) |  | 2016-08-01 | 2018-01-31 | 549 | 25% | 78.6 | 393 | 2nd Half 9: TSOs develop first report; 1st Half 4: Consultation; 2nd Half 8: NRA Approval
0.0.3 | Fallback | TBC |  | [ID #] | FCA 42(2) |  | 2016-08-01 | 2017-07-31 | 365 | 80% | 52.2 | 261 | 2nd Half 9: TSOs develop - Timing unclear in FCA
0.0.4 | SAP estabilshment (Single Allocation Platform) | TBC |  | 3.6.5 | FCA 48(2) |  | 2017-08-01 | 2019-07-31 | 730 | 0% | 104.4 | 522 | 2nd Half 10: EIF; 2nd Half 8: TSOs Develop
0.0.5 | SAP requirements | TBC |  | [ID #] | FCA 49(1) |  | 2017-08-01 | 2018-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 8: TSOs Develop; 1st Half 2: NRA Approval
0.0.6 | Hermonised Allocation Rules(HAR) | TBC |  | [ID #] | FCA 51(1) |  | 2017-08-01 | 2018-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 8: TSOs Dev; 2nd Half 10: Consultation; 1st Half 2: NRA Approval
0.0.7 | SAP costs | TBC |  | [ID #] | FCA 59 |  | 2017-08-01 | 2018-07-31 | 365 | 20% | 52.2 | 261 | 2nd Half 8: TSOs Develop; 1st Half 2: NRA Approval
1 | System Operation (TSOG & ER) | John Young | Stefan D'alessandro (IS PM) |  |  |  | 2016-06-01 | 2020-07-31 |  | 0.6973%
1.1 | GENERAL PROVISIONS | John Young |  | [ID #] |  |  | 2016-11-14 | 2018-07-31 |  | 0% | bar: 2nd Half 11 to 2nd Half 7
1.1.1 | GENERAL PROVISIONS |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval
1.1.2 | Modification Approval (GB code) |  |  | 4.1.1 | [Articles] |  | 2016-11-14 | 2018-07-31 | 625 | 0% | 89.4 | 447 | 2nd Half 11: Mod Assessment; 1st Half 2: Mod Approval
1.2 | Data Exchange | John Young |  | [ID #] |  |  | 2016-09-07 | 2018-08-31 |  | 4.167% |  |  | 2nd Half 9: 4.167%
1.2.1 | Ref Art 72 - Exchange data with all other TSOs to the extent that it is necessary for carrying out the operational security analysis |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-04-30 | 454 | 0% | 64.8 | 324 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: IMP
1.2.2 | Agree on key organisational requirements, roles and responsibilities in relation to data exchange [EIF+6m] |  |  | [ID #] | [Articles] |  | 2016-09-07 | 2017-01-31 | 147 | 25% | 21 | 105 | 1st Half 1: EIF; 1st Half 2: Consultation; 1st Half 4: -; 1st Half 5: -; 1st Half 6: -; 2nd Half 8: ("Rreport to Authority" folloby "Modification Approval", Then "All TSOs shall define a harmonised data format for data exchange")
1.2.3 | Define Data Exchange Scope [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 8: (Modification change & approval)
1.2.4 | Scheduled & Structural Data Exchange [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 8: (Modification change & approval)
1.2.5 | Real time Data Exchange [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 8: (Modification change & approval)
1.2.6 | Modification Approval (GB code) |  |  | 4.2.1/4.2.2/4.2.3/4.2.4/4.2.5 | [Articles] |  | 2017-06-01 | 2018-08-31 | 457 | 0% | 65.4 | 327 | 1st Half 1: EIF; 1st Half 6: Mod Assessment; 1st Half 2: Mod Approval
1.3 | Reserve Providers | John Young |  | [ID #] |  |  | 2016-09-07 | 2018-04-30 |  | 0% | bar: 2nd Half 9 to 1st Half 4
1.3.1 | Define reserve technical requirements [EIF+12m] |  |  | [ID #] | [Articles] |  | 2016-09-07 | 2017-09-06 | 365 | 0% | 52.2 | 261 | 2nd Half 9: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.3.2 | Pre-Qualification of Reserves Process (JY??) [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.3.3 | Modification Approval (GB code) |  |  | 4.3.1/4.3.2 | [Articles] |  | 2017-03-01 | 2018-04-30 | 426 | 0% | 60.8 | 304 | 1st Half 1: EIF; 1st Half 3: Mod Assessment; 2nd Half 11: Mod Approval
1.4 | Planning & Scheduling | John Young |  | [ID #] |  |  | 2017-02-01 | 2018-11-30 |  | 0% | bar: 1st Half 1 to 2nd Half 11
1.4.1 | OP Contingency analysis and handling (=6months NRA Approval) [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.2 | Operational security analysis [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.3 | Methodology for assessing relevance of assets. [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.4 | Availability Plans [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.4.5 | Regional Security Coordination(NRA Approval 75 +3months) [EIF+19m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-08-31 | 577 | 0% | 82.6 | 413 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 9: (Modification change & approval)
1.4.6 | Proposal for Regional Operational Security Coordination [EIF+21] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.7 | Com Grid Model building [EIF+21m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.8 | Lists of relevant generating modules and relevant facilities [EIF+21] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.9 | Lists of relevant grid elements [EIF+21] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.4.10 | Year Ahead Availability plans [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.11 | Procedure for handling forced outages [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.12 | Adequacy Analysis [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.13 | ENTSO-E Operational Planning Data Environment [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-04-03 | 2018-11-30 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 4: Proposal Development; 2nd Half 10: NRA Approval; 1st Half 4: -; 2nd Half 7: IMP; 2nd Half 12: (Modification change & approval)
1.4.14 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2017-02-01 | 2018-09-28 | 605 | 0% | 86.6 | 433 | 1st Half 1: EIF; 1st Half 2: Mod Assessment; 1st Half 4: Mod Approval
1.5 | LFCR | John Young |  | [ID #] |  |  | 2016-06-01 | 2018-12-31 |  | 0% | bar: 1st Half 1 to 2nd Half 12
1.5.1 | LFCR TITLE 2 - Frequency Quality Parameters |  |  | [ID #] | [Articles] |  | 2017-01-02 | 2018-08-31 | 607 | 0% | 87 | 435 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP
1.5.2 | Process Structure [EIF+4m] (Check with JY Code Mapping) |  |  | [ID #] | [Articles] |  | 2017-01-02 | 2017-04-13 | 102 | 0% | 14.8 | 74 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 4: -; 1st Half 5: -; 1st Half 6: ("Rreport to Authority" folloby "Modification Approval")
1.5.3 | LFCR - Opearational Agreement [EIF+12m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-01-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 1st Half 5: NRA Approval; 2nd Half 11: IMP
1.5.4 | Automatic and manual frequency restoration process implementation [EIF+24m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-12-31 | 699 | 0% | 99.8 | 499 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: Implementation & Testing; 1st Half 1: (Modification Approval)
1.5.5 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2016-06-01 | 2017-07-31 | 426 | 0% | 60.8 | 304 | 1st Half 1: EIF; 1st Half 6: Mod Assessment; 1st Half 2: Mod Approval
1.6 | Operational Practices (TBC) | John Young |  | [ID #] |  |  | 2017-02-01 | 2018-12-31 |  | 0.7143% |  |  | 1st Half 2: 0.7143%
1.6.1 | Operational Security |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 5% | 47.6 | 238 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 5: IMP; 2nd Half 10: (Modification change & approval)
1.6.1.1 | Modification Approval | [5 empty] | 2017-09-01 | 2018-07-31 | 334 | 5% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.1 | OS TITLE 1 - Operational Security Requirements |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.2 | OS TITLE 3 - Compliance |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.3 | OP TITLE 3 - Procedure for handling forced outages |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.4 | OP TITLE 5 - Ancillary Services |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 0% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.1.1.5 | OP TITLE 6 - Scheduling |  |  | [ID #] | [Articles] |  | 2017-09-01 | 2018-07-31 | 334 | 25% | 47.6 | 238 | 1st Half 1: EIF; 2nd Half 9: Mod assessment; 1st Half 2: Raise Mod
1.6.2 | OS - Business continuity plan [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: -; 1st Half 4: IMP; 2nd Half 8: (Modification change & approval); 2nd Half 9: (Modification change & approval)
1.6.3 | Training plan [EIF+18m] |  |  | [ID #] | [Articles] |  | 2017-02-01 | 2018-07-31 | 546 | 0% | 78 | 390 | 1st Half 1: EIF; 1st Half 2: Training Plan; 2nd Half 7: Resource Identification; 1st Half 1: Communication; 2nd Half 8: (IMP)
1.6.4 | Dynamic stability study [EIF+24m] |  |  | [ID #] | [Articles] |  | 2018-01-01 | 2018-12-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 1: Proposal Development; 1st Half 4: NRA Approval; 2nd Half 10: IMP
1.6.5 | Updates of year-ahead individual and comgrid models [EIF+18m] |  |  | [ID #] | [Articles] |  | 2018-01-01 | 2018-12-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 1: Proposal Development; 1st Half 4: NRA Approval; 2nd Half 10: IMP
1.6.6 | Define minimum required inertia by 6months following study in Art 39a [EIF+30m] |  |  | [ID #] | [Articles] |  | 2018-01-01 | 2018-12-31 | 365 | 0% | 52.2 | 261 | 1st Half 1: EIF; 1st Half 1: Proposal Development; 1st Half 4: NRA Approval; 2nd Half 10: IMP
1.6.7 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2018-02-01 | 2018-08-03 | 184 | 0% | 26.4 | 132 | 1st Half 1: EIF; 1st Half 2: Mod Assessment; 2nd Half 10: Mod Approval
1.7 | Emergency Restoration(TBC) | John Young |  | [ID #] |  |  | 2017-05-01 | 2020-07-31 |  | 0% | bar: 1st Half 5 to 2nd Half 7
1.7.1 | Emergency Restoration [EIF+12] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2018-04-30 | 365 | 0% | 52.2 | 261 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 8: NRA Approval; 2nd Half 11: Compliance Testing; 1st Half 2: Monitoring
1.7.2 | Restoration Plan [EIF+12] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2018-04-30 | 365 | 0% | 52.2 | 261 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 11: NRA Approval
1.7.3 | System Defence Plan [EIF+12] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2018-04-30 | 365 | 0% | 52.2 | 261 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 11: NRA Approval
1.7.4 | Defence System Implementation [EIF+24] |  |  | [ID #] | [Articles] |  | 2017-05-01 | 2019-04-30 | 730 | 0% | 104.4 | 522 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 11: NRA Approval; 1st Half 5: Compliance Testing; 2nd Half 11: Monitoring
1.7.5 | Automatic under-frequency control scheme [EIF+60] |  |  | [ID #] | [Articles] |  | 2019-05-01 | 2020-04-30 | 366 | 0% | 52.4 | 262 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: IMP
1.7.6 | Tools and Communication [EIF+60] |  |  | [ID #] | [Articles] |  | 2019-05-01 | 2020-04-30 | 366 | 0% | 52.4 | 262 | 1st Half 4: EIF; 1st Half 5: Proposal Development; 2nd Half 8: NRA Approval; 1st Half 2: IMP
1.7.7 | Modification Approval (GB code) |  |  | all | [Articles] |  | 2019-05-01 | 2020-07-31 | 458 | 0% | 65.6 | 328 | 1st Half 4: EIF; 1st Half 6: Mod Assessment; 1st Half 2: Mod Approval
Article 57 - Performing operational tests and analysis
Article 57 Performing operational tests and analysis
Formulas:
EIF = IF([Completed Task]=0,[Proposal Development/ Consultation],[Proposal Development/ Consultation]+[Completed Task]-1)
EIF = MAX([EIF, row below],I21,I28,I32,I47,I53,I67)
Proposal Development/ Consultation = MIN([Proposal Development/ Consultation, row below],H21,H28,H32,H47,H53,H67)
Proposal Development/ Consultation = MIN([Proposal Development/ Consultation, row below],H20)
Note on A9: ID - Task Number Level 1: 1, 2, 3, ... Level 2: 1.1, 1.2, 1.3, ... Level 3: 1.1.1, 1.1.2, 1.1.3, … The WBS uses a formula to control the numbering, but the formulas are different for different levels. When you add rows, you need to use th etemaplte located at the bottom of this document.
Note on B9: Work stream - Task Name Enter the name of each task and sub-task. Use indents for sub-tasks.
Note on C9: Task Lead Enter the name of the Task Lead in this column. Preferbly with the percetage allocation
Note on E9: Dependencies Insert Task ID number which has dependencies against.
Note on F9: Articles: Articles against the document. Article Number(section) XX(Y) ie. 12(3)
Note on H9: Task Start Date
Note on I9: Task End Date
Note on J9: Manual Input - How Many days(including weekends). This will determin the END DATE.
Note on K9: % Completed This is a manual input. Once you enter the percentage progressed/completed, the GREY bar will appear.
Note on L9: Calculation for number of Working Weeks from "Cal.Days"
Note on M9: Calculation for number of Working Days from "Cal.Days". (Excluding Weekends)

## EIF Dates (hidden)
Work Stream | EIF Dates | Officaly confirmed? | When was it confirmed? | Success Criteria | NOTE
Balancing | 2017-04-01 | No | No
Common Grid Model (CGM) | TBC | No | No
Capacity Calculation (CACM) | 2015-08-14 | Yes | 2015 | Complete proposal
Capacity Calculation (FCA) | 2016-10-17 | Yes | 2016-10-01 | Complete proposal
System Operation (TSOG) | 2017-01-01 | No | No
System Operation (ER) | 2016-04-01 | No | No
Grid Connection Code (RfG) | 2016-05-17 | Yes | 2016 | Complete Implementation | Generation 800w and above
Grid Connection Code (HVDC) | 2016-09-15 | Yes | 2016 | Complete Implementation | to be confirmed by WS leads
Grid Connection Code (DCC) | 2016-09-06 | Yes | 2016 | Complete Implementation | to be confirmed by WS leads

## Code mapping extract
Title | Chapter | Section | Article | Paragraph | Article Text | Grid Code [NGET] | D-Code [ENA] | SQSS [NGET] | STC [NGET] | BSC [Elexon] | CUSC [NGET] | D-CUSC Distribution & Connection & Use of System Agreement [ElectraLink] | Legislation | Licences | I/C Access Rules | No GB Framework | RFG | DCC | HVDC | CACM | E&R | FCA | Balancing | Comments relative to GB regulation and codes
1 | 0 | 0 | 3 | 0 | Article 3 - Definitions | [18 empty] | Relevant/neccesary definions picked up in code mods
1 | 0 | 0 | 3 | 1 | For the purposes of this Regulation, the definitions in Article 2 of Regulation (EC) No 714/2009, Article 2 of Commission Regulation No (EU) No 2015/12226, Article 2 of Commission Regulation No (EU) 2016/631, Article 2 of Commission Regulation No (EU) 2016/1388, Article 2 of Commission Regulation No (EU) 2016/1447, Article 2 of Commission Regulation No [000/2015 FCA], Article 2 of Regulation (EU) No 543/20137 on submission and publication of data in electricity markets and Article 2 of Directive 2009/72/EC8 shall apply.
1 | 0 | 0 | 3 | 1 | In addition, the following definitions shall apply:
1 | 0 | 0 | 3 | 6 | 6. ‘frequency containment reserves or 'FCR' means the balancing reserves available to contain system frequency after the occurrence of an imbalance; | GC0114 (copy definition)
1 | 0 | 0 | 3 | 7 | 7. ‘frequency restoration reserve or 'FRR' means the balancing reserves available to restore system frequency to the nominal frequency and for a synchronous area consisting of more than one LFC area power balance to the scheduled value; | GC0114 (copy definition)
1 | 0 | 0 | 3 | 8 | 8. ‘replacement reserves' or 'RR' means the active power reserves available to restore or support the required level of FRR to be prepared for additional system imbalances, including generation reserves; | GC0114 (copy definition)
1 | 0 | 0 | 3 | 9 | 9. ‘reserve provider’ means a legal entity with a legal or contractual obligation to supply FCR, FRR or RR from at least one reserve providing unit or reserve providing group; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 10 | 10. ‘reserve providing unit’ means a single or an aggregation of power generating modules and/or demand units connected to a common connection point fulfilling the requirements to provide FCR, FRR or RR; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 11 | 11. ‘reserve providing group’ means an aggregation of power generating modules, demand unit and/or reserve providing units connected to more than one connection point fulfilling the requirements to provide FCR, FRR or RR; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 58 | 58. ‘reference incident’ means the maximum positive or negative power deviation occurring instantaneously between generation and demand in a synchronous area, considered in the FCR dimensioning; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 95 | 95. ‘reserve capacity’ means the amount of FCR, FRR or RR that needs to be available to the TSO; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 96 | 96. ‘exchange of reserves’ means the possibility of a TSO to access reserve capacity connected to another LFC area, LFC block, or synchronous area to comply with the amount of required reserves resulting from its own reserve dimensioning process of either FCR, FRR or RR and where that reserve capacity is exclusively for that TSO, and is not taken into account by any other TSO to comply with the amount of required reserves resulting from their respective reserve dimensioning processes; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 97 | 97. ‘sharing of reserves’ means a mechanism in which more than one TSO takes the same reserve capacity, being FCR, FRR or RR, into account to fulfil their respective reserve requirements resulting from their reserve dimensioning processes; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 111 | 111. ‘FCR full activation frequency deviation’ means the rated value of frequency deviation at which the FCR in a synchronous area is fully activated; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 112 | 112. ‘FCR full activation time’ means the time period between the occurrence of the reference incident and the corresponding full activation of the FCR; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 113 | 113. ‘FCR obligation’ means the part of all of the FCR that falls under the responsibility of a TSO; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 117 | 117. ‘frequency quality target parameter’ means the main system frequency target on which the behaviour of FCR, FRR and RR activation processes is evaluated in normal state; | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 130 | 130. ‘initial FCR obligation’ means the amount of FCR allocated to a TSO on the basis of a sharing key | [18 empty] | No intention to include definiton in GB codes at present.
1 | 0 | 0 | 3 | 152 | 152. ‘reserve replacement process or 'RRP’ means a process to restore activated FRR and additionally for GB and IE/NI to restore the activated FCR; | [18 empty] | No intention to include definiton in GB codes at present.
2 | 0 | 0 | 45 | 0 | Article 45 - Structural data exchange
2 | 0 | 0 | 45 | 1 | 1. Each SGU which is a power generating facility owner of a type D power generating module connected to the transmission system shall provide the TSO with at least the following data: | PC.A.2 | [17 empty] | Grid Code PC.A.2
2 | 0 | 0 | 45 | 1(a) | (a) general data of the power generating module, including installed capacity and primary energy source; | PC.A.3.2.2(a) | [17 empty] | Grid Code PC.A.3.2.2(a)
2 | 0 | 0 | 45 | 1(b) | (b) turbine and power generating facility data including time for cold and warm start; | DRC.6.1.2 | [17 empty] | Grid Code - Planning Code, PC.A.2 , Data Registration Code DRC.6.1.2
2 | 0 | 0 | 45 | 1(c ) | (c) data for short-circuit current calculation; | PC.A.2.5 | [17 empty] | Grid Code - Planning Code, PC.A.2, Data Registration Code
2 | 0 | 0 | 45 | 1(d) | (d) power generating facility transformer data; | PC.A.2.2.5 | [17 empty] | Grid Code - Planning Code, PART 1 - STANDARD PLANNING DATA, PC.A.2 , Data Registration Code
2 | 0 | 0 | 45 | 1(e ) | (e) FCR data of power generating modules offering or providing that service, in accordance with Article 154; | [17 empty] | X | See SOGL Article 154
2 | 0 | 0 | 45 | 1(f) | (f) FRR data of power generating modules offering or providing that service, in accordance with Article 158; | [17 empty] | X | See SOGL Article 158
2 | 0 | 0 | 45 | 1(g) | (g) RR data of power generating modules that offer or provide that service in accordance with Article 161; | [17 empty] | X | See SOGL Article 161
2 | 0 | 0 | 45 | 1(h) | (h) data necessary for restoration of the transmission system; | DRC.6.1.16 PC.A.5.7 | [17 empty] | Grid Code, Operating Codes, OC9 Contingency Planning, OC10, OC10.1 - OC10.4, OC12, OC12.1 - OC12.4
2 | 0 | 0 | 45 | 1(h)(i) | (i) data and models necessary for performing dynamic simulation; | DRC.6.1.7 and more | [17 empty] | Grid Code, PC.A.2, PC.A.3, PC.A.4, PC.A.5, PC.A.5.7, DRC.6.1.16
2 | 0 | 0 | 45 | 1(h)(i) | (j) protection data; | DRC.6.1.5 | [17 empty] | Grid Code, PC.A.6.6, DRC.6
2 | 0 | 0 | 45 | 1(k) | (k) data necessary for determining the costs of remedial actions in accordance with Article 78(1)(b); where a TSO makes use of market based mechanisms in line with Article 4(2)(d), the provision of prices to be paid by the TSO shall be considered sufficient; | BC4 | [17 empty] | BSC Section 4
2 | 0 | 0 | 45 | 1(l) | (l) voltage and reactive power control capability. | PC.A.2.4 | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6, 7, BC2 PC.A.2.4
2 | 0 | 0 | 45 | 2 | 2. Each SGU which is a power generating facility owner of a type B or a type C power generating module connected to the transmission system shall provide the TSO with at least the following data: | [18 empty] | CC.6.3.2, CC6.3, CC.6.3.8, APPENDIX 6 , 7 , BC2
2 | 0 | 0 | 45 | 1(a) | (a) general data of the power generating module, including installed capacity and primary energy source; | DRC.6.1.3 | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 , 7 , BC2
2 | 0 | 0 | 45 | 2(b) | (b) data for short-circuit current calculation; | DRC.6.1.13 | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 2(c ) | (c) FCR data according to the definition and requirements of the Article 173 for power generating modules offering or providing that service; | X | [17 empty] | CC6.3, CC.6.3.2, CC6.3, CC.6.3.8, APPENDIX 6, 7 , BC2,
2 | 0 | 0 | 45 | 2(d) | (d) FRR data for power generating modules that offer or provide that service; | X | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 2(e ) | (e) RR data for power generating modules that offer or provide that service; | X | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 2(f) | (f) protection data; | DRC.6.1.5 | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 2(g) | (g) reactive power control capability; | DRC.6.1.5 | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 2(h) | (h) data necessary for determining the costs of remedial actions in accordance with Article 78(1)(b); where a TSO makes use of market based mechanisms in line with Article 4 (2) d), the provision of prices to be paid by the TSO shall be considered sufficient; | X | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 2(h)(i) | (i) data necessary for performing dynamic stability assessment according to Article 38. | DRC.6.1.7 and more | [17 empty] | Grid Code CC6.3, CC.6.3.2, CC.6.3.8, APPENDIX 6 ,7 , BC2 , DRC.6.1.13
2 | 0 | 0 | 45 | 3 | 3. A TSO may request the power generating facility owner of a power generating module connected to the transmission system to provide further data where appropriate for operational security analysis in accordance with Title 2 of Part III. | [18 empty] | PC.A.6.1.3, PC.A.7
2 | 0 | 0 | 45 | 4 | 4. Each HVDC system owner or interconnector owner shall provide the TSO with the following data regarding the HVDC system or interconnector: | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(a) | (a) nameplate data of the installation; | PC.A.3.2.2(a) | [17 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(b) | (b) transformers data; | [18 empty] | Grid Code PC.A.3.2.2(a)
2 | 0 | 0 | 45 | 4(c ) | (c) data on filters and filter banks; | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(d) | (d) reactive power compensation data; | PC.A.2.4 | [17 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(e ) | (e) active power control capability; | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(f) | (f) reactive power and voltage control capability; | PC.A.2.4 | [17 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(g) | (g) active or reactive operational mode prioritization, if existing; | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(h) | (h) frequency response capability; | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(h)(i) | (i) dynamic models for dynamic simulation; | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(h)(i) | (j) protection data; and | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 4(k) | (k) fault-ride-through capability. | [18 empty] | Grid Code PC.A.5.4.3
2 | 0 | 0 | 45 | 5 | 5. Each AC interconnector owner shall provide the TSO with at least the following data: | [18 empty] | N/A in GB
2 | 0 | 0 | 45 | 5(a) | (a) nameplate data of the installation; | [18 empty] | N/A in GB
2 | 0 | 0 | 45 | 5(b) | (b) electrical parameters; | [18 empty] | N/A in GB
2 | 0 | 0 | 45 | 5(c ) | (c) associated protections. | [18 empty] | N/A in GB
2 | 0 | 0 | 48 | 0 | Article 48 - Structural data exchange | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1 | 1. Unless otherwise provided by the TSO, each power generating facility owner of a power generating module which is a SGU pursuant to Article 2(1)(a) and by aggregation of the SGUs pursuant to Article 2(1)(e) connected to the distribution system shall provide at least the following data to the TSO and to the DSO to which it has a connection point: | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements (CC).
2 | 0 | 0 | 48 | 1(a) | (a) general data of the power generating module, including installed capacity and primary energy source or fuel type; |  | DPC8, DDRC | [16 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(b) | (b) FCR data according to the definition and requirements of Article 173 for power generating facilities offering or providing the FCR service; | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(c ) | (c) FRR data for power generating facilities offering or providing the FRR service; | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(d) | (d) RR data for power generating modules offering or providing the RR service; | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(e ) | (e) protection data; | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(f) | (f) reactive power control capability; | CCs | [17 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(g) | (g) capability of remote access to the circuit breaker; | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(h) | (h) data necessary for performing dynamic simulation according to the provisions in Commission Regulation No (EU) 2016/631; and | CCs | [10 empty] | X | [6 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 1(h)(i) | (i) voltage level and location of each power generating module. | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
2 | 0 | 0 | 48 | 2 | 2. Each power generating facility owner of a power generating module which is a SGU in accordance with Article 2(1)(a) and 2(1)(e) shall inform the TSO and the DSO to which it has a connection point, within the agreed time and not later than the first commissioning or any changes to the existing installation, about any change in the scope and the contents of the data listed in paragraph 1. | [18 empty] | Flexible as per Article 40.5- Maintain existing data exchange as per Distribution and Grid Code framework. Future mods will be raised based on changes to system operational requirements.
4 | 0 | 0 | 152 | 0 | System states related to system frequency
4 | 0 | 0 | 152 | 1 | 1. Each TSO shall operate its control area with sufficient upward and downward active power reserve, which may include shared or exchanged reserves, to face imbalances of demand and supply within its control area. Each TSO shall control the FRCE as defined in the Article 143 in order to reach the required frequency quality within the synchronous area in cooperation with the TSOs in the same synchronous area. | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 152 | 2 | 2. Each TSO shall monitor close to real-time generation and exchange schedules, power flows, node injections and withdrawals and other parameters within its control area relevant for anticipating a risk of a frequency deviation and shall take, in coordination with other TSOs of its synchronous area, measures to limit their negative effects on the balance between generation and demand. | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 152 | 3 | 3. All TSOs of each synchronous area shall specify a real-time data exchange in accordance with Article 42 which shall include: | [18 empty] | This is being developed under Grid Code modification GC0106
4 | 0 | 0 | 152 | 3(a) | (a) the system state of the transmission system in accordance with Article 19; and | [18 empty] | This is being developed under Grid Code modification GC0106
4 | 0 | 0 | 152 | 3(b) | (b) the real-time measurement data of the FRCE of the LFC blocks and LFC areas of the synchronous area. | [18 empty] | This is being developed under Grid Code modification GC0106
4 | 0 | 0 | 152 | 4 | 4. The synchronous area monitor shall determine the system state with regard to the system frequency in accordance with Article 19 and in accordance with the system frequency limits specified in Article 18(5) and (6). | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 152 | 5 | 5. The synchronous area monitor shall ensure that all TSOs of all synchronous areas are informed in case the system frequency deviation fulfils one of the criteria for the alert state referred to in Article 18. | [18 empty] | NGET intends to use the ENTSO-E Awareness System (EAS) and Crisis Communication Tool (CCT) to manage this requirement.
4 | 0 | 0 | 152 | 6 | 6. All TSOs of a synchronous area shall define in the synchronous area operational agreement common rules for the operation of load-frequency control in the normal state and alert state. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 152 | 7 | 7. All TSOs of the GB and IE/NI synchronous areas shall specify in the synchronous area operational agreement operational procedures for cases of exhausted FCR. In those operational procedures the TSOs of a synchronous area shall have the right to require changes in the active power production or consumption of power generating modules and demand units. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 152 | 8 | 8. All TSOs of a LFC block shall specify operational procedures for cases of exhausted FRR or RR in the LFC block operational agreement. In those operational procedures the TSOs of a LFC block shall have the right to require changes in the active power production or consumption of power generating modules and demand units. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 152 | 9 | 9. The TSOs of a LFC block shall endeavour to avoid FRCEs which last longer than the time to restore frequency. | [18 empty] | NGET manages thris requirement through the application of the Security and Quality of Supply Standards in operational timescales.
4 | 0 | 0 | 152 | 10 | 10. All the TSOs of a synchronous area shall specify in the synchronous area operational agreement the operational procedures for cases of alert state due to a violation of system frequency limits. The operational procedures shall aim at reducing the system frequency deviation to restore the system state to the normal state and to limit the risk of emergency state by determining procedures in the synchronous area operational agreement in respect of which the TSOs shall have the right to deviate from the obligation set in Article 142(1). | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 152 | 11 | 11. If the system state is in the alert state due to insufficient active power reserves in accordance with Article 18, the TSOs of the concerned LFC blocks shall, in close cooperation with the other TSOs of the synchronous area and the TSOs of other synchronous areas, act to restore and replace the necessary levels of active power reserves. For that purpose, the TSOs of a LFC block shall have the right to require changes in the active power production or consumption of power generating modules or demand units within its area to reduce or to remove the violation of the requirements concerning active power reserve. | [18 empty] | This is fulfilled firstly by BM and ancillary services and backed-up by the capability to perform emergency instructions to change generation output or to disconnect parties to restore frequency, balance and critical reserve levels.
4 | 0 | 0 | 152 | 12 | 12. If the 1-minute average of the FRCE of a LFC block is above the Level 2 FRCE range at least during the time necessary to restore frequency and where the TSOs of a LFC block do not expect that FRCE will be sufficiently reduced by undertaking the actions in paragraph 15, TSOs shall have the right to require changes in the active power production or consumption of power generating modules and demand units within their respective areas to reduce the FRCE as specified in paragraph 16. | [18 empty] | Currently applies to Large Power Stations CC.6.3.7 If required for demand will be via contract
4 | 0 | 0 | 152 | 13 | 13. For the CE and Nordic synchronous areas, where the FRCE of a LFC block exceeds 25 % of the reference incident of the synchronous area for more than 30 consecutive minutes and if the TSOs of that LFC block do not expect to reduce sufficiently the FRCE with the actions taken pursuant to paragraph 15, the TSOs shall require changes in the active power production or consumption of power generating modules and demand units within their respective areas to reduce the FRCE as specified in paragraph 16. | [18 empty] | NA - CE and Nordic region only
4 | 0 | 0 | 152 | 14 | 14. The LFC block monitor shall be responsible for identifying any violation of the limits in paragraphs 12 and 13 and: | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 152 | 14(a) | (a) shall inform the other TSOs of the LFC block; and | [18 empty] | NA - As the single System Operator for the GB synchronous area, there is no-one else to inform in GB LFC block.
4 | 0 | 0 | 152 | 14(b) | (b) together with the TSOs of the LFC block shall implement coordinated actions to reduce the FRCE which shall be specified in the LFC block operational agreement. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 152 | 15 | 15. For the cases referred to in paragraphs 11 to 13 all the TSOs of each synchronous area shall specify in the synchronous area operational agreement the actions to enable the TSOs of a LFC block to actively reduce the frequency deviation with the cross-border activation of reserves. In the cases referred to in paragraphs 11 to 13 the TSOs of the synchronous area shall endeavour to enable the TSOs of the concerned LFC block to reduce their FRCE. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 152 | 16 | 16. The TSOs of a LFC block shall specify, in the LFC block operational agreement, measures to reduce the FRCE by means of changes in the active power production or consumption of power generating modules and demand units within their area. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 153 | 0 | FCR dimensioning
4 | 0 | 0 | 153 | 1 | 1. All TSOs of each synchronous area shall determine at least annually the reserve capacity on FCR required for the synchronous area and the initial FCR obligation of each TSO in accordance with paragraph 2. | 1 | 0 | 1 | 0 | 0 | 0 | 0 | [11 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 153 | 2 | 2. All TSOs of each synchronous area shall specify dimensioning rules in the synchronous area operational agreement in accordance with the following criteria: | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 153 | 2(a) | (a) the reserve capacity on FCR required for the synchronous area shall cover at least the reference incident and, for the CE and Nordic synchronous areas, the results of the probabilistic dimensioning approach for FCR carried out pursuant to point (c); | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 153 | 2(b) | (b) the TSOs of a synchronous area shall determine the size of the reference incident in accordance with the following conditions: | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 153 | 2(b)(i) | (i) for the CE synchronous area, the reference incident shall be 3000 MW in positive direction and 3000 MW in negative direction; | [18 empty] | NA - only applies to CE region.
4 | 0 | 0 | 153 | 2(b)(ii) | (ii) for the GB, IE/NI, and Nordic synchronous areas, the reference incident shall be the largest imbalance that may result from an instantaneous change of active power such as that of a single power generating module, single demand facility, or single HVDC interconnector or from a tripping of an AC-line, or it shall be the maximum instantaneous loss of active power consumption due to the tripping of one or two connection points. The reference incident shall be determined separately for positive and negative direction. | X |  | X | [15 empty] | BC1.5.4
4 | 0 | 0 | 153 | 2(c ) | (c) for the CE and Nordic synchronous areas, all TSOs of the synchronous area shall have the right to define a probabilistic dimensioning approach for FCR taking into account the pattern of load, generation and inertia and synthetic inertia as well as the available means to deploy minimum inertia in real-time in accordance with the methodology referred to in Article 39 with the aim of reducing the probability of insufficient FCR to below or equal to once in 20 years; and | [18 empty] | NA- only applies to CE and Nordic regions
4 | 0 | 0 | 153 | 2(d) | (d) the shares of the reserve capacity on FCR required for each TSO as initial FCR obligation shall be based on the sum of the net generation and consumption of its area divided by the sum of net generation and consumption of the synchronous area over a period of one year. | [18 empty] | NA - as NGET is the single system Operator in GB therefore no requirement to share FCR capacity between TSOs.
4 | 0 | 0 | 154 | 0 | FCR technical minimum requirements
4 | 0 | 0 | 154 | 1 | 1. Each reserve connecting TSO shall ensure that the FCR corresponds to the properties listed for its synchronous area in Table 1 of Annex V applying to all FCR providing units and FCR providing groups consistent with the values. | GC0114 BC4.2.1 | [17 empty] | The existing requirements of Grid Code CC.6.3.7 align with Table 1 of Annex V.
4 | 0 | 0 | 154 | 2 | 2. All TSOs of a synchronous area shall have the right to specify, in the synchronous area operational agreement, common additional properties of the FCR required to ensure operational security in the synchronous area, by means of a set of technical parameters and within the ranges in Article 15(2)(d) of Commission Regulation No (EU) 2016/631 and Article 27 and 28 of Commission Regulation No (EU) 2016/1388. Those common additional properties of FCR shall take into account the installed capacity, structure and pattern of consumption and generation of the synchronous area. The TSOs shall apply a transitional period for the introduction of additional properties, defined in consultation with the affected FCR providers. | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.2 | [17 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 154 | 3 | 3. The reserve connecting TSO shall have the right to set out additional requirements for FCR providing groups within the ranges in Article 15(2)(d) of Commission Regulation No (EU) 2016/631 and Article 27 and 28 of Commission Regulation No (EU) 2016/1388 in order to ensure operational security. Those additional requirements shall be based on technical reasons such as the geographical distribution of the power generating modules or demand units belonging to an FCR providing group. The FCR provider shall ensure that the monitoring of the FCR activation of the FCR providing units within a reserve providing group is possible. | BC3 C.C 6.3.6-6.3.7 | [17 empty] | BC3 C.C 6.3.6-6.3.7
4 | 0 | 0 | 154 | 4 | 4. To ensure operational security, the reserve connecting TSO shall have the right to exclude FCR providing groups from the provision of FCR based on technical arguments such as the geographical distribution of the power generating modules or demand units belonging to an FCR providing group. | BC3 C.C 6.3.6-6.3.7 | [17 empty] | BC3 C.C 6.3.6-6.3.7
4 | 0 | 0 | 154 | 5 | 5. Each FCR providing unit and each FCR providing group shall have only one reserve connecting TSO. | BC3 C.C 6.3.6-6.3.7 | [17 empty] | BC3 C.C 6.3.6-6.3.7
4 | 0 | 0 | 154 | 6 | 6. Each FCR providing unit and each FCR providing group shall comply with the properties required for FCR in Table 1 of Annex V and with any additional properties or requirements specified in accordance with paragraphs 2 and 3 and activate the agreed FCR by means of a proportional governor reacting to frequency deviations or alternatively based on a monotonic piecewise linear power-frequency characteristic in case of relay activated FCR. They shall be capable of activating FCR within the frequency ranges specified in Article 13(1) of Commission Regulation No (EU) 2016/631. | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 7 | 7. Each TSO of the CE synchronous area shall ensure that the combined reaction of FCR of a LFC area comply with the following requirements: | [18 empty] | NA - CE region only
4 | 0 | 0 | 154 | 7(a) | (a) the activation of FCR shall not be artificially delayed and begin as soon as possible after a frequency deviation; | [18 empty] | NA - CE region only
4 | 0 | 0 | 154 | 7(b) | (b) in case of a frequency deviation equal to or larger than 200 mHz, at least 50 % of the full FCR capacity shall be delivered at the latest after 15 seconds; | [18 empty] | NA - CE region only
4 | 0 | 0 | 154 | 7(c ) | (c) in case of a frequency deviation equal to or larger than 200 mHz, 100 % of the full FCR capacity shall be delivered at the latest after 30 seconds; | [18 empty] | NA - CE region only
4 | 0 | 0 | 154 | 7(d) | (d) in case of a frequency deviation equal to or larger than 200 mHz, the activation of the full FCR capacity shall rise at least linearly from 15 to 30 seconds; and | [18 empty] | NA - CE region only
4 | 0 | 0 | 154 | 7(e ) | (e) in case of a frequency deviation smaller than 200 mHz the related activated FCR capacity shall be at least proportional with the same time behaviour referred to in points (a) to (d). | [18 empty] | NA - CE region only
4 | 0 | 0 | 154 | 8 | 8. Each reserve connecting TSO shall monitor its contribution to the FCP and its FCR activation with respect to its FCR obligation, including FCR providing units and FCR providing groups. Each FCR provider shall make available to the reserve connecting TSO, for each of its FCR providing units and FCR providing groups, at least the following information: | BC3 C.C 6.3.6-6.3.7 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 8(a) | (a) time-stamped status indicating if FCR is on or off; | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 8(b) | (b) time-stamped active power data needed to verify FCR activation. which shall include time-stamped instantaneous active power; | GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 8(c ) | (c) droop of the governor for type C and type D power generating modules as defined in Article 5 of Commission Regulation No (EU) 2016/631 acting as FCR providing units, or its equivalent parameter for FCR providing groups consisting of type A and/or type B power generating modules as defined in Article 5 of Commission Regulation No (EU) 2016/631, and/or demand units with demand response active power control as defined in Article 28 of Commission Regulation No (EU) 2016/1388. | GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 9 | 9. Each FCR provider shall have the right to aggregate the respective data for more than one FCR providing unit if the maximum power of the aggregated units is below 1.5 MW and a clear verification of activation of FCR is possible. | C.C6.3.7 GC0114 BC 4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 10 | 10. At the request of the reserve connecting TSO, the FCR provider shall make the information listed in paragraph 9 available in real-time, with a time resolution of at least 10 seconds. | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 154 | 11 | 11. At the request of the reserve connecting TSO and where necessary for the verification of the activation of FCR, a FCR provider shall make available the data listed in paragraph 9 concerning technical installations that are part of the same FCR providing unit. | BC3 C.C 6.3.6-6.3.7 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 155 | 0 | FCR prequalification process | BC3 C.C 6.3.6-6.3.7 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 155 | 1 | 1. By 12 months after entry into force of this regulation, each TSO shall develop an FCR prequalification process and shall make publicly available the details of the FCR prequalification process. | GC0114 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 155 | 2 | 2. A potential FCR provider shall demonstrate to the reserve connecting TSO that it complies with the technical and availability requirements set out in Article 154 by completing successfully the prequalification process of potential FCR providing units or FCR providing groups, described in paragraphs 3 to 6 of this Article. | BC3 C.C 6.3.6-6.3.7 GC0114 | [17 empty] | GC0114 BC4
4 | 0 | 0 | 155 | 3 | 3. A potential FCR provider shall submit a formal application to the reserve connecting TSO together with the required information of potential FCR providing units or FCR providing groups. Within 8 weeks from receipt of the application, the reserve connecting TSO shall confirm whether the application is complete. Where the reserve connecting TSO considers that the application is incomplete, the potential FCR provider shall submit the additional required information within 4 weeks from receipt of the request for additional information. Where the potential FCR provider does not supply the requested information within that deadline, the application shall be deemed withdrawn. | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.1 | [17 empty] | GC0114 BC4
4 | 0 | 0 | 155 | 4 | 4. Within 3 months of confirmation that the application is complete, the reserve connecting TSO shall evaluate the information provided and decide whether the potential FCR providing units or FCR providing groups meet the criteria for an FCR prequalification. The reserve connecting TSO shall notify its decision to the potential FCR provider. | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.1 | [17 empty] | GC0114 BC4
4 | 0 | 0 | 155 | 5 | 5. Where the compliance with certain requirements of this Regulation has already been verified by the reserve connecting TSO, it will be recognised in the prequalification | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.1 | [17 empty] | GC0114 BC4.1 "Where the Connection Conditions or European Connection Conditions require the capability as a condition of connection, the connection application shall be understood to fulfil this formal application.". The intention was that any connection compliance processes could be used in prequalification to avoid a duplicate process.
4 | 0 | 0 | 155 | 6 | 6. The qualification of FCR providing units or FCR providing groups shall be reassessed: | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.1.1 | [17 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 155 | 6(a) | (a) at least once every five years; and | BC3 C.C 6.3.6-6.3.7 GC0114 BC4.1.1 | [17 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 155 | 6(b) | (a) in case the technical or availability requirements or the equipment have changed. | GC0114 BC4.1.1 | [17 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 156 | 0 | FCR provision
4 | 0 | 0 | 156 | 1 | 1. Each TSO shall ensure the availability of at least its FCR obligations agreed between all TSOs of the same synchronous area in accordance with Articles 153, 163, 173 and 174. | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 2 | 2. All TSOs of a synchronous area shall determine, at least on an annual basis, the size of the K-factor of the synchronous area, taking into account the following factors : | BC3 C.C 6.3.6-6.3.7 | [17 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 156 | 2(a) | (a) the reserve capacity on FCR divided by the maximum steady-state frequency deviation; | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 156 | 2(b) | (b) the auto-control of generation; | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 156 | 2(c ) | (c) the self-regulation of load, taking into account the contribution in accordance with Articles 27 and 28 of Commission Regulation No (EU) 2016/1388; | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 156 | 2(d) | (d) the frequency response of HVDC interconnectors referred to in Article 172; and, | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 156 | 2(e) | (e) the LFSM and FSM activation in accordance with Articles 13 and 15 of Commission Regulation No (EU) 2016/631. | [18 empty] | NGET has responsibility to manage this requirement.
4 | 0 | 0 | 156 | 3 | 3. All TSOs of a synchronous area consisting of more than one LFC area shall, in the synchronous area operational agreement, determine the shares of the K-factor for each LFC area, which shall be based on at least: | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 3(a) | (a) the initial FCR obligations; | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 3(b) | (b) auto-control of generation; | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 3(c) | (c) the self-regulation of load; | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 3(d) | (d) frequency coupling via HVDC between synchronous areas; | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 3(e) | (e) exchange of FCR. | [18 empty] | NA as only NGET reponsible in GB synchronous area
4 | 0 | 0 | 156 | 4 | 4. An FCR provider shall guarantee the continuous availability of FCR, with the exception of a forced outage of a FCR providing unit, during the period of time in which it is obliged to provide FCR. | GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 156 | 5 | 5. Each FCR provider shall inform its reserve connecting TSO, as soon as possible, about any changes in the actual availability of its FCR providing unit and/or its FCR providing group, in whole or in part, relevant for the results of prequalification. | GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 156 | 6 | 6. Each TSO shall ensure, or shall require its FCR providers to ensure that the loss of a FCR providing unit does not endanger the system security by: | [18 empty] | Managed by NGET as detailed in Synchronous Area Methodology. No additional requirement for FCR providers.
4 | 0 | 0 | 156 | 6(a) | (a) limiting the share of the FCR provided per FCR providing unit to 5 % of the reserve capacity of FCR required for each of the whole CE and Nordic synchronous areas; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 6(b) | (b) excluding the FCR provided by the unit defining the reference incident of the synchronous area from the dimensioning process for GB, IE/NI and Nordic synchronous areas; and | [18 empty] | Managed by NGET as detailed in Synchronous Area Methodology. No additional requirement for FCR providers.
4 | 0 | 0 | 156 | 6(c ) | (c) replacing the FCR which is made unavailable due to a forced outage or the unavailability of an FCR providing unit or FCR providing group as soon as technically possible and in accordance with the conditions that shall be defined by the reserve connecting TSO. | [18 empty] | Managed by NGET as detailed in Synchronous Area Methodology. No additional requirement for FCR providers.
4 | 0 | 0 | 156 | 7 | 7. An FCR providing unit or FCR providing group with an energy reservoir that does not limit its capability to provide FCR shall activate its FCR for as long as the frequency deviation persists. For the GB and IE/NI synchronous areas, a FCR providing unit or FCR providing group with an energy reservoir that does not limit its capability to provide FCR shall activate its FCR until it activates its FRR or for the period specified in the synchronous area operational agreement. | [18 empty] | Synchronous Area Operational Methodology currently under consultation - no new requirements identified as yet.
4 | 0 | 0 | 156 | 8 | 8. A FCR providing unit or FCR providing group with an energy reservoir that limits its capability to provide FCR shall activate its FCR for as long as the frequency deviation persists, unless its energy reservoir is exhausted in either the positive or negative direction. For the GB and IE/NI synchronous areas, a FCR providing unit or FCR providing group with an energy reservoir that limits its capability to provide FCR shall activate its FCR until it activates its FRR or for the period specified in the synchronous area operational agreement. | [18 empty] | Synchronous Area Operational Methodology currently under consultation - no new requirements identified as yet.
4 | 0 | 0 | 156 | 9 | 9. For the CE and Nordic synchronous areas, each FCR provider shall ensure that the FCR from its FCR providing units or groups with limited energy reservoirs are continuously available during normal state. For the CE and Nordic synchronous areas, as of triggering the alert state and during the alert state, each FCR provider shall ensure that the FCR from its FCR providing units or groups with limited energy reservoirs are able to fully activate FCR continuously for a time period to be defined pursuant to paragraphs 10 and 11. Where no period has been determined pursuant to paragraphs 10 and 11, each FCR provider shall ensure that the FCR from its FCR providing units or groups with limited energy reservoirs are able to fully activate FCR continuously for at least 15 minutes or, in case of frequency deviations that are smaller than a frequency deviation requiring full FCR activation, for an equivalent length of time, or for a period defined by each TSO, which shall not be greater than 30 or smaller than 15 minutes. | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 10 | 10. For the CE and Nordic synchronous areas, all TSOs shall develop a proposal concerning the minimum activation period to be ensured by FCR providers in the CE and Nordic synchronous areas. The period determined shall not be greater than 30 or smaller than 15 minutes. The proposal shall take full account of the results of the cost–benefit analysis conducted pursuant to paragraph 11. | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 11 | 11. By [12months] after entry into force of this regulation, all TSOs of the CE and Nordic synchronous areas shall propose assumptions and methodology for a cost-benefit analysis to be conducted, in order to assess the time period required for FCR providing units or groups with limited energy reservoirs to remain available during alert state. By [18 months] after approval of the assumptions and methodology by all regulatory authorities of the concerned region, the TSOs of the CE and Nordic synchronous areas shall submit the results of their cost-benefit analysis, suggesting a time period which shall not be greater than 30 or smaller than 15 minutes. The cost-benefit analysis shall take into account at least: | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 11(a) | (a) experiences gathered with different time frames and shares of emerging technologies in different LFC blocks; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 11(b) | (b) the impact of a defined time period on the total cost of FCR reserves in the synchronous area; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 11(c ) | (c) the impact of a defined time period on system stability risks, in particular through prolonged or repeated frequency events; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 11(d) | (d) the impact on system stability risks and total cost of FCR reserves of increasing total volume of FCR reserves; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 11(e ) | (e) the impact of technological developments on costs of availability periods for FCR from its FCR providing units or groups with limited energy reservoirs. | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 156 | 12 | 12. The FCR provider shall specify the limitations of the energy reservoir of its FCR providing units or FCR providing groups in the prequalification process in accordance with Article 155. | GC0114 BC4.2.1 | [17 empty] | GC0114 BC4.2.1
4 | 0 | 0 | 156 | 13 | 13. A FCR provider using FCR providing units or FCR providing group with an energy reservoir that limits their capability to provide FCR shall ensure the recovery of the energy reservoirs in the positive or negative directions in accordance with the following criteria: | [18 empty] | Specific requirements set out below.
4 | 0 | 0 | 156 | 13(a) | (a) for the GB and IE/NI synchronous areas, the FCR provider shall use the methods specified in the synchronous area operational agreement; | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 156 | 13(b) | (b) for the CE and Nordic synchronous areas, the FCR provider shall ensure the recovery of the energy reservoirs as soon as possible, within 2 hours after the end of the alert state. | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 157 | 0 | FRR dimensioning
4 | 0 | 0 | 157 | 1 | 1. All TSOs of a LFC Block shall set out FRR dimensioning rules in the LFC Block operational agreement. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 157 | 2 | 2. The FRR dimensioning rules shall include at least the following: | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 157 | 2(a) | (a) all TSOs of a LFC block in the CE and Nordic synchronous areas shall determine the required reserve capacity on FRR of the LFC block based on consecutive historical records comprising at least the historical LFC block imbalance values. The sampling of those historical records shall cover at least the time to restore frequency. The time period considered for those records shall be representative and include at least one full year period ending not earlier than 6 months before the calculation date; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 157 | 2(b) | (b) all TSOs of a LFC block in the CE and Nordic synchronous areas shall determine the reserve capacity on FRR of the LFC block sufficient to respect the current FRCE target parameters in Article 128 for the time period referred to in point (a) based at least on a probabilistic methodology. In using that probabilistic methodology, the TSOs shall take into account the restrictions defined in the agreements for the sharing or exchange of reserves due to possible violations of operational security and the FRR availability requirements. All TSOs of a LFC block shall take into account any expected significant changes to the distribution of LFC block imbalances or take into account other relevant influencing factors relative to the time period considered; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 157 | 2(c ) | (c) all TSOs of a LFC block shall determine the ratio of automatic reserve capacity on FRR, manual reserve capacity on FRR, the automatic FRR full activation time and manual FRR full activation time in order to comply with the requirement of paragraph (b). For that purpose, the automatic FRR full activation time of a LFC block and the manual FRR full activation time of the LFC block shall not be more than the time to restore frequency; | [18 empty] | NA. As set out in the LFC block operational agreement there is no aFRP in GB Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 157 | 2(d) | (d) the TSOs of a LFC block shall determine the size of the reference incident which shall be the largest imbalance that may result from an instantaneous change of active power of a single power generating module, single demand facility, or single HVDC interconnector or from a tripping of an AC line within the LFC block; | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(e ) | (e) all TSOs of a LFC block shall determine the positive reserve capacity on FRR, which shall not be less than the positive dimensioning incident of the LFC block; | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(f) | (f) all TSOs of a LFC block shall determine the negative reserve capacity on FRR, which shall not be less than the negative dimensioning incident of the LFC block; | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(g) | (g) all TSOs of a LFC block shall determine the reserve capacity on FRR of a LFC block, any possible geographical limitations for its distribution within the LFC block and any possible geographical limitations for any exchange of reserves or sharing of reserves with other LFC blocks to comply with the operational security limits; | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(h) | (h) all TSOs of a LFC block shall ensure that the positive reserve capacity on FRR or a combination of reserve capacity on FRR and RR is sufficient to cover the positive LFC block imbalances for at least 99 % of the time, based on the historical records referred to in point (a); | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(i) | (i) all TSOs of a LFC block shall ensure that the negative reserve capacity on FRR or a combination of reserve capacity on FRR and RR is sufficient to cover the negative LFC block imbalances for at least 99 % of the time, based on the historical record referred to in point (a); | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(j) | (j) all TSOs of a LFC block may reduce the positive reserve capacity on FRR of the LFC block resulting from the FRR dimensioning process by concluding a FRR sharing agreement with other LFC blocks in accordance with provisions in Title 8. The following requirements shall apply to that sharing agreement: | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(j)(i) | (i) for the CE and Nordic synchronous areas, the reduction of the positive reserve capacity on FRR of a LFC block shall be limited to the difference, if positive, between the size of the positive dimensioning incident and the reserve capacity on FRR required to cover the positive LFC block imbalances during 99 % of the time, based on the historical records referred to in point (a). The reduction of the positive reserve capacity shall not exceed 30 % of the size of the positive dimensioning incident; | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 157 | 2(j)(ii) | (ii) for the GB and IE/NI synchronous areas, the positive reserve capacity on FRR and the risk of non-delivery due to sharing shall be assessed continually by the TSOs of the LFC block; | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(k) | (k) all TSOs of a LFC block may reduce the negative reserve capacity on FRR of the LFC block, resulting from the FRR dimensioning process by concluding a FRR sharing agreement with other LFC blocks in accordance with the provisions of Title 8. The following requirements shall apply to that sharing agreement: | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 2(k)(i) | (i) for the CE and Nordic synchronous areas, the reduction of the negative reserve capacity on FRR of a LFC block shall be limited to the difference, if positive, between the size of the negative dimensioning incident and the reserve capacity on FRR required to cover the negative LFC block imbalances during99 % of the time, based on the historical records referred to in point (a); | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 157 | 2(k)(ii) | (ii) for the GB and IE/NI synchronous areas, the negative reserve capacity on FRR and the risk of non-delivery due to sharing shall be assessed continually by the TSOs of the LFC block. | BC1.5.4 | [17 empty] | BC1.5.4
4 | 0 | 0 | 157 | 3 | 3. All TSOs of a LFC block where the LFC block comprises more than one TSO shall set out, in the LFC block operational agreement, the specific allocation of responsibilities between the TSOs of the LFC areas for the implementation of the obligations established in paragraph 2. | [18 empty] | NA as only applicable to CE and Nordic regions
4 | 0 | 0 | 157 | 4 | 4. All TSOs of a LFC block shall have sufficient reserve capacity on FRR at any time in accordance with the FRR dimensioning rules. The TSOs of a LFC block shall specify in the LFC block operational agreement an escalation procedure for cases of severe risk of insufficient reserve capacity on FRR in the LFC block. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 158 | 0 | FRR minimum technical requirements
4 | 0 | 0 | 158 | 1 | 1. The FRR minimum technical requirements shall be the following:
4 | 0 | 0 | 158 | 1(a) | (a) each FRR providing unit and each FRR providing group shall be connected to only one reserve connecting TSO; | BC2.6 | [17 empty] | NA - only possible to connect to single System Operator in GB.
4 | 0 | 0 | 158 | 1(b) | (b) a FRR providing unit or FRR providing group shall activate FRR in accordance with the setpoint received from the reserve instructing TSO; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(c ) | (c) the reserve instructing TSO shall be the reserve connecting TSO or a TSO designated by the reserve connecting TSO in an FRR exchange agreement pursuant to Article 165(3) or Article 171(4); | BC2.6 | [17 empty] | NGET to develop SO-SO agreements
4 | 0 | 0 | 158 | 1(d) | (d) a FRR providing unit or FRR providing group for automatic FRR shall have an automatic FRR activation delay not exceeding 30 seconds; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(e ) | (e) a FRR provider shall ensure that the FRR activation of the FRR providing units within a reserve providing group can be monitored. For that purpose, the FRR provider shall be capable of supplying to the reserve connecting TSO and the reserve instructing TSO real-time measurements of the connection point or another point of interaction agreed with the reserve connecting TSO concerning: | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(e )(i) | (i) time-stamped scheduled active power output; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(e )(ii) | (ii) time-stamped instantaneous active power for: | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(e )(ii) | (A) each FRR providing unit; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(e )(ii) | (B) each FRR providing group; and | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(e )(ii) | (C) each power generating module or demand unit of a FRR providing group with a maximum active power output larger than or equal to 1.5 MW; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(f) | (f) a FRR providing unit or FRR providing group for automatic FRR shall be capable of activating its complete automatic reserve capacity on FRR within the automatic FRR full activation time; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(g) | (g) a FRR providing unit or FRR providing group for manual FRR shall be capable of activating its complete manual reserve capacity on FRR within the manual FRR full activation time; | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(h) | (h) a FRR provider shall fulfil the FRR availability requirements ; and | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 1(i) | (i) a FRR providing unit or FRR providing group shall fulfil the ramping rate requirements of the LFC block. | GC0114 BC4.3.1 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 2 | 2. All TSOs of a LFC block shall specify FRR availability requirements and requirements on the control quality of FRR providing units and FRR providing groups for their LFC block in the LFC block operational agreement pursuant to Article 119. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 158 | 3 | 3. The reserve connecting TSO shall adopt the technical requirements for the connection of FRR providing units and FRR providing groups to ensure the safe and secure delivery of FRR. | BC2.6 | [17 empty] | NGET should specify the technical requirements for connection, these are set out in the Grid Code and include the provision of mandatory services such as BM participation and mandatory frequency response.
4 | 0 | 0 | 158 | 4 | 4. Each FRR provider shall: | BC2.6 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 4(a) | (a) ensure that its FRR providing units and FRR providing groups fulfil the FRR technical minimum requirements, the FRR availability requirements and the ramping rate requirements in paragraphs 1 to 3; and | BC2.6 | [17 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 4(b) | (b) inform its reserve instructing TSO about a reduction of the actual availability of its FRR providing unit or its FRR providing group or a part of its FRR providing group as soon as possible. | [18 empty] | GC0114 BC 4.3.1
4 | 0 | 0 | 158 | 5 | 5. Each reserve instructing TSO shall ensure the monitoring of the compliance with the FRR minimum technical requirements in paragraph 1, the FRR availability requirements in paragraph 2, the ramping rate requirements in paragraph 1 and the connection requirements in paragraph 3 by its FRR providing units and FRR providing groups. | [18 empty] | NGEt has a responsibility to appropriately monitor the compliance with technical requirements
4 | 0 | 0 | 159 | 0 | FRR prequalification process | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 1 | 1. By 12 months after entry into force of this Regulation each TSO shall develop a FRR prequalification process and shall clarify and make publicly available its details. | GC0114 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 2 | 2. A potential FRR provider shall demonstrate to the reserve connecting TSO or the TSO designated by the reserve connecting TSO in the FRR exchange agreement that it complies with the FRR minimum technical requirements in Article 158(1), the FRR availability requirements in Article 158(2),the ramping rate requirements in Article 158(1) and the connection requirements in Article 158(3) by completing successfully the prequalification process of potential FRR providing units or FRR providing groups, described in paragraphs 3 to 6 of this Article. | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 3 | 3. A potential FRR provider shall submit a formal application to the relevant reserve connecting TSO or the designated TSO together with the required information of potential FRR providing units or FRR providing groups. Within 8 weeks from receipt of the application, the reserve connecting TSO or the designated TSO shall confirm whether the application is complete. Where the reserve connecting TSO or the designated TSO considers that the application is incomplete they shall request additional information and the potential FRR provider shall submit the additional required information within 4 weeks from the receipt of the request. Where the potential FRR provider does not supply the requested information within that deadline, the application shall be deemed to be withdrawn. | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 4 | 4. Within 3 months after the reserve connecting TSO or the designated TSO confirms that the application is complete, the reserve connecting TSO or the designated TSO shall evaluate the information provided and decide whether the potential FRR providing units or FRR providing groups meet the criteria for a FRR prequalification. The reserve connecting TSO or the designated TSO shall notify their decision to the potential FRR provider. | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 5 | 5. The qualification of FRR providing units or FRR providing groups by the reserve connecting TSO or the designated TSO shall be valid for the entire LFC Block. | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 6 | 6. The qualification of FRR providing units or FRR providing groups shall be reassessed: | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 6(a) | (a) at least once every five years; and | BC2.6 | [17 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 6(b) | (b) where the technical or availability requirements or the equipment have changed. | [18 empty] | GC0114 BC 4.1.1
4 | 0 | 0 | 159 | 7 | 7. To ensure operational security, the reserve connecting TSO shall have the right to exclude FRR providing groups from the provision of FRR based on technical arguments such as the geographical distribution of the power generating modules or demand units belonging to a FRR providing group.
4 | 0 | 0 | 160 | 0 | Replacement reserves dimensioning | BC2.6
4 | 0 | 0 | 160 | 1 | 1. All TSOs of an LFC block shall have the right to implement a reserve replacement process.
4 | 0 | 0 | 160 | 2 | 2. To comply with the FRCE target parameters referred to in Article 128, all TSOs of a LFC block with a RRP, performing a combined dimensioning process of FRR and RR to fulfil the requirements of Article 157(2), shall define RR dimensioning rules in the LFC block operational agreement. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 160 | 3 | 3. The RR dimensioning rules shall comprise at least the following requirements:
4 | 0 | 0 | 160 | 3(a) | (a) for the Nordic and CE synchronous areas there shall be sufficient positive reserve capacity on RR to restore the required amount of positive FRR. For the GB and IE/NI synchronous areas there shall be sufficient positive reserve capacity on RR to restore the required amount of positive FCR and positive FRR; | [18 empty] | NA - only applies to CE and nordic regions
4 | 0 | 0 | 160 | 3(b) | (b) for the Nordic and CE synchronous areas, there shall be sufficient negative reserve capacity on RR to restore the required amount of negative FRR. For the GB and IE/NI synchronous areas, there shall be sufficient negative reserve capacity on RR to restore the required amount of negative FCR and negative FRR; | [18 empty] | NA - only applies to CE and nordic regions
4 | 0 | 0 | 160 | 3(c ) | (c) there shall be sufficient reserve capacity on RR, where this is taken into account to dimension the reserve capacity on FRR in order to respect the FRCE quality target for the period of time concerned; and
4 | 0 | 0 | 160 | 3(d) | (d) compliance with the operational security within a LFC block to determine the reserve capacity on RR.
4 | 0 | 0 | 160 | 4 | 4. All TSOs of an LFC block may reduce the positive reserve capacity on RR of the LFC block, resulting from the RR dimensioning process, by developing a RR sharing agreement for that positive reserve capacity on RR with other LFC blocks in accordance with the provisions of Title 8 of Part IV. The control capability receiving TSO shall limit the reduction of its positive reserve capacity on RR in order to: | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 4(a) | (a) guarantee that it can still meet its FRCE target parameters set out in Article 128; | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 4(b) | (b) ensure that operational security is not endangered; and | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 4(c ) | (c) ensure that the reduction of the positive reserve capacity on RR does not exceed the remaining positive reserve capacity on RR of the LFC block. | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 5 | 5. All TSOs of a LFC block may reduce the negative reserve capacity on RR of the LFC block, resulting from the RR dimensioning process, by developing a RR sharing agreement for that negative reserve capacity on RR with other LFC blocks in accordance with the provisions of Title 8 of Part IV. The control capability receiving TSO shall limit the reduction of its negative reserve capacity on RR in order to: | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 5(a) | (a) guarantee that it can still meet its FRCE target parameters set out in Article 128; | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 5(b) | (a) ensure that operational security is not endangered; and | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 5(c ) | (b) ensure that the reduction of the negative reserve capacity on RR does not exceed the remaining negative reserve capacity on RR of the LFC block. | [18 empty] | NGET may enter into sharing agreements with other TSOs.
4 | 0 | 0 | 160 | 6 | 2. Where a LFC block is operated by more than one TSO and if the process is necessary for the LFC block, all TSOs of that LFC block shall specify in the LFC block operational agreement the allocation of responsibilities between the TSOs of different LFC areas for the implementation of the dimensioning rules referred set out in paragraph 3. | [18 empty] | NA - as NGET is the single System Operator in GB
4 | 0 | 0 | 160 | 7 | 3. A TSO shall have sufficient reserve capacity on RR in accordance with the RR dimensioning rules at any time. The TSOs of a LFC block shall specify in the LFC block operational agreement an escalation procedure for cases of severe risk of insufficient reserve capacity on RR in the LFC block. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 161 | 0 | RR minimum technical requirements
4 | 0 | 0 | 161 | 1 | 1. RR providing units and RR providing groups shall comply with the following minimum technical requirements: | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(a) | (a) connection to only one reserve connecting TSO; | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(b) | (b) RR activation according to the setpoint received from the reserve instructing TSO; | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(c ) | (c) the reserve instructing TSO shall be the reserve connecting TSO or a TSO that shall be designated by the reserve connecting TSO in the RR exchange agreement pursuant to Article 165(3) or Article 171(4); | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(d) | (d) activation of complete reserve capacity on RR within the activation time defined by the Instructing TSO; | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(e ) | (e) de-activation RR according to the setpoint received from the reserve instructing TSO; | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(f) | (f) a RR provider shall ensure that the RR activation of the RR providing units within a reserve providing group can be monitored. For that purpose, the RR provider shall be capable of supplying to the reserve connecting TSO and the reserve instructing TSO real-time measurements of the connection point or another point of interaction agreed with the reserve connecting TSO concerning: | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(f)(i) | (i) the time-stamped scheduled active power output, for each RR providing unit and group and for each power generating module or demand unit of a RR providing group with a maximum active power output larger than or equal to 1.5 MW; | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(f)(ii) | (ii) the time-stamped instantaneous active power, for each RR providing unit and group, and for each power generating module or demand unit of a RR providing group with a maximum active power output larger than or equal to 1.5 MW; | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 1(g) | (g) fulfilment of the RR availability requirements. | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 2 | 2. All TSOs of a LFC block shall specify RR availability requirements and requirements on the control quality of RR providing units and RR providing groups in the LFC block operational agreement in accordance with Article 119. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 161 | 3 | 3. The reserve connecting TSO shall adopt the technical requirements for the connection of RR providing units and RR providing groups to ensure the safe and secure delivery of RR in the prequalification process description. | [18 empty] | GC0114
4 | 0 | 0 | 161 | 4 | 4. Each RR provider shall: | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 4(a) | (a) ensure that its RR providing units and RR providing groups fulfil the RR technical minimum requirements and the RR availability requirements referred to in paragraphs 1 to 3; and | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 4(b) | (b) inform its reserve instructing TSO about a reduction of the actual availability or a forced outage of its RR providing unit or its RR providing group or a part of its RR providing group as soon as possible. | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 161 | 5 | 5. Each reserve instructing TSO shall ensure compliance with the RR technical requirements, the RR availability requirements and the connection requirements referred to in this Article with regard to its RR providing units and RR providing groups. | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 162 | 0 | Replacement reserves prequalification process | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 162 | 1 | 1. Each TSO of a LFC block which has implemented a RRP shall develop a RR prequalification process within 12 months after entry into force of this Regulation and shall clarify and make publicly available the details thereof. | [18 empty] | GC0114 BC4.4.1
4 | 0 | 0 | 162 | 2 | 2. A potential RR provider shall demonstrate to the reserve connecting TSO or the TSO designated by the reserve connecting TSO in the RR exchange agreement that it complies with the RR technical minimum requirements, the RR availability requirements and the connection requirements referred to in Article 161 by completing successfully the prequalification process of potential RR providing units or RR providing groups, described in paragraphs 3 to 6. | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 162 | 3 | 3. A potential RR provider shall submit a formal application to the relevant reserve connecting TSO or the designated TSO together with the required information of potential RR providing units or RR providing groups. Within 8 weeks from receipt of the application, the reserve connecting TSO or the designated TSO shall confirm whether the application is complete. Where the reserve connecting TSO or the designated TSO considers that the application is incomplete, the potential RR provider shall submit the additional required information within 4 weeks from the receipt of the request for additional information. Where the potential RR provider does not supply the requested information within that deadline, the application shall be deemed withdrawn. | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 162 | 4 | 4. Within 3 months of confirmation of the completeness of the application, the reserve connecting TSO or the designated TSO shall evaluate the information provided and decide whether the potential RR providing units or RR providing groups meet the criteria for a RR prequalification. The reserve connecting TSO or the designated TSO shall notify its decision to the potential RR provider. | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 162 | 5 | 5. The qualification of RR providing units or RR providing groups shall be reassessed: | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 162 | 5(a) | (a) at least once every five years; and | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 162 | 5(b) | (b) where the technical or availability requirements or the equipment have changed. | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 162 | 6 | 6. To ensure operational security, the reserve connecting TSO shall have the right to reject the provision of RR by RR providing groups, based on technical arguments such as the geographical distribution of the power generating modules or demand units establishing a RR providing group. | [18 empty] | GC0114 BC4.1.1
4 | 0 | 0 | 173 | 0 | Exchange of FCR between synchronous areas
4 | 0 | 0 | 173 | 1 | 1. All TSOs of a synchronous area involved in a frequency coupling process shall have the right to use the FCR exchange process to exchange FCR between synchronous areas. | [18 empty] | NGET has the right to exchange FCR with other TSOs
4 | 0 | 0 | 173 | 2 | 2. All TSOs of synchronous areas involved in the exchange of FCR between synchronous areas shall organise that exchange so that the TSOs of one synchronous area receive from another synchronous area a share of the total reserve capacity on FCR required for their synchronous area pursuant to Article 153. | [18 empty] | NGET has the right to exchange FCR with other TSOs
4 | 0 | 0 | 173 | 3 | 3. The share of the total reserve capacity on FCR required for synchronous area where it is exchanged shall be provided in the second synchronous area in addition to the total reserve capacity on FCR required for that second synchronous area in accordance with Article 153. | [18 empty] | NGET has the right to exchange FCR with other TSOs
4 | 0 | 0 | 173 | 4 | 4. All TSOs of the synchronous area shall specify in the synchronous area operational agreement the limits for FCR exchange. | [18 empty] | Synchronous area operational agreement and LFC block operational agreement are currently under developed. Public consultation 23 July to 23 August here; https://consultations.entsoe.eu/
4 | 0 | 0 | 173 | 5 | 5. All TSOs of the involved synchronous areas shall draw up an FCR exchange agreement whereby they agree upon the exchange of FCR. | [18 empty] | NGET has the right to exchange FCR with other TSOs
4 | 0 | 0 | 182 | 0 | Reserve providing groups or units connected to the DSO grid
4 | 0 | 0 | 182 | 1 | 1. TSOs and DSOs shall cooperate in order to facilitate and enable the delivery of active power reserves by reserve providing groups or reserve providing units located in the distribution networks.
4 | 0 | 0 | 182 | 2 | 2. For the purposes of the prequalification processes for FCR in Article 155, FRR in Article 159 and RR in Article 162, each TSO shall develop and specify, in an agreement with its reserve connecting DSOs and intermediate DSOs, the terms of the exchange of information required for these prequalification processes for reserve providing units or groups located in the distributed networks and the delivery of active power reserves. The prequalification processes for FCR in Article 155, FRR in Article 159 and RR in Article 162 shall specify the information to be provided by the potential reserve providing units or groups, which shall include: | [17 empty] | X | Datqa exchange requirements being developed under GC0106
4 | 0 | 0 | 182 | 2(a) | (a) voltage levels and connection points of the reserve providing units or groups; | [17 empty] | X | GC0114 BC4.2.1, BC4.3.1, BC4.4.1
4 | 0 | 0 | 182 | 2(b) | (b) the type of active power reserves; | [18 empty] | GC0114 BC4.2.1, BC4.3.1, BC4.4.1
4 | 0 | 0 | 182 | 2(c ) | (c) the maximum reserve capacity provided by the reserve providing units or groups at each connection point; and | [18 empty] | GC0114 BC4.2.1, BC4.3.1, BC4.4.1
4 | 0 | 0 | 182 | 2(d) | (d) the maximum rate of change of active power for the reserve providing units or groups. | [18 empty] | GC0114 BC4.2.1, BC4.3.1, BC4.4.1
4 | 0 | 0 | 182 | 3 | 3. The prequalification process shall rely on the agreed timeline and rules concerning information exchanges and the delivery of active power reserves between the TSO, the reserve connecting DSO and the intermediate DSOs. The prequalification process shall have a maximum duration of three months from the submission of a complete formal application by the reserve providing unit or group. | [18 empty] | GC0114 BC4.2.1, BC4.3.1, BC4.4.1
4 | 0 | 0 | 182 | 4 | 4. During the prequalification of a reserve providing unit or group connected to its distribution network, each reserve connecting DSO and each intermediate DSO, in cooperation with the TSO, shall have the right to set limits to or exclude the delivery of active power reserves located in its distribution network, based on technical reasons such as the geographical distribution of the reserve providing units and reserve providing groups. | [17 empty] | X
4 | 0 | 0 | 182 | 5 | 5. Each reserve connecting DSO and each intermediate DSO shall have the right, in cooperation with the TSO, to set, before the activation of reserves, temporary limits to the delivery of active power reserves located in its distribution system. The respective TSOs shall agree with their reserve connecting DSOs and intermediate DSOs on the applicable procedures. | [17 empty] | X
Note on B1: ZERO("0") is allcated for TITLES row.
Note on C1: ZERO("0") is allcated for TITLES row.
Note on D1: ZERO("0") is allcated for TITLES row.
Note on E1: ZERO("0") is allcated for TITLES row.
Note on I1: Distribution Code [ENA]
Note on J1: Security and Quality of Supply Standards [NGET]
Note on K1: System Operator Transmission Code [NGET]
Note on L1: Balancing & Settlement Code
Note on M1: Connection & Use of System Code [NGET]

## Relevant prequalification art.
Article
3
45
48
152
153
154
155
156
157
158
159
160
161
162
182