## Note
Note to 2018 ETYS Appendix B
Where overhead line circuits are strung on the same transmission towers, their proximity to each other can lead to current and voltage in one circuit inducing current and voltage in the other. This mutual coupling between circuits can affect the Positive Phase Sequence parameters of overhead line circuits. The Positive Phase Sequence values in these tables are taken from PowerFactory models used by National Grid for 2018 ETYS analysis which include these mutual coupling effects.
When using power analysis applications that are not capable of modelling mutual coupling, it may be necessary to adjust overhead line parameters in line with accepted industry assumptions. These adjustments are likely to only have minor impact on power flow but can have material impact on voltages over larger networks. ETYS data users are advised to contact National Grid for advice if intending to use this data in this way.

## Menu
Electricity Ten Year Statement (ETYS) 2018
Appendix B - Supplementary Technical Data
Table | Title
B.1.1a | SHE Transmission Index of Substation Codes
B.1.1b | SPT Index of Substation Codes
B.1.1c | NGET Index of Substation Codes
B.1.1d | OFTO Index of Substation Codes
B.2.1a | SHE Transmission Circuits 2018/19
B.2.1b | SPT Circuits 2018/19
B.2.1c | NGET Circuits 2018/19
B.2.1d | OFTO Circuits 2018/19
B.2.2a | SHE Transmission Circuit Changes 2019/20 to 2027/28
B.2.2b | SPT Transmission Circuit Changes 2019/20 to 2027/28
B.2.2c | NGET Transmission Circuit Changes 2019/20 to 2027/28
B.2.2d | OFTO Circuit Changes 2019/20 to 2027/28
B.3.1a | SHE Transmission Transformers Winter 2018/19
B.3.1b | SPT Transformers Winter 2018/19
B.3.1c | NGET Transformers Winter 2018/19
B.3.1d | OFTO Transformers 2018/19
B.3.2a | SHE Transmission Transformer Changes 2019/20 to 2027/28
B.3.2b | SPT Transformer Changes 2019/20 to 2027/28
B.3.2c | NGET Transformer Changes 2019/20 to 2027/28
B.3.2d | OFTO Transformer Changes 2019/20 to 2027/28
B.4.1a | SHE Transmission Reactive Compensation Equipment Winter 2018/19
B.4.1b | SPT Reactive Compensation Equipment Winter 2018/19
B.4.1c | NGET Reactive Compensation Equipment Winter 2018/19
B.4.1d | OFTO Reactive Compensation Equipment Winter 2018/19
B.4.2a | SHE Transmission Reactive Compensation Equipment Changes 2019/20 to 2027/28
B.4.2b | SPT Reactive Compensation Equipment Changes 2019/20 to 2027/28
B.4.2c | NGET Reactive Compensation Equipment Changes 2019/20 to 2027/28
B.4.2d | OFTO Reactive Compensation Equipment Changes 2019/20 to 2027/28

## B-1-1a
Table B.1.1a - SHE Transmission Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
ABBA | Aberdeen Bay | 132
ABBA | Aberdeen Bay | 66
ABBA | Aberdeen Bay | 13
ABED | Aberarder | 132
ABED | Aberarder | 33
ABNE | Abernethy | 132
ABNE | Abernethy | 33
ACHL | Achlachan | 33
ACHR | A-Cruach | 132
ACHR | A-Cruach | 33
AIGA | Aigas | 132
AIGA | Aigas | 11
ALNE | Alness | 132
ALNE | Alness | 33
ALYT | Alyth | 400
ALYT | Alyth | 275
ALYT | Alyth | 33
AMUL | Amulree | 132
ANSU | An Suidhe | 132
ANSU | An Suidhe | 33
ARBR | Arbroath | 132
ARBR | Arbroath | 33
ARDK | Ardkinglas | 132
ARDK | Ardkinglas | 33
ARDR | Ardross | 275
ARMO | Ardmore | 132
ARMO | Ardmore | 33
ARNI | Arnish | 132
ARNI | Arnish | 33
BADA | Bad A Cheo | 33
BEAT | Beatrice Wind | 400
BEAU | Beauly | 400
BEAU | Beauly | 275
BEAU | Beauly | 132
BEAU | Beauly | 33
BEIN | Beinneun | 132
BEIN | Beinneun | 33
BENA | Ben Aketil | 33
BERB | Berryburn | 275
BERB | Berryburn | 33
BETH | Beinn Tharsuinn | 33
BEWF | Beaw Field | 132
BEWF | Beaw Field | 33
BHLA | Bhlaraidh | 132
BHLA | Bhlaraidh | 33
BIHI | Birkhill | 132
BLHI | Blackhillock | 400
BLHI | Blackhillock | 275
BLHI | Blackhillock | 132
BLHI | Blackhillock | 33
BLRH | Blary Hill | 33
BOAG | Boat of Garten | 132
BOAG | Boat of Garten | 33
BOYN | Boyndie | 33
BRCW | Braco West | 275
BRCW | Braco West | 33
BRDU | Braes of Doune Wind | 33
BREC | Brechin | 132
BRID | Bridge of Dun | 132
BRID | Bridge of Dun | 33
BRMS | Brimms Tidal | 33
BROA | Broadford | 132
BROA | Broadford | 33
BROR | Brora | 132
BROR | Brora | 33
BTUI | Beinn an Tuirc | 33
BUMU | Burghmuir | 132
BUMU | Burghmuir | 33
BUWH | Burn of Whilk | 33
CAAD | Carradale | 132
CAAD | Carradale | 33
CAIN | Cairnford | 275
CAIN | Cairnford | 33
CAIR | Cairn Uish Rothes | 33
CAMW | Camster Wind | 33
CASH | Cashlie | 33
CASH | Cashlie | 11
CASS | Cashley | 132
CASS | Cashley | 33
CAUS | Causeymire | 33
CEAN | Ceannacroc | 132
CEAN | Ceannacroc | 33
CEAN | Ceannacroc | 11
CHAR | Charleston | 132
CHAR | Charleston | 33
CLAC | Clachan | 132
CLAC | Clachan | 33
CLAC | Clachan | 11
CLAS | Clashindarroch | 33
CLAY | Clayhills | 132
CLAY | Clayhills | 33
CLUN | Clunie | 132
CLUN | Clunie | 11
COGA | Corriegarth | 132
COGA | Corriegarth | 33
COGL | Coire Glas | 400
COGL | Coire Glas | 15
COIN | Coire Na Cloiche | 33
CONN | Connagill | 275
CONN | Connagill | 132
CONN | Connagill | 33
CORI | Corriemoillie | 132
CORI | Corriemoillie | 33
COST | Costa Head | 33
COUA | Coupar Angus | 132
COUA | Coupar Angus | 33
COUW | Cour Wind | 33
CRAI | Craigiebuckler | 132
CRAI | Craigiebuckler | 33
CRDH | Creag Dhubh | 275
CRDH | Creag Dhubh | 132
CRDH | Creag Dhubh | 33
CREA | Creag Riabhach | 132
CREA | Creag Riabhach | 33
CRMY | Corrimony | 33
CRSS | Crossaig | 220
CRSS | Crossaig | 132
CRSS | Crossaig | 33
CULL | Culligran | 132
CULL | Culligran | 11
DAAS | Dallas | 275
DAAS | Dallas | 33
DEAN | Deanie | 132
DEAN | Deanie | 11
DENS | Denside | 132
DEUC | Deucherin Hill | 33
DORE | Dorenell | 132
DORE | Dorenell | 33
DOUN | Dounreay | 275
DOUN | Dounreay | 220
DOUN | Dounreay | 132
DOUN | Dounreay | 33
DRUL | Druim Lethann | 132
DRUL | Druim Lethann | 33
DUBE | Dunbeath | 132
DUBE | Dunbeath | 33
DUCC | Dunmore Cable Compound | 132
DUDH | Dudhope | 132
DUDH | Dudhope | 33
DUGR | Dunvegan | 132
DUGR | Dunvegan | 33
DUNM | Dunmaglass | 132
DUNM | Dunmaglass | 33
DYCE | Dyce | 132
DYCE | Dyce | 33
EDIN | Edinbane | 132
EDIN | Edinbane | 33
EDNT | Edintore | 33
ELCH | Elchies Wind | 132
ELCH | Elchies Wind | 33
ELGI | Elgin | 132
ELGI | Elgin | 33
ERRO | Errochty | 132
ERRO | Errochty | 11
FAAR | Farr Windfarm | 132
FAAR | Farr Windfarm | 33
FARI | Farigaig | 275
FARI | Farigaig | 132
FARI | Farigaig | 33
FASN | Fasnakyle | 275
FASN | Fasnakyle | 33
FASN | Fasnakyle | 11
FAUG | Fort Augustus | 400
FAUG | Fort Augustus | 275
FAUG | Fort Augustus | 132
FAUG | Fort Augustus | 33
FAWI | Fairburn Wind | 33
FERO | Fernoch | 132
FERO | Fernoch | 33
FETT | Fetteresso | 400
FETT | Fetteresso | 275
FETT | Fetteresso | 132
FETT | Fetteresso | 33
FEWI | Fetteresso Wind | 33
FIDD | Fiddes | 132
FIDD | Fiddes | 33
FINL | Finlarig | 132
FINL | Finlarig | 11
FINS | Finstown | 220
FINS | Finstown | 132
FINS | Finstown | 33
FOFF | Firth of Forth | 275
FOGG | Foggieton | 132
FOYE | Foyers | 275
FOYE | Foyers | 18
FRAS | Fraserburgh | 132
FRAS | Fraserburgh | 33
FRSD | Freasdail | 33
FWIL | Fort William | 132
FWIL | Fort William | 33
FYRI | Fyrish | 275
FYRI | Fyrish | 132
FYRI | Fyrish | 33
GILB | Gills Bay | 132
GLAG | Glen Agnes | 132
GLCA | Glencassley | 33
GLDO | Glendoe | 132
GLDO | Glendoe | 18
GLEN | Glenmoriston | 132
GLEN | Glenmoriston | 11
GLFA | Glenfarclas | 132
GLFA | Glenfarclas | 33
GLKO | Glen Kyllachy | 132
GLKO | Glen Kyllachy | 33
GLNE | Glean Eoghainn | 33
GLNU | Glen Ullinish | 33
GLOF | Glens of Foundland | 33
GLSH | Glenshero | 132
GLSH | Glenshero | 33
GOHI | Gordonstown Hill | 33
GOLT | Golticlay | 132
GOLT | Golticlay | 33
GORW | Gordonbush Wind | 275
GORW | Gordonbush Wind | 33
GRIF | Griffin Wind | 132
GRIF | Griffin Wind | 33
GRUB | Grudie Bridge | 132
GRUB | Grudie Bridge | 33
GRUB | Grudie Bridge | 11
HALY | Halsary | 33
HEST | Hesta Head | 33
HIGL | Hill of Glaschyle | 33
HITO | Hill of Towie | 33
HUNN | Hunterston North | 220
HYWD | Hywind | 33
INAW | Inverawe | 33
INAW | Inverawe | 11
INGA | Invergarry | 400
INGA | Invergarry | 132
INGA | Invergarry | 33
INGA | Invergarry | 11
INNE | Inverness | 132
INNE | Inverness | 33
INRU | Inverugie | 132
INVE | Inveraray | 132
INVR | Inverarnan | 132
INVR | Inverarnan | 33
KEIT | Keith | 275
KEIT | Keith | 132
KEIT | Keith | 33
KIIN | Killin | 132
KIIN | Killin | 33
KILC | Kilchrenan | 132
KILO | Kinlochleven | 132
KILO | Kinlochleven | 33
KINT | Kintore | 400
KINT | Kintore | 275
KINT | Kintore | 132
KINT | Kintore | 33
KINW | Kincardine Wind | 33
KIOR | Kilmorack | 132
KIOR | Kilmorack | 11
KNOC | Knocknagael | 275
KNOC | Knocknagael | 132
KNOC | Knocknagael | 33
LAGG | Laggan | 132
LAIR | Lairg | 132
LAIR | Lairg | 33
LHBR | Lochaber Hydro | 33
LIMK | Limekilns | 132
LIMK | Limekilns | 33
LIVI | Livishie | 11
LLUC | Livishie | 33
LOCB | Loch Buidhe | 275
LOCB | Loch Buidhe | 132
LOCB | Loch Buidhe | 33
LOCH | Lochay | 132
LOCH | Lochay | 33
LOCH | Lochay | 11
LOCL | Loch Lundie | 132
LUBR | Lubreoch | 33
LUIC | Luichart | 132
LUIC | Luichart | 11
LUMB | Lumbs | 132
LUNA | Lunanhead | 132
LUNA | Lunanhead | 33
LUND | Lundavra | 132
LYND | Lyndhurst | 132
LYND | Lyndhurst | 33
MACD | Macduff | 132
MACD | Macduff | 33
MEIK | Meikle | 33
MELG | Melgarve | 400
MELG | Melgarve | 132
MELG | Melgarve | 33
MIHW | Midhill Wind | 33
MILC | Milton of Craigie | 132
MILC | Milton of Craigie | 33
MILS | Millenium South | 132
MILS | Millenium South | 33
MILW | Millenium Wind | 132
MILW | Millenium Wind | 33
MITA | Milltown Airfield | 33
MKTG | Marketgait | 132
MORF | Moray Firth Wind | 400
MORF | Moray Firth Wind | 275
MOSS | Mossford | 132
MOSS | Mossford | 11
MOTA | Moultaive | 132
MOYW | Moy Wind | 33
MUAI | Muaithebheal | 132
MUAI | Muaithebheal | 33
MYBS | Mybster | 132
MYBS | Mybster | 33
NAIR | Nairn | 132
NAIR | Nairn | 33
NANT | Nant | 132
NANT | Nant | 11
NEDE | New Deer | 400
NEDE | New Deer | 275
NESQ | Ness of Quoys | 33
NOVA | Novar | 33
NOVW | Novar Wind | 33
NWGL | Norwegian Link 2 | 400
ORRI | Orrin | 132
ORRI | Orrin | 33
ORRI | Orrin | 11
PAUL | Paul's Hill | 33
PEHE | Peterhead | 400
PEHE | Peterhead | 275
PEHE | Peterhead | 132
PEHE | Peterhead | 33
PEHE | Peterhead | 23.5
PEHE | Peterhead | 15.8
PEHG | Peterhead Grange | 132
PEHG | Peterhead Grange | 33
PEHS | Peterhead Shell | 11
PENF | Pentland Firth (Meygen Tidal) | 132
PENF | Pentland Firth (Meygen Tidal) | 33
PERS | Persley | 275
PERS | Persley | 132
PERS | Persley | 33
PITL | Pitlochry Hydro Station | 11
PORA | Port Ann | 132
PORA | Port Ann | 33
QUOI | Quoich | 132
QUOI | Quoich | 11
RANN | Rannoch | 132
RANN | Rannoch | 33
RANN | Rannoch | 11
REDM | Redmoss | 132
REDM | Redmoss | 33
ROSE | Rosehall | 33
ROTI | Rothienorman | 400
ROTI | Rothienorman | 275
ROTI | Rothienorman | 132
ROTI | Rothienorman | 33
RTHE | Rothes III | 33
SALA | Sallachy | 132
SALA | Sallachy | 33
SFEG | St Fergus Gas Terminal | 132
SFEG | St Fergus Gas Terminal | 11
SFEM | St Fergus Mobil | 132
SFEM | St Fergus Mobil | 11
SFER | St Fergus | 132
SFIL | St Fillians | 132
SFIL | St Fillians | 33
SFIL | St Fillians | 11
SHET | Shetland | 132
SHIN | Shin | 132
SHIN | Shin | 33
SHIN | Shin | 11
SLKB | Slackbuie | 132
SLOY | Sloy | 132
SLOY | Sloy | 11
SOUI | Sound of Islay | 33
SPCH | Speyside CHP | 33
SPCH | Speyside CHP | 11
SPIT | Spittal | 275
SPIT | Spittal | 132
SPIT | Spittal | 33
SPYW | Speyslaw | 33
STOM | Stoneywood Mills | 33
STOM | Stoneywood Mills | 11
STRB | Strathbrora | 275
STRB | Strathbrora | 33
STRI | Strichen | 132
STRI | Strichen | 33
STRL | Stronelairg Wind | 132
STRL | Stronelairg Wind | 33
STRS | Stroupster Wind | 33
STRW | Strathy | 132
STRW | Strathy | 33
STWN | Stornoway Wind | 132
STWN | Stornoway Wind | 33
TANG | Tangy | 33
TARL | Tarland | 132
TARL | Tarland | 33
TAYN | Taynuilt | 132
TAYN | Taynuilt | 33
TEAL | Tealing | 275
TEAL | Tealing | 132
TEAL | Tealing | 33
THUS | Thurso | 275
THUS | Thurso | 132
THUS | Thurso | 33
TLYM | Tullymurdoch | 33
TOMN | Tom Na Clach | 33
TOMT | Tomatin | 275
TOMT | Tomatin | 132
TOMT | Tomatin | 33
TORA | Torr Achilty | 33
TORA | Torr Achilty | 11
TULW | Tullo 2 | 33
TUMB | Tummel Bridge | 132
TUMB | Tummel Bridge | 33
TUMB | Tummel Bridge | 11
TUMM | Tummel | 400
TUMM | Tummel | 275
TUMM | Tummel | 132
TUMM | Tummel | 33
WATH | Wathegar 2 | 33
WESR | Westray | 33
WHIB | Whitebridge | 132
WILW | Willow | 132
WILW | Willow | 33
WIOW | Willowdale | 132
WIOW | Willowdale | 33
WISL | West Islay | 33
WOHI | Woodhill | 132
WOHI | Woodhill | 33

## B-1-1b
Table B.1.1b - SPT Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
AIKE | Aikengall Wind Farm | 33
AIRI | Airies Windfarm | 33
ANDE | Andershaw Wind Farm | 33
ANNA | Annabaglish Wind Farm | 33
AREC | Arecleoch | 132
AREC | Arecleoch | 33
ASVA | Assel Valley Wind Farm | 33
AUCH | Auchencrosh | 275
AUCW | Auchenwynd | 132
AURO | Auchrobert Windfarm | 33
AYR- | Ayr | 275
AYR- | Ayr | 33
BAGA | Bathgate | 132
BAGA | Bathgate | 33
BAGA | Bathgate Rail | 25
BAIN | Bainsford | 132
BAIN | Bainsford | 33
BEQU | Benbrack and Quantans Hill | 132
BEQU | Benbrack and Quantans Hill | 33
BERW | Berwick | 132
BERW | Berwick | 33
BLAH | Blackhill | 132
BLAH | Blackhill | 33
BLCW | Blackcraig | 132
BLCW | Blackcraig | 33
BLKL | Blacklaw Windfarm | 132
BLKL | Blacklaw Windfarm | 33
BLKS | Blackcraig South | 33
BLLX | Blacklaw Extension | 132
BLLX | Blacklaw Extension | 33
BONB | Bonnybridge Border Node | 400
BONB | Bonnybridge Border Node | 275
BONN | Bonnybridge | 275
BONN | Bonnybridge | 132
BONN | Bonnybridge | 33
BONN | Bonnybridge | 25
BOWB | Bowbeat Hill | 33
BPGR | BP Grangemouth | 33
BRAE | Braehead | 132
BRAP | Braehead Park | 132
BRAP | Braehead Park | 33
BRNX | Branxton | 400
BROX | Broxburn | 132
BROX | Broxburn | 33
BUSB | Busby | 275
CAFA | Carsfad | 132
CAFA | Carsfad | 11
CALD | Calder Water | 33
CATY | Carntyne | 132
CATY | Carntyne | 33
CATY | Carntyne | 25
CHAP | Chapelcross | 132
CHAP | Chapelcross | 33
CHAS | Charlotte Street | 275
CHAS | Charlotte Street | 33
CHMO | Chirmorie Wind Farm | 132
CLYM | Clyde's Mill | 275
CLYM | Clyde's Mill | 33
CLYN | Clyde North | 275
CLYN | Clyde North | 33
CLYS | Clyde South | 275
CLYS | Clyde South | 33
COAL | Coalburn | 400
COAL | Coalburn | 132
COAL | Coalburn | 33
COAT | Coatbridge | 275
COAT | Coatbridge | 33
COCK | Cockenzie | 400
COCK | Cockenzie | 275
COCK | Cockenzie | 33
CONO | Coalburn North | 132
COYL | Coylton | 275
COYL | Coylton | 132
COYL | Coylton | 33
COYT | Coylton Tee | 132
COYW | Coylton West | 275
CRDY | Crossdykes Windfarm | 33
CRMH | Cruach Mhor | 33
CROE | Crookedstane Wind Farm | 33
CROO | Crookston | 132
CROO | Crookston | 33
CRUA | Cruachan | 275
CRYR | Crystal Rig | 400
CRYR | Crystal Rig | 132
CRYR | Crystal Rig | 33
CUMB | Cumbernauld | 132
CUMB | Cumbernauld | 33
CUMH | Cumberhead Wind Farm | 33
CUPA | Cupar | 132
CUPA | Cupar | 33
CURR | Currie | 275
CURR | Currie | 132
CURR | Currie | 33
CURR | Currie | 11
DALB | Dalmally Boundary | 275
DALL | Dalmally | 275
DALM | Dalmarnock | 275
DALM | Dalmarnock | 132
DALM | Dalmarnock | 33
DALQ | Dalquhandy Collector | 132
DALQ | Dalquhandy | 33
DALS | Dalswinton | 33
DENN | Denny North | 400
DENN | Denny North | 275
DENN | Denny North | 132
DENN | Denny North | 33
DESA | Dersalloch | 132
DESA | Dersalloch | 33
DEVM | Devol Moor | 400
DEVM | Devol Moor | 132
DEVM | Devol Moor | 33
DEVM | Devol Moor | 25
DEVO | Devonside | 132
DEVO | Devonside | 33
DEWP | Dewar Place | 275
DEWP | Dewar Place | 33
DOWE | Douglas West | 33
DRCR | Drumcross | 132
DRCR | Drumcross | 33
DRUM | Drumchapel | 275
DRUM | Drumchapel | 33
DUMF | Dumfries | 132
DUMF | Dumfries | 33
DUNB | Dunbar | 132
DUNB | Dunbar | 33
DUNE | Dunlaw Extension | 132
DUNE | Dunlaw Extension | 33
DUNF | Dunfermline | 132
DUNF | Dunfermline | 33
DUNH | Dunhill | 132
DUNH | Dunhill | 33
DUNO | Dunoon | 132
DUNO | Dunoon | 33
EARB | Earlsburn | 33
EAST | Earlstoun | 132
EAST | Earlstoun | 11
ECCF | Ecclefechan | 132
ECCF | Ecclefechan | 25
ECCL | Eccles | 400
ECCL | Eccles | 132
ECCL | Eccles | 33
EERH | Easterhouse | 275
EERH | Easterhouse | 33
EKIL | East Kilbride | 275
EKIL | East Kilbride | 33
EKIS | East Kilbride South | 275
EKIS | East Kilbride South | 33
ELDE | Elderslie | 132
ELDE | Elderslie | 33
ELVA | Elvanfoot | 400
ELVA | Elvanfoot | 275
ELVA | Elvanfoot | 132
ELVA | Elvanfoot | 33
ELVA | Elvanfoot | 25
ENHI | Enoch Hill Wind Farm | 132
ENHI | Enoch Hill Wind Farm | 33
ERSK | Erskine | 132
ERSK | Erskine | 33
ESST | Essenside | 132
EWEH | Ewe Hill | 132
EWEH | Ewe Hill | 33
EXON | Exxon mobil | 33
EXON | Exxon mobil | 11
FALL | Fallago | 400
FALL | Fallago | 33
FIFE | Fife Energy | 132
FINN | Finnieston | 132
FINN | Finnieston | 33
GALA | Galashiels | 132
GALA | Galashiels | 33
GARB | Gareloch Boundary | 132
GARE | Gareloch | 132
GAWH | Galawhistle | 132
GAWH | Galawhistle | 33
GIFF | Giffnock | 275
GIFF | Giffnock | 33
GIHI | Gilston Hill Wind Farm | 33
GLAP | Glen App Wind Farm | 33
GLGL | Glenglass | 132
GLGL | Glenglass | 33
GLLE | Glenlee | 132
GLLE | Glenlee | 11
GLLU | Glenluce | 132
GLLU | Glenluce | 33
GLMU | Glenmuckloch | 33
GLNI | Glenniston | 132
GLNI | Glenniston | 33
GLOU | Glenouther Windfarm | 33
GLRB | Glenrothes Boundary | 275
GLRO | Glenrothes | 275
GLRO | Glenrothes | 33
GORG | Gorgie | 132
GORG | Gorgie | 33
GOVA | Govan | 132
GOVA | Govan | 33
GRMO | Grangemouth | 275
GRMO | Grangemouth | 33
GRNA | Gretna | 400
GRNA | Gretna | 132
GRNA | Gretna | 33
HABU | Harry Burn Wind Farm | 33
HADH | Hadyard Hill | 132
HADH | Hadyard Hill | 33
HAGR | Haggs Road | 132
HAGR | Haggs Road | 33
HAKB | Harker Border Node | 400
HAKB | Harker Border Node | 132
HARE | Harestanes | 132
HARE | Harestanes | 33
HARG | Harting Rig Wind Farm | 33
HARH | Harburn Head Wind Farm | 33
HAWI | Hawick | 132
HAWI | Hawick | 33
HELE | Helensburgh | 132
HELE | Helensburgh | 33
HOPR | Hopsrig Wind Farm | 132
HOPR | Hopsrig Wind Farm | 33
HUCS | Hunterston Converter Station | 400
HUER | Hunterston | 400
HUER | Hunterston | 132
HUER | Hunterston | 33
HUNE | Hunterston East | 400
HUNF | Hunterston Farm | 132
HUNF | Hunterston Farm | 33
HUNN | Hunterston North | 400
HUNN | Hunterston North | 220
HUNN | Hunterston North | 33
INKE | Inverkeithing | 132
INKE | Inverkeithing | 33
INVB | Inverarnan | 275
INVR | Inverarnan | 275
INWI | Innerwick | 132
INWI | Innerwick | 25
JOHN | Johnstone | 132
JOHN | Johnstone | 33
JUNA | Junction A | 132
JUNV | Junction V | 132
KAIM | Kaimes | 275
KAIM | Kaimes | 33
KEIH | Keithshill | 33
KENN | Kennoxhead | 132
KENN | Kennoxhead | 33
KEON | Kendoon North | 132
KEOO | Kendoon | 132
KEOO | Kendoon | 11
KIER | Killermont | 132
KIER | Killermont | 33
KILB | Kilbowie | 132
KILB | Kilbowie | 33
KILB | Kilbowie | 11
KILG | Kilgalleoch | 275
KILG | Kilgalleoch | 33
KILS | Kilmarnock South | 400
KILS | Kilmarnock South | 275
KILS | Kilmarnock South | 132
KILS | Kilmarnock South | 33
KILT | Kilmarnock Town | 275
KILT | Kilmarnock Town | 33
KILW | Kilwinning | 132
KILW | Kilwinning | 33
KINB | Kincardine Boundary | 275
KINC | Kincardine | 275
KYPE | Kype Muir | 132
KYPE | Kype Muir | 33
LAMB | Lambhill | 275
LETH | Lethans | 132
LETH | Lethans | 33
LEVE | Leven | 132
LEVE | Leven | 33
LEVT | Leven Tee | 132
LING | Livingston | 132
LING | Livingston | 33
LINM | Linmill | 132
LINM | Linmill | 33
LOAN | Longannet | 275
LOCH | Loch Hill Windfarm 33kV | 33
LONB | Longburn Wind Farm | 132
LOPA | Longpark | 33
LORG | Lorg Wind Farm | 132
LORG | Lorg Wind Farm | 33
MAHI | Mark's Hill | 275
MAHI | Mark's Hill | 132
MAHI | Mark's Hill | 33
MARG | Margree | 132
MARG | Margree | 33
MARM | Marshall Meadows | 25
MAYB | Maybole | 132
MAYB | Maybole | 33
MAYT | Maybole Tee | 132
MEAD | Meadowhead | 132
MEAD | Meadowhead | 11
MIDM | Middle Muir Wind Farm | 132
MIDM | Middle Muir Wind Farm | 33
MINN | Minnygap Wind Farm | 33
MINS | Minsca | 33
MOFF | Moffat | 400
MOFF | Moffat | 132
MOFF | Moffat | 33
MOSH | Mossmorran Shell | 132
MOSH | Mossmorran Shell | 11
MOSM | Mossmorran | 275
MOSM | Mossmorran | 132
MOSM | Mossmorran | 33
NEAR | Newarthill | 275
NEAR | Newarthill | 33
NECU | New Cumnock | 275
NECU | New Cumnock | 132
NECU | New Cumnock | 33
NECU | New Cumnock | 33
NEIL | Neilston | 400
NEIL | Neilston | 275
NEIL | Neilston | 132
NEIL | Neilston | 33
NETS | Newton Stewart | 132
NETS | Newton Stewart | 33
NLEI | North Lowther Energy Initiative | 132
NLEI | North Lowther Energy Initiative | 33
NNGA | Neart na Gaoithe | 220
NNGA | Neart na Gaoithe | 33
NNGB | Neart na Gaoithe | 220
NNGB | Neart na Gaoithe | 33
PAIS | Paisley | 132
PAIS | Paisley | 33
PART | Partick | 132
PART | Partick | 33
PENC | Pencloe | 33
POGB | Pogbie Windfarm | 33
POOB | Portobello | 275
POOB | Portobello | 33
POOB | Portobello | 25
PORD | Port Dundas | 275
PORD | Port Dundas | 33
RAVE | Ravenscraig | 33
REDH | Redhouse | 132
REDH | Redhouse | 33
ROBP | Rothes BioPower | 33
ROBP | Rothes BioPower | 11
SACO | Saltcoats | 132
SACO | Saltcoats | 33
SACO | Saltcoats | 25
SAKN | Sandy Knowe Wind Farm | 132
SANQ | Sanquhar Wind Farm | 132
SANX | St Andrews Cross | 132
SANX | St Andrews Cross | 33
SANX | St Andrews Cross | 25
SHRU | Shrubhill | 275
SHRU | Shrubhill | 33
SIGH | Sighthill | 275
SIGH | Sighthill | 33
SMEA | Smeaton | 400
SMEA | Smeaton | 275
SMEA | Smeaton | 132
SMEA | Smeaton | 33
SNED | Sneddon Law | 33
SOKY | South Kyle | 132
SOKY | South Kyle | 33
SOLW | Solway Bank Wind Farm | 33
SPAV | Spango Valley | 132
SPAV | Spango Valley | 33
STCR | Steven's Croft | 33
STCR | Steven's Croft | 11
STHA | Strathaven | 400
STHA | Strathaven | 275
STHA | Strathaven | 33
STIR | Stirling | 132
STIR | Stirling | 33
STLE | Strathleven | 132
STLE | Strathleven | 33
STLE | Strathleven | 25
STNO | Stranoch Wind Farm | 132
STNO | Stranoch Wind Farm | 33
STVE | Striven | 33
STWB | Stella West Border Node | 400
TELR | Telford Road | 132
TELR | Telford Road | 33
TODD | Toddleburn | 33
TONG | Tongland | 132
TONG | Tongland | 33
TONG | Tongland | 11
TORM | Tormywheel Wind Farm | 33
TORN | Torness | 400
TORN | Torness | 132
TORN | Torness | 33
TRAL | Tralorg Wind Farm | 33
ULZI | Ulzieside | 33
VIRD | Viridor | 33
WGEO | West George Street | 275
WGEO | West George Street | 33
WESE | Westerdod | 132
WFIB | Westfield Boundary | 275
WFIE | Westfield | 275
WFIE | Westfield | 132
WFIE | Westfield | 33
WHBR | Whitelaw Brae Wind Farm | 33
WHHO | Whitehouse | 275
WHHO | Whitehouse | 33
WHLL | Whiteside Hill | 33
WHTB | Whistlefield Boundary | 132
WHTL | Whistlefield | 132
WHTL | Whistlefield | 33
WISH | Wishaw (Gowkthrapple) | 400
WISH | Wishaw (Gowkthrapple) | 275
WISH | Wishaw (Gowkthrapple) | 132
WISH | Wishaw (Gowkthrapple) | 33
WISH | Wishaw (Gowkthrapple) | 25
WIYH | Windyhill | 400
WIYH | Windyhill | 275
WIYH | Windyhill | 132
WIYH | Windyhill | 33
WLEE | Whitelee | 275
WLEE | Whitelee | 33
WLEX | Whitelee Extension | 275
WLEX | Whitelee Extension | 33

## B-1-1c
Table B.1.1c - NGET Index of Substation Codes |  |  | Back To Menu
Site Code | Site Name | Voltage (kV)
ABHA | Abham | 400
ABTH | Aberthaw | 275
ABTH | Aberthaw | 132
ACTL | Acton Lane | 22
ALDW | Aldwarke | 275
ALST | Alpha Steel | 33
ALVE | Alverdiscott | 400
AMEM | Amersham | 132
AUST | Aust | 400
AXMI | Axminster | 400
AXMI | Axminster | 132
BACT | Bacton | 400
BAGB | Baglan Bay | 275
BARK | Barking | 400
BARK | Barking | 275
BARK | Barking | 132
BARP | Barking Power | 275
BARW | Barking West | 33
BEDD | Beddington | 400
BEDD | Beddington | 275
BESW | Berkswell | 275
BICF | Bicker Fen | 400
BIRK | Birkenhead | 275
BISW | Bishops Wood | 275
BLYT | Blyth | 400
BLYT | Blyth | 275
BLYT | Blyth | 66
BODE | Bodelwyddan | 400
BOLN | Bolney | 400
BOTW | Botley Wood | 400
BRAI | Braintree | 400
BRAW | Bradford West | 400
BRAW | Bradford West | 275
BRED | Bredbury | 275
BRFO | Bramford | 400
BRIM | Brimsdown | 400
BRIM | Brimsdown | 275
BRIM | Brimsdown | 132
BRIN | Brinsworth | 400
BRIN | Brinsworth | 275
BRIT | Britannia Bridge | 275
BRIW | Bridgewater | 400
BRLE | Bramley | 400
BRWA | Bridgewater | 400
BRWA | Bridgwater | 275
BRWA | Bridgwater | 132
BURW | Burwell | 400
BUSH | Bushbury | 275
BUST | Bustleholm | 400
BUST | Bustleholm | 275
CAMA | Cambridge Arms | 132
CAML | Camblesforth | 66
CANT | Canterbury | 400
CANW | Carnedd Wen | 400
CAPE | Capenhurst | 400
CAPE | Capenhurst | 275
CARE | Cardiff East | 275
CARN | Carnedd Wen | 400
CARR | Carrington | 400
CARR | Carrington | 275
CARR | Carrington | 132
CELL | Cellarhead | 400
CELL | Cellarhead | 132
CHIC | Chickerell | 400
CHIL | Chilling | 400
CHSI | Chessington | 275
CHTE | Chesterfield | 275
CILF | Cilfynydd | 400
CILF | Cilfynydd | 275
CITR | City Road | 400
CLEH | Cleve Hill | 400
CONQ | Connahs Quay | 400
COSO | Coryton South | 400
COTT | Cottam | 400
COVE | Coventry | 275
COWL | Cowley | 400
COWT | Cowbridge Tee | 275
CREB | Creyke Beck | 400
CREB | Creyke Beck | 275
CULJ | Culham Jet | 400
DAIN | Daines | 400
DAMC | Damhead Creek | 400
DEES | Deeside | 400
DIDC | Didcot | 400
DINO | Dinorwig | 400
DISS | Diss | 132
DRAK | Drakelow | 400
DRAK | Drakelow | 275
DRAK | Drakelow | 132
DRAX | Drax | 400
DRAX | Drax | 132
DUNG | Dungeness | 400
DUNG | Dungeness | 275
EALI | Ealing | 275
EALI | Ealing | 66
EASO | Eaton Socon | 400
ECLA | East Claydon | 400
ECLA | East Claydon | 132
EGGB | Eggborough | 400
ELLA | Elland | 275
ELLA | Elland | 132
ELST | Elstree | 400
ELST | Elstree | 275
ELST | Elstree | 132
ENDE | Enderby | 400
EXET | Exeter | 400
EYES | EYE | 400
FAWL | Fawley | 400
FAWL | Fawley | 132
FECK | Feckenham | 400
FECK | Feckenham | 275
FENW | Fenwick Tee | 400
FERR | Ferrybridge | 400
FERR | Ferrybridge | 275
FERR | Ferrybridge | 132
FFES | Ffestiniog | 275
FIDF | Fiddler's Ferry | 275
FINP | Finsbury Park | 400
FLEE | Fleet | 400
FLIB | Flintshire Bridge WestHVDC | 400
FOUR | Fourstones | 275
FOUX | Four Crosses | 400
FROD | Frodsham | 400
FROD | Frodsham | 275
GART | Garforth | 400
GRAI | Grain | 400
GRAN | Grange | 66
GREN | Grendon | 400
GREN | Grendon | 132
GRIW | Grimsby West | 400
GRSA | Greystones 'A' | 275
GRSB | Greystones 'B' | 275
GRST | Greystones | 275
GRTO | Grangetown | 275
GWYN | Gmynt Y Mor Tee | 400
GYWN | Gmynt Y Mor | 132
HACK | Hackney | 400
HACK | Hackney | 275
HAKB | Harker Border (Node) | 400
HAMB | Hambleton Tee | 400
HAMH | Hams Hall | 400
HAMH | Hams Hall | 275
HAMH | Hams Hall | 132
HARK | Harker | 400
HARK | Harker | 275
HARK | Harker | 132
HARM | Hart Moor | 275
HATL | Hartlepool | 275
HAWP | Hawthorn Pit | 400
HAWP | Hawthorn Pit | 275
HEDD | Heddon Tee | 400
HEDN | Hedon | 150
HEDO | Hedon | 275
HEYS | Heysham | 400
HEYS | Heysham | 132
HIBU | Highbury | 400
HIGM | High Marnham | 400
HIGM | High Marnham | 275
HIKP | Hinckley Point C | 400
HINP | Hinkley Point | 400
HINP | Hinkley Point | 275
HIRN | Hirst North | 400
HUMR | Humber Refinery | 400
HURS | Hurst | 275
HUTT | Hutton | 400
IMPP | Imperial Park | 400
INDQ | Indian Queens | 400
IROA | Iron Acton | 275
IROA | Iron Acton | 132
IRON | Ironbridge | 400
IRON | Ironbridge | 132
IVER | Iver | 400
IVER | Iver | 275
JORD | Jordanthorpe | 275
KEAD | Keadby | 400
KEAP | Keadby Power | 400
KEAR | Kearsley | 400
KEAR | Kearsley | 275
KEMS | Kemsley | 400
KENG | Kensal Green | 400
KIBY | Kirkby | 275
KILL | Killinghome | 400
KILY | Kings Lynn | 400
KINL | King Lynn | 400
KINO | Kingsnorth | 400
KINO | Kingsnorth | 132
KIRK | Kirkstall | 275
KITW | Kitwell | 275
KNAR | Knaresborough | 275
KNOT | Knottingley | 400
LACK | Lackenby | 400
LACK | Lackenby | 275
LAGA | Langage | 400
LAKE | Lakeside | 400
LALE | Laleham | 275
LAND | Landulph | 400
LEGA | Legacy | 400
LEIB | Leighton Buzzard | 400
LEIS | Leiston | 400
LEMR | Lea Marston | 132
LISD | Lister Drive | 275
LITB | Little Barford | 400
LITD | Little Dunham | 275
LITT | Littlebrook | 400
LITT | Littlebrook | 275
LITT | Littlebrook | 132
LODR | Lodge Road | 66
LOFI | Longfield | 400
LOVE | Lovedean | 400
LOWE | Lowestoft | 400
MACC | Macclesfield | 400
MACC | Macclesfield | 275
MAGA | Margam | 275
MANN | Mannington | 400
MAWO | Marchwood | 400
MEDW | Medway | 400
MELK | Melksham | 400
MELK | Melksham | 275
MELK | Melksham | 132
MIDL | Middleton | 400
MILH | Mill Hill | 275
MILH | Mill Hill | 132
MITY | Minety | 400
MIWW | Mid Wales West | 400
MOEL | St Asaph | 400
MONF | Monk Fryston | 400
MONF | Monk Fryston | 275
MUCF | Mucking Flats | 400
MUMB | Mumby | 400
NECH | Nechells | 275
NECT | Necton | 400
NEEP | Neepsend | 400
NEEP | Neepsend | 275
NEWF | Newton Flotman | 400
NEWX | New Cross | 275
NFLE | Northfleet East | 400
NHYD | North Hyde | 275
NHYD | North Hyde | 66
NINF | Ninfield | 400
NORL | Norton Lees | 275
NORM | Norwich Main | 400
NORT | Norton | 400
NORT | Norton | 275
NORW | Norwich Main | 400
NURS | Nursling | 400
OCKH | Ocker Hill | 275
OCKH | Ocker Hill | 132
OFFE | Offerton | 275
OLDB | Oldbury | 400
OLDB | Oldbury | 275
OLDS | Oldbury-on-Severn | 400
OLDS | Oldbury-on-Severn | 132
OSBA | Osbaldwick | 400
OSWE | Oswestry | 400
PADI | Padiham | 400
PADI | Padiham | 132
PAFB | Patford Bridge | 400
PELH | Pelham | 400
PEMB | Pembroke | 400
PEMB | Pembroke | 132
PENE | Penwortham East | 132
PENI | Peniarwaun | 400
PENN | Penn | 400
PENN | Penn | 275
PENT | Pentir | 400
PENW | Penwortham West | 132
PERH | Penrhos | 132
PEWO | Penwortham | 400
PEWO | Penwortham | 275
PITS | Pitsmoor | 275
POPP | Poppleton | 275
PORH | Port Ham | 132
PUDM | Pudding Mill Lane | 400
PURI | Puriton Tee | 400
PYLE | Pyle | 275
QUER | Quernmoor Tee | 400
RAIN | Rainhill | 275
RASS | Rassau | 400
RATS | Ratcliffe-on-Soar | 400
RATS | Ratcliffe-on-Soar | 275
RATS | Ratcliffe-on-Soar | 132
RAYL | Rayleigh | 400
RAYM | Rayleigh Main | 132
REBR | Redbridge | 275
RHIG | Rhigos | 400
RICH | Richborough | 400
ROCH | Rochdale | 400
ROCH | Rochdale | 275
ROCK | Rocksavage | 400
ROWD | Rowdown | 400
RUGE | Rugeley | 400
RUGE | Rugeley | 132
RYEH | Rye House | 400
RYHA | Ryhall | 400
SAEN | Saltend North | 275
SAES | Saltend South | 275
SAFO | Sandford | 400
SALH | Saltholme | 275
SASA | St. Asaph | 132
SBAR | Stoke Bardolph | 400
SEAB | Seabank | 400
SELL | Sellindge | 400
SELT | Sellindge Tee | 400
SELW | Sellindge West | 400
SETW | Sellindge Tee West | 400
SHBA | South Humber Bank | 400
SHEC | Sheffield City | 275
SHRE | Shrewsbury | 400
SING | Singlewell | 400
SIZE | Sizewell | 400
SIZE | Sizewell | 132
SJOW | St Johns Wood | 400
SJOW | St Johns Wood | 275
SKLG | Skelton Grange | 275
SMAN | South Manchester | 275
SPEN | Spennymoor | 400
SPEN | Spennymoor | 275
SPLN | Spalding North | 400
SSHI | South Shields | 275
STAH | Stanah | 400
STAL | Stalybridge | 400
STAL | Stalybridge | 275
STAY | Staythorpe | 400
STEN | Stella North | 132
STES | Stella South | 132
STEW | Stella West | 400
STEW | Stella West | 275
STOB | Stoke Bardolph | 400
STSB | Stocksbridge | 400
STYC | Staythorpe | 132
SUND | Sundon | 400
SUTB | Sutton Bridge | 400
SWAN | Swansea North | 400
SWAN | Swansea North | 275
TAUN | Taunton | 400
TEMP | Templeborough | 275
THOM | Thorpe Marsh | 400
THOM | Thorpe Marsh | 275
THOM | Thorpe Marsh | 66
THOR | Brine Field | 400
THTO | Thornton | 400
THUR | Thurcroft | 275
TILB | Tilbury | 400
TILB | Tilbury | 275
TINP | Tinsley Park | 275
TOCK | Tockington | 400
TODP | Tod Point | 400
TODP | Tod Point | 275
TOTE | Tottenham East | 275
TOTT | Tottenham | 400
TOTT | Tottenham | 275
TOTW | Tottenham West | 275
TRAW | Trawsfynydd | 400
TRAW | Trawsfynydd | 275
TREM | Tremorfa | 275
TREU | Treuddyn Tee | 400
TYNE | Tynemouth | 275
UPPB | Upper Boat | 275
USKM | Uskmouth | 275
USKM | Uskmouth | 132
WALH | Walham | 400
WALP | Walpole | 400
WALP | Walpole | 132
WALX | Waltham Cross | 400
WALX | Waltham Cross | 275
WARL | Warley | 275
WASF | Washway Farm | 275
WATS | Watford South | 275
WBOL | West Boldon | 275
WBUR | West Burton | 400
WBUR | West Burton | 132
WEAV | Weaver Junction | 25
WHAM | West Ham | 400
WHGA | Whitegate | 275
WHSO | Whitson | 400
WHSO | Whitson | 275
WIBA | Wincobank | 275
WIEN | Willenhall | 275
WILE | Willington East | 400
WILL | Willington | 275
WILL | Willington | 132
WILT | Wilton | 275
WIMB | Wimbledon | 400
WIMB | Wimbledon | 275
WIMC | Wimbledon | 33
WISD | Willesden | 275
WISD | Willesden | 66
WLSD | Willesden | 400
WMAR | Weston Marsh | 400
WMEL | West Melton | 275
WTHU | West Thurrock | 400
WWEY | West Weybridge | 400
WWEY | West Weybridge | 275
WYLF | Wylfa | 400
WYLF | Wylfa | 132
WYMO | Wymondley | 400

## B-1-1d
Table B1.1d - Sites Relevant to Offshore Transmission |  | Back To Menu
Code | Site
BOSO | Barrow Wind Farm Onshore Site
BOSW | Barrow Offshore Wind Farm
BUBO | Burbo Bank Extension Onshore Substation
BUBW | Burbo Bank Extension Offshore Wind Farm
BURB | Burbo Bank
CLTO | Clacton
DOCO | Docking Shoal Onshore Connection
DOCS | Docking Shoal Offshore Wind Farm
DOGG | Dogger Bank
DUDG | Dudgeon Offshore Wind Farm
DUDO | Dudgeon Onshore Substation
GAOF | Galloper Offshore Substation
GAON | Galloper Onshore
GGON | Greater Gabbard Onshore Substation
GREG | Greater Gabbard Offshore Wind Farm
GUNS | Gunfleet Sands
GWAW | Gwynt-Y-Mor Offshore Wind Farm A
GWBW | Gwynt-Y-Mor Offshore Wind Farm B
GWYO | Gwynt-Y-Mor Onshore Site
GWYW | Gwynt-Y-Mor Offshore Wind Farm
HONW | Hornsea
HOWA | Hornsea Onshore Wind Farm
HOWW | Hornsea Offshore Wind Farm
HOWR | Hornsea Reactive platform
HUMO | Humber Gateway Onshore Site
HUMW | Humber Gateway Offshore Wind Farm
IGOF | Inner Gabbard Offshore
LINO | Lincs Onshore Connection
LINS | Lincs Offshore Wind Farm
LONO | London Array Onshore Site
LONW | London Array Offshore Wind Farm
ORMO | Ormonde Onshore Connection
ORMW | Ormonde Offshore Wind Farm
RABO | Rack Bank Onshore
RACB | Race Bank
RACO | Race Bank Onshore Connection
RACW | Race Bank Offshore Windfarm
RAFO | Rack Bank Offshore
RAMP | Rampion
RORE | Robin Rigg East
RORW | Robin Rigg West
RREW | Robin Rigg East Wind Farm
RRWW | Robin Rigg West Wind Farm
SALL | Sall
SHSW | Sherringham Shoal Offshore Wind Farm
SSAW | Sherringham Shoal Offshore Platform 1
SSBW | Sherringham Shoal Offshore Platform 2
THAW | Thanet Wind Onshore Substation
THOW | Thanet Wind Offshore Substation
TRIM | Trimpell
TWIN | Twineham
WAAO | Walney 1 Onshore Site
WAAW | Walney 1 Offshore Substation
WABO | Walney 2 Onshore Site
WABW | Walney 2 Offshore Substation
WACW | Walney 3 Offshore Substation
WADW | Walney 4 Offshore Substation
WAEN | Walney Extension
WALE | Walney Extension
WDSO | West Of Duddon Sands Onshore Site
WDSW | West Of Duddon Sands Offshore Wind Farm
WDSW | West of Duddon Sands Offshore Wind Farm
WERW | Westermost Rough Wind Farm

## B-2-1a
Table B.2.1a - SHE Transmission Circuits ETYS Yr1 - 2018/19 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABBA6- | ABBA6J | 0 | 4.35 | Cable | 0.8279 | 1.1577 | 1.595 | 60 | 60 | 60 | 60
ABBA6- | ABBA6K | 0 | 3.98 | Cable | 0.7612 | 1.0645 | 1.467 | 60 | 60 | 60 | 60
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 132 | 123 | 106 | 123
ABNE1R | AMUL1G | 28.0986 | 0.001404 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
AIGA1Q | KIOR1Q | 2.7974 | 0.12264 | Composite | 0.264 | 0.594 | 0.66 | 111 | 102.675 | 88.6335 | 102.675
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
ALNE3J | BETH3- | 13.3 | 0 | OHL | 6.07 | 13.557 | 1.456 | 47.9 | 47 | 43 | 47
ALNE3J | COIN3- | 0 | 17.5 | Cable | 12.95 | 16.8 | 1.785 | 38.3 | 34.8 | 34.8 | 34.8
ALNE3J | NOVA3- | 8.45 | 0 | OHL | 13.36 | 25.4 | 0.09 | 22.3 | 20.6275 | 17.8066 | 20.6275
ALNE3J | NOVW32 | 13 | 0 | OHL | 5.93 | 13.25 | 1.42 | 47.9 | 46.9 | 43.4 | 46.9
ALNE3J | NOVW32 | 13 | 0 | OHL | 5.93 | 13.25 | 1.42 | 47.9 | 46.9 | 43.4 | 46.9
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
ANSU3- | ANSU3W | 0 | 11 | Cable | 2.81 | 5.78 | 0.61 | 39 | 39 | 39 | 39
ARBR1Q | DENS1Q | 14.4 | 0 | OHL | 0.61 | 3.08 | 0.75 | 183 | 160 | 149 | 160
ARBR1R | TEAL1- | 23.2 | 0 | OHL | 0.99 | 4.97 | 1.2 | 183 | 160 | 149 | 160
ARDK1- | INVE1J | 9 | 0 | OHL | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123
ARDK1- | SLOY1T | 10 | 0 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123
ARDK3K | ARDK3- | 0.03 | 0 | OHL | 0.05 | 0.105 | 0 | 22.5 | 21 | 18 | 21
ARDR2Q | FYRI2J | 1.8 | 0 | OHL | 0.0108 | 0.0988 | 0.381 | 702 | 665 | 599 | 665
ARDR2Q | LOCB2K | 34.13 | 0 | OHL | 0.2048 | 1.8774 | 7.236 | 702 | 665 | 599 | 665
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 83 | 77 | 67 | 77
BEAT4- | BEAT4A | 0 | 0.6 | Cable | 0.01 | 0.01 | 4.645 | 497 | 497 | 497 | 497
BEAT4- | BEAT4B | 0 | 0.6 | Cable | 0.01 | 0.01 | 4.645 | 497 | 497 | 497 | 497
BEAU1J | BEAU1R | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136
BEAU1J | CULL1Q | 3.542 | 10.458 | Composite | 1.43 | 3.28 | 0.69 | 111 | 103 | 89 | 103
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | BEAU1S | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | KIOR1Q | 1.2402 | 0.0598 | Composite | 0.13 | 0.29 | 0.06 | 111 | 103 | 89 | 103
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117
BEAU1N | BEAU1K | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136
BEAU1N | FAAR1R | 29.85 | 0 | OHL | 2.953 | 6.7683 | 1.436 | 132 | 123 | 106 | 123
BEAU1P | BEAU1L | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1Q | BEAU1M | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1R | INNE1Q | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1S | INNE1R | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1T | FAAR1Q | 29.88 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BEAU2J | FASN2- | 24.288 | 1.012 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU3- | TORA3- | 0 | 1 | Cable | 30.4 | 58.3 | 0 | 17 | 17 | 17 | 17
BEAU4- | FAUG4- | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BERB3- | BERB3W | 0 | 3 | Cable | 1.369 | 3.058 | 0.329 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | BERB3W | 0 | 3 | Cable | 1.369 | 3.058 | 0.329 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | BERB3W | 0 | 3 | Cable | 1.369 | 3.058 | 0.329 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | HIGL31 | 1.2 | 0 | OHL | 0.5472 | 1.223 | 0.132 | 47.9 | 46.9 | 43.4 | 46.9
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.171 | 5.295 | 1.286 | 203 | 193 | 176 | 193
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.171 | 5.297 | 1.318 | 203 | 193 | 176 | 193
BLHI2J | BERB2Q | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.044 | 13.793 | 580 | 546 | 546 | 546
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.0456 | 14.286 | 580 | 546 | 546 | 546
BLHI2L | KINT2J | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2M | PEHERSV1 | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BLHI4- | BLHI4R | 0 | 1 | Cable | 0.0001 | 0.0001 | 0 | 1272 | 1272 | 1272 | 1272
BOAG1Q | FAAR1Q | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOAG1Q | GLFA1- | 33 | 0 | OHL | 3.3496 | 7.6799 | 1.633 | 126 | 117 | 101 | 117
BOAG1R | FAAR1R | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOYN3Q | BOYN3- | 0 | 1 | Cable | 1.17 | 1.12 | 0.08 | 26 | 26 | 26 | 26
BRCW2J | TUMM2K | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
BRCW2K | BONB2J | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BRCW3- | BRDU3J | 0 | 11 | Cable | 3.647 | 10.472 | 1.242 | 49 | 49 | 49 | 49
BRCW3- | BRDU3K | 0 | 11 | Cable | 3.647 | 10.472 | 1.242 | 49 | 49 | 49 | 49
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BRID3- | TULW39 | 10 | 0 | OHL | 17 | 35 | 0 | 22.5 | 21 | 18 | 21
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 83 | 77 | 67 | 77
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 83 | 77 | 67 | 77
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.12 | 0.27 | 0.06 | 111 | 103 | 89 | 103
BROR1Q | DUBE1Q | 38.7224 | 0.077599 | Composite | 3.94 | 9.01 | 1.91 | 126 | 117 | 101 | 117
BROR1Q | LOCB1K | 22.12 | 0 | OHL | 2.2511 | 5.1536 | 1.096 | 126 | 117 | 101 | 117
BUMU1Q | CHAR1- | 38.4999 | 3.7001 | Composite | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
BUMU1R | AMUL1E | 13.9486 | 3.8514 | Composite | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD3- | TANG3- | 0 | 1 | Cable | 36.41 | 76.64 | 0.46 | 22.3 | 21.1 | 18 | 21.1
CAAD3J | BTUI3- | 0 | 1 | Cable | 2.75 | 6.06 | 0.61 | 39.4 | 39.4 | 39.4 | 39.4
CAAD3J | BTUI3K | 0 | 9 | Cable | 4.21 | 8.68 | 0.92 | 47.9 | 43.4 | 43.4 | 43.4
CAAD3J | DEUC3- | 0 | 1 | Cable | 12.08 | 24.84 | 0 | 22.3 | 21.1 | 18 | 21.1
CAIN2- | BLHI2K | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880
CAIN3J | CLAS3K | 0 | 8 | Cable | 1.469 | 3.93 | 1.915 | 107.4 | 97.6 | 97.6 | 97.6
CASH3- | LUBR3- | 0 | 1 | Cable | 9 | 20 | 0 | 24 | 24 | 24 | 24
CASS1Q | LAIR1Q | 28 | 0 | OHL | 2.84 | 6.75 | 1.33 | 111 | 103 | 89 | 103
CEAN1Q | BEIN11 | 0.87 | 0 | OHL | 0.099 | 0.205 | 0.042 | 221 | 216 | 208 | 216
CHAR1- | BIHI1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
CHAR1- | CHAR1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 229 | 211 | 183 | 211
CHAR1- | CHAR1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1R | BIHI1Q | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
CHAR1S | GLAG1Q | 0.93541 | 1.3746 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 0.93541 | 1.3746 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117
CLAC1Q | SLOY1K | 14.2 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLAY1S | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1T | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1R | CLUN1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN5J | CLUN5K | 0 | 1 | Cable | 0.0001 | 0.25 | 0 | 20 | 20 | 20 | 20
CLUN5J | PITL5J | 0 | 1 | Cable | 0.3328 | 0.153 | 0 | 12.2 | 12.2 | 12.2 | 12.2
CLUN5J | PITL5K | 0 | 1 | Cable | 0.3328 | 0.153 | 0 | 12.2 | 12.2 | 12.2 | 12.2
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7002 | 2.8782 | 0.778 | 203 | 193 | 176 | 193
CONN1C | STRW1C | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 203 | 193 | 176 | 193
CONN1J | CONN1C | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 76.0713 | 0.26872 | Composite | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211
CORI3- | LLUC3- | 0 | 2.6 | Cable | 0.48 | 1.28 | 0.62 | 107 | 98 | 98 | 98
CORI3K | CORI3J | 0 | 1 | Cable | 0.468 | 0.5 | 0.186 | 67.2 | 65.8 | 61 | 65.8
COUA1Q | BIHI1Q | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
COUA1R | BIHI1R | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
COUA3- | COUA38 | 24.3 | 0 | OHL | 35.9901 | 76.7099 | 0 | 22.3 | 21.1 | 18 | 21.1
COUA3- | COUA39 | 17.39 | 0 | OHL | 23.92 | 52.7901 | 0.01 | 22.3 | 21.1 | 18 | 21.1
COUA3- | TLYM3- | 0 | 19 | Cable | 17.48 | 16.34 | 3.04 | 28.3 | 28.3 | 28.3 | 28.3
COUW31 | COUW32 | 0 | 4 | Cable | 4.776 | 4.152 | 0.34 | 29.4 | 26.7 | 26.7 | 26.7
COUW31 | FRSD3- | 9 | 0 | OHL | 4.104 | 9.171 | 0.99 | 47.9 | 46.9 | 43.4 | 46.9
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 145 | 131 | 116 | 131
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103
DAAS3- | CAIR3W | 0 | 1 | Cable | 1.193 | 3.427 | 0.406 | 49 | 49 | 49 | 49
DAAS3- | CAIR3W | 0 | 1 | Cable | 1.193 | 3.427 | 0.406 | 49 | 49 | 49 | 49
DAAS3- | CAIR3W | 0 | 1 | Cable | 1.193 | 3.427 | 0.406 | 49 | 49 | 49 | 49
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.37 | 1.86 | 0.45 | 183 | 160 | 149 | 160
DOUN2- | CONN2J | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 702 | 665 | 599 | 665
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.4621 | 3.1663 | 12.268 | 535 | 490 | 430 | 490
DOUN2- | THUS2J | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DUBE1Q | MYBS1R | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 117 | 101 | 117
DUBE3- | DUBE3D | 0 | 1 | Cable | 4.55 | 1.13 | 0.216 | 26 | 26 | 26 | 26
DUDH1Q | GLAG1Q | 0 | 1.95 | Cable | 0.0582 | 0.1153 | 2.908 | 160 | 145 | 145 | 145
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 0 | 1.95 | Cable | 0.0582 | 0.1153 | 2.908 | 160 | 145 | 145 | 145
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 83 | 77 | 67 | 77
DUGR3- | BENA3- | 5 | 0 | OHL | 5.3 | 14.55 | 0 | 34.3 | 32.3 | 29.2 | 32.3
DUNM1- | DUNM1C | 6 | 0 | OHL | 0.3023 | 1.2424 | 0.336 | 203 | 193 | 176 | 193
DYCE1J | ABBA1- | 0 | 7.8 | Cable | 0.1092 | 1.2324 | 10.14 | 173 | 158 | 158 | 158
DYCE1Q | DYCE1J | 1.93 | 0 | OHL | 0.0978 | 0.4332 | 0.33 | 241 | 230 | 210 | 230
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.5187 | 2.2781 | 0.525 | 241 | 230 | 210 | 230
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.6335 | 2.2972 | 0.519 | 145 | 131 | 116 | 131
DYCE3- | STOM3- | 0 | 1 | Cable | 3.51 | 3.023 | 0 | 24 | 24 | 24 | 24
ELGI1L | NAIR1Q | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1M | NAIR1R | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1Q | ELGI1L | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1Q | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1R | ELGI1M | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1R | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280
ERRO1J | ERRO1A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1K | ERRO1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123
FARI1J | COGA1C | 0 | 4.11 | Cable | 0.065 | 0.334 | 6.245 | 176 | 176 | 176 | 176
FARI1K | DUNM1C | 0 | 4.07 | Cable | 0.064 | 0.28 | 6.175 | 210 | 196 | 196 | 196
FASN2- | FAUG2J | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830
FAUG1- | FAUG1M | 0 | 0.29 | Cable | 0.0106 | 0.0196 | 0.357 | 153 | 134 | 134 | 134
FAUG1- | FAUG1N | 0 | 0.2 | Cable | 0.01 | 0.0137 | 0.249 | 153 | 134 | 134 | 134
FAUG1- | FAUG1P | 0 | 0.59 | Cable | 0.01 | 0.0602 | 0.868 | 202 | 202 | 202 | 202
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.01 | 0.012 | 0.002 | 126 | 117 | 101 | 117
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127
FAUG1- | LAGG1Q | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1- | LAGG1R | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1M | LOCL1Q | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 8.5 | 0 | OHL | 0.7735 | 1.972 | 0.425 | 126 | 117 | 101 | 117
FAUG1P | LOCL1S | 8.66 | 0 | OHL | 0.4365 | 1.7942 | 0.485 | 203 | 193 | 176 | 193
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FAUG4- | MELG4J | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.7089 | 1.0659 | 0.265 | 83 | 77 | 67 | 77
FETT2P | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 999 | 999 | 999 | 999
FETT2Q | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 999 | 999 | 999 | 999
FETT2Q | KINB2J | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT3S | MIHW3- | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 48.6 | 48.6 | 48.6 | 48.6
FETT3S | MIHW3- | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 48.6 | 48.6 | 48.6 | 48.6
FIDD1Q | FOGG1R | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD3- | TULW3- | 15 | 0 | OHL | 11.1 | 14.4 | 1.53 | 38.3 | 38.1 | 34.8 | 38.1
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 111 | 103 | 89 | 103
FOYE2- | FARI2J | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FOYE2- | FARI2K | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FOYE2- | FOYE2J | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 133 | 124 | 107 | 124
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.1759 | 8.0968 | 1.745 | 126 | 117 | 101 | 117
FWIL3- | LHBR3- | 0 | 1.3 | Cable | 0.51 | 1.25 | 0.15 | 53.7 | 48.6 | 48.6 | 48.6
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
GLDO8- | GLDO8J | 0 | 1.2 | Cable | 0.39 | 1.02 | 0.01 | 131 | 131 | 131 | 131
GLEN1Q | BHLA11 | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 208 | 187 | 187 | 187
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.546 | 1.132 | 0.232 | 221 | 216 | 208 | 216
GLFA3- | PAUL3- | 0 | 1 | Cable | 4.193 | 12.043 | 1.428 | 49 | 49 | 49 | 49
GLFA3- | PAUL3- | 0 | 1 | Cable | 4.193 | 12.043 | 1.428 | 49 | 49 | 49 | 49
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0819 | 0.5613 | 2.175 | 535 | 490 | 430 | 490
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211
HYWD30 | HYWD31 | 0 | 1.5 | Cable | 0.58 | 1.41 | 0.17 | 40.6 | 40.6 | 40.6 | 40.6
HYWD31 | HYWD32 | 0 | 26 | Cable | 19.11 | 26.26 | 2.31 | 32.6 | 32.6 | 32.6 | 32.6
INGA1Q | LOCL1Q | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.1051 | 0.3818 | 6.326 | 171 | 165 | 165 | 165
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1042 | 0.3784 | 6.27 | 171 | 165 | 165 | 165
INNE1Q | NAIR1Q | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1R | INNE1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
INNE1T | NAIR1R | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE3- | MOYW3- | 17.5 | 0 | OHL | 3.99 | 8.9 | 3.83 | 95.8 | 93.8 | 86.8 | 93.8
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 142 | 128 | 142
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.18 | 0.41 | 0.09 | 126 | 117 | 101 | 117
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.311 | 1.3664 | 0.317 | 202 | 193 | 176 | 193
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 117 | 101 | 117
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.18 | 0.41 | 0.09 | 126 | 117 | 101 | 117
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.311 | 1.3664 | 0.317 | 202 | 193 | 176 | 193
INRU1S | PEHE1- | 0 | 3 | Cable | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181
INVE1J | ACHR1R | 21.17 | 0 | OHL | 3.002 | 4.9754 | 1.035 | 99 | 92 | 79 | 92
INVE1J | FERO1S | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
INVE1K | ANSU1- | 11.13 | 0 | OHL | 1.578 | 2.615 | 0.544 | 99 | 92 | 79 | 92
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
INVE1K | SLOY1J | 22.6 | 0 | OHL | 2.29 | 5.25 | 1.11 | 126 | 117 | 101 | 117
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126
KEIT1- | GLFA1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117
KEIT1- | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT3- | EDNT3- | 0 | 4.55 | Cable | 5.43 | 4.72 | 0.39 | 29.4 | 26.7 | 26.7 | 26.7
KEIT3- | GLOF3J | 25.5 | 0 | OHL | 62.749 | 83.8449 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KEIT3- | KEIT39 | 18.6 | 0 | OHL | 47.608 | 52.757 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
KEITH3A | HITO3- | 9 | 0 | OHL | 0.73 | 0.97 | 0.11 | 38.3 | 37.5 | 34.8 | 37.5
KEITH3A | HITO3- | 9 | 0 | OHL | 0.73 | 0.97 | 0.11 | 38.3 | 37.5 | 34.8 | 37.5
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 111 | 103 | 89 | 103
KIIN3- | LOCH3- | 0 | 1 | Cable | 3 | 7 | 0 | 24 | 24 | 24 | 24
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 83 | 77 | 67 | 77
KILC1Q | TAYN1Q | 7.562 | 0.038 | Composite | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILO3- | KILO3Q | 0 | 1 | Cable | 0.8 | 3.24 | 0.01 | 43 | 41 | 38 | 41
KINT1- | FOGG1Q | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 104 | 90 | 104
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.0154 | 0.354 | 148 | 140 | 140 | 140
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.0148 | 0.341 | 148 | 140 | 140 | 140
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030
KINT2J | TEAL2J | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | FETT2P | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 880 | 760 | 880
KINT2K | FETT2Q | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 885 | 760 | 885
KINT2K | PEHE2Q | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KINT2K | TEAL2K | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT3- | GLOF3K | 33.7 | 0 | OHL | 82.928 | 115.3029 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KINT3- | GOHI3- | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
KNOC2J | BERB2Q | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
KNOC2J | FARI2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.042 | 8.36 | 930 | 900 | 900 | 900
KNOC2K | DAAS2- | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
KNOC2K | FARI2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
KNOC2M | KNOC2K | 0 | 1.29 | Cable | 0.01 | 0.037 | 7.336 | 930 | 900 | 900 | 900
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.648 | 1.344 | 0.276 | 221 | 216 | 208 | 216
LAIR1Q | SHIN1- | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 111 | 103 | 89 | 103
LAIR3- | LAIR3W | 0 | 10 | Cable | 4.564 | 10.193 | 1.095 | 40 | 40 | 40 | 40
LAIR3- | LAIR3W | 0 | 10 | Cable | 4.564 | 10.193 | 1.095 | 40 | 40 | 40 | 40
LOCH3- | LUBR3- | 0 | 1 | Cable | 21 | 45 | 0 | 24 | 24 | 24 | 24
LOCL1S | QUOI1Q | 18.3 | 0 | OHL | 1.91 | 4.54 | 0.9 | 111 | 103 | 89 | 103
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 133 | 124 | 107 | 124
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 133 | 124 | 107 | 124
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUND- | FWIL1Q | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129
LUND- | KILO1- | 15.2 | 0 | OHL | 1.054 | 3.441 | 0.775 | 111 | 103 | 89 | 103
MACD3- | BOYN3Q | 8 | 0 | OHL | 5.95 | 7.71 | 0.82 | 38.3 | 37.5 | 34.8 | 37.5
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILW1S | BEIN11 | 2.8 | 0 | OHL | 0.319 | 0.66 | 0.135 | 221 | 216 | 208 | 216
MILW1S | MILW1Q | 1.3 | 0 | OHL | 0.065 | 0.2691 | 0.073 | 203 | 193 | 176 | 193
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MYBS1Q | LOCB1J | 81.61 | 0 | OHL | 8.2998 | 19.0008 | 4.028 | 126 | 117 | 101 | 117
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1S | SPIT1M | 4.5 | 0 | OHL | 0.104 | 1.002 | 0.237 | 463 | 444 | 415 | 444
MYBS1T | SPIT1K | 4.5 | 0 | OHL | 0.104 | 1.002 | 0.237 | 463 | 444 | 415 | 444
MYBS3J | ACHL3- | 0 | 2 | Cable | 2.39 | 2.07 | 0.17 | 29.4 | 26.7 | 26.7 | 26.7
MYBS3J | BUWH3- | 20 | 0 | OHL | 2.388 | 20.6999 | 1.7 | 32.6 | 28.8 | 26.7 | 28.8
MYBS3J | WATH3- | 0 | 5 | Cable | 5.875 | 5.6 | 0.4 | 26.3 | 26.3 | 26.3 | 26.3
MYBS3K | CAMW3W | 12 | 0 | OHL | 3.24 | 5.52 | 2.64 | 75.7 | 66.9 | 62.1 | 66.9
MYBS3K | CAUS3J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 34 | 34 | 34 | 34
MYBS3K | CAUS3K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 34 | 34 | 34 | 34
MYBS3N | BADA3- | 0 | 5 | Cable | 2.28 | 5.095 | 0.55 | 47.9 | 43.4 | 43.4 | 43.4
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1R | ORRI1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1S | DUCC1J | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
ORRI1T | DUCC1K | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
ORRI3- | FAWI3W | 3.5 | 0 | OHL | 1.28 | 3.44 | 0.69 | 59.5 | 52.7 | 48.8 | 52.7
PEHE2- | PEHE2S | 0 | 1 | Cable | 0.01 | 0.033 | 14.21 | 776 | 776 | 776 | 776
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE2T | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.032 | 13.51 | 776 | 776 | 776 | 776
PEHE2U | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2V | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2W | PEHEMEC1 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHG3- | HYWD30 | 0 | 0.5 | Cable | 0.19 | 0.47 | 0.06 | 40.6 | 40.6 | 40.6 | 40.6
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PORA1Q | ANSU1- | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99 | 92 | 79 | 92
PORA1Q | CRSS1Q | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
PORA1R | ACHR1R | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
PORA1R | CRSS1R | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 126 | 119 | 108 | 119
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
REDM3- | KINW3 | 24 | 0 | OHL | 17.52 | 23.28 | 4.8 | 38.4 | 37.5 | 34.6 | 37.5
REDM3- | KINW3 | 24 | 0 | OHL | 17.52 | 23.28 | 4.8 | 38.4 | 37.5 | 34.6 | 37.5
SFEG1Q | SFEG1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1R | SFEG1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1S | SFEG1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFEM5J | SFEM5K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1L | SFEG1Q | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 117 | 101 | 117
SFER1L | SFEM1Q | 3.1 | 0 | OHL | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1M | SFEG1R | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 117 | 101 | 117
SFER1M | SFEM1R | 3.1 | 0 | OHL | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SHET1J | SHET1R | 0 | 1 | Cable | 0.01 | 0.11 | 0 | 720 | 720 | 720 | 720
SHIN1- | LOCB1J | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 117 | 101 | 117
SHIN1- | LOCB1K | 12.18 | 0 | OHL | 1.239 | 2.8365 | 0.604 | 126 | 117 | 101 | 117
SHIN3- | ROSE3- | 9.5 | 0 | OHL | 8.93 | 9.5 | 0.855 | 33.6 | 32 | 30.5 | 32
SLOY1J | GARB1R | 14.1848 | 0.7152 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
SLOY1J | GARB1S | 14.2295 | 0.6705 | Composite | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
SLOY1J | SLOY1N | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 111 | 103 | 89 | 103
SLOY1J | SLOY1P | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 111 | 103 | 89 | 103
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123
SLOY1K | GARB1Q | 14.2295 | 0.6705 | Composite | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
SLOY1K | GARB1T | 14.1848 | 0.7152 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
SLOY1K | INVR1- | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126
SLOY1K | SLOY1L | 1.2896 | 0.0104 | Composite | 0.13 | 0.3 | 0.06 | 111 | 103 | 89 | 103
SLOY1K | SLOY1M | 1.2896 | 0.0104 | Composite | 0.13 | 0.3 | 0.06 | 111 | 103 | 89 | 103
SPIT2K | SPIT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 960 | 960 | 960 | 960
STRB2- | LOCB2K | 18.9 | 0 | OHL | 0.1503 | 1.0299 | 3.991 | 535 | 490 | 430 | 490
STRL1- | MELG1J | 0 | 10 | Cable | 0.061 | 0.798 | 18.0121 | 317 | 281 | 281 | 281
STRW12 | STRW1C | 0 | 0.35 | Cable | 0.01 | 0.0631 | 0.48 | 200 | 178 | 178 | 178
TARL1Q | FOGG1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
TARL1R | FOGG1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
TARL3- | TARL3J | 9.8 | 0 | OHL | 15.17 | 32.24 | 0 | 26.5 | 24.7 | 21.3 | 24.7
TARL3J | TARL3K | 15.3 | 0 | OHL | 25.2501 | 50.7999 | 0 | 25.2 | 23.9 | 21.6 | 23.9
TAYN1R | FERO1S | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92
TAYN3- | INAW3Q | 0 | 1 | Cable | 2.04 | 1.59 | 0.05 | 30 | 30 | 30 | 30
TEAL1- | BIHI1Q | 5.4992 | 0.1008 | Composite | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
TEAL1- | BIHI1R | 5.4992 | 0.1008 | Composite | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
TEAL2J | KINB2K | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
TEAL2J | WFIB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2K | FETT2P | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
TEAL2K | GLRB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
THUS2J | SPIT2J | 12.1 | 0 | OHL | 0.0605 | 0.6655 | 2.577 | 965 | 925 | 865 | 925
THUS2K | SPIT2K | 12.1 | 0 | OHL | 0.0605 | 0.6655 | 2.577 | 965 | 925 | 865 | 925
THUS3- | STRS30 | 0 | 27 | Cable | 12.32 | 27.5199 | 2.96 | 47.9 | 43.4 | 43.4 | 43.4
TUMM4- | BONB4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670
TUMM4- | MELG4J | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670
WHIB1A | ERRO1J | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1B | ERRO1K | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1G | GRIF1T | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
WHIB1H | GRIF1S | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147

## B-2-1b
Table B.2.1b - SPT Circuits ETYS Yr1 - 2018/19 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.43633 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.67477 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.10903 | 0.83007 | 2.9503 | 570 | 570 | 570 | 570
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 2e-06 | 0.008959 | 0.068205 | 140 | 140 | 140 | 140
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.042843 | 0.39661 | 2.542 | 955 | 885 | 760 | 885
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.042843 | 0.39661 | 2.542 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.71964 | 3.9815 | 0.96906 | 146 | 146 | 146 | 146
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.57721 | 1.4684 | 2.8736 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.72357 | 4.0032 | 0.97436 | 146 | 146 | 146 | 146
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.57678 | 1.4673 | 2.8658 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.27751 | 1.5328 | 0.46581 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.28107 | 1.5519 | 0.69919 | 114 | 114 | 114 | 114
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.9649 | 5.0014 | 1.5026 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.9642 | 4.9975 | 1.4468 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.029596 | 0.21272 | 0.071297 | 418 | 386 | 386 | 386
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.029596 | 0.21272 | 0.071297 | 466 | 430 | 418 | 430
BLAH1- | GLGL1Q | 13.6 | 0.375 | Composite | 0.5234 | 3.0382 | 1.176 | 134 | 123 | 123 | 123
BLAH1- | GLGL1R | 13.6 | 0.375 | Composite | 0.5234 | 3.0382 | 1.176 | 134 | 123 | 123 | 123
BLCW1- | MARG1- | 1.8 | 0 | OHL | 0.13522 | 0.39606 | 0.094795 | 166 | 159 | 147 | 159
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.65421 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.05485 | 0.81047 | 5.6521 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.025925 | 0.38307 | 11.9581 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.42822 | 2.3699 | 0.57646 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.42822 | 2.3699 | 0.57646 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 8.08 | 0.3 | Composite | 0.18756 | 0.42387 | 1.241 | 240 | 234 | 202 | 234
BONN1- | STIR1S | 3.3 | 12.2 | Composite | 0.25248 | 1.5536 | 21.8264 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 3.3 | 12.2 | Composite | 0.25248 | 1.5536 | 21.8264 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.01852 | 0.18073 | 4.3533 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.018337 | 0.17825 | 3.8059 | 722 | 647 | 593 | 647
BRAE1G | BRAP1- | 0 | 2.5 | Cable | 0.049788 | 0.20805 | 3.5991 | 250 | 250 | 250 | 250
BRAE1G | GOVA1R | 0 | 3.5 | Cable | 0.152 | 0.239 | 6.934 | 125 | 113 | 110 | 113
BRAE1P | GOVA1Q | 0 | 3.5 | Cable | 0.152 | 0.239 | 6.934 | 125 | 113 | 110 | 113
BRAE1P | PAIS1Q | 4.52 | 0 | OHL | 0.089547 | 0.85193 | 0.27542 | 268 | 268 | 268 | 268
BRAP1- | ERSK1Q | 3.17 | 5.19 | Composite | 0.46054 | 1.3015 | 5.2712 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6 | Composite | 0.47495 | 1.4274 | 6.4114 | 102 | 79 | 79 | 79
BRAP1- | PAIS1R | 4.52 | 2.59 | Composite | 0.13998 | 1.0674 | 4.2386 | 274 | 274 | 274 | 274
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.79713 | 2.4031 | 0.51619 | 132 | 123 | 106 | 123
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.79713 | 2.4031 | 0.51619 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.087023 | 0.85972 | 5.4929 | 1120 | 1060 | 990 | 1060
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.06509 | 0.6428 | 4.1106 | 750 | 690 | 630 | 690
CAFA5- | CAFA5R | 0 | 0 | Series Reactor | 0.33333 | 21.1544 | 0 | 30 | 30 | 30 | 30
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.23415 | 0.52894 | 0.14457 | 132 | 123 | 106 | 123
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.30183 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.30183 | 6.1089 | 122 | 107 | 107 | 107
CHAP1- | DUMF1- | 26.9 | 0 | OHL | 1.0611 | 5.8608 | 1.9647 | 171 | 171 | 171 | 171
CHAP1- | ECCF1J | 6.569 | 0.181 | Composite | 0.60152 | 1.5317 | 0.89809 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.126 | Composite | 0.6003 | 1.527 | 0.72438 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.1764 | 2.9978 | 1.0015 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 1.1751 | 2.9926 | 0.94954 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.01925 | 0.1782 | 1.1421 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.01955 | 0.1806 | 1.8131 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 9.17 | 0 | OHL | 0.021036 | 0.33756 | 2.8562 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.025567 | 0.24883 | 1.4571 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.025567 | 0.24883 | 1.4571 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.22 | 0 | OHL | 0.12438 | 1.9959 | 16.8879 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.058 | 0.079 | 24.356 | 291 | 245 | 245 | 245
COAL1- | GAWH1Q | 0 | 10.5 | Cable | 0.16512 | 0.90393 | 17.3003 | 241 | 241 | 241 | 241
COAL1- | LINM1Q | 8.97 | 0 | Cable | 0.16342 | 1.5637 | 6.2562 | 134 | 123 | 123 | 123
COAL1- | LINM1R | 8.91 | 0 | Cable | 0.2748 | 1.516 | 2.8754 | 134 | 123 | 123 | 123
COAL1- | MIDM1- | 0 | 14.47 | Cable | 0.40859 | 0.93923 | 17.8217 | 194 | 181 | 181 | 181
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.047473 | 0.53038 | 15.5286 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038622 | 0.43149 | 12.6334 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.04518 | 0.25418 | 17.1143 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.04518 | 0.25418 | 17.1143 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.078564 | 0.77714 | 4.9683 | 1090 | 1030 | 925 | 1030
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.04085 | 0.40408 | 2.5833 | 1090 | 1030 | 925 | 1030
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.1417 | 1.3791 | 36.149 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.14168 | 1.3789 | 36.1435 | 1090 | 1030 | 925 | 1030
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4035 | 1.0262 | 0.50656 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.84308 | 2.1714 | 1.0596 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.285 | 0.08 | Composite | 0.0058148 | 0.053577 | 0.45572 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.005896 | 0.054282 | 0.36908 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.36123 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.053773 | 0.60076 | 3.9295 | 1540 | 1480 | 1380 | 1480
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.053773 | 0.60076 | 3.9295 | 1540 | 1480 | 1380 | 1480
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.946 | 0 | Composite | 1.6113 | 4.0336 | 1.1914 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 14.135 | 0 | OHL | 0.059707 | 0.54891 | 3.744 | 1120 | 1060 | 990 | 1060
COYW2T | KILS2- | 14.135 | 0 | OHL | 0.059707 | 0.54891 | 3.744 | 1120 | 1060 | 990 | 1060
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4966 | 2.7546 | 0.97161 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.49672 | 2.7556 | 0.98555 | 229 | 211 | 183 | 211
CRUA2Q | CRUA2S | 0 | 0.4 | Cable | 0.0001 | 0.010256 | 2.0513 | 283 | 283 | 283 | 283
CRUA2R | CRUA2T | 0 | 0.4 | Cable | 0.0001 | 0.010256 | 2.0513 | 283 | 283 | 283 | 283
CRUA2S | DALL2- | 8.16 | 0 | OHL | 0.035051 | 0.34672 | 2.2166 | 570 | 570 | 570 | 570
CRUA2T | DALL2- | 8.16 | 0 | OHL | 0.035051 | 0.34672 | 2.2166 | 570 | 570 | 570 | 570
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.055895 | 0.34727 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.018044 | 0.26639 | 8.3478 | 2473 | 2349 | 2148 | 2349
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.014156 | 0.21246 | 44.2495 | 935 | 785 | 785 | 785
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.207 | 3.0626 | 0.65939 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.207 | 3.0626 | 0.65939 | 143 | 142 | 128 | 142
CURR1B | GORG1Q | 1.49 | 5.78 | Composite | 0.26242 | 0.95214 | 5.0969 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.79542 | 2.3146 | 6.4736 | 132 | 123 | 106 | 123
CURR1A | GORG1R | 1.49 | 5.8 | Composite | 0.26313 | 0.95431 | 5.1142 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.80001 | 2.3287 | 6.5864 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.18 | 0 | OHL | 0.19286 | 1.7854 | 11.4431 | 1090 | 1030 | 920 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.042752 | 0.39576 | 2.5366 | 1090 | 1030 | 925 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.042752 | 0.39576 | 2.5366 | 1090 | 1030 | 925 | 1030
CURR2- | KINC2- | 55.82 | 0 | OHL | 0.25523 | 2.3627 | 15.1435 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.017332 | 0.10214 | 6.0434 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.01715 | 0.10149 | 5.9441 | 120 | 120 | 120 | 120
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.096863 | 0.95814 | 6.1255 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.33569 | 3.3206 | 21.2289 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.19546 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.16321 | 0.21894 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 32.08 | 0 | OHL | 0.14628 | 1.3541 | 8.6789 | 957 | 881 | 762 | 881
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.050694 | 0.80689 | 6.6393 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.56525 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 123 | 106 | 123
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.69402 | 1.7609 | 0.37914 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.6831 | 1.7333 | 0.37317 | 107 | 107 | 101 | 107
DEVM4- | HUNE4- | 50.471 | 0.167 | Composite | 0.090488 | 0.97976 | 33.476 | 1316 | 1067 | 1067 | 1067
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.047004 | 0.54534 | 17.8155 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1T | 5.8 | 5.4 | Composite | 0.31365 | 1.7888 | 7.1063 | 162 | 154 | 141 | 154
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8876 | 7.3367 | 1.5779 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.015938 | 0.055946 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.016387 | 0.057525 | 7.9728 | 276 | 240 | 240 | 240
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.011447 | 0.11212 | 3.8774 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.011248 | 0.10413 | 0.66738 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNB1Q | INWI1Q | 11.6 | 0 | OHL | 1.0551 | 2.6772 | 0.57641 | 110 | 100 | 90 | 100
DUNB1R | INWI1R | 11.6 | 0 | OHL | 1.0551 | 2.6772 | 0.57641 | 110 | 100 | 90 | 100
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 152 | 122 | 122 | 122
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.69341 | 1.7561 | 0.55253 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1- | 10.46 | 0 | OHL | 0.5579 | 2.348 | 0.541 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.69341 | 1.7561 | 0.55253 | 132 | 122 | 106 | 122
DUNF1R | MOSM1- | 10.46 | 0 | OHL | 0.55786 | 2.348 | 0.54104 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.03696 | 0.27589 | 159 | 147 | 147 | 147
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3513 | 2.5249 | 0.84627 | 484 | 458 | 418 | 458
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.04092 | 0.30544 | 159 | 147 | 147 | 147
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3513 | 2.5249 | 0.84627 | 484 | 458 | 418 | 458
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.2923 | 3.8204 | 0.98371 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.2923 | 3.8204 | 0.98371 | 99 | 92 | 79 | 92
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.15337 | 0.34647 | 0.094699 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.848 | 7.3696 | 1.5301 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8142 | 7.133 | 1.538 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.00652 | 0.12694 | 4.9754 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.00652 | 0.12694 | 4.9754 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 46.23 | 0 | OHL | 0.10605 | 1.7018 | 14.3993 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.014046 | 0.19251 | 1.6118 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.021791 | 0.21208 | 1.2419 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.014086 | 0.18599 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.021791 | 0.21208 | 1.2419 | 1050 | 965 | 880 | 965
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.12718 | 1.2564 | 8.0276 | 1120 | 1060 | 990 | 1060
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.024933 | 0.24608 | 1.5758 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 0 | 2.79 | Cable | 0.12 | 0.559 | 0.684 | 229 | 211 | 183 | 211
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.15243 | 0.84871 | 0.45318 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 0 | 2.79 | Cable | 0.121 | 0.561 | 0.73 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 3.82 | 0.23 | Cable | 0.15305 | 0.85353 | 0.52289 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.11649 | 1.3014 | 38.1036 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.041768 | 0.46664 | 13.6624 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.086308 | 0.96426 | 28.2318 | 2210 | 2130 | 1980 | 2130
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
ESST1R | KIER1R | 0 | 4.56 | Cable | 0.133 | 0.19 | 8.531 | 100 | 80 | 60 | 80
ESST1R | WIYH1- | 2.089 | 1.376 | Composite | 0.236 | 0.6357 | 2.5748 | 233 | 200 | 200 | 200
EWEH1Q | GRNA1- | 15.7 | 0.12 | Composite | 1.1828 | 3.4623 | 0.98442 | 131 | 131 | 131 | 131
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.040489 | 0.59776 | 18.7313 | 2473 | 2349 | 2148 | 2349
FIFE1A | WFIE1A | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 100 | 100 | 100
FIFE1B | WFIE1B | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 100 | 100 | 100
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.056344 | 0.15821 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.056985 | 0.16002 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1- | 15.3129 | 0 | OHL | 1.3918 | 3.5305 | 0.76154 | 132 | 123 | 106 | 123
GARB1R | STLE1- | 26.9091 | 0 | OHL | 2.4458 | 6.2041 | 1.3382 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.0304 | 0 | OHL | 0.45722 | 1.1598 | 0.25017 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.0609 | 0 | OHL | 0.46 | 1.1668 | 0.25169 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.21277 | 0.3546 | 0.091306 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.0819 | 0.3304 | Composite | 3.2036 | 8.1237 | 2.3777 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2115 | 0.35249 | 0.090762 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.7398 | 0.1623 | Composite | 3.1649 | 8.0269 | 2.0386 | 109 | 105 | 101 | 105
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.69701 | 1.6798 | 0.40483 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7324 | 6.933 | 1.4927 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7324 | 6.933 | 1.4927 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0011 | 5.0774 | 1.0932 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0011 | 5.0774 | 1.0932 | 49 | 49 | 49 | 49
GLNI1- | MOSM1- | 1.41 | 0.09 | Composite | 0.065394 | 0.24481 | 0.37686 | 171 | 171 | 171 | 171
GLNI1- | MOSM1- | 1.41 | 0.11 | Composite | 0.065663 | 0.24654 | 0.43926 | 171 | 171 | 171 | 171
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.95552 | 2.3056 | 0.55203 | 161 | 156 | 145 | 156
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.35905 | 0.7999 | 0.7252 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.53 | 0 | OHL | 0.067007 | 0.63749 | 3.8824 | 875 | 875 | 760 | 875
GLRO2- | WFIE2- | 11.92 | 0 | OHL | 0.055139 | 0.52459 | 3.1948 | 955 | 885 | 760 | 885
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GOVA1Q | HAGR1Q | 0 | 4.2 | Cable | 0.218 | 0.262 | 6.322 | 70 | 64 | 64 | 64
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068403 | 0.63322 | 4.0585 | 1050 | 965 | 880 | 965
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 5.0351 | 12.8073 | 2.7435 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.43115 | 1.094 | 0.23553 | 132 | 123 | 106 | 123
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.07783 | 0.86954 | 25.4586 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.304 | 1.375 | 21.563 | 184 | 184 | 184 | 184
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 4.5794 | 11.6508 | 2.4946 | 132 | 123 | 106 | 123
HELE1- | WIYH1- | 24.7994 | 0.182 | Composite | 2.2623 | 5.7372 | 1.582 | 109 | 105 | 101 | 105
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.000334 | 0.008879 | 7.3943 | 1448 | 1448 | 1448 | 1448
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.000339 | 0.009012 | 7.5055 | 1448 | 1448 | 1448 | 1448
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.000142 | 0.00103 | 0.72634 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.000142 | 0.00103 | 0.72634 | 2770 | 2770 | 2770 | 2770
HUER4- | KILS4- | 59.125 | 0 | OHL | 0.084881 | 1.0902 | 37.0252 | 2030 | 1930 | 1770 | 1930
HUER4- | STHA4B | 94.151 | 0 | OHL | 0.1559 | 1.7959 | 57.0851 | 1995 | 1926 | 1787 | 1926
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.000793 | 0.002746 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.000542 | 0.001877 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | NEIL4Q | 35.617 | 0.167 | Composite | 0.071227 | 0.71725 | 23.749 | 1320 | 1070 | 1070 | 1070
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.60243 | 3.1055 | 6.8778 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.43357 | 2.1725 | 6.6108 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.021179 | 0.10684 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.021625 | 0.10873 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.23883 | 2.3624 | 15.1033 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 110 | 100 | 90 | 100
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 110 | 100 | 90 | 100
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.48831 | 2.7025 | 0.65735 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.32009 | 1.7715 | 0.43089 | 151 | 151 | 151 | 151
KAIM2- | SMEA2- | 8.64 | 0 | OHL | 0.037714 | 0.37306 | 2.385 | 1090 | 1030 | 925 | 1030
KAIM2- | WHHO2Q | 0 | 6.45 | Cable | 0.041483 | 0.14562 | 20.1822 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.22 | Cable | 0.040467 | 0.14205 | 19.6882 | 276 | 240 | 240 | 240
KEOO1- | NECU1R | 26.51 | 0 | OHL | 0.82922 | 5.0188 | 1.6132 | 133 | 123 | 106 | 123
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3888 | 0.94223 | 7.6146 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14.4 | Cable | 0.071932 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.45 | Composite | 0.01774 | 0.16081 | 2.059 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 3.56 | 0.45 | Composite | 0.017945 | 0.16166 | 2.2132 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.070896 | 0.70412 | 20.0164 | 1995 | 1926 | 1787 | 1926
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.736 | 3.0978 | 0.71381 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.736 | 3.0978 | 0.71381 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.325 | 0.385 | Composite | 0.047363 | 0.44069 | 6.9969 | 760 | 620 | 620 | 620
KINB2K | KINC2- | 10.71 | 0 | OHL | 0.04897 | 0.45333 | 2.9052 | 910 | 885 | 760 | 885
KINC2- | LOAN2Q | 4.28 | 0.31 | Composite | 0.018987 | 0.19016 | 4.4568 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 4.28 | 0.17 | Composite | 0.018749 | 0.18624 | 2.8678 | 765 | 620 | 620 | 620
COAL1- | KYPE1- | 0 | 17.09 | Cable | 0.32865 | 1.5387 | 24.4568 | 229 | 215 | 215 | 215
LAMB2- | LAMB2T | 0.001 | 0 | Cable | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.018015 | 0.16677 | 1.0689 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.019015 | 0.16877 | 2.1709 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.076876 | 0.75948 | 4.8524 | 1050 | 965 | 880 | 965
LAMB2T | LOAN2- | 53.67 | 0.225 | Composite | 0.19776 | 2.1709 | 17.8013 | 795 | 620 | 620 | 620
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.076876 | 0.75948 | 4.8524 | 950 | 885 | 760 | 885
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.19647 | 0.49851 | 0.10733 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.20557 | 0.52159 | 0.1123 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.78316 | 1.9871 | 0.42783 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.5939 | 4.2994 | 0.93538 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | MOSM2L | 26.196 | 0.194 | Composite | 0.12005 | 1.142 | 8.6702 | 760 | 620 | 620 | 620
LOAN2- | WFIE2- | 29.169 | 0.154 | Composite | 0.13352 | 1.2702 | 9.0972 | 760 | 620 | 620 | 620
MARG1- | NECU1Q | 34.35 | 0.9 | Composite | 1.1434 | 6.7098 | 3.5381 | 241 | 230 | 210 | 230
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1521 | 2.9259 | 0.95789 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOSH1Q | MOSM1- | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1- | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | MOSM2L | 5.3 | 0 | OHL | 0.024192 | 0.23016 | 1.4017 | 955 | 885 | 760 | 885
MOSM2- | MOSM2T | 5.3 | 0 | OHL | 0.024192 | 0.23016 | 1.4017 | 955 | 885 | 760 | 885
MOSM2T | WFIE2- | 2.943 | 0 | OHL | 0.013433 | 0.1278 | 0.77832 | 955 | 885 | 760 | 885
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.073615 | 0.68147 | 4.3678 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.073615 | 0.68147 | 4.3678 | 285 | 285 | 285 | 285
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.012571 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.17004 | 1.5479 | 0.93618 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.17824 | 1.5629 | 0.77447 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.11073 | 1.0811 | 6.9183 | 957 | 881 | 764 | 881
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.037054 | 0.34373 | 0.117 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.037054 | 0.34373 | 0.117 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.034051 | 0.33547 | 2.9286 | 360 | 300 | 240 | 300
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.034051 | 0.33547 | 2.9286 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
RAVE3- | WISH3S | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3S | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3T | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3T | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.81077 | 2.3122 | 0.50754 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 75.76 | 0 | OHL | 0.16257 | 1.517 | 43.53 | 1390 | 1280 | 1110 | 1280
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.072659 | 1.0761 | 70.7405 | 945 | 800 | 800 | 800
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1333 | 1.2364 | 35.4874 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0243 | 0.2326 | 6.6686 | 2000 | 1920 | 1790 | 1920
STIR1S | WFIE1A | 37.6 | 5.4 | Composite | 3.2013 | 9.1255 | 8.6842 | 162 | 154 | 141 | 154
STLE1- | WIYH1- | 12.8916 | 0.2908 | Composite | 1.1849 | 3.0034 | 1.1983 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.25 | 0 | OHL | 0.10261 | 0.97622 | 5.9452 | 950 | 885 | 760 | 885
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
Table B.2.1c - NGET Circuits ETYS Yr1 - 2018/19 | [11 empty] | Back To Menu
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABHA41 | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 1389 | 1284 | 1108 | 1284
ABHA41 | LAGA41 | 26.121 | 0 | OHL | 0.0423 | 0.5251 | 15.0165 | 1389 | 1284 | 1108 | 1284
ABHA42 | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078
ABHA42 | LAGA41 | 26.121 | 0 | OHL | 0.0423 | 0.5251 | 15.0165 | 2423 | 2327 | 2168 | 2327
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629
ABTH21 | UPPB22 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882
ABTH22 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879
ABTH22 | UPPB21 | 27.035 | 1.094 | parallel Composite | 0.124 | 1.1519 | 19.226 | 772 | 772 | 772 | 595
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882
ALVE41 | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE41 | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM41 | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933
AMEM41 | IVER41 | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 1975 | 1933 | 1766 | 1933
AMEM42 | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911
AMEM42 | IVER42 | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2009 | 1911 | 1746 | 1911
AXMI41 | CHIC42 | 39.5 | 0 | OHL | 0.0429 | 0.687 | 26.0389 | 2779 | 2568 | 2217 | 2568
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2779 | 2568 | 2568 | 2568
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115
BAGB21 | SWAN2A | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431
BARK21 | BARP22 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK21 | REBR21 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081
BARK22 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK22 | REBR22 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127
BARK41 | LAKE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | LAKE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0155 | 0.191 | 5.6429 | 2009 | 1911 | 1746 | 1911
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0156 | 0.1915 | 10.4541 | 2009 | 1909 | 1710 | 1909
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.068 | 0.7365 | 7.9729 | 944 | 882 | 762 | 835
BEDD21 | WIMB21 | 8.5 | 1.968 | Composite | 0.0412 | 0.3922 | 10.7954 | 1100 | 1100 | 1100 | 1100
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0677 | 0.7328 | 6.4221 | 762 | 762 | 662 | 662
BEDD23 | WIMB21 | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 1100 | 1100 | 1100 | 1100
BEDD4A | ROWD41 | 0 | 11.676 | Cable | 0.0079 | 0.138 | 127.4459 | 1309 | 1309 | 1309 | 1309
BEDD4B | ROWD42 | 0 | 11.676 | Cable | 0.0105 | 0.0957 | 210.168 | 1415 | 1415 | 1415 | 1415
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 56.939 | 0.631 | Composite | 0.2314 | 2.4189 | 22.4142 | 819 | 819 | 638 | 638
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF41 | WMAR4B | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3326 | 3076.55 | 2655.811 | 3076.55
BICF42 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF42 | WMAR4A | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3190 | 2950.75 | 2547.215 | 2950.75
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1236 | 1176 | 1074 | 1176
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1236 | 1176 | 1074 | 1176
BLYT4A | HEDD4A | 26.636 | 0.121 | Composite | 0.0426 | 0.514 | 18.0175 | 2199 | 2092 | 1911 | 2092
BLYT4B | HEDD4B | 26.636 | 0.49 | Composite | 0.0429 | 0.5194 | 24.1171 | 2199 | 2092 | 1911 | 2092
BODE41 | GWYN4A | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
BODE41 | GWYN4B | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
BODE4A | BODE4C | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 500 | 500 | 500
BODE4B | BODE4D | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 500 | 500 | 500
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOTW41 | FAWL41 | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 1025.825 | 901 | 901
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0451 | 0.8316 | 32.2964 | 2779 | 2568 | 2217 | 2568
BRAI4A | RAYL41 | 32.993 | 0 | OHL | 0.0358 | 0.5738 | 21.7484 | 2779 | 2568 | 2217 | 2568
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.065 | 1.1398 | 43.92 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0358 | 0.5745 | 21.7727 | 2779 | 2568 | 2217 | 2568
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.095 | 1.8583 | 16.2816 | 2800 | 2800 | 2800 | 2800
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0655 | 1.0887 | 37.4778 | 2470 | 2350 | 2146 | 2350
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0895 | 0.8305 | 5.3251 | 948 | 882 | 753 | 753
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.762 | 850 | 850 | 675 | 675
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0687 | 0.6374 | 4.087 | 1093 | 1031 | 925 | 1031
BRFO41 | LEIS4A | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2780 | 1883 | 2780 | 2780
BRFO41 | LEIS4B | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2780 | 1500 | 2780 | 2780
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2570 | 2220 | 2570
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1093 | 1031 | 925 | 1031
BRIM2B | TOTT24 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1085 | 1031 | 925 | 1031
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1093 | 1031 | 925 | 1031
BRIM2C | TOTT22 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT23 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499
BRIN21 | NORL22 | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 686 | 686 | 686 | 686
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2568 | 2217 | 2568
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2568 | 2217 | 2568
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | WWEY41 | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRLE41 | WWEY42 | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRWA2A | HINP22 | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 767 | 620 | 620
BRWA2B | HINP21 | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 767 | 767 | 620 | 620
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0224 | 0.3591 | 13.6101 | 2779 | 2568 | 2217 | 2568
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3102 | 2869.35 | 2476.947 | 2869.35
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2910 | 2238 | 2510
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3102 | 2869.35 | 2476.947 | 2869.35
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3102 | 2869.35 | 2476.947 | 2869.35
BUSH21 | DRAK2A | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762
BUSH21 | WIEN21 | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 704.85 | 608.457 | 704.85
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 635
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 635
BUST4A | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119
BUST4B | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568
CANT42 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102
CANT42 | CLEH41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102
CAPE41 | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2780 | 2570 | 2220 | 2570
CAPE42 | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2890 | 2750 | 2420 | 2750
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629
CARE21 | USKM22 | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3102 | 3048 | 2958 | 3048
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO4A | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR42 | DAIN41 | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 1507 | 1507 | 1507 | 1507
CARR41 | DAIN42 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1524 | 1524 | 1524 | 1524
CARR43 | DAIN41 | 53.412 | 2.31 | parallel Composite | 0.0847 | 1.031 | 76.931 | 2508 | 2508 | 2300 | 2300
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2175 | 2069 | 1890 | 2069
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2175 | 2069 | 1890 | 2069
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0495 | 0.6067 | 18.9879 | 3102 | 3048 | 2958 | 3048
CHIC41 | EXET41 | 75.92 | 0 | OHL | 0.0824 | 1.3205 | 50.0469 | 2779 | 2568 | 2217 | 2568
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829
CHIC42 | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CILF21 | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF22 | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0295 | 0.491 | 17.0223 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0273 | 0.4458 | 16.1543 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136
CLEH41 | KEMS4B | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048
CONQ41 | CAPE42 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 2780 | 2780 | 2780 | 2780
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 2771 | 2853 | 3048
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 1710 | 1581.75 | 1365.435 | 1581.75
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2217.225 | 1914.0045 | 2217.225
CONQ42 | DAIN42 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048
CONQ42 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389
CONQ42 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 1710 | 1581.75 | 1365.435 | 1581.75
CONQ42 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2046.1 | 1766.282 | 2046.1
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 3075 | 2876 | 2663 | 2876
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 2423 | 2327 | 2167 | 2327
COTT41 | GREN41 | 129.478 | 0 | OHL | 0.2293 | 2.5548 | 75.7188 | 2009 | 1911 | 1746 | 1911
COTT41 | KEAD4A | 34.628 | 0 | OHL | 0.0595 | 0.6862 | 20.1667 | 2212 | 1710 | 1979 | 2125
COTT41 | RYHA42 | 76.891 | 0 | OHL | 0.0834 | 1.3374 | 50.6872 | 2780 | 2780 | 2780 | 2780
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0506 | 0.5544 | 21.5604 | 2212 | 2125 | 1979 | 2052
COTT42 | KEAD4B | 34.479 | 0 | OHL | 0.0592 | 0.6832 | 20.0806 | 2212 | 2046.1 | 1766.282 | 2046.1
COTT42 | RYHA41 | 76.816 | 0 | OHL | 0.0834 | 1.3361 | 50.638 | 2780 | 2780 | 2780 | 2780
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0096 | 0.1298 | 4.0616 | 3326 | 3160 | 2971 | 3160
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0619 | 1.1211 | 9.699 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ41 | 6.496 | 0 | OHL | 0.007 | 0.113 | 4.2822 | 2771 | 2568 | 2217 | 2568
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0125 | 0.2001 | 7.5827 | 2779 | 2568 | 2217 | 2568
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0394 | 0.6314 | 23.9301 | 2779 | 2568 | 2217 | 2568
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0537 | 0.9095 | 34.8191 | 2779 | 2568 | 2217 | 2568
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 979
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879
CREB21 | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB22 | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 2771 | 2771 | 2663 | 2771
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO41 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO42 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CULJ41 | DIDC41 | 4.898 | 0 | OHL | 0.0053 | 0.0852 | 3.2288 | 2771 | 2568 | 2217 | 2568
DAIN42 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0541 | 0.6511 | 66.8001 | 2397 | 2302 | 2144 | 2300
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1604 | 1604 | 1557 | 1557
DINO41 | PENT41 | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9578 | 1623 | 1604 | 1557 | 1557
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2009 | 1911 | 1746 | 1911
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1769 | 1769 | 1320 | 1320
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2089 | 2089 | 1878 | 1878
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2771 | 2568 | 2217 | 2568
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM42 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505
DRAX42 | THTO42 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2779 | 2568 | 2217 | 2568
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3065 | 2829 | 2418 | 2829
DUNG41 | SETW4A | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2778 | 2418 | 2830
DUNG41 | SETW4B | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2867 | 2418 | 2830
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 524 | 518 | 401 | 401
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 3048 | 3048 | 2971 | 3048
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1389 | 1284 | 1108 | 1284
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122
EGGB41 | THOM42 | 28.07 | 0.197 | Composite | 0.028 | 0.4883 | 21.9374 | 2217 | 2217 | 1801 | 1801
EGGB42 | FERR41 | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
EGGB42 | STSB41 | 48.084 | 0 | OHL | 0.0458 | 0.8295 | 32.1304 | 2779 | 2568 | 2217 | 2568
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST21 | MILH21 | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430
ELST21 | MILH22 | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST42 | SUND42 | 34.706 | 0 | OHL | 0.0747 | 0.6944 | 19.9464 | 1590 | 1500 | 1346 | 1500
ELST4A | ELST41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0749 | 0.6969 | 20.0233 | 1590 | 1500 | 1346 | 1500
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568
ENDE41 | RATS42 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911
FAWL41 | LOVE41 | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 1025.825 | 885.5365 | 1025.825
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2570.575 | 2219.0315 | 2570.575
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4527 | 1967 | 1874 | 1712 | 1874
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1967 | 1875 | 1712 | 1875
FENW4A | DRAX41 | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000
FENW4A | THOM41 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FERR21 | FERR2D | 0 | 0.8161 | Cable | 0.0027 | 0.0204 | 6.0881 | 600 | 600 | 600 | 600
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823
FERR23 | FERR2E | 0 | 0.726 | Cable | 0.0024 | 0.0182 | 5.4162 | 600 | 600 | 600 | 600
FERR2A | FERR23 | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1229
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1113.7 | 961.394 | 1113.7
FERR2B | FERR22 | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 953.675 | 823.2535 | 953.675
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 480 | 480 | 330 | 330
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512
FIDF21 | FIDF23 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF22 | FIDF24 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF22 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1217.3 | 1050.826 | 1217.3
FIDF23 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1217.3 | 1050.826 | 1217.3
FIDF24 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1217.3 | 1050.826 | 1217.3
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2212 | 2125 | 1979 | 2125
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2212 | 2125 | 1979 | 2125
FOUR21 | HARK21 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW2A | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 789.95 | 681.919 | 789.95
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3102 | 2935 | 2633 | 2813
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390
GRAI41 | TILB41 | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2003 | 2003 | 1939 | 2003
GREN41 | STAY41 | 101.832 | 0 | OHL | 0.1852 | 2.0259 | 59.0223 | 2514 | 2439 | 2314 | 2439
GREN41 | SUND41 | 39.75 | 0 | OHL | 0.0723 | 0.7909 | 23.0368 | 2009 | 1911 | 1746 | 1911
GREN41 | SUND42 | 39.955 | 0 | OHL | 0.0727 | 0.795 | 23.1553 | 2009 | 1911 | 1746 | 1911
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GRSA21 | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119
GRSA21 | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1000
GRSA21 | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GRSA21 | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GRSB21 | LACK21 | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRSB21 | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRSB21 | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GRSB21 | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2570.575 | 2219.0315 | 2570.575
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2570.575 | 2219.0315 | 2570.575
HACK21 | TOTT21 | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK22 | TOTT22 | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1330 | 1300 | 1200 | 1300
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HAKB1 | HARK13 | 8.487 | 0 | OHL | 0.917 | 2.075 | 0.451 | 132 | 122.1 | 105.402 | 122.1
HAKB4- | HARK41 | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2169 | 2006.325 | 1731.9465 | 2006.325
HAKB4B | HARK41 | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2170 | 2007.25 | 1732.745 | 2007.25
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3076.55 | 2655.811 | 3076.55
HAMB4A | PEWO41 | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2470 | 2284.75 | 1972.295 | 2284.75
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 222 | 191.64 | 222
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3076.55 | 2655.811 | 3076.55
HAMB4B | PEWO41 | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2287.525 | 1974.6905 | 2287.525
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 222 | 191.64 | 222
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1362 | 1285 | 1202 | 1285
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1206 | 1.5777 | 77.2944 | 2009 | 1912 | 1746 | 1912
HARK13 | JUNV1- | 16.243 | 0 | OHL | 1.194 | 2.729 | 0.743 | 132 | 122.1 | 105.402 | 122.1
HARK22 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HARK41 | HUTT4A | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2563.175 | 2212.6435 | 2563.175
HARK41 | HUTT4B | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2563.175 | 2212.6435 | 2563.175
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9125 | 1110 | 1038 | 962 | 1038
HATL21 | HARM21 | 13.983 | 0 | OHL | 0.0531 | 0.5772 | 3.9082 | 1093 | 1031 | 925 | 1031
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0332 | 0.335 | 2.0887 | 1382 | 1279 | 1157 | 1279
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1148 | 1086 | 1021 | 1086
HATL21 | WBOL21 | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1093 | 1031 | 926 | 1031
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 801
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1093 | 1031 | 925 | 1031
HAWP41 | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2545 | 2354.125 | 2032.1825 | 2354.125
HEDD4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3076.55 | 2655.811 | 3076.55
HEDD4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3076.55 | 2655.811 | 3076.55
HEDD4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3076.55 | 2655.811 | 3076.55
HEDD4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3076.55 | 2655.811 | 3076.55
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3330 | 3160 | 2970 | 3160
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3076.55 | 2655.811 | 3076.55
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0241 | 0.291 | 17.0214 | 2212 | 2125 | 1979 | 2125
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056
HINP41 | MELK41 | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | MELK41 | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | TAUN41 | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1979 | 2125
HINP41 | TAUN42 | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1979 | 2125
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771
HURS21 | LITT2A | 5.164 | 2.613 | Composite | 0.0288 | 0.2786 | 27.8693 | 864 | 864 | 824 | 855
HURS21 | LITT2B | 5.14 | 2.659 | Composite | 0.0288 | 0.2786 | 28.329 | 864 | 864 | 824 | 861
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 882 | 704 | 784
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 882 | 704 | 784
HUTT41 | HUTT4A | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2470 | 2284.75 | 1972.295 | 2284.75
HUTT41 | HUTT4A | 0 | 0 | Series Capacitor | 0 | -0.5114 | 0 | 2750 | 2543.75 | 2195.875 | 2543.75
HUTT41 | HUTT4B | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2470 | 2284.75 | 1972.295 | 2284.75
HUTT41 | HUTT4B | 0 | 0 | Series Capacitor | 0 | -0.5114 | 0 | 2750 | 2543.75 | 2195.875 | 2543.75
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 2869.35 | 2476.947 | 2869.35
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 2869.35 | 2476.947 | 2869.35
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1317.2 | 1137.064 | 1317.2
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1930 | 1785.25 | 1540.14 | 1785.25
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1930 | 1785.25 | 1540.14 | 1785.25
IROA11 | CAMA11 | 1 | 0 | Cable | 0.814 | 5.749 | 3.3761 | 455 | 455 | 455 | 455
IROA11 | CAMA12 | 1 | 0 | Cable | 0.814 | 5.749 | 3.3761 | 455 | 455 | 455 | 455
IROA11 | OLDS12 | 12.577 | 0 | Cable | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372
IROA12 | OLDS12 | 12.572 | 0 | Cable | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372
IROA21 | MELK21 | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750
IRON41 | LEGA4A | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 1851.85 | 1598.597 | 1851.85
IRON41 | PENN41 | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500
IRON41 | PENN42 | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.2909 | 9.0977 | 2397 | 2217.225 | 1914.0045 | 2217.225
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631
IVER23 | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 1360 | 1280 | 1200 | 1280
JORD21 | NORL21 | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381
KEAD41 | GART4B | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3180 | 3000 | 2692 | 3000
KEAD41 | KEAP41 | 0.321 | 0 | OHL | 0.0007 | 0.0066 | 0.179 | 3000 | 3000 | 3000 | 3000
KEAD42 | FENW4A | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876
KEAD42 | KEAP42 | 0.433 | 0.42 | Composite | 0.0013 | 0.0151 | 7.1841 | 3000 | 3000 | 3000 | 3000
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0308 | 0.4944 | 18.7376 | 2779 | 2568 | 2217 | 2568
KEAD43 | GART4A | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3180 | 3000 | 2692 | 3000
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0307 | 0.4916 | 18.6331 | 3326 | 3160 | 2971 | 3160
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 830 | 830 | 830 | 830
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0535 | 0.7262 | 24.4122 | 2169 | 2084 | 1940 | 2084
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0721 | 0.7367 | 22.6825 | 1926 | 1781.55 | 1537.911 | 1781.55
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0717 | 0.7289 | 22.3721 | 1926 | 1781.55 | 1537.911 | 1781.55
KENG41 | SJOW41 | 0 | 4.5 | Cable | 0.002 | 0.0567 | 54.7391 | 2000 | 2000 | 2000 | 2000
KENG41 | SJOW41 | 0 | 4.63 | Cable | 0.0021 | 0.0583 | 56.3205 | 1770 | 1730 | 1600 | 1730
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 2000 | 2000 | 2000 | 2000
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 2000 | 2000 | 2000 | 2000
KENG41 | WLSD41 | 0 | 2.892 | Cable | 0.0013 | 0.0372 | 35.179 | 1770 | 1730 | 1600 | 1730
KENG41 | WLSD42 | 0 | 2.892 | Cable | 0.0013 | 0.0372 | 35.179 | 1770 | 1730 | 1600 | 1730
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 698
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 619
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | WASF22 | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KIBY22 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1381 | 1339 | 1258 | 1339
KIBY22 | WASF21 | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KILL41 | KILL41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2750 | 2750 | 2750 | 2750
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720
KINO41 | KINO41 | 0 | 0 | Series Reactor | 0.0027 | 2 | 0 | 2002 | 2002 | 2002 | 2002
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2672.325 | 2306.8665 | 2672.325
KINO41 | TILB41 | 15.4784 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2003 | 2003 | 1948 | 1948
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619
KITW21 | OCKH21 | 13.738 | 0.222 | Composite | 0.0525 | 0.5743 | 6.2479 | 772 | 772 | 619 | 619
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 551 | 512 | 442 | 512
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 551 | 512 | 442 | 512
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1148 | 1086 | 1021 | 1086
LACK41 | NORT41 | 22.443 | 0.25 | Composite | 0.0404 | 0.4515 | 17.428 | 1831 | 1739 | 1588 | 1739
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LAGA41 | LAND42 | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7631 | 2423 | 2241.275 | 1934.7655 | 2241.275
LAGA41 | LAND42 | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8376 | 1389 | 1284.825 | 1109.1165 | 1284.825
LAKE4A | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2614.975 | 2257.3595 | 2614.975
LAKE4A | WTHU42 | 2.4188 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 2869.35 | 2476.947 | 2869.35
LAKE4B | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2704.7 | 2334.814 | 2704.7
LAKE4B | WTHU41 | 2.5806 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 2869.35 | 2476.947 | 2869.35
LALE21 | WWEY23 | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA4B | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 1851.85 | 1598.597 | 1851.85
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 3326 | 3326 | 3317 | 3326
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2780 | 2571.5 | 2219.83 | 2571.5
LEIS4B | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2780 | 2571.5 | 2219.83 | 2571.5
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 693.75 | 598.875 | 693.75
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6835 | 1389 | 1284.825 | 1109.1165 | 1284.825
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6835 | 1389 | 1284.825 | 1109.1165 | 1284.825
LITT41 | WTHU41 | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LITT41 | WTHU42 | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LOFI4A | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1470.75 | 1269.615 | 1470.75
LOFI4B | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1470.75 | 1269.615 | 1470.75
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568
MACC41 | STAL41 | 31.196 | 0 | OHL | 0.0669 | 0.6239 | 17.9405 | 1710 | 1627 | 1488 | 1627
MAGA21 | PYLE2A | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1113.7 | 961.394 | 1113.7
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3076.55 | 2655.811 | 3076.55
MONF21 | POPP21 | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 682 | 629 | 538 | 629
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.0905 | 1.5789 | 56.6993 | 2518 | 2395 | 2188 | 2395
NECT4A | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3330 | 3080.25 | 2659.005 | 3080.25
NECT4A | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3330 | 3080.25 | 2659.005 | 3080.25
NECT4B | NECT41 | 0 | 0.129 | Cable | 0 | 0 | 1.61 | 3190 | 2950.75 | 2547.215 | 2950.75
NECT4B | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3330 | 3080.25 | 2659.005 | 3080.25
NECT4B | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3330 | 3080.25 | 2659.005 | 3080.25
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381
NEEP4A | STSB41 | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568
NEWX21 | NEWX21 | 0 | 0.15 | Cable | 0.0003 | 0.0034 | 1.5195 | 1143 | 1143 | 1143 | 1143
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 827 | 779 | 779
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1853.7 | 1600.194 | 1853.7
NORL21 | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381
NORL22 | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1372 | 1293 | 1197 | 1293
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
OCKH21 | WIEN2A | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 621.6 | 536.592 | 621.6
OCKH2A | WIEN21 | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0375 | 0.3474 | 2.2265 | 1093 | 1031 | 925 | 1031
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2771 | 2568 | 2217 | 2568
PADI41 | PEWO4B | 37.608 | 0 | OHL | 0.0524 | 0.7014 | 23.3846 | 2169 | 2006.325 | 1731.9465 | 2006.325
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2779 | 2568 | 2217 | 2568
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2779 | 2569 | 2217 | 2569
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2771 | 2771 | 2692 | 2771
PEMB41 | SWAN41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2570.575 | 2219.0315 | 2570.575
PEMB41 | SWAN41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2779 | 2570.575 | 2219.0315 | 2570.575
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2577 | 2453 | 2217 | 2453
PEMB41 | WALH41 | 217.727 | 5.468 | parallel Composite | 0.2373 | 3.8184 | 207.0444 | 2779 | 2568 | 2568 | 2568
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0633 | 0.9555 | 131.5497 | 1135 | 1135 | 992 | 992
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PEWO21 | WASF21 | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO22 | WASF22 | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 2869.35 | 2476.947 | 2869.35
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 2869.35 | 2476.947 | 2869.35
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 439 | 439 | 381 | 381
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136
PYLE21 | PYLE2A | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1204 | 1115 | 1018 | 1115
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2848 | 109.657 | 2779 | 2568 | 2217 | 2568
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2757 | 2147 | 2056 | 1904 | 2056
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067
RATS42 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2147 | 2056 | 1904 | 2056
RATS42 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 2212 | 2125 | 1979 | 2125
REBR21 | TOTT21 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1114.625 | 962.1925 | 1114.625
REBR22 | TOTT22 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1114.625 | 962.1925 | 1114.625
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2570.575 | 2219.0315 | 2570.575
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 905 | 882 | 762 | 800
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 841 | 841
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2780 | 2780 | 2780 | 2780
RYEH41 | WALX41 | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2779 | 2568 | 2217 | 2568
RYEH4A | RYEH4C | 0.264 | 0 | OHL | 0.0006 | 0.0053 | 0.1512 | 9999 | 9249.075 | 7984.2015 | 9249.075
RYEH4A | WALX42 | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2779 | 2570.575 | 2219.0315 | 2570.575
RYEH4B | RYEH4D | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2570.575 | 2219.0315 | 2570.575
RYHA41 | EASO41 | 58.95 | 0 | OHL | 0.064 | 1.0253 | 38.8593 | 2780 | 2571.5 | 2219.83 | 2571.5
RYHA4B | EASO41 | 58.769 | 0 | OHL | 0.0638 | 1.0222 | 38.7404 | 2780 | 2571.5 | 2219.83 | 2571.5
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1517 | 1517 | 1517 | 1517
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424
SELL41 | SELL41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860
SELL41 | SELT4A | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL41 | SELT4A | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 2414.25 | 2082.78 | 2414.25
SELL41 | SELT4B | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 2610 | 2414.25 | 2082.78 | 2414.25
SELL41 | SETW4A | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3052.5 | 2635.05 | 3052.5
SELL41 | SETW4A | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL41 | SETW4B | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3052.5 | 2635.05 | 3052.5
SELL41 | SETW4B | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SHRE4A | SHRE4B | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 2170 | 2007.25 | 1732.745 | 2007.25
SING41 | NFLE41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748
SJOW21 | TOTT23 | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 868 | 835 | 682 | 762
SJOW21 | TOTT24 | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 868 | 835 | 682 | 762
SJOW41 | SJOW4A | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 240 | 222 | 191.64 | 222
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2350 | 2146 | 2350
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2350 | 2146 | 2350
SPLN41 | WMAR4A | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3160 | 2923 | 2523.26 | 2923
SPLN41 | WMAR4B | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3160 | 2923 | 2523.26 | 2923
SSHI21 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1236 | 1176 | 1074 | 1176
SSHI21 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1093 | 1031 | 925 | 1031
STAL41 | STSB4A | 28.555 | 5.057 | Composite | 0.0366 | 0.5666 | 94.9484 | 1649 | 1528 | 1399 | 1528
STAL42 | THOM42 | 71.245 | 4.978 | Composite | 0.0738 | 1.299 | 122.495 | 1330 | 1171 | 1001 | 1171
STEW21 | STEW2A | 0 | 0.435 | Cable | 0.0007 | 0.0116 | 2.5837 | 854 | 795 | 700 | 795
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3048 | 2935 | 2692 | 2935
SUTB41 | WALP41 | 3.85 | 0 | OHL | 0.008 | 0.0773 | 2.2055 | 1450 | 1340 | 1150 | 1340
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 2819.4 | 2433.828 | 2819.4
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 421 | 421 | 381 | 381
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698
THOM22 | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 883.375 | 762.5675 | 883.375
THUR2A | THUR21 | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1120 | 1119 | 1023 | 1119
TILB41 | TILB4B | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
TILB4A | TILB41 | 0.0581 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1001 | 1.2332 | 38.5742 | 3100 | 3100 | 3100 | 3100
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1001 | 1.2332 | 38.5742 | 3100 | 3100 | 3100 | 3100
TREM21 | USKM23 | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1093 | 1031 | 925 | 1031
USKM12 | USKM11 | 0 | 0 | Series Reactor | 0.25 | 20 | 0 | 90 | 83.25 | 71.865 | 83.25
USKM21 | USKM23 | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956
USKM22 | USKM21 | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629
USKM22 | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629
USKM23 | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641
WADW21 | WACW21 | 0 | 24.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 203.5 | 175.67 | 203.5
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1500 | 1500 | 1500
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.001026 | 0.009762 | 0.059452 | 952.6279 | 881.1808 | 760.6734 | 881.1808
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 2780 | 2571.5 | 2219.83 | 2571.5
WIMB21 | WISD2B | 0 | 20.669 | Cable | 0.0413 | 0.4733 | 209.377 | 738 | 738 | 629 | 629
WMAR4A | WALP41 | 23.475 | 0 | OHL | 0.0208 | 0.4032 | 15.7777 | 3190 | 2950.75 | 2547.215 | 2950.75
WMAR4B | WALP41 | 23.425 | 0 | OHL | 0.0208 | 0.4023 | 15.7443 | 3190 | 2950.75 | 2547.215 | 2950.75
WTHU41 | WTHU41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WTHU42 | WTHU42 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WYLF11 | PERH11 | 1 | 0 | OHL | 0.435 | 3.172 | 17.6099 | 330 | 305.25 | 239.55 | 305.25
WYLF12 | PERH11 | 1 | 0 | OHL | 0.435 | 3.177 | 17.772 | 330 | 305.25 | 239.55 | 305.25

## B-2-1d
Table B.2.1d - Offshore Transmission Circuits 2018/19 | [11 empty] | Back To Menu
OFTO | Station | Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO1A | BOSW10 | 0 | 26.9 | Cable | 0.0154 | 0.0216 | 0.2209 | -- | 132
" | " | BOSO10 | BOSO1A | 0 | 2.633 | Cable | 0.00074 | 0.00219 | 0.02292 | -- | 132
- | Burbo Bank Extension Offshore Wind Farm | BURB41 | BODE41 | 0 | 2.602 | Cable | 0.0009 | 0.0064 | 5.1442 | 277 | 400
- | " | BUBO20 | BURB21 | 0 | 34.622 | Cable | 0.3875 | 0.9335 | 103.7527 | 277 | 220
- | Galloper | GAON11 | LEIS11 | 0 | 2.28 | Cable | 0.01 | 0.03 | 0.38 | 300 | 132
- | " | GAON11 | LEIS11 | 0 | 2.28 | Cable | 0.01 | 0.03 | 0.38 | 300 | 132
- | " | GAON11 | GAOF1A | 0 | 47.8 | Cable | 1.23 | 2.8301 | 58.38 | 780 | 132
- | " | GAON11 | GAOF1B | 0 | 47.8 | Cable | 1.23 | 2.8301 | 58.38 | 780 | 132
- | Greater Gabbard Offshore Wind Farm | GGON11 | GREG11 | 0 | 46 | Cable | 1.9688 | 6.1189 | 59.7739 | 180 | 132
- | " | GGON12 | GREG12 | 0 | 46.15 | Cable | 1.9726 | 6.132 | 60.0083 | 180 | 132
- | " | GGON11 | GREG11 | 0 | 46 | Cable | 1.9688 | 6.1189 | 59.7739 | 180 | 132
- | " | GREG12 | GAOF10 | 0 | 17 | Cable | 0.36 | 1.07 | 0.6224 | 180 | 132
Gwynt y Môr OFTO Plc | GWYNT Y MOR PS | GWYN11 | GWYN1A | 0 | 0.1 | Cable | 0.0015 | 0.0085 | 4.5303 | 320 | 132
- | " | GWYN12 | GWYN1B | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 148.6 | 132
- | " | GWYN11 | GWYN1B | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 148.6 | 132
- | " | GWYN11 | GWYN1C | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 148.6 | 132
- | " | GWYN12 | GWYN1B | 0 | 1 | Cable | 1.15 | 2.88 | 34.8 | 148.6 | 132
- | " | GWYN12 | GWYN1C | 0 | 0.1 | Cable | 0.0015 | 0.0085 | 4.5303 | 320 | 132
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | BODE41 | BODE4C | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 400
" | " | BODE41 | BODE4D | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 400
" | " | GWYO1A | GWYO10 | 0 | 0 | Cable | 0.247 | 1.017 | 14.78 | -- | 132
" | " | GWYW10 | GWYO1A | 0 | 0 | Cable | 0.726 | 1.524 | 22.91 | -- | 132
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS1A | 0 | 0 | Cable | 0.0653 | 0.3483 | 4.5678 | -- | 132
" | " | GUNS1A | GUNS10 | 0 | 0 | Cable | 0.2656 | 0.478 | 11.2974 | -- | 132
- | Humber Gateway Onshore Wind Farm | HUMO11 | HUMO1A | 0 | 36 | Cable | 0.3276 | 3.6108 | 80.4564 | 200 | 132
- | " | HUMO12 | HUMO1B | 0 | 36 | Cable | 0.3276 | 3.6108 | 80.4564 | 200 | 132
- | Humber Gateway Offshore Wind Farm | HUMO1A | HUMW11 | 0 | 10 | Cable | 0.00396 | 0.007 | 0.10784 | 121.17 | 132
- | " | HUMO1B | HUMW12 | 0 | 10 | Cable | 0.00396 | 0.007 | 0.10784 | 121.17 | 132
TC Lincs OFTO Limited | Lincolnshire Offshore Windfarm | LINS10 | LINO1A | 0 | 12 | Cable | 0.2163 | 1.0055 | 15.8962 | -- | 132
" | " | LINS10 | LINO1B | 0 | 12 | Cable | 0.2163 | 1.0055 | 15.8962 | -- | 132
" | " | LINO1A | LINO10 | 0 | 49 | Cable | 1.8279 | 3.459 | 53.6443 | -- | 132
" | " | LINO1B | LINO10 | 0 | 49 | Cable | 1.8279 | 3.459 | 53.6443 | -- | 132
" | " | LINO1A | WALP41 | 0 | 1 | Cable | 0.0007 | 0.0118 | 10.9152 | -- | 400
Blue Transmission London Array Limited | London Array Offshore Wind Farm | CLEH40 | LONO41 | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
" | " | CLEH40 | LONO42 | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
" | " | LONO11 | LONO1A | 0 | 0.055 | Cable | 0.00121 | 0.0031533 | 0.077765 | 180 | 150
" | " | LONO1A | LONO1B | 0 | 3.048 | Cable | 0.08 | 0.16 | 4.49 | 164.9778 | 150
" | " | LONO1B | LONW1A | 0 | 48.065 | Cable | 1.37 | 2.65 | 64.65 | 158.4826 | 150
" | " | LONW1A | LONW11 | 0 | 1.633 | Cable | 0.04 | 0.09 | 2.41 | 155.8846 | 150
" | " | LONO12 | LONO1C | 0 | 0.105 | Cable | 0.00198 | 0.00516 | 0.12725 | 180 | 150
" | " | LONO1C | LONO1D | 0 | 3.033 | Cable | 0.08 | 0.16 | 4.47 | 164.9778 | 150
" | " | LONO1D | LONW1C | 0 | 48.213 | Cable | 1.37 | 2.66 | 64.85 | 158.4826 | 150
" | " | LONW1C | LONW11 | 0 | 1.913 | Cable | 0.05 | 0.1 | 2.82 | 155.8846 | 150
" | " | LONO13 | LONO1E | 0 | 0.09 | Cable | 0.00209 | 0.0054467 | 0.13432 | 180 | 150
" | " | LONO1E | LONO1F | 0 | 3.102 | Cable | 0.08 | 0.16 | 4.57 | 164.9778 | 150
" | " | LONO1F | LONW1E | 0 | 47.995 | Cable | 1.37 | 2.65 | 64.56 | 158.4826 | 150
" | " | LONW1E | LONW12 | 0 | 1.712 | Cable | 0.04 | 0.09 | 2.52 | 155.8846 | 150
" | " | LONO14 | LONO1G | 0 | 0.115 | Cable | 0.00253 | 0.0065933 | 0.1626 | 180 | 150
" | " | LONO1G | LONO1H | 0 | 3.067 | Cable | 0.08 | 0.16 | 4.52 | 164.9778 | 150
" | " | LONO1H | LONW1G | 0 | 48.785 | Cable | 1.39 | 2.69 | 65.62 | 158.4826 | 150
" | " | LONW1G | LONW12 | 0 | 0.905 | Cable | 0.02 | 0.05 | 1.33 | 155.8846 | 150
- | Walney Extension | MIDL41 | WAEN41 | 0 | 2.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
- | " | MIDL41 | WAEN42 | 0 | 2.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMO11 | ORMO1B | 0 | 41.5 | Cable | 0.674 | 2.858 | 43.85 | 789 | 132
" | " | ORMO1B | ORMO1A | 0 | 2.767 | Cable | 0.0583 | 0.246 | 2.83 | 789 | 132
" | " | ORMO1A | TRIM12 | 0 | 0.08 | Cable | 0.00169 | 0.0071 | 0.0818 | 789 | 132
- | Dudgeon Offshore Wind Farm | DUDG11 | NECT11 | 0 | 91.31 | Cable | 1.8163 | 6.8193 | 110.6215 | 204 | 132
- | " | DUDG11 | NECT12 | 0 | 91.31 | Cable | 1.8163 | 6.8193 | 110.6215 | 204 | 132
- | Race Bank Offshore | RABO21 | RAOF2A | 0 | 82.5 | Cable | 0.487 | 2.1112 | 247.8447 | 484 | 220
- | " | RABO22 | RAOF2B | 0 | 83.5 | Cable | 0.4934 | 2.136 | 250.7489 | 484 | 220
- | " | RACB4A | RACB4C | 0 | 0.3 | Cable | 0.0004 | 0.0032 | 2.4278 | 484 | 400
- | " | RACB4B | RACB4D | 0 | 0.3 | Cable | 0.0004 | 0.0032 | 2.4278 | 484 | 400
- | " | RAOF21 | RAOF22 | 0 | 13.4 | Cable | 0.0433 | 0.1661 | 19.4582 | 484 | 220
- | " | WALP41 | RACB4A | 0 | 1 | Cable | 0.0025 | 0.0093 | 21.1035 | 1330 | 400 |  | Missing
- | " | WALP41 | RACB4B | 0 | 1 | Cable | 0.0025 | 0.0093 | 21.1035 | 1330 | 400 |  | Missing
TC Robib Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RORE1A | 0 | 1 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
" | " | RORE12 | DITN1A | 0 | 1 | Cable | 0.0225 | 0.0575 | 0 | -- | 132
" | " | RORE10 | RORE1A | 0 | 1.8 | Cable | 0.3632 | 0.5992 | 22.2551 | 136 | 132
" |  | RORE1A | RREW10 | 0 | 12.5 | Cable | 0.3632 | 0.5992 | 22.2551 | 136 | 132
" | Robin Rigg West Offshore Wind Farm | RORW10 | RORW1A | 0 | 1.8 | Cable | 0.3632 | 0.5992 | 22.2551 | 136 | 132
|  | RORW1A | RRWW10 | 0 | 12.5 | Cable | 0.3632 | 0.5992 | 22.2551 | 136 | 132
- | Sheringham Shoal Offshore Wind Farm | SHSW1B | SSAW10 | 0 | 22.4 | Cable | 0.8099 | 1.5427 | 24.5231 | -- | 132
- | " | SHSW1A | SHSW1B | 0 | 0.4 | Cable | 8.2645e-05 | 0.00027548 | 0.0052548 | 178 | 132
- | " | SHSW1D | SSBW10 | 0 | 20.5 | Cable | 0.7412 | 1.4118 | 22.443 | -- | 132
- | " | SHSW1C | SHSW1D | 0 | 0.4 | Cable | 8.2645e-05 | 0.00027548 | 0.0052548 | 178 | 132
- | " | SALL10 | SHSW1A | 0 | 22 | Cable | 0.4028 | 1.7904 | 30.2871 | -- | 132
- | " | SALL10 | SHSW1C | 0 | 22 | Cable | 0.4028 | 1.7904 | 30.2871 | -- | 132
- | Rampion Offshore Wind Farm | BOLN41 | TWIN4A | 0 | 2.602 | Cable | 0.0028 | 0.0042 | 4.4179 | 411.1 | 400
- | " | BOLN41 | TWIN4B | 0 | 2.764 | Cable | 0.0036 | 0.0053 | 5.6068 | 411.1 | 400
- | " | TWIN1A | RAMP1A | 0 | 42.346 | Cable | 0.6872 | 1.9295 | 78.5805 | 209.9 | 150
- | " | TWIN1B | RAMP1B | 0 | 42.286 | Cable | 0.6864 | 1.9267 | 78.4554 | 209.9 | 150
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW10 | THAW1A | 0 | 2.3 | Cable | 0.049 | 0.191 | 3.336 | -- | 132
" | " | THAW1A | THAW1B | 0 | 2.26 | Cable | 0.036 | 0.145 | 3.08 | -- | 132
" | " | THAW1B | THOW10 | 0 | 24.33 | Cable | 0.846 | 1.703 | 26.23 | -- | 132
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAO10 | WAAO1A | 0 | 0 | Cable | 0.076045 | 0.13688 | 3.5539 | -- | 132
" | " | WAAO1A | WAAW10 | 0 | 0 | Cable | 1.2943 | 2.3298 | 55.0577 | -- | 132
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABO10 | WABO1A | 0 | 0 | Cable | 0.15 | 0.27 | 6.384 | -- | 132
" | " | WABO1A | WABW10 | 0 | 0 | Cable | 1.266 | 2.279 | 53.869 | -- | 132
" | Walney 3 Offshore Wind Farm | WACW21 | WADW21 | 0 | 24.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 220
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | HEYS11 | WDSO11 | 0 | 42.075 | Cable | 0.663 | 1.9978 | 69.3822 | 232.2247 | 132
" | " | HEYS12 | WDSO12 | 0 | 3.675 | Cable | 0.0396 | 0.2076 | 6.7788 | 232.2247 | 132
| " | WDSO1A | WDSW11 | 0 | 39.4 | Cable | 0.6396 | 1.8368 | 64.2338 | 209 | 155
" | " | WDSO1B | WDSW12 | 0 | 39.4 | Cable | 0.6396 | 1.8368 | 64.2338 | 209 | 155
" | " | WDSO11 | WDSO1A | 0 | 2.675 | Cable | 0.0234 | 0.161 | 5.1485 | 209 | 155
" | " | WDSO12 | WDSO1B | 0 | 2.675 | Cable | 0.0234 | 0.161 | 5.1485 | 209 | 155
" | " | HEYS40 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
" | " | HEYS40 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
| Walney 3 Offshore Wind Farm | WACW21 | WOWE2A | 0 | 82.1 | Cable | 0.9432 | 1.99 | 251.59 | 347 | 220
| Walney 4 Offshore Wind Farm | WADW21 | WOWE2B | 0 | 68.7 | Cable | 0.7775 | 1.6599 | 209.9395 | 347 | 220
- | Westermost Rough Offshore Wind Farm | WERW12 | WERW1C | 0 | 9.6525 | Cable | 0.13835 | 0.50506 | 15.2902 | 214.3413 | 150
- | " | WERW1C | WERW1B | 0 | 1.482 | Cable | 0.016282 | 0.073145 | 2.6692 | 231.7484 | 150
- | " | WERW1B | WERW1A | 0 | 13.9185 | Cable | 0.13374 | 0.85744 | 26.2286 | 229.4101 | 150
- | " | WERW1A | WERW11 | 0 | 0.78055 | Cable | 0.0065636 | 0.046673 | 1.5245 | 140.0623 | 150
- | " | WERW22 | WERW2A | 0 | 0.039 | Cable | 0.00031845 | 0.0012888 | 0.13463 | 256.7809 | 275
- | " | WERW2A | HEDO20 | 0 | 0.29 | Cable | 0.0023679 | 0.0095833 | 1.0011 | 256.7809 | 275
- | " | WERW21 | WERW2B | 0 | 0.103 | Cable | 0.00084102 | 0.0034037 | 0.35556 | 256.7809 | 275
- | " | WERW2B | HEDO20 | 0 | 0.265 | Cable | 0.0021638 | 0.0087572 | 0.9148 | 394.1498 | 275

## B-2-2a
Table B.2.2a - SHE Transmission Circuit Changes 2019/20 to 2027/28 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BEAU1N | FAAR1R | 2019 | Removed | 29.85 | 0 | OHL | 2.953 | 6.7683 | 1.436 | 132 | 123 | 106 | 123
BEAU1N | KNOC1J | 2019 | Addition | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU1T | FAAR1Q | 2019 | Removed | 29.88 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BEAU1T | KNOC1J | 2019 | Addition | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BOAG1Q | FAAR1Q | 2019 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOAG1Q | TOMT1K | 2019 | Addition | 23.42 | 0 | OHL | 2.1306 | 5.4442 | 1.172 | 132 | 123 | 106 | 123
BOAG1R | FAAR1R | 2019 | Removed | 30.1 | 0 | OHL | 3.065 | 7.025 | 1.49 | 132 | 123 | 106 | 123
BOAG1R | TOMT1J | 2019 | Addition | 23.42 | 0 | OHL | 2.1306 | 5.4442 | 1.172 | 132 | 123 | 106 | 123
BOAG3- | TOMN3J | 2019 | Addition | 0 | 22 | Cable | 8.5 | 20.62 | 2.46 | 48.6 | 48.6 | 48.6 | 48.6
FAAR1Q | TOMT1K | 2019 | Addition | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FAAR1R | TOMT1J | 2019 | Addition | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FAUG1- | FAUG1M | 2019 | Removed | 0 | 0.29 | Cable | 0.0106 | 0.0196 | 0.357 | 153 | 134 | 134 | 134
FAUG1- | FAUG1M | 2019 | Addition | 0 | 0.29 | Cable | 0.01 | 0.0225 | 0.486 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 2019 | Removed | 0 | 0.2 | Cable | 0.01 | 0.0137 | 0.249 | 153 | 134 | 134 | 134
FAUG1- | FAUG1N | 2019 | Addition | 0 | 0.2 | Cable | 0.01 | 0.0157 | 0.339 | 220 | 209 | 209 | 209
FAUG1N | LOCL1R | 2019 | Removed | 8.5 | 0 | OHL | 0.7735 | 1.972 | 0.425 | 126 | 117 | 101 | 117
FAUG1N | LOCL1R | 2019 | Addition | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FWIL1R | LLUC1R | 2019 | Removed | 34.9 | 0 | OHL | 3.1759 | 8.0968 | 1.745 | 126 | 117 | 101 | 117
FWIL1R | LOCL1R | 2019 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
INRU1Q | SFER1L | 2019 | Removed | 6.1 | 0 | OHL | 0.311 | 1.3664 | 0.317 | 202 | 193 | 176 | 193
INRU1Q | SFER1L | 2019 | Addition | 6.1 | 0 | OHL | 0.309 | 1.3684 | 0.315 | 242 | 229 | 209 | 229
INRU1R | SFER1M | 2019 | Removed | 6.1 | 0 | OHL | 0.311 | 1.3664 | 0.317 | 202 | 193 | 176 | 193
INRU1R | SFER1M | 2019 | Addition | 6.1 | 0 | OHL | 0.309 | 1.3684 | 0.315 | 242 | 229 | 209 | 229
KNOC2J | TOMT2K | 2019 | Addition | 18.46 | 0 | OHL | 0.0923 | 1.0153 | 3.932 | 810 | 765 | 685 | 765
KNOC2K | TOMT2J | 2019 | Addition | 18.46 | 0 | OHL | 0.0923 | 1.0153 | 3.932 | 810 | 765 | 685 | 765
LUND- | FWIL1R | 2019 | Addition | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129
LUND- | FWIL1Q | 2019 | Removed | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129
ABED1T | ABED1- | 2020 | Addition | 5 | 0 | OHL | 0.25 | 1.035 | 0.28 | 163 | 152 | 131 | 152
BLHI1J | KEIT1K | 2020 | Addition | 0 | 4.5 | Cable | 0.0941 | 0.3771 | 6.169 | 200 | 178 | 178 | 178
BLHI1K | KEIT1J | 2020 | Addition | 0 | 4.5 | Cable | 0.0941 | 0.3771 | 6.169 | 200 | 178 | 178 | 178
BLHI2M | PEHERSV1 | 2020 | Removed | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BLHI2M | ROTI2J | 2020 | Addition | 35.36 | 0 | OHL | 0.1795 | 1.5286 | 9.232 | 1090 | 1030 | 920 | 1030
CAAD3J | BTUI3L | 2020 | Addition | 12 | 0 | OHL | 1.699 | 2.8214 | 0.584 | 99 | 92 | 79 | 92
DOUN2- | GORW2- | 2020 | Removed | 58.1 | 0 | OHL | 0.4621 | 3.1663 | 12.268 | 535 | 490 | 430 | 490
DOUN2- | GORW2- | 2020 | Addition | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DUDH1Q | GLAG1Q | 2020 | Removed | 0 | 1.95 | Cable | 0.0582 | 0.1153 | 2.908 | 160 | 145 | 145 | 145
DUDH1Q | MKTG1A | 2020 | Addition | 0 | 0.4 | Cable | 0.0119 | 0.0237 | 0.597 | 160 | 145 | 145 | 145
DUDH1R | GLAG1R | 2020 | Removed | 0 | 1.95 | Cable | 0.0582 | 0.1153 | 2.908 | 160 | 145 | 145 | 145
DUDH1R | MKTG1D | 2020 | Addition | 0 | 0.4 | Cable | 0.0119 | 0.0237 | 0.597 | 160 | 145 | 145 | 145
DUNM1- | ABED1T | 2020 | Addition | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193
DUNM1- | DUNM1C | 2020 | Removed | 6 | 0 | OHL | 0.3023 | 1.2424 | 0.336 | 203 | 193 | 176 | 193
DUNM1C | ABED1T | 2020 | Addition | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193
ELGI3- | MEIK3- | 2020 | Addition | 0 | 18 | Cable | 16.87 | 18.02 | 1.67 | 33.6 | 30.5 | 30.5 | 30.5
FIDD1Q | FETT1- | 2020 | Addition | 10 | 0 | OHL | 0.5 | 2.07 | 0.56 | 241 | 230 | 210 | 230
FIDD1Q | FOGG1R | 2020 | Removed | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD1R | FOGG1R | 2020 | Addition | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD1S | FETT1- | 2020 | Addition | 10 | 0 | OHL | 0.5 | 2.07 | 0.56 | 241 | 230 | 210 | 230
GLAG1Q | MKTG1C | 2020 | Addition | 0 | 1.55 | Cable | 0.0463 | 0.0916 | 2.311 | 160 | 145 | 145 | 145
GLAG1R | MKTG1F | 2020 | Addition | 0 | 1.55 | Cable | 0.0463 | 0.0916 | 2.311 | 160 | 145 | 145 | 145
GORW2- | STRB2- | 2020 | Removed | 10.3 | 0 | OHL | 0.0819 | 0.5613 | 2.175 | 535 | 490 | 430 | 490
GORW2- | STRB2- | 2020 | Addition | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 702 | 665 | 599 | 665
KEIT1- | MACD1Q | 2020 | Removed | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | MACD1R | 2020 | Removed | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1J | MACD1Q | 2020 | Addition | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1K | MACD1R | 2020 | Addition | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT3- | GLOF3J | 2020 | Removed | 25.5 | 0 | OHL | 62.749 | 83.845 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KEIT3- | KEIT39 | 2020 | Removed | 18.6 | 0 | OHL | 47.608 | 52.757 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
KINT3- | GLOF3K | 2020 | Removed | 33.7 | 0 | OHL | 82.928 | 115.303 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KINT3- | GOHI3- | 2020 | Removed | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
LOCL1S | QUOI1Q | 2020 | Removed | 18.3 | 0 | OHL | 1.91 | 4.54 | 0.9 | 111 | 103 | 89 | 103
LOCL1S | QUOI1Q | 2020 | Addition | 18.3 | 0 | OHL | 0.9219 | 3.7893 | 1.025 | 203 | 193 | 176 | 193
MKTG1A | MKTG1B | 2020 | Addition | 0 | 0.25 | Cable | 0.01 | 0.0149 | 0.3448 | 155 | 129 | 129 | 129
MKTG1C | MKTG1B | 2020 | Addition | 0 | 0.25 | Cable | 0.01 | 0.0149 | 0.3448 | 155 | 129 | 129 | 129
MKTG1D | MKTG1E | 2020 | Addition | 0 | 0.25 | Cable | 0.01 | 0.0149 | 0.3448 | 155 | 129 | 129 | 129
MKTG1F | MKTG1E | 2020 | Addition | 0 | 0.25 | Cable | 0.01 | 0.0149 | 0.3448 | 155 | 129 | 129 | 129
ROTI2J | PEHERSV1 | 2020 | Addition | 47.36 | 0 | OHL | 0.2405 | 2.0474 | 12.366 | 1090 | 1030 | 920 | 1030
ROTI3- | GLOF3J | 2020 | Addition | 25.5 | 0 | OHL | 62.749 | 83.845 | 0 | 17.1 | 16.3 | 13.7 | 16.3
ROTI3- | GLOF3K | 2020 | Addition | 33.7 | 0 | OHL | 82.928 | 115.303 | 0 | 17.1 | 16.3 | 13.7 | 16.3
ROTI3- | GOHI3- | 2020 | Addition | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
ROTI3- | KEIT39 | 2020 | Addition | 18.6 | 0 | OHL | 47.608 | 52.757 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
STRB2- | LOCB2K | 2020 | Removed | 18.9 | 0 | OHL | 0.1503 | 1.0299 | 3.991 | 535 | 490 | 430 | 490
STRB2- | LOCB2K | 2020 | Addition | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 702 | 665 | 599 | 665
BEAU1J | BEAU1R | 2021 | Removed | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1J | BEAU1R | 2021 | Addition | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1K | BEAU1S | 2021 | Removed | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1K | BEAU1S | 2021 | Addition | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1R | INNE1Q | 2021 | Removed | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1R | INNE1Q | 2021 | Addition | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BEAU1S | INNE1R | 2021 | Removed | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1S | INNE1R | 2021 | Addition | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BEAU4- | FAUG4- | 2021 | Removed | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BEAU4- | FAUG4J | 2021 | Addition | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BLHI2L | KINT2J | 2021 | Removed | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2L | ROTI2J | 2021 | Addition | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2J | 2021 | Removed | 35.36 | 0 | OHL | 0.1795 | 1.5286 | 9.232 | 1090 | 1030 | 920 | 1030
BLHI2M | ROTI2K | 2021 | Addition | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BROR1Q | DUBE1Q | 2021 | Addition | 38.8 | 0 | OHL | 3.94 | 9.01 | 1.91 | 126 | 117 | 101 | 117
BROR1Q | DUBE1Q | 2021 | Removed | 38.5 | 0.077599 | Composite | 1.9676 | 8.6419 | 2.006 | 224 | 211 | 189 | 211
BROR1Q | LOCB1K | 2021 | Removed | 22.12 | 0 | OHL | 2.2511 | 5.1536 | 1.096 | 126 | 117 | 101 | 117
BROR1Q | LOCB1P | 2021 | Addition | 25.88 | 0 | OHL | 1.3199 | 5.7971 | 1.346 | 224 | 211 | 189 | 211
CAAD3- | BLRH3- | 2021 | Addition | 8.5 | 0 | OHL | 3.976 | 8.198 | 0.869 | 47.9 | 46.9 | 43.4 | 46.9
DUBE1Q | MYBS1R | 2021 | Removed | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 117 | 101 | 117
DUBE1Q | MYBS1R | 2021 | Addition | 20.84 | 0 | OHL | 1.0628 | 4.6682 | 1.084 | 224 | 211 | 189 | 211
ELGI1L | NAIR1Q | 2021 | Removed | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1L | NAIR1Q | 2021 | Addition | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1M | NAIR1R | 2021 | Removed | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1M | NAIR1R | 2021 | Addition | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1Q | ELGI1L | 2021 | Removed | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1Q | ELGI1L | 2021 | Addition | 0 | 1.8 | Cable | 0.0354 | 0.052 | 1.41 | 252 | 252 | 252 | 252
ELGI1Q | KEIT1- | 2021 | Removed | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1Q | KEIT1- | 2021 | Addition | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ELGI1R | ELGI1M | 2021 | Removed | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1R | ELGI1M | 2021 | Addition | 0 | 1.8 | Cable | 0.0354 | 0.052 | 1.41 | 251 | 252 | 252 | 252
ELGI1R | KEIT1- | 2021 | Removed | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1R | KEIT1- | 2021 | Addition | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
FAUG1- | LAGG1Q | 2021 | Removed | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1- | LAGG1R | 2021 | Removed | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1J | LAGG1Q | 2021 | Addition | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1K | LAGG1R | 2021 | Addition | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1P | LOCL1S | 2021 | Removed | 8.66 | 0 | OHL | 0.4365 | 1.7942 | 0.485 | 203 | 193 | 176 | 193
FAUG1P | MILS1Q | 2021 | Addition | 5.41 | 0 | OHL | 0.2727 | 1.1208 | 0.303 | 203 | 193 | 176 | 193
FAUG4- | MELG4J | 2021 | Removed | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
FAUG4J | MELG4J | 2021 | Addition | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
FETT3S | FEWI3- | 2021 | Addition | 6 | 0 | OHL | 2.736 | 6.114 | 0.66 | 47.9 | 46.9 | 43.4 | 46.9
INNE1Q | NAIR1Q | 2021 | Removed | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1Q | SLKB1J | 2021 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INNE1T | NAIR1R | 2021 | Removed | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1T | SLKB1K | 2021 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INNE1R | INNE1T | 2021 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
INNE1R | INNE1T | 2021 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 241 | 230 | 210 | 230
INVE1J | ACHR1R | 2021 | Removed | 21.17 | 0 | OHL | 3.002 | 4.9754 | 1.035 | 99 | 92 | 79 | 92
INVE1J | ACHR1R | 2021 | Addition | 21.17 | 0 | OHL | 0.3387 | 3.9588 | 1.291 | 739 | 710 | 662 | 710
INVE1K | ANSU1- | 2021 | Removed | 11.13 | 0 | OHL | 1.578 | 2.615 | 0.544 | 99 | 92 | 79 | 92
INVE1K | ANSU1- | 2021 | Addition | 11.13 | 0 | OHL | 0.1781 | 2.0813 | 0.679 | 739 | 710 | 662 | 710
KEIT3- | SPCH3- | 2021 | Addition | 1 | 0 | OHL | 0.72 | 1.04 | 0.09 | 29.4 | 28.8 | 26.7 | 28.8
KINT2K | PEHE2Q | 2021 | Removed | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
LOCB1J | LOCB1L | 2021 | Addition | 0 | 0.79 | Cable | 0.022 | 0.0694 | 1.039 | 149 | 137 | 137 | 137
LOCB1J | LOCB1N | 2021 | Addition | 0 | 0.38 | Cable | 0.0105 | 0.0332 | 0.496 | 149 | 137 | 137 | 137
LOCB1K | LOCB1M | 2021 | Addition | 0 | 0.73 | Cable | 0.0204 | 0.0641 | 0.96 | 149 | 137 | 137 | 137
LOCB1K | LOCB1P | 2021 | Addition | 0 | 0.28 | Cable | 0.01 | 0.0252 | 0.377 | 149 | 137 | 137 | 137
LOCL1S | MILS1Q | 2021 | Addition | 0 | 0 | OHL | 0.1638 | 0.6734 | 0.182 | 203 | 193 | 176 | 193
MILS3J | MILS3K | 2021 | Addition | 0 | 5 | Cable | 2.8926 | 4.9128 | 0.484 | 38 | 38 | 38 | 38
MYBS1Q | LOCB1J | 2021 | Removed | 81.61 | 0 | OHL | 8.2998 | 19.0008 | 4.028 | 126 | 117 | 101 | 117
MYBS1Q | LOCB1N | 2021 | Addition | 85.3 | 0 | OHL | 4.3503 | 19.1072 | 4.436 | 224 | 211 | 189 | 211
MYBS1Q | SPIT1J | 2021 | Removed | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1Q | SPIT1J | 2021 | Addition | 3.99 | 0 | OHL | 0.2035 | 0.8938 | 0.207 | 224 | 211 | 189 | 211
MYBS1R | SPIT1J | 2021 | Removed | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 2021 | Addition | 3.99 | 0 | OHL | 0.2035 | 0.8938 | 0.207 | 224 | 211 | 189 | 211
NAIR1Q | SLKB1L | 2021 | Addition | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
NAIR1R | SLKB1M | 2021 | Addition | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
PEHE2Q | NEDE2K | 2021 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHERSV1 | NEDE2J | 2021 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PORA1Q | ANSU1- | 2021 | Removed | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99 | 92 | 79 | 92
PORA1Q | ANSU1- | 2021 | Addition | 24.27 | 0 | OHL | 0.3883 | 4.5385 | 1.481 | 739 | 710 | 662 | 710
PORA1R | ACHR1R | 2021 | Removed | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
PORA1S | ACHR1R | 2021 | Addition | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ROTI2J | KINT2J | 2021 | Addition | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2021 | Addition | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
ROTI2J | PEHERSV1 | 2021 | Removed | 47.36 | 0 | OHL | 0.2405 | 2.0474 | 12.366 | 1090 | 1030 | 920 | 1030
ROTI2K | KINT2K | 2021 | Addition | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2K | NEDE2K | 2021 | Addition | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
SHIN1- | LOCB1J | 2021 | Removed | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 117 | 101 | 117
SHIN1- | LOCB1K | 2021 | Removed | 12.18 | 0 | OHL | 1.239 | 2.8365 | 0.604 | 126 | 117 | 101 | 117
SHIN1- | LOCB1L | 2021 | Addition | 8.34 | 0 | OHL | 0.4253 | 1.8682 | 0.434 | 224 | 211 | 189 | 211
SHIN1- | LOCB1M | 2021 | Addition | 8.34 | 0 | OHL | 0.4253 | 1.8682 | 0.434 | 224 | 211 | 189 | 211
SLKB1J | SLKB1L | 2021 | Addition | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLKB1K | SLKB1M | 2021 | Addition | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
TOMT1K | GLKO1- | 2021 | Addition | 3 | 0 | OHL | 0.417 | 0.627 | 0.156 | 83 | 77 | 67 | 77
BROA1Q | EDIN1- | 2022 | Removed | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 83 | 77 | 67 | 77
CAAD3- | WISL3- | 2022 | Addition | 0 | 85 | Cable | 38.714 | 88.2762 | 7.561 | 30 | 30 | 30 | 30
CAAD3J | TANG30 | 2022 | Addition | 17 | 0 | OHL | 6.24 | 16.7 | 2.04 | 53.7 | 48.8 | 47.1 | 48.8
CASS1Q | SALA1- | 2022 | Addition | 6 | 0 | OHL | 0.63 | 1.308 | 0.318 | 112 | 104 | 90 | 104
DOUN1- | LIMK1- | 2022 | Addition | 4 | 0 | OHL | 0.364 | 0.864 | 0.216 | 111 | 103 | 89 | 103
DOUN2A | DOUN2B | 2022 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 292 | 292 | 292 | 292
DOUN2B | DOUN2C | 2022 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 294 | 294 | 294 | 294
DOUN2C | FINS2C | 2022 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 270 | 270 | 270 | 270
DUGR1Q | EDIN1- | 2022 | Removed | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 83 | 77 | 67 | 77
DUGR1Q | EDIN1- | 2022 | Addition | 8.99 | 0 | OHL | 0.4497 | 1.8617 | 0.504 | 203 | 193 | 176 | 193
FAUG1- | EDIN1- | 2022 | Addition | 137.01 | 0 | OHL | 6.8503 | 28.3603 | 7.672 | 203 | 193 | 176 | 193
FINS2A | FINS2B | 2022 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 292 | 292 | 292 | 292
FINS2B | FINS2C | 2022 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 294 | 294 | 294 | 294
GARB1S | GARE1S | 2022 | Addition | 0 | 5.03 | Cable | 0.4558 | 1.1211 | 0.256 | 150.9 | 150.9 | 150.9 | 150.9
GARB1T | GARE1T | 2022 | Addition | 0 | 5.06 | Cable | 0.4586 | 1.1279 | 0.258 | 150.9 | 150.9 | 150.9 | 150.9
GILB1J | GILB1L | 2022 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1K | GILB1M | 2022 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GLRB2- | GLRO2- | 2022 | Addition | 14.53 | 0 | OHL | 0.0663 | 0.631 | 3.843 | 1171.7 | 1085.8 | 932.5 | 1085.8
LAIR1Q | LOCB1J | 2022 | Addition | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
LAIR1Q | SHIN1- | 2022 | Removed | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 111 | 103 | 89 | 103
LAIR1R | LOCB1K | 2022 | Addition | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
MYBS3M | HALY3- | 2022 | Addition | 5 | 0 | OHL | 2.28 | 5.095 | 0.55 | 47.9 | 43.4 | 43.1 | 43.4
PORA3- | SOUI3- | 2022 | Addition | 50 | 0 | OHL | 129 | 156.2 | 0.73 | 16.9 | 15.7 | 13.5 | 15.7
THUS1J | THUS1L | 2022 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
THUS1K | THUS1M | 2022 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
THUS1L | GILB1L | 2022 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
THUS1M | GILB1M | 2022 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
ALYT2A | FETT2P | 2024 | Addition | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2024 | Addition | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2024 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2024 | Addition | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2024 | Addition | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2024 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
CONN1K | CONN1D | 2024 | Addition | 0.66 | 0 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 2024 | Removed | 76.0713 | 0.26872 | Composite | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CRSS1J | WILW1- | 2024 | Addition | 10 | 0 | OHL | 0.91 | 2.16 | 0.54 | 132 | 123 | 106 | 123
DAAS3- | RTHE3- | 2024 | Addition | 0 | 3.5 | Cable | 3.28 | 3.5 | 0.33 | 37.2 | 30.5 | 30.5 | 30.5
DALB2A | CRDH2J | 2024 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
DALB2B | CRDH2K | 2024 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
DOUN2- | CONN2K | 2024 | Addition | 10.34 | 0 | OHL | 0.062 | 0.5688 | 2.193 | 702 | 665 | 599 | 665
DOUN2- | GORW2- | 2024 | Removed | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DOUN2A | DOUN2B | 2024 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 240 | 240 | 240 | 240
DOUN2A | DOUN2B | 2024 | Removed | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 292 | 292 | 292 | 292
DOUN2B | DOUN2C | 2024 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 240 | 240 | 240 | 240
DOUN2B | DOUN2C | 2024 | Removed | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 294 | 294 | 294 | 294
DOUN2C | FINS2C | 2024 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 240 | 240 | 240 | 240
DOUN2C | FINS2C | 2024 | Removed | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 270 | 270 | 270 | 270
DOUN2D | DOUN2E | 2024 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 240 | 240 | 240 | 240
DOUN2E | DOUN2F | 2024 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 240 | 240 | 240 | 240
DOUN2F | FINS2F | 2024 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 240 | 240 | 240 | 240
ELGI3- | MITA3- | 2024 | Addition | 0 | 7 | Cable | 5.21 | 6.75 | 0.71 | 42.4 | 34.8 | 34.8 | 34.8
FERO1S | CRDH1K | 2024 | Addition | 5.02 | 0 | OHL | 0.2662 | 1.0883 | 0.266 | 241.0001 | 230 | 210 | 230
FETT2Q | KINB2J | 2024 | Removed | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FINS2A | FINS2B | 2024 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 240 | 240 | 240 | 240
FINS2A | FINS2B | 2024 | Removed | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 292 | 292 | 292 | 292
FINS2B | FINS2C | 2024 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 240 | 240 | 240 | 240
FINS2B | FINS2C | 2024 | Removed | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 294 | 294 | 294 | 294
FINS2D | FINS2E | 2024 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 240 | 240 | 240 | 240
FINS2E | FINS2F | 2024 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.666 | 240 | 240 | 240 | 240
GARB1S | GARE1S | 2024 | Removed | 0 | 5.03 | Cable | 0.4558 | 1.1211 | 0.256 | 150.9 | 150.9 | 150.9 | 150.9
GARB1T | GARE1T | 2024 | Removed | 0 | 5.06 | Cable | 0.4586 | 1.1279 | 0.258 | 150.9 | 150.9 | 150.9 | 150.9
GLFA3- | PAUL30 | 2024 | Addition | 0 | 12.5 | Cable | 14.93 | 12.98 | 1.06 | 32.6 | 26.7 | 26.7 | 26.7
GLRB2- | GLRO2- | 2024 | Removed | 14.53 | 0 | OHL | 0.0663 | 0.631 | 3.843 | 1171.7 | 1085.8 | 932.5 | 1085.8
GOLT1T | GOLT1- | 2024 | Addition | 3 | 0 | OHL | 0.305 | 0.689 | 0.148 | 111 | 103 | 89 | 103
GORW2- | STRB2- | 2024 | Removed | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 702 | 665 | 599 | 665
GORW2A | CONN2J | 2024 | Addition | 46.57 | 0 | OHL | 0.2794 | 2.5612 | 9.872 | 702 | 665 | 599 | 665
GORW2A | LOCB2J | 2024 | Addition | 18.7893 | 10.9807 | Composite | 0.1786 | 1.6375 | 6.312 | 702.0001 | 665 | 599 | 665
INVE1J | CRDH1K | 2024 | Addition | 10.19 | 0 | OHL | 1.4452 | 2.3926 | 0.498 | 99 | 92 | 79 | 92
INVE1J | FERO1S | 2024 | Removed | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99.0001 | 92 | 79 | 92
INVE1K | CRDH1J | 2024 | Addition | 10.12 | 0 | OHL | 1.4405 | 2.3785 | 0.496 | 99 | 92 | 79 | 92
INVE1K | KILC1Q | 2024 | Removed | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
KILC1Q | CRDH1J | 2024 | Addition | 4.98 | 0 | OHL | 0.2643 | 1.0805 | 0.264 | 241.0001 | 230 | 210 | 230
KILC1Q | TAYN1Q | 2024 | Removed | 7.6 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILC1Q | TAYN1Q | 2024 | Addition | 7.6 | 0 | OHL | 0.4031 | 1.6479 | 0.403 | 241 | 230 | 210 | 230
KINT2J | TEAL2A | 2024 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2J | TEAL2J | 2024 | Removed | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | FETT2P | 2024 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 880 | 760 | 880
KINT2K | FETT2P | 2024 | Addition | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
KINT2K | FETT2Q | 2024 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 885 | 760 | 885
KINT2K | FETT2Q | 2024 | Addition | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
KINT2K | TEAL2B | 2024 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | TEAL2K | 2024 | Removed | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
LAIR1R | CREA1- | 2024 | Addition | 22 | 0 | OHL | 2.234 | 5.128 | 1.083 | 132 | 123 | 106 | 123
LOCB1N | GOLT1T | 2024 | Addition | 71.65 | 0 | OHL | 3.6542 | 16.05 | 3.726 | 224 | 211 | 189 | 211
MELG1J | GLSH1J | 2024 | Addition | 0 | 0.2 | Cable | 0.01 | 0.0153 | 0.271 | 220 | 211 | 211 | 211
MYBS1Q | GOLT1T | 2024 | Addition | 13.65 | 0 | OHL | 0.696 | 3.0571 | 0.71 | 224 | 211 | 189 | 211
MYBS1Q | LOCB1N | 2024 | Removed | 85.3 | 0 | OHL | 4.3503 | 19.1072 | 4.436 | 224 | 211 | 189 | 211
PEHE2J | NEDE2K | 2024 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHE2K | NEDE2J | 2024 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHE2Q | NEDE2K | 2024 | Removed | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHERSV1 | NEDE2J | 2024 | Removed | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PORA1Q | CRSS1Q | 2024 | Removed | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
PORA1Q | CRSS1Q | 2024 | Addition | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
PORA1R | ACHR1R | 2024 | Addition | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
PORA1R | CRSS1R | 2024 | Removed | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
PORA1R | CRSS1R | 2024 | Addition | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
PORA1S | ACHR1R | 2024 | Removed | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
STRB2- | CONN2K | 2024 | Addition | 58.06 | 0 | OHL | 0.3484 | 3.1937 | 12.311 | 702 | 665 | 599 | 665
STRW13 | STRW17 | 2024 | Addition | 0 | 0.27 | Cable | 0.01 | 0.0226 | 0.37 | 200 | 178 | 178 | 178
STRW17 | CONN1D | 2024 | Addition | 12.12 | 0 | OHL | 0.6109 | 2.5094 | 0.679 | 203 | 193 | 176 | 193
TAYN1R | FERO1S | 2024 | Removed | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92
TAYN1R | FERO1S | 2024 | Addition | 7.49 | 0 | OHL | 0.3973 | 1.624 | 0.397 | 241 | 230 | 210 | 230
TEAL2J | KINB2K | 2024 | Removed | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
TEAL2J | WFIB2- | 2024 | Removed | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2J | WFIB2- | 2024 | Addition | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
TEAL2K | FETT2P | 2024 | Removed | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
TEAL2K | GLRB2- | 2024 | Removed | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2K | GLRB2- | 2024 | Addition | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
ALYT2A | FETT2P | 2027 | Removed | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2027 | Removed | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2027 | Removed | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2K | 2027 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2027 | Removed | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2027 | Removed | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2J | 2027 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2027 | Removed | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT4J | FETT4Q | 2027 | Addition | 67.35 | 0 | OHL | 0.144 | 1.3213 | 38.757 | 1590 | 1500 | 1340 | 1500
ALYT4J | KINB4J | 2027 | Addition | 69.98 | 0 | OHL | 0.1496 | 1.3729 | 40.27 | 1590 | 1500 | 1340 | 1500
ALYT4K | FETT4R | 2027 | Addition | 67.35 | 0 | OHL | 0.144 | 1.3213 | 38.757 | 1590 | 1500 | 1340 | 1500
ALYT4K | KINB4K | 2027 | Addition | 69.98 | 0 | OHL | 0.1496 | 1.3729 | 40.27 | 1590 | 1500 | 1340 | 1500
BLHI1J | ELCH1- | 2027 | Addition | 20 | 0 | OHL | 1 | 4.14 | 1.12 | 203 | 193 | 176 | 193
BLHI2A | BERB2Q | 2027 | Addition | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 934.9996 | 880 | 790 | 880
BLHI2B | DAAS2- | 2027 | Addition | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2J | BERB2Q | 2027 | Removed | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935.0001 | 880 | 790 | 880
BLHI2K | DAAS2- | 2027 | Removed | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2L | ROTI2J | 2027 | Removed | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2K | 2027 | Removed | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI4- | ROTI4J | 2027 | Addition | 35.4 | 0 | OHL | 0.0757 | 0.6945 | 20.371 | 1590 | 1500 | 1340 | 1500
BLHI4- | ROTI4K | 2027 | Addition | 35.4 | 0 | OHL | 0.0757 | 0.6945 | 20.371 | 1590 | 1500 | 1340 | 1500
COGL4- | COGL4J | 2027 | Addition | 0 | 1.95 | Cable | 0.01 | 0.0264 | 9.165 | 930 | 900 | 900 | 900
COGL4- | COGL4K | 2027 | Addition | 0 | 1.95 | Cable | 0.01 | 0.0264 | 9.165 | 930 | 900 | 900 | 900
ELGI3- | SPYW3- | 2027 | Addition | 0 | 8.8 | Cable | 8.25 | 8.81 | 0.82 | 37.2 | 30.5 | 30.5 | 30.5
FAUG1- | FAUG1M | 2027 | Removed | 0 | 0.29 | Cable | 0.01 | 0.0225 | 0.486 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 2027 | Removed | 0 | 0.2 | Cable | 0.01 | 0.0157 | 0.339 | 220 | 209 | 209 | 209
FAUG1M | LOCL1Q | 2027 | Removed | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 2027 | Removed | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG4J | INGA4K | 2027 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940 | 1860 | 1720 | 1860
FAUG4K | INGA4J | 2027 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940 | 1860 | 1720 | 1860
FWIL1Q | INGA1J | 2027 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1Q | LOCL1Q | 2027 | Removed | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | INGA1K | 2027 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 2027 | Removed | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
INGA1Q | INGA1K | 2027 | Addition | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
INGA1Q | LOCL1Q | 2027 | Removed | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
INGA4J | COGL4J | 2027 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1470 | 1350 | 1170 | 1350
INGA4K | COGL4K | 2027 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1470 | 1350 | 1170 | 1350
KINT2J | PERS2R | 2027 | Removed | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030
KINT2J | PERS2R | 2027 | Addition | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1180 | 1120 | 1020 | 1120
KINT2K | FETT2P | 2027 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
KINT2K | FETT2Q | 2027 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
KINT2K | PEHE2R | 2027 | Removed | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 2027 | Addition | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1180 | 1120 | 1020 | 1120
KINT4J | FETT4Q | 2027 | Addition | 32.15 | 0 | OHL | 0.0687 | 0.6307 | 18.501 | 1590 | 1500 | 1340 | 1500
KINT4K | FETT4R | 2027 | Addition | 32.15 | 0 | OHL | 0.0687 | 0.6307 | 18.501 | 1590 | 1500 | 1340 | 1500
PEHE2- | PERS2Q | 2027 | Removed | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE2- | PERS2Q | 2027 | Addition | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1180 | 1120 | 1020 | 1120
PEHE2J | NEDE2K | 2027 | Removed | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHE2K | NEDE2J | 2027 | Removed | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHE4J | NEDE4J | 2027 | Addition | 22.39 | 0 | OHL | 0.0479 | 0.4393 | 12.886 | 1590 | 1500 | 1340 | 1500
PEHE4K | NEDE4K | 2027 | Addition | 22.39 | 0 | OHL | 0.0479 | 0.4393 | 12.886 | 1590 | 1500 | 1340 | 1500
ROTI2J | KINT2J | 2027 | Removed | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2027 | Removed | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
ROTI2K | KINT2K | 2027 | Removed | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2K | NEDE2K | 2027 | Removed | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
ROTI4J | KINT4J | 2027 | Addition | 23.2 | 0 | OHL | 0.0482 | 0.4436 | 13.769 | 1670 | 1570 | 1400 | 1570
ROTI4J | NEDE4J | 2027 | Addition | 24.97 | 0 | OHL | 0.0534 | 0.4898 | 14.368 | 1590 | 1500 | 1340 | 1500
ROTI4K | KINT4K | 2027 | Addition | 23.2 | 0 | OHL | 0.0482 | 0.4436 | 13.769 | 1670 | 1570 | 1400 | 1570
ROTI4K | NEDE4K | 2027 | Addition | 24.97 | 0 | OHL | 0.0534 | 0.4898 | 14.368 | 1590 | 1500 | 1340 | 1500
SHIN3- | GLCA3- | 2027 | Addition | 0 | 9.8 | Cable | 3.78 | 9.18 | 1.1 | 53.7 | 48.8 | 48.8 | 48.8

## B-2-2b
Table B.2.2b - SPT Circuit Changes 2019/20 to 2027/28 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
COAL1A | LINM1Q | 2019 | Addition | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
COAL1- | LINM1R | 2019 | Change | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 130 | 130 | 130 | 130
HUER4- | KILS4T | 2019 | Addition | 59.125 | 2e-06 | Composite | 0.0849 | 1.0902 | 37.0252 | 2037 | 1940 | 1760 | 1940
KILS4T | STHA4B | 2019 | Addition | 34.988 | 0 | OHL | 0.071312 | 0.7181 | 19.8609 | 1995 | 1926 | 1787 | 1926
COAL1A | GAWH1Q | 2019 | Addition | 0 | 10.5 | Cable | 0.16512 | 0.90393 | 17.3003 | 241 | 241 | 241 | 241
COAL1- | GAWH1Q | 2019 | Removed | 0 | 10.5 | Cable | 0.16512 | 0.90393 | 17.3003 | 241 | 241 | 241 | 241
COCK2- | KAIM2- | 2019 | Change | 18.29 | 0 | OHL | 0.0786 | 0.7771 | 4.9683 | 1372 | 1324 | 1228 | 1324
COCK2- | SMEA2- | 2019 | Change | 9.51 | 0 | OHL | 0.0408 | 0.4041 | 2.5833 | 1372 | 1324 | 1228 | 1324
COYL2- | COYW2S | 2019 | Change | 1.29 | 0.08 | Composite | 0.0058 | 0.0536 | 0.4557 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 2019 | Change | 1.32 | 0 | OHL | 0.0059 | 0.0543 | 0.3691 | 1910 | 1881 | 1834 | 1881
COYW2S | KILS2- | 2019 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 2019 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1500 | 1500 | 1500
KAIM2- | SMEA2- | 2019 | Change | 8.64 | 0 | OHL | 0.0371 | 0.3671 | 2.347 | 1372 | 1324 | 1228 | 1324
COAL1- | LINM1Q | 2019 | Removed | 0 | 8.97 | Cable | 0.246 | 1.521 | 3.108 | 134 | 123 | 123 | 123
HUER4- | STHA4B | 2019 | Removed | 94.151 | 0 | OHL | 0.1559 | 1.7959 | 57.0851 | 1995 | 1926 | 1787 | 1926
COAL1A | CUMH1A | 2020 | Change | 0 | 7.5 | Cable | 0.1179 | 0.6457 | 12.3574 | 241 | 241 | 241 | 241
COAL1A | LINM1Q | 2020 | Addition | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
CUMH1A | CUMH1- | 2020 | Addition | 0 | 0.2 | Cable | 0.0031 | 0.0172 | 0.3295 | 241 | 241 | 241 | 241
CUMH1B | CUMH1- | 2020 | Addition | 0 | 0.2 | Cable | 0.0031 | 0.0172 | 0.3295 | 241 | 241 | 241 | 241
CUMH1B | GAWH1Q | 2020 | Addition | 0 | 3 | Cable | 0.0472 | 0.2583 | 4.9429 | 241 | 241 | 241 | 241
CURR2- | GRMO2- | 2020 | Change | 42.18 | 0 | OHL | 0.1812 | 1.7922 | 11.4579 | 1372 | 1324 | 1228 | 1324
CURR2- | KAIM2- | 2020 | Change | 9.35 | 0 | OHL | 0.0402 | 0.3973 | 2.5399 | 1372 | 1324 | 1228 | 1324
CURR2- | KAIM2- | 2020 | Change | 9.35 | 0 | OHL | 0.0402 | 0.3973 | 2.5399 | 1372 | 1324 | 1228 | 1324
CURR2- | KINC2- | 2020 | Change | 57.14 | 0 | OHL | 0.2454 | 2.4279 | 15.5217 | 1372 | 1324 | 1228 | 1324
GORG1Q | TELR1Q | 2020 | Change | 0 | 3.74 | Cable | 0.0595 | 0.2797 | 5.8453 | 200 | 200 | 200 | 200
GORG1R | TELR1R | 2020 | Change | 0 | 3.72 | Cable | 0.0592 | 0.2782 | 5.814 | 200 | 200 | 200 | 200
GRMO2- | KINC2- | 2020 | Change | 14.96 | 0 | OHL | 0.0643 | 0.6356 | 4.0638 | 1372 | 1324 | 1228 | 1324
HUER4- | KILS4T | 2020 | Change | 59.125 | 2e-06 | Composite | 0.0849 | 1.0902 | 37.0252 | 2037 | 1940 | 1760 | 1940
KILS4T | STHA4B | 2020 | Change | 34.988 | 2e-06 | Composite | 0.071 | 0.7049 | 20.0387 | 1995 | 1926 | 1787 | 1926
NEIL2- | WIYH2R | 2020 | Change | 25.453 | 0 | OHL | 0.1092 | 1.082 | 6.9204 | 1372 | 1324 | 1228 | 1324
COAL1A | DALQ1- | 2022 | Addition | 4.1 | 1.4 | Composite | 0.2398 | 0.9927 | 2.5304 | 226 | 209 | 181 | 209
CONO1- | COAL1A | 2022 | Addition | 0 | 0.95 | Cable | 0.0078 | 0.0776 | 1.7691 | 293 | 293 | 293 | 293
CONO1- | LINM1Q | 2022 | Addition | 5.774 | 2.35 | Composite | 0.1565 | 1.4943 | 4.6733 | 293 | 293 | 293 | 293
COYL1- | COYT1T | 2022 | Change | 4.37 | 0.27 | Composite | 0.3368 | 1.0349 | 0.6613 | 284 | 278 | 270 | 278
COYL1- | MAYT1T | 2022 | Change | 9.14 | 0.57 | Composite | 0.7039 | 2.093 | 1.4079 | 284 | 278 | 270 | 278
COYT1T | MAYB1- | 2022 | Change | 17.666 | 0.28 | Composite | 1.3499 | 4.0068 | 1.3602 | 284 | 278 | 270 | 278
CRYR4- | TORN4- | 2022 | Change | 9.36 | 2.1 | Composite | 0.0127 | 0.1939 | 52.3382 | 1400 | 1400 | 1400 | 1400
DENN2- | LAMB2T | 2022 | Addition | 32.18 | 0 | OHL | 0.1471 | 1.3621 | 8.7301 | 953 | 882 | 762 | 882
DENN2- | LOAN2- | 2022 | Addition | 21.59 | 0 | OHL | 0.0507 | 0.8069 | 6.6393 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1C | 2022 | Change | 6.4 | 4.3 | Composite | 0.5762 | 1.7993 | 6.3388 | 135 | 125 | 108 | 125
DUNB1Q | DUNB1S | 2022 | Addition | 0 | 0.15 | Cable | 0.005 | 0.0152 | 0.3194 | 90 | 90 | 90 | 90
DUNB1Q | INWI1Q | 2022 | Change | 7.8 | 3.7 | Composite | 0.7914 | 2.1559 | 5.5488 | 165 | 165 | 165 | 165
DUNB1R | DUNB1T | 2022 | Addition | 0 | 0.15 | Cable | 0.005 | 0.0165 | 0.1478 | 90 | 90 | 90 | 90
DUNB1R | INWI1R | 2022 | Change | 7.8 | 4.3 | Composite | 0.8033 | 2.2103 | 6.3863 | 165 | 165 | 165 | 165
ERSK1Q | DEVM1- | 2022 | Change | 16.5 | 0 | OHL | 1.2378 | 3.6336 | 0.8679 | 167 | 154 | 134 | 154
EWEH1Q | GRNA1- | 2022 | Change | 15.7 | 0.11996 | Composite | 1.1946 | 3.405 | 1.1449 | 284 | 265 | 231 | 265
GARE1S | WHTL1S | 2022 | Change | 1.68 | 0 | OHL | 0.1265 | 0.39 | 0.0839 | 167 | 160 | 148 | 160
GARE1T | WHTL1T | 2022 | Change | 1.67 | 0 | OHL | 0.1258 | 0.3877 | 0.0834 | 167 | 160 | 148 | 160
GLGL1Q | SAKN1- | 2022 | Addition | 6.5 | 0 | OHL | 0.4876 | 1.4314 | 0.3419 | 166 | 159 | 147 | 159
GLRB2- | GLRO2- | 2022 | Change | 14.68 | 0 | OHL | 0.067 | 0.6375 | 3.8824 | 1096 | 1029 | 924 | 1029
GLRO2- | WFIE2- | 2022 | Change | 12.08 | 0 | OHL | 0.0551 | 0.5246 | 3.1948 | 1096 | 1029 | 924 | 1029
GRNA1- | HAWI1- | 2022 | Change | 55.35 | 0 | OHL | 5.0022 | 12.8111 | 2.7441 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 2022 | Change | 4.74 | 0 | OHL | 0.3983 | 1.0978 | 0.2361 | 135 | 126 | 108 | 126
INWI1Q | TORN1- | 2022 | Change | 0 | 1.15 | Cable | 0.0181 | 0.099 | 1.8948 | 165 | 165 | 165 | 165
INWI1R | TORN1- | 2022 | Change | 0 | 1.12 | Cable | 0.0176 | 0.0964 | 1.8454 | 165 | 165 | 165 | 165
MAHI1B | MAHI1R | 2022 | Addition | 13.5 | 0.5 | Composite | 1.0336 | 2.9676 | 1.5373 | 284 | 267 | 240 | 267
MAYB1- | MAYT1T | 2022 | Change | 12.59 | 0.31 | Composite | 0.9647 | 2.9098 | 1.1414 | 284 | 278 | 270 | 278
MOSM2- | MOSM2L | 2022 | Change | 5.3 | 0 | OHL | 0.0242 | 0.2302 | 1.4017 | 1090 | 1030 | 925 | 1030
MOSM2- | MOSM2T | 2022 | Change | 5.3 | 0 | OHL | 0.0242 | 0.2302 | 1.4017 | 1096 | 1029 | 924 | 1029
MOSM2T | WFIE2- | 2022 | Change | 2.943 | 0 | OHL | 0.0134 | 0.1278 | 0.7783 | 1096 | 1029 | 924 | 1029
NNGA2- | NNGA2T | 2022 | Addition | 0 | 12.3 | Cable | 0.093 | 0.447 | 31.794 | 381 | 381 | 381 | 381
NNGA2G | NNGA2T | 2022 | Addition | 0 | 34 | Cable | 0.225 | 0.882 | 87.8859 | 381 | 381 | 381 | 381
NNGB2- | NNGB2T | 2022 | Addition | 0 | 12.3 | Cable | 0.093 | 0.447 | 31.794 | 381 | 381 | 381 | 381
NNGB2G | NNGB2T | 2022 | Addition | 0 | 34 | Cable | 0.225 | 0.882 | 87.8859 | 381 | 381 | 381 | 381
WFIB2- | WFIE2- | 2022 | Change | 22.48 | 0 | OHL | 0.1026 | 0.9762 | 5.9452 | 1096 | 1029 | 924 | 1029
KEOO1R | LONB1T | 2022 | Addition | 10 | 0 | OHL | 0.5312 | 2.1273 | 0.5456 | 242 | 234 | 217 | 234
LAMB2T | LOAN2- | 2022 | Removed | 53.67 | 0.225 | Composite | 0.1978 | 2.1709 | 17.8013 | 795 | 620 | 620 | 620
COAL1A | LINM1Q | 2022 | Removed | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
AREC1- | MAHI1- | 2024 | Change | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
BAGA1Q | BONN1- | 2024 | Change | 18.3 | 0 | OHL | 0.7196 | 3.9815 | 0.9691 | 146 | 146 | 146 | 146
BAGA1Q | DRCR1Q | 2024 | Change | 4.71 | 3.39 | Composite | 0.5772 | 1.4684 | 2.8736 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 2024 | Change | 18.4 | 0 | OHL | 0.7236 | 4.0032 | 0.9744 | 146 | 146 | 146 | 146
BAGA1R | DRCR1R | 2024 | Change | 4.71 | 3.38 | Composite | 0.5768 | 1.4673 | 2.8658 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 2024 | Change | 7.02 | 0.08 | Composite | 0.2775 | 1.5328 | 0.4658 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 2024 | Change | 7.02 | 0.28 | Composite | 0.2811 | 1.5519 | 0.6992 | 114 | 114 | 114 | 114
BENB1B | BENB1- | 2024 | Addition | 3 | 0 | OHL | 0.225 | 0.6606 | 0.1578 | 167 | 154 | 134 | 154
BENB1B | KEOO1Q | 2024 | Addition | 4 | 0 | OHL | 0.1029 | 0.7399 | 0.248 | 482 | 445 | 385 | 445
BENB1B | NECU1B | 2024 | Addition | 20.25 | 0 | OHL | 0.5212 | 3.7458 | 1.2554 | 482 | 445 | 385 | 445
BERW1Q | ECCL1- | 2024 | Change | 21.54 | 0.31 | Composite | 1.9649 | 5.0014 | 1.5026 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 2024 | Change | 21.54 | 0.27 | Composite | 1.9642 | 4.9975 | 1.4468 | 132 | 123 | 106 | 123
BLAH1- | GLGL1- | 2024 | Change | 13.6 | 0.375 | Composite | 0.5181 | 3.026 | 1.6378 | 268 | 246 | 246 | 246
BLAH1- | GLGL1- | 2024 | Change | 13.6 | 0.375 | Composite | 0.5181 | 3.026 | 1.6378 | 268 | 246 | 246 | 246
BLKL1- | WISH1- | 2024 | Change | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 2024 | Change | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 2024 | Change | 19.894 | 0 | OHL | 0.0549 | 0.8105 | 5.6521 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 2024 | Change | 19.894 | 0 | OHL | 0.0259 | 0.3831 | 11.9581 | 2570 | 2570 | 2508 | 2570
BONN1- | STIR1S | 2024 | Change | 3.3 | 12.2 | Composite | 0.2525 | 1.5536 | 21.8264 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 2024 | Change | 3.3 | 12.2 | Composite | 0.2525 | 1.5536 | 21.8264 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 2024 | Change | 3.812 | 0.55 | Composite | 0.0185 | 0.1807 | 4.3533 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 2024 | Change | 3.812 | 0.46 | Composite | 0.0183 | 0.1782 | 3.8059 | 722 | 647 | 593 | 647
BRAP1- | ERSK1Q | 2024 | Change | 3.17 | 5.19 | Composite | 0.4605 | 1.3015 | 5.2712 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 2024 | Change | 3.45 | 6 | Composite | 0.475 | 1.4274 | 6.4114 | 102 | 79 | 79 | 79
BRAP1- | PAIS1R | 2024 | Change | 4.52 | 2.59 | Composite | 0.14 | 1.0674 | 4.2386 | 274 | 274 | 274 | 274
BRNX4- | ECCL4A | 2024 | Addition | 34.2 | 0 | OHL | 0.0445 | 0.6573 | 20.5984 | 2522 | 2397 | 2189 | 2397
BRNX4- | ECCL4B | 2024 | Addition | 34.2 | 0 | OHL | 0.0445 | 0.6573 | 20.5984 | 2522 | 2397 | 2189 | 2397
BRNX4- | SMEA4Q | 2024 | Addition | 58.82 | 0 | OHL | 0.0766 | 1.1305 | 35.4268 | 2473 | 2349 | 2148 | 2349
BRNX4- | TORN4- | 2024 | Addition | 0 | 1 | Cable | 0.0003 | 0.0067 | 22.2385 | 1040 | 900 | 900 | 900
BRNX4- | TORN4- | 2024 | Addition | 0 | 1 | Cable | 0.0003 | 0.0067 | 22.2385 | 1040 | 900 | 900 | 900
BUSB2- | STHA2A | 2024 | Change | 15.14 | 0 | OHL | 0.0651 | 0.6428 | 4.1106 | 750 | 690 | 630 | 690
CAFA1Q | KEOO1- | 2024 | Change | 0 | 2.58 | Cable | 0.0574 | 0.2571 | 2.7655 | 167 | 160 | 147 | 160
CHAP1- | DUMF1- | 2024 | Change | 26.9 | 0.17 | Composite | 1.0611 | 5.8608 | 1.9647 | 171 | 171 | 171 | 171
CHAP1- | ECCF1J | 2024 | Change | 6.569 | 0.181 | Composite | 0.6015 | 1.5317 | 0.8981 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 2024 | Change | 6.569 | 0.126 | Composite | 0.6003 | 1.527 | 0.7244 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 2024 | Change | 12.83 | 0.3 | Composite | 1.1751 | 2.9926 | 0.9495 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 2024 | Change | 12.83 | 0.35 | Composite | 1.1764 | 2.9978 | 1.0015 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 2024 | Change | 14.72 | 0 | OHL | 1.1184 | 3.1888 | 0.7779 | 284 | 263 | 227 | 263
CLYM2- | DALM2R | 2024 | Change | 4.21 | 0.093 | Composite | 0.0195 | 0.1806 | 1.8131 | 695 | 560 | 500 | 560
CLYM2- | LOAN2- | 2024 | Change | 54.22 | 0 | OHL | 0.1244 | 1.9959 | 16.8879 | 1500 | 1500 | 1500 | 1500
COAT2Q | NEAR2Q | 2024 | Change | 3.4 | 4.9 | Composite | 0.0452 | 0.2542 | 17.1143 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 2024 | Change | 3.4 | 4.9 | Composite | 0.0452 | 0.2542 | 17.1143 | 176 | 156 | 156 | 156
COYL1- | COYT1T | 2024 | Change | 4.37 | 0.27 | Composite | 0.3368 | 1.0349 | 0.6613 | 284 | 278 | 270 | 278
COYL1- | MAYT1T | 2024 | Change | 9.14 | 0.57 | Composite | 0.7039 | 2.093 | 1.4079 | 284 | 278 | 270 | 278
COYL2- | COYW2S | 2024 | Change | 1.29 | 0.08 | Composite | 0.0058 | 0.0536 | 0.4557 | 1500 | 1500 | 1500 | 1500
COYT1T | KILS1- | 2024 | Change | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 2024 | Change | 17.666 | 0.28 | Composite | 1.3499 | 4.0068 | 1.3602 | 284 | 278 | 270 | 278
COYW2S | KILS2- | 2024 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 2024 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1500 | 1500 | 1500
CROO1Q | NEIL1- | 2024 | Change | 12.56 | 0.22 | Composite | 0.4966 | 2.7546 | 0.9716 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 2024 | Change | 12.56 | 0.23 | Composite | 0.4967 | 2.7556 | 0.9855 | 229 | 211 | 183 | 211
CRYR4- | BRNX4- | 2024 | Addition | 13.86 | 0 | OHL | 0.018 | 0.2664 | 8.3478 | 2522 | 2397 | 2189 | 2397
CURR1A | GORG1Q | 2024 | Change | 1.49 | 5.8 | Composite | 0.2631 | 0.9543 | 5.1142 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 2024 | Change | 8.323 | 5.205 | Composite | 0.7954 | 2.3146 | 6.4736 | 132 | 123 | 106 | 123
CURR1B | GORG1R | 2024 | Change | 1.49 | 5.78 | Composite | 0.2624 | 0.9521 | 5.0969 | 111 | 100 | 92 | 100
CURR1B | LING1R | 2024 | Change | 8.323 | 5.335 | Composite | 0.8 | 2.3287 | 6.5864 | 132 | 123 | 106 | 123
CURR2- | SIGH2Q | 2024 | Change | 1.54 | 1.7 | Composite | 0.0173 | 0.1021 | 6.0434 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 2024 | Change | 1.54 | 1.67 | Composite | 0.0172 | 0.1015 | 5.9441 | 120 | 120 | 120 | 120
DALL2- | WIYH2- | 2024 | Change | 78.15 | 0 | OHL | 0.3357 | 3.3206 | 21.2289 | 570 | 570 | 570 | 570
DALQ1- | KENN1- | 2024 | Addition | 13 | 0 | OHL | 0.9752 | 2.8628 | 0.6838 | 166 | 159 | 147 | 159
DENN2- | LOAN2- | 2024 | Change | 21.59 | 0 | OHL | 0.0507 | 0.8069 | 6.6393 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2- | 2024 | Change | 21.59 | 0 | OHL | 0.0507 | 0.8069 | 6.6393 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1C | 2024 | Change | 6.4 | 4.3 | Composite | 0.5762 | 1.7993 | 6.3388 | 135 | 125 | 108 | 125
DEVM4- | NEIL4R | 2024 | Addition | 28.474 | 0 | OHL | 0.0465 | 0.5364 | 17.5637 | 1386 | 1282 | 1109 | 1282
DEVM4- | WIYH4Q | 2024 | Change | 28.908 | 0 | OHL | 0.047 | 0.5453 | 17.8155 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1T | 2024 | Change | 5.8 | 5.4 | Composite | 0.3137 | 1.7888 | 7.1063 | 162 | 154 | 141 | 154
DRUM2Q | WIYH2- | 2024 | Change | 2.46 | 0.29 | Composite | 0.0114 | 0.1121 | 3.8774 | 120 | 120 | 120 | 120
DUNB1Q | INWI1Q | 2024 | Change | 7.8 | 3.7 | Composite | 0.7914 | 2.1559 | 5.5488 | 165 | 165 | 165 | 165
DUNB1R | INWI1R | 2024 | Change | 7.8 | 4.3 | Composite | 0.8033 | 2.2103 | 6.3863 | 165 | 165 | 165 | 165
DUNE1- | SMEA1- | 2024 | Change | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 152 | 122 | 122 | 122
DUNF1Q | INKE1Q | 2024 | Change | 7.58 | 0.09 | Composite | 0.6934 | 1.7561 | 0.5525 | 132 | 122 | 106 | 122
DUNF1R | INKE1R | 2024 | Change | 7.58 | 0.09 | Composite | 0.6934 | 1.7561 | 0.5525 | 132 | 122 | 106 | 122
EAST1Q | GLLE1- | 2024 | Change | 0 | 1.69 | Cable | 0.0376 | 0.1684 | 1.8115 | 167 | 160 | 147 | 160
EERH2- | LOAN2- | 2024 | Change | 46.23 | 0 | OHL | 0.1061 | 1.7018 | 14.3993 | 1500 | 1500 | 1500 | 1500
EKIL2R | EKIL2T | 2024 | Change | 5.17 | 0.108 | Composite | 0.0144 | 0.1951 | 2.0737 | 480 | 405 | 405 | 405
EKIS2- | NEIL2- | 2024 | Change | 29.58 | 0 | OHL | 0.1272 | 1.2564 | 8.0276 | 1120 | 1060 | 990 | 1060
EKIS2- | STHA2B | 2024 | Change | 5.8 | 0 | OHL | 0.0249 | 0.2461 | 1.5758 | 1050 | 965 | 880 | 965
ELDE1Q | NEIL1- | 2024 | Change | 3.82 | 0.18 | Composite | 0.1524 | 0.8487 | 0.4532 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 2024 | Change | 3.82 | 0.23 | Composite | 0.153 | 0.8535 | 0.5229 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 2024 | Change | 65.54 | 0 | OHL | 0.1415 | 1.345 | 36.6292 | 3222 | 3167 | 3090 | 3167
ELVA4- | MOFF4- | 2024 | Change | 23.5 | 0 | OHL | 0.0507 | 0.4823 | 13.1337 | 3222 | 3167 | 3090 | 3167
ELVA4- | STHA4A | 2024 | Change | 48.56 | 0 | OHL | 0.0863 | 0.9643 | 28.2318 | 2210 | 2130 | 1980 | 2130
ENHI1- | NECU1C | 2024 | Addition | 0 | 5 | Cable | 0.1412 | 0.3245 | 6.5687 | 122 | 107 | 107 | 107
ESST1R | WIYH1- | 2024 | Change | 2.089 | 1.376 | Composite | 0.236 | 0.6357 | 2.5748 | 233 | 200 | 200 | 200
EWEH1Q | GRNA1- | 2024 | Change | 15.7 | 0.11996 | Composite | 1.1946 | 3.405 | 1.1449 | 284 | 265 | 231 | 265
GALA1- | ECCL1- | 2024 | Addition | 30.5 | 0 | OHL | 2.2947 | 7.1644 | 1.5057 | 166 | 159 | 147 | 159
GALA1- | ECCL1- | 2024 | Addition | 30.5 | 0 | OHL | 2.2947 | 7.1644 | 1.5057 | 166 | 159 | 147 | 159
GARB1Q | HELE1- | 2024 | Change | 15.3129 | 0 | OHL | 1.3918 | 3.5305 | 0.7615 | 132 | 123 | 106 | 123
GARB1R | STLE1- | 2024 | Change | 26.9091 | 0 | OHL | 2.4458 | 6.2041 | 1.3382 | 132 | 123 | 106 | 123
GARE1S | WIYH1- | 2024 | Change | 35.0819 | 0.3304 | Composite | 3.2036 | 8.1237 | 2.3777 | 109 | 105 | 101 | 105
GARE1T | WIYH1- | 2024 | Change | 34.7398 | 0.1623 | Composite | 3.1649 | 8.0269 | 2.0386 | 109 | 105 | 101 | 105
GHPS1- | GLGL1- | 2024 | Addition | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 272 | 251 | 272
GHPS1- | GLGL1- | 2024 | Addition | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 272 | 251 | 272
GLLE1- | NETS1- | 2024 | Change | 30.04 | 0 | OHL | 2.2901 | 6.8792 | 1.5047 | 284 | 278 | 270 | 278
GLLE1- | NETS1- | 2024 | Change | 30.04 | 0 | OHL | 2.2901 | 6.8792 | 1.5047 | 284 | 278 | 270 | 278
GLLE1- | TONG1- | 2024 | Change | 33.1 | 33.1 | Composite | 2.0233 | 7.551 | 1.6852 | 163 | 150 | 127 | 150
GLLE1- | TONG1- | 2024 | Addition | 33.1 | 0 | OHL | 2.0233 | 7.551 | 1.6852 | 163 | 150 | 127 | 150
GLLU1Q | NETS1- | 2024 | Change | 22 | 0 | OHL | 1.3448 | 5.0188 | 1.1201 | 163 | 150 | 127 | 150
GLLU1R | NETS1- | 2024 | Change | 22 | 0 | OHL | 1.3448 | 5.0188 | 1.1201 | 163 | 150 | 127 | 150
GLNI1- | MOSM1- | 2024 | Change | 1.41 | 0.09 | Composite | 0.0654 | 0.2448 | 0.3769 | 171 | 171 | 171 | 171
GLNI1- | MOSM1- | 2024 | Change | 1.41 | 0.11 | Composite | 0.0657 | 0.2465 | 0.4393 | 171 | 171 | 171 | 171
GRNA1- | HAWI1- | 2024 | Change | 55.35 | 0 | OHL | 5.0022 | 12.8111 | 2.7441 | 132 | 123 | 106 | 123
GRNA4- | HAKB4B | 2024 | Change | 1.97 | 0 | OHL | 0.0043 | 0.0404 | 1.101 | 3222 | 3167 | 3090 | 3167
HAKB4- | MOFF4C | 2024 | Change | 43.79 | 0 | OHL | 0.0946 | 0.8986 | 24.4735 | 3222 | 3167 | 3090 | 3167
HELE1- | WIYH1- | 2024 | Change | 24.7994 | 0.182 | Composite | 2.2623 | 5.7372 | 1.582 | 109 | 105 | 101 | 105
HUER4- | KILS4- | 2024 | Change | 59.125 | 0 | OHL | 0.0849 | 1.0902 | 37.0252 | 2030 | 1930 | 1770 | 1930
HUNE4- | NEIL4Q | 2024 | Change | 35.198 | 0 | OHL | 0.0711 | 0.7088 | 20.1355 | 1386 | 1282 | 1109 | 1282
HUNE4- | NEIL4R | 2024 | Addition | 34.97 | 0 | OHL | 0.0706 | 0.7042 | 20.0047 | 1386 | 1282 | 1109 | 1282
HUNF1Q | KILW1R | 2024 | Change | 12.85 | 3.06 | Composite | 0.6024 | 3.1055 | 6.8778 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 2024 | Change | 8.572 | 3.04 | Composite | 0.4336 | 2.1725 | 6.6108 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 2024 | Change | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 2024 | Change | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240
KEOO1- | GLLE1- | 2024 | Addition | 7.68 | 0 | OHL | 0.1977 | 1.4206 | 0.4761 | 482 | 445 | 385 | 445
KEOO1- | KEOO1R | 2024 | Addition | 2.5 | 0 | OHL | 0.0643 | 0.4624 | 0.155 | 482 | 445 | 385 | 445
KEOO1Q | KEOO1S | 2024 | Addition | 2.5 | 0 | OHL | 0.0643 | 0.4624 | 0.155 | 482 | 445 | 385 | 445
KEOO1Q | MARG1Q | 2024 | Addition | 0 | 0.9 | Cable | 0.0142 | 0.0775 | 1.4829 | 241 | 241 | 241 | 241
KEOO1R | NECU1B | 2024 | Addition | 24.25 | 0 | OHL | 0.6241 | 4.4857 | 1.5034 | 482 | 445 | 385 | 445
KEOO1S | GLLE1- | 2024 | Addition | 7.68 | 0 | OHL | 0.1977 | 1.4206 | 0.4761 | 482 | 445 | 385 | 445
KIER1Q | WIYH1- | 2024 | Change | 2.089 | 4.183 | Composite | 0.3888 | 0.9422 | 7.6146 | 100 | 80 | 60 | 80
KILS2- | KILT2Q | 2024 | Change | 3.56 | 0.29 | Composite | 0.0177 | 0.1608 | 2.059 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 2024 | Change | 3.56 | 0.33 | Composite | 0.0179 | 0.1617 | 2.2132 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 2024 | Change | 34.948 | 0 | OHL | 0.0709 | 0.7041 | 20.0164 | 2000 | 1920 | 1790 | 1920
KINB2J | KINC2- | 2024 | Change | 10.325 | 0.385 | Composite | 0.0474 | 0.4407 | 6.9969 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2024 | Change | 10.71 | 0 | OHL | 0.049 | 0.4533 | 2.9052 | 1090 | 1030 | 925 | 1030
KINC2- | LOAN2Q | 2024 | Change | 4.28 | 0.31 | Composite | 0.019 | 0.1902 | 4.4568 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 2024 | Change | 4.28 | 0.17 | Composite | 0.0187 | 0.1862 | 2.8678 | 765 | 620 | 620 | 620
KYPE1- | COAL1- | 2024 | Change | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 229 | 215 | 215 | 215
LAMB2- | PORD2R | 2024 | Change | 3.94 | 0.177 | Composite | 0.019 | 0.1688 | 2.1709 | 300 | 300 | 300 | 300
LEVT1R | WFIE1B | 2024 | Change | 18.707 | 0 | OHL | 1.5939 | 4.2994 | 0.9354 | 143 | 142 | 128 | 142
LOAN2- | MOSM2L | 2024 | Change | 26.196 | 0.194 | Composite | 0.12 | 1.142 | 8.6702 | 1090 | 1030 | 925 | 1030
LOAN2- | WFIE2- | 2024 | Change | 29.169 | 0.154 | Composite | 0.1335 | 1.2702 | 9.0972 | 1090 | 1030 | 925 | 1030
LONB1T | LONB1- | 2024 | Addition | 2 | 0 | OHL | 0.15 | 0.4404 | 0.1052 | 166 | 159 | 147 | 159
LONB1T | LORG1- | 2024 | Addition | 8 | 0 | OHL | 0.6001 | 1.7617 | 0.4208 | 166 | 159 | 147 | 159
MAHI1B | MAHI1R | 2024 | Change | 13.5 | 0.5 | Composite | 1.0336 | 2.9676 | 1.5373 | 284 | 267 | 240 | 267
MAHI1R | CHMO1- | 2024 | Addition | 1.01 | 0 | OHL | 0.0759 | 0.2222 | 0.0532 | 167 | 154 | 134 | 154
MARG1Q | MARG1- | 2024 | Addition | 10.1 | 0 | OHL | 0.5052 | 2.1466 | 0.5518 | 241 | 230 | 210 | 230
MAYB1- | MAYT1T | 2024 | Change | 12.59 | 0.31 | Composite | 0.9647 | 2.9098 | 1.1414 | 284 | 278 | 270 | 278
NECU1C | SOKY1- | 2024 | Addition | 0 | 4.5 | Cable | 0.0292 | 0.2677 | 7.8824 | 242 | 223 | 192 | 223
NEIL1- | PAIS1R | 2024 | Change | 8.31 | 0.31 | Composite | 0.1782 | 1.5629 | 0.7745 | 268 | 268 | 268 | 268
NEIL2- | WIYH2R | 2024 | Change | 25.453 | 0 | OHL | 0.11 | 1.0816 | 6.9193 | 1372 | 1324 | 1228 | 1324
POOB2Q | SMEA2- | 2024 | Change | 7.79 | 0.19 | Composite | 0.0341 | 0.3355 | 2.9286 | 360 | 300 | 240 | 300
POOB2R | SMEA2- | 2024 | Change | 7.79 | 0.19 | Composite | 0.0341 | 0.3355 | 2.9286 | 360 | 300 | 240 | 300
REDH1- | WFIE1A | 2024 | Change | 10.097 | 0 | OHL | 0.8108 | 2.3122 | 0.5075 | 157 | 152 | 141 | 152
SANQ1- | GLGL1- | 2024 | Addition | 4 | 0 | OHL | 0.3001 | 0.8809 | 0.2104 | 166 | 159 | 147 | 159
SMEA4Q | WISH4- | 2024 | Addition | 61.77 | 0 | OHL | 0.1253 | 1.2408 | 35.4861 | 1995 | 1926 | 1787 | 1926
SMEA4R | WISH4- | 2024 | Change | 61.77 | 0 | OHL | 0.1253 | 1.2408 | 35.4861 | 1995 | 1926 | 1787 | 1926
SQHR1- | NECU1C | 2024 | Addition | 22 | 0 | OHL | 1.6504 | 4.8447 | 1.1571 | 167 | 157 | 141 | 157
STHA4A | WISH4- | 2024 | Change | 11.6 | 0 | OHL | 0.0235 | 0.233 | 6.6641 | 1995 | 1926 | 1787 | 1926
STHA4B | WISH4- | 2024 | Addition | 13.99 | 0 | OHL | 0.0284 | 0.281 | 8.0371 | 1995 | 1926 | 1787 | 1926
STIR1S | WFIE1A | 2024 | Change | 37.6 | 5.4 | Composite | 3.2013 | 9.1255 | 8.6842 | 162 | 154 | 141 | 154
STLE1- | WIYH1- | 2024 | Change | 12.8916 | 0.2908 | Composite | 1.1849 | 3.0034 | 1.1983 | 109 | 105 | 101 | 105
STNO1- | MAHI1R | 2024 | Addition | 7.5 | 0 | OHL | 0.5626 | 1.6516 | 0.3945 | 167 | 160 | 146 | 160
DEVM4- | HUNE4- | 2024 | Removed | 50.471 | 0.167 | Composite | 0.0897 | 0.9802 | 33.4802 | 1316 | 1067 | 1067 | 1067
CRYR4- | TORN4- | 2024 | Removed | 9.36 | 2.1 | Composite | 0.0127 | 0.1939 | 52.3382 | 1400 | 1400 | 1400 | 1400
ECCL4B | TORN4- | 2024 | Removed | 34.2 | 2.1 | Composite | 0.0451 | 0.6714 | 67.2991 | 2330 | 1840 | 1840 | 1840
SMEA4Q | STHA4B | 2024 | Removed | 75.76 | 0 | OHL | 0.1626 | 1.517 | 43.53 | 1390 | 1280 | 1110 | 1280
ECCL1- | GALA1- | 2024 | Removed | 31.37 | 0 | OHL | 2.848 | 7.3696 | 1.5301 | 132 | 123 | 106 | 123
DUMF1- | TONG1Q | 2024 | Removed | 0 | 43.58 | Cable | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
ECCL4A | TORN4- | 2024 | Removed | 34.2 | 2.1 | Composite | 0.0451 | 0.6714 | 67.2991 | 2330 | 1840 | 1840 | 1840
GLLE1- | KEOO1- | 2024 | Removed | 7.68 | 0 | OHL | 0.697 | 1.6798 | 0.4048 | 132 | 123 | 106 | 123
MARG1- | NECU1B | 2024 | Removed | 34.35 | 0.9 | Composite | 1.1434 | 6.7098 | 3.5381 | 241 | 230 | 210 | 230
SMEA4Q | TORN4- | 2024 | Removed | 54.32 | 1.94 | Composite | 0.0727 | 1.0761 | 70.7405 | 945 | 800 | 800 | 800
ECCL1- | GALA1- | 2024 | Removed | 30.94 | 0 | OHL | 2.8142 | 7.133 | 1.538 | 132 | 123 | 106 | 123
KEOO1- | NECU1B | 2024 | Removed | 26.51 | 0 | OHL | 0.8292 | 5.0188 | 1.6132 | 133 | 123 | 106 | 123
BRNX4A | BRNX4- | 2027 | Addition | 0 | 0.25 | Cable | 0 | 0 | 0 | 6928 | 6928 | 6928 | 6928
ELVA1- | NLEI1- | 2027 | Addition | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 209 | 181 | 209
FASI1- | FASI1T | 2027 | Addition | 2.6 | 0 | OHL | 0.1975 | 0.5632 | 0.1374 | 284 | 270 | 247 | 270
FASI1T | GRNA1- | 2027 | Addition | 36.24 | 0 | OHL | 2.7527 | 7.9175 | 1.9018 | 284 | 278 | 270 | 278
FASI1T | HAWI1- | 2027 | Addition | 19.11 | 0 | OHL | 1.7313 | 4.1776 | 1.0002 | 161 | 149 | 129 | 149
GRNA1- | JUNV1- | 2027 | Change | 4.74 | 0 | OHL | 0.3593 | 1.0935 | 0.237 | 167 | 164 | 159 | 164
KINC4B | KINC4S | 2027 | Addition | 0 | 0.35 | Cable | 0.0002 | 0.0047 | 3.8917 | 1590 | 1500 | 1350 | 1500
SCOP1- | MOFF1- | 2027 | Addition | 0 | 10 | Cable | 0.0723 | 0.8232 | 40.4522 | 280 | 280 | 280 | 280
SCOP1- | MOFF1- | 2027 | Addition | 0 | 10 | Cable | 0.0723 | 0.8232 | 40.4522 | 280 | 280 | 280 | 280
KINB2J | KINC2- | 2027 | Removed | 10.325 | 0.385 | Composite | 0.0474 | 0.4407 | 6.9969 | 760 | 620 | 620 | 620
GRNA1- | HAWI1- | 2027 | Removed | 55.35 | 0 | OHL | 5.0022 | 12.8111 | 2.7441 | 132 | 123 | 106 | 123
KINB2K | KINC2- | 2027 | Removed | 10.71 | 0 | OHL | 0.049 | 0.4533 | 2.9052 | 910 | 885 | 760 | 885
KINB4K | KINC4S | 2027 | Addition | 10.15 | 0 | OHL | 0.0002 | 0.0047 | 3.8917 | 1590 | 1470.75 | 1269.615 | 1470.75
KINC4B | KINC4S | 2027 | Addition | 0 | 0.35 | Cable | 0.0002 | 0.0047 | 3.8917 | 1590 | 1470.75 | 1269.615 | 1470.75

## B-2-2c
Table B.2.2c - NGET Circuit Changes 2019/20 to 2027/28 | [13 empty] | Back To Menu
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
BRED21 | MACC21 | 2019 | Change | 19.612 | 0 | OHL | 0.000768 | 0.008127 | 0.054608 | 948 | 876.9 | 756.978 | 876.9
BRED21 | STAL21 | 2019 | Change | 15.054 | 0 | OHL | 0.000665 | 0.006343 | 0.041113 | 1093 | 1011.025 | 872.7605 | 1011.025
BRFO41 | DISS41 | 2019 | Addition | 30 | 0.1 | Composite | 0.000479 | 0.006057 | 0.19206 | 1590 | 1470.75 | 1269.615 | 1470.75
BRFO41 | DISS41 | 2019 | Addition | 30 | 0.1 | Composite | 0.000479 | 0.006057 | 0.19206 | 3070 | 2839.75 | 2451.395 | 2839.75
DISS41 | NORM41 | 2019 | Addition | 31.576 | 0 | OHL | 0.000504 | 0.006363 | 0.1811 | 3070 | 2839.75 | 2451.395 | 2839.75
DISS41 | NORM41 | 2019 | Addition | 31.576 | 0 | OHL | 0.000504 | 0.006363 | 0.1811 | 3070 | 2839.75 | 2451.395 | 2839.75
EYES41 | DISS41 | 2019 | Addition | 5 | 0 | OHL | 4.4e-05 | 0.000859 | 0.033607 | 1590 | 1470.75 | 1269.615 | 1470.75
EYES41 | DISS41 | 2019 | Addition | 5 | 0 | OHL | 4.4e-05 | 0.000859 | 0.033607 | 1590 | 1470.75 | 1269.615 | 1470.75
HFLD41 | THOM41 | 2019 | Addition | 0 | 5 | Cable | 4e-05 | 0.000735 | 0.8265 | 1050 | 971.25 | 838.425 | 971.25
KENG41 | SJOW41 | 2019 | Change | 0 | 6 | Cable | 2.7e-05 | 0.000473 | 0.43661 | 2000 | 1850 | 1597 | 1850
KENG41 | SJOW41 | 2019 | Change | 0 | 6 | Cable | 2.7e-05 | 0.000473 | 0.43661 | 2000 | 1850 | 1597 | 1850
KENG41 | WLSD41 | 2019 | Change | 0 | 3 | Cable | 2e-05 | 0.000355 | 0.32746 | 1770 | 1637.25 | 1413.345 | 1637.25
KENG41 | WLSD42 | 2019 | Change | 0 | 3 | Cable | 2e-05 | 0.000355 | 0.32746 | 1770 | 1637.25 | 1413.345 | 1637.25
KINO41 | NFLE41 | 2019 | Change | 23.626 | 0 | OHL | 0.000249 | 0.004177 | 0.15452 | 3102 | 2869.35 | 2476.947 | 2869.35
MACC41 | STAL41 | 2019 | Change | 31.196 | 0 | OHL | 0.00062 | 0.00617 | 0.18176 | 1710 | 1581.75 | 1365.435 | 1581.75
SING41 | KINO41 | 2019 | Change | 17.685 | 0 | OHL | 0.000157 | 0.003038 | 0.11887 | 3820 | 3533.5 | 3050.27 | 3533.5
WISD21 | EALI21 | 2019 | Addition | 0 | 8.075 | Cable | 2e-05 | 0.000229 | 0.1013 | 665 | 615.125 | 531.0025 | 615.125
BRFO41 | NORM41 | 2019 | Removed | 61.576 | 0.1 | Composite | 0.000983 | 0.01242 | 0.37315 | 1590 | 1470.75 | 1269.615 | 1470.75
WIMB21 | WISD2B | 2019 | Removed | 0 | 20.669 | Cable | 0.000413 | 0.004733 | 2.0938 | 738 | 682.65 | 589.293 | 682.65
BRFO41 | NORM41 | 2019 | Removed | 61.576 | 0.1 | Composite | 0.000983 | 0.01242 | 0.37315 | 1590 | 1470.75 | 1269.615 | 1470.75
BOTW41 | CHIL41 | 2020 | Addition | 7.479 | 0 | OHL | 6.6e-05 | 0.001285 | 0.05027 | 692.8203 | 640.8588 | 553.217 | 640.8588
BRAI4A | BRFO41 | 2020 | Change | 49.699 | 0 | OHL | 0.000443 | 0.008539 | 0.33386 | 2779 | 2570.575 | 2219.0315 | 2570.575
BRAI4B | RAYL41 | 2020 | Change | 53.678 | 0 | OHL | 0.000582 | 0.009335 | 0.35391 | 2779 | 2570.575 | 2219.0315 | 2570.575
BRFO41 | BRAI4B | 2020 | Addition | 48.267 | 0 | OHL | 0.000428 | 0.00829 | 0.32442 | 2780 | 2571.5 | 2219.83 | 2571.5
BRFO41 | PELH41 | 2020 | Addition | 69.301 | 0 | OHL | 0.000701 | 0.011997 | 0.46018 | 3100 | 2867.5 | 2475.35 | 2867.5
BRFO41 | PELH41 | 2020 | Change | 69.301 | 0 | OHL | 0.000701 | 0.011997 | 0.46018 | 3102 | 2869.35 | 2476.947 | 2869.35
CHIL41 | FAWL41 | 2020 | Addition | 0 | 7.14 | parallel Cable | 1.8e-05 | 0.000112 | 1.091 | 1099.9999 | 1017.4999 | 878.3499 | 1017.4999
CHIL41 | LOVE41 | 2020 | Addition | 22.379 | 0.315 | Composite | 0.000201 | 0.00389 | 0.20248 | 692.8203 | 640.8588 | 553.217 | 640.8588
FLEE41 | LOVE41 | 2020 | Change | 41.095 | 0 | OHL | 0.00064 | 0.007885 | 0.24661 | 3100 | 2867.5 | 2475.35 | 2867.5
FLEE41 | LOVE41 | 2020 | Change | 41.095 | 0 | OHL | 0.00064 | 0.007885 | 0.24661 | 3100 | 2867.5 | 2475.35 | 2867.5
KEMS41 | LOFI4A | 2020 | Change | 38.035 | 0 | OHL | 0.000594 | 0.007327 | 0.22719 | 1926 | 1781.55 | 1537.911 | 1781.55
KEMS41 | LOFI4B | 2020 | Change | 37.572 | 0 | OHL | 0.000587 | 0.007235 | 0.22451 | 1926 | 1781.55 | 1537.911 | 1781.55
KILL41 | KILL41 | 2020 | Addition | -- | -- | Series Reactor | 0 | 0.01 | -- | 2750 | 2543.75 | 2195.875 | 2543.75
LITT41 | LOFI4A | 2020 | Change | 8.152 | 0 | OHL | 0.000127 | 0.00157 | 0.048712 | 1389 | 1284.825 | 1109.1165 | 1284.825
LITT41 | LOFI4B | 2020 | Change | 8.152 | 0 | OHL | 0.000127 | 0.00157 | 0.048712 | 1389 | 1284.825 | 1109.1165 | 1284.825
NORT41 | OSBA41 | 2020 | Change | 83.839 | 0 | OHL | 0.001097 | 0.015842 | 0.51294 | 2780 | 2571.5 | 2219.83 | 2571.5
NORT41 | OSBA42 | 2020 | Change | 83.839 | 0 | OHL | 0.001097 | 0.015842 | 0.51294 | 2009 | 1858.325 | 1604.1865 | 1858.325
TILB4A | TILB41 | 2020 | Removed | 0.05808 | 0 | OHL | 1e-06 | 1.2e-05 | 0.00033 | 3102 | 2869.35 | 2476.947 | 2869.35
BOTW41 | FAWL41 | 2020 | Removed | 7.479 | 3.57 | Composite | 0.000102 | 0.001509 | 0.59577 | 1109 | 1025.825 | 885.5365 | 1025.825
TILB41 | TILB4B | 2020 | Removed | 0.0589 | 0 | OHL | 1e-06 | 1.1e-05 | 0.000353 | 3102 | 2869.35 | 2476.947 | 2869.35
FAWL41 | LOVE41 | 2020 | Removed | 22.379 | 3.885 | Composite | 0.000237 | 0.004115 | 0.74798 | 1109 | 1025.825 | 885.5365 | 1025.825
BRAI4B | PELH41 | 2020 | Removed | 65.942 | 0 | OHL | 0.00065 | 0.011398 | 0.4392 | 2779 | 2570.575 | 2219.0315 | 2570.575
LISD21 | LISD21 | 2020 | Removed | -- | -- | Series Reactor | 0.000173 | 0.01387 | -- | 750 | 693.75 | 598.875 | 693.75
CANW41 | OSWE41 | 2022 | Addition | 34.812 | 0 | OHL | 0.000556 | 0.006695 | 0.20934 | 2400 | 2220 | 1916.4 | 2220
CANW41 | OSWE41 | 2022 | Addition | 34.812 | 0 | OHL | 0.000556 | 0.006695 | 0.20934 | 2400 | 2220 | 1916.4 | 2220
FLEE41 | LOVE41 | 2022 | Change | 41.095 | 0 | OHL | 0.000748 | 0.008176 | 0.23816 | 2212 | 2046.1 | 1766.282 | 2046.1
FLEE41 | LOVE41 | 2022 | Change | 41.095 | 0 | OHL | 0.000748 | 0.008176 | 0.23816 | 2212 | 2046.1 | 1766.282 | 2046.1
HARM21 | HAWP21 | 2022 | Change | 17.287 | 0 | OHL | 0.000584 | 0.007033 | 0.049126 | 1110 | 1026.75 | 886.335 | 1026.75
HATL21 | HARM21 | 2022 | Change | 13.983 | 0 | OHL | 0.000472 | 0.005702 | 0.039648 | 1093 | 1011.025 | 872.7605 | 1011.025
HATL21 | SALH21 | 2022 | Change | 7.794 | 0 | OHL | 0.000327 | 0.003353 | 0.020878 | 1382 | 1278.35 | 1103.527 | 1278.35
HAWP21 | HATL21 | 2022 | Addition | 31.443 | 0 | OHL | 0.001066 | 0.012811 | 0.089228 | 1090 | 1008.25 | 870.365 | 1008.25
HAWP21 | OFFE21 | 2022 | Change | 9.514 | 0 | OHL | 0.000379 | 0.003948 | 0.026412 | 1093 | 1011.025 | 872.7605 | 1011.025
IRON41 | OSWE41 | 2022 | Addition | 27.261 | 0 | OHL | 0.000435 | 0.005242 | 0.16393 | 3100 | 2867.5 | 2475.35 | 2867.5
KEMS41 | LOFI4A | 2022 | Change | 38.035 | 0 | OHL | 0.000721 | 0.007367 | 0.22682 | 1926 | 1781.55 | 1537.911 | 1781.55
KEMS41 | LOFI4B | 2022 | Change | 37.572 | 0 | OHL | 0.000717 | 0.007289 | 0.22372 | 1926 | 1781.55 | 1537.911 | 1781.55
LEGA41 | OSWE41 | 2022 | Addition | 34.812 | 0 | OHL | 0.000556 | 0.006695 | 0.20934 | 2000 | 1850 | 1597 | 1850
LEGA41 | OSWE41 | 2022 | Addition | 34.812 | 0 | OHL | 0.000556 | 0.006695 | 0.20934 | 2000 | 1850 | 1597 | 1850
LITT41 | LOFI4A | 2022 | Change | 8.152 | 0 | OHL | 0.000176 | 0.001632 | 0.046835 | 1389 | 1284.825 | 1109.1165 | 1284.825
LITT41 | LOFI4B | 2022 | Change | 8.152 | 0 | OHL | 0.000176 | 0.001632 | 0.046835 | 1389 | 1284.825 | 1109.1165 | 1284.825
NORT41 | OSBA41 | 2022 | Change | 83.839 | 0 | OHL | 0.001168 | 0.016114 | 0.50397 | 2780 | 2571.5 | 2219.83 | 2571.5
NORT41 | OSBA42 | 2022 | Change | 83.839 | 0 | OHL | 0.001168 | 0.016114 | 0.50397 | 2400 | 2220 | 1916.4 | 2220
OFFE21 | WBOL21 | 2022 | Change | 8.207 | 0 | OHL | 0.000327 | 0.003406 | 0.022784 | 1093 | 1011.025 | 872.7605 | 1011.025
RAYL41 | RAYL41 | 2022 | Addition | -- | -- | Series Reactor | 0 | 0.009375 | -- | 4000 | 3700 | 3194 | 3700
RAYL41 | RAYL41 | 2022 | Addition | -- | -- | Series Reactor | 0 | 0.009375 | -- | 4000 | 3700 | 3194 | 3700
SHRE4A | OSWE41 | 2022 | Addition | 12.132 | 0 | OHL | 0.000194 | 0.002333 | 0.072955 | 3100 | 2867.5 | 2475.35 | 2867.5
TILB41 | TILB4B | 2022 | Addition | 0.0589 | 0 | OHL | 1e-06 | 1.1e-05 | 0.000353 | 3102 | 2869.35 | 2476.947 | 2869.35
TILB4A | TILB41 | 2022 | Addition | 0.05808 | 0 | OHL | 1e-06 | 1.2e-05 | 0.00033 | 3102 | 2869.35 | 2476.947 | 2869.35
WBOL21 | HAWP21 | 2022 | Addition | 17.721 | 0 | OHL | 0.000705 | 0.007355 | 0.049196 | 1090 | 1008.25 | 870.365 | 1008.25
LEGA41 | SHRE4A | 2022 | Removed | 46.944 | 0 | OHL | 0.00075 | 0.009028 | 0.2823 | 2002 | 1851.85 | 1598.597 | 1851.85
SHRE4B | SHRE4A | 2022 | Removed | 0.054 | 0 | OHL | 1e-06 | 1e-05 | 0.000324 | 9999 | 9249.075 | 7984.2015 | 9249.075
HATL21 | WBOL21 | 2022 | Removed | 49.164 | 0 | OHL | 0.001929 | 0.020384 | 0.13673 | 1093 | 1011.025 | 872.7605 | 1011.025
IRON41 | LEGA41 | 2022 | Removed | 62.073 | 0 | OHL | 0.000991 | 0.011937 | 0.37327 | 2002 | 1851.85 | 1598.597 | 1851.85
CARR41 | CARR41 | 2024 | Addition | -- | -- | Series Reactor | 0 | 0.005 | -- | 2750 | 2543.75 | 2195.875 | 2543.75
CILF41 | RASS41 | 2024 | Change | 26.901 | 0 | OHL | 0.000293 | 0.004789 | 0.17393 | 2779 | 2570.575 | 2219.0315 | 2570.575
HIKP41 | HIKP42 | 2024 | Addition | -- | -- | Series Reactor | 0 | 0.02 | -- | 2000 | 1850 | 1597 | 1850
HIKP41 | PURI41 | 2024 | Addition | 15 | 0 | OHL | 0.000234 | 0.002878 | 0.090015 | 3100 | 2867.5 | 2475.35 | 2867.5
HIKP41 | TAUN42 | 2024 | Addition | 27.657 | 0 | OHL | 0.000503 | 0.005503 | 0.16028 | 2210 | 2044.25 | 1764.685 | 2044.25
HIKP42 | PURI41 | 2024 | Addition | 15 | 0 | OHL | 0.000234 | 0.002878 | 0.090015 | 3100 | 2867.5 | 2475.35 | 2867.5
HIKP42 | TAUN41 | 2024 | Addition | 27.644 | 0 | OHL | 0.000503 | 0.0055 | 0.16021 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | HIKP41 | 2024 | Addition | 1 | 0 | OHL | 1.8e-05 | 0.000199 | 0.005795 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | HIKP42 | 2024 | Addition | 1 | 0 | OHL | 1.8e-05 | 0.000199 | 0.005795 | 2210 | 2044.25 | 1764.685 | 2044.25
HINP41 | SAFO41 | 2024 | Addition | 24.54 | 8.15 | Composite | 0.000376 | 0.005627 | 2.0318 | 3070 | 2839.75 | 2451.395 | 2839.75
HINP41 | SEAB41 | 2024 | Addition | 53.385 | 8.15 | Composite | 0.000697 | 0.011063 | 2.2092 | 3100 | 2867.5 | 2475.35 | 2867.5
INDQ41 | LAND41 | 2024 | Change | 49.565 | 0 | OHL | 0.000946 | 0.009615 | 0.29513 | 1930 | 1785.25 | 1541.105 | 1785.25
INDQ41 | LAND42 | 2024 | Change | 49.565 | 0 | OHL | 0.000946 | 0.009615 | 0.29513 | 1930 | 1785.25 | 1541.105 | 1785.25
MELK41 | PURI41 | 2024 | Addition | 78.5 | 0 | OHL | 0.001223 | 0.015103 | 0.46977 | 3100 | 2867.5 | 2475.35 | 2867.5
MELK41 | PURI41 | 2024 | Addition | 78.5 | 0 | OHL | 0.001223 | 0.015103 | 0.46977 | 3100 | 2867.5 | 2475.35 | 2867.5
PEMB41 | SWAN41 | 2024 | Addition | 83.975 | 0 | OHL | 0.000911 | 0.014606 | 0.55357 | 2780 | 2571.5 | 2219.83 | 2571.5
PURI41 | BRIW41 | 2024 | Addition | 4 | 0 | OHL | 6.2e-05 | 0.000767 | 0.024004 | 3100 | 2867.5 | 2475.35 | 2867.5
PURI41 | BRIW41 | 2024 | Addition | 4 | 0 | OHL | 6.2e-05 | 0.000767 | 0.024004 | 3100 | 2867.5 | 2475.35 | 2867.5
SAFO41 | SEAB41 | 2024 | Addition | 28.845 | 0 | OHL | 0.000322 | 0.005436 | 0.17739 | 3070 | 2839.75 | 2451.395 | 2839.75
SWAN41 | WALH41 | 2024 | Addition | 133.452 | 5.468 | parallel Composite | 0.001457 | 0.023405 | 1.5186 | 2780 | 2571.5 | 2219.83 | 2571.5
WYLF41 | PENT41 | 2024 | Addition | 33.74 | 3 | parallel Composite | 0.000446 | 0.006576 | 0.90441 | 2780 | 2571.5 | 2219.83 | 2571.5
WYLF41 | PENT41 | 2024 | Addition | 33.74 | 3 | parallel Composite | 0.000446 | 0.006576 | 0.90441 | 2780 | 2571.5 | 2219.83 | 2571.5
PEMB41 | WALH41 | 2024 | Removed | 217.727 | 5.468 | Composite | 0.002373 | 0.038184 | 2.0704 | 2779 | 2570.575 | 2219.0315 | 2570.575
HINP22 | BRWA2A | 2024 | Removed | 17.867 | 0.61 | Composite | 0.000827 | 0.007732 | 0.11478 | 767 | 709.475 | 612.4495 | 709.475
HINP41 | TAUN41 | 2024 | Removed | 26.644 | 0 | OHL | 0.000485 | 0.005301 | 0.15441 | 2212 | 2046.1 | 1766.282 | 2046.1
HINP41 | MELK41 | 2024 | Removed | 86.448 | 0 | OHL | 0.001573 | 0.0172 | 0.501 | 2009 | 1858.325 | 1604.1865 | 1858.325
HINP21 | BRWA2B | 2024 | Removed | 17.867 | 0.68 | Composite | 0.000828 | 0.007752 | 0.12239 | 762 | 704.85 | 608.457 | 704.85
SWAN42 | SWAN4A | 2024 | Removed | 0.64 | 0 | OHL | 1.4e-05 | 0.000128 | 0.003677 | 1389 | 1284.825 | 1109.1165 | 1284.825
HINP41 | TAUN42 | 2024 | Removed | 26.657 | 0 | OHL | 0.000485 | 0.005304 | 0.15448 | 2212 | 2046.1 | 1766.282 | 2046.1
HINP41 | MELK41 | 2024 | Removed | 86.439 | 0 | OHL | 0.001572 | 0.017198 | 0.50095 | 2009 | 1858.325 | 1604.1865 | 1858.325
BRFO41 | PELH41 | 2027 | Change | 69.301 | 0 | OHL | 0.0007 | 0.011997 | 0.4602 | 2780 | 2571.5 | 2219.83 | 2571.5
HAWP41 | NORT41 | 2027 | Change | 30.157 | 0 | OHL | 0.000327 | 0.005245 | 0.1988 | 2550 | 2358.75 | 2036.175 | 2358.75
KINB4J | KINC4A | 2027 | Addition | 10.5 | 0 | OHL | 0.000227 | 0.002102 | 0.060323 | 1590 | 1470.75 | 1269.615 | 1470.75
KINB4K | KINC4S | 2027 | Addition | 10.15 | 0 | OHL | 0.000219 | 0.002032 | 0.058313 | 1590 | 1470.75 | 1269.615 | 1470.75
NORT41 | HAWP41 | 2027 | Addition | 30.157 | 0 | OHL | 0.000327 | 0.005245 | 0.1988 | 2550 | 2358.75 | 2036.175 | 2358.75
NORT41 | OSBA41 | 2027 | Change | 83.839 | 0 | OHL | 0.001309 | 0.016144 | 0.50097 | 3120 | 2886 | 2491.32 | 2886
NORT41 | OSBA42 | 2027 | Change | 83.839 | 0 | OHL | 0.001309 | 0.016144 | 0.50097 | 3120 | 2886 | 2491.32 | 2886
NECT4A | KINL41 | 2027 | Addition | 30.347 | 0 | OHL | 0.000269 | 0.005209 | 0.20404 | 2520 | 2331 | 2012.22 | 2331
WALP41 | KINL41 | 2027 | Addition | 44.319 | 0 | OHL | 0.000393 | 0.007609 | 0.29795 | 2520 | 2331 | 2012.22 | 2331
SJOW21 | TOTT22 | 2027 | Removed | 0 | 16.508 | Cable | 0.000297 | 0.003632 | 1.7944 | 868 | 802.9 | 693.098 | 802.9
NECT4A | WALP41 | 2027 | Removed | 41.619 | 0 | OHL | 0.000369 | 0.007148 | 0.27974 | 3326 | 3076.55 | 2655.811 | 3076.55
HAWP21 | NORT21 | 2027 | Removed | 30.238 | 0.459 | Composite | 0.000719 | 0.011367 | 0.14237 | 908 | 839.9 | 725.038 | 839.9
SJOW21 | TOTT21 | 2027 | Removed | 0 | 16.368 | Cable | 0.000295 | 0.003601 | 1.7792 | 868 | 802.9 | 693.098 | 802.9

## B-2-2d
Table B.2.2d - Indicative Offshore Transmission Circuit Changes 2019/20 to 2027/28 | [13 empty] | Back To Menu
OFTO | Site | Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage (kV)
- | Dogger Bank | DOGG41 | CREB41 | 2023 | Addition | 1.5 | 0 | OHL | 0 | 0.0001 | 0 | 2500 | 400
- | Dogger Bank | DOGG41 | CREB41 | 2023 | Addition | 1.5 | 0 | OHL | 0 | 0.0001 | 0 | 2500 | 400
- | Dogger Bank | DOGG4 | LACK41 | 2026 | Addition | 0 | 0.5 | Cable | 0 | 0.0001 | 0 | 2500 | 400
- | Dogger Bank | DOGG4 | LACK41 | 2026 | Addition | 0 | 0.5 | Cable | 0 | 0.0001 | 0 | 2500 | 400
| East Anglia one | EAAW41 | BRFO41 | 2019 | Addition | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
| East Anglia one | EAAW41 | BRFO41 | 2019 | Addition | 0 | 0.47 | Cable | 0.0012052 | 0.0060172 | 3.8508 | 369 | 400
| East Anglia one | EAAW2 | EAAW2 | 2019 | Addition | 0 | 36.9 | Cable | 0.13748 | 1.2511 | 0 | 370 | 220
| East Anglia one | EAAW2 | EAAW2 | 2019 | Addition | 0 | 36.9 | Cable | 0.13748 | 1.2511 | 0 | 370 | 220
| East Anglia one | EANO2 | EAAW2 | 2019 | Addition | 0 | 85 | Cable | 0.0098975 | 0.034332 | 5.1671 | 344 | 220
| East Anglia one | EANO2 | EAAW2 | 2019 | Addition | 0 | 85 | Cable | 0.0098975 | 0.034332 | 5.1671 | 344 | 220
| Hornsea P1 | HOWW2A | HOWR2A | 2019 | Addition | 0 | 66.2 | Cable | 0.4924 | 1.6413 | 175.1469 | - | 220
| Hornsea P2 | HOWW2B | HOWR2B | 2019 | Addition | 0 | 72.2 | Cable | 0.47736 | 1.7155 | 203.0972 | - | 220
| Hornsea P3 | HOWW2C | HOWR2C | 2019 | Addition | 0 | 85 | Cable | 0.63223 | 2.1074 | 224.8866 | - | 220
| Hornsea P1 | HOWR2A | HOWA2 | 2019 | Addition | 0 | 67.6 | Cable | 0.50281 | 1.676 | 178.8509 | - | 220
| Hornsea P2 | HOWR2B | HOWA2 | 2019 | Addition | 0 | 67.4 | Cable | 0.51525 | 1.6014 | 190.6199 | - | 220
| Hornsea P3 | HOWR2C | HOWA2 | 2019 | Addition | 0 | 67.2 | Cable | 0.49984 | 1.6661 | 177.7927 | - | 220
| Hornsea P1 | HOWA2 | HOWA4 | 2019 | Addition | 0 | 37.503 | Cable | 0.18103 | 1.594 | 113.2774 | - | 220
| Hornsea P2 | HOWA2 | HOWA4 | 2019 | Addition | 0 | 37.503 | Cable | 0.18103 | 1.594 | 113.2774 | - | 220
| Hornsea P3 | HOWA2 | HOWA4 | 2019 | Addition | 0 | 37.503 | Cable | 0.18103 | 1.594 | 113.2774 | - | 220
| Hornsea P1 | HOWW2A | HOWW2B | 2019 | Addition | 0 | 12.3 | Cable | 0.15756 | 0.30496 | 34.5997 | - | 220
| Hornsea P1 | HOWW2B | HOWW2C | 2019 | Addition | 0 | 13.9 | Cable | 0.17806 | 0.34463 | 39.1004 | - | 220

## B-3-1a
Table B.3.1a - SHE Transmission Transformers 2018/19 | [5 empty] | Back To Menu
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABBA1- | ABBA6- | 0.795 | 15.9 | 0 | 120
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
ACHR1R | ACHR3- | 0.36 | 18 | 0 | 90
AIGA1Q | AIGA5- | 1.76 | 44.89 | 0 | 22.5
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.615 | 17.8201 | -0.026 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU3- | 1.04 | 27.7301 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.7301 | 0 | 45
BEAU2J | BEAU1J | 0.6786 | 12.2312 | 0 | 120
BEAU2J | BEAU1J | 0.6786 | 12.1644 | 0 | 120
BEAU2K | BEAU1K | 0.6786 | 12.1895 | 0 | 120
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.001 | 1200
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.001 | 1200
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 0.1486 | 5.3035 | -0.002 | 360
BLHI2K | BLHI1K | 0.1506 | 5.3034 | -0.002 | 360
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2L | 0.0252 | 1.1997 | -0.0005 | 1200
BLHI4- | BLHI2M | 0.0253 | 1.2081 | -0.0005 | 1200
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRCW2J | BRCW3- | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 0.42 | 20 | 0 | 120
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 38.9998 | 0 | 30
BROR1- | BROR3- | 0.763 | 25.144 | 0 | 45
BUMU1Q | BUMU3- | 0.366 | 25.37 | -0.034 | 90
BUMU1R | BUMU3- | 0.376 | 25.42 | -0.035 | 90
CAAD1Q | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1Q | CAAD3J | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1R | CAAD3J | 0.5 | 25 | 0 | 90
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120
CASS1Q | CASS3- | 1.518 | 39.8711 | 0 | 30
CEAN1Q | CEAN5- | 1.182 | 36.714 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAC1Q | CLAC5J | 0.75 | 25 | 0 | 60
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
CLUN1Q | CLUN5J | 0.71 | 19.53 | 0 | 60
CLUN1R | CLUN5K | 0.71 | 19.55 | 0 | 60
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90
CONN2J | CONN1J | 0.143 | 5.3036 | -0.002 | 360
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
CORI1J | CORI3J | 8.3 | 27.5001 | 0 | 60
COUA1Q | COUA3- | 0.2143 | 25.0741 | -0.0067 | 120
COUA1R | COUA3- | 0.2151 | 25.1241 | -0.0092 | 120
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
CRSS1J | COUW31 | 0.3629 | 18.0297 | -0.0123 | 90
CRSS1J | CRSS1Q | 0.0582 | 2.145 | 0 | 240
CRSS1K | CRSS1R | 0.0582 | 2.1492 | 0 | 240
CRSS2A | CRSS1J | 0.2466 | 9.0008 | -0.003 | 240
CRSS2B | CRSS1K | 0.2459 | 9.0175 | -0.004 | 240
CULL1Q | CULL5- | 1.46 | 37.6 | 0 | 25
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DEAN1Q | DEAN5- | 1.01 | 25.1 | 0 | 40
DORE11 | DORE31 | 0.21 | 9.89 | 0 | 120
DORE12 | DORE32 | 0.21 | 9.89 | 0 | 120
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DOUN2- | DOUN1- | 0.2112 | 7.7054 | -0.004 | 240
DOUN2- | DOUN1- | 0.2237 | 7.9135 | -0.004 | 240
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.617 | 17.6501 | -0.029 | 60
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120
DYCE1Q | DYCE3- | 0.9463 | 26.6499 | -0.4258 | 60
DYCE1R | DYCE3- | 0.9517 | 26.7164 | -0.4078 | 60
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1J | ERRO1A | 0.04 | 1.942 | 0 | 240
ERRO1J | ERRO1T | 0.068 | 3.73 | 0 | 150
ERRO1J | ERRO5L | 0.72 | 26.6 | 0 | 60
ERRO1K | ERRO1B | 0.04 | 1.942 | 0 | 240
ERRO1K | ERRO5J | 0.72 | 26.6 | 0 | 60
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FARI2J | FARI1J | 0.4989 | 8.2933 | -0.038 | 120
FARI2K | FARI1K | 0.4955 | 8.3186 | -0.038 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1Q | FAUG3- | 2.23 | 64.33 | 0 | 15
FAUG2J | FAUG1- | 0.2606 | 7.7039 | -0.003 | 240
FAUG2K | FAUG1- | 0.2629 | 7.7038 | -0.004 | 240
FAUG4- | FAUG1- | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 0.3185 | 8.4523 | -0.013 | 240
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FETT2R | FETT1- | 0.217 | 4.2737 | -0.006 | 240
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FINL1Q | FINL5- | 0.96 | 27.11 | 0 | 45
FOYE2J | FOYE0J | 0.17 | 8.17 | 0 | 165
FOYE2J | FOYE0K | 0.18 | 7.99 | 0 | 165
FRAS1Q | FRAS3- | 0.642 | 26.9039 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.9039 | 0 | 45
FWIL1Q | FWIL3- | 0.499 | 24.995 | 0 | 120
FWIL1R | FWIL3- | 0.499 | 24.995 | 0 | 120
FYRI2J | FYRI1J | 0.0967 | 3.8863 | -0.003 | 480
FYRI2K | FYRI1K | 0.0971 | 3.8738 | -0.002 | 480
GLDO1G | GLDO8- | 0.206 | 10.681 | 0 | 120
GLEN1Q | GLEN5- | 0.55 | 21.94 | 0 | 70
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90
INGA1Q | INGA5- | 1.162 | 25.006 | 0 | 25
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
INVB2A | INVR1- | 0.2217 | 4.3026 | -0.007 | 240
INVB2B | INVR1- | 0.2164 | 4.257 | -0.007 | 240
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEITH3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEITH3A | 0.499 | 24.995 | 0 | 90
KEIT2Q | KEIT1- | 0.2735 | 8.6123 | -0.005 | 240
KEIT2R | KEIT1- | 0.3328 | 8.9105 | -0.0389 | 240
KIIN1- | KIIN3- | 0.772 | 24.8769 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.5211 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.7801 | 0 | 45
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT1- | 0.3771 | 10.1929 | -0.018 | 240
KINT2K | KINT1- | 0.3751 | 10.2314 | -0.0147 | 240
KINT2K | KINT1- | 0.6786 | 12.1477 | 0 | 120
KIOR1Q | KIOR5- | 1.78 | 45.42 | 0 | 22.5
KNOC2J | KNOC1J | 0.2216 | 4.311 | -0.0076 | 240
KNOC2K | KNOC1J | 0.2205 | 4.3319 | -0.006 | 240
LAIR1Q | LAIR3- | 0.425 | 24.674 | 0 | 90
LOCB2J | LOCB1J | 0.2181 | 8.1262 | -0.004 | 240
LOCB2K | LOCB1K | 0.22 | 8.197 | -0.005 | 240
LOCH1- | LOCH5J | 1.93 | 38.52 | 0 | 25
LOCH1- | LOCH5K | 1.93 | 38.2 | 0 | 25
LUIC1Q | LUIC5J | 0.763 | 37.548 | 0 | 45
LUIC1R | LUIC5K | 0.7668 | 37.548 | 0 | 45
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.429 | 25.741 | 0 | 90
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MELG4J | MELG1J | 0.108 | 3.957 | -0.003 | 480
MILC1R | MILC3- | 0.78 | 24.8299 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.1301 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MOSS1Q | MOSS5- | 1.192 | 36.847 | 0 | 30
MOSS1R | MOSS5- | 1.2267 | 36.913 | 0 | 30
MYBS1S | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1S | MYBS3M | 0.2645 | 24.6069 | -0.024 | 120
MYBS1T | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3N | 0.2578 | 24.757 | -0.024 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6001 | 0 | 60
NANT1Q | NANT5- | 1.47 | 56.67 | 0 | 30
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
ORRI1R | ORRI5- | 2.17 | 48.75 | 0 | 20
PEHE2S | PEHE0J | 0.02 | 1.93 | 0 | 776
PEHE2T | PEHE0K | 0.02 | 1.94 | 0 | 776
PEHE2U | PEHE0L | 0.097 | 4.8 | 0 | 313
PEHE2V | PEHE0M | 0.097 | 4.8 | 0 | 313
PEHE2W | PEHE0N | 0.097 | 4.8 | 0 | 313
PEHE1- | PEHS5- | 2.58 | 42.33 | 0 | 15
PEHE2Q | PEHE1- | 0.4842 | 9.9549 | -0.0178 | 240
PEHE2R | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240
PEHERSV1 | PEHE1- | 0.2649 | 9.2254 | -0.005 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.3999 | 0 | 45
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PERS2Q | PERS1Q | 0.3363 | 8.9062 | -0.0412 | 240
PERS2R | PERS1R | 0.3341 | 8.8645 | -0.0419 | 240
PORA1Q | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 1.803 | 29.812 | 0 | 30
QUOI1- | QUOI5- | 1.34 | 33.13 | 0 | 30
RANN1Q | RANN3Q | 0.43 | 24.66 | 0 | 90
RANN1R | RANN3Q | 0.43 | 24.66 | 0 | 90
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
SFEG1Q | SFEG5- | 2.28 | 93.87 | 0 | 30
SFEG1R | SFEG5- | 2.28 | 92.8 | 0 | 30
SFEM1Q | SFEM5J | 1.8 | 41.19 | 0 | 27
SFEM1R | SFEM5K | 1.8 | 41.19 | 0 | 27
SFIL1Q | SFIL5- | 1.99 | 39.48 | 0 | 25
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
SHIN1- | SHIN5- | 1.4823 | 80.16 | 0 | 40
SLOY1L | SLOY5L | 0.79 | 23.08 | 0 | 50
SLOY1M | SLOY5M | 0.79 | 22.9 | 0 | 50
SLOY1N | SLOY5N | 0.79 | 22.98 | 0 | 50
SLOY1P | SLOY5P | 0.8 | 23.2 | 0 | 50
SPIT2J | SPIT1J | 0.218 | 8.185 | -0.004 | 240
SPIT2J | SPIT1J | 0.218 | 8.23 | -0.004 | 240
SPIT2K | SPIT1K | 0.131 | 4.99 | -0.003 | 360
SPIT2K | SPIT1M | 0.129 | 4.99 | -0.003 | 360
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
STRL1- | STRL3P | 0.2 | 17.74 | -0.01 | 120
STRL1- | STRL3Q | 0.2 | 17.65 | -0.01 | 120
STRL1- | STRL3R | 0.2 | 17.67 | -0.01 | 120
STRW12 | STRW31 | 0.05 | 18 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.5298 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.7869 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.7869 | 0 | 90
TEAL2J | TEAL1- | 0.3619 | 10.1602 | -0.0118 | 180
TEAL2K | TEAL1- | 0.2564 | 11.7305 | -0.0131 | 180
TEAL2K | TEAL1- | 0.5506 | 11.8761 | 0 | 180
THUS1J | THUS3- | 0.2621 | 24.6736 | -0.022 | 120
THUS1K | THUS3- | 0.2614 | 24.7403 | -0.02 | 120
THUS2J | THUS1J | 0.0985 | 3.9363 | -0.003 | 480
THUS2K | THUS1K | 0.1 | 3.9362 | -0.002 | 480
TUMB1Q | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMB1R | TUMB5- | 0.499 | 24.995 | 0 | 21
TUMM2J | TUMM1J | 0.259 | 7.7457 | -0.004 | 240
TUMM2K | TUMM1K | 0.2595 | 7.829 | -0.004 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.2399 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
Table B.3.1b - SPT Transformers 2018/19 | [5 empty] | Back To Menu
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
BAGA1Q | BAGA0J | 0.5559 | 33.3287 | 0 | 18
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA0K | 0.5559 | 33.3287 | 0 | 18
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1Q | MARM0J | 0.933 | 56.0122 | 0 | 10
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BERW1R | MARM0K | 0.933 | 56.0122 | 0 | 10
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN0J | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN0K | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN0L | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY0J | 2.24 | 57.9567 | -0.0633 | 10
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY0K | 2.2 | 57.9583 | -0.0625 | 10
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3- | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3- | 0.4868 | 20.6609 | -0.2478 | 120
CLYM2- | CLYM3- | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3- | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1- | 0.1216 | 9.6242 | -0.0793 | 240
COAL4- | COAL1- | 0.1258 | 9.7909 | -0.0801 | 240
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1718 | 8.665 | -0.0204 | 120
COYL2- | COYL1- | 0.3396 | 12.8288 | -0.2375 | 120
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR1- | CRYR31 | 0.29514 | 16.664 | -0.20024 | 120
CRYR1- | CRYR32 | 0.29514 | 16.664 | -0.20024 | 120
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR1B | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1A | 0.086068 | 8.4495 | -0.072954 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM0J | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM0K | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 160
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 160
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3- | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3- | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
DUNO1Q | DUNO3- | 2 | 24.49 | 0 | 45
DUNO1R | DUNO3- | 2 | 24.5801 | 0 | 45
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCF1J | ECCF0J | 1.4773 | 33.3006 | -0.0896 | 15
ECCF1K | ECCF0K | 0.4481 | 26.8629 | 0 | 18
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EKIL2S | EKIL3- | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3- | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3- | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3- | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA4- | ELVA0J | 0.1612 | 34.0696 | -0.0029 | 80
ELVA4- | ELVA0K | 0.1613 | 34.0696 | -0.0101 | 80
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 1.7778 | 33.4528 | 0 | 30
ERSK1R | ERSK3- | 0.3119 | 21.8311 | 0 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FALL4- | FALL3A | 0.25638 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.25638 | 16.6647 | 0 | 120
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 0.3635 | 25.4418 | 0 | 90
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3- | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3- | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60
GORG1R | GORG3- | 0.7875 | 26.9885 | -0.0062 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.3876 | 19.4628 | -0.0275 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.9806 | 20.7268 | -1.3737 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1- | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1- | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
INWI1Q | INWI0J | 0.917 | 55.0024 | 0 | 10
INWI1R | INWI0K | 0.917 | 55.0024 | 0 | 10
JOHN1Q | JOHN3- | 0.9461 | 21.8128 | 0 | 60
JOHN1R | JOHN3- | 0.9461 | 21.8128 | 0 | 60
KAIM2- | KAIM3A | 0.4819 | 20.2443 | -0.2454 | 120
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILT2Q | KILT3- | 0.4927 | 18.4934 | -0.1756 | 120
KILT2R | KILT3- | 0.4976 | 18.4933 | -0.1775 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KYPE1- | KYPE3- | 0.19221 | 14.207 | -0.011304 | 120
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MIDM1- | MIDM3- | 0.47222 | 13.325 | 0 | 60
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 38
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 38
MOSM1- | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1- | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1- | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1- | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0312 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0312 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0312 | 240
NECU2- | NECU1Q | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1R | 0.1476 | 8.7488 | -0.1299 | 240
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB0J | 0.5559 | 33.3287 | 0 | 18
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB0K | 0.5559 | 33.3287 | 0 | 18
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 60
REDH1- | REDH3- | 1.41 | 20.7522 | 0 | 90
SACO1Q | SACO0J | 0.933 | 56.0022 | 0 | 10
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO0K | 0.933 | 56.0022 | 0 | 10
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SANX1Q | SANX0J | 0.558 | 33.4787 | 0 | 18
SANX1Q | SANX3- | 0.8844 | 21.5485 | -0.309 | 60
SANX1R | SANX0K | 0.558 | 33.4787 | 0 | 18
SANX1R | SANX3- | 0.8767 | 21.2319 | -0.3087 | 60
SHRU2Q | SHRU3- | 0.4926 | 19.9939 | -0.2739 | 120
SHRU2R | SHRU3- | 0.4656 | 19.9946 | -0.3204 | 120
SIGH2Q | SIGH3A | 0.2282 | 13.7759 | -0.032 | 180
SIGH2R | SIGH3A | 0.2141 | 13.765 | -0.0372 | 180
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4722 | 18.7441 | -0.1542 | 120
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 120
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1- | STLE0J | 0.958 | 57.502 | 0 | 10
STLE1- | STLE0K | 0.958 | 57.502 | 0 | 10
STLE1- | STLE3S | 0.4217 | 25.741 | -0.028 | 90
STLE1- | STLE3S | 0.4235 | 25.6743 | -0.0254 | 90
TELR1Q | TELR3- | 0.9575 | 20.6778 | 0 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG1R | 0.0267 | 1.3331 | 0 | 90
TONG1- | TONG3- | 0.31194 | 21.8311 | 0 | 60
TONG1- | TONG3- | 0.31194 | 21.8311 | 0 | 60
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30
TONG1Q | TONG1R | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WESE1- | AIKE3A | 0.56667 | 13.2333 | 0 | 90
WESE1- | AIKE3B | 0.56667 | 13.2333 | 0 | 90
WFIE1A | WFIE3- | 0.9889 | 20.4928 | 0 | 60
WFIE1B | WFIE3- | 0.9528 | 20.5613 | 0 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH0J | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH0K | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH3- | 0.4821 | 24.1785 | -0.226 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.1517 | 8.707 | -0.1161 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.231 | 12.258 | 0 | 120
WLEX2- | WLEX3B | 0.231 | 12.275 | 0 | 120
WLEX2- | WLEX3C | 0.232 | 12.292 | 0 | 120

## B-3-1c
Table B.3.1c - NGET Transformers 2018/19 | [5 empty] | Back To Menu
Node 1 | Node 2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA41 | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264
ABHA42 | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275
ABTH21 | ABTH11 | 0.0977 | 8.1994 | -1.7127 | 212
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 279
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALVE41 | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275
AMEM41 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255
AMEM42 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 275
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARK11 | 0.1646 | 8.0383 | -0.1808 | 211
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 256
BEDD21 | BEDD11 | 0.1067 | 8.0868 | -0.034 | 240
BEDD21 | BEDD1B | 0.2264 | 12.2479 | -0.6062 | 126
BEDD22 | BEDD11 | 0.1067 | 8.0868 | -0.034 | 240
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD23 | BEDD1A | 0.2264 | 12.2479 | -0.6062 | 126
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 867
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 273
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 278
BICF42 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 274
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 131
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 131
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209
BLYT4A | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BLYT4B | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BODE4D | GWYN11 | 0.0547 | 3.513 | -0.8921 | 320
BODE4C | GWYN11 | 0.0547 | 3.513 | -0.8921 | 320
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 276
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 277
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 278
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 278
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 312
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO11 | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 271
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 272
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1096
BRLE41 | BRLE11 | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE11 | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270
BRWA2A | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BURB41 | BURB21 | 0.08 | 5.8995 | -0.3558 | 200
BURB41 | BURB21 | 0.08 | 5.8995 | -0.3558 | 200
BURW41 | BURW11 | 0.1372 | 8.0197 | -0.1238 | 240
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 265
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST4A | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST4B | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT13 | 0.1509 | 8.2849 | -0.3279 | 264
CANT41 | CANT14 | 0.1658 | 8.426 | -0.2939 | 264
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 180
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 279
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE41 | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886
CAPE42 | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARR21 | CARR11 | 0.2847 | 12.2467 | -1.4346 | 120
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272
CARR42 | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CARR43 | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 273
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 273
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 278
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254
CHSI21 | CHSI1A | 0.2264 | 12.2479 | -0.6062 | 126
CHSI21 | CHSI1B | 0.2264 | 12.2479 | -0.6062 | 126
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 255
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 249
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 251
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 278
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 251
CILF41 | CILF21 | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF22 | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR12 | 0.0997 | 8.0088 | -0.093 | 266
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259
CONQ41 | CONQ12 | 0.1057 | 7.9352 | -0.339 | 240
CONQ42 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261
CONQ42 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 266
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 279
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CULJ41 | CULJ31 | 0.069 | 25 | 0 | 90
CULJ41 | CULJ32 | 0.069 | 25 | 0 | 90
CULJ41 | CULJ33 | 0.069 | 25 | 0 | 90
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240
DRAK41 | DRAK2A | 0.0178 | 1.5995 | -1.2431 | 849
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EASO41 | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
EASO41 | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 272
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279
ELST21 | ELST11 | 0.1954 | 8.0796 | -0.2295 | 189
ELST21 | ELST11 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST12 | 0.1985 | 8.1167 | -0.4624 | 189
ELST22 | ELST13 | 0.1923 | 8.081 | -1.4418 | 189
ELST22 | ELST13 | 0.1031 | 8.1045 | -0.0494 | 212
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1100
ELST42 | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 271
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139
FECK41 | FECK21 | 0.0211 | 1.6463 | -14.2471 | 1114
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278
FERR2D | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR2D | FERR61 | 0.237 | 10.8633 | -0.263 | 204
FERR2E | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR2E | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR41 | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR41 | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113
FIDF21 | FIDF12 | 0.1594 | 8.6081 | -0.2215 | 261
FIDF21 | FIDF13 | 0.2847 | 12.2467 | -1.4346 | 120
FIDF22 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271
FIDF23 | FIDF11 | 0.2847 | 12.2467 | -1.4346 | 120
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 240
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 300
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLIB41 | FLIB41 | 0 | 8 | 0 | 3000
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 146
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD11 | 0.054 | 4.8906 | -0.1253 | 499
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063
FROD41 | WEAV71 | 0.3209 | 20.5475 | -0.1224 | 80
FROD41 | WEAV71 | 0.3209 | 20.5475 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GREN41 | GREN11 | 0.1035 | 7.8472 | -0.0758 | 240
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268
HACK21 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK22 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK21 | 0.0182 | 1.5763 | -0.0904 | 1152
HACK41 | HACK22 | 0.0182 | 1.5763 | -0.0904 | 1155
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147
HAMH41 | LEMR12 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278
HAMH41 | LEMR12 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 137
HARK22 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK22 | 0.0292 | 2.402 | -0.2732 | 573
HARK41 | HARK21 | 0.0321 | 2.4344 | -0.0528 | 555
HARK41 | HARK22 | 0.0376 | 2.3797 | -3.9009 | 547
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 191
HAWP41 | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1000
HEDO21 | HEDN11 | 0.133 | 8.0758 | -0.2287 | 218
HEDO21 | HEDN11 | 0.133 | 8.0758 | -0.2287 | 218
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 240
HIBU41 | HIBU11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | HIBU11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | HIBU11 | 0.1264 | 8.4534 | -0.357 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2150
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 539
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 507
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 279
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 279
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 180
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 240
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 278
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 279
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 265
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 125
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER22 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 180
IVER41 | IVER21 | 0.0326 | 2.3798 | -3.9003 | 1135
IVER42 | IVER22 | 0.0326 | 2.3798 | -3.9003 | 500
IVER41 | IVER23 | 0.0132 | 1.4627 | -2.0624 | 500
IVER42 | IVER21 | 0.0176 | 1.5828 | -0.1018 | 595
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 256
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 276
KEAD41 | KEAD4A | 0.0002 | 0.4178 | 0 | 2210
KEAD41 | KEAD4B | 0.0002 | 0.2873 | 0 | 2210
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 257
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEMS41 | KEMS11 | 0.1621 | 8.0984 | -0.0747 | 236
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 240
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279
KIBY21 | KIBY12 | 0.1221 | 8.0467 | -0.0391 | 279
KIBY22 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261
KIBY22 | KIBY12 | 0.1681 | 8.3396 | -1.4878 | 211
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 269
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 278
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 279
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264
KIRK21 | KIRK11 | 0.1575 | 8.0988 | -0.027 | 266
KIRK2A | KIRK21 | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | GRTO61 | 0.1747 | 11.0542 | -0.6256 | 133
LACK21 | GRTO61 | 0.1747 | 11.0542 | -0.6256 | 133
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128
LACK41 | LACK21 | 0.0174 | 1.598 | -0.1503 | 1154
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1100
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 240
LEGA41 | LEGA4A | 0.001 | 0.35 | 0 | 2000
LEGA41 | LEGA4B | 0.001 | 0.35 | 0 | 2000
LEIS4A | LEIS11 | 0.103 | 7.9231 | -0.0638 | 240
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 253
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 267
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 240
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 240
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 272
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269
LOVE41 | LOVE4A | 0.3995 | 7.99 | -0.1549 | 170
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 555
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 240
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 279
MELK41 | MELK11 | 0.1041 | 7.8535 | -0.0851 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK21 | 0 | 1.692 | 0 | 886
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MILH21 | MILH11 | 0.179 | 8.3648 | -4.7616 | 211
MILH21 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH22 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH22 | MILH11 | 0.179 | 8.3648 | -4.7616 | 199
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 240
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 263
MITY41 | MITY12 | 0.137 | 7.9818 | -0.1471 | 240
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 263
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1138
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 272
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 269
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 270
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 131
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 130
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 886
NEWX21 | NEWX11 | 0.1053 | 8.0451 | -0.0277 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2B | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 187
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278
NINF41 | NINF12 | 0.1509 | 7.9378 | -0.9251 | 253
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273
NORL21 | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORL22 | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORM41 | NORW11 | 0.1307 | 7.9515 | -0.1098 | 240
NORM41 | NORW12 | 0.1264 | 8.4534 | -0.357 | 277
NORM41 | NORW13 | 0.1509 | 7.9378 | -0.9251 | 253
NORM41 | NORW14 | 0.1118 | 8.3874 | -0.0906 | 278
NORM41 | NORW15 | 0.1509 | 7.9378 | -0.9251 | 267
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 280
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 253
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 252
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 262
OCKH21 | OCKH11 | 0.179 | 8.3648 | -4.7616 | 202
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH2A | OCKH21 | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 100
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 115
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB4A | OLDB21 | 0.0146 | 1.609 | -1.8746 | 1115
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 240
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 278
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN41 | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063
PENN42 | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 257
PEWO21 | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO22 | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278
PEWO41 | PEWO21 | 0.021 | 1.669 | -12.6082 | 876
PEWO41 | PEWO21 | 0.0175 | 1.5879 | -4.0069 | 1139
PEWO41 | PEWO22 | 0.0178 | 1.5995 | -1.2431 | 845
PEWO41 | PEWO22 | 0.0189 | 1.6132 | -0.7226 | 1129
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS31 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS32 | 0.4975 | 20.4439 | -0.2606 | 110
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 110
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 120
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 279
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273
RATS41 | RATS11 | 0.1373 | 8.1976 | -0.1719 | 278
RATS41 | RATS12 | 0.103 | 7.9231 | -0.0638 | 262
RATS41 | RATS12 | 0.1046 | 7.8493 | -0.0881 | 240
RATS42 | RATS11 | 0.1278 | 8.0061 | -0.2276 | 277
RATS42 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125
RAYL41 | RAYM11 | 0.1759 | 7.9134 | -0.267 | 240
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240
RAYL41 | RAYM12 | 0.1303 | 7.8698 | -0.4285 | 278
RAYL41 | RAYM12 | 0.1309 | 7.8656 | -0.4549 | 262
REBR21 | REBR32 | 0.665 | 28.1922 | -0.151 | 112
REBR22 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132
REBR22 | REBR31 | 0.665 | 28.1922 | -0.151 | 111
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH12 | 0.2847 | 12.2467 | -1.4346 | 140
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RYEH4C | RYEH13 | 0.1326 | 8.774 | -0.7141 | 260
RYEH4D | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260
RYEH41 | RYEH12 | 0.1372 | 8.0197 | -0.1238 | 253
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.103 | 7.9231 | -0.0638 | 256
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1307 | 7.9515 | -0.1098 | 276
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273
SELL41 | SELL12 | 0.103 | 7.9231 | -0.0638 | 270
SELL41 | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 269
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 240
SJOW21 | SJOW13 | 0.1441 | 8.6238 | -0.2707 | 251
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273
SJOW4A | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 270
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 804
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 800
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 279
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN42 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 240
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 279
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198
STAL21 | STAL11 | 0.2188 | 8.097 | -1.9861 | 240
STAL42 | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271
STAY4A | STAY41 | 0.0002 | 0.4178 | -13.831 | 2750
STEW21 | STEN11 | 0.3392 | 11.9012 | -0.7294 | 141
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 274
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1172
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STSB4A | STSB41 | 0.0003 | 0.1825 | 0 | 2000
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252
SUND41 | SUND11 | 0.1303 | 7.8698 | -0.4285 | 278
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250
SWAN21 | SWAN11 | 0.1646 | 8.0383 | -0.1808 | 211
SWAN21 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211
SWAN41 | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 240
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210
SWAN4A | SWAN21 | 0.0178 | 1.5995 | -1.2431 | 851
TAUN42 | TAUN11 | 0.1759 | 7.9134 | -0.267 | 279
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
THOM41 | THOM21 | 0.0152 | 1.6463 | -0.1118 | 1100
THOM41 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM41 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM42 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879
THOM42 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 879
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
TILB21 | TILB11 | 0.3792 | 12.0524 | -0.3982 | 131
TILB21 | TILB12 | 0.3792 | 12.0524 | -0.3982 | 134
TILB41 | TILB13 | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 1153
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP21 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 135
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP22 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 172
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 139
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TOTT21 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265
TOTT22 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198
TOTT23 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT24 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 279
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 222
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 262
UPPB22 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 105
UPPB22 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 105
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 312
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 263
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 253
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 240
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 240
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 266
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 274
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275
WALX41 | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX41 | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX42 | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1137
WALX42 | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1137
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WASF21 | WASF12 | 0.197 | 7.9698 | -0.2553 | 207
WASF22 | WASF11 | 0.197 | 7.9698 | -0.2553 | 207
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 279
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 139
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 264
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 263
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 271
WHAM4A | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHAM4B | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO32 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.5913 | 19.0842 | -0.4269 | 100
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIEN21 | WIEN11 | 0.1594 | 8.6081 | -0.2215 | 288
WIEN21 | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 296
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278
WILE41 | WILL21 | 0.0268 | 2.7989 | -0.3188 | 686
WILL21 | WILL11 | 0.2847 | 12.2467 | -1.4346 | 140
WILL21 | WILL12 | 0.2847 | 12.2467 | -1.4346 | 140
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206
WIMB21 | WIMB14 | 0.1923 | 8.081 | -1.4418 | 189
WIMB21 | WIMB12 | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB12 | 0.1845 | 7.8956 | -0.1938 | 249
WIMB21 | WIMB13 | 0.1845 | 7.8956 | -0.1938 | 249
WIMB21 | WIMB13 | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB14 | 0.179 | 8.3648 | -4.7616 | 202
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 249
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD2B | 0.007 | 0.667 | 0 | 1140
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WLSD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949
WLSD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 1000
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WTHU4B | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 202
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250
WWEY22 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 202
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY41 | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY41 | WWEY22 | 0.0185 | 1.614 | -0.5638 | 886
WWEY42 | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845
WWEY42 | WWEY23 | 0.0178 | 1.5995 | -1.2431 | 845
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273

## B-3-1d
Table B.3.1d - Offshore Transmission Transformers 2018/19 | [8 empty] | Back To Menu
OFTO | Site | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW10 | BOSW30 | 0.316 | 15.0833 | 0 | 120 | 132/33
- | Burbo Bank Extension Wind Farm | BURB41 | BURB21 | 0.08 | 5.8995 | -0.3558 | 200 | 400/220/15.5
- | " | BURB41 | BURB21 | 0.08 | 5.8995 | -0.3558 | 200 | 400/220/15.5
- | " | BUBW20 | BUBW30 | 0.1 | 6.0492 | -0.8147 | 200 | 220/34
- | " | BUBW20 | BUBW30 | 0.1 | 6.0992 | -0.8147 | 200 | 220/34
- | Dudgeon Offshore Wind Farm | DUDG1 | DUDG3 | 0.1275 | 6.117 | 0 | 200 | 132/33
- | " | DUDG1 | DUDG3 | 0.1275 | 6.117 | 0 | 200 | 132/33
- | " | NECT41 | DUDO1 | 0.1264 | 8.4534 | -0.357 | 240 | 400/132/33
- | " | NECT41 | DUDO1 | 0.1264 | 8.4534 | -0.357 | 240 | 400/132/33
- | Galloper | GAON11 | GAON51 | 0.4 | 9.8919 | 0 | 90 | 132/20
- | " | GAON11 | GAON52 | 0.4 | 9.8919 | 0 | 90 | 132/20
- | " | GAOF1A | GAOF31/GAOF32 | 0.6 | 50.3964 | 0 | 180 | 132/33
- | " | GAOF1B | GAOF31/GAOF32 | 0.6 | 50.3964 | 0 | 180 | 132/33
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON11 | GGON51 | 0.0241 | 11 | 0 | 90 | 132/13.9
" | " | GGON12 | GGON52 | 0.0241 | 11 | 0 | 90 | 132/13.9
" | " | GGON13 | GGON53 | 0.0241 | 11 | 0 | 90 | 132/13.9
" | " | IGOF11 | IGOF31 | 0.3667 | 23.3305 | 0 | 180 | 132/33
" | " | IGOF12 | IGOF32 | 0.3667 | 23.3305 | 0 | 180 | 132/33
" | " | IGOF1A | IGOF3A | 0.4111 | 23.3297 | 0 | 90 | 132/33
" | " | IGOF1B | IGOF3B | 0.4111 | 23.3297 | 0 | 90 | 132/33
" | " | IGOF13 | IGOF33 | 0.3667 | 23.3305 | 0 | 180 | 132/33
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | GUNS10 | GUNS30 | 0.2372 | 8.5717 | 0 | 120 | 132/33
" | " | GUNS10 | GUNS30 | 0.2372 | 8.5717 | 0 | 120 | 132/33
- | Humber Gateway Offshore Wind Farm | HEDO20 | HUMO11 | 0.1441 | 8.6238 | -0.2707 | 240 | 275/132/33
- | " | HEDO20 | HUMO12 | 0.1441 | 8.6238 | -0.2707 | 240 | 275/132/33
- | " | HUMW11 | HUMW31 | 0.23 | 8.57 | 0 | 140 | 132/33
- | " | HUMW12 | HUMW32 | 0.23 | 8.57 | 0 | 140 | 132/33
TC Lincs OFTO Limited | Lincs Wind Farm | LINO40 | LINO10 | 0.0367 | 4.6665 | 0 | 300 | 400/132/13
" | " | LINO40 | LINO10 | 0.0367 | 4.6665 | 0 | 300 | 400/132/13
" | " | LINS10 | LINS30 | 0.2778 | 5.8328 | -0.351 | 180 | 132/33
" | " | LINS10 | LINS30 | 0.2778 | 5.8328 | -0.351 | 180 | 132/33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | LONO11 | 0.33 | 6.4556 | 0 | 180/180/90 | 400/150/13.9
" | " | LONO42 | LONO12 | 0.33 | 6.4111 | 0 | 180/180/90 | 400/150/13.9
" | " | LONO41 | LONO13 | 0.33 | 6.4611 | 0 | 180/180/90 | 400/150/13.9
" | " | LONO42 | LONO14 | 0.33 | 6.4389 | 0 | 180/180/90 | 400/150/13.9
" | " | LOAW11 | LOAW31 | 0.2222 | 6.663 | 0 | 180 | 150/33
" | " | LOAW12 | LOAW32 | 0.2222 | 6.663 | 0 | 180 | 150/33
" | " | LOAW13 | LOAW33 | 0.2222 | 6.663 | 0 | 180 | 150/33
" | " | LOAW14 | LOAW34 | 0.2222 | 6.663 | 0 | 180 | 150/33
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | BODE4C | GWYO10 | 0.054688 | 3.7469 | 0 | 320 | 400/132/13.9
" | " | BODE4D | GWYO10 | 0.054688 | 3.7469 | 0 | 320 | 400/132/13.9
" | " | GWYW10 | GWBW30 | 0.15625 | 11.25 | 0 | 160 | 132/33
" | " | GWYW10 | GWAW30 | 0.15625 | 11.25 | 0 | 160 | 132/33
" | " | GWYW10 | GWBW30 | 0.15625 | 11.25 | 0 | 160 | 132/33
" | " | GWYW10 | GWAW30 | 0.15625 | 11.25 | 0 | 160 | 132/33
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMO11 | ORMO31 | 0 | 14.7059 | 0 | 85 | 132/33
" | " | ORMO11 | ORMO31 | 0 | 14.7059 | 0 | 85 | 132/33
" | " | ORMO12 | ORMO32 | 0 | 13.6364 | 0 | 110 | 132/33
- | Race Bank Offshore Wind Farm | RAOF21 | RAOF31 | 0.15 | 5.9981 | 0 | 200 | 220/34
- | " | RAOF21 | RAOF32 | 0.15 | 5.9981 | 0 | 200 | 220/34
- | " | RAOF22 | RAOF33 | 0.15 | 5.9981 | 0 | 200 | 220/34
- | " | RAOF22 | RAOF34 | 0.15 | 5.9981 | 0 | 200 | 220/34
- | " | RABO21 | RABO31 | 0.1917 | 8.5302 | 0 | 130 | 220/27
- | " | RABO21 | RABO31 | 0.1917 | 8.5302 | 0 | 130 | 220/27
- | " | RACB41 | RABO21 | 0.0667 | 3.0548 | -0.8396 | 360 | 400/220
- | " | RACB42 | RABO22 | 0.0306 | 3.0554 | -0.8396 | 360 | 400/220
- | Rampion Offshore Wind Farm | RAMP1C | RAMP31 | 0.0868 | 4.9992 | -0.144 | 240 | 150/33
- | " | RAMP1D | RAMP32 | 0.0868 | 4.9992 | -0.144 | 240 | 150/33
- | " | TWIN41 | TWIN11 | 0.0708 | 12.2398 | -1.9406 | 240 | 400/150/33
- | " | TWIN42 | TWIN12 | 0.0708 | 12.2398 | -1.9406 | 240 | 400/150/33
- | Robin Rigg East Offshore Wind Farm | RORE11 | RORE31 | 1.9545 | 58.6341 | 0 | 30 | 132/33
- | " | RORE11 | RORE32 | 0.3 | 11.36 | 0 | 100 | 132/33
- | " | RORE12 | RORE33 | 0 | 15.7895 | 0 | 95 | 132/33
- | Robin Rigg West Offshore Wind Farm | RORW11 | RORW31 | 1.9545 | 58.6341 | 0 | 30 | 132/33
- | " | RORW11 | RORW32 | 0.3 | 11.36 | 0 | 100 | 132/33
- | " | RORW12 | RORW33 | 0 | 15.7895 | 0 | 95 | 132/33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW10 | SSAW30 | 0.23 | 12.07 | 0 | 90 | 132/33
" | " | SSAW10 | SSAW30 | 0.23 | 12.07 | 0 | 90 | 132/33
" | " | SSAW10 | SSAW30 | 0.23 | 12.07 | 0 | 90 | 132/33
" | " | SSAW10 | SSAW30 | 0.23 | 12.07 | 0 | 90 | 132/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW10 | THOW30 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
" | " | THOW10 | THOW30 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAW10 | WAAW30 | 0.41667 | 8.75 | 0 | 120 | 132/33
" | " | WAAW10 | WAAW30 | 0.41667 | 8.75 | 0 | 120 | 132/33
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABW10 | WABW30 | 0.41667 | 8.75 | 0 | 120 | 132/33
" | " | WABW10 | WABW30 | 0.41667 | 8.75 | 0 | 120 | 132/33
" | Walney 3 Offshore Wind Farm | WACW21 | WACW31 | 0.0821 | 4.2992 | -0.6518 | 280 | 220/34
" | Walney 3 Offshore Wind Farm | WACW22 | WACW32 | 0.0821 | 4.2992 | -0.6518 | 280 | 220/34
" | Walney 4 Offshore Wind Farm | WADW21 | WADW31 | 0.0821 | 4.2992 | -0.6518 | 280 | 220/34
" | Walney 4 Offshore Wind Farm | WADW22 | WADW32 | 0.0821 | 4.2992 | -0.6518 | 280 | 220/34
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | WDSW11 | WDSW30 | 0.0208 | 5 | 0 | 240 | 155/33
" | " | WDSW12 | WDSW30 | 0.0208 | 5 | 0 | 240 | 155/33
- | Walney Extension | WAEN41 | WAEN21 | 0.0255 | 2.6169 | -1.0975 | 470 | 400/220
- | " | WAEN42 | WAEN22 | 0.0255 | 2.6169 | -1.0975 | 470 | 400/220
- | " | WAEN21 | WAEN51 | 0.1286 | 8.5705 | -0.3212 | 140 | 220/22
- | " | WAEN22 | WAEN52 | 0.1286 | 8.5705 | -0.3212 | 140 | 220/22
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | WDSO11 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
" | " | WDSO42 | WDSO12 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
" | " | WDSW11 | WDSW30 | 0.20833 | 5 | 0 | 240 | 155/34
" | " | WDSW12 | WDSW30 | 0.20833 | 5 | 0 | 240 | 155/34
- | Westernost Rough Offshore Wind Farm | WERW21 | WERW11 | 0.003458 | 0.20997 | 0 | 160 | 275/150/33
- | " | WERW22 | WERW11 | 0.003458 | 0.20997 | 0 | 160 | 275/150/33
- | " | WERW12 | WERW30 | 0.016 | 0.1592 | 0 | 140 | 150/33
- | " | WERW12 | WERW30 | 0.016 | 0.1592 | 0 | 140 | 150/33

## B-3-2a
Table B.3.2a - SHE Transmission Transformer Changes 2019/20 to 2027/28 | [7 empty] | Back To Menu
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 2019 | Addition | 0.2621 | 24.6736 | -0.022 | 120
ABNE1Q | ABNE3- | 2019 | Removed | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 2019 | Addition | 0.2614 | 24.7403 | -0.02 | 120
ABNE1R | ABNE3- | 2019 | Removed | 1.05 | 28.5 | 0 | 60
MELG4K | MELG1K | 2019 | Addition | 0.106 | 3.957 | -0.003 | 480
TOMT2J | TOMT1J | 2019 | Addition | 0.0985 | 3.9363 | -0.003 | 480
TOMT2K | TOMT1K | 2019 | Addition | 0.0985 | 3.9363 | -0.003 | 480
ABED1- | ABED3- | 2020 | Addition | 0.33 | 21.7 | 0 | 60
DUDH1Q | DUDH3- | 2020 | Removed | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 2020 | Removed | 0.78 | 23.93 | 0 | 60
DYCE1Q | DYCE3- | 2020 | Addition | 0.5828 | 24.9932 | 0 | 90
DYCE1Q | DYCE3- | 2020 | Removed | 0.9463 | 26.6499 | -0.426 | 60
DYCE1R | DYCE3- | 2020 | Addition | 0.5828 | 24.9932 | 0 | 90
DYCE1R | DYCE3- | 2020 | Removed | 0.9517 | 26.7164 | -0.408 | 60
FARI2K | FARI1K | 2020 | Addition | 0.2184 | 8.2304 | -0.004 | 240
FARI2K | FARI1K | 2020 | Removed | 0.4955 | 8.3186 | -0.038 | 120
FETT2R | FETT1- | 2020 | Addition | 0.2217 | 4.2737 | -0.0006 | 240
FIDD1R | FIDD3- | 2020 | Removed | 0.4562 | 26.084 | 0 | 90
FIDD1S | FIDD3- | 2020 | Addition | 0.4562 | 26.084 | 0 | 90
LOCH1- | LOCH5J | 2020 | Addition | 1.968 | 79.976 | 0 | 36
LOCH1- | LOCH5J | 2020 | Removed | 1.93 | 38.52 | 0 | 25
LOCH1- | LOCH5K | 2020 | Addition | 1.968 | 79.976 | 0 | 36
LOCH1- | LOCH5K | 2020 | Removed | 1.93 | 38.2 | 0 | 25
MKTG1B | DUDH3A | 2020 | Addition | 0.5828 | 24.9932 | 0 | 90
MKTG1E | DUDH3B | 2020 | Addition | 0.5828 | 24.9932 | 0 | 90
NANT1Q | NANT5- | 2020 | Addition | 1.968 | 79.976 | 0 | 36
NANT1Q | NANT5- | 2020 | Removed | 1.47 | 56.67 | 0 | 30
ROTI2J | ROTI3- | 2020 | Addition | 0.39 | 18 | 0 | 120
CAAD1Q | CAAD3- | 2021 | Addition | 0.2621 | 24.6736 | -0.022 | 120
CAAD1Q | CAAD3- | 2021 | Removed | 1.04 | 27.65 | 0 | 60
CAAD1R | CAAD3- | 2021 | Addition | 0.2621 | 24.6736 | -0.022 | 120
CAAD1R | CAAD3- | 2021 | Removed | 1.04 | 27.65 | 0 | 60
FAUG4- | FAUG1- | 2021 | Removed | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 2021 | Removed | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1J | 2021 | Addition | 0.108 | 3.957 | -0.003 | 480
FAUG4K | FAUG1K | 2021 | Addition | 0.108 | 3.957 | -0.003 | 480
GLKO1- | GLKO3J | 2021 | Addition | 0.36 | 18 | 0 | 60
MILS1Q | MILS3J | 2021 | Addition | 0.36 | 18 | 0 | 60
PORA1Q | PORA3- | 2021 | Removed | 1.803 | 29.812 | 0 | 30
PORA1S | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
CAAD1Q | CAAD3J | 2022 | Addition | 0.2621 | 24.6736 | -0.022 | 120
CAAD1Q | CAAD3J | 2022 | Removed | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3J | 2022 | Addition | 0.2621 | 24.6736 | -0.022 | 120
CAAD1R | CAAD3J | 2022 | Removed | 0.5 | 25 | 0 | 90
DOUN2- | DOUN2A | 2022 | Addition | 0.066 | 5.333 | 0 | 360
EDIN1- | GLNU3- | 2022 | Addition | 0.36 | 18 | 0 | 60
FINS1- | COST3- | 2022 | Addition | 0.54 | 18 | 0 | 45
FINS1- | FINS3- | 2022 | Addition | 0.451 | 25 | 0 | 120
FINS1- | HEST3- | 2022 | Addition | 0.54 | 18 | 0 | 45
FINS2A | FINS1- | 2022 | Addition | 0.044 | 5.833 | 0 | 360
LIMK1- | LIMK3- | 2022 | Addition | 0.36 | 18 | 0 | 120
PENF1- | PENF3A | 2022 | Addition | 0.36 | 18 | 0 | 42
SALA1- | SALA3- | 2022 | Addition | 0.36 | 17.99 | 0 | 90
SFEG1Q | SFEG5- | 2022 | Addition | 2.3813 | 74.9622 | 0 | 40
SFEG1Q | SFEG5- | 2022 | Removed | 2.28 | 93.87 | 0 | 30
SFEG1R | SFEG5- | 2022 | Addition | 2.3813 | 74.9622 | 0 | 40
SFEG1R | SFEG5- | 2022 | Removed | 2.28 | 92.8 | 0 | 30
ARNI1K | ARNI3- | 2024 | Addition | 0.36 | 18 | 0 | 60
BEWF1- | BEWF3- | 2024 | Addition | 0.36 | 18 | 0 | 90
CONN2K | CONN1K | 2024 | Addition | 0.143 | 5.3036 | -0.002 | 360
CRDH2J | CRDH1J | 2024 | Addition | 0.098 | 3.936 | -0.003 | 480
CRDH2K | CRDH1K | 2024 | Addition | 0.098 | 3.936 | -0.003 | 480
CREA1- | CREA3- | 2024 | Addition | 0.4 | 20 | 0 | 90
DOUN2- | DOUN2D | 2024 | Addition | 0.066 | 5.333 | 0 | 360
DRUL1- | DRUL3- | 2024 | Addition | 0.36 | 18 | 0 | 60
FINS1- | BRMS3- | 2024 | Addition | 0.543 | 20 | 0 | 90
FINS1- | WESR3- | 2024 | Addition | 0.36 | 18 | 0 | 90
FINS2D | FINS1- | 2024 | Addition | 0.044 | 5.833 | 0 | 360
GLSH1J | GLSH31 | 2024 | Addition | 0.6 | 17.4 | 0 | 120
GLSH1J | GLSH32 | 2024 | Addition | 0.6 | 17.4 | 0 | 120
GOLT1- | GOLT3- | 2024 | Addition | 0.36 | 18 | 0 | 90
GORW2- | GORW3- | 2024 | Removed | 0.258 | 20.06 | 0 | 120
GORW2A | GORW3- | 2024 | Addition | 0.258 | 20.06 | 0 | 120
MUAI1- | MUAI3J | 2024 | Addition | 0.36 | 18 | 0 | 90
MUAI1- | MUAI3K | 2024 | Addition | 0.36 | 18 | 0 | 90
PEHE4J | PEHE2J | 2024 | Addition | 0.026 | 1.533 | -0.001 | 1200
PEHE4J | PEHE2Q | 2024 | Addition | 0.026 | 1.533 | -0.001 | 1200
PEHE4K | PEHE2K | 2024 | Addition | 0.026 | 1.533 | -0.001 | 1200
PEHE4K | PEHERSV1 | 2024 | Addition | 0.026 | 1.533 | -0.001 | 1200
PENF1- | PENF3A | 2024 | Addition | 0.36 | 18 | 0 | 84
PENF1- | PENF3A | 2024 | Removed | 0.36 | 18 | 0 | 42
PORA1Q | PORA3- | 2024 | Addition | 1.803 | 29.812 | 0 | 30
PORA1S | PORA3- | 2024 | Removed | 1.803 | 29.812 | 0 | 30
STRW13 | STRW33 | 2024 | Addition | 0.5 | 25 | 0 | 90
STRW13 | STRW34 | 2024 | Addition | 0.5 | 25 | 0 | 90
STRW1C | STRW35 | 2024 | Addition | 0.36 | 18 | 0 | 120
STWN1- | STWN3J | 2024 | Addition | 0.36 | 18 | 0 | 90
STWN1- | STWN3K | 2024 | Addition | 0.36 | 18 | 0 | 90
TEAL2B | TEAL2K | 2024 | Addition | 0.005 | 0.4 | 0 | 700
TEAL2J | TEAL2A | 2024 | Addition | 0.005 | 0.4 | 0 | 700
WILW1- | WILW3- | 2024 | Addition | 0.36 | 18 | 0 | 60
ALYT4J | ALYT2A | 2027 | Addition | 0.017 | 1.59 | -0.001 | 1000
ALYT4K | ALYT2B | 2027 | Addition | 0.017 | 1.59 | -0.001 | 1000
BLHI2J | BLHI2A | 2027 | Addition | 0.005 | 0.4 | 0 | 865
BLHI2K | BLHI1K | 2027 | Addition | 0.1486 | 5.3035 | -0.002 | 360
BLHI2K | BLHI2B | 2027 | Addition | 0.005 | 0.4 | 0 | 865
BLHI4- | BLHI2L | 2027 | Removed | 0.0252 | 1.1997 | -0.001 | 1200
BLHI4- | BLHI2M | 2027 | Removed | 0.0253 | 1.2081 | -0.001 | 1200
COGL4- | COGL8A | 2027 | Addition | 0.32 | 6.4 | 0 | 195
COGL4- | COGL8B | 2027 | Addition | 0.32 | 6.4 | 0 | 195
COGL4- | COGL8C | 2027 | Addition | 0.32 | 6.4 | 0 | 195
COGL4- | COGL8D | 2027 | Addition | 0.32 | 6.4 | 0 | 195
ELCH1- | ELCH3- | 2027 | Addition | 0.75 | 15 | 0 | 120
FETT2R | FETT1- | 2027 | Removed | 0.2217 | 4.2737 | -0.0006 | 240
FETT2R | FETT1- | 2027 | Removed | 0.217 | 4.2737 | -0.0006 | 240
FETT4J | FETT1- | 2027 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FETT4K | FETT1- | 2027 | Addition | 0.2149 | 8.0138 | -0.013 | 240
INGA4J | INGA1K | 2027 | Addition | 0.131 | 7.952 | -0.11 | 240
INGA4K | INGA1J | 2027 | Addition | 0.131 | 7.952 | -0.11 | 240
KINT4J | KINT2K | 2027 | Addition | 0.0252 | 1.1997 | -0.001 | 1200
KINT4K | KINT2J | 2027 | Addition | 0.0253 | 1.2081 | -0.001 | 1200
PEHE4J | PEHE2J | 2027 | Removed | 0.026 | 1.533 | -0.001 | 1200
PEHE4K | PEHE2K | 2027 | Removed | 0.026 | 1.533 | -0.001 | 1200
PENF1B | PENF3B | 2027 | Addition | 3.6 | 18 | 0 | 96
PENF1C | PENF3C | 2027 | Addition | 3.6 | 18 | 0 | 96
ROTI1J | ROTI3- | 2027 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI1K | ROTI3- | 2027 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI2J | ROTI3- | 2027 | Removed | 0.39 | 18 | 0 | 120
ROTI4J | ROTI1J | 2027 | Addition | 0.2149 | 8.0138 | -0.013 | 240
ROTI4K | ROTI1K | 2027 | Addition | 0.2149 | 8.0138 | -0.013 | 240

## B-3-2b
Table B.3.2b - SPT Transformer Changes 2019/20 to 2027/28 | [7 empty] | Back To Menu
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
COAL4- | COAL1- | 2019 | Removed | 0.1216 | 9.6242 | -0.0793 | 240
KILS4T | KILS2- | 2019 | Addition | 0.0148 | 1.6509 | -0.1193 | 1000
ERSK1Q | ERSK3- | 2019 | Change | 0.3119 | 21.8311 | 0 | 60
SHRU2R | SHRU3- | 2019 | Change | 0.2917 | 24.5816 | -0.0132 | 120
COAL4- | COAL1A | 2019 | Addition | 0.0733 | 6.6663 | -0.1905 | 360
COAL4- | COAL1A | 2019 | Addition | 0.1216 | 9.6242 | -0.0793 | 240
CUMH1- | CUMH3- | 2020 | Addition | 0.3488 | 24.4142 | 0 | 120
NEIL1- | NEIL3A | 2020 | Addition | 0.3119 | 21.8311 | 0 | 60
CONO1- | DOWE3G | 2021 | Addition | 0.3119 | 21.8311 | 0 | 60
DUNB1S | DUNB3B | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
DUNB1T | DUNB3B | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
EWEH1Q | EWEH3A | 2021 | Addition | 0.3635 | 25.4418 | 0 | 90
FALL4- | FALL3C | 2021 | Addition | 0.2564 | 16.6647 | 0 | 120
CRYR4- | NNGA2- | 2022 | Addition | 0.1071 | 5.8919 | -0.0108 | 280
CRYR4- | NNGB2- | 2022 | Addition | 0.1071 | 5.8919 | -0.0108 | 280
DALQ1- | DALQ3- | 2022 | Addition | 0.3119 | 21.8311 | 0 | 60
ELVA2R | ELVA1- | 2022 | Addition | 0.0984 | 5.8325 | -0.2121 | 360
KYPE1- | HARG3- | 2022 | Addition | 0.3635 | 25.4418 | 0 | 90
MAHI2- | MAHI1B | 2022 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
MARG1- | MARG3- | 2022 | Addition | 0.3635 | 25.4418 | 0 | 90
NECU2- | NECU1B | 2022 | Addition | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1164 | 8.5534 | -0.0287 | 240
NECU2- | NECU1C | 2022 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1C | 2022 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NNGA2G | NNGA3- | 2022 | Addition | 0.1777 | 7.998 | -0.1152 | 250
NNGB2G | NNGB3- | 2022 | Addition | 0.1777 | 7.998 | -0.1152 | 250
COYL2- | COYL1- | 2022 | Change | 0.1476 | 8.7488 | -0.1299 | 240
COYL2- | COYL1- | 2022 | Change | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1Q | 2022 | Removed | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 2022 | Removed | 0.1164 | 8.5534 | -0.0287 | 240
BENB1- | BENB3- | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
ELVA1- | HABU3- | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
ENHI1- | ENHI3- | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
GHPS1- | GHPS3A | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
GHPS1- | GHPS3B | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
GHPS1- | GHPS3C | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
GLLU1Q | GLLU3B | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
GLLU1R | GLLU3B | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
KENN1- | KENN3- | 2024 | Addition | 0.3488 | 24.4142 | 0 | 120
LORG1- | LORG3- | 2024 | Addition | 0.3119 | 21.8311 | 0 | 60
NEIL4R | NEIL2- | 2024 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
NETS1- | NETS3- | 2024 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
SOKY1- | SOKY3- | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
SOKY1- | SOKY3- | 2024 | Addition | 0.3635 | 25.4418 | 0 | 90
SQHR1- | SQHR3- | 2024 | Addition | 0.3488 | 24.4142 | 0 | 120
STNO1- | STNO3- | 2024 | Addition | 0.3488 | 24.4142 | 0 | 120
GLGL1- | GLGL3- | 2024 | Addition | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1- | GLGL3- | 2024 | Addition | 0.3349 | 27.9091 | -0.0086 | 90
GLGL1Q | GLGL3- | 2024 | Removed | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 2024 | Removed | 0.3349 | 27.9091 | -0.0086 | 90
TONG1Q | TONG1R | 2024 | Removed | 0.0125 | 2.5 | 0 | 90
TONG1- | TONG1R | 2024 | Removed | 0.0267 | 1.3331 | 0 | 90
DENN4- | DENN2- | 2027 | Addition | 0.0164 | 1.6449 | -0.1161 | 1000
KINC4A | KINC2- | 2027 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4A | KINC2- | 2027 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4B | KINC2- | 2027 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4B | KINC2- | 2027 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
MOFF4- | MOFF1- | 2027 | Addition | 0.1483 | 10.0614 | -0.3432 | 240
NLEI1- | NLEI3A | 2027 | Addition | 0.3635 | 25.4418 | 0 | 90
NLEI1- | NLEI3B | 2027 | Addition | 0.3635 | 25.4418 | 0 | 90

## B-3-2c
Table B.3.2c - NGET Transformer Changes 2019/20 to 2027/28 | [7 empty] | Back To Menu
Node 1 | Node 2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
IVER42 | IVER21 | 2019 | Addition | 0.000152 | 0.016463 | -0.001118 | 775
RICH4* | RICH4* | 2019 | Addition | 0 | 0.0014 | 0 | 2500
TILB21 | TILB11 | 2019 | Addition | 0.001307 | 0.079515 | -0.001098 | 131
WIMB41 | WIMB11 | 2019 | Addition | 0.001303 | 0.078698 | -0.004285 | 240
WIMB41 | WIMB12 | 2019 | Addition | 0.001303 | 0.078698 | -0.004285 | 240
WIMB21 | WIMB14 | 2019 | Removed | 0.00179 | 0.083648 | -0.047616 | 202
WIMB21 | WIMB11 | 2019 | Removed | 0.001923 | 0.08081 | -0.014418 | 189
ELST22 | ELST16 | 2019 | Removed | 0.003567 | 0.11136 | -0.007303 | 127
IVER41 | IVER21 | 2019 | Removed | 0.000326 | 0.023798 | -0.039003 | 500
ELST21 | ELST15 | 2019 | Removed | 0.003567 | 0.11136 | -0.007303 | 126
TILB21 | TILB11 | 2019 | Removed | 0.003792 | 0.12052 | -0.003982 | 131
BICF41 | BICF11 | 2020 | Addition | 0.001307 | 0.079515 | -0.001098 | 278
BICF41 | BICF11 | 2020 | Addition | 0.001307 | 0.079515 | -0.001098 | 274
Eleclink HVDC Connections* | Eleclink HVDC Connections* | 2020 | Addition | 0 | 0.01 | 0 | 1200
WIMB41 | WIMB11 | 2020 | Addition | 0.001303 | 0.078698 | -0.004285 | 240
WIMB41 | WIMB12 | 2020 | Addition | 0.001303 | 0.078698 | -0.004285 | 240
WIMB21 | WIMB11 | 2020 | Removed | 0.001845 | 0.078956 | -0.001938 | 249
BICF42 | BICF11 | 2020 | Removed | 0.001307 | 0.079515 | -0.001098 | 274
WIMB21 | WIMB12 | 2020 | Removed | 0.00167 | 0.079774 | -0.002092 | 255
BICF41 | BICF11 | 2020 | Removed | 0.001307 | 0.079515 | -0.001098 | 278
BLYT41 | BLYT21 | 2022 | Addition | 0.000152 | 0.016463 | -0.001118 | 1100
BLYT41 | BLYT21 | 2022 | Addition | 0.000152 | 0.016463 | -0.001118 | 1148
CANW4* | CANW1* | 2022 | Addition | 0.001139 | 0.081036 | -0.02059 | 240
CANW4* | CANW1* | 2022 | Addition | 0.001139 | 0.081036 | -0.02059 | 240
CANW4* | CANW1* | 2022 | Addition | 0.001139 | 0.081036 | -0.02059 | 240
CANW4* | CANW1* | 2022 | Addition | 0.001139 | 0.081036 | -0.02059 | 240
CANW4* | CANW1* | 2022 | Addition | 0.001139 | 0.081036 | -0.02059 | 240
HARK41 | HARK21 | 2022 | Change | 0.000152 | 0.016463 | -0.001118 | 555
BLYT41 | BLYT21 | 2022 | Removed | 0.000152 | 0.016463 | -0.001118 | 1100
BLYT41 | BLYT21 | 2022 | Removed | 0.000152 | 0.016463 | -0.001118 | 1148
BRIW4* | BRWA11 | 2024 | Addition | 0.001307 | 0.079515 | -0.001098 | 180
BRIW4* | BRWA11 | 2024 | Addition | 0.001307 | 0.079515 | -0.001098 | 180
EXET41 | EXET41 | 2024 | Addition | 1e-05 | 0.001019 | 0 | 1500
SAFO41 | SAFO11 | 2024 | Addition | 0.001307 | 0.079515 | -0.001098 | 200
SAFO41 | SAFO12 | 2024 | Addition | 0.001307 | 0.079515 | -0.001098 | 180
WIMB41 | WIMB22 | 2024 | Addition | 0.00014 | 0.026567 | -0.001528 | 950
BRWA2B | BRWA11 | 2024 | Removed | 0.00167 | 0.079774 | -0.002092 | 255
SEAB41 | SEAB11 | 2024 | Removed | 0.001307 | 0.079515 | -0.001098 | 276
BRWA2A | BRWA11 | 2024 | Removed | 0.00167 | 0.079774 | -0.002092 | 255
HAWP41 | HAWP21 | 2027 | Addition | 0.000132 | 0.016756 | -0.004337 | 1000
HAWP41 | HAWP41 | 2027 | Addition | 0 | 0.000556 | 0 | 4500

## B-3-2d
Table B.3.2d - Indicative Offshore Transmission Transformer Changes 2019/20 to 2027/28 | [10 empty] | Back To Menu
OFTO | Site | Node 1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage Ratio (kV)
- | Dogger Bank | DOGG4 | DOGG2 | 2024 | Addition | 0 | 1.5 | 0 | 1000 | 400/320
| Hornsea 1 | HOWA2 | HOWA4 | 2019 | Addition | - | - | - | 430 | 400/220
| Hornsea 1 | HOWA2 | HOWA4 | 2019 | Addition | - | - | - | 430 | 400/220
| Hornsea 1 | HOWA2 | HOWA4 | 2019 | Addition | - | - | - | 430 | 400/220
| Hornsea 1 | HONW3 | HOWW2 | 2019 | Addition | - | - | - | 240 | 220/34
| Hornsea 1 | HONW3 | HOWW2 | 2019 | Addition | - | - | - | 240 | 220/34
| Hornsea 1 | HONW3 | HOWW2 | 2019 | Addition | - | - | - | 240 | 220/34
| Hornsea 1 | HONW3 | HOWW2 | 2019 | Addition | - | - | - | 240 | 220/34
| Hornsea 1 | HONW3 | HOWW2 | 2019 | Addition | - | - | - | 240 | 220/34
| Hornsea 1 | HONW3 | HOWW2 | 2019 | Addition | - | - | - | 240 | 220/34
Note: Transformers data to be confimed

## B-4-1a
Table B.4.1a - SHE Transmission Reactive Compensation Equipment, Winter 2018/19 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
BEAULY | BEAU3U | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU3V | 2 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU1K | 1 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1J | 2 | 45 |  | Mechanically Switched Capacitor | 132
CROSSAIG | CRSS3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3W | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Z | 4 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT1- | 1 |  | 200 | Shunt Reactor | 132
TEALING | TEAL3W | 1 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 3 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275
TEALING | TEAL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL1- | 1 |  | 100 | Shunt Reactor | 132
Macduff | MACD3- | 1 | 10 |  | Mechanically Switched Capacitor | 33

## B-4-1b
Table B.4.1b - SPT Reactive Compensation Equipment, Winter 2018/19 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Auchencrosh | AUCH2- | 1 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 2 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 3 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 4 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 5 | 59 |  | FILTER BANK | 275
COALBURN | COAL3U | 1 |  | 60 | REACTOR | 33
COCKENZIE | COCK2- | 1 | 225 |  | MSCDN | 275
CRYSTAL RIG | CRYR3V | 1 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 1 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 2 |  | 60 | REACTOR | 33
ECCLES | ECCL3V | 1 |  | 60 | REACTOR | 33
ELVANFOOT | ELVA4- | 1 | 225 |  | MSCDN | 400
ELVANFOOT | ELVA3V | 1 |  | 60 | REACTOR | 33
GIFFNOCK | GIFF3- | 1 |  | 60 | REACTOR | 33
Hunterston Converter Station | HUCS4- | 1 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 2 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 3 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 4 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 5 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 6 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 7 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 8 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 1 |  | 200 | REACTOR | 400
Hunterston Converter Station | HUCS4- | 1 | 250 | 382 | STATCOM | 400
HUNTERSTON NORTH | HUNN3W | 1 |  | 60 | REACTOR | 33
HUNTERSTON NORTH | HUNN3X | 1 |  | 60 | REACTOR | 33
KILLGALLIOCH WIND FARM | KILG2- | 1 |  | 60 | REACTOR | 275
KILMARNOCK SOUTH | KILS3U | 1 |  | 60 | REACTOR | 33
LONGANNET | LOAN2- | 1 | 225 |  | MSCDN | 275
LONGANNET | LOAN2- | 2 | 225 |  | MSCDN | 275
MARK'S HILL | MAHI3U | 1 |  | 60 | REACTOR | 33
MOFFAT | MOFF4- | 1 | 225 |  | MSCDN | 400
MOFFAT | MOFF3U | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3U | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3V | 1 |  | 60 | REACTOR | 33
TORNESS | TORN4- | 1 |  | 9 | REACTOR | 400
TORNESS | TORN4- | 2 |  | 150 | REACTOR | 400
TORNESS | TORN4- | 3 |  | 150 | REACTOR | 400
West George Street | WGEO3- | 1 |  | 60 | REACTOR | 33
West George Street | WGEO3- | 2 |  | 60 | REACTOR | 33
WINDYHILL | WIYH3W | 3 |  | 60 | REACTOR | 33
WINDYHILL | WIYH2- | 1 | 150 |  | MSCDN | 275
CURRIE | CURR3W | 1 |  | 60 | REACTOR | 33
WISHAW | WISH3- | 1 |  | 60 | REACTOR | 33
Shrubhill | SHRU3- | 1 |  | 60 | REACTOR | 33
Shrubhill | SHRU3- | 1 |  | 60 | REACTOR | 33
SMEATON | SMEA3U | 1 |  | 60 | REACTOR | 33
SMEATON | SMEA3V | 1 |  | 60 | REACTOR | 33

## B-4-1c
Table B.4.1c - NGET Reactive Compensation Equipment, Winter 2018/19 | [6 empty] | Back To Menu
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
Aberthaw | ABTH12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Aberthaw | ABTH12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Abham | ABHA12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Abham | ABHA11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Alverdiscott | ALVE10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Barking | BARK2 | 2B WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Barking | BARK2 | 2B WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Barking | BARK2 | 4B WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Barking | BARK2 | 4B WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Beddington | BEDD21 | 3B | 150 |  | Mechanically Switched Capacitor | 275
Beddington | BEDD22 | 4B | 150 |  | Mechanically Switched Capacitor | 275
Beddington | BEDD11 | 1B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD11 | 2B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD11 | 3B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD11 | 4B |  | 60 | Reactor | Tertiary Connected
Beddington | BEDD21 | 5B |  | 100 | Reactor | 275
Beddington | BEDD22 | 6A |  | 100 | Reactor | 275
Berkswell | BESW20 | 4 | 150 |  | Mechanically Switched Capacitor | 275
Berkswell | BESW10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Berkswell | BESW10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Berkswell | BESW10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Birkenhead | BIRK10 | 4 WDG A |  | 60 | Reactor | Tertiary Connected
Birkenhead | BIRK10 | 4 WDG B |  | 60 | Reactor | Tertiary Connected
Bishops Wood | BISW10 | A | 60 |  | Mechanically Switched Capacitor | 132
Bishops Wood | BISW10 | B | 60 |  | Mechanically Switched Capacitor | 132
Bishops Wood | BISW10 | C | 60 |  | Mechanically Switched Capacitor | 132
Blyth | BLYT21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Blyth | BLYT22 | 2 | 150 |  | Mechanically Switched Capacitor | 275
Bolney | BOLN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | BOLN13 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN14 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN40 | 1 |  | 55 | Reactor | Tertiary Connected
Bolney | BOLN40 | 2 |  | 55 | Reactor | Tertiary Connected
Bolney | BOLN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Bradford West | BRAW12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Bradford West | BRAW2 | 3 |  | 60 | Reactor | Tertiary Connected
Bradford West | BRAW2 | 4A |  | 30 | Reactor | Tertiary Connected
Bradford West | BRAW2 | 4B |  | 30 | Reactor | Tertiary Connected
Bramford | BRFO10 | A | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO10 | B | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO10 | C | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO40 | 1 |  | 200 | Reactor | 400
Bredbury | BRED2 | 1 WDG 1 |  | 30 | Reactor | Tertiary Connected
Bredbury | BRED2 | 1 WDG 2 |  | 30 | Reactor | Tertiary Connected
Bredbury | BRED2 | 3 WDG 1 |  | 30 | Reactor | Tertiary Connected
Bredbury | BRED2 | 3 WDG 2 |  | 30 | Reactor | Tertiary Connected
Bridgewater | BRWA10 | 1A | 45 |  | Mechanically Switched Capacitor | 132
Bridgewater | BRWA10 | 1B | 45 |  | Mechanically Switched Capacitor | 132
Bridgewater | BRWA2B |  | 60 |  | SVC | Tertiary Connected
Bushbury | BUSH20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Bushbury | BUSH10 | A | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH10 | B | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH10 | C | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH2 | 3 |  | 60 | Reactor | Tertiary Connected
Bustleholm | BUST2 | 4 | 20 |  | Mechanically Switched Capacitor | Tertiary Connected
Bustleholm | BUST2 | 4 |  | 60 | Reactor | Tertiary Connected
Bustleholm | BUST2 | 1A |  | 30 | Reactor | Tertiary Connected
Bustleholm | BUST2 | 1B |  | 30 | Reactor | Tertiary Connected
Canterbury | CANT40 | 1 |  | 200 | Reactor | 400
Capenhurst | CAPE21 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Cellarhead | CELL11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL40 | 7 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | CELL40 | 8 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | CELL11 | 2A | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2B | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2 WDG A |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL11 | 2 WDG B |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL11 | 3 WDG A |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL11 | 3 WDG B |  | 30 | Reactor | Tertiary Connected
Cellarhead | CELL40 | 5 | 150 | -75 | SVC | 400
Cellarhead | CELL40 | 6 | 150 | -75 | SVC | 400
Chesterfield | CHTE11 | 1 |  | 60 | Reactor | Tertiary Connected
Chickerell | CHIC42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Chickerell | CHIC10 | 1 |  | 60 | Reactor | Tertiary Connected
Cilfynydd | CILF4 | 1 |  | 60 | Reactor | Tertiary Connected
Cilfynydd | CILF4 | 2 |  | 60 | Reactor | Tertiary Connected
Cilfynydd | CILF40 | 4 |  | 200 | Reactor | 400
Cilfynydd | CILF40 | 6 |  | 200 | Reactor | 400
City Road | CITR12 | 1 | 55 |  | Mechanically Switched Capacitor | Tertiary Connected
City Road | CITR11 | 2 | 55 |  | Mechanically Switched Capacitor | Tertiary Connected
City Road | CITR41 | 1 |  | 200 | Reactor | 400
Connah's Quay | CONQ11 | 1 WDG 1 |  | 30 | Reactor | Tertiary Connected
Connah's Quay | CONQ11 | 1 WDG 2 |  | 30 | Reactor | Tertiary Connected
Coventry | COVE10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE10 | 1 |  | 60 | Reactor | Tertiary Connected
Coventry | COVE20 |  | 60 |  | SVC | Tertiary Connected
Cowley | COWL10 | A | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL10 | B | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL10 | C | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL40 | 2 |  | 200 | Reactor | 400
Cowley | COWL40 | 3 |  | 200 | Reactor | 400
Daines | DAIN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Didcot | DIDC41 | 1 |  | 2640 | Series Reactor (bypassed) | 400
Drakelow | DRAK40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Drakelow | DRAK40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Drakelow | DRAK40 | 4 |  | 200 | Reactor | 400
Drakelow | DRAK40 | 6 |  | 200 | Reactor | 400
Drax | DRAX12 | 1 |  | 60 | Reactor | Tertiary Connected
Drax | DRAX11 | 2 |  | 60 | Reactor | Tertiary Connected
Drax | DRAX41 | 1 |  | 1320 | Series Reactor (bypassed) | 400
East Claydon | ECLA40 | 5 | 225 |  | Mechanically Switched Capacitor | 400
East Claydon | ECLA40 | 7 | 225 |  | Mechanically Switched Capacitor | 400
East Claydon | ECLA10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
East Claydon | ECLA40 | 1 WDG A |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 1 WDG B |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 2 WDG A |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 2 WDG B |  | 30 | Reactor | Tertiary Connected
East Claydon | ECLA40 | 6 | 150 | -75 | SVC | 400
Elland | ELLA2 | 2 |  | 60 | Reactor | Tertiary Connected
Elstree | ELST40 | 1 |  | 200 | Reactor | 400
Elstree | ELST21 |  | 60 |  | SVC | Tertiary Connected
Elstree | ELST22 |  | 60 |  | SVC | Tertiary Connected
Elstree | ELST4A | 1 |  | 2000 | Series Reactor (bypassed) | 400
Enderby | ENDE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Enderby | ENDE40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Exeter | EXET10 | 1 | 56 |  | Mechanically Switched Capacitor | 132
Exeter | EXET40 | 1/2 | 51 |  | Mechanically Switched Capacitor | Tertiary Connected
Exeter | EXET40 | 3 | 150 | -75 | SVC | 400
Exeter | EXET41 | 5 | 150 | -75 | SVC | 400
Feckenham | FECK40 | 4 WDG A |  | 30 | Reactor | Tertiary Connected
Feckenham | FECK40 | 4 WDG B |  | 30 | Reactor | Tertiary Connected
Feckenham | FECK20 | 6 | 150 | -75 | SVC | 275
Fiddlers Ferry | FIDF21 | 1 |  | 750 | Series Reactor (bypassed) | 275
Fiddlers Ferry | FIDF22 | 2 |  | 750 | Series Reactor (bypassed) | 275
Fleet | FLEE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Fleet | FLEE11 | 2A | 52 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2B | 52 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2C | 52 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 3A WDG 1 |  | 30 | Reactor | Tertiary Connected
Fleet | FLEE12 | 3A WDG 2 |  | 30 | Reactor | Tertiary Connected
Fleet | FLEE11 | 4A WDG 1 |  | 30 | Reactor | Tertiary Connected
Fleet | FLEE12 | 4A WDG 2 |  | 30 | Reactor | Tertiary Connected
Flintshire Bridge | FLIB40 | 1 |  | 235 | Reactor | 400
Flintshire Bridge | FLIB40 | 2 |  | 235 | Reactor | 400
Flintshire Bridge | FLIB40 | 3 |  | 235 | Reactor | 400
Grain | GRAI4 | 1 |  | 200 | Reactor | 400
Grain | GRAI41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Grendon | GREN40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN40 | 4 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN12 | 1A | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN12 | 1B | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN12 | 1C | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN40 | 1 |  | 60 | Reactor | Tertiary Connected
Greystones | GRSB20 | 3 |  | 100 | Reactor | 275
Greystones | GRSA20 | 1 |  | 100 | Reactor | 275
Hams Hall | HAMH40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Hams Hall | HAMH40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 1 |  | 200 | Reactor | 400
Harker | HARK40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK40 | 3A | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK40 | 3B | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK21 | 2 | 150 |  | Mechanically Switched Capacitor | 275
Harker | HARK21 | 7 | 150 | -75 | SVC | 275
Harker | HARK22 | 8 | 150 | -75 | SVC | 275
Hurst | HURS20 | 2B | 150 |  | Mechanically Switched Capacitor | 275
Hurst | HURS2 | 2 |  | 60 | Reactor | Tertiary Connected
Hurst | HURS2 | 3 |  | 60 | Reactor | Tertiary Connected
Hurst | HURS20 | 4 |  | 100 | Reactor | 275
Hurst | HURS20 | 7 |  | 100 | Reactor | 275
Hurst | HURS20 | 1 |  | 100 | Reactor | 275
Hurst | HURS20 | 2A |  | 100 | Reactor | 275
Hutton | HUTT40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Hutton | HUTT41 | 1 |  | 2470 | Series Reactor (bypassed) | 400 (in parallel with series capacitor)
Hutton | HUTT41 | 2 |  | 2470 | Series Reactor (bypassed) | 400 (in parallel with series capacitor)
Indian Queens | INDQ40 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Indian Queens | INDQ10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ40 | 2 |  | 200 | Reactor | 400
Indian Queens | INDQ40 | 1 |  | 60 | Reactor | Tertiary Connected
Iron Acton | IROA1 | 6 | 45 |  | Mechanically Switched Capacitor | 132
Iron Acton | IROA20 |  | 60 |  | SVC | Tertiary Connected
Iron Acton | IROA20 |  | 60 |  | SVC | Tertiary Connected
Ironbridge | IRON40 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Ironbridge | IRON12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Ironbridge | IRON11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Iver | IVER2 | 1A |  | 60 | Reactor | Tertiary Connected
Iver | IVER2 | 3A |  | 60 | Reactor | Tertiary Connected
Iver | IVER4B | 5A |  | 55 | Reactor | Tertiary Connected
Iver | IVER4A | 6B |  | 55 | Reactor | Tertiary Connected
Jordanthorpe | JORD30 | 1 |  | 60 | Reactor | 33
Kearsley | KEAR11 | A | 52 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | B | 52 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | C | 52 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | 1 |  | 60 | Reactor | Tertiary Connected
Killingholme | KILL41 | 1 |  | 2750 | Series Reactor (bypassed) | 400
Kingsnorth | KINO4 | 3 |  | 200 | Reactor | 400
Kingsnorth | KINO4 | 4 |  | 200 | Reactor | 400
Kingsnorth | KINO4 | 1 WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO4 | 1 WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO4 | 2 WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO4 | 2 WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Kingsnorth | KINO41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Kirkby | KIBY11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 4 | 45 |  | Mechanically Switched Capacitor | 132
Kirkstall | KIRK20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Kirkstall | KIRK20 | 2 |  | 60 | Reactor | Tertiary Connected
Kirkstall | KIRK20 | 4 |  | 60 | Reactor | Tertiary Connected
Lackenby | LACK2 | A/B/C | 60 |  | Mechanically Switched Capacitor | Tertiary Connected
Lackenby | LACK2 | 1 | 100 |  | Reactor | 275
Laleham | LALE20 | 3 |  | 100 | Reactor | 275
Laleham | LALE20 | 1 |  | 100 | Reactor | 275
Laleham | LALE20 | 2 |  | 100 | Reactor | 275
Landulph | LAND10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Landulph | LAND40 | 1 |  | 200 | Reactor | 400
Landulph | LAND40 | 2 WDG A |  | 30 | Reactor | Tertiary Connected
Landulph | LAND40 | 2 WDG B |  | 30 | Reactor | Tertiary Connected
Landulph | LAND40 |  | 60 |  | SVC | Tertiary Connected
Legacy | LEGA40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Legacy | LEGA40 | 1 |  | 60 | Reactor | Tertiary Connected
Legacy | LEGA40 | 2 |  | 60 | Reactor | Tertiary Connected
Lister Drive | LISD20 | 1 |  | 100 | Reactor | 275
Lister Drive | LISD21 | 1 |  | 750 | Series Reactor | 275 (Birkenhead circuit)
Lovedean | LOVE40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Lovedean | LOVE40 | 3 |  | 60 | Reactor | Tertiary Connected
Lovedean | LOVE40 | 7 |  | 200 | Reactor | 400
Lovedean | LOVE40 | 1 |  | 200 | Reactor | 400
Lovedean | LOVE40 | 1 |  | 60 | Reactor | Tertiary Connected
Lovedean | LOVE40 | 4A | 150 | -75 | SVC | 400
Mannington | MANN10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 5 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN10 | 6 | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN40 | 1 | 150 | -75 | SVC | 400
Mannington | MANN41 | 2 | 150 | -75 | SVC | 400
Melksham | MELK10 | A | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK10 | B | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK10 | C | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK40 | 5 |  | 60 | Reactor | Tertiary Connected
Melksham | MELK40 | 6 |  | 60 | Reactor | Tertiary Connected
Melksham | MELK40 | 1 |  | 200 | Reactor | 400
Mill Hill | MILH2 | 1 |  | 60 | Reactor | Tertiary Connected
Mill Hill | MILH2 | 2 |  | 60 | Reactor | Tertiary Connected
Monk Fryston | MONF22 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Nechells | NECH2 | 4 |  | 60 | Reactor | Tertiary Connected
Nechells | NECH2 | 1 |  | 60 | Reactor | Tertiary Connected
Newcross | NEWX20 | 5 |  | 100 | Reactor | 275
Newcross | NEWX20 | 6 |  | 100 | Reactor | 275
Ninfield | NINF40 | 5 | 225 | -100 | SVC | 400
Ninfield | NINF40 | 6 | 150 | -84 | SVC | 400
Ninfield | NINF40 |  |  | 200 | Shunt Reactor | 400
Ninfield | NINF40 |  | 225 |  | Mechanically Switched Capacitor | 400
Norwich Trowse | NORW10 | A | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW10 | B | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW10 | C | 60 |  | Mechanically Switched Capacitor | 132
Nursling | NURS40 | 2 |  | 60 | Shunt Reactor | Tertiary Connected
Ocker Hill | OCKH20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Oldbury | OLDB10 | 2A/2B |  | 60 | Reactor | Tertiary Connected
Oldbury | OLDB20 |  | 60 |  | SVC | Tertiary Connected
Pelham | PELH41 | 3 |  | 200 | Reactor | 400
Pelham | PELH40 | 5 | 150 | -75 | SVC | 400
Pelham | PELH40 | 6 | 150 | -75 | SVC | 400
Pembroke | PEMB4 | 1 |  | 60 | Reactor | Tertiary Connected
Pembroke | PEMB4 | 2 |  | 60 | Reactor | Tertiary Connected
Penn | PENN20 |  | 60 |  | SVC | Tertiary Connected
Penrhos | PERH1 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Pentir | PENT40 | 2 |  | 200 | Reactor | 400
Pentir | PENT40 | 5 |  | 200 | Reactor | 400
Penwortham | PEWO4 | 6 |  | 60 | Reactor | Tertiary Connected
Pitsmoor | PITS32 | 1 |  | 60 | Reactor | 33
Pitsmoor | PITS32 | 2 |  | 60 | Reactor | 33
Pyle | PYLE20 |  | 60 |  | SVC | Tertiary Connected
Pyle | PYLE20 |  | 60 |  | SVC | Tertiary Connected
Port Ham | PORH11 | 2 |  | 60 | Reactor | 132
Port Ham | PORH12 | 4 |  | 60 | Reactor | 132
Rainhill | RAIN11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 4 | 45 |  | Mechanically Switched Capacitor | 132
Ratcliffe-On-Soar | RATS40 | 3 |  | 60 | Reactor | Tertiary Connected
Ratcliffe-On-Soar | RATS40 | 2 |  | 200 | Reactor | 400
Rayleigh | RAYL4 | 1 |  | 60 | Reactor | Tertiary Connected
Richborough | RICH41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Rochdale | ROCH10 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Rochdale | ROCH10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Rochdale | ROCH10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Sellindge | SELL40 | 1 | 150 | -150 | SVC | 400
Sellindge | SELL40 | 2 | 150 | -150 | SVC | 400
Sellindge | SELL41 | 1 |  | 1860 | Series Reactor (bypassed) | 400
Skelton Grange | SKLG10 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG10 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG10 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG20 | 6 | 150 |  | Mechanically Switched Capacitor | 275
Skelton Grange | SKLG20 | 3 |  | 100 | Reactor | 275
Spennymoor | SPEN40 | 1 |  | 60 | Reactor | Tertiary Connected
St Johns Wood | SJOW11 | A | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW11 | B | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW11 | C | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW40 | 2 |  | 200 | Reactor | 400
St Johns Wood | SJOW40 | 4 |  | 200 | Reactor | 400
St Johns Wood | SJOW20 | 1 |  | 60 | Reactor | Tertiary Connected
St Johns Wood | SJOW40 | 1 |  | 200 | Reactor | 400
St Johns Wood | SJOW20 | 1 | 150 | -106 | SVC | 275
St Johns Wood | SJOW20 | 3 | 150 | -106 | SVC | 275
Staythorpe | STAY41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW2 | 2 | 100 |  | Reactor | 275
Sundon | SUND41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Sundon | SUND42 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Sundon | SUND4 | 5 WDG 1 |  | 30 | Reactor | Tertiary Connected
Sundon | SUND4 | 5 WDG 2 |  | 30 | Reactor | Tertiary Connected
Sundon | SUND4 | 8 WDG 1 |  | 30 | Reactor | Tertiary Connected
Sundon | SUND4 | 8 WDG 2 |  | 30 | Reactor | Tertiary Connected
Swansea | SWAN12 | A | 60 |  | Mechanically Switched Capacitor | 132
Swansea | SWAN12 | B | 60 |  | Mechanically Switched Capacitor | 132
Swansea | SWAN12 | C | 60 |  | Mechanically Switched Capacitor | 132
Thorpe Marsh | THOM40 | 2 |  | 200 | Reactor | 400
Thorpe Marsh | THOM40 | 6 |  | 200 | Reactor | 400
Tottenham | TOTT2 | 3 |  | 100 | Reactor | 275
Tottenham | TOTT2 | 5 |  | 100 | Reactor | 275
Tottenham | TOTT2 | 1 |  | 100 | Reactor | 275
Tynemouth | TYNE20 | 1 |  | 60 | Reactor | Tertiary Connected
Uskmouth | USKM10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Walham | WALH40 | 1 | 57 |  | Mechanically Switched Capacitor | Tertiary Connected
Walham | WALH40 | 2 |  | 60 | Reactor | Tertiary Connected
Walham | WALH40 | 3 |  | 60 | Reactor | Tertiary Connected
Walham | WALH40 | 4 |  | 200 | Reactor | 400
Walpole | WALP11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP4 | 1 |  | 60 | Reactor | Tertiary Connected
Walpole | WALP4 | 2 |  | 60 | Reactor | Tertiary Connected
Walpole | WALP4 | 3 |  | 60 | Reactor | Tertiary Connected
Warley | WARL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Warley | WARL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Warley | WARL10 | 3 | 45 |  | Mechanically Switched Capacitor | 132
West Boldon | WBOL60 | 1 | 50 |  | Mechanically Switched Capacitor | 66
West Burton | WBUR40 | 1 |  | 200 | Reactor | 400
Uskmouth | USKM11 | 1 |  | 90 | Series Reactor | 132
West Burton | WBUR41 | 1 |  | 1500 | Series Reactor (bypassed) | 400
West Ham | WHAM40 | 4 | 225 |  | Mechanically Switched Capacitor | 400
West Ham | WHAM40 | 1 |  | 200 | Reactor | 400
West Melton | WMEL12 | 3A | 45 |  | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3B | 45 |  | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3C | 45 |  | Mechanically Switched Capacitor | 132
West Thurrock | WTHU41 | 1 |  | 2400 | Series Reactor (bypassed) | 400 (Littlebrook-Tilbury circuit)
West Thurrock | WTHU42 | 2 |  | 2400 | Series Reactor (bypassed) | 400 (Littlebrook-Tilbury circuit)
West Weybridge | WWEY2 | 1 |  | 100 | Reactor | 275
Whitegate | WHGA20 | 1 | 150 |  | Mechanically Switched Capacitor | 275
Whitegate | WHGA20 | 4A |  | 60 | Reactor | Tertiary Connected
Whitegate | WHGA20 | 4B |  | 60 | Reactor | Tertiary Connected
Willesden | WISD2 | 2B |  | 55 | Reactor | Tertiary Connected
Willesden | WISD2 | 3B WDG 1 |  | 27.5 | Reactor | Tertiary Connected
Willesden | WISD2 | 3B WDG 2 |  | 27.5 | Reactor | Tertiary Connected
Willington | WILE40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Willington | WILE40 | 8 | 150 | -75 | SVC | 400
Wimbledon | WIMB20 | 2 |  | 100 | Reactor | 275
Wimbledon | WIMB20 | 4 |  | 100 | Reactor | 275
Wimbledon | WIMB40 | 6 | 225 |  |  | 400
Wymondley | WYMO40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Wymondley | WYMO40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Wymondley | WYMO40 | 3 | 200 |  | Reactor | 400
Bolney | BOLN40 | 6 | 75 | 225 | SVC | 400
Richborough | RICH40 | 1 | 75 | 225 | SVC | 400

## B-4-1d
Table B.4.1d - Offshore Reactive Compensation Equipment, 2018/19 | [8 empty] | Back To Menu
OFTO | Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Tapping
Blue Transmission London Array Limited | London Array Offshore Wind Farm | SGT1A tertiary | SVC PLUS 1A | 50 | 50 | SVC | 13.9
" | " | SGT2A tertiary | SVC PLUS 2A | 50 | 50 | SVC | 13.9
" | " | SGT1B tertiary | SVC PLUS 1B | 50 | 50 | SVC | 13.9
" | " | SGT2B tertiary | SVC PLUS 2B | 50 | 50 | SVC | 13.9
" | " | SGT1A tertiary | MSR 1A | - | 50 | Shunt Reactor | 13.9
" | " | SGT2A tertiary | MSR 2A | - | 50 | Shunt Reactor | 13.9
" | " | SGT1B tertiary | MSR 1B | - | 50 | Shunt Reactor | 13.9
" | " | SGT2B tertiary | MSR 2B | - | 50 | Shunt Reactor | 13.9
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SALL10 | 1 | - | 30 - 60 | Shunt Reactor | 132 | 18 taps from 30 to 60 MVAr
" | " | SALL10 | 2 | - | 30 - 60 | Shunt Reactor | 132 | 18 taps from 30 to 60 MVAr
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAO10 | RCT1 | - | 64 | Shunt Reactor | 132
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABO10 | RCT1 | - | 40-80 | Shunt Reactor | 132
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON51 | 1 | - | 40 | Shunt Reactor | 13.9
" | " | GGON52 | 2 | - | 40 | Shunt Reactor | 13.9
" | " | GGON53 | 3 | - | 40 | Shunt Reactor | 13.9
" | " | GGON51 | 1 | 47.3 | - | MSC | 13.9
" | " | GGON52 | 2 | 47.3 | - | MSC | 13.9
" | " | GGON53 | 3 | 47.3 | - | MSC | 13.9
" | " | GGON51 | 1 | 50 | 50 | SVC | 13.9
" | " | GGON52 | 2 | 50 | 50 | SVC | 13.9
" | " | GGON53 | 3 | 50 | 50 | SVC | 13.9
" | " | GAOF30 | 1 | - | 30 | Shunt Reactor | 33
" | " | GAOF30 | 2 | - | 30 | Shunt Reactor | 33
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | SGT1 tertiary | SVC-1 | 50 | 50 | SVC | 13.9
" | " | SGT2 tertiary | SVC-2 | 50 | 50 | SVC | 13.9
" | " | SGT1 tertiary | MSR1A | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT1 tertiary | MSR1B | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT2 tertiary | MSR2A | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT2 tertiary | MSR2B | - | 55.4 | Shunt Reactor | 13.9
" | " | SGT1 tertiary | MSC1A | 30 | - | MSC | 13.9
" | " | SGT1 tertiary | MSC1B | 30 | - | MSC | 13.9
" | " | SGT2 tertiary | MSC2A | 30 | - | MSC | 13.9
" | " | SGT2 tertiary | MSC2B | 30 | - | MSC | 13.9
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW10 | 1 | - | 24 | Shunt Reactor | 132
" | " | BOSW30 | 1 | 5 | - | MSC | 33
" | " | BOSW30 | 2 | 5 | - | MSC | 33
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | - | - | - | - | - | -
TC Lincs OFTO Limited | Lincs Wind Farm | LINO10 | Reactor 1 | - | 40 | Shunt Reactor | 132
" | " | LINO10 | Reactor 2 | - | 40 | Shunt Reactor | 132
" | " | SGT1A/SGT1B tertiary | SVC Plus 1 | 50 | 50 | SVC | 13.9
" | " | SGT1A/SGT1B tertiary | MSR2 | - | 53.48 | Shunt Reactor | 13.9
" | " | SGT1A/SGT1B tertiary | MSC3 | 31.18 | - | MSC | 13.9
" | " | SGT1A/SGT1B tertiary | MSR4 | - | 53.48 | Shunt Reactor | 13.9
" | " | SGT1A/SGT1B tertiary | MSC5 | 31.18 | - | MSC | 13.9
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMO32 | Reactor 1 | - | 35 | Shunt Reactor | 33
" | " | ORMO32 | Reactor 2 | - | 35 | Shunt Reactor | 33
" | " | ORMO32 | Shunt Capacitor 1 | 15 | - | MSC | 33
" | " | ORMO32 | SVC 1 | 28 | 28 | SVC | 33
TC Robin Rigg OFTO Limited | Robin Rigg East & West Offshore Wind Farms | RORE11 | RREW10_Cap-1 | 18 |  | MSC | 132
" | " | RORE11 | RREW10_Reac-1 |  | 18 | Shunt Reactor | 132
" | " | RORW11 | RRWW10_Cap-1 | 18 |  | MSC | 132
" | " | RORW11 | RRWW10_Reac-1 |  | 18 | Shunt Reactor | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW10 | SVC 1 | 55 | 55 | SVC | 132
" | " | THAW10 | SVC 2 | 55 | 55 | SVC | 132
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | SGT1 tertiary | 13.9kV Reactor 1A | - | 30 | Shunt Reactor | 13.9
" | " | SGT2 tertiary | 13.9kV Reactor 2A | - | 30 | Shunt Reactor | 13.9
" | " | WDSO11 | Shunt Reactor 3 | - | 60 | Shunt Reactor | 155
" | " | WDSO12 | Shunt Reactor 4 | - | 60 | Shunt Reactor | 155
" | " | SGT1 tertiary | SVC1B | 50 | 50 | SVC | 13.9
" | " | SGT2 tertiary | SVC2B | 50 | 50 | SVC | 13.9
- | Humber Gateway Offshore Wind Farm | HUMO11 | SHR1 |  | 28.2 | Shunt Reactor | 132
- | " | SGT1 tertiary | SVC | 24 | 24 | SVC | 33
- | " | SGT1 tertiary | MSR1A |  | 28 | Shunt Reactor | 33
- | " | SGT1 tertiary | MSR1B |  | 28 | Shunt Reactor | 33
- | " | SGT1 tertiary | MSC1 | 25 |  | MSC | 33
- | " | HUMO12 | SHR2 |  | 28.2 | Shunt Reactor | 132
- | " | SGT2 tertiary | SVC | 24 | 24 | SVC | 33
- | " | SGT2 tertiary | MSR2A |  | 28 | Shunt Reactor | 33
- | " | SGT2 tertiary | MSR2B |  | 28 | Shunt Reactor | 33
- | " | SGT2 tertiary | MSC2 | 25 |  | MSC | 33
- | Westermost Rough Offshore Wind Farm | SGT1/SGT2 tertiary | Statcom1 | 25 | 25 | SVC | 33
- | " | SGT1/SGT2 tertiary | Statcom2 | 25 | 25 | SVC | 33
- | " | WERW11 | 1 |  | 50 | Shunt Reactor | 150
- | Dudgeon Offshore Wind Farm | DUDO10 | SHR1 |  | 70 | Shunt Reactor | 132
- | Dudgeon Offshore Wind Farm | DUDO10 | SHR2 |  | 70 | Shunt Reactor | 132
- | Dudgeon Offshore Wind Farm | DUDO31 | SVC1 | 118 | 118 | SVC | 33
- | Dudgeon Offshore Wind Farm | DUDO32 | SVC2 | 118 | 118 | SVC | 33
- | Burbo Bank Extension Offshore Wind Farm | BURB40 | C1 | 60 |  | MSC | 400
- | Burbo Bank Extension Offshore Wind Farm | BURB20 | R1 |  | 125 | Shunt Reactor | 220
- | Burbo Bank Extension Offshore Wind Farm | BURB40 | R2 |  | 67 | Shunt Reactor | 400
- | Burbo Bank Extension Offshore Wind Farm | BURB40 | SVS-9 | 15 | 15 | SVC | 13
- | Race Bank Offshore Wind Farm | RABO31 | STATCOM1 | -100 | -100 | SVC | 27
- | " | RABO32 | STATCOM1 | -100 | -100 | SVC | 27
- | " | RABO21 | SHR1 |  | 200 | Shunt Reactor | 220
- | " | RABO22 | SHR2 |  | 200 | Shunt Reactor | 220
- | " | RAOF2A | SHR1 |  | 90 | Shunt Reactor | 220
- | " | RAOF2B | SHR2 |  | 90 | Shunt Reactor | 220
- | Rampion Offshore Wind Farm | TWIN31 | SVC1 | 75 | 50 | Shunt Reactor | SGT1 33kV tertiary
- | " | TWIN32 | SVC2 | 75 | 50 | Shunt Reactor | SGT2 33kV tertiary
- | " | TWIN1A | SHR1 |  | 64 | Shunt Reactor | 150
- | " | TWIN1B | SHR2 |  | 64 | Shunt Reactor | 150
- | Galloper Onshore |  |  | 50 | 50 | SVC | 13.9
- | Galloper Onshore |  |  | 50 | 50 | SVC | 13.9
- | Galloper Onshore |  |  | 55.1 |  | Mechanically Switched Capacitor | 13.9
- | Galloper Onshore |  |  | 55.1 |  | Mechanically Switched Capacitor | 13.9
- | Galloper Onshore |  |  |  | 85 | Shunt Reactor | 132
- | Galloper Onshore |  |  |  | 85 | Shunt Reactor | 132

## B-4-2a
Table B.4.2a - SHE Transmission Reactive Compensation Equipment, 2019/20 to 2027/28 | [8 empty] | Back To Menu
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
DOUNREAY | Addition | 2022 | DOUN3Y | 3 |  | 90 | Shunt Reactor - SGT tertiary | 33
Finstown | Addition | 2022 | FINS3Y | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
ALYTH | Addition | 2024 | ALYT2 | 1 | 225 | 75 | SVC | 275
Melgarve | Addition | 2019 | MELG4J | 1 | 100 | 100 | STATCOM | 400
Melgarve | Addition | 2019 | MELG4K | 1 | 100 | 100 | STATCOM | 400
DOUNREAY | Addition | 2024 | DOUN3Z | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
Finstown | Addition | 2024 | FINS3Z | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
ALYTH | Addition | 2024 | ALYT2A | 1 | 100 |  | Mechanically Switched Capacitor | 275
Tummel | Addition | 2024 | TUMM2J | 1 | 100 |  | Mechanically Switched Capacitor | 275
Tummel | Addition | 2024 | TUMM2J | 1 | 225 | 75 | SVC | 275
ALYTH | Addition | 2027 | ALYT4J | 1 | 100 |  | Mechanically Switched Capacitor | 400
ALYTH | Removed | 2027 | ALYT2A | 1 | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | Addition | 2027 | ALYT4J | 1 | 225 | 75 | SVC | 400
ALYTH | Removed | 2027 | ALYT2 | 1 | 225 | 75 | SVC | 275

## B-4-2b
Table B.4.2b - SPT Reactive Compensation Equipment, 2019/20 to 2027/28 | [8 empty] | Back To Menu
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Bonnybridge | Addition | 2019 | BONN3U | 1 |  | 60 | REACTOR | 33
Bonnybridge | Addition | 2019 | BONN3V | 2 |  | 60 | REACTOR | 33
Shrubhill | Remove | 2019 | SHRU3- | 2 |  | 60 | REACTOR | 33
West George Street | Remove | 2019 | WGEO3- | 1 |  | 30 | REACTOR | 33
West George Street | Remove | 2019 | WGEO3- | 2 |  | 30 | REACTOR | 33
WISHAW | Remove | 2020 | WISH3- | 1 |  | 60 | REACTOR | 33
WISHAW | Addition | 2020 | WISH3W | 1 |  | 60 | REACTOR | 33
NNG OFFSHORE WIND FARM | Addition | 2022 | NNGA2- | 1 |  | 130 | REACTOR | 220
NNG OFFSHORE WIND FARM | Addition | 2022 | NNGB2- | 1 |  | 130 | REACTOR | 220

## B-4-2c
Table B.4.2c - NGET Reactive Compensation Equipment, 2019/20 to 2027/28 | [8 empty] | Back To Menu
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Lister Drive | Removed | 2020 | LISD21 | 1 | 750 |  | Series Reactor | 275 (Birkenhead circuit)
Killingholme | Addition | 2021 | KILL41 | 1 | 2750 |  | Series Reactor (bypassed) | 400
Rayleigh | Addition | 2022 | RAYL41 | 1 | 4000 |  | Series Reactor (bypassed) | 400 (Tilbury circuit)
Rayleigh | Addition | 2022 | RAYL41 | 2 | 4000 |  | Series Reactor (bypassed) | 400 (Coryton circuit)
Ninfield | Addition | 2024 | NINF40 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Carrington | Addition | 2023 | CARR41 | 1 | 2750 |  | Series Reactor (bypassed) | 400
Wimbledon | Addition | 2024 | WIMB40 | 2 |  | 225 | Shunt Reactor | 400
Hinkley Point | Addition | 2024 | HIKP41 | 1 | 2000 |  | Series Reactor (bypassed) | 400
Bolney | Addition | 2024 | BOLN40 | 9 | 80 | 75 | SVC | 400
Ninfield | Addition | 2024 | NINF40 | 9 | 75 | 75 | SVC | 400
Bridgwater | Removal | 2024 | BRWA2 |  | 60 | 0 | SVC | Tertiary Connected
Bolney | Addition | 2027 | BOLN40 | 8 | 225 |  | Mechanically Switched Capacitor | 400

## B-4-2d
Table B.4.2d - Indicative Offshore Reactive Compensation Equipment Changes, 2019/20 to 2027/28 | [8 empty] | Back To Menu
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
East Anglia 1 | Addition | 2019 | EAAW2 | 1 |  | 173 | Reactor | 220kV
East Anglia 1 | Addition | 2019 | EAAW3 | 2 |  | 173 | Reactor | 220kV
Neart na Gaoithe | Addition | 2022 | NNGA2- | 1 |  | 130 | Reactor | 220kV
Neart na Gaoithe | Addition | 2022 | NNGB2- | 2 |  | 130 | Reactor | 220kV