## Slide 1: GC0117
Antony Johnson
National Grid
April 2019

## Slide 2: Summary
The Defect
What are the implications of Regional Differences
When is a Generator caught by the requirements of the Grid Code
What Type of Connection Agreements apply
What other requirements apply
What is the relationship between Small, Medium and Large and Type A, B, C and D Power Generating Modules
What are the differences in the Grid Code requirements between Small, Medium and Large (Transmission Connected and Embedded)
How is consistency best achieved across GB
Options
What are the Implications and what needs to be considered
Expected Changes to the Grid Code
Retrospectivity
Examples / Costs – Discussion Points
Volumes
Next Steps
Current Progress & Next Steps

## Slide 3: The Defect
The Concept of Large, Medium and Small Power Stations was introduced at Vesting (Privatisation in 1990) being a cornerstone of the industry codes
They defined:-
    The Connection Process
    Charging Arrangements
    Technical Requirements
At vesting there were separate Grid Codes between England and Wales and Scotland
With the introduction of BETTA in 2005, regional differences were introduced such that the definition of Small, Medium and Large are different for each Transmission Area
RfG has removed the difference in technical requirements across GB but fundamental differences remain in the connection process, data requirements and the industry codes that apply.

## Slide 4
What are the implications of Regional Differences
With the introduction of RfG in 2018 the technical requirements are now based on whether the Power Generating Module is of Type, A, B, C or D not Power Station Size. This is common across the whole of GB.
    Type A – 800W – 1MW, Type B 1MW – 10MW, Type C 10MW – 50MW (all connected below 110kV)
    Type D – 50MW and above or connected at or above 110kV
The Connection Process and Charging arrangements however are still dependent upon the Large, Medium and Small criteria for which regional differences exist
Charging is a separate issue which is outside the scope of this workgroup.
A Large Power Station in SHE Transmission Area is classified as 10MW or above. A Large Power Station in England and Wales is classified as 100MW or above. These classifications apply irrespective of weather the Power Station is Embedded or directly connected.
As the CUSC and Grid Code apply to Large Power Stations it means a 10MW Embedded Power Station in SHE Transmission Area or Offshore will have to meet the applicable requirements of the Grid Code (including BC1 and BC2), the CUSC and have an agreement with National Grid whereas a 10MW Embedded Power Station in Scottish Power’s Transmission Area or in England and Wales will only require a connection with the DNO and have to meet the Distribution Code.

## Slide 5
Power Station Size – Definitions
Defined under the Grid Code
Based on Registered Capacity not CEC / TEC or any other Commercial Product
Large
  England and Wales – 100MW or Greater
  SPT’s - Transmission Area – 30 MW or greater
  SHETL – Transmission Area – 10MW or greater
  Offshore – Transmission Area – 10MW or greater
Medium
  Apply only in England and Wales – 50 MW or greater but less than 100MW
Small
  England and Wales – Less than 50MW
  SPT’s - Transmission Area – Less than 30MW
  SHETL – Transmission Area – Less than 10MW
  Offshore – Transmission Area – Less than 10MW

## Slide 6
When is a Generator caught by the requirements of the Grid Code
This is defined under the CUSC but in summary the following rules apply:-
The Generator is directly connected (irrespective of being Small, Medium or Large)
The Generator is Large (either Embedded or Directly connected)
The Generator is Embedded Medium or Small and applies for TEC
LEEMPS (License Exempt Embedded Medium Power Stations)
    LEEMPS are not CUSC parties and there is no contract between National Grid and Generators in respect of LEEMPS. DNO’s under CUSC however do have obligations in respect of LEEMPS
    LEEMPS have to meet specific requirements of the Grid Code in relation to data submission (PC.3.3) and Technical requirements (CC/ECC3.3) through obligations in the Distribution Code
    LEEMPS do not need to satisfy the requirements of the Balancing Codes or Operating Codes unlike BELLA’s.
    Any site specific requirements that National Grid require from a LEEMPS are placed in the agreement (Appendix E) between National Grid and the DNO which the DNO in turn places on the Generator.

## Slide 7
What Type of Connection Agreements apply
Bilateral Connection Agreement (BCA) – A CUSC Contract which applies between National Grid and any directly connected party irrespective of being Demand or Generation
Bilateral Embedded Generation Agreement (BEGA) – A CUSC Contract which applies between National Grid and any Embedded Generator who has applied for TEC. All Large Embedded Power Stations greater than 100MW must have a BEGA.
Any Embedded Generator under 100MW can apply for TEC if they so wish . In this case a BEGA would still be used.
Bilateral Exemptable Large Licence Exempt Generator Agreement (BELLA) apply only in Scotland and applicable to Large Power Stations under 100MW.
  BELLA’s do not have TEC
  They have to meet the requirements of the Grid Code applicable to Large
  In general they will need to meet the requirements of BC1 and BC2 (a requirement of the Bilateral Agreement) but are classed as Generating Units and not BM Parties for which the requirements are different.
LEEMPS – specific agreements do not exist in respect of LEEMPS – this is achieved through the BCA between National Grid and the DNO (Appendix E)

## Slide 8
What other Requirements Apply
Any Generator who owns a Power Station (irrespective of size) which is directly connected must be in the Wholesale Market (i.e. in the BM)
Any Generator who owns a Large Embedded Power station of 100MW or greater must also be in the Wholesale Market (i.e. in the BM).
Any Generator who owns an Embedded Power Station and less than 100MW can choose to be in the BM – this would mean they apply for TEC.
LEEMPS are not required to be in the BM (England and Wales only – 50 – 100MW)
BELLA’s as a condition of their Connection Agreement are required to meet the requirements of BC1 and BC2 but they are treated as Generating Units not BM Parties and therefore a form of BM subset.

## Slide 9
What is the relationship between Small, Medium and Large and Type A, B, C and D
A Small, Medium or Large Power Station is defined in the Grid Code with specific thresholds – see slide 5 –
There are regional differences between England and Wales, Scottish Power’s Transmission Area, SHE’s Transmission Area and Offshore.
Type A, Type B, Type C and Type D Power Generating Modules are defined in the Grid Code to the size of Power Generating Module. The thresholds between each are the same across GB and they define the technical requirements which is required of each module. There are no regional differences in GB between Type A – D Power Generating Modules.
A Small, Medium or Large Power Station could be made up of any combination of a Type A, Type B, Type C or Type D Power Generating Module.
If a Power Generating Module is connected at 110kV or above they are automatically classified as Type D.

## Slide 10
What are the differences in the Grid Code requirements between Small, Medium and Large
If a Power Station is directly connected there is very little difference between Small, Medium and Large other than a few minor data items and technical requirements - some minor differences apply in terms of how specific items are delivered – e.g. operational metering.
Embedded Large Power Stations
The effect of Regional differences (Scotland / England and Wales is significant) – i.e. a 10MW Power Station Embedded in the North of Scotland will have to meet the requirements of the Grid Code, CUSC, BSC, DCUSA and Distribution Code whereas a 10MW Embedded Power Station in England and Wales will only have to meet the requirements of the DCUSA and Distribution Code.
In summary however, a Large Embedded Power Station in England and Wales would have to meet the same requirements as a Large Embedded Power Station in Scotland.
In Scotland, Large Embedded Power Stations between 100 – 10MW (SHE) and 100MW – 30 MW (SPT) (BELLA’s) will be required to meet the requirements of the Grid Code as applicable to Large Power Stations which would generally include compliance with BC1 and BC2
Embedded Medium Power Stations
If they apply for TEC the requirements are similar to Large Embedded
If they become a LEEMPS only data and technical requirements apply under the PC and CC/ECC’s. There is no requirement to meet the OC’s or BC’s

## Slide 11
Grid Code Requirement | Directly Connected Small | Directly Connected Medium | Directly Connected Large
Planning Code | • | • | •
European Connection Conditions | • | • | •
European Compliance Processes | • | • | •
Operating Codes | • | • | •
Balancing Codes | • | • | •
Data Registration Code | • | • | •
What are the differences in the Grid Code requirements between Small, Medium and Large
(Transmission Connections)

## Slide 12: DRC Structural and Scheduled data differences – Transmission Connected Small, Medium and Large Power Stations (1)
DRC Schedule | Transmission Connected Small | Transmission Connected Medium | Transmission Connected Large
Schedule 1 – Power Generating Module and HVDC Data | • | • | •
Schedule 2 – Generating Planning Parameters |  | • (Part) | •
Schedule 3 – Large Power Station Outage Programmes, Output Useable and Flexibility Information |  |  | •
Schedule 4 – Large Power Station Droop and Response Data |  |  | •
Schedule 5 – Users System Data | • | • | •
Schedule 6 – Users Outage Information | • | • | •
Schedule 7 – Load Characteristics at Grid Supply Points |  |  | 
Schedule 8 – Data supplied by BM Participants | • | • | •
Schedule 9 – Data supplied by The Company to User’s | • | • | •

## Slide 13: DRC Structural and Scheduled data differences – Transmission Connected Small, Medium and Large Power Stations (2)
DRC Schedule | Transmission Connected Small | Transmission Connected Medium | Transmission Connected Large
Schedule 10 – Demand Profiles and Active Energy Data |  |  | 
Schedule 11 – Connection Point Data |  |  | 
Schedule 12 – Demand Control |  |  | 
Schedule 13 – Fault Infeed Data |  |  | 
Schedule 14 – Fault Infeed Data (Generators) | • | • | •
Schedule 15 – Mothballed Generating and HVDC Data | • | • | •
Schedule 16 – Black Start Information |  |  | •
Schedule 17 – Access Period Data |  |  | 
Schedule 18 – Offshore Transmission System Data |  |  | 
Schedule 19 – User Data File Structure Data | • | • | •

## Slide 14
What are the differences in the Grid Code requirements between Small, Medium and Large
(Embedded Connections)
Grid Code Requirement | Embedded Small | Embedded Small (BEGA) | LEEMPS | Embedded Medium (BEGA) | BELLA | Embedded Large
Planning Code | No | Part | Part as defined under PC3.3 | Yes | Yes | Yes
European Connection Conditions | No | ECC.6.5 (Note equivalent RfG requirements would be picked up under the D Code) | Part as defined under ECC3.3 | Yes | Except EDL | Yes
European Compliance Processes | No | Yes | No | Yes | Yes | Yes
Operating Codes | No | Part | No | Yes | Yes | Yes
Balancing Codes | No | Only in respect of them operating as a BM Participant | No | Part | BC1/2 apply only in respect of Generating Units not BM Units BC3 does not apply | Yes
Data Registration Code | No | Only in respect of them operating as a BM Participant | As required under PC | Yes | Yes | Yes

## Slide 15
How is consistency best achieved across GB
To adopt a consistent set of thresholds for Large, (Medium and) Small across GB.
The preferred approach is to define two new thresholds between Large and Small with Medium being removed? – Several options are under consideration – see next slide
This would apply across the whole of GB
LEEMPS would/could be removed.
Code changes are believed to be minimal as most changes are made to the definitions between Large, (Medium) and Small

## Slide 16
Options
Option | Small | Medium | Large
Option 1 | Less than 10MW | N/A | 10MW and greater
Option 2 | Less than 30MW | N/A | 30MW and greater
Option 3 | Less than 50MW | N/A | 50MW and greater
Option 4 | Less than 100MW | N/A | 100MW and greater
Option 1 Increases visibility to the ESO, reduces Balancing Costs and enables greater use of services from
Smaller Players in a more holistic way. It will increase costs for the ESO, DNO’s and Generators with
respect to agreements and metering issues
Option 4 Reduces visibility to the ESO, increases Balancing Costs and reduces the ability to utilise services
from Smaller Players unless they choose to participate in the BM. It will reduce costs for the ESO, DNO’s
and Generators with respect to agreements and metering issues
Options 2 and 3 are a mix of Options 1 and 4 but are not necessarily the cheapest or most efficient.

## Slide 17
What are the Implications and What needs to be considered
Changes to the Grid Code
Retrospectivity
Volumes involved for each Option
Costs – Both to Generators and the ESO/DNO’s
Benefits

## Slide 18
Expected Changes to the Grid Code
Irrespective of the Option eventually selected, Grid Code and Distribution Code changes are expected to be minimal.
Medium Power Stations would be removed including LEEMPS
Data requirements would be consistent across the whole of GB (Structural, Scheduled and Real Time)
The BELLA Approach would effectively be applied across the whole of GB – Options 1 – 3 only)
Option 4 simply sets the threshold between Large and Small at 100MW
Any Plant which is 100MW or greater or directly connected would have to be in the BM
Any Plant which is Large and less than 100MW (Options 1 – 3 only) would be treated in the same way as a BELLA unless they choose to apply for TEC in which case they would become a BEGA – This is the choice of the Generator
In summary, the Existing Grid Code requirements would apply other than removal of Medium Power Stations and changes to the definitions
Consequential changes to other Industry Codes including the Distribution Code would need to be assessed.

## Slide 19
Retrospectivity
It is envisaged that these requirements could apply retrospectively
There would be no requirement for existing plant to meet the technical requirements of RfG however they would be required to satisfy the requirements of the other relevant parts of the Grid Code (e.g. Planning Code, Operating Codes, Balancing Codes and DRC). A specific carve out would however be required for existing generators who are not currently required to satisfy the requirements of the Connection Conditions.
There will be costs upon currently Small Power Stations who subsequently become Large Power Stations other than Option 3 and 4
There will also be costs for current Medium Power Stations who become Large though these are expected to be more limited.

## Slide 20
What would an Embedded Small Power Station have to do if in the future it became an Embedded Large Power Station
Satisfy the applicable requirements of the Grid Code and sign CUSC
Comply with the requirements of the Planning Code, Operating Codes, Connection Conditions or European Connection Conditions (as applicable), Compliance Processes or European Compliance Processes, Balancing Code 1 & 2 and Data Registration Code.
Compliance with the Connection Conditions for pre RfG plant is expected to be a real issue as they are generally exempt from these requirements. Some form of exemption is likely here other then in respect of CC.6.5 as it would otherwise make a number of projects uneconomic. Compliance is also expected to be an issue.
The main additional requirements would be:
    Signature to the CUSC
    Comply with the applicable requirements of the Grid Code
    New Connection Agreements for existing Small Parties caught by the New thresholds
    Submission of Static, Scheduled and Real time data
    Mechanisms of receiving real time data
    Some areas of synergy could be developed by identifying those obligations that such Generators have to provide under the Distribution Code

## Slide 21
Example – Comparison between a 40MW Embedded Power Station in England and Wales and a 40MW Embedded Power Station in Scotland
Requirement | 40MW Embedded Power Station in E&W | 40MW Embedded Power Station in Scotland | Cost of making changes
CUSC Signatory | No | Yes | To be discussed – Different options and conditions apply
Comply with Grid Code | No | Yes | 
Planning Code Data Submissions | No | Yes | 
Connection Conditions Inc. Control Telephony, Operational metering and EDT | No | Yes | 
Compliance Processes | No | Yes | 
Operating Codes | No | Yes | 
Balancing Codes 1 and 2 | No | Yes | 
Data Registration Code | No | Yes | 

## Slide 22
Volumes
Further information to be provided

## Slide 23: Next Steps
Ensure Stakeholders are comfortable with the proposed approach
Establish individual costs
Establish Benefits
Complete Cost Benefit Analysis
Establish overall most economic and efficient option
Finalise preferred option and develop legal text changes