## Slide 1
GC0096 Electricity Storage
Grid Code Requirements
Workgroup 4
10/04/2017

## Slide 2: Agenda
Definitions
Technical Requirements
  Confirm onshore
  Discuss offshore
  Flywheels/Supercapacitors – in or out of scope?
Next steps

## Slide 3: Definitions hierarchy – Standalone Electricity Storage Installations
Electricity Storage Owner
Onshore Electricity Storage Module
Offshore Electricity Storage Module
Synchronous Electricity Storage Unit
Non-synchronous Electricity Storage Unit
Synchronous Electricity Storage Unit
Non-synchronous Electricity Storage Unit
Power Station
Key:
Existing definition requiring changes
New definition

## Slide 4: Definitions hierarchy – Co-located Electricity Storage Installations
Onshore Electricity Storage Module
Offshore Electricity Storage Module
Power Station
Key:
Existing definition requiring changes
New definition
Onshore Generating Unit
Offshore Generating Unit
Non-synch. Electricity Storage Unit [?]
Non-synch. Electricity Storage Unit
Synch. Electricity Storage Unit
Non-synch. Electricity Storage Unit [?]
Non-synch. Electricity Storage Unit
Synch. Electricity Storage Unit

## Slide 5: Definitions hierarchy – Co-located Electricity Storage Installations Cont’d
Non-synch. Electricity Storage Unit
Power Station
Key:
Existing definition requiring changes
New definition
Power Park Module
Onshore Power Park Module
Offshore Power Park Module
Non-synch. Electricity Storage Unit
Non-synch. Electricity Storage Unit
Non-synch. Electricity Storage Unit
Offshore Electricity Storage Module
Onshore Electricity Storage Module

## Slide 6: Definitions – proposed text
Electricity Storage is the conversion of electrical energy into a form of energy which can be stored, the storing of that energy, and the subsequent reconversion of that energy back into electrical energy [RJW – “…in a controllable manner” or; EL – “…at a controlled power level”]
Electricity Storage Owner means a natural or legal entity owning an Electricity Storage Module
Power Station An installation comprising one or more Generating Units or Power Park Modules or Electricity Storage Modules (even where sited separately) owned and/or controlled by the same Generator or Electricity Storage Owner, which may reasonably be considered as being managed as one Power Station.
Power Park Module Any Onshore Power Park Module or Offshore Power Park Module or Onshore Electricity Storage Module or Offshore Electricity Storage Module

## Slide 7: Definitions – proposed text
Offshore Electricity Storage Module A collection of Synchronous Electricity Storage Units or Non-Synchronous Electricity Storage Units joined together by cables forming part of a User System with a single point of connection to an Offshore Transmission System. The connection to an Offshore Transmission System may include a DC Converter.
Onshore Electricity Storage Module A collection of Synchronous Electricity Storage Units or Non-Synchronous Electricity Storage Units, joined together by a System with a single electrical point of connection directly to the Onshore Transmission System (or User System if Embedded).
Synchronous Electricity Storage Unit Any Synchronous Generating Unit which is capable of importing or exporting electricity.
Non-Synchronous Electricity Storage Unit An Electricity Storage Unit that is capable of importing or exporting electricity which is not an Synchronous Electricity Storage Unit.

## Slide 8: Electricity Storage technologies map to Grid Code requirements
Battery
Satisfies requirements of CC.6.3.2 – CC.6.3.15
Compressed Air
Satisfies requirements of CC.6.3.2 – CC.6.3.15
Flywheels (provides inertia only – no real Power Injection)
Will not satisfy the requirements of CC.6.3.2 – CC.6.3.15 in entirety – how do we manage this (see later slides)?
Supercapacitors (provides a short burst of power only)
Will struggle to satisfy longer term frequency response requirements – how do we manage this (see later slides)
Simulations
These requirements in

## Slide 9: Electricity Storage Unit Types
ESU – Non Synchronous
Generating Unit – Battery
ESU – Synchronous
Generating Unit –
Synch. Generator
ESU – Synchronous
Generating Unit – Flywheel
ESU – Non Synchronous
Generating Unit - Supercapacitor

## Slide 10
Configurations and Definitions
Series connected Storage Devices with HVDC connection
Grid Entry
Points
(As per HVDC CC.6.3.2 – CC.6.3.16)
Power Station
SD
SD
SD
SD
SD
Electricity Storage Unit
(Non Synchronous Generating Unit)
Electricity Storage Module
Onshore
Transmission System
SD
SD
SD
SD
SD
Electricity Storage Module
Electricity Storage Unit
(Non Synchronous Generating Unit)
Storage Devices in series
Supercapacitors may struggle with these requirements

## Slide 11
Configurations and Definitions
Parallel connected Electricity Storage Units
Grid Entry
Points
(As per PPM CC.6.3.2 – CC.6.3.15)
Power Station
Electricity
Storage Module
Electricity
Storage Module
ESU’s in parallel
ESU’s in parallel
Electricity Storage Unit
(Non Synchronous Generating Unit)
ESU
ESU
ESU
ESU
ESU
ESU
ESU
ESU
ESU
ESU
ESU
ESU
Electricity Storage Unit
(Non Synchronous Generating Unit)
Onshore
Transmission System
Supercapacitors may struggle with these requirements

## Slide 12
Configurations and Definitions
Electricity Storage Units within a
New or existing Power Station with a direct connection
Grid Entry
Point
Transmission System
Power Station
Electricity
Storage Module
Electricity Storage Unit
(Non Synchronous Generating Unit)
Synchronous Generating Units
ESU
ESU
ESU
ESU
ESU
ESU
Grid Entry
Point
(As per PPM CC.6.3.2 – CC.6.3.15)
(As per Synchronous Generators CC.6.3.2 – CC.6.3.15)
Supercapacitors and Flywheels may struggle with these requirements

## Slide 13
Configurations and Definitions
Electricity Storage Units Integrated within a
Existing Power Station
Synchronous Generating Units
Transmission System
Power Station
Electricity
Storage Module
Electricity Storage Unit
(Non Synchronous Generating Unit)
ESU
ESU
ESU
ESU
ESU
ESU
(As per PPM CC.6.3.2 – CC.6.3.15) – Reactive Capability required at Grid Entry Point
Grid Entry
Points
(As per Synchronous CC.6.3.2 – CC.6.3.16)
Supercapacitors and flywheels may struggle with these requirements
Under the current Grid Code, the requirements would generally apply at the Generating Unit terminals.

## Slide 14
Configurations and Definitions
Electricity Storage Units Integrated within a
New Power Station post EU Code
Synchronous Generating Units
Transmission System
Power Station
Electricity Storage Unit
(Non Synchronous Generating Unit)
ESU
ESU
ESU
ESU
ESU
ESU
Grid Entry
Points
(As per RfG post May 2018
Going forward should consideration be given to considering an Electricity Storage Module as part of a Synchronous Generating Module – ie the European Term
This approach could
favour other storage technologies and provide benefits to both the Generator and Network Operator – Would require limits to ratio of storage units to Synchronous Generator capacity.
Requirements would be on the Maximum capacity of the complete synchronous Power Generating Module eg if Pmax was 500MW on the Synch Gen and Pmax on the Storage unit was 50MW the requirements at the connection point would be on a Pmax of 550MW The approach would assume the installation forms part of one power station and there is no separate ownership

## Slide 15
Configurations and Definitions
Electricity Storage Units connected to a Synchronous
Power Generating Module – EU Code – See Previous Slide
Transmission System
Power Station
Synchronous Power Generating Module
Electricity Storage Units
(Non Synchronous Generating Units)
ESU
ESU
ESU
ESU
ESU
ESU
Grid Entry
Point
Going forward should consideration be given to considering an Electricity Storage Module as part of a Synchronous Generating Module – ie the European Term

## Slide 16
Configurations and Definitions
Electricity Storage Module and Power Park Modules
Electricity Storage Unit
(Non Synchronous Generating Unit)
Power Park Unit
(Non Synchronous Generating Unit)
Power Station
Electricity
Storage
Module
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
Power Park Module
ESU
ESU
ESU
ESU
ESU
ESU
Grid Entry
Point
Transmission System
(As per PPM
CC.6.3.2 – CC.6.3.15)
Grid Entry
Point
(ESM PPM CC.6.3.2 – CC.6.3.15)

## Slide 17
Configurations and Definitions
Electricity Storage Units Integrated into a
Power Park Module
Power Station
Grid Entry
Point
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
Power Park Module
Electricity Storage
Unit
(Non Synchronous Generating Unit)
Power Park Unit
(Non Synchronous Generating Unit)
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
PPU
ESU
ESU
Transmission System
(As per PPM
CC.6.3.2 – CC.6.3.15)

## Slide 18
Configurations and Definitions
Offshore Connections
OFTO
Interface Points
PPU
PPU
PPU
PPU
Offshore Power Park Module
Electricity Storage
Unit
(Non Synchronous Generating Unit)
Power Park Unit
(Non Synchronous Generating Unit)
PPU
PPU
PPU
PPU
Offshore Power Station
Transmission System
ESU
ESU
(As per PPM
CC.6.3.2 – CC.6.3.15)

## Slide 19
Configurations and Definitions
Electricity Storage Units Connected to a
Distribution System
Transmission System
Electricity Storage Module
Distribution
Other Users
Power Station
Electricity Storage
Unit
(Non Synchronous Generating Unit)
User System Entry
Point
ESU
ESU
ESU
ESU
ESU
ESU
(As per PPM
CC.6.3.2 – CC.6.3.15)

## Slide 20: Data / Modelling and Simulation
Updates may be required to the Planning Code and Data Registration Code for modelling purposes
The data / model supplied should provide a true and accurate representation of the plant as built
Synchronous Generating Unit data which is part of a Electricity Storage Module would generally be treated the same way as Synchronous Generating Unit – Data generally well understood
Non Synchronous Electricity Storage Modules connected via a Power Electronic Converter, the data requirements need further thought. This would be a combination of Power Park Module data and HVDC Converter data
Additional running data may also be required such operating characteristics e.g. maximum charge rate; maximum discharge rate (a future mod, if needed?)
Notes: Introduction slide.

## Slide 21
Next Steps