## Response
Frequency Deviation (Hz) | Primary () |  | Secondary () |  | High () |  |  | kW or MW? |  | Active Power (kW)
| Contracted | Actual | Contracted | Actual | Contracted | Actual |  | Active Power (MW) |  | Active Power (MW)
0.1Hz | 1 | 0.999 | 1 |  | -1 | -1.001
0.2Hz | 2 | 2.001 | 2 |  | -2 | -2.002
0.3Hz | 3 | 3.017 | 3 |  | -3 | -3.02
0.4Hz | 4 | 4.033 | 4 |  | -4 | -4.038
0.5Hz | 5 | 5.046 | 5 | 5.046 | -5 | -5.046
Frequency Deviation (Hz) |  | Primary () |  |  | Secondary () |  |  | High ()
| Tolerance | Contracted | Actual | Error % | Contracted | Actual | Error % | Contracted | Actual | Error %
0.1Hz | 5%/-4% | 1 | 0.999 | -0.1 | 1 | 0 | -100 | -1 | -1.001 | 0.1
0.2Hz | 5%/-3% | 2 | 2.001 | 0.05 | 2 | 0 | -100 | -2 | -2.002 | 0.1
0.3Hz | 5%/-2% | 3 | 3.017 | 0.56667 | 3 | 0 | -100 | -3 | -3.02 | 0.66667
0.4Hz | 5%/-1% | 4 | 4.033 | 0.825 | 4 | 0 | -100 | -4 | -4.038 | 0.95
0.5Hz | 5%/-0% | 5 | 5.046 | 0.92 | 5 | 5.046 | 0.92 | -5 | -5.046 | 0.92
Dynamic Analysis Tool
Instructions
1.) Enter the contracted response of power in the green cells of this tab under primary, secondary and high. Make sure the contracted response is written in the same units as the power data recorded in the raw file.
2.) Select the units what the raw data was measured in from the drop down cell above. Select either MW or KW.
3.) All data in this tool should be entered in green cells only. Do not edit pink cells.

## Test 1.1 Single Asset
Time (s) | Frequency (Hz) | Active Power (MW)
0 | 50 | 0 | Asset/s Name/Ref
0.1 | 50 | 0 |  |  |  |  | Frequency Change
0.2 | 50 | 0 |  |  |  |  | Primary Start
0.3 | 50 | 0 | NewVol1 |  |  |  | Secondary Start
0.4 | 50 | 0 |  |  |  |  | 30
0.5 | 50 | 0 | Time Value at Which Frequency Changes |  |  |  | 30
0.6 | 50 | 0 |  |  |  | $C$402 | 40
0.7 | 50 | 0 |  |  |  | $C$602 | 40
0.8 | 50 | 0 | 30 |  |  | $C$18301 | 60
0.9 | 50 | 0 |  |  | primary | 1.0094 | 60
1 | 50 | 0 | Primary Start |  | secondary | 1.0094 | 40
1.1 | 50 | 0 |  |  |  |  | 60
1.2 | 50 | 0 | 40 |  |  |  | 2 Second Limit
1.3 | 50 | 0 |  |  |  |  | 32
1.4 | 50 | 0 | Secondary Start | pre-Average | 0 |  | 32
1.5 | 50 | 0 |  | (edit range to average 10s before frequency change)
1.6 | 50 | 0 | 60
1.7 | 50 | 0
1.8 | 50 | 0 | Secondary End
1.9 | 50 | 0
2 | 50 | 0 | 1829.9
2.1 | 50 | 0
2.2 | 50 | 0 | Primary Response
2.3 | 50 | 0
2.4 | 50 | 0 | 1.0094
2.5 | 50 | 0
2.6 | 50 | 0 | Secondary Response
2.7 | 50 | 0
2.8 | 50 | 0 | 1.0094
2.9 | 50 | 0
3 | 50 | 0
3.1 | 50 | 0
3.2 | 50 | 0
3.3 | 50 | 0
3.4 | 50 | 0
3.5 | 50 | 0
3.6 | 50 | 0
3.7 | 50 | 0
3.8 | 50 | 0
3.9 | 50 | 0
4 | 50 | 0
4.1 | 50 | 0
4.2 | 50 | 0
4.3 | 50 | 0
4.4 | 50 | 0
4.5 | 50 | 0
4.6 | 50 | 0
4.7 | 50 | 0
4.8 | 50 | 0
4.9 | 50 | 0
5 | 50 | 0
5.1 | 50 | 0
5.2 | 50 | 0
5.3 | 50 | 0
5.4 | 50 | 0
5.5 | 50 | 0
5.6 | 50 | 0
5.7 | 50 | 0
5.8 | 50 | 0
5.9 | 50 | 0
6 | 50 | 0
6.1 | 50 | 0
6.2 | 50 | 0
6.3 | 50 | 0
6.4 | 50 | 0
6.5 | 50 | 0
6.6 | 50 | 0
6.7 | 50 | 0
6.8 | 50 | 0
6.9 | 50 | 0
7 | 50 | 0
7.1 | 50 | 0
7.2 | 50 | 0
7.3 | 50 | 0
7.4 | 50 | 0
7.5 | 50 | 0
7.6 | 50 | 0
7.7 | 50 | 0
7.8 | 50 | 0
7.9 | 50 | 0
8 | 50 | 0
8.1 | 50 | 0
8.2 | 50 | 0
8.3 | 50 | 0
8.4 | 50 | 0
8.5 | 50 | 0
8.6 | 50 | 0
8.7 | 50 | 0
8.8 | 50 | 0
8.9 | 50 | 0
9 | 50 | 0
9.1 | 50 | 0
9.2 | 50 | 0
9.3 | 50 | 0
9.4 | 50 | 0
9.5 | 50 | 0
9.6 | 50 | 0
9.7 | 50 | 0
9.8 | 50 | 0
9.9 | 50 | 0
10 | 50 | 0
10.1 | 50 | 0
10.2 | 50 | 0
10.3 | 50 | 0
10.4 | 50 | 0
10.5 | 50 | 0
10.6 | 50 | 0
10.7 | 50 | 0
10.8 | 50 | 0
10.9 | 50 | 0
11 | 50 | 0
11.1 | 50 | 0
11.2 | 50 | 0
11.3 | 50 | 0
11.4 | 50 | 0
11.5 | 50 | 0
11.6 | 50 | 0
11.7 | 50 | 0
11.8 | 50 | 0
11.9 | 50 | 0
12 | 50 | 0
12.1 | 50 | 0
12.2 | 50 | 0
12.3 | 50 | 0
12.4 | 50 | 0
12.5 | 50 | 0
12.6 | 50 | 0
12.7 | 50 | 0
12.8 | 50 | 0
12.9 | 50 | 0
13 | 50 | 0
13.1 | 50 | 0
13.2 | 50 | 0
13.3 | 50 | 0
13.4 | 50 | 0
13.5 | 50 | 0
13.6 | 50 | 0
13.7 | 50 | 0
13.8 | 50 | 0
13.9 | 50 | 0
14 | 50 | 0
14.1 | 50 | 0
14.2 | 50 | 0
14.3 | 50 | 0
14.4 | 50 | 0
14.5 | 50 | 0
14.6 | 50 | 0
14.7 | 50 | 0
14.8 | 50 | 0
14.9 | 50 | 0
15 | 50 | 0
15.1 | 50 | 0
15.2 | 50 | 0
15.3 | 50 | 0
15.4 | 50 | 0
15.5 | 50 | 0
15.6 | 50 | 0
15.7 | 50 | 0
15.8 | 50 | 0
15.9 | 50 | 0
16 | 50 | 0
16.1 | 50 | 0
16.2 | 50 | 0
16.3 | 50 | 0
16.4 | 50 | 0
16.5 | 50 | 0
16.6 | 50 | 0
16.7 | 50 | 0
16.8 | 50 | 0
16.9 | 50 | 0
17 | 50 | 0
17.1 | 50 | 0
17.2 | 50 | 0
17.3 | 50 | 0
17.4 | 50 | 0
17.5 | 50 | 0
17.6 | 50 | 0
17.7 | 50 | 0
17.8 | 50 | 0
17.9 | 50 | 0
18 | 50 | 0
18.1 | 50 | 0
18.2 | 50 | 0
18.3 | 50 | 0
18.4 | 50 | 0
18.5 | 50 | 0
18.6 | 50 | 0
18.7 | 50 | 0
18.8 | 50 | 0
18.9 | 50 | 0
19 | 50 | 0
19.1 | 50 | 0
19.2 | 50 | 0
19.3 | 50 | 0
19.4 | 50 | 0
19.5 | 50 | 0
19.6 | 50 | 0
19.7 | 50 | 0
19.8 | 50 | 0
19.9 | 50 | 0
20 | 50 | 0
20.1 | 50 | 0
20.2 | 50 | 0
20.3 | 50 | 0
20.4 | 50 | 0
20.5 | 50 | 0
20.6 | 50 | 0
20.7 | 50 | 0
20.8 | 50 | 0
20.9 | 50 | 0
21 | 50 | 0
21.1 | 50 | 0
21.2 | 50 | 0
21.3 | 50 | 0
21.4 | 50 | 0
21.5 | 50 | 0
21.6 | 50 | 0
21.7 | 50 | 0
21.8 | 50 | 0
21.9 | 50 | 0
22 | 50 | 0
22.1 | 50 | 0
22.2 | 50 | 0
22.3 | 50 | 0
22.4 | 50 | 0
22.5 | 50 | 0
22.6 | 50 | 0
22.7 | 50 | 0
22.8 | 50 | 0
22.9 | 50 | 0
23 | 50 | 0
23.1 | 50 | 0
23.2 | 50 | 0
23.3 | 50 | 0
23.4 | 50 | 0
23.5 | 50 | 0
23.6 | 50 | 0
23.7 | 50 | 0
23.8 | 50 | 0
23.9 | 50 | 0
24 | 50 | 0
24.1 | 50 | 0
24.2 | 50 | 0
24.3 | 50 | 0
24.4 | 50 | 0
24.5 | 50 | 0
24.6 | 50 | 0
24.7 | 50 | 0
24.8 | 50 | 0
24.9 | 50 | 0
25 | 50 | 0
25.1 | 50 | 0
25.2 | 50 | 0
25.3 | 50 | 0
25.4 | 50 | 0
25.5 | 50 | 0
25.6 | 50 | 0
25.7 | 50 | 0
25.8 | 50 | 0
25.9 | 50 | 0
26 | 50 | 0
26.1 | 50 | 0
26.2 | 50 | 0
26.3 | 50 | 0
26.4 | 50 | 0
26.5 | 50 | 0
26.6 | 50 | 0
26.7 | 50 | 0
26.8 | 50 | 0
26.9 | 50 | 0
27 | 50 | 0
27.1 | 50 | 0
27.2 | 50 | 0
27.3 | 50 | 0
27.4 | 50 | 0
27.5 | 50 | 0
27.6 | 50 | 0
27.7 | 50 | 0
27.8 | 50 | 0
27.9 | 50 | 0
28 | 50 | 0
28.1 | 50 | 0
28.2 | 50 | 0
28.3 | 50 | 0
28.4 | 50 | 0
28.5 | 50 | 0
28.6 | 50 | 0
28.7 | 50 | 0
28.8 | 50 | 0
28.9 | 50 | 0
29 | 50 | 0
29.1 | 50 | 0
29.2 | 50 | 0
29.3 | 50 | 0
29.4 | 50 | 0
29.5 | 50 | 0
29.6 | 50 | 0
29.7 | 50 | 0
29.8 | 50 | 0
29.9 | 50 | 0
30 | 49.5 | 0
30.1 | 49.5 | 0.0006
30.2 | 49.5 | 0.0052
30.3 | 49.5 | 0.282
30.4 | 49.5 | 0.7314
30.5 | 49.5 | 0.9646
30.6 | 49.5 | 1.0216
30.7 | 49.5 | 1.0208
30.8 | 49.5 | 1.0202
30.9 | 49.5 | 1.02
31 | 49.5 | 1.02
31.1 | 49.5 | 1.02
31.2 | 49.5 | 1.02
31.3 | 49.5 | 1.02
31.4 | 49.5 | 1.02
31.5 | 49.5 | 1.02
31.6 | 49.5 | 1.02
31.7 | 49.5 | 1.02
31.8 | 49.5 | 1.02
31.9 | 49.5 | 1.02
32 | 49.5 | 1.02
32.1 | 49.5 | 1.02
32.2 | 49.5 | 1.02
32.3 | 49.5 | 1.02
32.4 | 49.5 | 1.02
32.5 | 49.5 | 1.02
32.6 | 49.5 | 1.02
32.7 | 49.5 | 1.02
32.8 | 49.5 | 1.02
32.9 | 49.5 | 1.02
33 | 49.5 | 1.02
33.1 | 49.5 | 1.02
33.2 | 49.5 | 1.02
33.3 | 49.5 | 1.02
33.4 | 49.5 | 1.02
33.5 | 49.5 | 1.02
33.6 | 49.5 | 1.02
33.7 | 49.5 | 1.02
33.8 | 49.5 | 1.0198
33.9 | 49.5 | 1.0198
34 | 49.5 | 1.0198
34.1 | 49.5 | 1.02
34.2 | 49.5 | 1.02
34.3 | 49.5 | 1.0198
34.4 | 49.5 | 1.0198
34.5 | 49.5 | 1.0198
34.6 | 49.5 | 1.0198
34.7 | 49.5 | 1.0198
34.8 | 49.5 | 1.0198
34.9 | 49.5 | 1.0198
35 | 49.5 | 1.0198
35.1 | 49.5 | 1.0192
35.2 | 49.5 | 1.0176
35.3 | 49.5 | 1.0164
35.4 | 49.5 | 1.0162
35.5 | 49.5 | 1.0162
35.6 | 49.5 | 1.0158
35.7 | 49.5 | 1.0156
35.8 | 49.5 | 1.0156
35.9 | 49.5 | 1.0156
36 | 49.5 | 1.0156
36.1 | 49.5 | 1.0154
36.2 | 49.5 | 1.0152
36.3 | 49.5 | 1.015
36.4 | 49.5 | 1.015
36.5 | 49.5 | 1.015
36.6 | 49.5 | 1.015
36.7 | 49.5 | 1.015
36.8 | 49.5 | 1.0148
36.9 | 49.5 | 1.0148
37 | 49.5 | 1.0148
37.1 | 49.5 | 1.0146
37.2 | 49.5 | 1.0146
37.3 | 49.5 | 1.0144
37.4 | 49.5 | 1.0144
37.5 | 49.5 | 1.0142
37.6 | 49.5 | 1.0142
37.7 | 49.5 | 1.0142
37.8 | 49.5 | 1.0142
37.9 | 49.5 | 1.014
38 | 49.5 | 1.014
38.1 | 49.5 | 1.0138
38.2 | 49.5 | 1.0138
38.3 | 49.5 | 1.0138
38.4 | 49.5 | 1.0136
38.5 | 49.5 | 1.0136
38.6 | 49.5 | 1.0134
38.7 | 49.5 | 1.0134
38.8 | 49.5 | 1.0134
38.9 | 49.5 | 1.0134
39 | 49.5 | 1.0134
39.1 | 49.5 | 1.0132
39.2 | 49.5 | 1.0128
39.3 | 49.5 | 1.0126
39.4 | 49.5 | 1.0126
39.5 | 49.5 | 1.0126
39.6 | 49.5 | 1.0126
39.7 | 49.5 | 1.0124
39.8 | 49.5 | 1.0122
39.9 | 49.5 | 1.0122
40 | 49.5 | 1.0122
40.1 | 49.5 | 1.0122
40.2 | 49.5 | 1.0122
40.3 | 49.5 | 1.012
40.4 | 49.5 | 1.012
40.5 | 49.5 | 1.012
40.6 | 49.5 | 1.012
40.7 | 49.5 | 1.0118
40.8 | 49.5 | 1.0118
40.9 | 49.5 | 1.0114
41 | 49.5 | 1.0114
41.1 | 49.5 | 1.0114
41.2 | 49.5 | 1.0114
41.3 | 49.5 | 1.0114
41.4 | 49.5 | 1.0112
41.5 | 49.5 | 1.0112
41.6 | 49.5 | 1.0112
41.7 | 49.5 | 1.0112
41.8 | 49.5 | 1.0112
41.9 | 49.5 | 1.0112
42 | 49.5 | 1.0112
42.1 | 49.5 | 1.011
42.2 | 49.5 | 1.011
42.3 | 49.5 | 1.011
42.4 | 49.5 | 1.011
42.5 | 49.5 | 1.011
42.6 | 49.5 | 1.0108
42.7 | 49.5 | 1.0108
42.8 | 49.5 | 1.0108
42.9 | 49.5 | 1.0104
43 | 49.5 | 1.0104
43.1 | 49.5 | 1.0104
43.2 | 49.5 | 1.0104
43.3 | 49.5 | 1.0104
43.4 | 49.5 | 1.0104
43.5 | 49.5 | 1.0104
43.6 | 49.5 | 1.0104
43.7 | 49.5 | 1.0104
43.8 | 49.5 | 1.0104
43.9 | 49.5 | 1.0104
44 | 49.5 | 1.0104
44.1 | 49.5 | 1.0104
44.2 | 49.5 | 1.0104
44.3 | 49.5 | 1.0102
44.4 | 49.5 | 1.01
44.5 | 49.5 | 1.01
44.6 | 49.5 | 1.01
44.7 | 49.5 | 1.01
44.8 | 49.5 | 1.01
44.9 | 49.5 | 1.01
45 | 49.5 | 1.01
45.1 | 49.5 | 1.01
45.2 | 49.5 | 1.01
45.3 | 49.5 | 1.01
45.4 | 49.5 | 1.0098
45.5 | 49.5 | 1.0098
45.6 | 49.5 | 1.0098
45.7 | 49.5 | 1.0098
45.8 | 49.5 | 1.0098
45.9 | 49.5 | 1.0098
46 | 49.5 | 1.0098
46.1 | 49.5 | 1.0098
46.2 | 49.5 | 1.0096
46.3 | 49.5 | 1.0096
46.4 | 49.5 | 1.0096
46.5 | 49.5 | 1.0096
46.6 | 49.5 | 1.0096
46.7 | 49.5 | 1.0096
46.8 | 49.5 | 1.0096
46.9 | 49.5 | 1.0096
47 | 49.5 | 1.0096
47.1 | 49.5 | 1.0096
47.2 | 49.5 | 1.0096
47.3 | 49.5 | 1.0096
47.4 | 49.5 | 1.0096
47.5 | 49.5 | 1.0096
47.6 | 49.5 | 1.0096
47.7 | 49.5 | 1.0096
47.8 | 49.5 | 1.0096
47.9 | 49.5 | 1.0096
48 | 49.5 | 1.0096
48.1 | 49.5 | 1.0096
48.2 | 49.5 | 1.0096
48.3 | 49.5 | 1.0096
48.4 | 49.5 | 1.0096
48.5 | 49.5 | 1.0096
48.6 | 49.5 | 1.0096
48.7 | 49.5 | 1.0096
48.8 | 49.5 | 1.0096
48.9 | 49.5 | 1.0096
49 | 49.5 | 1.0096
49.1 | 49.5 | 1.0096
49.2 | 49.5 | 1.0094
49.3 | 49.5 | 1.0094
49.4 | 49.5 | 1.0094
49.5 | 49.5 | 1.0094
49.6 | 49.5 | 1.0094
49.7 | 49.5 | 1.0094
49.8 | 49.5 | 1.0094
49.9 | 49.5 | 1.0094
50 | 49.5 | 1.0094
50.1 | 49.5 | 1.0094
50.2 | 49.5 | 1.0094
50.3 | 49.5 | 1.0094
50.4 | 49.5 | 1.0094
50.5 | 49.5 | 1.0094
50.6 | 49.5 | 1.0094
50.7 | 49.5 | 1.0096
50.8 | 49.5 | 1.0096
50.9 | 49.5 | 1.0096
51 | 49.5 | 1.0096
51.1 | 49.5 | 1.0096
51.2 | 49.5 | 1.0096
51.3 | 49.5 | 1.0096
51.4 | 49.5 | 1.0096
51.5 | 49.5 | 1.0098
51.6 | 49.5 | 1.0098
51.7 | 49.5 | 1.0098
51.8 | 49.5 | 1.0098
51.9 | 49.5 | 1.0098
52 | 49.5 | 1.0098
52.1 | 49.5 | 1.0098
52.2 | 49.5 | 1.0096
52.3 | 49.5 | 1.0096
52.4 | 49.5 | 1.0096
52.5 | 49.5 | 1.0096
52.6 | 49.5 | 1.0096
52.7 | 49.5 | 1.0098
52.8 | 49.5 | 1.0098
52.9 | 49.5 | 1.0098
53 | 49.5 | 1.0098
53.1 | 49.5 | 1.0098
53.2 | 49.5 | 1.0098
53.3 | 49.5 | 1.0098
53.4 | 49.5 | 1.0096
53.5 | 49.5 | 1.0096
53.6 | 49.5 | 1.0096
53.7 | 49.5 | 1.0096
53.8 | 49.5 | 1.0096
53.9 | 49.5 | 1.0096
54 | 49.5 | 1.0096
54.1 | 49.5 | 1.0096
54.2 | 49.5 | 1.0096
54.3 | 49.5 | 1.0096
54.4 | 49.5 | 1.0096
54.5 | 49.5 | 1.0096
54.6 | 49.5 | 1.0096
54.7 | 49.5 | 1.0096
54.8 | 49.5 | 1.0096
54.9 | 49.5 | 1.0096
55 | 49.5 | 1.0096
55.1 | 49.5 | 1.0096
55.2 | 49.5 | 1.0096
55.3 | 49.5 | 1.0096
55.4 | 49.5 | 1.0096
55.5 | 49.5 | 1.0096
55.6 | 49.5 | 1.0096
55.7 | 49.5 | 1.0098
55.8 | 49.5 | 1.0098
55.9 | 49.5 | 1.0098
56 | 49.5 | 1.0098
56.1 | 49.5 | 1.0098
56.2 | 49.5 | 1.0098
56.3 | 49.5 | 1.0098
56.4 | 49.5 | 1.0098
56.5 | 49.5 | 1.0098
56.6 | 49.5 | 1.0098
56.7 | 49.5 | 1.0098
56.8 | 49.5 | 1.0098
56.9 | 49.5 | 1.0098
57 | 49.5 | 1.0098
57.1 | 49.5 | 1.0098
57.2 | 49.5 | 1.0098
57.3 | 49.5 | 1.0098
57.4 | 49.5 | 1.0098
57.5 | 49.5 | 1.0098
57.6 | 49.5 | 1.0098
57.7 | 49.5 | 1.0098
57.8 | 49.5 | 1.0098
57.9 | 49.5 | 1.0098
58 | 49.5 | 1.0096
58.1 | 49.5 | 1.0096
58.2 | 49.5 | 1.0096
58.3 | 49.5 | 1.0096
58.4 | 49.5 | 1.0096
58.5 | 49.5 | 1.0096
58.6 | 49.5 | 1.0096
58.7 | 49.5 | 1.0096
58.8 | 49.5 | 1.0096
58.9 | 49.5 | 1.0096
59 | 49.5 | 1.0096
59.1 | 49.5 | 1.0096
59.2 | 49.5 | 1.0096
59.3 | 49.5 | 1.0096
59.4 | 49.5 | 1.0096
59.5 | 49.5 | 1.0096
59.6 | 49.5 | 1.0096
59.7 | 49.5 | 1.0094
59.8 | 49.5 | 1.0094
59.9 | 49.5 | 1.0094
60 | 49.5 | 1.0094
60.1 | 49.5 | 1.0094
60.2 | 49.5 | 1.0094
60.3 | 49.5 | 1.0094
60.4 | 49.5 | 1.0096
60.5 | 49.5 | 1.0096
60.6 | 49.5 | 1.0096
60.7 | 49.5 | 1.0096
60.8 | 49.5 | 1.0096
60.9 | 49.5 | 1.0096
61 | 49.5 | 1.0098
61.1 | 49.5 | 1.0098
61.2 | 49.5 | 1.0098
61.3 | 49.5 | 1.0098
61.4 | 49.5 | 1.0098
61.5 | 49.5 | 1.0098
61.6 | 49.5 | 1.0098
61.7 | 49.5 | 1.0098
61.8 | 49.5 | 1.0098
61.9 | 49.5 | 1.0098
62 | 49.5 | 1.0098
62.1 | 49.5 | 1.0098
62.2 | 49.5 | 1.0098
62.3 | 49.5 | 1.0098
62.4 | 49.5 | 1.0098
62.5 | 49.5 | 1.0098
62.6 | 49.5 | 1.0098
62.7 | 49.5 | 1.0098
62.8 | 49.5 | 1.0098
62.9 | 49.5 | 1.0098
63 | 49.5 | 1.0098
63.1 | 49.5 | 1.0098
63.2 | 49.5 | 1.0098
63.3 | 49.5 | 1.0098
63.4 | 49.5 | 1.0098
63.5 | 49.5 | 1.0098
63.6 | 49.5 | 1.0098
63.7 | 49.5 | 1.0098
63.8 | 49.5 | 1.0098
63.9 | 49.5 | 1.0098
64 | 49.5 | 1.0096
64.1 | 49.5 | 1.0096
64.2 | 49.5 | 1.0096
64.3 | 49.5 | 1.0096
64.4 | 49.5 | 1.0096
64.5 | 49.5 | 1.0096
64.6 | 49.5 | 1.0096
64.7 | 49.5 | 1.0096
64.8 | 49.5 | 1.0096
64.9 | 49.5 | 1.0096
65 | 49.5 | 1.0096
65.1 | 49.5 | 1.0096
65.2 | 49.5 | 1.0096
65.3 | 49.5 | 1.0096
65.4 | 49.5 | 1.0096
65.5 | 49.5 | 1.0094
65.6 | 49.5 | 1.0094
65.7 | 49.5 | 1.0094
65.8 | 49.5 | 1.0094
65.9 | 49.5 | 1.0094
66 | 49.5 | 1.0094
66.1 | 49.5 | 1.0094
66.2 | 49.5 | 1.0094
66.3 | 49.5 | 1.0096
66.4 | 49.5 | 1.0096
66.5 | 49.5 | 1.0096
66.6 | 49.5 | 1.0096
66.7 | 49.5 | 1.0096
66.8 | 49.5 | 1.0096
66.9 | 49.5 | 1.0096
67 | 49.5 | 1.0096
67.1 | 49.5 | 1.0096
67.2 | 49.5 | 1.0096
67.3 | 49.5 | 1.0096
67.4 | 49.5 | 1.0096
67.5 | 49.5 | 1.0096
67.6 | 49.5 | 1.0096
67.7 | 49.5 | 1.0096
67.8 | 49.5 | 1.0098
67.9 | 49.5 | 1.0098
68 | 49.5 | 1.0098
68.1 | 49.5 | 1.0098
68.2 | 49.5 | 1.0098
68.3 | 49.5 | 1.0098
68.4 | 49.5 | 1.0098
68.5 | 49.5 | 1.0098
68.6 | 49.5 | 1.0098
68.7 | 49.5 | 1.0098
68.8 | 49.5 | 1.0098
68.9 | 49.5 | 1.0098
69 | 49.5 | 1.0098
69.1 | 49.5 | 1.0098
69.2 | 49.5 | 1.0098
69.3 | 49.5 | 1.0098
69.4 | 49.5 | 1.0098
69.5 | 49.5 | 1.0098
69.6 | 49.5 | 1.0098
69.7 | 49.5 | 1.0098
69.8 | 49.5 | 1.0098
69.9 | 49.5 | 1.0098
70 | 49.5 | 1.0098
70.1 | 49.5 | 1.0096
70.2 | 49.5 | 1.0096
70.3 | 49.5 | 1.0096
70.4 | 49.5 | 1.0096
70.5 | 49.5 | 1.0096
70.6 | 49.5 | 1.0096
70.7 | 49.5 | 1.0096
70.8 | 49.5 | 1.0096
70.9 | 49.5 | 1.0098
71 | 49.5 | 1.0098
71.1 | 49.5 | 1.0098
71.2 | 49.5 | 1.0098
71.3 | 49.5 | 1.0096
71.4 | 49.5 | 1.0096
71.5 | 49.5 | 1.0096
71.6 | 49.5 | 1.0096
71.7 | 49.5 | 1.0096
71.8 | 49.5 | 1.0096
71.9 | 49.5 | 1.0096
72 | 49.5 | 1.0096
72.1 | 49.5 | 1.0096
72.2 | 49.5 | 1.0096
72.3 | 49.5 | 1.0096
72.4 | 49.5 | 1.0096
72.5 | 49.5 | 1.0096
72.6 | 49.5 | 1.0096
72.7 | 49.5 | 1.0096
72.8 | 49.5 | 1.0096
72.9 | 49.5 | 1.0096
73 | 49.5 | 1.0096
73.1 | 49.5 | 1.0096
73.2 | 49.5 | 1.0096
73.3 | 49.5 | 1.0096
73.4 | 49.5 | 1.0096
73.5 | 49.5 | 1.0096
73.6 | 49.5 | 1.0096
73.7 | 49.5 | 1.0096
73.8 | 49.5 | 1.0096
73.9 | 49.5 | 1.0096
74 | 49.5 | 1.0096
74.1 | 49.5 | 1.0096
74.2 | 49.5 | 1.0096
74.3 | 49.5 | 1.0096
74.4 | 49.5 | 1.0096
74.5 | 49.5 | 1.0096
74.6 | 49.5 | 1.0096
74.7 | 49.5 | 1.0096
74.8 | 49.5 | 1.0096
74.9 | 49.5 | 1.0096
75 | 49.5 | 1.0096
75.1 | 49.5 | 1.0096
75.2 | 49.5 | 1.0096
75.3 | 49.5 | 1.0096
75.4 | 49.5 | 1.0096
75.5 | 49.5 | 1.0096
75.6 | 49.5 | 1.0096
75.7 | 49.5 | 1.0096
75.8 | 49.5 | 1.0096
75.9 | 49.5 | 1.0096
76 | 49.5 | 1.0096
76.1 | 49.5 | 1.0096
76.2 | 49.5 | 1.0096
76.3 | 49.5 | 1.0096
76.4 | 49.5 | 1.0096
76.5 | 49.5 | 1.0096
76.6 | 49.5 | 1.0096
76.7 | 49.5 | 1.0096
76.8 | 49.5 | 1.0096
76.9 | 49.5 | 1.0096
77 | 49.5 | 1.0096
77.1 | 49.5 | 1.0096
77.2 | 49.5 | 1.0096
77.3 | 49.5 | 1.0096
77.4 | 49.5 | 1.0096
77.5 | 49.5 | 1.0096
77.6 | 49.5 | 1.0096
77.7 | 49.5 | 1.0096
77.8 | 49.5 | 1.0096
77.9 | 49.5 | 1.0096
78 | 49.5 | 1.0096
78.1 | 49.5 | 1.0096
78.2 | 49.5 | 1.0096
78.3 | 49.5 | 1.0096
78.4 | 49.5 | 1.0096
78.5 | 49.5 | 1.0096
78.6 | 49.5 | 1.0096
78.7 | 49.5 | 1.0096
78.8 | 49.5 | 1.0096
78.9 | 49.5 | 1.0096
79 | 49.5 | 1.0096
79.1 | 49.5 | 1.0096
79.2 | 49.5 | 1.0096
79.3 | 49.5 | 1.0096
79.4 | 49.5 | 1.0096
79.5 | 49.5 | 1.0096
79.6 | 49.5 | 1.0096
79.7 | 49.5 | 1.0096
79.8 | 49.5 | 1.0096
79.9 | 49.5 | 1.0096
80 | 49.5 | 1.0096
80.1 | 49.5 | 1.0096
80.2 | 49.5 | 1.0096
80.3 | 49.5 | 1.0096
80.4 | 49.5 | 1.0096
80.5 | 49.5 | 1.0096
80.6 | 49.5 | 1.0096
80.7 | 49.5 | 1.0096
80.8 | 49.5 | 1.0096
80.9 | 49.5 | 1.0096
81 | 49.5 | 1.0096
81.1 | 49.5 | 1.0096
81.2 | 49.5 | 1.0096
81.3 | 49.5 | 1.0096
81.4 | 49.5 | 1.0096
81.5 | 49.5 | 1.0096
81.6 | 49.5 | 1.0096
81.7 | 49.5 | 1.0096
81.8 | 49.5 | 1.0098
81.9 | 49.5 | 1.0098
82 | 49.5 | 1.0098
82.1 | 49.5 | 1.0098
82.2 | 49.5 | 1.0098
82.3 | 49.5 | 1.0098
82.4 | 49.5 | 1.0098
82.5 | 49.5 | 1.0098
82.6 | 49.5 | 1.0098
82.7 | 49.5 | 1.0098
82.8 | 49.5 | 1.0098
82.9 | 49.5 | 1.0098
83 | 49.5 | 1.0098
83.1 | 49.5 | 1.0098
83.2 | 49.5 | 1.0098
83.3 | 49.5 | 1.0098
83.4 | 49.5 | 1.0098
83.5 | 49.5 | 1.0098
83.6 | 49.5 | 1.0098
83.7 | 49.5 | 1.0098
83.8 | 49.5 | 1.0098
83.9 | 49.5 | 1.0098
84 | 49.5 | 1.0098
84.1 | 49.5 | 1.0098
84.2 | 49.5 | 1.0098
84.3 | 49.5 | 1.0098
84.4 | 49.5 | 1.0098
84.5 | 49.5 | 1.0098
84.6 | 49.5 | 1.0098
84.7 | 49.5 | 1.0098
84.8 | 49.5 | 1.0098
84.9 | 49.5 | 1.0098
85 | 49.5 | 1.0098
85.1 | 49.5 | 1.0098
85.2 | 49.5 | 1.0098
85.3 | 49.5 | 1.0098
85.4 | 49.5 | 1.0098
85.5 | 49.5 | 1.0096
85.6 | 49.5 | 1.0096
85.7 | 49.5 | 1.0096
85.8 | 49.5 | 1.0096
85.9 | 49.5 | 1.0096
86 | 49.5 | 1.0096
86.1 | 49.5 | 1.0096
86.2 | 49.5 | 1.0096
86.3 | 49.5 | 1.0096
86.4 | 49.5 | 1.0096
86.5 | 49.5 | 1.0096
86.6 | 49.5 | 1.0096
86.7 | 49.5 | 1.0096
86.8 | 49.5 | 1.0096
86.9 | 49.5 | 1.0096
87 | 49.5 | 1.0096
87.1 | 49.5 | 1.0096
87.2 | 49.5 | 1.0096
87.3 | 49.5 | 1.0096
87.4 | 49.5 | 1.0096
87.5 | 49.5 | 1.0096
87.6 | 49.5 | 1.0096
87.7 | 49.5 | 1.0096
87.8 | 49.5 | 1.0096
87.9 | 49.5 | 1.0096
88 | 49.5 | 1.0096
88.1 | 49.5 | 1.0096
88.2 | 49.5 | 1.0096
88.3 | 49.5 | 1.0096
88.4 | 49.5 | 1.0096
88.5 | 49.5 | 1.0096
88.6 | 49.5 | 1.0096
88.7 | 49.5 | 1.0096
88.8 | 49.5 | 1.0096
88.9 | 49.5 | 1.0098
89 | 49.5 | 1.0098
89.1 | 49.5 | 1.0098
89.2 | 49.5 | 1.0098
89.3 | 49.5 | 1.0098
89.4 | 49.5 | 1.0098
89.5 | 49.5 | 1.0098
89.6 | 49.5 | 1.0098
89.7 | 49.5 | 1.0098
89.8 | 49.5 | 1.0098
89.9 | 49.5 | 1.0098
90 | 49.5 | 1.0098
90.1 | 49.5 | 1.0098
90.2 | 49.5 | 1.0098
90.3 | 49.5 | 1.0098
90.4 | 49.5 | 1.0098
90.5 | 49.5 | 1.0098
90.6 | 49.5 | 1.0098
90.7 | 49.5 | 1.0098
90.8 | 49.5 | 1.0098
90.9 | 49.5 | 1.0098
91 | 49.5 | 1.0098
91.1 | 49.5 | 1.0098
91.2 | 49.5 | 1.0098
91.3 | 49.5 | 1.0096
91.4 | 49.5 | 1.0096
91.5 | 49.5 | 1.0096
91.6 | 49.5 | 1.0096
91.7 | 49.5 | 1.0096
91.8 | 49.5 | 1.0096
91.9 | 49.5 | 1.0096
92 | 49.5 | 1.0096
92.1 | 49.5 | 1.0096
92.2 | 49.5 | 1.0096
92.3 | 49.5 | 1.0096
92.4 | 49.5 | 1.0096
92.5 | 49.5 | 1.0096
92.6 | 49.5 | 1.0096
92.7 | 49.5 | 1.0096
92.8 | 49.5 | 1.0096
92.9 | 49.5 | 1.0096
93 | 49.5 | 1.0096
93.1 | 49.5 | 1.0096
93.2 | 49.5 | 1.0096
93.3 | 49.5 | 1.0096
93.4 | 49.5 | 1.0096
93.5 | 49.5 | 1.0096
93.6 | 49.5 | 1.0096
93.7 | 49.5 | 1.0096
93.8 | 49.5 | 1.0096
93.9 | 49.5 | 1.0096
94 | 49.5 | 1.0096
94.1 | 49.5 | 1.0096
94.2 | 49.5 | 1.0096
94.3 | 49.5 | 1.0096
94.4 | 49.5 | 1.0096
94.5 | 49.5 | 1.0096
94.6 | 49.5 | 1.0096
94.7 | 49.5 | 1.0096
94.8 | 49.5 | 1.0096
94.9 | 49.5 | 1.0096
95 | 49.5 | 1.0096
95.1 | 49.5 | 1.0096
95.2 | 49.5 | 1.0096
95.3 | 49.5 | 1.0096
95.4 | 49.5 | 1.0096
95.5 | 49.5 | 1.0096
95.6 | 49.5 | 1.0096
95.7 | 49.5 | 1.0096
95.8 | 49.5 | 1.0096
95.9 | 49.5 | 1.0096
96 | 49.5 | 1.0096
96.1 | 49.5 | 1.0096
96.2 | 49.5 | 1.0096
96.3 | 49.5 | 1.0096
96.4 | 49.5 | 1.0096
96.5 | 49.5 | 1.0096
96.6 | 49.5 | 1.0096
96.7 | 49.5 | 1.0096
96.8 | 49.5 | 1.0096
96.9 | 49.5 | 1.0096
97 | 49.5 | 1.0096
97.1 | 49.5 | 1.0096
97.2 | 49.5 | 1.0096
97.3 | 49.5 | 1.0096
97.4 | 49.5 | 1.0096
97.5 | 49.5 | 1.0096
97.6 | 49.5 | 1.0096
97.7 | 49.5 | 1.0096
97.8 | 49.5 | 1.0096
97.9 | 49.5 | 1.0096
98 | 49.5 | 1.0096
98.1 | 49.5 | 1.0096
98.2 | 49.5 | 1.0096
98.3 | 49.5 | 1.0096
98.4 | 49.5 | 1.0096
98.5 | 49.5 | 1.0096
98.6 | 49.5 | 1.0096
98.7 | 49.5 | 1.0096
98.8 | 49.5 | 1.0096
98.9 | 49.5 | 1.0096
99 | 49.5 | 1.0096
99.1 | 49.5 | 1.0096
99.2 | 49.5 | 1.0096
99.3 | 49.5 | 1.0096
99.4 | 49.5 | 1.0096
99.5 | 49.5 | 1.0096
99.6 | 49.5 | 1.0096
99.7 | 49.5 | 1.0096
99.8 | 49.5 | 1.0096
99.9 | 49.5 | 1.0096
100 | 49.5 | 1.0096
100.1 | 49.5 | 1.0096
100.2 | 49.5 | 1.0096
100.3 | 49.5 | 1.0096
100.4 | 49.5 | 1.0096
100.5 | 49.5 | 1.0096
100.6 | 49.5 | 1.0098
100.7 | 49.5 | 1.0098
100.8 | 49.5 | 1.0098
100.9 | 49.5 | 1.0098
101 | 49.5 | 1.0098
101.1 | 49.5 | 1.0098
101.2 | 49.5 | 1.0098
101.3 | 49.5 | 1.0098
101.4 | 49.5 | 1.0098
101.5 | 49.5 | 1.0098
101.6 | 49.5 | 1.0098
101.7 | 49.5 | 1.0098
101.8 | 49.5 | 1.0098
101.9 | 49.5 | 1.0098
102 | 49.5 | 1.0098
102.1 | 49.5 | 1.0098
102.2 | 49.5 | 1.0098
102.3 | 49.5 | 1.0098
102.4 | 49.5 | 1.0098
102.5 | 49.5 | 1.0098
102.6 | 49.5 | 1.0098
102.7 | 49.5 | 1.0098
102.8 | 49.5 | 1.0098
102.9 | 49.5 | 1.0098
103 | 49.5 | 1.0098
103.1 | 49.5 | 1.0098
103.2 | 49.5 | 1.0098
103.3 | 49.5 | 1.0098
103.4 | 49.5 | 1.0098
103.5 | 49.5 | 1.0098
103.6 | 49.5 | 1.0098
103.7 | 49.5 | 1.0096
103.8 | 49.5 | 1.0096
103.9 | 49.5 | 1.0096
104 | 49.5 | 1.0096
104.1 | 49.5 | 1.0096
104.2 | 49.5 | 1.0096
104.3 | 49.5 | 1.0096
104.4 | 49.5 | 1.0096
104.5 | 49.5 | 1.0096
104.6 | 49.5 | 1.0096
104.7 | 49.5 | 1.0096
104.8 | 49.5 | 1.0096
104.9 | 49.5 | 1.0096
105 | 49.5 | 1.0096
105.1 | 49.5 | 1.0096
105.2 | 49.5 | 1.0096
105.3 | 49.5 | 1.0096
105.4 | 49.5 | 1.0096
105.5 | 49.5 | 1.0096
105.6 | 49.5 | 1.0096
105.7 | 49.5 | 1.0096
105.8 | 49.5 | 1.0096
105.9 | 49.5 | 1.0096
106 | 49.5 | 1.0096
106.1 | 49.5 | 1.0096
106.2 | 49.5 | 1.0096
106.3 | 49.5 | 1.0096
106.4 | 49.5 | 1.0096
106.5 | 49.5 | 1.0096
106.6 | 49.5 | 1.0096
106.7 | 49.5 | 1.0096
106.8 | 49.5 | 1.0096
106.9 | 49.5 | 1.0096
107 | 49.5 | 1.0096
107.1 | 49.5 | 1.0096
107.2 | 49.5 | 1.0096
107.3 | 49.5 | 1.0096
107.4 | 49.5 | 1.0096
107.5 | 49.5 | 1.0096
107.6 | 49.5 | 1.0096
107.7 | 49.5 | 1.0096
107.8 | 49.5 | 1.0096
107.9 | 49.5 | 1.0096
108 | 49.5 | 1.0096
108.1 | 49.5 | 1.0096
108.2 | 49.5 | 1.0096
108.3 | 49.5 | 1.0096
108.4 | 49.5 | 1.0096
108.5 | 49.5 | 1.0096
108.6 | 49.5 | 1.0096
108.7 | 49.5 | 1.0096
108.8 | 49.5 | 1.0096
108.9 | 49.5 | 1.0096
109 | 49.5 | 1.0096
109.1 | 49.5 | 1.0096
109.2 | 49.5 | 1.0096
109.3 | 49.5 | 1.0096
109.4 | 49.5 | 1.0096
109.5 | 49.5 | 1.0096
109.6 | 49.5 | 1.0096
109.7 | 49.5 | 1.0096
109.8 | 49.5 | 1.0096
109.9 | 49.5 | 1.0096
110 | 49.5 | 1.0098
110.1 | 49.5 | 1.0098
110.2 | 49.5 | 1.0098
110.3 | 49.5 | 1.0098
110.4 | 49.5 | 1.0098
110.5 | 49.5 | 1.0098
110.6 | 49.5 | 1.0098
110.7 | 49.5 | 1.0098
110.8 | 49.5 | 1.0098
110.9 | 49.5 | 1.0098
111 | 49.5 | 1.0098
111.1 | 49.5 | 1.0098
111.2 | 49.5 | 1.0096
111.3 | 49.5 | 1.0096
111.4 | 49.5 | 1.0096
111.5 | 49.5 | 1.0096
111.6 | 49.5 | 1.0096
111.7 | 49.5 | 1.0096
111.8 | 49.5 | 1.0096
111.9 | 49.5 | 1.0096
112 | 49.5 | 1.0096
112.1 | 49.5 | 1.0096
112.2 | 49.5 | 1.0096
112.3 | 49.5 | 1.0096
112.4 | 49.5 | 1.0096
112.5 | 49.5 | 1.0096
112.6 | 49.5 | 1.0096
112.7 | 49.5 | 1.0096
112.8 | 49.5 | 1.0096
112.9 | 49.5 | 1.0096
113 | 49.5 | 1.0096
113.1 | 49.5 | 1.0096
113.2 | 49.5 | 1.0096
113.3 | 49.5 | 1.0096
113.4 | 49.5 | 1.0096
113.5 | 49.5 | 1.0096
113.6 | 49.5 | 1.0096
113.7 | 49.5 | 1.0096
113.8 | 49.5 | 1.0096
113.9 | 49.5 | 1.0096
114 | 49.5 | 1.0096
114.1 | 49.5 | 1.0096
114.2 | 49.5 | 1.0096
114.3 | 49.5 | 1.0096
114.4 | 49.5 | 1.0096
114.5 | 49.5 | 1.0096
114.6 | 49.5 | 1.0096
114.7 | 49.5 | 1.0096
114.8 | 49.5 | 1.0096
114.9 | 49.5 | 1.0096
115 | 49.5 | 1.0096
115.1 | 49.5 | 1.0096
115.2 | 49.5 | 1.0096
115.3 | 49.5 | 1.0096
115.4 | 49.5 | 1.0096
115.5 | 49.5 | 1.0096
115.6 | 49.5 | 1.0096
115.7 | 49.5 | 1.0096
115.8 | 49.5 | 1.0098
115.9 | 49.5 | 1.0098
116 | 49.5 | 1.0098
116.1 | 49.5 | 1.0098
116.2 | 49.5 | 1.0098
116.3 | 49.5 | 1.0098
116.4 | 49.5 | 1.0098
116.5 | 49.5 | 1.0098
116.6 | 49.5 | 1.0096
116.7 | 49.5 | 1.0096
116.8 | 49.5 | 1.0096
116.9 | 49.5 | 1.0096
117 | 49.5 | 1.0096
117.1 | 49.5 | 1.0096
117.2 | 49.5 | 1.0096
117.3 | 49.5 | 1.0096
117.4 | 49.5 | 1.0096
117.5 | 49.5 | 1.0096
117.6 | 49.5 | 1.0096
117.7 | 49.5 | 1.0096
117.8 | 49.5 | 1.0096
117.9 | 49.5 | 1.0096
118 | 49.5 | 1.0096
118.1 | 49.5 | 1.0096
118.2 | 49.5 | 1.0096
118.3 | 49.5 | 1.0096
118.4 | 49.5 | 1.0096
118.5 | 49.5 | 1.0096
118.6 | 49.5 | 1.0096
118.7 | 49.5 | 1.0096
118.8 | 49.5 | 1.0096
118.9 | 49.5 | 1.0096
119 | 49.5 | 1.0096
119.1 | 49.5 | 1.0096
119.2 | 49.5 | 1.0096
119.3 | 49.5 | 1.0096
119.4 | 49.5 | 1.0096
119.5 | 49.5 | 1.0096
119.6 | 49.5 | 1.0096
119.7 | 49.5 | 1.0096
119.8 | 49.5 | 1.0096
119.9 | 49.5 | 1.0096
120 | 49.5 | 1.0096
120.1 | 49.5 | 1.0096
120.2 | 49.5 | 1.0096
120.3 | 49.5 | 1.0096
120.4 | 49.5 | 1.0096
120.5 | 49.5 | 1.0096
120.6 | 49.5 | 1.0096
120.7 | 49.5 | 1.0096
120.8 | 49.5 | 1.0096
120.9 | 49.5 | 1.0096
121 | 49.5 | 1.0096
121.1 | 49.5 | 1.0096
121.2 | 49.5 | 1.0096
121.3 | 49.5 | 1.0096
121.4 | 49.5 | 1.0096
121.5 | 49.5 | 1.0096
121.6 | 49.5 | 1.0096
121.7 | 49.5 | 1.0096
121.8 | 49.5 | 1.0096
121.9 | 49.5 | 1.0096
122 | 49.5 | 1.0096
122.1 | 49.5 | 1.0096
122.2 | 49.5 | 1.0096
122.3 | 49.5 | 1.0096
122.4 | 49.5 | 1.0096
122.5 | 49.5 | 1.0096
122.6 | 49.5 | 1.0096
122.7 | 49.5 | 1.0096
122.8 | 49.5 | 1.0096
122.9 | 49.5 | 1.0096
123 | 49.5 | 1.0096
123.1 | 49.5 | 1.0096
123.2 | 49.5 | 1.0096
123.3 | 49.5 | 1.0096
123.4 | 49.5 | 1.0096
123.5 | 49.5 | 1.0096
123.6 | 49.5 | 1.0096
123.7 | 49.5 | 1.0096
123.8 | 49.5 | 1.0096
123.9 | 49.5 | 1.0096
124 | 49.5 | 1.0096
124.1 | 49.5 | 1.0096
124.2 | 49.5 | 1.0096
124.3 | 49.5 | 1.0096
124.4 | 49.5 | 1.0096
124.5 | 49.5 | 1.0096
124.6 | 49.5 | 1.0096
124.7 | 49.5 | 1.0096
124.8 | 49.5 | 1.0096
124.9 | 49.5 | 1.0096
125 | 49.5 | 1.0096
125.1 | 49.5 | 1.0096
125.2 | 49.5 | 1.0096
125.3 | 49.5 | 1.0096
125.4 | 49.5 | 1.0096
125.5 | 49.5 | 1.0096
125.6 | 49.5 | 1.0096
125.7 | 49.5 | 1.0096
125.8 | 49.5 | 1.0096
125.9 | 49.5 | 1.0096
126 | 49.5 | 1.0096
126.1 | 49.5 | 1.0096
126.2 | 49.5 | 1.0096
126.3 | 49.5 | 1.0096
126.4 | 49.5 | 1.0096
126.5 | 49.5 | 1.0096
126.6 | 49.5 | 1.0096
126.7 | 49.5 | 1.0096
126.8 | 49.5 | 1.0096
126.9 | 49.5 | 1.0096
127 | 49.5 | 1.0096
127.1 | 49.5 | 1.0096
127.2 | 49.5 | 1.0096
127.3 | 49.5 | 1.0096
127.4 | 49.5 | 1.0096
127.5 | 49.5 | 1.0096
127.6 | 49.5 | 1.0096
127.7 | 49.5 | 1.0096
127.8 | 49.5 | 1.0096
127.9 | 49.5 | 1.0096
128 | 49.5 | 1.0096
128.1 | 49.5 | 1.0096
128.2 | 49.5 | 1.0096
128.3 | 49.5 | 1.0096
128.4 | 49.5 | 1.0096
128.5 | 49.5 | 1.0096
128.6 | 49.5 | 1.0096
128.7 | 49.5 | 1.0098
128.8 | 49.5 | 1.0098
128.9 | 49.5 | 1.0098
129 | 49.5 | 1.0098
129.1 | 49.5 | 1.0098
129.2 | 49.5 | 1.0098
129.3 | 49.5 | 1.0098
129.4 | 49.5 | 1.0098
129.5 | 49.5 | 1.0098
129.6 | 49.5 | 1.0098
129.7 | 49.5 | 1.0096
129.8 | 49.5 | 1.0096
129.9 | 49.5 | 1.0096
130 | 49.5 | 1.0096
130.1 | 49.5 | 1.0096
130.2 | 49.5 | 1.0096
130.3 | 49.5 | 1.0096
130.4 | 49.5 | 1.0096
130.5 | 49.5 | 1.0096
130.6 | 49.5 | 1.0096
130.7 | 49.5 | 1.0096
130.8 | 49.5 | 1.0096
130.9 | 49.5 | 1.0096
131 | 49.5 | 1.0096
131.1 | 49.5 | 1.0096
131.2 | 49.5 | 1.0096
131.3 | 49.5 | 1.0096
131.4 | 49.5 | 1.0096
131.5 | 49.5 | 1.0096
131.6 | 49.5 | 1.0096
131.7 | 49.5 | 1.0096
131.8 | 49.5 | 1.0096
131.9 | 49.5 | 1.0096
132 | 49.5 | 1.0096
132.1 | 49.5 | 1.0096
132.2 | 49.5 | 1.0096
132.3 | 49.5 | 1.0098
132.4 | 49.5 | 1.0098
132.5 | 49.5 | 1.0098
132.6 | 49.5 | 1.0098
132.7 | 49.5 | 1.0098
132.8 | 49.5 | 1.0098
132.9 | 49.5 | 1.0098
133 | 49.5 | 1.0098
133.1 | 49.5 | 1.0098
133.2 | 49.5 | 1.0096
133.3 | 49.5 | 1.0096
133.4 | 49.5 | 1.0096
133.5 | 49.5 | 1.0096
133.6 | 49.5 | 1.0096
133.7 | 49.5 | 1.0096
133.8 | 49.5 | 1.0096
133.9 | 49.5 | 1.0096
134 | 49.5 | 1.0096
134.1 | 49.5 | 1.0096
134.2 | 49.5 | 1.0096
134.3 | 49.5 | 1.0096
134.4 | 49.5 | 1.0096
134.5 | 49.5 | 1.0096
134.6 | 49.5 | 1.0098
134.7 | 49.5 | 1.0098
134.8 | 49.5 | 1.0098
134.9 | 49.5 | 1.0098
135 | 49.5 | 1.0098
135.1 | 49.5 | 1.0098
135.2 | 49.5 | 1.0098
135.3 | 49.5 | 1.0098
135.4 | 49.5 | 1.0098
135.5 | 49.5 | 1.0098
135.6 | 49.5 | 1.0098
135.7 | 49.5 | 1.0096
135.8 | 49.5 | 1.0096
135.9 | 49.5 | 1.0096
136 | 49.5 | 1.0096
136.1 | 49.5 | 1.0096
136.2 | 49.5 | 1.0096
136.3 | 49.5 | 1.0096
136.4 | 49.5 | 1.0096
136.5 | 49.5 | 1.0096
136.6 | 49.5 | 1.0096
136.7 | 49.5 | 1.0096
136.8 | 49.5 | 1.0096
136.9 | 49.5 | 1.0096
137 | 49.5 | 1.0096
137.1 | 49.5 | 1.0096
137.2 | 49.5 | 1.0096
137.3 | 49.5 | 1.0096
137.4 | 49.5 | 1.0096
137.5 | 49.5 | 1.0096
137.6 | 49.5 | 1.0096
137.7 | 49.5 | 1.0096
137.8 | 49.5 | 1.0096
137.9 | 49.5 | 1.0096
138 | 49.5 | 1.0096
138.1 | 49.5 | 1.0096
138.2 | 49.5 | 1.0096
138.3 | 49.5 | 1.0096
138.4 | 49.5 | 1.0096
138.5 | 49.5 | 1.0096
138.6 | 49.5 | 1.0096
138.7 | 49.5 | 1.0096
138.8 | 49.5 | 1.0096
138.9 | 49.5 | 1.0096
139 | 49.5 | 1.0096
139.1 | 49.5 | 1.0096
139.2 | 49.5 | 1.0096
139.3 | 49.5 | 1.0096
139.4 | 49.5 | 1.0096
139.5 | 49.5 | 1.0096
139.6 | 49.5 | 1.0096
139.7 | 49.5 | 1.0096
139.8 | 49.5 | 1.0096
139.9 | 49.5 | 1.0096
140 | 49.5 | 1.0096
140.1 | 49.5 | 1.0096
140.2 | 49.5 | 1.0096
140.3 | 49.5 | 1.0096
140.4 | 49.5 | 1.0098
140.5 | 49.5 | 1.0098
140.6 | 49.5 | 1.0098
140.7 | 49.5 | 1.0098
140.8 | 49.5 | 1.0098
140.9 | 49.5 | 1.0098
141 | 49.5 | 1.0098
141.1 | 49.5 | 1.0098
141.2 | 49.5 | 1.0098
141.3 | 49.5 | 1.0098
141.4 | 49.5 | 1.0098
141.5 | 49.5 | 1.0098
141.6 | 49.5 | 1.0096
141.7 | 49.5 | 1.0096
141.8 | 49.5 | 1.0096
141.9 | 49.5 | 1.0096
142 | 49.5 | 1.0096
142.1 | 49.5 | 1.0096
142.2 | 49.5 | 1.0096
142.3 | 49.5 | 1.0096
142.4 | 49.5 | 1.0096
142.5 | 49.5 | 1.0096
142.6 | 49.5 | 1.0096
142.7 | 49.5 | 1.0096
142.8 | 49.5 | 1.0096
142.9 | 49.5 | 1.0096
143 | 49.5 | 1.0096
143.1 | 49.5 | 1.0096
143.2 | 49.5 | 1.0096
143.3 | 49.5 | 1.0096
143.4 | 49.5 | 1.0096
143.5 | 49.5 | 1.0096
143.6 | 49.5 | 1.0096
143.7 | 49.5 | 1.0096
143.8 | 49.5 | 1.0096
143.9 | 49.5 | 1.0096
144 | 49.5 | 1.0096
144.1 | 49.5 | 1.0096
144.2 | 49.5 | 1.0096
144.3 | 49.5 | 1.0096
144.4 | 49.5 | 1.0096
144.5 | 49.5 | 1.0096
144.6 | 49.5 | 1.0096
144.7 | 49.5 | 1.0096
144.8 | 49.5 | 1.0096
144.9 | 49.5 | 1.0096
145 | 49.5 | 1.0096
145.1 | 49.5 | 1.0096
145.2 | 49.5 | 1.0096
145.3 | 49.5 | 1.0096
145.4 | 49.5 | 1.0096
145.5 | 49.5 | 1.0096
145.6 | 49.5 | 1.0096
145.7 | 49.5 | 1.0096
145.8 | 49.5 | 1.0096
145.9 | 49.5 | 1.0096
146 | 49.5 | 1.0096
146.1 | 49.5 | 1.0096
146.2 | 49.5 | 1.0096
146.3 | 49.5 | 1.0096
146.4 | 49.5 | 1.0096
146.5 | 49.5 | 1.0096
146.6 | 49.5 | 1.0096
146.7 | 49.5 | 1.0096
146.8 | 49.5 | 1.0096
146.9 | 49.5 | 1.0096
147 | 49.5 | 1.0096
147.1 | 49.5 | 1.0096
147.2 | 49.5 | 1.0096
147.3 | 49.5 | 1.0096
147.4 | 49.5 | 1.0096
147.5 | 49.5 | 1.0096
147.6 | 49.5 | 1.0096
147.7 | 49.5 | 1.0096
147.8 | 49.5 | 1.0096
147.9 | 49.5 | 1.0096
148 | 49.5 | 1.0096
148.1 | 49.5 | 1.0096
148.2 | 49.5 | 1.0096
148.3 | 49.5 | 1.0096
148.4 | 49.5 | 1.0096
148.5 | 49.5 | 1.0096
148.6 | 49.5 | 1.0096
148.7 | 49.5 | 1.0096
148.8 | 49.5 | 1.0096
148.9 | 49.5 | 1.0096
149 | 49.5 | 1.0096
149.1 | 49.5 | 1.0096
149.2 | 49.5 | 1.0096
149.3 | 49.5 | 1.0096
149.4 | 49.5 | 1.0096
149.5 | 49.5 | 1.0096
149.6 | 49.5 | 1.0096
149.7 | 49.5 | 1.0096
149.8 | 49.5 | 1.0098
149.9 | 49.5 | 1.0098
150 | 49.5 | 1.0098
150.1 | 49.5 | 1.0098
150.2 | 49.5 | 1.0098
150.3 | 49.5 | 1.0098
150.4 | 49.5 | 1.0098
150.5 | 49.5 | 1.0096
150.6 | 49.5 | 1.0096
150.7 | 49.5 | 1.0096
150.8 | 49.5 | 1.0096
150.9 | 49.5 | 1.0096
151 | 49.5 | 1.0096
151.1 | 49.5 | 1.0096
151.2 | 49.5 | 1.0096
151.3 | 49.5 | 1.0096
151.4 | 49.5 | 1.0096
151.5 | 49.5 | 1.0096
151.6 | 49.5 | 1.0096
151.7 | 49.5 | 1.0096
151.8 | 49.5 | 1.0096
151.9 | 49.5 | 1.0096
152 | 49.5 | 1.0096
152.1 | 49.5 | 1.0096
152.2 | 49.5 | 1.0096
152.3 | 49.5 | 1.0096
152.4 | 49.5 | 1.0096
152.5 | 49.5 | 1.0096
152.6 | 49.5 | 1.0096
152.7 | 49.5 | 1.0096
152.8 | 49.5 | 1.0096
152.9 | 49.5 | 1.0096
153 | 49.5 | 1.0096
153.1 | 49.5 | 1.0096
153.2 | 49.5 | 1.0096
153.3 | 49.5 | 1.0096
153.4 | 49.5 | 1.0096
153.5 | 49.5 | 1.0096
153.6 | 49.5 | 1.0096
153.7 | 49.5 | 1.0096
153.8 | 49.5 | 1.0096
153.9 | 49.5 | 1.0096
154 | 49.5 | 1.0096
154.1 | 49.5 | 1.0096
154.2 | 49.5 | 1.0096
154.3 | 49.5 | 1.0096
154.4 | 49.5 | 1.0096
154.5 | 49.5 | 1.0096
154.6 | 49.5 | 1.0096
154.7 | 49.5 | 1.0096
154.8 | 49.5 | 1.0096
154.9 | 49.5 | 1.0096
155 | 49.5 | 1.0096
155.1 | 49.5 | 1.0096
155.2 | 49.5 | 1.0096
155.3 | 49.5 | 1.0096
155.4 | 49.5 | 1.0096
155.5 | 49.5 | 1.0096
155.6 | 49.5 | 1.0096
155.7 | 49.5 | 1.0096
155.8 | 49.5 | 1.0096
155.9 | 49.5 | 1.0096
156 | 49.5 | 1.0096
156.1 | 49.5 | 1.0096
156.2 | 49.5 | 1.0096
156.3 | 49.5 | 1.0096
156.4 | 49.5 | 1.0096
156.5 | 49.5 | 1.0096
156.6 | 49.5 | 1.0096
156.7 | 49.5 | 1.0096
156.8 | 49.5 | 1.0096
156.9 | 49.5 | 1.0096
157 | 49.5 | 1.0096
157.1 | 49.5 | 1.0096
157.2 | 49.5 | 1.0096
157.3 | 49.5 | 1.0096
157.4 | 49.5 | 1.0096
157.5 | 49.5 | 1.0096
157.6 | 49.5 | 1.0096
157.7 | 49.5 | 1.0096
157.8 | 49.5 | 1.0096
157.9 | 49.5 | 1.0096
158 | 49.5 | 1.0096
158.1 | 49.5 | 1.0096
158.2 | 49.5 | 1.0096
158.3 | 49.5 | 1.0096
158.4 | 49.5 | 1.0096
158.5 | 49.5 | 1.0096
158.6 | 49.5 | 1.0096
158.7 | 49.5 | 1.0096
158.8 | 49.5 | 1.0096
158.9 | 49.5 | 1.0096
159 | 49.5 | 1.0096
159.1 | 49.5 | 1.0096
159.2 | 49.5 | 1.0096
159.3 | 49.5 | 1.0096
159.4 | 49.5 | 1.0096
159.5 | 49.5 | 1.0096
159.6 | 49.5 | 1.0096
159.7 | 49.5 | 1.0096
159.8 | 49.5 | 1.0096
159.9 | 49.5 | 1.0096
160 | 49.5 | 1.0096
160.1 | 49.5 | 1.0096
160.2 | 49.5 | 1.0096
160.3 | 49.5 | 1.0096
160.4 | 49.5 | 1.0096
160.5 | 49.5 | 1.0096
160.6 | 49.5 | 1.0096
160.7 | 49.5 | 1.0096
160.8 | 49.5 | 1.0096
160.9 | 49.5 | 1.0096
161 | 49.5 | 1.0096
161.1 | 49.5 | 1.0096
161.2 | 49.5 | 1.0096
161.3 | 49.5 | 1.0096
161.4 | 49.5 | 1.0096
161.5 | 49.5 | 1.0096
161.6 | 49.5 | 1.0096
161.7 | 49.5 | 1.0096
161.8 | 49.5 | 1.0096
161.9 | 49.5 | 1.0096
162 | 49.5 | 1.0096
162.1 | 49.5 | 1.0096
162.2 | 49.5 | 1.0096
162.3 | 49.5 | 1.0096
162.4 | 49.5 | 1.0096
162.5 | 49.5 | 1.0096
162.6 | 49.5 | 1.0096
162.7 | 49.5 | 1.0096
162.8 | 49.5 | 1.0096
162.9 | 49.5 | 1.0096
163 | 49.5 | 1.0096
163.1 | 49.5 | 1.0096
163.2 | 49.5 | 1.0096
163.3 | 49.5 | 1.0096
163.4 | 49.5 | 1.0096
163.5 | 49.5 | 1.0096
163.6 | 49.5 | 1.0096
163.7 | 49.5 | 1.0096
163.8 | 49.5 | 1.0096
163.9 | 49.5 | 1.0096
164 | 49.5 | 1.0096
164.1 | 49.5 | 1.0096
164.2 | 49.5 | 1.0096
164.3 | 49.5 | 1.0096
164.4 | 49.5 | 1.0096
164.5 | 49.5 | 1.0096
164.6 | 49.5 | 1.0096
164.7 | 49.5 | 1.0096
164.8 | 49.5 | 1.0096
164.9 | 49.5 | 1.0096
165 | 49.5 | 1.0096
165.1 | 49.5 | 1.0096
165.2 | 49.5 | 1.0096
165.3 | 49.5 | 1.0096
165.4 | 49.5 | 1.0096
165.5 | 49.5 | 1.0096
165.6 | 49.5 | 1.0096
165.7 | 49.5 | 1.0096
165.8 | 49.5 | 1.0096
165.9 | 49.5 | 1.0096
166 | 49.5 | 1.0096
166.1 | 49.5 | 1.0096
166.2 | 49.5 | 1.0096
166.3 | 49.5 | 1.0096
166.4 | 49.5 | 1.0096
166.5 | 49.5 | 1.0096
166.6 | 49.5 | 1.0096
166.7 | 49.5 | 1.0096
166.8 | 49.5 | 1.0096
166.9 | 49.5 | 1.0096
167 | 49.5 | 1.0096
167.1 | 49.5 | 1.0096
167.2 | 49.5 | 1.0096
167.3 | 49.5 | 1.0096
167.4 | 49.5 | 1.0096
167.5 | 49.5 | 1.0096
167.6 | 49.5 | 1.0096
167.7 | 49.5 | 1.0096
167.8 | 49.5 | 1.0096
167.9 | 49.5 | 1.0096
168 | 49.5 | 1.0096
168.1 | 49.5 | 1.0096
168.2 | 49.5 | 1.0096
168.3 | 49.5 | 1.0096
168.4 | 49.5 | 1.0096
168.5 | 49.5 | 1.0096
168.6 | 49.5 | 1.0096
168.7 | 49.5 | 1.0096
168.8 | 49.5 | 1.0096
168.9 | 49.5 | 1.0096
169 | 49.5 | 1.0096
169.1 | 49.5 | 1.0096
169.2 | 49.5 | 1.0096
169.3 | 49.5 | 1.0096
169.4 | 49.5 | 1.0096
169.5 | 49.5 | 1.0096
169.6 | 49.5 | 1.0096
169.7 | 49.5 | 1.0096
169.8 | 49.5 | 1.0096
169.9 | 49.5 | 1.0096
170 | 49.5 | 1.0096
170.1 | 49.5 | 1.0096
170.2 | 49.5 | 1.0096
170.3 | 49.5 | 1.0096
170.4 | 49.5 | 1.0096
170.5 | 49.5 | 1.0096
170.6 | 49.5 | 1.0096
170.7 | 49.5 | 1.0096
170.8 | 49.5 | 1.0096
170.9 | 49.5 | 1.0096
171 | 49.5 | 1.0096
171.1 | 49.5 | 1.0096
171.2 | 49.5 | 1.0096
171.3 | 49.5 | 1.0096
171.4 | 49.5 | 1.0096
171.5 | 49.5 | 1.0096
171.6 | 49.5 | 1.0096
171.7 | 49.5 | 1.0096
171.8 | 49.5 | 1.0096
171.9 | 49.5 | 1.0096
172 | 49.5 | 1.0096
172.1 | 49.5 | 1.0096
172.2 | 49.5 | 1.0096
172.3 | 49.5 | 1.0096
172.4 | 49.5 | 1.0096
172.5 | 49.5 | 1.0096
172.6 | 49.5 | 1.0096
172.7 | 49.5 | 1.0096
172.8 | 49.5 | 1.0096
172.9 | 49.5 | 1.0096
173 | 49.5 | 1.0096
173.1 | 49.5 | 1.0096
173.2 | 49.5 | 1.0096
173.3 | 49.5 | 1.0096
173.4 | 49.5 | 1.0096
173.5 | 49.5 | 1.0096
173.6 | 49.5 | 1.0096
173.7 | 49.5 | 1.0096
173.8 | 49.5 | 1.0096
173.9 | 49.5 | 1.0096
174 | 49.5 | 1.0096
174.1 | 49.5 | 1.0096
174.2 | 49.5 | 1.0096
174.3 | 49.5 | 1.0096
174.4 | 49.5 | 1.0096
174.5 | 49.5 | 1.0096
174.6 | 49.5 | 1.0096
174.7 | 49.5 | 1.0096
174.8 | 49.5 | 1.0096
174.9 | 49.5 | 1.0096
175 | 49.5 | 1.0096
175.1 | 49.5 | 1.0096
175.2 | 49.5 | 1.0096
175.3 | 49.5 | 1.0096
175.4 | 49.5 | 1.0096
175.5 | 49.5 | 1.0096
175.6 | 49.5 | 1.0096
175.7 | 49.5 | 1.0096
175.8 | 49.5 | 1.0096
175.9 | 49.5 | 1.0096
176 | 49.5 | 1.0096
176.1 | 49.5 | 1.0096
176.2 | 49.5 | 1.0096
176.3 | 49.5 | 1.0096
176.4 | 49.5 | 1.0096
176.5 | 49.5 | 1.0096
176.6 | 49.5 | 1.0096
176.7 | 49.5 | 1.0096
176.8 | 49.5 | 1.0096
176.9 | 49.5 | 1.0096
177 | 49.5 | 1.0096
177.1 | 49.5 | 1.0096
177.2 | 49.5 | 1.0096
177.3 | 49.5 | 1.0096
177.4 | 49.5 | 1.0096
177.5 | 49.5 | 1.0096
177.6 | 49.5 | 1.0096
177.7 | 49.5 | 1.0096
177.8 | 49.5 | 1.0096
177.9 | 49.5 | 1.0096
178 | 49.5 | 1.0096
178.1 | 49.5 | 1.0096
178.2 | 49.5 | 1.0096
178.3 | 49.5 | 1.0096
178.4 | 49.5 | 1.0096
178.5 | 49.5 | 1.0096
178.6 | 49.5 | 1.0096
178.7 | 49.5 | 1.0096
178.8 | 49.5 | 1.0096
178.9 | 49.5 | 1.0096
179 | 49.5 | 1.0096
179.1 | 49.5 | 1.0096
179.2 | 49.5 | 1.0096
179.3 | 49.5 | 1.0096
179.4 | 49.5 | 1.0096
179.5 | 49.5 | 1.0096
179.6 | 49.5 | 1.0096
179.7 | 49.5 | 1.0096
179.8 | 49.5 | 1.0096
179.9 | 49.5 | 1.0096
180 | 49.5 | 1.0096
180.1 | 49.5 | 1.0096
180.2 | 49.5 | 1.0096
180.3 | 49.5 | 1.0096
180.4 | 49.5 | 1.0096
180.5 | 49.5 | 1.0096
180.6 | 49.5 | 1.0096
180.7 | 49.5 | 1.0096
180.8 | 49.5 | 1.0096
180.9 | 49.5 | 1.0096
181 | 49.5 | 1.0096
181.1 | 49.5 | 1.0096
181.2 | 49.5 | 1.0096
181.3 | 49.5 | 1.0096
181.4 | 49.5 | 1.0096
181.5 | 49.5 | 1.0096
181.6 | 49.5 | 1.0096
181.7 | 49.5 | 1.0096
181.8 | 49.5 | 1.0096
181.9 | 49.5 | 1.0096
182 | 49.5 | 1.0096
182.1 | 49.5 | 1.0096
182.2 | 49.5 | 1.0096
182.3 | 49.5 | 1.0096
182.4 | 49.5 | 1.0096
182.5 | 49.5 | 1.0096
182.6 | 49.5 | 1.0096
182.7 | 49.5 | 1.0096
182.8 | 49.5 | 1.0096
182.9 | 49.5 | 1.0096
183 | 49.5 | 1.0096
183.1 | 49.5 | 1.0096
183.2 | 49.5 | 1.0096
183.3 | 49.5 | 1.0096
183.4 | 49.5 | 1.0096
183.5 | 49.5 | 1.0096
183.6 | 49.5 | 1.0096
183.7 | 49.5 | 1.0096
183.8 | 49.5 | 1.0096
183.9 | 49.5 | 1.0096
184 | 49.5 | 1.0096
184.1 | 49.5 | 1.0096
184.2 | 49.5 | 1.0096
184.3 | 49.5 | 1.0096
184.4 | 49.5 | 1.0096
184.5 | 49.5 | 1.0096
184.6 | 49.5 | 1.0096
184.7 | 49.5 | 1.0096
184.8 | 49.5 | 1.0096
184.9 | 49.5 | 1.0096
185 | 49.5 | 1.0096
185.1 | 49.5 | 1.0096
185.2 | 49.5 | 1.0096
185.3 | 49.5 | 1.0096
185.4 | 49.5 | 1.0096
185.5 | 49.5 | 1.0096
185.6 | 49.5 | 1.0096
185.7 | 49.5 | 1.0096
185.8 | 49.5 | 1.0096
185.9 | 49.5 | 1.0096
186 | 49.5 | 1.0096
186.1 | 49.5 | 1.0096
186.2 | 49.5 | 1.0096
186.3 | 49.5 | 1.0096
186.4 | 49.5 | 1.0096
186.5 | 49.5 | 1.0096
186.6 | 49.5 | 1.0096
186.7 | 49.5 | 1.0096
186.8 | 49.5 | 1.0096
186.9 | 49.5 | 1.0096
187 | 49.5 | 1.0096
187.1 | 49.5 | 1.0096
187.2 | 49.5 | 1.0096
187.3 | 49.5 | 1.0096
187.4 | 49.5 | 1.0096
187.5 | 49.5 | 1.0096
187.6 | 49.5 | 1.0096
187.7 | 49.5 | 1.0096
187.8 | 49.5 | 1.0096
187.9 | 49.5 | 1.0096
188 | 49.5 | 1.0096
188.1 | 49.5 | 1.0096
188.2 | 49.5 | 1.0096
188.3 | 49.5 | 1.0096
188.4 | 49.5 | 1.0096
188.5 | 49.5 | 1.0096
188.6 | 49.5 | 1.0096
188.7 | 49.5 | 1.0096
188.8 | 49.5 | 1.0096
188.9 | 49.5 | 1.0096
189 | 49.5 | 1.0096
189.1 | 49.5 | 1.0096
189.2 | 49.5 | 1.0096
189.3 | 49.5 | 1.0096
189.4 | 49.5 | 1.0096
189.5 | 49.5 | 1.0096
189.6 | 49.5 | 1.0096
189.7 | 49.5 | 1.0096
189.8 | 49.5 | 1.0096
189.9 | 49.5 | 1.0096
190 | 49.5 | 1.0096
190.1 | 49.5 | 1.0096
190.2 | 49.5 | 1.0096
190.3 | 49.5 | 1.0096
190.4 | 49.5 | 1.0096
190.5 | 49.5 | 1.0096
190.6 | 49.5 | 1.0096
190.7 | 49.5 | 1.0096
190.8 | 49.5 | 1.0096
190.9 | 49.5 | 1.0096
191 | 49.5 | 1.0096
191.1 | 49.5 | 1.0096
191.2 | 49.5 | 1.0096
191.3 | 49.5 | 1.0096
191.4 | 49.5 | 1.0096
191.5 | 49.5 | 1.0096
191.6 | 49.5 | 1.0096
191.7 | 49.5 | 1.0096
191.8 | 49.5 | 1.0096
191.9 | 49.5 | 1.0096
192 | 49.5 | 1.0096
192.1 | 49.5 | 1.0096
192.2 | 49.5 | 1.0096
192.3 | 49.5 | 1.0096
192.4 | 49.5 | 1.0096
192.5 | 49.5 | 1.0096
192.6 | 49.5 | 1.0096
192.7 | 49.5 | 1.0096
192.8 | 49.5 | 1.0096
192.9 | 49.5 | 1.0096
193 | 49.5 | 1.0096
193.1 | 49.5 | 1.0096
193.2 | 49.5 | 1.0096
193.3 | 49.5 | 1.0096
193.4 | 49.5 | 1.0096
193.5 | 49.5 | 1.0096
193.6 | 49.5 | 1.0096
193.7 | 49.5 | 1.0096
193.8 | 49.5 | 1.0096
193.9 | 49.5 | 1.0096
194 | 49.5 | 1.0096
194.1 | 49.5 | 1.0096
194.2 | 49.5 | 1.0098
194.3 | 49.5 | 1.0098
194.4 | 49.5 | 1.0098
194.5 | 49.5 | 1.0098
194.6 | 49.5 | 1.0098
194.7 | 49.5 | 1.0098
194.8 | 49.5 | 1.0098
194.9 | 49.5 | 1.0098
195 | 49.5 | 1.0098
195.1 | 49.5 | 1.0098
195.2 | 49.5 | 1.0098
195.3 | 49.5 | 1.0098
195.4 | 49.5 | 1.0098
195.5 | 49.5 | 1.0098
195.6 | 49.5 | 1.0098
195.7 | 49.5 | 1.0098
195.8 | 49.5 | 1.0098
195.9 | 49.5 | 1.0098
196 | 49.5 | 1.0098
196.1 | 49.5 | 1.0098
196.2 | 49.5 | 1.0098
196.3 | 49.5 | 1.0098
196.4 | 49.5 | 1.0098
196.5 | 49.5 | 1.0096
196.6 | 49.5 | 1.0096
196.7 | 49.5 | 1.0096
196.8 | 49.5 | 1.0096
196.9 | 49.5 | 1.0096
197 | 49.5 | 1.0096
197.1 | 49.5 | 1.0096
197.2 | 49.5 | 1.0096
197.3 | 49.5 | 1.0096
197.4 | 49.5 | 1.0096
197.5 | 49.5 | 1.0096
197.6 | 49.5 | 1.0096
197.7 | 49.5 | 1.0096
197.8 | 49.5 | 1.0096
197.9 | 49.5 | 1.0096
198 | 49.5 | 1.0096
198.1 | 49.5 | 1.0096
198.2 | 49.5 | 1.0096
198.3 | 49.5 | 1.0096
198.4 | 49.5 | 1.0096
198.5 | 49.5 | 1.0096
198.6 | 49.5 | 1.0096
198.7 | 49.5 | 1.0096
198.8 | 49.5 | 1.0096
198.9 | 49.5 | 1.0096
199 | 49.5 | 1.0096
199.1 | 49.5 | 1.0096
199.2 | 49.5 | 1.0096
199.3 | 49.5 | 1.0096
199.4 | 49.5 | 1.0096
199.5 | 49.5 | 1.0096
199.6 | 49.5 | 1.0096
199.7 | 49.5 | 1.0096
199.8 | 49.5 | 1.0096
199.9 | 49.5 | 1.0096
200 | 49.5 | 1.0096
200.1 | 49.5 | 1.0096
200.2 | 49.5 | 1.0096
200.3 | 49.5 | 1.0096
200.4 | 49.5 | 1.0096
200.5 | 49.5 | 1.0096
200.6 | 49.5 | 1.0096
200.7 | 49.5 | 1.0096
200.8 | 49.5 | 1.0096
200.9 | 49.5 | 1.0096
201 | 49.5 | 1.0096
201.1 | 49.5 | 1.0096
201.2 | 49.5 | 1.0096
201.3 | 49.5 | 1.0096
201.4 | 49.5 | 1.0096
201.5 | 49.5 | 1.0096
201.6 | 49.5 | 1.0096
201.7 | 49.5 | 1.0096
201.8 | 49.5 | 1.0096
201.9 | 49.5 | 1.0096
202 | 49.5 | 1.0096
202.1 | 49.5 | 1.0096
202.2 | 49.5 | 1.0096
202.3 | 49.5 | 1.0096
202.4 | 49.5 | 1.0096
202.5 | 49.5 | 1.0096
202.6 | 49.5 | 1.0096
202.7 | 49.5 | 1.0096
202.8 | 49.5 | 1.0096
202.9 | 49.5 | 1.0096
203 | 49.5 | 1.0096
203.1 | 49.5 | 1.0096
203.2 | 49.5 | 1.0096
203.3 | 49.5 | 1.0096
203.4 | 49.5 | 1.0096
203.5 | 49.5 | 1.0096
203.6 | 49.5 | 1.0096
203.7 | 49.5 | 1.0096
203.8 | 49.5 | 1.0096
203.9 | 49.5 | 1.0096
204 | 49.5 | 1.0096
204.1 | 49.5 | 1.0096
204.2 | 49.5 | 1.0096
204.3 | 49.5 | 1.0096
204.4 | 49.5 | 1.0096
204.5 | 49.5 | 1.0096
204.6 | 49.5 | 1.0096
204.7 | 49.5 | 1.0096
204.8 | 49.5 | 1.0096
204.9 | 49.5 | 1.0096
205 | 49.5 | 1.0096
205.1 | 49.5 | 1.0096
205.2 | 49.5 | 1.0096
205.3 | 49.5 | 1.0096
205.4 | 49.5 | 1.0096
205.5 | 49.5 | 1.0096
205.6 | 49.5 | 1.0096
205.7 | 49.5 | 1.0096
205.8 | 49.5 | 1.0096
205.9 | 49.5 | 1.0096
206 | 49.5 | 1.0096
206.1 | 49.5 | 1.0096
206.2 | 49.5 | 1.0096
206.3 | 49.5 | 1.0096
206.4 | 49.5 | 1.0096
206.5 | 49.5 | 1.0096
206.6 | 49.5 | 1.0096
206.7 | 49.5 | 1.0096
206.8 | 49.5 | 1.0096
206.9 | 49.5 | 1.0096
207 | 49.5 | 1.0096
207.1 | 49.5 | 1.0096
207.2 | 49.5 | 1.0096
207.3 | 49.5 | 1.0096
207.4 | 49.5 | 1.0096
207.5 | 49.5 | 1.0096
207.6 | 49.5 | 1.0096
207.7 | 49.5 | 1.0096
207.8 | 49.5 | 1.0096
207.9 | 49.5 | 1.0096
208 | 49.5 | 1.0096
208.1 | 49.5 | 1.0096
208.2 | 49.5 | 1.0096
208.3 | 49.5 | 1.0096
208.4 | 49.5 | 1.0096
208.5 | 49.5 | 1.0096
208.6 | 49.5 | 1.0096
208.7 | 49.5 | 1.0096
208.8 | 49.5 | 1.0096
208.9 | 49.5 | 1.0096
209 | 49.5 | 1.0096
209.1 | 49.5 | 1.0096
209.2 | 49.5 | 1.0096
209.3 | 49.5 | 1.0096
209.4 | 49.5 | 1.0096
209.5 | 49.5 | 1.0096
209.6 | 49.5 | 1.0096
209.7 | 49.5 | 1.0096
209.8 | 49.5 | 1.0096
209.9 | 49.5 | 1.0096
210 | 49.5 | 1.0096
210.1 | 49.5 | 1.0096
210.2 | 49.5 | 1.0096
210.3 | 49.5 | 1.0096
210.4 | 49.5 | 1.0096
210.5 | 49.5 | 1.0096
210.6 | 49.5 | 1.0096
210.7 | 49.5 | 1.0096
210.8 | 49.5 | 1.0096
210.9 | 49.5 | 1.0096
211 | 49.5 | 1.0096
211.1 | 49.5 | 1.0096
211.2 | 49.5 | 1.0096
211.3 | 49.5 | 1.0096
211.4 | 49.5 | 1.0096
211.5 | 49.5 | 1.0098
211.6 | 49.5 | 1.0098
211.7 | 49.5 | 1.0096
211.8 | 49.5 | 1.0096
211.9 | 49.5 | 1.0096
212 | 49.5 | 1.0096
212.1 | 49.5 | 1.0096
212.2 | 49.5 | 1.0096
212.3 | 49.5 | 1.0096
212.4 | 49.5 | 1.0096
212.5 | 49.5 | 1.0096
212.6 | 49.5 | 1.0096
212.7 | 49.5 | 1.0096
212.8 | 49.5 | 1.0096
212.9 | 49.5 | 1.0096
213 | 49.5 | 1.0096
213.1 | 49.5 | 1.0096
213.2 | 49.5 | 1.0096
213.3 | 49.5 | 1.0096
213.4 | 49.5 | 1.0096
213.5 | 49.5 | 1.0096
213.6 | 49.5 | 1.0096
213.7 | 49.5 | 1.0096
213.8 | 49.5 | 1.0096
213.9 | 49.5 | 1.0096
214 | 49.5 | 1.0096
214.1 | 49.5 | 1.0096
214.2 | 49.5 | 1.0096
214.3 | 49.5 | 1.0096
214.4 | 49.5 | 1.0096
214.5 | 49.5 | 1.0096
214.6 | 49.5 | 1.0096
214.7 | 49.5 | 1.0096
214.8 | 49.5 | 1.0096
214.9 | 49.5 | 1.0096
215 | 49.5 | 1.0096
215.1 | 49.5 | 1.0096
215.2 | 49.5 | 1.0096
215.3 | 49.5 | 1.0096
215.4 | 49.5 | 1.0096
215.5 | 49.5 | 1.0096
215.6 | 49.5 | 1.0096
215.7 | 49.5 | 1.0096
215.8 | 49.5 | 1.0096
215.9 | 49.5 | 1.0096
216 | 49.5 | 1.0096
216.1 | 49.5 | 1.0096
216.2 | 49.5 | 1.0096
216.3 | 49.5 | 1.0096
216.4 | 49.5 | 1.0096
216.5 | 49.5 | 1.0096
216.6 | 49.5 | 1.0096
216.7 | 49.5 | 1.0096
216.8 | 49.5 | 1.0096
216.9 | 49.5 | 1.0096
217 | 49.5 | 1.0096
217.1 | 49.5 | 1.0096
217.2 | 49.5 | 1.0096
217.3 | 49.5 | 1.0096
217.4 | 49.5 | 1.0096
217.5 | 49.5 | 1.0096
217.6 | 49.5 | 1.0096
217.7 | 49.5 | 1.0096
217.8 | 49.5 | 1.0096
217.9 | 49.5 | 1.0096
218 | 49.5 | 1.0096
218.1 | 49.5 | 1.0096
218.2 | 49.5 | 1.0096
218.3 | 49.5 | 1.0096
218.4 | 49.5 | 1.0096
218.5 | 49.5 | 1.0096
218.6 | 49.5 | 1.0096
218.7 | 49.5 | 1.0096
218.8 | 49.5 | 1.0096
218.9 | 49.5 | 1.0096
219 | 49.5 | 1.0096
219.1 | 49.5 | 1.0096
219.2 | 49.5 | 1.0096
219.3 | 49.5 | 1.0096
219.4 | 49.5 | 1.0096
219.5 | 49.5 | 1.0096
219.6 | 49.5 | 1.0096
219.7 | 49.5 | 1.0096
219.8 | 49.5 | 1.0096
219.9 | 49.5 | 1.0096
220 | 49.5 | 1.0096
220.1 | 49.5 | 1.0096
220.2 | 49.5 | 1.0096
220.3 | 49.5 | 1.0096
220.4 | 49.5 | 1.0096
220.5 | 49.5 | 1.0096
220.6 | 49.5 | 1.0096
220.7 | 49.5 | 1.0096
220.8 | 49.5 | 1.0096
220.9 | 49.5 | 1.0096
221 | 49.5 | 1.0096
221.1 | 49.5 | 1.0096
221.2 | 49.5 | 1.0096
221.3 | 49.5 | 1.0096
221.4 | 49.5 | 1.0096
221.5 | 49.5 | 1.0096
221.6 | 49.5 | 1.0096
221.7 | 49.5 | 1.0096
221.8 | 49.5 | 1.0096
221.9 | 49.5 | 1.0096
222 | 49.5 | 1.0096
222.1 | 49.5 | 1.0096
222.2 | 49.5 | 1.0096
222.3 | 49.5 | 1.0096
222.4 | 49.5 | 1.0096
222.5 | 49.5 | 1.0096
222.6 | 49.5 | 1.0096
222.7 | 49.5 | 1.0096
222.8 | 49.5 | 1.0096
222.9 | 49.5 | 1.0096
223 | 49.5 | 1.0096
223.1 | 49.5 | 1.0096
223.2 | 49.5 | 1.0096
223.3 | 49.5 | 1.0096
223.4 | 49.5 | 1.0096
223.5 | 49.5 | 1.0096
223.6 | 49.5 | 1.0096
223.7 | 49.5 | 1.0096
223.8 | 49.5 | 1.0096
223.9 | 49.5 | 1.0096
224 | 49.5 | 1.0096
224.1 | 49.5 | 1.0096
224.2 | 49.5 | 1.0096
224.3 | 49.5 | 1.0096
224.4 | 49.5 | 1.0096
224.5 | 49.5 | 1.0096
224.6 | 49.5 | 1.0096
224.7 | 49.5 | 1.0096
224.8 | 49.5 | 1.0096
224.9 | 49.5 | 1.0096
225 | 49.5 | 1.0096
225.1 | 49.5 | 1.0096
225.2 | 49.5 | 1.0096
225.3 | 49.5 | 1.0096
225.4 | 49.5 | 1.0096
225.5 | 49.5 | 1.0096
225.6 | 49.5 | 1.0096
225.7 | 49.5 | 1.0096
225.8 | 49.5 | 1.0096
225.9 | 49.5 | 1.0096
226 | 49.5 | 1.0096
226.1 | 49.5 | 1.0096
226.2 | 49.5 | 1.0096
226.3 | 49.5 | 1.0096
226.4 | 49.5 | 1.0096
226.5 | 49.5 | 1.0096
226.6 | 49.5 | 1.0096
226.7 | 49.5 | 1.0096
226.8 | 49.5 | 1.0096
226.9 | 49.5 | 1.0096
227 | 49.5 | 1.0096
227.1 | 49.5 | 1.0096
227.2 | 49.5 | 1.0096
227.3 | 49.5 | 1.0096
227.4 | 49.5 | 1.0096
227.5 | 49.5 | 1.0096
227.6 | 49.5 | 1.0096
227.7 | 49.5 | 1.0096
227.8 | 49.5 | 1.0096
227.9 | 49.5 | 1.0096
228 | 49.5 | 1.0096
228.1 | 49.5 | 1.0096
228.2 | 49.5 | 1.0096
228.3 | 49.5 | 1.0096
228.4 | 49.5 | 1.0096
228.5 | 49.5 | 1.0096
228.6 | 49.5 | 1.0096
228.7 | 49.5 | 1.0096
228.8 | 49.5 | 1.0096
228.9 | 49.5 | 1.0096
229 | 49.5 | 1.0096
229.1 | 49.5 | 1.0096
229.2 | 49.5 | 1.0096
229.3 | 49.5 | 1.0096
229.4 | 49.5 | 1.0096
229.5 | 49.5 | 1.0096
229.6 | 49.5 | 1.0096
229.7 | 49.5 | 1.0096
229.8 | 49.5 | 1.0096
229.9 | 49.5 | 1.0096
230 | 49.5 | 1.0096
230.1 | 49.5 | 1.0096
230.2 | 49.5 | 1.0096
230.3 | 49.5 | 1.0096
230.4 | 49.5 | 1.0096
230.5 | 49.5 | 1.0096
230.6 | 49.5 | 1.0096
230.7 | 49.5 | 1.0096
230.8 | 49.5 | 1.0096
230.9 | 49.5 | 1.0096
231 | 49.5 | 1.0096
231.1 | 49.5 | 1.0096
231.2 | 49.5 | 1.0096
231.3 | 49.5 | 1.0096
231.4 | 49.5 | 1.0096
231.5 | 49.5 | 1.0096
231.6 | 49.5 | 1.0096
231.7 | 49.5 | 1.0096
231.8 | 49.5 | 1.0096
231.9 | 49.5 | 1.0096
232 | 49.5 | 1.0096
232.1 | 49.5 | 1.0096
232.2 | 49.5 | 1.0096
232.3 | 49.5 | 1.0096
232.4 | 49.5 | 1.0096
232.5 | 49.5 | 1.0096
232.6 | 49.5 | 1.0096
232.7 | 49.5 | 1.0096
232.8 | 49.5 | 1.0096
232.9 | 49.5 | 1.0096
233 | 49.5 | 1.0096
233.1 | 49.5 | 1.0096
233.2 | 49.5 | 1.0096
233.3 | 49.5 | 1.0096
233.4 | 49.5 | 1.0096
233.5 | 49.5 | 1.0096
233.6 | 49.5 | 1.0096
233.7 | 49.5 | 1.0096
233.8 | 49.5 | 1.0096
233.9 | 49.5 | 1.0096
234 | 49.5 | 1.0096
234.1 | 49.5 | 1.0096
234.2 | 49.5 | 1.0096
234.3 | 49.5 | 1.0096
234.4 | 49.5 | 1.0096
234.5 | 49.5 | 1.0096
234.6 | 49.5 | 1.0096
234.7 | 49.5 | 1.0096
234.8 | 49.5 | 1.0096
234.9 | 49.5 | 1.0096
235 | 49.5 | 1.0096
235.1 | 49.5 | 1.0096
235.2 | 49.5 | 1.0096
235.3 | 49.5 | 1.0096
235.4 | 49.5 | 1.0096
235.5 | 49.5 | 1.0096
235.6 | 49.5 | 1.0096
235.7 | 49.5 | 1.0096
235.8 | 49.5 | 1.0096
235.9 | 49.5 | 1.0096
236 | 49.5 | 1.0096
236.1 | 49.5 | 1.0096
236.2 | 49.5 | 1.0096
236.3 | 49.5 | 1.0096
236.4 | 49.5 | 1.0096
236.5 | 49.5 | 1.0096
236.6 | 49.5 | 1.0096
236.7 | 49.5 | 1.0096
236.8 | 49.5 | 1.0096
236.9 | 49.5 | 1.0096
237 | 49.5 | 1.0096
237.1 | 49.5 | 1.0096
237.2 | 49.5 | 1.0096
237.3 | 49.5 | 1.0096
237.4 | 49.5 | 1.0096
237.5 | 49.5 | 1.0096
237.6 | 49.5 | 1.0096
237.7 | 49.5 | 1.0096
237.8 | 49.5 | 1.0096
237.9 | 49.5 | 1.0096
238 | 49.5 | 1.0096
238.1 | 49.5 | 1.0096
238.2 | 49.5 | 1.0096
238.3 | 49.5 | 1.0096
238.4 | 49.5 | 1.0096
238.5 | 49.5 | 1.0096
238.6 | 49.5 | 1.0096
238.7 | 49.5 | 1.0096
238.8 | 49.5 | 1.0096
238.9 | 49.5 | 1.0096
239 | 49.5 | 1.0096
239.1 | 49.5 | 1.0096
239.2 | 49.5 | 1.0096
239.3 | 49.5 | 1.0096
239.4 | 49.5 | 1.0096
239.5 | 49.5 | 1.0096
239.6 | 49.5 | 1.0096
239.7 | 49.5 | 1.0096
239.8 | 49.5 | 1.0096
239.9 | 49.5 | 1.0096
240 | 49.5 | 1.0096
240.1 | 49.5 | 1.0096
240.2 | 49.5 | 1.0096
240.3 | 49.5 | 1.0096
240.4 | 49.5 | 1.0096
240.5 | 49.5 | 1.0096
240.6 | 49.5 | 1.0096
240.7 | 49.5 | 1.0096
240.8 | 49.5 | 1.0096
240.9 | 49.5 | 1.0096
241 | 49.5 | 1.0096
241.1 | 49.5 | 1.0096
241.2 | 49.5 | 1.0096
241.3 | 49.5 | 1.0096
241.4 | 49.5 | 1.0096
241.5 | 49.5 | 1.0096
241.6 | 49.5 | 1.0096
241.7 | 49.5 | 1.0096
241.8 | 49.5 | 1.0096
241.9 | 49.5 | 1.0096
242 | 49.5 | 1.0096
242.1 | 49.5 | 1.0096
242.2 | 49.5 | 1.0096
242.3 | 49.5 | 1.0096
242.4 | 49.5 | 1.0096
242.5 | 49.5 | 1.0096
242.6 | 49.5 | 1.0096
242.7 | 49.5 | 1.0096
242.8 | 49.5 | 1.0096
242.9 | 49.5 | 1.0096
243 | 49.5 | 1.0096
243.1 | 49.5 | 1.0096
243.2 | 49.5 | 1.0096
243.3 | 49.5 | 1.0096
243.4 | 49.5 | 1.0096
243.5 | 49.5 | 1.0096
243.6 | 49.5 | 1.0096
243.7 | 49.5 | 1.0096
243.8 | 49.5 | 1.0096
243.9 | 49.5 | 1.0096
244 | 49.5 | 1.0096
244.1 | 49.5 | 1.0096
244.2 | 49.5 | 1.0096
244.3 | 49.5 | 1.0096
244.4 | 49.5 | 1.0096
244.5 | 49.5 | 1.0096
244.6 | 49.5 | 1.0096
244.7 | 49.5 | 1.0096
244.8 | 49.5 | 1.0096
244.9 | 49.5 | 1.0096
245 | 49.5 | 1.0096
245.1 | 49.5 | 1.0096
245.2 | 49.5 | 1.0096
245.3 | 49.5 | 1.0096
245.4 | 49.5 | 1.0096
245.5 | 49.5 | 1.0096
245.6 | 49.5 | 1.0096
245.7 | 49.5 | 1.0096
245.8 | 49.5 | 1.0096
245.9 | 49.5 | 1.0096
246 | 49.5 | 1.0096
246.1 | 49.5 | 1.0096
246.2 | 49.5 | 1.0096
246.3 | 49.5 | 1.0096
246.4 | 49.5 | 1.0096
246.5 | 49.5 | 1.0096
246.6 | 49.5 | 1.0098
246.7 | 49.5 | 1.0098
246.8 | 49.5 | 1.0098
246.9 | 49.5 | 1.0098
247 | 49.5 | 1.0098
247.1 | 49.5 | 1.0098
247.2 | 49.5 | 1.0098
247.3 | 49.5 | 1.0098
247.4 | 49.5 | 1.0098
247.5 | 49.5 | 1.0098
247.6 | 49.5 | 1.0098
247.7 | 49.5 | 1.0096
247.8 | 49.5 | 1.0096
247.9 | 49.5 | 1.0096
248 | 49.5 | 1.0096
248.1 | 49.5 | 1.0096
248.2 | 49.5 | 1.0096
248.3 | 49.5 | 1.0096
248.4 | 49.5 | 1.0096
248.5 | 49.5 | 1.0096
248.6 | 49.5 | 1.0096
248.7 | 49.5 | 1.0096
248.8 | 49.5 | 1.0096
248.9 | 49.5 | 1.0096
249 | 49.5 | 1.0096
249.1 | 49.5 | 1.0096
249.2 | 49.5 | 1.0096
249.3 | 49.5 | 1.0096
249.4 | 49.5 | 1.0096
249.5 | 49.5 | 1.0096
249.6 | 49.5 | 1.0096
249.7 | 49.5 | 1.0096
249.8 | 49.5 | 1.0096
249.9 | 49.5 | 1.0096
250 | 49.5 | 1.0096
250.1 | 49.5 | 1.0096
250.2 | 49.5 | 1.0096
250.3 | 49.5 | 1.0096
250.4 | 49.5 | 1.0096
250.5 | 49.5 | 1.0096
250.6 | 49.5 | 1.0096
250.7 | 49.5 | 1.0096
250.8 | 49.5 | 1.0096
250.9 | 49.5 | 1.0096
251 | 49.5 | 1.0096
251.1 | 49.5 | 1.0096
251.2 | 49.5 | 1.0096
251.3 | 49.5 | 1.0096
251.4 | 49.5 | 1.0096
251.5 | 49.5 | 1.0096
251.6 | 49.5 | 1.0096
251.7 | 49.5 | 1.0096
251.8 | 49.5 | 1.0096
251.9 | 49.5 | 1.0096
252 | 49.5 | 1.0096
252.1 | 49.5 | 1.0096
252.2 | 49.5 | 1.0096
252.3 | 49.5 | 1.0096
252.4 | 49.5 | 1.0096
252.5 | 49.5 | 1.0096
252.6 | 49.5 | 1.0096
252.7 | 49.5 | 1.0096
252.8 | 49.5 | 1.0096
252.9 | 49.5 | 1.0096
253 | 49.5 | 1.0096
253.1 | 49.5 | 1.0096
253.2 | 49.5 | 1.0096
253.3 | 49.5 | 1.0096
253.4 | 49.5 | 1.0096
253.5 | 49.5 | 1.0096
253.6 | 49.5 | 1.0096
253.7 | 49.5 | 1.0096
253.8 | 49.5 | 1.0096
253.9 | 49.5 | 1.0096
254 | 49.5 | 1.0096
254.1 | 49.5 | 1.0096
254.2 | 49.5 | 1.0096
254.3 | 49.5 | 1.0096
254.4 | 49.5 | 1.0096
254.5 | 49.5 | 1.0096
254.6 | 49.5 | 1.0096
254.7 | 49.5 | 1.0096
254.8 | 49.5 | 1.0096
254.9 | 49.5 | 1.0096
255 | 49.5 | 1.0096
255.1 | 49.5 | 1.0096
255.2 | 49.5 | 1.0096
255.3 | 49.5 | 1.0096
255.4 | 49.5 | 1.0096
255.5 | 49.5 | 1.0096
255.6 | 49.5 | 1.0096
255.7 | 49.5 | 1.0096
255.8 | 49.5 | 1.0096
255.9 | 49.5 | 1.0096
256 | 49.5 | 1.0096
256.1 | 49.5 | 1.0096
256.2 | 49.5 | 1.0096
256.3 | 49.5 | 1.0096
256.4 | 49.5 | 1.0096
256.5 | 49.5 | 1.0096
256.6 | 49.5 | 1.0096
256.7 | 49.5 | 1.0096
256.8 | 49.5 | 1.0096
256.9 | 49.5 | 1.0096
257 | 49.5 | 1.0096
257.1 | 49.5 | 1.0096
257.2 | 49.5 | 1.0096
257.3 | 49.5 | 1.0096
257.4 | 49.5 | 1.0096
257.5 | 49.5 | 1.0096
257.6 | 49.5 | 1.0096
257.7 | 49.5 | 1.0096
257.8 | 49.5 | 1.0096
257.9 | 49.5 | 1.0096
258 | 49.5 | 1.0096
258.1 | 49.5 | 1.0096
258.2 | 49.5 | 1.0096
258.3 | 49.5 | 1.0096
258.4 | 49.5 | 1.0096
258.5 | 49.5 | 1.0096
258.6 | 49.5 | 1.0096
258.7 | 49.5 | 1.0096
258.8 | 49.5 | 1.0096
258.9 | 49.5 | 1.0096
259 | 49.5 | 1.0096
259.1 | 49.5 | 1.0096
259.2 | 49.5 | 1.0096
259.3 | 49.5 | 1.0096
259.4 | 49.5 | 1.0096
259.5 | 49.5 | 1.0096
259.6 | 49.5 | 1.0096
259.7 | 49.5 | 1.0096
259.8 | 49.5 | 1.0096
259.9 | 49.5 | 1.0096
260 | 49.5 | 1.0096
260.1 | 49.5 | 1.0096
260.2 | 49.5 | 1.0096
260.3 | 49.5 | 1.0096
260.4 | 49.5 | 1.0096
260.5 | 49.5 | 1.0096
260.6 | 49.5 | 1.0096
260.7 | 49.5 | 1.0096
260.8 | 49.5 | 1.0096
260.9 | 49.5 | 1.0096
261 | 49.5 | 1.0096
261.1 | 49.5 | 1.0096
261.2 | 49.5 | 1.0096
261.3 | 49.5 | 1.0096
261.4 | 49.5 | 1.0096
261.5 | 49.5 | 1.0096
261.6 | 49.5 | 1.0096
261.7 | 49.5 | 1.0096
261.8 | 49.5 | 1.0096
261.9 | 49.5 | 1.0096
262 | 49.5 | 1.0096
262.1 | 49.5 | 1.0096
262.2 | 49.5 | 1.0096
262.3 | 49.5 | 1.0096
262.4 | 49.5 | 1.0096
262.5 | 49.5 | 1.0096
262.6 | 49.5 | 1.0096
262.7 | 49.5 | 1.0096
262.8 | 49.5 | 1.0096
262.9 | 49.5 | 1.0096
263 | 49.5 | 1.0096
263.1 | 49.5 | 1.0096
263.2 | 49.5 | 1.0096
263.3 | 49.5 | 1.0096
263.4 | 49.5 | 1.0096
263.5 | 49.5 | 1.0096
263.6 | 49.5 | 1.0096
263.7 | 49.5 | 1.0096
263.8 | 49.5 | 1.0096
263.9 | 49.5 | 1.0096
264 | 49.5 | 1.0096
264.1 | 49.5 | 1.0096
264.2 | 49.5 | 1.0096
264.3 | 49.5 | 1.0096
264.4 | 49.5 | 1.0096
264.5 | 49.5 | 1.0096
264.6 | 49.5 | 1.0096
264.7 | 49.5 | 1.0096
264.8 | 49.5 | 1.0096
264.9 | 49.5 | 1.0096
265 | 49.5 | 1.0096
265.1 | 49.5 | 1.0096
265.2 | 49.5 | 1.0096
265.3 | 49.5 | 1.0096
265.4 | 49.5 | 1.0096
265.5 | 49.5 | 1.0096
265.6 | 49.5 | 1.0096
265.7 | 49.5 | 1.0096
265.8 | 49.5 | 1.0096
265.9 | 49.5 | 1.0096
266 | 49.5 | 1.0096
266.1 | 49.5 | 1.0096
266.2 | 49.5 | 1.0096
266.3 | 49.5 | 1.0096
266.4 | 49.5 | 1.0096
266.5 | 49.5 | 1.0096
266.6 | 49.5 | 1.0096
266.7 | 49.5 | 1.0096
266.8 | 49.5 | 1.0096
266.9 | 49.5 | 1.0096
267 | 49.5 | 1.0096
267.1 | 49.5 | 1.0096
267.2 | 49.5 | 1.0096
267.3 | 49.5 | 1.0096
267.4 | 49.5 | 1.0096
267.5 | 49.5 | 1.0096
267.6 | 49.5 | 1.0096
267.7 | 49.5 | 1.0096
267.8 | 49.5 | 1.0096
267.9 | 49.5 | 1.0096
268 | 49.5 | 1.0096
268.1 | 49.5 | 1.0096
268.2 | 49.5 | 1.0096
268.3 | 49.5 | 1.0096
268.4 | 49.5 | 1.0096
268.5 | 49.5 | 1.0096
268.6 | 49.5 | 1.0096
268.7 | 49.5 | 1.0096
268.8 | 49.5 | 1.0096
268.9 | 49.5 | 1.0096
269 | 49.5 | 1.0096
269.1 | 49.5 | 1.0096
269.2 | 49.5 | 1.0096
269.3 | 49.5 | 1.0096
269.4 | 49.5 | 1.0096
269.5 | 49.5 | 1.0096
269.6 | 49.5 | 1.0096
269.7 | 49.5 | 1.0096
269.8 | 49.5 | 1.0096
269.9 | 49.5 | 1.0096
270 | 49.5 | 1.0096
270.1 | 49.5 | 1.0096
270.2 | 49.5 | 1.0096
270.3 | 49.5 | 1.0096
270.4 | 49.5 | 1.0096
270.5 | 49.5 | 1.0096
270.6 | 49.5 | 1.0096
270.7 | 49.5 | 1.0096
270.8 | 49.5 | 1.0096
270.9 | 49.5 | 1.0096
271 | 49.5 | 1.0096
271.1 | 49.5 | 1.0096
271.2 | 49.5 | 1.0096
271.3 | 49.5 | 1.0096
271.4 | 49.5 | 1.0096
271.5 | 49.5 | 1.0096
271.6 | 49.5 | 1.0096
271.7 | 49.5 | 1.0096
271.8 | 49.5 | 1.0096
271.9 | 49.5 | 1.0096
272 | 49.5 | 1.0096
272.1 | 49.5 | 1.0096
272.2 | 49.5 | 1.0096
272.3 | 49.5 | 1.0096
272.4 | 49.5 | 1.0096
272.5 | 49.5 | 1.0096
272.6 | 49.5 | 1.0096
272.7 | 49.5 | 1.0096
272.8 | 49.5 | 1.0096
272.9 | 49.5 | 1.0096
273 | 49.5 | 1.0096
273.1 | 49.5 | 1.0096
273.2 | 49.5 | 1.0096
273.3 | 49.5 | 1.0096
273.4 | 49.5 | 1.0096
273.5 | 49.5 | 1.0096
273.6 | 49.5 | 1.0096
273.7 | 49.5 | 1.0096
273.8 | 49.5 | 1.0096
273.9 | 49.5 | 1.0096
274 | 49.5 | 1.0096
274.1 | 49.5 | 1.0096
274.2 | 49.5 | 1.0096
274.3 | 49.5 | 1.0096
274.4 | 49.5 | 1.0096
274.5 | 49.5 | 1.0096
274.6 | 49.5 | 1.0096
274.7 | 49.5 | 1.0096
274.8 | 49.5 | 1.0096
274.9 | 49.5 | 1.0096
275 | 49.5 | 1.0096
275.1 | 49.5 | 1.0096
275.2 | 49.5 | 1.0096
275.3 | 49.5 | 1.0096
275.4 | 49.5 | 1.0096
275.5 | 49.5 | 1.0096
275.6 | 49.5 | 1.0096
275.7 | 49.5 | 1.0096
275.8 | 49.5 | 1.0096
275.9 | 49.5 | 1.0096
276 | 49.5 | 1.0096
276.1 | 49.5 | 1.0096
276.2 | 49.5 | 1.0096
276.3 | 49.5 | 1.0096
276.4 | 49.5 | 1.0096
276.5 | 49.5 | 1.0096
276.6 | 49.5 | 1.0096
276.7 | 49.5 | 1.0096
276.8 | 49.5 | 1.0096
276.9 | 49.5 | 1.0096
277 | 49.5 | 1.0096
277.1 | 49.5 | 1.0096
277.2 | 49.5 | 1.0096
277.3 | 49.5 | 1.0096
277.4 | 49.5 | 1.0096
277.5 | 49.5 | 1.0096
277.6 | 49.5 | 1.0096
277.7 | 49.5 | 1.0096
277.8 | 49.5 | 1.0096
277.9 | 49.5 | 1.0096
278 | 49.5 | 1.0096
278.1 | 49.5 | 1.0096
278.2 | 49.5 | 1.0096
278.3 | 49.5 | 1.0096
278.4 | 49.5 | 1.0096
278.5 | 49.5 | 1.0096
278.6 | 49.5 | 1.0096
278.7 | 49.5 | 1.0096
278.8 | 49.5 | 1.0096
278.9 | 49.5 | 1.0096
279 | 49.5 | 1.0096
279.1 | 49.5 | 1.0096
279.2 | 49.5 | 1.0096
279.3 | 49.5 | 1.0096
279.4 | 49.5 | 1.0096
279.5 | 49.5 | 1.0096
279.6 | 49.5 | 1.0096
279.7 | 49.5 | 1.0096
279.8 | 49.5 | 1.0096
279.9 | 49.5 | 1.0096
280 | 49.5 | 1.0096
280.1 | 49.5 | 1.0096
280.2 | 49.5 | 1.0096
280.3 | 49.5 | 1.0096
280.4 | 49.5 | 1.0096
280.5 | 49.5 | 1.0096
280.6 | 49.5 | 1.0096
280.7 | 49.5 | 1.0096
280.8 | 49.5 | 1.0096
280.9 | 49.5 | 1.0098
281 | 49.5 | 1.0098
281.1 | 49.5 | 1.0098
281.2 | 49.5 | 1.0098
281.3 | 49.5 | 1.0098
281.4 | 49.5 | 1.0098
281.5 | 49.5 | 1.0098
281.6 | 49.5 | 1.0098
281.7 | 49.5 | 1.0098
281.8 | 49.5 | 1.0098
281.9 | 49.5 | 1.0098
282 | 49.5 | 1.0098
282.1 | 49.5 | 1.0096
282.2 | 49.5 | 1.0096
282.3 | 49.5 | 1.0096
282.4 | 49.5 | 1.0096
282.5 | 49.5 | 1.0096
282.6 | 49.5 | 1.0096
282.7 | 49.5 | 1.0096
282.8 | 49.5 | 1.0096
282.9 | 49.5 | 1.0096
283 | 49.5 | 1.0096
283.1 | 49.5 | 1.0096
283.2 | 49.5 | 1.0096
283.3 | 49.5 | 1.0094
283.4 | 49.5 | 1.0094
283.5 | 49.5 | 1.0094
283.6 | 49.5 | 1.0094
283.7 | 49.5 | 1.0094
283.8 | 49.5 | 1.0094
283.9 | 49.5 | 1.0094
284 | 49.5 | 1.0094
284.1 | 49.5 | 1.0094
284.2 | 49.5 | 1.0094
284.3 | 49.5 | 1.0094
284.4 | 49.5 | 1.0094
284.5 | 49.5 | 1.0096
284.6 | 49.5 | 1.0096
284.7 | 49.5 | 1.0096
284.8 | 49.5 | 1.0096
284.9 | 49.5 | 1.0096
285 | 49.5 | 1.0096
285.1 | 49.5 | 1.0096
285.2 | 49.5 | 1.0096
285.3 | 49.5 | 1.0096
285.4 | 49.5 | 1.0096
285.5 | 49.5 | 1.0096
285.6 | 49.5 | 1.0096
285.7 | 49.5 | 1.0096
285.8 | 49.5 | 1.0096
285.9 | 49.5 | 1.0096
286 | 49.5 | 1.0096
286.1 | 49.5 | 1.0096
286.2 | 49.5 | 1.0096
286.3 | 49.5 | 1.0096
286.4 | 49.5 | 1.0096
286.5 | 49.5 | 1.0096
286.6 | 49.5 | 1.0096
286.7 | 49.5 | 1.0096
286.8 | 49.5 | 1.0098
286.9 | 49.5 | 1.0098
287 | 49.5 | 1.0098
287.1 | 49.5 | 1.0098
287.2 | 49.5 | 1.0098
287.3 | 49.5 | 1.0098
287.4 | 49.5 | 1.0098
287.5 | 49.5 | 1.0098
287.6 | 49.5 | 1.0098
287.7 | 49.5 | 1.0098
287.8 | 49.5 | 1.0098
287.9 | 49.5 | 1.0098
288 | 49.5 | 1.0096
288.1 | 49.5 | 1.0096
288.2 | 49.5 | 1.0096
288.3 | 49.5 | 1.0096
288.4 | 49.5 | 1.0096
288.5 | 49.5 | 1.0096
288.6 | 49.5 | 1.0096
288.7 | 49.5 | 1.0096
288.8 | 49.5 | 1.0096
288.9 | 49.5 | 1.0096
289 | 49.5 | 1.0096
289.1 | 49.5 | 1.0094
289.2 | 49.5 | 1.0096
289.3 | 49.5 | 1.0096
289.4 | 49.5 | 1.0096
289.5 | 49.5 | 1.0096
289.6 | 49.5 | 1.0096
289.7 | 49.5 | 1.0096
289.8 | 49.5 | 1.0096
289.9 | 49.5 | 1.0096
290 | 49.5 | 1.0096
290.1 | 49.5 | 1.0096
290.2 | 49.5 | 1.0096
290.3 | 49.5 | 1.0096
290.4 | 49.5 | 1.0096
290.5 | 49.5 | 1.0096
290.6 | 49.5 | 1.0096
290.7 | 49.5 | 1.0096
290.8 | 49.5 | 1.0096
290.9 | 49.5 | 1.0096
291 | 49.5 | 1.0096
291.1 | 49.5 | 1.0096
291.2 | 49.5 | 1.0096
291.3 | 49.5 | 1.0094
291.4 | 49.5 | 1.0096
291.5 | 49.5 | 1.0096
291.6 | 49.5 | 1.0096
291.7 | 49.5 | 1.0096
291.8 | 49.5 | 1.0096
291.9 | 49.5 | 1.0096
292 | 49.5 | 1.0096
292.1 | 49.5 | 1.0096
292.2 | 49.5 | 1.0096
292.3 | 49.5 | 1.0096
292.4 | 49.5 | 1.0096
292.5 | 49.5 | 1.0096
292.6 | 49.5 | 1.0098
292.7 | 49.5 | 1.0098
292.8 | 49.5 | 1.0098
292.9 | 49.5 | 1.0098
293 | 49.5 | 1.0098
293.1 | 49.5 | 1.0098
293.2 | 49.5 | 1.0098
293.3 | 49.5 | 1.0098
293.4 | 49.5 | 1.0098
293.5 | 49.5 | 1.0098
293.6 | 49.5 | 1.0098
293.7 | 49.5 | 1.0098
293.8 | 49.5 | 1.0096
293.9 | 49.5 | 1.0096
294 | 49.5 | 1.0096
294.1 | 49.5 | 1.0096
294.2 | 49.5 | 1.0096
294.3 | 49.5 | 1.0096
294.4 | 49.5 | 1.0096
294.5 | 49.5 | 1.0096
294.6 | 49.5 | 1.0096
294.7 | 49.5 | 1.0096
294.8 | 49.5 | 1.0096
294.9 | 49.5 | 1.0096
295 | 49.5 | 1.0096
295.1 | 49.5 | 1.0096
295.2 | 49.5 | 1.0096
295.3 | 49.5 | 1.0096
295.4 | 49.5 | 1.0096
295.5 | 49.5 | 1.0096
295.6 | 49.5 | 1.0096
295.7 | 49.5 | 1.0096
295.8 | 49.5 | 1.0096
295.9 | 49.5 | 1.0096
296 | 49.5 | 1.0096
296.1 | 49.5 | 1.0096
296.2 | 49.5 | 1.0096
296.3 | 49.5 | 1.0096
296.4 | 49.5 | 1.0096
296.5 | 49.5 | 1.0096
296.6 | 49.5 | 1.0096
296.7 | 49.5 | 1.0096
296.8 | 49.5 | 1.0096
296.9 | 49.5 | 1.0096
297 | 49.5 | 1.0096
297.1 | 49.5 | 1.0096
297.2 | 49.5 | 1.0096
297.3 | 49.5 | 1.0096
297.4 | 49.5 | 1.0096
297.5 | 49.5 | 1.0096
297.6 | 49.5 | 1.0096
297.7 | 49.5 | 1.0096
297.8 | 49.5 | 1.0096
297.9 | 49.5 | 1.0096
298 | 49.5 | 1.0096
298.1 | 49.5 | 1.0096
298.2 | 49.5 | 1.0096
298.3 | 49.5 | 1.0096
298.4 | 49.5 | 1.0096
298.5 | 49.5 | 1.0096
298.6 | 49.5 | 1.0098
298.7 | 49.5 | 1.0098
298.8 | 49.5 | 1.0098
298.9 | 49.5 | 1.0098
299 | 49.5 | 1.0098
299.1 | 49.5 | 1.0098
299.2 | 49.5 | 1.0098
299.3 | 49.5 | 1.0098
299.4 | 49.5 | 1.0098
299.5 | 49.5 | 1.0098
299.6 | 49.5 | 1.0098
299.7 | 49.5 | 1.0098
299.8 | 49.5 | 1.0098
299.9 | 49.5 | 1.0098
300 | 49.5 | 1.0098
300.1 | 49.5 | 1.0098
300.2 | 49.5 | 1.0098
300.3 | 49.5 | 1.0098
300.4 | 49.5 | 1.0098
300.5 | 49.5 | 1.0098
300.6 | 49.5 | 1.0098
300.7 | 49.5 | 1.0098
300.8 | 49.5 | 1.0098
300.9 | 49.5 | 1.0096
301 | 49.5 | 1.0096
301.1 | 49.5 | 1.0096
301.2 | 49.5 | 1.0096
301.3 | 49.5 | 1.0096
301.4 | 49.5 | 1.0096
301.5 | 49.5 | 1.0096
301.6 | 49.5 | 1.0096
301.7 | 49.5 | 1.0096
301.8 | 49.5 | 1.0096
301.9 | 49.5 | 1.0096
302 | 49.5 | 1.0096
302.1 | 49.5 | 1.0096
302.2 | 49.5 | 1.0096
302.3 | 49.5 | 1.0096
302.4 | 49.5 | 1.0096
302.5 | 49.5 | 1.0096
302.6 | 49.5 | 1.0096
302.7 | 49.5 | 1.0096
302.8 | 49.5 | 1.0096
302.9 | 49.5 | 1.0096
303 | 49.5 | 1.0096
303.1 | 49.5 | 1.0096
303.2 | 49.5 | 1.0096
303.3 | 49.5 | 1.0096
303.4 | 49.5 | 1.0096
303.5 | 49.5 | 1.0096
303.6 | 49.5 | 1.0096
303.7 | 49.5 | 1.0096
303.8 | 49.5 | 1.0096
303.9 | 49.5 | 1.0096
304 | 49.5 | 1.0096
304.1 | 49.5 | 1.0096
304.2 | 49.5 | 1.0096
304.3 | 49.5 | 1.0096
304.4 | 49.5 | 1.0098
304.5 | 49.5 | 1.0098
304.6 | 49.5 | 1.0098
304.7 | 49.5 | 1.0098
304.8 | 49.5 | 1.0098
304.9 | 49.5 | 1.0098
305 | 49.5 | 1.0098
305.1 | 49.5 | 1.0098
305.2 | 49.5 | 1.0098
305.3 | 49.5 | 1.0098
305.4 | 49.5 | 1.0098
305.5 | 49.5 | 1.0098
305.6 | 49.5 | 1.0098
305.7 | 49.5 | 1.0098
305.8 | 49.5 | 1.0098
305.9 | 49.5 | 1.0098
306 | 49.5 | 1.0098
306.1 | 49.5 | 1.0098
306.2 | 49.5 | 1.0098
306.3 | 49.5 | 1.0098
306.4 | 49.5 | 1.0098
306.5 | 49.5 | 1.0098
306.6 | 49.5 | 1.0098
306.7 | 49.5 | 1.0098
306.8 | 49.5 | 1.0098
306.9 | 49.5 | 1.0098
307 | 49.5 | 1.0098
307.1 | 49.5 | 1.0098
307.2 | 49.5 | 1.0098
307.3 | 49.5 | 1.0098
307.4 | 49.5 | 1.0098
307.5 | 49.5 | 1.0098
307.6 | 49.5 | 1.0098
307.7 | 49.5 | 1.0098
307.8 | 49.5 | 1.0096
307.9 | 49.5 | 1.0096
308 | 49.5 | 1.0096
308.1 | 49.5 | 1.0096
308.2 | 49.5 | 1.0096
308.3 | 49.5 | 1.0096
308.4 | 49.5 | 1.0096
308.5 | 49.5 | 1.0096
308.6 | 49.5 | 1.0096
308.7 | 49.5 | 1.0096
308.8 | 49.5 | 1.0096
308.9 | 49.5 | 1.0096
309 | 49.5 | 1.0096
309.1 | 49.5 | 1.0096
309.2 | 49.5 | 1.0096
309.3 | 49.5 | 1.0096
309.4 | 49.5 | 1.0096
309.5 | 49.5 | 1.0096
309.6 | 49.5 | 1.0096
309.7 | 49.5 | 1.0096
309.8 | 49.5 | 1.0096
309.9 | 49.5 | 1.0096
310 | 49.5 | 1.0096
310.1 | 49.5 | 1.0096
310.2 | 49.5 | 1.0098
310.3 | 49.5 | 1.0098
310.4 | 49.5 | 1.0098
310.5 | 49.5 | 1.0098
310.6 | 49.5 | 1.0098
310.7 | 49.5 | 1.0098
310.8 | 49.5 | 1.0098
310.9 | 49.5 | 1.0098
311 | 49.5 | 1.0098
311.1 | 49.5 | 1.0098
311.2 | 49.5 | 1.0098
311.3 | 49.5 | 1.0098
311.4 | 49.5 | 1.0098
311.5 | 49.5 | 1.0098
311.6 | 49.5 | 1.0098
311.7 | 49.5 | 1.0098
311.8 | 49.5 | 1.0098
311.9 | 49.5 | 1.0098
312 | 49.5 | 1.0098
312.1 | 49.5 | 1.0098
312.2 | 49.5 | 1.0098
312.3 | 49.5 | 1.0098
312.4 | 49.5 | 1.0098
312.5 | 49.5 | 1.0096
312.6 | 49.5 | 1.0096
312.7 | 49.5 | 1.0096
312.8 | 49.5 | 1.0096
312.9 | 49.5 | 1.0096
313 | 49.5 | 1.0096
313.1 | 49.5 | 1.0096
313.2 | 49.5 | 1.0096
313.3 | 49.5 | 1.0096
313.4 | 49.5 | 1.0096
313.5 | 49.5 | 1.0096
313.6 | 49.5 | 1.0096
313.7 | 49.5 | 1.0096
313.8 | 49.5 | 1.0096
313.9 | 49.5 | 1.0096
314 | 49.5 | 1.0096
314.1 | 49.5 | 1.0096
314.2 | 49.5 | 1.0096
314.3 | 49.5 | 1.0096
314.4 | 49.5 | 1.0096
314.5 | 49.5 | 1.0096
314.6 | 49.5 | 1.0096
314.7 | 49.5 | 1.0096
314.8 | 49.5 | 1.0096
314.9 | 49.5 | 1.0096
315 | 49.5 | 1.0096
315.1 | 49.5 | 1.0096
315.2 | 49.5 | 1.0096
315.3 | 49.5 | 1.0096
315.4 | 49.5 | 1.0096
315.5 | 49.5 | 1.0096
315.6 | 49.5 | 1.0096
315.7 | 49.5 | 1.0096
315.8 | 49.5 | 1.0096
315.9 | 49.5 | 1.0096
316 | 49.5 | 1.0096
316.1 | 49.5 | 1.0096
316.2 | 49.5 | 1.0096
316.3 | 49.5 | 1.0096
316.4 | 49.5 | 1.0096
316.5 | 49.5 | 1.0096
316.6 | 49.5 | 1.0096
316.7 | 49.5 | 1.0096
316.8 | 49.5 | 1.0096
316.9 | 49.5 | 1.0096
317 | 49.5 | 1.0096
317.1 | 49.5 | 1.0096
317.2 | 49.5 | 1.0096
317.3 | 49.5 | 1.0096
317.4 | 49.5 | 1.0096
317.5 | 49.5 | 1.0096
317.6 | 49.5 | 1.0096
317.7 | 49.5 | 1.0096
317.8 | 49.5 | 1.0096
317.9 | 49.5 | 1.0096
318 | 49.5 | 1.0096
318.1 | 49.5 | 1.0096
318.2 | 49.5 | 1.0096
318.3 | 49.5 | 1.0096
318.4 | 49.5 | 1.0096
318.5 | 49.5 | 1.0096
318.6 | 49.5 | 1.0096
318.7 | 49.5 | 1.0096
318.8 | 49.5 | 1.0096
318.9 | 49.5 | 1.0096
319 | 49.5 | 1.0096
319.1 | 49.5 | 1.0096
319.2 | 49.5 | 1.0096
319.3 | 49.5 | 1.0096
319.4 | 49.5 | 1.0096
319.5 | 49.5 | 1.0096
319.6 | 49.5 | 1.0096
319.7 | 49.5 | 1.0096
319.8 | 49.5 | 1.0096
319.9 | 49.5 | 1.0096
320 | 49.5 | 1.0096
320.1 | 49.5 | 1.0096
320.2 | 49.5 | 1.0096
320.3 | 49.5 | 1.0096
320.4 | 49.5 | 1.0096
320.5 | 49.5 | 1.0096
320.6 | 49.5 | 1.0096
320.7 | 49.5 | 1.0096
320.8 | 49.5 | 1.0096
320.9 | 49.5 | 1.0096
321 | 49.5 | 1.0096
321.1 | 49.5 | 1.0096
321.2 | 49.5 | 1.0096
321.3 | 49.5 | 1.0096
321.4 | 49.5 | 1.0096
321.5 | 49.5 | 1.0096
321.6 | 49.5 | 1.0096
321.7 | 49.5 | 1.0096
321.8 | 49.5 | 1.0096
321.9 | 49.5 | 1.0096
322 | 49.5 | 1.0096
322.1 | 49.5 | 1.0096
322.2 | 49.5 | 1.0096
322.3 | 49.5 | 1.0096
322.4 | 49.5 | 1.0096
322.5 | 49.5 | 1.0096
322.6 | 49.5 | 1.0096
322.7 | 49.5 | 1.0096
322.8 | 49.5 | 1.0096
322.9 | 49.5 | 1.0096
323 | 49.5 | 1.0096
323.1 | 49.5 | 1.0096
323.2 | 49.5 | 1.0096
323.3 | 49.5 | 1.0096
323.4 | 49.5 | 1.0096
323.5 | 49.5 | 1.0096
323.6 | 49.5 | 1.0096
323.7 | 49.5 | 1.0096
323.8 | 49.5 | 1.0096
323.9 | 49.5 | 1.0096
324 | 49.5 | 1.0096
324.1 | 49.5 | 1.0096
324.2 | 49.5 | 1.0096
324.3 | 49.5 | 1.0096
324.4 | 49.5 | 1.0096
324.5 | 49.5 | 1.0096
324.6 | 49.5 | 1.0096
324.7 | 49.5 | 1.0096
324.8 | 49.5 | 1.0096
324.9 | 49.5 | 1.0096
325 | 49.5 | 1.0096
325.1 | 49.5 | 1.0096
325.2 | 49.5 | 1.0096
325.3 | 49.5 | 1.0096
325.4 | 49.5 | 1.0096
325.5 | 49.5 | 1.0096
325.6 | 49.5 | 1.0096
325.7 | 49.5 | 1.0096
325.8 | 49.5 | 1.0096
325.9 | 49.5 | 1.0096
326 | 49.5 | 1.0096
326.1 | 49.5 | 1.0096
326.2 | 49.5 | 1.0096
326.3 | 49.5 | 1.0096
326.4 | 49.5 | 1.0096
326.5 | 49.5 | 1.0096
326.6 | 49.5 | 1.0096
326.7 | 49.5 | 1.0096
326.8 | 49.5 | 1.0096
326.9 | 49.5 | 1.0096
327 | 49.5 | 1.0096
327.1 | 49.5 | 1.0096
327.2 | 49.5 | 1.0096
327.3 | 49.5 | 1.0096
327.4 | 49.5 | 1.0096
327.5 | 49.5 | 1.0096
327.6 | 49.5 | 1.0096
327.7 | 49.5 | 1.0096
327.8 | 49.5 | 1.0096
327.9 | 49.5 | 1.0096
328 | 49.5 | 1.0096
328.1 | 49.5 | 1.0096
328.2 | 49.5 | 1.0096
328.3 | 49.5 | 1.0096
328.4 | 49.5 | 1.0096
328.5 | 49.5 | 1.0096
328.6 | 49.5 | 1.0096
328.7 | 49.5 | 1.0096
328.8 | 49.5 | 1.0096
328.9 | 49.5 | 1.0096
329 | 49.5 | 1.0096
329.1 | 49.5 | 1.0096
329.2 | 49.5 | 1.0096
329.3 | 49.5 | 1.0096
329.4 | 49.5 | 1.0096
329.5 | 49.5 | 1.0096
329.6 | 49.5 | 1.0096
329.7 | 49.5 | 1.0096
329.8 | 49.5 | 1.0096
329.9 | 49.5 | 1.0096
330 | 49.5 | 1.0096
330.1 | 49.5 | 1.0096
330.2 | 49.5 | 1.0096
330.3 | 49.5 | 1.0096
330.4 | 49.5 | 1.0096
330.5 | 49.5 | 1.0096
330.6 | 49.5 | 1.0096
330.7 | 49.5 | 1.0096
330.8 | 49.5 | 1.0096
330.9 | 49.5 | 1.0096
331 | 49.5 | 1.0096
331.1 | 49.5 | 1.0096
331.2 | 49.5 | 1.0096
331.3 | 49.5 | 1.0096
331.4 | 49.5 | 1.0096
331.5 | 49.5 | 1.0096
331.6 | 49.5 | 1.0096
331.7 | 49.5 | 1.0096
331.8 | 49.5 | 1.0096
331.9 | 49.5 | 1.0096
332 | 49.5 | 1.0096
332.1 | 49.5 | 1.0096
332.2 | 49.5 | 1.0096
332.3 | 49.5 | 1.0096
332.4 | 49.5 | 1.0096
332.5 | 49.5 | 1.0096
332.6 | 49.5 | 1.0096
332.7 | 49.5 | 1.0096
332.8 | 49.5 | 1.0096
332.9 | 49.5 | 1.0096
333 | 49.5 | 1.0096
333.1 | 49.5 | 1.0096
333.2 | 49.5 | 1.0096
333.3 | 49.5 | 1.0096
333.4 | 49.5 | 1.0096
333.5 | 49.5 | 1.0096
333.6 | 49.5 | 1.0096
333.7 | 49.5 | 1.0096
333.8 | 49.5 | 1.0096
333.9 | 49.5 | 1.0096
334 | 49.5 | 1.0096
334.1 | 49.5 | 1.0096
334.2 | 49.5 | 1.0096
334.3 | 49.5 | 1.0096
334.4 | 49.5 | 1.0096
334.5 | 49.5 | 1.0096
334.6 | 49.5 | 1.0096
334.7 | 49.5 | 1.0096
334.8 | 49.5 | 1.0096
334.9 | 49.5 | 1.0096
335 | 49.5 | 1.0096
335.1 | 49.5 | 1.0096
335.2 | 49.5 | 1.0096
335.3 | 49.5 | 1.0096
335.4 | 49.5 | 1.0096
335.5 | 49.5 | 1.0096
335.6 | 49.5 | 1.0096
335.7 | 49.5 | 1.0096
335.8 | 49.5 | 1.0096
335.9 | 49.5 | 1.0096
336 | 49.5 | 1.0096
336.1 | 49.5 | 1.0096
336.2 | 49.5 | 1.0096
336.3 | 49.5 | 1.0096
336.4 | 49.5 | 1.0096
336.5 | 49.5 | 1.0096
336.6 | 49.5 | 1.0096
336.7 | 49.5 | 1.0096
336.8 | 49.5 | 1.0096
336.9 | 49.5 | 1.0096
337 | 49.5 | 1.0096
337.1 | 49.5 | 1.0096
337.2 | 49.5 | 1.0096
337.3 | 49.5 | 1.0096
337.4 | 49.5 | 1.0096
337.5 | 49.5 | 1.0096
337.6 | 49.5 | 1.0096
337.7 | 49.5 | 1.0096
337.8 | 49.5 | 1.0096
337.9 | 49.5 | 1.0096
338 | 49.5 | 1.0096
338.1 | 49.5 | 1.0096
338.2 | 49.5 | 1.0096
338.3 | 49.5 | 1.0096
338.4 | 49.5 | 1.0096
338.5 | 49.5 | 1.0096
338.6 | 49.5 | 1.0096
338.7 | 49.5 | 1.0096
338.8 | 49.5 | 1.0096
338.9 | 49.5 | 1.0096
339 | 49.5 | 1.0096
339.1 | 49.5 | 1.0096
339.2 | 49.5 | 1.0096
339.3 | 49.5 | 1.0096
339.4 | 49.5 | 1.0096
339.5 | 49.5 | 1.0096
339.6 | 49.5 | 1.0096
339.7 | 49.5 | 1.0096
339.8 | 49.5 | 1.0096
339.9 | 49.5 | 1.0096
340 | 49.5 | 1.0096
340.1 | 49.5 | 1.0096
340.2 | 49.5 | 1.0096
340.3 | 49.5 | 1.0096
340.4 | 49.5 | 1.0096
340.5 | 49.5 | 1.0096
340.6 | 49.5 | 1.0096
340.7 | 49.5 | 1.0096
340.8 | 49.5 | 1.0096
340.9 | 49.5 | 1.0096
341 | 49.5 | 1.0096
341.1 | 49.5 | 1.0096
341.2 | 49.5 | 1.0096
341.3 | 49.5 | 1.0096
341.4 | 49.5 | 1.0096
341.5 | 49.5 | 1.0096
341.6 | 49.5 | 1.0096
341.7 | 49.5 | 1.0096
341.8 | 49.5 | 1.0096
341.9 | 49.5 | 1.0096
342 | 49.5 | 1.0096
342.1 | 49.5 | 1.0096
342.2 | 49.5 | 1.0096
342.3 | 49.5 | 1.0096
342.4 | 49.5 | 1.0096
342.5 | 49.5 | 1.0096
342.6 | 49.5 | 1.0096
342.7 | 49.5 | 1.0096
342.8 | 49.5 | 1.0096
342.9 | 49.5 | 1.0096
343 | 49.5 | 1.0096
343.1 | 49.5 | 1.0096
343.2 | 49.5 | 1.0096
343.3 | 49.5 | 1.0096
343.4 | 49.5 | 1.0096
343.5 | 49.5 | 1.0096
343.6 | 49.5 | 1.0096
343.7 | 49.5 | 1.0096
343.8 | 49.5 | 1.0096
343.9 | 49.5 | 1.0096
344 | 49.5 | 1.0096
344.1 | 49.5 | 1.0096
344.2 | 49.5 | 1.0096
344.3 | 49.5 | 1.0096
344.4 | 49.5 | 1.0096
344.5 | 49.5 | 1.0096
344.6 | 49.5 | 1.0096
344.7 | 49.5 | 1.0096
344.8 | 49.5 | 1.0096
344.9 | 49.5 | 1.0096
345 | 49.5 | 1.0096
345.1 | 49.5 | 1.0096
345.2 | 49.5 | 1.0096
345.3 | 49.5 | 1.0096
345.4 | 49.5 | 1.0096
345.5 | 49.5 | 1.0096
345.6 | 49.5 | 1.0096
345.7 | 49.5 | 1.0096
345.8 | 49.5 | 1.0096
345.9 | 49.5 | 1.0096
346 | 49.5 | 1.0096
346.1 | 49.5 | 1.0096
346.2 | 49.5 | 1.0096
346.3 | 49.5 | 1.0096
346.4 | 49.5 | 1.0098
346.5 | 49.5 | 1.0098
346.6 | 49.5 | 1.01
346.7 | 49.5 | 1.01
346.8 | 49.5 | 1.01
346.9 | 49.5 | 1.01
347 | 49.5 | 1.01
347.1 | 49.5 | 1.01
347.2 | 49.5 | 1.01
347.3 | 49.5 | 1.0098
347.4 | 49.5 | 1.0098
347.5 | 49.5 | 1.0098
347.6 | 49.5 | 1.0098
347.7 | 49.5 | 1.0098
347.8 | 49.5 | 1.0098
347.9 | 49.5 | 1.0098
348 | 49.5 | 1.0098
348.1 | 49.5 | 1.0098
348.2 | 49.5 | 1.0098
348.3 | 49.5 | 1.0098
348.4 | 49.5 | 1.0098
348.5 | 49.5 | 1.0098
348.6 | 49.5 | 1.0098
348.7 | 49.5 | 1.0098
348.8 | 49.5 | 1.0098
348.9 | 49.5 | 1.0098
349 | 49.5 | 1.0096
349.1 | 49.5 | 1.0096
349.2 | 49.5 | 1.0096
349.3 | 49.5 | 1.0096
349.4 | 49.5 | 1.0096
349.5 | 49.5 | 1.0096
349.6 | 49.5 | 1.0096
349.7 | 49.5 | 1.0096
349.8 | 49.5 | 1.0096
349.9 | 49.5 | 1.0096
350 | 49.5 | 1.0096
350.1 | 49.5 | 1.0096
350.2 | 49.5 | 1.0096
350.3 | 49.5 | 1.0096
350.4 | 49.5 | 1.0096
350.5 | 49.5 | 1.0096
350.6 | 49.5 | 1.0096
350.7 | 49.5 | 1.0096
350.8 | 49.5 | 1.0096
350.9 | 49.5 | 1.0096
351 | 49.5 | 1.0096
351.1 | 49.5 | 1.0096
351.2 | 49.5 | 1.0096
351.3 | 49.5 | 1.0096
351.4 | 49.5 | 1.0096
351.5 | 49.5 | 1.0096
351.6 | 49.5 | 1.0096
351.7 | 49.5 | 1.0096
351.8 | 49.5 | 1.0096
351.9 | 49.5 | 1.0096
352 | 49.5 | 1.0096
352.1 | 49.5 | 1.0096
352.2 | 49.5 | 1.0096
352.3 | 49.5 | 1.0096
352.4 | 49.5 | 1.0096
352.5 | 49.5 | 1.0096
352.6 | 49.5 | 1.0096
352.7 | 49.5 | 1.0096
352.8 | 49.5 | 1.0096
352.9 | 49.5 | 1.0096
353 | 49.5 | 1.0096
353.1 | 49.5 | 1.0096
353.2 | 49.5 | 1.0096
353.3 | 49.5 | 1.0096
353.4 | 49.5 | 1.0096
353.5 | 49.5 | 1.0098
353.6 | 49.5 | 1.0098
353.7 | 49.5 | 1.0098
353.8 | 49.5 | 1.0098
353.9 | 49.5 | 1.0098
354 | 49.5 | 1.0098
354.1 | 49.5 | 1.0098
354.2 | 49.5 | 1.0098
354.3 | 49.5 | 1.0098
354.4 | 49.5 | 1.0098
354.5 | 49.5 | 1.0098
354.6 | 49.5 | 1.0098
354.7 | 49.5 | 1.0096
354.8 | 49.5 | 1.0098
354.9 | 49.5 | 1.0098
355 | 49.5 | 1.0098
355.1 | 49.5 | 1.0098
355.2 | 49.5 | 1.0098
355.3 | 49.5 | 1.0098
355.4 | 49.5 | 1.0098
355.5 | 49.5 | 1.0098
355.6 | 49.5 | 1.0098
355.7 | 49.5 | 1.0096
355.8 | 49.5 | 1.0096
355.9 | 49.5 | 1.0096
356 | 49.5 | 1.0096
356.1 | 49.5 | 1.0096
356.2 | 49.5 | 1.0096
356.3 | 49.5 | 1.0096
356.4 | 49.5 | 1.0096
356.5 | 49.5 | 1.0096
356.6 | 49.5 | 1.0096
356.7 | 49.5 | 1.0096
356.8 | 49.5 | 1.0096
356.9 | 49.5 | 1.0096
357 | 49.5 | 1.0096
357.1 | 49.5 | 1.0096
357.2 | 49.5 | 1.0096
357.3 | 49.5 | 1.0096
357.4 | 49.5 | 1.0096
357.5 | 49.5 | 1.0096
357.6 | 49.5 | 1.0096
357.7 | 49.5 | 1.0096
357.8 | 49.5 | 1.0096
357.9 | 49.5 | 1.0096
358 | 49.5 | 1.0096
358.1 | 49.5 | 1.0096
358.2 | 49.5 | 1.0096
358.3 | 49.5 | 1.0096
358.4 | 49.5 | 1.0096
358.5 | 49.5 | 1.0096
358.6 | 49.5 | 1.0096
358.7 | 49.5 | 1.0096
358.8 | 49.5 | 1.0096
358.9 | 49.5 | 1.0096
359 | 49.5 | 1.0096
359.1 | 49.5 | 1.0096
359.2 | 49.5 | 1.0096
359.3 | 49.5 | 1.0098
359.4 | 49.5 | 1.0098
359.5 | 49.5 | 1.0098
359.6 | 49.5 | 1.0098
359.7 | 49.5 | 1.0098
359.8 | 49.5 | 1.0098
359.9 | 49.5 | 1.0098
360 | 49.5 | 1.0098
360.1 | 49.5 | 1.0098
360.2 | 49.5 | 1.0098
360.3 | 49.5 | 1.0098
360.4 | 49.5 | 1.0098
360.5 | 49.5 | 1.0098
360.6 | 49.5 | 1.0098
360.7 | 49.5 | 1.0098
360.8 | 49.5 | 1.0098
360.9 | 49.5 | 1.0098
361 | 49.5 | 1.0098
361.1 | 49.5 | 1.0098
361.2 | 49.5 | 1.0098
361.3 | 49.5 | 1.0098
361.4 | 49.5 | 1.0098
361.5 | 49.5 | 1.0098
361.6 | 49.5 | 1.0098
361.7 | 49.5 | 1.0096
361.8 | 49.5 | 1.0096
361.9 | 49.5 | 1.0096
362 | 49.5 | 1.0096
362.1 | 49.5 | 1.0096
362.2 | 49.5 | 1.0096
362.3 | 49.5 | 1.0096
362.4 | 49.5 | 1.0096
362.5 | 49.5 | 1.0096
362.6 | 49.5 | 1.0096
362.7 | 49.5 | 1.0096
362.8 | 49.5 | 1.0096
362.9 | 49.5 | 1.0096
363 | 49.5 | 1.0096
363.1 | 49.5 | 1.0096
363.2 | 49.5 | 1.0096
363.3 | 49.5 | 1.0096
363.4 | 49.5 | 1.0096
363.5 | 49.5 | 1.0096
363.6 | 49.5 | 1.0096
363.7 | 49.5 | 1.0096
363.8 | 49.5 | 1.0096
363.9 | 49.5 | 1.0096
364 | 49.5 | 1.0096
364.1 | 49.5 | 1.0096
364.2 | 49.5 | 1.0096
364.3 | 49.5 | 1.0096
364.4 | 49.5 | 1.0096
364.5 | 49.5 | 1.0096
364.6 | 49.5 | 1.0096
364.7 | 49.5 | 1.0096
364.8 | 49.5 | 1.0096
364.9 | 49.5 | 1.0096
365 | 49.5 | 1.0096
365.1 | 49.5 | 1.0096
365.2 | 49.5 | 1.0098
365.3 | 49.5 | 1.0098
365.4 | 49.5 | 1.0098
365.5 | 49.5 | 1.0098
365.6 | 49.5 | 1.0098
365.7 | 49.5 | 1.0098
365.8 | 49.5 | 1.0098
365.9 | 49.5 | 1.0098
366 | 49.5 | 1.0098
366.1 | 49.5 | 1.0098
366.2 | 49.5 | 1.0098
366.3 | 49.5 | 1.0096
366.4 | 49.5 | 1.0096
366.5 | 49.5 | 1.0096
366.6 | 49.5 | 1.0096
366.7 | 49.5 | 1.0096
366.8 | 49.5 | 1.0096
366.9 | 49.5 | 1.0096
367 | 49.5 | 1.0096
367.1 | 49.5 | 1.0096
367.2 | 49.5 | 1.0096
367.3 | 49.5 | 1.0096
367.4 | 49.5 | 1.0096
367.5 | 49.5 | 1.0096
367.6 | 49.5 | 1.0096
367.7 | 49.5 | 1.0096
367.8 | 49.5 | 1.0096
367.9 | 49.5 | 1.0096
368 | 49.5 | 1.0096
368.1 | 49.5 | 1.0096
368.2 | 49.5 | 1.0096
368.3 | 49.5 | 1.0096
368.4 | 49.5 | 1.0096
368.5 | 49.5 | 1.0096
368.6 | 49.5 | 1.0096
368.7 | 49.5 | 1.0098
368.8 | 49.5 | 1.0098
368.9 | 49.5 | 1.0098
369 | 49.5 | 1.0098
369.1 | 49.5 | 1.0098
369.2 | 49.5 | 1.0098
369.3 | 49.5 | 1.0098
369.4 | 49.5 | 1.0098
369.5 | 49.5 | 1.0098
369.6 | 49.5 | 1.0098
369.7 | 49.5 | 1.0098
369.8 | 49.5 | 1.0096
369.9 | 49.5 | 1.0096
370 | 49.5 | 1.0096
370.1 | 49.5 | 1.0096
370.2 | 49.5 | 1.0096
370.3 | 49.5 | 1.0096
370.4 | 49.5 | 1.0096
370.5 | 49.5 | 1.0096
370.6 | 49.5 | 1.0096
370.7 | 49.5 | 1.0096
370.8 | 49.5 | 1.0096
370.9 | 49.5 | 1.0096
371 | 49.5 | 1.0096
371.1 | 49.5 | 1.0096
371.2 | 49.5 | 1.0096
371.3 | 49.5 | 1.0096
371.4 | 49.5 | 1.0096
371.5 | 49.5 | 1.0096
371.6 | 49.5 | 1.0096
371.7 | 49.5 | 1.0096
371.8 | 49.5 | 1.0096
371.9 | 49.5 | 1.0096
372 | 49.5 | 1.0096
372.1 | 49.5 | 1.0096
372.2 | 49.5 | 1.0096
372.3 | 49.5 | 1.0096
372.4 | 49.5 | 1.0096
372.5 | 49.5 | 1.0096
372.6 | 49.5 | 1.0096
372.7 | 49.5 | 1.0096
372.8 | 49.5 | 1.0096
372.9 | 49.5 | 1.0096
373 | 49.5 | 1.0096
373.1 | 49.5 | 1.0096
373.2 | 49.5 | 1.0096
373.3 | 49.5 | 1.0096
373.4 | 49.5 | 1.0096
373.5 | 49.5 | 1.0096
373.6 | 49.5 | 1.0096
373.7 | 49.5 | 1.0096
373.8 | 49.5 | 1.0096
373.9 | 49.5 | 1.0096
374 | 49.5 | 1.0096
374.1 | 49.5 | 1.0096
374.2 | 49.5 | 1.0096
374.3 | 49.5 | 1.0096
374.4 | 49.5 | 1.0096
374.5 | 49.5 | 1.0096
374.6 | 49.5 | 1.0098
374.7 | 49.5 | 1.0098
374.8 | 49.5 | 1.0098
374.9 | 49.5 | 1.0098
375 | 49.5 | 1.0098
375.1 | 49.5 | 1.0098
375.2 | 49.5 | 1.0098
375.3 | 49.5 | 1.0098
375.4 | 49.5 | 1.0098
375.5 | 49.5 | 1.0098
375.6 | 49.5 | 1.0098
375.7 | 49.5 | 1.0098
375.8 | 49.5 | 1.0096
375.9 | 49.5 | 1.0096
376 | 49.5 | 1.0096
376.1 | 49.5 | 1.0096
376.2 | 49.5 | 1.0096
376.3 | 49.5 | 1.0096
376.4 | 49.5 | 1.0096
376.5 | 49.5 | 1.0096
376.6 | 49.5 | 1.0096
376.7 | 49.5 | 1.0096
376.8 | 49.5 | 1.0096
376.9 | 49.5 | 1.0096
377 | 49.5 | 1.0096
377.1 | 49.5 | 1.0096
377.2 | 49.5 | 1.0096
377.3 | 49.5 | 1.0096
377.4 | 49.5 | 1.0096
377.5 | 49.5 | 1.0096
377.6 | 49.5 | 1.0096
377.7 | 49.5 | 1.0096
377.8 | 49.5 | 1.0096
377.9 | 49.5 | 1.0096
378 | 49.5 | 1.0096
378.1 | 49.5 | 1.0096
378.2 | 49.5 | 1.0096
378.3 | 49.5 | 1.0096
378.4 | 49.5 | 1.0096
378.5 | 49.5 | 1.0096
378.6 | 49.5 | 1.0096
378.7 | 49.5 | 1.0096
378.8 | 49.5 | 1.0096
378.9 | 49.5 | 1.0096
379 | 49.5 | 1.0096
379.1 | 49.5 | 1.0096
379.2 | 49.5 | 1.0096
379.3 | 49.5 | 1.0096
379.4 | 49.5 | 1.0096
379.5 | 49.5 | 1.0096
379.6 | 49.5 | 1.0096
379.7 | 49.5 | 1.0096
379.8 | 49.5 | 1.0096
379.9 | 49.5 | 1.0096
380 | 49.5 | 1.0096
380.1 | 49.5 | 1.0096
380.2 | 49.5 | 1.0096
380.3 | 49.5 | 1.0098
380.4 | 49.5 | 1.0098
380.5 | 49.5 | 1.0098
380.6 | 49.5 | 1.0098
380.7 | 49.5 | 1.0098
380.8 | 49.5 | 1.0098
380.9 | 49.5 | 1.0098
381 | 49.5 | 1.0098
381.1 | 49.5 | 1.0098
381.2 | 49.5 | 1.0098
381.3 | 49.5 | 1.0098
381.4 | 49.5 | 1.0098
381.5 | 49.5 | 1.0098
381.6 | 49.5 | 1.0096
381.7 | 49.5 | 1.0096
381.8 | 49.5 | 1.0096
381.9 | 49.5 | 1.0096
382 | 49.5 | 1.0096
382.1 | 49.5 | 1.0096
382.2 | 49.5 | 1.0096
382.3 | 49.5 | 1.0096
382.4 | 49.5 | 1.0096
382.5 | 49.5 | 1.0096
382.6 | 49.5 | 1.0094
382.7 | 49.5 | 1.0094
382.8 | 49.5 | 1.0096
382.9 | 49.5 | 1.0096
383 | 49.5 | 1.0096
383.1 | 49.5 | 1.0096
383.2 | 49.5 | 1.0096
383.3 | 49.5 | 1.0096
383.4 | 49.5 | 1.0096
383.5 | 49.5 | 1.0096
383.6 | 49.5 | 1.0096
383.7 | 49.5 | 1.0096
383.8 | 49.5 | 1.0098
383.9 | 49.5 | 1.0098
384 | 49.5 | 1.0098
384.1 | 49.5 | 1.0096
384.2 | 49.5 | 1.0096
384.3 | 49.5 | 1.0096
384.4 | 49.5 | 1.0096
384.5 | 49.5 | 1.0096
384.6 | 49.5 | 1.0096
384.7 | 49.5 | 1.0096
384.8 | 49.5 | 1.0096
384.9 | 49.5 | 1.0098
385 | 49.5 | 1.0098
385.1 | 49.5 | 1.0098
385.2 | 49.5 | 1.0098
385.3 | 49.5 | 1.0098
385.4 | 49.5 | 1.0098
385.5 | 49.5 | 1.0098
385.6 | 49.5 | 1.0098
385.7 | 49.5 | 1.0098
385.8 | 49.5 | 1.0098
385.9 | 49.5 | 1.0098
386 | 49.5 | 1.0098
386.1 | 49.5 | 1.0098
386.2 | 49.5 | 1.0098
386.3 | 49.5 | 1.0096
386.4 | 49.5 | 1.0096
386.5 | 49.5 | 1.0096
386.6 | 49.5 | 1.0096
386.7 | 49.5 | 1.0096
386.8 | 49.5 | 1.0096
386.9 | 49.5 | 1.0096
387 | 49.5 | 1.0096
387.1 | 49.5 | 1.0096
387.2 | 49.5 | 1.0096
387.3 | 49.5 | 1.0096
387.4 | 49.5 | 1.0096
387.5 | 49.5 | 1.0096
387.6 | 49.5 | 1.0096
387.7 | 49.5 | 1.0096
387.8 | 49.5 | 1.0096
387.9 | 49.5 | 1.0096
388 | 49.5 | 1.0096
388.1 | 49.5 | 1.0096
388.2 | 49.5 | 1.0096
388.3 | 49.5 | 1.0096
388.4 | 49.5 | 1.0096
388.5 | 49.5 | 1.0096
388.6 | 49.5 | 1.0096
388.7 | 49.5 | 1.0096
388.8 | 49.5 | 1.0096
388.9 | 49.5 | 1.0096
389 | 49.5 | 1.0096
389.1 | 49.5 | 1.0096
389.2 | 49.5 | 1.0096
389.3 | 49.5 | 1.0096
389.4 | 49.5 | 1.0096
389.5 | 49.5 | 1.0096
389.6 | 49.5 | 1.0096
389.7 | 49.5 | 1.0096
389.8 | 49.5 | 1.0096
389.9 | 49.5 | 1.0096
390 | 49.5 | 1.0096
390.1 | 49.5 | 1.0096
390.2 | 49.5 | 1.0096
390.3 | 49.5 | 1.0096
390.4 | 49.5 | 1.0096
390.5 | 49.5 | 1.0096
390.6 | 49.5 | 1.0096
390.7 | 49.5 | 1.0096
390.8 | 49.5 | 1.0096
390.9 | 49.5 | 1.0096
391 | 49.5 | 1.0096
391.1 | 49.5 | 1.0096
391.2 | 49.5 | 1.0096
391.3 | 49.5 | 1.0096
391.4 | 49.5 | 1.0096
391.5 | 49.5 | 1.0096
391.6 | 49.5 | 1.0096
391.7 | 49.5 | 1.0096
391.8 | 49.5 | 1.0096
391.9 | 49.5 | 1.0098
392 | 49.5 | 1.0098
392.1 | 49.5 | 1.0098
392.2 | 49.5 | 1.0096
392.3 | 49.5 | 1.0096
392.4 | 49.5 | 1.0096
392.5 | 49.5 | 1.0096
392.6 | 49.5 | 1.0096
392.7 | 49.5 | 1.0096
392.8 | 49.5 | 1.0096
392.9 | 49.5 | 1.0096
393 | 49.5 | 1.0096
393.1 | 49.5 | 1.0096
393.2 | 49.5 | 1.0096
393.3 | 49.5 | 1.0096
393.4 | 49.5 | 1.0098
393.5 | 49.5 | 1.0098
393.6 | 49.5 | 1.0098
393.7 | 49.5 | 1.0098
393.8 | 49.5 | 1.0098
393.9 | 49.5 | 1.0098
394 | 49.5 | 1.0098
394.1 | 49.5 | 1.0098
394.2 | 49.5 | 1.0098
394.3 | 49.5 | 1.0096
394.4 | 49.5 | 1.0096
394.5 | 49.5 | 1.0096
394.6 | 49.5 | 1.0096
394.7 | 49.5 | 1.0096
394.8 | 49.5 | 1.0096
394.9 | 49.5 | 1.0096
395 | 49.5 | 1.0096
395.1 | 49.5 | 1.0096
395.2 | 49.5 | 1.0096
395.3 | 49.5 | 1.0096
395.4 | 49.5 | 1.0096
395.5 | 49.5 | 1.0096
395.6 | 49.5 | 1.0096
395.7 | 49.5 | 1.0098
395.8 | 49.5 | 1.0098
395.9 | 49.5 | 1.0098
396 | 49.5 | 1.0098
396.1 | 49.5 | 1.0098
396.2 | 49.5 | 1.0098
396.3 | 49.5 | 1.0098
396.4 | 49.5 | 1.0098
396.5 | 49.5 | 1.0098
396.6 | 49.5 | 1.0098
396.7 | 49.5 | 1.0098
396.8 | 49.5 | 1.0098
396.9 | 49.5 | 1.0096
397 | 49.5 | 1.0096
397.1 | 49.5 | 1.0096
397.2 | 49.5 | 1.0096
397.3 | 49.5 | 1.0096
397.4 | 49.5 | 1.0096
397.5 | 49.5 | 1.0096
397.6 | 49.5 | 1.0096
397.7 | 49.5 | 1.0096
397.8 | 49.5 | 1.0096
397.9 | 49.5 | 1.0096
398 | 49.5 | 1.0096
398.1 | 49.5 | 1.0096
398.2 | 49.5 | 1.0096
398.3 | 49.5 | 1.0096
398.4 | 49.5 | 1.0096
398.5 | 49.5 | 1.0096
398.6 | 49.5 | 1.0096
398.7 | 49.5 | 1.0096
398.8 | 49.5 | 1.0096
398.9 | 49.5 | 1.0096
399 | 49.5 | 1.0096
399.1 | 49.5 | 1.0096
399.2 | 49.5 | 1.0096
399.3 | 49.5 | 1.0096
399.4 | 49.5 | 1.0096
399.5 | 49.5 | 1.0096
399.6 | 49.5 | 1.0096
399.7 | 49.5 | 1.0096
399.8 | 49.5 | 1.0096
399.9 | 49.5 | 1.0096
400 | 49.5 | 1.0096
400.1 | 49.5 | 1.0096
400.2 | 49.5 | 1.0096
400.3 | 49.5 | 1.0096
400.4 | 49.5 | 1.0096
400.5 | 49.5 | 1.0096
400.6 | 49.5 | 1.0096
400.7 | 49.5 | 1.0096
400.8 | 49.5 | 1.0096
400.9 | 49.5 | 1.0096
401 | 49.5 | 1.0096
401.1 | 49.5 | 1.0096
401.2 | 49.5 | 1.0096
401.3 | 49.5 | 1.0096
401.4 | 49.5 | 1.0096
401.5 | 49.5 | 1.0096
401.6 | 49.5 | 1.0096
401.7 | 49.5 | 1.0096
401.8 | 49.5 | 1.0096
401.9 | 49.5 | 1.0096
402 | 49.5 | 1.0096
402.1 | 49.5 | 1.0096
402.2 | 49.5 | 1.0096
402.3 | 49.5 | 1.0096
402.4 | 49.5 | 1.0096
402.5 | 49.5 | 1.0096
402.6 | 49.5 | 1.0096
402.7 | 49.5 | 1.0096
402.8 | 49.5 | 1.0096
402.9 | 49.5 | 1.0096
403 | 49.5 | 1.0096
403.1 | 49.5 | 1.0096
403.2 | 49.5 | 1.0096
403.3 | 49.5 | 1.0096
403.4 | 49.5 | 1.0096
403.5 | 49.5 | 1.0096
403.6 | 49.5 | 1.0096
403.7 | 49.5 | 1.0096
403.8 | 49.5 | 1.0096
403.9 | 49.5 | 1.0096
404 | 49.5 | 1.0096
404.1 | 49.5 | 1.0096
404.2 | 49.5 | 1.0096
404.3 | 49.5 | 1.0096
404.4 | 49.5 | 1.0096
404.5 | 49.5 | 1.0096
404.6 | 49.5 | 1.0096
404.7 | 49.5 | 1.0096
404.8 | 49.5 | 1.0096
404.9 | 49.5 | 1.0096
405 | 49.5 | 1.0096
405.1 | 49.5 | 1.0096
405.2 | 49.5 | 1.0096
405.3 | 49.5 | 1.0096
405.4 | 49.5 | 1.0096
405.5 | 49.5 | 1.0096
405.6 | 49.5 | 1.0096
405.7 | 49.5 | 1.0096
405.8 | 49.5 | 1.0096
405.9 | 49.5 | 1.0098
406 | 49.5 | 1.0098
406.1 | 49.5 | 1.0098
406.2 | 49.5 | 1.0098
406.3 | 49.5 | 1.0098
406.4 | 49.5 | 1.0098
406.5 | 49.5 | 1.0098
406.6 | 49.5 | 1.0098
406.7 | 49.5 | 1.0098
406.8 | 49.5 | 1.0098
406.9 | 49.5 | 1.0096
407 | 49.5 | 1.0096
407.1 | 49.5 | 1.0096
407.2 | 49.5 | 1.0096
407.3 | 49.5 | 1.0096
407.4 | 49.5 | 1.0096
407.5 | 49.5 | 1.0096
407.6 | 49.5 | 1.0096
407.7 | 49.5 | 1.0096
407.8 | 49.5 | 1.0096
407.9 | 49.5 | 1.0096
408 | 49.5 | 1.0096
408.1 | 49.5 | 1.0096
408.2 | 49.5 | 1.0096
408.3 | 49.5 | 1.0096
408.4 | 49.5 | 1.0096
408.5 | 49.5 | 1.0096
408.6 | 49.5 | 1.0096
408.7 | 49.5 | 1.0096
408.8 | 49.5 | 1.0096
408.9 | 49.5 | 1.0096
409 | 49.5 | 1.0096
409.1 | 49.5 | 1.0096
409.2 | 49.5 | 1.0096
409.3 | 49.5 | 1.0096
409.4 | 49.5 | 1.0096
409.5 | 49.5 | 1.0096
409.6 | 49.5 | 1.0096
409.7 | 49.5 | 1.0096
409.8 | 49.5 | 1.0096
409.9 | 49.5 | 1.0096
410 | 49.5 | 1.0096
410.1 | 49.5 | 1.0096
410.2 | 49.5 | 1.0096
410.3 | 49.5 | 1.0096
410.4 | 49.5 | 1.0096
410.5 | 49.5 | 1.0096
410.6 | 49.5 | 1.0096
410.7 | 49.5 | 1.0096
410.8 | 49.5 | 1.0096
410.9 | 49.5 | 1.0096
411 | 49.5 | 1.0096
411.1 | 49.5 | 1.0096
411.2 | 49.5 | 1.0096
411.3 | 49.5 | 1.0096
411.4 | 49.5 | 1.0096
411.5 | 49.5 | 1.0096
411.6 | 49.5 | 1.0096
411.7 | 49.5 | 1.0096
411.8 | 49.5 | 1.0096
411.9 | 49.5 | 1.0096
412 | 49.5 | 1.0096
412.1 | 49.5 | 1.0096
412.2 | 49.5 | 1.0096
412.3 | 49.5 | 1.0096
412.4 | 49.5 | 1.0096
412.5 | 49.5 | 1.0096
412.6 | 49.5 | 1.0096
412.7 | 49.5 | 1.0096
412.8 | 49.5 | 1.0096
412.9 | 49.5 | 1.0096
413 | 49.5 | 1.0096
413.1 | 49.5 | 1.0096
413.2 | 49.5 | 1.0096
413.3 | 49.5 | 1.0096
413.4 | 49.5 | 1.0096
413.5 | 49.5 | 1.0096
413.6 | 49.5 | 1.0096
413.7 | 49.5 | 1.0096
413.8 | 49.5 | 1.0096
413.9 | 49.5 | 1.0096
414 | 49.5 | 1.0096
414.1 | 49.5 | 1.0096
414.2 | 49.5 | 1.0096
414.3 | 49.5 | 1.0096
414.4 | 49.5 | 1.0096
414.5 | 49.5 | 1.0096
414.6 | 49.5 | 1.0096
414.7 | 49.5 | 1.0096
414.8 | 49.5 | 1.0096
414.9 | 49.5 | 1.0096
415 | 49.5 | 1.0096
415.1 | 49.5 | 1.0096
415.2 | 49.5 | 1.0096
415.3 | 49.5 | 1.0096
415.4 | 49.5 | 1.0096
415.5 | 49.5 | 1.0096
415.6 | 49.5 | 1.0096
415.7 | 49.5 | 1.0096
415.8 | 49.5 | 1.0096
415.9 | 49.5 | 1.0096
416 | 49.5 | 1.0096
416.1 | 49.5 | 1.0096
416.2 | 49.5 | 1.0096
416.3 | 49.5 | 1.0096
416.4 | 49.5 | 1.0096
416.5 | 49.5 | 1.0096
416.6 | 49.5 | 1.0096
416.7 | 49.5 | 1.0096
416.8 | 49.5 | 1.0096
416.9 | 49.5 | 1.0096
417 | 49.5 | 1.0096
417.1 | 49.5 | 1.0096
417.2 | 49.5 | 1.0096
417.3 | 49.5 | 1.0096
417.4 | 49.5 | 1.0096
417.5 | 49.5 | 1.0096
417.6 | 49.5 | 1.0096
417.7 | 49.5 | 1.0096
417.8 | 49.5 | 1.0096
417.9 | 49.5 | 1.0096
418 | 49.5 | 1.0096
418.1 | 49.5 | 1.0096
418.2 | 49.5 | 1.0096
418.3 | 49.5 | 1.0096
418.4 | 49.5 | 1.0096
418.5 | 49.5 | 1.0096
418.6 | 49.5 | 1.0096
418.7 | 49.5 | 1.0096
418.8 | 49.5 | 1.0096
418.9 | 49.5 | 1.0096
419 | 49.5 | 1.0096
419.1 | 49.5 | 1.0096
419.2 | 49.5 | 1.0096
419.3 | 49.5 | 1.0096
419.4 | 49.5 | 1.0096
419.5 | 49.5 | 1.0096
419.6 | 49.5 | 1.0096
419.7 | 49.5 | 1.0096
419.8 | 49.5 | 1.0096
419.9 | 49.5 | 1.0096
420 | 49.5 | 1.0096
420.1 | 49.5 | 1.0096
420.2 | 49.5 | 1.0096
420.3 | 49.5 | 1.0096
420.4 | 49.5 | 1.0096
420.5 | 49.5 | 1.0096
420.6 | 49.5 | 1.0096
420.7 | 49.5 | 1.0096
420.8 | 49.5 | 1.0096
420.9 | 49.5 | 1.0096
421 | 49.5 | 1.0096
421.1 | 49.5 | 1.0096
421.2 | 49.5 | 1.0096
421.3 | 49.5 | 1.0096
421.4 | 49.5 | 1.0096
421.5 | 49.5 | 1.0096
421.6 | 49.5 | 1.0096
421.7 | 49.5 | 1.0096
421.8 | 49.5 | 1.0096
421.9 | 49.5 | 1.0096
422 | 49.5 | 1.0096
422.1 | 49.5 | 1.0096
422.2 | 49.5 | 1.0096
422.3 | 49.5 | 1.0098
422.4 | 49.5 | 1.0098
422.5 | 49.5 | 1.0098
422.6 | 49.5 | 1.0098
422.7 | 49.5 | 1.0098
422.8 | 49.5 | 1.0098
422.9 | 49.5 | 1.0098
423 | 49.5 | 1.0098
423.1 | 49.5 | 1.0098
423.2 | 49.5 | 1.0098
423.3 | 49.5 | 1.0098
423.4 | 49.5 | 1.0098
423.5 | 49.5 | 1.0098
423.6 | 49.5 | 1.0098
423.7 | 49.5 | 1.0098
423.8 | 49.5 | 1.0098
423.9 | 49.5 | 1.0098
424 | 49.5 | 1.0098
424.1 | 49.5 | 1.0098
424.2 | 49.5 | 1.0098
424.3 | 49.5 | 1.0098
424.4 | 49.5 | 1.0098
424.5 | 49.5 | 1.0098
424.6 | 49.5 | 1.0098
424.7 | 49.5 | 1.0098
424.8 | 49.5 | 1.0098
424.9 | 49.5 | 1.0098
425 | 49.5 | 1.0098
425.1 | 49.5 | 1.0098
425.2 | 49.5 | 1.0098
425.3 | 49.5 | 1.0098
425.4 | 49.5 | 1.0098
425.5 | 49.5 | 1.0098
425.6 | 49.5 | 1.0098
425.7 | 49.5 | 1.0096
425.8 | 49.5 | 1.0096
425.9 | 49.5 | 1.0096
426 | 49.5 | 1.0096
426.1 | 49.5 | 1.0096
426.2 | 49.5 | 1.0096
426.3 | 49.5 | 1.0096
426.4 | 49.5 | 1.0096
426.5 | 49.5 | 1.0096
426.6 | 49.5 | 1.0096
426.7 | 49.5 | 1.0096
426.8 | 49.5 | 1.0096
426.9 | 49.5 | 1.0096
427 | 49.5 | 1.0096
427.1 | 49.5 | 1.0096
427.2 | 49.5 | 1.0096
427.3 | 49.5 | 1.0096
427.4 | 49.5 | 1.0096
427.5 | 49.5 | 1.0096
427.6 | 49.5 | 1.0096
427.7 | 49.5 | 1.0096
427.8 | 49.5 | 1.0096
427.9 | 49.5 | 1.0096
428 | 49.5 | 1.0096
428.1 | 49.5 | 1.0096
428.2 | 49.5 | 1.0096
428.3 | 49.5 | 1.0096
428.4 | 49.5 | 1.0096
428.5 | 49.5 | 1.0096
428.6 | 49.5 | 1.0096
428.7 | 49.5 | 1.0096
428.8 | 49.5 | 1.0096
428.9 | 49.5 | 1.0096
429 | 49.5 | 1.0096
429.1 | 49.5 | 1.0096
429.2 | 49.5 | 1.0096
429.3 | 49.5 | 1.0096
429.4 | 49.5 | 1.0096
429.5 | 49.5 | 1.0096
429.6 | 49.5 | 1.0096
429.7 | 49.5 | 1.0096
429.8 | 49.5 | 1.0096
429.9 | 49.5 | 1.0096
430 | 49.5 | 1.0096
430.1 | 49.5 | 1.0096
430.2 | 49.5 | 1.0096
430.3 | 49.5 | 1.0096
430.4 | 49.5 | 1.0096
430.5 | 49.5 | 1.0096
430.6 | 49.5 | 1.0096
430.7 | 49.5 | 1.0096
430.8 | 49.5 | 1.0096
430.9 | 49.5 | 1.0096
431 | 49.5 | 1.0096
431.1 | 49.5 | 1.0096
431.2 | 49.5 | 1.0096
431.3 | 49.5 | 1.0096
431.4 | 49.5 | 1.0096
431.5 | 49.5 | 1.0096
431.6 | 49.5 | 1.0096
431.7 | 49.5 | 1.0096
431.8 | 49.5 | 1.0096
431.9 | 49.5 | 1.0096
432 | 49.5 | 1.0096
432.1 | 49.5 | 1.0096
432.2 | 49.5 | 1.0096
432.3 | 49.5 | 1.0096
432.4 | 49.5 | 1.0096
432.5 | 49.5 | 1.0096
432.6 | 49.5 | 1.0096
432.7 | 49.5 | 1.0096
432.8 | 49.5 | 1.0098
432.9 | 49.5 | 1.0098
433 | 49.5 | 1.0098
433.1 | 49.5 | 1.0098
433.2 | 49.5 | 1.0098
433.3 | 49.5 | 1.0098
433.4 | 49.5 | 1.0098
433.5 | 49.5 | 1.0098
433.6 | 49.5 | 1.0098
433.7 | 49.5 | 1.0098
433.8 | 49.5 | 1.0098
433.9 | 49.5 | 1.0098
434 | 49.5 | 1.0098
434.1 | 49.5 | 1.0098
434.2 | 49.5 | 1.0098
434.3 | 49.5 | 1.0098
434.4 | 49.5 | 1.0098
434.5 | 49.5 | 1.0098
434.6 | 49.5 | 1.0098
434.7 | 49.5 | 1.0098
434.8 | 49.5 | 1.0098
434.9 | 49.5 | 1.0098
435 | 49.5 | 1.0096
435.1 | 49.5 | 1.0096
435.2 | 49.5 | 1.0096
435.3 | 49.5 | 1.0096
435.4 | 49.5 | 1.0096
435.5 | 49.5 | 1.0096
435.6 | 49.5 | 1.0096
435.7 | 49.5 | 1.0096
435.8 | 49.5 | 1.0096
435.9 | 49.5 | 1.0096
436 | 49.5 | 1.0096
436.1 | 49.5 | 1.0096
436.2 | 49.5 | 1.0096
436.3 | 49.5 | 1.0096
436.4 | 49.5 | 1.0096
436.5 | 49.5 | 1.0096
436.6 | 49.5 | 1.0096
436.7 | 49.5 | 1.0096
436.8 | 49.5 | 1.0096
436.9 | 49.5 | 1.0096
437 | 49.5 | 1.0096
437.1 | 49.5 | 1.0096
437.2 | 49.5 | 1.0096
437.3 | 49.5 | 1.0096
437.4 | 49.5 | 1.0096
437.5 | 49.5 | 1.0096
437.6 | 49.5 | 1.0096
437.7 | 49.5 | 1.0096
437.8 | 49.5 | 1.0096
437.9 | 49.5 | 1.0096
438 | 49.5 | 1.0096
438.1 | 49.5 | 1.0096
438.2 | 49.5 | 1.0096
438.3 | 49.5 | 1.0096
438.4 | 49.5 | 1.0096
438.5 | 49.5 | 1.0096
438.6 | 49.5 | 1.0096
438.7 | 49.5 | 1.0096
438.8 | 49.5 | 1.0096
438.9 | 49.5 | 1.0096
439 | 49.5 | 1.0096
439.1 | 49.5 | 1.0096
439.2 | 49.5 | 1.0096
439.3 | 49.5 | 1.0096
439.4 | 49.5 | 1.0096
439.5 | 49.5 | 1.0096
439.6 | 49.5 | 1.0096
439.7 | 49.5 | 1.0096
439.8 | 49.5 | 1.0096
439.9 | 49.5 | 1.0096
440 | 49.5 | 1.0096
440.1 | 49.5 | 1.0096
440.2 | 49.5 | 1.0096
440.3 | 49.5 | 1.0096
440.4 | 49.5 | 1.0096
440.5 | 49.5 | 1.0096
440.6 | 49.5 | 1.0096
440.7 | 49.5 | 1.0096
440.8 | 49.5 | 1.0096
440.9 | 49.5 | 1.0096
441 | 49.5 | 1.0096
441.1 | 49.5 | 1.0096
441.2 | 49.5 | 1.0096
441.3 | 49.5 | 1.0096
441.4 | 49.5 | 1.0096
441.5 | 49.5 | 1.0096
441.6 | 49.5 | 1.0096
441.7 | 49.5 | 1.0096
441.8 | 49.5 | 1.0096
441.9 | 49.5 | 1.0096
442 | 49.5 | 1.0096
442.1 | 49.5 | 1.0096
442.2 | 49.5 | 1.0098
442.3 | 49.5 | 1.0098
442.4 | 49.5 | 1.0098
442.5 | 49.5 | 1.0098
442.6 | 49.5 | 1.0098
442.7 | 49.5 | 1.0098
442.8 | 49.5 | 1.0098
442.9 | 49.5 | 1.0098
443 | 49.5 | 1.0098
443.1 | 49.5 | 1.0098
443.2 | 49.5 | 1.0098
443.3 | 49.5 | 1.0096
443.4 | 49.5 | 1.0096
443.5 | 49.5 | 1.0096
443.6 | 49.5 | 1.0096
443.7 | 49.5 | 1.0096
443.8 | 49.5 | 1.0096
443.9 | 49.5 | 1.0096
444 | 49.5 | 1.0096
444.1 | 49.5 | 1.0096
444.2 | 49.5 | 1.0096
444.3 | 49.5 | 1.0096
444.4 | 49.5 | 1.0096
444.5 | 49.5 | 1.0096
444.6 | 49.5 | 1.0096
444.7 | 49.5 | 1.0096
444.8 | 49.5 | 1.0096
444.9 | 49.5 | 1.0096
445 | 49.5 | 1.0096
445.1 | 49.5 | 1.0096
445.2 | 49.5 | 1.0096
445.3 | 49.5 | 1.0096
445.4 | 49.5 | 1.0096
445.5 | 49.5 | 1.0096
445.6 | 49.5 | 1.0096
445.7 | 49.5 | 1.0096
445.8 | 49.5 | 1.0096
445.9 | 49.5 | 1.0096
446 | 49.5 | 1.0096
446.1 | 49.5 | 1.0096
446.2 | 49.5 | 1.0096
446.3 | 49.5 | 1.0096
446.4 | 49.5 | 1.0096
446.5 | 49.5 | 1.0096
446.6 | 49.5 | 1.0096
446.7 | 49.5 | 1.0096
446.8 | 49.5 | 1.0098
446.9 | 49.5 | 1.0098
447 | 49.5 | 1.0098
447.1 | 49.5 | 1.0098
447.2 | 49.5 | 1.0098
447.3 | 49.5 | 1.0098
447.4 | 49.5 | 1.0098
447.5 | 49.5 | 1.0098
447.6 | 49.5 | 1.0098
447.7 | 49.5 | 1.0098
447.8 | 49.5 | 1.0098
447.9 | 49.5 | 1.0098
448 | 49.5 | 1.0098
448.1 | 49.5 | 1.0096
448.2 | 49.5 | 1.0096
448.3 | 49.5 | 1.0096
448.4 | 49.5 | 1.0096
448.5 | 49.5 | 1.0096
448.6 | 49.5 | 1.0096
448.7 | 49.5 | 1.0096
448.8 | 49.5 | 1.0096
448.9 | 49.5 | 1.0096
449 | 49.5 | 1.0096
449.1 | 49.5 | 1.0096
449.2 | 49.5 | 1.0096
449.3 | 49.5 | 1.0096
449.4 | 49.5 | 1.0096
449.5 | 49.5 | 1.0096
449.6 | 49.5 | 1.0096
449.7 | 49.5 | 1.0096
449.8 | 49.5 | 1.0096
449.9 | 49.5 | 1.0096
450 | 49.5 | 1.0096
450.1 | 49.5 | 1.0096
450.2 | 49.5 | 1.0096
450.3 | 49.5 | 1.0096
450.4 | 49.5 | 1.0096
450.5 | 49.5 | 1.0096
450.6 | 49.5 | 1.0096
450.7 | 49.5 | 1.0096
450.8 | 49.5 | 1.0096
450.9 | 49.5 | 1.0096
451 | 49.5 | 1.0096
451.1 | 49.5 | 1.0096
451.2 | 49.5 | 1.0096
451.3 | 49.5 | 1.0096
451.4 | 49.5 | 1.0096
451.5 | 49.5 | 1.0096
451.6 | 49.5 | 1.0096
451.7 | 49.5 | 1.0096
451.8 | 49.5 | 1.0096
451.9 | 49.5 | 1.0096
452 | 49.5 | 1.0096
452.1 | 49.5 | 1.0096
452.2 | 49.5 | 1.0096
452.3 | 49.5 | 1.0096
452.4 | 49.5 | 1.0096
452.5 | 49.5 | 1.0096
452.6 | 49.5 | 1.0096
452.7 | 49.5 | 1.0096
452.8 | 49.5 | 1.0096
452.9 | 49.5 | 1.0096
453 | 49.5 | 1.0096
453.1 | 49.5 | 1.0096
453.2 | 49.5 | 1.0096
453.3 | 49.5 | 1.0096
453.4 | 49.5 | 1.0096
453.5 | 49.5 | 1.0096
453.6 | 49.5 | 1.0096
453.7 | 49.5 | 1.0096
453.8 | 49.5 | 1.0096
453.9 | 49.5 | 1.0096
454 | 49.5 | 1.0096
454.1 | 49.5 | 1.0096
454.2 | 49.5 | 1.0096
454.3 | 49.5 | 1.0096
454.4 | 49.5 | 1.0096
454.5 | 49.5 | 1.0096
454.6 | 49.5 | 1.0096
454.7 | 49.5 | 1.0096
454.8 | 49.5 | 1.0096
454.9 | 49.5 | 1.0096
455 | 49.5 | 1.0096
455.1 | 49.5 | 1.0096
455.2 | 49.5 | 1.0096
455.3 | 49.5 | 1.0096
455.4 | 49.5 | 1.0096
455.5 | 49.5 | 1.0096
455.6 | 49.5 | 1.0096
455.7 | 49.5 | 1.0096
455.8 | 49.5 | 1.0096
455.9 | 49.5 | 1.0096
456 | 49.5 | 1.0096
456.1 | 49.5 | 1.0096
456.2 | 49.5 | 1.0096
456.3 | 49.5 | 1.0096
456.4 | 49.5 | 1.0096
456.5 | 49.5 | 1.0096
456.6 | 49.5 | 1.0096
456.7 | 49.5 | 1.0096
456.8 | 49.5 | 1.0096
456.9 | 49.5 | 1.0096
457 | 49.5 | 1.0096
457.1 | 49.5 | 1.0096
457.2 | 49.5 | 1.0096
457.3 | 49.5 | 1.0096
457.4 | 49.5 | 1.0096
457.5 | 49.5 | 1.0096
457.6 | 49.5 | 1.0096
457.7 | 49.5 | 1.0096
457.8 | 49.5 | 1.0096
457.9 | 49.5 | 1.0096
458 | 49.5 | 1.0096
458.1 | 49.5 | 1.0096
458.2 | 49.5 | 1.0096
458.3 | 49.5 | 1.0096
458.4 | 49.5 | 1.0096
458.5 | 49.5 | 1.0096
458.6 | 49.5 | 1.0096
458.7 | 49.5 | 1.0096
458.8 | 49.5 | 1.0096
458.9 | 49.5 | 1.0096
459 | 49.5 | 1.0096
459.1 | 49.5 | 1.0096
459.2 | 49.5 | 1.0096
459.3 | 49.5 | 1.0096
459.4 | 49.5 | 1.0096
459.5 | 49.5 | 1.0096
459.6 | 49.5 | 1.0096
459.7 | 49.5 | 1.0096
459.8 | 49.5 | 1.0096
459.9 | 49.5 | 1.0096
460 | 49.5 | 1.0096
460.1 | 49.5 | 1.0096
460.2 | 49.5 | 1.0096
460.3 | 49.5 | 1.0096
460.4 | 49.5 | 1.0096
460.5 | 49.5 | 1.0096
460.6 | 49.5 | 1.0096
460.7 | 49.5 | 1.0096
460.8 | 49.5 | 1.0096
460.9 | 49.5 | 1.0096
461 | 49.5 | 1.0096
461.1 | 49.5 | 1.0096
461.2 | 49.5 | 1.0096
461.3 | 49.5 | 1.0096
461.4 | 49.5 | 1.0096
461.5 | 49.5 | 1.0096
461.6 | 49.5 | 1.0096
461.7 | 49.5 | 1.0096
461.8 | 49.5 | 1.0096
461.9 | 49.5 | 1.0096
462 | 49.5 | 1.0096
462.1 | 49.5 | 1.0096
462.2 | 49.5 | 1.0096
462.3 | 49.5 | 1.0096
462.4 | 49.5 | 1.0096
462.5 | 49.5 | 1.0098
462.6 | 49.5 | 1.0098
462.7 | 49.5 | 1.0098
462.8 | 49.5 | 1.0098
462.9 | 49.5 | 1.0098
463 | 49.5 | 1.0098
463.1 | 49.5 | 1.0098
463.2 | 49.5 | 1.0098
463.3 | 49.5 | 1.0098
463.4 | 49.5 | 1.0098
463.5 | 49.5 | 1.0098
463.6 | 49.5 | 1.0098
463.7 | 49.5 | 1.0098
463.8 | 49.5 | 1.0098
463.9 | 49.5 | 1.0098
464 | 49.5 | 1.0098
464.1 | 49.5 | 1.0098
464.2 | 49.5 | 1.0098
464.3 | 49.5 | 1.0098
464.4 | 49.5 | 1.0098
464.5 | 49.5 | 1.0098
464.6 | 49.5 | 1.0098
464.7 | 49.5 | 1.0098
464.8 | 49.5 | 1.0098
464.9 | 49.5 | 1.0096
465 | 49.5 | 1.0096
465.1 | 49.5 | 1.0096
465.2 | 49.5 | 1.0096
465.3 | 49.5 | 1.0096
465.4 | 49.5 | 1.0096
465.5 | 49.5 | 1.0096
465.6 | 49.5 | 1.0096
465.7 | 49.5 | 1.0096
465.8 | 49.5 | 1.0096
465.9 | 49.5 | 1.0096
466 | 49.5 | 1.0096
466.1 | 49.5 | 1.0096
466.2 | 49.5 | 1.0096
466.3 | 49.5 | 1.0096
466.4 | 49.5 | 1.0096
466.5 | 49.5 | 1.0096
466.6 | 49.5 | 1.0096
466.7 | 49.5 | 1.0096
466.8 | 49.5 | 1.0096
466.9 | 49.5 | 1.0096
467 | 49.5 | 1.0096
467.1 | 49.5 | 1.0096
467.2 | 49.5 | 1.0096
467.3 | 49.5 | 1.0096
467.4 | 49.5 | 1.0096
467.5 | 49.5 | 1.0096
467.6 | 49.5 | 1.0096
467.7 | 49.5 | 1.0096
467.8 | 49.5 | 1.0096
467.9 | 49.5 | 1.0096
468 | 49.5 | 1.0096
468.1 | 49.5 | 1.0096
468.2 | 49.5 | 1.0096
468.3 | 49.5 | 1.0096
468.4 | 49.5 | 1.0096
468.5 | 49.5 | 1.0096
468.6 | 49.5 | 1.0096
468.7 | 49.5 | 1.0096
468.8 | 49.5 | 1.0096
468.9 | 49.5 | 1.0096
469 | 49.5 | 1.0096
469.1 | 49.5 | 1.0096
469.2 | 49.5 | 1.0096
469.3 | 49.5 | 1.0096
469.4 | 49.5 | 1.0096
469.5 | 49.5 | 1.0096
469.6 | 49.5 | 1.0096
469.7 | 49.5 | 1.0096
469.8 | 49.5 | 1.0096
469.9 | 49.5 | 1.0096
470 | 49.5 | 1.0096
470.1 | 49.5 | 1.0096
470.2 | 49.5 | 1.0096
470.3 | 49.5 | 1.0096
470.4 | 49.5 | 1.0096
470.5 | 49.5 | 1.0096
470.6 | 49.5 | 1.0096
470.7 | 49.5 | 1.0096
470.8 | 49.5 | 1.0096
470.9 | 49.5 | 1.0096
471 | 49.5 | 1.0096
471.1 | 49.5 | 1.0096
471.2 | 49.5 | 1.0096
471.3 | 49.5 | 1.0096
471.4 | 49.5 | 1.0096
471.5 | 49.5 | 1.0096
471.6 | 49.5 | 1.0096
471.7 | 49.5 | 1.0096
471.8 | 49.5 | 1.0096
471.9 | 49.5 | 1.0098
472 | 49.5 | 1.0098
472.1 | 49.5 | 1.0098
472.2 | 49.5 | 1.0098
472.3 | 49.5 | 1.0098
472.4 | 49.5 | 1.0098
472.5 | 49.5 | 1.0098
472.6 | 49.5 | 1.0098
472.7 | 49.5 | 1.0098
472.8 | 49.5 | 1.0098
472.9 | 49.5 | 1.0096
473 | 49.5 | 1.0096
473.1 | 49.5 | 1.0096
473.2 | 49.5 | 1.0096
473.3 | 49.5 | 1.0096
473.4 | 49.5 | 1.0096
473.5 | 49.5 | 1.0096
473.6 | 49.5 | 1.0096
473.7 | 49.5 | 1.0096
473.8 | 49.5 | 1.0096
473.9 | 49.5 | 1.0096
474 | 49.5 | 1.0096
474.1 | 49.5 | 1.0096
474.2 | 49.5 | 1.0096
474.3 | 49.5 | 1.0096
474.4 | 49.5 | 1.0096
474.5 | 49.5 | 1.0096
474.6 | 49.5 | 1.0096
474.7 | 49.5 | 1.0096
474.8 | 49.5 | 1.0096
474.9 | 49.5 | 1.0096
475 | 49.5 | 1.0096
475.1 | 49.5 | 1.0096
475.2 | 49.5 | 1.0096
475.3 | 49.5 | 1.0096
475.4 | 49.5 | 1.0096
475.5 | 49.5 | 1.0096
475.6 | 49.5 | 1.0096
475.7 | 49.5 | 1.0096
475.8 | 49.5 | 1.0096
475.9 | 49.5 | 1.0096
476 | 49.5 | 1.0096
476.1 | 49.5 | 1.0096
476.2 | 49.5 | 1.0096
476.3 | 49.5 | 1.0096
476.4 | 49.5 | 1.0096
476.5 | 49.5 | 1.0096
476.6 | 49.5 | 1.0096
476.7 | 49.5 | 1.0096
476.8 | 49.5 | 1.0096
476.9 | 49.5 | 1.0096
477 | 49.5 | 1.0096
477.1 | 49.5 | 1.0096
477.2 | 49.5 | 1.0096
477.3 | 49.5 | 1.0096
477.4 | 49.5 | 1.0096
477.5 | 49.5 | 1.0096
477.6 | 49.5 | 1.0096
477.7 | 49.5 | 1.0096
477.8 | 49.5 | 1.0096
477.9 | 49.5 | 1.0096
478 | 49.5 | 1.0096
478.1 | 49.5 | 1.0096
478.2 | 49.5 | 1.0096
478.3 | 49.5 | 1.0096
478.4 | 49.5 | 1.0096
478.5 | 49.5 | 1.0096
478.6 | 49.5 | 1.0096
478.7 | 49.5 | 1.0096
478.8 | 49.5 | 1.0096
478.9 | 49.5 | 1.0096
479 | 49.5 | 1.0096
479.1 | 49.5 | 1.0096
479.2 | 49.5 | 1.0096
479.3 | 49.5 | 1.0096
479.4 | 49.5 | 1.0096
479.5 | 49.5 | 1.0096
479.6 | 49.5 | 1.0096
479.7 | 49.5 | 1.0096
479.8 | 49.5 | 1.0096
479.9 | 49.5 | 1.0098
480 | 49.5 | 1.0098
480.1 | 49.5 | 1.0098
480.2 | 49.5 | 1.0098
480.3 | 49.5 | 1.0098
480.4 | 49.5 | 1.0098
480.5 | 49.5 | 1.0098
480.6 | 49.5 | 1.0098
480.7 | 49.5 | 1.0098
480.8 | 49.5 | 1.0098
480.9 | 49.5 | 1.0098
481 | 49.5 | 1.0098
481.1 | 49.5 | 1.0098
481.2 | 49.5 | 1.0098
481.3 | 49.5 | 1.0098
481.4 | 49.5 | 1.0098
481.5 | 49.5 | 1.0098
481.6 | 49.5 | 1.0098
481.7 | 49.5 | 1.0098
481.8 | 49.5 | 1.0098
481.9 | 49.5 | 1.0098
482 | 49.5 | 1.0096
482.1 | 49.5 | 1.0096
482.2 | 49.5 | 1.0096
482.3 | 49.5 | 1.0096
482.4 | 49.5 | 1.0096
482.5 | 49.5 | 1.0096
482.6 | 49.5 | 1.0096
482.7 | 49.5 | 1.0096
482.8 | 49.5 | 1.0096
482.9 | 49.5 | 1.0096
483 | 49.5 | 1.0096
483.1 | 49.5 | 1.0096
483.2 | 49.5 | 1.0096
483.3 | 49.5 | 1.0096
483.4 | 49.5 | 1.0096
483.5 | 49.5 | 1.0096
483.6 | 49.5 | 1.0096
483.7 | 49.5 | 1.0096
483.8 | 49.5 | 1.0096
483.9 | 49.5 | 1.0096
484 | 49.5 | 1.0096
484.1 | 49.5 | 1.0096
484.2 | 49.5 | 1.0096
484.3 | 49.5 | 1.0096
484.4 | 49.5 | 1.0096
484.5 | 49.5 | 1.0096
484.6 | 49.5 | 1.0096
484.7 | 49.5 | 1.0096
484.8 | 49.5 | 1.0096
484.9 | 49.5 | 1.0096
485 | 49.5 | 1.0096
485.1 | 49.5 | 1.0096
485.2 | 49.5 | 1.0096
485.3 | 49.5 | 1.0096
485.4 | 49.5 | 1.0096
485.5 | 49.5 | 1.0096
485.6 | 49.5 | 1.0096
485.7 | 49.5 | 1.0096
485.8 | 49.5 | 1.0096
485.9 | 49.5 | 1.0096
486 | 49.5 | 1.0096
486.1 | 49.5 | 1.0096
486.2 | 49.5 | 1.0096
486.3 | 49.5 | 1.0096
486.4 | 49.5 | 1.0096
486.5 | 49.5 | 1.0096
486.6 | 49.5 | 1.0096
486.7 | 49.5 | 1.0096
486.8 | 49.5 | 1.0096
486.9 | 49.5 | 1.0096
487 | 49.5 | 1.0096
487.1 | 49.5 | 1.0096
487.2 | 49.5 | 1.0096
487.3 | 49.5 | 1.0096
487.4 | 49.5 | 1.0096
487.5 | 49.5 | 1.0096
487.6 | 49.5 | 1.0096
487.7 | 49.5 | 1.0096
487.8 | 49.5 | 1.0096
487.9 | 49.5 | 1.0096
488 | 49.5 | 1.0096
488.1 | 49.5 | 1.0096
488.2 | 49.5 | 1.0096
488.3 | 49.5 | 1.0096
488.4 | 49.5 | 1.0096
488.5 | 49.5 | 1.0096
488.6 | 49.5 | 1.0096
488.7 | 49.5 | 1.0096
488.8 | 49.5 | 1.0096
488.9 | 49.5 | 1.0096
489 | 49.5 | 1.0096
489.1 | 49.5 | 1.0096
489.2 | 49.5 | 1.0096
489.3 | 49.5 | 1.0096
489.4 | 49.5 | 1.0096
489.5 | 49.5 | 1.0096
489.6 | 49.5 | 1.0096
489.7 | 49.5 | 1.0096
489.8 | 49.5 | 1.0096
489.9 | 49.5 | 1.0096
490 | 49.5 | 1.0096
490.1 | 49.5 | 1.0096
490.2 | 49.5 | 1.0096
490.3 | 49.5 | 1.0096
490.4 | 49.5 | 1.0096
490.5 | 49.5 | 1.0096
490.6 | 49.5 | 1.0096
490.7 | 49.5 | 1.0096
490.8 | 49.5 | 1.0096
490.9 | 49.5 | 1.0096
491 | 49.5 | 1.0096
491.1 | 49.5 | 1.0096
491.2 | 49.5 | 1.0096
491.3 | 49.5 | 1.0096
491.4 | 49.5 | 1.0096
491.5 | 49.5 | 1.0096
491.6 | 49.5 | 1.0096
491.7 | 49.5 | 1.0096
491.8 | 49.5 | 1.0096
491.9 | 49.5 | 1.0096
492 | 49.5 | 1.0096
492.1 | 49.5 | 1.0096
492.2 | 49.5 | 1.0096
492.3 | 49.5 | 1.0096
492.4 | 49.5 | 1.0096
492.5 | 49.5 | 1.0096
492.6 | 49.5 | 1.0096
492.7 | 49.5 | 1.0096
492.8 | 49.5 | 1.0096
492.9 | 49.5 | 1.0096
493 | 49.5 | 1.0096
493.1 | 49.5 | 1.0096
493.2 | 49.5 | 1.0096
493.3 | 49.5 | 1.0096
493.4 | 49.5 | 1.0096
493.5 | 49.5 | 1.0096
493.6 | 49.5 | 1.0096
493.7 | 49.5 | 1.0096
493.8 | 49.5 | 1.0096
493.9 | 49.5 | 1.0096
494 | 49.5 | 1.0096
494.1 | 49.5 | 1.0096
494.2 | 49.5 | 1.0096
494.3 | 49.5 | 1.0096
494.4 | 49.5 | 1.0096
494.5 | 49.5 | 1.0096
494.6 | 49.5 | 1.0096
494.7 | 49.5 | 1.0096
494.8 | 49.5 | 1.0096
494.9 | 49.5 | 1.0096
495 | 49.5 | 1.0096
495.1 | 49.5 | 1.0096
495.2 | 49.5 | 1.0096
495.3 | 49.5 | 1.0096
495.4 | 49.5 | 1.0096
495.5 | 49.5 | 1.0096
495.6 | 49.5 | 1.0096
495.7 | 49.5 | 1.0096
495.8 | 49.5 | 1.0096
495.9 | 49.5 | 1.0096
496 | 49.5 | 1.0096
496.1 | 49.5 | 1.0096
496.2 | 49.5 | 1.0096
496.3 | 49.5 | 1.0096
496.4 | 49.5 | 1.0096
496.5 | 49.5 | 1.0096
496.6 | 49.5 | 1.0096
496.7 | 49.5 | 1.0096
496.8 | 49.5 | 1.0096
496.9 | 49.5 | 1.0096
497 | 49.5 | 1.0096
497.1 | 49.5 | 1.0096
497.2 | 49.5 | 1.0096
497.3 | 49.5 | 1.0096
497.4 | 49.5 | 1.0096
497.5 | 49.5 | 1.0098
497.6 | 49.5 | 1.0098
497.7 | 49.5 | 1.0098
497.8 | 49.5 | 1.0098
497.9 | 49.5 | 1.0098
498 | 49.5 | 1.0098
498.1 | 49.5 | 1.0098
498.2 | 49.5 | 1.0098
498.3 | 49.5 | 1.0098
498.4 | 49.5 | 1.0098
498.5 | 49.5 | 1.0098
498.6 | 49.5 | 1.0098
498.7 | 49.5 | 1.0098
498.8 | 49.5 | 1.0098
498.9 | 49.5 | 1.0098
499 | 49.5 | 1.0098
499.1 | 49.5 | 1.0098
499.2 | 49.5 | 1.0098
499.3 | 49.5 | 1.0098
499.4 | 49.5 | 1.0098
499.5 | 49.5 | 1.0098
499.6 | 49.5 | 1.0098
499.7 | 49.5 | 1.0098
499.8 | 49.5 | 1.0098
499.9 | 49.5 | 1.0096
500 | 49.5 | 1.0096
500.1 | 49.5 | 1.0096
500.2 | 49.5 | 1.0096
500.3 | 49.5 | 1.0096
500.4 | 49.5 | 1.0096
500.5 | 49.5 | 1.0096
500.6 | 49.5 | 1.0096
500.7 | 49.5 | 1.0096
500.8 | 49.5 | 1.0096
500.9 | 49.5 | 1.0096
501 | 49.5 | 1.0096
501.1 | 49.5 | 1.0096
501.2 | 49.5 | 1.0096
501.3 | 49.5 | 1.0096
501.4 | 49.5 | 1.0096
501.5 | 49.5 | 1.0096
501.6 | 49.5 | 1.0096
501.7 | 49.5 | 1.0096
501.8 | 49.5 | 1.0096
501.9 | 49.5 | 1.0096
502 | 49.5 | 1.0096
502.1 | 49.5 | 1.0096
502.2 | 49.5 | 1.0096
502.3 | 49.5 | 1.0096
502.4 | 49.5 | 1.0096
502.5 | 49.5 | 1.0096
502.6 | 49.5 | 1.0096
502.7 | 49.5 | 1.0096
502.8 | 49.5 | 1.0096
502.9 | 49.5 | 1.0096
503 | 49.5 | 1.0096
503.1 | 49.5 | 1.0096
503.2 | 49.5 | 1.0096
503.3 | 49.5 | 1.0096
503.4 | 49.5 | 1.0096
503.5 | 49.5 | 1.0096
503.6 | 49.5 | 1.0096
503.7 | 49.5 | 1.0096
503.8 | 49.5 | 1.0096
503.9 | 49.5 | 1.0096
504 | 49.5 | 1.0096
504.1 | 49.5 | 1.0096
504.2 | 49.5 | 1.0096
504.3 | 49.5 | 1.0096
504.4 | 49.5 | 1.0096
504.5 | 49.5 | 1.0096
504.6 | 49.5 | 1.0096
504.7 | 49.5 | 1.0096
504.8 | 49.5 | 1.0096
504.9 | 49.5 | 1.0096
505 | 49.5 | 1.0096
505.1 | 49.5 | 1.0096
505.2 | 49.5 | 1.0096
505.3 | 49.5 | 1.0096
505.4 | 49.5 | 1.0096
505.5 | 49.5 | 1.0096
505.6 | 49.5 | 1.0096
505.7 | 49.5 | 1.0096
505.8 | 49.5 | 1.0096
505.9 | 49.5 | 1.0096
506 | 49.5 | 1.0096
506.1 | 49.5 | 1.0096
506.2 | 49.5 | 1.0096
506.3 | 49.5 | 1.0096
506.4 | 49.5 | 1.0096
506.5 | 49.5 | 1.0096
506.6 | 49.5 | 1.0096
506.7 | 49.5 | 1.0096
506.8 | 49.5 | 1.0096
506.9 | 49.5 | 1.0096
507 | 49.5 | 1.0096
507.1 | 49.5 | 1.0096
507.2 | 49.5 | 1.0096
507.3 | 49.5 | 1.0096
507.4 | 49.5 | 1.0096
507.5 | 49.5 | 1.0096
507.6 | 49.5 | 1.0096
507.7 | 49.5 | 1.0096
507.8 | 49.5 | 1.0096
507.9 | 49.5 | 1.0096
508 | 49.5 | 1.0096
508.1 | 49.5 | 1.0096
508.2 | 49.5 | 1.0096
508.3 | 49.5 | 1.0096
508.4 | 49.5 | 1.0096
508.5 | 49.5 | 1.0096
508.6 | 49.5 | 1.0096
508.7 | 49.5 | 1.0096
508.8 | 49.5 | 1.0096
508.9 | 49.5 | 1.0096
509 | 49.5 | 1.0096
509.1 | 49.5 | 1.0096
509.2 | 49.5 | 1.0096
509.3 | 49.5 | 1.0096
509.4 | 49.5 | 1.0096
509.5 | 49.5 | 1.0096
509.6 | 49.5 | 1.0096
509.7 | 49.5 | 1.0096
509.8 | 49.5 | 1.0096
509.9 | 49.5 | 1.0096
510 | 49.5 | 1.0096
510.1 | 49.5 | 1.0096
510.2 | 49.5 | 1.0096
510.3 | 49.5 | 1.0096
510.4 | 49.5 | 1.0096
510.5 | 49.5 | 1.0096
510.6 | 49.5 | 1.0096
510.7 | 49.5 | 1.0096
510.8 | 49.5 | 1.0096
510.9 | 49.5 | 1.0096
511 | 49.5 | 1.0096
511.1 | 49.5 | 1.0096
511.2 | 49.5 | 1.0096
511.3 | 49.5 | 1.0096
511.4 | 49.5 | 1.0096
511.5 | 49.5 | 1.0096
511.6 | 49.5 | 1.0096
511.7 | 49.5 | 1.0096
511.8 | 49.5 | 1.0096
511.9 | 49.5 | 1.0096
512 | 49.5 | 1.0096
512.1 | 49.5 | 1.0096
512.2 | 49.5 | 1.0096
512.3 | 49.5 | 1.0096
512.4 | 49.5 | 1.0096
512.5 | 49.5 | 1.0096
512.6 | 49.5 | 1.0096
512.7 | 49.5 | 1.0096
512.8 | 49.5 | 1.0096
512.9 | 49.5 | 1.0096
513 | 49.5 | 1.0096
513.1 | 49.5 | 1.0096
513.2 | 49.5 | 1.0096
513.3 | 49.5 | 1.0096
513.4 | 49.5 | 1.0096
513.5 | 49.5 | 1.0096
513.6 | 49.5 | 1.0096
513.7 | 49.5 | 1.0096
513.8 | 49.5 | 1.0096
513.9 | 49.5 | 1.0096
514 | 49.5 | 1.0096
514.1 | 49.5 | 1.0096
514.2 | 49.5 | 1.0096
514.3 | 49.5 | 1.0096
514.4 | 49.5 | 1.0096
514.5 | 49.5 | 1.0096
514.6 | 49.5 | 1.0096
514.7 | 49.5 | 1.0096
514.8 | 49.5 | 1.0096
514.9 | 49.5 | 1.0096
515 | 49.5 | 1.0096
515.1 | 49.5 | 1.0096
515.2 | 49.5 | 1.0096
515.3 | 49.5 | 1.0096
515.4 | 49.5 | 1.0096
515.5 | 49.5 | 1.0096
515.6 | 49.5 | 1.0096
515.7 | 49.5 | 1.0096
515.8 | 49.5 | 1.0096
515.9 | 49.5 | 1.0096
516 | 49.5 | 1.0096
516.1 | 49.5 | 1.0096
516.2 | 49.5 | 1.0096
516.3 | 49.5 | 1.0096
516.4 | 49.5 | 1.0096
516.5 | 49.5 | 1.0096
516.6 | 49.5 | 1.0096
516.7 | 49.5 | 1.0096
516.8 | 49.5 | 1.0096
516.9 | 49.5 | 1.0096
517 | 49.5 | 1.0096
517.1 | 49.5 | 1.0096
517.2 | 49.5 | 1.0096
517.3 | 49.5 | 1.0096
517.4 | 49.5 | 1.0096
517.5 | 49.5 | 1.0096
517.6 | 49.5 | 1.0096
517.7 | 49.5 | 1.0096
517.8 | 49.5 | 1.0096
517.9 | 49.5 | 1.0096
518 | 49.5 | 1.0096
518.1 | 49.5 | 1.0096
518.2 | 49.5 | 1.0096
518.3 | 49.5 | 1.0096
518.4 | 49.5 | 1.0096
518.5 | 49.5 | 1.0096
518.6 | 49.5 | 1.0096
518.7 | 49.5 | 1.0096
518.8 | 49.5 | 1.0096
518.9 | 49.5 | 1.0096
519 | 49.5 | 1.0096
519.1 | 49.5 | 1.0096
519.2 | 49.5 | 1.0096
519.3 | 49.5 | 1.0096
519.4 | 49.5 | 1.0096
519.5 | 49.5 | 1.0096
519.6 | 49.5 | 1.0096
519.7 | 49.5 | 1.0096
519.8 | 49.5 | 1.0096
519.9 | 49.5 | 1.0096
520 | 49.5 | 1.0096
520.1 | 49.5 | 1.0096
520.2 | 49.5 | 1.0096
520.3 | 49.5 | 1.0096
520.4 | 49.5 | 1.0096
520.5 | 49.5 | 1.0096
520.6 | 49.5 | 1.0096
520.7 | 49.5 | 1.0096
520.8 | 49.5 | 1.0096
520.9 | 49.5 | 1.0096
521 | 49.5 | 1.0096
521.1 | 49.5 | 1.0096
521.2 | 49.5 | 1.0096
521.3 | 49.5 | 1.0096
521.4 | 49.5 | 1.0096
521.5 | 49.5 | 1.0096
521.6 | 49.5 | 1.0096
521.7 | 49.5 | 1.0096
521.8 | 49.5 | 1.0096
521.9 | 49.5 | 1.0096
522 | 49.5 | 1.0096
522.1 | 49.5 | 1.0096
522.2 | 49.5 | 1.0096
522.3 | 49.5 | 1.0096
522.4 | 49.5 | 1.0096
522.5 | 49.5 | 1.0096
522.6 | 49.5 | 1.0096
522.7 | 49.5 | 1.0096
522.8 | 49.5 | 1.0096
522.9 | 49.5 | 1.0096
523 | 49.5 | 1.0098
523.1 | 49.5 | 1.0098
523.2 | 49.5 | 1.0098
523.3 | 49.5 | 1.0098
523.4 | 49.5 | 1.0098
523.5 | 49.5 | 1.0098
523.6 | 49.5 | 1.0098
523.7 | 49.5 | 1.0098
523.8 | 49.5 | 1.0098
523.9 | 49.5 | 1.0098
524 | 49.5 | 1.0098
524.1 | 49.5 | 1.0096
524.2 | 49.5 | 1.0096
524.3 | 49.5 | 1.0096
524.4 | 49.5 | 1.0096
524.5 | 49.5 | 1.0096
524.6 | 49.5 | 1.0096
524.7 | 49.5 | 1.0096
524.8 | 49.5 | 1.0096
524.9 | 49.5 | 1.0096
525 | 49.5 | 1.0096
525.1 | 49.5 | 1.0096
525.2 | 49.5 | 1.0096
525.3 | 49.5 | 1.0096
525.4 | 49.5 | 1.0096
525.5 | 49.5 | 1.0096
525.6 | 49.5 | 1.0096
525.7 | 49.5 | 1.0096
525.8 | 49.5 | 1.0096
525.9 | 49.5 | 1.0096
526 | 49.5 | 1.0096
526.1 | 49.5 | 1.0096
526.2 | 49.5 | 1.0096
526.3 | 49.5 | 1.0096
526.4 | 49.5 | 1.0096
526.5 | 49.5 | 1.0096
526.6 | 49.5 | 1.0098
526.7 | 49.5 | 1.0098
526.8 | 49.5 | 1.0098
526.9 | 49.5 | 1.0098
527 | 49.5 | 1.0098
527.1 | 49.5 | 1.0098
527.2 | 49.5 | 1.0098
527.3 | 49.5 | 1.0098
527.4 | 49.5 | 1.0098
527.5 | 49.5 | 1.0098
527.6 | 49.5 | 1.0098
527.7 | 49.5 | 1.0096
527.8 | 49.5 | 1.0096
527.9 | 49.5 | 1.0096
528 | 49.5 | 1.0096
528.1 | 49.5 | 1.0096
528.2 | 49.5 | 1.0096
528.3 | 49.5 | 1.0096
528.4 | 49.5 | 1.0096
528.5 | 49.5 | 1.0096
528.6 | 49.5 | 1.0096
528.7 | 49.5 | 1.0096
528.8 | 49.5 | 1.0096
528.9 | 49.5 | 1.0096
529 | 49.5 | 1.0096
529.1 | 49.5 | 1.0096
529.2 | 49.5 | 1.0096
529.3 | 49.5 | 1.0096
529.4 | 49.5 | 1.0096
529.5 | 49.5 | 1.0096
529.6 | 49.5 | 1.0096
529.7 | 49.5 | 1.0096
529.8 | 49.5 | 1.0096
529.9 | 49.5 | 1.0096
530 | 49.5 | 1.0096
530.1 | 49.5 | 1.0096
530.2 | 49.5 | 1.0096
530.3 | 49.5 | 1.0096
530.4 | 49.5 | 1.0096
530.5 | 49.5 | 1.0096
530.6 | 49.5 | 1.0096
530.7 | 49.5 | 1.0096
530.8 | 49.5 | 1.0096
530.9 | 49.5 | 1.0096
531 | 49.5 | 1.0096
531.1 | 49.5 | 1.0096
531.2 | 49.5 | 1.0096
531.3 | 49.5 | 1.0096
531.4 | 49.5 | 1.0096
531.5 | 49.5 | 1.0096
531.6 | 49.5 | 1.0096
531.7 | 49.5 | 1.0096
531.8 | 49.5 | 1.0096
531.9 | 49.5 | 1.0096
532 | 49.5 | 1.0096
532.1 | 49.5 | 1.0096
532.2 | 49.5 | 1.0096
532.3 | 49.5 | 1.0096
532.4 | 49.5 | 1.0096
532.5 | 49.5 | 1.0096
532.6 | 49.5 | 1.0096
532.7 | 49.5 | 1.0096
532.8 | 49.5 | 1.0096
532.9 | 49.5 | 1.0096
533 | 49.5 | 1.0096
533.1 | 49.5 | 1.0096
533.2 | 49.5 | 1.0096
533.3 | 49.5 | 1.0096
533.4 | 49.5 | 1.0096
533.5 | 49.5 | 1.0096
533.6 | 49.5 | 1.0096
533.7 | 49.5 | 1.0096
533.8 | 49.5 | 1.0096
533.9 | 49.5 | 1.0096
534 | 49.5 | 1.0096
534.1 | 49.5 | 1.0096
534.2 | 49.5 | 1.0096
534.3 | 49.5 | 1.0096
534.4 | 49.5 | 1.0096
534.5 | 49.5 | 1.0096
534.6 | 49.5 | 1.0096
534.7 | 49.5 | 1.0096
534.8 | 49.5 | 1.0096
534.9 | 49.5 | 1.0096
535 | 49.5 | 1.0096
535.1 | 49.5 | 1.0096
535.2 | 49.5 | 1.0096
535.3 | 49.5 | 1.0096
535.4 | 49.5 | 1.0096
535.5 | 49.5 | 1.0096
535.6 | 49.5 | 1.0096
535.7 | 49.5 | 1.0096
535.8 | 49.5 | 1.0096
535.9 | 49.5 | 1.0096
536 | 49.5 | 1.0096
536.1 | 49.5 | 1.0096
536.2 | 49.5 | 1.0096
536.3 | 49.5 | 1.0096
536.4 | 49.5 | 1.0096
536.5 | 49.5 | 1.0096
536.6 | 49.5 | 1.0096
536.7 | 49.5 | 1.0096
536.8 | 49.5 | 1.0096
536.9 | 49.5 | 1.0096
537 | 49.5 | 1.0096
537.1 | 49.5 | 1.0096
537.2 | 49.5 | 1.0096
537.3 | 49.5 | 1.0096
537.4 | 49.5 | 1.0096
537.5 | 49.5 | 1.0096
537.6 | 49.5 | 1.0096
537.7 | 49.5 | 1.0096
537.8 | 49.5 | 1.0096
537.9 | 49.5 | 1.0096
538 | 49.5 | 1.0096
538.1 | 49.5 | 1.0096
538.2 | 49.5 | 1.0096
538.3 | 49.5 | 1.0096
538.4 | 49.5 | 1.0096
538.5 | 49.5 | 1.0096
538.6 | 49.5 | 1.0096
538.7 | 49.5 | 1.0096
538.8 | 49.5 | 1.0096
538.9 | 49.5 | 1.0096
539 | 49.5 | 1.0096
539.1 | 49.5 | 1.0096
539.2 | 49.5 | 1.0096
539.3 | 49.5 | 1.0096
539.4 | 49.5 | 1.0096
539.5 | 49.5 | 1.0096
539.6 | 49.5 | 1.0096
539.7 | 49.5 | 1.0096
539.8 | 49.5 | 1.0096
539.9 | 49.5 | 1.0096
540 | 49.5 | 1.0096
540.1 | 49.5 | 1.0096
540.2 | 49.5 | 1.0096
540.3 | 49.5 | 1.0096
540.4 | 49.5 | 1.0096
540.5 | 49.5 | 1.0096
540.6 | 49.5 | 1.0096
540.7 | 49.5 | 1.0096
540.8 | 49.5 | 1.0096
540.9 | 49.5 | 1.0096
541 | 49.5 | 1.0096
541.1 | 49.5 | 1.0096
541.2 | 49.5 | 1.0096
541.3 | 49.5 | 1.0096
541.4 | 49.5 | 1.0096
541.5 | 49.5 | 1.0096
541.6 | 49.5 | 1.0096
541.7 | 49.5 | 1.0096
541.8 | 49.5 | 1.0096
541.9 | 49.5 | 1.0096
542 | 49.5 | 1.0096
542.1 | 49.5 | 1.0096
542.2 | 49.5 | 1.0096
542.3 | 49.5 | 1.0096
542.4 | 49.5 | 1.0096
542.5 | 49.5 | 1.0096
542.6 | 49.5 | 1.0096
542.7 | 49.5 | 1.0096
542.8 | 49.5 | 1.0096
542.9 | 49.5 | 1.0096
543 | 49.5 | 1.0096
543.1 | 49.5 | 1.0096
543.2 | 49.5 | 1.0096
543.3 | 49.5 | 1.0096
543.4 | 49.5 | 1.0096
543.5 | 49.5 | 1.0096
543.6 | 49.5 | 1.0096
543.7 | 49.5 | 1.0096
543.8 | 49.5 | 1.0096
543.9 | 49.5 | 1.0096
544 | 49.5 | 1.0096
544.1 | 49.5 | 1.0096
544.2 | 49.5 | 1.0096
544.3 | 49.5 | 1.0096
544.4 | 49.5 | 1.0096
544.5 | 49.5 | 1.0096
544.6 | 49.5 | 1.0096
544.7 | 49.5 | 1.0096
544.8 | 49.5 | 1.0096
544.9 | 49.5 | 1.0096
545 | 49.5 | 1.0096
545.1 | 49.5 | 1.0096
545.2 | 49.5 | 1.0096
545.3 | 49.5 | 1.0096
545.4 | 49.5 | 1.0096
545.5 | 49.5 | 1.0096
545.6 | 49.5 | 1.0096
545.7 | 49.5 | 1.0096
545.8 | 49.5 | 1.0096
545.9 | 49.5 | 1.0096
546 | 49.5 | 1.0096
546.1 | 49.5 | 1.0096
546.2 | 49.5 | 1.0096
546.3 | 49.5 | 1.0096
546.4 | 49.5 | 1.0096
546.5 | 49.5 | 1.0096
546.6 | 49.5 | 1.0096
546.7 | 49.5 | 1.0096
546.8 | 49.5 | 1.0096
546.9 | 49.5 | 1.0096
547 | 49.5 | 1.0096
547.1 | 49.5 | 1.0096
547.2 | 49.5 | 1.0096
547.3 | 49.5 | 1.0096
547.4 | 49.5 | 1.0096
547.5 | 49.5 | 1.0096
547.6 | 49.5 | 1.0096
547.7 | 49.5 | 1.0096
547.8 | 49.5 | 1.0096
547.9 | 49.5 | 1.0096
548 | 49.5 | 1.0096
548.1 | 49.5 | 1.0096
548.2 | 49.5 | 1.0096
548.3 | 49.5 | 1.0096
548.4 | 49.5 | 1.0096
548.5 | 49.5 | 1.0096
548.6 | 49.5 | 1.0096
548.7 | 49.5 | 1.0096
548.8 | 49.5 | 1.0096
548.9 | 49.5 | 1.0096
549 | 49.5 | 1.0096
549.1 | 49.5 | 1.0096
549.2 | 49.5 | 1.0096
549.3 | 49.5 | 1.0096
549.4 | 49.5 | 1.0096
549.5 | 49.5 | 1.0096
549.6 | 49.5 | 1.0096
549.7 | 49.5 | 1.0096
549.8 | 49.5 | 1.0096
549.9 | 49.5 | 1.0096
550 | 49.5 | 1.0096
550.1 | 49.5 | 1.0096
550.2 | 49.5 | 1.0096
550.3 | 49.5 | 1.0096
550.4 | 49.5 | 1.0096
550.5 | 49.5 | 1.0096
550.6 | 49.5 | 1.0096
550.7 | 49.5 | 1.0096
550.8 | 49.5 | 1.0096
550.9 | 49.5 | 1.0096
551 | 49.5 | 1.0096
551.1 | 49.5 | 1.0096
551.2 | 49.5 | 1.0096
551.3 | 49.5 | 1.0096
551.4 | 49.5 | 1.0096
551.5 | 49.5 | 1.0096
551.6 | 49.5 | 1.0096
551.7 | 49.5 | 1.0096
551.8 | 49.5 | 1.0096
551.9 | 49.5 | 1.0096
552 | 49.5 | 1.0096
552.1 | 49.5 | 1.0096
552.2 | 49.5 | 1.0096
552.3 | 49.5 | 1.0096
552.4 | 49.5 | 1.0096
552.5 | 49.5 | 1.0096
552.6 | 49.5 | 1.0096
552.7 | 49.5 | 1.0096
552.8 | 49.5 | 1.0096
552.9 | 49.5 | 1.0096
553 | 49.5 | 1.0096
553.1 | 49.5 | 1.0096
553.2 | 49.5 | 1.0096
553.3 | 49.5 | 1.0096
553.4 | 49.5 | 1.0096
553.5 | 49.5 | 1.0096
553.6 | 49.5 | 1.0096
553.7 | 49.5 | 1.0096
553.8 | 49.5 | 1.0096
553.9 | 49.5 | 1.0096
554 | 49.5 | 1.0096
554.1 | 49.5 | 1.0096
554.2 | 49.5 | 1.0096
554.3 | 49.5 | 1.0096
554.4 | 49.5 | 1.0096
554.5 | 49.5 | 1.0096
554.6 | 49.5 | 1.0096
554.7 | 49.5 | 1.0096
554.8 | 49.5 | 1.0096
554.9 | 49.5 | 1.0096
555 | 49.5 | 1.0094
555.1 | 49.5 | 1.0094
555.2 | 49.5 | 1.0094
555.3 | 49.5 | 1.0094
555.4 | 49.5 | 1.0094
555.5 | 49.5 | 1.0094
555.6 | 49.5 | 1.0094
555.7 | 49.5 | 1.0094
555.8 | 49.5 | 1.0094
555.9 | 49.5 | 1.0094
556 | 49.5 | 1.0094
556.1 | 49.5 | 1.0096
556.2 | 49.5 | 1.0096
556.3 | 49.5 | 1.0096
556.4 | 49.5 | 1.0096
556.5 | 49.5 | 1.0096
556.6 | 49.5 | 1.0096
556.7 | 49.5 | 1.0096
556.8 | 49.5 | 1.0096
556.9 | 49.5 | 1.0096
557 | 49.5 | 1.0096
557.1 | 49.5 | 1.0096
557.2 | 49.5 | 1.0096
557.3 | 49.5 | 1.0096
557.4 | 49.5 | 1.0096
557.5 | 49.5 | 1.0096
557.6 | 49.5 | 1.0096
557.7 | 49.5 | 1.0096
557.8 | 49.5 | 1.0096
557.9 | 49.5 | 1.0096
558 | 49.5 | 1.0096
558.1 | 49.5 | 1.0096
558.2 | 49.5 | 1.0096
558.3 | 49.5 | 1.0096
558.4 | 49.5 | 1.0096
558.5 | 49.5 | 1.0096
558.6 | 49.5 | 1.0096
558.7 | 49.5 | 1.0096
558.8 | 49.5 | 1.0096
558.9 | 49.5 | 1.0096
559 | 49.5 | 1.0096
559.1 | 49.5 | 1.0096
559.2 | 49.5 | 1.0096
559.3 | 49.5 | 1.0096
559.4 | 49.5 | 1.0096
559.5 | 49.5 | 1.0096
559.6 | 49.5 | 1.0096
559.7 | 49.5 | 1.0096
559.8 | 49.5 | 1.0098
559.9 | 49.5 | 1.0098
560 | 49.5 | 1.0098
560.1 | 49.5 | 1.0098
560.2 | 49.5 | 1.0098
560.3 | 49.5 | 1.0098
560.4 | 49.5 | 1.0098
560.5 | 49.5 | 1.0098
560.6 | 49.5 | 1.0098
560.7 | 49.5 | 1.0098
560.8 | 49.5 | 1.0096
560.9 | 49.5 | 1.0096
561 | 49.5 | 1.0096
561.1 | 49.5 | 1.0096
561.2 | 49.5 | 1.0096
561.3 | 49.5 | 1.0096
561.4 | 49.5 | 1.0096
561.5 | 49.5 | 1.0096
561.6 | 49.5 | 1.0096
561.7 | 49.5 | 1.0096
561.8 | 49.5 | 1.0096
561.9 | 49.5 | 1.0096
562 | 49.5 | 1.0094
562.1 | 49.5 | 1.0094
562.2 | 49.5 | 1.0094
562.3 | 49.5 | 1.0094
562.4 | 49.5 | 1.0094
562.5 | 49.5 | 1.0094
562.6 | 49.5 | 1.0094
562.7 | 49.5 | 1.0094
562.8 | 49.5 | 1.0094
562.9 | 49.5 | 1.0094
563 | 49.5 | 1.0094
563.1 | 49.5 | 1.0094
563.2 | 49.5 | 1.0094
563.3 | 49.5 | 1.0094
563.4 | 49.5 | 1.0094
563.5 | 49.5 | 1.0094
563.6 | 49.5 | 1.0094
563.7 | 49.5 | 1.0094
563.8 | 49.5 | 1.0094
563.9 | 49.5 | 1.0094
564 | 49.5 | 1.0094
564.1 | 49.5 | 1.0094
564.2 | 49.5 | 1.0096
564.3 | 49.5 | 1.0096
564.4 | 49.5 | 1.0096
564.5 | 49.5 | 1.0096
564.6 | 49.5 | 1.0096
564.7 | 49.5 | 1.0096
564.8 | 49.5 | 1.0096
564.9 | 49.5 | 1.0096
565 | 49.5 | 1.0096
565.1 | 49.5 | 1.0096
565.2 | 49.5 | 1.0096
565.3 | 49.5 | 1.0096
565.4 | 49.5 | 1.0096
565.5 | 49.5 | 1.0096
565.6 | 49.5 | 1.0096
565.7 | 49.5 | 1.0096
565.8 | 49.5 | 1.0096
565.9 | 49.5 | 1.0096
566 | 49.5 | 1.0096
566.1 | 49.5 | 1.0096
566.2 | 49.5 | 1.0096
566.3 | 49.5 | 1.0096
566.4 | 49.5 | 1.0096
566.5 | 49.5 | 1.0096
566.6 | 49.5 | 1.0098
566.7 | 49.5 | 1.0098
566.8 | 49.5 | 1.0098
566.9 | 49.5 | 1.0098
567 | 49.5 | 1.0098
567.1 | 49.5 | 1.0098
567.2 | 49.5 | 1.0098
567.3 | 49.5 | 1.0098
567.4 | 49.5 | 1.0098
567.5 | 49.5 | 1.0098
567.6 | 49.5 | 1.0098
567.7 | 49.5 | 1.0098
567.8 | 49.5 | 1.0096
567.9 | 49.5 | 1.0096
568 | 49.5 | 1.0096
568.1 | 49.5 | 1.0096
568.2 | 49.5 | 1.0096
568.3 | 49.5 | 1.0096
568.4 | 49.5 | 1.0096
568.5 | 49.5 | 1.0096
568.6 | 49.5 | 1.0096
568.7 | 49.5 | 1.0096
568.8 | 49.5 | 1.0096
568.9 | 49.5 | 1.0096
569 | 49.5 | 1.0096
569.1 | 49.5 | 1.0096
569.2 | 49.5 | 1.0096
569.3 | 49.5 | 1.0096
569.4 | 49.5 | 1.0096
569.5 | 49.5 | 1.0096
569.6 | 49.5 | 1.0096
569.7 | 49.5 | 1.0096
569.8 | 49.5 | 1.0096
569.9 | 49.5 | 1.0096
570 | 49.5 | 1.0096
570.1 | 49.5 | 1.0096
570.2 | 49.5 | 1.0096
570.3 | 49.5 | 1.0096
570.4 | 49.5 | 1.0096
570.5 | 49.5 | 1.0096
570.6 | 49.5 | 1.0096
570.7 | 49.5 | 1.0096
570.8 | 49.5 | 1.0096
570.9 | 49.5 | 1.0096
571 | 49.5 | 1.0096
571.1 | 49.5 | 1.0096
571.2 | 49.5 | 1.0096
571.3 | 49.5 | 1.0096
571.4 | 49.5 | 1.0096
571.5 | 49.5 | 1.0096
571.6 | 49.5 | 1.0096
571.7 | 49.5 | 1.0096
571.8 | 49.5 | 1.0096
571.9 | 49.5 | 1.0096
572 | 49.5 | 1.0096
572.1 | 49.5 | 1.0096
572.2 | 49.5 | 1.0096
572.3 | 49.5 | 1.0096
572.4 | 49.5 | 1.0098
572.5 | 49.5 | 1.0098
572.6 | 49.5 | 1.0098
572.7 | 49.5 | 1.0098
572.8 | 49.5 | 1.0098
572.9 | 49.5 | 1.0098
573 | 49.5 | 1.0098
573.1 | 49.5 | 1.0098
573.2 | 49.5 | 1.0098
573.3 | 49.5 | 1.0098
573.4 | 49.5 | 1.0098
573.5 | 49.5 | 1.0098
573.6 | 49.5 | 1.0098
573.7 | 49.5 | 1.0096
573.8 | 49.5 | 1.0096
573.9 | 49.5 | 1.0096
574 | 49.5 | 1.0096
574.1 | 49.5 | 1.0096
574.2 | 49.5 | 1.0096
574.3 | 49.5 | 1.0096
574.4 | 49.5 | 1.0096
574.5 | 49.5 | 1.0096
574.6 | 49.5 | 1.0096
574.7 | 49.5 | 1.0096
574.8 | 49.5 | 1.0096
574.9 | 49.5 | 1.0096
575 | 49.5 | 1.0096
575.1 | 49.5 | 1.0096
575.2 | 49.5 | 1.0096
575.3 | 49.5 | 1.0096
575.4 | 49.5 | 1.0096
575.5 | 49.5 | 1.0096
575.6 | 49.5 | 1.0096
575.7 | 49.5 | 1.0096
575.8 | 49.5 | 1.0096
575.9 | 49.5 | 1.0096
576 | 49.5 | 1.0096
576.1 | 49.5 | 1.0096
576.2 | 49.5 | 1.0096
576.3 | 49.5 | 1.0096
576.4 | 49.5 | 1.0096
576.5 | 49.5 | 1.0096
576.6 | 49.5 | 1.0096
576.7 | 49.5 | 1.0096
576.8 | 49.5 | 1.0096
576.9 | 49.5 | 1.0096
577 | 49.5 | 1.0096
577.1 | 49.5 | 1.0096
577.2 | 49.5 | 1.0096
577.3 | 49.5 | 1.0096
577.4 | 49.5 | 1.0096
577.5 | 49.5 | 1.0096
577.6 | 49.5 | 1.0096
577.7 | 49.5 | 1.0096
577.8 | 49.5 | 1.0096
577.9 | 49.5 | 1.0096
578 | 49.5 | 1.0096
578.1 | 49.5 | 1.0096
578.2 | 49.5 | 1.0098
578.3 | 49.5 | 1.0098
578.4 | 49.5 | 1.0098
578.5 | 49.5 | 1.0098
578.6 | 49.5 | 1.0098
578.7 | 49.5 | 1.0098
578.8 | 49.5 | 1.0098
578.9 | 49.5 | 1.0098
579 | 49.5 | 1.0098
579.1 | 49.5 | 1.0098
579.2 | 49.5 | 1.0098
579.3 | 49.5 | 1.0098
579.4 | 49.5 | 1.0098
579.5 | 49.5 | 1.0098
579.6 | 49.5 | 1.0098
579.7 | 49.5 | 1.0098
579.8 | 49.5 | 1.0098
579.9 | 49.5 | 1.0098
580 | 49.5 | 1.0098
580.1 | 49.5 | 1.0098
580.2 | 49.5 | 1.0098
580.3 | 49.5 | 1.0098
580.4 | 49.5 | 1.0098
580.5 | 49.5 | 1.0098
580.6 | 49.5 | 1.0096
580.7 | 49.5 | 1.0096
580.8 | 49.5 | 1.0096
580.9 | 49.5 | 1.0096
581 | 49.5 | 1.0096
581.1 | 49.5 | 1.0096
581.2 | 49.5 | 1.0096
581.3 | 49.5 | 1.0096
581.4 | 49.5 | 1.0096
581.5 | 49.5 | 1.0096
581.6 | 49.5 | 1.0096
581.7 | 49.5 | 1.0096
581.8 | 49.5 | 1.0096
581.9 | 49.5 | 1.0096
582 | 49.5 | 1.0096
582.1 | 49.5 | 1.0096
582.2 | 49.5 | 1.0096
582.3 | 49.5 | 1.0096
582.4 | 49.5 | 1.0096
582.5 | 49.5 | 1.0096
582.6 | 49.5 | 1.0096
582.7 | 49.5 | 1.0096
582.8 | 49.5 | 1.0096
582.9 | 49.5 | 1.0096
583 | 49.5 | 1.0096
583.1 | 49.5 | 1.0096
583.2 | 49.5 | 1.0096
583.3 | 49.5 | 1.0096
583.4 | 49.5 | 1.0096
583.5 | 49.5 | 1.0096
583.6 | 49.5 | 1.0096
583.7 | 49.5 | 1.0096
583.8 | 49.5 | 1.0096
583.9 | 49.5 | 1.0096
584 | 49.5 | 1.0096
584.1 | 49.5 | 1.0096
584.2 | 49.5 | 1.0096
584.3 | 49.5 | 1.0096
584.4 | 49.5 | 1.0096
584.5 | 49.5 | 1.0096
584.6 | 49.5 | 1.0096
584.7 | 49.5 | 1.0096
584.8 | 49.5 | 1.0096
584.9 | 49.5 | 1.0096
585 | 49.5 | 1.0096
585.1 | 49.5 | 1.0096
585.2 | 49.5 | 1.0096
585.3 | 49.5 | 1.0096
585.4 | 49.5 | 1.0096
585.5 | 49.5 | 1.0096
585.6 | 49.5 | 1.0096
585.7 | 49.5 | 1.0096
585.8 | 49.5 | 1.0096
585.9 | 49.5 | 1.0096
586 | 49.5 | 1.0096
586.1 | 49.5 | 1.0096
586.2 | 49.5 | 1.0096
586.3 | 49.5 | 1.0096
586.4 | 49.5 | 1.0096
586.5 | 49.5 | 1.0096
586.6 | 49.5 | 1.0096
586.7 | 49.5 | 1.0096
586.8 | 49.5 | 1.0096
586.9 | 49.5 | 1.0096
587 | 49.5 | 1.0096
587.1 | 49.5 | 1.0096
587.2 | 49.5 | 1.0096
587.3 | 49.5 | 1.0096
587.4 | 49.5 | 1.0096
587.5 | 49.5 | 1.0096
587.6 | 49.5 | 1.0096
587.7 | 49.5 | 1.0096
587.8 | 49.5 | 1.0096
587.9 | 49.5 | 1.0096
588 | 49.5 | 1.0096
588.1 | 49.5 | 1.0096
588.2 | 49.5 | 1.0096
588.3 | 49.5 | 1.0096
588.4 | 49.5 | 1.0096
588.5 | 49.5 | 1.0096
588.6 | 49.5 | 1.0096
588.7 | 49.5 | 1.0096
588.8 | 49.5 | 1.0096
588.9 | 49.5 | 1.0096
589 | 49.5 | 1.0096
589.1 | 49.5 | 1.0096
589.2 | 49.5 | 1.0096
589.3 | 49.5 | 1.0096
589.4 | 49.5 | 1.0096
589.5 | 49.5 | 1.0096
589.6 | 49.5 | 1.0096
589.7 | 49.5 | 1.0096
589.8 | 49.5 | 1.0096
589.9 | 49.5 | 1.0096
590 | 49.5 | 1.0096
590.1 | 49.5 | 1.0096
590.2 | 49.5 | 1.0096
590.3 | 49.5 | 1.0096
590.4 | 49.5 | 1.0096
590.5 | 49.5 | 1.0096
590.6 | 49.5 | 1.0096
590.7 | 49.5 | 1.0096
590.8 | 49.5 | 1.0096
590.9 | 49.5 | 1.0096
591 | 49.5 | 1.0096
591.1 | 49.5 | 1.0096
591.2 | 49.5 | 1.0096
591.3 | 49.5 | 1.0096
591.4 | 49.5 | 1.0096
591.5 | 49.5 | 1.0096
591.6 | 49.5 | 1.0096
591.7 | 49.5 | 1.0096
591.8 | 49.5 | 1.0096
591.9 | 49.5 | 1.0096
592 | 49.5 | 1.0096
592.1 | 49.5 | 1.0096
592.2 | 49.5 | 1.0096
592.3 | 49.5 | 1.0096
592.4 | 49.5 | 1.0096
592.5 | 49.5 | 1.0096
592.6 | 49.5 | 1.0096
592.7 | 49.5 | 1.0096
592.8 | 49.5 | 1.0096
592.9 | 49.5 | 1.0096
593 | 49.5 | 1.0096
593.1 | 49.5 | 1.0096
593.2 | 49.5 | 1.0096
593.3 | 49.5 | 1.0096
593.4 | 49.5 | 1.0096
593.5 | 49.5 | 1.0096
593.6 | 49.5 | 1.0096
593.7 | 49.5 | 1.0096
593.8 | 49.5 | 1.0096
593.9 | 49.5 | 1.0096
594 | 49.5 | 1.0096
594.1 | 49.5 | 1.0096
594.2 | 49.5 | 1.0096
594.3 | 49.5 | 1.0096
594.4 | 49.5 | 1.0096
594.5 | 49.5 | 1.0096
594.6 | 49.5 | 1.0096
594.7 | 49.5 | 1.0096
594.8 | 49.5 | 1.0096
594.9 | 49.5 | 1.0096
595 | 49.5 | 1.0096
595.1 | 49.5 | 1.0096
595.2 | 49.5 | 1.0096
595.3 | 49.5 | 1.0096
595.4 | 49.5 | 1.0096
595.5 | 49.5 | 1.0096
595.6 | 49.5 | 1.0096
595.7 | 49.5 | 1.0096
595.8 | 49.5 | 1.0096
595.9 | 49.5 | 1.0096
596 | 49.5 | 1.0096
596.1 | 49.5 | 1.0096
596.2 | 49.5 | 1.0096
596.3 | 49.5 | 1.0096
596.4 | 49.5 | 1.0096
596.5 | 49.5 | 1.0096
596.6 | 49.5 | 1.0096
596.7 | 49.5 | 1.0096
596.8 | 49.5 | 1.0096
596.9 | 49.5 | 1.0096
597 | 49.5 | 1.0096
597.1 | 49.5 | 1.0096
597.2 | 49.5 | 1.0096
597.3 | 49.5 | 1.0096
597.4 | 49.5 | 1.0096
597.5 | 49.5 | 1.0096
597.6 | 49.5 | 1.0096
597.7 | 49.5 | 1.0096
597.8 | 49.5 | 1.0096
597.9 | 49.5 | 1.0096
598 | 49.5 | 1.0096
598.1 | 49.5 | 1.0096
598.2 | 49.5 | 1.0096
598.3 | 49.5 | 1.0096
598.4 | 49.5 | 1.0096
598.5 | 49.5 | 1.0096
598.6 | 49.5 | 1.0096
598.7 | 49.5 | 1.0096
598.8 | 49.5 | 1.0096
598.9 | 49.5 | 1.0096
599 | 49.5 | 1.0096
599.1 | 49.5 | 1.0096
599.2 | 49.5 | 1.0096
599.3 | 49.5 | 1.0096
599.4 | 49.5 | 1.0096
599.5 | 49.5 | 1.0096
599.6 | 49.5 | 1.0096
599.7 | 49.5 | 1.0096
599.8 | 49.5 | 1.0096
599.9 | 49.5 | 1.0096
600 | 49.5 | 1.0096
600.1 | 49.5 | 1.0096
600.2 | 49.5 | 1.0096
600.3 | 49.5 | 1.0096
600.4 | 49.5 | 1.0096
600.5 | 49.5 | 1.0096
600.6 | 49.5 | 1.0096
600.7 | 49.5 | 1.0096
600.8 | 49.5 | 1.0096
600.9 | 49.5 | 1.0096
601 | 49.5 | 1.0096
601.1 | 49.5 | 1.0096
601.2 | 49.5 | 1.0096
601.3 | 49.5 | 1.0096
601.4 | 49.5 | 1.0096
601.5 | 49.5 | 1.0096
601.6 | 49.5 | 1.0096
601.7 | 49.5 | 1.0096
601.8 | 49.5 | 1.0096
601.9 | 49.5 | 1.0096
602 | 49.5 | 1.0096
602.1 | 49.5 | 1.0096
602.2 | 49.5 | 1.0096
602.3 | 49.5 | 1.0096
602.4 | 49.5 | 1.0096
602.5 | 49.5 | 1.0096
602.6 | 49.5 | 1.0096
602.7 | 49.5 | 1.0096
602.8 | 49.5 | 1.0096
602.9 | 49.5 | 1.0096
603 | 49.5 | 1.0096
603.1 | 49.5 | 1.0096
603.2 | 49.5 | 1.0096
603.3 | 49.5 | 1.0096
603.4 | 49.5 | 1.0096
603.5 | 49.5 | 1.0096
603.6 | 49.5 | 1.0096
603.7 | 49.5 | 1.0096
603.8 | 49.5 | 1.0096
603.9 | 49.5 | 1.0096
604 | 49.5 | 1.0096
604.1 | 49.5 | 1.0096
604.2 | 49.5 | 1.0096
604.3 | 49.5 | 1.0096
604.4 | 49.5 | 1.0096
604.5 | 49.5 | 1.0096
604.6 | 49.5 | 1.0096
604.7 | 49.5 | 1.0096
604.8 | 49.5 | 1.0096
604.9 | 49.5 | 1.0096
605 | 49.5 | 1.0096
605.1 | 49.5 | 1.0098
605.2 | 49.5 | 1.0098
605.3 | 49.5 | 1.0098
605.4 | 49.5 | 1.0098
605.5 | 49.5 | 1.0098
605.6 | 49.5 | 1.0098
605.7 | 49.5 | 1.0098
605.8 | 49.5 | 1.0098
605.9 | 49.5 | 1.0098
606 | 49.5 | 1.0098
606.1 | 49.5 | 1.0096
606.2 | 49.5 | 1.0096
606.3 | 49.5 | 1.0096
606.4 | 49.5 | 1.0096
606.5 | 49.5 | 1.0096
606.6 | 49.5 | 1.0096
606.7 | 49.5 | 1.0096
606.8 | 49.5 | 1.0096
606.9 | 49.5 | 1.0096
607 | 49.5 | 1.0096
607.1 | 49.5 | 1.0096
607.2 | 49.5 | 1.0096
607.3 | 49.5 | 1.0096
607.4 | 49.5 | 1.0096
607.5 | 49.5 | 1.0096
607.6 | 49.5 | 1.0096
607.7 | 49.5 | 1.0096
607.8 | 49.5 | 1.0096
607.9 | 49.5 | 1.0096
608 | 49.5 | 1.0096
608.1 | 49.5 | 1.0096
608.2 | 49.5 | 1.0096
608.3 | 49.5 | 1.0096
608.4 | 49.5 | 1.0096
608.5 | 49.5 | 1.0096
608.6 | 49.5 | 1.0096
608.7 | 49.5 | 1.0096
608.8 | 49.5 | 1.0096
608.9 | 49.5 | 1.0096
609 | 49.5 | 1.0096
609.1 | 49.5 | 1.0096
609.2 | 49.5 | 1.0096
609.3 | 49.5 | 1.0096
609.4 | 49.5 | 1.0096
609.5 | 49.5 | 1.0096
609.6 | 49.5 | 1.0096
609.7 | 49.5 | 1.0096
609.8 | 49.5 | 1.0096
609.9 | 49.5 | 1.0096
610 | 49.5 | 1.0096
610.1 | 49.5 | 1.0096
610.2 | 49.5 | 1.0096
610.3 | 49.5 | 1.0096
610.4 | 49.5 | 1.0096
610.5 | 49.5 | 1.0096
610.6 | 49.5 | 1.0096
610.7 | 49.5 | 1.0096
610.8 | 49.5 | 1.0096
610.9 | 49.5 | 1.0096
611 | 49.5 | 1.0096
611.1 | 49.5 | 1.0096
611.2 | 49.5 | 1.0096
611.3 | 49.5 | 1.0096
611.4 | 49.5 | 1.0096
611.5 | 49.5 | 1.0096
611.6 | 49.5 | 1.0096
611.7 | 49.5 | 1.0096
611.8 | 49.5 | 1.0096
611.9 | 49.5 | 1.0096
612 | 49.5 | 1.0096
612.1 | 49.5 | 1.0096
612.2 | 49.5 | 1.0096
612.3 | 49.5 | 1.0096
612.4 | 49.5 | 1.0096
612.5 | 49.5 | 1.0096
612.6 | 49.5 | 1.0096
612.7 | 49.5 | 1.0096
612.8 | 49.5 | 1.0096
612.9 | 49.5 | 1.0096
613 | 49.5 | 1.0096
613.1 | 49.5 | 1.0096
613.2 | 49.5 | 1.0096
613.3 | 49.5 | 1.0096
613.4 | 49.5 | 1.0096
613.5 | 49.5 | 1.0096
613.6 | 49.5 | 1.0096
613.7 | 49.5 | 1.0096
613.8 | 49.5 | 1.0096
613.9 | 49.5 | 1.0096
614 | 49.5 | 1.0096
614.1 | 49.5 | 1.0096
614.2 | 49.5 | 1.0096
614.3 | 49.5 | 1.0096
614.4 | 49.5 | 1.0096
614.5 | 49.5 | 1.0096
614.6 | 49.5 | 1.0096
614.7 | 49.5 | 1.0096
614.8 | 49.5 | 1.0096
614.9 | 49.5 | 1.0096
615 | 49.5 | 1.0096
615.1 | 49.5 | 1.0096
615.2 | 49.5 | 1.0096
615.3 | 49.5 | 1.0096
615.4 | 49.5 | 1.0096
615.5 | 49.5 | 1.0096
615.6 | 49.5 | 1.0096
615.7 | 49.5 | 1.0096
615.8 | 49.5 | 1.0096
615.9 | 49.5 | 1.0096
616 | 49.5 | 1.0096
616.1 | 49.5 | 1.0096
616.2 | 49.5 | 1.0096
616.3 | 49.5 | 1.0096
616.4 | 49.5 | 1.0096
616.5 | 49.5 | 1.0096
616.6 | 49.5 | 1.0096
616.7 | 49.5 | 1.0096
616.8 | 49.5 | 1.0096
616.9 | 49.5 | 1.0096
617 | 49.5 | 1.0096
617.1 | 49.5 | 1.0096
617.2 | 49.5 | 1.0096
617.3 | 49.5 | 1.0096
617.4 | 49.5 | 1.0096
617.5 | 49.5 | 1.0096
617.6 | 49.5 | 1.0096
617.7 | 49.5 | 1.0096
617.8 | 49.5 | 1.0096
617.9 | 49.5 | 1.0096
618 | 49.5 | 1.0096
618.1 | 49.5 | 1.0096
618.2 | 49.5 | 1.0096
618.3 | 49.5 | 1.0096
618.4 | 49.5 | 1.0096
618.5 | 49.5 | 1.0096
618.6 | 49.5 | 1.0096
618.7 | 49.5 | 1.0096
618.8 | 49.5 | 1.0096
618.9 | 49.5 | 1.0096
619 | 49.5 | 1.0096
619.1 | 49.5 | 1.0096
619.2 | 49.5 | 1.0096
619.3 | 49.5 | 1.0096
619.4 | 49.5 | 1.0096
619.5 | 49.5 | 1.0096
619.6 | 49.5 | 1.0096
619.7 | 49.5 | 1.0096
619.8 | 49.5 | 1.0096
619.9 | 49.5 | 1.0096
620 | 49.5 | 1.0096
620.1 | 49.5 | 1.0096
620.2 | 49.5 | 1.0096
620.3 | 49.5 | 1.0096
620.4 | 49.5 | 1.0096
620.5 | 49.5 | 1.0096
620.6 | 49.5 | 1.0096
620.7 | 49.5 | 1.0096
620.8 | 49.5 | 1.0096
620.9 | 49.5 | 1.0096
621 | 49.5 | 1.0096
621.1 | 49.5 | 1.0096
621.2 | 49.5 | 1.0096
621.3 | 49.5 | 1.0096
621.4 | 49.5 | 1.0096
621.5 | 49.5 | 1.0096
621.6 | 49.5 | 1.0096
621.7 | 49.5 | 1.0096
621.8 | 49.5 | 1.0096
621.9 | 49.5 | 1.0096
622 | 49.5 | 1.0096
622.1 | 49.5 | 1.0096
622.2 | 49.5 | 1.0096
622.3 | 49.5 | 1.0096
622.4 | 49.5 | 1.0096
622.5 | 49.5 | 1.0096
622.6 | 49.5 | 1.0096
622.7 | 49.5 | 1.0096
622.8 | 49.5 | 1.0096
622.9 | 49.5 | 1.0096
623 | 49.5 | 1.0096
623.1 | 49.5 | 1.0096
623.2 | 49.5 | 1.0096
623.3 | 49.5 | 1.0096
623.4 | 49.5 | 1.0096
623.5 | 49.5 | 1.0096
623.6 | 49.5 | 1.0096
623.7 | 49.5 | 1.0096
623.8 | 49.5 | 1.0096
623.9 | 49.5 | 1.0096
624 | 49.5 | 1.0096
624.1 | 49.5 | 1.0096
624.2 | 49.5 | 1.0096
624.3 | 49.5 | 1.0096
624.4 | 49.5 | 1.0096
624.5 | 49.5 | 1.0096
624.6 | 49.5 | 1.0096
624.7 | 49.5 | 1.0096
624.8 | 49.5 | 1.0096
624.9 | 49.5 | 1.0096
625 | 49.5 | 1.0096
625.1 | 49.5 | 1.0096
625.2 | 49.5 | 1.0096
625.3 | 49.5 | 1.0096
625.4 | 49.5 | 1.0096
625.5 | 49.5 | 1.0096
625.6 | 49.5 | 1.0096
625.7 | 49.5 | 1.0096
625.8 | 49.5 | 1.0096
625.9 | 49.5 | 1.0096
626 | 49.5 | 1.0096
626.1 | 49.5 | 1.0096
626.2 | 49.5 | 1.0096
626.3 | 49.5 | 1.0096
626.4 | 49.5 | 1.0096
626.5 | 49.5 | 1.0096
626.6 | 49.5 | 1.0096
626.7 | 49.5 | 1.0096
626.8 | 49.5 | 1.0096
626.9 | 49.5 | 1.0096
627 | 49.5 | 1.0096
627.1 | 49.5 | 1.0096
627.2 | 49.5 | 1.0096
627.3 | 49.5 | 1.0096
627.4 | 49.5 | 1.0096
627.5 | 49.5 | 1.0096
627.6 | 49.5 | 1.0096
627.7 | 49.5 | 1.0096
627.8 | 49.5 | 1.0096
627.9 | 49.5 | 1.0096
628 | 49.5 | 1.0096
628.1 | 49.5 | 1.0096
628.2 | 49.5 | 1.0096
628.3 | 49.5 | 1.0098
628.4 | 49.5 | 1.0098
628.5 | 49.5 | 1.0098
628.6 | 49.5 | 1.0098
628.7 | 49.5 | 1.0098
628.8 | 49.5 | 1.0098
628.9 | 49.5 | 1.0098
629 | 49.5 | 1.0098
629.1 | 49.5 | 1.0098
629.2 | 49.5 | 1.0098
629.3 | 49.5 | 1.0098
629.4 | 49.5 | 1.0098
629.5 | 49.5 | 1.0098
629.6 | 49.5 | 1.0098
629.7 | 49.5 | 1.0098
629.8 | 49.5 | 1.0098
629.9 | 49.5 | 1.0098
630 | 49.5 | 1.0098
630.1 | 49.5 | 1.0098
630.2 | 49.5 | 1.0098
630.3 | 49.5 | 1.0098
630.4 | 49.5 | 1.0098
630.5 | 49.5 | 1.0098
630.6 | 49.5 | 1.0096
630.7 | 49.5 | 1.0096
630.8 | 49.5 | 1.0096
630.9 | 49.5 | 1.0096
631 | 49.5 | 1.0096
631.1 | 49.5 | 1.0096
631.2 | 49.5 | 1.0096
631.3 | 49.5 | 1.0096
631.4 | 49.5 | 1.0096
631.5 | 49.5 | 1.0096
631.6 | 49.5 | 1.0096
631.7 | 49.5 | 1.0096
631.8 | 49.5 | 1.0096
631.9 | 49.5 | 1.0096
632 | 49.5 | 1.0096
632.1 | 49.5 | 1.0096
632.2 | 49.5 | 1.0096
632.3 | 49.5 | 1.0096
632.4 | 49.5 | 1.0096
632.5 | 49.5 | 1.0096
632.6 | 49.5 | 1.0096
632.7 | 49.5 | 1.0096
632.8 | 49.5 | 1.0096
632.9 | 49.5 | 1.0096
633 | 49.5 | 1.0096
633.1 | 49.5 | 1.0096
633.2 | 49.5 | 1.0096
633.3 | 49.5 | 1.0096
633.4 | 49.5 | 1.0096
633.5 | 49.5 | 1.0096
633.6 | 49.5 | 1.0096
633.7 | 49.5 | 1.0096
633.8 | 49.5 | 1.0096
633.9 | 49.5 | 1.0096
634 | 49.5 | 1.0096
634.1 | 49.5 | 1.0096
634.2 | 49.5 | 1.0096
634.3 | 49.5 | 1.0096
634.4 | 49.5 | 1.0096
634.5 | 49.5 | 1.0096
634.6 | 49.5 | 1.0096
634.7 | 49.5 | 1.0096
634.8 | 49.5 | 1.0096
634.9 | 49.5 | 1.0096
635 | 49.5 | 1.0096
635.1 | 49.5 | 1.0096
635.2 | 49.5 | 1.0096
635.3 | 49.5 | 1.0096
635.4 | 49.5 | 1.0096
635.5 | 49.5 | 1.0096
635.6 | 49.5 | 1.0096
635.7 | 49.5 | 1.0096
635.8 | 49.5 | 1.0096
635.9 | 49.5 | 1.0096
636 | 49.5 | 1.0096
636.1 | 49.5 | 1.0096
636.2 | 49.5 | 1.0096
636.3 | 49.5 | 1.0096
636.4 | 49.5 | 1.0096
636.5 | 49.5 | 1.0096
636.6 | 49.5 | 1.0096
636.7 | 49.5 | 1.0096
636.8 | 49.5 | 1.0096
636.9 | 49.5 | 1.0096
637 | 49.5 | 1.0096
637.1 | 49.5 | 1.0096
637.2 | 49.5 | 1.0096
637.3 | 49.5 | 1.0096
637.4 | 49.5 | 1.0096
637.5 | 49.5 | 1.0096
637.6 | 49.5 | 1.0096
637.7 | 49.5 | 1.0096
637.8 | 49.5 | 1.0096
637.9 | 49.5 | 1.0096
638 | 49.5 | 1.0096
638.1 | 49.5 | 1.0096
638.2 | 49.5 | 1.0096
638.3 | 49.5 | 1.0096
638.4 | 49.5 | 1.0096
638.5 | 49.5 | 1.0096
638.6 | 49.5 | 1.0096
638.7 | 49.5 | 1.0096
638.8 | 49.5 | 1.0096
638.9 | 49.5 | 1.0096
639 | 49.5 | 1.0096
639.1 | 49.5 | 1.0096
639.2 | 49.5 | 1.0096
639.3 | 49.5 | 1.0096
639.4 | 49.5 | 1.0096
639.5 | 49.5 | 1.0096
639.6 | 49.5 | 1.0096
639.7 | 49.5 | 1.0096
639.8 | 49.5 | 1.0096
639.9 | 49.5 | 1.0098
640 | 49.5 | 1.0098
640.1 | 49.5 | 1.0098
640.2 | 49.5 | 1.0098
640.3 | 49.5 | 1.0098
640.4 | 49.5 | 1.0098
640.5 | 49.5 | 1.0098
640.6 | 49.5 | 1.0098
640.7 | 49.5 | 1.0098
640.8 | 49.5 | 1.0098
640.9 | 49.5 | 1.0098
641 | 49.5 | 1.0098
641.1 | 49.5 | 1.0098
641.2 | 49.5 | 1.0098
641.3 | 49.5 | 1.0098
641.4 | 49.5 | 1.0098
641.5 | 49.5 | 1.0098
641.6 | 49.5 | 1.0098
641.7 | 49.5 | 1.0098
641.8 | 49.5 | 1.0098
641.9 | 49.5 | 1.0098
642 | 49.5 | 1.0098
642.1 | 49.5 | 1.0098
642.2 | 49.5 | 1.0098
642.3 | 49.5 | 1.0096
642.4 | 49.5 | 1.0096
642.5 | 49.5 | 1.0096
642.6 | 49.5 | 1.0096
642.7 | 49.5 | 1.0096
642.8 | 49.5 | 1.0096
642.9 | 49.5 | 1.0096
643 | 49.5 | 1.0096
643.1 | 49.5 | 1.0096
643.2 | 49.5 | 1.0096
643.3 | 49.5 | 1.0096
643.4 | 49.5 | 1.0096
643.5 | 49.5 | 1.0096
643.6 | 49.5 | 1.0096
643.7 | 49.5 | 1.0096
643.8 | 49.5 | 1.0096
643.9 | 49.5 | 1.0096
644 | 49.5 | 1.0096
644.1 | 49.5 | 1.0096
644.2 | 49.5 | 1.0096
644.3 | 49.5 | 1.0096
644.4 | 49.5 | 1.0096
644.5 | 49.5 | 1.0096
644.6 | 49.5 | 1.0096
644.7 | 49.5 | 1.0096
644.8 | 49.5 | 1.0096
644.9 | 49.5 | 1.0096
645 | 49.5 | 1.0096
645.1 | 49.5 | 1.0096
645.2 | 49.5 | 1.0096
645.3 | 49.5 | 1.0096
645.4 | 49.5 | 1.0096
645.5 | 49.5 | 1.0096
645.6 | 49.5 | 1.0096
645.7 | 49.5 | 1.0096
645.8 | 49.5 | 1.0096
645.9 | 49.5 | 1.0096
646 | 49.5 | 1.0096
646.1 | 49.5 | 1.0096
646.2 | 49.5 | 1.0096
646.3 | 49.5 | 1.0096
646.4 | 49.5 | 1.0096
646.5 | 49.5 | 1.0096
646.6 | 49.5 | 1.0096
646.7 | 49.5 | 1.0096
646.8 | 49.5 | 1.0096
646.9 | 49.5 | 1.0096
647 | 49.5 | 1.0096
647.1 | 49.5 | 1.0096
647.2 | 49.5 | 1.0096
647.3 | 49.5 | 1.0096
647.4 | 49.5 | 1.0096
647.5 | 49.5 | 1.0096
647.6 | 49.5 | 1.0096
647.7 | 49.5 | 1.0096
647.8 | 49.5 | 1.0096
647.9 | 49.5 | 1.0096
648 | 49.5 | 1.0096
648.1 | 49.5 | 1.0096
648.2 | 49.5 | 1.0096
648.3 | 49.5 | 1.0096
648.4 | 49.5 | 1.0096
648.5 | 49.5 | 1.0096
648.6 | 49.5 | 1.0096
648.7 | 49.5 | 1.0096
648.8 | 49.5 | 1.0096
648.9 | 49.5 | 1.0096
649 | 49.5 | 1.0096
649.1 | 49.5 | 1.0096
649.2 | 49.5 | 1.0096
649.3 | 49.5 | 1.0096
649.4 | 49.5 | 1.0098
649.5 | 49.5 | 1.0098
649.6 | 49.5 | 1.0098
649.7 | 49.5 | 1.0098
649.8 | 49.5 | 1.0098
649.9 | 49.5 | 1.0098
650 | 49.5 | 1.0098
650.1 | 49.5 | 1.0098
650.2 | 49.5 | 1.0098
650.3 | 49.5 | 1.0098
650.4 | 49.5 | 1.0098
650.5 | 49.5 | 1.0098
650.6 | 49.5 | 1.0098
650.7 | 49.5 | 1.0098
650.8 | 49.5 | 1.0098
650.9 | 49.5 | 1.0098
651 | 49.5 | 1.0098
651.1 | 49.5 | 1.0098
651.2 | 49.5 | 1.0098
651.3 | 49.5 | 1.0098
651.4 | 49.5 | 1.0098
651.5 | 49.5 | 1.0098
651.6 | 49.5 | 1.0098
651.7 | 49.5 | 1.0096
651.8 | 49.5 | 1.0096
651.9 | 49.5 | 1.0096
652 | 49.5 | 1.0096
652.1 | 49.5 | 1.0096
652.2 | 49.5 | 1.0096
652.3 | 49.5 | 1.0096
652.4 | 49.5 | 1.0096
652.5 | 49.5 | 1.0096
652.6 | 49.5 | 1.0096
652.7 | 49.5 | 1.0096
652.8 | 49.5 | 1.0096
652.9 | 49.5 | 1.0094
653 | 49.5 | 1.0094
653.1 | 49.5 | 1.0094
653.2 | 49.5 | 1.0094
653.3 | 49.5 | 1.0096
653.4 | 49.5 | 1.0096
653.5 | 49.5 | 1.0096
653.6 | 49.5 | 1.0096
653.7 | 49.5 | 1.0096
653.8 | 49.5 | 1.0096
653.9 | 49.5 | 1.0096
654 | 49.5 | 1.0096
654.1 | 49.5 | 1.0096
654.2 | 49.5 | 1.0096
654.3 | 49.5 | 1.0096
654.4 | 49.5 | 1.0096
654.5 | 49.5 | 1.0096
654.6 | 49.5 | 1.0096
654.7 | 49.5 | 1.0096
654.8 | 49.5 | 1.0096
654.9 | 49.5 | 1.0096
655 | 49.5 | 1.0096
655.1 | 49.5 | 1.0096
655.2 | 49.5 | 1.0096
655.3 | 49.5 | 1.0096
655.4 | 49.5 | 1.0096
655.5 | 49.5 | 1.0096
655.6 | 49.5 | 1.0096
655.7 | 49.5 | 1.0096
655.8 | 49.5 | 1.0096
655.9 | 49.5 | 1.0096
656 | 49.5 | 1.0096
656.1 | 49.5 | 1.0096
656.2 | 49.5 | 1.0096
656.3 | 49.5 | 1.0096
656.4 | 49.5 | 1.0096
656.5 | 49.5 | 1.0096
656.6 | 49.5 | 1.0096
656.7 | 49.5 | 1.0096
656.8 | 49.5 | 1.0096
656.9 | 49.5 | 1.0096
657 | 49.5 | 1.0096
657.1 | 49.5 | 1.0096
657.2 | 49.5 | 1.0096
657.3 | 49.5 | 1.0096
657.4 | 49.5 | 1.0098
657.5 | 49.5 | 1.0098
657.6 | 49.5 | 1.0098
657.7 | 49.5 | 1.0098
657.8 | 49.5 | 1.0098
657.9 | 49.5 | 1.0098
658 | 49.5 | 1.0098
658.1 | 49.5 | 1.0098
658.2 | 49.5 | 1.0098
658.3 | 49.5 | 1.0098
658.4 | 49.5 | 1.0098
658.5 | 49.5 | 1.0098
658.6 | 49.5 | 1.0096
658.7 | 49.5 | 1.0096
658.8 | 49.5 | 1.0096
658.9 | 49.5 | 1.0096
659 | 49.5 | 1.0096
659.1 | 49.5 | 1.0096
659.2 | 49.5 | 1.0096
659.3 | 49.5 | 1.0096
659.4 | 49.5 | 1.0096
659.5 | 49.5 | 1.0096
659.6 | 49.5 | 1.0096
659.7 | 49.5 | 1.0096
659.8 | 49.5 | 1.0096
659.9 | 49.5 | 1.0096
660 | 49.5 | 1.0096
660.1 | 49.5 | 1.0096
660.2 | 49.5 | 1.0096
660.3 | 49.5 | 1.0096
660.4 | 49.5 | 1.0096
660.5 | 49.5 | 1.0096
660.6 | 49.5 | 1.0096
660.7 | 49.5 | 1.0096
660.8 | 49.5 | 1.0096
660.9 | 49.5 | 1.0096
661 | 49.5 | 1.0096
661.1 | 49.5 | 1.0096
661.2 | 49.5 | 1.0096
661.3 | 49.5 | 1.0096
661.4 | 49.5 | 1.0096
661.5 | 49.5 | 1.0096
661.6 | 49.5 | 1.0096
661.7 | 49.5 | 1.0096
661.8 | 49.5 | 1.0096
661.9 | 49.5 | 1.0096
662 | 49.5 | 1.0096
662.1 | 49.5 | 1.0096
662.2 | 49.5 | 1.0096
662.3 | 49.5 | 1.0096
662.4 | 49.5 | 1.0096
662.5 | 49.5 | 1.0096
662.6 | 49.5 | 1.0096
662.7 | 49.5 | 1.0096
662.8 | 49.5 | 1.0096
662.9 | 49.5 | 1.0096
663 | 49.5 | 1.0096
663.1 | 49.5 | 1.0096
663.2 | 49.5 | 1.0096
663.3 | 49.5 | 1.0096
663.4 | 49.5 | 1.0096
663.5 | 49.5 | 1.0096
663.6 | 49.5 | 1.0096
663.7 | 49.5 | 1.0096
663.8 | 49.5 | 1.0096
663.9 | 49.5 | 1.0096
664 | 49.5 | 1.0096
664.1 | 49.5 | 1.0096
664.2 | 49.5 | 1.0096
664.3 | 49.5 | 1.0096
664.4 | 49.5 | 1.0096
664.5 | 49.5 | 1.0096
664.6 | 49.5 | 1.0096
664.7 | 49.5 | 1.0096
664.8 | 49.5 | 1.0096
664.9 | 49.5 | 1.0096
665 | 49.5 | 1.0096
665.1 | 49.5 | 1.0096
665.2 | 49.5 | 1.0096
665.3 | 49.5 | 1.0096
665.4 | 49.5 | 1.0096
665.5 | 49.5 | 1.0096
665.6 | 49.5 | 1.0096
665.7 | 49.5 | 1.0096
665.8 | 49.5 | 1.0096
665.9 | 49.5 | 1.0096
666 | 49.5 | 1.0096
666.1 | 49.5 | 1.0096
666.2 | 49.5 | 1.0096
666.3 | 49.5 | 1.0096
666.4 | 49.5 | 1.0096
666.5 | 49.5 | 1.0096
666.6 | 49.5 | 1.0096
666.7 | 49.5 | 1.0096
666.8 | 49.5 | 1.0096
666.9 | 49.5 | 1.0096
667 | 49.5 | 1.0096
667.1 | 49.5 | 1.0096
667.2 | 49.5 | 1.0096
667.3 | 49.5 | 1.0096
667.4 | 49.5 | 1.0096
667.5 | 49.5 | 1.0096
667.6 | 49.5 | 1.0096
667.7 | 49.5 | 1.0096
667.8 | 49.5 | 1.0096
667.9 | 49.5 | 1.0096
668 | 49.5 | 1.0096
668.1 | 49.5 | 1.0096
668.2 | 49.5 | 1.0096
668.3 | 49.5 | 1.0096
668.4 | 49.5 | 1.0096
668.5 | 49.5 | 1.0096
668.6 | 49.5 | 1.0096
668.7 | 49.5 | 1.0096
668.8 | 49.5 | 1.0096
668.9 | 49.5 | 1.0096
669 | 49.5 | 1.0096
669.1 | 49.5 | 1.0096
669.2 | 49.5 | 1.0096
669.3 | 49.5 | 1.0096
669.4 | 49.5 | 1.0096
669.5 | 49.5 | 1.0096
669.6 | 49.5 | 1.0096
669.7 | 49.5 | 1.0096
669.8 | 49.5 | 1.0096
669.9 | 49.5 | 1.0096
670 | 49.5 | 1.0096
670.1 | 49.5 | 1.0096
670.2 | 49.5 | 1.0096
670.3 | 49.5 | 1.0096
670.4 | 49.5 | 1.0096
670.5 | 49.5 | 1.0096
670.6 | 49.5 | 1.0096
670.7 | 49.5 | 1.0096
670.8 | 49.5 | 1.0096
670.9 | 49.5 | 1.0096
671 | 49.5 | 1.0096
671.1 | 49.5 | 1.0096
671.2 | 49.5 | 1.0096
671.3 | 49.5 | 1.0096
671.4 | 49.5 | 1.0096
671.5 | 49.5 | 1.0096
671.6 | 49.5 | 1.0096
671.7 | 49.5 | 1.0096
671.8 | 49.5 | 1.0096
671.9 | 49.5 | 1.0096
672 | 49.5 | 1.0096
672.1 | 49.5 | 1.0096
672.2 | 49.5 | 1.0096
672.3 | 49.5 | 1.0096
672.4 | 49.5 | 1.0096
672.5 | 49.5 | 1.0096
672.6 | 49.5 | 1.0096
672.7 | 49.5 | 1.0096
672.8 | 49.5 | 1.0096
672.9 | 49.5 | 1.0096
673 | 49.5 | 1.0096
673.1 | 49.5 | 1.0096
673.2 | 49.5 | 1.0096
673.3 | 49.5 | 1.0096
673.4 | 49.5 | 1.0096
673.5 | 49.5 | 1.0096
673.6 | 49.5 | 1.0096
673.7 | 49.5 | 1.0096
673.8 | 49.5 | 1.0096
673.9 | 49.5 | 1.0096
674 | 49.5 | 1.0096
674.1 | 49.5 | 1.0096
674.2 | 49.5 | 1.0096
674.3 | 49.5 | 1.0096
674.4 | 49.5 | 1.0096
674.5 | 49.5 | 1.0096
674.6 | 49.5 | 1.0096
674.7 | 49.5 | 1.0096
674.8 | 49.5 | 1.0096
674.9 | 49.5 | 1.0096
675 | 49.5 | 1.0096
675.1 | 49.5 | 1.0096
675.2 | 49.5 | 1.0096
675.3 | 49.5 | 1.0096
675.4 | 49.5 | 1.0096
675.5 | 49.5 | 1.0096
675.6 | 49.5 | 1.0096
675.7 | 49.5 | 1.0096
675.8 | 49.5 | 1.0096
675.9 | 49.5 | 1.0096
676 | 49.5 | 1.0096
676.1 | 49.5 | 1.0096
676.2 | 49.5 | 1.0096
676.3 | 49.5 | 1.0096
676.4 | 49.5 | 1.0096
676.5 | 49.5 | 1.0096
676.6 | 49.5 | 1.0096
676.7 | 49.5 | 1.0096
676.8 | 49.5 | 1.0096
676.9 | 49.5 | 1.0096
677 | 49.5 | 1.0096
677.1 | 49.5 | 1.0096
677.2 | 49.5 | 1.0096
677.3 | 49.5 | 1.0096
677.4 | 49.5 | 1.0096
677.5 | 49.5 | 1.0096
677.6 | 49.5 | 1.0096
677.7 | 49.5 | 1.0096
677.8 | 49.5 | 1.0096
677.9 | 49.5 | 1.0096
678 | 49.5 | 1.0096
678.1 | 49.5 | 1.0096
678.2 | 49.5 | 1.0096
678.3 | 49.5 | 1.0096
678.4 | 49.5 | 1.0096
678.5 | 49.5 | 1.0096
678.6 | 49.5 | 1.0096
678.7 | 49.5 | 1.0096
678.8 | 49.5 | 1.0096
678.9 | 49.5 | 1.0096
679 | 49.5 | 1.0096
679.1 | 49.5 | 1.0096
679.2 | 49.5 | 1.0096
679.3 | 49.5 | 1.0096
679.4 | 49.5 | 1.0096
679.5 | 49.5 | 1.0096
679.6 | 49.5 | 1.0096
679.7 | 49.5 | 1.0096
679.8 | 49.5 | 1.0096
679.9 | 49.5 | 1.0096
680 | 49.5 | 1.0096
680.1 | 49.5 | 1.0096
680.2 | 49.5 | 1.0096
680.3 | 49.5 | 1.0096
680.4 | 49.5 | 1.0096
680.5 | 49.5 | 1.0096
680.6 | 49.5 | 1.0096
680.7 | 49.5 | 1.0096
680.8 | 49.5 | 1.0096
680.9 | 49.5 | 1.0096
681 | 49.5 | 1.0096
681.1 | 49.5 | 1.0096
681.2 | 49.5 | 1.0096
681.3 | 49.5 | 1.0096
681.4 | 49.5 | 1.0096
681.5 | 49.5 | 1.0096
681.6 | 49.5 | 1.0096
681.7 | 49.5 | 1.0096
681.8 | 49.5 | 1.0096
681.9 | 49.5 | 1.0096
682 | 49.5 | 1.0096
682.1 | 49.5 | 1.0096
682.2 | 49.5 | 1.0096
682.3 | 49.5 | 1.0096
682.4 | 49.5 | 1.0096
682.5 | 49.5 | 1.0096
682.6 | 49.5 | 1.0096
682.7 | 49.5 | 1.0096
682.8 | 49.5 | 1.0096
682.9 | 49.5 | 1.0096
683 | 49.5 | 1.0096
683.1 | 49.5 | 1.0096
683.2 | 49.5 | 1.0096
683.3 | 49.5 | 1.0096
683.4 | 49.5 | 1.0096
683.5 | 49.5 | 1.0096
683.6 | 49.5 | 1.0096
683.7 | 49.5 | 1.0096
683.8 | 49.5 | 1.0096
683.9 | 49.5 | 1.0096
684 | 49.5 | 1.0096
684.1 | 49.5 | 1.0096
684.2 | 49.5 | 1.0096
684.3 | 49.5 | 1.0096
684.4 | 49.5 | 1.0096
684.5 | 49.5 | 1.0096
684.6 | 49.5 | 1.0096
684.7 | 49.5 | 1.0096
684.8 | 49.5 | 1.0096
684.9 | 49.5 | 1.0096
685 | 49.5 | 1.0096
685.1 | 49.5 | 1.0096
685.2 | 49.5 | 1.0096
685.3 | 49.5 | 1.0096
685.4 | 49.5 | 1.0096
685.5 | 49.5 | 1.0096
685.6 | 49.5 | 1.0096
685.7 | 49.5 | 1.0096
685.8 | 49.5 | 1.0096
685.9 | 49.5 | 1.0096
686 | 49.5 | 1.0096
686.1 | 49.5 | 1.0096
686.2 | 49.5 | 1.0096
686.3 | 49.5 | 1.0096
686.4 | 49.5 | 1.0096
686.5 | 49.5 | 1.0096
686.6 | 49.5 | 1.0096
686.7 | 49.5 | 1.0096
686.8 | 49.5 | 1.0096
686.9 | 49.5 | 1.0096
687 | 49.5 | 1.0096
687.1 | 49.5 | 1.0096
687.2 | 49.5 | 1.0096
687.3 | 49.5 | 1.0096
687.4 | 49.5 | 1.0096
687.5 | 49.5 | 1.0096
687.6 | 49.5 | 1.0096
687.7 | 49.5 | 1.0096
687.8 | 49.5 | 1.0096
687.9 | 49.5 | 1.0096
688 | 49.5 | 1.0096
688.1 | 49.5 | 1.0096
688.2 | 49.5 | 1.0096
688.3 | 49.5 | 1.0096
688.4 | 49.5 | 1.0096
688.5 | 49.5 | 1.0096
688.6 | 49.5 | 1.0096
688.7 | 49.5 | 1.0096
688.8 | 49.5 | 1.0096
688.9 | 49.5 | 1.0096
689 | 49.5 | 1.0096
689.1 | 49.5 | 1.0096
689.2 | 49.5 | 1.0096
689.3 | 49.5 | 1.0096
689.4 | 49.5 | 1.0096
689.5 | 49.5 | 1.0096
689.6 | 49.5 | 1.0096
689.7 | 49.5 | 1.0096
689.8 | 49.5 | 1.0096
689.9 | 49.5 | 1.0096
690 | 49.5 | 1.0096
690.1 | 49.5 | 1.0096
690.2 | 49.5 | 1.0096
690.3 | 49.5 | 1.0096
690.4 | 49.5 | 1.0096
690.5 | 49.5 | 1.0096
690.6 | 49.5 | 1.0096
690.7 | 49.5 | 1.0096
690.8 | 49.5 | 1.0096
690.9 | 49.5 | 1.0096
691 | 49.5 | 1.0096
691.1 | 49.5 | 1.0096
691.2 | 49.5 | 1.0096
691.3 | 49.5 | 1.0096
691.4 | 49.5 | 1.0098
691.5 | 49.5 | 1.0098
691.6 | 49.5 | 1.0098
691.7 | 49.5 | 1.0098
691.8 | 49.5 | 1.0098
691.9 | 49.5 | 1.0098
692 | 49.5 | 1.0098
692.1 | 49.5 | 1.0098
692.2 | 49.5 | 1.0098
692.3 | 49.5 | 1.0098
692.4 | 49.5 | 1.0098
692.5 | 49.5 | 1.0098
692.6 | 49.5 | 1.0096
692.7 | 49.5 | 1.0096
692.8 | 49.5 | 1.0096
692.9 | 49.5 | 1.0096
693 | 49.5 | 1.0096
693.1 | 49.5 | 1.0096
693.2 | 49.5 | 1.0096
693.3 | 49.5 | 1.0096
693.4 | 49.5 | 1.0096
693.5 | 49.5 | 1.0096
693.6 | 49.5 | 1.0096
693.7 | 49.5 | 1.0096
693.8 | 49.5 | 1.0096
693.9 | 49.5 | 1.0096
694 | 49.5 | 1.0096
694.1 | 49.5 | 1.0096
694.2 | 49.5 | 1.0096
694.3 | 49.5 | 1.0096
694.4 | 49.5 | 1.0096
694.5 | 49.5 | 1.0096
694.6 | 49.5 | 1.0096
694.7 | 49.5 | 1.0096
694.8 | 49.5 | 1.0096
694.9 | 49.5 | 1.0096
695 | 49.5 | 1.0096
695.1 | 49.5 | 1.0096
695.2 | 49.5 | 1.0096
695.3 | 49.5 | 1.0096
695.4 | 49.5 | 1.0096
695.5 | 49.5 | 1.0096
695.6 | 49.5 | 1.0096
695.7 | 49.5 | 1.0096
695.8 | 49.5 | 1.0096
695.9 | 49.5 | 1.0096
696 | 49.5 | 1.0096
696.1 | 49.5 | 1.0096
696.2 | 49.5 | 1.0096
696.3 | 49.5 | 1.0096
696.4 | 49.5 | 1.0096
696.5 | 49.5 | 1.0096
696.6 | 49.5 | 1.0096
696.7 | 49.5 | 1.0096
696.8 | 49.5 | 1.0096
696.9 | 49.5 | 1.0096
697 | 49.5 | 1.0096
697.1 | 49.5 | 1.0096
697.2 | 49.5 | 1.0096
697.3 | 49.5 | 1.0096
697.4 | 49.5 | 1.0096
697.5 | 49.5 | 1.0098
697.6 | 49.5 | 1.0098
697.7 | 49.5 | 1.0098
697.8 | 49.5 | 1.0098
697.9 | 49.5 | 1.0098
698 | 49.5 | 1.0098
698.1 | 49.5 | 1.0098
698.2 | 49.5 | 1.0098
698.3 | 49.5 | 1.0098
698.4 | 49.5 | 1.0098
698.5 | 49.5 | 1.0098
698.6 | 49.5 | 1.0098
698.7 | 49.5 | 1.0098
698.8 | 49.5 | 1.0098
698.9 | 49.5 | 1.0098
699 | 49.5 | 1.0098
699.1 | 49.5 | 1.0098
699.2 | 49.5 | 1.0098
699.3 | 49.5 | 1.0098
699.4 | 49.5 | 1.0098
699.5 | 49.5 | 1.0098
699.6 | 49.5 | 1.0098
699.7 | 49.5 | 1.0098
699.8 | 49.5 | 1.0098
699.9 | 49.5 | 1.0098
700 | 49.5 | 1.0098
700.1 | 49.5 | 1.0098
700.2 | 49.5 | 1.0098
700.3 | 49.5 | 1.0098
700.4 | 49.5 | 1.0098
700.5 | 49.5 | 1.0098
700.6 | 49.5 | 1.0098
700.7 | 49.5 | 1.0098
700.8 | 49.5 | 1.0098
700.9 | 49.5 | 1.0098
701 | 49.5 | 1.0098
701.1 | 49.5 | 1.0096
701.2 | 49.5 | 1.0096
701.3 | 49.5 | 1.0096
701.4 | 49.5 | 1.0096
701.5 | 49.5 | 1.0096
701.6 | 49.5 | 1.0096
701.7 | 49.5 | 1.0096
701.8 | 49.5 | 1.0096
701.9 | 49.5 | 1.0096
702 | 49.5 | 1.0096
702.1 | 49.5 | 1.0096
702.2 | 49.5 | 1.0096
702.3 | 49.5 | 1.0096
702.4 | 49.5 | 1.0096
702.5 | 49.5 | 1.0096
702.6 | 49.5 | 1.0096
702.7 | 49.5 | 1.0096
702.8 | 49.5 | 1.0096
702.9 | 49.5 | 1.0096
703 | 49.5 | 1.0096
703.1 | 49.5 | 1.0096
703.2 | 49.5 | 1.0096
703.3 | 49.5 | 1.0096
703.4 | 49.5 | 1.0098
703.5 | 49.5 | 1.0098
703.6 | 49.5 | 1.0098
703.7 | 49.5 | 1.0098
703.8 | 49.5 | 1.0098
703.9 | 49.5 | 1.0098
704 | 49.5 | 1.0098
704.1 | 49.5 | 1.0098
704.2 | 49.5 | 1.0098
704.3 | 49.5 | 1.0098
704.4 | 49.5 | 1.0098
704.5 | 49.5 | 1.0096
704.6 | 49.5 | 1.0096
704.7 | 49.5 | 1.0096
704.8 | 49.5 | 1.0096
704.9 | 49.5 | 1.0096
705 | 49.5 | 1.0096
705.1 | 49.5 | 1.0096
705.2 | 49.5 | 1.0096
705.3 | 49.5 | 1.0096
705.4 | 49.5 | 1.0096
705.5 | 49.5 | 1.0096
705.6 | 49.5 | 1.0096
705.7 | 49.5 | 1.0096
705.8 | 49.5 | 1.0096
705.9 | 49.5 | 1.0096
706 | 49.5 | 1.0096
706.1 | 49.5 | 1.0096
706.2 | 49.5 | 1.0096
706.3 | 49.5 | 1.0096
706.4 | 49.5 | 1.0096
706.5 | 49.5 | 1.0096
706.6 | 49.5 | 1.0096
706.7 | 49.5 | 1.0096
706.8 | 49.5 | 1.0096
706.9 | 49.5 | 1.0096
707 | 49.5 | 1.0096
707.1 | 49.5 | 1.0096
707.2 | 49.5 | 1.0096
707.3 | 49.5 | 1.0096
707.4 | 49.5 | 1.0096
707.5 | 49.5 | 1.0096
707.6 | 49.5 | 1.0096
707.7 | 49.5 | 1.0096
707.8 | 49.5 | 1.0096
707.9 | 49.5 | 1.0096
708 | 49.5 | 1.0096
708.1 | 49.5 | 1.0096
708.2 | 49.5 | 1.0096
708.3 | 49.5 | 1.0096
708.4 | 49.5 | 1.0096
708.5 | 49.5 | 1.0096
708.6 | 49.5 | 1.0096
708.7 | 49.5 | 1.0096
708.8 | 49.5 | 1.0096
708.9 | 49.5 | 1.0096
709 | 49.5 | 1.0096
709.1 | 49.5 | 1.0096
709.2 | 49.5 | 1.0096
709.3 | 49.5 | 1.0096
709.4 | 49.5 | 1.0096
709.5 | 49.5 | 1.0096
709.6 | 49.5 | 1.0096
709.7 | 49.5 | 1.0096
709.8 | 49.5 | 1.0096
709.9 | 49.5 | 1.0096
710 | 49.5 | 1.0096
710.1 | 49.5 | 1.0096
710.2 | 49.5 | 1.0096
710.3 | 49.5 | 1.0096
710.4 | 49.5 | 1.0096
710.5 | 49.5 | 1.0096
710.6 | 49.5 | 1.0096
710.7 | 49.5 | 1.0096
710.8 | 49.5 | 1.0096
710.9 | 49.5 | 1.0096
711 | 49.5 | 1.0096
711.1 | 49.5 | 1.0096
711.2 | 49.5 | 1.0096
711.3 | 49.5 | 1.0096
711.4 | 49.5 | 1.0096
711.5 | 49.5 | 1.0096
711.6 | 49.5 | 1.0096
711.7 | 49.5 | 1.0096
711.8 | 49.5 | 1.0096
711.9 | 49.5 | 1.0098
712 | 49.5 | 1.0098
712.1 | 49.5 | 1.0098
712.2 | 49.5 | 1.0098
712.3 | 49.5 | 1.0098
712.4 | 49.5 | 1.0098
712.5 | 49.5 | 1.0098
712.6 | 49.5 | 1.0098
712.7 | 49.5 | 1.0098
712.8 | 49.5 | 1.0098
712.9 | 49.5 | 1.0096
713 | 49.5 | 1.0096
713.1 | 49.5 | 1.0096
713.2 | 49.5 | 1.0096
713.3 | 49.5 | 1.0096
713.4 | 49.5 | 1.0096
713.5 | 49.5 | 1.0096
713.6 | 49.5 | 1.0096
713.7 | 49.5 | 1.0096
713.8 | 49.5 | 1.0096
713.9 | 49.5 | 1.0096
714 | 49.5 | 1.0096
714.1 | 49.5 | 1.0096
714.2 | 49.5 | 1.0096
714.3 | 49.5 | 1.0098
714.4 | 49.5 | 1.0098
714.5 | 49.5 | 1.0098
714.6 | 49.5 | 1.0098
714.7 | 49.5 | 1.0098
714.8 | 49.5 | 1.0098
714.9 | 49.5 | 1.0098
715 | 49.5 | 1.0098
715.1 | 49.5 | 1.0098
715.2 | 49.5 | 1.0098
715.3 | 49.5 | 1.0098
715.4 | 49.5 | 1.0098
715.5 | 49.5 | 1.0098
715.6 | 49.5 | 1.0098
715.7 | 49.5 | 1.0098
715.8 | 49.5 | 1.0098
715.9 | 49.5 | 1.0098
716 | 49.5 | 1.0098
716.1 | 49.5 | 1.0096
716.2 | 49.5 | 1.0096
716.3 | 49.5 | 1.0096
716.4 | 49.5 | 1.0096
716.5 | 49.5 | 1.0096
716.6 | 49.5 | 1.0096
716.7 | 49.5 | 1.0096
716.8 | 49.5 | 1.0096
716.9 | 49.5 | 1.0096
717 | 49.5 | 1.0096
717.1 | 49.5 | 1.0096
717.2 | 49.5 | 1.0096
717.3 | 49.5 | 1.0096
717.4 | 49.5 | 1.0096
717.5 | 49.5 | 1.0096
717.6 | 49.5 | 1.0096
717.7 | 49.5 | 1.0096
717.8 | 49.5 | 1.0096
717.9 | 49.5 | 1.0096
718 | 49.5 | 1.0096
718.1 | 49.5 | 1.0096
718.2 | 49.5 | 1.0096
718.3 | 49.5 | 1.0096
718.4 | 49.5 | 1.0096
718.5 | 49.5 | 1.0098
718.6 | 49.5 | 1.0098
718.7 | 49.5 | 1.0098
718.8 | 49.5 | 1.0098
718.9 | 49.5 | 1.0098
719 | 49.5 | 1.0098
719.1 | 49.5 | 1.0098
719.2 | 49.5 | 1.0098
719.3 | 49.5 | 1.0098
719.4 | 49.5 | 1.0098
719.5 | 49.5 | 1.0098
719.6 | 49.5 | 1.0098
719.7 | 49.5 | 1.0098
719.8 | 49.5 | 1.0098
719.9 | 49.5 | 1.0098
720 | 49.5 | 1.0098
720.1 | 49.5 | 1.0098
720.2 | 49.5 | 1.0098
720.3 | 49.5 | 1.0096
720.4 | 49.5 | 1.0096
720.5 | 49.5 | 1.0096
720.6 | 49.5 | 1.0096
720.7 | 49.5 | 1.0094
720.8 | 49.5 | 1.0094
720.9 | 49.5 | 1.0094
721 | 49.5 | 1.0094
721.1 | 49.5 | 1.0094
721.2 | 49.5 | 1.0094
721.3 | 49.5 | 1.0094
721.4 | 49.5 | 1.0094
721.5 | 49.5 | 1.0096
721.6 | 49.5 | 1.0096
721.7 | 49.5 | 1.0096
721.8 | 49.5 | 1.0096
721.9 | 49.5 | 1.0096
722 | 49.5 | 1.0098
722.1 | 49.5 | 1.0098
722.2 | 49.5 | 1.0098
722.3 | 49.5 | 1.0098
722.4 | 49.5 | 1.0098
722.5 | 49.5 | 1.0098
722.6 | 49.5 | 1.0098
722.7 | 49.5 | 1.0098
722.8 | 49.5 | 1.0098
722.9 | 49.5 | 1.0098
723 | 49.5 | 1.0098
723.1 | 49.5 | 1.0096
723.2 | 49.5 | 1.0096
723.3 | 49.5 | 1.0096
723.4 | 49.5 | 1.0096
723.5 | 49.5 | 1.0096
723.6 | 49.5 | 1.0096
723.7 | 49.5 | 1.0096
723.8 | 49.5 | 1.0096
723.9 | 49.5 | 1.0096
724 | 49.5 | 1.0096
724.1 | 49.5 | 1.0096
724.2 | 49.5 | 1.0096
724.3 | 49.5 | 1.0096
724.4 | 49.5 | 1.0096
724.5 | 49.5 | 1.0096
724.6 | 49.5 | 1.0096
724.7 | 49.5 | 1.0096
724.8 | 49.5 | 1.0096
724.9 | 49.5 | 1.0096
725 | 49.5 | 1.0096
725.1 | 49.5 | 1.0096
725.2 | 49.5 | 1.0096
725.3 | 49.5 | 1.0096
725.4 | 49.5 | 1.0096
725.5 | 49.5 | 1.0096
725.6 | 49.5 | 1.0096
725.7 | 49.5 | 1.0096
725.8 | 49.5 | 1.0096
725.9 | 49.5 | 1.0096
726 | 49.5 | 1.0096
726.1 | 49.5 | 1.0096
726.2 | 49.5 | 1.0096
726.3 | 49.5 | 1.0096
726.4 | 49.5 | 1.0096
726.5 | 49.5 | 1.0096
726.6 | 49.5 | 1.0096
726.7 | 49.5 | 1.0096
726.8 | 49.5 | 1.0096
726.9 | 49.5 | 1.0096
727 | 49.5 | 1.0096
727.1 | 49.5 | 1.0096
727.2 | 49.5 | 1.0096
727.3 | 49.5 | 1.0096
727.4 | 49.5 | 1.0096
727.5 | 49.5 | 1.0096
727.6 | 49.5 | 1.0096
727.7 | 49.5 | 1.0096
727.8 | 49.5 | 1.0096
727.9 | 49.5 | 1.0096
728 | 49.5 | 1.0096
728.1 | 49.5 | 1.0096
728.2 | 49.5 | 1.0096
728.3 | 49.5 | 1.0096
728.4 | 49.5 | 1.0096
728.5 | 49.5 | 1.0096
728.6 | 49.5 | 1.0096
728.7 | 49.5 | 1.0096
728.8 | 49.5 | 1.0096
728.9 | 49.5 | 1.0096
729 | 49.5 | 1.0096
729.1 | 49.5 | 1.0096
729.2 | 49.5 | 1.0096
729.3 | 49.5 | 1.0096
729.4 | 49.5 | 1.0096
729.5 | 49.5 | 1.0096
729.6 | 49.5 | 1.0096
729.7 | 49.5 | 1.0096
729.8 | 49.5 | 1.0096
729.9 | 49.5 | 1.0096
730 | 49.5 | 1.0096
730.1 | 49.5 | 1.0096
730.2 | 49.5 | 1.0096
730.3 | 49.5 | 1.0096
730.4 | 49.5 | 1.0096
730.5 | 49.5 | 1.0096
730.6 | 49.5 | 1.0096
730.7 | 49.5 | 1.0096
730.8 | 49.5 | 1.0096
730.9 | 49.5 | 1.0096
731 | 49.5 | 1.0096
731.1 | 49.5 | 1.0096
731.2 | 49.5 | 1.0096
731.3 | 49.5 | 1.0096
731.4 | 49.5 | 1.0096
731.5 | 49.5 | 1.0096
731.6 | 49.5 | 1.0096
731.7 | 49.5 | 1.0096
731.8 | 49.5 | 1.0096
731.9 | 49.5 | 1.0096
732 | 49.5 | 1.0096
732.1 | 49.5 | 1.0096
732.2 | 49.5 | 1.0096
732.3 | 49.5 | 1.0096
732.4 | 49.5 | 1.0096
732.5 | 49.5 | 1.0096
732.6 | 49.5 | 1.0096
732.7 | 49.5 | 1.0096
732.8 | 49.5 | 1.0096
732.9 | 49.5 | 1.0096
733 | 49.5 | 1.0096
733.1 | 49.5 | 1.0096
733.2 | 49.5 | 1.0096
733.3 | 49.5 | 1.0096
733.4 | 49.5 | 1.0096
733.5 | 49.5 | 1.0096
733.6 | 49.5 | 1.0096
733.7 | 49.5 | 1.0096
733.8 | 49.5 | 1.0096
733.9 | 49.5 | 1.0096
734 | 49.5 | 1.0096
734.1 | 49.5 | 1.0096
734.2 | 49.5 | 1.0096
734.3 | 49.5 | 1.0096
734.4 | 49.5 | 1.0096
734.5 | 49.5 | 1.0096
734.6 | 49.5 | 1.0096
734.7 | 49.5 | 1.0096
734.8 | 49.5 | 1.0096
734.9 | 49.5 | 1.0096
735 | 49.5 | 1.0096
735.1 | 49.5 | 1.0096
735.2 | 49.5 | 1.0096
735.3 | 49.5 | 1.0096
735.4 | 49.5 | 1.0096
735.5 | 49.5 | 1.0096
735.6 | 49.5 | 1.0096
735.7 | 49.5 | 1.0096
735.8 | 49.5 | 1.0096
735.9 | 49.5 | 1.0096
736 | 49.5 | 1.0096
736.1 | 49.5 | 1.0096
736.2 | 49.5 | 1.0096
736.3 | 49.5 | 1.0096
736.4 | 49.5 | 1.0096
736.5 | 49.5 | 1.0096
736.6 | 49.5 | 1.0096
736.7 | 49.5 | 1.0096
736.8 | 49.5 | 1.0096
736.9 | 49.5 | 1.0096
737 | 49.5 | 1.0096
737.1 | 49.5 | 1.0096
737.2 | 49.5 | 1.0096
737.3 | 49.5 | 1.0096
737.4 | 49.5 | 1.0096
737.5 | 49.5 | 1.0096
737.6 | 49.5 | 1.0096
737.7 | 49.5 | 1.0096
737.8 | 49.5 | 1.0096
737.9 | 49.5 | 1.0096
738 | 49.5 | 1.0096
738.1 | 49.5 | 1.0096
738.2 | 49.5 | 1.0096
738.3 | 49.5 | 1.0096
738.4 | 49.5 | 1.0096
738.5 | 49.5 | 1.0096
738.6 | 49.5 | 1.0096
738.7 | 49.5 | 1.0096
738.8 | 49.5 | 1.0096
738.9 | 49.5 | 1.0096
739 | 49.5 | 1.0096
739.1 | 49.5 | 1.0096
739.2 | 49.5 | 1.0096
739.3 | 49.5 | 1.0096
739.4 | 49.5 | 1.0096
739.5 | 49.5 | 1.0096
739.6 | 49.5 | 1.0096
739.7 | 49.5 | 1.0096
739.8 | 49.5 | 1.0096
739.9 | 49.5 | 1.0096
740 | 49.5 | 1.0096
740.1 | 49.5 | 1.0096
740.2 | 49.5 | 1.0096
740.3 | 49.5 | 1.0096
740.4 | 49.5 | 1.0096
740.5 | 49.5 | 1.0096
740.6 | 49.5 | 1.0096
740.7 | 49.5 | 1.0096
740.8 | 49.5 | 1.0096
740.9 | 49.5 | 1.0096
741 | 49.5 | 1.0096
741.1 | 49.5 | 1.0096
741.2 | 49.5 | 1.0096
741.3 | 49.5 | 1.0096
741.4 | 49.5 | 1.0096
741.5 | 49.5 | 1.0096
741.6 | 49.5 | 1.0096
741.7 | 49.5 | 1.0096
741.8 | 49.5 | 1.0096
741.9 | 49.5 | 1.0096
742 | 49.5 | 1.0096
742.1 | 49.5 | 1.0096
742.2 | 49.5 | 1.0096
742.3 | 49.5 | 1.0096
742.4 | 49.5 | 1.0096
742.5 | 49.5 | 1.0096
742.6 | 49.5 | 1.0096
742.7 | 49.5 | 1.0096
742.8 | 49.5 | 1.0096
742.9 | 49.5 | 1.0096
743 | 49.5 | 1.0096
743.1 | 49.5 | 1.0096
743.2 | 49.5 | 1.0096
743.3 | 49.5 | 1.0096
743.4 | 49.5 | 1.0096
743.5 | 49.5 | 1.0096
743.6 | 49.5 | 1.0096
743.7 | 49.5 | 1.0096
743.8 | 49.5 | 1.0096
743.9 | 49.5 | 1.0096
744 | 49.5 | 1.0096
744.1 | 49.5 | 1.0096
744.2 | 49.5 | 1.0096
744.3 | 49.5 | 1.0096
744.4 | 49.5 | 1.0096
744.5 | 49.5 | 1.0096
744.6 | 49.5 | 1.0096
744.7 | 49.5 | 1.0096
744.8 | 49.5 | 1.0096
744.9 | 49.5 | 1.0096
745 | 49.5 | 1.0096
745.1 | 49.5 | 1.0096
745.2 | 49.5 | 1.0096
745.3 | 49.5 | 1.0096
745.4 | 49.5 | 1.0096
745.5 | 49.5 | 1.0096
745.6 | 49.5 | 1.0096
745.7 | 49.5 | 1.0096
745.8 | 49.5 | 1.0096
745.9 | 49.5 | 1.0096
746 | 49.5 | 1.0096
746.1 | 49.5 | 1.0096
746.2 | 49.5 | 1.0096
746.3 | 49.5 | 1.0096
746.4 | 49.5 | 1.0096
746.5 | 49.5 | 1.0096
746.6 | 49.5 | 1.0096
746.7 | 49.5 | 1.0096
746.8 | 49.5 | 1.0096
746.9 | 49.5 | 1.0096
747 | 49.5 | 1.0096
747.1 | 49.5 | 1.0096
747.2 | 49.5 | 1.0096
747.3 | 49.5 | 1.0096
747.4 | 49.5 | 1.0096
747.5 | 49.5 | 1.0096
747.6 | 49.5 | 1.0096
747.7 | 49.5 | 1.0096
747.8 | 49.5 | 1.0096
747.9 | 49.5 | 1.0096
748 | 49.5 | 1.0096
748.1 | 49.5 | 1.0096
748.2 | 49.5 | 1.0096
748.3 | 49.5 | 1.0096
748.4 | 49.5 | 1.0096
748.5 | 49.5 | 1.0096
748.6 | 49.5 | 1.0096
748.7 | 49.5 | 1.0096
748.8 | 49.5 | 1.0096
748.9 | 49.5 | 1.0096
749 | 49.5 | 1.0096
749.1 | 49.5 | 1.0096
749.2 | 49.5 | 1.0096
749.3 | 49.5 | 1.0096
749.4 | 49.5 | 1.0096
749.5 | 49.5 | 1.0096
749.6 | 49.5 | 1.0096
749.7 | 49.5 | 1.0096
749.8 | 49.5 | 1.0096
749.9 | 49.5 | 1.0096
750 | 49.5 | 1.0096
750.1 | 49.5 | 1.0096
750.2 | 49.5 | 1.0096
750.3 | 49.5 | 1.0096
750.4 | 49.5 | 1.0096
750.5 | 49.5 | 1.0096
750.6 | 49.5 | 1.0096
750.7 | 49.5 | 1.0096
750.8 | 49.5 | 1.0096
750.9 | 49.5 | 1.0096
751 | 49.5 | 1.0096
751.1 | 49.5 | 1.0096
751.2 | 49.5 | 1.0096
751.3 | 49.5 | 1.0096
751.4 | 49.5 | 1.0096
751.5 | 49.5 | 1.0096
751.6 | 49.5 | 1.0096
751.7 | 49.5 | 1.0096
751.8 | 49.5 | 1.0096
751.9 | 49.5 | 1.0096
752 | 49.5 | 1.0096
752.1 | 49.5 | 1.0096
752.2 | 49.5 | 1.0096
752.3 | 49.5 | 1.0096
752.4 | 49.5 | 1.0096
752.5 | 49.5 | 1.0096
752.6 | 49.5 | 1.0096
752.7 | 49.5 | 1.0096
752.8 | 49.5 | 1.0096
752.9 | 49.5 | 1.0096
753 | 49.5 | 1.0096
753.1 | 49.5 | 1.0096
753.2 | 49.5 | 1.0096
753.3 | 49.5 | 1.0096
753.4 | 49.5 | 1.0096
753.5 | 49.5 | 1.0096
753.6 | 49.5 | 1.0096
753.7 | 49.5 | 1.0096
753.8 | 49.5 | 1.0096
753.9 | 49.5 | 1.0096
754 | 49.5 | 1.0096
754.1 | 49.5 | 1.0096
754.2 | 49.5 | 1.0096
754.3 | 49.5 | 1.0096
754.4 | 49.5 | 1.0096
754.5 | 49.5 | 1.0096
754.6 | 49.5 | 1.0096
754.7 | 49.5 | 1.0096
754.8 | 49.5 | 1.0096
754.9 | 49.5 | 1.0096
755 | 49.5 | 1.0096
755.1 | 49.5 | 1.0096
755.2 | 49.5 | 1.0096
755.3 | 49.5 | 1.0096
755.4 | 49.5 | 1.0096
755.5 | 49.5 | 1.0096
755.6 | 49.5 | 1.0096
755.7 | 49.5 | 1.0096
755.8 | 49.5 | 1.0096
755.9 | 49.5 | 1.0096
756 | 49.5 | 1.0096
756.1 | 49.5 | 1.0096
756.2 | 49.5 | 1.0096
756.3 | 49.5 | 1.0096
756.4 | 49.5 | 1.0096
756.5 | 49.5 | 1.0096
756.6 | 49.5 | 1.0096
756.7 | 49.5 | 1.0096
756.8 | 49.5 | 1.0096
756.9 | 49.5 | 1.0096
757 | 49.5 | 1.0096
757.1 | 49.5 | 1.0096
757.2 | 49.5 | 1.0096
757.3 | 49.5 | 1.0096
757.4 | 49.5 | 1.0096
757.5 | 49.5 | 1.0096
757.6 | 49.5 | 1.0096
757.7 | 49.5 | 1.0096
757.8 | 49.5 | 1.0096
757.9 | 49.5 | 1.0096
758 | 49.5 | 1.0096
758.1 | 49.5 | 1.0096
758.2 | 49.5 | 1.0096
758.3 | 49.5 | 1.0096
758.4 | 49.5 | 1.0096
758.5 | 49.5 | 1.0096
758.6 | 49.5 | 1.0096
758.7 | 49.5 | 1.0096
758.8 | 49.5 | 1.0096
758.9 | 49.5 | 1.0096
759 | 49.5 | 1.0096
759.1 | 49.5 | 1.0096
759.2 | 49.5 | 1.0096
759.3 | 49.5 | 1.0096
759.4 | 49.5 | 1.0096
759.5 | 49.5 | 1.0096
759.6 | 49.5 | 1.0096
759.7 | 49.5 | 1.0096
759.8 | 49.5 | 1.0096
759.9 | 49.5 | 1.0096
760 | 49.5 | 1.0096
760.1 | 49.5 | 1.0096
760.2 | 49.5 | 1.0096
760.3 | 49.5 | 1.0096
760.4 | 49.5 | 1.0096
760.5 | 49.5 | 1.0096
760.6 | 49.5 | 1.0096
760.7 | 49.5 | 1.0096
760.8 | 49.5 | 1.0096
760.9 | 49.5 | 1.0096
761 | 49.5 | 1.0096
761.1 | 49.5 | 1.0096
761.2 | 49.5 | 1.0096
761.3 | 49.5 | 1.0096
761.4 | 49.5 | 1.0096
761.5 | 49.5 | 1.0096
761.6 | 49.5 | 1.0096
761.7 | 49.5 | 1.0096
761.8 | 49.5 | 1.0096
761.9 | 49.5 | 1.0096
762 | 49.5 | 1.0096
762.1 | 49.5 | 1.0096
762.2 | 49.5 | 1.0096
762.3 | 49.5 | 1.0096
762.4 | 49.5 | 1.0096
762.5 | 49.5 | 1.0096
762.6 | 49.5 | 1.0096
762.7 | 49.5 | 1.0096
762.8 | 49.5 | 1.0096
762.9 | 49.5 | 1.0096
763 | 49.5 | 1.0096
763.1 | 49.5 | 1.0096
763.2 | 49.5 | 1.0096
763.3 | 49.5 | 1.0096
763.4 | 49.5 | 1.0096
763.5 | 49.5 | 1.0096
763.6 | 49.5 | 1.0096
763.7 | 49.5 | 1.0096
763.8 | 49.5 | 1.0096
763.9 | 49.5 | 1.0096
764 | 49.5 | 1.0096
764.1 | 49.5 | 1.0096
764.2 | 49.5 | 1.0096
764.3 | 49.5 | 1.0096
764.4 | 49.5 | 1.0096
764.5 | 49.5 | 1.0096
764.6 | 49.5 | 1.0096
764.7 | 49.5 | 1.0096
764.8 | 49.5 | 1.0096
764.9 | 49.5 | 1.0096
765 | 49.5 | 1.0096
765.1 | 49.5 | 1.0096
765.2 | 49.5 | 1.0096
765.3 | 49.5 | 1.0096
765.4 | 49.5 | 1.0096
765.5 | 49.5 | 1.0096
765.6 | 49.5 | 1.0096
765.7 | 49.5 | 1.0096
765.8 | 49.5 | 1.0096
765.9 | 49.5 | 1.0096
766 | 49.5 | 1.0096
766.1 | 49.5 | 1.0096
766.2 | 49.5 | 1.0096
766.3 | 49.5 | 1.0096
766.4 | 49.5 | 1.0096
766.5 | 49.5 | 1.0096
766.6 | 49.5 | 1.0096
766.7 | 49.5 | 1.0096
766.8 | 49.5 | 1.0096
766.9 | 49.5 | 1.0096
767 | 49.5 | 1.0096
767.1 | 49.5 | 1.0096
767.2 | 49.5 | 1.0096
767.3 | 49.5 | 1.0096
767.4 | 49.5 | 1.0096
767.5 | 49.5 | 1.0096
767.6 | 49.5 | 1.0096
767.7 | 49.5 | 1.0096
767.8 | 49.5 | 1.0096
767.9 | 49.5 | 1.0096
768 | 49.5 | 1.0096
768.1 | 49.5 | 1.0096
768.2 | 49.5 | 1.0096
768.3 | 49.5 | 1.0096
768.4 | 49.5 | 1.0096
768.5 | 49.5 | 1.0096
768.6 | 49.5 | 1.0096
768.7 | 49.5 | 1.0096
768.8 | 49.5 | 1.0096
768.9 | 49.5 | 1.0096
769 | 49.5 | 1.0096
769.1 | 49.5 | 1.0096
769.2 | 49.5 | 1.0096
769.3 | 49.5 | 1.0096
769.4 | 49.5 | 1.0096
769.5 | 49.5 | 1.0096
769.6 | 49.5 | 1.0096
769.7 | 49.5 | 1.0096
769.8 | 49.5 | 1.0096
769.9 | 49.5 | 1.0096
770 | 49.5 | 1.0096
770.1 | 49.5 | 1.0096
770.2 | 49.5 | 1.0096
770.3 | 49.5 | 1.0096
770.4 | 49.5 | 1.0096
770.5 | 49.5 | 1.0096
770.6 | 49.5 | 1.0096
770.7 | 49.5 | 1.0096
770.8 | 49.5 | 1.0096
770.9 | 49.5 | 1.0096
771 | 49.5 | 1.0096
771.1 | 49.5 | 1.0096
771.2 | 49.5 | 1.0096
771.3 | 49.5 | 1.0096
771.4 | 49.5 | 1.0096
771.5 | 49.5 | 1.0096
771.6 | 49.5 | 1.0096
771.7 | 49.5 | 1.0096
771.8 | 49.5 | 1.0096
771.9 | 49.5 | 1.0096
772 | 49.5 | 1.0096
772.1 | 49.5 | 1.0096
772.2 | 49.5 | 1.0096
772.3 | 49.5 | 1.0096
772.4 | 49.5 | 1.0096
772.5 | 49.5 | 1.0096
772.6 | 49.5 | 1.0096
772.7 | 49.5 | 1.0096
772.8 | 49.5 | 1.0096
772.9 | 49.5 | 1.0096
773 | 49.5 | 1.0096
773.1 | 49.5 | 1.0096
773.2 | 49.5 | 1.0096
773.3 | 49.5 | 1.0096
773.4 | 49.5 | 1.0096
773.5 | 49.5 | 1.0096
773.6 | 49.5 | 1.0096
773.7 | 49.5 | 1.0096
773.8 | 49.5 | 1.0096
773.9 | 49.5 | 1.0096
774 | 49.5 | 1.0096
774.1 | 49.5 | 1.0096
774.2 | 49.5 | 1.0096
774.3 | 49.5 | 1.0096
774.4 | 49.5 | 1.0096
774.5 | 49.5 | 1.0096
774.6 | 49.5 | 1.0096
774.7 | 49.5 | 1.0096
774.8 | 49.5 | 1.0096
774.9 | 49.5 | 1.0096
775 | 49.5 | 1.0096
775.1 | 49.5 | 1.0096
775.2 | 49.5 | 1.0096
775.3 | 49.5 | 1.0096
775.4 | 49.5 | 1.0096
775.5 | 49.5 | 1.0096
775.6 | 49.5 | 1.0096
775.7 | 49.5 | 1.0096
775.8 | 49.5 | 1.0096
775.9 | 49.5 | 1.0096
776 | 49.5 | 1.0096
776.1 | 49.5 | 1.0096
776.2 | 49.5 | 1.0096
776.3 | 49.5 | 1.0096
776.4 | 49.5 | 1.0096
776.5 | 49.5 | 1.0096
776.6 | 49.5 | 1.0096
776.7 | 49.5 | 1.0096
776.8 | 49.5 | 1.0096
776.9 | 49.5 | 1.0096
777 | 49.5 | 1.0096
777.1 | 49.5 | 1.0096
777.2 | 49.5 | 1.0096
777.3 | 49.5 | 1.0096
777.4 | 49.5 | 1.0096
777.5 | 49.5 | 1.0096
777.6 | 49.5 | 1.0096
777.7 | 49.5 | 1.0096
777.8 | 49.5 | 1.0096
777.9 | 49.5 | 1.0096
778 | 49.5 | 1.0096
778.1 | 49.5 | 1.0096
778.2 | 49.5 | 1.0096
778.3 | 49.5 | 1.0096
778.4 | 49.5 | 1.0096
778.5 | 49.5 | 1.0096
778.6 | 49.5 | 1.0096
778.7 | 49.5 | 1.0096
778.8 | 49.5 | 1.0096
778.9 | 49.5 | 1.0096
779 | 49.5 | 1.0096
779.1 | 49.5 | 1.0096
779.2 | 49.5 | 1.0096
779.3 | 49.5 | 1.0096
779.4 | 49.5 | 1.0096
779.5 | 49.5 | 1.0096
779.6 | 49.5 | 1.0096
779.7 | 49.5 | 1.0096
779.8 | 49.5 | 1.0096
779.9 | 49.5 | 1.0096
780 | 49.5 | 1.0096
780.1 | 49.5 | 1.0096
780.2 | 49.5 | 1.0096
780.3 | 49.5 | 1.0096
780.4 | 49.5 | 1.0096
780.5 | 49.5 | 1.0096
780.6 | 49.5 | 1.0096
780.7 | 49.5 | 1.0096
780.8 | 49.5 | 1.0096
780.9 | 49.5 | 1.0096
781 | 49.5 | 1.0096
781.1 | 49.5 | 1.0096
781.2 | 49.5 | 1.0096
781.3 | 49.5 | 1.0096
781.4 | 49.5 | 1.0096
781.5 | 49.5 | 1.0096
781.6 | 49.5 | 1.0096
781.7 | 49.5 | 1.0096
781.8 | 49.5 | 1.0096
781.9 | 49.5 | 1.0096
782 | 49.5 | 1.0096
782.1 | 49.5 | 1.0096
782.2 | 49.5 | 1.0096
782.3 | 49.5 | 1.0096
782.4 | 49.5 | 1.0096
782.5 | 49.5 | 1.0096
782.6 | 49.5 | 1.0096
782.7 | 49.5 | 1.0096
782.8 | 49.5 | 1.0096
782.9 | 49.5 | 1.0096
783 | 49.5 | 1.0096
783.1 | 49.5 | 1.0096
783.2 | 49.5 | 1.0096
783.3 | 49.5 | 1.0096
783.4 | 49.5 | 1.0096
783.5 | 49.5 | 1.0096
783.6 | 49.5 | 1.0096
783.7 | 49.5 | 1.0096
783.8 | 49.5 | 1.0096
783.9 | 49.5 | 1.0096
784 | 49.5 | 1.0096
784.1 | 49.5 | 1.0096
784.2 | 49.5 | 1.0096
784.3 | 49.5 | 1.0096
784.4 | 49.5 | 1.0096
784.5 | 49.5 | 1.0096
784.6 | 49.5 | 1.0096
784.7 | 49.5 | 1.0096
784.8 | 49.5 | 1.0096
784.9 | 49.5 | 1.0096
785 | 49.5 | 1.0096
785.1 | 49.5 | 1.0096
785.2 | 49.5 | 1.0096
785.3 | 49.5 | 1.0096
785.4 | 49.5 | 1.0096
785.5 | 49.5 | 1.0096
785.6 | 49.5 | 1.0096
785.7 | 49.5 | 1.0096
785.8 | 49.5 | 1.0096
785.9 | 49.5 | 1.0096
786 | 49.5 | 1.0096
786.1 | 49.5 | 1.0096
786.2 | 49.5 | 1.0096
786.3 | 49.5 | 1.0096
786.4 | 49.5 | 1.0098
786.5 | 49.5 | 1.0098
786.6 | 49.5 | 1.0098
786.7 | 49.5 | 1.0098
786.8 | 49.5 | 1.0098
786.9 | 49.5 | 1.0098
787 | 49.5 | 1.0098
787.1 | 49.5 | 1.0098
787.2 | 49.5 | 1.0098
787.3 | 49.5 | 1.0098
787.4 | 49.5 | 1.0096
787.5 | 49.5 | 1.0096
787.6 | 49.5 | 1.0096
787.7 | 49.5 | 1.0096
787.8 | 49.5 | 1.0096
787.9 | 49.5 | 1.0096
788 | 49.5 | 1.0096
788.1 | 49.5 | 1.0096
788.2 | 49.5 | 1.0096
788.3 | 49.5 | 1.0096
788.4 | 49.5 | 1.0096
788.5 | 49.5 | 1.0096
788.6 | 49.5 | 1.0096
788.7 | 49.5 | 1.0096
788.8 | 49.5 | 1.0096
788.9 | 49.5 | 1.0096
789 | 49.5 | 1.0096
789.1 | 49.5 | 1.0096
789.2 | 49.5 | 1.0096
789.3 | 49.5 | 1.0096
789.4 | 49.5 | 1.0096
789.5 | 49.5 | 1.0096
789.6 | 49.5 | 1.0096
789.7 | 49.5 | 1.0096
789.8 | 49.5 | 1.0096
789.9 | 49.5 | 1.0096
790 | 49.5 | 1.0096
790.1 | 49.5 | 1.0096
790.2 | 49.5 | 1.0096
790.3 | 49.5 | 1.0096
790.4 | 49.5 | 1.0096
790.5 | 49.5 | 1.0096
790.6 | 49.5 | 1.0096
790.7 | 49.5 | 1.0096
790.8 | 49.5 | 1.0096
790.9 | 49.5 | 1.0096
791 | 49.5 | 1.0096
791.1 | 49.5 | 1.0096
791.2 | 49.5 | 1.0096
791.3 | 49.5 | 1.0096
791.4 | 49.5 | 1.0096
791.5 | 49.5 | 1.0096
791.6 | 49.5 | 1.0096
791.7 | 49.5 | 1.0096
791.8 | 49.5 | 1.0096
791.9 | 49.5 | 1.0096
792 | 49.5 | 1.0096
792.1 | 49.5 | 1.0096
792.2 | 49.5 | 1.0096
792.3 | 49.5 | 1.0096
792.4 | 49.5 | 1.0096
792.5 | 49.5 | 1.0096
792.6 | 49.5 | 1.0096
792.7 | 49.5 | 1.0096
792.8 | 49.5 | 1.0096
792.9 | 49.5 | 1.0096
793 | 49.5 | 1.0096
793.1 | 49.5 | 1.0096
793.2 | 49.5 | 1.0096
793.3 | 49.5 | 1.0096
793.4 | 49.5 | 1.0096
793.5 | 49.5 | 1.0096
793.6 | 49.5 | 1.0096
793.7 | 49.5 | 1.0096
793.8 | 49.5 | 1.0096
793.9 | 49.5 | 1.0096
794 | 49.5 | 1.0096
794.1 | 49.5 | 1.0096
794.2 | 49.5 | 1.0096
794.3 | 49.5 | 1.0096
794.4 | 49.5 | 1.0096
794.5 | 49.5 | 1.0096
794.6 | 49.5 | 1.0096
794.7 | 49.5 | 1.0096
794.8 | 49.5 | 1.0096
794.9 | 49.5 | 1.0096
795 | 49.5 | 1.0096
795.1 | 49.5 | 1.0096
795.2 | 49.5 | 1.0096
795.3 | 49.5 | 1.0096
795.4 | 49.5 | 1.0096
795.5 | 49.5 | 1.0096
795.6 | 49.5 | 1.0096
795.7 | 49.5 | 1.0096
795.8 | 49.5 | 1.0096
795.9 | 49.5 | 1.0096
796 | 49.5 | 1.0096
796.1 | 49.5 | 1.0096
796.2 | 49.5 | 1.0096
796.3 | 49.5 | 1.0096
796.4 | 49.5 | 1.0096
796.5 | 49.5 | 1.0096
796.6 | 49.5 | 1.0096
796.7 | 49.5 | 1.0096
796.8 | 49.5 | 1.0096
796.9 | 49.5 | 1.0096
797 | 49.5 | 1.0096
797.1 | 49.5 | 1.0096
797.2 | 49.5 | 1.0096
797.3 | 49.5 | 1.0096
797.4 | 49.5 | 1.0096
797.5 | 49.5 | 1.0096
797.6 | 49.5 | 1.0096
797.7 | 49.5 | 1.0096
797.8 | 49.5 | 1.0096
797.9 | 49.5 | 1.0096
798 | 49.5 | 1.0096
798.1 | 49.5 | 1.0096
798.2 | 49.5 | 1.0096
798.3 | 49.5 | 1.0096
798.4 | 49.5 | 1.0096
798.5 | 49.5 | 1.0096
798.6 | 49.5 | 1.0096
798.7 | 49.5 | 1.0096
798.8 | 49.5 | 1.0096
798.9 | 49.5 | 1.0096
799 | 49.5 | 1.0096
799.1 | 49.5 | 1.0096
799.2 | 49.5 | 1.0096
799.3 | 49.5 | 1.0096
799.4 | 49.5 | 1.0096
799.5 | 49.5 | 1.0096
799.6 | 49.5 | 1.0096
799.7 | 49.5 | 1.0096
799.8 | 49.5 | 1.0096
799.9 | 49.5 | 1.0096
800 | 49.5 | 1.0096
800.1 | 49.5 | 1.0096
800.2 | 49.5 | 1.0096
800.3 | 49.5 | 1.0096
800.4 | 49.5 | 1.0096
800.5 | 49.5 | 1.0096
800.6 | 49.5 | 1.0096
800.7 | 49.5 | 1.0096
800.8 | 49.5 | 1.0096
800.9 | 49.5 | 1.0096
801 | 49.5 | 1.0096
801.1 | 49.5 | 1.0096
801.2 | 49.5 | 1.0096
801.3 | 49.5 | 1.0096
801.4 | 49.5 | 1.0096
801.5 | 49.5 | 1.0096
801.6 | 49.5 | 1.0096
801.7 | 49.5 | 1.0096
801.8 | 49.5 | 1.0096
801.9 | 49.5 | 1.0096
802 | 49.5 | 1.0096
802.1 | 49.5 | 1.0096
802.2 | 49.5 | 1.0096
802.3 | 49.5 | 1.0096
802.4 | 49.5 | 1.0096
802.5 | 49.5 | 1.0096
802.6 | 49.5 | 1.0096
802.7 | 49.5 | 1.0096
802.8 | 49.5 | 1.0096
802.9 | 49.5 | 1.0096
803 | 49.5 | 1.0096
803.1 | 49.5 | 1.0096
803.2 | 49.5 | 1.0096
803.3 | 49.5 | 1.0096
803.4 | 49.5 | 1.0096
803.5 | 49.5 | 1.0096
803.6 | 49.5 | 1.0096
803.7 | 49.5 | 1.0096
803.8 | 49.5 | 1.0096
803.9 | 49.5 | 1.0096
804 | 49.5 | 1.0096
804.1 | 49.5 | 1.0096
804.2 | 49.5 | 1.0096
804.3 | 49.5 | 1.0096
804.4 | 49.5 | 1.0096
804.5 | 49.5 | 1.0096
804.6 | 49.5 | 1.0096
804.7 | 49.5 | 1.0096
804.8 | 49.5 | 1.0098
804.9 | 49.5 | 1.0098
805 | 49.5 | 1.0098
805.1 | 49.5 | 1.0098
805.2 | 49.5 | 1.0098
805.3 | 49.5 | 1.0098
805.4 | 49.5 | 1.0098
805.5 | 49.5 | 1.0098
805.6 | 49.5 | 1.0098
805.7 | 49.5 | 1.0098
805.8 | 49.5 | 1.0096
805.9 | 49.5 | 1.0096
806 | 49.5 | 1.0096
806.1 | 49.5 | 1.0096
806.2 | 49.5 | 1.0096
806.3 | 49.5 | 1.0096
806.4 | 49.5 | 1.0096
806.5 | 49.5 | 1.0096
806.6 | 49.5 | 1.0096
806.7 | 49.5 | 1.0096
806.8 | 49.5 | 1.0096
806.9 | 49.5 | 1.0096
807 | 49.5 | 1.0096
807.1 | 49.5 | 1.0096
807.2 | 49.5 | 1.0096
807.3 | 49.5 | 1.0096
807.4 | 49.5 | 1.0096
807.5 | 49.5 | 1.0096
807.6 | 49.5 | 1.0096
807.7 | 49.5 | 1.0096
807.8 | 49.5 | 1.0096
807.9 | 49.5 | 1.0096
808 | 49.5 | 1.0096
808.1 | 49.5 | 1.0096
808.2 | 49.5 | 1.0096
808.3 | 49.5 | 1.0096
808.4 | 49.5 | 1.0096
808.5 | 49.5 | 1.0096
808.6 | 49.5 | 1.0096
808.7 | 49.5 | 1.0096
808.8 | 49.5 | 1.0096
808.9 | 49.5 | 1.0096
809 | 49.5 | 1.0096
809.1 | 49.5 | 1.0096
809.2 | 49.5 | 1.0096
809.3 | 49.5 | 1.0096
809.4 | 49.5 | 1.0096
809.5 | 49.5 | 1.0096
809.6 | 49.5 | 1.0096
809.7 | 49.5 | 1.0096
809.8 | 49.5 | 1.0096
809.9 | 49.5 | 1.0096
810 | 49.5 | 1.0096
810.1 | 49.5 | 1.0096
810.2 | 49.5 | 1.0096
810.3 | 49.5 | 1.0096
810.4 | 49.5 | 1.0096
810.5 | 49.5 | 1.0096
810.6 | 49.5 | 1.0096
810.7 | 49.5 | 1.0096
810.8 | 49.5 | 1.0096
810.9 | 49.5 | 1.0096
811 | 49.5 | 1.0096
811.1 | 49.5 | 1.0096
811.2 | 49.5 | 1.0096
811.3 | 49.5 | 1.0096
811.4 | 49.5 | 1.0096
811.5 | 49.5 | 1.0096
811.6 | 49.5 | 1.0096
811.7 | 49.5 | 1.0096
811.8 | 49.5 | 1.0096
811.9 | 49.5 | 1.0096
812 | 49.5 | 1.0096
812.1 | 49.5 | 1.0096
812.2 | 49.5 | 1.0096
812.3 | 49.5 | 1.0096
812.4 | 49.5 | 1.0096
812.5 | 49.5 | 1.0096
812.6 | 49.5 | 1.0096
812.7 | 49.5 | 1.0096
812.8 | 49.5 | 1.0096
812.9 | 49.5 | 1.0094
813 | 49.5 | 1.0094
813.1 | 49.5 | 1.0094
813.2 | 49.5 | 1.0094
813.3 | 49.5 | 1.0096
813.4 | 49.5 | 1.0096
813.5 | 49.5 | 1.0096
813.6 | 49.5 | 1.0096
813.7 | 49.5 | 1.0096
813.8 | 49.5 | 1.0096
813.9 | 49.5 | 1.0096
814 | 49.5 | 1.0096
814.1 | 49.5 | 1.0098
814.2 | 49.5 | 1.0098
814.3 | 49.5 | 1.0098
814.4 | 49.5 | 1.0098
814.5 | 49.5 | 1.0098
814.6 | 49.5 | 1.0098
814.7 | 49.5 | 1.0098
814.8 | 49.5 | 1.0098
814.9 | 49.5 | 1.0098
815 | 49.5 | 1.0098
815.1 | 49.5 | 1.0098
815.2 | 49.5 | 1.0098
815.3 | 49.5 | 1.0098
815.4 | 49.5 | 1.0098
815.5 | 49.5 | 1.0098
815.6 | 49.5 | 1.0098
815.7 | 49.5 | 1.0096
815.8 | 49.5 | 1.0096
815.9 | 49.5 | 1.0096
816 | 49.5 | 1.0096
816.1 | 49.5 | 1.0096
816.2 | 49.5 | 1.0096
816.3 | 49.5 | 1.0096
816.4 | 49.5 | 1.0098
816.5 | 49.5 | 1.0098
816.6 | 49.5 | 1.0098
816.7 | 49.5 | 1.0096
816.8 | 49.5 | 1.0096
816.9 | 49.5 | 1.0096
817 | 49.5 | 1.0096
817.1 | 49.5 | 1.0096
817.2 | 49.5 | 1.0096
817.3 | 49.5 | 1.0096
817.4 | 49.5 | 1.0096
817.5 | 49.5 | 1.0096
817.6 | 49.5 | 1.0096
817.7 | 49.5 | 1.0096
817.8 | 49.5 | 1.0096
817.9 | 49.5 | 1.0096
818 | 49.5 | 1.0096
818.1 | 49.5 | 1.0096
818.2 | 49.5 | 1.0096
818.3 | 49.5 | 1.0096
818.4 | 49.5 | 1.0096
818.5 | 49.5 | 1.0096
818.6 | 49.5 | 1.0096
818.7 | 49.5 | 1.0094
818.8 | 49.5 | 1.0094
818.9 | 49.5 | 1.0094
819 | 49.5 | 1.0094
819.1 | 49.5 | 1.0094
819.2 | 49.5 | 1.0096
819.3 | 49.5 | 1.0096
819.4 | 49.5 | 1.0096
819.5 | 49.5 | 1.0096
819.6 | 49.5 | 1.0096
819.7 | 49.5 | 1.0096
819.8 | 49.5 | 1.0096
819.9 | 49.5 | 1.0096
820 | 49.5 | 1.0096
820.1 | 49.5 | 1.0096
820.2 | 49.5 | 1.0096
820.3 | 49.5 | 1.0096
820.4 | 49.5 | 1.0098
820.5 | 49.5 | 1.0098
820.6 | 49.5 | 1.0098
820.7 | 49.5 | 1.0098
820.8 | 49.5 | 1.0098
820.9 | 49.5 | 1.0098
821 | 49.5 | 1.0098
821.1 | 49.5 | 1.0098
821.2 | 49.5 | 1.0098
821.3 | 49.5 | 1.0098
821.4 | 49.5 | 1.0098
821.5 | 49.5 | 1.0096
821.6 | 49.5 | 1.0096
821.7 | 49.5 | 1.0096
821.8 | 49.5 | 1.0096
821.9 | 49.5 | 1.0096
822 | 49.5 | 1.0096
822.1 | 49.5 | 1.0096
822.2 | 49.5 | 1.0096
822.3 | 49.5 | 1.0096
822.4 | 49.5 | 1.0098
822.5 | 49.5 | 1.0098
822.6 | 49.5 | 1.0098
822.7 | 49.5 | 1.0098
822.8 | 49.5 | 1.0098
822.9 | 49.5 | 1.0098
823 | 49.5 | 1.0098
823.1 | 49.5 | 1.0098
823.2 | 49.5 | 1.0098
823.3 | 49.5 | 1.0098
823.4 | 49.5 | 1.0096
823.5 | 49.5 | 1.0096
823.6 | 49.5 | 1.0096
823.7 | 49.5 | 1.0096
823.8 | 49.5 | 1.0096
823.9 | 49.5 | 1.0096
824 | 49.5 | 1.0096
824.1 | 49.5 | 1.0096
824.2 | 49.5 | 1.0096
824.3 | 49.5 | 1.0096
824.4 | 49.5 | 1.0096
824.5 | 49.5 | 1.0096
824.6 | 49.5 | 1.0096
824.7 | 49.5 | 1.0096
824.8 | 49.5 | 1.0096
824.9 | 49.5 | 1.0096
825 | 49.5 | 1.0096
825.1 | 49.5 | 1.0096
825.2 | 49.5 | 1.0096
825.3 | 49.5 | 1.0096
825.4 | 49.5 | 1.0096
825.5 | 49.5 | 1.0096
825.6 | 49.5 | 1.0096
825.7 | 49.5 | 1.0096
825.8 | 49.5 | 1.0094
825.9 | 49.5 | 1.0094
826 | 49.5 | 1.0094
826.1 | 49.5 | 1.0094
826.2 | 49.5 | 1.0094
826.3 | 49.5 | 1.0094
826.4 | 49.5 | 1.0094
826.5 | 49.5 | 1.0094
826.6 | 49.5 | 1.0094
826.7 | 49.5 | 1.0094
826.8 | 49.5 | 1.0094
826.9 | 49.5 | 1.0094
827 | 49.5 | 1.0094
827.1 | 49.5 | 1.0094
827.2 | 49.5 | 1.0094
827.3 | 49.5 | 1.0096
827.4 | 49.5 | 1.0096
827.5 | 49.5 | 1.0096
827.6 | 49.5 | 1.0096
827.7 | 49.5 | 1.0096
827.8 | 49.5 | 1.0096
827.9 | 49.5 | 1.0096
828 | 49.5 | 1.0096
828.1 | 49.5 | 1.0096
828.2 | 49.5 | 1.0098
828.3 | 49.5 | 1.0098
828.4 | 49.5 | 1.0098
828.5 | 49.5 | 1.0098
828.6 | 49.5 | 1.0098
828.7 | 49.5 | 1.0098
828.8 | 49.5 | 1.0098
828.9 | 49.5 | 1.0098
829 | 49.5 | 1.0098
829.1 | 49.5 | 1.0098
829.2 | 49.5 | 1.0098
829.3 | 49.5 | 1.0098
829.4 | 49.5 | 1.0098
829.5 | 49.5 | 1.0098
829.6 | 49.5 | 1.0098
829.7 | 49.5 | 1.0098
829.8 | 49.5 | 1.0098
829.9 | 49.5 | 1.0098
830 | 49.5 | 1.0098
830.1 | 49.5 | 1.0098
830.2 | 49.5 | 1.0098
830.3 | 49.5 | 1.0098
830.4 | 49.5 | 1.0098
830.5 | 49.5 | 1.0098
830.6 | 49.5 | 1.0098
830.7 | 49.5 | 1.0098
830.8 | 49.5 | 1.0098
830.9 | 49.5 | 1.0098
831 | 49.5 | 1.0098
831.1 | 49.5 | 1.0098
831.2 | 49.5 | 1.0098
831.3 | 49.5 | 1.0098
831.4 | 49.5 | 1.0098
831.5 | 49.5 | 1.0096
831.6 | 49.5 | 1.0096
831.7 | 49.5 | 1.0096
831.8 | 49.5 | 1.0096
831.9 | 49.5 | 1.0096
832 | 49.5 | 1.0096
832.1 | 49.5 | 1.0096
832.2 | 49.5 | 1.0096
832.3 | 49.5 | 1.0096
832.4 | 49.5 | 1.0096
832.5 | 49.5 | 1.0096
832.6 | 49.5 | 1.0096
832.7 | 49.5 | 1.0096
832.8 | 49.5 | 1.0096
832.9 | 49.5 | 1.0096
833 | 49.5 | 1.0096
833.1 | 49.5 | 1.0096
833.2 | 49.5 | 1.0096
833.3 | 49.5 | 1.0096
833.4 | 49.5 | 1.0096
833.5 | 49.5 | 1.0096
833.6 | 49.5 | 1.0096
833.7 | 49.5 | 1.0096
833.8 | 49.5 | 1.0096
833.9 | 49.5 | 1.0096
834 | 49.5 | 1.0096
834.1 | 49.5 | 1.0096
834.2 | 49.5 | 1.0096
834.3 | 49.5 | 1.0096
834.4 | 49.5 | 1.0096
834.5 | 49.5 | 1.0096
834.6 | 49.5 | 1.0096
834.7 | 49.5 | 1.0096
834.8 | 49.5 | 1.0096
834.9 | 49.5 | 1.0096
835 | 49.5 | 1.0096
835.1 | 49.5 | 1.0096
835.2 | 49.5 | 1.0096
835.3 | 49.5 | 1.0096
835.4 | 49.5 | 1.0096
835.5 | 49.5 | 1.0096
835.6 | 49.5 | 1.0096
835.7 | 49.5 | 1.0096
835.8 | 49.5 | 1.0096
835.9 | 49.5 | 1.0096
836 | 49.5 | 1.0096
836.1 | 49.5 | 1.0096
836.2 | 49.5 | 1.0096
836.3 | 49.5 | 1.0096
836.4 | 49.5 | 1.0096
836.5 | 49.5 | 1.0096
836.6 | 49.5 | 1.0096
836.7 | 49.5 | 1.0096
836.8 | 49.5 | 1.0096
836.9 | 49.5 | 1.0096
837 | 49.5 | 1.0096
837.1 | 49.5 | 1.0096
837.2 | 49.5 | 1.0096
837.3 | 49.5 | 1.0096
837.4 | 49.5 | 1.0096
837.5 | 49.5 | 1.0096
837.6 | 49.5 | 1.0096
837.7 | 49.5 | 1.0096
837.8 | 49.5 | 1.0096
837.9 | 49.5 | 1.0096
838 | 49.5 | 1.0096
838.1 | 49.5 | 1.0096
838.2 | 49.5 | 1.0096
838.3 | 49.5 | 1.0096
838.4 | 49.5 | 1.0096
838.5 | 49.5 | 1.0096
838.6 | 49.5 | 1.0096
838.7 | 49.5 | 1.0096
838.8 | 49.5 | 1.0096
838.9 | 49.5 | 1.0096
839 | 49.5 | 1.0096
839.1 | 49.5 | 1.0096
839.2 | 49.5 | 1.0096
839.3 | 49.5 | 1.0096
839.4 | 49.5 | 1.0096
839.5 | 49.5 | 1.0096
839.6 | 49.5 | 1.0096
839.7 | 49.5 | 1.0096
839.8 | 49.5 | 1.0096
839.9 | 49.5 | 1.0096
840 | 49.5 | 1.0096
840.1 | 49.5 | 1.0096
840.2 | 49.5 | 1.0096
840.3 | 49.5 | 1.0096
840.4 | 49.5 | 1.0096
840.5 | 49.5 | 1.0096
840.6 | 49.5 | 1.0096
840.7 | 49.5 | 1.0096
840.8 | 49.5 | 1.0096
840.9 | 49.5 | 1.0096
841 | 49.5 | 1.0096
841.1 | 49.5 | 1.0096
841.2 | 49.5 | 1.0096
841.3 | 49.5 | 1.0096
841.4 | 49.5 | 1.0096
841.5 | 49.5 | 1.0096
841.6 | 49.5 | 1.0096
841.7 | 49.5 | 1.0096
841.8 | 49.5 | 1.0096
841.9 | 49.5 | 1.0096
842 | 49.5 | 1.0096
842.1 | 49.5 | 1.0096
842.2 | 49.5 | 1.0096
842.3 | 49.5 | 1.0096
842.4 | 49.5 | 1.0096
842.5 | 49.5 | 1.0096
842.6 | 49.5 | 1.0096
842.7 | 49.5 | 1.0096
842.8 | 49.5 | 1.0096
842.9 | 49.5 | 1.0096
843 | 49.5 | 1.0096
843.1 | 49.5 | 1.0096
843.2 | 49.5 | 1.0096
843.3 | 49.5 | 1.0096
843.4 | 49.5 | 1.0096
843.5 | 49.5 | 1.0096
843.6 | 49.5 | 1.0096
843.7 | 49.5 | 1.0096
843.8 | 49.5 | 1.0096
843.9 | 49.5 | 1.0096
844 | 49.5 | 1.0096
844.1 | 49.5 | 1.0096
844.2 | 49.5 | 1.0096
844.3 | 49.5 | 1.0096
844.4 | 49.5 | 1.0096
844.5 | 49.5 | 1.0096
844.6 | 49.5 | 1.0096
844.7 | 49.5 | 1.0096
844.8 | 49.5 | 1.0096
844.9 | 49.5 | 1.0096
845 | 49.5 | 1.0096
845.1 | 49.5 | 1.0096
845.2 | 49.5 | 1.0096
845.3 | 49.5 | 1.0096
845.4 | 49.5 | 1.0096
845.5 | 49.5 | 1.0096
845.6 | 49.5 | 1.0096
845.7 | 49.5 | 1.0096
845.8 | 49.5 | 1.0096
845.9 | 49.5 | 1.0096
846 | 49.5 | 1.0096
846.1 | 49.5 | 1.0096
846.2 | 49.5 | 1.0096
846.3 | 49.5 | 1.0096
846.4 | 49.5 | 1.0096
846.5 | 49.5 | 1.0096
846.6 | 49.5 | 1.0096
846.7 | 49.5 | 1.0096
846.8 | 49.5 | 1.0096
846.9 | 49.5 | 1.0096
847 | 49.5 | 1.0096
847.1 | 49.5 | 1.0096
847.2 | 49.5 | 1.0096
847.3 | 49.5 | 1.0096
847.4 | 49.5 | 1.0096
847.5 | 49.5 | 1.0096
847.6 | 49.5 | 1.0096
847.7 | 49.5 | 1.0096
847.8 | 49.5 | 1.0096
847.9 | 49.5 | 1.0096
848 | 49.5 | 1.0096
848.1 | 49.5 | 1.0096
848.2 | 49.5 | 1.0096
848.3 | 49.5 | 1.0096
848.4 | 49.5 | 1.0096
848.5 | 49.5 | 1.0096
848.6 | 49.5 | 1.0096
848.7 | 49.5 | 1.0096
848.8 | 49.5 | 1.0096
848.9 | 49.5 | 1.0096
849 | 49.5 | 1.0096
849.1 | 49.5 | 1.0096
849.2 | 49.5 | 1.0096
849.3 | 49.5 | 1.0096
849.4 | 49.5 | 1.0096
849.5 | 49.5 | 1.0096
849.6 | 49.5 | 1.0096
849.7 | 49.5 | 1.0096
849.8 | 49.5 | 1.0096
849.9 | 49.5 | 1.0096
850 | 49.5 | 1.0096
850.1 | 49.5 | 1.0096
850.2 | 49.5 | 1.0096
850.3 | 49.5 | 1.0096
850.4 | 49.5 | 1.0096
850.5 | 49.5 | 1.0096
850.6 | 49.5 | 1.0096
850.7 | 49.5 | 1.0096
850.8 | 49.5 | 1.0096
850.9 | 49.5 | 1.0096
851 | 49.5 | 1.0096
851.1 | 49.5 | 1.0096
851.2 | 49.5 | 1.0096
851.3 | 49.5 | 1.0096
851.4 | 49.5 | 1.0096
851.5 | 49.5 | 1.0096
851.6 | 49.5 | 1.0096
851.7 | 49.5 | 1.0096
851.8 | 49.5 | 1.0096
851.9 | 49.5 | 1.0096
852 | 49.5 | 1.0096
852.1 | 49.5 | 1.0096
852.2 | 49.5 | 1.0096
852.3 | 49.5 | 1.0096
852.4 | 49.5 | 1.0096
852.5 | 49.5 | 1.0096
852.6 | 49.5 | 1.0096
852.7 | 49.5 | 1.0096
852.8 | 49.5 | 1.0096
852.9 | 49.5 | 1.0096
853 | 49.5 | 1.0096
853.1 | 49.5 | 1.0096
853.2 | 49.5 | 1.0096
853.3 | 49.5 | 1.0096
853.4 | 49.5 | 1.0096
853.5 | 49.5 | 1.0096
853.6 | 49.5 | 1.0096
853.7 | 49.5 | 1.0096
853.8 | 49.5 | 1.0096
853.9 | 49.5 | 1.0096
854 | 49.5 | 1.0096
854.1 | 49.5 | 1.0096
854.2 | 49.5 | 1.0096
854.3 | 49.5 | 1.0096
854.4 | 49.5 | 1.0096
854.5 | 49.5 | 1.0096
854.6 | 49.5 | 1.0096
854.7 | 49.5 | 1.0096
854.8 | 49.5 | 1.0096
854.9 | 49.5 | 1.0096
855 | 49.5 | 1.0096
855.1 | 49.5 | 1.0096
855.2 | 49.5 | 1.0096
855.3 | 49.5 | 1.0096
855.4 | 49.5 | 1.0096
855.5 | 49.5 | 1.0094
855.6 | 49.5 | 1.0094
855.7 | 49.5 | 1.0094
855.8 | 49.5 | 1.0094
855.9 | 49.5 | 1.0094
856 | 49.5 | 1.0094
856.1 | 49.5 | 1.0094
856.2 | 49.5 | 1.0094
856.3 | 49.5 | 1.0094
856.4 | 49.5 | 1.0094
856.5 | 49.5 | 1.0096
856.6 | 49.5 | 1.0098
856.7 | 49.5 | 1.0098
856.8 | 49.5 | 1.0098
856.9 | 49.5 | 1.0098
857 | 49.5 | 1.0098
857.1 | 49.5 | 1.0098
857.2 | 49.5 | 1.0098
857.3 | 49.5 | 1.0098
857.4 | 49.5 | 1.0098
857.5 | 49.5 | 1.0098
857.6 | 49.5 | 1.0098
857.7 | 49.5 | 1.0098
857.8 | 49.5 | 1.0098
857.9 | 49.5 | 1.0098
858 | 49.5 | 1.0098
858.1 | 49.5 | 1.0098
858.2 | 49.5 | 1.0098
858.3 | 49.5 | 1.0098
858.4 | 49.5 | 1.0098
858.5 | 49.5 | 1.0098
858.6 | 49.5 | 1.0098
858.7 | 49.5 | 1.0098
858.8 | 49.5 | 1.0098
858.9 | 49.5 | 1.0098
859 | 49.5 | 1.0098
859.1 | 49.5 | 1.0098
859.2 | 49.5 | 1.0098
859.3 | 49.5 | 1.0098
859.4 | 49.5 | 1.0098
859.5 | 49.5 | 1.0098
859.6 | 49.5 | 1.0098
859.7 | 49.5 | 1.0098
859.8 | 49.5 | 1.0098
859.9 | 49.5 | 1.0098
860 | 49.5 | 1.0098
860.1 | 49.5 | 1.0096
860.2 | 49.5 | 1.0096
860.3 | 49.5 | 1.0096
860.4 | 49.5 | 1.0096
860.5 | 49.5 | 1.0096
860.6 | 49.5 | 1.0096
860.7 | 49.5 | 1.0096
860.8 | 49.5 | 1.0096
860.9 | 49.5 | 1.0096
861 | 49.5 | 1.0096
861.1 | 49.5 | 1.0096
861.2 | 49.5 | 1.0096
861.3 | 49.5 | 1.0096
861.4 | 49.5 | 1.0096
861.5 | 49.5 | 1.0096
861.6 | 49.5 | 1.0096
861.7 | 49.5 | 1.0096
861.8 | 49.5 | 1.0096
861.9 | 49.5 | 1.0096
862 | 49.5 | 1.0096
862.1 | 49.5 | 1.0096
862.2 | 49.5 | 1.0096
862.3 | 49.5 | 1.0096
862.4 | 49.5 | 1.0096
862.5 | 49.5 | 1.0096
862.6 | 49.5 | 1.0096
862.7 | 49.5 | 1.0096
862.8 | 49.5 | 1.0096
862.9 | 49.5 | 1.0096
863 | 49.5 | 1.0096
863.1 | 49.5 | 1.0096
863.2 | 49.5 | 1.0096
863.3 | 49.5 | 1.0096
863.4 | 49.5 | 1.0096
863.5 | 49.5 | 1.0096
863.6 | 49.5 | 1.0096
863.7 | 49.5 | 1.0096
863.8 | 49.5 | 1.0096
863.9 | 49.5 | 1.0096
864 | 49.5 | 1.0096
864.1 | 49.5 | 1.0096
864.2 | 49.5 | 1.0096
864.3 | 49.5 | 1.0096
864.4 | 49.5 | 1.0096
864.5 | 49.5 | 1.0096
864.6 | 49.5 | 1.0096
864.7 | 49.5 | 1.0096
864.8 | 49.5 | 1.0098
864.9 | 49.5 | 1.0098
865 | 49.5 | 1.0098
865.1 | 49.5 | 1.0098
865.2 | 49.5 | 1.0098
865.3 | 49.5 | 1.0098
865.4 | 49.5 | 1.0098
865.5 | 49.5 | 1.0098
865.6 | 49.5 | 1.0098
865.7 | 49.5 | 1.0098
865.8 | 49.5 | 1.0098
865.9 | 49.5 | 1.0096
866 | 49.5 | 1.0096
866.1 | 49.5 | 1.0096
866.2 | 49.5 | 1.0096
866.3 | 49.5 | 1.0096
866.4 | 49.5 | 1.0096
866.5 | 49.5 | 1.0096
866.6 | 49.5 | 1.0096
866.7 | 49.5 | 1.0096
866.8 | 49.5 | 1.0096
866.9 | 49.5 | 1.0096
867 | 49.5 | 1.0096
867.1 | 49.5 | 1.0096
867.2 | 49.5 | 1.0096
867.3 | 49.5 | 1.0096
867.4 | 49.5 | 1.0096
867.5 | 49.5 | 1.0096
867.6 | 49.5 | 1.0096
867.7 | 49.5 | 1.0096
867.8 | 49.5 | 1.0096
867.9 | 49.5 | 1.0096
868 | 49.5 | 1.0096
868.1 | 49.5 | 1.0096
868.2 | 49.5 | 1.0096
868.3 | 49.5 | 1.0096
868.4 | 49.5 | 1.0098
868.5 | 49.5 | 1.0098
868.6 | 49.5 | 1.0098
868.7 | 49.5 | 1.0098
868.8 | 49.5 | 1.0098
868.9 | 49.5 | 1.0098
869 | 49.5 | 1.0098
869.1 | 49.5 | 1.0098
869.2 | 49.5 | 1.0098
869.3 | 49.5 | 1.0098
869.4 | 49.5 | 1.0098
869.5 | 49.5 | 1.0096
869.6 | 49.5 | 1.0096
869.7 | 49.5 | 1.0096
869.8 | 49.5 | 1.0096
869.9 | 49.5 | 1.0096
870 | 49.5 | 1.0096
870.1 | 49.5 | 1.0096
870.2 | 49.5 | 1.0096
870.3 | 49.5 | 1.0096
870.4 | 49.5 | 1.0096
870.5 | 49.5 | 1.0096
870.6 | 49.5 | 1.0096
870.7 | 49.5 | 1.0096
870.8 | 49.5 | 1.0096
870.9 | 49.5 | 1.0096
871 | 49.5 | 1.0096
871.1 | 49.5 | 1.0096
871.2 | 49.5 | 1.0096
871.3 | 49.5 | 1.0096
871.4 | 49.5 | 1.0096
871.5 | 49.5 | 1.0096
871.6 | 49.5 | 1.0096
871.7 | 49.5 | 1.0096
871.8 | 49.5 | 1.0096
871.9 | 49.5 | 1.0096
872 | 49.5 | 1.0096
872.1 | 49.5 | 1.0096
872.2 | 49.5 | 1.0096
872.3 | 49.5 | 1.0096
872.4 | 49.5 | 1.0096
872.5 | 49.5 | 1.0096
872.6 | 49.5 | 1.0096
872.7 | 49.5 | 1.0096
872.8 | 49.5 | 1.0096
872.9 | 49.5 | 1.0096
873 | 49.5 | 1.0096
873.1 | 49.5 | 1.0096
873.2 | 49.5 | 1.0096
873.3 | 49.5 | 1.0096
873.4 | 49.5 | 1.0096
873.5 | 49.5 | 1.0096
873.6 | 49.5 | 1.0096
873.7 | 49.5 | 1.0096
873.8 | 49.5 | 1.0096
873.9 | 49.5 | 1.0096
874 | 49.5 | 1.0096
874.1 | 49.5 | 1.0096
874.2 | 49.5 | 1.0096
874.3 | 49.5 | 1.0096
874.4 | 49.5 | 1.0096
874.5 | 49.5 | 1.0096
874.6 | 49.5 | 1.0096
874.7 | 49.5 | 1.0096
874.8 | 49.5 | 1.0096
874.9 | 49.5 | 1.0096
875 | 49.5 | 1.0096
875.1 | 49.5 | 1.0096
875.2 | 49.5 | 1.0096
875.3 | 49.5 | 1.0096
875.4 | 49.5 | 1.0096
875.5 | 49.5 | 1.0096
875.6 | 49.5 | 1.0096
875.7 | 49.5 | 1.0096
875.8 | 49.5 | 1.0096
875.9 | 49.5 | 1.0096
876 | 49.5 | 1.0096
876.1 | 49.5 | 1.0096
876.2 | 49.5 | 1.0096
876.3 | 49.5 | 1.0096
876.4 | 49.5 | 1.0096
876.5 | 49.5 | 1.0096
876.6 | 49.5 | 1.0096
876.7 | 49.5 | 1.0096
876.8 | 49.5 | 1.0096
876.9 | 49.5 | 1.0096
877 | 49.5 | 1.0096
877.1 | 49.5 | 1.0096
877.2 | 49.5 | 1.0096
877.3 | 49.5 | 1.0096
877.4 | 49.5 | 1.0096
877.5 | 49.5 | 1.0096
877.6 | 49.5 | 1.0096
877.7 | 49.5 | 1.0096
877.8 | 49.5 | 1.0096
877.9 | 49.5 | 1.0096
878 | 49.5 | 1.0096
878.1 | 49.5 | 1.0096
878.2 | 49.5 | 1.0096
878.3 | 49.5 | 1.0096
878.4 | 49.5 | 1.0096
878.5 | 49.5 | 1.0096
878.6 | 49.5 | 1.0096
878.7 | 49.5 | 1.0096
878.8 | 49.5 | 1.0096
878.9 | 49.5 | 1.0096
879 | 49.5 | 1.0096
879.1 | 49.5 | 1.0096
879.2 | 49.5 | 1.0096
879.3 | 49.5 | 1.0096
879.4 | 49.5 | 1.0096
879.5 | 49.5 | 1.0096
879.6 | 49.5 | 1.0096
879.7 | 49.5 | 1.0096
879.8 | 49.5 | 1.0096
879.9 | 49.5 | 1.0096
880 | 49.5 | 1.0096
880.1 | 49.5 | 1.0096
880.2 | 49.5 | 1.0096
880.3 | 49.5 | 1.0096
880.4 | 49.5 | 1.0096
880.5 | 49.5 | 1.0096
880.6 | 49.5 | 1.0096
880.7 | 49.5 | 1.0096
880.8 | 49.5 | 1.0096
880.9 | 49.5 | 1.0096
881 | 49.5 | 1.0096
881.1 | 49.5 | 1.0096
881.2 | 49.5 | 1.0096
881.3 | 49.5 | 1.0096
881.4 | 49.5 | 1.0096
881.5 | 49.5 | 1.0096
881.6 | 49.5 | 1.0096
881.7 | 49.5 | 1.0096
881.8 | 49.5 | 1.0096
881.9 | 49.5 | 1.0096
882 | 49.5 | 1.0096
882.1 | 49.5 | 1.0096
882.2 | 49.5 | 1.0096
882.3 | 49.5 | 1.0096
882.4 | 49.5 | 1.0096
882.5 | 49.5 | 1.0096
882.6 | 49.5 | 1.0096
882.7 | 49.5 | 1.0096
882.8 | 49.5 | 1.0096
882.9 | 49.5 | 1.0096
883 | 49.5 | 1.0096
883.1 | 49.5 | 1.0096
883.2 | 49.5 | 1.0096
883.3 | 49.5 | 1.0096
883.4 | 49.5 | 1.0096
883.5 | 49.5 | 1.0096
883.6 | 49.5 | 1.0096
883.7 | 49.5 | 1.0096
883.8 | 49.5 | 1.0096
883.9 | 49.5 | 1.0096
884 | 49.5 | 1.0096
884.1 | 49.5 | 1.0096
884.2 | 49.5 | 1.0096
884.3 | 49.5 | 1.0096
884.4 | 49.5 | 1.0096
884.5 | 49.5 | 1.0096
884.6 | 49.5 | 1.0096
884.7 | 49.5 | 1.0096
884.8 | 49.5 | 1.0096
884.9 | 49.5 | 1.0096
885 | 49.5 | 1.0096
885.1 | 49.5 | 1.0096
885.2 | 49.5 | 1.0096
885.3 | 49.5 | 1.0096
885.4 | 49.5 | 1.0096
885.5 | 49.5 | 1.0096
885.6 | 49.5 | 1.0096
885.7 | 49.5 | 1.0096
885.8 | 49.5 | 1.0096
885.9 | 49.5 | 1.0096
886 | 49.5 | 1.0096
886.1 | 49.5 | 1.0096
886.2 | 49.5 | 1.0096
886.3 | 49.5 | 1.0096
886.4 | 49.5 | 1.0096
886.5 | 49.5 | 1.0096
886.6 | 49.5 | 1.0096
886.7 | 49.5 | 1.0096
886.8 | 49.5 | 1.0096
886.9 | 49.5 | 1.0096
887 | 49.5 | 1.0096
887.1 | 49.5 | 1.0096
887.2 | 49.5 | 1.0096
887.3 | 49.5 | 1.0096
887.4 | 49.5 | 1.0096
887.5 | 49.5 | 1.0096
887.6 | 49.5 | 1.0096
887.7 | 49.5 | 1.0096
887.8 | 49.5 | 1.0096
887.9 | 49.5 | 1.0096
888 | 49.5 | 1.0096
888.1 | 49.5 | 1.0096
888.2 | 49.5 | 1.0096
888.3 | 49.5 | 1.0096
888.4 | 49.5 | 1.0096
888.5 | 49.5 | 1.0096
888.6 | 49.5 | 1.0096
888.7 | 49.5 | 1.0096
888.8 | 49.5 | 1.0096
888.9 | 49.5 | 1.0096
889 | 49.5 | 1.0096
889.1 | 49.5 | 1.0096
889.2 | 49.5 | 1.0096
889.3 | 49.5 | 1.0096
889.4 | 49.5 | 1.0096
889.5 | 49.5 | 1.0096
889.6 | 49.5 | 1.0096
889.7 | 49.5 | 1.0096
889.8 | 49.5 | 1.0096
889.9 | 49.5 | 1.0096
890 | 49.5 | 1.0096
890.1 | 49.5 | 1.0096
890.2 | 49.5 | 1.0096
890.3 | 49.5 | 1.0096
890.4 | 49.5 | 1.0096
890.5 | 49.5 | 1.0096
890.6 | 49.5 | 1.0096
890.7 | 49.5 | 1.0096
890.8 | 49.5 | 1.0096
890.9 | 49.5 | 1.0096
891 | 49.5 | 1.0096
891.1 | 49.5 | 1.0096
891.2 | 49.5 | 1.0096
891.3 | 49.5 | 1.0096
891.4 | 49.5 | 1.0096
891.5 | 49.5 | 1.0096
891.6 | 49.5 | 1.0096
891.7 | 49.5 | 1.0096
891.8 | 49.5 | 1.0096
891.9 | 49.5 | 1.0096
892 | 49.5 | 1.0096
892.1 | 49.5 | 1.0096
892.2 | 49.5 | 1.0096
892.3 | 49.5 | 1.0096
892.4 | 49.5 | 1.0096
892.5 | 49.5 | 1.0096
892.6 | 49.5 | 1.0096
892.7 | 49.5 | 1.0096
892.8 | 49.5 | 1.0096
892.9 | 49.5 | 1.0096
893 | 49.5 | 1.0096
893.1 | 49.5 | 1.0096
893.2 | 49.5 | 1.0096
893.3 | 49.5 | 1.0096
893.4 | 49.5 | 1.0096
893.5 | 49.5 | 1.0096
893.6 | 49.5 | 1.0096
893.7 | 49.5 | 1.0096
893.8 | 49.5 | 1.0096
893.9 | 49.5 | 1.0096
894 | 49.5 | 1.0096
894.1 | 49.5 | 1.0096
894.2 | 49.5 | 1.0096
894.3 | 49.5 | 1.0096
894.4 | 49.5 | 1.0096
894.5 | 49.5 | 1.0096
894.6 | 49.5 | 1.0096
894.7 | 49.5 | 1.0096
894.8 | 49.5 | 1.0096
894.9 | 49.5 | 1.0096
895 | 49.5 | 1.0096
895.1 | 49.5 | 1.0096
895.2 | 49.5 | 1.0096
895.3 | 49.5 | 1.0096
895.4 | 49.5 | 1.0096
895.5 | 49.5 | 1.0096
895.6 | 49.5 | 1.0096
895.7 | 49.5 | 1.0096
895.8 | 49.5 | 1.0096
895.9 | 49.5 | 1.0096
896 | 49.5 | 1.0096
896.1 | 49.5 | 1.0096
896.2 | 49.5 | 1.0096
896.3 | 49.5 | 1.0096
896.4 | 49.5 | 1.0096
896.5 | 49.5 | 1.0096
896.6 | 49.5 | 1.0096
896.7 | 49.5 | 1.0096
896.8 | 49.5 | 1.0096
896.9 | 49.5 | 1.0096
897 | 49.5 | 1.0096
897.1 | 49.5 | 1.0096
897.2 | 49.5 | 1.0096
897.3 | 49.5 | 1.0096
897.4 | 49.5 | 1.0096
897.5 | 49.5 | 1.0096
897.6 | 49.5 | 1.0096
897.7 | 49.5 | 1.0096
897.8 | 49.5 | 1.0096
897.9 | 49.5 | 1.0096
898 | 49.5 | 1.0096
898.1 | 49.5 | 1.0096
898.2 | 49.5 | 1.0096
898.3 | 49.5 | 1.0096
898.4 | 49.5 | 1.0096
898.5 | 49.5 | 1.0096
898.6 | 49.5 | 1.0096
898.7 | 49.5 | 1.0096
898.8 | 49.5 | 1.0096
898.9 | 49.5 | 1.0096
899 | 49.5 | 1.0098
899.1 | 49.5 | 1.0098
899.2 | 49.5 | 1.0098
899.3 | 49.5 | 1.0098
899.4 | 49.5 | 1.0098
899.5 | 49.5 | 1.0098
899.6 | 49.5 | 1.0098
899.7 | 49.5 | 1.0098
899.8 | 49.5 | 1.0098
899.9 | 49.5 | 1.0098
900 | 49.5 | 1.0098
900.1 | 49.5 | 1.0098
900.2 | 49.5 | 1.0098
900.3 | 49.5 | 1.0098
900.4 | 49.5 | 1.0098
900.5 | 49.5 | 1.0098
900.6 | 49.5 | 1.0098
900.7 | 49.5 | 1.0098
900.8 | 49.5 | 1.0098
900.9 | 49.5 | 1.0098
901 | 49.5 | 1.0098
901.1 | 49.5 | 1.0098
901.2 | 49.5 | 1.0096
901.3 | 49.5 | 1.0096
901.4 | 49.5 | 1.0096
901.5 | 49.5 | 1.0096
901.6 | 49.5 | 1.0096
901.7 | 49.5 | 1.0096
901.8 | 49.5 | 1.0096
901.9 | 49.5 | 1.0096
902 | 49.5 | 1.0096
902.1 | 49.5 | 1.0096
902.2 | 49.5 | 1.0096
902.3 | 49.5 | 1.0096
902.4 | 49.5 | 1.0096
902.5 | 49.5 | 1.0096
902.6 | 49.5 | 1.0096
902.7 | 49.5 | 1.0096
902.8 | 49.5 | 1.0096
902.9 | 49.5 | 1.0096
903 | 49.5 | 1.0096
903.1 | 49.5 | 1.0096
903.2 | 49.5 | 1.0096
903.3 | 49.5 | 1.0096
903.4 | 49.5 | 1.0096
903.5 | 49.5 | 1.0096
903.6 | 49.5 | 1.0096
903.7 | 49.5 | 1.0096
903.8 | 49.5 | 1.0096
903.9 | 49.5 | 1.0096
904 | 49.5 | 1.0096
904.1 | 49.5 | 1.0096
904.2 | 49.5 | 1.0096
904.3 | 49.5 | 1.0096
904.4 | 49.5 | 1.0096
904.5 | 49.5 | 1.0096
904.6 | 49.5 | 1.0096
904.7 | 49.5 | 1.0096
904.8 | 49.5 | 1.0096
904.9 | 49.5 | 1.0096
905 | 49.5 | 1.0096
905.1 | 49.5 | 1.0096
905.2 | 49.5 | 1.0096
905.3 | 49.5 | 1.0096
905.4 | 49.5 | 1.0096
905.5 | 49.5 | 1.0096
905.6 | 49.5 | 1.0096
905.7 | 49.5 | 1.0096
905.8 | 49.5 | 1.0096
905.9 | 49.5 | 1.0096
906 | 49.5 | 1.0096
906.1 | 49.5 | 1.0096
906.2 | 49.5 | 1.0096
906.3 | 49.5 | 1.0096
906.4 | 49.5 | 1.0096
906.5 | 49.5 | 1.0096
906.6 | 49.5 | 1.0096
906.7 | 49.5 | 1.0096
906.8 | 49.5 | 1.0096
906.9 | 49.5 | 1.0096
907 | 49.5 | 1.0096
907.1 | 49.5 | 1.0096
907.2 | 49.5 | 1.0096
907.3 | 49.5 | 1.0096
907.4 | 49.5 | 1.0096
907.5 | 49.5 | 1.0096
907.6 | 49.5 | 1.0096
907.7 | 49.5 | 1.0096
907.8 | 49.5 | 1.0096
907.9 | 49.5 | 1.0096
908 | 49.5 | 1.0096
908.1 | 49.5 | 1.0096
908.2 | 49.5 | 1.0096
908.3 | 49.5 | 1.0096
908.4 | 49.5 | 1.0096
908.5 | 49.5 | 1.0096
908.6 | 49.5 | 1.0096
908.7 | 49.5 | 1.0096
908.8 | 49.5 | 1.0096
908.9 | 49.5 | 1.0096
909 | 49.5 | 1.0096
909.1 | 49.5 | 1.0096
909.2 | 49.5 | 1.0096
909.3 | 49.5 | 1.0096
909.4 | 49.5 | 1.0096
909.5 | 49.5 | 1.0096
909.6 | 49.5 | 1.0096
909.7 | 49.5 | 1.0096
909.8 | 49.5 | 1.0096
909.9 | 49.5 | 1.0096
910 | 49.5 | 1.0096
910.1 | 49.5 | 1.0096
910.2 | 49.5 | 1.0096
910.3 | 49.5 | 1.0096
910.4 | 49.5 | 1.0096
910.5 | 49.5 | 1.0096
910.6 | 49.5 | 1.0096
910.7 | 49.5 | 1.0098
910.8 | 49.5 | 1.0098
910.9 | 49.5 | 1.0098
911 | 49.5 | 1.0098
911.1 | 49.5 | 1.0098
911.2 | 49.5 | 1.0098
911.3 | 49.5 | 1.0098
911.4 | 49.5 | 1.0098
911.5 | 49.5 | 1.0098
911.6 | 49.5 | 1.0098
911.7 | 49.5 | 1.0098
911.8 | 49.5 | 1.0098
911.9 | 49.5 | 1.0096
912 | 49.5 | 1.0096
912.1 | 49.5 | 1.0096
912.2 | 49.5 | 1.0096
912.3 | 49.5 | 1.0096
912.4 | 49.5 | 1.0096
912.5 | 49.5 | 1.0096
912.6 | 49.5 | 1.0096
912.7 | 49.5 | 1.0096
912.8 | 49.5 | 1.0096
912.9 | 49.5 | 1.0096
913 | 49.5 | 1.0096
913.1 | 49.5 | 1.0096
913.2 | 49.5 | 1.0096
913.3 | 49.5 | 1.0096
913.4 | 49.5 | 1.0096
913.5 | 49.5 | 1.0096
913.6 | 49.5 | 1.0096
913.7 | 49.5 | 1.0096
913.8 | 49.5 | 1.0096
913.9 | 49.5 | 1.0096
914 | 49.5 | 1.0096
914.1 | 49.5 | 1.0096
914.2 | 49.5 | 1.0096
914.3 | 49.5 | 1.0096
914.4 | 49.5 | 1.0096
914.5 | 49.5 | 1.0096
914.6 | 49.5 | 1.0096
914.7 | 49.5 | 1.0096
914.8 | 49.5 | 1.0096
914.9 | 49.5 | 1.0096
915 | 49.5 | 1.0096
915.1 | 49.5 | 1.0096
915.2 | 49.5 | 1.0096
915.3 | 49.5 | 1.0096
915.4 | 49.5 | 1.0096
915.5 | 49.5 | 1.0096
915.6 | 49.5 | 1.0096
915.7 | 49.5 | 1.0096
915.8 | 49.5 | 1.0096
915.9 | 49.5 | 1.0096
916 | 49.5 | 1.0096
916.1 | 49.5 | 1.0096
916.2 | 49.5 | 1.0096
916.3 | 49.5 | 1.0096
916.4 | 49.5 | 1.0096
916.5 | 49.5 | 1.0098
916.6 | 49.5 | 1.0098
916.7 | 49.5 | 1.0098
916.8 | 49.5 | 1.0098
916.9 | 49.5 | 1.0098
917 | 49.5 | 1.0098
917.1 | 49.5 | 1.0098
917.2 | 49.5 | 1.0098
917.3 | 49.5 | 1.0098
917.4 | 49.5 | 1.0098
917.5 | 49.5 | 1.0098
917.6 | 49.5 | 1.0098
917.7 | 49.5 | 1.0098
917.8 | 49.5 | 1.0096
917.9 | 49.5 | 1.0096
918 | 49.5 | 1.0096
918.1 | 49.5 | 1.0096
918.2 | 49.5 | 1.0096
918.3 | 49.5 | 1.0096
918.4 | 49.5 | 1.0096
918.5 | 49.5 | 1.0096
918.6 | 49.5 | 1.0096
918.7 | 49.5 | 1.0096
918.8 | 49.5 | 1.0096
918.9 | 49.5 | 1.0096
919 | 49.5 | 1.0096
919.1 | 49.5 | 1.0096
919.2 | 49.5 | 1.0096
919.3 | 49.5 | 1.0096
919.4 | 49.5 | 1.0096
919.5 | 49.5 | 1.0096
919.6 | 49.5 | 1.0096
919.7 | 49.5 | 1.0096
919.8 | 49.5 | 1.0096
919.9 | 49.5 | 1.0096
920 | 49.5 | 1.0096
920.1 | 49.5 | 1.0096
920.2 | 49.5 | 1.0096
920.3 | 49.5 | 1.0096
920.4 | 49.5 | 1.0096
920.5 | 49.5 | 1.0096
920.6 | 49.5 | 1.0096
920.7 | 49.5 | 1.0096
920.8 | 49.5 | 1.0096
920.9 | 49.5 | 1.0096
921 | 49.5 | 1.0096
921.1 | 49.5 | 1.0096
921.2 | 49.5 | 1.0096
921.3 | 49.5 | 1.0096
921.4 | 49.5 | 1.0096
921.5 | 49.5 | 1.0096
921.6 | 49.5 | 1.0096
921.7 | 49.5 | 1.0096
921.8 | 49.5 | 1.0096
921.9 | 49.5 | 1.0096
922 | 49.5 | 1.0096
922.1 | 49.5 | 1.0096
922.2 | 49.5 | 1.0096
922.3 | 49.5 | 1.0096
922.4 | 49.5 | 1.0096
922.5 | 49.5 | 1.0096
922.6 | 49.5 | 1.0096
922.7 | 49.5 | 1.0096
922.8 | 49.5 | 1.0096
922.9 | 49.5 | 1.0096
923 | 49.5 | 1.0096
923.1 | 49.5 | 1.0096
923.2 | 49.5 | 1.0096
923.3 | 49.5 | 1.0096
923.4 | 49.5 | 1.0096
923.5 | 49.5 | 1.0096
923.6 | 49.5 | 1.0096
923.7 | 49.5 | 1.0096
923.8 | 49.5 | 1.0096
923.9 | 49.5 | 1.0096
924 | 49.5 | 1.0096
924.1 | 49.5 | 1.0096
924.2 | 49.5 | 1.0096
924.3 | 49.5 | 1.0096
924.4 | 49.5 | 1.0096
924.5 | 49.5 | 1.0096
924.6 | 49.5 | 1.0096
924.7 | 49.5 | 1.0096
924.8 | 49.5 | 1.0096
924.9 | 49.5 | 1.0096
925 | 49.5 | 1.0096
925.1 | 49.5 | 1.0096
925.2 | 49.5 | 1.0096
925.3 | 49.5 | 1.0096
925.4 | 49.5 | 1.0096
925.5 | 49.5 | 1.0096
925.6 | 49.5 | 1.0096
925.7 | 49.5 | 1.0096
925.8 | 49.5 | 1.0096
925.9 | 49.5 | 1.0096
926 | 49.5 | 1.0096
926.1 | 49.5 | 1.0096
926.2 | 49.5 | 1.0096
926.3 | 49.5 | 1.0096
926.4 | 49.5 | 1.0096
926.5 | 49.5 | 1.0096
926.6 | 49.5 | 1.0096
926.7 | 49.5 | 1.0096
926.8 | 49.5 | 1.0096
926.9 | 49.5 | 1.0096
927 | 49.5 | 1.0096
927.1 | 49.5 | 1.0096
927.2 | 49.5 | 1.0096
927.3 | 49.5 | 1.0096
927.4 | 49.5 | 1.0096
927.5 | 49.5 | 1.0096
927.6 | 49.5 | 1.0096
927.7 | 49.5 | 1.0096
927.8 | 49.5 | 1.0096
927.9 | 49.5 | 1.0096
928 | 49.5 | 1.0096
928.1 | 49.5 | 1.0096
928.2 | 49.5 | 1.0096
928.3 | 49.5 | 1.0096
928.4 | 49.5 | 1.0096
928.5 | 49.5 | 1.0096
928.6 | 49.5 | 1.0096
928.7 | 49.5 | 1.0096
928.8 | 49.5 | 1.0096
928.9 | 49.5 | 1.0096
929 | 49.5 | 1.0096
929.1 | 49.5 | 1.0096
929.2 | 49.5 | 1.0096
929.3 | 49.5 | 1.0096
929.4 | 49.5 | 1.0096
929.5 | 49.5 | 1.0096
929.6 | 49.5 | 1.0096
929.7 | 49.5 | 1.0096
929.8 | 49.5 | 1.0096
929.9 | 49.5 | 1.0096
930 | 49.5 | 1.0096
930.1 | 49.5 | 1.0096
930.2 | 49.5 | 1.0096
930.3 | 49.5 | 1.0096
930.4 | 49.5 | 1.0096
930.5 | 49.5 | 1.0096
930.6 | 49.5 | 1.0096
930.7 | 49.5 | 1.0096
930.8 | 49.5 | 1.0096
930.9 | 49.5 | 1.0096
931 | 49.5 | 1.0096
931.1 | 49.5 | 1.0096
931.2 | 49.5 | 1.0096
931.3 | 49.5 | 1.0096
931.4 | 49.5 | 1.0096
931.5 | 49.5 | 1.0096
931.6 | 49.5 | 1.0096
931.7 | 49.5 | 1.0096
931.8 | 49.5 | 1.0096
931.9 | 49.5 | 1.0096
932 | 49.5 | 1.0096
932.1 | 49.5 | 1.0096
932.2 | 49.5 | 1.0096
932.3 | 49.5 | 1.0096
932.4 | 49.5 | 1.0096
932.5 | 49.5 | 1.0096
932.6 | 49.5 | 1.0096
932.7 | 49.5 | 1.0096
932.8 | 49.5 | 1.0096
932.9 | 49.5 | 1.0096
933 | 49.5 | 1.0096
933.1 | 49.5 | 1.0096
933.2 | 49.5 | 1.0096
933.3 | 49.5 | 1.0096
933.4 | 49.5 | 1.0096
933.5 | 49.5 | 1.0096
933.6 | 49.5 | 1.0096
933.7 | 49.5 | 1.0096
933.8 | 49.5 | 1.0096
933.9 | 49.5 | 1.0096
934 | 49.5 | 1.0096
934.1 | 49.5 | 1.0096
934.2 | 49.5 | 1.0096
934.3 | 49.5 | 1.0096
934.4 | 49.5 | 1.0096
934.5 | 49.5 | 1.0096
934.6 | 49.5 | 1.0096
934.7 | 49.5 | 1.0096
934.8 | 49.5 | 1.0096
934.9 | 49.5 | 1.0096
935 | 49.5 | 1.0096
935.1 | 49.5 | 1.0096
935.2 | 49.5 | 1.0096
935.3 | 49.5 | 1.0096
935.4 | 49.5 | 1.0096
935.5 | 49.5 | 1.0096
935.6 | 49.5 | 1.0096
935.7 | 49.5 | 1.0096
935.8 | 49.5 | 1.0096
935.9 | 49.5 | 1.0096
936 | 49.5 | 1.0096
936.1 | 49.5 | 1.0096
936.2 | 49.5 | 1.0096
936.3 | 49.5 | 1.0096
936.4 | 49.5 | 1.0096
936.5 | 49.5 | 1.0096
936.6 | 49.5 | 1.0096
936.7 | 49.5 | 1.0096
936.8 | 49.5 | 1.0096
936.9 | 49.5 | 1.0096
937 | 49.5 | 1.0096
937.1 | 49.5 | 1.0096
937.2 | 49.5 | 1.0096
937.3 | 49.5 | 1.0096
937.4 | 49.5 | 1.0096
937.5 | 49.5 | 1.0096
937.6 | 49.5 | 1.0096
937.7 | 49.5 | 1.0096
937.8 | 49.5 | 1.0096
937.9 | 49.5 | 1.0096
938 | 49.5 | 1.0096
938.1 | 49.5 | 1.0096
938.2 | 49.5 | 1.0096
938.3 | 49.5 | 1.0096
938.4 | 49.5 | 1.0096
938.5 | 49.5 | 1.0096
938.6 | 49.5 | 1.0096
938.7 | 49.5 | 1.0096
938.8 | 49.5 | 1.0096
938.9 | 49.5 | 1.0096
939 | 49.5 | 1.0096
939.1 | 49.5 | 1.0096
939.2 | 49.5 | 1.0096
939.3 | 49.5 | 1.0096
939.4 | 49.5 | 1.0096
939.5 | 49.5 | 1.0096
939.6 | 49.5 | 1.0096
939.7 | 49.5 | 1.0096
939.8 | 49.5 | 1.0096
939.9 | 49.5 | 1.0096
940 | 49.5 | 1.0096
940.1 | 49.5 | 1.0096
940.2 | 49.5 | 1.0096
940.3 | 49.5 | 1.0096
940.4 | 49.5 | 1.0096
940.5 | 49.5 | 1.0096
940.6 | 49.5 | 1.0096
940.7 | 49.5 | 1.0096
940.8 | 49.5 | 1.0096
940.9 | 49.5 | 1.0096
941 | 49.5 | 1.0096
941.1 | 49.5 | 1.0096
941.2 | 49.5 | 1.0096
941.3 | 49.5 | 1.0096
941.4 | 49.5 | 1.0096
941.5 | 49.5 | 1.0096
941.6 | 49.5 | 1.0096
941.7 | 49.5 | 1.0096
941.8 | 49.5 | 1.0096
941.9 | 49.5 | 1.0096
942 | 49.5 | 1.0096
942.1 | 49.5 | 1.0096
942.2 | 49.5 | 1.0096
942.3 | 49.5 | 1.0096
942.4 | 49.5 | 1.0096
942.5 | 49.5 | 1.0096
942.6 | 49.5 | 1.0096
942.7 | 49.5 | 1.0096
942.8 | 49.5 | 1.0096
942.9 | 49.5 | 1.0096
943 | 49.5 | 1.0096
943.1 | 49.5 | 1.0096
943.2 | 49.5 | 1.0096
943.3 | 49.5 | 1.0096
943.4 | 49.5 | 1.0096
943.5 | 49.5 | 1.0096
943.6 | 49.5 | 1.0096
943.7 | 49.5 | 1.0096
943.8 | 49.5 | 1.0096
943.9 | 49.5 | 1.0096
944 | 49.5 | 1.0096
944.1 | 49.5 | 1.0096
944.2 | 49.5 | 1.0096
944.3 | 49.5 | 1.0096
944.4 | 49.5 | 1.0096
944.5 | 49.5 | 1.0096
944.6 | 49.5 | 1.0096
944.7 | 49.5 | 1.0096
944.8 | 49.5 | 1.0096
944.9 | 49.5 | 1.0096
945 | 49.5 | 1.0096
945.1 | 49.5 | 1.0096
945.2 | 49.5 | 1.0096
945.3 | 49.5 | 1.0096
945.4 | 49.5 | 1.0096
945.5 | 49.5 | 1.0096
945.6 | 49.5 | 1.0096
945.7 | 49.5 | 1.0096
945.8 | 49.5 | 1.0096
945.9 | 49.5 | 1.0096
946 | 49.5 | 1.0096
946.1 | 49.5 | 1.0096
946.2 | 49.5 | 1.0096
946.3 | 49.5 | 1.0096
946.4 | 49.5 | 1.0096
946.5 | 49.5 | 1.0096
946.6 | 49.5 | 1.0096
946.7 | 49.5 | 1.0096
946.8 | 49.5 | 1.0096
946.9 | 49.5 | 1.0096
947 | 49.5 | 1.0096
947.1 | 49.5 | 1.0096
947.2 | 49.5 | 1.0096
947.3 | 49.5 | 1.0096
947.4 | 49.5 | 1.0096
947.5 | 49.5 | 1.0096
947.6 | 49.5 | 1.0096
947.7 | 49.5 | 1.0096
947.8 | 49.5 | 1.0096
947.9 | 49.5 | 1.0096
948 | 49.5 | 1.0096
948.1 | 49.5 | 1.0096
948.2 | 49.5 | 1.0096
948.3 | 49.5 | 1.0096
948.4 | 49.5 | 1.0096
948.5 | 49.5 | 1.0096
948.6 | 49.5 | 1.0096
948.7 | 49.5 | 1.0096
948.8 | 49.5 | 1.0096
948.9 | 49.5 | 1.0096
949 | 49.5 | 1.0096
949.1 | 49.5 | 1.0096
949.2 | 49.5 | 1.0096
949.3 | 49.5 | 1.0096
949.4 | 49.5 | 1.0096
949.5 | 49.5 | 1.0096
949.6 | 49.5 | 1.0096
949.7 | 49.5 | 1.0096
949.8 | 49.5 | 1.0096
949.9 | 49.5 | 1.0096
950 | 49.5 | 1.0096
950.1 | 49.5 | 1.0096
950.2 | 49.5 | 1.0096
950.3 | 49.5 | 1.0096
950.4 | 49.5 | 1.0096
950.5 | 49.5 | 1.0096
950.6 | 49.5 | 1.0096
950.7 | 49.5 | 1.0096
950.8 | 49.5 | 1.0096
950.9 | 49.5 | 1.0096
951 | 49.5 | 1.0096
951.1 | 49.5 | 1.0096
951.2 | 49.5 | 1.0096
951.3 | 49.5 | 1.0096
951.4 | 49.5 | 1.0096
951.5 | 49.5 | 1.0096
951.6 | 49.5 | 1.0096
951.7 | 49.5 | 1.0096
951.8 | 49.5 | 1.0096
951.9 | 49.5 | 1.0096
952 | 49.5 | 1.0096
952.1 | 49.5 | 1.0096
952.2 | 49.5 | 1.0096
952.3 | 49.5 | 1.0096
952.4 | 49.5 | 1.0096
952.5 | 49.5 | 1.0096
952.6 | 49.5 | 1.0096
952.7 | 49.5 | 1.0096
952.8 | 49.5 | 1.0096
952.9 | 49.5 | 1.0096
953 | 49.5 | 1.0096
953.1 | 49.5 | 1.0096
953.2 | 49.5 | 1.0096
953.3 | 49.5 | 1.0096
953.4 | 49.5 | 1.0096
953.5 | 49.5 | 1.0096
953.6 | 49.5 | 1.0096
953.7 | 49.5 | 1.0096
953.8 | 49.5 | 1.0096
953.9 | 49.5 | 1.0096
954 | 49.5 | 1.0096
954.1 | 49.5 | 1.0096
954.2 | 49.5 | 1.0096
954.3 | 49.5 | 1.0096
954.4 | 49.5 | 1.0096
954.5 | 49.5 | 1.0096
954.6 | 49.5 | 1.0096
954.7 | 49.5 | 1.0096
954.8 | 49.5 | 1.0096
954.9 | 49.5 | 1.0096
955 | 49.5 | 1.0096
955.1 | 49.5 | 1.0096
955.2 | 49.5 | 1.0096
955.3 | 49.5 | 1.0096
955.4 | 49.5 | 1.0096
955.5 | 49.5 | 1.0096
955.6 | 49.5 | 1.0096
955.7 | 49.5 | 1.0096
955.8 | 49.5 | 1.0096
955.9 | 49.5 | 1.0096
956 | 49.5 | 1.0096
956.1 | 49.5 | 1.0096
956.2 | 49.5 | 1.0096
956.3 | 49.5 | 1.0096
956.4 | 49.5 | 1.0096
956.5 | 49.5 | 1.0096
956.6 | 49.5 | 1.0096
956.7 | 49.5 | 1.0096
956.8 | 49.5 | 1.0096
956.9 | 49.5 | 1.0096
957 | 49.5 | 1.0096
957.1 | 49.5 | 1.0096
957.2 | 49.5 | 1.0096
957.3 | 49.5 | 1.0096
957.4 | 49.5 | 1.0096
957.5 | 49.5 | 1.0096
957.6 | 49.5 | 1.0096
957.7 | 49.5 | 1.0096
957.8 | 49.5 | 1.0096
957.9 | 49.5 | 1.0096
958 | 49.5 | 1.0096
958.1 | 49.5 | 1.0096
958.2 | 49.5 | 1.0096
958.3 | 49.5 | 1.0096
958.4 | 49.5 | 1.0096
958.5 | 49.5 | 1.0096
958.6 | 49.5 | 1.0096
958.7 | 49.5 | 1.0096
958.8 | 49.5 | 1.0096
958.9 | 49.5 | 1.0096
959 | 49.5 | 1.0096
959.1 | 49.5 | 1.0096
959.2 | 49.5 | 1.0096
959.3 | 49.5 | 1.0096
959.4 | 49.5 | 1.0096
959.5 | 49.5 | 1.0096
959.6 | 49.5 | 1.0096
959.7 | 49.5 | 1.0096
959.8 | 49.5 | 1.0096
959.9 | 49.5 | 1.0096
960 | 49.5 | 1.0096
960.1 | 49.5 | 1.0096
960.2 | 49.5 | 1.0096
960.3 | 49.5 | 1.0096
960.4 | 49.5 | 1.0096
960.5 | 49.5 | 1.0096
960.6 | 49.5 | 1.0096
960.7 | 49.5 | 1.0096
960.8 | 49.5 | 1.0096
960.9 | 49.5 | 1.0096
961 | 49.5 | 1.0096
961.1 | 49.5 | 1.0096
961.2 | 49.5 | 1.0096
961.3 | 49.5 | 1.0096
961.4 | 49.5 | 1.0096
961.5 | 49.5 | 1.0096
961.6 | 49.5 | 1.0096
961.7 | 49.5 | 1.0096
961.8 | 49.5 | 1.0096
961.9 | 49.5 | 1.0096
962 | 49.5 | 1.0096
962.1 | 49.5 | 1.0096
962.2 | 49.5 | 1.0096
962.3 | 49.5 | 1.0096
962.4 | 49.5 | 1.0096
962.5 | 49.5 | 1.0096
962.6 | 49.5 | 1.0096
962.7 | 49.5 | 1.0096
962.8 | 49.5 | 1.0096
962.9 | 49.5 | 1.0096
963 | 49.5 | 1.0096
963.1 | 49.5 | 1.0096
963.2 | 49.5 | 1.0096
963.3 | 49.5 | 1.0096
963.4 | 49.5 | 1.0096
963.5 | 49.5 | 1.0096
963.6 | 49.5 | 1.0096
963.7 | 49.5 | 1.0096
963.8 | 49.5 | 1.0096
963.9 | 49.5 | 1.0096
964 | 49.5 | 1.0096
964.1 | 49.5 | 1.0096
964.2 | 49.5 | 1.0096
964.3 | 49.5 | 1.0096
964.4 | 49.5 | 1.0096
964.5 | 49.5 | 1.0096
964.6 | 49.5 | 1.0096
964.7 | 49.5 | 1.0096
964.8 | 49.5 | 1.0096
964.9 | 49.5 | 1.0096
965 | 49.5 | 1.0096
965.1 | 49.5 | 1.0096
965.2 | 49.5 | 1.0096
965.3 | 49.5 | 1.0096
965.4 | 49.5 | 1.0096
965.5 | 49.5 | 1.0096
965.6 | 49.5 | 1.0096
965.7 | 49.5 | 1.0096
965.8 | 49.5 | 1.0096
965.9 | 49.5 | 1.0096
966 | 49.5 | 1.0096
966.1 | 49.5 | 1.0096
966.2 | 49.5 | 1.0096
966.3 | 49.5 | 1.0096
966.4 | 49.5 | 1.0096
966.5 | 49.5 | 1.0096
966.6 | 49.5 | 1.0096
966.7 | 49.5 | 1.0096
966.8 | 49.5 | 1.0098
966.9 | 49.5 | 1.0098
967 | 49.5 | 1.0098
967.1 | 49.5 | 1.0098
967.2 | 49.5 | 1.0098
967.3 | 49.5 | 1.0096
967.4 | 49.5 | 1.0096
967.5 | 49.5 | 1.0096
967.6 | 49.5 | 1.0096
967.7 | 49.5 | 1.0096
967.8 | 49.5 | 1.0096
967.9 | 49.5 | 1.0096
968 | 49.5 | 1.0096
968.1 | 49.5 | 1.0096
968.2 | 49.5 | 1.0096
968.3 | 49.5 | 1.0096
968.4 | 49.5 | 1.0096
968.5 | 49.5 | 1.0096
968.6 | 49.5 | 1.0096
968.7 | 49.5 | 1.0096
968.8 | 49.5 | 1.0096
968.9 | 49.5 | 1.0096
969 | 49.5 | 1.0096
969.1 | 49.5 | 1.0096
969.2 | 49.5 | 1.0096
969.3 | 49.5 | 1.0096
969.4 | 49.5 | 1.0096
969.5 | 49.5 | 1.0096
969.6 | 49.5 | 1.0096
969.7 | 49.5 | 1.0096
969.8 | 49.5 | 1.0096
969.9 | 49.5 | 1.0096
970 | 49.5 | 1.0096
970.1 | 49.5 | 1.0096
970.2 | 49.5 | 1.0096
970.3 | 49.5 | 1.0096
970.4 | 49.5 | 1.0096
970.5 | 49.5 | 1.0096
970.6 | 49.5 | 1.0096
970.7 | 49.5 | 1.0096
970.8 | 49.5 | 1.0096
970.9 | 49.5 | 1.0096
971 | 49.5 | 1.0096
971.1 | 49.5 | 1.0096
971.2 | 49.5 | 1.0096
971.3 | 49.5 | 1.0096
971.4 | 49.5 | 1.0096
971.5 | 49.5 | 1.0096
971.6 | 49.5 | 1.0096
971.7 | 49.5 | 1.0096
971.8 | 49.5 | 1.0096
971.9 | 49.5 | 1.0096
972 | 49.5 | 1.0098
972.1 | 49.5 | 1.0098
972.2 | 49.5 | 1.0098
972.3 | 49.5 | 1.0098
972.4 | 49.5 | 1.0098
972.5 | 49.5 | 1.0098
972.6 | 49.5 | 1.0098
972.7 | 49.5 | 1.0098
972.8 | 49.5 | 1.0096
972.9 | 49.5 | 1.0096
973 | 49.5 | 1.0096
973.1 | 49.5 | 1.0096
973.2 | 49.5 | 1.0098
973.3 | 49.5 | 1.0098
973.4 | 49.5 | 1.0098
973.5 | 49.5 | 1.0098
973.6 | 49.5 | 1.0098
973.7 | 49.5 | 1.0098
973.8 | 49.5 | 1.0098
973.9 | 49.5 | 1.0098
974 | 49.5 | 1.0098
974.1 | 49.5 | 1.0098
974.2 | 49.5 | 1.0098
974.3 | 49.5 | 1.0098
974.4 | 49.5 | 1.0098
974.5 | 49.5 | 1.0098
974.6 | 49.5 | 1.0098
974.7 | 49.5 | 1.0098
974.8 | 49.5 | 1.0098
974.9 | 49.5 | 1.0098
975 | 49.5 | 1.0098
975.1 | 49.5 | 1.0098
975.2 | 49.5 | 1.0098
975.3 | 49.5 | 1.0098
975.4 | 49.5 | 1.0098
975.5 | 49.5 | 1.0096
975.6 | 49.5 | 1.0096
975.7 | 49.5 | 1.0096
975.8 | 49.5 | 1.0096
975.9 | 49.5 | 1.0096
976 | 49.5 | 1.0096
976.1 | 49.5 | 1.0096
976.2 | 49.5 | 1.0096
976.3 | 49.5 | 1.0096
976.4 | 49.5 | 1.0096
976.5 | 49.5 | 1.0096
976.6 | 49.5 | 1.0096
976.7 | 49.5 | 1.0096
976.8 | 49.5 | 1.0096
976.9 | 49.5 | 1.0096
977 | 49.5 | 1.0096
977.1 | 49.5 | 1.0096
977.2 | 49.5 | 1.0096
977.3 | 49.5 | 1.0096
977.4 | 49.5 | 1.0096
977.5 | 49.5 | 1.0096
977.6 | 49.5 | 1.0096
977.7 | 49.5 | 1.0096
977.8 | 49.5 | 1.0096
977.9 | 49.5 | 1.0096
978 | 49.5 | 1.0098
978.1 | 49.5 | 1.0098
978.2 | 49.5 | 1.0098
978.3 | 49.5 | 1.0098
978.4 | 49.5 | 1.0098
978.5 | 49.5 | 1.0098
978.6 | 49.5 | 1.0098
978.7 | 49.5 | 1.0098
978.8 | 49.5 | 1.0098
978.9 | 49.5 | 1.0098
979 | 49.5 | 1.0098
979.1 | 49.5 | 1.0098
979.2 | 49.5 | 1.0098
979.3 | 49.5 | 1.0098
979.4 | 49.5 | 1.0098
979.5 | 49.5 | 1.0098
979.6 | 49.5 | 1.0098
979.7 | 49.5 | 1.0098
979.8 | 49.5 | 1.0098
979.9 | 49.5 | 1.0098
980 | 49.5 | 1.0098
980.1 | 49.5 | 1.0098
980.2 | 49.5 | 1.0098
980.3 | 49.5 | 1.0098
980.4 | 49.5 | 1.0098
980.5 | 49.5 | 1.0098
980.6 | 49.5 | 1.0098
980.7 | 49.5 | 1.0098
980.8 | 49.5 | 1.0098
980.9 | 49.5 | 1.0098
981 | 49.5 | 1.0098
981.1 | 49.5 | 1.0098
981.2 | 49.5 | 1.0098
981.3 | 49.5 | 1.0098
981.4 | 49.5 | 1.0096
981.5 | 49.5 | 1.0096
981.6 | 49.5 | 1.0096
981.7 | 49.5 | 1.0096
981.8 | 49.5 | 1.0096
981.9 | 49.5 | 1.0096
982 | 49.5 | 1.0096
982.1 | 49.5 | 1.0096
982.2 | 49.5 | 1.0096
982.3 | 49.5 | 1.0096
982.4 | 49.5 | 1.0096
982.5 | 49.5 | 1.0096
982.6 | 49.5 | 1.0096
982.7 | 49.5 | 1.0096
982.8 | 49.5 | 1.0096
982.9 | 49.5 | 1.0096
983 | 49.5 | 1.0096
983.1 | 49.5 | 1.0096
983.2 | 49.5 | 1.0096
983.3 | 49.5 | 1.0096
983.4 | 49.5 | 1.0096
983.5 | 49.5 | 1.0096
983.6 | 49.5 | 1.0096
983.7 | 49.5 | 1.0096
983.8 | 49.5 | 1.0096
983.9 | 49.5 | 1.0096
984 | 49.5 | 1.0096
984.1 | 49.5 | 1.0096
984.2 | 49.5 | 1.0096
984.3 | 49.5 | 1.0096
984.4 | 49.5 | 1.0096
984.5 | 49.5 | 1.0096
984.6 | 49.5 | 1.0096
984.7 | 49.5 | 1.0096
984.8 | 49.5 | 1.0096
984.9 | 49.5 | 1.0096
985 | 49.5 | 1.0098
985.1 | 49.5 | 1.0098
985.2 | 49.5 | 1.0098
985.3 | 49.5 | 1.0098
985.4 | 49.5 | 1.0098
985.5 | 49.5 | 1.0098
985.6 | 49.5 | 1.0098
985.7 | 49.5 | 1.0098
985.8 | 49.5 | 1.0098
985.9 | 49.5 | 1.0098
986 | 49.5 | 1.0098
986.1 | 49.5 | 1.0098
986.2 | 49.5 | 1.0098
986.3 | 49.5 | 1.0098
986.4 | 49.5 | 1.0098
986.5 | 49.5 | 1.0098
986.6 | 49.5 | 1.0098
986.7 | 49.5 | 1.0098
986.8 | 49.5 | 1.0096
986.9 | 49.5 | 1.0096
987 | 49.5 | 1.0096
987.1 | 49.5 | 1.0096
987.2 | 49.5 | 1.0096
987.3 | 49.5 | 1.0096
987.4 | 49.5 | 1.0096
987.5 | 49.5 | 1.0096
987.6 | 49.5 | 1.0096
987.7 | 49.5 | 1.0096
987.8 | 49.5 | 1.0096
987.9 | 49.5 | 1.0096
988 | 49.5 | 1.0096
988.1 | 49.5 | 1.0096
988.2 | 49.5 | 1.0096
988.3 | 49.5 | 1.0096
988.4 | 49.5 | 1.0096
988.5 | 49.5 | 1.0096
988.6 | 49.5 | 1.0096
988.7 | 49.5 | 1.0096
988.8 | 49.5 | 1.0096
988.9 | 49.5 | 1.0096
989 | 49.5 | 1.0096
989.1 | 49.5 | 1.0096
989.2 | 49.5 | 1.0096
989.3 | 49.5 | 1.0096
989.4 | 49.5 | 1.0096
989.5 | 49.5 | 1.0096
989.6 | 49.5 | 1.0096
989.7 | 49.5 | 1.0096
989.8 | 49.5 | 1.0096
989.9 | 49.5 | 1.0096
990 | 49.5 | 1.0096
990.1 | 49.5 | 1.0096
990.2 | 49.5 | 1.0096
990.3 | 49.5 | 1.0096
990.4 | 49.5 | 1.0096
990.5 | 49.5 | 1.0096
990.6 | 49.5 | 1.0096
990.7 | 49.5 | 1.0096
990.8 | 49.5 | 1.0096
990.9 | 49.5 | 1.0096
991 | 49.5 | 1.0096
991.1 | 49.5 | 1.0096
991.2 | 49.5 | 1.0096
991.3 | 49.5 | 1.0096
991.4 | 49.5 | 1.0096
991.5 | 49.5 | 1.0096
991.6 | 49.5 | 1.0096
991.7 | 49.5 | 1.0096
991.8 | 49.5 | 1.0096
991.9 | 49.5 | 1.0096
992 | 49.5 | 1.0096
992.1 | 49.5 | 1.0096
992.2 | 49.5 | 1.0096
992.3 | 49.5 | 1.0096
992.4 | 49.5 | 1.0096
992.5 | 49.5 | 1.0096
992.6 | 49.5 | 1.0096
992.7 | 49.5 | 1.0096
992.8 | 49.5 | 1.0096
992.9 | 49.5 | 1.0096
993 | 49.5 | 1.0096
993.1 | 49.5 | 1.0096
993.2 | 49.5 | 1.0096
993.3 | 49.5 | 1.0096
993.4 | 49.5 | 1.0096
993.5 | 49.5 | 1.0096
993.6 | 49.5 | 1.0096
993.7 | 49.5 | 1.0096
993.8 | 49.5 | 1.0096
993.9 | 49.5 | 1.0096
994 | 49.5 | 1.0096
994.1 | 49.5 | 1.0096
994.2 | 49.5 | 1.0096
994.3 | 49.5 | 1.0096
994.4 | 49.5 | 1.0096
994.5 | 49.5 | 1.0096
994.6 | 49.5 | 1.0096
994.7 | 49.5 | 1.0096
994.8 | 49.5 | 1.0096
994.9 | 49.5 | 1.0096
995 | 49.5 | 1.0096
995.1 | 49.5 | 1.0096
995.2 | 49.5 | 1.0096
995.3 | 49.5 | 1.0096
995.4 | 49.5 | 1.0096
995.5 | 49.5 | 1.0096
995.6 | 49.5 | 1.0096
995.7 | 49.5 | 1.0096
995.8 | 49.5 | 1.0096
995.9 | 49.5 | 1.0096
996 | 49.5 | 1.0096
996.1 | 49.5 | 1.0096
996.2 | 49.5 | 1.0096
996.3 | 49.5 | 1.0096
996.4 | 49.5 | 1.0096
996.5 | 49.5 | 1.0096
996.6 | 49.5 | 1.0096
996.7 | 49.5 | 1.0096
996.8 | 49.5 | 1.0096
996.9 | 49.5 | 1.0096
997 | 49.5 | 1.0096
997.1 | 49.5 | 1.0096
997.2 | 49.5 | 1.0096
997.3 | 49.5 | 1.0096
997.4 | 49.5 | 1.0096
997.5 | 49.5 | 1.0096
997.6 | 49.5 | 1.0096
997.7 | 49.5 | 1.0096
997.8 | 49.5 | 1.0096
997.9 | 49.5 | 1.0096
998 | 49.5 | 1.0096
998.1 | 49.5 | 1.0096
998.2 | 49.5 | 1.0096
998.3 | 49.5 | 1.0096
998.4 | 49.5 | 1.0096
998.5 | 49.5 | 1.0096
998.6 | 49.5 | 1.0096
998.7 | 49.5 | 1.0096
998.8 | 49.5 | 1.0096
998.9 | 49.5 | 1.0096
999 | 49.5 | 1.0096
999.1 | 49.5 | 1.0096
999.2 | 49.5 | 1.0096
999.3 | 49.5 | 1.0096
999.4 | 49.5 | 1.0096
999.5 | 49.5 | 1.0096
999.6 | 49.5 | 1.0096
999.7 | 49.5 | 1.0096
999.8 | 49.5 | 1.0096
999.9 | 49.5 | 1.0096
1000 | 49.5 | 1.0096
1000.1 | 49.5 | 1.0096
1000.2 | 49.5 | 1.0096
1000.3 | 49.5 | 1.0096
1000.4 | 49.5 | 1.0096
1000.5 | 49.5 | 1.0096
1000.6 | 49.5 | 1.0096
1000.7 | 49.5 | 1.0096
1000.8 | 49.5 | 1.0096
1000.9 | 49.5 | 1.0096
1001 | 49.5 | 1.0096
1001.1 | 49.5 | 1.0096
1001.2 | 49.5 | 1.0096
1001.3 | 49.5 | 1.0096
1001.4 | 49.5 | 1.0096
1001.5 | 49.5 | 1.0096
1001.6 | 49.5 | 1.0096
1001.7 | 49.5 | 1.0096
1001.8 | 49.5 | 1.0096
1001.9 | 49.5 | 1.0096
1002 | 49.5 | 1.0096
1002.1 | 49.5 | 1.0096
1002.2 | 49.5 | 1.0096
1002.3 | 49.5 | 1.0096
1002.4 | 49.5 | 1.0096
1002.5 | 49.5 | 1.0096
1002.6 | 49.5 | 1.0096
1002.7 | 49.5 | 1.0096
1002.8 | 49.5 | 1.0096
1002.9 | 49.5 | 1.0096
1003 | 49.5 | 1.0096
1003.1 | 49.5 | 1.0096
1003.2 | 49.5 | 1.0096
1003.3 | 49.5 | 1.0096
1003.4 | 49.5 | 1.0096
1003.5 | 49.5 | 1.0096
1003.6 | 49.5 | 1.0096
1003.7 | 49.5 | 1.0096
1003.8 | 49.5 | 1.0096
1003.9 | 49.5 | 1.0096
1004 | 49.5 | 1.0096
1004.1 | 49.5 | 1.0096
1004.2 | 49.5 | 1.0096
1004.3 | 49.5 | 1.0096
1004.4 | 49.5 | 1.0096
1004.5 | 49.5 | 1.0096
1004.6 | 49.5 | 1.0096
1004.7 | 49.5 | 1.0096
1004.8 | 49.5 | 1.0096
1004.9 | 49.5 | 1.0096
1005 | 49.5 | 1.0096
1005.1 | 49.5 | 1.0096
1005.2 | 49.5 | 1.0096
1005.3 | 49.5 | 1.0096
1005.4 | 49.5 | 1.0096
1005.5 | 49.5 | 1.0096
1005.6 | 49.5 | 1.0096
1005.7 | 49.5 | 1.0096
1005.8 | 49.5 | 1.0096
1005.9 | 49.5 | 1.0096
1006 | 49.5 | 1.0096
1006.1 | 49.5 | 1.0096
1006.2 | 49.5 | 1.0096
1006.3 | 49.5 | 1.0096
1006.4 | 49.5 | 1.0096
1006.5 | 49.5 | 1.0096
1006.6 | 49.5 | 1.0096
1006.7 | 49.5 | 1.0096
1006.8 | 49.5 | 1.0096
1006.9 | 49.5 | 1.0096
1007 | 49.5 | 1.0096
1007.1 | 49.5 | 1.0096
1007.2 | 49.5 | 1.0096
1007.3 | 49.5 | 1.0096
1007.4 | 49.5 | 1.0096
1007.5 | 49.5 | 1.0096
1007.6 | 49.5 | 1.0096
1007.7 | 49.5 | 1.0096
1007.8 | 49.5 | 1.0096
1007.9 | 49.5 | 1.0096
1008 | 49.5 | 1.0096
1008.1 | 49.5 | 1.0096
1008.2 | 49.5 | 1.0096
1008.3 | 49.5 | 1.0096
1008.4 | 49.5 | 1.0096
1008.5 | 49.5 | 1.0096
1008.6 | 49.5 | 1.0096
1008.7 | 49.5 | 1.0096
1008.8 | 49.5 | 1.0096
1008.9 | 49.5 | 1.0096
1009 | 49.5 | 1.0096
1009.1 | 49.5 | 1.0096
1009.2 | 49.5 | 1.0096
1009.3 | 49.5 | 1.0096
1009.4 | 49.5 | 1.0096
1009.5 | 49.5 | 1.0096
1009.6 | 49.5 | 1.0096
1009.7 | 49.5 | 1.0096
1009.8 | 49.5 | 1.0096
1009.9 | 49.5 | 1.0096
1010 | 49.5 | 1.0096
1010.1 | 49.5 | 1.0096
1010.2 | 49.5 | 1.0096
1010.3 | 49.5 | 1.0096
1010.4 | 49.5 | 1.0096
1010.5 | 49.5 | 1.0096
1010.6 | 49.5 | 1.0096
1010.7 | 49.5 | 1.0096
1010.8 | 49.5 | 1.0096
1010.9 | 49.5 | 1.0096
1011 | 49.5 | 1.0096
1011.1 | 49.5 | 1.0096
1011.2 | 49.5 | 1.0096
1011.3 | 49.5 | 1.0096
1011.4 | 49.5 | 1.0096
1011.5 | 49.5 | 1.0096
1011.6 | 49.5 | 1.0098
1011.7 | 49.5 | 1.0098
1011.8 | 49.5 | 1.0098
1011.9 | 49.5 | 1.0098
1012 | 49.5 | 1.0098
1012.1 | 49.5 | 1.0098
1012.2 | 49.5 | 1.0098
1012.3 | 49.5 | 1.0098
1012.4 | 49.5 | 1.0098
1012.5 | 49.5 | 1.0098
1012.6 | 49.5 | 1.0096
1012.7 | 49.5 | 1.0096
1012.8 | 49.5 | 1.0096
1012.9 | 49.5 | 1.0096
1013 | 49.5 | 1.0096
1013.1 | 49.5 | 1.0096
1013.2 | 49.5 | 1.0096
1013.3 | 49.5 | 1.0096
1013.4 | 49.5 | 1.0096
1013.5 | 49.5 | 1.0096
1013.6 | 49.5 | 1.0096
1013.7 | 49.5 | 1.0096
1013.8 | 49.5 | 1.0096
1013.9 | 49.5 | 1.0096
1014 | 49.5 | 1.0096
1014.1 | 49.5 | 1.0096
1014.2 | 49.5 | 1.0096
1014.3 | 49.5 | 1.0096
1014.4 | 49.5 | 1.0096
1014.5 | 49.5 | 1.0096
1014.6 | 49.5 | 1.0096
1014.7 | 49.5 | 1.0096
1014.8 | 49.5 | 1.0096
1014.9 | 49.5 | 1.0096
1015 | 49.5 | 1.0096
1015.1 | 49.5 | 1.0096
1015.2 | 49.5 | 1.0096
1015.3 | 49.5 | 1.0096
1015.4 | 49.5 | 1.0096
1015.5 | 49.5 | 1.0096
1015.6 | 49.5 | 1.0096
1015.7 | 49.5 | 1.0096
1015.8 | 49.5 | 1.0096
1015.9 | 49.5 | 1.0096
1016 | 49.5 | 1.0098
1016.1 | 49.5 | 1.0098
1016.2 | 49.5 | 1.0098
1016.3 | 49.5 | 1.0098
1016.4 | 49.5 | 1.0098
1016.5 | 49.5 | 1.0098
1016.6 | 49.5 | 1.0098
1016.7 | 49.5 | 1.0098
1016.8 | 49.5 | 1.0098
1016.9 | 49.5 | 1.0098
1017 | 49.5 | 1.0098
1017.1 | 49.5 | 1.0098
1017.2 | 49.5 | 1.0098
1017.3 | 49.5 | 1.0098
1017.4 | 49.5 | 1.0098
1017.5 | 49.5 | 1.0098
1017.6 | 49.5 | 1.0098
1017.7 | 49.5 | 1.0098
1017.8 | 49.5 | 1.0098
1017.9 | 49.5 | 1.0098
1018 | 49.5 | 1.0098
1018.1 | 49.5 | 1.0098
1018.2 | 49.5 | 1.0098
1018.3 | 49.5 | 1.0096
1018.4 | 49.5 | 1.0096
1018.5 | 49.5 | 1.0096
1018.6 | 49.5 | 1.0096
1018.7 | 49.5 | 1.0096
1018.8 | 49.5 | 1.0096
1018.9 | 49.5 | 1.0096
1019 | 49.5 | 1.0096
1019.1 | 49.5 | 1.0096
1019.2 | 49.5 | 1.0096
1019.3 | 49.5 | 1.0096
1019.4 | 49.5 | 1.0096
1019.5 | 49.5 | 1.0096
1019.6 | 49.5 | 1.0096
1019.7 | 49.5 | 1.0096
1019.8 | 49.5 | 1.0096
1019.9 | 49.5 | 1.0096
1020 | 49.5 | 1.0096
1020.1 | 49.5 | 1.0096
1020.2 | 49.5 | 1.0096
1020.3 | 49.5 | 1.0096
1020.4 | 49.5 | 1.0096
1020.5 | 49.5 | 1.0096
1020.6 | 49.5 | 1.0096
1020.7 | 49.5 | 1.0096
1020.8 | 49.5 | 1.0096
1020.9 | 49.5 | 1.0096
1021 | 49.5 | 1.0096
1021.1 | 49.5 | 1.0096
1021.2 | 49.5 | 1.0096
1021.3 | 49.5 | 1.0096
1021.4 | 49.5 | 1.0096
1021.5 | 49.5 | 1.0096
1021.6 | 49.5 | 1.0096
1021.7 | 49.5 | 1.0096
1021.8 | 49.5 | 1.0096
1021.9 | 49.5 | 1.0098
1022 | 49.5 | 1.0098
1022.1 | 49.5 | 1.0098
1022.2 | 49.5 | 1.0098
1022.3 | 49.5 | 1.0098
1022.4 | 49.5 | 1.0098
1022.5 | 49.5 | 1.0098
1022.6 | 49.5 | 1.0098
1022.7 | 49.5 | 1.0098
1022.8 | 49.5 | 1.0098
1022.9 | 49.5 | 1.0098
1023 | 49.5 | 1.0098
1023.1 | 49.5 | 1.0098
1023.2 | 49.5 | 1.0098
1023.3 | 49.5 | 1.0098
1023.4 | 49.5 | 1.0098
1023.5 | 49.5 | 1.0098
1023.6 | 49.5 | 1.0098
1023.7 | 49.5 | 1.0098
1023.8 | 49.5 | 1.0098
1023.9 | 49.5 | 1.0098
1024 | 49.5 | 1.0098
1024.1 | 49.5 | 1.0096
1024.2 | 49.5 | 1.0096
1024.3 | 49.5 | 1.0096
1024.4 | 49.5 | 1.0096
1024.5 | 49.5 | 1.0096
1024.6 | 49.5 | 1.0096
1024.7 | 49.5 | 1.0096
1024.8 | 49.5 | 1.0096
1024.9 | 49.5 | 1.0096
1025 | 49.5 | 1.0096
1025.1 | 49.5 | 1.0096
1025.2 | 49.5 | 1.0096
1025.3 | 49.5 | 1.0096
1025.4 | 49.5 | 1.0096
1025.5 | 49.5 | 1.0096
1025.6 | 49.5 | 1.0096
1025.7 | 49.5 | 1.0096
1025.8 | 49.5 | 1.0096
1025.9 | 49.5 | 1.0096
1026 | 49.5 | 1.0096
1026.1 | 49.5 | 1.0096
1026.2 | 49.5 | 1.0096
1026.3 | 49.5 | 1.0096
1026.4 | 49.5 | 1.0096
1026.5 | 49.5 | 1.0096
1026.6 | 49.5 | 1.0096
1026.7 | 49.5 | 1.0094
1026.8 | 49.5 | 1.0094
1026.9 | 49.5 | 1.0094
1027 | 49.5 | 1.0094
1027.1 | 49.5 | 1.0094
1027.2 | 49.5 | 1.0094
1027.3 | 49.5 | 1.0094
1027.4 | 49.5 | 1.0094
1027.5 | 49.5 | 1.0094
1027.6 | 49.5 | 1.0094
1027.7 | 49.5 | 1.0096
1027.8 | 49.5 | 1.0096
1027.9 | 49.5 | 1.0096
1028 | 49.5 | 1.0096
1028.1 | 49.5 | 1.0096
1028.2 | 49.5 | 1.0096
1028.3 | 49.5 | 1.0096
1028.4 | 49.5 | 1.0096
1028.5 | 49.5 | 1.0096
1028.6 | 49.5 | 1.0096
1028.7 | 49.5 | 1.0096
1028.8 | 49.5 | 1.0096
1028.9 | 49.5 | 1.0096
1029 | 49.5 | 1.0096
1029.1 | 49.5 | 1.0098
1029.2 | 49.5 | 1.0098
1029.3 | 49.5 | 1.0098
1029.4 | 49.5 | 1.0098
1029.5 | 49.5 | 1.0098
1029.6 | 49.5 | 1.0098
1029.7 | 49.5 | 1.0098
1029.8 | 49.5 | 1.0098
1029.9 | 49.5 | 1.0096
1030 | 49.5 | 1.0096
1030.1 | 49.5 | 1.0096
1030.2 | 49.5 | 1.0096
1030.3 | 49.5 | 1.0098
1030.4 | 49.5 | 1.0098
1030.5 | 49.5 | 1.0098
1030.6 | 49.5 | 1.0098
1030.7 | 49.5 | 1.0098
1030.8 | 49.5 | 1.0098
1030.9 | 49.5 | 1.0098
1031 | 49.5 | 1.0098
1031.1 | 49.5 | 1.0096
1031.2 | 49.5 | 1.0096
1031.3 | 49.5 | 1.0096
1031.4 | 49.5 | 1.0096
1031.5 | 49.5 | 1.0096
1031.6 | 49.5 | 1.0096
1031.7 | 49.5 | 1.0096
1031.8 | 49.5 | 1.0096
1031.9 | 49.5 | 1.0096
1032 | 49.5 | 1.0096
1032.1 | 49.5 | 1.0096
1032.2 | 49.5 | 1.0096
1032.3 | 49.5 | 1.0096
1032.4 | 49.5 | 1.0096
1032.5 | 49.5 | 1.0096
1032.6 | 49.5 | 1.0096
1032.7 | 49.5 | 1.0096
1032.8 | 49.5 | 1.0096
1032.9 | 49.5 | 1.0096
1033 | 49.5 | 1.0096
1033.1 | 49.5 | 1.0096
1033.2 | 49.5 | 1.0096
1033.3 | 49.5 | 1.0096
1033.4 | 49.5 | 1.0096
1033.5 | 49.5 | 1.0096
1033.6 | 49.5 | 1.0096
1033.7 | 49.5 | 1.0096
1033.8 | 49.5 | 1.0096
1033.9 | 49.5 | 1.0096
1034 | 49.5 | 1.0096
1034.1 | 49.5 | 1.0096
1034.2 | 49.5 | 1.0096
1034.3 | 49.5 | 1.0096
1034.4 | 49.5 | 1.0096
1034.5 | 49.5 | 1.0096
1034.6 | 49.5 | 1.0096
1034.7 | 49.5 | 1.0098
1034.8 | 49.5 | 1.0098
1034.9 | 49.5 | 1.0098
1035 | 49.5 | 1.0098
1035.1 | 49.5 | 1.0096
1035.2 | 49.5 | 1.0096
1035.3 | 49.5 | 1.0096
1035.4 | 49.5 | 1.0096
1035.5 | 49.5 | 1.0096
1035.6 | 49.5 | 1.0096
1035.7 | 49.5 | 1.0096
1035.8 | 49.5 | 1.0096
1035.9 | 49.5 | 1.0096
1036 | 49.5 | 1.0096
1036.1 | 49.5 | 1.0096
1036.2 | 49.5 | 1.0096
1036.3 | 49.5 | 1.0096
1036.4 | 49.5 | 1.0096
1036.5 | 49.5 | 1.0096
1036.6 | 49.5 | 1.0096
1036.7 | 49.5 | 1.0096
1036.8 | 49.5 | 1.0096
1036.9 | 49.5 | 1.0096
1037 | 49.5 | 1.0096
1037.1 | 49.5 | 1.0096
1037.2 | 49.5 | 1.0098
1037.3 | 49.5 | 1.0098
1037.4 | 49.5 | 1.0098
1037.5 | 49.5 | 1.0098
1037.6 | 49.5 | 1.0098
1037.7 | 49.5 | 1.0098
1037.8 | 49.5 | 1.0098
1037.9 | 49.5 | 1.0098
1038 | 49.5 | 1.0098
1038.1 | 49.5 | 1.0096
1038.2 | 49.5 | 1.0096
1038.3 | 49.5 | 1.0096
1038.4 | 49.5 | 1.0096
1038.5 | 49.5 | 1.0096
1038.6 | 49.5 | 1.0096
1038.7 | 49.5 | 1.0096
1038.8 | 49.5 | 1.0096
1038.9 | 49.5 | 1.0096
1039 | 49.5 | 1.0096
1039.1 | 49.5 | 1.0096
1039.2 | 49.5 | 1.0096
1039.3 | 49.5 | 1.0096
1039.4 | 49.5 | 1.0096
1039.5 | 49.5 | 1.0096
1039.6 | 49.5 | 1.0096
1039.7 | 49.5 | 1.0096
1039.8 | 49.5 | 1.0096
1039.9 | 49.5 | 1.0096
1040 | 49.5 | 1.0096
1040.1 | 49.5 | 1.0096
1040.2 | 49.5 | 1.0096
1040.3 | 49.5 | 1.0096
1040.4 | 49.5 | 1.0096
1040.5 | 49.5 | 1.0096
1040.6 | 49.5 | 1.0096
1040.7 | 49.5 | 1.0096
1040.8 | 49.5 | 1.0096
1040.9 | 49.5 | 1.0096
1041 | 49.5 | 1.0096
1041.1 | 49.5 | 1.0096
1041.2 | 49.5 | 1.0096
1041.3 | 49.5 | 1.0096
1041.4 | 49.5 | 1.0096
1041.5 | 49.5 | 1.0096
1041.6 | 49.5 | 1.0096
1041.7 | 49.5 | 1.0096
1041.8 | 49.5 | 1.0098
1041.9 | 49.5 | 1.0098
1042 | 49.5 | 1.0098
1042.1 | 49.5 | 1.0098
1042.2 | 49.5 | 1.0098
1042.3 | 49.5 | 1.0098
1042.4 | 49.5 | 1.0098
1042.5 | 49.5 | 1.0098
1042.6 | 49.5 | 1.0098
1042.7 | 49.5 | 1.0098
1042.8 | 49.5 | 1.0098
1042.9 | 49.5 | 1.0096
1043 | 49.5 | 1.0096
1043.1 | 49.5 | 1.0096
1043.2 | 49.5 | 1.0096
1043.3 | 49.5 | 1.0096
1043.4 | 49.5 | 1.0096
1043.5 | 49.5 | 1.0096
1043.6 | 49.5 | 1.0096
1043.7 | 49.5 | 1.0096
1043.8 | 49.5 | 1.0096
1043.9 | 49.5 | 1.0096
1044 | 49.5 | 1.0096
1044.1 | 49.5 | 1.0096
1044.2 | 49.5 | 1.0094
1044.3 | 49.5 | 1.0094
1044.4 | 49.5 | 1.0094
1044.5 | 49.5 | 1.0094
1044.6 | 49.5 | 1.0094
1044.7 | 49.5 | 1.0094
1044.8 | 49.5 | 1.0094
1044.9 | 49.5 | 1.0094
1045 | 49.5 | 1.0094
1045.1 | 49.5 | 1.0094
1045.2 | 49.5 | 1.0094
1045.3 | 49.5 | 1.0094
1045.4 | 49.5 | 1.0096
1045.5 | 49.5 | 1.0096
1045.6 | 49.5 | 1.0096
1045.7 | 49.5 | 1.0096
1045.8 | 49.5 | 1.0096
1045.9 | 49.5 | 1.0096
1046 | 49.5 | 1.0096
1046.1 | 49.5 | 1.0096
1046.2 | 49.5 | 1.0096
1046.3 | 49.5 | 1.0096
1046.4 | 49.5 | 1.0096
1046.5 | 49.5 | 1.0096
1046.6 | 49.5 | 1.0098
1046.7 | 49.5 | 1.0098
1046.8 | 49.5 | 1.0098
1046.9 | 49.5 | 1.0098
1047 | 49.5 | 1.0098
1047.1 | 49.5 | 1.0098
1047.2 | 49.5 | 1.0098
1047.3 | 49.5 | 1.0098
1047.4 | 49.5 | 1.0098
1047.5 | 49.5 | 1.0098
1047.6 | 49.5 | 1.0098
1047.7 | 49.5 | 1.0098
1047.8 | 49.5 | 1.0098
1047.9 | 49.5 | 1.0098
1048 | 49.5 | 1.0098
1048.1 | 49.5 | 1.0098
1048.2 | 49.5 | 1.0098
1048.3 | 49.5 | 1.0098
1048.4 | 49.5 | 1.0098
1048.5 | 49.5 | 1.0098
1048.6 | 49.5 | 1.0098
1048.7 | 49.5 | 1.0098
1048.8 | 49.5 | 1.0098
1048.9 | 49.5 | 1.0096
1049 | 49.5 | 1.0096
1049.1 | 49.5 | 1.0096
1049.2 | 49.5 | 1.0096
1049.3 | 49.5 | 1.0096
1049.4 | 49.5 | 1.0096
1049.5 | 49.5 | 1.0096
1049.6 | 49.5 | 1.0096
1049.7 | 49.5 | 1.0096
1049.8 | 49.5 | 1.0096
1049.9 | 49.5 | 1.0096
1050 | 49.5 | 1.0096
1050.1 | 49.5 | 1.0096
1050.2 | 49.5 | 1.0096
1050.3 | 49.5 | 1.0096
1050.4 | 49.5 | 1.0096
1050.5 | 49.5 | 1.0096
1050.6 | 49.5 | 1.0096
1050.7 | 49.5 | 1.0096
1050.8 | 49.5 | 1.0096
1050.9 | 49.5 | 1.0096
1051 | 49.5 | 1.0094
1051.1 | 49.5 | 1.0094
1051.2 | 49.5 | 1.0094
1051.3 | 49.5 | 1.0094
1051.4 | 49.5 | 1.0094
1051.5 | 49.5 | 1.0094
1051.6 | 49.5 | 1.0094
1051.7 | 49.5 | 1.0094
1051.8 | 49.5 | 1.0094
1051.9 | 49.5 | 1.0094
1052 | 49.5 | 1.0094
1052.1 | 49.5 | 1.0094
1052.2 | 49.5 | 1.0094
1052.3 | 49.5 | 1.0094
1052.4 | 49.5 | 1.0096
1052.5 | 49.5 | 1.0096
1052.6 | 49.5 | 1.0096
1052.7 | 49.5 | 1.0096
1052.8 | 49.5 | 1.0096
1052.9 | 49.5 | 1.0098
1053 | 49.5 | 1.0098
1053.1 | 49.5 | 1.0098
1053.2 | 49.5 | 1.0098
1053.3 | 49.5 | 1.0098
1053.4 | 49.5 | 1.0098
1053.5 | 49.5 | 1.0098
1053.6 | 49.5 | 1.0098
1053.7 | 49.5 | 1.0098
1053.8 | 49.5 | 1.0098
1053.9 | 49.5 | 1.0098
1054 | 49.5 | 1.0098
1054.1 | 49.5 | 1.0098
1054.2 | 49.5 | 1.0098
1054.3 | 49.5 | 1.0098
1054.4 | 49.5 | 1.0098
1054.5 | 49.5 | 1.0098
1054.6 | 49.5 | 1.01
1054.7 | 49.5 | 1.01
1054.8 | 49.5 | 1.01
1054.9 | 49.5 | 1.01
1055 | 49.5 | 1.01
1055.1 | 49.5 | 1.01
1055.2 | 49.5 | 1.01
1055.3 | 49.5 | 1.0098
1055.4 | 49.5 | 1.0098
1055.5 | 49.5 | 1.0098
1055.6 | 49.5 | 1.0098
1055.7 | 49.5 | 1.0098
1055.8 | 49.5 | 1.0098
1055.9 | 49.5 | 1.0098
1056 | 49.5 | 1.0098
1056.1 | 49.5 | 1.0098
1056.2 | 49.5 | 1.0098
1056.3 | 49.5 | 1.0096
1056.4 | 49.5 | 1.0096
1056.5 | 49.5 | 1.0096
1056.6 | 49.5 | 1.0096
1056.7 | 49.5 | 1.0096
1056.8 | 49.5 | 1.0096
1056.9 | 49.5 | 1.0096
1057 | 49.5 | 1.0094
1057.1 | 49.5 | 1.0094
1057.2 | 49.5 | 1.0094
1057.3 | 49.5 | 1.0094
1057.4 | 49.5 | 1.0094
1057.5 | 49.5 | 1.0094
1057.6 | 49.5 | 1.0094
1057.7 | 49.5 | 1.0094
1057.8 | 49.5 | 1.0094
1057.9 | 49.5 | 1.0094
1058 | 49.5 | 1.0094
1058.1 | 49.5 | 1.0094
1058.2 | 49.5 | 1.0094
1058.3 | 49.5 | 1.0094
1058.4 | 49.5 | 1.0094
1058.5 | 49.5 | 1.0094
1058.6 | 49.5 | 1.0094
1058.7 | 49.5 | 1.0094
1058.8 | 49.5 | 1.0094
1058.9 | 49.5 | 1.0094
1059 | 49.5 | 1.0094
1059.1 | 49.5 | 1.0094
1059.2 | 49.5 | 1.0094
1059.3 | 49.5 | 1.0096
1059.4 | 49.5 | 1.0096
1059.5 | 49.5 | 1.0096
1059.6 | 49.5 | 1.0096
1059.7 | 49.5 | 1.0096
1059.8 | 49.5 | 1.0096
1059.9 | 49.5 | 1.0096
1060 | 49.5 | 1.0096
1060.1 | 49.5 | 1.0096
1060.2 | 49.5 | 1.0096
1060.3 | 49.5 | 1.0096
1060.4 | 49.5 | 1.0096
1060.5 | 49.5 | 1.0098
1060.6 | 49.5 | 1.0098
1060.7 | 49.5 | 1.0098
1060.8 | 49.5 | 1.0098
1060.9 | 49.5 | 1.0098
1061 | 49.5 | 1.0098
1061.1 | 49.5 | 1.0098
1061.2 | 49.5 | 1.0098
1061.3 | 49.5 | 1.0098
1061.4 | 49.5 | 1.0098
1061.5 | 49.5 | 1.0098
1061.6 | 49.5 | 1.0098
1061.7 | 49.5 | 1.0098
1061.8 | 49.5 | 1.0098
1061.9 | 49.5 | 1.0098
1062 | 49.5 | 1.0098
1062.1 | 49.5 | 1.0098
1062.2 | 49.5 | 1.0098
1062.3 | 49.5 | 1.0098
1062.4 | 49.5 | 1.0098
1062.5 | 49.5 | 1.0098
1062.6 | 49.5 | 1.0098
1062.7 | 49.5 | 1.0098
1062.8 | 49.5 | 1.0098
1062.9 | 49.5 | 1.0098
1063 | 49.5 | 1.0096
1063.1 | 49.5 | 1.0096
1063.2 | 49.5 | 1.0096
1063.3 | 49.5 | 1.0096
1063.4 | 49.5 | 1.0096
1063.5 | 49.5 | 1.0096
1063.6 | 49.5 | 1.0096
1063.7 | 49.5 | 1.0096
1063.8 | 49.5 | 1.0096
1063.9 | 49.5 | 1.0096
1064 | 49.5 | 1.0096
1064.1 | 49.5 | 1.0096
1064.2 | 49.5 | 1.0094
1064.3 | 49.5 | 1.0094
1064.4 | 49.5 | 1.0094
1064.5 | 49.5 | 1.0094
1064.6 | 49.5 | 1.0094
1064.7 | 49.5 | 1.0094
1064.8 | 49.5 | 1.0094
1064.9 | 49.5 | 1.0094
1065 | 49.5 | 1.0094
1065.1 | 49.5 | 1.0096
1065.2 | 49.5 | 1.0096
1065.3 | 49.5 | 1.0096
1065.4 | 49.5 | 1.0096
1065.5 | 49.5 | 1.0096
1065.6 | 49.5 | 1.0096
1065.7 | 49.5 | 1.0096
1065.8 | 49.5 | 1.0096
1065.9 | 49.5 | 1.0096
1066 | 49.5 | 1.0096
1066.1 | 49.5 | 1.0096
1066.2 | 49.5 | 1.0096
1066.3 | 49.5 | 1.0098
1066.4 | 49.5 | 1.0098
1066.5 | 49.5 | 1.0098
1066.6 | 49.5 | 1.0098
1066.7 | 49.5 | 1.0098
1066.8 | 49.5 | 1.0098
1066.9 | 49.5 | 1.0098
1067 | 49.5 | 1.0098
1067.1 | 49.5 | 1.0098
1067.2 | 49.5 | 1.0098
1067.3 | 49.5 | 1.0098
1067.4 | 49.5 | 1.0098
1067.5 | 49.5 | 1.0098
1067.6 | 49.5 | 1.0098
1067.7 | 49.5 | 1.0098
1067.8 | 49.5 | 1.0098
1067.9 | 49.5 | 1.0098
1068 | 49.5 | 1.0098
1068.1 | 49.5 | 1.0098
1068.2 | 49.5 | 1.0098
1068.3 | 49.5 | 1.0098
1068.4 | 49.5 | 1.0098
1068.5 | 49.5 | 1.0098
1068.6 | 49.5 | 1.0098
1068.7 | 49.5 | 1.0098
1068.8 | 49.5 | 1.0098
1068.9 | 49.5 | 1.0098
1069 | 49.5 | 1.0098
1069.1 | 49.5 | 1.0096
1069.2 | 49.5 | 1.0096
1069.3 | 49.5 | 1.0096
1069.4 | 49.5 | 1.0096
1069.5 | 49.5 | 1.0096
1069.6 | 49.5 | 1.0096
1069.7 | 49.5 | 1.0096
1069.8 | 49.5 | 1.0096
1069.9 | 49.5 | 1.0096
1070 | 49.5 | 1.0096
1070.1 | 49.5 | 1.0096
1070.2 | 49.5 | 1.0096
1070.3 | 49.5 | 1.0096
1070.4 | 49.5 | 1.0096
1070.5 | 49.5 | 1.0096
1070.6 | 49.5 | 1.0096
1070.7 | 49.5 | 1.0096
1070.8 | 49.5 | 1.0096
1070.9 | 49.5 | 1.0096
1071 | 49.5 | 1.0096
1071.1 | 49.5 | 1.0096
1071.2 | 49.5 | 1.0096
1071.3 | 49.5 | 1.0096
1071.4 | 49.5 | 1.0096
1071.5 | 49.5 | 1.0096
1071.6 | 49.5 | 1.0096
1071.7 | 49.5 | 1.0096
1071.8 | 49.5 | 1.0096
1071.9 | 49.5 | 1.0096
1072 | 49.5 | 1.0096
1072.1 | 49.5 | 1.0096
1072.2 | 49.5 | 1.0096
1072.3 | 49.5 | 1.0096
1072.4 | 49.5 | 1.0096
1072.5 | 49.5 | 1.0096
1072.6 | 49.5 | 1.0096
1072.7 | 49.5 | 1.0096
1072.8 | 49.5 | 1.0096
1072.9 | 49.5 | 1.0096
1073 | 49.5 | 1.0096
1073.1 | 49.5 | 1.0096
1073.2 | 49.5 | 1.0096
1073.3 | 49.5 | 1.0096
1073.4 | 49.5 | 1.0096
1073.5 | 49.5 | 1.0096
1073.6 | 49.5 | 1.0096
1073.7 | 49.5 | 1.0096
1073.8 | 49.5 | 1.0096
1073.9 | 49.5 | 1.0096
1074 | 49.5 | 1.0096
1074.1 | 49.5 | 1.0096
1074.2 | 49.5 | 1.0096
1074.3 | 49.5 | 1.0096
1074.4 | 49.5 | 1.0096
1074.5 | 49.5 | 1.0096
1074.6 | 49.5 | 1.0096
1074.7 | 49.5 | 1.0096
1074.8 | 49.5 | 1.0096
1074.9 | 49.5 | 1.0096
1075 | 49.5 | 1.0096
1075.1 | 49.5 | 1.0096
1075.2 | 49.5 | 1.0096
1075.3 | 49.5 | 1.0096
1075.4 | 49.5 | 1.0096
1075.5 | 49.5 | 1.0096
1075.6 | 49.5 | 1.0096
1075.7 | 49.5 | 1.0096
1075.8 | 49.5 | 1.0096
1075.9 | 49.5 | 1.0096
1076 | 49.5 | 1.0096
1076.1 | 49.5 | 1.0096
1076.2 | 49.5 | 1.0096
1076.3 | 49.5 | 1.0096
1076.4 | 49.5 | 1.0096
1076.5 | 49.5 | 1.0096
1076.6 | 49.5 | 1.0096
1076.7 | 49.5 | 1.0096
1076.8 | 49.5 | 1.0096
1076.9 | 49.5 | 1.0096
1077 | 49.5 | 1.0096
1077.1 | 49.5 | 1.0096
1077.2 | 49.5 | 1.0096
1077.3 | 49.5 | 1.0096
1077.4 | 49.5 | 1.0098
1077.5 | 49.5 | 1.0098
1077.6 | 49.5 | 1.0098
1077.7 | 49.5 | 1.0098
1077.8 | 49.5 | 1.0098
1077.9 | 49.5 | 1.0098
1078 | 49.5 | 1.0098
1078.1 | 49.5 | 1.0098
1078.2 | 49.5 | 1.0098
1078.3 | 49.5 | 1.0098
1078.4 | 49.5 | 1.0098
1078.5 | 49.5 | 1.0098
1078.6 | 49.5 | 1.0096
1078.7 | 49.5 | 1.0096
1078.8 | 49.5 | 1.0096
1078.9 | 49.5 | 1.0096
1079 | 49.5 | 1.0096
1079.1 | 49.5 | 1.0096
1079.2 | 49.5 | 1.0096
1079.3 | 49.5 | 1.0096
1079.4 | 49.5 | 1.0096
1079.5 | 49.5 | 1.0096
1079.6 | 49.5 | 1.0096
1079.7 | 49.5 | 1.0096
1079.8 | 49.5 | 1.0096
1079.9 | 49.5 | 1.0096
1080 | 49.5 | 1.0096
1080.1 | 49.5 | 1.0096
1080.2 | 49.5 | 1.0094
1080.3 | 49.5 | 1.0094
1080.4 | 49.5 | 1.0094
1080.5 | 49.5 | 1.0094
1080.6 | 49.5 | 1.0094
1080.7 | 49.5 | 1.0094
1080.8 | 49.5 | 1.0094
1080.9 | 49.5 | 1.0094
1081 | 49.5 | 1.0096
1081.1 | 49.5 | 1.0096
1081.2 | 49.5 | 1.0096
1081.3 | 49.5 | 1.0096
1081.4 | 49.5 | 1.0096
1081.5 | 49.5 | 1.0096
1081.6 | 49.5 | 1.0096
1081.7 | 49.5 | 1.0096
1081.8 | 49.5 | 1.0096
1081.9 | 49.5 | 1.0096
1082 | 49.5 | 1.0096
1082.1 | 49.5 | 1.0096
1082.2 | 49.5 | 1.0096
1082.3 | 49.5 | 1.0096
1082.4 | 49.5 | 1.0096
1082.5 | 49.5 | 1.0096
1082.6 | 49.5 | 1.0096
1082.7 | 49.5 | 1.0096
1082.8 | 49.5 | 1.0096
1082.9 | 49.5 | 1.0096
1083 | 49.5 | 1.0096
1083.1 | 49.5 | 1.0096
1083.2 | 49.5 | 1.0096
1083.3 | 49.5 | 1.0096
1083.4 | 49.5 | 1.0096
1083.5 | 49.5 | 1.0096
1083.6 | 49.5 | 1.0096
1083.7 | 49.5 | 1.0096
1083.8 | 49.5 | 1.0096
1083.9 | 49.5 | 1.0096
1084 | 49.5 | 1.0096
1084.1 | 49.5 | 1.0096
1084.2 | 49.5 | 1.0096
1084.3 | 49.5 | 1.0096
1084.4 | 49.5 | 1.0096
1084.5 | 49.5 | 1.0096
1084.6 | 49.5 | 1.0096
1084.7 | 49.5 | 1.0096
1084.8 | 49.5 | 1.0096
1084.9 | 49.5 | 1.0096
1085 | 49.5 | 1.0096
1085.1 | 49.5 | 1.0096
1085.2 | 49.5 | 1.0096
1085.3 | 49.5 | 1.0096
1085.4 | 49.5 | 1.0096
1085.5 | 49.5 | 1.0096
1085.6 | 49.5 | 1.0096
1085.7 | 49.5 | 1.0096
1085.8 | 49.5 | 1.0096
1085.9 | 49.5 | 1.0096
1086 | 49.5 | 1.0096
1086.1 | 49.5 | 1.0096
1086.2 | 49.5 | 1.0096
1086.3 | 49.5 | 1.0096
1086.4 | 49.5 | 1.0096
1086.5 | 49.5 | 1.0096
1086.6 | 49.5 | 1.0096
1086.7 | 49.5 | 1.0096
1086.8 | 49.5 | 1.0096
1086.9 | 49.5 | 1.0096
1087 | 49.5 | 1.0096
1087.1 | 49.5 | 1.0096
1087.2 | 49.5 | 1.0096
1087.3 | 49.5 | 1.0096
1087.4 | 49.5 | 1.0096
1087.5 | 49.5 | 1.0096
1087.6 | 49.5 | 1.0096
1087.7 | 49.5 | 1.0096
1087.8 | 49.5 | 1.0096
1087.9 | 49.5 | 1.0096
1088 | 49.5 | 1.0096
1088.1 | 49.5 | 1.0096
1088.2 | 49.5 | 1.0096
1088.3 | 49.5 | 1.0096
1088.4 | 49.5 | 1.0096
1088.5 | 49.5 | 1.0096
1088.6 | 49.5 | 1.0096
1088.7 | 49.5 | 1.0096
1088.8 | 49.5 | 1.0096
1088.9 | 49.5 | 1.0096
1089 | 49.5 | 1.0096
1089.1 | 49.5 | 1.0096
1089.2 | 49.5 | 1.0096
1089.3 | 49.5 | 1.0096
1089.4 | 49.5 | 1.0096
1089.5 | 49.5 | 1.0096
1089.6 | 49.5 | 1.0096
1089.7 | 49.5 | 1.0098
1089.8 | 49.5 | 1.0098
1089.9 | 49.5 | 1.0098
1090 | 49.5 | 1.0098
1090.1 | 49.5 | 1.0098
1090.2 | 49.5 | 1.0098
1090.3 | 49.5 | 1.0098
1090.4 | 49.5 | 1.0098
1090.5 | 49.5 | 1.0098
1090.6 | 49.5 | 1.0098
1090.7 | 49.5 | 1.0098
1090.8 | 49.5 | 1.0098
1090.9 | 49.5 | 1.0096
1091 | 49.5 | 1.0096
1091.1 | 49.5 | 1.0096
1091.2 | 49.5 | 1.0096
1091.3 | 49.5 | 1.0096
1091.4 | 49.5 | 1.0096
1091.5 | 49.5 | 1.0096
1091.6 | 49.5 | 1.0096
1091.7 | 49.5 | 1.0096
1091.8 | 49.5 | 1.0096
1091.9 | 49.5 | 1.0096
1092 | 49.5 | 1.0096
1092.1 | 49.5 | 1.0096
1092.2 | 49.5 | 1.0096
1092.3 | 49.5 | 1.0096
1092.4 | 49.5 | 1.0096
1092.5 | 49.5 | 1.0096
1092.6 | 49.5 | 1.0096
1092.7 | 49.5 | 1.0096
1092.8 | 49.5 | 1.0098
1092.9 | 49.5 | 1.0098
1093 | 49.5 | 1.0098
1093.1 | 49.5 | 1.0098
1093.2 | 49.5 | 1.0098
1093.3 | 49.5 | 1.0098
1093.4 | 49.5 | 1.0098
1093.5 | 49.5 | 1.0098
1093.6 | 49.5 | 1.0098
1093.7 | 49.5 | 1.0098
1093.8 | 49.5 | 1.0096
1093.9 | 49.5 | 1.0096
1094 | 49.5 | 1.0096
1094.1 | 49.5 | 1.0096
1094.2 | 49.5 | 1.0096
1094.3 | 49.5 | 1.0096
1094.4 | 49.5 | 1.0096
1094.5 | 49.5 | 1.0096
1094.6 | 49.5 | 1.0096
1094.7 | 49.5 | 1.0096
1094.8 | 49.5 | 1.0096
1094.9 | 49.5 | 1.0096
1095 | 49.5 | 1.0096
1095.1 | 49.5 | 1.0096
1095.2 | 49.5 | 1.0096
1095.3 | 49.5 | 1.0096
1095.4 | 49.5 | 1.0096
1095.5 | 49.5 | 1.0096
1095.6 | 49.5 | 1.0096
1095.7 | 49.5 | 1.0096
1095.8 | 49.5 | 1.0096
1095.9 | 49.5 | 1.0096
1096 | 49.5 | 1.0096
1096.1 | 49.5 | 1.0096
1096.2 | 49.5 | 1.0096
1096.3 | 49.5 | 1.0096
1096.4 | 49.5 | 1.0096
1096.5 | 49.5 | 1.0096
1096.6 | 49.5 | 1.0096
1096.7 | 49.5 | 1.0096
1096.8 | 49.5 | 1.0096
1096.9 | 49.5 | 1.0096
1097 | 49.5 | 1.0096
1097.1 | 49.5 | 1.0096
1097.2 | 49.5 | 1.0096
1097.3 | 49.5 | 1.0096
1097.4 | 49.5 | 1.0096
1097.5 | 49.5 | 1.0096
1097.6 | 49.5 | 1.0096
1097.7 | 49.5 | 1.0096
1097.8 | 49.5 | 1.0096
1097.9 | 49.5 | 1.0096
1098 | 49.5 | 1.0096
1098.1 | 49.5 | 1.0096
1098.2 | 49.5 | 1.0096
1098.3 | 49.5 | 1.0096
1098.4 | 49.5 | 1.0096
1098.5 | 49.5 | 1.0096
1098.6 | 49.5 | 1.0096
1098.7 | 49.5 | 1.0096
1098.8 | 49.5 | 1.0096
1098.9 | 49.5 | 1.0096
1099 | 49.5 | 1.0096
1099.1 | 49.5 | 1.0096
1099.2 | 49.5 | 1.0096
1099.3 | 49.5 | 1.0096
1099.4 | 49.5 | 1.0096
1099.5 | 49.5 | 1.0096
1099.6 | 49.5 | 1.0096
1099.7 | 49.5 | 1.0096
1099.8 | 49.5 | 1.0096
1099.9 | 49.5 | 1.0096
1100 | 49.5 | 1.0096
1100.1 | 49.5 | 1.0096
1100.2 | 49.5 | 1.0096
1100.3 | 49.5 | 1.0096
1100.4 | 49.5 | 1.0096
1100.5 | 49.5 | 1.0096
1100.6 | 49.5 | 1.0096
1100.7 | 49.5 | 1.0096
1100.8 | 49.5 | 1.0096
1100.9 | 49.5 | 1.0096
1101 | 49.5 | 1.0096
1101.1 | 49.5 | 1.0096
1101.2 | 49.5 | 1.0096
1101.3 | 49.5 | 1.0096
1101.4 | 49.5 | 1.0096
1101.5 | 49.5 | 1.0096
1101.6 | 49.5 | 1.0096
1101.7 | 49.5 | 1.0096
1101.8 | 49.5 | 1.0096
1101.9 | 49.5 | 1.0096
1102 | 49.5 | 1.0096
1102.1 | 49.5 | 1.0096
1102.2 | 49.5 | 1.0096
1102.3 | 49.5 | 1.0096
1102.4 | 49.5 | 1.0096
1102.5 | 49.5 | 1.0096
1102.6 | 49.5 | 1.0096
1102.7 | 49.5 | 1.0096
1102.8 | 49.5 | 1.0096
1102.9 | 49.5 | 1.0096
1103 | 49.5 | 1.0096
1103.1 | 49.5 | 1.0096
1103.2 | 49.5 | 1.0096
1103.3 | 49.5 | 1.0096
1103.4 | 49.5 | 1.0096
1103.5 | 49.5 | 1.0096
1103.6 | 49.5 | 1.0096
1103.7 | 49.5 | 1.0096
1103.8 | 49.5 | 1.0096
1103.9 | 49.5 | 1.0096
1104 | 49.5 | 1.0096
1104.1 | 49.5 | 1.0096
1104.2 | 49.5 | 1.0096
1104.3 | 49.5 | 1.0096
1104.4 | 49.5 | 1.0098
1104.5 | 49.5 | 1.0098
1104.6 | 49.5 | 1.0098
1104.7 | 49.5 | 1.0098
1104.8 | 49.5 | 1.0098
1104.9 | 49.5 | 1.0098
1105 | 49.5 | 1.0098
1105.1 | 49.5 | 1.0098
1105.2 | 49.5 | 1.0098
1105.3 | 49.5 | 1.0098
1105.4 | 49.5 | 1.0098
1105.5 | 49.5 | 1.0098
1105.6 | 49.5 | 1.0098
1105.7 | 49.5 | 1.0098
1105.8 | 49.5 | 1.0098
1105.9 | 49.5 | 1.0098
1106 | 49.5 | 1.0098
1106.1 | 49.5 | 1.0098
1106.2 | 49.5 | 1.0098
1106.3 | 49.5 | 1.0098
1106.4 | 49.5 | 1.0098
1106.5 | 49.5 | 1.0098
1106.6 | 49.5 | 1.0096
1106.7 | 49.5 | 1.0096
1106.8 | 49.5 | 1.0096
1106.9 | 49.5 | 1.0096
1107 | 49.5 | 1.0096
1107.1 | 49.5 | 1.0096
1107.2 | 49.5 | 1.0096
1107.3 | 49.5 | 1.0096
1107.4 | 49.5 | 1.0096
1107.5 | 49.5 | 1.0096
1107.6 | 49.5 | 1.0096
1107.7 | 49.5 | 1.0096
1107.8 | 49.5 | 1.0096
1107.9 | 49.5 | 1.0096
1108 | 49.5 | 1.0096
1108.1 | 49.5 | 1.0096
1108.2 | 49.5 | 1.0096
1108.3 | 49.5 | 1.0096
1108.4 | 49.5 | 1.0096
1108.5 | 49.5 | 1.0096
1108.6 | 49.5 | 1.0096
1108.7 | 49.5 | 1.0096
1108.8 | 49.5 | 1.0096
1108.9 | 49.5 | 1.0096
1109 | 49.5 | 1.0096
1109.1 | 49.5 | 1.0096
1109.2 | 49.5 | 1.0096
1109.3 | 49.5 | 1.0096
1109.4 | 49.5 | 1.0096
1109.5 | 49.5 | 1.0096
1109.6 | 49.5 | 1.0096
1109.7 | 49.5 | 1.0096
1109.8 | 49.5 | 1.0096
1109.9 | 49.5 | 1.0096
1110 | 49.5 | 1.0096
1110.1 | 49.5 | 1.0096
1110.2 | 49.5 | 1.0096
1110.3 | 49.5 | 1.0096
1110.4 | 49.5 | 1.0096
1110.5 | 49.5 | 1.0096
1110.6 | 49.5 | 1.0096
1110.7 | 49.5 | 1.0096
1110.8 | 49.5 | 1.0096
1110.9 | 49.5 | 1.0096
1111 | 49.5 | 1.0096
1111.1 | 49.5 | 1.0096
1111.2 | 49.5 | 1.0096
1111.3 | 49.5 | 1.0096
1111.4 | 49.5 | 1.0096
1111.5 | 49.5 | 1.0096
1111.6 | 49.5 | 1.0096
1111.7 | 49.5 | 1.0096
1111.8 | 49.5 | 1.0096
1111.9 | 49.5 | 1.0096
1112 | 49.5 | 1.0096
1112.1 | 49.5 | 1.0096
1112.2 | 49.5 | 1.0096
1112.3 | 49.5 | 1.0096
1112.4 | 49.5 | 1.0096
1112.5 | 49.5 | 1.0096
1112.6 | 49.5 | 1.0096
1112.7 | 49.5 | 1.0096
1112.8 | 49.5 | 1.0096
1112.9 | 49.5 | 1.0096
1113 | 49.5 | 1.0096
1113.1 | 49.5 | 1.0096
1113.2 | 49.5 | 1.0096
1113.3 | 49.5 | 1.0096
1113.4 | 49.5 | 1.0096
1113.5 | 49.5 | 1.0096
1113.6 | 49.5 | 1.0096
1113.7 | 49.5 | 1.0096
1113.8 | 49.5 | 1.0096
1113.9 | 49.5 | 1.0096
1114 | 49.5 | 1.0096
1114.1 | 49.5 | 1.0096
1114.2 | 49.5 | 1.0096
1114.3 | 49.5 | 1.0096
1114.4 | 49.5 | 1.0096
1114.5 | 49.5 | 1.0096
1114.6 | 49.5 | 1.0096
1114.7 | 49.5 | 1.0096
1114.8 | 49.5 | 1.0096
1114.9 | 49.5 | 1.0096
1115 | 49.5 | 1.0096
1115.1 | 49.5 | 1.0096
1115.2 | 49.5 | 1.0096
1115.3 | 49.5 | 1.0096
1115.4 | 49.5 | 1.0096
1115.5 | 49.5 | 1.0096
1115.6 | 49.5 | 1.0096
1115.7 | 49.5 | 1.0096
1115.8 | 49.5 | 1.0096
1115.9 | 49.5 | 1.0096
1116 | 49.5 | 1.0096
1116.1 | 49.5 | 1.0096
1116.2 | 49.5 | 1.0096
1116.3 | 49.5 | 1.0096
1116.4 | 49.5 | 1.0096
1116.5 | 49.5 | 1.0096
1116.6 | 49.5 | 1.0096
1116.7 | 49.5 | 1.0096
1116.8 | 49.5 | 1.0096
1116.9 | 49.5 | 1.0096
1117 | 49.5 | 1.0096
1117.1 | 49.5 | 1.0096
1117.2 | 49.5 | 1.0096
1117.3 | 49.5 | 1.0096
1117.4 | 49.5 | 1.0096
1117.5 | 49.5 | 1.0096
1117.6 | 49.5 | 1.0096
1117.7 | 49.5 | 1.0096
1117.8 | 49.5 | 1.0096
1117.9 | 49.5 | 1.0096
1118 | 49.5 | 1.0096
1118.1 | 49.5 | 1.0096
1118.2 | 49.5 | 1.0096
1118.3 | 49.5 | 1.0096
1118.4 | 49.5 | 1.0096
1118.5 | 49.5 | 1.0096
1118.6 | 49.5 | 1.0096
1118.7 | 49.5 | 1.0096
1118.8 | 49.5 | 1.0096
1118.9 | 49.5 | 1.0096
1119 | 49.5 | 1.0096
1119.1 | 49.5 | 1.0096
1119.2 | 49.5 | 1.0096
1119.3 | 49.5 | 1.0096
1119.4 | 49.5 | 1.0096
1119.5 | 49.5 | 1.0096
1119.6 | 49.5 | 1.0096
1119.7 | 49.5 | 1.0096
1119.8 | 49.5 | 1.0096
1119.9 | 49.5 | 1.0096
1120 | 49.5 | 1.0096
1120.1 | 49.5 | 1.0096
1120.2 | 49.5 | 1.0096
1120.3 | 49.5 | 1.0096
1120.4 | 49.5 | 1.0096
1120.5 | 49.5 | 1.0096
1120.6 | 49.5 | 1.0096
1120.7 | 49.5 | 1.0096
1120.8 | 49.5 | 1.0096
1120.9 | 49.5 | 1.0096
1121 | 49.5 | 1.0096
1121.1 | 49.5 | 1.0096
1121.2 | 49.5 | 1.0096
1121.3 | 49.5 | 1.0096
1121.4 | 49.5 | 1.0096
1121.5 | 49.5 | 1.0096
1121.6 | 49.5 | 1.0096
1121.7 | 49.5 | 1.0096
1121.8 | 49.5 | 1.0096
1121.9 | 49.5 | 1.0096
1122 | 49.5 | 1.0096
1122.1 | 49.5 | 1.0096
1122.2 | 49.5 | 1.0096
1122.3 | 49.5 | 1.0096
1122.4 | 49.5 | 1.0098
1122.5 | 49.5 | 1.0098
1122.6 | 49.5 | 1.0098
1122.7 | 49.5 | 1.0098
1122.8 | 49.5 | 1.0098
1122.9 | 49.5 | 1.0098
1123 | 49.5 | 1.0098
1123.1 | 49.5 | 1.0098
1123.2 | 49.5 | 1.0098
1123.3 | 49.5 | 1.0098
1123.4 | 49.5 | 1.0098
1123.5 | 49.5 | 1.0096
1123.6 | 49.5 | 1.0096
1123.7 | 49.5 | 1.0096
1123.8 | 49.5 | 1.0096
1123.9 | 49.5 | 1.0096
1124 | 49.5 | 1.0096
1124.1 | 49.5 | 1.0096
1124.2 | 49.5 | 1.0096
1124.3 | 49.5 | 1.0096
1124.4 | 49.5 | 1.0096
1124.5 | 49.5 | 1.0096
1124.6 | 49.5 | 1.0096
1124.7 | 49.5 | 1.0096
1124.8 | 49.5 | 1.0096
1124.9 | 49.5 | 1.0096
1125 | 49.5 | 1.0096
1125.1 | 49.5 | 1.0096
1125.2 | 49.5 | 1.0096
1125.3 | 49.5 | 1.0096
1125.4 | 49.5 | 1.0096
1125.5 | 49.5 | 1.0096
1125.6 | 49.5 | 1.0096
1125.7 | 49.5 | 1.0096
1125.8 | 49.5 | 1.0096
1125.9 | 49.5 | 1.0096
1126 | 49.5 | 1.0096
1126.1 | 49.5 | 1.0096
1126.2 | 49.5 | 1.0096
1126.3 | 49.5 | 1.0096
1126.4 | 49.5 | 1.0096
1126.5 | 49.5 | 1.0096
1126.6 | 49.5 | 1.0096
1126.7 | 49.5 | 1.0096
1126.8 | 49.5 | 1.0096
1126.9 | 49.5 | 1.0096
1127 | 49.5 | 1.0096
1127.1 | 49.5 | 1.0096
1127.2 | 49.5 | 1.0096
1127.3 | 49.5 | 1.0096
1127.4 | 49.5 | 1.0096
1127.5 | 49.5 | 1.0096
1127.6 | 49.5 | 1.0096
1127.7 | 49.5 | 1.0096
1127.8 | 49.5 | 1.0096
1127.9 | 49.5 | 1.0096
1128 | 49.5 | 1.0096
1128.1 | 49.5 | 1.0096
1128.2 | 49.5 | 1.0096
1128.3 | 49.5 | 1.0096
1128.4 | 49.5 | 1.0096
1128.5 | 49.5 | 1.0096
1128.6 | 49.5 | 1.0096
1128.7 | 49.5 | 1.0096
1128.8 | 49.5 | 1.0096
1128.9 | 49.5 | 1.0096
1129 | 49.5 | 1.0096
1129.1 | 49.5 | 1.0096
1129.2 | 49.5 | 1.0096
1129.3 | 49.5 | 1.0096
1129.4 | 49.5 | 1.0096
1129.5 | 49.5 | 1.0096
1129.6 | 49.5 | 1.0096
1129.7 | 49.5 | 1.0096
1129.8 | 49.5 | 1.0096
1129.9 | 49.5 | 1.0096
1130 | 49.5 | 1.0096
1130.1 | 49.5 | 1.0096
1130.2 | 49.5 | 1.0096
1130.3 | 49.5 | 1.0096
1130.4 | 49.5 | 1.0096
1130.5 | 49.5 | 1.0096
1130.6 | 49.5 | 1.0096
1130.7 | 49.5 | 1.0096
1130.8 | 49.5 | 1.0096
1130.9 | 49.5 | 1.0096
1131 | 49.5 | 1.0096
1131.1 | 49.5 | 1.0096
1131.2 | 49.5 | 1.0096
1131.3 | 49.5 | 1.0096
1131.4 | 49.5 | 1.0096
1131.5 | 49.5 | 1.0096
1131.6 | 49.5 | 1.0096
1131.7 | 49.5 | 1.0096
1131.8 | 49.5 | 1.0096
1131.9 | 49.5 | 1.0096
1132 | 49.5 | 1.0096
1132.1 | 49.5 | 1.0096
1132.2 | 49.5 | 1.0096
1132.3 | 49.5 | 1.0096
1132.4 | 49.5 | 1.0096
1132.5 | 49.5 | 1.0096
1132.6 | 49.5 | 1.0096
1132.7 | 49.5 | 1.0096
1132.8 | 49.5 | 1.0096
1132.9 | 49.5 | 1.0096
1133 | 49.5 | 1.0096
1133.1 | 49.5 | 1.0096
1133.2 | 49.5 | 1.0096
1133.3 | 49.5 | 1.0096
1133.4 | 49.5 | 1.0096
1133.5 | 49.5 | 1.0096
1133.6 | 49.5 | 1.0096
1133.7 | 49.5 | 1.0096
1133.8 | 49.5 | 1.0096
1133.9 | 49.5 | 1.0096
1134 | 49.5 | 1.0096
1134.1 | 49.5 | 1.0096
1134.2 | 49.5 | 1.0096
1134.3 | 49.5 | 1.0096
1134.4 | 49.5 | 1.0096
1134.5 | 49.5 | 1.0096
1134.6 | 49.5 | 1.0096
1134.7 | 49.5 | 1.0096
1134.8 | 49.5 | 1.0096
1134.9 | 49.5 | 1.0096
1135 | 49.5 | 1.0096
1135.1 | 49.5 | 1.0096
1135.2 | 49.5 | 1.0096
1135.3 | 49.5 | 1.0096
1135.4 | 49.5 | 1.0096
1135.5 | 49.5 | 1.0096
1135.6 | 49.5 | 1.0096
1135.7 | 49.5 | 1.0096
1135.8 | 49.5 | 1.0096
1135.9 | 49.5 | 1.0096
1136 | 49.5 | 1.0096
1136.1 | 49.5 | 1.0096
1136.2 | 49.5 | 1.0096
1136.3 | 49.5 | 1.0096
1136.4 | 49.5 | 1.0096
1136.5 | 49.5 | 1.0096
1136.6 | 49.5 | 1.0096
1136.7 | 49.5 | 1.0096
1136.8 | 49.5 | 1.0096
1136.9 | 49.5 | 1.0096
1137 | 49.5 | 1.0096
1137.1 | 49.5 | 1.0096
1137.2 | 49.5 | 1.0096
1137.3 | 49.5 | 1.0096
1137.4 | 49.5 | 1.0096
1137.5 | 49.5 | 1.0096
1137.6 | 49.5 | 1.0096
1137.7 | 49.5 | 1.0096
1137.8 | 49.5 | 1.0096
1137.9 | 49.5 | 1.0096
1138 | 49.5 | 1.0096
1138.1 | 49.5 | 1.0096
1138.2 | 49.5 | 1.0096
1138.3 | 49.5 | 1.0096
1138.4 | 49.5 | 1.0096
1138.5 | 49.5 | 1.0096
1138.6 | 49.5 | 1.0096
1138.7 | 49.5 | 1.0096
1138.8 | 49.5 | 1.0096
1138.9 | 49.5 | 1.0096
1139 | 49.5 | 1.0096
1139.1 | 49.5 | 1.0096
1139.2 | 49.5 | 1.0096
1139.3 | 49.5 | 1.0096
1139.4 | 49.5 | 1.0096
1139.5 | 49.5 | 1.0096
1139.6 | 49.5 | 1.0096
1139.7 | 49.5 | 1.0096
1139.8 | 49.5 | 1.0096
1139.9 | 49.5 | 1.0096
1140 | 49.5 | 1.0096
1140.1 | 49.5 | 1.0096
1140.2 | 49.5 | 1.0096
1140.3 | 49.5 | 1.0096
1140.4 | 49.5 | 1.0096
1140.5 | 49.5 | 1.0096
1140.6 | 49.5 | 1.0096
1140.7 | 49.5 | 1.0096
1140.8 | 49.5 | 1.0096
1140.9 | 49.5 | 1.0096
1141 | 49.5 | 1.0096
1141.1 | 49.5 | 1.0096
1141.2 | 49.5 | 1.0096
1141.3 | 49.5 | 1.0096
1141.4 | 49.5 | 1.0096
1141.5 | 49.5 | 1.0096
1141.6 | 49.5 | 1.0096
1141.7 | 49.5 | 1.0096
1141.8 | 49.5 | 1.0096
1141.9 | 49.5 | 1.0096
1142 | 49.5 | 1.0096
1142.1 | 49.5 | 1.0096
1142.2 | 49.5 | 1.0096
1142.3 | 49.5 | 1.0096
1142.4 | 49.5 | 1.0096
1142.5 | 49.5 | 1.0096
1142.6 | 49.5 | 1.0096
1142.7 | 49.5 | 1.0096
1142.8 | 49.5 | 1.0096
1142.9 | 49.5 | 1.0096
1143 | 49.5 | 1.0096
1143.1 | 49.5 | 1.0096
1143.2 | 49.5 | 1.0096
1143.3 | 49.5 | 1.0096
1143.4 | 49.5 | 1.0096
1143.5 | 49.5 | 1.0096
1143.6 | 49.5 | 1.0096
1143.7 | 49.5 | 1.0096
1143.8 | 49.5 | 1.0096
1143.9 | 49.5 | 1.0096
1144 | 49.5 | 1.0096
1144.1 | 49.5 | 1.0096
1144.2 | 49.5 | 1.0096
1144.3 | 49.5 | 1.0096
1144.4 | 49.5 | 1.0096
1144.5 | 49.5 | 1.0096
1144.6 | 49.5 | 1.0096
1144.7 | 49.5 | 1.0096
1144.8 | 49.5 | 1.0096
1144.9 | 49.5 | 1.0096
1145 | 49.5 | 1.0096
1145.1 | 49.5 | 1.0096
1145.2 | 49.5 | 1.0096
1145.3 | 49.5 | 1.0096
1145.4 | 49.5 | 1.0096
1145.5 | 49.5 | 1.0096
1145.6 | 49.5 | 1.0096
1145.7 | 49.5 | 1.0096
1145.8 | 49.5 | 1.0096
1145.9 | 49.5 | 1.0096
1146 | 49.5 | 1.0096
1146.1 | 49.5 | 1.0096
1146.2 | 49.5 | 1.0096
1146.3 | 49.5 | 1.0096
1146.4 | 49.5 | 1.0096
1146.5 | 49.5 | 1.0096
1146.6 | 49.5 | 1.0096
1146.7 | 49.5 | 1.0096
1146.8 | 49.5 | 1.0096
1146.9 | 49.5 | 1.0096
1147 | 49.5 | 1.0096
1147.1 | 49.5 | 1.0096
1147.2 | 49.5 | 1.0096
1147.3 | 49.5 | 1.0096
1147.4 | 49.5 | 1.0096
1147.5 | 49.5 | 1.0096
1147.6 | 49.5 | 1.0096
1147.7 | 49.5 | 1.0096
1147.8 | 49.5 | 1.0096
1147.9 | 49.5 | 1.0096
1148 | 49.5 | 1.0096
1148.1 | 49.5 | 1.0096
1148.2 | 49.5 | 1.0096
1148.3 | 49.5 | 1.0096
1148.4 | 49.5 | 1.0096
1148.5 | 49.5 | 1.0096
1148.6 | 49.5 | 1.0096
1148.7 | 49.5 | 1.0096
1148.8 | 49.5 | 1.0096
1148.9 | 49.5 | 1.0096
1149 | 49.5 | 1.0096
1149.1 | 49.5 | 1.0096
1149.2 | 49.5 | 1.0096
1149.3 | 49.5 | 1.0096
1149.4 | 49.5 | 1.0096
1149.5 | 49.5 | 1.0096
1149.6 | 49.5 | 1.0096
1149.7 | 49.5 | 1.0096
1149.8 | 49.5 | 1.0096
1149.9 | 49.5 | 1.0096
1150 | 49.5 | 1.0096
1150.1 | 49.5 | 1.0096
1150.2 | 49.5 | 1.0096
1150.3 | 49.5 | 1.0096
1150.4 | 49.5 | 1.0096
1150.5 | 49.5 | 1.0096
1150.6 | 49.5 | 1.0096
1150.7 | 49.5 | 1.0096
1150.8 | 49.5 | 1.0096
1150.9 | 49.5 | 1.0096
1151 | 49.5 | 1.0096
1151.1 | 49.5 | 1.0096
1151.2 | 49.5 | 1.0096
1151.3 | 49.5 | 1.0096
1151.4 | 49.5 | 1.0096
1151.5 | 49.5 | 1.0096
1151.6 | 49.5 | 1.0096
1151.7 | 49.5 | 1.0096
1151.8 | 49.5 | 1.0096
1151.9 | 49.5 | 1.0096
1152 | 49.5 | 1.0096
1152.1 | 49.5 | 1.0096
1152.2 | 49.5 | 1.0096
1152.3 | 49.5 | 1.0096
1152.4 | 49.5 | 1.0096
1152.5 | 49.5 | 1.0096
1152.6 | 49.5 | 1.0096
1152.7 | 49.5 | 1.0096
1152.8 | 49.5 | 1.0096
1152.9 | 49.5 | 1.0096
1153 | 49.5 | 1.0096
1153.1 | 49.5 | 1.0096
1153.2 | 49.5 | 1.0096
1153.3 | 49.5 | 1.0096
1153.4 | 49.5 | 1.0096
1153.5 | 49.5 | 1.0096
1153.6 | 49.5 | 1.0096
1153.7 | 49.5 | 1.0096
1153.8 | 49.5 | 1.0096
1153.9 | 49.5 | 1.0096
1154 | 49.5 | 1.0096
1154.1 | 49.5 | 1.0096
1154.2 | 49.5 | 1.0096
1154.3 | 49.5 | 1.0096
1154.4 | 49.5 | 1.0096
1154.5 | 49.5 | 1.0096
1154.6 | 49.5 | 1.0096
1154.7 | 49.5 | 1.0096
1154.8 | 49.5 | 1.0096
1154.9 | 49.5 | 1.0096
1155 | 49.5 | 1.0096
1155.1 | 49.5 | 1.0096
1155.2 | 49.5 | 1.0096
1155.3 | 49.5 | 1.0096
1155.4 | 49.5 | 1.0096
1155.5 | 49.5 | 1.0096
1155.6 | 49.5 | 1.0096
1155.7 | 49.5 | 1.0096
1155.8 | 49.5 | 1.0096
1155.9 | 49.5 | 1.0096
1156 | 49.5 | 1.0096
1156.1 | 49.5 | 1.0096
1156.2 | 49.5 | 1.0096
1156.3 | 49.5 | 1.0096
1156.4 | 49.5 | 1.0096
1156.5 | 49.5 | 1.0096
1156.6 | 49.5 | 1.0096
1156.7 | 49.5 | 1.0096
1156.8 | 49.5 | 1.0096
1156.9 | 49.5 | 1.0096
1157 | 49.5 | 1.0096
1157.1 | 49.5 | 1.0096
1157.2 | 49.5 | 1.0096
1157.3 | 49.5 | 1.0096
1157.4 | 49.5 | 1.0096
1157.5 | 49.5 | 1.0096
1157.6 | 49.5 | 1.0096
1157.7 | 49.5 | 1.0096
1157.8 | 49.5 | 1.0096
1157.9 | 49.5 | 1.0096
1158 | 49.5 | 1.0096
1158.1 | 49.5 | 1.0096
1158.2 | 49.5 | 1.0096
1158.3 | 49.5 | 1.0096
1158.4 | 49.5 | 1.0096
1158.5 | 49.5 | 1.0096
1158.6 | 49.5 | 1.0096
1158.7 | 49.5 | 1.0096
1158.8 | 49.5 | 1.0096
1158.9 | 49.5 | 1.0096
1159 | 49.5 | 1.0096
1159.1 | 49.5 | 1.0096
1159.2 | 49.5 | 1.0096
1159.3 | 49.5 | 1.0096
1159.4 | 49.5 | 1.0096
1159.5 | 49.5 | 1.0096
1159.6 | 49.5 | 1.0096
1159.7 | 49.5 | 1.0096
1159.8 | 49.5 | 1.0096
1159.9 | 49.5 | 1.0096
1160 | 49.5 | 1.0096
1160.1 | 49.5 | 1.0096
1160.2 | 49.5 | 1.0096
1160.3 | 49.5 | 1.0096
1160.4 | 49.5 | 1.0096
1160.5 | 49.5 | 1.0096
1160.6 | 49.5 | 1.0096
1160.7 | 49.5 | 1.0096
1160.8 | 49.5 | 1.0096
1160.9 | 49.5 | 1.0096
1161 | 49.5 | 1.0096
1161.1 | 49.5 | 1.0096
1161.2 | 49.5 | 1.0096
1161.3 | 49.5 | 1.0096
1161.4 | 49.5 | 1.0096
1161.5 | 49.5 | 1.0096
1161.6 | 49.5 | 1.0096
1161.7 | 49.5 | 1.0096
1161.8 | 49.5 | 1.0096
1161.9 | 49.5 | 1.0096
1162 | 49.5 | 1.0096
1162.1 | 49.5 | 1.0096
1162.2 | 49.5 | 1.0096
1162.3 | 49.5 | 1.0096
1162.4 | 49.5 | 1.0096
1162.5 | 49.5 | 1.0098
1162.6 | 49.5 | 1.0098
1162.7 | 49.5 | 1.0098
1162.8 | 49.5 | 1.0098
1162.9 | 49.5 | 1.0098
1163 | 49.5 | 1.0098
1163.1 | 49.5 | 1.0098
1163.2 | 49.5 | 1.0098
1163.3 | 49.5 | 1.0096
1163.4 | 49.5 | 1.0096
1163.5 | 49.5 | 1.0096
1163.6 | 49.5 | 1.0096
1163.7 | 49.5 | 1.0096
1163.8 | 49.5 | 1.0096
1163.9 | 49.5 | 1.0096
1164 | 49.5 | 1.0096
1164.1 | 49.5 | 1.0096
1164.2 | 49.5 | 1.0096
1164.3 | 49.5 | 1.0096
1164.4 | 49.5 | 1.0096
1164.5 | 49.5 | 1.0096
1164.6 | 49.5 | 1.0098
1164.7 | 49.5 | 1.0098
1164.8 | 49.5 | 1.0098
1164.9 | 49.5 | 1.0096
1165 | 49.5 | 1.0096
1165.1 | 49.5 | 1.0096
1165.2 | 49.5 | 1.0096
1165.3 | 49.5 | 1.0096
1165.4 | 49.5 | 1.0096
1165.5 | 49.5 | 1.0096
1165.6 | 49.5 | 1.0096
1165.7 | 49.5 | 1.0098
1165.8 | 49.5 | 1.0098
1165.9 | 49.5 | 1.0098
1166 | 49.5 | 1.0098
1166.1 | 49.5 | 1.0098
1166.2 | 49.5 | 1.0098
1166.3 | 49.5 | 1.0098
1166.4 | 49.5 | 1.0098
1166.5 | 49.5 | 1.0098
1166.6 | 49.5 | 1.0098
1166.7 | 49.5 | 1.0098
1166.8 | 49.5 | 1.0098
1166.9 | 49.5 | 1.0098
1167 | 49.5 | 1.0098
1167.1 | 49.5 | 1.0098
1167.2 | 49.5 | 1.0098
1167.3 | 49.5 | 1.0098
1167.4 | 49.5 | 1.0098
1167.5 | 49.5 | 1.0098
1167.6 | 49.5 | 1.0098
1167.7 | 49.5 | 1.0098
1167.8 | 49.5 | 1.0098
1167.9 | 49.5 | 1.0098
1168 | 49.5 | 1.0098
1168.1 | 49.5 | 1.0096
1168.2 | 49.5 | 1.0096
1168.3 | 49.5 | 1.0096
1168.4 | 49.5 | 1.0096
1168.5 | 49.5 | 1.0096
1168.6 | 49.5 | 1.0096
1168.7 | 49.5 | 1.0096
1168.8 | 49.5 | 1.0096
1168.9 | 49.5 | 1.0096
1169 | 49.5 | 1.0096
1169.1 | 49.5 | 1.0096
1169.2 | 49.5 | 1.0096
1169.3 | 49.5 | 1.0096
1169.4 | 49.5 | 1.0096
1169.5 | 49.5 | 1.0096
1169.6 | 49.5 | 1.0096
1169.7 | 49.5 | 1.0096
1169.8 | 49.5 | 1.0096
1169.9 | 49.5 | 1.0096
1170 | 49.5 | 1.0096
1170.1 | 49.5 | 1.0096
1170.2 | 49.5 | 1.0096
1170.3 | 49.5 | 1.0096
1170.4 | 49.5 | 1.0096
1170.5 | 49.5 | 1.0096
1170.6 | 49.5 | 1.0096
1170.7 | 49.5 | 1.0096
1170.8 | 49.5 | 1.0096
1170.9 | 49.5 | 1.0096
1171 | 49.5 | 1.0096
1171.1 | 49.5 | 1.0096
1171.2 | 49.5 | 1.0096
1171.3 | 49.5 | 1.0096
1171.4 | 49.5 | 1.0096
1171.5 | 49.5 | 1.0096
1171.6 | 49.5 | 1.0096
1171.7 | 49.5 | 1.0096
1171.8 | 49.5 | 1.0096
1171.9 | 49.5 | 1.0096
1172 | 49.5 | 1.0096
1172.1 | 49.5 | 1.0096
1172.2 | 49.5 | 1.0096
1172.3 | 49.5 | 1.0096
1172.4 | 49.5 | 1.0096
1172.5 | 49.5 | 1.0096
1172.6 | 49.5 | 1.0096
1172.7 | 49.5 | 1.0096
1172.8 | 49.5 | 1.0096
1172.9 | 49.5 | 1.0098
1173 | 49.5 | 1.0098
1173.1 | 49.5 | 1.0098
1173.2 | 49.5 | 1.0098
1173.3 | 49.5 | 1.0098
1173.4 | 49.5 | 1.0098
1173.5 | 49.5 | 1.0098
1173.6 | 49.5 | 1.0098
1173.7 | 49.5 | 1.0098
1173.8 | 49.5 | 1.0098
1173.9 | 49.5 | 1.0098
1174 | 49.5 | 1.0098
1174.1 | 49.5 | 1.0098
1174.2 | 49.5 | 1.0098
1174.3 | 49.5 | 1.0098
1174.4 | 49.5 | 1.0098
1174.5 | 49.5 | 1.0098
1174.6 | 49.5 | 1.0098
1174.7 | 49.5 | 1.0098
1174.8 | 49.5 | 1.0098
1174.9 | 49.5 | 1.0098
1175 | 49.5 | 1.0098
1175.1 | 49.5 | 1.0096
1175.2 | 49.5 | 1.0096
1175.3 | 49.5 | 1.0096
1175.4 | 49.5 | 1.0096
1175.5 | 49.5 | 1.0096
1175.6 | 49.5 | 1.0096
1175.7 | 49.5 | 1.0096
1175.8 | 49.5 | 1.0096
1175.9 | 49.5 | 1.0096
1176 | 49.5 | 1.0096
1176.1 | 49.5 | 1.0096
1176.2 | 49.5 | 1.0096
1176.3 | 49.5 | 1.0096
1176.4 | 49.5 | 1.0096
1176.5 | 49.5 | 1.0096
1176.6 | 49.5 | 1.0096
1176.7 | 49.5 | 1.0096
1176.8 | 49.5 | 1.0096
1176.9 | 49.5 | 1.0096
1177 | 49.5 | 1.0096
1177.1 | 49.5 | 1.0096
1177.2 | 49.5 | 1.0096
1177.3 | 49.5 | 1.0096
1177.4 | 49.5 | 1.0096
1177.5 | 49.5 | 1.0096
1177.6 | 49.5 | 1.0096
1177.7 | 49.5 | 1.0096
1177.8 | 49.5 | 1.0096
1177.9 | 49.5 | 1.0096
1178 | 49.5 | 1.0096
1178.1 | 49.5 | 1.0096
1178.2 | 49.5 | 1.0096
1178.3 | 49.5 | 1.0096
1178.4 | 49.5 | 1.0096
1178.5 | 49.5 | 1.0096
1178.6 | 49.5 | 1.0096
1178.7 | 49.5 | 1.0096
1178.8 | 49.5 | 1.0096
1178.9 | 49.5 | 1.0096
1179 | 49.5 | 1.0096
1179.1 | 49.5 | 1.0096
1179.2 | 49.5 | 1.0096
1179.3 | 49.5 | 1.0096
1179.4 | 49.5 | 1.0096
1179.5 | 49.5 | 1.0096
1179.6 | 49.5 | 1.0096
1179.7 | 49.5 | 1.0096
1179.8 | 49.5 | 1.0096
1179.9 | 49.5 | 1.0096
1180 | 49.5 | 1.0096
1180.1 | 49.5 | 1.0096
1180.2 | 49.5 | 1.0096
1180.3 | 49.5 | 1.0096
1180.4 | 49.5 | 1.0096
1180.5 | 49.5 | 1.0096
1180.6 | 49.5 | 1.0096
1180.7 | 49.5 | 1.0096
1180.8 | 49.5 | 1.0096
1180.9 | 49.5 | 1.0096
1181 | 49.5 | 1.0096
1181.1 | 49.5 | 1.0096
1181.2 | 49.5 | 1.0096
1181.3 | 49.5 | 1.0096
1181.4 | 49.5 | 1.0096
1181.5 | 49.5 | 1.0096
1181.6 | 49.5 | 1.0096
1181.7 | 49.5 | 1.0096
1181.8 | 49.5 | 1.0096
1181.9 | 49.5 | 1.0096
1182 | 49.5 | 1.0096
1182.1 | 49.5 | 1.0096
1182.2 | 49.5 | 1.0096
1182.3 | 49.5 | 1.0096
1182.4 | 49.5 | 1.0096
1182.5 | 49.5 | 1.0096
1182.6 | 49.5 | 1.0096
1182.7 | 49.5 | 1.0096
1182.8 | 49.5 | 1.0096
1182.9 | 49.5 | 1.0096
1183 | 49.5 | 1.0096
1183.1 | 49.5 | 1.0096
1183.2 | 49.5 | 1.0096
1183.3 | 49.5 | 1.0096
1183.4 | 49.5 | 1.0096
1183.5 | 49.5 | 1.0096
1183.6 | 49.5 | 1.0096
1183.7 | 49.5 | 1.0096
1183.8 | 49.5 | 1.0096
1183.9 | 49.5 | 1.0096
1184 | 49.5 | 1.0096
1184.1 | 49.5 | 1.0096
1184.2 | 49.5 | 1.0096
1184.3 | 49.5 | 1.0096
1184.4 | 49.5 | 1.0096
1184.5 | 49.5 | 1.0096
1184.6 | 49.5 | 1.0096
1184.7 | 49.5 | 1.0096
1184.8 | 49.5 | 1.0096
1184.9 | 49.5 | 1.0096
1185 | 49.5 | 1.0096
1185.1 | 49.5 | 1.0096
1185.2 | 49.5 | 1.0096
1185.3 | 49.5 | 1.0096
1185.4 | 49.5 | 1.0096
1185.5 | 49.5 | 1.0096
1185.6 | 49.5 | 1.0096
1185.7 | 49.5 | 1.0096
1185.8 | 49.5 | 1.0096
1185.9 | 49.5 | 1.0096
1186 | 49.5 | 1.0096
1186.1 | 49.5 | 1.0096
1186.2 | 49.5 | 1.0096
1186.3 | 49.5 | 1.0096
1186.4 | 49.5 | 1.0096
1186.5 | 49.5 | 1.0096
1186.6 | 49.5 | 1.0096
1186.7 | 49.5 | 1.0096
1186.8 | 49.5 | 1.0096
1186.9 | 49.5 | 1.0096
1187 | 49.5 | 1.0096
1187.1 | 49.5 | 1.0096
1187.2 | 49.5 | 1.0098
1187.3 | 49.5 | 1.0098
1187.4 | 49.5 | 1.0098
1187.5 | 49.5 | 1.0098
1187.6 | 49.5 | 1.0098
1187.7 | 49.5 | 1.0098
1187.8 | 49.5 | 1.0098
1187.9 | 49.5 | 1.0098
1188 | 49.5 | 1.0098
1188.1 | 49.5 | 1.0098
1188.2 | 49.5 | 1.0098
1188.3 | 49.5 | 1.0096
1188.4 | 49.5 | 1.0096
1188.5 | 49.5 | 1.0096
1188.6 | 49.5 | 1.0096
1188.7 | 49.5 | 1.0098
1188.8 | 49.5 | 1.0098
1188.9 | 49.5 | 1.0098
1189 | 49.5 | 1.0098
1189.1 | 49.5 | 1.0098
1189.2 | 49.5 | 1.0098
1189.3 | 49.5 | 1.0098
1189.4 | 49.5 | 1.0098
1189.5 | 49.5 | 1.0098
1189.6 | 49.5 | 1.0098
1189.7 | 49.5 | 1.0098
1189.8 | 49.5 | 1.0098
1189.9 | 49.5 | 1.0096
1190 | 49.5 | 1.0096
1190.1 | 49.5 | 1.0096
1190.2 | 49.5 | 1.0096
1190.3 | 49.5 | 1.0096
1190.4 | 49.5 | 1.0096
1190.5 | 49.5 | 1.0096
1190.6 | 49.5 | 1.0096
1190.7 | 49.5 | 1.0096
1190.8 | 49.5 | 1.0096
1190.9 | 49.5 | 1.0096
1191 | 49.5 | 1.0096
1191.1 | 49.5 | 1.0096
1191.2 | 49.5 | 1.0096
1191.3 | 49.5 | 1.0096
1191.4 | 49.5 | 1.0096
1191.5 | 49.5 | 1.0096
1191.6 | 49.5 | 1.0096
1191.7 | 49.5 | 1.0096
1191.8 | 49.5 | 1.0096
1191.9 | 49.5 | 1.0096
1192 | 49.5 | 1.0096
1192.1 | 49.5 | 1.0096
1192.2 | 49.5 | 1.0096
1192.3 | 49.5 | 1.0096
1192.4 | 49.5 | 1.0096
1192.5 | 49.5 | 1.0096
1192.6 | 49.5 | 1.0096
1192.7 | 49.5 | 1.0096
1192.8 | 49.5 | 1.0096
1192.9 | 49.5 | 1.0096
1193 | 49.5 | 1.0096
1193.1 | 49.5 | 1.0096
1193.2 | 49.5 | 1.0096
1193.3 | 49.5 | 1.0096
1193.4 | 49.5 | 1.0096
1193.5 | 49.5 | 1.0096
1193.6 | 49.5 | 1.0096
1193.7 | 49.5 | 1.0096
1193.8 | 49.5 | 1.0096
1193.9 | 49.5 | 1.0096
1194 | 49.5 | 1.0096
1194.1 | 49.5 | 1.0096
1194.2 | 49.5 | 1.0098
1194.3 | 49.5 | 1.0098
1194.4 | 49.5 | 1.0098
1194.5 | 49.5 | 1.0098
1194.6 | 49.5 | 1.0098
1194.7 | 49.5 | 1.0098
1194.8 | 49.5 | 1.0098
1194.9 | 49.5 | 1.0098
1195 | 49.5 | 1.0098
1195.1 | 49.5 | 1.0098
1195.2 | 49.5 | 1.0098
1195.3 | 49.5 | 1.0098
1195.4 | 49.5 | 1.0096
1195.5 | 49.5 | 1.0096
1195.6 | 49.5 | 1.0096
1195.7 | 49.5 | 1.0096
1195.8 | 49.5 | 1.0096
1195.9 | 49.5 | 1.0096
1196 | 49.5 | 1.0096
1196.1 | 49.5 | 1.0096
1196.2 | 49.5 | 1.0096
1196.3 | 49.5 | 1.0096
1196.4 | 49.5 | 1.0096
1196.5 | 49.5 | 1.0096
1196.6 | 49.5 | 1.0096
1196.7 | 49.5 | 1.0096
1196.8 | 49.5 | 1.0096
1196.9 | 49.5 | 1.0096
1197 | 49.5 | 1.0096
1197.1 | 49.5 | 1.0096
1197.2 | 49.5 | 1.0096
1197.3 | 49.5 | 1.0096
1197.4 | 49.5 | 1.0096
1197.5 | 49.5 | 1.0096
1197.6 | 49.5 | 1.0096
1197.7 | 49.5 | 1.0096
1197.8 | 49.5 | 1.0096
1197.9 | 49.5 | 1.0096
1198 | 49.5 | 1.0096
1198.1 | 49.5 | 1.0096
1198.2 | 49.5 | 1.0096
1198.3 | 49.5 | 1.0096
1198.4 | 49.5 | 1.0096
1198.5 | 49.5 | 1.0096
1198.6 | 49.5 | 1.0096
1198.7 | 49.5 | 1.0096
1198.8 | 49.5 | 1.0096
1198.9 | 49.5 | 1.0096
1199 | 49.5 | 1.0096
1199.1 | 49.5 | 1.0096
1199.2 | 49.5 | 1.0096
1199.3 | 49.5 | 1.0096
1199.4 | 49.5 | 1.0096
1199.5 | 49.5 | 1.0096
1199.6 | 49.5 | 1.0096
1199.7 | 49.5 | 1.0096
1199.8 | 49.5 | 1.0096
1199.9 | 49.5 | 1.0096
1200 | 49.5 | 1.0096
1200.1 | 49.5 | 1.0096
1200.2 | 49.5 | 1.0096
1200.3 | 49.5 | 1.0096
1200.4 | 49.5 | 1.0096
1200.5 | 49.5 | 1.0096
1200.6 | 49.5 | 1.0096
1200.7 | 49.5 | 1.0096
1200.8 | 49.5 | 1.0096
1200.9 | 49.5 | 1.0096
1201 | 49.5 | 1.0096
1201.1 | 49.5 | 1.0096
1201.2 | 49.5 | 1.0096
1201.3 | 49.5 | 1.0096
1201.4 | 49.5 | 1.0096
1201.5 | 49.5 | 1.0096
1201.6 | 49.5 | 1.0096
1201.7 | 49.5 | 1.0096
1201.8 | 49.5 | 1.0096
1201.9 | 49.5 | 1.0096
1202 | 49.5 | 1.0096
1202.1 | 49.5 | 1.0096
1202.2 | 49.5 | 1.0096
1202.3 | 49.5 | 1.0096
1202.4 | 49.5 | 1.0096
1202.5 | 49.5 | 1.0096
1202.6 | 49.5 | 1.0096
1202.7 | 49.5 | 1.0096
1202.8 | 49.5 | 1.0096
1202.9 | 49.5 | 1.0096
1203 | 49.5 | 1.0096
1203.1 | 49.5 | 1.0096
1203.2 | 49.5 | 1.0096
1203.3 | 49.5 | 1.0096
1203.4 | 49.5 | 1.0096
1203.5 | 49.5 | 1.0096
1203.6 | 49.5 | 1.0096
1203.7 | 49.5 | 1.0096
1203.8 | 49.5 | 1.0096
1203.9 | 49.5 | 1.0096
1204 | 49.5 | 1.0096
1204.1 | 49.5 | 1.0096
1204.2 | 49.5 | 1.0096
1204.3 | 49.5 | 1.0096
1204.4 | 49.5 | 1.0096
1204.5 | 49.5 | 1.0096
1204.6 | 49.5 | 1.0096
1204.7 | 49.5 | 1.0096
1204.8 | 49.5 | 1.0096
1204.9 | 49.5 | 1.0096
1205 | 49.5 | 1.0096
1205.1 | 49.5 | 1.0096
1205.2 | 49.5 | 1.0096
1205.3 | 49.5 | 1.0096
1205.4 | 49.5 | 1.0096
1205.5 | 49.5 | 1.0096
1205.6 | 49.5 | 1.0096
1205.7 | 49.5 | 1.0096
1205.8 | 49.5 | 1.0096
1205.9 | 49.5 | 1.0096
1206 | 49.5 | 1.0096
1206.1 | 49.5 | 1.0096
1206.2 | 49.5 | 1.0096
1206.3 | 49.5 | 1.0096
1206.4 | 49.5 | 1.0096
1206.5 | 49.5 | 1.0096
1206.6 | 49.5 | 1.0096
1206.7 | 49.5 | 1.0096
1206.8 | 49.5 | 1.0096
1206.9 | 49.5 | 1.0096
1207 | 49.5 | 1.0098
1207.1 | 49.5 | 1.0098
1207.2 | 49.5 | 1.0098
1207.3 | 49.5 | 1.0098
1207.4 | 49.5 | 1.0098
1207.5 | 49.5 | 1.0098
1207.6 | 49.5 | 1.0098
1207.7 | 49.5 | 1.0098
1207.8 | 49.5 | 1.0098
1207.9 | 49.5 | 1.0098
1208 | 49.5 | 1.0098
1208.1 | 49.5 | 1.0098
1208.2 | 49.5 | 1.0096
1208.3 | 49.5 | 1.0096
1208.4 | 49.5 | 1.0096
1208.5 | 49.5 | 1.0096
1208.6 | 49.5 | 1.0096
1208.7 | 49.5 | 1.0096
1208.8 | 49.5 | 1.0096
1208.9 | 49.5 | 1.0096
1209 | 49.5 | 1.0096
1209.1 | 49.5 | 1.0096
1209.2 | 49.5 | 1.0096
1209.3 | 49.5 | 1.0096
1209.4 | 49.5 | 1.0096
1209.5 | 49.5 | 1.0096
1209.6 | 49.5 | 1.0096
1209.7 | 49.5 | 1.0096
1209.8 | 49.5 | 1.0096
1209.9 | 49.5 | 1.0096
1210 | 49.5 | 1.0096
1210.1 | 49.5 | 1.0096
1210.2 | 49.5 | 1.0096
1210.3 | 49.5 | 1.0096
1210.4 | 49.5 | 1.0096
1210.5 | 49.5 | 1.0096
1210.6 | 49.5 | 1.0096
1210.7 | 49.5 | 1.0096
1210.8 | 49.5 | 1.0096
1210.9 | 49.5 | 1.0096
1211 | 49.5 | 1.0096
1211.1 | 49.5 | 1.0096
1211.2 | 49.5 | 1.0096
1211.3 | 49.5 | 1.0096
1211.4 | 49.5 | 1.0096
1211.5 | 49.5 | 1.0096
1211.6 | 49.5 | 1.0096
1211.7 | 49.5 | 1.0096
1211.8 | 49.5 | 1.0096
1211.9 | 49.5 | 1.0096
1212 | 49.5 | 1.0096
1212.1 | 49.5 | 1.0096
1212.2 | 49.5 | 1.0096
1212.3 | 49.5 | 1.0096
1212.4 | 49.5 | 1.0096
1212.5 | 49.5 | 1.0096
1212.6 | 49.5 | 1.0096
1212.7 | 49.5 | 1.0096
1212.8 | 49.5 | 1.0096
1212.9 | 49.5 | 1.0098
1213 | 49.5 | 1.0098
1213.1 | 49.5 | 1.0098
1213.2 | 49.5 | 1.0098
1213.3 | 49.5 | 1.0098
1213.4 | 49.5 | 1.0098
1213.5 | 49.5 | 1.0098
1213.6 | 49.5 | 1.0098
1213.7 | 49.5 | 1.0098
1213.8 | 49.5 | 1.0098
1213.9 | 49.5 | 1.0098
1214 | 49.5 | 1.0098
1214.1 | 49.5 | 1.0096
1214.2 | 49.5 | 1.0096
1214.3 | 49.5 | 1.0098
1214.4 | 49.5 | 1.0098
1214.5 | 49.5 | 1.0098
1214.6 | 49.5 | 1.0098
1214.7 | 49.5 | 1.0098
1214.8 | 49.5 | 1.0098
1214.9 | 49.5 | 1.0096
1215 | 49.5 | 1.0096
1215.1 | 49.5 | 1.0096
1215.2 | 49.5 | 1.0096
1215.3 | 49.5 | 1.0096
1215.4 | 49.5 | 1.0096
1215.5 | 49.5 | 1.0096
1215.6 | 49.5 | 1.0096
1215.7 | 49.5 | 1.0096
1215.8 | 49.5 | 1.0096
1215.9 | 49.5 | 1.0096
1216 | 49.5 | 1.0096
1216.1 | 49.5 | 1.0098
1216.2 | 49.5 | 1.0098
1216.3 | 49.5 | 1.0098
1216.4 | 49.5 | 1.0098
1216.5 | 49.5 | 1.0098
1216.6 | 49.5 | 1.0098
1216.7 | 49.5 | 1.0096
1216.8 | 49.5 | 1.0096
1216.9 | 49.5 | 1.0096
1217 | 49.5 | 1.0096
1217.1 | 49.5 | 1.0096
1217.2 | 49.5 | 1.0096
1217.3 | 49.5 | 1.0096
1217.4 | 49.5 | 1.0096
1217.5 | 49.5 | 1.0094
1217.6 | 49.5 | 1.0094
1217.7 | 49.5 | 1.0094
1217.8 | 49.5 | 1.0094
1217.9 | 49.5 | 1.0094
1218 | 49.5 | 1.0094
1218.1 | 49.5 | 1.0094
1218.2 | 49.5 | 1.0094
1218.3 | 49.5 | 1.0094
1218.4 | 49.5 | 1.0094
1218.5 | 49.5 | 1.0094
1218.6 | 49.5 | 1.0094
1218.7 | 49.5 | 1.0094
1218.8 | 49.5 | 1.0094
1218.9 | 49.5 | 1.0094
1219 | 49.5 | 1.0096
1219.1 | 49.5 | 1.0096
1219.2 | 49.5 | 1.0096
1219.3 | 49.5 | 1.0096
1219.4 | 49.5 | 1.0096
1219.5 | 49.5 | 1.0096
1219.6 | 49.5 | 1.0096
1219.7 | 49.5 | 1.0096
1219.8 | 49.5 | 1.0096
1219.9 | 49.5 | 1.0096
1220 | 49.5 | 1.0098
1220.1 | 49.5 | 1.0098
1220.2 | 49.5 | 1.0098
1220.3 | 49.5 | 1.0098
1220.4 | 49.5 | 1.0098
1220.5 | 49.5 | 1.0098
1220.6 | 49.5 | 1.0098
1220.7 | 49.5 | 1.0098
1220.8 | 49.5 | 1.0098
1220.9 | 49.5 | 1.0096
1221 | 49.5 | 1.0096
1221.1 | 49.5 | 1.0096
1221.2 | 49.5 | 1.0098
1221.3 | 49.5 | 1.0098
1221.4 | 49.5 | 1.0098
1221.5 | 49.5 | 1.0098
1221.6 | 49.5 | 1.0098
1221.7 | 49.5 | 1.0098
1221.8 | 49.5 | 1.0098
1221.9 | 49.5 | 1.0098
1222 | 49.5 | 1.0098
1222.1 | 49.5 | 1.0098
1222.2 | 49.5 | 1.0098
1222.3 | 49.5 | 1.0098
1222.4 | 49.5 | 1.0098
1222.5 | 49.5 | 1.0098
1222.6 | 49.5 | 1.0096
1222.7 | 49.5 | 1.0096
1222.8 | 49.5 | 1.0096
1222.9 | 49.5 | 1.0096
1223 | 49.5 | 1.0096
1223.1 | 49.5 | 1.0096
1223.2 | 49.5 | 1.0096
1223.3 | 49.5 | 1.0096
1223.4 | 49.5 | 1.0096
1223.5 | 49.5 | 1.0096
1223.6 | 49.5 | 1.0098
1223.7 | 49.5 | 1.0096
1223.8 | 49.5 | 1.0096
1223.9 | 49.5 | 1.0096
1224 | 49.5 | 1.0096
1224.1 | 49.5 | 1.0096
1224.2 | 49.5 | 1.0098
1224.3 | 49.5 | 1.0098
1224.4 | 49.5 | 1.0098
1224.5 | 49.5 | 1.0098
1224.6 | 49.5 | 1.0096
1224.7 | 49.5 | 1.0096
1224.8 | 49.5 | 1.0096
1224.9 | 49.5 | 1.0096
1225 | 49.5 | 1.0096
1225.1 | 49.5 | 1.0096
1225.2 | 49.5 | 1.0096
1225.3 | 49.5 | 1.0096
1225.4 | 49.5 | 1.0096
1225.5 | 49.5 | 1.0096
1225.6 | 49.5 | 1.0096
1225.7 | 49.5 | 1.0096
1225.8 | 49.5 | 1.0096
1225.9 | 49.5 | 1.0096
1226 | 49.5 | 1.0094
1226.1 | 49.5 | 1.0094
1226.2 | 49.5 | 1.0094
1226.3 | 49.5 | 1.0094
1226.4 | 49.5 | 1.0094
1226.5 | 49.5 | 1.0094
1226.6 | 49.5 | 1.0094
1226.7 | 49.5 | 1.0094
1226.8 | 49.5 | 1.0094
1226.9 | 49.5 | 1.0094
1227 | 49.5 | 1.0094
1227.1 | 49.5 | 1.0094
1227.2 | 49.5 | 1.0096
1227.3 | 49.5 | 1.0096
1227.4 | 49.5 | 1.0096
1227.5 | 49.5 | 1.0096
1227.6 | 49.5 | 1.0096
1227.7 | 49.5 | 1.0096
1227.8 | 49.5 | 1.0096
1227.9 | 49.5 | 1.0096
1228 | 49.5 | 1.0096
1228.1 | 49.5 | 1.0096
1228.2 | 49.5 | 1.0096
1228.3 | 49.5 | 1.0096
1228.4 | 49.5 | 1.0096
1228.5 | 49.5 | 1.0096
1228.6 | 49.5 | 1.0096
1228.7 | 49.5 | 1.0096
1228.8 | 49.5 | 1.0096
1228.9 | 49.5 | 1.0096
1229 | 49.5 | 1.0096
1229.1 | 49.5 | 1.0096
1229.2 | 49.5 | 1.0096
1229.3 | 49.5 | 1.0096
1229.4 | 49.5 | 1.0096
1229.5 | 49.5 | 1.0098
1229.6 | 49.5 | 1.0098
1229.7 | 49.5 | 1.0098
1229.8 | 49.5 | 1.0098
1229.9 | 49.5 | 1.0098
1230 | 49.5 | 1.0098
1230.1 | 49.5 | 1.0096
1230.2 | 49.5 | 1.0096
1230.3 | 49.5 | 1.0096
1230.4 | 49.5 | 1.0096
1230.5 | 49.5 | 1.0096
1230.6 | 49.5 | 1.0096
1230.7 | 49.5 | 1.0096
1230.8 | 49.5 | 1.0096
1230.9 | 49.5 | 1.0096
1231 | 49.5 | 1.0096
1231.1 | 49.5 | 1.0096
1231.2 | 49.5 | 1.0096
1231.3 | 49.5 | 1.0096
1231.4 | 49.5 | 1.0098
1231.5 | 49.5 | 1.0098
1231.6 | 49.5 | 1.0098
1231.7 | 49.5 | 1.0096
1231.8 | 49.5 | 1.0096
1231.9 | 49.5 | 1.0096
1232 | 49.5 | 1.0096
1232.1 | 49.5 | 1.0096
1232.2 | 49.5 | 1.0096
1232.3 | 49.5 | 1.0096
1232.4 | 49.5 | 1.0096
1232.5 | 49.5 | 1.0096
1232.6 | 49.5 | 1.0096
1232.7 | 49.5 | 1.0096
1232.8 | 49.5 | 1.0096
1232.9 | 49.5 | 1.0094
1233 | 49.5 | 1.0094
1233.1 | 49.5 | 1.0094
1233.2 | 49.5 | 1.0094
1233.3 | 49.5 | 1.0094
1233.4 | 49.5 | 1.0094
1233.5 | 49.5 | 1.0094
1233.6 | 49.5 | 1.0094
1233.7 | 49.5 | 1.0094
1233.8 | 49.5 | 1.0094
1233.9 | 49.5 | 1.0094
1234 | 49.5 | 1.0096
1234.1 | 49.5 | 1.0096
1234.2 | 49.5 | 1.0096
1234.3 | 49.5 | 1.0096
1234.4 | 49.5 | 1.0098
1234.5 | 49.5 | 1.0098
1234.6 | 49.5 | 1.0098
1234.7 | 49.5 | 1.0098
1234.8 | 49.5 | 1.0098
1234.9 | 49.5 | 1.0098
1235 | 49.5 | 1.0098
1235.1 | 49.5 | 1.0098
1235.2 | 49.5 | 1.0098
1235.3 | 49.5 | 1.0098
1235.4 | 49.5 | 1.0098
1235.5 | 49.5 | 1.0098
1235.6 | 49.5 | 1.0098
1235.7 | 49.5 | 1.0098
1235.8 | 49.5 | 1.0098
1235.9 | 49.5 | 1.0098
1236 | 49.5 | 1.0098
1236.1 | 49.5 | 1.0098
1236.2 | 49.5 | 1.0098
1236.3 | 49.5 | 1.0098
1236.4 | 49.5 | 1.0098
1236.5 | 49.5 | 1.0098
1236.6 | 49.5 | 1.0098
1236.7 | 49.5 | 1.0098
1236.8 | 49.5 | 1.0098
1236.9 | 49.5 | 1.0098
1237 | 49.5 | 1.0098
1237.1 | 49.5 | 1.0098
1237.2 | 49.5 | 1.0098
1237.3 | 49.5 | 1.0098
1237.4 | 49.5 | 1.0098
1237.5 | 49.5 | 1.0098
1237.6 | 49.5 | 1.0096
1237.7 | 49.5 | 1.0096
1237.8 | 49.5 | 1.0096
1237.9 | 49.5 | 1.0096
1238 | 49.5 | 1.0096
1238.1 | 49.5 | 1.0096
1238.2 | 49.5 | 1.0096
1238.3 | 49.5 | 1.0096
1238.4 | 49.5 | 1.0096
1238.5 | 49.5 | 1.0096
1238.6 | 49.5 | 1.0096
1238.7 | 49.5 | 1.0096
1238.8 | 49.5 | 1.0096
1238.9 | 49.5 | 1.0094
1239 | 49.5 | 1.0094
1239.1 | 49.5 | 1.0094
1239.2 | 49.5 | 1.0094
1239.3 | 49.5 | 1.0094
1239.4 | 49.5 | 1.0094
1239.5 | 49.5 | 1.0094
1239.6 | 49.5 | 1.0094
1239.7 | 49.5 | 1.0094
1239.8 | 49.5 | 1.0094
1239.9 | 49.5 | 1.0096
1240 | 49.5 | 1.0096
1240.1 | 49.5 | 1.0096
1240.2 | 49.5 | 1.0096
1240.3 | 49.5 | 1.0096
1240.4 | 49.5 | 1.0096
1240.5 | 49.5 | 1.0096
1240.6 | 49.5 | 1.0096
1240.7 | 49.5 | 1.0096
1240.8 | 49.5 | 1.0098
1240.9 | 49.5 | 1.0098
1241 | 49.5 | 1.0098
1241.1 | 49.5 | 1.0098
1241.2 | 49.5 | 1.0098
1241.3 | 49.5 | 1.0098
1241.4 | 49.5 | 1.0098
1241.5 | 49.5 | 1.0098
1241.6 | 49.5 | 1.0098
1241.7 | 49.5 | 1.0098
1241.8 | 49.5 | 1.0098
1241.9 | 49.5 | 1.0098
1242 | 49.5 | 1.0098
1242.1 | 49.5 | 1.0098
1242.2 | 49.5 | 1.0098
1242.3 | 49.5 | 1.0098
1242.4 | 49.5 | 1.0098
1242.5 | 49.5 | 1.0098
1242.6 | 49.5 | 1.0098
1242.7 | 49.5 | 1.0098
1242.8 | 49.5 | 1.0098
1242.9 | 49.5 | 1.0098
1243 | 49.5 | 1.0098
1243.1 | 49.5 | 1.0098
1243.2 | 49.5 | 1.0098
1243.3 | 49.5 | 1.0098
1243.4 | 49.5 | 1.0096
1243.5 | 49.5 | 1.0096
1243.6 | 49.5 | 1.0096
1243.7 | 49.5 | 1.0096
1243.8 | 49.5 | 1.0096
1243.9 | 49.5 | 1.0096
1244 | 49.5 | 1.0096
1244.1 | 49.5 | 1.0096
1244.2 | 49.5 | 1.0096
1244.3 | 49.5 | 1.0096
1244.4 | 49.5 | 1.0096
1244.5 | 49.5 | 1.0096
1244.6 | 49.5 | 1.0096
1244.7 | 49.5 | 1.0096
1244.8 | 49.5 | 1.0096
1244.9 | 49.5 | 1.0096
1245 | 49.5 | 1.0096
1245.1 | 49.5 | 1.0096
1245.2 | 49.5 | 1.0096
1245.3 | 49.5 | 1.0096
1245.4 | 49.5 | 1.0096
1245.5 | 49.5 | 1.0096
1245.6 | 49.5 | 1.0096
1245.7 | 49.5 | 1.0096
1245.8 | 49.5 | 1.0096
1245.9 | 49.5 | 1.0096
1246 | 49.5 | 1.0096
1246.1 | 49.5 | 1.0096
1246.2 | 49.5 | 1.0096
1246.3 | 49.5 | 1.0096
1246.4 | 49.5 | 1.0096
1246.5 | 49.5 | 1.0096
1246.6 | 49.5 | 1.0096
1246.7 | 49.5 | 1.0096
1246.8 | 49.5 | 1.0096
1246.9 | 49.5 | 1.0096
1247 | 49.5 | 1.0098
1247.1 | 49.5 | 1.0098
1247.2 | 49.5 | 1.0098
1247.3 | 49.5 | 1.0098
1247.4 | 49.5 | 1.0098
1247.5 | 49.5 | 1.0098
1247.6 | 49.5 | 1.0098
1247.7 | 49.5 | 1.0098
1247.8 | 49.5 | 1.0098
1247.9 | 49.5 | 1.0098
1248 | 49.5 | 1.0098
1248.1 | 49.5 | 1.0098
1248.2 | 49.5 | 1.0098
1248.3 | 49.5 | 1.0098
1248.4 | 49.5 | 1.0098
1248.5 | 49.5 | 1.0098
1248.6 | 49.5 | 1.0098
1248.7 | 49.5 | 1.0098
1248.8 | 49.5 | 1.0098
1248.9 | 49.5 | 1.0098
1249 | 49.5 | 1.0096
1249.1 | 49.5 | 1.0096
1249.2 | 49.5 | 1.0096
1249.3 | 49.5 | 1.0096
1249.4 | 49.5 | 1.0096
1249.5 | 49.5 | 1.0096
1249.6 | 49.5 | 1.0096
1249.7 | 49.5 | 1.0096
1249.8 | 49.5 | 1.0096
1249.9 | 49.5 | 1.0096
1250 | 49.5 | 1.0096
1250.1 | 49.5 | 1.0096
1250.2 | 49.5 | 1.0096
1250.3 | 49.5 | 1.0096
1250.4 | 49.5 | 1.0096
1250.5 | 49.5 | 1.0096
1250.6 | 49.5 | 1.0096
1250.7 | 49.5 | 1.0096
1250.8 | 49.5 | 1.0096
1250.9 | 49.5 | 1.0096
1251 | 49.5 | 1.0096
1251.1 | 49.5 | 1.0096
1251.2 | 49.5 | 1.0096
1251.3 | 49.5 | 1.0096
1251.4 | 49.5 | 1.0096
1251.5 | 49.5 | 1.0096
1251.6 | 49.5 | 1.0096
1251.7 | 49.5 | 1.0096
1251.8 | 49.5 | 1.0096
1251.9 | 49.5 | 1.0096
1252 | 49.5 | 1.0096
1252.1 | 49.5 | 1.0096
1252.2 | 49.5 | 1.0096
1252.3 | 49.5 | 1.0096
1252.4 | 49.5 | 1.0096
1252.5 | 49.5 | 1.0096
1252.6 | 49.5 | 1.0096
1252.7 | 49.5 | 1.0096
1252.8 | 49.5 | 1.0096
1252.9 | 49.5 | 1.0096
1253 | 49.5 | 1.0096
1253.1 | 49.5 | 1.0096
1253.2 | 49.5 | 1.0096
1253.3 | 49.5 | 1.0096
1253.4 | 49.5 | 1.0096
1253.5 | 49.5 | 1.0096
1253.6 | 49.5 | 1.0096
1253.7 | 49.5 | 1.0096
1253.8 | 49.5 | 1.0096
1253.9 | 49.5 | 1.0096
1254 | 49.5 | 1.0096
1254.1 | 49.5 | 1.0096
1254.2 | 49.5 | 1.0096
1254.3 | 49.5 | 1.0096
1254.4 | 49.5 | 1.0096
1254.5 | 49.5 | 1.0096
1254.6 | 49.5 | 1.0096
1254.7 | 49.5 | 1.0096
1254.8 | 49.5 | 1.0096
1254.9 | 49.5 | 1.0096
1255 | 49.5 | 1.0096
1255.1 | 49.5 | 1.0096
1255.2 | 49.5 | 1.0098
1255.3 | 49.5 | 1.0098
1255.4 | 49.5 | 1.0098
1255.5 | 49.5 | 1.0098
1255.6 | 49.5 | 1.0098
1255.7 | 49.5 | 1.0098
1255.8 | 49.5 | 1.0098
1255.9 | 49.5 | 1.0098
1256 | 49.5 | 1.0098
1256.1 | 49.5 | 1.0098
1256.2 | 49.5 | 1.0096
1256.3 | 49.5 | 1.0096
1256.4 | 49.5 | 1.0096
1256.5 | 49.5 | 1.0096
1256.6 | 49.5 | 1.0096
1256.7 | 49.5 | 1.0096
1256.8 | 49.5 | 1.0096
1256.9 | 49.5 | 1.0096
1257 | 49.5 | 1.0096
1257.1 | 49.5 | 1.0096
1257.2 | 49.5 | 1.0096
1257.3 | 49.5 | 1.0096
1257.4 | 49.5 | 1.0096
1257.5 | 49.5 | 1.0096
1257.6 | 49.5 | 1.0096
1257.7 | 49.5 | 1.0096
1257.8 | 49.5 | 1.0096
1257.9 | 49.5 | 1.0096
1258 | 49.5 | 1.0096
1258.1 | 49.5 | 1.0096
1258.2 | 49.5 | 1.0096
1258.3 | 49.5 | 1.0096
1258.4 | 49.5 | 1.0096
1258.5 | 49.5 | 1.0096
1258.6 | 49.5 | 1.0096
1258.7 | 49.5 | 1.0096
1258.8 | 49.5 | 1.0096
1258.9 | 49.5 | 1.0096
1259 | 49.5 | 1.0096
1259.1 | 49.5 | 1.0096
1259.2 | 49.5 | 1.0096
1259.3 | 49.5 | 1.0096
1259.4 | 49.5 | 1.0096
1259.5 | 49.5 | 1.0096
1259.6 | 49.5 | 1.0096
1259.7 | 49.5 | 1.0096
1259.8 | 49.5 | 1.0098
1259.9 | 49.5 | 1.0098
1260 | 49.5 | 1.0098
1260.1 | 49.5 | 1.0096
1260.2 | 49.5 | 1.0096
1260.3 | 49.5 | 1.0096
1260.4 | 49.5 | 1.0096
1260.5 | 49.5 | 1.0096
1260.6 | 49.5 | 1.0096
1260.7 | 49.5 | 1.0096
1260.8 | 49.5 | 1.0096
1260.9 | 49.5 | 1.0096
1261 | 49.5 | 1.0098
1261.1 | 49.5 | 1.0098
1261.2 | 49.5 | 1.0098
1261.3 | 49.5 | 1.0098
1261.4 | 49.5 | 1.0098
1261.5 | 49.5 | 1.0098
1261.6 | 49.5 | 1.0098
1261.7 | 49.5 | 1.0098
1261.8 | 49.5 | 1.0098
1261.9 | 49.5 | 1.0098
1262 | 49.5 | 1.0098
1262.1 | 49.5 | 1.0098
1262.2 | 49.5 | 1.0096
1262.3 | 49.5 | 1.0096
1262.4 | 49.5 | 1.0096
1262.5 | 49.5 | 1.0096
1262.6 | 49.5 | 1.0096
1262.7 | 49.5 | 1.0096
1262.8 | 49.5 | 1.0096
1262.9 | 49.5 | 1.0096
1263 | 49.5 | 1.0096
1263.1 | 49.5 | 1.0096
1263.2 | 49.5 | 1.0096
1263.3 | 49.5 | 1.0096
1263.4 | 49.5 | 1.0096
1263.5 | 49.5 | 1.0096
1263.6 | 49.5 | 1.0096
1263.7 | 49.5 | 1.0096
1263.8 | 49.5 | 1.0096
1263.9 | 49.5 | 1.0096
1264 | 49.5 | 1.0096
1264.1 | 49.5 | 1.0096
1264.2 | 49.5 | 1.0096
1264.3 | 49.5 | 1.0096
1264.4 | 49.5 | 1.0096
1264.5 | 49.5 | 1.0096
1264.6 | 49.5 | 1.0096
1264.7 | 49.5 | 1.0096
1264.8 | 49.5 | 1.0096
1264.9 | 49.5 | 1.0096
1265 | 49.5 | 1.0096
1265.1 | 49.5 | 1.0096
1265.2 | 49.5 | 1.0096
1265.3 | 49.5 | 1.0096
1265.4 | 49.5 | 1.0096
1265.5 | 49.5 | 1.0096
1265.6 | 49.5 | 1.0096
1265.7 | 49.5 | 1.0096
1265.8 | 49.5 | 1.0096
1265.9 | 49.5 | 1.0096
1266 | 49.5 | 1.0096
1266.1 | 49.5 | 1.0096
1266.2 | 49.5 | 1.0096
1266.3 | 49.5 | 1.0096
1266.4 | 49.5 | 1.0096
1266.5 | 49.5 | 1.0096
1266.6 | 49.5 | 1.0096
1266.7 | 49.5 | 1.0096
1266.8 | 49.5 | 1.0096
1266.9 | 49.5 | 1.0096
1267 | 49.5 | 1.0096
1267.1 | 49.5 | 1.0096
1267.2 | 49.5 | 1.0096
1267.3 | 49.5 | 1.0096
1267.4 | 49.5 | 1.0096
1267.5 | 49.5 | 1.0096
1267.6 | 49.5 | 1.0096
1267.7 | 49.5 | 1.0096
1267.8 | 49.5 | 1.0096
1267.9 | 49.5 | 1.0096
1268 | 49.5 | 1.0096
1268.1 | 49.5 | 1.0096
1268.2 | 49.5 | 1.0096
1268.3 | 49.5 | 1.0096
1268.4 | 49.5 | 1.0096
1268.5 | 49.5 | 1.0096
1268.6 | 49.5 | 1.0096
1268.7 | 49.5 | 1.0096
1268.8 | 49.5 | 1.0096
1268.9 | 49.5 | 1.0096
1269 | 49.5 | 1.0096
1269.1 | 49.5 | 1.0096
1269.2 | 49.5 | 1.0096
1269.3 | 49.5 | 1.0096
1269.4 | 49.5 | 1.0096
1269.5 | 49.5 | 1.0096
1269.6 | 49.5 | 1.0096
1269.7 | 49.5 | 1.0096
1269.8 | 49.5 | 1.0096
1269.9 | 49.5 | 1.0096
1270 | 49.5 | 1.0096
1270.1 | 49.5 | 1.0096
1270.2 | 49.5 | 1.0096
1270.3 | 49.5 | 1.0096
1270.4 | 49.5 | 1.0096
1270.5 | 49.5 | 1.0096
1270.6 | 49.5 | 1.0096
1270.7 | 49.5 | 1.0096
1270.8 | 49.5 | 1.0096
1270.9 | 49.5 | 1.0096
1271 | 49.5 | 1.0096
1271.1 | 49.5 | 1.0096
1271.2 | 49.5 | 1.0096
1271.3 | 49.5 | 1.0096
1271.4 | 49.5 | 1.0096
1271.5 | 49.5 | 1.0096
1271.6 | 49.5 | 1.0096
1271.7 | 49.5 | 1.0096
1271.8 | 49.5 | 1.0096
1271.9 | 49.5 | 1.0096
1272 | 49.5 | 1.0096
1272.1 | 49.5 | 1.0096
1272.2 | 49.5 | 1.0096
1272.3 | 49.5 | 1.0096
1272.4 | 49.5 | 1.0096
1272.5 | 49.5 | 1.0096
1272.6 | 49.5 | 1.0096
1272.7 | 49.5 | 1.0096
1272.8 | 49.5 | 1.0096
1272.9 | 49.5 | 1.0096
1273 | 49.5 | 1.0096
1273.1 | 49.5 | 1.0096
1273.2 | 49.5 | 1.0096
1273.3 | 49.5 | 1.0096
1273.4 | 49.5 | 1.0096
1273.5 | 49.5 | 1.0096
1273.6 | 49.5 | 1.0096
1273.7 | 49.5 | 1.0096
1273.8 | 49.5 | 1.0096
1273.9 | 49.5 | 1.0096
1274 | 49.5 | 1.0096
1274.1 | 49.5 | 1.0096
1274.2 | 49.5 | 1.0096
1274.3 | 49.5 | 1.0096
1274.4 | 49.5 | 1.0096
1274.5 | 49.5 | 1.0096
1274.6 | 49.5 | 1.0096
1274.7 | 49.5 | 1.0096
1274.8 | 49.5 | 1.0096
1274.9 | 49.5 | 1.0096
1275 | 49.5 | 1.0096
1275.1 | 49.5 | 1.0096
1275.2 | 49.5 | 1.0096
1275.3 | 49.5 | 1.0096
1275.4 | 49.5 | 1.0096
1275.5 | 49.5 | 1.0096
1275.6 | 49.5 | 1.0096
1275.7 | 49.5 | 1.0096
1275.8 | 49.5 | 1.0096
1275.9 | 49.5 | 1.0096
1276 | 49.5 | 1.0096
1276.1 | 49.5 | 1.0096
1276.2 | 49.5 | 1.0096
1276.3 | 49.5 | 1.0096
1276.4 | 49.5 | 1.0096
1276.5 | 49.5 | 1.0096
1276.6 | 49.5 | 1.0096
1276.7 | 49.5 | 1.0096
1276.8 | 49.5 | 1.0096
1276.9 | 49.5 | 1.0096
1277 | 49.5 | 1.0096
1277.1 | 49.5 | 1.0096
1277.2 | 49.5 | 1.0096
1277.3 | 49.5 | 1.0096
1277.4 | 49.5 | 1.0096
1277.5 | 49.5 | 1.0096
1277.6 | 49.5 | 1.0096
1277.7 | 49.5 | 1.0096
1277.8 | 49.5 | 1.0096
1277.9 | 49.5 | 1.0096
1278 | 49.5 | 1.0096
1278.1 | 49.5 | 1.0096
1278.2 | 49.5 | 1.0096
1278.3 | 49.5 | 1.0096
1278.4 | 49.5 | 1.0096
1278.5 | 49.5 | 1.0096
1278.6 | 49.5 | 1.0096
1278.7 | 49.5 | 1.0096
1278.8 | 49.5 | 1.0096
1278.9 | 49.5 | 1.0096
1279 | 49.5 | 1.0096
1279.1 | 49.5 | 1.0096
1279.2 | 49.5 | 1.0096
1279.3 | 49.5 | 1.0096
1279.4 | 49.5 | 1.0096
1279.5 | 49.5 | 1.0096
1279.6 | 49.5 | 1.0096
1279.7 | 49.5 | 1.0096
1279.8 | 49.5 | 1.0096
1279.9 | 49.5 | 1.0096
1280 | 49.5 | 1.0096
1280.1 | 49.5 | 1.0096
1280.2 | 49.5 | 1.0096
1280.3 | 49.5 | 1.0096
1280.4 | 49.5 | 1.0096
1280.5 | 49.5 | 1.0096
1280.6 | 49.5 | 1.0096
1280.7 | 49.5 | 1.0096
1280.8 | 49.5 | 1.0096
1280.9 | 49.5 | 1.0096
1281 | 49.5 | 1.0096
1281.1 | 49.5 | 1.0096
1281.2 | 49.5 | 1.0096
1281.3 | 49.5 | 1.0096
1281.4 | 49.5 | 1.0096
1281.5 | 49.5 | 1.0096
1281.6 | 49.5 | 1.0096
1281.7 | 49.5 | 1.0096
1281.8 | 49.5 | 1.0096
1281.9 | 49.5 | 1.0096
1282 | 49.5 | 1.0096
1282.1 | 49.5 | 1.0096
1282.2 | 49.5 | 1.0096
1282.3 | 49.5 | 1.0096
1282.4 | 49.5 | 1.0096
1282.5 | 49.5 | 1.0096
1282.6 | 49.5 | 1.0096
1282.7 | 49.5 | 1.0096
1282.8 | 49.5 | 1.0096
1282.9 | 49.5 | 1.0096
1283 | 49.5 | 1.0096
1283.1 | 49.5 | 1.0096
1283.2 | 49.5 | 1.0096
1283.3 | 49.5 | 1.0096
1283.4 | 49.5 | 1.0096
1283.5 | 49.5 | 1.0096
1283.6 | 49.5 | 1.0096
1283.7 | 49.5 | 1.0096
1283.8 | 49.5 | 1.0096
1283.9 | 49.5 | 1.0096
1284 | 49.5 | 1.0096
1284.1 | 49.5 | 1.0096
1284.2 | 49.5 | 1.0096
1284.3 | 49.5 | 1.0096
1284.4 | 49.5 | 1.0096
1284.5 | 49.5 | 1.0096
1284.6 | 49.5 | 1.0096
1284.7 | 49.5 | 1.0096
1284.8 | 49.5 | 1.0096
1284.9 | 49.5 | 1.0096
1285 | 49.5 | 1.0096
1285.1 | 49.5 | 1.0096
1285.2 | 49.5 | 1.0096
1285.3 | 49.5 | 1.0098
1285.4 | 49.5 | 1.0098
1285.5 | 49.5 | 1.0098
1285.6 | 49.5 | 1.0098
1285.7 | 49.5 | 1.0098
1285.8 | 49.5 | 1.0098
1285.9 | 49.5 | 1.0098
1286 | 49.5 | 1.0098
1286.1 | 49.5 | 1.0098
1286.2 | 49.5 | 1.0098
1286.3 | 49.5 | 1.0098
1286.4 | 49.5 | 1.0098
1286.5 | 49.5 | 1.0098
1286.6 | 49.5 | 1.0098
1286.7 | 49.5 | 1.0098
1286.8 | 49.5 | 1.0098
1286.9 | 49.5 | 1.0098
1287 | 49.5 | 1.0098
1287.1 | 49.5 | 1.0098
1287.2 | 49.5 | 1.0098
1287.3 | 49.5 | 1.0098
1287.4 | 49.5 | 1.0098
1287.5 | 49.5 | 1.0098
1287.6 | 49.5 | 1.0096
1287.7 | 49.5 | 1.0096
1287.8 | 49.5 | 1.0096
1287.9 | 49.5 | 1.0096
1288 | 49.5 | 1.0096
1288.1 | 49.5 | 1.0096
1288.2 | 49.5 | 1.0096
1288.3 | 49.5 | 1.0096
1288.4 | 49.5 | 1.0096
1288.5 | 49.5 | 1.0096
1288.6 | 49.5 | 1.0096
1288.7 | 49.5 | 1.0096
1288.8 | 49.5 | 1.0096
1288.9 | 49.5 | 1.0096
1289 | 49.5 | 1.0096
1289.1 | 49.5 | 1.0096
1289.2 | 49.5 | 1.0096
1289.3 | 49.5 | 1.0096
1289.4 | 49.5 | 1.0096
1289.5 | 49.5 | 1.0096
1289.6 | 49.5 | 1.0096
1289.7 | 49.5 | 1.0096
1289.8 | 49.5 | 1.0096
1289.9 | 49.5 | 1.0096
1290 | 49.5 | 1.0096
1290.1 | 49.5 | 1.0096
1290.2 | 49.5 | 1.0096
1290.3 | 49.5 | 1.0096
1290.4 | 49.5 | 1.0096
1290.5 | 49.5 | 1.0096
1290.6 | 49.5 | 1.0096
1290.7 | 49.5 | 1.0096
1290.8 | 49.5 | 1.0096
1290.9 | 49.5 | 1.0096
1291 | 49.5 | 1.0096
1291.1 | 49.5 | 1.0096
1291.2 | 49.5 | 1.0096
1291.3 | 49.5 | 1.0096
1291.4 | 49.5 | 1.0096
1291.5 | 49.5 | 1.0096
1291.6 | 49.5 | 1.0096
1291.7 | 49.5 | 1.0096
1291.8 | 49.5 | 1.0096
1291.9 | 49.5 | 1.0096
1292 | 49.5 | 1.0096
1292.1 | 49.5 | 1.0096
1292.2 | 49.5 | 1.0096
1292.3 | 49.5 | 1.0096
1292.4 | 49.5 | 1.0096
1292.5 | 49.5 | 1.0096
1292.6 | 49.5 | 1.0096
1292.7 | 49.5 | 1.0096
1292.8 | 49.5 | 1.0096
1292.9 | 49.5 | 1.0096
1293 | 49.5 | 1.0096
1293.1 | 49.5 | 1.0096
1293.2 | 49.5 | 1.0096
1293.3 | 49.5 | 1.0096
1293.4 | 49.5 | 1.0096
1293.5 | 49.5 | 1.0096
1293.6 | 49.5 | 1.0096
1293.7 | 49.5 | 1.0096
1293.8 | 49.5 | 1.0096
1293.9 | 49.5 | 1.0096
1294 | 49.5 | 1.0096
1294.1 | 49.5 | 1.0096
1294.2 | 49.5 | 1.0096
1294.3 | 49.5 | 1.0096
1294.4 | 49.5 | 1.0096
1294.5 | 49.5 | 1.0096
1294.6 | 49.5 | 1.0096
1294.7 | 49.5 | 1.0096
1294.8 | 49.5 | 1.0096
1294.9 | 49.5 | 1.0096
1295 | 49.5 | 1.0096
1295.1 | 49.5 | 1.0096
1295.2 | 49.5 | 1.0096
1295.3 | 49.5 | 1.0096
1295.4 | 49.5 | 1.0096
1295.5 | 49.5 | 1.0096
1295.6 | 49.5 | 1.0096
1295.7 | 49.5 | 1.0096
1295.8 | 49.5 | 1.0096
1295.9 | 49.5 | 1.0096
1296 | 49.5 | 1.0096
1296.1 | 49.5 | 1.0096
1296.2 | 49.5 | 1.0096
1296.3 | 49.5 | 1.0096
1296.4 | 49.5 | 1.0096
1296.5 | 49.5 | 1.0096
1296.6 | 49.5 | 1.0096
1296.7 | 49.5 | 1.0096
1296.8 | 49.5 | 1.0096
1296.9 | 49.5 | 1.0096
1297 | 49.5 | 1.0096
1297.1 | 49.5 | 1.0096
1297.2 | 49.5 | 1.0096
1297.3 | 49.5 | 1.0096
1297.4 | 49.5 | 1.0096
1297.5 | 49.5 | 1.0096
1297.6 | 49.5 | 1.0096
1297.7 | 49.5 | 1.0096
1297.8 | 49.5 | 1.0096
1297.9 | 49.5 | 1.0096
1298 | 49.5 | 1.0096
1298.1 | 49.5 | 1.0096
1298.2 | 49.5 | 1.0096
1298.3 | 49.5 | 1.0096
1298.4 | 49.5 | 1.0096
1298.5 | 49.5 | 1.0096
1298.6 | 49.5 | 1.0096
1298.7 | 49.5 | 1.0096
1298.8 | 49.5 | 1.0096
1298.9 | 49.5 | 1.0096
1299 | 49.5 | 1.0096
1299.1 | 49.5 | 1.0096
1299.2 | 49.5 | 1.0096
1299.3 | 49.5 | 1.0096
1299.4 | 49.5 | 1.0096
1299.5 | 49.5 | 1.0096
1299.6 | 49.5 | 1.0096
1299.7 | 49.5 | 1.0096
1299.8 | 49.5 | 1.0096
1299.9 | 49.5 | 1.0096
1300 | 49.5 | 1.0096
1300.1 | 49.5 | 1.0096
1300.2 | 49.5 | 1.0096
1300.3 | 49.5 | 1.0096
1300.4 | 49.5 | 1.0096
1300.5 | 49.5 | 1.0096
1300.6 | 49.5 | 1.0096
1300.7 | 49.5 | 1.0096
1300.8 | 49.5 | 1.0096
1300.9 | 49.5 | 1.0096
1301 | 49.5 | 1.0096
1301.1 | 49.5 | 1.0096
1301.2 | 49.5 | 1.0096
1301.3 | 49.5 | 1.0096
1301.4 | 49.5 | 1.0096
1301.5 | 49.5 | 1.0096
1301.6 | 49.5 | 1.0096
1301.7 | 49.5 | 1.0096
1301.8 | 49.5 | 1.0096
1301.9 | 49.5 | 1.0096
1302 | 49.5 | 1.0096
1302.1 | 49.5 | 1.0096
1302.2 | 49.5 | 1.0096
1302.3 | 49.5 | 1.0096
1302.4 | 49.5 | 1.0096
1302.5 | 49.5 | 1.0096
1302.6 | 49.5 | 1.0096
1302.7 | 49.5 | 1.0096
1302.8 | 49.5 | 1.0096
1302.9 | 49.5 | 1.0096
1303 | 49.5 | 1.0096
1303.1 | 49.5 | 1.0096
1303.2 | 49.5 | 1.0096
1303.3 | 49.5 | 1.0096
1303.4 | 49.5 | 1.0096
1303.5 | 49.5 | 1.0096
1303.6 | 49.5 | 1.0096
1303.7 | 49.5 | 1.0096
1303.8 | 49.5 | 1.0096
1303.9 | 49.5 | 1.0096
1304 | 49.5 | 1.0096
1304.1 | 49.5 | 1.0096
1304.2 | 49.5 | 1.0096
1304.3 | 49.5 | 1.0096
1304.4 | 49.5 | 1.0096
1304.5 | 49.5 | 1.0096
1304.6 | 49.5 | 1.0096
1304.7 | 49.5 | 1.0096
1304.8 | 49.5 | 1.0096
1304.9 | 49.5 | 1.0096
1305 | 49.5 | 1.0096
1305.1 | 49.5 | 1.0096
1305.2 | 49.5 | 1.0096
1305.3 | 49.5 | 1.0096
1305.4 | 49.5 | 1.0096
1305.5 | 49.5 | 1.0096
1305.6 | 49.5 | 1.0096
1305.7 | 49.5 | 1.0096
1305.8 | 49.5 | 1.0096
1305.9 | 49.5 | 1.0096
1306 | 49.5 | 1.0096
1306.1 | 49.5 | 1.0096
1306.2 | 49.5 | 1.0096
1306.3 | 49.5 | 1.0096
1306.4 | 49.5 | 1.0096
1306.5 | 49.5 | 1.0096
1306.6 | 49.5 | 1.0096
1306.7 | 49.5 | 1.0096
1306.8 | 49.5 | 1.0096
1306.9 | 49.5 | 1.0096
1307 | 49.5 | 1.0096
1307.1 | 49.5 | 1.0096
1307.2 | 49.5 | 1.0096
1307.3 | 49.5 | 1.0096
1307.4 | 49.5 | 1.0096
1307.5 | 49.5 | 1.0096
1307.6 | 49.5 | 1.0096
1307.7 | 49.5 | 1.0096
1307.8 | 49.5 | 1.0096
1307.9 | 49.5 | 1.0096
1308 | 49.5 | 1.0096
1308.1 | 49.5 | 1.0096
1308.2 | 49.5 | 1.0096
1308.3 | 49.5 | 1.0096
1308.4 | 49.5 | 1.0096
1308.5 | 49.5 | 1.0096
1308.6 | 49.5 | 1.0096
1308.7 | 49.5 | 1.0096
1308.8 | 49.5 | 1.0096
1308.9 | 49.5 | 1.0096
1309 | 49.5 | 1.0096
1309.1 | 49.5 | 1.0096
1309.2 | 49.5 | 1.0096
1309.3 | 49.5 | 1.0096
1309.4 | 49.5 | 1.0096
1309.5 | 49.5 | 1.0096
1309.6 | 49.5 | 1.0096
1309.7 | 49.5 | 1.0096
1309.8 | 49.5 | 1.0096
1309.9 | 49.5 | 1.0096
1310 | 49.5 | 1.0096
1310.1 | 49.5 | 1.0096
1310.2 | 49.5 | 1.0096
1310.3 | 49.5 | 1.0096
1310.4 | 49.5 | 1.0096
1310.5 | 49.5 | 1.0096
1310.6 | 49.5 | 1.0096
1310.7 | 49.5 | 1.0096
1310.8 | 49.5 | 1.0096
1310.9 | 49.5 | 1.0096
1311 | 49.5 | 1.0096
1311.1 | 49.5 | 1.0096
1311.2 | 49.5 | 1.0096
1311.3 | 49.5 | 1.0096
1311.4 | 49.5 | 1.0096
1311.5 | 49.5 | 1.0096
1311.6 | 49.5 | 1.0096
1311.7 | 49.5 | 1.0096
1311.8 | 49.5 | 1.0096
1311.9 | 49.5 | 1.0096
1312 | 49.5 | 1.0096
1312.1 | 49.5 | 1.0096
1312.2 | 49.5 | 1.0096
1312.3 | 49.5 | 1.0096
1312.4 | 49.5 | 1.0096
1312.5 | 49.5 | 1.0096
1312.6 | 49.5 | 1.0096
1312.7 | 49.5 | 1.0096
1312.8 | 49.5 | 1.0096
1312.9 | 49.5 | 1.0096
1313 | 49.5 | 1.0096
1313.1 | 49.5 | 1.0096
1313.2 | 49.5 | 1.0096
1313.3 | 49.5 | 1.0096
1313.4 | 49.5 | 1.0096
1313.5 | 49.5 | 1.0096
1313.6 | 49.5 | 1.0096
1313.7 | 49.5 | 1.0096
1313.8 | 49.5 | 1.0096
1313.9 | 49.5 | 1.0096
1314 | 49.5 | 1.0096
1314.1 | 49.5 | 1.0096
1314.2 | 49.5 | 1.0096
1314.3 | 49.5 | 1.0096
1314.4 | 49.5 | 1.0096
1314.5 | 49.5 | 1.0096
1314.6 | 49.5 | 1.0096
1314.7 | 49.5 | 1.0096
1314.8 | 49.5 | 1.0096
1314.9 | 49.5 | 1.0096
1315 | 49.5 | 1.0096
1315.1 | 49.5 | 1.0096
1315.2 | 49.5 | 1.0096
1315.3 | 49.5 | 1.0096
1315.4 | 49.5 | 1.0096
1315.5 | 49.5 | 1.0096
1315.6 | 49.5 | 1.0096
1315.7 | 49.5 | 1.0096
1315.8 | 49.5 | 1.0096
1315.9 | 49.5 | 1.0096
1316 | 49.5 | 1.0096
1316.1 | 49.5 | 1.0096
1316.2 | 49.5 | 1.0096
1316.3 | 49.5 | 1.0096
1316.4 | 49.5 | 1.0096
1316.5 | 49.5 | 1.0096
1316.6 | 49.5 | 1.0096
1316.7 | 49.5 | 1.0096
1316.8 | 49.5 | 1.0096
1316.9 | 49.5 | 1.0096
1317 | 49.5 | 1.0096
1317.1 | 49.5 | 1.0096
1317.2 | 49.5 | 1.0096
1317.3 | 49.5 | 1.0096
1317.4 | 49.5 | 1.0096
1317.5 | 49.5 | 1.0096
1317.6 | 49.5 | 1.0096
1317.7 | 49.5 | 1.0096
1317.8 | 49.5 | 1.0096
1317.9 | 49.5 | 1.0096
1318 | 49.5 | 1.0096
1318.1 | 49.5 | 1.0096
1318.2 | 49.5 | 1.0098
1318.3 | 49.5 | 1.0098
1318.4 | 49.5 | 1.0098
1318.5 | 49.5 | 1.0098
1318.6 | 49.5 | 1.0098
1318.7 | 49.5 | 1.0098
1318.8 | 49.5 | 1.0098
1318.9 | 49.5 | 1.0098
1319 | 49.5 | 1.0098
1319.1 | 49.5 | 1.0098
1319.2 | 49.5 | 1.0098
1319.3 | 49.5 | 1.0098
1319.4 | 49.5 | 1.0098
1319.5 | 49.5 | 1.0096
1319.6 | 49.5 | 1.0096
1319.7 | 49.5 | 1.0096
1319.8 | 49.5 | 1.0096
1319.9 | 49.5 | 1.0096
1320 | 49.5 | 1.0096
1320.1 | 49.5 | 1.0096
1320.2 | 49.5 | 1.0096
1320.3 | 49.5 | 1.0096
1320.4 | 49.5 | 1.0096
1320.5 | 49.5 | 1.0096
1320.6 | 49.5 | 1.0096
1320.7 | 49.5 | 1.0096
1320.8 | 49.5 | 1.0096
1320.9 | 49.5 | 1.0096
1321 | 49.5 | 1.0096
1321.1 | 49.5 | 1.0096
1321.2 | 49.5 | 1.0096
1321.3 | 49.5 | 1.0096
1321.4 | 49.5 | 1.0096
1321.5 | 49.5 | 1.0096
1321.6 | 49.5 | 1.0096
1321.7 | 49.5 | 1.0096
1321.8 | 49.5 | 1.0096
1321.9 | 49.5 | 1.0096
1322 | 49.5 | 1.0096
1322.1 | 49.5 | 1.0096
1322.2 | 49.5 | 1.0096
1322.3 | 49.5 | 1.0096
1322.4 | 49.5 | 1.0096
1322.5 | 49.5 | 1.0096
1322.6 | 49.5 | 1.0096
1322.7 | 49.5 | 1.0096
1322.8 | 49.5 | 1.0096
1322.9 | 49.5 | 1.0096
1323 | 49.5 | 1.0096
1323.1 | 49.5 | 1.0096
1323.2 | 49.5 | 1.0096
1323.3 | 49.5 | 1.0096
1323.4 | 49.5 | 1.0096
1323.5 | 49.5 | 1.0096
1323.6 | 49.5 | 1.0096
1323.7 | 49.5 | 1.0096
1323.8 | 49.5 | 1.0096
1323.9 | 49.5 | 1.0096
1324 | 49.5 | 1.0096
1324.1 | 49.5 | 1.0096
1324.2 | 49.5 | 1.0096
1324.3 | 49.5 | 1.0096
1324.4 | 49.5 | 1.0096
1324.5 | 49.5 | 1.0096
1324.6 | 49.5 | 1.0096
1324.7 | 49.5 | 1.0096
1324.8 | 49.5 | 1.0096
1324.9 | 49.5 | 1.0096
1325 | 49.5 | 1.0096
1325.1 | 49.5 | 1.0096
1325.2 | 49.5 | 1.0096
1325.3 | 49.5 | 1.0096
1325.4 | 49.5 | 1.0096
1325.5 | 49.5 | 1.0096
1325.6 | 49.5 | 1.0096
1325.7 | 49.5 | 1.0096
1325.8 | 49.5 | 1.0096
1325.9 | 49.5 | 1.0096
1326 | 49.5 | 1.0096
1326.1 | 49.5 | 1.0096
1326.2 | 49.5 | 1.0096
1326.3 | 49.5 | 1.0096
1326.4 | 49.5 | 1.0096
1326.5 | 49.5 | 1.0096
1326.6 | 49.5 | 1.0096
1326.7 | 49.5 | 1.0096
1326.8 | 49.5 | 1.0096
1326.9 | 49.5 | 1.0096
1327 | 49.5 | 1.0096
1327.1 | 49.5 | 1.0096
1327.2 | 49.5 | 1.0096
1327.3 | 49.5 | 1.0096
1327.4 | 49.5 | 1.0096
1327.5 | 49.5 | 1.0096
1327.6 | 49.5 | 1.0096
1327.7 | 49.5 | 1.0096
1327.8 | 49.5 | 1.0096
1327.9 | 49.5 | 1.0096
1328 | 49.5 | 1.0096
1328.1 | 49.5 | 1.0096
1328.2 | 49.5 | 1.0096
1328.3 | 49.5 | 1.0096
1328.4 | 49.5 | 1.0096
1328.5 | 49.5 | 1.0096
1328.6 | 49.5 | 1.0096
1328.7 | 49.5 | 1.0096
1328.8 | 49.5 | 1.0096
1328.9 | 49.5 | 1.0096
1329 | 49.5 | 1.0096
1329.1 | 49.5 | 1.0096
1329.2 | 49.5 | 1.0096
1329.3 | 49.5 | 1.0096
1329.4 | 49.5 | 1.0096
1329.5 | 49.5 | 1.0096
1329.6 | 49.5 | 1.0096
1329.7 | 49.5 | 1.0096
1329.8 | 49.5 | 1.0096
1329.9 | 49.5 | 1.0096
1330 | 49.5 | 1.0096
1330.1 | 49.5 | 1.0096
1330.2 | 49.5 | 1.0096
1330.3 | 49.5 | 1.0096
1330.4 | 49.5 | 1.0096
1330.5 | 49.5 | 1.0096
1330.6 | 49.5 | 1.0096
1330.7 | 49.5 | 1.0096
1330.8 | 49.5 | 1.0096
1330.9 | 49.5 | 1.0096
1331 | 49.5 | 1.0096
1331.1 | 49.5 | 1.0096
1331.2 | 49.5 | 1.0096
1331.3 | 49.5 | 1.0096
1331.4 | 49.5 | 1.0096
1331.5 | 49.5 | 1.0096
1331.6 | 49.5 | 1.0096
1331.7 | 49.5 | 1.0096
1331.8 | 49.5 | 1.0096
1331.9 | 49.5 | 1.0096
1332 | 49.5 | 1.0096
1332.1 | 49.5 | 1.0096
1332.2 | 49.5 | 1.0096
1332.3 | 49.5 | 1.0096
1332.4 | 49.5 | 1.0096
1332.5 | 49.5 | 1.0096
1332.6 | 49.5 | 1.0096
1332.7 | 49.5 | 1.0096
1332.8 | 49.5 | 1.0096
1332.9 | 49.5 | 1.0096
1333 | 49.5 | 1.0096
1333.1 | 49.5 | 1.0096
1333.2 | 49.5 | 1.0096
1333.3 | 49.5 | 1.0096
1333.4 | 49.5 | 1.0096
1333.5 | 49.5 | 1.0096
1333.6 | 49.5 | 1.0096
1333.7 | 49.5 | 1.0096
1333.8 | 49.5 | 1.0096
1333.9 | 49.5 | 1.0096
1334 | 49.5 | 1.0096
1334.1 | 49.5 | 1.0096
1334.2 | 49.5 | 1.0096
1334.3 | 49.5 | 1.0096
1334.4 | 49.5 | 1.0096
1334.5 | 49.5 | 1.0096
1334.6 | 49.5 | 1.0096
1334.7 | 49.5 | 1.0096
1334.8 | 49.5 | 1.0096
1334.9 | 49.5 | 1.0096
1335 | 49.5 | 1.0096
1335.1 | 49.5 | 1.0096
1335.2 | 49.5 | 1.0096
1335.3 | 49.5 | 1.0096
1335.4 | 49.5 | 1.0096
1335.5 | 49.5 | 1.0096
1335.6 | 49.5 | 1.0096
1335.7 | 49.5 | 1.0096
1335.8 | 49.5 | 1.0096
1335.9 | 49.5 | 1.0096
1336 | 49.5 | 1.0096
1336.1 | 49.5 | 1.0096
1336.2 | 49.5 | 1.0096
1336.3 | 49.5 | 1.0096
1336.4 | 49.5 | 1.0096
1336.5 | 49.5 | 1.0096
1336.6 | 49.5 | 1.0096
1336.7 | 49.5 | 1.0096
1336.8 | 49.5 | 1.0096
1336.9 | 49.5 | 1.0096
1337 | 49.5 | 1.0096
1337.1 | 49.5 | 1.0096
1337.2 | 49.5 | 1.0096
1337.3 | 49.5 | 1.0096
1337.4 | 49.5 | 1.0096
1337.5 | 49.5 | 1.0096
1337.6 | 49.5 | 1.0096
1337.7 | 49.5 | 1.0096
1337.8 | 49.5 | 1.0096
1337.9 | 49.5 | 1.0096
1338 | 49.5 | 1.0096
1338.1 | 49.5 | 1.0096
1338.2 | 49.5 | 1.0096
1338.3 | 49.5 | 1.0096
1338.4 | 49.5 | 1.0096
1338.5 | 49.5 | 1.0096
1338.6 | 49.5 | 1.0096
1338.7 | 49.5 | 1.0096
1338.8 | 49.5 | 1.0096
1338.9 | 49.5 | 1.0096
1339 | 49.5 | 1.0096
1339.1 | 49.5 | 1.0096
1339.2 | 49.5 | 1.0096
1339.3 | 49.5 | 1.0096
1339.4 | 49.5 | 1.0096
1339.5 | 49.5 | 1.0096
1339.6 | 49.5 | 1.0096
1339.7 | 49.5 | 1.0096
1339.8 | 49.5 | 1.0096
1339.9 | 49.5 | 1.0096
1340 | 49.5 | 1.0096
1340.1 | 49.5 | 1.0096
1340.2 | 49.5 | 1.0096
1340.3 | 49.5 | 1.0096
1340.4 | 49.5 | 1.0096
1340.5 | 49.5 | 1.0096
1340.6 | 49.5 | 1.0096
1340.7 | 49.5 | 1.0096
1340.8 | 49.5 | 1.0096
1340.9 | 49.5 | 1.0096
1341 | 49.5 | 1.0096
1341.1 | 49.5 | 1.0096
1341.2 | 49.5 | 1.0096
1341.3 | 49.5 | 1.0096
1341.4 | 49.5 | 1.0096
1341.5 | 49.5 | 1.0096
1341.6 | 49.5 | 1.0096
1341.7 | 49.5 | 1.0096
1341.8 | 49.5 | 1.0096
1341.9 | 49.5 | 1.0096
1342 | 49.5 | 1.0096
1342.1 | 49.5 | 1.0096
1342.2 | 49.5 | 1.0096
1342.3 | 49.5 | 1.0096
1342.4 | 49.5 | 1.0096
1342.5 | 49.5 | 1.0096
1342.6 | 49.5 | 1.0096
1342.7 | 49.5 | 1.0096
1342.8 | 49.5 | 1.0096
1342.9 | 49.5 | 1.0096
1343 | 49.5 | 1.0096
1343.1 | 49.5 | 1.0096
1343.2 | 49.5 | 1.0096
1343.3 | 49.5 | 1.0096
1343.4 | 49.5 | 1.0096
1343.5 | 49.5 | 1.0096
1343.6 | 49.5 | 1.0096
1343.7 | 49.5 | 1.0096
1343.8 | 49.5 | 1.0096
1343.9 | 49.5 | 1.0096
1344 | 49.5 | 1.0096
1344.1 | 49.5 | 1.0096
1344.2 | 49.5 | 1.0096
1344.3 | 49.5 | 1.0096
1344.4 | 49.5 | 1.0096
1344.5 | 49.5 | 1.0096
1344.6 | 49.5 | 1.0096
1344.7 | 49.5 | 1.0096
1344.8 | 49.5 | 1.0096
1344.9 | 49.5 | 1.0096
1345 | 49.5 | 1.0096
1345.1 | 49.5 | 1.0096
1345.2 | 49.5 | 1.0096
1345.3 | 49.5 | 1.0096
1345.4 | 49.5 | 1.0096
1345.5 | 49.5 | 1.0096
1345.6 | 49.5 | 1.0096
1345.7 | 49.5 | 1.0096
1345.8 | 49.5 | 1.0096
1345.9 | 49.5 | 1.0096
1346 | 49.5 | 1.0096
1346.1 | 49.5 | 1.0096
1346.2 | 49.5 | 1.0096
1346.3 | 49.5 | 1.0096
1346.4 | 49.5 | 1.0096
1346.5 | 49.5 | 1.0096
1346.6 | 49.5 | 1.0096
1346.7 | 49.5 | 1.0096
1346.8 | 49.5 | 1.0096
1346.9 | 49.5 | 1.0096
1347 | 49.5 | 1.0096
1347.1 | 49.5 | 1.0096
1347.2 | 49.5 | 1.0096
1347.3 | 49.5 | 1.0096
1347.4 | 49.5 | 1.0096
1347.5 | 49.5 | 1.0096
1347.6 | 49.5 | 1.0096
1347.7 | 49.5 | 1.0096
1347.8 | 49.5 | 1.0096
1347.9 | 49.5 | 1.0096
1348 | 49.5 | 1.0096
1348.1 | 49.5 | 1.0096
1348.2 | 49.5 | 1.0096
1348.3 | 49.5 | 1.0096
1348.4 | 49.5 | 1.0096
1348.5 | 49.5 | 1.0096
1348.6 | 49.5 | 1.0096
1348.7 | 49.5 | 1.0096
1348.8 | 49.5 | 1.0096
1348.9 | 49.5 | 1.0096
1349 | 49.5 | 1.0096
1349.1 | 49.5 | 1.0096
1349.2 | 49.5 | 1.0096
1349.3 | 49.5 | 1.0096
1349.4 | 49.5 | 1.0096
1349.5 | 49.5 | 1.0096
1349.6 | 49.5 | 1.0096
1349.7 | 49.5 | 1.0096
1349.8 | 49.5 | 1.0096
1349.9 | 49.5 | 1.0096
1350 | 49.5 | 1.0096
1350.1 | 49.5 | 1.0096
1350.2 | 49.5 | 1.0096
1350.3 | 49.5 | 1.0096
1350.4 | 49.5 | 1.0096
1350.5 | 49.5 | 1.0096
1350.6 | 49.5 | 1.0098
1350.7 | 49.5 | 1.0098
1350.8 | 49.5 | 1.0098
1350.9 | 49.5 | 1.0098
1351 | 49.5 | 1.0098
1351.1 | 49.5 | 1.0098
1351.2 | 49.5 | 1.0098
1351.3 | 49.5 | 1.0098
1351.4 | 49.5 | 1.0098
1351.5 | 49.5 | 1.0098
1351.6 | 49.5 | 1.0098
1351.7 | 49.5 | 1.0098
1351.8 | 49.5 | 1.0096
1351.9 | 49.5 | 1.0096
1352 | 49.5 | 1.0096
1352.1 | 49.5 | 1.0096
1352.2 | 49.5 | 1.0096
1352.3 | 49.5 | 1.0096
1352.4 | 49.5 | 1.0096
1352.5 | 49.5 | 1.0096
1352.6 | 49.5 | 1.0096
1352.7 | 49.5 | 1.0096
1352.8 | 49.5 | 1.0096
1352.9 | 49.5 | 1.0096
1353 | 49.5 | 1.0096
1353.1 | 49.5 | 1.0096
1353.2 | 49.5 | 1.0096
1353.3 | 49.5 | 1.0096
1353.4 | 49.5 | 1.0096
1353.5 | 49.5 | 1.0096
1353.6 | 49.5 | 1.0096
1353.7 | 49.5 | 1.0096
1353.8 | 49.5 | 1.0096
1353.9 | 49.5 | 1.0096
1354 | 49.5 | 1.0096
1354.1 | 49.5 | 1.0096
1354.2 | 49.5 | 1.0096
1354.3 | 49.5 | 1.0096
1354.4 | 49.5 | 1.0096
1354.5 | 49.5 | 1.0096
1354.6 | 49.5 | 1.0096
1354.7 | 49.5 | 1.0096
1354.8 | 49.5 | 1.0096
1354.9 | 49.5 | 1.0096
1355 | 49.5 | 1.0096
1355.1 | 49.5 | 1.0096
1355.2 | 49.5 | 1.0096
1355.3 | 49.5 | 1.0096
1355.4 | 49.5 | 1.0096
1355.5 | 49.5 | 1.0096
1355.6 | 49.5 | 1.0096
1355.7 | 49.5 | 1.0096
1355.8 | 49.5 | 1.0096
1355.9 | 49.5 | 1.0096
1356 | 49.5 | 1.0096
1356.1 | 49.5 | 1.0096
1356.2 | 49.5 | 1.0096
1356.3 | 49.5 | 1.0096
1356.4 | 49.5 | 1.0096
1356.5 | 49.5 | 1.0096
1356.6 | 49.5 | 1.0096
1356.7 | 49.5 | 1.0096
1356.8 | 49.5 | 1.0096
1356.9 | 49.5 | 1.0096
1357 | 49.5 | 1.0096
1357.1 | 49.5 | 1.0096
1357.2 | 49.5 | 1.0096
1357.3 | 49.5 | 1.0096
1357.4 | 49.5 | 1.0096
1357.5 | 49.5 | 1.0096
1357.6 | 49.5 | 1.0096
1357.7 | 49.5 | 1.0096
1357.8 | 49.5 | 1.0096
1357.9 | 49.5 | 1.0096
1358 | 49.5 | 1.0098
1358.1 | 49.5 | 1.0098
1358.2 | 49.5 | 1.0098
1358.3 | 49.5 | 1.0098
1358.4 | 49.5 | 1.0098
1358.5 | 49.5 | 1.0098
1358.6 | 49.5 | 1.0098
1358.7 | 49.5 | 1.0098
1358.8 | 49.5 | 1.0098
1358.9 | 49.5 | 1.0098
1359 | 49.5 | 1.0098
1359.1 | 49.5 | 1.0096
1359.2 | 49.5 | 1.0096
1359.3 | 49.5 | 1.0096
1359.4 | 49.5 | 1.0096
1359.5 | 49.5 | 1.0096
1359.6 | 49.5 | 1.0096
1359.7 | 49.5 | 1.0096
1359.8 | 49.5 | 1.0096
1359.9 | 49.5 | 1.0096
1360 | 49.5 | 1.0096
1360.1 | 49.5 | 1.0096
1360.2 | 49.5 | 1.0096
1360.3 | 49.5 | 1.0096
1360.4 | 49.5 | 1.0096
1360.5 | 49.5 | 1.0096
1360.6 | 49.5 | 1.0096
1360.7 | 49.5 | 1.0096
1360.8 | 49.5 | 1.0096
1360.9 | 49.5 | 1.0096
1361 | 49.5 | 1.0096
1361.1 | 49.5 | 1.0096
1361.2 | 49.5 | 1.0096
1361.3 | 49.5 | 1.0096
1361.4 | 49.5 | 1.0096
1361.5 | 49.5 | 1.0096
1361.6 | 49.5 | 1.0096
1361.7 | 49.5 | 1.0096
1361.8 | 49.5 | 1.0096
1361.9 | 49.5 | 1.0096
1362 | 49.5 | 1.0096
1362.1 | 49.5 | 1.0096
1362.2 | 49.5 | 1.0096
1362.3 | 49.5 | 1.0096
1362.4 | 49.5 | 1.0096
1362.5 | 49.5 | 1.0096
1362.6 | 49.5 | 1.0096
1362.7 | 49.5 | 1.0096
1362.8 | 49.5 | 1.0096
1362.9 | 49.5 | 1.0096
1363 | 49.5 | 1.0096
1363.1 | 49.5 | 1.0096
1363.2 | 49.5 | 1.0096
1363.3 | 49.5 | 1.0096
1363.4 | 49.5 | 1.0096
1363.5 | 49.5 | 1.0096
1363.6 | 49.5 | 1.0096
1363.7 | 49.5 | 1.0096
1363.8 | 49.5 | 1.0096
1363.9 | 49.5 | 1.0096
1364 | 49.5 | 1.0096
1364.1 | 49.5 | 1.0096
1364.2 | 49.5 | 1.0096
1364.3 | 49.5 | 1.0096
1364.4 | 49.5 | 1.0096
1364.5 | 49.5 | 1.0096
1364.6 | 49.5 | 1.0096
1364.7 | 49.5 | 1.0096
1364.8 | 49.5 | 1.0096
1364.9 | 49.5 | 1.0096
1365 | 49.5 | 1.0096
1365.1 | 49.5 | 1.0096
1365.2 | 49.5 | 1.0096
1365.3 | 49.5 | 1.0096
1365.4 | 49.5 | 1.0096
1365.5 | 49.5 | 1.0096
1365.6 | 49.5 | 1.0096
1365.7 | 49.5 | 1.0096
1365.8 | 49.5 | 1.0096
1365.9 | 49.5 | 1.0096
1366 | 49.5 | 1.0096
1366.1 | 49.5 | 1.0096
1366.2 | 49.5 | 1.0096
1366.3 | 49.5 | 1.0096
1366.4 | 49.5 | 1.0096
1366.5 | 49.5 | 1.0096
1366.6 | 49.5 | 1.0096
1366.7 | 49.5 | 1.0096
1366.8 | 49.5 | 1.0096
1366.9 | 49.5 | 1.0096
1367 | 49.5 | 1.0096
1367.1 | 49.5 | 1.0096
1367.2 | 49.5 | 1.0096
1367.3 | 49.5 | 1.0096
1367.4 | 49.5 | 1.0096
1367.5 | 49.5 | 1.0096
1367.6 | 49.5 | 1.0098
1367.7 | 49.5 | 1.0098
1367.8 | 49.5 | 1.0098
1367.9 | 49.5 | 1.0098
1368 | 49.5 | 1.0098
1368.1 | 49.5 | 1.0098
1368.2 | 49.5 | 1.0098
1368.3 | 49.5 | 1.0098
1368.4 | 49.5 | 1.0098
1368.5 | 49.5 | 1.0098
1368.6 | 49.5 | 1.0098
1368.7 | 49.5 | 1.0098
1368.8 | 49.5 | 1.0098
1368.9 | 49.5 | 1.0098
1369 | 49.5 | 1.0098
1369.1 | 49.5 | 1.0098
1369.2 | 49.5 | 1.0098
1369.3 | 49.5 | 1.0098
1369.4 | 49.5 | 1.0098
1369.5 | 49.5 | 1.0098
1369.6 | 49.5 | 1.0098
1369.7 | 49.5 | 1.0096
1369.8 | 49.5 | 1.0096
1369.9 | 49.5 | 1.0096
1370 | 49.5 | 1.0096
1370.1 | 49.5 | 1.0096
1370.2 | 49.5 | 1.0096
1370.3 | 49.5 | 1.0096
1370.4 | 49.5 | 1.0096
1370.5 | 49.5 | 1.0096
1370.6 | 49.5 | 1.0096
1370.7 | 49.5 | 1.0096
1370.8 | 49.5 | 1.0096
1370.9 | 49.5 | 1.0096
1371 | 49.5 | 1.0096
1371.1 | 49.5 | 1.0096
1371.2 | 49.5 | 1.0096
1371.3 | 49.5 | 1.0096
1371.4 | 49.5 | 1.0096
1371.5 | 49.5 | 1.0096
1371.6 | 49.5 | 1.0096
1371.7 | 49.5 | 1.0096
1371.8 | 49.5 | 1.0096
1371.9 | 49.5 | 1.0096
1372 | 49.5 | 1.0096
1372.1 | 49.5 | 1.0096
1372.2 | 49.5 | 1.0096
1372.3 | 49.5 | 1.0096
1372.4 | 49.5 | 1.0096
1372.5 | 49.5 | 1.0096
1372.6 | 49.5 | 1.0096
1372.7 | 49.5 | 1.0096
1372.8 | 49.5 | 1.0096
1372.9 | 49.5 | 1.0096
1373 | 49.5 | 1.0096
1373.1 | 49.5 | 1.0096
1373.2 | 49.5 | 1.0096
1373.3 | 49.5 | 1.0096
1373.4 | 49.5 | 1.0096
1373.5 | 49.5 | 1.0096
1373.6 | 49.5 | 1.0096
1373.7 | 49.5 | 1.0096
1373.8 | 49.5 | 1.0096
1373.9 | 49.5 | 1.0096
1374 | 49.5 | 1.0096
1374.1 | 49.5 | 1.0096
1374.2 | 49.5 | 1.0096
1374.3 | 49.5 | 1.0096
1374.4 | 49.5 | 1.0096
1374.5 | 49.5 | 1.0096
1374.6 | 49.5 | 1.0096
1374.7 | 49.5 | 1.0096
1374.8 | 49.5 | 1.0096
1374.9 | 49.5 | 1.0096
1375 | 49.5 | 1.0096
1375.1 | 49.5 | 1.0096
1375.2 | 49.5 | 1.0096
1375.3 | 49.5 | 1.0096
1375.4 | 49.5 | 1.0096
1375.5 | 49.5 | 1.0096
1375.6 | 49.5 | 1.0096
1375.7 | 49.5 | 1.0096
1375.8 | 49.5 | 1.0096
1375.9 | 49.5 | 1.0096
1376 | 49.5 | 1.0096
1376.1 | 49.5 | 1.0096
1376.2 | 49.5 | 1.0096
1376.3 | 49.5 | 1.0096
1376.4 | 49.5 | 1.0096
1376.5 | 49.5 | 1.0096
1376.6 | 49.5 | 1.0096
1376.7 | 49.5 | 1.0096
1376.8 | 49.5 | 1.0096
1376.9 | 49.5 | 1.0096
1377 | 49.5 | 1.0096
1377.1 | 49.5 | 1.0096
1377.2 | 49.5 | 1.0096
1377.3 | 49.5 | 1.0096
1377.4 | 49.5 | 1.0096
1377.5 | 49.5 | 1.0096
1377.6 | 49.5 | 1.0096
1377.7 | 49.5 | 1.0096
1377.8 | 49.5 | 1.0096
1377.9 | 49.5 | 1.0096
1378 | 49.5 | 1.0096
1378.1 | 49.5 | 1.0096
1378.2 | 49.5 | 1.0096
1378.3 | 49.5 | 1.0096
1378.4 | 49.5 | 1.0096
1378.5 | 49.5 | 1.0096
1378.6 | 49.5 | 1.0096
1378.7 | 49.5 | 1.0096
1378.8 | 49.5 | 1.0096
1378.9 | 49.5 | 1.0096
1379 | 49.5 | 1.0096
1379.1 | 49.5 | 1.0096
1379.2 | 49.5 | 1.0096
1379.3 | 49.5 | 1.0096
1379.4 | 49.5 | 1.0096
1379.5 | 49.5 | 1.0096
1379.6 | 49.5 | 1.0096
1379.7 | 49.5 | 1.0096
1379.8 | 49.5 | 1.0096
1379.9 | 49.5 | 1.0096
1380 | 49.5 | 1.0096
1380.1 | 49.5 | 1.0096
1380.2 | 49.5 | 1.0096
1380.3 | 49.5 | 1.0096
1380.4 | 49.5 | 1.0096
1380.5 | 49.5 | 1.0096
1380.6 | 49.5 | 1.0096
1380.7 | 49.5 | 1.0096
1380.8 | 49.5 | 1.0096
1380.9 | 49.5 | 1.0096
1381 | 49.5 | 1.0096
1381.1 | 49.5 | 1.0096
1381.2 | 49.5 | 1.0098
1381.3 | 49.5 | 1.0098
1381.4 | 49.5 | 1.0098
1381.5 | 49.5 | 1.0098
1381.6 | 49.5 | 1.0098
1381.7 | 49.5 | 1.0098
1381.8 | 49.5 | 1.0098
1381.9 | 49.5 | 1.0098
1382 | 49.5 | 1.0098
1382.1 | 49.5 | 1.0098
1382.2 | 49.5 | 1.0098
1382.3 | 49.5 | 1.0098
1382.4 | 49.5 | 1.0098
1382.5 | 49.5 | 1.0098
1382.6 | 49.5 | 1.0098
1382.7 | 49.5 | 1.0098
1382.8 | 49.5 | 1.0098
1382.9 | 49.5 | 1.0098
1383 | 49.5 | 1.0098
1383.1 | 49.5 | 1.0098
1383.2 | 49.5 | 1.0098
1383.3 | 49.5 | 1.0098
1383.4 | 49.5 | 1.0098
1383.5 | 49.5 | 1.0098
1383.6 | 49.5 | 1.0098
1383.7 | 49.5 | 1.0096
1383.8 | 49.5 | 1.0096
1383.9 | 49.5 | 1.0096
1384 | 49.5 | 1.0096
1384.1 | 49.5 | 1.0096
1384.2 | 49.5 | 1.0096
1384.3 | 49.5 | 1.0096
1384.4 | 49.5 | 1.0096
1384.5 | 49.5 | 1.0096
1384.6 | 49.5 | 1.0096
1384.7 | 49.5 | 1.0096
1384.8 | 49.5 | 1.0096
1384.9 | 49.5 | 1.0096
1385 | 49.5 | 1.0096
1385.1 | 49.5 | 1.0096
1385.2 | 49.5 | 1.0096
1385.3 | 49.5 | 1.0096
1385.4 | 49.5 | 1.0096
1385.5 | 49.5 | 1.0096
1385.6 | 49.5 | 1.0096
1385.7 | 49.5 | 1.0096
1385.8 | 49.5 | 1.0096
1385.9 | 49.5 | 1.0096
1386 | 49.5 | 1.0096
1386.1 | 49.5 | 1.0096
1386.2 | 49.5 | 1.0096
1386.3 | 49.5 | 1.0096
1386.4 | 49.5 | 1.0096
1386.5 | 49.5 | 1.0096
1386.6 | 49.5 | 1.0096
1386.7 | 49.5 | 1.0096
1386.8 | 49.5 | 1.0096
1386.9 | 49.5 | 1.0096
1387 | 49.5 | 1.0096
1387.1 | 49.5 | 1.0096
1387.2 | 49.5 | 1.0096
1387.3 | 49.5 | 1.0096
1387.4 | 49.5 | 1.0096
1387.5 | 49.5 | 1.0096
1387.6 | 49.5 | 1.0096
1387.7 | 49.5 | 1.0096
1387.8 | 49.5 | 1.0096
1387.9 | 49.5 | 1.0096
1388 | 49.5 | 1.0096
1388.1 | 49.5 | 1.0096
1388.2 | 49.5 | 1.0096
1388.3 | 49.5 | 1.0096
1388.4 | 49.5 | 1.0096
1388.5 | 49.5 | 1.0096
1388.6 | 49.5 | 1.0096
1388.7 | 49.5 | 1.0096
1388.8 | 49.5 | 1.0096
1388.9 | 49.5 | 1.0096
1389 | 49.5 | 1.0096
1389.1 | 49.5 | 1.0096
1389.2 | 49.5 | 1.0096
1389.3 | 49.5 | 1.0096
1389.4 | 49.5 | 1.0096
1389.5 | 49.5 | 1.0096
1389.6 | 49.5 | 1.0096
1389.7 | 49.5 | 1.0096
1389.8 | 49.5 | 1.0096
1389.9 | 49.5 | 1.0096
1390 | 49.5 | 1.0096
1390.1 | 49.5 | 1.0096
1390.2 | 49.5 | 1.0096
1390.3 | 49.5 | 1.0096
1390.4 | 49.5 | 1.0096
1390.5 | 49.5 | 1.0096
1390.6 | 49.5 | 1.0096
1390.7 | 49.5 | 1.0096
1390.8 | 49.5 | 1.0096
1390.9 | 49.5 | 1.0096
1391 | 49.5 | 1.0096
1391.1 | 49.5 | 1.0096
1391.2 | 49.5 | 1.0096
1391.3 | 49.5 | 1.0096
1391.4 | 49.5 | 1.0096
1391.5 | 49.5 | 1.0096
1391.6 | 49.5 | 1.0096
1391.7 | 49.5 | 1.0096
1391.8 | 49.5 | 1.0096
1391.9 | 49.5 | 1.0096
1392 | 49.5 | 1.0096
1392.1 | 49.5 | 1.0096
1392.2 | 49.5 | 1.0096
1392.3 | 49.5 | 1.0096
1392.4 | 49.5 | 1.0096
1392.5 | 49.5 | 1.0096
1392.6 | 49.5 | 1.0096
1392.7 | 49.5 | 1.0096
1392.8 | 49.5 | 1.0096
1392.9 | 49.5 | 1.0096
1393 | 49.5 | 1.0096
1393.1 | 49.5 | 1.0096
1393.2 | 49.5 | 1.0096
1393.3 | 49.5 | 1.0096
1393.4 | 49.5 | 1.0096
1393.5 | 49.5 | 1.0096
1393.6 | 49.5 | 1.0096
1393.7 | 49.5 | 1.0096
1393.8 | 49.5 | 1.0096
1393.9 | 49.5 | 1.0096
1394 | 49.5 | 1.0096
1394.1 | 49.5 | 1.0096
1394.2 | 49.5 | 1.0096
1394.3 | 49.5 | 1.0096
1394.4 | 49.5 | 1.0096
1394.5 | 49.5 | 1.0096
1394.6 | 49.5 | 1.0096
1394.7 | 49.5 | 1.0096
1394.8 | 49.5 | 1.0096
1394.9 | 49.5 | 1.0096
1395 | 49.5 | 1.0096
1395.1 | 49.5 | 1.0096
1395.2 | 49.5 | 1.0096
1395.3 | 49.5 | 1.0096
1395.4 | 49.5 | 1.0096
1395.5 | 49.5 | 1.0096
1395.6 | 49.5 | 1.0096
1395.7 | 49.5 | 1.0096
1395.8 | 49.5 | 1.0096
1395.9 | 49.5 | 1.0096
1396 | 49.5 | 1.0096
1396.1 | 49.5 | 1.0096
1396.2 | 49.5 | 1.0096
1396.3 | 49.5 | 1.0096
1396.4 | 49.5 | 1.0096
1396.5 | 49.5 | 1.0096
1396.6 | 49.5 | 1.0096
1396.7 | 49.5 | 1.0096
1396.8 | 49.5 | 1.0096
1396.9 | 49.5 | 1.0096
1397 | 49.5 | 1.0096
1397.1 | 49.5 | 1.0096
1397.2 | 49.5 | 1.0096
1397.3 | 49.5 | 1.0096
1397.4 | 49.5 | 1.0096
1397.5 | 49.5 | 1.0096
1397.6 | 49.5 | 1.0096
1397.7 | 49.5 | 1.0096
1397.8 | 49.5 | 1.0096
1397.9 | 49.5 | 1.0096
1398 | 49.5 | 1.0096
1398.1 | 49.5 | 1.0096
1398.2 | 49.5 | 1.0096
1398.3 | 49.5 | 1.0096
1398.4 | 49.5 | 1.0096
1398.5 | 49.5 | 1.0096
1398.6 | 49.5 | 1.0096
1398.7 | 49.5 | 1.0096
1398.8 | 49.5 | 1.0098
1398.9 | 49.5 | 1.0098
1399 | 49.5 | 1.0098
1399.1 | 49.5 | 1.0098
1399.2 | 49.5 | 1.0098
1399.3 | 49.5 | 1.0098
1399.4 | 49.5 | 1.0098
1399.5 | 49.5 | 1.0098
1399.6 | 49.5 | 1.0098
1399.7 | 49.5 | 1.0098
1399.8 | 49.5 | 1.0098
1399.9 | 49.5 | 1.0098
1400 | 49.5 | 1.0098
1400.1 | 49.5 | 1.0098
1400.2 | 49.5 | 1.0098
1400.3 | 49.5 | 1.0098
1400.4 | 49.5 | 1.0098
1400.5 | 49.5 | 1.0098
1400.6 | 49.5 | 1.0098
1400.7 | 49.5 | 1.0098
1400.8 | 49.5 | 1.0098
1400.9 | 49.5 | 1.0098
1401 | 49.5 | 1.0098
1401.1 | 49.5 | 1.0096
1401.2 | 49.5 | 1.0096
1401.3 | 49.5 | 1.0096
1401.4 | 49.5 | 1.0096
1401.5 | 49.5 | 1.0096
1401.6 | 49.5 | 1.0096
1401.7 | 49.5 | 1.0096
1401.8 | 49.5 | 1.0096
1401.9 | 49.5 | 1.0096
1402 | 49.5 | 1.0096
1402.1 | 49.5 | 1.0096
1402.2 | 49.5 | 1.0096
1402.3 | 49.5 | 1.0096
1402.4 | 49.5 | 1.0096
1402.5 | 49.5 | 1.0096
1402.6 | 49.5 | 1.0096
1402.7 | 49.5 | 1.0096
1402.8 | 49.5 | 1.0096
1402.9 | 49.5 | 1.0096
1403 | 49.5 | 1.0096
1403.1 | 49.5 | 1.0096
1403.2 | 49.5 | 1.0096
1403.3 | 49.5 | 1.0096
1403.4 | 49.5 | 1.0096
1403.5 | 49.5 | 1.0096
1403.6 | 49.5 | 1.0096
1403.7 | 49.5 | 1.0096
1403.8 | 49.5 | 1.0096
1403.9 | 49.5 | 1.0096
1404 | 49.5 | 1.0096
1404.1 | 49.5 | 1.0096
1404.2 | 49.5 | 1.0096
1404.3 | 49.5 | 1.0096
1404.4 | 49.5 | 1.0096
1404.5 | 49.5 | 1.0096
1404.6 | 49.5 | 1.0096
1404.7 | 49.5 | 1.0096
1404.8 | 49.5 | 1.0096
1404.9 | 49.5 | 1.0096
1405 | 49.5 | 1.0096
1405.1 | 49.5 | 1.0096
1405.2 | 49.5 | 1.0096
1405.3 | 49.5 | 1.0096
1405.4 | 49.5 | 1.0096
1405.5 | 49.5 | 1.0096
1405.6 | 49.5 | 1.0096
1405.7 | 49.5 | 1.0096
1405.8 | 49.5 | 1.0098
1405.9 | 49.5 | 1.0098
1406 | 49.5 | 1.0098
1406.1 | 49.5 | 1.0098
1406.2 | 49.5 | 1.0098
1406.3 | 49.5 | 1.0098
1406.4 | 49.5 | 1.0098
1406.5 | 49.5 | 1.0098
1406.6 | 49.5 | 1.0098
1406.7 | 49.5 | 1.0098
1406.8 | 49.5 | 1.0098
1406.9 | 49.5 | 1.0098
1407 | 49.5 | 1.0098
1407.1 | 49.5 | 1.0098
1407.2 | 49.5 | 1.0098
1407.3 | 49.5 | 1.0098
1407.4 | 49.5 | 1.0098
1407.5 | 49.5 | 1.0098
1407.6 | 49.5 | 1.0098
1407.7 | 49.5 | 1.0098
1407.8 | 49.5 | 1.0098
1407.9 | 49.5 | 1.0098
1408 | 49.5 | 1.0098
1408.1 | 49.5 | 1.0098
1408.2 | 49.5 | 1.0096
1408.3 | 49.5 | 1.0096
1408.4 | 49.5 | 1.0096
1408.5 | 49.5 | 1.0096
1408.6 | 49.5 | 1.0096
1408.7 | 49.5 | 1.0096
1408.8 | 49.5 | 1.0096
1408.9 | 49.5 | 1.0096
1409 | 49.5 | 1.0096
1409.1 | 49.5 | 1.0096
1409.2 | 49.5 | 1.0096
1409.3 | 49.5 | 1.0096
1409.4 | 49.5 | 1.0096
1409.5 | 49.5 | 1.0096
1409.6 | 49.5 | 1.0096
1409.7 | 49.5 | 1.0096
1409.8 | 49.5 | 1.0096
1409.9 | 49.5 | 1.0096
1410 | 49.5 | 1.0096
1410.1 | 49.5 | 1.0096
1410.2 | 49.5 | 1.0096
1410.3 | 49.5 | 1.0096
1410.4 | 49.5 | 1.0096
1410.5 | 49.5 | 1.0096
1410.6 | 49.5 | 1.0096
1410.7 | 49.5 | 1.0096
1410.8 | 49.5 | 1.0096
1410.9 | 49.5 | 1.0096
1411 | 49.5 | 1.0096
1411.1 | 49.5 | 1.0096
1411.2 | 49.5 | 1.0096
1411.3 | 49.5 | 1.0096
1411.4 | 49.5 | 1.0096
1411.5 | 49.5 | 1.0096
1411.6 | 49.5 | 1.0096
1411.7 | 49.5 | 1.0096
1411.8 | 49.5 | 1.0096
1411.9 | 49.5 | 1.0096
1412 | 49.5 | 1.0096
1412.1 | 49.5 | 1.0096
1412.2 | 49.5 | 1.0096
1412.3 | 49.5 | 1.0096
1412.4 | 49.5 | 1.0096
1412.5 | 49.5 | 1.0096
1412.6 | 49.5 | 1.0096
1412.7 | 49.5 | 1.0096
1412.8 | 49.5 | 1.0096
1412.9 | 49.5 | 1.0096
1413 | 49.5 | 1.0096
1413.1 | 49.5 | 1.0096
1413.2 | 49.5 | 1.0096
1413.3 | 49.5 | 1.0096
1413.4 | 49.5 | 1.0096
1413.5 | 49.5 | 1.0096
1413.6 | 49.5 | 1.0096
1413.7 | 49.5 | 1.0096
1413.8 | 49.5 | 1.0096
1413.9 | 49.5 | 1.0096
1414 | 49.5 | 1.0096
1414.1 | 49.5 | 1.0096
1414.2 | 49.5 | 1.0096
1414.3 | 49.5 | 1.0096
1414.4 | 49.5 | 1.0096
1414.5 | 49.5 | 1.0096
1414.6 | 49.5 | 1.0096
1414.7 | 49.5 | 1.0096
1414.8 | 49.5 | 1.0096
1414.9 | 49.5 | 1.0096
1415 | 49.5 | 1.0096
1415.1 | 49.5 | 1.0096
1415.2 | 49.5 | 1.0096
1415.3 | 49.5 | 1.0096
1415.4 | 49.5 | 1.0096
1415.5 | 49.5 | 1.0096
1415.6 | 49.5 | 1.0096
1415.7 | 49.5 | 1.0096
1415.8 | 49.5 | 1.0096
1415.9 | 49.5 | 1.0096
1416 | 49.5 | 1.0096
1416.1 | 49.5 | 1.0096
1416.2 | 49.5 | 1.0096
1416.3 | 49.5 | 1.0096
1416.4 | 49.5 | 1.0096
1416.5 | 49.5 | 1.0096
1416.6 | 49.5 | 1.0096
1416.7 | 49.5 | 1.0096
1416.8 | 49.5 | 1.0096
1416.9 | 49.5 | 1.0096
1417 | 49.5 | 1.0096
1417.1 | 49.5 | 1.0096
1417.2 | 49.5 | 1.0096
1417.3 | 49.5 | 1.0096
1417.4 | 49.5 | 1.0096
1417.5 | 49.5 | 1.0096
1417.6 | 49.5 | 1.0096
1417.7 | 49.5 | 1.0096
1417.8 | 49.5 | 1.0096
1417.9 | 49.5 | 1.0096
1418 | 49.5 | 1.0096
1418.1 | 49.5 | 1.0096
1418.2 | 49.5 | 1.0096
1418.3 | 49.5 | 1.0096
1418.4 | 49.5 | 1.0096
1418.5 | 49.5 | 1.0096
1418.6 | 49.5 | 1.0096
1418.7 | 49.5 | 1.0096
1418.8 | 49.5 | 1.0096
1418.9 | 49.5 | 1.0096
1419 | 49.5 | 1.0096
1419.1 | 49.5 | 1.0096
1419.2 | 49.5 | 1.0096
1419.3 | 49.5 | 1.0096
1419.4 | 49.5 | 1.0096
1419.5 | 49.5 | 1.0096
1419.6 | 49.5 | 1.0096
1419.7 | 49.5 | 1.0096
1419.8 | 49.5 | 1.0096
1419.9 | 49.5 | 1.0096
1420 | 49.5 | 1.0096
1420.1 | 49.5 | 1.0096
1420.2 | 49.5 | 1.0096
1420.3 | 49.5 | 1.0096
1420.4 | 49.5 | 1.0096
1420.5 | 49.5 | 1.0096
1420.6 | 49.5 | 1.0096
1420.7 | 49.5 | 1.0096
1420.8 | 49.5 | 1.0096
1420.9 | 49.5 | 1.0096
1421 | 49.5 | 1.0096
1421.1 | 49.5 | 1.0096
1421.2 | 49.5 | 1.0096
1421.3 | 49.5 | 1.0096
1421.4 | 49.5 | 1.0096
1421.5 | 49.5 | 1.0096
1421.6 | 49.5 | 1.0096
1421.7 | 49.5 | 1.0096
1421.8 | 49.5 | 1.0096
1421.9 | 49.5 | 1.0096
1422 | 49.5 | 1.0096
1422.1 | 49.5 | 1.0096
1422.2 | 49.5 | 1.0096
1422.3 | 49.5 | 1.0096
1422.4 | 49.5 | 1.0096
1422.5 | 49.5 | 1.0096
1422.6 | 49.5 | 1.0096
1422.7 | 49.5 | 1.0096
1422.8 | 49.5 | 1.0096
1422.9 | 49.5 | 1.0096
1423 | 49.5 | 1.0096
1423.1 | 49.5 | 1.0096
1423.2 | 49.5 | 1.0096
1423.3 | 49.5 | 1.0096
1423.4 | 49.5 | 1.0096
1423.5 | 49.5 | 1.0096
1423.6 | 49.5 | 1.0096
1423.7 | 49.5 | 1.0096
1423.8 | 49.5 | 1.0096
1423.9 | 49.5 | 1.0096
1424 | 49.5 | 1.0096
1424.1 | 49.5 | 1.0096
1424.2 | 49.5 | 1.0096
1424.3 | 49.5 | 1.0096
1424.4 | 49.5 | 1.0096
1424.5 | 49.5 | 1.0096
1424.6 | 49.5 | 1.0096
1424.7 | 49.5 | 1.0096
1424.8 | 49.5 | 1.0096
1424.9 | 49.5 | 1.0096
1425 | 49.5 | 1.0096
1425.1 | 49.5 | 1.0096
1425.2 | 49.5 | 1.0096
1425.3 | 49.5 | 1.0096
1425.4 | 49.5 | 1.0096
1425.5 | 49.5 | 1.0096
1425.6 | 49.5 | 1.0096
1425.7 | 49.5 | 1.0096
1425.8 | 49.5 | 1.0096
1425.9 | 49.5 | 1.0096
1426 | 49.5 | 1.0096
1426.1 | 49.5 | 1.0096
1426.2 | 49.5 | 1.0096
1426.3 | 49.5 | 1.0096
1426.4 | 49.5 | 1.0096
1426.5 | 49.5 | 1.0096
1426.6 | 49.5 | 1.0096
1426.7 | 49.5 | 1.0096
1426.8 | 49.5 | 1.0096
1426.9 | 49.5 | 1.0096
1427 | 49.5 | 1.0096
1427.1 | 49.5 | 1.0096
1427.2 | 49.5 | 1.0096
1427.3 | 49.5 | 1.0096
1427.4 | 49.5 | 1.0096
1427.5 | 49.5 | 1.0096
1427.6 | 49.5 | 1.0096
1427.7 | 49.5 | 1.0096
1427.8 | 49.5 | 1.0096
1427.9 | 49.5 | 1.0096
1428 | 49.5 | 1.0096
1428.1 | 49.5 | 1.0096
1428.2 | 49.5 | 1.0096
1428.3 | 49.5 | 1.0096
1428.4 | 49.5 | 1.0096
1428.5 | 49.5 | 1.0096
1428.6 | 49.5 | 1.0096
1428.7 | 49.5 | 1.0096
1428.8 | 49.5 | 1.0096
1428.9 | 49.5 | 1.0096
1429 | 49.5 | 1.0096
1429.1 | 49.5 | 1.0096
1429.2 | 49.5 | 1.0096
1429.3 | 49.5 | 1.0096
1429.4 | 49.5 | 1.0096
1429.5 | 49.5 | 1.0096
1429.6 | 49.5 | 1.0096
1429.7 | 49.5 | 1.0096
1429.8 | 49.5 | 1.0096
1429.9 | 49.5 | 1.0096
1430 | 49.5 | 1.0096
1430.1 | 49.5 | 1.0096
1430.2 | 49.5 | 1.0096
1430.3 | 49.5 | 1.0096
1430.4 | 49.5 | 1.0096
1430.5 | 49.5 | 1.0096
1430.6 | 49.5 | 1.0096
1430.7 | 49.5 | 1.0096
1430.8 | 49.5 | 1.0096
1430.9 | 49.5 | 1.0096
1431 | 49.5 | 1.0096
1431.1 | 49.5 | 1.0096
1431.2 | 49.5 | 1.0096
1431.3 | 49.5 | 1.0096
1431.4 | 49.5 | 1.0096
1431.5 | 49.5 | 1.0096
1431.6 | 49.5 | 1.0096
1431.7 | 49.5 | 1.0096
1431.8 | 49.5 | 1.0096
1431.9 | 49.5 | 1.0096
1432 | 49.5 | 1.0096
1432.1 | 49.5 | 1.0096
1432.2 | 49.5 | 1.0096
1432.3 | 49.5 | 1.0096
1432.4 | 49.5 | 1.0096
1432.5 | 49.5 | 1.0096
1432.6 | 49.5 | 1.0096
1432.7 | 49.5 | 1.0096
1432.8 | 49.5 | 1.0096
1432.9 | 49.5 | 1.0096
1433 | 49.5 | 1.0096
1433.1 | 49.5 | 1.0096
1433.2 | 49.5 | 1.0096
1433.3 | 49.5 | 1.0096
1433.4 | 49.5 | 1.0096
1433.5 | 49.5 | 1.0096
1433.6 | 49.5 | 1.0096
1433.7 | 49.5 | 1.0096
1433.8 | 49.5 | 1.0096
1433.9 | 49.5 | 1.0096
1434 | 49.5 | 1.0096
1434.1 | 49.5 | 1.0096
1434.2 | 49.5 | 1.0096
1434.3 | 49.5 | 1.0096
1434.4 | 49.5 | 1.0096
1434.5 | 49.5 | 1.0096
1434.6 | 49.5 | 1.0096
1434.7 | 49.5 | 1.0096
1434.8 | 49.5 | 1.0096
1434.9 | 49.5 | 1.0096
1435 | 49.5 | 1.0096
1435.1 | 49.5 | 1.0096
1435.2 | 49.5 | 1.0096
1435.3 | 49.5 | 1.0096
1435.4 | 49.5 | 1.0096
1435.5 | 49.5 | 1.0096
1435.6 | 49.5 | 1.0096
1435.7 | 49.5 | 1.0096
1435.8 | 49.5 | 1.0096
1435.9 | 49.5 | 1.0096
1436 | 49.5 | 1.0096
1436.1 | 49.5 | 1.0096
1436.2 | 49.5 | 1.0096
1436.3 | 49.5 | 1.0096
1436.4 | 49.5 | 1.0096
1436.5 | 49.5 | 1.0096
1436.6 | 49.5 | 1.0096
1436.7 | 49.5 | 1.0096
1436.8 | 49.5 | 1.0096
1436.9 | 49.5 | 1.0096
1437 | 49.5 | 1.0096
1437.1 | 49.5 | 1.0096
1437.2 | 49.5 | 1.0096
1437.3 | 49.5 | 1.0096
1437.4 | 49.5 | 1.0096
1437.5 | 49.5 | 1.0096
1437.6 | 49.5 | 1.0096
1437.7 | 49.5 | 1.0096
1437.8 | 49.5 | 1.0096
1437.9 | 49.5 | 1.0096
1438 | 49.5 | 1.0096
1438.1 | 49.5 | 1.0096
1438.2 | 49.5 | 1.0096
1438.3 | 49.5 | 1.0096
1438.4 | 49.5 | 1.0096
1438.5 | 49.5 | 1.0096
1438.6 | 49.5 | 1.0096
1438.7 | 49.5 | 1.0096
1438.8 | 49.5 | 1.0096
1438.9 | 49.5 | 1.0096
1439 | 49.5 | 1.0096
1439.1 | 49.5 | 1.0096
1439.2 | 49.5 | 1.0096
1439.3 | 49.5 | 1.0096
1439.4 | 49.5 | 1.0096
1439.5 | 49.5 | 1.0096
1439.6 | 49.5 | 1.0096
1439.7 | 49.5 | 1.0096
1439.8 | 49.5 | 1.0096
1439.9 | 49.5 | 1.0096
1440 | 49.5 | 1.0096
1440.1 | 49.5 | 1.0096
1440.2 | 49.5 | 1.0096
1440.3 | 49.5 | 1.0096
1440.4 | 49.5 | 1.0096
1440.5 | 49.5 | 1.0096
1440.6 | 49.5 | 1.0096
1440.7 | 49.5 | 1.0096
1440.8 | 49.5 | 1.0096
1440.9 | 49.5 | 1.0096
1441 | 49.5 | 1.0096
1441.1 | 49.5 | 1.0096
1441.2 | 49.5 | 1.0096
1441.3 | 49.5 | 1.0096
1441.4 | 49.5 | 1.0096
1441.5 | 49.5 | 1.0096
1441.6 | 49.5 | 1.0096
1441.7 | 49.5 | 1.0096
1441.8 | 49.5 | 1.0096
1441.9 | 49.5 | 1.0096
1442 | 49.5 | 1.0096
1442.1 | 49.5 | 1.0096
1442.2 | 49.5 | 1.0096
1442.3 | 49.5 | 1.0096
1442.4 | 49.5 | 1.0096
1442.5 | 49.5 | 1.0096
1442.6 | 49.5 | 1.0096
1442.7 | 49.5 | 1.0096
1442.8 | 49.5 | 1.0096
1442.9 | 49.5 | 1.0096
1443 | 49.5 | 1.0096
1443.1 | 49.5 | 1.0096
1443.2 | 49.5 | 1.0096
1443.3 | 49.5 | 1.0096
1443.4 | 49.5 | 1.0096
1443.5 | 49.5 | 1.0096
1443.6 | 49.5 | 1.0096
1443.7 | 49.5 | 1.0096
1443.8 | 49.5 | 1.0096
1443.9 | 49.5 | 1.0096
1444 | 49.5 | 1.0096
1444.1 | 49.5 | 1.0096
1444.2 | 49.5 | 1.0096
1444.3 | 49.5 | 1.0096
1444.4 | 49.5 | 1.0096
1444.5 | 49.5 | 1.0096
1444.6 | 49.5 | 1.0096
1444.7 | 49.5 | 1.0096
1444.8 | 49.5 | 1.0096
1444.9 | 49.5 | 1.0096
1445 | 49.5 | 1.0096
1445.1 | 49.5 | 1.0096
1445.2 | 49.5 | 1.0096
1445.3 | 49.5 | 1.0096
1445.4 | 49.5 | 1.0096
1445.5 | 49.5 | 1.0096
1445.6 | 49.5 | 1.0096
1445.7 | 49.5 | 1.0096
1445.8 | 49.5 | 1.0096
1445.9 | 49.5 | 1.0096
1446 | 49.5 | 1.0096
1446.1 | 49.5 | 1.0096
1446.2 | 49.5 | 1.0096
1446.3 | 49.5 | 1.0096
1446.4 | 49.5 | 1.0096
1446.5 | 49.5 | 1.0096
1446.6 | 49.5 | 1.0096
1446.7 | 49.5 | 1.0096
1446.8 | 49.5 | 1.0096
1446.9 | 49.5 | 1.0096
1447 | 49.5 | 1.0096
1447.1 | 49.5 | 1.0096
1447.2 | 49.5 | 1.0096
1447.3 | 49.5 | 1.0096
1447.4 | 49.5 | 1.0096
1447.5 | 49.5 | 1.0096
1447.6 | 49.5 | 1.0096
1447.7 | 49.5 | 1.0096
1447.8 | 49.5 | 1.0096
1447.9 | 49.5 | 1.0096
1448 | 49.5 | 1.0096
1448.1 | 49.5 | 1.0096
1448.2 | 49.5 | 1.0096
1448.3 | 49.5 | 1.0096
1448.4 | 49.5 | 1.0096
1448.5 | 49.5 | 1.0096
1448.6 | 49.5 | 1.0096
1448.7 | 49.5 | 1.0096
1448.8 | 49.5 | 1.0096
1448.9 | 49.5 | 1.0096
1449 | 49.5 | 1.0096
1449.1 | 49.5 | 1.0096
1449.2 | 49.5 | 1.0096
1449.3 | 49.5 | 1.0096
1449.4 | 49.5 | 1.0096
1449.5 | 49.5 | 1.0096
1449.6 | 49.5 | 1.0098
1449.7 | 49.5 | 1.0098
1449.8 | 49.5 | 1.0098
1449.9 | 49.5 | 1.0098
1450 | 49.5 | 1.0098
1450.1 | 49.5 | 1.0098
1450.2 | 49.5 | 1.0098
1450.3 | 49.5 | 1.0098
1450.4 | 49.5 | 1.0098
1450.5 | 49.5 | 1.0098
1450.6 | 49.5 | 1.0098
1450.7 | 49.5 | 1.0098
1450.8 | 49.5 | 1.0098
1450.9 | 49.5 | 1.0098
1451 | 49.5 | 1.0098
1451.1 | 49.5 | 1.0098
1451.2 | 49.5 | 1.0098
1451.3 | 49.5 | 1.0098
1451.4 | 49.5 | 1.0098
1451.5 | 49.5 | 1.0098
1451.6 | 49.5 | 1.0098
1451.7 | 49.5 | 1.0098
1451.8 | 49.5 | 1.0098
1451.9 | 49.5 | 1.0098
1452 | 49.5 | 1.0098
1452.1 | 49.5 | 1.0098
1452.2 | 49.5 | 1.0098
1452.3 | 49.5 | 1.0098
1452.4 | 49.5 | 1.0098
1452.5 | 49.5 | 1.0098
1452.6 | 49.5 | 1.0098
1452.7 | 49.5 | 1.0098
1452.8 | 49.5 | 1.0098
1452.9 | 49.5 | 1.0098
1453 | 49.5 | 1.0098
1453.1 | 49.5 | 1.0096
1453.2 | 49.5 | 1.0096
1453.3 | 49.5 | 1.0096
1453.4 | 49.5 | 1.0096
1453.5 | 49.5 | 1.0096
1453.6 | 49.5 | 1.0096
1453.7 | 49.5 | 1.0096
1453.8 | 49.5 | 1.0096
1453.9 | 49.5 | 1.0096
1454 | 49.5 | 1.0096
1454.1 | 49.5 | 1.0096
1454.2 | 49.5 | 1.0096
1454.3 | 49.5 | 1.0096
1454.4 | 49.5 | 1.0096
1454.5 | 49.5 | 1.0096
1454.6 | 49.5 | 1.0096
1454.7 | 49.5 | 1.0096
1454.8 | 49.5 | 1.0096
1454.9 | 49.5 | 1.0096
1455 | 49.5 | 1.0096
1455.1 | 49.5 | 1.0096
1455.2 | 49.5 | 1.0096
1455.3 | 49.5 | 1.0096
1455.4 | 49.5 | 1.0096
1455.5 | 49.5 | 1.0096
1455.6 | 49.5 | 1.0096
1455.7 | 49.5 | 1.0096
1455.8 | 49.5 | 1.0096
1455.9 | 49.5 | 1.0096
1456 | 49.5 | 1.0096
1456.1 | 49.5 | 1.0096
1456.2 | 49.5 | 1.0096
1456.3 | 49.5 | 1.0096
1456.4 | 49.5 | 1.0096
1456.5 | 49.5 | 1.0096
1456.6 | 49.5 | 1.0096
1456.7 | 49.5 | 1.0096
1456.8 | 49.5 | 1.0096
1456.9 | 49.5 | 1.0096
1457 | 49.5 | 1.0096
1457.1 | 49.5 | 1.0096
1457.2 | 49.5 | 1.0096
1457.3 | 49.5 | 1.0096
1457.4 | 49.5 | 1.0096
1457.5 | 49.5 | 1.0096
1457.6 | 49.5 | 1.0096
1457.7 | 49.5 | 1.0096
1457.8 | 49.5 | 1.0096
1457.9 | 49.5 | 1.0096
1458 | 49.5 | 1.0096
1458.1 | 49.5 | 1.0096
1458.2 | 49.5 | 1.0096
1458.3 | 49.5 | 1.0096
1458.4 | 49.5 | 1.0096
1458.5 | 49.5 | 1.0096
1458.6 | 49.5 | 1.0096
1458.7 | 49.5 | 1.0096
1458.8 | 49.5 | 1.0096
1458.9 | 49.5 | 1.0096
1459 | 49.5 | 1.0096
1459.1 | 49.5 | 1.0096
1459.2 | 49.5 | 1.0096
1459.3 | 49.5 | 1.0096
1459.4 | 49.5 | 1.0096
1459.5 | 49.5 | 1.0096
1459.6 | 49.5 | 1.0096
1459.7 | 49.5 | 1.0096
1459.8 | 49.5 | 1.0096
1459.9 | 49.5 | 1.0096
1460 | 49.5 | 1.0096
1460.1 | 49.5 | 1.0096
1460.2 | 49.5 | 1.0096
1460.3 | 49.5 | 1.0096
1460.4 | 49.5 | 1.0096
1460.5 | 49.5 | 1.0096
1460.6 | 49.5 | 1.0096
1460.7 | 49.5 | 1.0096
1460.8 | 49.5 | 1.0096
1460.9 | 49.5 | 1.0096
1461 | 49.5 | 1.0096
1461.1 | 49.5 | 1.0096
1461.2 | 49.5 | 1.0096
1461.3 | 49.5 | 1.0096
1461.4 | 49.5 | 1.0096
1461.5 | 49.5 | 1.0096
1461.6 | 49.5 | 1.0096
1461.7 | 49.5 | 1.0096
1461.8 | 49.5 | 1.0096
1461.9 | 49.5 | 1.0096
1462 | 49.5 | 1.0096
1462.1 | 49.5 | 1.0096
1462.2 | 49.5 | 1.0096
1462.3 | 49.5 | 1.0096
1462.4 | 49.5 | 1.0096
1462.5 | 49.5 | 1.0096
1462.6 | 49.5 | 1.0096
1462.7 | 49.5 | 1.0096
1462.8 | 49.5 | 1.0096
1462.9 | 49.5 | 1.0096
1463 | 49.5 | 1.0096
1463.1 | 49.5 | 1.0096
1463.2 | 49.5 | 1.0096
1463.3 | 49.5 | 1.0096
1463.4 | 49.5 | 1.0096
1463.5 | 49.5 | 1.0096
1463.6 | 49.5 | 1.0096
1463.7 | 49.5 | 1.0096
1463.8 | 49.5 | 1.0096
1463.9 | 49.5 | 1.0096
1464 | 49.5 | 1.0096
1464.1 | 49.5 | 1.0096
1464.2 | 49.5 | 1.0098
1464.3 | 49.5 | 1.0098
1464.4 | 49.5 | 1.0098
1464.5 | 49.5 | 1.0098
1464.6 | 49.5 | 1.0098
1464.7 | 49.5 | 1.0098
1464.8 | 49.5 | 1.0098
1464.9 | 49.5 | 1.0098
1465 | 49.5 | 1.0098
1465.1 | 49.5 | 1.0098
1465.2 | 49.5 | 1.0098
1465.3 | 49.5 | 1.0098
1465.4 | 49.5 | 1.0098
1465.5 | 49.5 | 1.0098
1465.6 | 49.5 | 1.0098
1465.7 | 49.5 | 1.0098
1465.8 | 49.5 | 1.0098
1465.9 | 49.5 | 1.0098
1466 | 49.5 | 1.0098
1466.1 | 49.5 | 1.0098
1466.2 | 49.5 | 1.0098
1466.3 | 49.5 | 1.0098
1466.4 | 49.5 | 1.0098
1466.5 | 49.5 | 1.0098
1466.6 | 49.5 | 1.0096
1466.7 | 49.5 | 1.0096
1466.8 | 49.5 | 1.0096
1466.9 | 49.5 | 1.0096
1467 | 49.5 | 1.0096
1467.1 | 49.5 | 1.0096
1467.2 | 49.5 | 1.0096
1467.3 | 49.5 | 1.0096
1467.4 | 49.5 | 1.0096
1467.5 | 49.5 | 1.0096
1467.6 | 49.5 | 1.0096
1467.7 | 49.5 | 1.0096
1467.8 | 49.5 | 1.0096
1467.9 | 49.5 | 1.0096
1468 | 49.5 | 1.0096
1468.1 | 49.5 | 1.0096
1468.2 | 49.5 | 1.0096
1468.3 | 49.5 | 1.0096
1468.4 | 49.5 | 1.0096
1468.5 | 49.5 | 1.0096
1468.6 | 49.5 | 1.0096
1468.7 | 49.5 | 1.0096
1468.8 | 49.5 | 1.0096
1468.9 | 49.5 | 1.0096
1469 | 49.5 | 1.0096
1469.1 | 49.5 | 1.0096
1469.2 | 49.5 | 1.0096
1469.3 | 49.5 | 1.0098
1469.4 | 49.5 | 1.0098
1469.5 | 49.5 | 1.0098
1469.6 | 49.5 | 1.0098
1469.7 | 49.5 | 1.0098
1469.8 | 49.5 | 1.0098
1469.9 | 49.5 | 1.0098
1470 | 49.5 | 1.0098
1470.1 | 49.5 | 1.0098
1470.2 | 49.5 | 1.0098
1470.3 | 49.5 | 1.0098
1470.4 | 49.5 | 1.0098
1470.5 | 49.5 | 1.0098
1470.6 | 49.5 | 1.0098
1470.7 | 49.5 | 1.0098
1470.8 | 49.5 | 1.0098
1470.9 | 49.5 | 1.0098
1471 | 49.5 | 1.0098
1471.1 | 49.5 | 1.0098
1471.2 | 49.5 | 1.0098
1471.3 | 49.5 | 1.0098
1471.4 | 49.5 | 1.0098
1471.5 | 49.5 | 1.0096
1471.6 | 49.5 | 1.0096
1471.7 | 49.5 | 1.0096
1471.8 | 49.5 | 1.0096
1471.9 | 49.5 | 1.0096
1472 | 49.5 | 1.0096
1472.1 | 49.5 | 1.0096
1472.2 | 49.5 | 1.0096
1472.3 | 49.5 | 1.0096
1472.4 | 49.5 | 1.0096
1472.5 | 49.5 | 1.0096
1472.6 | 49.5 | 1.0096
1472.7 | 49.5 | 1.0096
1472.8 | 49.5 | 1.0096
1472.9 | 49.5 | 1.0096
1473 | 49.5 | 1.0096
1473.1 | 49.5 | 1.0096
1473.2 | 49.5 | 1.0096
1473.3 | 49.5 | 1.0096
1473.4 | 49.5 | 1.0096
1473.5 | 49.5 | 1.0096
1473.6 | 49.5 | 1.0096
1473.7 | 49.5 | 1.0096
1473.8 | 49.5 | 1.0096
1473.9 | 49.5 | 1.0096
1474 | 49.5 | 1.0096
1474.1 | 49.5 | 1.0096
1474.2 | 49.5 | 1.0096
1474.3 | 49.5 | 1.0096
1474.4 | 49.5 | 1.0096
1474.5 | 49.5 | 1.0096
1474.6 | 49.5 | 1.0096
1474.7 | 49.5 | 1.0096
1474.8 | 49.5 | 1.0096
1474.9 | 49.5 | 1.0096
1475 | 49.5 | 1.0096
1475.1 | 49.5 | 1.0096
1475.2 | 49.5 | 1.0096
1475.3 | 49.5 | 1.0098
1475.4 | 49.5 | 1.0098
1475.5 | 49.5 | 1.0098
1475.6 | 49.5 | 1.0098
1475.7 | 49.5 | 1.0098
1475.8 | 49.5 | 1.0098
1475.9 | 49.5 | 1.0098
1476 | 49.5 | 1.0098
1476.1 | 49.5 | 1.0098
1476.2 | 49.5 | 1.0098
1476.3 | 49.5 | 1.0098
1476.4 | 49.5 | 1.0098
1476.5 | 49.5 | 1.0098
1476.6 | 49.5 | 1.0098
1476.7 | 49.5 | 1.0098
1476.8 | 49.5 | 1.0098
1476.9 | 49.5 | 1.0098
1477 | 49.5 | 1.0098
1477.1 | 49.5 | 1.0098
1477.2 | 49.5 | 1.0098
1477.3 | 49.5 | 1.0098
1477.4 | 49.5 | 1.0098
1477.5 | 49.5 | 1.0098
1477.6 | 49.5 | 1.0096
1477.7 | 49.5 | 1.0096
1477.8 | 49.5 | 1.0096
1477.9 | 49.5 | 1.0096
1478 | 49.5 | 1.0096
1478.1 | 49.5 | 1.0096
1478.2 | 49.5 | 1.0096
1478.3 | 49.5 | 1.0096
1478.4 | 49.5 | 1.0096
1478.5 | 49.5 | 1.0096
1478.6 | 49.5 | 1.0096
1478.7 | 49.5 | 1.0096
1478.8 | 49.5 | 1.0096
1478.9 | 49.5 | 1.0096
1479 | 49.5 | 1.0096
1479.1 | 49.5 | 1.0096
1479.2 | 49.5 | 1.0096
1479.3 | 49.5 | 1.0096
1479.4 | 49.5 | 1.0096
1479.5 | 49.5 | 1.0096
1479.6 | 49.5 | 1.0096
1479.7 | 49.5 | 1.0096
1479.8 | 49.5 | 1.0096
1479.9 | 49.5 | 1.0096
1480 | 49.5 | 1.0096
1480.1 | 49.5 | 1.0096
1480.2 | 49.5 | 1.0096
1480.3 | 49.5 | 1.0096
1480.4 | 49.5 | 1.0096
1480.5 | 49.5 | 1.0096
1480.6 | 49.5 | 1.0096
1480.7 | 49.5 | 1.0096
1480.8 | 49.5 | 1.0096
1480.9 | 49.5 | 1.0096
1481 | 49.5 | 1.0096
1481.1 | 49.5 | 1.0096
1481.2 | 49.5 | 1.0096
1481.3 | 49.5 | 1.0096
1481.4 | 49.5 | 1.0096
1481.5 | 49.5 | 1.0096
1481.6 | 49.5 | 1.0096
1481.7 | 49.5 | 1.0096
1481.8 | 49.5 | 1.0096
1481.9 | 49.5 | 1.0096
1482 | 49.5 | 1.0096
1482.1 | 49.5 | 1.0096
1482.2 | 49.5 | 1.0096
1482.3 | 49.5 | 1.0096
1482.4 | 49.5 | 1.0096
1482.5 | 49.5 | 1.0096
1482.6 | 49.5 | 1.0096
1482.7 | 49.5 | 1.0096
1482.8 | 49.5 | 1.0096
1482.9 | 49.5 | 1.0096
1483 | 49.5 | 1.0096
1483.1 | 49.5 | 1.0096
1483.2 | 49.5 | 1.0096
1483.3 | 49.5 | 1.0096
1483.4 | 49.5 | 1.0096
1483.5 | 49.5 | 1.0096
1483.6 | 49.5 | 1.0096
1483.7 | 49.5 | 1.0096
1483.8 | 49.5 | 1.0096
1483.9 | 49.5 | 1.0096
1484 | 49.5 | 1.0096
1484.1 | 49.5 | 1.0096
1484.2 | 49.5 | 1.0096
1484.3 | 49.5 | 1.0096
1484.4 | 49.5 | 1.0096
1484.5 | 49.5 | 1.0096
1484.6 | 49.5 | 1.0096
1484.7 | 49.5 | 1.0096
1484.8 | 49.5 | 1.0096
1484.9 | 49.5 | 1.0096
1485 | 49.5 | 1.0096
1485.1 | 49.5 | 1.0096
1485.2 | 49.5 | 1.0096
1485.3 | 49.5 | 1.0096
1485.4 | 49.5 | 1.0096
1485.5 | 49.5 | 1.0096
1485.6 | 49.5 | 1.0096
1485.7 | 49.5 | 1.0096
1485.8 | 49.5 | 1.0096
1485.9 | 49.5 | 1.0096
1486 | 49.5 | 1.0096
1486.1 | 49.5 | 1.0096
1486.2 | 49.5 | 1.0096
1486.3 | 49.5 | 1.0096
1486.4 | 49.5 | 1.0096
1486.5 | 49.5 | 1.0096
1486.6 | 49.5 | 1.0096
1486.7 | 49.5 | 1.0096
1486.8 | 49.5 | 1.0096
1486.9 | 49.5 | 1.0096
1487 | 49.5 | 1.0098
1487.1 | 49.5 | 1.0098
1487.2 | 49.5 | 1.0098
1487.3 | 49.5 | 1.0096
1487.4 | 49.5 | 1.0096
1487.5 | 49.5 | 1.0096
1487.6 | 49.5 | 1.0096
1487.7 | 49.5 | 1.0096
1487.8 | 49.5 | 1.0096
1487.9 | 49.5 | 1.0096
1488 | 49.5 | 1.0096
1488.1 | 49.5 | 1.0096
1488.2 | 49.5 | 1.0096
1488.3 | 49.5 | 1.0096
1488.4 | 49.5 | 1.0096
1488.5 | 49.5 | 1.0096
1488.6 | 49.5 | 1.0096
1488.7 | 49.5 | 1.0096
1488.8 | 49.5 | 1.0096
1488.9 | 49.5 | 1.0096
1489 | 49.5 | 1.0096
1489.1 | 49.5 | 1.0096
1489.2 | 49.5 | 1.0098
1489.3 | 49.5 | 1.0098
1489.4 | 49.5 | 1.0098
1489.5 | 49.5 | 1.0098
1489.6 | 49.5 | 1.0098
1489.7 | 49.5 | 1.0098
1489.8 | 49.5 | 1.0098
1489.9 | 49.5 | 1.0098
1490 | 49.5 | 1.0098
1490.1 | 49.5 | 1.0098
1490.2 | 49.5 | 1.0098
1490.3 | 49.5 | 1.0098
1490.4 | 49.5 | 1.0098
1490.5 | 49.5 | 1.0098
1490.6 | 49.5 | 1.0098
1490.7 | 49.5 | 1.0098
1490.8 | 49.5 | 1.0098
1490.9 | 49.5 | 1.0098
1491 | 49.5 | 1.0098
1491.1 | 49.5 | 1.0098
1491.2 | 49.5 | 1.0098
1491.3 | 49.5 | 1.0098
1491.4 | 49.5 | 1.0098
1491.5 | 49.5 | 1.0098
1491.6 | 49.5 | 1.0096
1491.7 | 49.5 | 1.0096
1491.8 | 49.5 | 1.0096
1491.9 | 49.5 | 1.0096
1492 | 49.5 | 1.0096
1492.1 | 49.5 | 1.0096
1492.2 | 49.5 | 1.0096
1492.3 | 49.5 | 1.0096
1492.4 | 49.5 | 1.0096
1492.5 | 49.5 | 1.0096
1492.6 | 49.5 | 1.0096
1492.7 | 49.5 | 1.0096
1492.8 | 49.5 | 1.0096
1492.9 | 49.5 | 1.0096
1493 | 49.5 | 1.0096
1493.1 | 49.5 | 1.0096
1493.2 | 49.5 | 1.0096
1493.3 | 49.5 | 1.0096
1493.4 | 49.5 | 1.0096
1493.5 | 49.5 | 1.0096
1493.6 | 49.5 | 1.0096
1493.7 | 49.5 | 1.0096
1493.8 | 49.5 | 1.0096
1493.9 | 49.5 | 1.0096
1494 | 49.5 | 1.0096
1494.1 | 49.5 | 1.0096
1494.2 | 49.5 | 1.0096
1494.3 | 49.5 | 1.0096
1494.4 | 49.5 | 1.0096
1494.5 | 49.5 | 1.0096
1494.6 | 49.5 | 1.0096
1494.7 | 49.5 | 1.0096
1494.8 | 49.5 | 1.0096
1494.9 | 49.5 | 1.0096
1495 | 49.5 | 1.0096
1495.1 | 49.5 | 1.0096
1495.2 | 49.5 | 1.0096
1495.3 | 49.5 | 1.0096
1495.4 | 49.5 | 1.0096
1495.5 | 49.5 | 1.0096
1495.6 | 49.5 | 1.0096
1495.7 | 49.5 | 1.0096
1495.8 | 49.5 | 1.0096
1495.9 | 49.5 | 1.0096
1496 | 49.5 | 1.0096
1496.1 | 49.5 | 1.0096
1496.2 | 49.5 | 1.0098
1496.3 | 49.5 | 1.0098
1496.4 | 49.5 | 1.0098
1496.5 | 49.5 | 1.0098
1496.6 | 49.5 | 1.0098
1496.7 | 49.5 | 1.0098
1496.8 | 49.5 | 1.0098
1496.9 | 49.5 | 1.0098
1497 | 49.5 | 1.0098
1497.1 | 49.5 | 1.0098
1497.2 | 49.5 | 1.0098
1497.3 | 49.5 | 1.0098
1497.4 | 49.5 | 1.0098
1497.5 | 49.5 | 1.0098
1497.6 | 49.5 | 1.0098
1497.7 | 49.5 | 1.0098
1497.8 | 49.5 | 1.0098
1497.9 | 49.5 | 1.0098
1498 | 49.5 | 1.0098
1498.1 | 49.5 | 1.0098
1498.2 | 49.5 | 1.0098
1498.3 | 49.5 | 1.0098
1498.4 | 49.5 | 1.0098
1498.5 | 49.5 | 1.0098
1498.6 | 49.5 | 1.0096
1498.7 | 49.5 | 1.0096
1498.8 | 49.5 | 1.0096
1498.9 | 49.5 | 1.0096
1499 | 49.5 | 1.0096
1499.1 | 49.5 | 1.0096
1499.2 | 49.5 | 1.0096
1499.3 | 49.5 | 1.0096
1499.4 | 49.5 | 1.0096
1499.5 | 49.5 | 1.0096
1499.6 | 49.5 | 1.0096
1499.7 | 49.5 | 1.0096
1499.8 | 49.5 | 1.0094
1499.9 | 49.5 | 1.0094
1500 | 49.5 | 1.0094
1500.1 | 49.5 | 1.0094
1500.2 | 49.5 | 1.0094
1500.3 | 49.5 | 1.0094
1500.4 | 49.5 | 1.0094
1500.5 | 49.5 | 1.0094
1500.6 | 49.5 | 1.0094
1500.7 | 49.5 | 1.0094
1500.8 | 49.5 | 1.0094
1500.9 | 49.5 | 1.0094
1501 | 49.5 | 1.0096
1501.1 | 49.5 | 1.0096
1501.2 | 49.5 | 1.0096
1501.3 | 49.5 | 1.0096
1501.4 | 49.5 | 1.0096
1501.5 | 49.5 | 1.0096
1501.6 | 49.5 | 1.0096
1501.7 | 49.5 | 1.0096
1501.8 | 49.5 | 1.0096
1501.9 | 49.5 | 1.0096
1502 | 49.5 | 1.0096
1502.1 | 49.5 | 1.0098
1502.2 | 49.5 | 1.0098
1502.3 | 49.5 | 1.0098
1502.4 | 49.5 | 1.0098
1502.5 | 49.5 | 1.0098
1502.6 | 49.5 | 1.0098
1502.7 | 49.5 | 1.0098
1502.8 | 49.5 | 1.0098
1502.9 | 49.5 | 1.0098
1503 | 49.5 | 1.0098
1503.1 | 49.5 | 1.0098
1503.2 | 49.5 | 1.0098
1503.3 | 49.5 | 1.0098
1503.4 | 49.5 | 1.0098
1503.5 | 49.5 | 1.0098
1503.6 | 49.5 | 1.0098
1503.7 | 49.5 | 1.0098
1503.8 | 49.5 | 1.0098
1503.9 | 49.5 | 1.0098
1504 | 49.5 | 1.0098
1504.1 | 49.5 | 1.0098
1504.2 | 49.5 | 1.0098
1504.3 | 49.5 | 1.0098
1504.4 | 49.5 | 1.0098
1504.5 | 49.5 | 1.0098
1504.6 | 49.5 | 1.0098
1504.7 | 49.5 | 1.0098
1504.8 | 49.5 | 1.0098
1504.9 | 49.5 | 1.0098
1505 | 49.5 | 1.0098
1505.1 | 49.5 | 1.0098
1505.2 | 49.5 | 1.0098
1505.3 | 49.5 | 1.0098
1505.4 | 49.5 | 1.0098
1505.5 | 49.5 | 1.0096
1505.6 | 49.5 | 1.0096
1505.7 | 49.5 | 1.0096
1505.8 | 49.5 | 1.0096
1505.9 | 49.5 | 1.0096
1506 | 49.5 | 1.0096
1506.1 | 49.5 | 1.0096
1506.2 | 49.5 | 1.0096
1506.3 | 49.5 | 1.0096
1506.4 | 49.5 | 1.0096
1506.5 | 49.5 | 1.0096
1506.6 | 49.5 | 1.0096
1506.7 | 49.5 | 1.0096
1506.8 | 49.5 | 1.0096
1506.9 | 49.5 | 1.0096
1507 | 49.5 | 1.0096
1507.1 | 49.5 | 1.0096
1507.2 | 49.5 | 1.0096
1507.3 | 49.5 | 1.0096
1507.4 | 49.5 | 1.0096
1507.5 | 49.5 | 1.0096
1507.6 | 49.5 | 1.0096
1507.7 | 49.5 | 1.0096
1507.8 | 49.5 | 1.0098
1507.9 | 49.5 | 1.0098
1508 | 49.5 | 1.0096
1508.1 | 49.5 | 1.0096
1508.2 | 49.5 | 1.0096
1508.3 | 49.5 | 1.0096
1508.4 | 49.5 | 1.0096
1508.5 | 49.5 | 1.0096
1508.6 | 49.5 | 1.0096
1508.7 | 49.5 | 1.0096
1508.8 | 49.5 | 1.0096
1508.9 | 49.5 | 1.0096
1509 | 49.5 | 1.0096
1509.1 | 49.5 | 1.0096
1509.2 | 49.5 | 1.0096
1509.3 | 49.5 | 1.0096
1509.4 | 49.5 | 1.0096
1509.5 | 49.5 | 1.0096
1509.6 | 49.5 | 1.0096
1509.7 | 49.5 | 1.0096
1509.8 | 49.5 | 1.0096
1509.9 | 49.5 | 1.0096
1510 | 49.5 | 1.0096
1510.1 | 49.5 | 1.0096
1510.2 | 49.5 | 1.0096
1510.3 | 49.5 | 1.0096
1510.4 | 49.5 | 1.0096
1510.5 | 49.5 | 1.0096
1510.6 | 49.5 | 1.0096
1510.7 | 49.5 | 1.0096
1510.8 | 49.5 | 1.0096
1510.9 | 49.5 | 1.0096
1511 | 49.5 | 1.0096
1511.1 | 49.5 | 1.0096
1511.2 | 49.5 | 1.0096
1511.3 | 49.5 | 1.0096
1511.4 | 49.5 | 1.0096
1511.5 | 49.5 | 1.0096
1511.6 | 49.5 | 1.0096
1511.7 | 49.5 | 1.0096
1511.8 | 49.5 | 1.0096
1511.9 | 49.5 | 1.0096
1512 | 49.5 | 1.0096
1512.1 | 49.5 | 1.0096
1512.2 | 49.5 | 1.0096
1512.3 | 49.5 | 1.0096
1512.4 | 49.5 | 1.0096
1512.5 | 49.5 | 1.0096
1512.6 | 49.5 | 1.0096
1512.7 | 49.5 | 1.0096
1512.8 | 49.5 | 1.0096
1512.9 | 49.5 | 1.0096
1513 | 49.5 | 1.0096
1513.1 | 49.5 | 1.0096
1513.2 | 49.5 | 1.0096
1513.3 | 49.5 | 1.0096
1513.4 | 49.5 | 1.0096
1513.5 | 49.5 | 1.0096
1513.6 | 49.5 | 1.0096
1513.7 | 49.5 | 1.0096
1513.8 | 49.5 | 1.0096
1513.9 | 49.5 | 1.0096
1514 | 49.5 | 1.0096
1514.1 | 49.5 | 1.0096
1514.2 | 49.5 | 1.0096
1514.3 | 49.5 | 1.0096
1514.4 | 49.5 | 1.0096
1514.5 | 49.5 | 1.0096
1514.6 | 49.5 | 1.0096
1514.7 | 49.5 | 1.0096
1514.8 | 49.5 | 1.0096
1514.9 | 49.5 | 1.0096
1515 | 49.5 | 1.0096
1515.1 | 49.5 | 1.0096
1515.2 | 49.5 | 1.0098
1515.3 | 49.5 | 1.0098
1515.4 | 49.5 | 1.0098
1515.5 | 49.5 | 1.0098
1515.6 | 49.5 | 1.0098
1515.7 | 49.5 | 1.0098
1515.8 | 49.5 | 1.0098
1515.9 | 49.5 | 1.0098
1516 | 49.5 | 1.0098
1516.1 | 49.5 | 1.0096
1516.2 | 49.5 | 1.0096
1516.3 | 49.5 | 1.0096
1516.4 | 49.5 | 1.0096
1516.5 | 49.5 | 1.0096
1516.6 | 49.5 | 1.0096
1516.7 | 49.5 | 1.0096
1516.8 | 49.5 | 1.0096
1516.9 | 49.5 | 1.0096
1517 | 49.5 | 1.0096
1517.1 | 49.5 | 1.0096
1517.2 | 49.5 | 1.0096
1517.3 | 49.5 | 1.0096
1517.4 | 49.5 | 1.0096
1517.5 | 49.5 | 1.0096
1517.6 | 49.5 | 1.0096
1517.7 | 49.5 | 1.0096
1517.8 | 49.5 | 1.0096
1517.9 | 49.5 | 1.0096
1518 | 49.5 | 1.0096
1518.1 | 49.5 | 1.0096
1518.2 | 49.5 | 1.0096
1518.3 | 49.5 | 1.0096
1518.4 | 49.5 | 1.0096
1518.5 | 49.5 | 1.0096
1518.6 | 49.5 | 1.0096
1518.7 | 49.5 | 1.0096
1518.8 | 49.5 | 1.0096
1518.9 | 49.5 | 1.0096
1519 | 49.5 | 1.0096
1519.1 | 49.5 | 1.0096
1519.2 | 49.5 | 1.0096
1519.3 | 49.5 | 1.0096
1519.4 | 49.5 | 1.0096
1519.5 | 49.5 | 1.0096
1519.6 | 49.5 | 1.0096
1519.7 | 49.5 | 1.0096
1519.8 | 49.5 | 1.0098
1519.9 | 49.5 | 1.0098
1520 | 49.5 | 1.0098
1520.1 | 49.5 | 1.0098
1520.2 | 49.5 | 1.0098
1520.3 | 49.5 | 1.0098
1520.4 | 49.5 | 1.0098
1520.5 | 49.5 | 1.0098
1520.6 | 49.5 | 1.0098
1520.7 | 49.5 | 1.0098
1520.8 | 49.5 | 1.0098
1520.9 | 49.5 | 1.0098
1521 | 49.5 | 1.0098
1521.1 | 49.5 | 1.0098
1521.2 | 49.5 | 1.0098
1521.3 | 49.5 | 1.0098
1521.4 | 49.5 | 1.0098
1521.5 | 49.5 | 1.0098
1521.6 | 49.5 | 1.0098
1521.7 | 49.5 | 1.0098
1521.8 | 49.5 | 1.0096
1521.9 | 49.5 | 1.0096
1522 | 49.5 | 1.0096
1522.1 | 49.5 | 1.0094
1522.2 | 49.5 | 1.0094
1522.3 | 49.5 | 1.0094
1522.4 | 49.5 | 1.0094
1522.5 | 49.5 | 1.0094
1522.6 | 49.5 | 1.0094
1522.7 | 49.5 | 1.0094
1522.8 | 49.5 | 1.0094
1522.9 | 49.5 | 1.0094
1523 | 49.5 | 1.0096
1523.1 | 49.5 | 1.0096
1523.2 | 49.5 | 1.0096
1523.3 | 49.5 | 1.0096
1523.4 | 49.5 | 1.0096
1523.5 | 49.5 | 1.0096
1523.6 | 49.5 | 1.0096
1523.7 | 49.5 | 1.0096
1523.8 | 49.5 | 1.0096
1523.9 | 49.5 | 1.0096
1524 | 49.5 | 1.0096
1524.1 | 49.5 | 1.0096
1524.2 | 49.5 | 1.0096
1524.3 | 49.5 | 1.0096
1524.4 | 49.5 | 1.0096
1524.5 | 49.5 | 1.0096
1524.6 | 49.5 | 1.0096
1524.7 | 49.5 | 1.0096
1524.8 | 49.5 | 1.0096
1524.9 | 49.5 | 1.0096
1525 | 49.5 | 1.0096
1525.1 | 49.5 | 1.0096
1525.2 | 49.5 | 1.0096
1525.3 | 49.5 | 1.0096
1525.4 | 49.5 | 1.0096
1525.5 | 49.5 | 1.0096
1525.6 | 49.5 | 1.0096
1525.7 | 49.5 | 1.0096
1525.8 | 49.5 | 1.0096
1525.9 | 49.5 | 1.0096
1526 | 49.5 | 1.0096
1526.1 | 49.5 | 1.0096
1526.2 | 49.5 | 1.0096
1526.3 | 49.5 | 1.0096
1526.4 | 49.5 | 1.0096
1526.5 | 49.5 | 1.0096
1526.6 | 49.5 | 1.0098
1526.7 | 49.5 | 1.0098
1526.8 | 49.5 | 1.0098
1526.9 | 49.5 | 1.0098
1527 | 49.5 | 1.0098
1527.1 | 49.5 | 1.0098
1527.2 | 49.5 | 1.0098
1527.3 | 49.5 | 1.0098
1527.4 | 49.5 | 1.0098
1527.5 | 49.5 | 1.0098
1527.6 | 49.5 | 1.0098
1527.7 | 49.5 | 1.0098
1527.8 | 49.5 | 1.0096
1527.9 | 49.5 | 1.0096
1528 | 49.5 | 1.0096
1528.1 | 49.5 | 1.0096
1528.2 | 49.5 | 1.0096
1528.3 | 49.5 | 1.0096
1528.4 | 49.5 | 1.0096
1528.5 | 49.5 | 1.0096
1528.6 | 49.5 | 1.0096
1528.7 | 49.5 | 1.0096
1528.8 | 49.5 | 1.0096
1528.9 | 49.5 | 1.0096
1529 | 49.5 | 1.0094
1529.1 | 49.5 | 1.0094
1529.2 | 49.5 | 1.0094
1529.3 | 49.5 | 1.0094
1529.4 | 49.5 | 1.0094
1529.5 | 49.5 | 1.0094
1529.6 | 49.5 | 1.0094
1529.7 | 49.5 | 1.0094
1529.8 | 49.5 | 1.0094
1529.9 | 49.5 | 1.0094
1530 | 49.5 | 1.0094
1530.1 | 49.5 | 1.0094
1530.2 | 49.5 | 1.0094
1530.3 | 49.5 | 1.0094
1530.4 | 49.5 | 1.0094
1530.5 | 49.5 | 1.0094
1530.6 | 49.5 | 1.0094
1530.7 | 49.5 | 1.0094
1530.8 | 49.5 | 1.0094
1530.9 | 49.5 | 1.0094
1531 | 49.5 | 1.0094
1531.1 | 49.5 | 1.0094
1531.2 | 49.5 | 1.0094
1531.3 | 49.5 | 1.0096
1531.4 | 49.5 | 1.0096
1531.5 | 49.5 | 1.0096
1531.6 | 49.5 | 1.0096
1531.7 | 49.5 | 1.0096
1531.8 | 49.5 | 1.0096
1531.9 | 49.5 | 1.0096
1532 | 49.5 | 1.0096
1532.1 | 49.5 | 1.0096
1532.2 | 49.5 | 1.0096
1532.3 | 49.5 | 1.0096
1532.4 | 49.5 | 1.0098
1532.5 | 49.5 | 1.0098
1532.6 | 49.5 | 1.0098
1532.7 | 49.5 | 1.0098
1532.8 | 49.5 | 1.0098
1532.9 | 49.5 | 1.0098
1533 | 49.5 | 1.0098
1533.1 | 49.5 | 1.0098
1533.2 | 49.5 | 1.0098
1533.3 | 49.5 | 1.0098
1533.4 | 49.5 | 1.0098
1533.5 | 49.5 | 1.0098
1533.6 | 49.5 | 1.0098
1533.7 | 49.5 | 1.0098
1533.8 | 49.5 | 1.0098
1533.9 | 49.5 | 1.0098
1534 | 49.5 | 1.0098
1534.1 | 49.5 | 1.0098
1534.2 | 49.5 | 1.0098
1534.3 | 49.5 | 1.0098
1534.4 | 49.5 | 1.0098
1534.5 | 49.5 | 1.0098
1534.6 | 49.5 | 1.0098
1534.7 | 49.5 | 1.0098
1534.8 | 49.5 | 1.0098
1534.9 | 49.5 | 1.0096
1535 | 49.5 | 1.0096
1535.1 | 49.5 | 1.0096
1535.2 | 49.5 | 1.0096
1535.3 | 49.5 | 1.0096
1535.4 | 49.5 | 1.0096
1535.5 | 49.5 | 1.0096
1535.6 | 49.5 | 1.0096
1535.7 | 49.5 | 1.0096
1535.8 | 49.5 | 1.0096
1535.9 | 49.5 | 1.0096
1536 | 49.5 | 1.0096
1536.1 | 49.5 | 1.0096
1536.2 | 49.5 | 1.0096
1536.3 | 49.5 | 1.0096
1536.4 | 49.5 | 1.0096
1536.5 | 49.5 | 1.0096
1536.6 | 49.5 | 1.0096
1536.7 | 49.5 | 1.0096
1536.8 | 49.5 | 1.0096
1536.9 | 49.5 | 1.0096
1537 | 49.5 | 1.0096
1537.1 | 49.5 | 1.0096
1537.2 | 49.5 | 1.0096
1537.3 | 49.5 | 1.0096
1537.4 | 49.5 | 1.0096
1537.5 | 49.5 | 1.0096
1537.6 | 49.5 | 1.0096
1537.7 | 49.5 | 1.0096
1537.8 | 49.5 | 1.0096
1537.9 | 49.5 | 1.0096
1538 | 49.5 | 1.0096
1538.1 | 49.5 | 1.0096
1538.2 | 49.5 | 1.0096
1538.3 | 49.5 | 1.0096
1538.4 | 49.5 | 1.0096
1538.5 | 49.5 | 1.0096
1538.6 | 49.5 | 1.0096
1538.7 | 49.5 | 1.0096
1538.8 | 49.5 | 1.0096
1538.9 | 49.5 | 1.0096
1539 | 49.5 | 1.0096
1539.1 | 49.5 | 1.0096
1539.2 | 49.5 | 1.0096
1539.3 | 49.5 | 1.0096
1539.4 | 49.5 | 1.0096
1539.5 | 49.5 | 1.0096
1539.6 | 49.5 | 1.0096
1539.7 | 49.5 | 1.0096
1539.8 | 49.5 | 1.0096
1539.9 | 49.5 | 1.0096
1540 | 49.5 | 1.0096
1540.1 | 49.5 | 1.0096
1540.2 | 49.5 | 1.0096
1540.3 | 49.5 | 1.0096
1540.4 | 49.5 | 1.0096
1540.5 | 49.5 | 1.0096
1540.6 | 49.5 | 1.0096
1540.7 | 49.5 | 1.0096
1540.8 | 49.5 | 1.0096
1540.9 | 49.5 | 1.0096
1541 | 49.5 | 1.0096
1541.1 | 49.5 | 1.0096
1541.2 | 49.5 | 1.0096
1541.3 | 49.5 | 1.0096
1541.4 | 49.5 | 1.0096
1541.5 | 49.5 | 1.0096
1541.6 | 49.5 | 1.0096
1541.7 | 49.5 | 1.0096
1541.8 | 49.5 | 1.0096
1541.9 | 49.5 | 1.0096
1542 | 49.5 | 1.0096
1542.1 | 49.5 | 1.0096
1542.2 | 49.5 | 1.0096
1542.3 | 49.5 | 1.0096
1542.4 | 49.5 | 1.0096
1542.5 | 49.5 | 1.0096
1542.6 | 49.5 | 1.0096
1542.7 | 49.5 | 1.0096
1542.8 | 49.5 | 1.0096
1542.9 | 49.5 | 1.0096
1543 | 49.5 | 1.0096
1543.1 | 49.5 | 1.0096
1543.2 | 49.5 | 1.0096
1543.3 | 49.5 | 1.0096
1543.4 | 49.5 | 1.0096
1543.5 | 49.5 | 1.0096
1543.6 | 49.5 | 1.0096
1543.7 | 49.5 | 1.0096
1543.8 | 49.5 | 1.0096
1543.9 | 49.5 | 1.0096
1544 | 49.5 | 1.0096
1544.1 | 49.5 | 1.0096
1544.2 | 49.5 | 1.0096
1544.3 | 49.5 | 1.0096
1544.4 | 49.5 | 1.0096
1544.5 | 49.5 | 1.0096
1544.6 | 49.5 | 1.0096
1544.7 | 49.5 | 1.0096
1544.8 | 49.5 | 1.0096
1544.9 | 49.5 | 1.0096
1545 | 49.5 | 1.0096
1545.1 | 49.5 | 1.0096
1545.2 | 49.5 | 1.0096
1545.3 | 49.5 | 1.0096
1545.4 | 49.5 | 1.0096
1545.5 | 49.5 | 1.0096
1545.6 | 49.5 | 1.0096
1545.7 | 49.5 | 1.0096
1545.8 | 49.5 | 1.0096
1545.9 | 49.5 | 1.0096
1546 | 49.5 | 1.0096
1546.1 | 49.5 | 1.0096
1546.2 | 49.5 | 1.0096
1546.3 | 49.5 | 1.0096
1546.4 | 49.5 | 1.0096
1546.5 | 49.5 | 1.0096
1546.6 | 49.5 | 1.0096
1546.7 | 49.5 | 1.0096
1546.8 | 49.5 | 1.0096
1546.9 | 49.5 | 1.0096
1547 | 49.5 | 1.0096
1547.1 | 49.5 | 1.0096
1547.2 | 49.5 | 1.0096
1547.3 | 49.5 | 1.0096
1547.4 | 49.5 | 1.0096
1547.5 | 49.5 | 1.0096
1547.6 | 49.5 | 1.0096
1547.7 | 49.5 | 1.0096
1547.8 | 49.5 | 1.0096
1547.9 | 49.5 | 1.0096
1548 | 49.5 | 1.0096
1548.1 | 49.5 | 1.0096
1548.2 | 49.5 | 1.0096
1548.3 | 49.5 | 1.0096
1548.4 | 49.5 | 1.0096
1548.5 | 49.5 | 1.0096
1548.6 | 49.5 | 1.0096
1548.7 | 49.5 | 1.0096
1548.8 | 49.5 | 1.0096
1548.9 | 49.5 | 1.0096
1549 | 49.5 | 1.0096
1549.1 | 49.5 | 1.0096
1549.2 | 49.5 | 1.0096
1549.3 | 49.5 | 1.0096
1549.4 | 49.5 | 1.0096
1549.5 | 49.5 | 1.0096
1549.6 | 49.5 | 1.0096
1549.7 | 49.5 | 1.0096
1549.8 | 49.5 | 1.0096
1549.9 | 49.5 | 1.0096
1550 | 49.5 | 1.0096
1550.1 | 49.5 | 1.0096
1550.2 | 49.5 | 1.0096
1550.3 | 49.5 | 1.0096
1550.4 | 49.5 | 1.0096
1550.5 | 49.5 | 1.0096
1550.6 | 49.5 | 1.0096
1550.7 | 49.5 | 1.0096
1550.8 | 49.5 | 1.0096
1550.9 | 49.5 | 1.0096
1551 | 49.5 | 1.0098
1551.1 | 49.5 | 1.0098
1551.2 | 49.5 | 1.0098
1551.3 | 49.5 | 1.0098
1551.4 | 49.5 | 1.0098
1551.5 | 49.5 | 1.0098
1551.6 | 49.5 | 1.0098
1551.7 | 49.5 | 1.0098
1551.8 | 49.5 | 1.0098
1551.9 | 49.5 | 1.0098
1552 | 49.5 | 1.0098
1552.1 | 49.5 | 1.0098
1552.2 | 49.5 | 1.0098
1552.3 | 49.5 | 1.0098
1552.4 | 49.5 | 1.0098
1552.5 | 49.5 | 1.0098
1552.6 | 49.5 | 1.0098
1552.7 | 49.5 | 1.0098
1552.8 | 49.5 | 1.0098
1552.9 | 49.5 | 1.0098
1553 | 49.5 | 1.0098
1553.1 | 49.5 | 1.0098
1553.2 | 49.5 | 1.0098
1553.3 | 49.5 | 1.0098
1553.4 | 49.5 | 1.0096
1553.5 | 49.5 | 1.0096
1553.6 | 49.5 | 1.0096
1553.7 | 49.5 | 1.0096
1553.8 | 49.5 | 1.0096
1553.9 | 49.5 | 1.0096
1554 | 49.5 | 1.0096
1554.1 | 49.5 | 1.0096
1554.2 | 49.5 | 1.0096
1554.3 | 49.5 | 1.0096
1554.4 | 49.5 | 1.0096
1554.5 | 49.5 | 1.0096
1554.6 | 49.5 | 1.0096
1554.7 | 49.5 | 1.0096
1554.8 | 49.5 | 1.0096
1554.9 | 49.5 | 1.0096
1555 | 49.5 | 1.0096
1555.1 | 49.5 | 1.0096
1555.2 | 49.5 | 1.0096
1555.3 | 49.5 | 1.0096
1555.4 | 49.5 | 1.0096
1555.5 | 49.5 | 1.0096
1555.6 | 49.5 | 1.0096
1555.7 | 49.5 | 1.0096
1555.8 | 49.5 | 1.0096
1555.9 | 49.5 | 1.0096
1556 | 49.5 | 1.0096
1556.1 | 49.5 | 1.0096
1556.2 | 49.5 | 1.0096
1556.3 | 49.5 | 1.0096
1556.4 | 49.5 | 1.0096
1556.5 | 49.5 | 1.0096
1556.6 | 49.5 | 1.0096
1556.7 | 49.5 | 1.0096
1556.8 | 49.5 | 1.0096
1556.9 | 49.5 | 1.0096
1557 | 49.5 | 1.0096
1557.1 | 49.5 | 1.0096
1557.2 | 49.5 | 1.0096
1557.3 | 49.5 | 1.0096
1557.4 | 49.5 | 1.0096
1557.5 | 49.5 | 1.0096
1557.6 | 49.5 | 1.0096
1557.7 | 49.5 | 1.0096
1557.8 | 49.5 | 1.0096
1557.9 | 49.5 | 1.0096
1558 | 49.5 | 1.0096
1558.1 | 49.5 | 1.0096
1558.2 | 49.5 | 1.0096
1558.3 | 49.5 | 1.0096
1558.4 | 49.5 | 1.0096
1558.5 | 49.5 | 1.0096
1558.6 | 49.5 | 1.0096
1558.7 | 49.5 | 1.0096
1558.8 | 49.5 | 1.0096
1558.9 | 49.5 | 1.0096
1559 | 49.5 | 1.0096
1559.1 | 49.5 | 1.0096
1559.2 | 49.5 | 1.0096
1559.3 | 49.5 | 1.0096
1559.4 | 49.5 | 1.0096
1559.5 | 49.5 | 1.0096
1559.6 | 49.5 | 1.0096
1559.7 | 49.5 | 1.0096
1559.8 | 49.5 | 1.0096
1559.9 | 49.5 | 1.0096
1560 | 49.5 | 1.0096
1560.1 | 49.5 | 1.0096
1560.2 | 49.5 | 1.0096
1560.3 | 49.5 | 1.0096
1560.4 | 49.5 | 1.0096
1560.5 | 49.5 | 1.0096
1560.6 | 49.5 | 1.0096
1560.7 | 49.5 | 1.0096
1560.8 | 49.5 | 1.0096
1560.9 | 49.5 | 1.0096
1561 | 49.5 | 1.0096
1561.1 | 49.5 | 1.0096
1561.2 | 49.5 | 1.0096
1561.3 | 49.5 | 1.0096
1561.4 | 49.5 | 1.0096
1561.5 | 49.5 | 1.0096
1561.6 | 49.5 | 1.0096
1561.7 | 49.5 | 1.0096
1561.8 | 49.5 | 1.0096
1561.9 | 49.5 | 1.0096
1562 | 49.5 | 1.0096
1562.1 | 49.5 | 1.0096
1562.2 | 49.5 | 1.0096
1562.3 | 49.5 | 1.0096
1562.4 | 49.5 | 1.0096
1562.5 | 49.5 | 1.0096
1562.6 | 49.5 | 1.0096
1562.7 | 49.5 | 1.0096
1562.8 | 49.5 | 1.0096
1562.9 | 49.5 | 1.0096
1563 | 49.5 | 1.0096
1563.1 | 49.5 | 1.0096
1563.2 | 49.5 | 1.0096
1563.3 | 49.5 | 1.0096
1563.4 | 49.5 | 1.0096
1563.5 | 49.5 | 1.0096
1563.6 | 49.5 | 1.0096
1563.7 | 49.5 | 1.0096
1563.8 | 49.5 | 1.0096
1563.9 | 49.5 | 1.0096
1564 | 49.5 | 1.0096
1564.1 | 49.5 | 1.0096
1564.2 | 49.5 | 1.0096
1564.3 | 49.5 | 1.0096
1564.4 | 49.5 | 1.0096
1564.5 | 49.5 | 1.0096
1564.6 | 49.5 | 1.0096
1564.7 | 49.5 | 1.0096
1564.8 | 49.5 | 1.0096
1564.9 | 49.5 | 1.0096
1565 | 49.5 | 1.0096
1565.1 | 49.5 | 1.0096
1565.2 | 49.5 | 1.0096
1565.3 | 49.5 | 1.0096
1565.4 | 49.5 | 1.0096
1565.5 | 49.5 | 1.0096
1565.6 | 49.5 | 1.0096
1565.7 | 49.5 | 1.0096
1565.8 | 49.5 | 1.0096
1565.9 | 49.5 | 1.0096
1566 | 49.5 | 1.0096
1566.1 | 49.5 | 1.0096
1566.2 | 49.5 | 1.0096
1566.3 | 49.5 | 1.0096
1566.4 | 49.5 | 1.0096
1566.5 | 49.5 | 1.0096
1566.6 | 49.5 | 1.0096
1566.7 | 49.5 | 1.0096
1566.8 | 49.5 | 1.0096
1566.9 | 49.5 | 1.0096
1567 | 49.5 | 1.0096
1567.1 | 49.5 | 1.0096
1567.2 | 49.5 | 1.0096
1567.3 | 49.5 | 1.0096
1567.4 | 49.5 | 1.0096
1567.5 | 49.5 | 1.0096
1567.6 | 49.5 | 1.0096
1567.7 | 49.5 | 1.0096
1567.8 | 49.5 | 1.0096
1567.9 | 49.5 | 1.0096
1568 | 49.5 | 1.0096
1568.1 | 49.5 | 1.0096
1568.2 | 49.5 | 1.0096
1568.3 | 49.5 | 1.0096
1568.4 | 49.5 | 1.0096
1568.5 | 49.5 | 1.0096
1568.6 | 49.5 | 1.0096
1568.7 | 49.5 | 1.0096
1568.8 | 49.5 | 1.0096
1568.9 | 49.5 | 1.0096
1569 | 49.5 | 1.0096
1569.1 | 49.5 | 1.0096
1569.2 | 49.5 | 1.0096
1569.3 | 49.5 | 1.0096
1569.4 | 49.5 | 1.0096
1569.5 | 49.5 | 1.0096
1569.6 | 49.5 | 1.0096
1569.7 | 49.5 | 1.0096
1569.8 | 49.5 | 1.0096
1569.9 | 49.5 | 1.0096
1570 | 49.5 | 1.0096
1570.1 | 49.5 | 1.0096
1570.2 | 49.5 | 1.0096
1570.3 | 49.5 | 1.0096
1570.4 | 49.5 | 1.0096
1570.5 | 49.5 | 1.0096
1570.6 | 49.5 | 1.0096
1570.7 | 49.5 | 1.0096
1570.8 | 49.5 | 1.0096
1570.9 | 49.5 | 1.0096
1571 | 49.5 | 1.0096
1571.1 | 49.5 | 1.0096
1571.2 | 49.5 | 1.0096
1571.3 | 49.5 | 1.0096
1571.4 | 49.5 | 1.0096
1571.5 | 49.5 | 1.0096
1571.6 | 49.5 | 1.0096
1571.7 | 49.5 | 1.0096
1571.8 | 49.5 | 1.0096
1571.9 | 49.5 | 1.0096
1572 | 49.5 | 1.0096
1572.1 | 49.5 | 1.0096
1572.2 | 49.5 | 1.0096
1572.3 | 49.5 | 1.0096
1572.4 | 49.5 | 1.0096
1572.5 | 49.5 | 1.0096
1572.6 | 49.5 | 1.0096
1572.7 | 49.5 | 1.0096
1572.8 | 49.5 | 1.0096
1572.9 | 49.5 | 1.0096
1573 | 49.5 | 1.0096
1573.1 | 49.5 | 1.0096
1573.2 | 49.5 | 1.0096
1573.3 | 49.5 | 1.0096
1573.4 | 49.5 | 1.0096
1573.5 | 49.5 | 1.0096
1573.6 | 49.5 | 1.0096
1573.7 | 49.5 | 1.0096
1573.8 | 49.5 | 1.0096
1573.9 | 49.5 | 1.0096
1574 | 49.5 | 1.0096
1574.1 | 49.5 | 1.0096
1574.2 | 49.5 | 1.0096
1574.3 | 49.5 | 1.0096
1574.4 | 49.5 | 1.0096
1574.5 | 49.5 | 1.0096
1574.6 | 49.5 | 1.0096
1574.7 | 49.5 | 1.0096
1574.8 | 49.5 | 1.0096
1574.9 | 49.5 | 1.0096
1575 | 49.5 | 1.0096
1575.1 | 49.5 | 1.0096
1575.2 | 49.5 | 1.0096
1575.3 | 49.5 | 1.0096
1575.4 | 49.5 | 1.0096
1575.5 | 49.5 | 1.0096
1575.6 | 49.5 | 1.0096
1575.7 | 49.5 | 1.0096
1575.8 | 49.5 | 1.0098
1575.9 | 49.5 | 1.0098
1576 | 49.5 | 1.0098
1576.1 | 49.5 | 1.0098
1576.2 | 49.5 | 1.0098
1576.3 | 49.5 | 1.0098
1576.4 | 49.5 | 1.0098
1576.5 | 49.5 | 1.0098
1576.6 | 49.5 | 1.0098
1576.7 | 49.5 | 1.0098
1576.8 | 49.5 | 1.0098
1576.9 | 49.5 | 1.0096
1577 | 49.5 | 1.0096
1577.1 | 49.5 | 1.0096
1577.2 | 49.5 | 1.0096
1577.3 | 49.5 | 1.0096
1577.4 | 49.5 | 1.0096
1577.5 | 49.5 | 1.0096
1577.6 | 49.5 | 1.0096
1577.7 | 49.5 | 1.0096
1577.8 | 49.5 | 1.0096
1577.9 | 49.5 | 1.0096
1578 | 49.5 | 1.0096
1578.1 | 49.5 | 1.0096
1578.2 | 49.5 | 1.0096
1578.3 | 49.5 | 1.0096
1578.4 | 49.5 | 1.0096
1578.5 | 49.5 | 1.0096
1578.6 | 49.5 | 1.0096
1578.7 | 49.5 | 1.0096
1578.8 | 49.5 | 1.0096
1578.9 | 49.5 | 1.0096
1579 | 49.5 | 1.0096
1579.1 | 49.5 | 1.0096
1579.2 | 49.5 | 1.0096
1579.3 | 49.5 | 1.0096
1579.4 | 49.5 | 1.0096
1579.5 | 49.5 | 1.0096
1579.6 | 49.5 | 1.0096
1579.7 | 49.5 | 1.0096
1579.8 | 49.5 | 1.0096
1579.9 | 49.5 | 1.0096
1580 | 49.5 | 1.0096
1580.1 | 49.5 | 1.0096
1580.2 | 49.5 | 1.0096
1580.3 | 49.5 | 1.0096
1580.4 | 49.5 | 1.0096
1580.5 | 49.5 | 1.0096
1580.6 | 49.5 | 1.0096
1580.7 | 49.5 | 1.0096
1580.8 | 49.5 | 1.0096
1580.9 | 49.5 | 1.0096
1581 | 49.5 | 1.0096
1581.1 | 49.5 | 1.0096
1581.2 | 49.5 | 1.0096
1581.3 | 49.5 | 1.0096
1581.4 | 49.5 | 1.0096
1581.5 | 49.5 | 1.0096
1581.6 | 49.5 | 1.0096
1581.7 | 49.5 | 1.0096
1581.8 | 49.5 | 1.0096
1581.9 | 49.5 | 1.0096
1582 | 49.5 | 1.0096
1582.1 | 49.5 | 1.0096
1582.2 | 49.5 | 1.0096
1582.3 | 49.5 | 1.0096
1582.4 | 49.5 | 1.0096
1582.5 | 49.5 | 1.0096
1582.6 | 49.5 | 1.0096
1582.7 | 49.5 | 1.0096
1582.8 | 49.5 | 1.0096
1582.9 | 49.5 | 1.0096
1583 | 49.5 | 1.0096
1583.1 | 49.5 | 1.0096
1583.2 | 49.5 | 1.0096
1583.3 | 49.5 | 1.0096
1583.4 | 49.5 | 1.0096
1583.5 | 49.5 | 1.0096
1583.6 | 49.5 | 1.0096
1583.7 | 49.5 | 1.0096
1583.8 | 49.5 | 1.0096
1583.9 | 49.5 | 1.0096
1584 | 49.5 | 1.0096
1584.1 | 49.5 | 1.0096
1584.2 | 49.5 | 1.0096
1584.3 | 49.5 | 1.0096
1584.4 | 49.5 | 1.0096
1584.5 | 49.5 | 1.0096
1584.6 | 49.5 | 1.0096
1584.7 | 49.5 | 1.0096
1584.8 | 49.5 | 1.0096
1584.9 | 49.5 | 1.0096
1585 | 49.5 | 1.0096
1585.1 | 49.5 | 1.0096
1585.2 | 49.5 | 1.0096
1585.3 | 49.5 | 1.0096
1585.4 | 49.5 | 1.0096
1585.5 | 49.5 | 1.0096
1585.6 | 49.5 | 1.0096
1585.7 | 49.5 | 1.0096
1585.8 | 49.5 | 1.0096
1585.9 | 49.5 | 1.0096
1586 | 49.5 | 1.0096
1586.1 | 49.5 | 1.0096
1586.2 | 49.5 | 1.0096
1586.3 | 49.5 | 1.0096
1586.4 | 49.5 | 1.0096
1586.5 | 49.5 | 1.0096
1586.6 | 49.5 | 1.0096
1586.7 | 49.5 | 1.0096
1586.8 | 49.5 | 1.0096
1586.9 | 49.5 | 1.0096
1587 | 49.5 | 1.0096
1587.1 | 49.5 | 1.0096
1587.2 | 49.5 | 1.0096
1587.3 | 49.5 | 1.0096
1587.4 | 49.5 | 1.0096
1587.5 | 49.5 | 1.0096
1587.6 | 49.5 | 1.0096
1587.7 | 49.5 | 1.0096
1587.8 | 49.5 | 1.0096
1587.9 | 49.5 | 1.0096
1588 | 49.5 | 1.0096
1588.1 | 49.5 | 1.0096
1588.2 | 49.5 | 1.0096
1588.3 | 49.5 | 1.0096
1588.4 | 49.5 | 1.0096
1588.5 | 49.5 | 1.0096
1588.6 | 49.5 | 1.0096
1588.7 | 49.5 | 1.0096
1588.8 | 49.5 | 1.0096
1588.9 | 49.5 | 1.0096
1589 | 49.5 | 1.0096
1589.1 | 49.5 | 1.0096
1589.2 | 49.5 | 1.0096
1589.3 | 49.5 | 1.0096
1589.4 | 49.5 | 1.0096
1589.5 | 49.5 | 1.0096
1589.6 | 49.5 | 1.0096
1589.7 | 49.5 | 1.0096
1589.8 | 49.5 | 1.0096
1589.9 | 49.5 | 1.0096
1590 | 49.5 | 1.0096
1590.1 | 49.5 | 1.0096
1590.2 | 49.5 | 1.0096
1590.3 | 49.5 | 1.0096
1590.4 | 49.5 | 1.0096
1590.5 | 49.5 | 1.0096
1590.6 | 49.5 | 1.0096
1590.7 | 49.5 | 1.0096
1590.8 | 49.5 | 1.0096
1590.9 | 49.5 | 1.0096
1591 | 49.5 | 1.0096
1591.1 | 49.5 | 1.0096
1591.2 | 49.5 | 1.0096
1591.3 | 49.5 | 1.0096
1591.4 | 49.5 | 1.0096
1591.5 | 49.5 | 1.0096
1591.6 | 49.5 | 1.0096
1591.7 | 49.5 | 1.0096
1591.8 | 49.5 | 1.0096
1591.9 | 49.5 | 1.0096
1592 | 49.5 | 1.0096
1592.1 | 49.5 | 1.0096
1592.2 | 49.5 | 1.0096
1592.3 | 49.5 | 1.0096
1592.4 | 49.5 | 1.0096
1592.5 | 49.5 | 1.0096
1592.6 | 49.5 | 1.0096
1592.7 | 49.5 | 1.0096
1592.8 | 49.5 | 1.0096
1592.9 | 49.5 | 1.0096
1593 | 49.5 | 1.0096
1593.1 | 49.5 | 1.0096
1593.2 | 49.5 | 1.0096
1593.3 | 49.5 | 1.0096
1593.4 | 49.5 | 1.0096
1593.5 | 49.5 | 1.0096
1593.6 | 49.5 | 1.0096
1593.7 | 49.5 | 1.0096
1593.8 | 49.5 | 1.0096
1593.9 | 49.5 | 1.0096
1594 | 49.5 | 1.0096
1594.1 | 49.5 | 1.0096
1594.2 | 49.5 | 1.0096
1594.3 | 49.5 | 1.0096
1594.4 | 49.5 | 1.0096
1594.5 | 49.5 | 1.0096
1594.6 | 49.5 | 1.0096
1594.7 | 49.5 | 1.0096
1594.8 | 49.5 | 1.0096
1594.9 | 49.5 | 1.0096
1595 | 49.5 | 1.0096
1595.1 | 49.5 | 1.0096
1595.2 | 49.5 | 1.0096
1595.3 | 49.5 | 1.0096
1595.4 | 49.5 | 1.0096
1595.5 | 49.5 | 1.0096
1595.6 | 49.5 | 1.0096
1595.7 | 49.5 | 1.0096
1595.8 | 49.5 | 1.0098
1595.9 | 49.5 | 1.0098
1596 | 49.5 | 1.0098
1596.1 | 49.5 | 1.0098
1596.2 | 49.5 | 1.0098
1596.3 | 49.5 | 1.0098
1596.4 | 49.5 | 1.0098
1596.5 | 49.5 | 1.0098
1596.6 | 49.5 | 1.0098
1596.7 | 49.5 | 1.0098
1596.8 | 49.5 | 1.0096
1596.9 | 49.5 | 1.0096
1597 | 49.5 | 1.0096
1597.1 | 49.5 | 1.0096
1597.2 | 49.5 | 1.0096
1597.3 | 49.5 | 1.0096
1597.4 | 49.5 | 1.0096
1597.5 | 49.5 | 1.0096
1597.6 | 49.5 | 1.0096
1597.7 | 49.5 | 1.0096
1597.8 | 49.5 | 1.0096
1597.9 | 49.5 | 1.0096
1598 | 49.5 | 1.0096
1598.1 | 49.5 | 1.0096
1598.2 | 49.5 | 1.0096
1598.3 | 49.5 | 1.0096
1598.4 | 49.5 | 1.0096
1598.5 | 49.5 | 1.0096
1598.6 | 49.5 | 1.0096
1598.7 | 49.5 | 1.0096
1598.8 | 49.5 | 1.0096
1598.9 | 49.5 | 1.0096
1599 | 49.5 | 1.0098
1599.1 | 49.5 | 1.0098
1599.2 | 49.5 | 1.0098
1599.3 | 49.5 | 1.0098
1599.4 | 49.5 | 1.0098
1599.5 | 49.5 | 1.0098
1599.6 | 49.5 | 1.0098
1599.7 | 49.5 | 1.0098
1599.8 | 49.5 | 1.0098
1599.9 | 49.5 | 1.0098
1600 | 49.5 | 1.0098
1600.1 | 49.5 | 1.0098
1600.2 | 49.5 | 1.0098
1600.3 | 49.5 | 1.0098
1600.4 | 49.5 | 1.0098
1600.5 | 49.5 | 1.0098
1600.6 | 49.5 | 1.0098
1600.7 | 49.5 | 1.0098
1600.8 | 49.5 | 1.0098
1600.9 | 49.5 | 1.0098
1601 | 49.5 | 1.0098
1601.1 | 49.5 | 1.0098
1601.2 | 49.5 | 1.0098
1601.3 | 49.5 | 1.0098
1601.4 | 49.5 | 1.0096
1601.5 | 49.5 | 1.0096
1601.6 | 49.5 | 1.0096
1601.7 | 49.5 | 1.0096
1601.8 | 49.5 | 1.0096
1601.9 | 49.5 | 1.0096
1602 | 49.5 | 1.0096
1602.1 | 49.5 | 1.0096
1602.2 | 49.5 | 1.0096
1602.3 | 49.5 | 1.0096
1602.4 | 49.5 | 1.0096
1602.5 | 49.5 | 1.0096
1602.6 | 49.5 | 1.0096
1602.7 | 49.5 | 1.0096
1602.8 | 49.5 | 1.0096
1602.9 | 49.5 | 1.0096
1603 | 49.5 | 1.0096
1603.1 | 49.5 | 1.0096
1603.2 | 49.5 | 1.0096
1603.3 | 49.5 | 1.0096
1603.4 | 49.5 | 1.0096
1603.5 | 49.5 | 1.0096
1603.6 | 49.5 | 1.0096
1603.7 | 49.5 | 1.0096
1603.8 | 49.5 | 1.0096
1603.9 | 49.5 | 1.0096
1604 | 49.5 | 1.0096
1604.1 | 49.5 | 1.0096
1604.2 | 49.5 | 1.0096
1604.3 | 49.5 | 1.0096
1604.4 | 49.5 | 1.0096
1604.5 | 49.5 | 1.0096
1604.6 | 49.5 | 1.0096
1604.7 | 49.5 | 1.0096
1604.8 | 49.5 | 1.0096
1604.9 | 49.5 | 1.0096
1605 | 49.5 | 1.0096
1605.1 | 49.5 | 1.0096
1605.2 | 49.5 | 1.0096
1605.3 | 49.5 | 1.0096
1605.4 | 49.5 | 1.0096
1605.5 | 49.5 | 1.0096
1605.6 | 49.5 | 1.0096
1605.7 | 49.5 | 1.0096
1605.8 | 49.5 | 1.0096
1605.9 | 49.5 | 1.0096
1606 | 49.5 | 1.0096
1606.1 | 49.5 | 1.0096
1606.2 | 49.5 | 1.0096
1606.3 | 49.5 | 1.0096
1606.4 | 49.5 | 1.0096
1606.5 | 49.5 | 1.0096
1606.6 | 49.5 | 1.0096
1606.7 | 49.5 | 1.0096
1606.8 | 49.5 | 1.0096
1606.9 | 49.5 | 1.0096
1607 | 49.5 | 1.0096
1607.1 | 49.5 | 1.0096
1607.2 | 49.5 | 1.0096
1607.3 | 49.5 | 1.0096
1607.4 | 49.5 | 1.0096
1607.5 | 49.5 | 1.0096
1607.6 | 49.5 | 1.0096
1607.7 | 49.5 | 1.0096
1607.8 | 49.5 | 1.0096
1607.9 | 49.5 | 1.0096
1608 | 49.5 | 1.0096
1608.1 | 49.5 | 1.0096
1608.2 | 49.5 | 1.0096
1608.3 | 49.5 | 1.0096
1608.4 | 49.5 | 1.0096
1608.5 | 49.5 | 1.0096
1608.6 | 49.5 | 1.0096
1608.7 | 49.5 | 1.0096
1608.8 | 49.5 | 1.0096
1608.9 | 49.5 | 1.0096
1609 | 49.5 | 1.0096
1609.1 | 49.5 | 1.0096
1609.2 | 49.5 | 1.0096
1609.3 | 49.5 | 1.0096
1609.4 | 49.5 | 1.0096
1609.5 | 49.5 | 1.0096
1609.6 | 49.5 | 1.0096
1609.7 | 49.5 | 1.0096
1609.8 | 49.5 | 1.0096
1609.9 | 49.5 | 1.0096
1610 | 49.5 | 1.0096
1610.1 | 49.5 | 1.0096
1610.2 | 49.5 | 1.0096
1610.3 | 49.5 | 1.0096
1610.4 | 49.5 | 1.0096
1610.5 | 49.5 | 1.0096
1610.6 | 49.5 | 1.0096
1610.7 | 49.5 | 1.0098
1610.8 | 49.5 | 1.0098
1610.9 | 49.5 | 1.0098
1611 | 49.5 | 1.0098
1611.1 | 49.5 | 1.0098
1611.2 | 49.5 | 1.0098
1611.3 | 49.5 | 1.0098
1611.4 | 49.5 | 1.0098
1611.5 | 49.5 | 1.0098
1611.6 | 49.5 | 1.0098
1611.7 | 49.5 | 1.0098
1611.8 | 49.5 | 1.0098
1611.9 | 49.5 | 1.0098
1612 | 49.5 | 1.0098
1612.1 | 49.5 | 1.0098
1612.2 | 49.5 | 1.0098
1612.3 | 49.5 | 1.0098
1612.4 | 49.5 | 1.0098
1612.5 | 49.5 | 1.0098
1612.6 | 49.5 | 1.0098
1612.7 | 49.5 | 1.0098
1612.8 | 49.5 | 1.0098
1612.9 | 49.5 | 1.0098
1613 | 49.5 | 1.0098
1613.1 | 49.5 | 1.0096
1613.2 | 49.5 | 1.0096
1613.3 | 49.5 | 1.0096
1613.4 | 49.5 | 1.0096
1613.5 | 49.5 | 1.0096
1613.6 | 49.5 | 1.0096
1613.7 | 49.5 | 1.0096
1613.8 | 49.5 | 1.0096
1613.9 | 49.5 | 1.0096
1614 | 49.5 | 1.0096
1614.1 | 49.5 | 1.0096
1614.2 | 49.5 | 1.0096
1614.3 | 49.5 | 1.0096
1614.4 | 49.5 | 1.0096
1614.5 | 49.5 | 1.0096
1614.6 | 49.5 | 1.0096
1614.7 | 49.5 | 1.0096
1614.8 | 49.5 | 1.0096
1614.9 | 49.5 | 1.0096
1615 | 49.5 | 1.0096
1615.1 | 49.5 | 1.0096
1615.2 | 49.5 | 1.0096
1615.3 | 49.5 | 1.0096
1615.4 | 49.5 | 1.0096
1615.5 | 49.5 | 1.0096
1615.6 | 49.5 | 1.0096
1615.7 | 49.5 | 1.0096
1615.8 | 49.5 | 1.0096
1615.9 | 49.5 | 1.0096
1616 | 49.5 | 1.0096
1616.1 | 49.5 | 1.0096
1616.2 | 49.5 | 1.0096
1616.3 | 49.5 | 1.0096
1616.4 | 49.5 | 1.0096
1616.5 | 49.5 | 1.0096
1616.6 | 49.5 | 1.0096
1616.7 | 49.5 | 1.0096
1616.8 | 49.5 | 1.0096
1616.9 | 49.5 | 1.0096
1617 | 49.5 | 1.0096
1617.1 | 49.5 | 1.0096
1617.2 | 49.5 | 1.0096
1617.3 | 49.5 | 1.0096
1617.4 | 49.5 | 1.0096
1617.5 | 49.5 | 1.0096
1617.6 | 49.5 | 1.0096
1617.7 | 49.5 | 1.0096
1617.8 | 49.5 | 1.0096
1617.9 | 49.5 | 1.0096
1618 | 49.5 | 1.0096
1618.1 | 49.5 | 1.0096
1618.2 | 49.5 | 1.0096
1618.3 | 49.5 | 1.0096
1618.4 | 49.5 | 1.0096
1618.5 | 49.5 | 1.0096
1618.6 | 49.5 | 1.0096
1618.7 | 49.5 | 1.0096
1618.8 | 49.5 | 1.0096
1618.9 | 49.5 | 1.0096
1619 | 49.5 | 1.0096
1619.1 | 49.5 | 1.0096
1619.2 | 49.5 | 1.0096
1619.3 | 49.5 | 1.0096
1619.4 | 49.5 | 1.0096
1619.5 | 49.5 | 1.0096
1619.6 | 49.5 | 1.0096
1619.7 | 49.5 | 1.0096
1619.8 | 49.5 | 1.0096
1619.9 | 49.5 | 1.0096
1620 | 49.5 | 1.0096
1620.1 | 49.5 | 1.0096
1620.2 | 49.5 | 1.0096
1620.3 | 49.5 | 1.0096
1620.4 | 49.5 | 1.0096
1620.5 | 49.5 | 1.0096
1620.6 | 49.5 | 1.0096
1620.7 | 49.5 | 1.0096
1620.8 | 49.5 | 1.0096
1620.9 | 49.5 | 1.0096
1621 | 49.5 | 1.0096
1621.1 | 49.5 | 1.0096
1621.2 | 49.5 | 1.0096
1621.3 | 49.5 | 1.0096
1621.4 | 49.5 | 1.0096
1621.5 | 49.5 | 1.0096
1621.6 | 49.5 | 1.0096
1621.7 | 49.5 | 1.0096
1621.8 | 49.5 | 1.0096
1621.9 | 49.5 | 1.0096
1622 | 49.5 | 1.0096
1622.1 | 49.5 | 1.0096
1622.2 | 49.5 | 1.0096
1622.3 | 49.5 | 1.0096
1622.4 | 49.5 | 1.0096
1622.5 | 49.5 | 1.0096
1622.6 | 49.5 | 1.0096
1622.7 | 49.5 | 1.0096
1622.8 | 49.5 | 1.0096
1622.9 | 49.5 | 1.0096
1623 | 49.5 | 1.0096
1623.1 | 49.5 | 1.0096
1623.2 | 49.5 | 1.0096
1623.3 | 49.5 | 1.0096
1623.4 | 49.5 | 1.0096
1623.5 | 49.5 | 1.0096
1623.6 | 49.5 | 1.0096
1623.7 | 49.5 | 1.0096
1623.8 | 49.5 | 1.0096
1623.9 | 49.5 | 1.0096
1624 | 49.5 | 1.0096
1624.1 | 49.5 | 1.0096
1624.2 | 49.5 | 1.0096
1624.3 | 49.5 | 1.0096
1624.4 | 49.5 | 1.0096
1624.5 | 49.5 | 1.0096
1624.6 | 49.5 | 1.0096
1624.7 | 49.5 | 1.0096
1624.8 | 49.5 | 1.0096
1624.9 | 49.5 | 1.0096
1625 | 49.5 | 1.0096
1625.1 | 49.5 | 1.0096
1625.2 | 49.5 | 1.0096
1625.3 | 49.5 | 1.0096
1625.4 | 49.5 | 1.0096
1625.5 | 49.5 | 1.0096
1625.6 | 49.5 | 1.0096
1625.7 | 49.5 | 1.0096
1625.8 | 49.5 | 1.0096
1625.9 | 49.5 | 1.0096
1626 | 49.5 | 1.0096
1626.1 | 49.5 | 1.0096
1626.2 | 49.5 | 1.0096
1626.3 | 49.5 | 1.0096
1626.4 | 49.5 | 1.0096
1626.5 | 49.5 | 1.0096
1626.6 | 49.5 | 1.0096
1626.7 | 49.5 | 1.0096
1626.8 | 49.5 | 1.0096
1626.9 | 49.5 | 1.0096
1627 | 49.5 | 1.0096
1627.1 | 49.5 | 1.0096
1627.2 | 49.5 | 1.0096
1627.3 | 49.5 | 1.0096
1627.4 | 49.5 | 1.0096
1627.5 | 49.5 | 1.0096
1627.6 | 49.5 | 1.0096
1627.7 | 49.5 | 1.0096
1627.8 | 49.5 | 1.0096
1627.9 | 49.5 | 1.0096
1628 | 49.5 | 1.0096
1628.1 | 49.5 | 1.0096
1628.2 | 49.5 | 1.0096
1628.3 | 49.5 | 1.0096
1628.4 | 49.5 | 1.0096
1628.5 | 49.5 | 1.0096
1628.6 | 49.5 | 1.0096
1628.7 | 49.5 | 1.0096
1628.8 | 49.5 | 1.0096
1628.9 | 49.5 | 1.0096
1629 | 49.5 | 1.0096
1629.1 | 49.5 | 1.0096
1629.2 | 49.5 | 1.0096
1629.3 | 49.5 | 1.0096
1629.4 | 49.5 | 1.0096
1629.5 | 49.5 | 1.0096
1629.6 | 49.5 | 1.0096
1629.7 | 49.5 | 1.0096
1629.8 | 49.5 | 1.0096
1629.9 | 49.5 | 1.0096
1630 | 49.5 | 1.0096
1630.1 | 49.5 | 1.0096
1630.2 | 49.5 | 1.0096
1630.3 | 49.5 | 1.0096
1630.4 | 49.5 | 1.0096
1630.5 | 49.5 | 1.0096
1630.6 | 49.5 | 1.0096
1630.7 | 49.5 | 1.0096
1630.8 | 49.5 | 1.0096
1630.9 | 49.5 | 1.0096
1631 | 49.5 | 1.0096
1631.1 | 49.5 | 1.0096
1631.2 | 49.5 | 1.0096
1631.3 | 49.5 | 1.0096
1631.4 | 49.5 | 1.0096
1631.5 | 49.5 | 1.0096
1631.6 | 49.5 | 1.0096
1631.7 | 49.5 | 1.0096
1631.8 | 49.5 | 1.0096
1631.9 | 49.5 | 1.0096
1632 | 49.5 | 1.0096
1632.1 | 49.5 | 1.0096
1632.2 | 49.5 | 1.0096
1632.3 | 49.5 | 1.0096
1632.4 | 49.5 | 1.0096
1632.5 | 49.5 | 1.0096
1632.6 | 49.5 | 1.0096
1632.7 | 49.5 | 1.0096
1632.8 | 49.5 | 1.0096
1632.9 | 49.5 | 1.0096
1633 | 49.5 | 1.0096
1633.1 | 49.5 | 1.0096
1633.2 | 49.5 | 1.0096
1633.3 | 49.5 | 1.0096
1633.4 | 49.5 | 1.0096
1633.5 | 49.5 | 1.0096
1633.6 | 49.5 | 1.0096
1633.7 | 49.5 | 1.0096
1633.8 | 49.5 | 1.0096
1633.9 | 49.5 | 1.0096
1634 | 49.5 | 1.0096
1634.1 | 49.5 | 1.0096
1634.2 | 49.5 | 1.0096
1634.3 | 49.5 | 1.0096
1634.4 | 49.5 | 1.0096
1634.5 | 49.5 | 1.0096
1634.6 | 49.5 | 1.0096
1634.7 | 49.5 | 1.0096
1634.8 | 49.5 | 1.0096
1634.9 | 49.5 | 1.0096
1635 | 49.5 | 1.0096
1635.1 | 49.5 | 1.0096
1635.2 | 49.5 | 1.0096
1635.3 | 49.5 | 1.0096
1635.4 | 49.5 | 1.0096
1635.5 | 49.5 | 1.0096
1635.6 | 49.5 | 1.0096
1635.7 | 49.5 | 1.0096
1635.8 | 49.5 | 1.0096
1635.9 | 49.5 | 1.0096
1636 | 49.5 | 1.0096
1636.1 | 49.5 | 1.0096
1636.2 | 49.5 | 1.0096
1636.3 | 49.5 | 1.0096
1636.4 | 49.5 | 1.0096
1636.5 | 49.5 | 1.0096
1636.6 | 49.5 | 1.0096
1636.7 | 49.5 | 1.0096
1636.8 | 49.5 | 1.0096
1636.9 | 49.5 | 1.0096
1637 | 49.5 | 1.0096
1637.1 | 49.5 | 1.0096
1637.2 | 49.5 | 1.0096
1637.3 | 49.5 | 1.0096
1637.4 | 49.5 | 1.0096
1637.5 | 49.5 | 1.0096
1637.6 | 49.5 | 1.0096
1637.7 | 49.5 | 1.0096
1637.8 | 49.5 | 1.0096
1637.9 | 49.5 | 1.0096
1638 | 49.5 | 1.0096
1638.1 | 49.5 | 1.0096
1638.2 | 49.5 | 1.0096
1638.3 | 49.5 | 1.0096
1638.4 | 49.5 | 1.0096
1638.5 | 49.5 | 1.0096
1638.6 | 49.5 | 1.0096
1638.7 | 49.5 | 1.0096
1638.8 | 49.5 | 1.0096
1638.9 | 49.5 | 1.0096
1639 | 49.5 | 1.0096
1639.1 | 49.5 | 1.0096
1639.2 | 49.5 | 1.0096
1639.3 | 49.5 | 1.0096
1639.4 | 49.5 | 1.0096
1639.5 | 49.5 | 1.0096
1639.6 | 49.5 | 1.0096
1639.7 | 49.5 | 1.0096
1639.8 | 49.5 | 1.0096
1639.9 | 49.5 | 1.0096
1640 | 49.5 | 1.0096
1640.1 | 49.5 | 1.0096
1640.2 | 49.5 | 1.0096
1640.3 | 49.5 | 1.0096
1640.4 | 49.5 | 1.0096
1640.5 | 49.5 | 1.0096
1640.6 | 49.5 | 1.0096
1640.7 | 49.5 | 1.0096
1640.8 | 49.5 | 1.0096
1640.9 | 49.5 | 1.0096
1641 | 49.5 | 1.0096
1641.1 | 49.5 | 1.0096
1641.2 | 49.5 | 1.0096
1641.3 | 49.5 | 1.0096
1641.4 | 49.5 | 1.0098
1641.5 | 49.5 | 1.0098
1641.6 | 49.5 | 1.0098
1641.7 | 49.5 | 1.0098
1641.8 | 49.5 | 1.0098
1641.9 | 49.5 | 1.0098
1642 | 49.5 | 1.0098
1642.1 | 49.5 | 1.0098
1642.2 | 49.5 | 1.0098
1642.3 | 49.5 | 1.0098
1642.4 | 49.5 | 1.0098
1642.5 | 49.5 | 1.0098
1642.6 | 49.5 | 1.0096
1642.7 | 49.5 | 1.0096
1642.8 | 49.5 | 1.0096
1642.9 | 49.5 | 1.0096
1643 | 49.5 | 1.0096
1643.1 | 49.5 | 1.0096
1643.2 | 49.5 | 1.0096
1643.3 | 49.5 | 1.0096
1643.4 | 49.5 | 1.0096
1643.5 | 49.5 | 1.0096
1643.6 | 49.5 | 1.0096
1643.7 | 49.5 | 1.0096
1643.8 | 49.5 | 1.0096
1643.9 | 49.5 | 1.0096
1644 | 49.5 | 1.0096
1644.1 | 49.5 | 1.0096
1644.2 | 49.5 | 1.0096
1644.3 | 49.5 | 1.0096
1644.4 | 49.5 | 1.0096
1644.5 | 49.5 | 1.0096
1644.6 | 49.5 | 1.0096
1644.7 | 49.5 | 1.0096
1644.8 | 49.5 | 1.0096
1644.9 | 49.5 | 1.0096
1645 | 49.5 | 1.0096
1645.1 | 49.5 | 1.0096
1645.2 | 49.5 | 1.0096
1645.3 | 49.5 | 1.0096
1645.4 | 49.5 | 1.0096
1645.5 | 49.5 | 1.0096
1645.6 | 49.5 | 1.0096
1645.7 | 49.5 | 1.0096
1645.8 | 49.5 | 1.0096
1645.9 | 49.5 | 1.0096
1646 | 49.5 | 1.0096
1646.1 | 49.5 | 1.0096
1646.2 | 49.5 | 1.0096
1646.3 | 49.5 | 1.0096
1646.4 | 49.5 | 1.0096
1646.5 | 49.5 | 1.0096
1646.6 | 49.5 | 1.0096
1646.7 | 49.5 | 1.0096
1646.8 | 49.5 | 1.0096
1646.9 | 49.5 | 1.0096
1647 | 49.5 | 1.0096
1647.1 | 49.5 | 1.0096
1647.2 | 49.5 | 1.0096
1647.3 | 49.5 | 1.0096
1647.4 | 49.5 | 1.0096
1647.5 | 49.5 | 1.0096
1647.6 | 49.5 | 1.0096
1647.7 | 49.5 | 1.0096
1647.8 | 49.5 | 1.0096
1647.9 | 49.5 | 1.0096
1648 | 49.5 | 1.0096
1648.1 | 49.5 | 1.0096
1648.2 | 49.5 | 1.0096
1648.3 | 49.5 | 1.0096
1648.4 | 49.5 | 1.0096
1648.5 | 49.5 | 1.0096
1648.6 | 49.5 | 1.0096
1648.7 | 49.5 | 1.0096
1648.8 | 49.5 | 1.0096
1648.9 | 49.5 | 1.0096
1649 | 49.5 | 1.0096
1649.1 | 49.5 | 1.0096
1649.2 | 49.5 | 1.0096
1649.3 | 49.5 | 1.0096
1649.4 | 49.5 | 1.0096
1649.5 | 49.5 | 1.0096
1649.6 | 49.5 | 1.0096
1649.7 | 49.5 | 1.0096
1649.8 | 49.5 | 1.0096
1649.9 | 49.5 | 1.0096
1650 | 49.5 | 1.0096
1650.1 | 49.5 | 1.0096
1650.2 | 49.5 | 1.0096
1650.3 | 49.5 | 1.0096
1650.4 | 49.5 | 1.0096
1650.5 | 49.5 | 1.0096
1650.6 | 49.5 | 1.0096
1650.7 | 49.5 | 1.0096
1650.8 | 49.5 | 1.0096
1650.9 | 49.5 | 1.0096
1651 | 49.5 | 1.0096
1651.1 | 49.5 | 1.0096
1651.2 | 49.5 | 1.0096
1651.3 | 49.5 | 1.0096
1651.4 | 49.5 | 1.0096
1651.5 | 49.5 | 1.0096
1651.6 | 49.5 | 1.0096
1651.7 | 49.5 | 1.0094
1651.8 | 49.5 | 1.0094
1651.9 | 49.5 | 1.0094
1652 | 49.5 | 1.0094
1652.1 | 49.5 | 1.0094
1652.2 | 49.5 | 1.0096
1652.3 | 49.5 | 1.0096
1652.4 | 49.5 | 1.0096
1652.5 | 49.5 | 1.0096
1652.6 | 49.5 | 1.0096
1652.7 | 49.5 | 1.0096
1652.8 | 49.5 | 1.0096
1652.9 | 49.5 | 1.0096
1653 | 49.5 | 1.0096
1653.1 | 49.5 | 1.0096
1653.2 | 49.5 | 1.0096
1653.3 | 49.5 | 1.0096
1653.4 | 49.5 | 1.0096
1653.5 | 49.5 | 1.0096
1653.6 | 49.5 | 1.0096
1653.7 | 49.5 | 1.0096
1653.8 | 49.5 | 1.0096
1653.9 | 49.5 | 1.0096
1654 | 49.5 | 1.0096
1654.1 | 49.5 | 1.0096
1654.2 | 49.5 | 1.0096
1654.3 | 49.5 | 1.0096
1654.4 | 49.5 | 1.0096
1654.5 | 49.5 | 1.0096
1654.6 | 49.5 | 1.0096
1654.7 | 49.5 | 1.0096
1654.8 | 49.5 | 1.0096
1654.9 | 49.5 | 1.0096
1655 | 49.5 | 1.0096
1655.1 | 49.5 | 1.0096
1655.2 | 49.5 | 1.0096
1655.3 | 49.5 | 1.0096
1655.4 | 49.5 | 1.0098
1655.5 | 49.5 | 1.0098
1655.6 | 49.5 | 1.0098
1655.7 | 49.5 | 1.0098
1655.8 | 49.5 | 1.0098
1655.9 | 49.5 | 1.0098
1656 | 49.5 | 1.0098
1656.1 | 49.5 | 1.0098
1656.2 | 49.5 | 1.0098
1656.3 | 49.5 | 1.0098
1656.4 | 49.5 | 1.0096
1656.5 | 49.5 | 1.0096
1656.6 | 49.5 | 1.0096
1656.7 | 49.5 | 1.0096
1656.8 | 49.5 | 1.0096
1656.9 | 49.5 | 1.0096
1657 | 49.5 | 1.0096
1657.1 | 49.5 | 1.0096
1657.2 | 49.5 | 1.0096
1657.3 | 49.5 | 1.0096
1657.4 | 49.5 | 1.0096
1657.5 | 49.5 | 1.0096
1657.6 | 49.5 | 1.0096
1657.7 | 49.5 | 1.0096
1657.8 | 49.5 | 1.0096
1657.9 | 49.5 | 1.0096
1658 | 49.5 | 1.0096
1658.1 | 49.5 | 1.0096
1658.2 | 49.5 | 1.0096
1658.3 | 49.5 | 1.0096
1658.4 | 49.5 | 1.0096
1658.5 | 49.5 | 1.0096
1658.6 | 49.5 | 1.0096
1658.7 | 49.5 | 1.0096
1658.8 | 49.5 | 1.0096
1658.9 | 49.5 | 1.0096
1659 | 49.5 | 1.0096
1659.1 | 49.5 | 1.0096
1659.2 | 49.5 | 1.0096
1659.3 | 49.5 | 1.0096
1659.4 | 49.5 | 1.0096
1659.5 | 49.5 | 1.0096
1659.6 | 49.5 | 1.0096
1659.7 | 49.5 | 1.0096
1659.8 | 49.5 | 1.0096
1659.9 | 49.5 | 1.0096
1660 | 49.5 | 1.0096
1660.1 | 49.5 | 1.0096
1660.2 | 49.5 | 1.0096
1660.3 | 49.5 | 1.0096
1660.4 | 49.5 | 1.0096
1660.5 | 49.5 | 1.0096
1660.6 | 49.5 | 1.0096
1660.7 | 49.5 | 1.0096
1660.8 | 49.5 | 1.0096
1660.9 | 49.5 | 1.0096
1661 | 49.5 | 1.0096
1661.1 | 49.5 | 1.0096
1661.2 | 49.5 | 1.0096
1661.3 | 49.5 | 1.0096
1661.4 | 49.5 | 1.0096
1661.5 | 49.5 | 1.0096
1661.6 | 49.5 | 1.0096
1661.7 | 49.5 | 1.0096
1661.8 | 49.5 | 1.0096
1661.9 | 49.5 | 1.0096
1662 | 49.5 | 1.0096
1662.1 | 49.5 | 1.0096
1662.2 | 49.5 | 1.0096
1662.3 | 49.5 | 1.0096
1662.4 | 49.5 | 1.0096
1662.5 | 49.5 | 1.0096
1662.6 | 49.5 | 1.0096
1662.7 | 49.5 | 1.0096
1662.8 | 49.5 | 1.0096
1662.9 | 49.5 | 1.0096
1663 | 49.5 | 1.0096
1663.1 | 49.5 | 1.0096
1663.2 | 49.5 | 1.0096
1663.3 | 49.5 | 1.0096
1663.4 | 49.5 | 1.0096
1663.5 | 49.5 | 1.0096
1663.6 | 49.5 | 1.0096
1663.7 | 49.5 | 1.0096
1663.8 | 49.5 | 1.0096
1663.9 | 49.5 | 1.0096
1664 | 49.5 | 1.0096
1664.1 | 49.5 | 1.0096
1664.2 | 49.5 | 1.0096
1664.3 | 49.5 | 1.0096
1664.4 | 49.5 | 1.0096
1664.5 | 49.5 | 1.0096
1664.6 | 49.5 | 1.0098
1664.7 | 49.5 | 1.0098
1664.8 | 49.5 | 1.0098
1664.9 | 49.5 | 1.0098
1665 | 49.5 | 1.0098
1665.1 | 49.5 | 1.0098
1665.2 | 49.5 | 1.0098
1665.3 | 49.5 | 1.0098
1665.4 | 49.5 | 1.0098
1665.5 | 49.5 | 1.0098
1665.6 | 49.5 | 1.0098
1665.7 | 49.5 | 1.0098
1665.8 | 49.5 | 1.0098
1665.9 | 49.5 | 1.0098
1666 | 49.5 | 1.0098
1666.1 | 49.5 | 1.0098
1666.2 | 49.5 | 1.0098
1666.3 | 49.5 | 1.0098
1666.4 | 49.5 | 1.0098
1666.5 | 49.5 | 1.0098
1666.6 | 49.5 | 1.0098
1666.7 | 49.5 | 1.0098
1666.8 | 49.5 | 1.0098
1666.9 | 49.5 | 1.0098
1667 | 49.5 | 1.0098
1667.1 | 49.5 | 1.0098
1667.2 | 49.5 | 1.0098
1667.3 | 49.5 | 1.0098
1667.4 | 49.5 | 1.0098
1667.5 | 49.5 | 1.0098
1667.6 | 49.5 | 1.0098
1667.7 | 49.5 | 1.0098
1667.8 | 49.5 | 1.0098
1667.9 | 49.5 | 1.0098
1668 | 49.5 | 1.0098
1668.1 | 49.5 | 1.0098
1668.2 | 49.5 | 1.0096
1668.3 | 49.5 | 1.0096
1668.4 | 49.5 | 1.0096
1668.5 | 49.5 | 1.0096
1668.6 | 49.5 | 1.0096
1668.7 | 49.5 | 1.0096
1668.8 | 49.5 | 1.0096
1668.9 | 49.5 | 1.0096
1669 | 49.5 | 1.0096
1669.1 | 49.5 | 1.0096
1669.2 | 49.5 | 1.0096
1669.3 | 49.5 | 1.0096
1669.4 | 49.5 | 1.0096
1669.5 | 49.5 | 1.0096
1669.6 | 49.5 | 1.0096
1669.7 | 49.5 | 1.0096
1669.8 | 49.5 | 1.0096
1669.9 | 49.5 | 1.0096
1670 | 49.5 | 1.0096
1670.1 | 49.5 | 1.0096
1670.2 | 49.5 | 1.0096
1670.3 | 49.5 | 1.0096
1670.4 | 49.5 | 1.0096
1670.5 | 49.5 | 1.0096
1670.6 | 49.5 | 1.0096
1670.7 | 49.5 | 1.0096
1670.8 | 49.5 | 1.0096
1670.9 | 49.5 | 1.0096
1671 | 49.5 | 1.0096
1671.1 | 49.5 | 1.0096
1671.2 | 49.5 | 1.0096
1671.3 | 49.5 | 1.0096
1671.4 | 49.5 | 1.0096
1671.5 | 49.5 | 1.0096
1671.6 | 49.5 | 1.0096
1671.7 | 49.5 | 1.0096
1671.8 | 49.5 | 1.0096
1671.9 | 49.5 | 1.0096
1672 | 49.5 | 1.0096
1672.1 | 49.5 | 1.0096
1672.2 | 49.5 | 1.0096
1672.3 | 49.5 | 1.0096
1672.4 | 49.5 | 1.0096
1672.5 | 49.5 | 1.0096
1672.6 | 49.5 | 1.0096
1672.7 | 49.5 | 1.0096
1672.8 | 49.5 | 1.0096
1672.9 | 49.5 | 1.0096
1673 | 49.5 | 1.0096
1673.1 | 49.5 | 1.0096
1673.2 | 49.5 | 1.0096
1673.3 | 49.5 | 1.0096
1673.4 | 49.5 | 1.0096
1673.5 | 49.5 | 1.0096
1673.6 | 49.5 | 1.0096
1673.7 | 49.5 | 1.0096
1673.8 | 49.5 | 1.0096
1673.9 | 49.5 | 1.0096
1674 | 49.5 | 1.0096
1674.1 | 49.5 | 1.0096
1674.2 | 49.5 | 1.0096
1674.3 | 49.5 | 1.0096
1674.4 | 49.5 | 1.0096
1674.5 | 49.5 | 1.0096
1674.6 | 49.5 | 1.0096
1674.7 | 49.5 | 1.0096
1674.8 | 49.5 | 1.0096
1674.9 | 49.5 | 1.0096
1675 | 49.5 | 1.0096
1675.1 | 49.5 | 1.0096
1675.2 | 49.5 | 1.0096
1675.3 | 49.5 | 1.0096
1675.4 | 49.5 | 1.0096
1675.5 | 49.5 | 1.0096
1675.6 | 49.5 | 1.0096
1675.7 | 49.5 | 1.0096
1675.8 | 49.5 | 1.0096
1675.9 | 49.5 | 1.0096
1676 | 49.5 | 1.0096
1676.1 | 49.5 | 1.0096
1676.2 | 49.5 | 1.0096
1676.3 | 49.5 | 1.0096
1676.4 | 49.5 | 1.0096
1676.5 | 49.5 | 1.0096
1676.6 | 49.5 | 1.0096
1676.7 | 49.5 | 1.0096
1676.8 | 49.5 | 1.0096
1676.9 | 49.5 | 1.0096
1677 | 49.5 | 1.0096
1677.1 | 49.5 | 1.0096
1677.2 | 49.5 | 1.0096
1677.3 | 49.5 | 1.0096
1677.4 | 49.5 | 1.0096
1677.5 | 49.5 | 1.0096
1677.6 | 49.5 | 1.0096
1677.7 | 49.5 | 1.0096
1677.8 | 49.5 | 1.0096
1677.9 | 49.5 | 1.0096
1678 | 49.5 | 1.0096
1678.1 | 49.5 | 1.0096
1678.2 | 49.5 | 1.0096
1678.3 | 49.5 | 1.0096
1678.4 | 49.5 | 1.0096
1678.5 | 49.5 | 1.0096
1678.6 | 49.5 | 1.0096
1678.7 | 49.5 | 1.0096
1678.8 | 49.5 | 1.0096
1678.9 | 49.5 | 1.0096
1679 | 49.5 | 1.0096
1679.1 | 49.5 | 1.0096
1679.2 | 49.5 | 1.0096
1679.3 | 49.5 | 1.0096
1679.4 | 49.5 | 1.0096
1679.5 | 49.5 | 1.0096
1679.6 | 49.5 | 1.0096
1679.7 | 49.5 | 1.0096
1679.8 | 49.5 | 1.0096
1679.9 | 49.5 | 1.0096
1680 | 49.5 | 1.0096
1680.1 | 49.5 | 1.0096
1680.2 | 49.5 | 1.0096
1680.3 | 49.5 | 1.0096
1680.4 | 49.5 | 1.0096
1680.5 | 49.5 | 1.0096
1680.6 | 49.5 | 1.0096
1680.7 | 49.5 | 1.0096
1680.8 | 49.5 | 1.0096
1680.9 | 49.5 | 1.0096
1681 | 49.5 | 1.0096
1681.1 | 49.5 | 1.0096
1681.2 | 49.5 | 1.0096
1681.3 | 49.5 | 1.0096
1681.4 | 49.5 | 1.0096
1681.5 | 49.5 | 1.0096
1681.6 | 49.5 | 1.0096
1681.7 | 49.5 | 1.0096
1681.8 | 49.5 | 1.0096
1681.9 | 49.5 | 1.0096
1682 | 49.5 | 1.0096
1682.1 | 49.5 | 1.0096
1682.2 | 49.5 | 1.0096
1682.3 | 49.5 | 1.0096
1682.4 | 49.5 | 1.0096
1682.5 | 49.5 | 1.0096
1682.6 | 49.5 | 1.0096
1682.7 | 49.5 | 1.0096
1682.8 | 49.5 | 1.0096
1682.9 | 49.5 | 1.0096
1683 | 49.5 | 1.0096
1683.1 | 49.5 | 1.0096
1683.2 | 49.5 | 1.0096
1683.3 | 49.5 | 1.0096
1683.4 | 49.5 | 1.0096
1683.5 | 49.5 | 1.0096
1683.6 | 49.5 | 1.0096
1683.7 | 49.5 | 1.0096
1683.8 | 49.5 | 1.0096
1683.9 | 49.5 | 1.0096
1684 | 49.5 | 1.0096
1684.1 | 49.5 | 1.0096
1684.2 | 49.5 | 1.0096
1684.3 | 49.5 | 1.0096
1684.4 | 49.5 | 1.0096
1684.5 | 49.5 | 1.0096
1684.6 | 49.5 | 1.0096
1684.7 | 49.5 | 1.0096
1684.8 | 49.5 | 1.0096
1684.9 | 49.5 | 1.0096
1685 | 49.5 | 1.0096
1685.1 | 49.5 | 1.0096
1685.2 | 49.5 | 1.0096
1685.3 | 49.5 | 1.0096
1685.4 | 49.5 | 1.0096
1685.5 | 49.5 | 1.0096
1685.6 | 49.5 | 1.0096
1685.7 | 49.5 | 1.0096
1685.8 | 49.5 | 1.0096
1685.9 | 49.5 | 1.0096
1686 | 49.5 | 1.0096
1686.1 | 49.5 | 1.0096
1686.2 | 49.5 | 1.0096
1686.3 | 49.5 | 1.0096
1686.4 | 49.5 | 1.0096
1686.5 | 49.5 | 1.0096
1686.6 | 49.5 | 1.0096
1686.7 | 49.5 | 1.0096
1686.8 | 49.5 | 1.0096
1686.9 | 49.5 | 1.0096
1687 | 49.5 | 1.0096
1687.1 | 49.5 | 1.0096
1687.2 | 49.5 | 1.0096
1687.3 | 49.5 | 1.0096
1687.4 | 49.5 | 1.0096
1687.5 | 49.5 | 1.0096
1687.6 | 49.5 | 1.0096
1687.7 | 49.5 | 1.0096
1687.8 | 49.5 | 1.0096
1687.9 | 49.5 | 1.0096
1688 | 49.5 | 1.0096
1688.1 | 49.5 | 1.0096
1688.2 | 49.5 | 1.0096
1688.3 | 49.5 | 1.0096
1688.4 | 49.5 | 1.0096
1688.5 | 49.5 | 1.0096
1688.6 | 49.5 | 1.0096
1688.7 | 49.5 | 1.0096
1688.8 | 49.5 | 1.0096
1688.9 | 49.5 | 1.0096
1689 | 49.5 | 1.0096
1689.1 | 49.5 | 1.0096
1689.2 | 49.5 | 1.0096
1689.3 | 49.5 | 1.0096
1689.4 | 49.5 | 1.0096
1689.5 | 49.5 | 1.0096
1689.6 | 49.5 | 1.0096
1689.7 | 49.5 | 1.0096
1689.8 | 49.5 | 1.0096
1689.9 | 49.5 | 1.0096
1690 | 49.5 | 1.0096
1690.1 | 49.5 | 1.0096
1690.2 | 49.5 | 1.0096
1690.3 | 49.5 | 1.0096
1690.4 | 49.5 | 1.0096
1690.5 | 49.5 | 1.0096
1690.6 | 49.5 | 1.0096
1690.7 | 49.5 | 1.0096
1690.8 | 49.5 | 1.0096
1690.9 | 49.5 | 1.0096
1691 | 49.5 | 1.0096
1691.1 | 49.5 | 1.0096
1691.2 | 49.5 | 1.0096
1691.3 | 49.5 | 1.0096
1691.4 | 49.5 | 1.0096
1691.5 | 49.5 | 1.0096
1691.6 | 49.5 | 1.0096
1691.7 | 49.5 | 1.0096
1691.8 | 49.5 | 1.0096
1691.9 | 49.5 | 1.0096
1692 | 49.5 | 1.0096
1692.1 | 49.5 | 1.0096
1692.2 | 49.5 | 1.0096
1692.3 | 49.5 | 1.0096
1692.4 | 49.5 | 1.0096
1692.5 | 49.5 | 1.0096
1692.6 | 49.5 | 1.0096
1692.7 | 49.5 | 1.0096
1692.8 | 49.5 | 1.0096
1692.9 | 49.5 | 1.0096
1693 | 49.5 | 1.0096
1693.1 | 49.5 | 1.0096
1693.2 | 49.5 | 1.0096
1693.3 | 49.5 | 1.0096
1693.4 | 49.5 | 1.0096
1693.5 | 49.5 | 1.0096
1693.6 | 49.5 | 1.0096
1693.7 | 49.5 | 1.0096
1693.8 | 49.5 | 1.0096
1693.9 | 49.5 | 1.0096
1694 | 49.5 | 1.0096
1694.1 | 49.5 | 1.0096
1694.2 | 49.5 | 1.0096
1694.3 | 49.5 | 1.0096
1694.4 | 49.5 | 1.0096
1694.5 | 49.5 | 1.0096
1694.6 | 49.5 | 1.0096
1694.7 | 49.5 | 1.0096
1694.8 | 49.5 | 1.0096
1694.9 | 49.5 | 1.0096
1695 | 49.5 | 1.0096
1695.1 | 49.5 | 1.0096
1695.2 | 49.5 | 1.0096
1695.3 | 49.5 | 1.0096
1695.4 | 49.5 | 1.0096
1695.5 | 49.5 | 1.0096
1695.6 | 49.5 | 1.0096
1695.7 | 49.5 | 1.0096
1695.8 | 49.5 | 1.0096
1695.9 | 49.5 | 1.0096
1696 | 49.5 | 1.0096
1696.1 | 49.5 | 1.0096
1696.2 | 49.5 | 1.0096
1696.3 | 49.5 | 1.0096
1696.4 | 49.5 | 1.0096
1696.5 | 49.5 | 1.0096
1696.6 | 49.5 | 1.0096
1696.7 | 49.5 | 1.0096
1696.8 | 49.5 | 1.0096
1696.9 | 49.5 | 1.0096
1697 | 49.5 | 1.0096
1697.1 | 49.5 | 1.0096
1697.2 | 49.5 | 1.0096
1697.3 | 49.5 | 1.0096
1697.4 | 49.5 | 1.0096
1697.5 | 49.5 | 1.0096
1697.6 | 49.5 | 1.0096
1697.7 | 49.5 | 1.0096
1697.8 | 49.5 | 1.0096
1697.9 | 49.5 | 1.0096
1698 | 49.5 | 1.0096
1698.1 | 49.5 | 1.0096
1698.2 | 49.5 | 1.0096
1698.3 | 49.5 | 1.0096
1698.4 | 49.5 | 1.0096
1698.5 | 49.5 | 1.0096
1698.6 | 49.5 | 1.0096
1698.7 | 49.5 | 1.0096
1698.8 | 49.5 | 1.0096
1698.9 | 49.5 | 1.0096
1699 | 49.5 | 1.0096
1699.1 | 49.5 | 1.0096
1699.2 | 49.5 | 1.0096
1699.3 | 49.5 | 1.0096
1699.4 | 49.5 | 1.0096
1699.5 | 49.5 | 1.0096
1699.6 | 49.5 | 1.0096
1699.7 | 49.5 | 1.0096
1699.8 | 49.5 | 1.0096
1699.9 | 49.5 | 1.0096
1700 | 49.5 | 1.0096
1700.1 | 49.5 | 1.0096
1700.2 | 49.5 | 1.0096
1700.3 | 49.5 | 1.0096
1700.4 | 49.5 | 1.0096
1700.5 | 49.5 | 1.0096
1700.6 | 49.5 | 1.0096
1700.7 | 49.5 | 1.0096
1700.8 | 49.5 | 1.0096
1700.9 | 49.5 | 1.0096
1701 | 49.5 | 1.0096
1701.1 | 49.5 | 1.0096
1701.2 | 49.5 | 1.0096
1701.3 | 49.5 | 1.0096
1701.4 | 49.5 | 1.0096
1701.5 | 49.5 | 1.0096
1701.6 | 49.5 | 1.0096
1701.7 | 49.5 | 1.0096
1701.8 | 49.5 | 1.0096
1701.9 | 49.5 | 1.0096
1702 | 49.5 | 1.0096
1702.1 | 49.5 | 1.0096
1702.2 | 49.5 | 1.0096
1702.3 | 49.5 | 1.0096
1702.4 | 49.5 | 1.0096
1702.5 | 49.5 | 1.0096
1702.6 | 49.5 | 1.0096
1702.7 | 49.5 | 1.0096
1702.8 | 49.5 | 1.0096
1702.9 | 49.5 | 1.0096
1703 | 49.5 | 1.0096
1703.1 | 49.5 | 1.0096
1703.2 | 49.5 | 1.0096
1703.3 | 49.5 | 1.0096
1703.4 | 49.5 | 1.0096
1703.5 | 49.5 | 1.0096
1703.6 | 49.5 | 1.0096
1703.7 | 49.5 | 1.0096
1703.8 | 49.5 | 1.0096
1703.9 | 49.5 | 1.0096
1704 | 49.5 | 1.0096
1704.1 | 49.5 | 1.0096
1704.2 | 49.5 | 1.0096
1704.3 | 49.5 | 1.0096
1704.4 | 49.5 | 1.0096
1704.5 | 49.5 | 1.0096
1704.6 | 49.5 | 1.0096
1704.7 | 49.5 | 1.0096
1704.8 | 49.5 | 1.0096
1704.9 | 49.5 | 1.0096
1705 | 49.5 | 1.0096
1705.1 | 49.5 | 1.0096
1705.2 | 49.5 | 1.0096
1705.3 | 49.5 | 1.0096
1705.4 | 49.5 | 1.0096
1705.5 | 49.5 | 1.0096
1705.6 | 49.5 | 1.0096
1705.7 | 49.5 | 1.0096
1705.8 | 49.5 | 1.0096
1705.9 | 49.5 | 1.0096
1706 | 49.5 | 1.0096
1706.1 | 49.5 | 1.0096
1706.2 | 49.5 | 1.0096
1706.3 | 49.5 | 1.0096
1706.4 | 49.5 | 1.0096
1706.5 | 49.5 | 1.0096
1706.6 | 49.5 | 1.0096
1706.7 | 49.5 | 1.0096
1706.8 | 49.5 | 1.0096
1706.9 | 49.5 | 1.0096
1707 | 49.5 | 1.0096
1707.1 | 49.5 | 1.0096
1707.2 | 49.5 | 1.0096
1707.3 | 49.5 | 1.0096
1707.4 | 49.5 | 1.0096
1707.5 | 49.5 | 1.0096
1707.6 | 49.5 | 1.0096
1707.7 | 49.5 | 1.0096
1707.8 | 49.5 | 1.0096
1707.9 | 49.5 | 1.0096
1708 | 49.5 | 1.0096
1708.1 | 49.5 | 1.0096
1708.2 | 49.5 | 1.0096
1708.3 | 49.5 | 1.0096
1708.4 | 49.5 | 1.0096
1708.5 | 49.5 | 1.0096
1708.6 | 49.5 | 1.0096
1708.7 | 49.5 | 1.0096
1708.8 | 49.5 | 1.0096
1708.9 | 49.5 | 1.0096
1709 | 49.5 | 1.0096
1709.1 | 49.5 | 1.0096
1709.2 | 49.5 | 1.0096
1709.3 | 49.5 | 1.0096
1709.4 | 49.5 | 1.0096
1709.5 | 49.5 | 1.0096
1709.6 | 49.5 | 1.0096
1709.7 | 49.5 | 1.0096
1709.8 | 49.5 | 1.0096
1709.9 | 49.5 | 1.0096
1710 | 49.5 | 1.0096
1710.1 | 49.5 | 1.0096
1710.2 | 49.5 | 1.0096
1710.3 | 49.5 | 1.0096
1710.4 | 49.5 | 1.0096
1710.5 | 49.5 | 1.0096
1710.6 | 49.5 | 1.0096
1710.7 | 49.5 | 1.0096
1710.8 | 49.5 | 1.0096
1710.9 | 49.5 | 1.0096
1711 | 49.5 | 1.0096
1711.1 | 49.5 | 1.0096
1711.2 | 49.5 | 1.0096
1711.3 | 49.5 | 1.0096
1711.4 | 49.5 | 1.0096
1711.5 | 49.5 | 1.0096
1711.6 | 49.5 | 1.0096
1711.7 | 49.5 | 1.0096
1711.8 | 49.5 | 1.0096
1711.9 | 49.5 | 1.0096
1712 | 49.5 | 1.0096
1712.1 | 49.5 | 1.0096
1712.2 | 49.5 | 1.0096
1712.3 | 49.5 | 1.0096
1712.4 | 49.5 | 1.0096
1712.5 | 49.5 | 1.0096
1712.6 | 49.5 | 1.0096
1712.7 | 49.5 | 1.0096
1712.8 | 49.5 | 1.0096
1712.9 | 49.5 | 1.0096
1713 | 49.5 | 1.0096
1713.1 | 49.5 | 1.0096
1713.2 | 49.5 | 1.0096
1713.3 | 49.5 | 1.0096
1713.4 | 49.5 | 1.0096
1713.5 | 49.5 | 1.0096
1713.6 | 49.5 | 1.0096
1713.7 | 49.5 | 1.0096
1713.8 | 49.5 | 1.0096
1713.9 | 49.5 | 1.0096
1714 | 49.5 | 1.0096
1714.1 | 49.5 | 1.0096
1714.2 | 49.5 | 1.0096
1714.3 | 49.5 | 1.0096
1714.4 | 49.5 | 1.0096
1714.5 | 49.5 | 1.0096
1714.6 | 49.5 | 1.0096
1714.7 | 49.5 | 1.0096
1714.8 | 49.5 | 1.0096
1714.9 | 49.5 | 1.0096
1715 | 49.5 | 1.0096
1715.1 | 49.5 | 1.0096
1715.2 | 49.5 | 1.0096
1715.3 | 49.5 | 1.0096
1715.4 | 49.5 | 1.0096
1715.5 | 49.5 | 1.0096
1715.6 | 49.5 | 1.0096
1715.7 | 49.5 | 1.0096
1715.8 | 49.5 | 1.0096
1715.9 | 49.5 | 1.0096
1716 | 49.5 | 1.0096
1716.1 | 49.5 | 1.0096
1716.2 | 49.5 | 1.0096
1716.3 | 49.5 | 1.0096
1716.4 | 49.5 | 1.0096
1716.5 | 49.5 | 1.0096
1716.6 | 49.5 | 1.0096
1716.7 | 49.5 | 1.0096
1716.8 | 49.5 | 1.0096
1716.9 | 49.5 | 1.0096
1717 | 49.5 | 1.0096
1717.1 | 49.5 | 1.0096
1717.2 | 49.5 | 1.0096
1717.3 | 49.5 | 1.0096
1717.4 | 49.5 | 1.0096
1717.5 | 49.5 | 1.0096
1717.6 | 49.5 | 1.0096
1717.7 | 49.5 | 1.0096
1717.8 | 49.5 | 1.0096
1717.9 | 49.5 | 1.0096
1718 | 49.5 | 1.0096
1718.1 | 49.5 | 1.0096
1718.2 | 49.5 | 1.0096
1718.3 | 49.5 | 1.0096
1718.4 | 49.5 | 1.0096
1718.5 | 49.5 | 1.0096
1718.6 | 49.5 | 1.0096
1718.7 | 49.5 | 1.0096
1718.8 | 49.5 | 1.0096
1718.9 | 49.5 | 1.0096
1719 | 49.5 | 1.0096
1719.1 | 49.5 | 1.0096
1719.2 | 49.5 | 1.0096
1719.3 | 49.5 | 1.0096
1719.4 | 49.5 | 1.0096
1719.5 | 49.5 | 1.0096
1719.6 | 49.5 | 1.0096
1719.7 | 49.5 | 1.0096
1719.8 | 49.5 | 1.0096
1719.9 | 49.5 | 1.0096
1720 | 49.5 | 1.0096
1720.1 | 49.5 | 1.0096
1720.2 | 49.5 | 1.0096
1720.3 | 49.5 | 1.0096
1720.4 | 49.5 | 1.0096
1720.5 | 49.5 | 1.0096
1720.6 | 49.5 | 1.0096
1720.7 | 49.5 | 1.0096
1720.8 | 49.5 | 1.0096
1720.9 | 49.5 | 1.0096
1721 | 49.5 | 1.0096
1721.1 | 49.5 | 1.0096
1721.2 | 49.5 | 1.0096
1721.3 | 49.5 | 1.0096
1721.4 | 49.5 | 1.0096
1721.5 | 49.5 | 1.0096
1721.6 | 49.5 | 1.0096
1721.7 | 49.5 | 1.0096
1721.8 | 49.5 | 1.0096
1721.9 | 49.5 | 1.0096
1722 | 49.5 | 1.0096
1722.1 | 49.5 | 1.0096
1722.2 | 49.5 | 1.0096
1722.3 | 49.5 | 1.0096
1722.4 | 49.5 | 1.0096
1722.5 | 49.5 | 1.0096
1722.6 | 49.5 | 1.0096
1722.7 | 49.5 | 1.0096
1722.8 | 49.5 | 1.0096
1722.9 | 49.5 | 1.0096
1723 | 49.5 | 1.0096
1723.1 | 49.5 | 1.0096
1723.2 | 49.5 | 1.0096
1723.3 | 49.5 | 1.0096
1723.4 | 49.5 | 1.0096
1723.5 | 49.5 | 1.0096
1723.6 | 49.5 | 1.0096
1723.7 | 49.5 | 1.0096
1723.8 | 49.5 | 1.0096
1723.9 | 49.5 | 1.0096
1724 | 49.5 | 1.0096
1724.1 | 49.5 | 1.0096
1724.2 | 49.5 | 1.0096
1724.3 | 49.5 | 1.0096
1724.4 | 49.5 | 1.0096
1724.5 | 49.5 | 1.0096
1724.6 | 49.5 | 1.0096
1724.7 | 49.5 | 1.0096
1724.8 | 49.5 | 1.0096
1724.9 | 49.5 | 1.0096
1725 | 49.5 | 1.0096
1725.1 | 49.5 | 1.0096
1725.2 | 49.5 | 1.0096
1725.3 | 49.5 | 1.0096
1725.4 | 49.5 | 1.0096
1725.5 | 49.5 | 1.0096
1725.6 | 49.5 | 1.0096
1725.7 | 49.5 | 1.0096
1725.8 | 49.5 | 1.0096
1725.9 | 49.5 | 1.0096
1726 | 49.5 | 1.0096
1726.1 | 49.5 | 1.0096
1726.2 | 49.5 | 1.0096
1726.3 | 49.5 | 1.0096
1726.4 | 49.5 | 1.0096
1726.5 | 49.5 | 1.0096
1726.6 | 49.5 | 1.0096
1726.7 | 49.5 | 1.0096
1726.8 | 49.5 | 1.0096
1726.9 | 49.5 | 1.0096
1727 | 49.5 | 1.0096
1727.1 | 49.5 | 1.0096
1727.2 | 49.5 | 1.0096
1727.3 | 49.5 | 1.0096
1727.4 | 49.5 | 1.0096
1727.5 | 49.5 | 1.0096
1727.6 | 49.5 | 1.0096
1727.7 | 49.5 | 1.0096
1727.8 | 49.5 | 1.0096
1727.9 | 49.5 | 1.0096
1728 | 49.5 | 1.0096
1728.1 | 49.5 | 1.0096
1728.2 | 49.5 | 1.0096
1728.3 | 49.5 | 1.0096
1728.4 | 49.5 | 1.0096
1728.5 | 49.5 | 1.0096
1728.6 | 49.5 | 1.0096
1728.7 | 49.5 | 1.0096
1728.8 | 49.5 | 1.0096
1728.9 | 49.5 | 1.0096
1729 | 49.5 | 1.0096
1729.1 | 49.5 | 1.0096
1729.2 | 49.5 | 1.0096
1729.3 | 49.5 | 1.0096
1729.4 | 49.5 | 1.0096
1729.5 | 49.5 | 1.0096
1729.6 | 49.5 | 1.0096
1729.7 | 49.5 | 1.0096
1729.8 | 49.5 | 1.0096
1729.9 | 49.5 | 1.0096
1730 | 49.5 | 1.0096
1730.1 | 49.5 | 1.0096
1730.2 | 49.5 | 1.0096
1730.3 | 49.5 | 1.0096
1730.4 | 49.5 | 1.0096
1730.5 | 49.5 | 1.0096
1730.6 | 49.5 | 1.0096
1730.7 | 49.5 | 1.0096
1730.8 | 49.5 | 1.0096
1730.9 | 49.5 | 1.0096
1731 | 49.5 | 1.0096
1731.1 | 49.5 | 1.0096
1731.2 | 49.5 | 1.0096
1731.3 | 49.5 | 1.0096
1731.4 | 49.5 | 1.0096
1731.5 | 49.5 | 1.0096
1731.6 | 49.5 | 1.0096
1731.7 | 49.5 | 1.0096
1731.8 | 49.5 | 1.0096
1731.9 | 49.5 | 1.0096
1732 | 49.5 | 1.0096
1732.1 | 49.5 | 1.0096
1732.2 | 49.5 | 1.0096
1732.3 | 49.5 | 1.0096
1732.4 | 49.5 | 1.0096
1732.5 | 49.5 | 1.0096
1732.6 | 49.5 | 1.0096
1732.7 | 49.5 | 1.0096
1732.8 | 49.5 | 1.0096
1732.9 | 49.5 | 1.0096
1733 | 49.5 | 1.0096
1733.1 | 49.5 | 1.0096
1733.2 | 49.5 | 1.0096
1733.3 | 49.5 | 1.0096
1733.4 | 49.5 | 1.0096
1733.5 | 49.5 | 1.0096
1733.6 | 49.5 | 1.0096
1733.7 | 49.5 | 1.0096
1733.8 | 49.5 | 1.0096
1733.9 | 49.5 | 1.0096
1734 | 49.5 | 1.0096
1734.1 | 49.5 | 1.0096
1734.2 | 49.5 | 1.0096
1734.3 | 49.5 | 1.0096
1734.4 | 49.5 | 1.0096
1734.5 | 49.5 | 1.0096
1734.6 | 49.5 | 1.0096
1734.7 | 49.5 | 1.0096
1734.8 | 49.5 | 1.0096
1734.9 | 49.5 | 1.0096
1735 | 49.5 | 1.0096
1735.1 | 49.5 | 1.0096
1735.2 | 49.5 | 1.0096
1735.3 | 49.5 | 1.0096
1735.4 | 49.5 | 1.0096
1735.5 | 49.5 | 1.0096
1735.6 | 49.5 | 1.0096
1735.7 | 49.5 | 1.0096
1735.8 | 49.5 | 1.0096
1735.9 | 49.5 | 1.0096
1736 | 49.5 | 1.0096
1736.1 | 49.5 | 1.0096
1736.2 | 49.5 | 1.0096
1736.3 | 49.5 | 1.0096
1736.4 | 49.5 | 1.0096
1736.5 | 49.5 | 1.0096
1736.6 | 49.5 | 1.0096
1736.7 | 49.5 | 1.0096
1736.8 | 49.5 | 1.0096
1736.9 | 49.5 | 1.0096
1737 | 49.5 | 1.0096
1737.1 | 49.5 | 1.0096
1737.2 | 49.5 | 1.0096
1737.3 | 49.5 | 1.0096
1737.4 | 49.5 | 1.0096
1737.5 | 49.5 | 1.0096
1737.6 | 49.5 | 1.0096
1737.7 | 49.5 | 1.0096
1737.8 | 49.5 | 1.0096
1737.9 | 49.5 | 1.0096
1738 | 49.5 | 1.0096
1738.1 | 49.5 | 1.0096
1738.2 | 49.5 | 1.0096
1738.3 | 49.5 | 1.0096
1738.4 | 49.5 | 1.0096
1738.5 | 49.5 | 1.0096
1738.6 | 49.5 | 1.0096
1738.7 | 49.5 | 1.0096
1738.8 | 49.5 | 1.0096
1738.9 | 49.5 | 1.0096
1739 | 49.5 | 1.0096
1739.1 | 49.5 | 1.0096
1739.2 | 49.5 | 1.0096
1739.3 | 49.5 | 1.0096
1739.4 | 49.5 | 1.0096
1739.5 | 49.5 | 1.0096
1739.6 | 49.5 | 1.0096
1739.7 | 49.5 | 1.0096
1739.8 | 49.5 | 1.0096
1739.9 | 49.5 | 1.0096
1740 | 49.5 | 1.0096
1740.1 | 49.5 | 1.0096
1740.2 | 49.5 | 1.0096
1740.3 | 49.5 | 1.0096
1740.4 | 49.5 | 1.0096
1740.5 | 49.5 | 1.0096
1740.6 | 49.5 | 1.0096
1740.7 | 49.5 | 1.0096
1740.8 | 49.5 | 1.0096
1740.9 | 49.5 | 1.0096
1741 | 49.5 | 1.0096
1741.1 | 49.5 | 1.0096
1741.2 | 49.5 | 1.0096
1741.3 | 49.5 | 1.0096
1741.4 | 49.5 | 1.0096
1741.5 | 49.5 | 1.0096
1741.6 | 49.5 | 1.0096
1741.7 | 49.5 | 1.0096
1741.8 | 49.5 | 1.0096
1741.9 | 49.5 | 1.0096
1742 | 49.5 | 1.0096
1742.1 | 49.5 | 1.0096
1742.2 | 49.5 | 1.0096
1742.3 | 49.5 | 1.0096
1742.4 | 49.5 | 1.0096
1742.5 | 49.5 | 1.0096
1742.6 | 49.5 | 1.0096
1742.7 | 49.5 | 1.0096
1742.8 | 49.5 | 1.0096
1742.9 | 49.5 | 1.0096
1743 | 49.5 | 1.0096
1743.1 | 49.5 | 1.0096
1743.2 | 49.5 | 1.0096
1743.3 | 49.5 | 1.0096
1743.4 | 49.5 | 1.0096
1743.5 | 49.5 | 1.0096
1743.6 | 49.5 | 1.0096
1743.7 | 49.5 | 1.0096
1743.8 | 49.5 | 1.0096
1743.9 | 49.5 | 1.0096
1744 | 49.5 | 1.0096
1744.1 | 49.5 | 1.0096
1744.2 | 49.5 | 1.0096
1744.3 | 49.5 | 1.0096
1744.4 | 49.5 | 1.0096
1744.5 | 49.5 | 1.0096
1744.6 | 49.5 | 1.0096
1744.7 | 49.5 | 1.0096
1744.8 | 49.5 | 1.0096
1744.9 | 49.5 | 1.0096
1745 | 49.5 | 1.0096
1745.1 | 49.5 | 1.0096
1745.2 | 49.5 | 1.0096
1745.3 | 49.5 | 1.0096
1745.4 | 49.5 | 1.0096
1745.5 | 49.5 | 1.0096
1745.6 | 49.5 | 1.0096
1745.7 | 49.5 | 1.0096
1745.8 | 49.5 | 1.0096
1745.9 | 49.5 | 1.0096
1746 | 49.5 | 1.0096
1746.1 | 49.5 | 1.0096
1746.2 | 49.5 | 1.0096
1746.3 | 49.5 | 1.0096
1746.4 | 49.5 | 1.0096
1746.5 | 49.5 | 1.0096
1746.6 | 49.5 | 1.0096
1746.7 | 49.5 | 1.0096
1746.8 | 49.5 | 1.0096
1746.9 | 49.5 | 1.0096
1747 | 49.5 | 1.0096
1747.1 | 49.5 | 1.0096
1747.2 | 49.5 | 1.0096
1747.3 | 49.5 | 1.0096
1747.4 | 49.5 | 1.0096
1747.5 | 49.5 | 1.0096
1747.6 | 49.5 | 1.0096
1747.7 | 49.5 | 1.0096
1747.8 | 49.5 | 1.0096
1747.9 | 49.5 | 1.0096
1748 | 49.5 | 1.0096
1748.1 | 49.5 | 1.0096
1748.2 | 49.5 | 1.0096
1748.3 | 49.5 | 1.0096
1748.4 | 49.5 | 1.0096
1748.5 | 49.5 | 1.0096
1748.6 | 49.5 | 1.0096
1748.7 | 49.5 | 1.0096
1748.8 | 49.5 | 1.0096
1748.9 | 49.5 | 1.0096
1749 | 49.5 | 1.0096
1749.1 | 49.5 | 1.0096
1749.2 | 49.5 | 1.0096
1749.3 | 49.5 | 1.0096
1749.4 | 49.5 | 1.0096
1749.5 | 49.5 | 1.0096
1749.6 | 49.5 | 1.0096
1749.7 | 49.5 | 1.0096
1749.8 | 49.5 | 1.0096
1749.9 | 49.5 | 1.0096
1750 | 49.5 | 1.0096
1750.1 | 49.5 | 1.0096
1750.2 | 49.5 | 1.0096
1750.3 | 49.5 | 1.0096
1750.4 | 49.5 | 1.0096
1750.5 | 49.5 | 1.0098
1750.6 | 49.5 | 1.0098
1750.7 | 49.5 | 1.0098
1750.8 | 49.5 | 1.0098
1750.9 | 49.5 | 1.0098
1751 | 49.5 | 1.0098
1751.1 | 49.5 | 1.0098
1751.2 | 49.5 | 1.0098
1751.3 | 49.5 | 1.0098
1751.4 | 49.5 | 1.0098
1751.5 | 49.5 | 1.0096
1751.6 | 49.5 | 1.0096
1751.7 | 49.5 | 1.0096
1751.8 | 49.5 | 1.0096
1751.9 | 49.5 | 1.0096
1752 | 49.5 | 1.0096
1752.1 | 49.5 | 1.0096
1752.2 | 49.5 | 1.0096
1752.3 | 49.5 | 1.0096
1752.4 | 49.5 | 1.0096
1752.5 | 49.5 | 1.0096
1752.6 | 49.5 | 1.0096
1752.7 | 49.5 | 1.0096
1752.8 | 49.5 | 1.0096
1752.9 | 49.5 | 1.0096
1753 | 49.5 | 1.0096
1753.1 | 49.5 | 1.0096
1753.2 | 49.5 | 1.0096
1753.3 | 49.5 | 1.0096
1753.4 | 49.5 | 1.0096
1753.5 | 49.5 | 1.0096
1753.6 | 49.5 | 1.0096
1753.7 | 49.5 | 1.0096
1753.8 | 49.5 | 1.0096
1753.9 | 49.5 | 1.0096
1754 | 49.5 | 1.0096
1754.1 | 49.5 | 1.0096
1754.2 | 49.5 | 1.0096
1754.3 | 49.5 | 1.0096
1754.4 | 49.5 | 1.0096
1754.5 | 49.5 | 1.0096
1754.6 | 49.5 | 1.0096
1754.7 | 49.5 | 1.0096
1754.8 | 49.5 | 1.0096
1754.9 | 49.5 | 1.0096
1755 | 49.5 | 1.0096
1755.1 | 49.5 | 1.0096
1755.2 | 49.5 | 1.0096
1755.3 | 49.5 | 1.0096
1755.4 | 49.5 | 1.0096
1755.5 | 49.5 | 1.0096
1755.6 | 49.5 | 1.0096
1755.7 | 49.5 | 1.0096
1755.8 | 49.5 | 1.0096
1755.9 | 49.5 | 1.0096
1756 | 49.5 | 1.0096
1756.1 | 49.5 | 1.0096
1756.2 | 49.5 | 1.0096
1756.3 | 49.5 | 1.0096
1756.4 | 49.5 | 1.0096
1756.5 | 49.5 | 1.0096
1756.6 | 49.5 | 1.0096
1756.7 | 49.5 | 1.0096
1756.8 | 49.5 | 1.0096
1756.9 | 49.5 | 1.0096
1757 | 49.5 | 1.0096
1757.1 | 49.5 | 1.0096
1757.2 | 49.5 | 1.0096
1757.3 | 49.5 | 1.0096
1757.4 | 49.5 | 1.0096
1757.5 | 49.5 | 1.0096
1757.6 | 49.5 | 1.0096
1757.7 | 49.5 | 1.0096
1757.8 | 49.5 | 1.0096
1757.9 | 49.5 | 1.0096
1758 | 49.5 | 1.0096
1758.1 | 49.5 | 1.0096
1758.2 | 49.5 | 1.0096
1758.3 | 49.5 | 1.0096
1758.4 | 49.5 | 1.0096
1758.5 | 49.5 | 1.0096
1758.6 | 49.5 | 1.0096
1758.7 | 49.5 | 1.0096
1758.8 | 49.5 | 1.0096
1758.9 | 49.5 | 1.0096
1759 | 49.5 | 1.0096
1759.1 | 49.5 | 1.0096
1759.2 | 49.5 | 1.0096
1759.3 | 49.5 | 1.0096
1759.4 | 49.5 | 1.0096
1759.5 | 49.5 | 1.0096
1759.6 | 49.5 | 1.0096
1759.7 | 49.5 | 1.0096
1759.8 | 49.5 | 1.0096
1759.9 | 49.5 | 1.0096
1760 | 49.5 | 1.0096
1760.1 | 49.5 | 1.0096
1760.2 | 49.5 | 1.0096
1760.3 | 49.5 | 1.0096
1760.4 | 49.5 | 1.0096
1760.5 | 49.5 | 1.0096
1760.6 | 49.5 | 1.0096
1760.7 | 49.5 | 1.0096
1760.8 | 49.5 | 1.0096
1760.9 | 49.5 | 1.0096
1761 | 49.5 | 1.0096
1761.1 | 49.5 | 1.0096
1761.2 | 49.5 | 1.0096
1761.3 | 49.5 | 1.0096
1761.4 | 49.5 | 1.0096
1761.5 | 49.5 | 1.0096
1761.6 | 49.5 | 1.0096
1761.7 | 49.5 | 1.0096
1761.8 | 49.5 | 1.0096
1761.9 | 49.5 | 1.0096
1762 | 49.5 | 1.0096
1762.1 | 49.5 | 1.0096
1762.2 | 49.5 | 1.0096
1762.3 | 49.5 | 1.0096
1762.4 | 49.5 | 1.0096
1762.5 | 49.5 | 1.0096
1762.6 | 49.5 | 1.0096
1762.7 | 49.5 | 1.0096
1762.8 | 49.5 | 1.0096
1762.9 | 49.5 | 1.0096
1763 | 49.5 | 1.0096
1763.1 | 49.5 | 1.0096
1763.2 | 49.5 | 1.0096
1763.3 | 49.5 | 1.0096
1763.4 | 49.5 | 1.0096
1763.5 | 49.5 | 1.0096
1763.6 | 49.5 | 1.0096
1763.7 | 49.5 | 1.0096
1763.8 | 49.5 | 1.0096
1763.9 | 49.5 | 1.0096
1764 | 49.5 | 1.0096
1764.1 | 49.5 | 1.0096
1764.2 | 49.5 | 1.0096
1764.3 | 49.5 | 1.0096
1764.4 | 49.5 | 1.0096
1764.5 | 49.5 | 1.0096
1764.6 | 49.5 | 1.0096
1764.7 | 49.5 | 1.0096
1764.8 | 49.5 | 1.0096
1764.9 | 49.5 | 1.0096
1765 | 49.5 | 1.0096
1765.1 | 49.5 | 1.0096
1765.2 | 49.5 | 1.0096
1765.3 | 49.5 | 1.0096
1765.4 | 49.5 | 1.0096
1765.5 | 49.5 | 1.0096
1765.6 | 49.5 | 1.0096
1765.7 | 49.5 | 1.0096
1765.8 | 49.5 | 1.0096
1765.9 | 49.5 | 1.0096
1766 | 49.5 | 1.0096
1766.1 | 49.5 | 1.0096
1766.2 | 49.5 | 1.0096
1766.3 | 49.5 | 1.0096
1766.4 | 49.5 | 1.0096
1766.5 | 49.5 | 1.0096
1766.6 | 49.5 | 1.0096
1766.7 | 49.5 | 1.0096
1766.8 | 49.5 | 1.0096
1766.9 | 49.5 | 1.0096
1767 | 49.5 | 1.0096
1767.1 | 49.5 | 1.0096
1767.2 | 49.5 | 1.0096
1767.3 | 49.5 | 1.0096
1767.4 | 49.5 | 1.0096
1767.5 | 49.5 | 1.0096
1767.6 | 49.5 | 1.0096
1767.7 | 49.5 | 1.0096
1767.8 | 49.5 | 1.0096
1767.9 | 49.5 | 1.0096
1768 | 49.5 | 1.0096
1768.1 | 49.5 | 1.0096
1768.2 | 49.5 | 1.0096
1768.3 | 49.5 | 1.0096
1768.4 | 49.5 | 1.0096
1768.5 | 49.5 | 1.0096
1768.6 | 49.5 | 1.0096
1768.7 | 49.5 | 1.0096
1768.8 | 49.5 | 1.0096
1768.9 | 49.5 | 1.0096
1769 | 49.5 | 1.0096
1769.1 | 49.5 | 1.0096
1769.2 | 49.5 | 1.0096
1769.3 | 49.5 | 1.0096
1769.4 | 49.5 | 1.0096
1769.5 | 49.5 | 1.0096
1769.6 | 49.5 | 1.0096
1769.7 | 49.5 | 1.0096
1769.8 | 49.5 | 1.0096
1769.9 | 49.5 | 1.0096
1770 | 49.5 | 1.0096
1770.1 | 49.5 | 1.0096
1770.2 | 49.5 | 1.0096
1770.3 | 49.5 | 1.0096
1770.4 | 49.5 | 1.0096
1770.5 | 49.5 | 1.0096
1770.6 | 49.5 | 1.0096
1770.7 | 49.5 | 1.0096
1770.8 | 49.5 | 1.0096
1770.9 | 49.5 | 1.0096
1771 | 49.5 | 1.0096
1771.1 | 49.5 | 1.0096
1771.2 | 49.5 | 1.0096
1771.3 | 49.5 | 1.0096
1771.4 | 49.5 | 1.0096
1771.5 | 49.5 | 1.0096
1771.6 | 49.5 | 1.0096
1771.7 | 49.5 | 1.0096
1771.8 | 49.5 | 1.0096
1771.9 | 49.5 | 1.0096
1772 | 49.5 | 1.0096
1772.1 | 49.5 | 1.0096
1772.2 | 49.5 | 1.0096
1772.3 | 49.5 | 1.0096
1772.4 | 49.5 | 1.0096
1772.5 | 49.5 | 1.0096
1772.6 | 49.5 | 1.0096
1772.7 | 49.5 | 1.0096
1772.8 | 49.5 | 1.0096
1772.9 | 49.5 | 1.0096
1773 | 49.5 | 1.0096
1773.1 | 49.5 | 1.0096
1773.2 | 49.5 | 1.0096
1773.3 | 49.5 | 1.0096
1773.4 | 49.5 | 1.0096
1773.5 | 49.5 | 1.0096
1773.6 | 49.5 | 1.0096
1773.7 | 49.5 | 1.0096
1773.8 | 49.5 | 1.0096
1773.9 | 49.5 | 1.0096
1774 | 49.5 | 1.0096
1774.1 | 49.5 | 1.0096
1774.2 | 49.5 | 1.0096
1774.3 | 49.5 | 1.0096
1774.4 | 49.5 | 1.0096
1774.5 | 49.5 | 1.0096
1774.6 | 49.5 | 1.0096
1774.7 | 49.5 | 1.0096
1774.8 | 49.5 | 1.0096
1774.9 | 49.5 | 1.0096
1775 | 49.5 | 1.0096
1775.1 | 49.5 | 1.0096
1775.2 | 49.5 | 1.0096
1775.3 | 49.5 | 1.0096
1775.4 | 49.5 | 1.0096
1775.5 | 49.5 | 1.0096
1775.6 | 49.5 | 1.0096
1775.7 | 49.5 | 1.0096
1775.8 | 49.5 | 1.0096
1775.9 | 49.5 | 1.0096
1776 | 49.5 | 1.0096
1776.1 | 49.5 | 1.0096
1776.2 | 49.5 | 1.0096
1776.3 | 49.5 | 1.0096
1776.4 | 49.5 | 1.0096
1776.5 | 49.5 | 1.0096
1776.6 | 49.5 | 1.0096
1776.7 | 49.5 | 1.0096
1776.8 | 49.5 | 1.0096
1776.9 | 49.5 | 1.0096
1777 | 49.5 | 1.0096
1777.1 | 49.5 | 1.0096
1777.2 | 49.5 | 1.0096
1777.3 | 49.5 | 1.0096
1777.4 | 49.5 | 1.0096
1777.5 | 49.5 | 1.0096
1777.6 | 49.5 | 1.0096
1777.7 | 49.5 | 1.0096
1777.8 | 49.5 | 1.0096
1777.9 | 49.5 | 1.0096
1778 | 49.5 | 1.0096
1778.1 | 49.5 | 1.0096
1778.2 | 49.5 | 1.0096
1778.3 | 49.5 | 1.0096
1778.4 | 49.5 | 1.0096
1778.5 | 49.5 | 1.0096
1778.6 | 49.5 | 1.0096
1778.7 | 49.5 | 1.0096
1778.8 | 49.5 | 1.0096
1778.9 | 49.5 | 1.0096
1779 | 49.5 | 1.0096
1779.1 | 49.5 | 1.0096
1779.2 | 49.5 | 1.0096
1779.3 | 49.5 | 1.0096
1779.4 | 49.5 | 1.0096
1779.5 | 49.5 | 1.0096
1779.6 | 49.5 | 1.0096
1779.7 | 49.5 | 1.0096
1779.8 | 49.5 | 1.0096
1779.9 | 49.5 | 1.0096
1780 | 49.5 | 1.0096
1780.1 | 49.5 | 1.0096
1780.2 | 49.5 | 1.0096
1780.3 | 49.5 | 1.0096
1780.4 | 49.5 | 1.0096
1780.5 | 49.5 | 1.0096
1780.6 | 49.5 | 1.0096
1780.7 | 49.5 | 1.0096
1780.8 | 49.5 | 1.0096
1780.9 | 49.5 | 1.0096
1781 | 49.5 | 1.0096
1781.1 | 49.5 | 1.0096
1781.2 | 49.5 | 1.0096
1781.3 | 49.5 | 1.0096
1781.4 | 49.5 | 1.0096
1781.5 | 49.5 | 1.0096
1781.6 | 49.5 | 1.0096
1781.7 | 49.5 | 1.0096
1781.8 | 49.5 | 1.0096
1781.9 | 49.5 | 1.0096
1782 | 49.5 | 1.0096
1782.1 | 49.5 | 1.0096
1782.2 | 49.5 | 1.0096
1782.3 | 49.5 | 1.0096
1782.4 | 49.5 | 1.0096
1782.5 | 49.5 | 1.0096
1782.6 | 49.5 | 1.0096
1782.7 | 49.5 | 1.0096
1782.8 | 49.5 | 1.0096
1782.9 | 49.5 | 1.0096
1783 | 49.5 | 1.0096
1783.1 | 49.5 | 1.0098
1783.2 | 49.5 | 1.0098
1783.3 | 49.5 | 1.0098
1783.4 | 49.5 | 1.0098
1783.5 | 49.5 | 1.0098
1783.6 | 49.5 | 1.0098
1783.7 | 49.5 | 1.0098
1783.8 | 49.5 | 1.0098
1783.9 | 49.5 | 1.0098
1784 | 49.5 | 1.0098
1784.1 | 49.5 | 1.0098
1784.2 | 49.5 | 1.0098
1784.3 | 49.5 | 1.0098
1784.4 | 49.5 | 1.0098
1784.5 | 49.5 | 1.0098
1784.6 | 49.5 | 1.0098
1784.7 | 49.5 | 1.0098
1784.8 | 49.5 | 1.0098
1784.9 | 49.5 | 1.0098
1785 | 49.5 | 1.0098
1785.1 | 49.5 | 1.0098
1785.2 | 49.5 | 1.0098
1785.3 | 49.5 | 1.0098
1785.4 | 49.5 | 1.0096
1785.5 | 49.5 | 1.0096
1785.6 | 49.5 | 1.0096
1785.7 | 49.5 | 1.0096
1785.8 | 49.5 | 1.0096
1785.9 | 49.5 | 1.0096
1786 | 49.5 | 1.0096
1786.1 | 49.5 | 1.0096
1786.2 | 49.5 | 1.0096
1786.3 | 49.5 | 1.0096
1786.4 | 49.5 | 1.0096
1786.5 | 49.5 | 1.0096
1786.6 | 49.5 | 1.0096
1786.7 | 49.5 | 1.0096
1786.8 | 49.5 | 1.0096
1786.9 | 49.5 | 1.0096
1787 | 49.5 | 1.0096
1787.1 | 49.5 | 1.0096
1787.2 | 49.5 | 1.0096
1787.3 | 49.5 | 1.0096
1787.4 | 49.5 | 1.0096
1787.5 | 49.5 | 1.0096
1787.6 | 49.5 | 1.0096
1787.7 | 49.5 | 1.0096
1787.8 | 49.5 | 1.0096
1787.9 | 49.5 | 1.0096
1788 | 49.5 | 1.0096
1788.1 | 49.5 | 1.0096
1788.2 | 49.5 | 1.0096
1788.3 | 49.5 | 1.0096
1788.4 | 49.5 | 1.0096
1788.5 | 49.5 | 1.0096
1788.6 | 49.5 | 1.0096
1788.7 | 49.5 | 1.0096
1788.8 | 49.5 | 1.0096
1788.9 | 49.5 | 1.0096
1789 | 49.5 | 1.0096
1789.1 | 49.5 | 1.0096
1789.2 | 49.5 | 1.0096
1789.3 | 49.5 | 1.0096
1789.4 | 49.5 | 1.0096
1789.5 | 49.5 | 1.0096
1789.6 | 49.5 | 1.0096
1789.7 | 49.5 | 1.0096
1789.8 | 49.5 | 1.0096
1789.9 | 49.5 | 1.0096
1790 | 49.5 | 1.0096
1790.1 | 49.5 | 1.0096
1790.2 | 49.5 | 1.0096
1790.3 | 49.5 | 1.0096
1790.4 | 49.5 | 1.0096
1790.5 | 49.5 | 1.0096
1790.6 | 49.5 | 1.0096
1790.7 | 49.5 | 1.0096
1790.8 | 49.5 | 1.0096
1790.9 | 49.5 | 1.0096
1791 | 49.5 | 1.0096
1791.1 | 49.5 | 1.0096
1791.2 | 49.5 | 1.0096
1791.3 | 49.5 | 1.0096
1791.4 | 49.5 | 1.0096
1791.5 | 49.5 | 1.0096
1791.6 | 49.5 | 1.0096
1791.7 | 49.5 | 1.0096
1791.8 | 49.5 | 1.0096
1791.9 | 49.5 | 1.0096
1792 | 49.5 | 1.0096
1792.1 | 49.5 | 1.0096
1792.2 | 49.5 | 1.0096
1792.3 | 49.5 | 1.0096
1792.4 | 49.5 | 1.0096
1792.5 | 49.5 | 1.0096
1792.6 | 49.5 | 1.0096
1792.7 | 49.5 | 1.0096
1792.8 | 49.5 | 1.0096
1792.9 | 49.5 | 1.0096
1793 | 49.5 | 1.0096
1793.1 | 49.5 | 1.0096
1793.2 | 49.5 | 1.0096
1793.3 | 49.5 | 1.0096
1793.4 | 49.5 | 1.0096
1793.5 | 49.5 | 1.0096
1793.6 | 49.5 | 1.0096
1793.7 | 49.5 | 1.0096
1793.8 | 49.5 | 1.0096
1793.9 | 49.5 | 1.0096
1794 | 49.5 | 1.0096
1794.1 | 49.5 | 1.0096
1794.2 | 49.5 | 1.0096
1794.3 | 49.5 | 1.0096
1794.4 | 49.5 | 1.0096
1794.5 | 49.5 | 1.0096
1794.6 | 49.5 | 1.0096
1794.7 | 49.5 | 1.0096
1794.8 | 49.5 | 1.0096
1794.9 | 49.5 | 1.0096
1795 | 49.5 | 1.0096
1795.1 | 49.5 | 1.0096
1795.2 | 49.5 | 1.0096
1795.3 | 49.5 | 1.0096
1795.4 | 49.5 | 1.0096
1795.5 | 49.5 | 1.0096
1795.6 | 49.5 | 1.0096
1795.7 | 49.5 | 1.0096
1795.8 | 49.5 | 1.0096
1795.9 | 49.5 | 1.0096
1796 | 49.5 | 1.0096
1796.1 | 49.5 | 1.0096
1796.2 | 49.5 | 1.0096
1796.3 | 49.5 | 1.0096
1796.4 | 49.5 | 1.0096
1796.5 | 49.5 | 1.0096
1796.6 | 49.5 | 1.0096
1796.7 | 49.5 | 1.0096
1796.8 | 49.5 | 1.0096
1796.9 | 49.5 | 1.0096
1797 | 49.5 | 1.0096
1797.1 | 49.5 | 1.0096
1797.2 | 49.5 | 1.0096
1797.3 | 49.5 | 1.0096
1797.4 | 49.5 | 1.0096
1797.5 | 49.5 | 1.0096
1797.6 | 49.5 | 1.0096
1797.7 | 49.5 | 1.0096
1797.8 | 49.5 | 1.0096
1797.9 | 49.5 | 1.0096
1798 | 49.5 | 1.0096
1798.1 | 49.5 | 1.0096
1798.2 | 49.5 | 1.0096
1798.3 | 49.5 | 1.0096
1798.4 | 49.5 | 1.0098
1798.5 | 49.5 | 1.0098
1798.6 | 49.5 | 1.0098
1798.7 | 49.5 | 1.0098
1798.8 | 49.5 | 1.0098
1798.9 | 49.5 | 1.0098
1799 | 49.5 | 1.0098
1799.1 | 49.5 | 1.0098
1799.2 | 49.5 | 1.0098
1799.3 | 49.5 | 1.0098
1799.4 | 49.5 | 1.0098
1799.5 | 49.5 | 1.0098
1799.6 | 49.5 | 1.0098
1799.7 | 49.5 | 1.0098
1799.8 | 49.5 | 1.0098
1799.9 | 49.5 | 1.0098
1800 | 49.5 | 1.0098
1800.1 | 49.5 | 1.0098
1800.2 | 49.5 | 1.0098
1800.3 | 49.5 | 1.0098
1800.4 | 49.5 | 1.0098
1800.5 | 49.5 | 1.0098
1800.6 | 49.5 | 1.0098
1800.7 | 49.5 | 1.0096
1800.8 | 49.5 | 1.0096
1800.9 | 49.5 | 1.0096
1801 | 49.5 | 1.0096
1801.1 | 49.5 | 1.0096
1801.2 | 49.5 | 1.0096
1801.3 | 49.5 | 1.0096
1801.4 | 49.5 | 1.0096
1801.5 | 49.5 | 1.0096
1801.6 | 49.5 | 1.0096
1801.7 | 49.5 | 1.0096
1801.8 | 49.5 | 1.0096
1801.9 | 49.5 | 1.0096
1802 | 49.5 | 1.0096
1802.1 | 49.5 | 1.0096
1802.2 | 49.5 | 1.0096
1802.3 | 49.5 | 1.0096
1802.4 | 49.5 | 1.0096
1802.5 | 49.5 | 1.0096
1802.6 | 49.5 | 1.0096
1802.7 | 49.5 | 1.0096
1802.8 | 49.5 | 1.0096
1802.9 | 49.5 | 1.0096
1803 | 49.5 | 1.0096
1803.1 | 49.5 | 1.0096
1803.2 | 49.5 | 1.0096
1803.3 | 49.5 | 1.0096
1803.4 | 49.5 | 1.0096
1803.5 | 49.5 | 1.0096
1803.6 | 49.5 | 1.0096
1803.7 | 49.5 | 1.0096
1803.8 | 49.5 | 1.0096
1803.9 | 49.5 | 1.0096
1804 | 49.5 | 1.0096
1804.1 | 49.5 | 1.0096
1804.2 | 49.5 | 1.0096
1804.3 | 49.5 | 1.0096
1804.4 | 49.5 | 1.0096
1804.5 | 49.5 | 1.0096
1804.6 | 49.5 | 1.0096
1804.7 | 49.5 | 1.0096
1804.8 | 49.5 | 1.0096
1804.9 | 49.5 | 1.0096
1805 | 49.5 | 1.0096
1805.1 | 49.5 | 1.0096
1805.2 | 49.5 | 1.0096
1805.3 | 49.5 | 1.0096
1805.4 | 49.5 | 1.0096
1805.5 | 49.5 | 1.0096
1805.6 | 49.5 | 1.0096
1805.7 | 49.5 | 1.0096
1805.8 | 49.5 | 1.0096
1805.9 | 49.5 | 1.0096
1806 | 49.5 | 1.0096
1806.1 | 49.5 | 1.0096
1806.2 | 49.5 | 1.0096
1806.3 | 49.5 | 1.0096
1806.4 | 49.5 | 1.0096
1806.5 | 49.5 | 1.0096
1806.6 | 49.5 | 1.0096
1806.7 | 49.5 | 1.0096
1806.8 | 49.5 | 1.0096
1806.9 | 49.5 | 1.0096
1807 | 49.5 | 1.0096
1807.1 | 49.5 | 1.0096
1807.2 | 49.5 | 1.0096
1807.3 | 49.5 | 1.0096
1807.4 | 49.5 | 1.0096
1807.5 | 49.5 | 1.0096
1807.6 | 49.5 | 1.0096
1807.7 | 49.5 | 1.0096
1807.8 | 49.5 | 1.0096
1807.9 | 49.5 | 1.0096
1808 | 49.5 | 1.0096
1808.1 | 49.5 | 1.0096
1808.2 | 49.5 | 1.0096
1808.3 | 49.5 | 1.0096
1808.4 | 49.5 | 1.0096
1808.5 | 49.5 | 1.0096
1808.6 | 49.5 | 1.0096
1808.7 | 49.5 | 1.0096
1808.8 | 49.5 | 1.0096
1808.9 | 49.5 | 1.0098
1809 | 49.5 | 1.0098
1809.1 | 49.5 | 1.0098
1809.2 | 49.5 | 1.0098
1809.3 | 49.5 | 1.0098
1809.4 | 49.5 | 1.0098
1809.5 | 49.5 | 1.0098
1809.6 | 49.5 | 1.0098
1809.7 | 49.5 | 1.0098
1809.8 | 49.5 | 1.0098
1809.9 | 49.5 | 1.0098
1810 | 49.5 | 1.0098
1810.1 | 49.5 | 1.0096
1810.2 | 49.5 | 1.0096
1810.3 | 49.5 | 1.0096
1810.4 | 49.5 | 1.0096
1810.5 | 49.5 | 1.0096
1810.6 | 49.5 | 1.0096
1810.7 | 49.5 | 1.0096
1810.8 | 49.5 | 1.0096
1810.9 | 49.5 | 1.0096
1811 | 49.5 | 1.0096
1811.1 | 49.5 | 1.0096
1811.2 | 49.5 | 1.0096
1811.3 | 49.5 | 1.0096
1811.4 | 49.5 | 1.0096
1811.5 | 49.5 | 1.0096
1811.6 | 49.5 | 1.0096
1811.7 | 49.5 | 1.0096
1811.8 | 49.5 | 1.0096
1811.9 | 49.5 | 1.0096
1812 | 49.5 | 1.0096
1812.1 | 49.5 | 1.0096
1812.2 | 49.5 | 1.0096
1812.3 | 49.5 | 1.0096
1812.4 | 49.5 | 1.0096
1812.5 | 49.5 | 1.0096
1812.6 | 49.5 | 1.0096
1812.7 | 49.5 | 1.0096
1812.8 | 49.5 | 1.0096
1812.9 | 49.5 | 1.0096
1813 | 49.5 | 1.0096
1813.1 | 49.5 | 1.0096
1813.2 | 49.5 | 1.0096
1813.3 | 49.5 | 1.0096
1813.4 | 49.5 | 1.0096
1813.5 | 49.5 | 1.0096
1813.6 | 49.5 | 1.0096
1813.7 | 49.5 | 1.0096
1813.8 | 49.5 | 1.0096
1813.9 | 49.5 | 1.0096
1814 | 49.5 | 1.0096
1814.1 | 49.5 | 1.0096
1814.2 | 49.5 | 1.0096
1814.3 | 49.5 | 1.0096
1814.4 | 49.5 | 1.0096
1814.5 | 49.5 | 1.0096
1814.6 | 49.5 | 1.0096
1814.7 | 49.5 | 1.0096
1814.8 | 49.5 | 1.0096
1814.9 | 49.5 | 1.0096
1815 | 49.5 | 1.0096
1815.1 | 49.5 | 1.0096
1815.2 | 49.5 | 1.0096
1815.3 | 49.5 | 1.0096
1815.4 | 49.5 | 1.0096
1815.5 | 49.5 | 1.0096
1815.6 | 49.5 | 1.0096
1815.7 | 49.5 | 1.0096
1815.8 | 49.5 | 1.0096
1815.9 | 49.5 | 1.0096
1816 | 49.5 | 1.0096
1816.1 | 49.5 | 1.0096
1816.2 | 49.5 | 1.0096
1816.3 | 49.5 | 1.0096
1816.4 | 49.5 | 1.0096
1816.5 | 49.5 | 1.0096
1816.6 | 49.5 | 1.0096
1816.7 | 49.5 | 1.0096
1816.8 | 49.5 | 1.0096
1816.9 | 49.5 | 1.0096
1817 | 49.5 | 1.0096
1817.1 | 49.5 | 1.0096
1817.2 | 49.5 | 1.0096
1817.3 | 49.5 | 1.0096
1817.4 | 49.5 | 1.0096
1817.5 | 49.5 | 1.0096
1817.6 | 49.5 | 1.0096
1817.7 | 49.5 | 1.0096
1817.8 | 49.5 | 1.0096
1817.9 | 49.5 | 1.0096
1818 | 49.5 | 1.0096
1818.1 | 49.5 | 1.0096
1818.2 | 49.5 | 1.0096
1818.3 | 49.5 | 1.0096
1818.4 | 49.5 | 1.0096
1818.5 | 49.5 | 1.0096
1818.6 | 49.5 | 1.0096
1818.7 | 49.5 | 1.0096
1818.8 | 49.5 | 1.0096
1818.9 | 49.5 | 1.0096
1819 | 49.5 | 1.0096
1819.1 | 49.5 | 1.0096
1819.2 | 49.5 | 1.0096
1819.3 | 49.5 | 1.0096
1819.4 | 49.5 | 1.0096
1819.5 | 49.5 | 1.0096
1819.6 | 49.5 | 1.0096
1819.7 | 49.5 | 1.0096
1819.8 | 49.5 | 1.0096
1819.9 | 49.5 | 1.0096
1820 | 49.5 | 1.0096
1820.1 | 49.5 | 1.0096
1820.2 | 49.5 | 1.0096
1820.3 | 49.5 | 1.0096
1820.4 | 49.5 | 1.0096
1820.5 | 49.5 | 1.0096
1820.6 | 49.5 | 1.0096
1820.7 | 49.5 | 1.0096
1820.8 | 49.5 | 1.0096
1820.9 | 49.5 | 1.0096
1821 | 49.5 | 1.0096
1821.1 | 49.5 | 1.0096
1821.2 | 49.5 | 1.0096
1821.3 | 49.5 | 1.0096
1821.4 | 49.5 | 1.0096
1821.5 | 49.5 | 1.0096
1821.6 | 49.5 | 1.0096
1821.7 | 49.5 | 1.0096
1821.8 | 49.5 | 1.0096
1821.9 | 49.5 | 1.0096
1822 | 49.5 | 1.0096
1822.1 | 49.5 | 1.0096
1822.2 | 49.5 | 1.0096
1822.3 | 49.5 | 1.0096
1822.4 | 49.5 | 1.0096
1822.5 | 49.5 | 1.0096
1822.6 | 49.5 | 1.0096
1822.7 | 49.5 | 1.0096
1822.8 | 49.5 | 1.0096
1822.9 | 49.5 | 1.0096
1823 | 49.5 | 1.0096
1823.1 | 49.5 | 1.0096
1823.2 | 49.5 | 1.0096
1823.3 | 49.5 | 1.0096
1823.4 | 49.5 | 1.0096
1823.5 | 49.5 | 1.0096
1823.6 | 49.5 | 1.0096
1823.7 | 49.5 | 1.0096
1823.8 | 49.5 | 1.0096
1823.9 | 49.5 | 1.0096
1824 | 49.5 | 1.0096
1824.1 | 49.5 | 1.0096
1824.2 | 49.5 | 1.0096
1824.3 | 49.5 | 1.0096
1824.4 | 49.5 | 1.0096
1824.5 | 49.5 | 1.0096
1824.6 | 49.5 | 1.0096
1824.7 | 49.5 | 1.0096
1824.8 | 49.5 | 1.0096
1824.9 | 49.5 | 1.0096
1825 | 49.5 | 1.0096
1825.1 | 49.5 | 1.0096
1825.2 | 49.5 | 1.0096
1825.3 | 49.5 | 1.0096
1825.4 | 49.5 | 1.0096
1825.5 | 49.5 | 1.0096
1825.6 | 49.5 | 1.0096
1825.7 | 49.5 | 1.0096
1825.8 | 49.5 | 1.0096
1825.9 | 49.5 | 1.0096
1826 | 49.5 | 1.0096
1826.1 | 49.5 | 1.0096
1826.2 | 49.5 | 1.0096
1826.3 | 49.5 | 1.0096
1826.4 | 49.5 | 1.0096
1826.5 | 49.5 | 1.0096
1826.6 | 49.5 | 1.0096
1826.7 | 49.5 | 1.0096
1826.8 | 49.5 | 1.0096
1826.9 | 49.5 | 1.0096
1827 | 49.5 | 1.0096
1827.1 | 49.5 | 1.0096
1827.2 | 49.5 | 1.0096
1827.3 | 49.5 | 1.0096
1827.4 | 49.5 | 1.0096
1827.5 | 49.5 | 1.0096
1827.6 | 49.5 | 1.0096
1827.7 | 49.5 | 1.0096
1827.8 | 49.5 | 1.0096
1827.9 | 49.5 | 1.0096
1828 | 49.5 | 1.0096
1828.1 | 49.5 | 1.0096
1828.2 | 49.5 | 1.0096
1828.3 | 49.5 | 1.0096
1828.4 | 49.5 | 1.0096
1828.5 | 49.5 | 1.0096
1828.6 | 49.5 | 1.0096
1828.7 | 49.5 | 1.0096
1828.8 | 49.5 | 1.0096
1828.9 | 49.5 | 1.0096
1829 | 49.5 | 1.0096
1829.1 | 49.5 | 1.0096
1829.2 | 49.5 | 1.0096
1829.3 | 49.5 | 1.0096
1829.4 | 49.5 | 1.0096
1829.5 | 49.5 | 1.0096
1829.6 | 49.5 | 1.0096
1829.7 | 49.5 | 1.0096
1829.8 | 49.5 | 1.0096
1829.9 | 49.5 | 1.0096
1830 | 50 | 1.0096
1830.1 | 50 | 1.0096
1830.2 | 50 | 1.0096
1830.3 | 50 | 1.0096
1830.4 | 50 | 1.0096
1830.5 | 50 | 1.0096
1830.6 | 50 | 1.0096
1830.7 | 50 | 1.0096
1830.8 | 50 | 1.0096
1830.9 | 50 | 1.0096
1831 | 50 | 1.0096
1831.1 | 50 | 1.0096
1831.2 | 50 | 0.9608
1831.3 | 50 | 0.708
1831.4 | 50 | 0.0504
1831.5 | 50 | 0.018
1831.6 | 50 | -0.0024
1831.7 | 50 | -0.0022
1831.8 | 50 | -0.002
1831.9 | 50 | -0.0018
1832 | 50 | -0.0016
1832.1 | 50 | -0.0016
1832.2 | 50 | -0.0016
1832.3 | 50 | -0.0016
1832.4 | 50 | -0.0016
1832.5 | 50 | -0.0016
1832.6 | 50 | -0.0016
1832.7 | 50 | -0.0016
1832.8 | 50 | -0.0016
1832.9 | 50 | -0.0016
1833 | 50 | -0.0014
1833.1 | 50 | -0.0014
1833.2 | 50 | -0.0014
1833.3 | 50 | -0.0014
1833.4 | 50 | -0.0012
1833.5 | 50 | -0.0012
1833.6 | 50 | -0.0012
1833.7 | 50 | -0.001
1833.8 | 50 | -0.001
1833.9 | 50 | -0.001
1834 | 50 | -0.001
1834.1 | 50 | -0.001
1834.2 | 50 | -0.001
1834.3 | 50 | -0.001
1834.4 | 50 | -0.001
1834.5 | 50 | -0.001
1834.6 | 50 | -0.001
1834.7 | 50 | -0.001
1834.8 | 50 | -0.001
1834.9 | 50 | -0.001
1835 | 50 | -0.001
1835.1 | 50 | -0.001
1835.2 | 50 | -0.001
1835.3 | 50 | -0.001
1835.4 | 50 | -0.001
1835.5 | 50 | -0.001
1835.6 | 50 | -0.001
1835.7 | 50 | -0.001
1835.8 | 50 | -0.001
1835.9 | 50 | -0.001
1836 | 50 | -0.001
1836.1 | 50 | -0.001
1836.2 | 50 | -0.0014
1836.3 | 50 | -0.0014
1836.4 | 50 | -0.0012
1836.5 | 50 | -0.0012
1836.6 | 50 | -0.001
1836.7 | 50 | -0.001
1836.8 | 50 | -0.0006
1836.9 | 50 | -0.0004
1837 | 50 | -0.0002
1837.1 | 50 | -0.0002
1837.2 | 50 | -0.0002
1837.3 | 50 | -0.0002
1837.4 | 50 | -0.0002
1837.5 | 50 | -0.0002
1837.6 | 50 | -0.0002
1837.7 | 50 | -0.0002
1837.8 | 50 | -0.0002
1837.9 | 50 | -0.0002
1838 | 50 | -0.0002
1838.1 | 50 | -0.0004
1838.2 | 50 | -0.0002
1838.3 | 50 | -0.0002
1838.4 | 50 | -0.0002
1838.5 | 50 | -0.0002
1838.6 | 50 | -0.0002
1838.7 | 50 | -0.0002
1838.8 | 50 | -0.0002
1838.9 | 50 | -0.0002
1839 | 50 | -0.0002
1839.1 | 50 | -0.0002
1839.2 | 50 | -0.0002
1839.3 | 50 | 0
1839.4 | 50 | 0
1839.5 | 50 | 0
1839.6 | 50 | 0
1839.7 | 50 | 0
1839.8 | 50 | 0
1839.9 | 50 | 0
1840 | 50 | 0
1840.1 | 50 | 0
1840.2 | 50 | 0
1840.3 | 50 | 0
1840.4 | 50 | 0
1840.5 | 50 | 0
1840.6 | 50 | 0
1840.7 | 50 | 0
1840.8 | 50 | 0
1840.9 | 50 | 0
1841 | 50 | 0
1841.1 | 50 | 0
1841.2 | 50 | 0
1841.3 | 50 | 0
1841.4 | 50 | 0
1841.5 | 50 | 0
1841.6 | 50 | 0
1841.7 | 50 | 0
1841.8 | 50 | 0
1841.9 | 50 | 0
1842 | 50 | 0
1842.1 | 50 | 0
1842.2 | 50 | 0
1842.3 | 50 | 0
1842.4 | 50 | 0
1842.5 | 50 | 0
1842.6 | 50 | 0
1842.7 | 50 | 0
1842.8 | 50 | 0
1842.9 | 50 | 0
1843 | 50 | 0
1843.1 | 50 | 0
1843.2 | 50 | 0
1843.3 | 50 | 0
1843.4 | 50 | 0
1843.5 | 50 | 0
1843.6 | 50 | 0
1843.7 | 50 | 0
1843.8 | 50 | 0
1843.9 | 50 | 0
1844 | 50 | 0
1844.1 | 50 | 0
1844.2 | 50 | 0
1844.3 | 50 | 0
1844.4 | 50 | 0
1844.5 | 50 | 0
1844.6 | 50 | 0
1844.7 | 50 | 0
1844.8 | 50 | 0
1844.9 | 50 | 0
1845 | 50 | 0
1845.1 | 50 | 0
1845.2 | 50 | 0
1845.3 | 50 | 0
1845.4 | 50 | 0
1845.5 | 50 | 0
1845.6 | 50 | 0
1845.7 | 50 | 0
1845.8 | 50 | 0
1845.9 | 50 | 0
1846 | 50 | 0
1846.1 | 50 | 0
1846.2 | 50 | 0
1846.3 | 50 | 0
1846.4 | 50 | 0
1846.5 | 50 | 0
1846.6 | 50 | 0
1846.7 | 50 | 0
1846.8 | 50 | 0
1846.9 | 50 | 0
1847 | 50 | 0
1847.1 | 50 | 0
1847.2 | 50 | 0
1847.3 | 50 | 0
1847.4 | 50 | 0
1847.5 | 50 | 0
1847.6 | 50 | 0
1847.7 | 50 | 0
1847.8 | 50 | 0
1847.9 | 50 | 0
1848 | 50 | 0
1848.1 | 50 | 0
1848.2 | 50 | 0
1848.3 | 50 | 0
1848.4 | 50 | 0
1848.5 | 50 | 0
1848.6 | 50 | 0
1848.7 | 50 | 0
1848.8 | 50 | 0
1848.9 | 50 | 0
1849 | 50 | 0
1849.1 | 50 | 0
1849.2 | 50 | 0
1849.3 | 50 | 0
1849.4 | 50 | 0
1849.5 | 50 | 0
1849.6 | 50 | 0
1849.7 | 50 | 0
1849.8 | 50 | 0
1849.9 | 50 | 0
1850 | 50 | 0
1850.1 | 50 | 0
1850.2 | 50 | 0
1850.3 | 50 | 0
1850.4 | 50 | 0
1850.5 | 50 | 0
1850.6 | 50 | 0
1850.7 | 50 | 0
1850.8 | 50 | 0
1850.9 | 50 | 0
1851 | 50 | 0
1851.1 | 50 | 0
1851.2 | 50 | 0
1851.3 | 50 | 0
1851.4 | 50 | 0
1851.5 | 50 | 0
1851.6 | 50 | 0
1851.7 | 50 | 0
1851.8 | 50 | 0
1851.9 | 50 | 0
1852 | 50 | 0
1852.1 | 50 | 0
1852.2 | 50 | 0
1852.3 | 50 | 0
1852.4 | 50 | 0
1852.5 | 50 | 0
1852.6 | 50 | 0
1852.7 | 50 | 0
1852.8 | 50 | 0
1852.9 | 50 | 0
1853 | 50 | 0
1853.1 | 50 | 0
1853.2 | 50 | 0
1853.3 | 50 | 0
1853.4 | 50 | 0
1853.5 | 50 | 0
1853.6 | 50 | 0
1853.7 | 50 | 0
1853.8 | 50 | 0
1853.9 | 50 | 0
1854 | 50 | 0
1854.1 | 50 | 0
1854.2 | 50 | 0
1854.3 | 50 | 0
1854.4 | 50 | 0
1854.5 | 50 | 0
1854.6 | 50 | 0
1854.7 | 50 | 0
1854.8 | 50 | 0
1854.9 | 50 | 0
1855 | 50 | 0
1855.1 | 50 | 0
1855.2 | 50 | 0
1855.3 | 50 | 0
1855.4 | 50 | 0
1855.5 | 50 | 0
1855.6 | 50 | 0
1855.7 | 50 | 0
1855.8 | 50 | 0
1855.9 | 50 | 0
1856 | 50 | 0
1856.1 | 50 | 0
1856.2 | 50 | 0
1856.3 | 50 | 0
1856.4 | 50 | 0
1856.5 | 50 | 0
1856.6 | 50 | 0
1856.7 | 50 | 0
1856.8 | 50 | 0
1856.9 | 50 | 0
1857 | 50 | 0
1857.1 | 50 | 0
1857.2 | 50 | 0
1857.3 | 50 | 0
1857.4 | 50 | 0
1857.5 | 50 | 0
1857.6 | 50 | 0
1857.7 | 50 | 0
1857.8 | 50 | 0
1857.9 | 50 | 0
1858 | 50 | 0
1858.1 | 50 | 0
1858.2 | 50 | 0
1858.3 | 50 | 0
1858.4 | 50 | 0
1858.5 | 50 | 0
1858.6 | 50 | 0
1858.7 | 50 | 0
1858.8 | 50 | 0
1858.9 | 50 | 0
1859 | 50 | 0
1859.1 | 50 | 0
1859.2 | 50 | 0
1859.3 | 50 | 0
1859.4 | 50 | 0
1859.5 | 50 | 0
1859.6 | 50 | 0
1859.7 | 50 | 0
1859.8 | 50 | 0
1859.9 | 50 | 0
Example assumes this asset can sustain maximum response for 30 minutes. It not the case, adjust cell E17 'Secondary End' accordingly and clearly state in test report.
This sheet to be used for single or group of assets e.g. 'NewVol1' which are subgroup of overall test.
In example shown this is a 1MW asset which will be assessed as part of a 5MW Unit.

## Test 1.1 Total
Time (s) | Frequency (Hz) | Active Power (MW)
0 | 50 | 0.001 | Time Value at Which Frequency Changes
0.1 | 50 | 0.001 |  |  |  |  | Frequency Change
0.2 | 50 | 0.001 |  |  |  |  | Primary Start
0.3 | 50 | 0.001 | 30 |  |  |  | Secondary Start
0.4 | 50 | 0.001 |  |  |  |  | 30
0.5 | 50 | 0.001 | Primary Start |  |  |  | 30
0.6 | 50 | 0.001 |  |  |  | $C$402 | 40
0.7 | 50 | 0.001 | 40 |  |  | $C$602 | 40
0.8 | 50 | 0.001 |  |  |  | $C$18301 | 60
0.9 | 50 | 0.001 | Secondary Start |  | primary | 5.047 | 60
1 | 50 | 0.001 |  |  | secondary | 5.047 | 40
1.1 | 50 | 0.001 | 60 |  | SD | 0.0005339 | 60
1.2 | 50 | 0.001 |  |  | % SD | 0.010678 | 2 Second Limit
1.3 | 50 | 0.001 | Secondary End |  |  |  | 32
1.4 | 50 | 0.001 |  | pre-Average | 0.001 |  | 32
1.5 | 50 | 0.001 | 1829.9 | (edit range to average 10s before frequency change)
1.6 | 50 | 0.001
1.7 | 50 | 0.001 | Primary Response
1.8 | 50 | 0.001
1.9 | 50 | 0.001 | 5.046
2 | 50 | 0.001
2.1 | 50 | 0.001 | Secondary Response
2.2 | 50 | 0.001
2.3 | 50 | 0.001 | 5.046
2.4 | 50 | 0.001
2.5 | 50 | 0.001
2.6 | 50 | 0.001
2.7 | 50 | 0.001
2.8 | 50 | 0.001
2.9 | 50 | 0.001
3 | 50 | 0.001
3.1 | 50 | 0.001
3.2 | 50 | 0.001
3.3 | 50 | 0.001
3.4 | 50 | 0.001
3.5 | 50 | 0.001
3.6 | 50 | 0.001
3.7 | 50 | 0.001
3.8 | 50 | 0.001
3.9 | 50 | 0.001
4 | 50 | 0.001
4.1 | 50 | 0.001
4.2 | 50 | 0.001
4.3 | 50 | 0.001
4.4 | 50 | 0.001
4.5 | 50 | 0.001
4.6 | 50 | 0.001
4.7 | 50 | 0.001
4.8 | 50 | 0.001
4.9 | 50 | 0.001
5 | 50 | 0.001
5.1 | 50 | 0.001
5.2 | 50 | 0.001
5.3 | 50 | 0.001
5.4 | 50 | 0.001
5.5 | 50 | 0.001
5.6 | 50 | 0.001
5.7 | 50 | 0.001
5.8 | 50 | 0.001
5.9 | 50 | 0.001
6 | 50 | 0.001
6.1 | 50 | 0.001
6.2 | 50 | 0.001
6.3 | 50 | 0.001
6.4 | 50 | 0.001
6.5 | 50 | 0.001
6.6 | 50 | 0.001
6.7 | 50 | 0.001
6.8 | 50 | 0.001
6.9 | 50 | 0.001
7 | 50 | 0.001
7.1 | 50 | 0.001
7.2 | 50 | 0.001
7.3 | 50 | 0.001
7.4 | 50 | 0.001
7.5 | 50 | 0.001
7.6 | 50 | 0.001
7.7 | 50 | 0.001
7.8 | 50 | 0.001
7.9 | 50 | 0.001
8 | 50 | 0.001
8.1 | 50 | 0.001
8.2 | 50 | 0.001
8.3 | 50 | 0.001
8.4 | 50 | 0.001
8.5 | 50 | 0.001
8.6 | 50 | 0.001
8.7 | 50 | 0.001
8.8 | 50 | 0.001
8.9 | 50 | 0.001
9 | 50 | 0.001
9.1 | 50 | 0.001
9.2 | 50 | 0.001
9.3 | 50 | 0.001
9.4 | 50 | 0.001
9.5 | 50 | 0.001
9.6 | 50 | 0.001
9.7 | 50 | 0.001
9.8 | 50 | 0.001
9.9 | 50 | 0.001
10 | 50 | 0.001
10.1 | 50 | 0.001
10.2 | 50 | 0.001
10.3 | 50 | 0.001
10.4 | 50 | 0.001
10.5 | 50 | 0.001
10.6 | 50 | 0.001
10.7 | 50 | 0.001
10.8 | 50 | 0.001
10.9 | 50 | 0.001
11 | 50 | 0.001
11.1 | 50 | 0.001
11.2 | 50 | 0.001
11.3 | 50 | 0.001
11.4 | 50 | 0.001
11.5 | 50 | 0.001
11.6 | 50 | 0.001
11.7 | 50 | 0.001
11.8 | 50 | 0.001
11.9 | 50 | 0.001
12 | 50 | 0.001
12.1 | 50 | 0.001
12.2 | 50 | 0.001
12.3 | 50 | 0.001
12.4 | 50 | 0.001
12.5 | 50 | 0.001
12.6 | 50 | 0.001
12.7 | 50 | 0.001
12.8 | 50 | 0.001
12.9 | 50 | 0.001
13 | 50 | 0.001
13.1 | 50 | 0.001
13.2 | 50 | 0.001
13.3 | 50 | 0.001
13.4 | 50 | 0.001
13.5 | 50 | 0.001
13.6 | 50 | 0.001
13.7 | 50 | 0.001
13.8 | 50 | 0.001
13.9 | 50 | 0.001
14 | 50 | 0.001
14.1 | 50 | 0.001
14.2 | 50 | 0.001
14.3 | 50 | 0.001
14.4 | 50 | 0.001
14.5 | 50 | 0.001
14.6 | 50 | 0.001
14.7 | 50 | 0.001
14.8 | 50 | 0.001
14.9 | 50 | 0.001
15 | 50 | 0.001
15.1 | 50 | 0.001
15.2 | 50 | 0.001
15.3 | 50 | 0.001
15.4 | 50 | 0.001
15.5 | 50 | 0.001
15.6 | 50 | 0.001
15.7 | 50 | 0.001
15.8 | 50 | 0.001
15.9 | 50 | 0.001
16 | 50 | 0.001
16.1 | 50 | 0.001
16.2 | 50 | 0.001
16.3 | 50 | 0.001
16.4 | 50 | 0.001
16.5 | 50 | 0.001
16.6 | 50 | 0.001
16.7 | 50 | 0.001
16.8 | 50 | 0.001
16.9 | 50 | 0.001
17 | 50 | 0.001
17.1 | 50 | 0.001
17.2 | 50 | 0.001
17.3 | 50 | 0.001
17.4 | 50 | 0.001
17.5 | 50 | 0.001
17.6 | 50 | 0.001
17.7 | 50 | 0.001
17.8 | 50 | 0.001
17.9 | 50 | 0.001
18 | 50 | 0.001
18.1 | 50 | 0.001
18.2 | 50 | 0.001
18.3 | 50 | 0.001
18.4 | 50 | 0.001
18.5 | 50 | 0.001
18.6 | 50 | 0.001
18.7 | 50 | 0.001
18.8 | 50 | 0.001
18.9 | 50 | 0.001
19 | 50 | 0.001
19.1 | 50 | 0.001
19.2 | 50 | 0.001
19.3 | 50 | 0.001
19.4 | 50 | 0.001
19.5 | 50 | 0.001
19.6 | 50 | 0.001
19.7 | 50 | 0.001
19.8 | 50 | 0.001
19.9 | 50 | 0.001
20 | 50 | 0.001
20.1 | 50 | 0.001
20.2 | 50 | 0.001
20.3 | 50 | 0.001
20.4 | 50 | 0.001
20.5 | 50 | 0.001
20.6 | 50 | 0.001
20.7 | 50 | 0.001
20.8 | 50 | 0.001
20.9 | 50 | 0.001
21 | 50 | 0.001
21.1 | 50 | 0.001
21.2 | 50 | 0.001
21.3 | 50 | 0.001
21.4 | 50 | 0.001
21.5 | 50 | 0.001
21.6 | 50 | 0.001
21.7 | 50 | 0.001
21.8 | 50 | 0.001
21.9 | 50 | 0.001
22 | 50 | 0.001
22.1 | 50 | 0.001
22.2 | 50 | 0.001
22.3 | 50 | 0.001
22.4 | 50 | 0.001
22.5 | 50 | 0.001
22.6 | 50 | 0.001
22.7 | 50 | 0.001
22.8 | 50 | 0.001
22.9 | 50 | 0.001
23 | 50 | 0.001
23.1 | 50 | 0.001
23.2 | 50 | 0.001
23.3 | 50 | 0.001
23.4 | 50 | 0.001
23.5 | 50 | 0.001
23.6 | 50 | 0.001
23.7 | 50 | 0.001
23.8 | 50 | 0.001
23.9 | 50 | 0.001
24 | 50 | 0.001
24.1 | 50 | 0.001
24.2 | 50 | 0.001
24.3 | 50 | 0.001
24.4 | 50 | 0.001
24.5 | 50 | 0.001
24.6 | 50 | 0.001
24.7 | 50 | 0.001
24.8 | 50 | 0.001
24.9 | 50 | 0.001
25 | 50 | 0.001
25.1 | 50 | 0.001
25.2 | 50 | 0.001
25.3 | 50 | 0.001
25.4 | 50 | 0.001
25.5 | 50 | 0.001
25.6 | 50 | 0.001
25.7 | 50 | 0.001
25.8 | 50 | 0.001
25.9 | 50 | 0.001
26 | 50 | 0.001
26.1 | 50 | 0.001
26.2 | 50 | 0.001
26.3 | 50 | 0.001
26.4 | 50 | 0.001
26.5 | 50 | 0.001
26.6 | 50 | 0.001
26.7 | 50 | 0.001
26.8 | 50 | 0.001
26.9 | 50 | 0.001
27 | 50 | 0.001
27.1 | 50 | 0.001
27.2 | 50 | 0.001
27.3 | 50 | 0.001
27.4 | 50 | 0.001
27.5 | 50 | 0.001
27.6 | 50 | 0.001
27.7 | 50 | 0.001
27.8 | 50 | 0.001
27.9 | 50 | 0.001
28 | 50 | 0.001
28.1 | 50 | 0.001
28.2 | 50 | 0.001
28.3 | 50 | 0.001
28.4 | 50 | 0.001
28.5 | 50 | 0.001
28.6 | 50 | 0.001
28.7 | 50 | 0.001
28.8 | 50 | 0.001
28.9 | 50 | 0.001
29 | 50 | 0.001
29.1 | 50 | 0.001
29.2 | 50 | 0.001
29.3 | 50 | 0.001
29.4 | 50 | 0.001
29.5 | 50 | 0.001
29.6 | 50 | 0.001
29.7 | 50 | 0.001
29.8 | 50 | 0.001
29.9 | 50 | 0.001
30 | 49.5 | 0.003
30.1 | 49.5 | 0.026
30.2 | 49.5 | 1.41
30.3 | 49.5 | 3.657
30.4 | 49.5 | 4.823
30.5 | 49.5 | 5.108
30.6 | 49.5 | 5.104
30.7 | 49.5 | 5.101
30.8 | 49.5 | 5.1
30.9 | 49.5 | 5.1
31 | 49.5 | 5.1
31.1 | 49.5 | 5.1
31.2 | 49.5 | 5.1
31.3 | 49.5 | 5.1
31.4 | 49.5 | 5.1
31.5 | 49.5 | 5.1
31.6 | 49.5 | 5.1
31.7 | 49.5 | 5.1
31.8 | 49.5 | 5.1
31.9 | 49.5 | 5.1
32 | 49.5 | 5.1
32.1 | 49.5 | 5.1
32.2 | 49.5 | 5.1
32.3 | 49.5 | 5.1
32.4 | 49.5 | 5.1
32.5 | 49.5 | 5.1
32.6 | 49.5 | 5.1
32.7 | 49.5 | 5.1
32.8 | 49.5 | 5.1
32.9 | 49.5 | 5.1
33 | 49.5 | 5.1
33.1 | 49.5 | 5.1
33.2 | 49.5 | 5.1
33.3 | 49.5 | 5.1
33.4 | 49.5 | 5.1
33.5 | 49.5 | 5.1
33.6 | 49.5 | 5.1
33.7 | 49.5 | 5.099
33.8 | 49.5 | 5.099
33.9 | 49.5 | 5.099
34 | 49.5 | 5.1
34.1 | 49.5 | 5.1
34.2 | 49.5 | 5.099
34.3 | 49.5 | 5.099
34.4 | 49.5 | 5.099
34.5 | 49.5 | 5.099
34.6 | 49.5 | 5.099
34.7 | 49.5 | 5.099
34.8 | 49.5 | 5.099
34.9 | 49.5 | 5.099
35 | 49.5 | 5.096
35.1 | 49.5 | 5.088
35.2 | 49.5 | 5.082
35.3 | 49.5 | 5.081
35.4 | 49.5 | 5.081
35.5 | 49.5 | 5.079
35.6 | 49.5 | 5.078
35.7 | 49.5 | 5.078
35.8 | 49.5 | 5.078
35.9 | 49.5 | 5.078
36 | 49.5 | 5.077
36.1 | 49.5 | 5.076
36.2 | 49.5 | 5.075
36.3 | 49.5 | 5.075
36.4 | 49.5 | 5.075
36.5 | 49.5 | 5.075
36.6 | 49.5 | 5.075
36.7 | 49.5 | 5.074
36.8 | 49.5 | 5.074
36.9 | 49.5 | 5.074
37 | 49.5 | 5.073
37.1 | 49.5 | 5.073
37.2 | 49.5 | 5.072
37.3 | 49.5 | 5.072
37.4 | 49.5 | 5.071
37.5 | 49.5 | 5.071
37.6 | 49.5 | 5.071
37.7 | 49.5 | 5.071
37.8 | 49.5 | 5.07
37.9 | 49.5 | 5.07
38 | 49.5 | 5.069
38.1 | 49.5 | 5.069
38.2 | 49.5 | 5.069
38.3 | 49.5 | 5.068
38.4 | 49.5 | 5.068
38.5 | 49.5 | 5.067
38.6 | 49.5 | 5.067
38.7 | 49.5 | 5.067
38.8 | 49.5 | 5.067
38.9 | 49.5 | 5.067
39 | 49.5 | 5.066
39.1 | 49.5 | 5.064
39.2 | 49.5 | 5.063
39.3 | 49.5 | 5.063
39.4 | 49.5 | 5.063
39.5 | 49.5 | 5.063
39.6 | 49.5 | 5.062
39.7 | 49.5 | 5.061
39.8 | 49.5 | 5.061
39.9 | 49.5 | 5.061
40 | 49.5 | 5.061
40.1 | 49.5 | 5.061
40.2 | 49.5 | 5.06
40.3 | 49.5 | 5.06
40.4 | 49.5 | 5.06
40.5 | 49.5 | 5.06
40.6 | 49.5 | 5.059
40.7 | 49.5 | 5.059
40.8 | 49.5 | 5.057
40.9 | 49.5 | 5.057
41 | 49.5 | 5.057
41.1 | 49.5 | 5.057
41.2 | 49.5 | 5.057
41.3 | 49.5 | 5.056
41.4 | 49.5 | 5.056
41.5 | 49.5 | 5.056
41.6 | 49.5 | 5.056
41.7 | 49.5 | 5.056
41.8 | 49.5 | 5.056
41.9 | 49.5 | 5.056
42 | 49.5 | 5.055
42.1 | 49.5 | 5.055
42.2 | 49.5 | 5.055
42.3 | 49.5 | 5.055
42.4 | 49.5 | 5.055
42.5 | 49.5 | 5.054
42.6 | 49.5 | 5.054
42.7 | 49.5 | 5.054
42.8 | 49.5 | 5.052
42.9 | 49.5 | 5.052
43 | 49.5 | 5.052
43.1 | 49.5 | 5.052
43.2 | 49.5 | 5.052
43.3 | 49.5 | 5.052
43.4 | 49.5 | 5.052
43.5 | 49.5 | 5.052
43.6 | 49.5 | 5.052
43.7 | 49.5 | 5.052
43.8 | 49.5 | 5.052
43.9 | 49.5 | 5.052
44 | 49.5 | 5.052
44.1 | 49.5 | 5.052
44.2 | 49.5 | 5.051
44.3 | 49.5 | 5.05
44.4 | 49.5 | 5.05
44.5 | 49.5 | 5.05
44.6 | 49.5 | 5.05
44.7 | 49.5 | 5.05
44.8 | 49.5 | 5.05
44.9 | 49.5 | 5.05
45 | 49.5 | 5.05
45.1 | 49.5 | 5.05
45.2 | 49.5 | 5.05
45.3 | 49.5 | 5.049
45.4 | 49.5 | 5.049
45.5 | 49.5 | 5.049
45.6 | 49.5 | 5.049
45.7 | 49.5 | 5.049
45.8 | 49.5 | 5.049
45.9 | 49.5 | 5.049
46 | 49.5 | 5.049
46.1 | 49.5 | 5.048
46.2 | 49.5 | 5.048
46.3 | 49.5 | 5.048
46.4 | 49.5 | 5.048
46.5 | 49.5 | 5.048
46.6 | 49.5 | 5.048
46.7 | 49.5 | 5.048
46.8 | 49.5 | 5.048
46.9 | 49.5 | 5.048
47 | 49.5 | 5.048
47.1 | 49.5 | 5.048
47.2 | 49.5 | 5.048
47.3 | 49.5 | 5.048
47.4 | 49.5 | 5.048
47.5 | 49.5 | 5.048
47.6 | 49.5 | 5.048
47.7 | 49.5 | 5.048
47.8 | 49.5 | 5.048
47.9 | 49.5 | 5.048
48 | 49.5 | 5.048
48.1 | 49.5 | 5.048
48.2 | 49.5 | 5.048
48.3 | 49.5 | 5.048
48.4 | 49.5 | 5.048
48.5 | 49.5 | 5.048
48.6 | 49.5 | 5.048
48.7 | 49.5 | 5.048
48.8 | 49.5 | 5.048
48.9 | 49.5 | 5.048
49 | 49.5 | 5.048
49.1 | 49.5 | 5.047
49.2 | 49.5 | 5.047
49.3 | 49.5 | 5.047
49.4 | 49.5 | 5.047
49.5 | 49.5 | 5.047
49.6 | 49.5 | 5.047
49.7 | 49.5 | 5.047
49.8 | 49.5 | 5.047
49.9 | 49.5 | 5.047
50 | 49.5 | 5.047
50.1 | 49.5 | 5.047
50.2 | 49.5 | 5.047
50.3 | 49.5 | 5.047
50.4 | 49.5 | 5.047
50.5 | 49.5 | 5.047
50.6 | 49.5 | 5.048
50.7 | 49.5 | 5.048
50.8 | 49.5 | 5.048
50.9 | 49.5 | 5.048
51 | 49.5 | 5.048
51.1 | 49.5 | 5.048
51.2 | 49.5 | 5.048
51.3 | 49.5 | 5.048
51.4 | 49.5 | 5.049
51.5 | 49.5 | 5.049
51.6 | 49.5 | 5.049
51.7 | 49.5 | 5.049
51.8 | 49.5 | 5.049
51.9 | 49.5 | 5.049
52 | 49.5 | 5.049
52.1 | 49.5 | 5.048
52.2 | 49.5 | 5.048
52.3 | 49.5 | 5.048
52.4 | 49.5 | 5.048
52.5 | 49.5 | 5.048
52.6 | 49.5 | 5.049
52.7 | 49.5 | 5.049
52.8 | 49.5 | 5.049
52.9 | 49.5 | 5.049
53 | 49.5 | 5.049
53.1 | 49.5 | 5.049
53.2 | 49.5 | 5.049
53.3 | 49.5 | 5.048
53.4 | 49.5 | 5.048
53.5 | 49.5 | 5.048
53.6 | 49.5 | 5.048
53.7 | 49.5 | 5.048
53.8 | 49.5 | 5.048
53.9 | 49.5 | 5.048
54 | 49.5 | 5.048
54.1 | 49.5 | 5.048
54.2 | 49.5 | 5.048
54.3 | 49.5 | 5.048
54.4 | 49.5 | 5.048
54.5 | 49.5 | 5.048
54.6 | 49.5 | 5.048
54.7 | 49.5 | 5.048
54.8 | 49.5 | 5.048
54.9 | 49.5 | 5.048
55 | 49.5 | 5.048
55.1 | 49.5 | 5.048
55.2 | 49.5 | 5.048
55.3 | 49.5 | 5.048
55.4 | 49.5 | 5.048
55.5 | 49.5 | 5.048
55.6 | 49.5 | 5.049
55.7 | 49.5 | 5.049
55.8 | 49.5 | 5.049
55.9 | 49.5 | 5.049
56 | 49.5 | 5.049
56.1 | 49.5 | 5.049
56.2 | 49.5 | 5.049
56.3 | 49.5 | 5.049
56.4 | 49.5 | 5.049
56.5 | 49.5 | 5.049
56.6 | 49.5 | 5.049
56.7 | 49.5 | 5.049
56.8 | 49.5 | 5.049
56.9 | 49.5 | 5.049
57 | 49.5 | 5.049
57.1 | 49.5 | 5.049
57.2 | 49.5 | 5.049
57.3 | 49.5 | 5.049
57.4 | 49.5 | 5.049
57.5 | 49.5 | 5.049
57.6 | 49.5 | 5.049
57.7 | 49.5 | 5.049
57.8 | 49.5 | 5.049
57.9 | 49.5 | 5.048
58 | 49.5 | 5.048
58.1 | 49.5 | 5.048
58.2 | 49.5 | 5.048
58.3 | 49.5 | 5.048
58.4 | 49.5 | 5.048
58.5 | 49.5 | 5.048
58.6 | 49.5 | 5.048
58.7 | 49.5 | 5.048
58.8 | 49.5 | 5.048
58.9 | 49.5 | 5.048
59 | 49.5 | 5.048
59.1 | 49.5 | 5.048
59.2 | 49.5 | 5.048
59.3 | 49.5 | 5.048
59.4 | 49.5 | 5.048
59.5 | 49.5 | 5.048
59.6 | 49.5 | 5.047
59.7 | 49.5 | 5.047
59.8 | 49.5 | 5.047
59.9 | 49.5 | 5.047
60 | 49.5 | 5.047
60.1 | 49.5 | 5.047
60.2 | 49.5 | 5.047
60.3 | 49.5 | 5.048
60.4 | 49.5 | 5.048
60.5 | 49.5 | 5.048
60.6 | 49.5 | 5.048
60.7 | 49.5 | 5.048
60.8 | 49.5 | 5.048
60.9 | 49.5 | 5.049
61 | 49.5 | 5.049
61.1 | 49.5 | 5.049
61.2 | 49.5 | 5.049
61.3 | 49.5 | 5.049
61.4 | 49.5 | 5.049
61.5 | 49.5 | 5.049
61.6 | 49.5 | 5.049
61.7 | 49.5 | 5.049
61.8 | 49.5 | 5.049
61.9 | 49.5 | 5.049
62 | 49.5 | 5.049
62.1 | 49.5 | 5.049
62.2 | 49.5 | 5.049
62.3 | 49.5 | 5.049
62.4 | 49.5 | 5.049
62.5 | 49.5 | 5.049
62.6 | 49.5 | 5.049
62.7 | 49.5 | 5.049
62.8 | 49.5 | 5.049
62.9 | 49.5 | 5.049
63 | 49.5 | 5.049
63.1 | 49.5 | 5.049
63.2 | 49.5 | 5.049
63.3 | 49.5 | 5.049
63.4 | 49.5 | 5.049
63.5 | 49.5 | 5.049
63.6 | 49.5 | 5.049
63.7 | 49.5 | 5.049
63.8 | 49.5 | 5.049
63.9 | 49.5 | 5.048
64 | 49.5 | 5.048
64.1 | 49.5 | 5.048
64.2 | 49.5 | 5.048
64.3 | 49.5 | 5.048
64.4 | 49.5 | 5.048
64.5 | 49.5 | 5.048
64.6 | 49.5 | 5.048
64.7 | 49.5 | 5.048
64.8 | 49.5 | 5.048
64.9 | 49.5 | 5.048
65 | 49.5 | 5.048
65.1 | 49.5 | 5.048
65.2 | 49.5 | 5.048
65.3 | 49.5 | 5.048
65.4 | 49.5 | 5.047
65.5 | 49.5 | 5.047
65.6 | 49.5 | 5.047
65.7 | 49.5 | 5.047
65.8 | 49.5 | 5.047
65.9 | 49.5 | 5.047
66 | 49.5 | 5.047
66.1 | 49.5 | 5.047
66.2 | 49.5 | 5.048
66.3 | 49.5 | 5.048
66.4 | 49.5 | 5.048
66.5 | 49.5 | 5.048
66.6 | 49.5 | 5.048
66.7 | 49.5 | 5.048
66.8 | 49.5 | 5.048
66.9 | 49.5 | 5.048
67 | 49.5 | 5.048
67.1 | 49.5 | 5.048
67.2 | 49.5 | 5.048
67.3 | 49.5 | 5.048
67.4 | 49.5 | 5.048
67.5 | 49.5 | 5.048
67.6 | 49.5 | 5.048
67.7 | 49.5 | 5.049
67.8 | 49.5 | 5.049
67.9 | 49.5 | 5.049
68 | 49.5 | 5.049
68.1 | 49.5 | 5.049
68.2 | 49.5 | 5.049
68.3 | 49.5 | 5.049
68.4 | 49.5 | 5.049
68.5 | 49.5 | 5.049
68.6 | 49.5 | 5.049
68.7 | 49.5 | 5.049
68.8 | 49.5 | 5.049
68.9 | 49.5 | 5.049
69 | 49.5 | 5.049
69.1 | 49.5 | 5.049
69.2 | 49.5 | 5.049
69.3 | 49.5 | 5.049
69.4 | 49.5 | 5.049
69.5 | 49.5 | 5.049
69.6 | 49.5 | 5.049
69.7 | 49.5 | 5.049
69.8 | 49.5 | 5.049
69.9 | 49.5 | 5.049
70 | 49.5 | 5.048
70.1 | 49.5 | 5.048
70.2 | 49.5 | 5.048
70.3 | 49.5 | 5.048
70.4 | 49.5 | 5.048
70.5 | 49.5 | 5.048
70.6 | 49.5 | 5.048
70.7 | 49.5 | 5.048
70.8 | 49.5 | 5.049
70.9 | 49.5 | 5.049
71 | 49.5 | 5.049
71.1 | 49.5 | 5.049
71.2 | 49.5 | 5.048
71.3 | 49.5 | 5.048
71.4 | 49.5 | 5.048
71.5 | 49.5 | 5.048
71.6 | 49.5 | 5.048
71.7 | 49.5 | 5.048
71.8 | 49.5 | 5.048
71.9 | 49.5 | 5.048
72 | 49.5 | 5.048
72.1 | 49.5 | 5.048
72.2 | 49.5 | 5.048
72.3 | 49.5 | 5.048
72.4 | 49.5 | 5.048
72.5 | 49.5 | 5.048
72.6 | 49.5 | 5.048
72.7 | 49.5 | 5.048
72.8 | 49.5 | 5.048
72.9 | 49.5 | 5.048
73 | 49.5 | 5.048
73.1 | 49.5 | 5.048
73.2 | 49.5 | 5.048
73.3 | 49.5 | 5.048
73.4 | 49.5 | 5.048
73.5 | 49.5 | 5.048
73.6 | 49.5 | 5.048
73.7 | 49.5 | 5.048
73.8 | 49.5 | 5.048
73.9 | 49.5 | 5.048
74 | 49.5 | 5.048
74.1 | 49.5 | 5.048
74.2 | 49.5 | 5.048
74.3 | 49.5 | 5.048
74.4 | 49.5 | 5.048
74.5 | 49.5 | 5.048
74.6 | 49.5 | 5.048
74.7 | 49.5 | 5.048
74.8 | 49.5 | 5.048
74.9 | 49.5 | 5.048
75 | 49.5 | 5.048
75.1 | 49.5 | 5.048
75.2 | 49.5 | 5.048
75.3 | 49.5 | 5.048
75.4 | 49.5 | 5.048
75.5 | 49.5 | 5.048
75.6 | 49.5 | 5.048
75.7 | 49.5 | 5.048
75.8 | 49.5 | 5.048
75.9 | 49.5 | 5.048
76 | 49.5 | 5.048
76.1 | 49.5 | 5.048
76.2 | 49.5 | 5.048
76.3 | 49.5 | 5.048
76.4 | 49.5 | 5.048
76.5 | 49.5 | 5.048
76.6 | 49.5 | 5.048
76.7 | 49.5 | 5.048
76.8 | 49.5 | 5.048
76.9 | 49.5 | 5.048
77 | 49.5 | 5.048
77.1 | 49.5 | 5.048
77.2 | 49.5 | 5.048
77.3 | 49.5 | 5.048
77.4 | 49.5 | 5.048
77.5 | 49.5 | 5.048
77.6 | 49.5 | 5.048
77.7 | 49.5 | 5.048
77.8 | 49.5 | 5.048
77.9 | 49.5 | 5.048
78 | 49.5 | 5.048
78.1 | 49.5 | 5.048
78.2 | 49.5 | 5.048
78.3 | 49.5 | 5.048
78.4 | 49.5 | 5.048
78.5 | 49.5 | 5.048
78.6 | 49.5 | 5.048
78.7 | 49.5 | 5.048
78.8 | 49.5 | 5.048
78.9 | 49.5 | 5.048
79 | 49.5 | 5.048
79.1 | 49.5 | 5.048
79.2 | 49.5 | 5.048
79.3 | 49.5 | 5.048
79.4 | 49.5 | 5.048
79.5 | 49.5 | 5.048
79.6 | 49.5 | 5.048
79.7 | 49.5 | 5.048
79.8 | 49.5 | 5.048
79.9 | 49.5 | 5.048
80 | 49.5 | 5.048
80.1 | 49.5 | 5.048
80.2 | 49.5 | 5.048
80.3 | 49.5 | 5.048
80.4 | 49.5 | 5.048
80.5 | 49.5 | 5.048
80.6 | 49.5 | 5.048
80.7 | 49.5 | 5.048
80.8 | 49.5 | 5.048
80.9 | 49.5 | 5.048
81 | 49.5 | 5.048
81.1 | 49.5 | 5.048
81.2 | 49.5 | 5.048
81.3 | 49.5 | 5.048
81.4 | 49.5 | 5.048
81.5 | 49.5 | 5.048
81.6 | 49.5 | 5.048
81.7 | 49.5 | 5.049
81.8 | 49.5 | 5.049
81.9 | 49.5 | 5.049
82 | 49.5 | 5.049
82.1 | 49.5 | 5.049
82.2 | 49.5 | 5.049
82.3 | 49.5 | 5.049
82.4 | 49.5 | 5.049
82.5 | 49.5 | 5.049
82.6 | 49.5 | 5.049
82.7 | 49.5 | 5.049
82.8 | 49.5 | 5.049
82.9 | 49.5 | 5.049
83 | 49.5 | 5.049
83.1 | 49.5 | 5.049
83.2 | 49.5 | 5.049
83.3 | 49.5 | 5.049
83.4 | 49.5 | 5.049
83.5 | 49.5 | 5.049
83.6 | 49.5 | 5.049
83.7 | 49.5 | 5.049
83.8 | 49.5 | 5.049
83.9 | 49.5 | 5.049
84 | 49.5 | 5.049
84.1 | 49.5 | 5.049
84.2 | 49.5 | 5.049
84.3 | 49.5 | 5.049
84.4 | 49.5 | 5.049
84.5 | 49.5 | 5.049
84.6 | 49.5 | 5.049
84.7 | 49.5 | 5.049
84.8 | 49.5 | 5.049
84.9 | 49.5 | 5.049
85 | 49.5 | 5.049
85.1 | 49.5 | 5.049
85.2 | 49.5 | 5.049
85.3 | 49.5 | 5.049
85.4 | 49.5 | 5.048
85.5 | 49.5 | 5.048
85.6 | 49.5 | 5.048
85.7 | 49.5 | 5.048
85.8 | 49.5 | 5.048
85.9 | 49.5 | 5.048
86 | 49.5 | 5.048
86.1 | 49.5 | 5.048
86.2 | 49.5 | 5.048
86.3 | 49.5 | 5.048
86.4 | 49.5 | 5.048
86.5 | 49.5 | 5.048
86.6 | 49.5 | 5.048
86.7 | 49.5 | 5.048
86.8 | 49.5 | 5.048
86.9 | 49.5 | 5.048
87 | 49.5 | 5.048
87.1 | 49.5 | 5.048
87.2 | 49.5 | 5.048
87.3 | 49.5 | 5.048
87.4 | 49.5 | 5.048
87.5 | 49.5 | 5.048
87.6 | 49.5 | 5.048
87.7 | 49.5 | 5.048
87.8 | 49.5 | 5.048
87.9 | 49.5 | 5.048
88 | 49.5 | 5.048
88.1 | 49.5 | 5.048
88.2 | 49.5 | 5.048
88.3 | 49.5 | 5.048
88.4 | 49.5 | 5.048
88.5 | 49.5 | 5.048
88.6 | 49.5 | 5.048
88.7 | 49.5 | 5.048
88.8 | 49.5 | 5.049
88.9 | 49.5 | 5.049
89 | 49.5 | 5.049
89.1 | 49.5 | 5.049
89.2 | 49.5 | 5.049
89.3 | 49.5 | 5.049
89.4 | 49.5 | 5.049
89.5 | 49.5 | 5.049
89.6 | 49.5 | 5.049
89.7 | 49.5 | 5.049
89.8 | 49.5 | 5.049
89.9 | 49.5 | 5.049
90 | 49.5 | 5.049
90.1 | 49.5 | 5.049
90.2 | 49.5 | 5.049
90.3 | 49.5 | 5.049
90.4 | 49.5 | 5.049
90.5 | 49.5 | 5.049
90.6 | 49.5 | 5.049
90.7 | 49.5 | 5.049
90.8 | 49.5 | 5.049
90.9 | 49.5 | 5.049
91 | 49.5 | 5.049
91.1 | 49.5 | 5.049
91.2 | 49.5 | 5.048
91.3 | 49.5 | 5.048
91.4 | 49.5 | 5.048
91.5 | 49.5 | 5.048
91.6 | 49.5 | 5.048
91.7 | 49.5 | 5.048
91.8 | 49.5 | 5.048
91.9 | 49.5 | 5.048
92 | 49.5 | 5.048
92.1 | 49.5 | 5.048
92.2 | 49.5 | 5.048
92.3 | 49.5 | 5.048
92.4 | 49.5 | 5.048
92.5 | 49.5 | 5.048
92.6 | 49.5 | 5.048
92.7 | 49.5 | 5.048
92.8 | 49.5 | 5.048
92.9 | 49.5 | 5.048
93 | 49.5 | 5.048
93.1 | 49.5 | 5.048
93.2 | 49.5 | 5.048
93.3 | 49.5 | 5.048
93.4 | 49.5 | 5.048
93.5 | 49.5 | 5.048
93.6 | 49.5 | 5.048
93.7 | 49.5 | 5.048
93.8 | 49.5 | 5.048
93.9 | 49.5 | 5.048
94 | 49.5 | 5.048
94.1 | 49.5 | 5.048
94.2 | 49.5 | 5.048
94.3 | 49.5 | 5.048
94.4 | 49.5 | 5.048
94.5 | 49.5 | 5.048
94.6 | 49.5 | 5.048
94.7 | 49.5 | 5.048
94.8 | 49.5 | 5.048
94.9 | 49.5 | 5.048
95 | 49.5 | 5.048
95.1 | 49.5 | 5.048
95.2 | 49.5 | 5.048
95.3 | 49.5 | 5.048
95.4 | 49.5 | 5.048
95.5 | 49.5 | 5.048
95.6 | 49.5 | 5.048
95.7 | 49.5 | 5.048
95.8 | 49.5 | 5.048
95.9 | 49.5 | 5.048
96 | 49.5 | 5.048
96.1 | 49.5 | 5.048
96.2 | 49.5 | 5.048
96.3 | 49.5 | 5.048
96.4 | 49.5 | 5.048
96.5 | 49.5 | 5.048
96.6 | 49.5 | 5.048
96.7 | 49.5 | 5.048
96.8 | 49.5 | 5.048
96.9 | 49.5 | 5.048
97 | 49.5 | 5.048
97.1 | 49.5 | 5.048
97.2 | 49.5 | 5.048
97.3 | 49.5 | 5.048
97.4 | 49.5 | 5.048
97.5 | 49.5 | 5.048
97.6 | 49.5 | 5.048
97.7 | 49.5 | 5.048
97.8 | 49.5 | 5.048
97.9 | 49.5 | 5.048
98 | 49.5 | 5.048
98.1 | 49.5 | 5.048
98.2 | 49.5 | 5.048
98.3 | 49.5 | 5.048
98.4 | 49.5 | 5.048
98.5 | 49.5 | 5.048
98.6 | 49.5 | 5.048
98.7 | 49.5 | 5.048
98.8 | 49.5 | 5.048
98.9 | 49.5 | 5.048
99 | 49.5 | 5.048
99.1 | 49.5 | 5.048
99.2 | 49.5 | 5.048
99.3 | 49.5 | 5.048
99.4 | 49.5 | 5.048
99.5 | 49.5 | 5.048
99.6 | 49.5 | 5.048
99.7 | 49.5 | 5.048
99.8 | 49.5 | 5.048
99.9 | 49.5 | 5.048
100 | 49.5 | 5.048
100.1 | 49.5 | 5.048
100.2 | 49.5 | 5.048
100.3 | 49.5 | 5.048
100.4 | 49.5 | 5.048
100.5 | 49.5 | 5.049
100.6 | 49.5 | 5.049
100.7 | 49.5 | 5.049
100.8 | 49.5 | 5.049
100.9 | 49.5 | 5.049
101 | 49.5 | 5.049
101.1 | 49.5 | 5.049
101.2 | 49.5 | 5.049
101.3 | 49.5 | 5.049
101.4 | 49.5 | 5.049
101.5 | 49.5 | 5.049
101.6 | 49.5 | 5.049
101.7 | 49.5 | 5.049
101.8 | 49.5 | 5.049
101.9 | 49.5 | 5.049
102 | 49.5 | 5.049
102.1 | 49.5 | 5.049
102.2 | 49.5 | 5.049
102.3 | 49.5 | 5.049
102.4 | 49.5 | 5.049
102.5 | 49.5 | 5.049
102.6 | 49.5 | 5.049
102.7 | 49.5 | 5.049
102.8 | 49.5 | 5.049
102.9 | 49.5 | 5.049
103 | 49.5 | 5.049
103.1 | 49.5 | 5.049
103.2 | 49.5 | 5.049
103.3 | 49.5 | 5.049
103.4 | 49.5 | 5.049
103.5 | 49.5 | 5.049
103.6 | 49.5 | 5.048
103.7 | 49.5 | 5.048
103.8 | 49.5 | 5.048
103.9 | 49.5 | 5.048
104 | 49.5 | 5.048
104.1 | 49.5 | 5.048
104.2 | 49.5 | 5.048
104.3 | 49.5 | 5.048
104.4 | 49.5 | 5.048
104.5 | 49.5 | 5.048
104.6 | 49.5 | 5.048
104.7 | 49.5 | 5.048
104.8 | 49.5 | 5.048
104.9 | 49.5 | 5.048
105 | 49.5 | 5.048
105.1 | 49.5 | 5.048
105.2 | 49.5 | 5.048
105.3 | 49.5 | 5.048
105.4 | 49.5 | 5.048
105.5 | 49.5 | 5.048
105.6 | 49.5 | 5.048
105.7 | 49.5 | 5.048
105.8 | 49.5 | 5.048
105.9 | 49.5 | 5.048
106 | 49.5 | 5.048
106.1 | 49.5 | 5.048
106.2 | 49.5 | 5.048
106.3 | 49.5 | 5.048
106.4 | 49.5 | 5.048
106.5 | 49.5 | 5.048
106.6 | 49.5 | 5.048
106.7 | 49.5 | 5.048
106.8 | 49.5 | 5.048
106.9 | 49.5 | 5.048
107 | 49.5 | 5.048
107.1 | 49.5 | 5.048
107.2 | 49.5 | 5.048
107.3 | 49.5 | 5.048
107.4 | 49.5 | 5.048
107.5 | 49.5 | 5.048
107.6 | 49.5 | 5.048
107.7 | 49.5 | 5.048
107.8 | 49.5 | 5.048
107.9 | 49.5 | 5.048
108 | 49.5 | 5.048
108.1 | 49.5 | 5.048
108.2 | 49.5 | 5.048
108.3 | 49.5 | 5.048
108.4 | 49.5 | 5.048
108.5 | 49.5 | 5.048
108.6 | 49.5 | 5.048
108.7 | 49.5 | 5.048
108.8 | 49.5 | 5.048
108.9 | 49.5 | 5.048
109 | 49.5 | 5.048
109.1 | 49.5 | 5.048
109.2 | 49.5 | 5.048
109.3 | 49.5 | 5.048
109.4 | 49.5 | 5.048
109.5 | 49.5 | 5.048
109.6 | 49.5 | 5.048
109.7 | 49.5 | 5.048
109.8 | 49.5 | 5.048
109.9 | 49.5 | 5.049
110 | 49.5 | 5.049
110.1 | 49.5 | 5.049
110.2 | 49.5 | 5.049
110.3 | 49.5 | 5.049
110.4 | 49.5 | 5.049
110.5 | 49.5 | 5.049
110.6 | 49.5 | 5.049
110.7 | 49.5 | 5.049
110.8 | 49.5 | 5.049
110.9 | 49.5 | 5.049
111 | 49.5 | 5.049
111.1 | 49.5 | 5.048
111.2 | 49.5 | 5.048
111.3 | 49.5 | 5.048
111.4 | 49.5 | 5.048
111.5 | 49.5 | 5.048
111.6 | 49.5 | 5.048
111.7 | 49.5 | 5.048
111.8 | 49.5 | 5.048
111.9 | 49.5 | 5.048
112 | 49.5 | 5.048
112.1 | 49.5 | 5.048
112.2 | 49.5 | 5.048
112.3 | 49.5 | 5.048
112.4 | 49.5 | 5.048
112.5 | 49.5 | 5.048
112.6 | 49.5 | 5.048
112.7 | 49.5 | 5.048
112.8 | 49.5 | 5.048
112.9 | 49.5 | 5.048
113 | 49.5 | 5.048
113.1 | 49.5 | 5.048
113.2 | 49.5 | 5.048
113.3 | 49.5 | 5.048
113.4 | 49.5 | 5.048
113.5 | 49.5 | 5.048
113.6 | 49.5 | 5.048
113.7 | 49.5 | 5.048
113.8 | 49.5 | 5.048
113.9 | 49.5 | 5.048
114 | 49.5 | 5.048
114.1 | 49.5 | 5.048
114.2 | 49.5 | 5.048
114.3 | 49.5 | 5.048
114.4 | 49.5 | 5.048
114.5 | 49.5 | 5.048
114.6 | 49.5 | 5.048
114.7 | 49.5 | 5.048
114.8 | 49.5 | 5.048
114.9 | 49.5 | 5.048
115 | 49.5 | 5.048
115.1 | 49.5 | 5.048
115.2 | 49.5 | 5.048
115.3 | 49.5 | 5.048
115.4 | 49.5 | 5.048
115.5 | 49.5 | 5.048
115.6 | 49.5 | 5.048
115.7 | 49.5 | 5.049
115.8 | 49.5 | 5.049
115.9 | 49.5 | 5.049
116 | 49.5 | 5.049
116.1 | 49.5 | 5.049
116.2 | 49.5 | 5.049
116.3 | 49.5 | 5.049
116.4 | 49.5 | 5.049
116.5 | 49.5 | 5.048
116.6 | 49.5 | 5.048
116.7 | 49.5 | 5.048
116.8 | 49.5 | 5.048
116.9 | 49.5 | 5.048
117 | 49.5 | 5.048
117.1 | 49.5 | 5.048
117.2 | 49.5 | 5.048
117.3 | 49.5 | 5.048
117.4 | 49.5 | 5.048
117.5 | 49.5 | 5.048
117.6 | 49.5 | 5.048
117.7 | 49.5 | 5.048
117.8 | 49.5 | 5.048
117.9 | 49.5 | 5.048
118 | 49.5 | 5.048
118.1 | 49.5 | 5.048
118.2 | 49.5 | 5.048
118.3 | 49.5 | 5.048
118.4 | 49.5 | 5.048
118.5 | 49.5 | 5.048
118.6 | 49.5 | 5.048
118.7 | 49.5 | 5.048
118.8 | 49.5 | 5.048
118.9 | 49.5 | 5.048
119 | 49.5 | 5.048
119.1 | 49.5 | 5.048
119.2 | 49.5 | 5.048
119.3 | 49.5 | 5.048
119.4 | 49.5 | 5.048
119.5 | 49.5 | 5.048
119.6 | 49.5 | 5.048
119.7 | 49.5 | 5.048
119.8 | 49.5 | 5.048
119.9 | 49.5 | 5.048
120 | 49.5 | 5.048
120.1 | 49.5 | 5.048
120.2 | 49.5 | 5.048
120.3 | 49.5 | 5.048
120.4 | 49.5 | 5.048
120.5 | 49.5 | 5.048
120.6 | 49.5 | 5.048
120.7 | 49.5 | 5.048
120.8 | 49.5 | 5.048
120.9 | 49.5 | 5.048
121 | 49.5 | 5.048
121.1 | 49.5 | 5.048
121.2 | 49.5 | 5.048
121.3 | 49.5 | 5.048
121.4 | 49.5 | 5.048
121.5 | 49.5 | 5.048
121.6 | 49.5 | 5.048
121.7 | 49.5 | 5.048
121.8 | 49.5 | 5.048
121.9 | 49.5 | 5.048
122 | 49.5 | 5.048
122.1 | 49.5 | 5.048
122.2 | 49.5 | 5.048
122.3 | 49.5 | 5.048
122.4 | 49.5 | 5.048
122.5 | 49.5 | 5.048
122.6 | 49.5 | 5.048
122.7 | 49.5 | 5.048
122.8 | 49.5 | 5.048
122.9 | 49.5 | 5.048
123 | 49.5 | 5.048
123.1 | 49.5 | 5.048
123.2 | 49.5 | 5.048
123.3 | 49.5 | 5.048
123.4 | 49.5 | 5.048
123.5 | 49.5 | 5.048
123.6 | 49.5 | 5.048
123.7 | 49.5 | 5.048
123.8 | 49.5 | 5.048
123.9 | 49.5 | 5.048
124 | 49.5 | 5.048
124.1 | 49.5 | 5.048
124.2 | 49.5 | 5.048
124.3 | 49.5 | 5.048
124.4 | 49.5 | 5.048
124.5 | 49.5 | 5.048
124.6 | 49.5 | 5.048
124.7 | 49.5 | 5.048
124.8 | 49.5 | 5.048
124.9 | 49.5 | 5.048
125 | 49.5 | 5.048
125.1 | 49.5 | 5.048
125.2 | 49.5 | 5.048
125.3 | 49.5 | 5.048
125.4 | 49.5 | 5.048
125.5 | 49.5 | 5.048
125.6 | 49.5 | 5.048
125.7 | 49.5 | 5.048
125.8 | 49.5 | 5.048
125.9 | 49.5 | 5.048
126 | 49.5 | 5.048
126.1 | 49.5 | 5.048
126.2 | 49.5 | 5.048
126.3 | 49.5 | 5.048
126.4 | 49.5 | 5.048
126.5 | 49.5 | 5.048
126.6 | 49.5 | 5.048
126.7 | 49.5 | 5.048
126.8 | 49.5 | 5.048
126.9 | 49.5 | 5.048
127 | 49.5 | 5.048
127.1 | 49.5 | 5.048
127.2 | 49.5 | 5.048
127.3 | 49.5 | 5.048
127.4 | 49.5 | 5.048
127.5 | 49.5 | 5.048
127.6 | 49.5 | 5.048
127.7 | 49.5 | 5.048
127.8 | 49.5 | 5.048
127.9 | 49.5 | 5.048
128 | 49.5 | 5.048
128.1 | 49.5 | 5.048
128.2 | 49.5 | 5.048
128.3 | 49.5 | 5.048
128.4 | 49.5 | 5.048
128.5 | 49.5 | 5.048
128.6 | 49.5 | 5.049
128.7 | 49.5 | 5.049
128.8 | 49.5 | 5.049
128.9 | 49.5 | 5.049
129 | 49.5 | 5.049
129.1 | 49.5 | 5.049
129.2 | 49.5 | 5.049
129.3 | 49.5 | 5.049
129.4 | 49.5 | 5.049
129.5 | 49.5 | 5.049
129.6 | 49.5 | 5.048
129.7 | 49.5 | 5.048
129.8 | 49.5 | 5.048
129.9 | 49.5 | 5.048
130 | 49.5 | 5.048
130.1 | 49.5 | 5.048
130.2 | 49.5 | 5.048
130.3 | 49.5 | 5.048
130.4 | 49.5 | 5.048
130.5 | 49.5 | 5.048
130.6 | 49.5 | 5.048
130.7 | 49.5 | 5.048
130.8 | 49.5 | 5.048
130.9 | 49.5 | 5.048
131 | 49.5 | 5.048
131.1 | 49.5 | 5.048
131.2 | 49.5 | 5.048
131.3 | 49.5 | 5.048
131.4 | 49.5 | 5.048
131.5 | 49.5 | 5.048
131.6 | 49.5 | 5.048
131.7 | 49.5 | 5.048
131.8 | 49.5 | 5.048
131.9 | 49.5 | 5.048
132 | 49.5 | 5.048
132.1 | 49.5 | 5.048
132.2 | 49.5 | 5.049
132.3 | 49.5 | 5.049
132.4 | 49.5 | 5.049
132.5 | 49.5 | 5.049
132.6 | 49.5 | 5.049
132.7 | 49.5 | 5.049
132.8 | 49.5 | 5.049
132.9 | 49.5 | 5.049
133 | 49.5 | 5.049
133.1 | 49.5 | 5.048
133.2 | 49.5 | 5.048
133.3 | 49.5 | 5.048
133.4 | 49.5 | 5.048
133.5 | 49.5 | 5.048
133.6 | 49.5 | 5.048
133.7 | 49.5 | 5.048
133.8 | 49.5 | 5.048
133.9 | 49.5 | 5.048
134 | 49.5 | 5.048
134.1 | 49.5 | 5.048
134.2 | 49.5 | 5.048
134.3 | 49.5 | 5.048
134.4 | 49.5 | 5.048
134.5 | 49.5 | 5.049
134.6 | 49.5 | 5.049
134.7 | 49.5 | 5.049
134.8 | 49.5 | 5.049
134.9 | 49.5 | 5.049
135 | 49.5 | 5.049
135.1 | 49.5 | 5.049
135.2 | 49.5 | 5.049
135.3 | 49.5 | 5.049
135.4 | 49.5 | 5.049
135.5 | 49.5 | 5.049
135.6 | 49.5 | 5.048
135.7 | 49.5 | 5.048
135.8 | 49.5 | 5.048
135.9 | 49.5 | 5.048
136 | 49.5 | 5.048
136.1 | 49.5 | 5.048
136.2 | 49.5 | 5.048
136.3 | 49.5 | 5.048
136.4 | 49.5 | 5.048
136.5 | 49.5 | 5.048
136.6 | 49.5 | 5.048
136.7 | 49.5 | 5.048
136.8 | 49.5 | 5.048
136.9 | 49.5 | 5.048
137 | 49.5 | 5.048
137.1 | 49.5 | 5.048
137.2 | 49.5 | 5.048
137.3 | 49.5 | 5.048
137.4 | 49.5 | 5.048
137.5 | 49.5 | 5.048
137.6 | 49.5 | 5.048
137.7 | 49.5 | 5.048
137.8 | 49.5 | 5.048
137.9 | 49.5 | 5.048
138 | 49.5 | 5.048
138.1 | 49.5 | 5.048
138.2 | 49.5 | 5.048
138.3 | 49.5 | 5.048
138.4 | 49.5 | 5.048
138.5 | 49.5 | 5.048
138.6 | 49.5 | 5.048
138.7 | 49.5 | 5.048
138.8 | 49.5 | 5.048
138.9 | 49.5 | 5.048
139 | 49.5 | 5.048
139.1 | 49.5 | 5.048
139.2 | 49.5 | 5.048
139.3 | 49.5 | 5.048
139.4 | 49.5 | 5.048
139.5 | 49.5 | 5.048
139.6 | 49.5 | 5.048
139.7 | 49.5 | 5.048
139.8 | 49.5 | 5.048
139.9 | 49.5 | 5.048
140 | 49.5 | 5.048
140.1 | 49.5 | 5.048
140.2 | 49.5 | 5.048
140.3 | 49.5 | 5.049
140.4 | 49.5 | 5.049
140.5 | 49.5 | 5.049
140.6 | 49.5 | 5.049
140.7 | 49.5 | 5.049
140.8 | 49.5 | 5.049
140.9 | 49.5 | 5.049
141 | 49.5 | 5.049
141.1 | 49.5 | 5.049
141.2 | 49.5 | 5.049
141.3 | 49.5 | 5.049
141.4 | 49.5 | 5.049
141.5 | 49.5 | 5.048
141.6 | 49.5 | 5.048
141.7 | 49.5 | 5.048
141.8 | 49.5 | 5.048
141.9 | 49.5 | 5.048
142 | 49.5 | 5.048
142.1 | 49.5 | 5.048
142.2 | 49.5 | 5.048
142.3 | 49.5 | 5.048
142.4 | 49.5 | 5.048
142.5 | 49.5 | 5.048
142.6 | 49.5 | 5.048
142.7 | 49.5 | 5.048
142.8 | 49.5 | 5.048
142.9 | 49.5 | 5.048
143 | 49.5 | 5.048
143.1 | 49.5 | 5.048
143.2 | 49.5 | 5.048
143.3 | 49.5 | 5.048
143.4 | 49.5 | 5.048
143.5 | 49.5 | 5.048
143.6 | 49.5 | 5.048
143.7 | 49.5 | 5.048
143.8 | 49.5 | 5.048
143.9 | 49.5 | 5.048
144 | 49.5 | 5.048
144.1 | 49.5 | 5.048
144.2 | 49.5 | 5.048
144.3 | 49.5 | 5.048
144.4 | 49.5 | 5.048
144.5 | 49.5 | 5.048
144.6 | 49.5 | 5.048
144.7 | 49.5 | 5.048
144.8 | 49.5 | 5.048
144.9 | 49.5 | 5.048
145 | 49.5 | 5.048
145.1 | 49.5 | 5.048
145.2 | 49.5 | 5.048
145.3 | 49.5 | 5.048
145.4 | 49.5 | 5.048
145.5 | 49.5 | 5.048
145.6 | 49.5 | 5.048
145.7 | 49.5 | 5.048
145.8 | 49.5 | 5.048
145.9 | 49.5 | 5.048
146 | 49.5 | 5.048
146.1 | 49.5 | 5.048
146.2 | 49.5 | 5.048
146.3 | 49.5 | 5.048
146.4 | 49.5 | 5.048
146.5 | 49.5 | 5.048
146.6 | 49.5 | 5.048
146.7 | 49.5 | 5.048
146.8 | 49.5 | 5.048
146.9 | 49.5 | 5.048
147 | 49.5 | 5.048
147.1 | 49.5 | 5.048
147.2 | 49.5 | 5.048
147.3 | 49.5 | 5.048
147.4 | 49.5 | 5.048
147.5 | 49.5 | 5.048
147.6 | 49.5 | 5.048
147.7 | 49.5 | 5.048
147.8 | 49.5 | 5.048
147.9 | 49.5 | 5.048
148 | 49.5 | 5.048
148.1 | 49.5 | 5.048
148.2 | 49.5 | 5.048
148.3 | 49.5 | 5.048
148.4 | 49.5 | 5.048
148.5 | 49.5 | 5.048
148.6 | 49.5 | 5.048
148.7 | 49.5 | 5.048
148.8 | 49.5 | 5.048
148.9 | 49.5 | 5.048
149 | 49.5 | 5.048
149.1 | 49.5 | 5.048
149.2 | 49.5 | 5.048
149.3 | 49.5 | 5.048
149.4 | 49.5 | 5.048
149.5 | 49.5 | 5.048
149.6 | 49.5 | 5.048
149.7 | 49.5 | 5.049
149.8 | 49.5 | 5.049
149.9 | 49.5 | 5.049
150 | 49.5 | 5.049
150.1 | 49.5 | 5.049
150.2 | 49.5 | 5.049
150.3 | 49.5 | 5.049
150.4 | 49.5 | 5.048
150.5 | 49.5 | 5.048
150.6 | 49.5 | 5.048
150.7 | 49.5 | 5.048
150.8 | 49.5 | 5.048
150.9 | 49.5 | 5.048
151 | 49.5 | 5.048
151.1 | 49.5 | 5.048
151.2 | 49.5 | 5.048
151.3 | 49.5 | 5.048
151.4 | 49.5 | 5.048
151.5 | 49.5 | 5.048
151.6 | 49.5 | 5.048
151.7 | 49.5 | 5.048
151.8 | 49.5 | 5.048
151.9 | 49.5 | 5.048
152 | 49.5 | 5.048
152.1 | 49.5 | 5.048
152.2 | 49.5 | 5.048
152.3 | 49.5 | 5.048
152.4 | 49.5 | 5.048
152.5 | 49.5 | 5.048
152.6 | 49.5 | 5.048
152.7 | 49.5 | 5.048
152.8 | 49.5 | 5.048
152.9 | 49.5 | 5.048
153 | 49.5 | 5.048
153.1 | 49.5 | 5.048
153.2 | 49.5 | 5.048
153.3 | 49.5 | 5.048
153.4 | 49.5 | 5.048
153.5 | 49.5 | 5.048
153.6 | 49.5 | 5.048
153.7 | 49.5 | 5.048
153.8 | 49.5 | 5.048
153.9 | 49.5 | 5.048
154 | 49.5 | 5.048
154.1 | 49.5 | 5.048
154.2 | 49.5 | 5.048
154.3 | 49.5 | 5.048
154.4 | 49.5 | 5.048
154.5 | 49.5 | 5.048
154.6 | 49.5 | 5.048
154.7 | 49.5 | 5.048
154.8 | 49.5 | 5.048
154.9 | 49.5 | 5.048
155 | 49.5 | 5.048
155.1 | 49.5 | 5.048
155.2 | 49.5 | 5.048
155.3 | 49.5 | 5.048
155.4 | 49.5 | 5.048
155.5 | 49.5 | 5.048
155.6 | 49.5 | 5.048
155.7 | 49.5 | 5.048
155.8 | 49.5 | 5.048
155.9 | 49.5 | 5.048
156 | 49.5 | 5.048
156.1 | 49.5 | 5.048
156.2 | 49.5 | 5.048
156.3 | 49.5 | 5.048
156.4 | 49.5 | 5.048
156.5 | 49.5 | 5.048
156.6 | 49.5 | 5.048
156.7 | 49.5 | 5.048
156.8 | 49.5 | 5.048
156.9 | 49.5 | 5.048
157 | 49.5 | 5.048
157.1 | 49.5 | 5.048
157.2 | 49.5 | 5.048
157.3 | 49.5 | 5.048
157.4 | 49.5 | 5.048
157.5 | 49.5 | 5.048
157.6 | 49.5 | 5.048
157.7 | 49.5 | 5.048
157.8 | 49.5 | 5.048
157.9 | 49.5 | 5.048
158 | 49.5 | 5.048
158.1 | 49.5 | 5.048
158.2 | 49.5 | 5.048
158.3 | 49.5 | 5.048
158.4 | 49.5 | 5.048
158.5 | 49.5 | 5.048
158.6 | 49.5 | 5.048
158.7 | 49.5 | 5.048
158.8 | 49.5 | 5.048
158.9 | 49.5 | 5.048
159 | 49.5 | 5.048
159.1 | 49.5 | 5.048
159.2 | 49.5 | 5.048
159.3 | 49.5 | 5.048
159.4 | 49.5 | 5.048
159.5 | 49.5 | 5.048
159.6 | 49.5 | 5.048
159.7 | 49.5 | 5.048
159.8 | 49.5 | 5.048
159.9 | 49.5 | 5.048
160 | 49.5 | 5.048
160.1 | 49.5 | 5.048
160.2 | 49.5 | 5.048
160.3 | 49.5 | 5.048
160.4 | 49.5 | 5.048
160.5 | 49.5 | 5.048
160.6 | 49.5 | 5.048
160.7 | 49.5 | 5.048
160.8 | 49.5 | 5.048
160.9 | 49.5 | 5.048
161 | 49.5 | 5.048
161.1 | 49.5 | 5.048
161.2 | 49.5 | 5.048
161.3 | 49.5 | 5.048
161.4 | 49.5 | 5.048
161.5 | 49.5 | 5.048
161.6 | 49.5 | 5.048
161.7 | 49.5 | 5.048
161.8 | 49.5 | 5.048
161.9 | 49.5 | 5.048
162 | 49.5 | 5.048
162.1 | 49.5 | 5.048
162.2 | 49.5 | 5.048
162.3 | 49.5 | 5.048
162.4 | 49.5 | 5.048
162.5 | 49.5 | 5.048
162.6 | 49.5 | 5.048
162.7 | 49.5 | 5.048
162.8 | 49.5 | 5.048
162.9 | 49.5 | 5.048
163 | 49.5 | 5.048
163.1 | 49.5 | 5.048
163.2 | 49.5 | 5.048
163.3 | 49.5 | 5.048
163.4 | 49.5 | 5.048
163.5 | 49.5 | 5.048
163.6 | 49.5 | 5.048
163.7 | 49.5 | 5.048
163.8 | 49.5 | 5.048
163.9 | 49.5 | 5.048
164 | 49.5 | 5.048
164.1 | 49.5 | 5.048
164.2 | 49.5 | 5.048
164.3 | 49.5 | 5.048
164.4 | 49.5 | 5.048
164.5 | 49.5 | 5.048
164.6 | 49.5 | 5.048
164.7 | 49.5 | 5.048
164.8 | 49.5 | 5.048
164.9 | 49.5 | 5.048
165 | 49.5 | 5.048
165.1 | 49.5 | 5.048
165.2 | 49.5 | 5.048
165.3 | 49.5 | 5.048
165.4 | 49.5 | 5.048
165.5 | 49.5 | 5.048
165.6 | 49.5 | 5.048
165.7 | 49.5 | 5.048
165.8 | 49.5 | 5.048
165.9 | 49.5 | 5.048
166 | 49.5 | 5.048
166.1 | 49.5 | 5.048
166.2 | 49.5 | 5.048
166.3 | 49.5 | 5.048
166.4 | 49.5 | 5.048
166.5 | 49.5 | 5.048
166.6 | 49.5 | 5.048
166.7 | 49.5 | 5.048
166.8 | 49.5 | 5.048
166.9 | 49.5 | 5.048
167 | 49.5 | 5.048
167.1 | 49.5 | 5.048
167.2 | 49.5 | 5.048
167.3 | 49.5 | 5.048
167.4 | 49.5 | 5.048
167.5 | 49.5 | 5.048
167.6 | 49.5 | 5.048
167.7 | 49.5 | 5.048
167.8 | 49.5 | 5.048
167.9 | 49.5 | 5.048
168 | 49.5 | 5.048
168.1 | 49.5 | 5.048
168.2 | 49.5 | 5.048
168.3 | 49.5 | 5.048
168.4 | 49.5 | 5.048
168.5 | 49.5 | 5.048
168.6 | 49.5 | 5.048
168.7 | 49.5 | 5.048
168.8 | 49.5 | 5.048
168.9 | 49.5 | 5.048
169 | 49.5 | 5.048
169.1 | 49.5 | 5.048
169.2 | 49.5 | 5.048
169.3 | 49.5 | 5.048
169.4 | 49.5 | 5.048
169.5 | 49.5 | 5.048
169.6 | 49.5 | 5.048
169.7 | 49.5 | 5.048
169.8 | 49.5 | 5.048
169.9 | 49.5 | 5.048
170 | 49.5 | 5.048
170.1 | 49.5 | 5.048
170.2 | 49.5 | 5.048
170.3 | 49.5 | 5.048
170.4 | 49.5 | 5.048
170.5 | 49.5 | 5.048
170.6 | 49.5 | 5.048
170.7 | 49.5 | 5.048
170.8 | 49.5 | 5.048
170.9 | 49.5 | 5.048
171 | 49.5 | 5.048
171.1 | 49.5 | 5.048
171.2 | 49.5 | 5.048
171.3 | 49.5 | 5.048
171.4 | 49.5 | 5.048
171.5 | 49.5 | 5.048
171.6 | 49.5 | 5.048
171.7 | 49.5 | 5.048
171.8 | 49.5 | 5.048
171.9 | 49.5 | 5.048
172 | 49.5 | 5.048
172.1 | 49.5 | 5.048
172.2 | 49.5 | 5.048
172.3 | 49.5 | 5.048
172.4 | 49.5 | 5.048
172.5 | 49.5 | 5.048
172.6 | 49.5 | 5.048
172.7 | 49.5 | 5.048
172.8 | 49.5 | 5.048
172.9 | 49.5 | 5.048
173 | 49.5 | 5.048
173.1 | 49.5 | 5.048
173.2 | 49.5 | 5.048
173.3 | 49.5 | 5.048
173.4 | 49.5 | 5.048
173.5 | 49.5 | 5.048
173.6 | 49.5 | 5.048
173.7 | 49.5 | 5.048
173.8 | 49.5 | 5.048
173.9 | 49.5 | 5.048
174 | 49.5 | 5.048
174.1 | 49.5 | 5.048
174.2 | 49.5 | 5.048
174.3 | 49.5 | 5.048
174.4 | 49.5 | 5.048
174.5 | 49.5 | 5.048
174.6 | 49.5 | 5.048
174.7 | 49.5 | 5.048
174.8 | 49.5 | 5.048
174.9 | 49.5 | 5.048
175 | 49.5 | 5.048
175.1 | 49.5 | 5.048
175.2 | 49.5 | 5.048
175.3 | 49.5 | 5.048
175.4 | 49.5 | 5.048
175.5 | 49.5 | 5.048
175.6 | 49.5 | 5.048
175.7 | 49.5 | 5.048
175.8 | 49.5 | 5.048
175.9 | 49.5 | 5.048
176 | 49.5 | 5.048
176.1 | 49.5 | 5.048
176.2 | 49.5 | 5.048
176.3 | 49.5 | 5.048
176.4 | 49.5 | 5.048
176.5 | 49.5 | 5.048
176.6 | 49.5 | 5.048
176.7 | 49.5 | 5.048
176.8 | 49.5 | 5.048
176.9 | 49.5 | 5.048
177 | 49.5 | 5.048
177.1 | 49.5 | 5.048
177.2 | 49.5 | 5.048
177.3 | 49.5 | 5.048
177.4 | 49.5 | 5.048
177.5 | 49.5 | 5.048
177.6 | 49.5 | 5.048
177.7 | 49.5 | 5.048
177.8 | 49.5 | 5.048
177.9 | 49.5 | 5.048
178 | 49.5 | 5.048
178.1 | 49.5 | 5.048
178.2 | 49.5 | 5.048
178.3 | 49.5 | 5.048
178.4 | 49.5 | 5.048
178.5 | 49.5 | 5.048
178.6 | 49.5 | 5.048
178.7 | 49.5 | 5.048
178.8 | 49.5 | 5.048
178.9 | 49.5 | 5.048
179 | 49.5 | 5.048
179.1 | 49.5 | 5.048
179.2 | 49.5 | 5.048
179.3 | 49.5 | 5.048
179.4 | 49.5 | 5.048
179.5 | 49.5 | 5.048
179.6 | 49.5 | 5.048
179.7 | 49.5 | 5.048
179.8 | 49.5 | 5.048
179.9 | 49.5 | 5.048
180 | 49.5 | 5.048
180.1 | 49.5 | 5.048
180.2 | 49.5 | 5.048
180.3 | 49.5 | 5.048
180.4 | 49.5 | 5.048
180.5 | 49.5 | 5.048
180.6 | 49.5 | 5.048
180.7 | 49.5 | 5.048
180.8 | 49.5 | 5.048
180.9 | 49.5 | 5.048
181 | 49.5 | 5.048
181.1 | 49.5 | 5.048
181.2 | 49.5 | 5.048
181.3 | 49.5 | 5.048
181.4 | 49.5 | 5.048
181.5 | 49.5 | 5.048
181.6 | 49.5 | 5.048
181.7 | 49.5 | 5.048
181.8 | 49.5 | 5.048
181.9 | 49.5 | 5.048
182 | 49.5 | 5.048
182.1 | 49.5 | 5.048
182.2 | 49.5 | 5.048
182.3 | 49.5 | 5.048
182.4 | 49.5 | 5.048
182.5 | 49.5 | 5.048
182.6 | 49.5 | 5.048
182.7 | 49.5 | 5.048
182.8 | 49.5 | 5.048
182.9 | 49.5 | 5.048
183 | 49.5 | 5.048
183.1 | 49.5 | 5.048
183.2 | 49.5 | 5.048
183.3 | 49.5 | 5.048
183.4 | 49.5 | 5.048
183.5 | 49.5 | 5.048
183.6 | 49.5 | 5.048
183.7 | 49.5 | 5.048
183.8 | 49.5 | 5.048
183.9 | 49.5 | 5.048
184 | 49.5 | 5.048
184.1 | 49.5 | 5.048
184.2 | 49.5 | 5.048
184.3 | 49.5 | 5.048
184.4 | 49.5 | 5.048
184.5 | 49.5 | 5.048
184.6 | 49.5 | 5.048
184.7 | 49.5 | 5.048
184.8 | 49.5 | 5.048
184.9 | 49.5 | 5.048
185 | 49.5 | 5.048
185.1 | 49.5 | 5.048
185.2 | 49.5 | 5.048
185.3 | 49.5 | 5.048
185.4 | 49.5 | 5.048
185.5 | 49.5 | 5.048
185.6 | 49.5 | 5.048
185.7 | 49.5 | 5.048
185.8 | 49.5 | 5.048
185.9 | 49.5 | 5.048
186 | 49.5 | 5.048
186.1 | 49.5 | 5.048
186.2 | 49.5 | 5.048
186.3 | 49.5 | 5.048
186.4 | 49.5 | 5.048
186.5 | 49.5 | 5.048
186.6 | 49.5 | 5.048
186.7 | 49.5 | 5.048
186.8 | 49.5 | 5.048
186.9 | 49.5 | 5.048
187 | 49.5 | 5.048
187.1 | 49.5 | 5.048
187.2 | 49.5 | 5.048
187.3 | 49.5 | 5.048
187.4 | 49.5 | 5.048
187.5 | 49.5 | 5.048
187.6 | 49.5 | 5.048
187.7 | 49.5 | 5.048
187.8 | 49.5 | 5.048
187.9 | 49.5 | 5.048
188 | 49.5 | 5.048
188.1 | 49.5 | 5.048
188.2 | 49.5 | 5.048
188.3 | 49.5 | 5.048
188.4 | 49.5 | 5.048
188.5 | 49.5 | 5.048
188.6 | 49.5 | 5.048
188.7 | 49.5 | 5.048
188.8 | 49.5 | 5.048
188.9 | 49.5 | 5.048
189 | 49.5 | 5.048
189.1 | 49.5 | 5.048
189.2 | 49.5 | 5.048
189.3 | 49.5 | 5.048
189.4 | 49.5 | 5.048
189.5 | 49.5 | 5.048
189.6 | 49.5 | 5.048
189.7 | 49.5 | 5.048
189.8 | 49.5 | 5.048
189.9 | 49.5 | 5.048
190 | 49.5 | 5.048
190.1 | 49.5 | 5.048
190.2 | 49.5 | 5.048
190.3 | 49.5 | 5.048
190.4 | 49.5 | 5.048
190.5 | 49.5 | 5.048
190.6 | 49.5 | 5.048
190.7 | 49.5 | 5.048
190.8 | 49.5 | 5.048
190.9 | 49.5 | 5.048
191 | 49.5 | 5.048
191.1 | 49.5 | 5.048
191.2 | 49.5 | 5.048
191.3 | 49.5 | 5.048
191.4 | 49.5 | 5.048
191.5 | 49.5 | 5.048
191.6 | 49.5 | 5.048
191.7 | 49.5 | 5.048
191.8 | 49.5 | 5.048
191.9 | 49.5 | 5.048
192 | 49.5 | 5.048
192.1 | 49.5 | 5.048
192.2 | 49.5 | 5.048
192.3 | 49.5 | 5.048
192.4 | 49.5 | 5.048
192.5 | 49.5 | 5.048
192.6 | 49.5 | 5.048
192.7 | 49.5 | 5.048
192.8 | 49.5 | 5.048
192.9 | 49.5 | 5.048
193 | 49.5 | 5.048
193.1 | 49.5 | 5.048
193.2 | 49.5 | 5.048
193.3 | 49.5 | 5.048
193.4 | 49.5 | 5.048
193.5 | 49.5 | 5.048
193.6 | 49.5 | 5.048
193.7 | 49.5 | 5.048
193.8 | 49.5 | 5.048
193.9 | 49.5 | 5.048
194 | 49.5 | 5.048
194.1 | 49.5 | 5.049
194.2 | 49.5 | 5.049
194.3 | 49.5 | 5.049
194.4 | 49.5 | 5.049
194.5 | 49.5 | 5.049
194.6 | 49.5 | 5.049
194.7 | 49.5 | 5.049
194.8 | 49.5 | 5.049
194.9 | 49.5 | 5.049
195 | 49.5 | 5.049
195.1 | 49.5 | 5.049
195.2 | 49.5 | 5.049
195.3 | 49.5 | 5.049
195.4 | 49.5 | 5.049
195.5 | 49.5 | 5.049
195.6 | 49.5 | 5.049
195.7 | 49.5 | 5.049
195.8 | 49.5 | 5.049
195.9 | 49.5 | 5.049
196 | 49.5 | 5.049
196.1 | 49.5 | 5.049
196.2 | 49.5 | 5.049
196.3 | 49.5 | 5.049
196.4 | 49.5 | 5.048
196.5 | 49.5 | 5.048
196.6 | 49.5 | 5.048
196.7 | 49.5 | 5.048
196.8 | 49.5 | 5.048
196.9 | 49.5 | 5.048
197 | 49.5 | 5.048
197.1 | 49.5 | 5.048
197.2 | 49.5 | 5.048
197.3 | 49.5 | 5.048
197.4 | 49.5 | 5.048
197.5 | 49.5 | 5.048
197.6 | 49.5 | 5.048
197.7 | 49.5 | 5.048
197.8 | 49.5 | 5.048
197.9 | 49.5 | 5.048
198 | 49.5 | 5.048
198.1 | 49.5 | 5.048
198.2 | 49.5 | 5.048
198.3 | 49.5 | 5.048
198.4 | 49.5 | 5.048
198.5 | 49.5 | 5.048
198.6 | 49.5 | 5.048
198.7 | 49.5 | 5.048
198.8 | 49.5 | 5.048
198.9 | 49.5 | 5.048
199 | 49.5 | 5.048
199.1 | 49.5 | 5.048
199.2 | 49.5 | 5.048
199.3 | 49.5 | 5.048
199.4 | 49.5 | 5.048
199.5 | 49.5 | 5.048
199.6 | 49.5 | 5.048
199.7 | 49.5 | 5.048
199.8 | 49.5 | 5.048
199.9 | 49.5 | 5.048
200 | 49.5 | 5.048
200.1 | 49.5 | 5.048
200.2 | 49.5 | 5.048
200.3 | 49.5 | 5.048
200.4 | 49.5 | 5.048
200.5 | 49.5 | 5.048
200.6 | 49.5 | 5.048
200.7 | 49.5 | 5.048
200.8 | 49.5 | 5.048
200.9 | 49.5 | 5.048
201 | 49.5 | 5.048
201.1 | 49.5 | 5.048
201.2 | 49.5 | 5.048
201.3 | 49.5 | 5.048
201.4 | 49.5 | 5.048
201.5 | 49.5 | 5.048
201.6 | 49.5 | 5.048
201.7 | 49.5 | 5.048
201.8 | 49.5 | 5.048
201.9 | 49.5 | 5.048
202 | 49.5 | 5.048
202.1 | 49.5 | 5.048
202.2 | 49.5 | 5.048
202.3 | 49.5 | 5.048
202.4 | 49.5 | 5.048
202.5 | 49.5 | 5.048
202.6 | 49.5 | 5.048
202.7 | 49.5 | 5.048
202.8 | 49.5 | 5.048
202.9 | 49.5 | 5.048
203 | 49.5 | 5.048
203.1 | 49.5 | 5.048
203.2 | 49.5 | 5.048
203.3 | 49.5 | 5.048
203.4 | 49.5 | 5.048
203.5 | 49.5 | 5.048
203.6 | 49.5 | 5.048
203.7 | 49.5 | 5.048
203.8 | 49.5 | 5.048
203.9 | 49.5 | 5.048
204 | 49.5 | 5.048
204.1 | 49.5 | 5.048
204.2 | 49.5 | 5.048
204.3 | 49.5 | 5.048
204.4 | 49.5 | 5.048
204.5 | 49.5 | 5.048
204.6 | 49.5 | 5.048
204.7 | 49.5 | 5.048
204.8 | 49.5 | 5.048
204.9 | 49.5 | 5.048
205 | 49.5 | 5.048
205.1 | 49.5 | 5.048
205.2 | 49.5 | 5.048
205.3 | 49.5 | 5.048
205.4 | 49.5 | 5.048
205.5 | 49.5 | 5.048
205.6 | 49.5 | 5.048
205.7 | 49.5 | 5.048
205.8 | 49.5 | 5.048
205.9 | 49.5 | 5.048
206 | 49.5 | 5.048
206.1 | 49.5 | 5.048
206.2 | 49.5 | 5.048
206.3 | 49.5 | 5.048
206.4 | 49.5 | 5.048
206.5 | 49.5 | 5.048
206.6 | 49.5 | 5.048
206.7 | 49.5 | 5.048
206.8 | 49.5 | 5.048
206.9 | 49.5 | 5.048
207 | 49.5 | 5.048
207.1 | 49.5 | 5.048
207.2 | 49.5 | 5.048
207.3 | 49.5 | 5.048
207.4 | 49.5 | 5.048
207.5 | 49.5 | 5.048
207.6 | 49.5 | 5.048
207.7 | 49.5 | 5.048
207.8 | 49.5 | 5.048
207.9 | 49.5 | 5.048
208 | 49.5 | 5.048
208.1 | 49.5 | 5.048
208.2 | 49.5 | 5.048
208.3 | 49.5 | 5.048
208.4 | 49.5 | 5.048
208.5 | 49.5 | 5.048
208.6 | 49.5 | 5.048
208.7 | 49.5 | 5.048
208.8 | 49.5 | 5.048
208.9 | 49.5 | 5.048
209 | 49.5 | 5.048
209.1 | 49.5 | 5.048
209.2 | 49.5 | 5.048
209.3 | 49.5 | 5.048
209.4 | 49.5 | 5.048
209.5 | 49.5 | 5.048
209.6 | 49.5 | 5.048
209.7 | 49.5 | 5.048
209.8 | 49.5 | 5.048
209.9 | 49.5 | 5.048
210 | 49.5 | 5.048
210.1 | 49.5 | 5.048
210.2 | 49.5 | 5.048
210.3 | 49.5 | 5.048
210.4 | 49.5 | 5.048
210.5 | 49.5 | 5.048
210.6 | 49.5 | 5.048
210.7 | 49.5 | 5.048
210.8 | 49.5 | 5.048
210.9 | 49.5 | 5.048
211 | 49.5 | 5.048
211.1 | 49.5 | 5.048
211.2 | 49.5 | 5.048
211.3 | 49.5 | 5.048
211.4 | 49.5 | 5.049
211.5 | 49.5 | 5.049
211.6 | 49.5 | 5.048
211.7 | 49.5 | 5.048
211.8 | 49.5 | 5.048
211.9 | 49.5 | 5.048
212 | 49.5 | 5.048
212.1 | 49.5 | 5.048
212.2 | 49.5 | 5.048
212.3 | 49.5 | 5.048
212.4 | 49.5 | 5.048
212.5 | 49.5 | 5.048
212.6 | 49.5 | 5.048
212.7 | 49.5 | 5.048
212.8 | 49.5 | 5.048
212.9 | 49.5 | 5.048
213 | 49.5 | 5.048
213.1 | 49.5 | 5.048
213.2 | 49.5 | 5.048
213.3 | 49.5 | 5.048
213.4 | 49.5 | 5.048
213.5 | 49.5 | 5.048
213.6 | 49.5 | 5.048
213.7 | 49.5 | 5.048
213.8 | 49.5 | 5.048
213.9 | 49.5 | 5.048
214 | 49.5 | 5.048
214.1 | 49.5 | 5.048
214.2 | 49.5 | 5.048
214.3 | 49.5 | 5.048
214.4 | 49.5 | 5.048
214.5 | 49.5 | 5.048
214.6 | 49.5 | 5.048
214.7 | 49.5 | 5.048
214.8 | 49.5 | 5.048
214.9 | 49.5 | 5.048
215 | 49.5 | 5.048
215.1 | 49.5 | 5.048
215.2 | 49.5 | 5.048
215.3 | 49.5 | 5.048
215.4 | 49.5 | 5.048
215.5 | 49.5 | 5.048
215.6 | 49.5 | 5.048
215.7 | 49.5 | 5.048
215.8 | 49.5 | 5.048
215.9 | 49.5 | 5.048
216 | 49.5 | 5.048
216.1 | 49.5 | 5.048
216.2 | 49.5 | 5.048
216.3 | 49.5 | 5.048
216.4 | 49.5 | 5.048
216.5 | 49.5 | 5.048
216.6 | 49.5 | 5.048
216.7 | 49.5 | 5.048
216.8 | 49.5 | 5.048
216.9 | 49.5 | 5.048
217 | 49.5 | 5.048
217.1 | 49.5 | 5.048
217.2 | 49.5 | 5.048
217.3 | 49.5 | 5.048
217.4 | 49.5 | 5.048
217.5 | 49.5 | 5.048
217.6 | 49.5 | 5.048
217.7 | 49.5 | 5.048
217.8 | 49.5 | 5.048
217.9 | 49.5 | 5.048
218 | 49.5 | 5.048
218.1 | 49.5 | 5.048
218.2 | 49.5 | 5.048
218.3 | 49.5 | 5.048
218.4 | 49.5 | 5.048
218.5 | 49.5 | 5.048
218.6 | 49.5 | 5.048
218.7 | 49.5 | 5.048
218.8 | 49.5 | 5.048
218.9 | 49.5 | 5.048
219 | 49.5 | 5.048
219.1 | 49.5 | 5.048
219.2 | 49.5 | 5.048
219.3 | 49.5 | 5.048
219.4 | 49.5 | 5.048
219.5 | 49.5 | 5.048
219.6 | 49.5 | 5.048
219.7 | 49.5 | 5.048
219.8 | 49.5 | 5.048
219.9 | 49.5 | 5.048
220 | 49.5 | 5.048
220.1 | 49.5 | 5.048
220.2 | 49.5 | 5.048
220.3 | 49.5 | 5.048
220.4 | 49.5 | 5.048
220.5 | 49.5 | 5.048
220.6 | 49.5 | 5.048
220.7 | 49.5 | 5.048
220.8 | 49.5 | 5.048
220.9 | 49.5 | 5.048
221 | 49.5 | 5.048
221.1 | 49.5 | 5.048
221.2 | 49.5 | 5.048
221.3 | 49.5 | 5.048
221.4 | 49.5 | 5.048
221.5 | 49.5 | 5.048
221.6 | 49.5 | 5.048
221.7 | 49.5 | 5.048
221.8 | 49.5 | 5.048
221.9 | 49.5 | 5.048
222 | 49.5 | 5.048
222.1 | 49.5 | 5.048
222.2 | 49.5 | 5.048
222.3 | 49.5 | 5.048
222.4 | 49.5 | 5.048
222.5 | 49.5 | 5.048
222.6 | 49.5 | 5.048
222.7 | 49.5 | 5.048
222.8 | 49.5 | 5.048
222.9 | 49.5 | 5.048
223 | 49.5 | 5.048
223.1 | 49.5 | 5.048
223.2 | 49.5 | 5.048
223.3 | 49.5 | 5.048
223.4 | 49.5 | 5.048
223.5 | 49.5 | 5.048
223.6 | 49.5 | 5.048
223.7 | 49.5 | 5.048
223.8 | 49.5 | 5.048
223.9 | 49.5 | 5.048
224 | 49.5 | 5.048
224.1 | 49.5 | 5.048
224.2 | 49.5 | 5.048
224.3 | 49.5 | 5.048
224.4 | 49.5 | 5.048
224.5 | 49.5 | 5.048
224.6 | 49.5 | 5.048
224.7 | 49.5 | 5.048
224.8 | 49.5 | 5.048
224.9 | 49.5 | 5.048
225 | 49.5 | 5.048
225.1 | 49.5 | 5.048
225.2 | 49.5 | 5.048
225.3 | 49.5 | 5.048
225.4 | 49.5 | 5.048
225.5 | 49.5 | 5.048
225.6 | 49.5 | 5.048
225.7 | 49.5 | 5.048
225.8 | 49.5 | 5.048
225.9 | 49.5 | 5.048
226 | 49.5 | 5.048
226.1 | 49.5 | 5.048
226.2 | 49.5 | 5.048
226.3 | 49.5 | 5.048
226.4 | 49.5 | 5.048
226.5 | 49.5 | 5.048
226.6 | 49.5 | 5.048
226.7 | 49.5 | 5.048
226.8 | 49.5 | 5.048
226.9 | 49.5 | 5.048
227 | 49.5 | 5.048
227.1 | 49.5 | 5.048
227.2 | 49.5 | 5.048
227.3 | 49.5 | 5.048
227.4 | 49.5 | 5.048
227.5 | 49.5 | 5.048
227.6 | 49.5 | 5.048
227.7 | 49.5 | 5.048
227.8 | 49.5 | 5.048
227.9 | 49.5 | 5.048
228 | 49.5 | 5.048
228.1 | 49.5 | 5.048
228.2 | 49.5 | 5.048
228.3 | 49.5 | 5.048
228.4 | 49.5 | 5.048
228.5 | 49.5 | 5.048
228.6 | 49.5 | 5.048
228.7 | 49.5 | 5.048
228.8 | 49.5 | 5.048
228.9 | 49.5 | 5.048
229 | 49.5 | 5.048
229.1 | 49.5 | 5.048
229.2 | 49.5 | 5.048
229.3 | 49.5 | 5.048
229.4 | 49.5 | 5.048
229.5 | 49.5 | 5.048
229.6 | 49.5 | 5.048
229.7 | 49.5 | 5.048
229.8 | 49.5 | 5.048
229.9 | 49.5 | 5.048
230 | 49.5 | 5.048
230.1 | 49.5 | 5.048
230.2 | 49.5 | 5.048
230.3 | 49.5 | 5.048
230.4 | 49.5 | 5.048
230.5 | 49.5 | 5.048
230.6 | 49.5 | 5.048
230.7 | 49.5 | 5.048
230.8 | 49.5 | 5.048
230.9 | 49.5 | 5.048
231 | 49.5 | 5.048
231.1 | 49.5 | 5.048
231.2 | 49.5 | 5.048
231.3 | 49.5 | 5.048
231.4 | 49.5 | 5.048
231.5 | 49.5 | 5.048
231.6 | 49.5 | 5.048
231.7 | 49.5 | 5.048
231.8 | 49.5 | 5.048
231.9 | 49.5 | 5.048
232 | 49.5 | 5.048
232.1 | 49.5 | 5.048
232.2 | 49.5 | 5.048
232.3 | 49.5 | 5.048
232.4 | 49.5 | 5.048
232.5 | 49.5 | 5.048
232.6 | 49.5 | 5.048
232.7 | 49.5 | 5.048
232.8 | 49.5 | 5.048
232.9 | 49.5 | 5.048
233 | 49.5 | 5.048
233.1 | 49.5 | 5.048
233.2 | 49.5 | 5.048
233.3 | 49.5 | 5.048
233.4 | 49.5 | 5.048
233.5 | 49.5 | 5.048
233.6 | 49.5 | 5.048
233.7 | 49.5 | 5.048
233.8 | 49.5 | 5.048
233.9 | 49.5 | 5.048
234 | 49.5 | 5.048
234.1 | 49.5 | 5.048
234.2 | 49.5 | 5.048
234.3 | 49.5 | 5.048
234.4 | 49.5 | 5.048
234.5 | 49.5 | 5.048
234.6 | 49.5 | 5.048
234.7 | 49.5 | 5.048
234.8 | 49.5 | 5.048
234.9 | 49.5 | 5.048
235 | 49.5 | 5.048
235.1 | 49.5 | 5.048
235.2 | 49.5 | 5.048
235.3 | 49.5 | 5.048
235.4 | 49.5 | 5.048
235.5 | 49.5 | 5.048
235.6 | 49.5 | 5.048
235.7 | 49.5 | 5.048
235.8 | 49.5 | 5.048
235.9 | 49.5 | 5.048
236 | 49.5 | 5.048
236.1 | 49.5 | 5.048
236.2 | 49.5 | 5.048
236.3 | 49.5 | 5.048
236.4 | 49.5 | 5.048
236.5 | 49.5 | 5.048
236.6 | 49.5 | 5.048
236.7 | 49.5 | 5.048
236.8 | 49.5 | 5.048
236.9 | 49.5 | 5.048
237 | 49.5 | 5.048
237.1 | 49.5 | 5.048
237.2 | 49.5 | 5.048
237.3 | 49.5 | 5.048
237.4 | 49.5 | 5.048
237.5 | 49.5 | 5.048
237.6 | 49.5 | 5.048
237.7 | 49.5 | 5.048
237.8 | 49.5 | 5.048
237.9 | 49.5 | 5.048
238 | 49.5 | 5.048
238.1 | 49.5 | 5.048
238.2 | 49.5 | 5.048
238.3 | 49.5 | 5.048
238.4 | 49.5 | 5.048
238.5 | 49.5 | 5.048
238.6 | 49.5 | 5.048
238.7 | 49.5 | 5.048
238.8 | 49.5 | 5.048
238.9 | 49.5 | 5.048
239 | 49.5 | 5.048
239.1 | 49.5 | 5.048
239.2 | 49.5 | 5.048
239.3 | 49.5 | 5.048
239.4 | 49.5 | 5.048
239.5 | 49.5 | 5.048
239.6 | 49.5 | 5.048
239.7 | 49.5 | 5.048
239.8 | 49.5 | 5.048
239.9 | 49.5 | 5.048
240 | 49.5 | 5.048
240.1 | 49.5 | 5.048
240.2 | 49.5 | 5.048
240.3 | 49.5 | 5.048
240.4 | 49.5 | 5.048
240.5 | 49.5 | 5.048
240.6 | 49.5 | 5.048
240.7 | 49.5 | 5.048
240.8 | 49.5 | 5.048
240.9 | 49.5 | 5.048
241 | 49.5 | 5.048
241.1 | 49.5 | 5.048
241.2 | 49.5 | 5.048
241.3 | 49.5 | 5.048
241.4 | 49.5 | 5.048
241.5 | 49.5 | 5.048
241.6 | 49.5 | 5.048
241.7 | 49.5 | 5.048
241.8 | 49.5 | 5.048
241.9 | 49.5 | 5.048
242 | 49.5 | 5.048
242.1 | 49.5 | 5.048
242.2 | 49.5 | 5.048
242.3 | 49.5 | 5.048
242.4 | 49.5 | 5.048
242.5 | 49.5 | 5.048
242.6 | 49.5 | 5.048
242.7 | 49.5 | 5.048
242.8 | 49.5 | 5.048
242.9 | 49.5 | 5.048
243 | 49.5 | 5.048
243.1 | 49.5 | 5.048
243.2 | 49.5 | 5.048
243.3 | 49.5 | 5.048
243.4 | 49.5 | 5.048
243.5 | 49.5 | 5.048
243.6 | 49.5 | 5.048
243.7 | 49.5 | 5.048
243.8 | 49.5 | 5.048
243.9 | 49.5 | 5.048
244 | 49.5 | 5.048
244.1 | 49.5 | 5.048
244.2 | 49.5 | 5.048
244.3 | 49.5 | 5.048
244.4 | 49.5 | 5.048
244.5 | 49.5 | 5.048
244.6 | 49.5 | 5.048
244.7 | 49.5 | 5.048
244.8 | 49.5 | 5.048
244.9 | 49.5 | 5.048
245 | 49.5 | 5.048
245.1 | 49.5 | 5.048
245.2 | 49.5 | 5.048
245.3 | 49.5 | 5.048
245.4 | 49.5 | 5.048
245.5 | 49.5 | 5.048
245.6 | 49.5 | 5.048
245.7 | 49.5 | 5.048
245.8 | 49.5 | 5.048
245.9 | 49.5 | 5.048
246 | 49.5 | 5.048
246.1 | 49.5 | 5.048
246.2 | 49.5 | 5.048
246.3 | 49.5 | 5.048
246.4 | 49.5 | 5.048
246.5 | 49.5 | 5.049
246.6 | 49.5 | 5.049
246.7 | 49.5 | 5.049
246.8 | 49.5 | 5.049
246.9 | 49.5 | 5.049
247 | 49.5 | 5.049
247.1 | 49.5 | 5.049
247.2 | 49.5 | 5.049
247.3 | 49.5 | 5.049
247.4 | 49.5 | 5.049
247.5 | 49.5 | 5.049
247.6 | 49.5 | 5.048
247.7 | 49.5 | 5.048
247.8 | 49.5 | 5.048
247.9 | 49.5 | 5.048
248 | 49.5 | 5.048
248.1 | 49.5 | 5.048
248.2 | 49.5 | 5.048
248.3 | 49.5 | 5.048
248.4 | 49.5 | 5.048
248.5 | 49.5 | 5.048
248.6 | 49.5 | 5.048
248.7 | 49.5 | 5.048
248.8 | 49.5 | 5.048
248.9 | 49.5 | 5.048
249 | 49.5 | 5.048
249.1 | 49.5 | 5.048
249.2 | 49.5 | 5.048
249.3 | 49.5 | 5.048
249.4 | 49.5 | 5.048
249.5 | 49.5 | 5.048
249.6 | 49.5 | 5.048
249.7 | 49.5 | 5.048
249.8 | 49.5 | 5.048
249.9 | 49.5 | 5.048
250 | 49.5 | 5.048
250.1 | 49.5 | 5.048
250.2 | 49.5 | 5.048
250.3 | 49.5 | 5.048
250.4 | 49.5 | 5.048
250.5 | 49.5 | 5.048
250.6 | 49.5 | 5.048
250.7 | 49.5 | 5.048
250.8 | 49.5 | 5.048
250.9 | 49.5 | 5.048
251 | 49.5 | 5.048
251.1 | 49.5 | 5.048
251.2 | 49.5 | 5.048
251.3 | 49.5 | 5.048
251.4 | 49.5 | 5.048
251.5 | 49.5 | 5.048
251.6 | 49.5 | 5.048
251.7 | 49.5 | 5.048
251.8 | 49.5 | 5.048
251.9 | 49.5 | 5.048
252 | 49.5 | 5.048
252.1 | 49.5 | 5.048
252.2 | 49.5 | 5.048
252.3 | 49.5 | 5.048
252.4 | 49.5 | 5.048
252.5 | 49.5 | 5.048
252.6 | 49.5 | 5.048
252.7 | 49.5 | 5.048
252.8 | 49.5 | 5.048
252.9 | 49.5 | 5.048
253 | 49.5 | 5.048
253.1 | 49.5 | 5.048
253.2 | 49.5 | 5.048
253.3 | 49.5 | 5.048
253.4 | 49.5 | 5.048
253.5 | 49.5 | 5.048
253.6 | 49.5 | 5.048
253.7 | 49.5 | 5.048
253.8 | 49.5 | 5.048
253.9 | 49.5 | 5.048
254 | 49.5 | 5.048
254.1 | 49.5 | 5.048
254.2 | 49.5 | 5.048
254.3 | 49.5 | 5.048
254.4 | 49.5 | 5.048
254.5 | 49.5 | 5.048
254.6 | 49.5 | 5.048
254.7 | 49.5 | 5.048
254.8 | 49.5 | 5.048
254.9 | 49.5 | 5.048
255 | 49.5 | 5.048
255.1 | 49.5 | 5.048
255.2 | 49.5 | 5.048
255.3 | 49.5 | 5.048
255.4 | 49.5 | 5.048
255.5 | 49.5 | 5.048
255.6 | 49.5 | 5.048
255.7 | 49.5 | 5.048
255.8 | 49.5 | 5.048
255.9 | 49.5 | 5.048
256 | 49.5 | 5.048
256.1 | 49.5 | 5.048
256.2 | 49.5 | 5.048
256.3 | 49.5 | 5.048
256.4 | 49.5 | 5.048
256.5 | 49.5 | 5.048
256.6 | 49.5 | 5.048
256.7 | 49.5 | 5.048
256.8 | 49.5 | 5.048
256.9 | 49.5 | 5.048
257 | 49.5 | 5.048
257.1 | 49.5 | 5.048
257.2 | 49.5 | 5.048
257.3 | 49.5 | 5.048
257.4 | 49.5 | 5.048
257.5 | 49.5 | 5.048
257.6 | 49.5 | 5.048
257.7 | 49.5 | 5.048
257.8 | 49.5 | 5.048
257.9 | 49.5 | 5.048
258 | 49.5 | 5.048
258.1 | 49.5 | 5.048
258.2 | 49.5 | 5.048
258.3 | 49.5 | 5.048
258.4 | 49.5 | 5.048
258.5 | 49.5 | 5.048
258.6 | 49.5 | 5.048
258.7 | 49.5 | 5.048
258.8 | 49.5 | 5.048
258.9 | 49.5 | 5.048
259 | 49.5 | 5.048
259.1 | 49.5 | 5.048
259.2 | 49.5 | 5.048
259.3 | 49.5 | 5.048
259.4 | 49.5 | 5.048
259.5 | 49.5 | 5.048
259.6 | 49.5 | 5.048
259.7 | 49.5 | 5.048
259.8 | 49.5 | 5.048
259.9 | 49.5 | 5.048
260 | 49.5 | 5.048
260.1 | 49.5 | 5.048
260.2 | 49.5 | 5.048
260.3 | 49.5 | 5.048
260.4 | 49.5 | 5.048
260.5 | 49.5 | 5.048
260.6 | 49.5 | 5.048
260.7 | 49.5 | 5.048
260.8 | 49.5 | 5.048
260.9 | 49.5 | 5.048
261 | 49.5 | 5.048
261.1 | 49.5 | 5.048
261.2 | 49.5 | 5.048
261.3 | 49.5 | 5.048
261.4 | 49.5 | 5.048
261.5 | 49.5 | 5.048
261.6 | 49.5 | 5.048
261.7 | 49.5 | 5.048
261.8 | 49.5 | 5.048
261.9 | 49.5 | 5.048
262 | 49.5 | 5.048
262.1 | 49.5 | 5.048
262.2 | 49.5 | 5.048
262.3 | 49.5 | 5.048
262.4 | 49.5 | 5.048
262.5 | 49.5 | 5.048
262.6 | 49.5 | 5.048
262.7 | 49.5 | 5.048
262.8 | 49.5 | 5.048
262.9 | 49.5 | 5.048
263 | 49.5 | 5.048
263.1 | 49.5 | 5.048
263.2 | 49.5 | 5.048
263.3 | 49.5 | 5.048
263.4 | 49.5 | 5.048
263.5 | 49.5 | 5.048
263.6 | 49.5 | 5.048
263.7 | 49.5 | 5.048
263.8 | 49.5 | 5.048
263.9 | 49.5 | 5.048
264 | 49.5 | 5.048
264.1 | 49.5 | 5.048
264.2 | 49.5 | 5.048
264.3 | 49.5 | 5.048
264.4 | 49.5 | 5.048
264.5 | 49.5 | 5.048
264.6 | 49.5 | 5.048
264.7 | 49.5 | 5.048
264.8 | 49.5 | 5.048
264.9 | 49.5 | 5.048
265 | 49.5 | 5.048
265.1 | 49.5 | 5.048
265.2 | 49.5 | 5.048
265.3 | 49.5 | 5.048
265.4 | 49.5 | 5.048
265.5 | 49.5 | 5.048
265.6 | 49.5 | 5.048
265.7 | 49.5 | 5.048
265.8 | 49.5 | 5.048
265.9 | 49.5 | 5.048
266 | 49.5 | 5.048
266.1 | 49.5 | 5.048
266.2 | 49.5 | 5.048
266.3 | 49.5 | 5.048
266.4 | 49.5 | 5.048
266.5 | 49.5 | 5.048
266.6 | 49.5 | 5.048
266.7 | 49.5 | 5.048
266.8 | 49.5 | 5.048
266.9 | 49.5 | 5.048
267 | 49.5 | 5.048
267.1 | 49.5 | 5.048
267.2 | 49.5 | 5.048
267.3 | 49.5 | 5.048
267.4 | 49.5 | 5.048
267.5 | 49.5 | 5.048
267.6 | 49.5 | 5.048
267.7 | 49.5 | 5.048
267.8 | 49.5 | 5.048
267.9 | 49.5 | 5.048
268 | 49.5 | 5.048
268.1 | 49.5 | 5.048
268.2 | 49.5 | 5.048
268.3 | 49.5 | 5.048
268.4 | 49.5 | 5.048
268.5 | 49.5 | 5.048
268.6 | 49.5 | 5.048
268.7 | 49.5 | 5.048
268.8 | 49.5 | 5.048
268.9 | 49.5 | 5.048
269 | 49.5 | 5.048
269.1 | 49.5 | 5.048
269.2 | 49.5 | 5.048
269.3 | 49.5 | 5.048
269.4 | 49.5 | 5.048
269.5 | 49.5 | 5.048
269.6 | 49.5 | 5.048
269.7 | 49.5 | 5.048
269.8 | 49.5 | 5.048
269.9 | 49.5 | 5.048
270 | 49.5 | 5.048
270.1 | 49.5 | 5.048
270.2 | 49.5 | 5.048
270.3 | 49.5 | 5.048
270.4 | 49.5 | 5.048
270.5 | 49.5 | 5.048
270.6 | 49.5 | 5.048
270.7 | 49.5 | 5.048
270.8 | 49.5 | 5.048
270.9 | 49.5 | 5.048
271 | 49.5 | 5.048
271.1 | 49.5 | 5.048
271.2 | 49.5 | 5.048
271.3 | 49.5 | 5.048
271.4 | 49.5 | 5.048
271.5 | 49.5 | 5.048
271.6 | 49.5 | 5.048
271.7 | 49.5 | 5.048
271.8 | 49.5 | 5.048
271.9 | 49.5 | 5.048
272 | 49.5 | 5.048
272.1 | 49.5 | 5.048
272.2 | 49.5 | 5.048
272.3 | 49.5 | 5.048
272.4 | 49.5 | 5.048
272.5 | 49.5 | 5.048
272.6 | 49.5 | 5.048
272.7 | 49.5 | 5.048
272.8 | 49.5 | 5.048
272.9 | 49.5 | 5.048
273 | 49.5 | 5.048
273.1 | 49.5 | 5.048
273.2 | 49.5 | 5.048
273.3 | 49.5 | 5.048
273.4 | 49.5 | 5.048
273.5 | 49.5 | 5.048
273.6 | 49.5 | 5.048
273.7 | 49.5 | 5.048
273.8 | 49.5 | 5.048
273.9 | 49.5 | 5.048
274 | 49.5 | 5.048
274.1 | 49.5 | 5.048
274.2 | 49.5 | 5.048
274.3 | 49.5 | 5.048
274.4 | 49.5 | 5.048
274.5 | 49.5 | 5.048
274.6 | 49.5 | 5.048
274.7 | 49.5 | 5.048
274.8 | 49.5 | 5.048
274.9 | 49.5 | 5.048
275 | 49.5 | 5.048
275.1 | 49.5 | 5.048
275.2 | 49.5 | 5.048
275.3 | 49.5 | 5.048
275.4 | 49.5 | 5.048
275.5 | 49.5 | 5.048
275.6 | 49.5 | 5.048
275.7 | 49.5 | 5.048
275.8 | 49.5 | 5.048
275.9 | 49.5 | 5.048
276 | 49.5 | 5.048
276.1 | 49.5 | 5.048
276.2 | 49.5 | 5.048
276.3 | 49.5 | 5.048
276.4 | 49.5 | 5.048
276.5 | 49.5 | 5.048
276.6 | 49.5 | 5.048
276.7 | 49.5 | 5.048
276.8 | 49.5 | 5.048
276.9 | 49.5 | 5.048
277 | 49.5 | 5.048
277.1 | 49.5 | 5.048
277.2 | 49.5 | 5.048
277.3 | 49.5 | 5.048
277.4 | 49.5 | 5.048
277.5 | 49.5 | 5.048
277.6 | 49.5 | 5.048
277.7 | 49.5 | 5.048
277.8 | 49.5 | 5.048
277.9 | 49.5 | 5.048
278 | 49.5 | 5.048
278.1 | 49.5 | 5.048
278.2 | 49.5 | 5.048
278.3 | 49.5 | 5.048
278.4 | 49.5 | 5.048
278.5 | 49.5 | 5.048
278.6 | 49.5 | 5.048
278.7 | 49.5 | 5.048
278.8 | 49.5 | 5.048
278.9 | 49.5 | 5.048
279 | 49.5 | 5.048
279.1 | 49.5 | 5.048
279.2 | 49.5 | 5.048
279.3 | 49.5 | 5.048
279.4 | 49.5 | 5.048
279.5 | 49.5 | 5.048
279.6 | 49.5 | 5.048
279.7 | 49.5 | 5.048
279.8 | 49.5 | 5.048
279.9 | 49.5 | 5.048
280 | 49.5 | 5.048
280.1 | 49.5 | 5.048
280.2 | 49.5 | 5.048
280.3 | 49.5 | 5.048
280.4 | 49.5 | 5.048
280.5 | 49.5 | 5.048
280.6 | 49.5 | 5.048
280.7 | 49.5 | 5.048
280.8 | 49.5 | 5.049
280.9 | 49.5 | 5.049
281 | 49.5 | 5.049
281.1 | 49.5 | 5.049
281.2 | 49.5 | 5.049
281.3 | 49.5 | 5.049
281.4 | 49.5 | 5.049
281.5 | 49.5 | 5.049
281.6 | 49.5 | 5.049
281.7 | 49.5 | 5.049
281.8 | 49.5 | 5.049
281.9 | 49.5 | 5.049
282 | 49.5 | 5.048
282.1 | 49.5 | 5.048
282.2 | 49.5 | 5.048
282.3 | 49.5 | 5.048
282.4 | 49.5 | 5.048
282.5 | 49.5 | 5.048
282.6 | 49.5 | 5.048
282.7 | 49.5 | 5.048
282.8 | 49.5 | 5.048
282.9 | 49.5 | 5.048
283 | 49.5 | 5.048
283.1 | 49.5 | 5.048
283.2 | 49.5 | 5.047
283.3 | 49.5 | 5.047
283.4 | 49.5 | 5.047
283.5 | 49.5 | 5.047
283.6 | 49.5 | 5.047
283.7 | 49.5 | 5.047
283.8 | 49.5 | 5.047
283.9 | 49.5 | 5.047
284 | 49.5 | 5.047
284.1 | 49.5 | 5.047
284.2 | 49.5 | 5.047
284.3 | 49.5 | 5.047
284.4 | 49.5 | 5.048
284.5 | 49.5 | 5.048
284.6 | 49.5 | 5.048
284.7 | 49.5 | 5.048
284.8 | 49.5 | 5.048
284.9 | 49.5 | 5.048
285 | 49.5 | 5.048
285.1 | 49.5 | 5.048
285.2 | 49.5 | 5.048
285.3 | 49.5 | 5.048
285.4 | 49.5 | 5.048
285.5 | 49.5 | 5.048
285.6 | 49.5 | 5.048
285.7 | 49.5 | 5.048
285.8 | 49.5 | 5.048
285.9 | 49.5 | 5.048
286 | 49.5 | 5.048
286.1 | 49.5 | 5.048
286.2 | 49.5 | 5.048
286.3 | 49.5 | 5.048
286.4 | 49.5 | 5.048
286.5 | 49.5 | 5.048
286.6 | 49.5 | 5.048
286.7 | 49.5 | 5.049
286.8 | 49.5 | 5.049
286.9 | 49.5 | 5.049
287 | 49.5 | 5.049
287.1 | 49.5 | 5.049
287.2 | 49.5 | 5.049
287.3 | 49.5 | 5.049
287.4 | 49.5 | 5.049
287.5 | 49.5 | 5.049
287.6 | 49.5 | 5.049
287.7 | 49.5 | 5.049
287.8 | 49.5 | 5.049
287.9 | 49.5 | 5.048
288 | 49.5 | 5.048
288.1 | 49.5 | 5.048
288.2 | 49.5 | 5.048
288.3 | 49.5 | 5.048
288.4 | 49.5 | 5.048
288.5 | 49.5 | 5.048
288.6 | 49.5 | 5.048
288.7 | 49.5 | 5.048
288.8 | 49.5 | 5.048
288.9 | 49.5 | 5.048
289 | 49.5 | 5.047
289.1 | 49.5 | 5.048
289.2 | 49.5 | 5.048
289.3 | 49.5 | 5.048
289.4 | 49.5 | 5.048
289.5 | 49.5 | 5.048
289.6 | 49.5 | 5.048
289.7 | 49.5 | 5.048
289.8 | 49.5 | 5.048
289.9 | 49.5 | 5.048
290 | 49.5 | 5.048
290.1 | 49.5 | 5.048
290.2 | 49.5 | 5.048
290.3 | 49.5 | 5.048
290.4 | 49.5 | 5.048
290.5 | 49.5 | 5.048
290.6 | 49.5 | 5.048
290.7 | 49.5 | 5.048
290.8 | 49.5 | 5.048
290.9 | 49.5 | 5.048
291 | 49.5 | 5.048
291.1 | 49.5 | 5.048
291.2 | 49.5 | 5.047
291.3 | 49.5 | 5.048
291.4 | 49.5 | 5.048
291.5 | 49.5 | 5.048
291.6 | 49.5 | 5.048
291.7 | 49.5 | 5.048
291.8 | 49.5 | 5.048
291.9 | 49.5 | 5.048
292 | 49.5 | 5.048
292.1 | 49.5 | 5.048
292.2 | 49.5 | 5.048
292.3 | 49.5 | 5.048
292.4 | 49.5 | 5.048
292.5 | 49.5 | 5.049
292.6 | 49.5 | 5.049
292.7 | 49.5 | 5.049
292.8 | 49.5 | 5.049
292.9 | 49.5 | 5.049
293 | 49.5 | 5.049
293.1 | 49.5 | 5.049
293.2 | 49.5 | 5.049
293.3 | 49.5 | 5.049
293.4 | 49.5 | 5.049
293.5 | 49.5 | 5.049
293.6 | 49.5 | 5.049
293.7 | 49.5 | 5.048
293.8 | 49.5 | 5.048
293.9 | 49.5 | 5.048
294 | 49.5 | 5.048
294.1 | 49.5 | 5.048
294.2 | 49.5 | 5.048
294.3 | 49.5 | 5.048
294.4 | 49.5 | 5.048
294.5 | 49.5 | 5.048
294.6 | 49.5 | 5.048
294.7 | 49.5 | 5.048
294.8 | 49.5 | 5.048
294.9 | 49.5 | 5.048
295 | 49.5 | 5.048
295.1 | 49.5 | 5.048
295.2 | 49.5 | 5.048
295.3 | 49.5 | 5.048
295.4 | 49.5 | 5.048
295.5 | 49.5 | 5.048
295.6 | 49.5 | 5.048
295.7 | 49.5 | 5.048
295.8 | 49.5 | 5.048
295.9 | 49.5 | 5.048
296 | 49.5 | 5.048
296.1 | 49.5 | 5.048
296.2 | 49.5 | 5.048
296.3 | 49.5 | 5.048
296.4 | 49.5 | 5.048
296.5 | 49.5 | 5.048
296.6 | 49.5 | 5.048
296.7 | 49.5 | 5.048
296.8 | 49.5 | 5.048
296.9 | 49.5 | 5.048
297 | 49.5 | 5.048
297.1 | 49.5 | 5.048
297.2 | 49.5 | 5.048
297.3 | 49.5 | 5.048
297.4 | 49.5 | 5.048
297.5 | 49.5 | 5.048
297.6 | 49.5 | 5.048
297.7 | 49.5 | 5.048
297.8 | 49.5 | 5.048
297.9 | 49.5 | 5.048
298 | 49.5 | 5.048
298.1 | 49.5 | 5.048
298.2 | 49.5 | 5.048
298.3 | 49.5 | 5.048
298.4 | 49.5 | 5.048
298.5 | 49.5 | 5.049
298.6 | 49.5 | 5.049
298.7 | 49.5 | 5.049
298.8 | 49.5 | 5.049
298.9 | 49.5 | 5.049
299 | 49.5 | 5.049
299.1 | 49.5 | 5.049
299.2 | 49.5 | 5.049
299.3 | 49.5 | 5.049
299.4 | 49.5 | 5.049
299.5 | 49.5 | 5.049
299.6 | 49.5 | 5.049
299.7 | 49.5 | 5.049
299.8 | 49.5 | 5.049
299.9 | 49.5 | 5.049
300 | 49.5 | 5.049
300.1 | 49.5 | 5.049
300.2 | 49.5 | 5.049
300.3 | 49.5 | 5.049
300.4 | 49.5 | 5.049
300.5 | 49.5 | 5.049
300.6 | 49.5 | 5.049
300.7 | 49.5 | 5.049
300.8 | 49.5 | 5.048
300.9 | 49.5 | 5.048
301 | 49.5 | 5.048
301.1 | 49.5 | 5.048
301.2 | 49.5 | 5.048
301.3 | 49.5 | 5.048
301.4 | 49.5 | 5.048
301.5 | 49.5 | 5.048
301.6 | 49.5 | 5.048
301.7 | 49.5 | 5.048
301.8 | 49.5 | 5.048
301.9 | 49.5 | 5.048
302 | 49.5 | 5.048
302.1 | 49.5 | 5.048
302.2 | 49.5 | 5.048
302.3 | 49.5 | 5.048
302.4 | 49.5 | 5.048
302.5 | 49.5 | 5.048
302.6 | 49.5 | 5.048
302.7 | 49.5 | 5.048
302.8 | 49.5 | 5.048
302.9 | 49.5 | 5.048
303 | 49.5 | 5.048
303.1 | 49.5 | 5.048
303.2 | 49.5 | 5.048
303.3 | 49.5 | 5.048
303.4 | 49.5 | 5.048
303.5 | 49.5 | 5.048
303.6 | 49.5 | 5.048
303.7 | 49.5 | 5.048
303.8 | 49.5 | 5.048
303.9 | 49.5 | 5.048
304 | 49.5 | 5.048
304.1 | 49.5 | 5.048
304.2 | 49.5 | 5.048
304.3 | 49.5 | 5.049
304.4 | 49.5 | 5.049
304.5 | 49.5 | 5.049
304.6 | 49.5 | 5.049
304.7 | 49.5 | 5.049
304.8 | 49.5 | 5.049
304.9 | 49.5 | 5.049
305 | 49.5 | 5.049
305.1 | 49.5 | 5.049
305.2 | 49.5 | 5.049
305.3 | 49.5 | 5.049
305.4 | 49.5 | 5.049
305.5 | 49.5 | 5.049
305.6 | 49.5 | 5.049
305.7 | 49.5 | 5.049
305.8 | 49.5 | 5.049
305.9 | 49.5 | 5.049
306 | 49.5 | 5.049
306.1 | 49.5 | 5.049
306.2 | 49.5 | 5.049
306.3 | 49.5 | 5.049
306.4 | 49.5 | 5.049
306.5 | 49.5 | 5.049
306.6 | 49.5 | 5.049
306.7 | 49.5 | 5.049
306.8 | 49.5 | 5.049
306.9 | 49.5 | 5.049
307 | 49.5 | 5.049
307.1 | 49.5 | 5.049
307.2 | 49.5 | 5.049
307.3 | 49.5 | 5.049
307.4 | 49.5 | 5.049
307.5 | 49.5 | 5.049
307.6 | 49.5 | 5.049
307.7 | 49.5 | 5.048
307.8 | 49.5 | 5.048
307.9 | 49.5 | 5.048
308 | 49.5 | 5.048
308.1 | 49.5 | 5.048
308.2 | 49.5 | 5.048
308.3 | 49.5 | 5.048
308.4 | 49.5 | 5.048
308.5 | 49.5 | 5.048
308.6 | 49.5 | 5.048
308.7 | 49.5 | 5.048
308.8 | 49.5 | 5.048
308.9 | 49.5 | 5.048
309 | 49.5 | 5.048
309.1 | 49.5 | 5.048
309.2 | 49.5 | 5.048
309.3 | 49.5 | 5.048
309.4 | 49.5 | 5.048
309.5 | 49.5 | 5.048
309.6 | 49.5 | 5.048
309.7 | 49.5 | 5.048
309.8 | 49.5 | 5.048
309.9 | 49.5 | 5.048
310 | 49.5 | 5.048
310.1 | 49.5 | 5.049
310.2 | 49.5 | 5.049
310.3 | 49.5 | 5.049
310.4 | 49.5 | 5.049
310.5 | 49.5 | 5.049
310.6 | 49.5 | 5.049
310.7 | 49.5 | 5.049
310.8 | 49.5 | 5.049
310.9 | 49.5 | 5.049
311 | 49.5 | 5.049
311.1 | 49.5 | 5.049
311.2 | 49.5 | 5.049
311.3 | 49.5 | 5.049
311.4 | 49.5 | 5.049
311.5 | 49.5 | 5.049
311.6 | 49.5 | 5.049
311.7 | 49.5 | 5.049
311.8 | 49.5 | 5.049
311.9 | 49.5 | 5.049
312 | 49.5 | 5.049
312.1 | 49.5 | 5.049
312.2 | 49.5 | 5.049
312.3 | 49.5 | 5.049
312.4 | 49.5 | 5.048
312.5 | 49.5 | 5.048
312.6 | 49.5 | 5.048
312.7 | 49.5 | 5.048
312.8 | 49.5 | 5.048
312.9 | 49.5 | 5.048
313 | 49.5 | 5.048
313.1 | 49.5 | 5.048
313.2 | 49.5 | 5.048
313.3 | 49.5 | 5.048
313.4 | 49.5 | 5.048
313.5 | 49.5 | 5.048
313.6 | 49.5 | 5.048
313.7 | 49.5 | 5.048
313.8 | 49.5 | 5.048
313.9 | 49.5 | 5.048
314 | 49.5 | 5.048
314.1 | 49.5 | 5.048
314.2 | 49.5 | 5.048
314.3 | 49.5 | 5.048
314.4 | 49.5 | 5.048
314.5 | 49.5 | 5.048
314.6 | 49.5 | 5.048
314.7 | 49.5 | 5.048
314.8 | 49.5 | 5.048
314.9 | 49.5 | 5.048
315 | 49.5 | 5.048
315.1 | 49.5 | 5.048
315.2 | 49.5 | 5.048
315.3 | 49.5 | 5.048
315.4 | 49.5 | 5.048
315.5 | 49.5 | 5.048
315.6 | 49.5 | 5.048
315.7 | 49.5 | 5.048
315.8 | 49.5 | 5.048
315.9 | 49.5 | 5.048
316 | 49.5 | 5.048
316.1 | 49.5 | 5.048
316.2 | 49.5 | 5.048
316.3 | 49.5 | 5.048
316.4 | 49.5 | 5.048
316.5 | 49.5 | 5.048
316.6 | 49.5 | 5.048
316.7 | 49.5 | 5.048
316.8 | 49.5 | 5.048
316.9 | 49.5 | 5.048
317 | 49.5 | 5.048
317.1 | 49.5 | 5.048
317.2 | 49.5 | 5.048
317.3 | 49.5 | 5.048
317.4 | 49.5 | 5.048
317.5 | 49.5 | 5.048
317.6 | 49.5 | 5.048
317.7 | 49.5 | 5.048
317.8 | 49.5 | 5.048
317.9 | 49.5 | 5.048
318 | 49.5 | 5.048
318.1 | 49.5 | 5.048
318.2 | 49.5 | 5.048
318.3 | 49.5 | 5.048
318.4 | 49.5 | 5.048
318.5 | 49.5 | 5.048
318.6 | 49.5 | 5.048
318.7 | 49.5 | 5.048
318.8 | 49.5 | 5.048
318.9 | 49.5 | 5.048
319 | 49.5 | 5.048
319.1 | 49.5 | 5.048
319.2 | 49.5 | 5.048
319.3 | 49.5 | 5.048
319.4 | 49.5 | 5.048
319.5 | 49.5 | 5.048
319.6 | 49.5 | 5.048
319.7 | 49.5 | 5.048
319.8 | 49.5 | 5.048
319.9 | 49.5 | 5.048
320 | 49.5 | 5.048
320.1 | 49.5 | 5.048
320.2 | 49.5 | 5.048
320.3 | 49.5 | 5.048
320.4 | 49.5 | 5.048
320.5 | 49.5 | 5.048
320.6 | 49.5 | 5.048
320.7 | 49.5 | 5.048
320.8 | 49.5 | 5.048
320.9 | 49.5 | 5.048
321 | 49.5 | 5.048
321.1 | 49.5 | 5.048
321.2 | 49.5 | 5.048
321.3 | 49.5 | 5.048
321.4 | 49.5 | 5.048
321.5 | 49.5 | 5.048
321.6 | 49.5 | 5.048
321.7 | 49.5 | 5.048
321.8 | 49.5 | 5.048
321.9 | 49.5 | 5.048
322 | 49.5 | 5.048
322.1 | 49.5 | 5.048
322.2 | 49.5 | 5.048
322.3 | 49.5 | 5.048
322.4 | 49.5 | 5.048
322.5 | 49.5 | 5.048
322.6 | 49.5 | 5.048
322.7 | 49.5 | 5.048
322.8 | 49.5 | 5.048
322.9 | 49.5 | 5.048
323 | 49.5 | 5.048
323.1 | 49.5 | 5.048
323.2 | 49.5 | 5.048
323.3 | 49.5 | 5.048
323.4 | 49.5 | 5.048
323.5 | 49.5 | 5.048
323.6 | 49.5 | 5.048
323.7 | 49.5 | 5.048
323.8 | 49.5 | 5.048
323.9 | 49.5 | 5.048
324 | 49.5 | 5.048
324.1 | 49.5 | 5.048
324.2 | 49.5 | 5.048
324.3 | 49.5 | 5.048
324.4 | 49.5 | 5.048
324.5 | 49.5 | 5.048
324.6 | 49.5 | 5.048
324.7 | 49.5 | 5.048
324.8 | 49.5 | 5.048
324.9 | 49.5 | 5.048
325 | 49.5 | 5.048
325.1 | 49.5 | 5.048
325.2 | 49.5 | 5.048
325.3 | 49.5 | 5.048
325.4 | 49.5 | 5.048
325.5 | 49.5 | 5.048
325.6 | 49.5 | 5.048
325.7 | 49.5 | 5.048
325.8 | 49.5 | 5.048
325.9 | 49.5 | 5.048
326 | 49.5 | 5.048
326.1 | 49.5 | 5.048
326.2 | 49.5 | 5.048
326.3 | 49.5 | 5.048
326.4 | 49.5 | 5.048
326.5 | 49.5 | 5.048
326.6 | 49.5 | 5.048
326.7 | 49.5 | 5.048
326.8 | 49.5 | 5.048
326.9 | 49.5 | 5.048
327 | 49.5 | 5.048
327.1 | 49.5 | 5.048
327.2 | 49.5 | 5.048
327.3 | 49.5 | 5.048
327.4 | 49.5 | 5.048
327.5 | 49.5 | 5.048
327.6 | 49.5 | 5.048
327.7 | 49.5 | 5.048
327.8 | 49.5 | 5.048
327.9 | 49.5 | 5.048
328 | 49.5 | 5.048
328.1 | 49.5 | 5.048
328.2 | 49.5 | 5.048
328.3 | 49.5 | 5.048
328.4 | 49.5 | 5.048
328.5 | 49.5 | 5.048
328.6 | 49.5 | 5.048
328.7 | 49.5 | 5.048
328.8 | 49.5 | 5.048
328.9 | 49.5 | 5.048
329 | 49.5 | 5.048
329.1 | 49.5 | 5.048
329.2 | 49.5 | 5.048
329.3 | 49.5 | 5.048
329.4 | 49.5 | 5.048
329.5 | 49.5 | 5.048
329.6 | 49.5 | 5.048
329.7 | 49.5 | 5.048
329.8 | 49.5 | 5.048
329.9 | 49.5 | 5.048
330 | 49.5 | 5.048
330.1 | 49.5 | 5.048
330.2 | 49.5 | 5.048
330.3 | 49.5 | 5.048
330.4 | 49.5 | 5.048
330.5 | 49.5 | 5.048
330.6 | 49.5 | 5.048
330.7 | 49.5 | 5.048
330.8 | 49.5 | 5.048
330.9 | 49.5 | 5.048
331 | 49.5 | 5.048
331.1 | 49.5 | 5.048
331.2 | 49.5 | 5.048
331.3 | 49.5 | 5.048
331.4 | 49.5 | 5.048
331.5 | 49.5 | 5.048
331.6 | 49.5 | 5.048
331.7 | 49.5 | 5.048
331.8 | 49.5 | 5.048
331.9 | 49.5 | 5.048
332 | 49.5 | 5.048
332.1 | 49.5 | 5.048
332.2 | 49.5 | 5.048
332.3 | 49.5 | 5.048
332.4 | 49.5 | 5.048
332.5 | 49.5 | 5.048
332.6 | 49.5 | 5.048
332.7 | 49.5 | 5.048
332.8 | 49.5 | 5.048
332.9 | 49.5 | 5.048
333 | 49.5 | 5.048
333.1 | 49.5 | 5.048
333.2 | 49.5 | 5.048
333.3 | 49.5 | 5.048
333.4 | 49.5 | 5.048
333.5 | 49.5 | 5.048
333.6 | 49.5 | 5.048
333.7 | 49.5 | 5.048
333.8 | 49.5 | 5.048
333.9 | 49.5 | 5.048
334 | 49.5 | 5.048
334.1 | 49.5 | 5.048
334.2 | 49.5 | 5.048
334.3 | 49.5 | 5.048
334.4 | 49.5 | 5.048
334.5 | 49.5 | 5.048
334.6 | 49.5 | 5.048
334.7 | 49.5 | 5.048
334.8 | 49.5 | 5.048
334.9 | 49.5 | 5.048
335 | 49.5 | 5.048
335.1 | 49.5 | 5.048
335.2 | 49.5 | 5.048
335.3 | 49.5 | 5.048
335.4 | 49.5 | 5.048
335.5 | 49.5 | 5.048
335.6 | 49.5 | 5.048
335.7 | 49.5 | 5.048
335.8 | 49.5 | 5.048
335.9 | 49.5 | 5.048
336 | 49.5 | 5.048
336.1 | 49.5 | 5.048
336.2 | 49.5 | 5.048
336.3 | 49.5 | 5.048
336.4 | 49.5 | 5.048
336.5 | 49.5 | 5.048
336.6 | 49.5 | 5.048
336.7 | 49.5 | 5.048
336.8 | 49.5 | 5.048
336.9 | 49.5 | 5.048
337 | 49.5 | 5.048
337.1 | 49.5 | 5.048
337.2 | 49.5 | 5.048
337.3 | 49.5 | 5.048
337.4 | 49.5 | 5.048
337.5 | 49.5 | 5.048
337.6 | 49.5 | 5.048
337.7 | 49.5 | 5.048
337.8 | 49.5 | 5.048
337.9 | 49.5 | 5.048
338 | 49.5 | 5.048
338.1 | 49.5 | 5.048
338.2 | 49.5 | 5.048
338.3 | 49.5 | 5.048
338.4 | 49.5 | 5.048
338.5 | 49.5 | 5.048
338.6 | 49.5 | 5.048
338.7 | 49.5 | 5.048
338.8 | 49.5 | 5.048
338.9 | 49.5 | 5.048
339 | 49.5 | 5.048
339.1 | 49.5 | 5.048
339.2 | 49.5 | 5.048
339.3 | 49.5 | 5.048
339.4 | 49.5 | 5.048
339.5 | 49.5 | 5.048
339.6 | 49.5 | 5.048
339.7 | 49.5 | 5.048
339.8 | 49.5 | 5.048
339.9 | 49.5 | 5.048
340 | 49.5 | 5.048
340.1 | 49.5 | 5.048
340.2 | 49.5 | 5.048
340.3 | 49.5 | 5.048
340.4 | 49.5 | 5.048
340.5 | 49.5 | 5.048
340.6 | 49.5 | 5.048
340.7 | 49.5 | 5.048
340.8 | 49.5 | 5.048
340.9 | 49.5 | 5.048
341 | 49.5 | 5.048
341.1 | 49.5 | 5.048
341.2 | 49.5 | 5.048
341.3 | 49.5 | 5.048
341.4 | 49.5 | 5.048
341.5 | 49.5 | 5.048
341.6 | 49.5 | 5.048
341.7 | 49.5 | 5.048
341.8 | 49.5 | 5.048
341.9 | 49.5 | 5.048
342 | 49.5 | 5.048
342.1 | 49.5 | 5.048
342.2 | 49.5 | 5.048
342.3 | 49.5 | 5.048
342.4 | 49.5 | 5.048
342.5 | 49.5 | 5.048
342.6 | 49.5 | 5.048
342.7 | 49.5 | 5.048
342.8 | 49.5 | 5.048
342.9 | 49.5 | 5.048
343 | 49.5 | 5.048
343.1 | 49.5 | 5.048
343.2 | 49.5 | 5.048
343.3 | 49.5 | 5.048
343.4 | 49.5 | 5.048
343.5 | 49.5 | 5.048
343.6 | 49.5 | 5.048
343.7 | 49.5 | 5.048
343.8 | 49.5 | 5.048
343.9 | 49.5 | 5.048
344 | 49.5 | 5.048
344.1 | 49.5 | 5.048
344.2 | 49.5 | 5.048
344.3 | 49.5 | 5.048
344.4 | 49.5 | 5.048
344.5 | 49.5 | 5.048
344.6 | 49.5 | 5.048
344.7 | 49.5 | 5.048
344.8 | 49.5 | 5.048
344.9 | 49.5 | 5.048
345 | 49.5 | 5.048
345.1 | 49.5 | 5.048
345.2 | 49.5 | 5.048
345.3 | 49.5 | 5.048
345.4 | 49.5 | 5.048
345.5 | 49.5 | 5.048
345.6 | 49.5 | 5.048
345.7 | 49.5 | 5.048
345.8 | 49.5 | 5.048
345.9 | 49.5 | 5.048
346 | 49.5 | 5.048
346.1 | 49.5 | 5.048
346.2 | 49.5 | 5.048
346.3 | 49.5 | 5.049
346.4 | 49.5 | 5.049
346.5 | 49.5 | 5.05
346.6 | 49.5 | 5.05
346.7 | 49.5 | 5.05
346.8 | 49.5 | 5.05
346.9 | 49.5 | 5.05
347 | 49.5 | 5.05
347.1 | 49.5 | 5.05
347.2 | 49.5 | 5.049
347.3 | 49.5 | 5.049
347.4 | 49.5 | 5.049
347.5 | 49.5 | 5.049
347.6 | 49.5 | 5.049
347.7 | 49.5 | 5.049
347.8 | 49.5 | 5.049
347.9 | 49.5 | 5.049
348 | 49.5 | 5.049
348.1 | 49.5 | 5.049
348.2 | 49.5 | 5.049
348.3 | 49.5 | 5.049
348.4 | 49.5 | 5.049
348.5 | 49.5 | 5.049
348.6 | 49.5 | 5.049
348.7 | 49.5 | 5.049
348.8 | 49.5 | 5.049
348.9 | 49.5 | 5.048
349 | 49.5 | 5.048
349.1 | 49.5 | 5.048
349.2 | 49.5 | 5.048
349.3 | 49.5 | 5.048
349.4 | 49.5 | 5.048
349.5 | 49.5 | 5.048
349.6 | 49.5 | 5.048
349.7 | 49.5 | 5.048
349.8 | 49.5 | 5.048
349.9 | 49.5 | 5.048
350 | 49.5 | 5.048
350.1 | 49.5 | 5.048
350.2 | 49.5 | 5.048
350.3 | 49.5 | 5.048
350.4 | 49.5 | 5.048
350.5 | 49.5 | 5.048
350.6 | 49.5 | 5.048
350.7 | 49.5 | 5.048
350.8 | 49.5 | 5.048
350.9 | 49.5 | 5.048
351 | 49.5 | 5.048
351.1 | 49.5 | 5.048
351.2 | 49.5 | 5.048
351.3 | 49.5 | 5.048
351.4 | 49.5 | 5.048
351.5 | 49.5 | 5.048
351.6 | 49.5 | 5.048
351.7 | 49.5 | 5.048
351.8 | 49.5 | 5.048
351.9 | 49.5 | 5.048
352 | 49.5 | 5.048
352.1 | 49.5 | 5.048
352.2 | 49.5 | 5.048
352.3 | 49.5 | 5.048
352.4 | 49.5 | 5.048
352.5 | 49.5 | 5.048
352.6 | 49.5 | 5.048
352.7 | 49.5 | 5.048
352.8 | 49.5 | 5.048
352.9 | 49.5 | 5.048
353 | 49.5 | 5.048
353.1 | 49.5 | 5.048
353.2 | 49.5 | 5.048
353.3 | 49.5 | 5.048
353.4 | 49.5 | 5.049
353.5 | 49.5 | 5.049
353.6 | 49.5 | 5.049
353.7 | 49.5 | 5.049
353.8 | 49.5 | 5.049
353.9 | 49.5 | 5.049
354 | 49.5 | 5.049
354.1 | 49.5 | 5.049
354.2 | 49.5 | 5.049
354.3 | 49.5 | 5.049
354.4 | 49.5 | 5.049
354.5 | 49.5 | 5.049
354.6 | 49.5 | 5.048
354.7 | 49.5 | 5.049
354.8 | 49.5 | 5.049
354.9 | 49.5 | 5.049
355 | 49.5 | 5.049
355.1 | 49.5 | 5.049
355.2 | 49.5 | 5.049
355.3 | 49.5 | 5.049
355.4 | 49.5 | 5.049
355.5 | 49.5 | 5.049
355.6 | 49.5 | 5.048
355.7 | 49.5 | 5.048
355.8 | 49.5 | 5.048
355.9 | 49.5 | 5.048
356 | 49.5 | 5.048
356.1 | 49.5 | 5.048
356.2 | 49.5 | 5.048
356.3 | 49.5 | 5.048
356.4 | 49.5 | 5.048
356.5 | 49.5 | 5.048
356.6 | 49.5 | 5.048
356.7 | 49.5 | 5.048
356.8 | 49.5 | 5.048
356.9 | 49.5 | 5.048
357 | 49.5 | 5.048
357.1 | 49.5 | 5.048
357.2 | 49.5 | 5.048
357.3 | 49.5 | 5.048
357.4 | 49.5 | 5.048
357.5 | 49.5 | 5.048
357.6 | 49.5 | 5.048
357.7 | 49.5 | 5.048
357.8 | 49.5 | 5.048
357.9 | 49.5 | 5.048
358 | 49.5 | 5.048
358.1 | 49.5 | 5.048
358.2 | 49.5 | 5.048
358.3 | 49.5 | 5.048
358.4 | 49.5 | 5.048
358.5 | 49.5 | 5.048
358.6 | 49.5 | 5.048
358.7 | 49.5 | 5.048
358.8 | 49.5 | 5.048
358.9 | 49.5 | 5.048
359 | 49.5 | 5.048
359.1 | 49.5 | 5.048
359.2 | 49.5 | 5.049
359.3 | 49.5 | 5.049
359.4 | 49.5 | 5.049
359.5 | 49.5 | 5.049
359.6 | 49.5 | 5.049
359.7 | 49.5 | 5.049
359.8 | 49.5 | 5.049
359.9 | 49.5 | 5.049
360 | 49.5 | 5.049
360.1 | 49.5 | 5.049
360.2 | 49.5 | 5.049
360.3 | 49.5 | 5.049
360.4 | 49.5 | 5.049
360.5 | 49.5 | 5.049
360.6 | 49.5 | 5.049
360.7 | 49.5 | 5.049
360.8 | 49.5 | 5.049
360.9 | 49.5 | 5.049
361 | 49.5 | 5.049
361.1 | 49.5 | 5.049
361.2 | 49.5 | 5.049
361.3 | 49.5 | 5.049
361.4 | 49.5 | 5.049
361.5 | 49.5 | 5.049
361.6 | 49.5 | 5.048
361.7 | 49.5 | 5.048
361.8 | 49.5 | 5.048
361.9 | 49.5 | 5.048
362 | 49.5 | 5.048
362.1 | 49.5 | 5.048
362.2 | 49.5 | 5.048
362.3 | 49.5 | 5.048
362.4 | 49.5 | 5.048
362.5 | 49.5 | 5.048
362.6 | 49.5 | 5.048
362.7 | 49.5 | 5.048
362.8 | 49.5 | 5.048
362.9 | 49.5 | 5.048
363 | 49.5 | 5.048
363.1 | 49.5 | 5.048
363.2 | 49.5 | 5.048
363.3 | 49.5 | 5.048
363.4 | 49.5 | 5.048
363.5 | 49.5 | 5.048
363.6 | 49.5 | 5.048
363.7 | 49.5 | 5.048
363.8 | 49.5 | 5.048
363.9 | 49.5 | 5.048
364 | 49.5 | 5.048
364.1 | 49.5 | 5.048
364.2 | 49.5 | 5.048
364.3 | 49.5 | 5.048
364.4 | 49.5 | 5.048
364.5 | 49.5 | 5.048
364.6 | 49.5 | 5.048
364.7 | 49.5 | 5.048
364.8 | 49.5 | 5.048
364.9 | 49.5 | 5.048
365 | 49.5 | 5.048
365.1 | 49.5 | 5.049
365.2 | 49.5 | 5.049
365.3 | 49.5 | 5.049
365.4 | 49.5 | 5.049
365.5 | 49.5 | 5.049
365.6 | 49.5 | 5.049
365.7 | 49.5 | 5.049
365.8 | 49.5 | 5.049
365.9 | 49.5 | 5.049
366 | 49.5 | 5.049
366.1 | 49.5 | 5.049
366.2 | 49.5 | 5.048
366.3 | 49.5 | 5.048
366.4 | 49.5 | 5.048
366.5 | 49.5 | 5.048
366.6 | 49.5 | 5.048
366.7 | 49.5 | 5.048
366.8 | 49.5 | 5.048
366.9 | 49.5 | 5.048
367 | 49.5 | 5.048
367.1 | 49.5 | 5.048
367.2 | 49.5 | 5.048
367.3 | 49.5 | 5.048
367.4 | 49.5 | 5.048
367.5 | 49.5 | 5.048
367.6 | 49.5 | 5.048
367.7 | 49.5 | 5.048
367.8 | 49.5 | 5.048
367.9 | 49.5 | 5.048
368 | 49.5 | 5.048
368.1 | 49.5 | 5.048
368.2 | 49.5 | 5.048
368.3 | 49.5 | 5.048
368.4 | 49.5 | 5.048
368.5 | 49.5 | 5.048
368.6 | 49.5 | 5.049
368.7 | 49.5 | 5.049
368.8 | 49.5 | 5.049
368.9 | 49.5 | 5.049
369 | 49.5 | 5.049
369.1 | 49.5 | 5.049
369.2 | 49.5 | 5.049
369.3 | 49.5 | 5.049
369.4 | 49.5 | 5.049
369.5 | 49.5 | 5.049
369.6 | 49.5 | 5.049
369.7 | 49.5 | 5.048
369.8 | 49.5 | 5.048
369.9 | 49.5 | 5.048
370 | 49.5 | 5.048
370.1 | 49.5 | 5.048
370.2 | 49.5 | 5.048
370.3 | 49.5 | 5.048
370.4 | 49.5 | 5.048
370.5 | 49.5 | 5.048
370.6 | 49.5 | 5.048
370.7 | 49.5 | 5.048
370.8 | 49.5 | 5.048
370.9 | 49.5 | 5.048
371 | 49.5 | 5.048
371.1 | 49.5 | 5.048
371.2 | 49.5 | 5.048
371.3 | 49.5 | 5.048
371.4 | 49.5 | 5.048
371.5 | 49.5 | 5.048
371.6 | 49.5 | 5.048
371.7 | 49.5 | 5.048
371.8 | 49.5 | 5.048
371.9 | 49.5 | 5.048
372 | 49.5 | 5.048
372.1 | 49.5 | 5.048
372.2 | 49.5 | 5.048
372.3 | 49.5 | 5.048
372.4 | 49.5 | 5.048
372.5 | 49.5 | 5.048
372.6 | 49.5 | 5.048
372.7 | 49.5 | 5.048
372.8 | 49.5 | 5.048
372.9 | 49.5 | 5.048
373 | 49.5 | 5.048
373.1 | 49.5 | 5.048
373.2 | 49.5 | 5.048
373.3 | 49.5 | 5.048
373.4 | 49.5 | 5.048
373.5 | 49.5 | 5.048
373.6 | 49.5 | 5.048
373.7 | 49.5 | 5.048
373.8 | 49.5 | 5.048
373.9 | 49.5 | 5.048
374 | 49.5 | 5.048
374.1 | 49.5 | 5.048
374.2 | 49.5 | 5.048
374.3 | 49.5 | 5.048
374.4 | 49.5 | 5.048
374.5 | 49.5 | 5.049
374.6 | 49.5 | 5.049
374.7 | 49.5 | 5.049
374.8 | 49.5 | 5.049
374.9 | 49.5 | 5.049
375 | 49.5 | 5.049
375.1 | 49.5 | 5.049
375.2 | 49.5 | 5.049
375.3 | 49.5 | 5.049
375.4 | 49.5 | 5.049
375.5 | 49.5 | 5.049
375.6 | 49.5 | 5.049
375.7 | 49.5 | 5.048
375.8 | 49.5 | 5.048
375.9 | 49.5 | 5.048
376 | 49.5 | 5.048
376.1 | 49.5 | 5.048
376.2 | 49.5 | 5.048
376.3 | 49.5 | 5.048
376.4 | 49.5 | 5.048
376.5 | 49.5 | 5.048
376.6 | 49.5 | 5.048
376.7 | 49.5 | 5.048
376.8 | 49.5 | 5.048
376.9 | 49.5 | 5.048
377 | 49.5 | 5.048
377.1 | 49.5 | 5.048
377.2 | 49.5 | 5.048
377.3 | 49.5 | 5.048
377.4 | 49.5 | 5.048
377.5 | 49.5 | 5.048
377.6 | 49.5 | 5.048
377.7 | 49.5 | 5.048
377.8 | 49.5 | 5.048
377.9 | 49.5 | 5.048
378 | 49.5 | 5.048
378.1 | 49.5 | 5.048
378.2 | 49.5 | 5.048
378.3 | 49.5 | 5.048
378.4 | 49.5 | 5.048
378.5 | 49.5 | 5.048
378.6 | 49.5 | 5.048
378.7 | 49.5 | 5.048
378.8 | 49.5 | 5.048
378.9 | 49.5 | 5.048
379 | 49.5 | 5.048
379.1 | 49.5 | 5.048
379.2 | 49.5 | 5.048
379.3 | 49.5 | 5.048
379.4 | 49.5 | 5.048
379.5 | 49.5 | 5.048
379.6 | 49.5 | 5.048
379.7 | 49.5 | 5.048
379.8 | 49.5 | 5.048
379.9 | 49.5 | 5.048
380 | 49.5 | 5.048
380.1 | 49.5 | 5.048
380.2 | 49.5 | 5.049
380.3 | 49.5 | 5.049
380.4 | 49.5 | 5.049
380.5 | 49.5 | 5.049
380.6 | 49.5 | 5.049
380.7 | 49.5 | 5.049
380.8 | 49.5 | 5.049
380.9 | 49.5 | 5.049
381 | 49.5 | 5.049
381.1 | 49.5 | 5.049
381.2 | 49.5 | 5.049
381.3 | 49.5 | 5.049
381.4 | 49.5 | 5.049
381.5 | 49.5 | 5.048
381.6 | 49.5 | 5.048
381.7 | 49.5 | 5.048
381.8 | 49.5 | 5.048
381.9 | 49.5 | 5.048
382 | 49.5 | 5.048
382.1 | 49.5 | 5.048
382.2 | 49.5 | 5.048
382.3 | 49.5 | 5.048
382.4 | 49.5 | 5.048
382.5 | 49.5 | 5.047
382.6 | 49.5 | 5.047
382.7 | 49.5 | 5.048
382.8 | 49.5 | 5.048
382.9 | 49.5 | 5.048
383 | 49.5 | 5.048
383.1 | 49.5 | 5.048
383.2 | 49.5 | 5.048
383.3 | 49.5 | 5.048
383.4 | 49.5 | 5.048
383.5 | 49.5 | 5.048
383.6 | 49.5 | 5.048
383.7 | 49.5 | 5.049
383.8 | 49.5 | 5.049
383.9 | 49.5 | 5.049
384 | 49.5 | 5.048
384.1 | 49.5 | 5.048
384.2 | 49.5 | 5.048
384.3 | 49.5 | 5.048
384.4 | 49.5 | 5.048
384.5 | 49.5 | 5.048
384.6 | 49.5 | 5.048
384.7 | 49.5 | 5.048
384.8 | 49.5 | 5.049
384.9 | 49.5 | 5.049
385 | 49.5 | 5.049
385.1 | 49.5 | 5.049
385.2 | 49.5 | 5.049
385.3 | 49.5 | 5.049
385.4 | 49.5 | 5.049
385.5 | 49.5 | 5.049
385.6 | 49.5 | 5.049
385.7 | 49.5 | 5.049
385.8 | 49.5 | 5.049
385.9 | 49.5 | 5.049
386 | 49.5 | 5.049
386.1 | 49.5 | 5.049
386.2 | 49.5 | 5.048
386.3 | 49.5 | 5.048
386.4 | 49.5 | 5.048
386.5 | 49.5 | 5.048
386.6 | 49.5 | 5.048
386.7 | 49.5 | 5.048
386.8 | 49.5 | 5.048
386.9 | 49.5 | 5.048
387 | 49.5 | 5.048
387.1 | 49.5 | 5.048
387.2 | 49.5 | 5.048
387.3 | 49.5 | 5.048
387.4 | 49.5 | 5.048
387.5 | 49.5 | 5.048
387.6 | 49.5 | 5.048
387.7 | 49.5 | 5.048
387.8 | 49.5 | 5.048
387.9 | 49.5 | 5.048
388 | 49.5 | 5.048
388.1 | 49.5 | 5.048
388.2 | 49.5 | 5.048
388.3 | 49.5 | 5.048
388.4 | 49.5 | 5.048
388.5 | 49.5 | 5.048
388.6 | 49.5 | 5.048
388.7 | 49.5 | 5.048
388.8 | 49.5 | 5.048
388.9 | 49.5 | 5.048
389 | 49.5 | 5.048
389.1 | 49.5 | 5.048
389.2 | 49.5 | 5.048
389.3 | 49.5 | 5.048
389.4 | 49.5 | 5.048
389.5 | 49.5 | 5.048
389.6 | 49.5 | 5.048
389.7 | 49.5 | 5.048
389.8 | 49.5 | 5.048
389.9 | 49.5 | 5.048
390 | 49.5 | 5.048
390.1 | 49.5 | 5.048
390.2 | 49.5 | 5.048
390.3 | 49.5 | 5.048
390.4 | 49.5 | 5.048
390.5 | 49.5 | 5.048
390.6 | 49.5 | 5.048
390.7 | 49.5 | 5.048
390.8 | 49.5 | 5.048
390.9 | 49.5 | 5.048
391 | 49.5 | 5.048
391.1 | 49.5 | 5.048
391.2 | 49.5 | 5.048
391.3 | 49.5 | 5.048
391.4 | 49.5 | 5.048
391.5 | 49.5 | 5.048
391.6 | 49.5 | 5.048
391.7 | 49.5 | 5.048
391.8 | 49.5 | 5.049
391.9 | 49.5 | 5.049
392 | 49.5 | 5.049
392.1 | 49.5 | 5.048
392.2 | 49.5 | 5.048
392.3 | 49.5 | 5.048
392.4 | 49.5 | 5.048
392.5 | 49.5 | 5.048
392.6 | 49.5 | 5.048
392.7 | 49.5 | 5.048
392.8 | 49.5 | 5.048
392.9 | 49.5 | 5.048
393 | 49.5 | 5.048
393.1 | 49.5 | 5.048
393.2 | 49.5 | 5.048
393.3 | 49.5 | 5.049
393.4 | 49.5 | 5.049
393.5 | 49.5 | 5.049
393.6 | 49.5 | 5.049
393.7 | 49.5 | 5.049
393.8 | 49.5 | 5.049
393.9 | 49.5 | 5.049
394 | 49.5 | 5.049
394.1 | 49.5 | 5.049
394.2 | 49.5 | 5.048
394.3 | 49.5 | 5.048
394.4 | 49.5 | 5.048
394.5 | 49.5 | 5.048
394.6 | 49.5 | 5.048
394.7 | 49.5 | 5.048
394.8 | 49.5 | 5.048
394.9 | 49.5 | 5.048
395 | 49.5 | 5.048
395.1 | 49.5 | 5.048
395.2 | 49.5 | 5.048
395.3 | 49.5 | 5.048
395.4 | 49.5 | 5.048
395.5 | 49.5 | 5.048
395.6 | 49.5 | 5.049
395.7 | 49.5 | 5.049
395.8 | 49.5 | 5.049
395.9 | 49.5 | 5.049
396 | 49.5 | 5.049
396.1 | 49.5 | 5.049
396.2 | 49.5 | 5.049
396.3 | 49.5 | 5.049
396.4 | 49.5 | 5.049
396.5 | 49.5 | 5.049
396.6 | 49.5 | 5.049
396.7 | 49.5 | 5.049
396.8 | 49.5 | 5.048
396.9 | 49.5 | 5.048
397 | 49.5 | 5.048
397.1 | 49.5 | 5.048
397.2 | 49.5 | 5.048
397.3 | 49.5 | 5.048
397.4 | 49.5 | 5.048
397.5 | 49.5 | 5.048
397.6 | 49.5 | 5.048
397.7 | 49.5 | 5.048
397.8 | 49.5 | 5.048
397.9 | 49.5 | 5.048
398 | 49.5 | 5.048
398.1 | 49.5 | 5.048
398.2 | 49.5 | 5.048
398.3 | 49.5 | 5.048
398.4 | 49.5 | 5.048
398.5 | 49.5 | 5.048
398.6 | 49.5 | 5.048
398.7 | 49.5 | 5.048
398.8 | 49.5 | 5.048
398.9 | 49.5 | 5.048
399 | 49.5 | 5.048
399.1 | 49.5 | 5.048
399.2 | 49.5 | 5.048
399.3 | 49.5 | 5.048
399.4 | 49.5 | 5.048
399.5 | 49.5 | 5.048
399.6 | 49.5 | 5.048
399.7 | 49.5 | 5.048
399.8 | 49.5 | 5.048
399.9 | 49.5 | 5.048
400 | 49.5 | 5.048
400.1 | 49.5 | 5.048
400.2 | 49.5 | 5.048
400.3 | 49.5 | 5.048
400.4 | 49.5 | 5.048
400.5 | 49.5 | 5.048
400.6 | 49.5 | 5.048
400.7 | 49.5 | 5.048
400.8 | 49.5 | 5.048
400.9 | 49.5 | 5.048
401 | 49.5 | 5.048
401.1 | 49.5 | 5.048
401.2 | 49.5 | 5.048
401.3 | 49.5 | 5.048
401.4 | 49.5 | 5.048
401.5 | 49.5 | 5.048
401.6 | 49.5 | 5.048
401.7 | 49.5 | 5.048
401.8 | 49.5 | 5.048
401.9 | 49.5 | 5.048
402 | 49.5 | 5.048
402.1 | 49.5 | 5.048
402.2 | 49.5 | 5.048
402.3 | 49.5 | 5.048
402.4 | 49.5 | 5.048
402.5 | 49.5 | 5.048
402.6 | 49.5 | 5.048
402.7 | 49.5 | 5.048
402.8 | 49.5 | 5.048
402.9 | 49.5 | 5.048
403 | 49.5 | 5.048
403.1 | 49.5 | 5.048
403.2 | 49.5 | 5.048
403.3 | 49.5 | 5.048
403.4 | 49.5 | 5.048
403.5 | 49.5 | 5.048
403.6 | 49.5 | 5.048
403.7 | 49.5 | 5.048
403.8 | 49.5 | 5.048
403.9 | 49.5 | 5.048
404 | 49.5 | 5.048
404.1 | 49.5 | 5.048
404.2 | 49.5 | 5.048
404.3 | 49.5 | 5.048
404.4 | 49.5 | 5.048
404.5 | 49.5 | 5.048
404.6 | 49.5 | 5.048
404.7 | 49.5 | 5.048
404.8 | 49.5 | 5.048
404.9 | 49.5 | 5.048
405 | 49.5 | 5.048
405.1 | 49.5 | 5.048
405.2 | 49.5 | 5.048
405.3 | 49.5 | 5.048
405.4 | 49.5 | 5.048
405.5 | 49.5 | 5.048
405.6 | 49.5 | 5.048
405.7 | 49.5 | 5.048
405.8 | 49.5 | 5.049
405.9 | 49.5 | 5.049
406 | 49.5 | 5.049
406.1 | 49.5 | 5.049
406.2 | 49.5 | 5.049
406.3 | 49.5 | 5.049
406.4 | 49.5 | 5.049
406.5 | 49.5 | 5.049
406.6 | 49.5 | 5.049
406.7 | 49.5 | 5.049
406.8 | 49.5 | 5.048
406.9 | 49.5 | 5.048
407 | 49.5 | 5.048
407.1 | 49.5 | 5.048
407.2 | 49.5 | 5.048
407.3 | 49.5 | 5.048
407.4 | 49.5 | 5.048
407.5 | 49.5 | 5.048
407.6 | 49.5 | 5.048
407.7 | 49.5 | 5.048
407.8 | 49.5 | 5.048
407.9 | 49.5 | 5.048
408 | 49.5 | 5.048
408.1 | 49.5 | 5.048
408.2 | 49.5 | 5.048
408.3 | 49.5 | 5.048
408.4 | 49.5 | 5.048
408.5 | 49.5 | 5.048
408.6 | 49.5 | 5.048
408.7 | 49.5 | 5.048
408.8 | 49.5 | 5.048
408.9 | 49.5 | 5.048
409 | 49.5 | 5.048
409.1 | 49.5 | 5.048
409.2 | 49.5 | 5.048
409.3 | 49.5 | 5.048
409.4 | 49.5 | 5.048
409.5 | 49.5 | 5.048
409.6 | 49.5 | 5.048
409.7 | 49.5 | 5.048
409.8 | 49.5 | 5.048
409.9 | 49.5 | 5.048
410 | 49.5 | 5.048
410.1 | 49.5 | 5.048
410.2 | 49.5 | 5.048
410.3 | 49.5 | 5.048
410.4 | 49.5 | 5.048
410.5 | 49.5 | 5.048
410.6 | 49.5 | 5.048
410.7 | 49.5 | 5.048
410.8 | 49.5 | 5.048
410.9 | 49.5 | 5.048
411 | 49.5 | 5.048
411.1 | 49.5 | 5.048
411.2 | 49.5 | 5.048
411.3 | 49.5 | 5.048
411.4 | 49.5 | 5.048
411.5 | 49.5 | 5.048
411.6 | 49.5 | 5.048
411.7 | 49.5 | 5.048
411.8 | 49.5 | 5.048
411.9 | 49.5 | 5.048
412 | 49.5 | 5.048
412.1 | 49.5 | 5.048
412.2 | 49.5 | 5.048
412.3 | 49.5 | 5.048
412.4 | 49.5 | 5.048
412.5 | 49.5 | 5.048
412.6 | 49.5 | 5.048
412.7 | 49.5 | 5.048
412.8 | 49.5 | 5.048
412.9 | 49.5 | 5.048
413 | 49.5 | 5.048
413.1 | 49.5 | 5.048
413.2 | 49.5 | 5.048
413.3 | 49.5 | 5.048
413.4 | 49.5 | 5.048
413.5 | 49.5 | 5.048
413.6 | 49.5 | 5.048
413.7 | 49.5 | 5.048
413.8 | 49.5 | 5.048
413.9 | 49.5 | 5.048
414 | 49.5 | 5.048
414.1 | 49.5 | 5.048
414.2 | 49.5 | 5.048
414.3 | 49.5 | 5.048
414.4 | 49.5 | 5.048
414.5 | 49.5 | 5.048
414.6 | 49.5 | 5.048
414.7 | 49.5 | 5.048
414.8 | 49.5 | 5.048
414.9 | 49.5 | 5.048
415 | 49.5 | 5.048
415.1 | 49.5 | 5.048
415.2 | 49.5 | 5.048
415.3 | 49.5 | 5.048
415.4 | 49.5 | 5.048
415.5 | 49.5 | 5.048
415.6 | 49.5 | 5.048
415.7 | 49.5 | 5.048
415.8 | 49.5 | 5.048
415.9 | 49.5 | 5.048
416 | 49.5 | 5.048
416.1 | 49.5 | 5.048
416.2 | 49.5 | 5.048
416.3 | 49.5 | 5.048
416.4 | 49.5 | 5.048
416.5 | 49.5 | 5.048
416.6 | 49.5 | 5.048
416.7 | 49.5 | 5.048
416.8 | 49.5 | 5.048
416.9 | 49.5 | 5.048
417 | 49.5 | 5.048
417.1 | 49.5 | 5.048
417.2 | 49.5 | 5.048
417.3 | 49.5 | 5.048
417.4 | 49.5 | 5.048
417.5 | 49.5 | 5.048
417.6 | 49.5 | 5.048
417.7 | 49.5 | 5.048
417.8 | 49.5 | 5.048
417.9 | 49.5 | 5.048
418 | 49.5 | 5.048
418.1 | 49.5 | 5.048
418.2 | 49.5 | 5.048
418.3 | 49.5 | 5.048
418.4 | 49.5 | 5.048
418.5 | 49.5 | 5.048
418.6 | 49.5 | 5.048
418.7 | 49.5 | 5.048
418.8 | 49.5 | 5.048
418.9 | 49.5 | 5.048
419 | 49.5 | 5.048
419.1 | 49.5 | 5.048
419.2 | 49.5 | 5.048
419.3 | 49.5 | 5.048
419.4 | 49.5 | 5.048
419.5 | 49.5 | 5.048
419.6 | 49.5 | 5.048
419.7 | 49.5 | 5.048
419.8 | 49.5 | 5.048
419.9 | 49.5 | 5.048
420 | 49.5 | 5.048
420.1 | 49.5 | 5.048
420.2 | 49.5 | 5.048
420.3 | 49.5 | 5.048
420.4 | 49.5 | 5.048
420.5 | 49.5 | 5.048
420.6 | 49.5 | 5.048
420.7 | 49.5 | 5.048
420.8 | 49.5 | 5.048
420.9 | 49.5 | 5.048
421 | 49.5 | 5.048
421.1 | 49.5 | 5.048
421.2 | 49.5 | 5.048
421.3 | 49.5 | 5.048
421.4 | 49.5 | 5.048
421.5 | 49.5 | 5.048
421.6 | 49.5 | 5.048
421.7 | 49.5 | 5.048
421.8 | 49.5 | 5.048
421.9 | 49.5 | 5.048
422 | 49.5 | 5.048
422.1 | 49.5 | 5.048
422.2 | 49.5 | 5.049
422.3 | 49.5 | 5.049
422.4 | 49.5 | 5.049
422.5 | 49.5 | 5.049
422.6 | 49.5 | 5.049
422.7 | 49.5 | 5.049
422.8 | 49.5 | 5.049
422.9 | 49.5 | 5.049
423 | 49.5 | 5.049
423.1 | 49.5 | 5.049
423.2 | 49.5 | 5.049
423.3 | 49.5 | 5.049
423.4 | 49.5 | 5.049
423.5 | 49.5 | 5.049
423.6 | 49.5 | 5.049
423.7 | 49.5 | 5.049
423.8 | 49.5 | 5.049
423.9 | 49.5 | 5.049
424 | 49.5 | 5.049
424.1 | 49.5 | 5.049
424.2 | 49.5 | 5.049
424.3 | 49.5 | 5.049
424.4 | 49.5 | 5.049
424.5 | 49.5 | 5.049
424.6 | 49.5 | 5.049
424.7 | 49.5 | 5.049
424.8 | 49.5 | 5.049
424.9 | 49.5 | 5.049
425 | 49.5 | 5.049
425.1 | 49.5 | 5.049
425.2 | 49.5 | 5.049
425.3 | 49.5 | 5.049
425.4 | 49.5 | 5.049
425.5 | 49.5 | 5.049
425.6 | 49.5 | 5.048
425.7 | 49.5 | 5.048
425.8 | 49.5 | 5.048
425.9 | 49.5 | 5.048
426 | 49.5 | 5.048
426.1 | 49.5 | 5.048
426.2 | 49.5 | 5.048
426.3 | 49.5 | 5.048
426.4 | 49.5 | 5.048
426.5 | 49.5 | 5.048
426.6 | 49.5 | 5.048
426.7 | 49.5 | 5.048
426.8 | 49.5 | 5.048
426.9 | 49.5 | 5.048
427 | 49.5 | 5.048
427.1 | 49.5 | 5.048
427.2 | 49.5 | 5.048
427.3 | 49.5 | 5.048
427.4 | 49.5 | 5.048
427.5 | 49.5 | 5.048
427.6 | 49.5 | 5.048
427.7 | 49.5 | 5.048
427.8 | 49.5 | 5.048
427.9 | 49.5 | 5.048
428 | 49.5 | 5.048
428.1 | 49.5 | 5.048
428.2 | 49.5 | 5.048
428.3 | 49.5 | 5.048
428.4 | 49.5 | 5.048
428.5 | 49.5 | 5.048
428.6 | 49.5 | 5.048
428.7 | 49.5 | 5.048
428.8 | 49.5 | 5.048
428.9 | 49.5 | 5.048
429 | 49.5 | 5.048
429.1 | 49.5 | 5.048
429.2 | 49.5 | 5.048
429.3 | 49.5 | 5.048
429.4 | 49.5 | 5.048
429.5 | 49.5 | 5.048
429.6 | 49.5 | 5.048
429.7 | 49.5 | 5.048
429.8 | 49.5 | 5.048
429.9 | 49.5 | 5.048
430 | 49.5 | 5.048
430.1 | 49.5 | 5.048
430.2 | 49.5 | 5.048
430.3 | 49.5 | 5.048
430.4 | 49.5 | 5.048
430.5 | 49.5 | 5.048
430.6 | 49.5 | 5.048
430.7 | 49.5 | 5.048
430.8 | 49.5 | 5.048
430.9 | 49.5 | 5.048
431 | 49.5 | 5.048
431.1 | 49.5 | 5.048
431.2 | 49.5 | 5.048
431.3 | 49.5 | 5.048
431.4 | 49.5 | 5.048
431.5 | 49.5 | 5.048
431.6 | 49.5 | 5.048
431.7 | 49.5 | 5.048
431.8 | 49.5 | 5.048
431.9 | 49.5 | 5.048
432 | 49.5 | 5.048
432.1 | 49.5 | 5.048
432.2 | 49.5 | 5.048
432.3 | 49.5 | 5.048
432.4 | 49.5 | 5.048
432.5 | 49.5 | 5.048
432.6 | 49.5 | 5.048
432.7 | 49.5 | 5.049
432.8 | 49.5 | 5.049
432.9 | 49.5 | 5.049
433 | 49.5 | 5.049
433.1 | 49.5 | 5.049
433.2 | 49.5 | 5.049
433.3 | 49.5 | 5.049
433.4 | 49.5 | 5.049
433.5 | 49.5 | 5.049
433.6 | 49.5 | 5.049
433.7 | 49.5 | 5.049
433.8 | 49.5 | 5.049
433.9 | 49.5 | 5.049
434 | 49.5 | 5.049
434.1 | 49.5 | 5.049
434.2 | 49.5 | 5.049
434.3 | 49.5 | 5.049
434.4 | 49.5 | 5.049
434.5 | 49.5 | 5.049
434.6 | 49.5 | 5.049
434.7 | 49.5 | 5.049
434.8 | 49.5 | 5.049
434.9 | 49.5 | 5.048
435 | 49.5 | 5.048
435.1 | 49.5 | 5.048
435.2 | 49.5 | 5.048
435.3 | 49.5 | 5.048
435.4 | 49.5 | 5.048
435.5 | 49.5 | 5.048
435.6 | 49.5 | 5.048
435.7 | 49.5 | 5.048
435.8 | 49.5 | 5.048
435.9 | 49.5 | 5.048
436 | 49.5 | 5.048
436.1 | 49.5 | 5.048
436.2 | 49.5 | 5.048
436.3 | 49.5 | 5.048
436.4 | 49.5 | 5.048
436.5 | 49.5 | 5.048
436.6 | 49.5 | 5.048
436.7 | 49.5 | 5.048
436.8 | 49.5 | 5.048
436.9 | 49.5 | 5.048
437 | 49.5 | 5.048
437.1 | 49.5 | 5.048
437.2 | 49.5 | 5.048
437.3 | 49.5 | 5.048
437.4 | 49.5 | 5.048
437.5 | 49.5 | 5.048
437.6 | 49.5 | 5.048
437.7 | 49.5 | 5.048
437.8 | 49.5 | 5.048
437.9 | 49.5 | 5.048
438 | 49.5 | 5.048
438.1 | 49.5 | 5.048
438.2 | 49.5 | 5.048
438.3 | 49.5 | 5.048
438.4 | 49.5 | 5.048
438.5 | 49.5 | 5.048
438.6 | 49.5 | 5.048
438.7 | 49.5 | 5.048
438.8 | 49.5 | 5.048
438.9 | 49.5 | 5.048
439 | 49.5 | 5.048
439.1 | 49.5 | 5.048
439.2 | 49.5 | 5.048
439.3 | 49.5 | 5.048
439.4 | 49.5 | 5.048
439.5 | 49.5 | 5.048
439.6 | 49.5 | 5.048
439.7 | 49.5 | 5.048
439.8 | 49.5 | 5.048
439.9 | 49.5 | 5.048
440 | 49.5 | 5.048
440.1 | 49.5 | 5.048
440.2 | 49.5 | 5.048
440.3 | 49.5 | 5.048
440.4 | 49.5 | 5.048
440.5 | 49.5 | 5.048
440.6 | 49.5 | 5.048
440.7 | 49.5 | 5.048
440.8 | 49.5 | 5.048
440.9 | 49.5 | 5.048
441 | 49.5 | 5.048
441.1 | 49.5 | 5.048
441.2 | 49.5 | 5.048
441.3 | 49.5 | 5.048
441.4 | 49.5 | 5.048
441.5 | 49.5 | 5.048
441.6 | 49.5 | 5.048
441.7 | 49.5 | 5.048
441.8 | 49.5 | 5.048
441.9 | 49.5 | 5.048
442 | 49.5 | 5.048
442.1 | 49.5 | 5.049
442.2 | 49.5 | 5.049
442.3 | 49.5 | 5.049
442.4 | 49.5 | 5.049
442.5 | 49.5 | 5.049
442.6 | 49.5 | 5.049
442.7 | 49.5 | 5.049
442.8 | 49.5 | 5.049
442.9 | 49.5 | 5.049
443 | 49.5 | 5.049
443.1 | 49.5 | 5.049
443.2 | 49.5 | 5.048
443.3 | 49.5 | 5.048
443.4 | 49.5 | 5.048
443.5 | 49.5 | 5.048
443.6 | 49.5 | 5.048
443.7 | 49.5 | 5.048
443.8 | 49.5 | 5.048
443.9 | 49.5 | 5.048
444 | 49.5 | 5.048
444.1 | 49.5 | 5.048
444.2 | 49.5 | 5.048
444.3 | 49.5 | 5.048
444.4 | 49.5 | 5.048
444.5 | 49.5 | 5.048
444.6 | 49.5 | 5.048
444.7 | 49.5 | 5.048
444.8 | 49.5 | 5.048
444.9 | 49.5 | 5.048
445 | 49.5 | 5.048
445.1 | 49.5 | 5.048
445.2 | 49.5 | 5.048
445.3 | 49.5 | 5.048
445.4 | 49.5 | 5.048
445.5 | 49.5 | 5.048
445.6 | 49.5 | 5.048
445.7 | 49.5 | 5.048
445.8 | 49.5 | 5.048
445.9 | 49.5 | 5.048
446 | 49.5 | 5.048
446.1 | 49.5 | 5.048
446.2 | 49.5 | 5.048
446.3 | 49.5 | 5.048
446.4 | 49.5 | 5.048
446.5 | 49.5 | 5.048
446.6 | 49.5 | 5.048
446.7 | 49.5 | 5.049
446.8 | 49.5 | 5.049
446.9 | 49.5 | 5.049
447 | 49.5 | 5.049
447.1 | 49.5 | 5.049
447.2 | 49.5 | 5.049
447.3 | 49.5 | 5.049
447.4 | 49.5 | 5.049
447.5 | 49.5 | 5.049
447.6 | 49.5 | 5.049
447.7 | 49.5 | 5.049
447.8 | 49.5 | 5.049
447.9 | 49.5 | 5.049
448 | 49.5 | 5.048
448.1 | 49.5 | 5.048
448.2 | 49.5 | 5.048
448.3 | 49.5 | 5.048
448.4 | 49.5 | 5.048
448.5 | 49.5 | 5.048
448.6 | 49.5 | 5.048
448.7 | 49.5 | 5.048
448.8 | 49.5 | 5.048
448.9 | 49.5 | 5.048
449 | 49.5 | 5.048
449.1 | 49.5 | 5.048
449.2 | 49.5 | 5.048
449.3 | 49.5 | 5.048
449.4 | 49.5 | 5.048
449.5 | 49.5 | 5.048
449.6 | 49.5 | 5.048
449.7 | 49.5 | 5.048
449.8 | 49.5 | 5.048
449.9 | 49.5 | 5.048
450 | 49.5 | 5.048
450.1 | 49.5 | 5.048
450.2 | 49.5 | 5.048
450.3 | 49.5 | 5.048
450.4 | 49.5 | 5.048
450.5 | 49.5 | 5.048
450.6 | 49.5 | 5.048
450.7 | 49.5 | 5.048
450.8 | 49.5 | 5.048
450.9 | 49.5 | 5.048
451 | 49.5 | 5.048
451.1 | 49.5 | 5.048
451.2 | 49.5 | 5.048
451.3 | 49.5 | 5.048
451.4 | 49.5 | 5.048
451.5 | 49.5 | 5.048
451.6 | 49.5 | 5.048
451.7 | 49.5 | 5.048
451.8 | 49.5 | 5.048
451.9 | 49.5 | 5.048
452 | 49.5 | 5.048
452.1 | 49.5 | 5.048
452.2 | 49.5 | 5.048
452.3 | 49.5 | 5.048
452.4 | 49.5 | 5.048
452.5 | 49.5 | 5.048
452.6 | 49.5 | 5.048
452.7 | 49.5 | 5.048
452.8 | 49.5 | 5.048
452.9 | 49.5 | 5.048
453 | 49.5 | 5.048
453.1 | 49.5 | 5.048
453.2 | 49.5 | 5.048
453.3 | 49.5 | 5.048
453.4 | 49.5 | 5.048
453.5 | 49.5 | 5.048
453.6 | 49.5 | 5.048
453.7 | 49.5 | 5.048
453.8 | 49.5 | 5.048
453.9 | 49.5 | 5.048
454 | 49.5 | 5.048
454.1 | 49.5 | 5.048
454.2 | 49.5 | 5.048
454.3 | 49.5 | 5.048
454.4 | 49.5 | 5.048
454.5 | 49.5 | 5.048
454.6 | 49.5 | 5.048
454.7 | 49.5 | 5.048
454.8 | 49.5 | 5.048
454.9 | 49.5 | 5.048
455 | 49.5 | 5.048
455.1 | 49.5 | 5.048
455.2 | 49.5 | 5.048
455.3 | 49.5 | 5.048
455.4 | 49.5 | 5.048
455.5 | 49.5 | 5.048
455.6 | 49.5 | 5.048
455.7 | 49.5 | 5.048
455.8 | 49.5 | 5.048
455.9 | 49.5 | 5.048
456 | 49.5 | 5.048
456.1 | 49.5 | 5.048
456.2 | 49.5 | 5.048
456.3 | 49.5 | 5.048
456.4 | 49.5 | 5.048
456.5 | 49.5 | 5.048
456.6 | 49.5 | 5.048
456.7 | 49.5 | 5.048
456.8 | 49.5 | 5.048
456.9 | 49.5 | 5.048
457 | 49.5 | 5.048
457.1 | 49.5 | 5.048
457.2 | 49.5 | 5.048
457.3 | 49.5 | 5.048
457.4 | 49.5 | 5.048
457.5 | 49.5 | 5.048
457.6 | 49.5 | 5.048
457.7 | 49.5 | 5.048
457.8 | 49.5 | 5.048
457.9 | 49.5 | 5.048
458 | 49.5 | 5.048
458.1 | 49.5 | 5.048
458.2 | 49.5 | 5.048
458.3 | 49.5 | 5.048
458.4 | 49.5 | 5.048
458.5 | 49.5 | 5.048
458.6 | 49.5 | 5.048
458.7 | 49.5 | 5.048
458.8 | 49.5 | 5.048
458.9 | 49.5 | 5.048
459 | 49.5 | 5.048
459.1 | 49.5 | 5.048
459.2 | 49.5 | 5.048
459.3 | 49.5 | 5.048
459.4 | 49.5 | 5.048
459.5 | 49.5 | 5.048
459.6 | 49.5 | 5.048
459.7 | 49.5 | 5.048
459.8 | 49.5 | 5.048
459.9 | 49.5 | 5.048
460 | 49.5 | 5.048
460.1 | 49.5 | 5.048
460.2 | 49.5 | 5.048
460.3 | 49.5 | 5.048
460.4 | 49.5 | 5.048
460.5 | 49.5 | 5.048
460.6 | 49.5 | 5.048
460.7 | 49.5 | 5.048
460.8 | 49.5 | 5.048
460.9 | 49.5 | 5.048
461 | 49.5 | 5.048
461.1 | 49.5 | 5.048
461.2 | 49.5 | 5.048
461.3 | 49.5 | 5.048
461.4 | 49.5 | 5.048
461.5 | 49.5 | 5.048
461.6 | 49.5 | 5.048
461.7 | 49.5 | 5.048
461.8 | 49.5 | 5.048
461.9 | 49.5 | 5.048
462 | 49.5 | 5.048
462.1 | 49.5 | 5.048
462.2 | 49.5 | 5.048
462.3 | 49.5 | 5.048
462.4 | 49.5 | 5.049
462.5 | 49.5 | 5.049
462.6 | 49.5 | 5.049
462.7 | 49.5 | 5.049
462.8 | 49.5 | 5.049
462.9 | 49.5 | 5.049
463 | 49.5 | 5.049
463.1 | 49.5 | 5.049
463.2 | 49.5 | 5.049
463.3 | 49.5 | 5.049
463.4 | 49.5 | 5.049
463.5 | 49.5 | 5.049
463.6 | 49.5 | 5.049
463.7 | 49.5 | 5.049
463.8 | 49.5 | 5.049
463.9 | 49.5 | 5.049
464 | 49.5 | 5.049
464.1 | 49.5 | 5.049
464.2 | 49.5 | 5.049
464.3 | 49.5 | 5.049
464.4 | 49.5 | 5.049
464.5 | 49.5 | 5.049
464.6 | 49.5 | 5.049
464.7 | 49.5 | 5.049
464.8 | 49.5 | 5.048
464.9 | 49.5 | 5.048
465 | 49.5 | 5.048
465.1 | 49.5 | 5.048
465.2 | 49.5 | 5.048
465.3 | 49.5 | 5.048
465.4 | 49.5 | 5.048
465.5 | 49.5 | 5.048
465.6 | 49.5 | 5.048
465.7 | 49.5 | 5.048
465.8 | 49.5 | 5.048
465.9 | 49.5 | 5.048
466 | 49.5 | 5.048
466.1 | 49.5 | 5.048
466.2 | 49.5 | 5.048
466.3 | 49.5 | 5.048
466.4 | 49.5 | 5.048
466.5 | 49.5 | 5.048
466.6 | 49.5 | 5.048
466.7 | 49.5 | 5.048
466.8 | 49.5 | 5.048
466.9 | 49.5 | 5.048
467 | 49.5 | 5.048
467.1 | 49.5 | 5.048
467.2 | 49.5 | 5.048
467.3 | 49.5 | 5.048
467.4 | 49.5 | 5.048
467.5 | 49.5 | 5.048
467.6 | 49.5 | 5.048
467.7 | 49.5 | 5.048
467.8 | 49.5 | 5.048
467.9 | 49.5 | 5.048
468 | 49.5 | 5.048
468.1 | 49.5 | 5.048
468.2 | 49.5 | 5.048
468.3 | 49.5 | 5.048
468.4 | 49.5 | 5.048
468.5 | 49.5 | 5.048
468.6 | 49.5 | 5.048
468.7 | 49.5 | 5.048
468.8 | 49.5 | 5.048
468.9 | 49.5 | 5.048
469 | 49.5 | 5.048
469.1 | 49.5 | 5.048
469.2 | 49.5 | 5.048
469.3 | 49.5 | 5.048
469.4 | 49.5 | 5.048
469.5 | 49.5 | 5.048
469.6 | 49.5 | 5.048
469.7 | 49.5 | 5.048
469.8 | 49.5 | 5.048
469.9 | 49.5 | 5.048
470 | 49.5 | 5.048
470.1 | 49.5 | 5.048
470.2 | 49.5 | 5.048
470.3 | 49.5 | 5.048
470.4 | 49.5 | 5.048
470.5 | 49.5 | 5.048
470.6 | 49.5 | 5.048
470.7 | 49.5 | 5.048
470.8 | 49.5 | 5.048
470.9 | 49.5 | 5.048
471 | 49.5 | 5.048
471.1 | 49.5 | 5.048
471.2 | 49.5 | 5.048
471.3 | 49.5 | 5.048
471.4 | 49.5 | 5.048
471.5 | 49.5 | 5.048
471.6 | 49.5 | 5.048
471.7 | 49.5 | 5.048
471.8 | 49.5 | 5.049
471.9 | 49.5 | 5.049
472 | 49.5 | 5.049
472.1 | 49.5 | 5.049
472.2 | 49.5 | 5.049
472.3 | 49.5 | 5.049
472.4 | 49.5 | 5.049
472.5 | 49.5 | 5.049
472.6 | 49.5 | 5.049
472.7 | 49.5 | 5.049
472.8 | 49.5 | 5.048
472.9 | 49.5 | 5.048
473 | 49.5 | 5.048
473.1 | 49.5 | 5.048
473.2 | 49.5 | 5.048
473.3 | 49.5 | 5.048
473.4 | 49.5 | 5.048
473.5 | 49.5 | 5.048
473.6 | 49.5 | 5.048
473.7 | 49.5 | 5.048
473.8 | 49.5 | 5.048
473.9 | 49.5 | 5.048
474 | 49.5 | 5.048
474.1 | 49.5 | 5.048
474.2 | 49.5 | 5.048
474.3 | 49.5 | 5.048
474.4 | 49.5 | 5.048
474.5 | 49.5 | 5.048
474.6 | 49.5 | 5.048
474.7 | 49.5 | 5.048
474.8 | 49.5 | 5.048
474.9 | 49.5 | 5.048
475 | 49.5 | 5.048
475.1 | 49.5 | 5.048
475.2 | 49.5 | 5.048
475.3 | 49.5 | 5.048
475.4 | 49.5 | 5.048
475.5 | 49.5 | 5.048
475.6 | 49.5 | 5.048
475.7 | 49.5 | 5.048
475.8 | 49.5 | 5.048
475.9 | 49.5 | 5.048
476 | 49.5 | 5.048
476.1 | 49.5 | 5.048
476.2 | 49.5 | 5.048
476.3 | 49.5 | 5.048
476.4 | 49.5 | 5.048
476.5 | 49.5 | 5.048
476.6 | 49.5 | 5.048
476.7 | 49.5 | 5.048
476.8 | 49.5 | 5.048
476.9 | 49.5 | 5.048
477 | 49.5 | 5.048
477.1 | 49.5 | 5.048
477.2 | 49.5 | 5.048
477.3 | 49.5 | 5.048
477.4 | 49.5 | 5.048
477.5 | 49.5 | 5.048
477.6 | 49.5 | 5.048
477.7 | 49.5 | 5.048
477.8 | 49.5 | 5.048
477.9 | 49.5 | 5.048
478 | 49.5 | 5.048
478.1 | 49.5 | 5.048
478.2 | 49.5 | 5.048
478.3 | 49.5 | 5.048
478.4 | 49.5 | 5.048
478.5 | 49.5 | 5.048
478.6 | 49.5 | 5.048
478.7 | 49.5 | 5.048
478.8 | 49.5 | 5.048
478.9 | 49.5 | 5.048
479 | 49.5 | 5.048
479.1 | 49.5 | 5.048
479.2 | 49.5 | 5.048
479.3 | 49.5 | 5.048
479.4 | 49.5 | 5.048
479.5 | 49.5 | 5.048
479.6 | 49.5 | 5.048
479.7 | 49.5 | 5.048
479.8 | 49.5 | 5.049
479.9 | 49.5 | 5.049
480 | 49.5 | 5.049
480.1 | 49.5 | 5.049
480.2 | 49.5 | 5.049
480.3 | 49.5 | 5.049
480.4 | 49.5 | 5.049
480.5 | 49.5 | 5.049
480.6 | 49.5 | 5.049
480.7 | 49.5 | 5.049
480.8 | 49.5 | 5.049
480.9 | 49.5 | 5.049
481 | 49.5 | 5.049
481.1 | 49.5 | 5.049
481.2 | 49.5 | 5.049
481.3 | 49.5 | 5.049
481.4 | 49.5 | 5.049
481.5 | 49.5 | 5.049
481.6 | 49.5 | 5.049
481.7 | 49.5 | 5.049
481.8 | 49.5 | 5.049
481.9 | 49.5 | 5.048
482 | 49.5 | 5.048
482.1 | 49.5 | 5.048
482.2 | 49.5 | 5.048
482.3 | 49.5 | 5.048
482.4 | 49.5 | 5.048
482.5 | 49.5 | 5.048
482.6 | 49.5 | 5.048
482.7 | 49.5 | 5.048
482.8 | 49.5 | 5.048
482.9 | 49.5 | 5.048
483 | 49.5 | 5.048
483.1 | 49.5 | 5.048
483.2 | 49.5 | 5.048
483.3 | 49.5 | 5.048
483.4 | 49.5 | 5.048
483.5 | 49.5 | 5.048
483.6 | 49.5 | 5.048
483.7 | 49.5 | 5.048
483.8 | 49.5 | 5.048
483.9 | 49.5 | 5.048
484 | 49.5 | 5.048
484.1 | 49.5 | 5.048
484.2 | 49.5 | 5.048
484.3 | 49.5 | 5.048
484.4 | 49.5 | 5.048
484.5 | 49.5 | 5.048
484.6 | 49.5 | 5.048
484.7 | 49.5 | 5.048
484.8 | 49.5 | 5.048
484.9 | 49.5 | 5.048
485 | 49.5 | 5.048
485.1 | 49.5 | 5.048
485.2 | 49.5 | 5.048
485.3 | 49.5 | 5.048
485.4 | 49.5 | 5.048
485.5 | 49.5 | 5.048
485.6 | 49.5 | 5.048
485.7 | 49.5 | 5.048
485.8 | 49.5 | 5.048
485.9 | 49.5 | 5.048
486 | 49.5 | 5.048
486.1 | 49.5 | 5.048
486.2 | 49.5 | 5.048
486.3 | 49.5 | 5.048
486.4 | 49.5 | 5.048
486.5 | 49.5 | 5.048
486.6 | 49.5 | 5.048
486.7 | 49.5 | 5.048
486.8 | 49.5 | 5.048
486.9 | 49.5 | 5.048
487 | 49.5 | 5.048
487.1 | 49.5 | 5.048
487.2 | 49.5 | 5.048
487.3 | 49.5 | 5.048
487.4 | 49.5 | 5.048
487.5 | 49.5 | 5.048
487.6 | 49.5 | 5.048
487.7 | 49.5 | 5.048
487.8 | 49.5 | 5.048
487.9 | 49.5 | 5.048
488 | 49.5 | 5.048
488.1 | 49.5 | 5.048
488.2 | 49.5 | 5.048
488.3 | 49.5 | 5.048
488.4 | 49.5 | 5.048
488.5 | 49.5 | 5.048
488.6 | 49.5 | 5.048
488.7 | 49.5 | 5.048
488.8 | 49.5 | 5.048
488.9 | 49.5 | 5.048
489 | 49.5 | 5.048
489.1 | 49.5 | 5.048
489.2 | 49.5 | 5.048
489.3 | 49.5 | 5.048
489.4 | 49.5 | 5.048
489.5 | 49.5 | 5.048
489.6 | 49.5 | 5.048
489.7 | 49.5 | 5.048
489.8 | 49.5 | 5.048
489.9 | 49.5 | 5.048
490 | 49.5 | 5.048
490.1 | 49.5 | 5.048
490.2 | 49.5 | 5.048
490.3 | 49.5 | 5.048
490.4 | 49.5 | 5.048
490.5 | 49.5 | 5.048
490.6 | 49.5 | 5.048
490.7 | 49.5 | 5.048
490.8 | 49.5 | 5.048
490.9 | 49.5 | 5.048
491 | 49.5 | 5.048
491.1 | 49.5 | 5.048
491.2 | 49.5 | 5.048
491.3 | 49.5 | 5.048
491.4 | 49.5 | 5.048
491.5 | 49.5 | 5.048
491.6 | 49.5 | 5.048
491.7 | 49.5 | 5.048
491.8 | 49.5 | 5.048
491.9 | 49.5 | 5.048
492 | 49.5 | 5.048
492.1 | 49.5 | 5.048
492.2 | 49.5 | 5.048
492.3 | 49.5 | 5.048
492.4 | 49.5 | 5.048
492.5 | 49.5 | 5.048
492.6 | 49.5 | 5.048
492.7 | 49.5 | 5.048
492.8 | 49.5 | 5.048
492.9 | 49.5 | 5.048
493 | 49.5 | 5.048
493.1 | 49.5 | 5.048
493.2 | 49.5 | 5.048
493.3 | 49.5 | 5.048
493.4 | 49.5 | 5.048
493.5 | 49.5 | 5.048
493.6 | 49.5 | 5.048
493.7 | 49.5 | 5.048
493.8 | 49.5 | 5.048
493.9 | 49.5 | 5.048
494 | 49.5 | 5.048
494.1 | 49.5 | 5.048
494.2 | 49.5 | 5.048
494.3 | 49.5 | 5.048
494.4 | 49.5 | 5.048
494.5 | 49.5 | 5.048
494.6 | 49.5 | 5.048
494.7 | 49.5 | 5.048
494.8 | 49.5 | 5.048
494.9 | 49.5 | 5.048
495 | 49.5 | 5.048
495.1 | 49.5 | 5.048
495.2 | 49.5 | 5.048
495.3 | 49.5 | 5.048
495.4 | 49.5 | 5.048
495.5 | 49.5 | 5.048
495.6 | 49.5 | 5.048
495.7 | 49.5 | 5.048
495.8 | 49.5 | 5.048
495.9 | 49.5 | 5.048
496 | 49.5 | 5.048
496.1 | 49.5 | 5.048
496.2 | 49.5 | 5.048
496.3 | 49.5 | 5.048
496.4 | 49.5 | 5.048
496.5 | 49.5 | 5.048
496.6 | 49.5 | 5.048
496.7 | 49.5 | 5.048
496.8 | 49.5 | 5.048
496.9 | 49.5 | 5.048
497 | 49.5 | 5.048
497.1 | 49.5 | 5.048
497.2 | 49.5 | 5.048
497.3 | 49.5 | 5.048
497.4 | 49.5 | 5.049
497.5 | 49.5 | 5.049
497.6 | 49.5 | 5.049
497.7 | 49.5 | 5.049
497.8 | 49.5 | 5.049
497.9 | 49.5 | 5.049
498 | 49.5 | 5.049
498.1 | 49.5 | 5.049
498.2 | 49.5 | 5.049
498.3 | 49.5 | 5.049
498.4 | 49.5 | 5.049
498.5 | 49.5 | 5.049
498.6 | 49.5 | 5.049
498.7 | 49.5 | 5.049
498.8 | 49.5 | 5.049
498.9 | 49.5 | 5.049
499 | 49.5 | 5.049
499.1 | 49.5 | 5.049
499.2 | 49.5 | 5.049
499.3 | 49.5 | 5.049
499.4 | 49.5 | 5.049
499.5 | 49.5 | 5.049
499.6 | 49.5 | 5.049
499.7 | 49.5 | 5.049
499.8 | 49.5 | 5.048
499.9 | 49.5 | 5.048
500 | 49.5 | 5.048
500.1 | 49.5 | 5.048
500.2 | 49.5 | 5.048
500.3 | 49.5 | 5.048
500.4 | 49.5 | 5.048
500.5 | 49.5 | 5.048
500.6 | 49.5 | 5.048
500.7 | 49.5 | 5.048
500.8 | 49.5 | 5.048
500.9 | 49.5 | 5.048
501 | 49.5 | 5.048
501.1 | 49.5 | 5.048
501.2 | 49.5 | 5.048
501.3 | 49.5 | 5.048
501.4 | 49.5 | 5.048
501.5 | 49.5 | 5.048
501.6 | 49.5 | 5.048
501.7 | 49.5 | 5.048
501.8 | 49.5 | 5.048
501.9 | 49.5 | 5.048
502 | 49.5 | 5.048
502.1 | 49.5 | 5.048
502.2 | 49.5 | 5.048
502.3 | 49.5 | 5.048
502.4 | 49.5 | 5.048
502.5 | 49.5 | 5.048
502.6 | 49.5 | 5.048
502.7 | 49.5 | 5.048
502.8 | 49.5 | 5.048
502.9 | 49.5 | 5.048
503 | 49.5 | 5.048
503.1 | 49.5 | 5.048
503.2 | 49.5 | 5.048
503.3 | 49.5 | 5.048
503.4 | 49.5 | 5.048
503.5 | 49.5 | 5.048
503.6 | 49.5 | 5.048
503.7 | 49.5 | 5.048
503.8 | 49.5 | 5.048
503.9 | 49.5 | 5.048
504 | 49.5 | 5.048
504.1 | 49.5 | 5.048
504.2 | 49.5 | 5.048
504.3 | 49.5 | 5.048
504.4 | 49.5 | 5.048
504.5 | 49.5 | 5.048
504.6 | 49.5 | 5.048
504.7 | 49.5 | 5.048
504.8 | 49.5 | 5.048
504.9 | 49.5 | 5.048
505 | 49.5 | 5.048
505.1 | 49.5 | 5.048
505.2 | 49.5 | 5.048
505.3 | 49.5 | 5.048
505.4 | 49.5 | 5.048
505.5 | 49.5 | 5.048
505.6 | 49.5 | 5.048
505.7 | 49.5 | 5.048
505.8 | 49.5 | 5.048
505.9 | 49.5 | 5.048
506 | 49.5 | 5.048
506.1 | 49.5 | 5.048
506.2 | 49.5 | 5.048
506.3 | 49.5 | 5.048
506.4 | 49.5 | 5.048
506.5 | 49.5 | 5.048
506.6 | 49.5 | 5.048
506.7 | 49.5 | 5.048
506.8 | 49.5 | 5.048
506.9 | 49.5 | 5.048
507 | 49.5 | 5.048
507.1 | 49.5 | 5.048
507.2 | 49.5 | 5.048
507.3 | 49.5 | 5.048
507.4 | 49.5 | 5.048
507.5 | 49.5 | 5.048
507.6 | 49.5 | 5.048
507.7 | 49.5 | 5.048
507.8 | 49.5 | 5.048
507.9 | 49.5 | 5.048
508 | 49.5 | 5.048
508.1 | 49.5 | 5.048
508.2 | 49.5 | 5.048
508.3 | 49.5 | 5.048
508.4 | 49.5 | 5.048
508.5 | 49.5 | 5.048
508.6 | 49.5 | 5.048
508.7 | 49.5 | 5.048
508.8 | 49.5 | 5.048
508.9 | 49.5 | 5.048
509 | 49.5 | 5.048
509.1 | 49.5 | 5.048
509.2 | 49.5 | 5.048
509.3 | 49.5 | 5.048
509.4 | 49.5 | 5.048
509.5 | 49.5 | 5.048
509.6 | 49.5 | 5.048
509.7 | 49.5 | 5.048
509.8 | 49.5 | 5.048
509.9 | 49.5 | 5.048
510 | 49.5 | 5.048
510.1 | 49.5 | 5.048
510.2 | 49.5 | 5.048
510.3 | 49.5 | 5.048
510.4 | 49.5 | 5.048
510.5 | 49.5 | 5.048
510.6 | 49.5 | 5.048
510.7 | 49.5 | 5.048
510.8 | 49.5 | 5.048
510.9 | 49.5 | 5.048
511 | 49.5 | 5.048
511.1 | 49.5 | 5.048
511.2 | 49.5 | 5.048
511.3 | 49.5 | 5.048
511.4 | 49.5 | 5.048
511.5 | 49.5 | 5.048
511.6 | 49.5 | 5.048
511.7 | 49.5 | 5.048
511.8 | 49.5 | 5.048
511.9 | 49.5 | 5.048
512 | 49.5 | 5.048
512.1 | 49.5 | 5.048
512.2 | 49.5 | 5.048
512.3 | 49.5 | 5.048
512.4 | 49.5 | 5.048
512.5 | 49.5 | 5.048
512.6 | 49.5 | 5.048
512.7 | 49.5 | 5.048
512.8 | 49.5 | 5.048
512.9 | 49.5 | 5.048
513 | 49.5 | 5.048
513.1 | 49.5 | 5.048
513.2 | 49.5 | 5.048
513.3 | 49.5 | 5.048
513.4 | 49.5 | 5.048
513.5 | 49.5 | 5.048
513.6 | 49.5 | 5.048
513.7 | 49.5 | 5.048
513.8 | 49.5 | 5.048
513.9 | 49.5 | 5.048
514 | 49.5 | 5.048
514.1 | 49.5 | 5.048
514.2 | 49.5 | 5.048
514.3 | 49.5 | 5.048
514.4 | 49.5 | 5.048
514.5 | 49.5 | 5.048
514.6 | 49.5 | 5.048
514.7 | 49.5 | 5.048
514.8 | 49.5 | 5.048
514.9 | 49.5 | 5.048
515 | 49.5 | 5.048
515.1 | 49.5 | 5.048
515.2 | 49.5 | 5.048
515.3 | 49.5 | 5.048
515.4 | 49.5 | 5.048
515.5 | 49.5 | 5.048
515.6 | 49.5 | 5.048
515.7 | 49.5 | 5.048
515.8 | 49.5 | 5.048
515.9 | 49.5 | 5.048
516 | 49.5 | 5.048
516.1 | 49.5 | 5.048
516.2 | 49.5 | 5.048
516.3 | 49.5 | 5.048
516.4 | 49.5 | 5.048
516.5 | 49.5 | 5.048
516.6 | 49.5 | 5.048
516.7 | 49.5 | 5.048
516.8 | 49.5 | 5.048
516.9 | 49.5 | 5.048
517 | 49.5 | 5.048
517.1 | 49.5 | 5.048
517.2 | 49.5 | 5.048
517.3 | 49.5 | 5.048
517.4 | 49.5 | 5.048
517.5 | 49.5 | 5.048
517.6 | 49.5 | 5.048
517.7 | 49.5 | 5.048
517.8 | 49.5 | 5.048
517.9 | 49.5 | 5.048
518 | 49.5 | 5.048
518.1 | 49.5 | 5.048
518.2 | 49.5 | 5.048
518.3 | 49.5 | 5.048
518.4 | 49.5 | 5.048
518.5 | 49.5 | 5.048
518.6 | 49.5 | 5.048
518.7 | 49.5 | 5.048
518.8 | 49.5 | 5.048
518.9 | 49.5 | 5.048
519 | 49.5 | 5.048
519.1 | 49.5 | 5.048
519.2 | 49.5 | 5.048
519.3 | 49.5 | 5.048
519.4 | 49.5 | 5.048
519.5 | 49.5 | 5.048
519.6 | 49.5 | 5.048
519.7 | 49.5 | 5.048
519.8 | 49.5 | 5.048
519.9 | 49.5 | 5.048
520 | 49.5 | 5.048
520.1 | 49.5 | 5.048
520.2 | 49.5 | 5.048
520.3 | 49.5 | 5.048
520.4 | 49.5 | 5.048
520.5 | 49.5 | 5.048
520.6 | 49.5 | 5.048
520.7 | 49.5 | 5.048
520.8 | 49.5 | 5.048
520.9 | 49.5 | 5.048
521 | 49.5 | 5.048
521.1 | 49.5 | 5.048
521.2 | 49.5 | 5.048
521.3 | 49.5 | 5.048
521.4 | 49.5 | 5.048
521.5 | 49.5 | 5.048
521.6 | 49.5 | 5.048
521.7 | 49.5 | 5.048
521.8 | 49.5 | 5.048
521.9 | 49.5 | 5.048
522 | 49.5 | 5.048
522.1 | 49.5 | 5.048
522.2 | 49.5 | 5.048
522.3 | 49.5 | 5.048
522.4 | 49.5 | 5.048
522.5 | 49.5 | 5.048
522.6 | 49.5 | 5.048
522.7 | 49.5 | 5.048
522.8 | 49.5 | 5.048
522.9 | 49.5 | 5.049
523 | 49.5 | 5.049
523.1 | 49.5 | 5.049
523.2 | 49.5 | 5.049
523.3 | 49.5 | 5.049
523.4 | 49.5 | 5.049
523.5 | 49.5 | 5.049
523.6 | 49.5 | 5.049
523.7 | 49.5 | 5.049
523.8 | 49.5 | 5.049
523.9 | 49.5 | 5.049
524 | 49.5 | 5.048
524.1 | 49.5 | 5.048
524.2 | 49.5 | 5.048
524.3 | 49.5 | 5.048
524.4 | 49.5 | 5.048
524.5 | 49.5 | 5.048
524.6 | 49.5 | 5.048
524.7 | 49.5 | 5.048
524.8 | 49.5 | 5.048
524.9 | 49.5 | 5.048
525 | 49.5 | 5.048
525.1 | 49.5 | 5.048
525.2 | 49.5 | 5.048
525.3 | 49.5 | 5.048
525.4 | 49.5 | 5.048
525.5 | 49.5 | 5.048
525.6 | 49.5 | 5.048
525.7 | 49.5 | 5.048
525.8 | 49.5 | 5.048
525.9 | 49.5 | 5.048
526 | 49.5 | 5.048
526.1 | 49.5 | 5.048
526.2 | 49.5 | 5.048
526.3 | 49.5 | 5.048
526.4 | 49.5 | 5.048
526.5 | 49.5 | 5.049
526.6 | 49.5 | 5.049
526.7 | 49.5 | 5.049
526.8 | 49.5 | 5.049
526.9 | 49.5 | 5.049
527 | 49.5 | 5.049
527.1 | 49.5 | 5.049
527.2 | 49.5 | 5.049
527.3 | 49.5 | 5.049
527.4 | 49.5 | 5.049
527.5 | 49.5 | 5.049
527.6 | 49.5 | 5.048
527.7 | 49.5 | 5.048
527.8 | 49.5 | 5.048
527.9 | 49.5 | 5.048
528 | 49.5 | 5.048
528.1 | 49.5 | 5.048
528.2 | 49.5 | 5.048
528.3 | 49.5 | 5.048
528.4 | 49.5 | 5.048
528.5 | 49.5 | 5.048
528.6 | 49.5 | 5.048
528.7 | 49.5 | 5.048
528.8 | 49.5 | 5.048
528.9 | 49.5 | 5.048
529 | 49.5 | 5.048
529.1 | 49.5 | 5.048
529.2 | 49.5 | 5.048
529.3 | 49.5 | 5.048
529.4 | 49.5 | 5.048
529.5 | 49.5 | 5.048
529.6 | 49.5 | 5.048
529.7 | 49.5 | 5.048
529.8 | 49.5 | 5.048
529.9 | 49.5 | 5.048
530 | 49.5 | 5.048
530.1 | 49.5 | 5.048
530.2 | 49.5 | 5.048
530.3 | 49.5 | 5.048
530.4 | 49.5 | 5.048
530.5 | 49.5 | 5.048
530.6 | 49.5 | 5.048
530.7 | 49.5 | 5.048
530.8 | 49.5 | 5.048
530.9 | 49.5 | 5.048
531 | 49.5 | 5.048
531.1 | 49.5 | 5.048
531.2 | 49.5 | 5.048
531.3 | 49.5 | 5.048
531.4 | 49.5 | 5.048
531.5 | 49.5 | 5.048
531.6 | 49.5 | 5.048
531.7 | 49.5 | 5.048
531.8 | 49.5 | 5.048
531.9 | 49.5 | 5.048
532 | 49.5 | 5.048
532.1 | 49.5 | 5.048
532.2 | 49.5 | 5.048
532.3 | 49.5 | 5.048
532.4 | 49.5 | 5.048
532.5 | 49.5 | 5.048
532.6 | 49.5 | 5.048
532.7 | 49.5 | 5.048
532.8 | 49.5 | 5.048
532.9 | 49.5 | 5.048
533 | 49.5 | 5.048
533.1 | 49.5 | 5.048
533.2 | 49.5 | 5.048
533.3 | 49.5 | 5.048
533.4 | 49.5 | 5.048
533.5 | 49.5 | 5.048
533.6 | 49.5 | 5.048
533.7 | 49.5 | 5.048
533.8 | 49.5 | 5.048
533.9 | 49.5 | 5.048
534 | 49.5 | 5.048
534.1 | 49.5 | 5.048
534.2 | 49.5 | 5.048
534.3 | 49.5 | 5.048
534.4 | 49.5 | 5.048
534.5 | 49.5 | 5.048
534.6 | 49.5 | 5.048
534.7 | 49.5 | 5.048
534.8 | 49.5 | 5.048
534.9 | 49.5 | 5.048
535 | 49.5 | 5.048
535.1 | 49.5 | 5.048
535.2 | 49.5 | 5.048
535.3 | 49.5 | 5.048
535.4 | 49.5 | 5.048
535.5 | 49.5 | 5.048
535.6 | 49.5 | 5.048
535.7 | 49.5 | 5.048
535.8 | 49.5 | 5.048
535.9 | 49.5 | 5.048
536 | 49.5 | 5.048
536.1 | 49.5 | 5.048
536.2 | 49.5 | 5.048
536.3 | 49.5 | 5.048
536.4 | 49.5 | 5.048
536.5 | 49.5 | 5.048
536.6 | 49.5 | 5.048
536.7 | 49.5 | 5.048
536.8 | 49.5 | 5.048
536.9 | 49.5 | 5.048
537 | 49.5 | 5.048
537.1 | 49.5 | 5.048
537.2 | 49.5 | 5.048
537.3 | 49.5 | 5.048
537.4 | 49.5 | 5.048
537.5 | 49.5 | 5.048
537.6 | 49.5 | 5.048
537.7 | 49.5 | 5.048
537.8 | 49.5 | 5.048
537.9 | 49.5 | 5.048
538 | 49.5 | 5.048
538.1 | 49.5 | 5.048
538.2 | 49.5 | 5.048
538.3 | 49.5 | 5.048
538.4 | 49.5 | 5.048
538.5 | 49.5 | 5.048
538.6 | 49.5 | 5.048
538.7 | 49.5 | 5.048
538.8 | 49.5 | 5.048
538.9 | 49.5 | 5.048
539 | 49.5 | 5.048
539.1 | 49.5 | 5.048
539.2 | 49.5 | 5.048
539.3 | 49.5 | 5.048
539.4 | 49.5 | 5.048
539.5 | 49.5 | 5.048
539.6 | 49.5 | 5.048
539.7 | 49.5 | 5.048
539.8 | 49.5 | 5.048
539.9 | 49.5 | 5.048
540 | 49.5 | 5.048
540.1 | 49.5 | 5.048
540.2 | 49.5 | 5.048
540.3 | 49.5 | 5.048
540.4 | 49.5 | 5.048
540.5 | 49.5 | 5.048
540.6 | 49.5 | 5.048
540.7 | 49.5 | 5.048
540.8 | 49.5 | 5.048
540.9 | 49.5 | 5.048
541 | 49.5 | 5.048
541.1 | 49.5 | 5.048
541.2 | 49.5 | 5.048
541.3 | 49.5 | 5.048
541.4 | 49.5 | 5.048
541.5 | 49.5 | 5.048
541.6 | 49.5 | 5.048
541.7 | 49.5 | 5.048
541.8 | 49.5 | 5.048
541.9 | 49.5 | 5.048
542 | 49.5 | 5.048
542.1 | 49.5 | 5.048
542.2 | 49.5 | 5.048
542.3 | 49.5 | 5.048
542.4 | 49.5 | 5.048
542.5 | 49.5 | 5.048
542.6 | 49.5 | 5.048
542.7 | 49.5 | 5.048
542.8 | 49.5 | 5.048
542.9 | 49.5 | 5.048
543 | 49.5 | 5.048
543.1 | 49.5 | 5.048
543.2 | 49.5 | 5.048
543.3 | 49.5 | 5.048
543.4 | 49.5 | 5.048
543.5 | 49.5 | 5.048
543.6 | 49.5 | 5.048
543.7 | 49.5 | 5.048
543.8 | 49.5 | 5.048
543.9 | 49.5 | 5.048
544 | 49.5 | 5.048
544.1 | 49.5 | 5.048
544.2 | 49.5 | 5.048
544.3 | 49.5 | 5.048
544.4 | 49.5 | 5.048
544.5 | 49.5 | 5.048
544.6 | 49.5 | 5.048
544.7 | 49.5 | 5.048
544.8 | 49.5 | 5.048
544.9 | 49.5 | 5.048
545 | 49.5 | 5.048
545.1 | 49.5 | 5.048
545.2 | 49.5 | 5.048
545.3 | 49.5 | 5.048
545.4 | 49.5 | 5.048
545.5 | 49.5 | 5.048
545.6 | 49.5 | 5.048
545.7 | 49.5 | 5.048
545.8 | 49.5 | 5.048
545.9 | 49.5 | 5.048
546 | 49.5 | 5.048
546.1 | 49.5 | 5.048
546.2 | 49.5 | 5.048
546.3 | 49.5 | 5.048
546.4 | 49.5 | 5.048
546.5 | 49.5 | 5.048
546.6 | 49.5 | 5.048
546.7 | 49.5 | 5.048
546.8 | 49.5 | 5.048
546.9 | 49.5 | 5.048
547 | 49.5 | 5.048
547.1 | 49.5 | 5.048
547.2 | 49.5 | 5.048
547.3 | 49.5 | 5.048
547.4 | 49.5 | 5.048
547.5 | 49.5 | 5.048
547.6 | 49.5 | 5.048
547.7 | 49.5 | 5.048
547.8 | 49.5 | 5.048
547.9 | 49.5 | 5.048
548 | 49.5 | 5.048
548.1 | 49.5 | 5.048
548.2 | 49.5 | 5.048
548.3 | 49.5 | 5.048
548.4 | 49.5 | 5.048
548.5 | 49.5 | 5.048
548.6 | 49.5 | 5.048
548.7 | 49.5 | 5.048
548.8 | 49.5 | 5.048
548.9 | 49.5 | 5.048
549 | 49.5 | 5.048
549.1 | 49.5 | 5.048
549.2 | 49.5 | 5.048
549.3 | 49.5 | 5.048
549.4 | 49.5 | 5.048
549.5 | 49.5 | 5.048
549.6 | 49.5 | 5.048
549.7 | 49.5 | 5.048
549.8 | 49.5 | 5.048
549.9 | 49.5 | 5.048
550 | 49.5 | 5.048
550.1 | 49.5 | 5.048
550.2 | 49.5 | 5.048
550.3 | 49.5 | 5.048
550.4 | 49.5 | 5.048
550.5 | 49.5 | 5.048
550.6 | 49.5 | 5.048
550.7 | 49.5 | 5.048
550.8 | 49.5 | 5.048
550.9 | 49.5 | 5.048
551 | 49.5 | 5.048
551.1 | 49.5 | 5.048
551.2 | 49.5 | 5.048
551.3 | 49.5 | 5.048
551.4 | 49.5 | 5.048
551.5 | 49.5 | 5.048
551.6 | 49.5 | 5.048
551.7 | 49.5 | 5.048
551.8 | 49.5 | 5.048
551.9 | 49.5 | 5.048
552 | 49.5 | 5.048
552.1 | 49.5 | 5.048
552.2 | 49.5 | 5.048
552.3 | 49.5 | 5.048
552.4 | 49.5 | 5.048
552.5 | 49.5 | 5.048
552.6 | 49.5 | 5.048
552.7 | 49.5 | 5.048
552.8 | 49.5 | 5.048
552.9 | 49.5 | 5.048
553 | 49.5 | 5.048
553.1 | 49.5 | 5.048
553.2 | 49.5 | 5.048
553.3 | 49.5 | 5.048
553.4 | 49.5 | 5.048
553.5 | 49.5 | 5.048
553.6 | 49.5 | 5.048
553.7 | 49.5 | 5.048
553.8 | 49.5 | 5.048
553.9 | 49.5 | 5.048
554 | 49.5 | 5.048
554.1 | 49.5 | 5.048
554.2 | 49.5 | 5.048
554.3 | 49.5 | 5.048
554.4 | 49.5 | 5.048
554.5 | 49.5 | 5.048
554.6 | 49.5 | 5.048
554.7 | 49.5 | 5.048
554.8 | 49.5 | 5.048
554.9 | 49.5 | 5.047
555 | 49.5 | 5.047
555.1 | 49.5 | 5.047
555.2 | 49.5 | 5.047
555.3 | 49.5 | 5.047
555.4 | 49.5 | 5.047
555.5 | 49.5 | 5.047
555.6 | 49.5 | 5.047
555.7 | 49.5 | 5.047
555.8 | 49.5 | 5.047
555.9 | 49.5 | 5.047
556 | 49.5 | 5.048
556.1 | 49.5 | 5.048
556.2 | 49.5 | 5.048
556.3 | 49.5 | 5.048
556.4 | 49.5 | 5.048
556.5 | 49.5 | 5.048
556.6 | 49.5 | 5.048
556.7 | 49.5 | 5.048
556.8 | 49.5 | 5.048
556.9 | 49.5 | 5.048
557 | 49.5 | 5.048
557.1 | 49.5 | 5.048
557.2 | 49.5 | 5.048
557.3 | 49.5 | 5.048
557.4 | 49.5 | 5.048
557.5 | 49.5 | 5.048
557.6 | 49.5 | 5.048
557.7 | 49.5 | 5.048
557.8 | 49.5 | 5.048
557.9 | 49.5 | 5.048
558 | 49.5 | 5.048
558.1 | 49.5 | 5.048
558.2 | 49.5 | 5.048
558.3 | 49.5 | 5.048
558.4 | 49.5 | 5.048
558.5 | 49.5 | 5.048
558.6 | 49.5 | 5.048
558.7 | 49.5 | 5.048
558.8 | 49.5 | 5.048
558.9 | 49.5 | 5.048
559 | 49.5 | 5.048
559.1 | 49.5 | 5.048
559.2 | 49.5 | 5.048
559.3 | 49.5 | 5.048
559.4 | 49.5 | 5.048
559.5 | 49.5 | 5.048
559.6 | 49.5 | 5.048
559.7 | 49.5 | 5.049
559.8 | 49.5 | 5.049
559.9 | 49.5 | 5.049
560 | 49.5 | 5.049
560.1 | 49.5 | 5.049
560.2 | 49.5 | 5.049
560.3 | 49.5 | 5.049
560.4 | 49.5 | 5.049
560.5 | 49.5 | 5.049
560.6 | 49.5 | 5.049
560.7 | 49.5 | 5.048
560.8 | 49.5 | 5.048
560.9 | 49.5 | 5.048
561 | 49.5 | 5.048
561.1 | 49.5 | 5.048
561.2 | 49.5 | 5.048
561.3 | 49.5 | 5.048
561.4 | 49.5 | 5.048
561.5 | 49.5 | 5.048
561.6 | 49.5 | 5.048
561.7 | 49.5 | 5.048
561.8 | 49.5 | 5.048
561.9 | 49.5 | 5.047
562 | 49.5 | 5.047
562.1 | 49.5 | 5.047
562.2 | 49.5 | 5.047
562.3 | 49.5 | 5.047
562.4 | 49.5 | 5.047
562.5 | 49.5 | 5.047
562.6 | 49.5 | 5.047
562.7 | 49.5 | 5.047
562.8 | 49.5 | 5.047
562.9 | 49.5 | 5.047
563 | 49.5 | 5.047
563.1 | 49.5 | 5.047
563.2 | 49.5 | 5.047
563.3 | 49.5 | 5.047
563.4 | 49.5 | 5.047
563.5 | 49.5 | 5.047
563.6 | 49.5 | 5.047
563.7 | 49.5 | 5.047
563.8 | 49.5 | 5.047
563.9 | 49.5 | 5.047
564 | 49.5 | 5.047
564.1 | 49.5 | 5.048
564.2 | 49.5 | 5.048
564.3 | 49.5 | 5.048
564.4 | 49.5 | 5.048
564.5 | 49.5 | 5.048
564.6 | 49.5 | 5.048
564.7 | 49.5 | 5.048
564.8 | 49.5 | 5.048
564.9 | 49.5 | 5.048
565 | 49.5 | 5.048
565.1 | 49.5 | 5.048
565.2 | 49.5 | 5.048
565.3 | 49.5 | 5.048
565.4 | 49.5 | 5.048
565.5 | 49.5 | 5.048
565.6 | 49.5 | 5.048
565.7 | 49.5 | 5.048
565.8 | 49.5 | 5.048
565.9 | 49.5 | 5.048
566 | 49.5 | 5.048
566.1 | 49.5 | 5.048
566.2 | 49.5 | 5.048
566.3 | 49.5 | 5.048
566.4 | 49.5 | 5.048
566.5 | 49.5 | 5.049
566.6 | 49.5 | 5.049
566.7 | 49.5 | 5.049
566.8 | 49.5 | 5.049
566.9 | 49.5 | 5.049
567 | 49.5 | 5.049
567.1 | 49.5 | 5.049
567.2 | 49.5 | 5.049
567.3 | 49.5 | 5.049
567.4 | 49.5 | 5.049
567.5 | 49.5 | 5.049
567.6 | 49.5 | 5.049
567.7 | 49.5 | 5.048
567.8 | 49.5 | 5.048
567.9 | 49.5 | 5.048
568 | 49.5 | 5.048
568.1 | 49.5 | 5.048
568.2 | 49.5 | 5.048
568.3 | 49.5 | 5.048
568.4 | 49.5 | 5.048
568.5 | 49.5 | 5.048
568.6 | 49.5 | 5.048
568.7 | 49.5 | 5.048
568.8 | 49.5 | 5.048
568.9 | 49.5 | 5.048
569 | 49.5 | 5.048
569.1 | 49.5 | 5.048
569.2 | 49.5 | 5.048
569.3 | 49.5 | 5.048
569.4 | 49.5 | 5.048
569.5 | 49.5 | 5.048
569.6 | 49.5 | 5.048
569.7 | 49.5 | 5.048
569.8 | 49.5 | 5.048
569.9 | 49.5 | 5.048
570 | 49.5 | 5.048
570.1 | 49.5 | 5.048
570.2 | 49.5 | 5.048
570.3 | 49.5 | 5.048
570.4 | 49.5 | 5.048
570.5 | 49.5 | 5.048
570.6 | 49.5 | 5.048
570.7 | 49.5 | 5.048
570.8 | 49.5 | 5.048
570.9 | 49.5 | 5.048
571 | 49.5 | 5.048
571.1 | 49.5 | 5.048
571.2 | 49.5 | 5.048
571.3 | 49.5 | 5.048
571.4 | 49.5 | 5.048
571.5 | 49.5 | 5.048
571.6 | 49.5 | 5.048
571.7 | 49.5 | 5.048
571.8 | 49.5 | 5.048
571.9 | 49.5 | 5.048
572 | 49.5 | 5.048
572.1 | 49.5 | 5.048
572.2 | 49.5 | 5.048
572.3 | 49.5 | 5.049
572.4 | 49.5 | 5.049
572.5 | 49.5 | 5.049
572.6 | 49.5 | 5.049
572.7 | 49.5 | 5.049
572.8 | 49.5 | 5.049
572.9 | 49.5 | 5.049
573 | 49.5 | 5.049
573.1 | 49.5 | 5.049
573.2 | 49.5 | 5.049
573.3 | 49.5 | 5.049
573.4 | 49.5 | 5.049
573.5 | 49.5 | 5.049
573.6 | 49.5 | 5.048
573.7 | 49.5 | 5.048
573.8 | 49.5 | 5.048
573.9 | 49.5 | 5.048
574 | 49.5 | 5.048
574.1 | 49.5 | 5.048
574.2 | 49.5 | 5.048
574.3 | 49.5 | 5.048
574.4 | 49.5 | 5.048
574.5 | 49.5 | 5.048
574.6 | 49.5 | 5.048
574.7 | 49.5 | 5.048
574.8 | 49.5 | 5.048
574.9 | 49.5 | 5.048
575 | 49.5 | 5.048
575.1 | 49.5 | 5.048
575.2 | 49.5 | 5.048
575.3 | 49.5 | 5.048
575.4 | 49.5 | 5.048
575.5 | 49.5 | 5.048
575.6 | 49.5 | 5.048
575.7 | 49.5 | 5.048
575.8 | 49.5 | 5.048
575.9 | 49.5 | 5.048
576 | 49.5 | 5.048
576.1 | 49.5 | 5.048
576.2 | 49.5 | 5.048
576.3 | 49.5 | 5.048
576.4 | 49.5 | 5.048
576.5 | 49.5 | 5.048
576.6 | 49.5 | 5.048
576.7 | 49.5 | 5.048
576.8 | 49.5 | 5.048
576.9 | 49.5 | 5.048
577 | 49.5 | 5.048
577.1 | 49.5 | 5.048
577.2 | 49.5 | 5.048
577.3 | 49.5 | 5.048
577.4 | 49.5 | 5.048
577.5 | 49.5 | 5.048
577.6 | 49.5 | 5.048
577.7 | 49.5 | 5.048
577.8 | 49.5 | 5.048
577.9 | 49.5 | 5.048
578 | 49.5 | 5.048
578.1 | 49.5 | 5.049
578.2 | 49.5 | 5.049
578.3 | 49.5 | 5.049
578.4 | 49.5 | 5.049
578.5 | 49.5 | 5.049
578.6 | 49.5 | 5.049
578.7 | 49.5 | 5.049
578.8 | 49.5 | 5.049
578.9 | 49.5 | 5.049
579 | 49.5 | 5.049
579.1 | 49.5 | 5.049
579.2 | 49.5 | 5.049
579.3 | 49.5 | 5.049
579.4 | 49.5 | 5.049
579.5 | 49.5 | 5.049
579.6 | 49.5 | 5.049
579.7 | 49.5 | 5.049
579.8 | 49.5 | 5.049
579.9 | 49.5 | 5.049
580 | 49.5 | 5.049
580.1 | 49.5 | 5.049
580.2 | 49.5 | 5.049
580.3 | 49.5 | 5.049
580.4 | 49.5 | 5.049
580.5 | 49.5 | 5.048
580.6 | 49.5 | 5.048
580.7 | 49.5 | 5.048
580.8 | 49.5 | 5.048
580.9 | 49.5 | 5.048
581 | 49.5 | 5.048
581.1 | 49.5 | 5.048
581.2 | 49.5 | 5.048
581.3 | 49.5 | 5.048
581.4 | 49.5 | 5.048
581.5 | 49.5 | 5.048
581.6 | 49.5 | 5.048
581.7 | 49.5 | 5.048
581.8 | 49.5 | 5.048
581.9 | 49.5 | 5.048
582 | 49.5 | 5.048
582.1 | 49.5 | 5.048
582.2 | 49.5 | 5.048
582.3 | 49.5 | 5.048
582.4 | 49.5 | 5.048
582.5 | 49.5 | 5.048
582.6 | 49.5 | 5.048
582.7 | 49.5 | 5.048
582.8 | 49.5 | 5.048
582.9 | 49.5 | 5.048
583 | 49.5 | 5.048
583.1 | 49.5 | 5.048
583.2 | 49.5 | 5.048
583.3 | 49.5 | 5.048
583.4 | 49.5 | 5.048
583.5 | 49.5 | 5.048
583.6 | 49.5 | 5.048
583.7 | 49.5 | 5.048
583.8 | 49.5 | 5.048
583.9 | 49.5 | 5.048
584 | 49.5 | 5.048
584.1 | 49.5 | 5.048
584.2 | 49.5 | 5.048
584.3 | 49.5 | 5.048
584.4 | 49.5 | 5.048
584.5 | 49.5 | 5.048
584.6 | 49.5 | 5.048
584.7 | 49.5 | 5.048
584.8 | 49.5 | 5.048
584.9 | 49.5 | 5.048
585 | 49.5 | 5.048
585.1 | 49.5 | 5.048
585.2 | 49.5 | 5.048
585.3 | 49.5 | 5.048
585.4 | 49.5 | 5.048
585.5 | 49.5 | 5.048
585.6 | 49.5 | 5.048
585.7 | 49.5 | 5.048
585.8 | 49.5 | 5.048
585.9 | 49.5 | 5.048
586 | 49.5 | 5.048
586.1 | 49.5 | 5.048
586.2 | 49.5 | 5.048
586.3 | 49.5 | 5.048
586.4 | 49.5 | 5.048
586.5 | 49.5 | 5.048
586.6 | 49.5 | 5.048
586.7 | 49.5 | 5.048
586.8 | 49.5 | 5.048
586.9 | 49.5 | 5.048
587 | 49.5 | 5.048
587.1 | 49.5 | 5.048
587.2 | 49.5 | 5.048
587.3 | 49.5 | 5.048
587.4 | 49.5 | 5.048
587.5 | 49.5 | 5.048
587.6 | 49.5 | 5.048
587.7 | 49.5 | 5.048
587.8 | 49.5 | 5.048
587.9 | 49.5 | 5.048
588 | 49.5 | 5.048
588.1 | 49.5 | 5.048
588.2 | 49.5 | 5.048
588.3 | 49.5 | 5.048
588.4 | 49.5 | 5.048
588.5 | 49.5 | 5.048
588.6 | 49.5 | 5.048
588.7 | 49.5 | 5.048
588.8 | 49.5 | 5.048
588.9 | 49.5 | 5.048
589 | 49.5 | 5.048
589.1 | 49.5 | 5.048
589.2 | 49.5 | 5.048
589.3 | 49.5 | 5.048
589.4 | 49.5 | 5.048
589.5 | 49.5 | 5.048
589.6 | 49.5 | 5.048
589.7 | 49.5 | 5.048
589.8 | 49.5 | 5.048
589.9 | 49.5 | 5.048
590 | 49.5 | 5.048
590.1 | 49.5 | 5.048
590.2 | 49.5 | 5.048
590.3 | 49.5 | 5.048
590.4 | 49.5 | 5.048
590.5 | 49.5 | 5.048
590.6 | 49.5 | 5.048
590.7 | 49.5 | 5.048
590.8 | 49.5 | 5.048
590.9 | 49.5 | 5.048
591 | 49.5 | 5.048
591.1 | 49.5 | 5.048
591.2 | 49.5 | 5.048
591.3 | 49.5 | 5.048
591.4 | 49.5 | 5.048
591.5 | 49.5 | 5.048
591.6 | 49.5 | 5.048
591.7 | 49.5 | 5.048
591.8 | 49.5 | 5.048
591.9 | 49.5 | 5.048
592 | 49.5 | 5.048
592.1 | 49.5 | 5.048
592.2 | 49.5 | 5.048
592.3 | 49.5 | 5.048
592.4 | 49.5 | 5.048
592.5 | 49.5 | 5.048
592.6 | 49.5 | 5.048
592.7 | 49.5 | 5.048
592.8 | 49.5 | 5.048
592.9 | 49.5 | 5.048
593 | 49.5 | 5.048
593.1 | 49.5 | 5.048
593.2 | 49.5 | 5.048
593.3 | 49.5 | 5.048
593.4 | 49.5 | 5.048
593.5 | 49.5 | 5.048
593.6 | 49.5 | 5.048
593.7 | 49.5 | 5.048
593.8 | 49.5 | 5.048
593.9 | 49.5 | 5.048
594 | 49.5 | 5.048
594.1 | 49.5 | 5.048
594.2 | 49.5 | 5.048
594.3 | 49.5 | 5.048
594.4 | 49.5 | 5.048
594.5 | 49.5 | 5.048
594.6 | 49.5 | 5.048
594.7 | 49.5 | 5.048
594.8 | 49.5 | 5.048
594.9 | 49.5 | 5.048
595 | 49.5 | 5.048
595.1 | 49.5 | 5.048
595.2 | 49.5 | 5.048
595.3 | 49.5 | 5.048
595.4 | 49.5 | 5.048
595.5 | 49.5 | 5.048
595.6 | 49.5 | 5.048
595.7 | 49.5 | 5.048
595.8 | 49.5 | 5.048
595.9 | 49.5 | 5.048
596 | 49.5 | 5.048
596.1 | 49.5 | 5.048
596.2 | 49.5 | 5.048
596.3 | 49.5 | 5.048
596.4 | 49.5 | 5.048
596.5 | 49.5 | 5.048
596.6 | 49.5 | 5.048
596.7 | 49.5 | 5.048
596.8 | 49.5 | 5.048
596.9 | 49.5 | 5.048
597 | 49.5 | 5.048
597.1 | 49.5 | 5.048
597.2 | 49.5 | 5.048
597.3 | 49.5 | 5.048
597.4 | 49.5 | 5.048
597.5 | 49.5 | 5.048
597.6 | 49.5 | 5.048
597.7 | 49.5 | 5.048
597.8 | 49.5 | 5.048
597.9 | 49.5 | 5.048
598 | 49.5 | 5.048
598.1 | 49.5 | 5.048
598.2 | 49.5 | 5.048
598.3 | 49.5 | 5.048
598.4 | 49.5 | 5.048
598.5 | 49.5 | 5.048
598.6 | 49.5 | 5.048
598.7 | 49.5 | 5.048
598.8 | 49.5 | 5.048
598.9 | 49.5 | 5.048
599 | 49.5 | 5.048
599.1 | 49.5 | 5.048
599.2 | 49.5 | 5.048
599.3 | 49.5 | 5.048
599.4 | 49.5 | 5.048
599.5 | 49.5 | 5.048
599.6 | 49.5 | 5.048
599.7 | 49.5 | 5.048
599.8 | 49.5 | 5.048
599.9 | 49.5 | 5.048
600 | 49.5 | 5.048
600.1 | 49.5 | 5.048
600.2 | 49.5 | 5.048
600.3 | 49.5 | 5.048
600.4 | 49.5 | 5.048
600.5 | 49.5 | 5.048
600.6 | 49.5 | 5.048
600.7 | 49.5 | 5.048
600.8 | 49.5 | 5.048
600.9 | 49.5 | 5.048
601 | 49.5 | 5.048
601.1 | 49.5 | 5.048
601.2 | 49.5 | 5.048
601.3 | 49.5 | 5.048
601.4 | 49.5 | 5.048
601.5 | 49.5 | 5.048
601.6 | 49.5 | 5.048
601.7 | 49.5 | 5.048
601.8 | 49.5 | 5.048
601.9 | 49.5 | 5.048
602 | 49.5 | 5.048
602.1 | 49.5 | 5.048
602.2 | 49.5 | 5.048
602.3 | 49.5 | 5.048
602.4 | 49.5 | 5.048
602.5 | 49.5 | 5.048
602.6 | 49.5 | 5.048
602.7 | 49.5 | 5.048
602.8 | 49.5 | 5.048
602.9 | 49.5 | 5.048
603 | 49.5 | 5.048
603.1 | 49.5 | 5.048
603.2 | 49.5 | 5.048
603.3 | 49.5 | 5.048
603.4 | 49.5 | 5.048
603.5 | 49.5 | 5.048
603.6 | 49.5 | 5.048
603.7 | 49.5 | 5.048
603.8 | 49.5 | 5.048
603.9 | 49.5 | 5.048
604 | 49.5 | 5.048
604.1 | 49.5 | 5.048
604.2 | 49.5 | 5.048
604.3 | 49.5 | 5.048
604.4 | 49.5 | 5.048
604.5 | 49.5 | 5.048
604.6 | 49.5 | 5.048
604.7 | 49.5 | 5.048
604.8 | 49.5 | 5.048
604.9 | 49.5 | 5.048
605 | 49.5 | 5.049
605.1 | 49.5 | 5.049
605.2 | 49.5 | 5.049
605.3 | 49.5 | 5.049
605.4 | 49.5 | 5.049
605.5 | 49.5 | 5.049
605.6 | 49.5 | 5.049
605.7 | 49.5 | 5.049
605.8 | 49.5 | 5.049
605.9 | 49.5 | 5.049
606 | 49.5 | 5.048
606.1 | 49.5 | 5.048
606.2 | 49.5 | 5.048
606.3 | 49.5 | 5.048
606.4 | 49.5 | 5.048
606.5 | 49.5 | 5.048
606.6 | 49.5 | 5.048
606.7 | 49.5 | 5.048
606.8 | 49.5 | 5.048
606.9 | 49.5 | 5.048
607 | 49.5 | 5.048
607.1 | 49.5 | 5.048
607.2 | 49.5 | 5.048
607.3 | 49.5 | 5.048
607.4 | 49.5 | 5.048
607.5 | 49.5 | 5.048
607.6 | 49.5 | 5.048
607.7 | 49.5 | 5.048
607.8 | 49.5 | 5.048
607.9 | 49.5 | 5.048
608 | 49.5 | 5.048
608.1 | 49.5 | 5.048
608.2 | 49.5 | 5.048
608.3 | 49.5 | 5.048
608.4 | 49.5 | 5.048
608.5 | 49.5 | 5.048
608.6 | 49.5 | 5.048
608.7 | 49.5 | 5.048
608.8 | 49.5 | 5.048
608.9 | 49.5 | 5.048
609 | 49.5 | 5.048
609.1 | 49.5 | 5.048
609.2 | 49.5 | 5.048
609.3 | 49.5 | 5.048
609.4 | 49.5 | 5.048
609.5 | 49.5 | 5.048
609.6 | 49.5 | 5.048
609.7 | 49.5 | 5.048
609.8 | 49.5 | 5.048
609.9 | 49.5 | 5.048
610 | 49.5 | 5.048
610.1 | 49.5 | 5.048
610.2 | 49.5 | 5.048
610.3 | 49.5 | 5.048
610.4 | 49.5 | 5.048
610.5 | 49.5 | 5.048
610.6 | 49.5 | 5.048
610.7 | 49.5 | 5.048
610.8 | 49.5 | 5.048
610.9 | 49.5 | 5.048
611 | 49.5 | 5.048
611.1 | 49.5 | 5.048
611.2 | 49.5 | 5.048
611.3 | 49.5 | 5.048
611.4 | 49.5 | 5.048
611.5 | 49.5 | 5.048
611.6 | 49.5 | 5.048
611.7 | 49.5 | 5.048
611.8 | 49.5 | 5.048
611.9 | 49.5 | 5.048
612 | 49.5 | 5.048
612.1 | 49.5 | 5.048
612.2 | 49.5 | 5.048
612.3 | 49.5 | 5.048
612.4 | 49.5 | 5.048
612.5 | 49.5 | 5.048
612.6 | 49.5 | 5.048
612.7 | 49.5 | 5.048
612.8 | 49.5 | 5.048
612.9 | 49.5 | 5.048
613 | 49.5 | 5.048
613.1 | 49.5 | 5.048
613.2 | 49.5 | 5.048
613.3 | 49.5 | 5.048
613.4 | 49.5 | 5.048
613.5 | 49.5 | 5.048
613.6 | 49.5 | 5.048
613.7 | 49.5 | 5.048
613.8 | 49.5 | 5.048
613.9 | 49.5 | 5.048
614 | 49.5 | 5.048
614.1 | 49.5 | 5.048
614.2 | 49.5 | 5.048
614.3 | 49.5 | 5.048
614.4 | 49.5 | 5.048
614.5 | 49.5 | 5.048
614.6 | 49.5 | 5.048
614.7 | 49.5 | 5.048
614.8 | 49.5 | 5.048
614.9 | 49.5 | 5.048
615 | 49.5 | 5.048
615.1 | 49.5 | 5.048
615.2 | 49.5 | 5.048
615.3 | 49.5 | 5.048
615.4 | 49.5 | 5.048
615.5 | 49.5 | 5.048
615.6 | 49.5 | 5.048
615.7 | 49.5 | 5.048
615.8 | 49.5 | 5.048
615.9 | 49.5 | 5.048
616 | 49.5 | 5.048
616.1 | 49.5 | 5.048
616.2 | 49.5 | 5.048
616.3 | 49.5 | 5.048
616.4 | 49.5 | 5.048
616.5 | 49.5 | 5.048
616.6 | 49.5 | 5.048
616.7 | 49.5 | 5.048
616.8 | 49.5 | 5.048
616.9 | 49.5 | 5.048
617 | 49.5 | 5.048
617.1 | 49.5 | 5.048
617.2 | 49.5 | 5.048
617.3 | 49.5 | 5.048
617.4 | 49.5 | 5.048
617.5 | 49.5 | 5.048
617.6 | 49.5 | 5.048
617.7 | 49.5 | 5.048
617.8 | 49.5 | 5.048
617.9 | 49.5 | 5.048
618 | 49.5 | 5.048
618.1 | 49.5 | 5.048
618.2 | 49.5 | 5.048
618.3 | 49.5 | 5.048
618.4 | 49.5 | 5.048
618.5 | 49.5 | 5.048
618.6 | 49.5 | 5.048
618.7 | 49.5 | 5.048
618.8 | 49.5 | 5.048
618.9 | 49.5 | 5.048
619 | 49.5 | 5.048
619.1 | 49.5 | 5.048
619.2 | 49.5 | 5.048
619.3 | 49.5 | 5.048
619.4 | 49.5 | 5.048
619.5 | 49.5 | 5.048
619.6 | 49.5 | 5.048
619.7 | 49.5 | 5.048
619.8 | 49.5 | 5.048
619.9 | 49.5 | 5.048
620 | 49.5 | 5.048
620.1 | 49.5 | 5.048
620.2 | 49.5 | 5.048
620.3 | 49.5 | 5.048
620.4 | 49.5 | 5.048
620.5 | 49.5 | 5.048
620.6 | 49.5 | 5.048
620.7 | 49.5 | 5.048
620.8 | 49.5 | 5.048
620.9 | 49.5 | 5.048
621 | 49.5 | 5.048
621.1 | 49.5 | 5.048
621.2 | 49.5 | 5.048
621.3 | 49.5 | 5.048
621.4 | 49.5 | 5.048
621.5 | 49.5 | 5.048
621.6 | 49.5 | 5.048
621.7 | 49.5 | 5.048
621.8 | 49.5 | 5.048
621.9 | 49.5 | 5.048
622 | 49.5 | 5.048
622.1 | 49.5 | 5.048
622.2 | 49.5 | 5.048
622.3 | 49.5 | 5.048
622.4 | 49.5 | 5.048
622.5 | 49.5 | 5.048
622.6 | 49.5 | 5.048
622.7 | 49.5 | 5.048
622.8 | 49.5 | 5.048
622.9 | 49.5 | 5.048
623 | 49.5 | 5.048
623.1 | 49.5 | 5.048
623.2 | 49.5 | 5.048
623.3 | 49.5 | 5.048
623.4 | 49.5 | 5.048
623.5 | 49.5 | 5.048
623.6 | 49.5 | 5.048
623.7 | 49.5 | 5.048
623.8 | 49.5 | 5.048
623.9 | 49.5 | 5.048
624 | 49.5 | 5.048
624.1 | 49.5 | 5.048
624.2 | 49.5 | 5.048
624.3 | 49.5 | 5.048
624.4 | 49.5 | 5.048
624.5 | 49.5 | 5.048
624.6 | 49.5 | 5.048
624.7 | 49.5 | 5.048
624.8 | 49.5 | 5.048
624.9 | 49.5 | 5.048
625 | 49.5 | 5.048
625.1 | 49.5 | 5.048
625.2 | 49.5 | 5.048
625.3 | 49.5 | 5.048
625.4 | 49.5 | 5.048
625.5 | 49.5 | 5.048
625.6 | 49.5 | 5.048
625.7 | 49.5 | 5.048
625.8 | 49.5 | 5.048
625.9 | 49.5 | 5.048
626 | 49.5 | 5.048
626.1 | 49.5 | 5.048
626.2 | 49.5 | 5.048
626.3 | 49.5 | 5.048
626.4 | 49.5 | 5.048
626.5 | 49.5 | 5.048
626.6 | 49.5 | 5.048
626.7 | 49.5 | 5.048
626.8 | 49.5 | 5.048
626.9 | 49.5 | 5.048
627 | 49.5 | 5.048
627.1 | 49.5 | 5.048
627.2 | 49.5 | 5.048
627.3 | 49.5 | 5.048
627.4 | 49.5 | 5.048
627.5 | 49.5 | 5.048
627.6 | 49.5 | 5.048
627.7 | 49.5 | 5.048
627.8 | 49.5 | 5.048
627.9 | 49.5 | 5.048
628 | 49.5 | 5.048
628.1 | 49.5 | 5.048
628.2 | 49.5 | 5.049
628.3 | 49.5 | 5.049
628.4 | 49.5 | 5.049
628.5 | 49.5 | 5.049
628.6 | 49.5 | 5.049
628.7 | 49.5 | 5.049
628.8 | 49.5 | 5.049
628.9 | 49.5 | 5.049
629 | 49.5 | 5.049
629.1 | 49.5 | 5.049
629.2 | 49.5 | 5.049
629.3 | 49.5 | 5.049
629.4 | 49.5 | 5.049
629.5 | 49.5 | 5.049
629.6 | 49.5 | 5.049
629.7 | 49.5 | 5.049
629.8 | 49.5 | 5.049
629.9 | 49.5 | 5.049
630 | 49.5 | 5.049
630.1 | 49.5 | 5.049
630.2 | 49.5 | 5.049
630.3 | 49.5 | 5.049
630.4 | 49.5 | 5.049
630.5 | 49.5 | 5.048
630.6 | 49.5 | 5.048
630.7 | 49.5 | 5.048
630.8 | 49.5 | 5.048
630.9 | 49.5 | 5.048
631 | 49.5 | 5.048
631.1 | 49.5 | 5.048
631.2 | 49.5 | 5.048
631.3 | 49.5 | 5.048
631.4 | 49.5 | 5.048
631.5 | 49.5 | 5.048
631.6 | 49.5 | 5.048
631.7 | 49.5 | 5.048
631.8 | 49.5 | 5.048
631.9 | 49.5 | 5.048
632 | 49.5 | 5.048
632.1 | 49.5 | 5.048
632.2 | 49.5 | 5.048
632.3 | 49.5 | 5.048
632.4 | 49.5 | 5.048
632.5 | 49.5 | 5.048
632.6 | 49.5 | 5.048
632.7 | 49.5 | 5.048
632.8 | 49.5 | 5.048
632.9 | 49.5 | 5.048
633 | 49.5 | 5.048
633.1 | 49.5 | 5.048
633.2 | 49.5 | 5.048
633.3 | 49.5 | 5.048
633.4 | 49.5 | 5.048
633.5 | 49.5 | 5.048
633.6 | 49.5 | 5.048
633.7 | 49.5 | 5.048
633.8 | 49.5 | 5.048
633.9 | 49.5 | 5.048
634 | 49.5 | 5.048
634.1 | 49.5 | 5.048
634.2 | 49.5 | 5.048
634.3 | 49.5 | 5.048
634.4 | 49.5 | 5.048
634.5 | 49.5 | 5.048
634.6 | 49.5 | 5.048
634.7 | 49.5 | 5.048
634.8 | 49.5 | 5.048
634.9 | 49.5 | 5.048
635 | 49.5 | 5.048
635.1 | 49.5 | 5.048
635.2 | 49.5 | 5.048
635.3 | 49.5 | 5.048
635.4 | 49.5 | 5.048
635.5 | 49.5 | 5.048
635.6 | 49.5 | 5.048
635.7 | 49.5 | 5.048
635.8 | 49.5 | 5.048
635.9 | 49.5 | 5.048
636 | 49.5 | 5.048
636.1 | 49.5 | 5.048
636.2 | 49.5 | 5.048
636.3 | 49.5 | 5.048
636.4 | 49.5 | 5.048
636.5 | 49.5 | 5.048
636.6 | 49.5 | 5.048
636.7 | 49.5 | 5.048
636.8 | 49.5 | 5.048
636.9 | 49.5 | 5.048
637 | 49.5 | 5.048
637.1 | 49.5 | 5.048
637.2 | 49.5 | 5.048
637.3 | 49.5 | 5.048
637.4 | 49.5 | 5.048
637.5 | 49.5 | 5.048
637.6 | 49.5 | 5.048
637.7 | 49.5 | 5.048
637.8 | 49.5 | 5.048
637.9 | 49.5 | 5.048
638 | 49.5 | 5.048
638.1 | 49.5 | 5.048
638.2 | 49.5 | 5.048
638.3 | 49.5 | 5.048
638.4 | 49.5 | 5.048
638.5 | 49.5 | 5.048
638.6 | 49.5 | 5.048
638.7 | 49.5 | 5.048
638.8 | 49.5 | 5.048
638.9 | 49.5 | 5.048
639 | 49.5 | 5.048
639.1 | 49.5 | 5.048
639.2 | 49.5 | 5.048
639.3 | 49.5 | 5.048
639.4 | 49.5 | 5.048
639.5 | 49.5 | 5.048
639.6 | 49.5 | 5.048
639.7 | 49.5 | 5.048
639.8 | 49.5 | 5.049
639.9 | 49.5 | 5.049
640 | 49.5 | 5.049
640.1 | 49.5 | 5.049
640.2 | 49.5 | 5.049
640.3 | 49.5 | 5.049
640.4 | 49.5 | 5.049
640.5 | 49.5 | 5.049
640.6 | 49.5 | 5.049
640.7 | 49.5 | 5.049
640.8 | 49.5 | 5.049
640.9 | 49.5 | 5.049
641 | 49.5 | 5.049
641.1 | 49.5 | 5.049
641.2 | 49.5 | 5.049
641.3 | 49.5 | 5.049
641.4 | 49.5 | 5.049
641.5 | 49.5 | 5.049
641.6 | 49.5 | 5.049
641.7 | 49.5 | 5.049
641.8 | 49.5 | 5.049
641.9 | 49.5 | 5.049
642 | 49.5 | 5.049
642.1 | 49.5 | 5.049
642.2 | 49.5 | 5.048
642.3 | 49.5 | 5.048
642.4 | 49.5 | 5.048
642.5 | 49.5 | 5.048
642.6 | 49.5 | 5.048
642.7 | 49.5 | 5.048
642.8 | 49.5 | 5.048
642.9 | 49.5 | 5.048
643 | 49.5 | 5.048
643.1 | 49.5 | 5.048
643.2 | 49.5 | 5.048
643.3 | 49.5 | 5.048
643.4 | 49.5 | 5.048
643.5 | 49.5 | 5.048
643.6 | 49.5 | 5.048
643.7 | 49.5 | 5.048
643.8 | 49.5 | 5.048
643.9 | 49.5 | 5.048
644 | 49.5 | 5.048
644.1 | 49.5 | 5.048
644.2 | 49.5 | 5.048
644.3 | 49.5 | 5.048
644.4 | 49.5 | 5.048
644.5 | 49.5 | 5.048
644.6 | 49.5 | 5.048
644.7 | 49.5 | 5.048
644.8 | 49.5 | 5.048
644.9 | 49.5 | 5.048
645 | 49.5 | 5.048
645.1 | 49.5 | 5.048
645.2 | 49.5 | 5.048
645.3 | 49.5 | 5.048
645.4 | 49.5 | 5.048
645.5 | 49.5 | 5.048
645.6 | 49.5 | 5.048
645.7 | 49.5 | 5.048
645.8 | 49.5 | 5.048
645.9 | 49.5 | 5.048
646 | 49.5 | 5.048
646.1 | 49.5 | 5.048
646.2 | 49.5 | 5.048
646.3 | 49.5 | 5.048
646.4 | 49.5 | 5.048
646.5 | 49.5 | 5.048
646.6 | 49.5 | 5.048
646.7 | 49.5 | 5.048
646.8 | 49.5 | 5.048
646.9 | 49.5 | 5.048
647 | 49.5 | 5.048
647.1 | 49.5 | 5.048
647.2 | 49.5 | 5.048
647.3 | 49.5 | 5.048
647.4 | 49.5 | 5.048
647.5 | 49.5 | 5.048
647.6 | 49.5 | 5.048
647.7 | 49.5 | 5.048
647.8 | 49.5 | 5.048
647.9 | 49.5 | 5.048
648 | 49.5 | 5.048
648.1 | 49.5 | 5.048
648.2 | 49.5 | 5.048
648.3 | 49.5 | 5.048
648.4 | 49.5 | 5.048
648.5 | 49.5 | 5.048
648.6 | 49.5 | 5.048
648.7 | 49.5 | 5.048
648.8 | 49.5 | 5.048
648.9 | 49.5 | 5.048
649 | 49.5 | 5.048
649.1 | 49.5 | 5.048
649.2 | 49.5 | 5.048
649.3 | 49.5 | 5.049
649.4 | 49.5 | 5.049
649.5 | 49.5 | 5.049
649.6 | 49.5 | 5.049
649.7 | 49.5 | 5.049
649.8 | 49.5 | 5.049
649.9 | 49.5 | 5.049
650 | 49.5 | 5.049
650.1 | 49.5 | 5.049
650.2 | 49.5 | 5.049
650.3 | 49.5 | 5.049
650.4 | 49.5 | 5.049
650.5 | 49.5 | 5.049
650.6 | 49.5 | 5.049
650.7 | 49.5 | 5.049
650.8 | 49.5 | 5.049
650.9 | 49.5 | 5.049
651 | 49.5 | 5.049
651.1 | 49.5 | 5.049
651.2 | 49.5 | 5.049
651.3 | 49.5 | 5.049
651.4 | 49.5 | 5.049
651.5 | 49.5 | 5.049
651.6 | 49.5 | 5.048
651.7 | 49.5 | 5.048
651.8 | 49.5 | 5.048
651.9 | 49.5 | 5.048
652 | 49.5 | 5.048
652.1 | 49.5 | 5.048
652.2 | 49.5 | 5.048
652.3 | 49.5 | 5.048
652.4 | 49.5 | 5.048
652.5 | 49.5 | 5.048
652.6 | 49.5 | 5.048
652.7 | 49.5 | 5.048
652.8 | 49.5 | 5.047
652.9 | 49.5 | 5.047
653 | 49.5 | 5.047
653.1 | 49.5 | 5.047
653.2 | 49.5 | 5.048
653.3 | 49.5 | 5.048
653.4 | 49.5 | 5.048
653.5 | 49.5 | 5.048
653.6 | 49.5 | 5.048
653.7 | 49.5 | 5.048
653.8 | 49.5 | 5.048
653.9 | 49.5 | 5.048
654 | 49.5 | 5.048
654.1 | 49.5 | 5.048
654.2 | 49.5 | 5.048
654.3 | 49.5 | 5.048
654.4 | 49.5 | 5.048
654.5 | 49.5 | 5.048
654.6 | 49.5 | 5.048
654.7 | 49.5 | 5.048
654.8 | 49.5 | 5.048
654.9 | 49.5 | 5.048
655 | 49.5 | 5.048
655.1 | 49.5 | 5.048
655.2 | 49.5 | 5.048
655.3 | 49.5 | 5.048
655.4 | 49.5 | 5.048
655.5 | 49.5 | 5.048
655.6 | 49.5 | 5.048
655.7 | 49.5 | 5.048
655.8 | 49.5 | 5.048
655.9 | 49.5 | 5.048
656 | 49.5 | 5.048
656.1 | 49.5 | 5.048
656.2 | 49.5 | 5.048
656.3 | 49.5 | 5.048
656.4 | 49.5 | 5.048
656.5 | 49.5 | 5.048
656.6 | 49.5 | 5.048
656.7 | 49.5 | 5.048
656.8 | 49.5 | 5.048
656.9 | 49.5 | 5.048
657 | 49.5 | 5.048
657.1 | 49.5 | 5.048
657.2 | 49.5 | 5.048
657.3 | 49.5 | 5.049
657.4 | 49.5 | 5.049
657.5 | 49.5 | 5.049
657.6 | 49.5 | 5.049
657.7 | 49.5 | 5.049
657.8 | 49.5 | 5.049
657.9 | 49.5 | 5.049
658 | 49.5 | 5.049
658.1 | 49.5 | 5.049
658.2 | 49.5 | 5.049
658.3 | 49.5 | 5.049
658.4 | 49.5 | 5.049
658.5 | 49.5 | 5.048
658.6 | 49.5 | 5.048
658.7 | 49.5 | 5.048
658.8 | 49.5 | 5.048
658.9 | 49.5 | 5.048
659 | 49.5 | 5.048
659.1 | 49.5 | 5.048
659.2 | 49.5 | 5.048
659.3 | 49.5 | 5.048
659.4 | 49.5 | 5.048
659.5 | 49.5 | 5.048
659.6 | 49.5 | 5.048
659.7 | 49.5 | 5.048
659.8 | 49.5 | 5.048
659.9 | 49.5 | 5.048
660 | 49.5 | 5.048
660.1 | 49.5 | 5.048
660.2 | 49.5 | 5.048
660.3 | 49.5 | 5.048
660.4 | 49.5 | 5.048
660.5 | 49.5 | 5.048
660.6 | 49.5 | 5.048
660.7 | 49.5 | 5.048
660.8 | 49.5 | 5.048
660.9 | 49.5 | 5.048
661 | 49.5 | 5.048
661.1 | 49.5 | 5.048
661.2 | 49.5 | 5.048
661.3 | 49.5 | 5.048
661.4 | 49.5 | 5.048
661.5 | 49.5 | 5.048
661.6 | 49.5 | 5.048
661.7 | 49.5 | 5.048
661.8 | 49.5 | 5.048
661.9 | 49.5 | 5.048
662 | 49.5 | 5.048
662.1 | 49.5 | 5.048
662.2 | 49.5 | 5.048
662.3 | 49.5 | 5.048
662.4 | 49.5 | 5.048
662.5 | 49.5 | 5.048
662.6 | 49.5 | 5.048
662.7 | 49.5 | 5.048
662.8 | 49.5 | 5.048
662.9 | 49.5 | 5.048
663 | 49.5 | 5.048
663.1 | 49.5 | 5.048
663.2 | 49.5 | 5.048
663.3 | 49.5 | 5.048
663.4 | 49.5 | 5.048
663.5 | 49.5 | 5.048
663.6 | 49.5 | 5.048
663.7 | 49.5 | 5.048
663.8 | 49.5 | 5.048
663.9 | 49.5 | 5.048
664 | 49.5 | 5.048
664.1 | 49.5 | 5.048
664.2 | 49.5 | 5.048
664.3 | 49.5 | 5.048
664.4 | 49.5 | 5.048
664.5 | 49.5 | 5.048
664.6 | 49.5 | 5.048
664.7 | 49.5 | 5.048
664.8 | 49.5 | 5.048
664.9 | 49.5 | 5.048
665 | 49.5 | 5.048
665.1 | 49.5 | 5.048
665.2 | 49.5 | 5.048
665.3 | 49.5 | 5.048
665.4 | 49.5 | 5.048
665.5 | 49.5 | 5.048
665.6 | 49.5 | 5.048
665.7 | 49.5 | 5.048
665.8 | 49.5 | 5.048
665.9 | 49.5 | 5.048
666 | 49.5 | 5.048
666.1 | 49.5 | 5.048
666.2 | 49.5 | 5.048
666.3 | 49.5 | 5.048
666.4 | 49.5 | 5.048
666.5 | 49.5 | 5.048
666.6 | 49.5 | 5.048
666.7 | 49.5 | 5.048
666.8 | 49.5 | 5.048
666.9 | 49.5 | 5.048
667 | 49.5 | 5.048
667.1 | 49.5 | 5.048
667.2 | 49.5 | 5.048
667.3 | 49.5 | 5.048
667.4 | 49.5 | 5.048
667.5 | 49.5 | 5.048
667.6 | 49.5 | 5.048
667.7 | 49.5 | 5.048
667.8 | 49.5 | 5.048
667.9 | 49.5 | 5.048
668 | 49.5 | 5.048
668.1 | 49.5 | 5.048
668.2 | 49.5 | 5.048
668.3 | 49.5 | 5.048
668.4 | 49.5 | 5.048
668.5 | 49.5 | 5.048
668.6 | 49.5 | 5.048
668.7 | 49.5 | 5.048
668.8 | 49.5 | 5.048
668.9 | 49.5 | 5.048
669 | 49.5 | 5.048
669.1 | 49.5 | 5.048
669.2 | 49.5 | 5.048
669.3 | 49.5 | 5.048
669.4 | 49.5 | 5.048
669.5 | 49.5 | 5.048
669.6 | 49.5 | 5.048
669.7 | 49.5 | 5.048
669.8 | 49.5 | 5.048
669.9 | 49.5 | 5.048
670 | 49.5 | 5.048
670.1 | 49.5 | 5.048
670.2 | 49.5 | 5.048
670.3 | 49.5 | 5.048
670.4 | 49.5 | 5.048
670.5 | 49.5 | 5.048
670.6 | 49.5 | 5.048
670.7 | 49.5 | 5.048
670.8 | 49.5 | 5.048
670.9 | 49.5 | 5.048
671 | 49.5 | 5.048
671.1 | 49.5 | 5.048
671.2 | 49.5 | 5.048
671.3 | 49.5 | 5.048
671.4 | 49.5 | 5.048
671.5 | 49.5 | 5.048
671.6 | 49.5 | 5.048
671.7 | 49.5 | 5.048
671.8 | 49.5 | 5.048
671.9 | 49.5 | 5.048
672 | 49.5 | 5.048
672.1 | 49.5 | 5.048
672.2 | 49.5 | 5.048
672.3 | 49.5 | 5.048
672.4 | 49.5 | 5.048
672.5 | 49.5 | 5.048
672.6 | 49.5 | 5.048
672.7 | 49.5 | 5.048
672.8 | 49.5 | 5.048
672.9 | 49.5 | 5.048
673 | 49.5 | 5.048
673.1 | 49.5 | 5.048
673.2 | 49.5 | 5.048
673.3 | 49.5 | 5.048
673.4 | 49.5 | 5.048
673.5 | 49.5 | 5.048
673.6 | 49.5 | 5.048
673.7 | 49.5 | 5.048
673.8 | 49.5 | 5.048
673.9 | 49.5 | 5.048
674 | 49.5 | 5.048
674.1 | 49.5 | 5.048
674.2 | 49.5 | 5.048
674.3 | 49.5 | 5.048
674.4 | 49.5 | 5.048
674.5 | 49.5 | 5.048
674.6 | 49.5 | 5.048
674.7 | 49.5 | 5.048
674.8 | 49.5 | 5.048
674.9 | 49.5 | 5.048
675 | 49.5 | 5.048
675.1 | 49.5 | 5.048
675.2 | 49.5 | 5.048
675.3 | 49.5 | 5.048
675.4 | 49.5 | 5.048
675.5 | 49.5 | 5.048
675.6 | 49.5 | 5.048
675.7 | 49.5 | 5.048
675.8 | 49.5 | 5.048
675.9 | 49.5 | 5.048
676 | 49.5 | 5.048
676.1 | 49.5 | 5.048
676.2 | 49.5 | 5.048
676.3 | 49.5 | 5.048
676.4 | 49.5 | 5.048
676.5 | 49.5 | 5.048
676.6 | 49.5 | 5.048
676.7 | 49.5 | 5.048
676.8 | 49.5 | 5.048
676.9 | 49.5 | 5.048
677 | 49.5 | 5.048
677.1 | 49.5 | 5.048
677.2 | 49.5 | 5.048
677.3 | 49.5 | 5.048
677.4 | 49.5 | 5.048
677.5 | 49.5 | 5.048
677.6 | 49.5 | 5.048
677.7 | 49.5 | 5.048
677.8 | 49.5 | 5.048
677.9 | 49.5 | 5.048
678 | 49.5 | 5.048
678.1 | 49.5 | 5.048
678.2 | 49.5 | 5.048
678.3 | 49.5 | 5.048
678.4 | 49.5 | 5.048
678.5 | 49.5 | 5.048
678.6 | 49.5 | 5.048
678.7 | 49.5 | 5.048
678.8 | 49.5 | 5.048
678.9 | 49.5 | 5.048
679 | 49.5 | 5.048
679.1 | 49.5 | 5.048
679.2 | 49.5 | 5.048
679.3 | 49.5 | 5.048
679.4 | 49.5 | 5.048
679.5 | 49.5 | 5.048
679.6 | 49.5 | 5.048
679.7 | 49.5 | 5.048
679.8 | 49.5 | 5.048
679.9 | 49.5 | 5.048
680 | 49.5 | 5.048
680.1 | 49.5 | 5.048
680.2 | 49.5 | 5.048
680.3 | 49.5 | 5.048
680.4 | 49.5 | 5.048
680.5 | 49.5 | 5.048
680.6 | 49.5 | 5.048
680.7 | 49.5 | 5.048
680.8 | 49.5 | 5.048
680.9 | 49.5 | 5.048
681 | 49.5 | 5.048
681.1 | 49.5 | 5.048
681.2 | 49.5 | 5.048
681.3 | 49.5 | 5.048
681.4 | 49.5 | 5.048
681.5 | 49.5 | 5.048
681.6 | 49.5 | 5.048
681.7 | 49.5 | 5.048
681.8 | 49.5 | 5.048
681.9 | 49.5 | 5.048
682 | 49.5 | 5.048
682.1 | 49.5 | 5.048
682.2 | 49.5 | 5.048
682.3 | 49.5 | 5.048
682.4 | 49.5 | 5.048
682.5 | 49.5 | 5.048
682.6 | 49.5 | 5.048
682.7 | 49.5 | 5.048
682.8 | 49.5 | 5.048
682.9 | 49.5 | 5.048
683 | 49.5 | 5.048
683.1 | 49.5 | 5.048
683.2 | 49.5 | 5.048
683.3 | 49.5 | 5.048
683.4 | 49.5 | 5.048
683.5 | 49.5 | 5.048
683.6 | 49.5 | 5.048
683.7 | 49.5 | 5.048
683.8 | 49.5 | 5.048
683.9 | 49.5 | 5.048
684 | 49.5 | 5.048
684.1 | 49.5 | 5.048
684.2 | 49.5 | 5.048
684.3 | 49.5 | 5.048
684.4 | 49.5 | 5.048
684.5 | 49.5 | 5.048
684.6 | 49.5 | 5.048
684.7 | 49.5 | 5.048
684.8 | 49.5 | 5.048
684.9 | 49.5 | 5.048
685 | 49.5 | 5.048
685.1 | 49.5 | 5.048
685.2 | 49.5 | 5.048
685.3 | 49.5 | 5.048
685.4 | 49.5 | 5.048
685.5 | 49.5 | 5.048
685.6 | 49.5 | 5.048
685.7 | 49.5 | 5.048
685.8 | 49.5 | 5.048
685.9 | 49.5 | 5.048
686 | 49.5 | 5.048
686.1 | 49.5 | 5.048
686.2 | 49.5 | 5.048
686.3 | 49.5 | 5.048
686.4 | 49.5 | 5.048
686.5 | 49.5 | 5.048
686.6 | 49.5 | 5.048
686.7 | 49.5 | 5.048
686.8 | 49.5 | 5.048
686.9 | 49.5 | 5.048
687 | 49.5 | 5.048
687.1 | 49.5 | 5.048
687.2 | 49.5 | 5.048
687.3 | 49.5 | 5.048
687.4 | 49.5 | 5.048
687.5 | 49.5 | 5.048
687.6 | 49.5 | 5.048
687.7 | 49.5 | 5.048
687.8 | 49.5 | 5.048
687.9 | 49.5 | 5.048
688 | 49.5 | 5.048
688.1 | 49.5 | 5.048
688.2 | 49.5 | 5.048
688.3 | 49.5 | 5.048
688.4 | 49.5 | 5.048
688.5 | 49.5 | 5.048
688.6 | 49.5 | 5.048
688.7 | 49.5 | 5.048
688.8 | 49.5 | 5.048
688.9 | 49.5 | 5.048
689 | 49.5 | 5.048
689.1 | 49.5 | 5.048
689.2 | 49.5 | 5.048
689.3 | 49.5 | 5.048
689.4 | 49.5 | 5.048
689.5 | 49.5 | 5.048
689.6 | 49.5 | 5.048
689.7 | 49.5 | 5.048
689.8 | 49.5 | 5.048
689.9 | 49.5 | 5.048
690 | 49.5 | 5.048
690.1 | 49.5 | 5.048
690.2 | 49.5 | 5.048
690.3 | 49.5 | 5.048
690.4 | 49.5 | 5.048
690.5 | 49.5 | 5.048
690.6 | 49.5 | 5.048
690.7 | 49.5 | 5.048
690.8 | 49.5 | 5.048
690.9 | 49.5 | 5.048
691 | 49.5 | 5.048
691.1 | 49.5 | 5.048
691.2 | 49.5 | 5.048
691.3 | 49.5 | 5.049
691.4 | 49.5 | 5.049
691.5 | 49.5 | 5.049
691.6 | 49.5 | 5.049
691.7 | 49.5 | 5.049
691.8 | 49.5 | 5.049
691.9 | 49.5 | 5.049
692 | 49.5 | 5.049
692.1 | 49.5 | 5.049
692.2 | 49.5 | 5.049
692.3 | 49.5 | 5.049
692.4 | 49.5 | 5.049
692.5 | 49.5 | 5.048
692.6 | 49.5 | 5.048
692.7 | 49.5 | 5.048
692.8 | 49.5 | 5.048
692.9 | 49.5 | 5.048
693 | 49.5 | 5.048
693.1 | 49.5 | 5.048
693.2 | 49.5 | 5.048
693.3 | 49.5 | 5.048
693.4 | 49.5 | 5.048
693.5 | 49.5 | 5.048
693.6 | 49.5 | 5.048
693.7 | 49.5 | 5.048
693.8 | 49.5 | 5.048
693.9 | 49.5 | 5.048
694 | 49.5 | 5.048
694.1 | 49.5 | 5.048
694.2 | 49.5 | 5.048
694.3 | 49.5 | 5.048
694.4 | 49.5 | 5.048
694.5 | 49.5 | 5.048
694.6 | 49.5 | 5.048
694.7 | 49.5 | 5.048
694.8 | 49.5 | 5.048
694.9 | 49.5 | 5.048
695 | 49.5 | 5.048
695.1 | 49.5 | 5.048
695.2 | 49.5 | 5.048
695.3 | 49.5 | 5.048
695.4 | 49.5 | 5.048
695.5 | 49.5 | 5.048
695.6 | 49.5 | 5.048
695.7 | 49.5 | 5.048
695.8 | 49.5 | 5.048
695.9 | 49.5 | 5.048
696 | 49.5 | 5.048
696.1 | 49.5 | 5.048
696.2 | 49.5 | 5.048
696.3 | 49.5 | 5.048
696.4 | 49.5 | 5.048
696.5 | 49.5 | 5.048
696.6 | 49.5 | 5.048
696.7 | 49.5 | 5.048
696.8 | 49.5 | 5.048
696.9 | 49.5 | 5.048
697 | 49.5 | 5.048
697.1 | 49.5 | 5.048
697.2 | 49.5 | 5.048
697.3 | 49.5 | 5.048
697.4 | 49.5 | 5.049
697.5 | 49.5 | 5.049
697.6 | 49.5 | 5.049
697.7 | 49.5 | 5.049
697.8 | 49.5 | 5.049
697.9 | 49.5 | 5.049
698 | 49.5 | 5.049
698.1 | 49.5 | 5.049
698.2 | 49.5 | 5.049
698.3 | 49.5 | 5.049
698.4 | 49.5 | 5.049
698.5 | 49.5 | 5.049
698.6 | 49.5 | 5.049
698.7 | 49.5 | 5.049
698.8 | 49.5 | 5.049
698.9 | 49.5 | 5.049
699 | 49.5 | 5.049
699.1 | 49.5 | 5.049
699.2 | 49.5 | 5.049
699.3 | 49.5 | 5.049
699.4 | 49.5 | 5.049
699.5 | 49.5 | 5.049
699.6 | 49.5 | 5.049
699.7 | 49.5 | 5.049
699.8 | 49.5 | 5.049
699.9 | 49.5 | 5.049
700 | 49.5 | 5.049
700.1 | 49.5 | 5.049
700.2 | 49.5 | 5.049
700.3 | 49.5 | 5.049
700.4 | 49.5 | 5.049
700.5 | 49.5 | 5.049
700.6 | 49.5 | 5.049
700.7 | 49.5 | 5.049
700.8 | 49.5 | 5.049
700.9 | 49.5 | 5.049
701 | 49.5 | 5.048
701.1 | 49.5 | 5.048
701.2 | 49.5 | 5.048
701.3 | 49.5 | 5.048
701.4 | 49.5 | 5.048
701.5 | 49.5 | 5.048
701.6 | 49.5 | 5.048
701.7 | 49.5 | 5.048
701.8 | 49.5 | 5.048
701.9 | 49.5 | 5.048
702 | 49.5 | 5.048
702.1 | 49.5 | 5.048
702.2 | 49.5 | 5.048
702.3 | 49.5 | 5.048
702.4 | 49.5 | 5.048
702.5 | 49.5 | 5.048
702.6 | 49.5 | 5.048
702.7 | 49.5 | 5.048
702.8 | 49.5 | 5.048
702.9 | 49.5 | 5.048
703 | 49.5 | 5.048
703.1 | 49.5 | 5.048
703.2 | 49.5 | 5.048
703.3 | 49.5 | 5.049
703.4 | 49.5 | 5.049
703.5 | 49.5 | 5.049
703.6 | 49.5 | 5.049
703.7 | 49.5 | 5.049
703.8 | 49.5 | 5.049
703.9 | 49.5 | 5.049
704 | 49.5 | 5.049
704.1 | 49.5 | 5.049
704.2 | 49.5 | 5.049
704.3 | 49.5 | 5.049
704.4 | 49.5 | 5.048
704.5 | 49.5 | 5.048
704.6 | 49.5 | 5.048
704.7 | 49.5 | 5.048
704.8 | 49.5 | 5.048
704.9 | 49.5 | 5.048
705 | 49.5 | 5.048
705.1 | 49.5 | 5.048
705.2 | 49.5 | 5.048
705.3 | 49.5 | 5.048
705.4 | 49.5 | 5.048
705.5 | 49.5 | 5.048
705.6 | 49.5 | 5.048
705.7 | 49.5 | 5.048
705.8 | 49.5 | 5.048
705.9 | 49.5 | 5.048
706 | 49.5 | 5.048
706.1 | 49.5 | 5.048
706.2 | 49.5 | 5.048
706.3 | 49.5 | 5.048
706.4 | 49.5 | 5.048
706.5 | 49.5 | 5.048
706.6 | 49.5 | 5.048
706.7 | 49.5 | 5.048
706.8 | 49.5 | 5.048
706.9 | 49.5 | 5.048
707 | 49.5 | 5.048
707.1 | 49.5 | 5.048
707.2 | 49.5 | 5.048
707.3 | 49.5 | 5.048
707.4 | 49.5 | 5.048
707.5 | 49.5 | 5.048
707.6 | 49.5 | 5.048
707.7 | 49.5 | 5.048
707.8 | 49.5 | 5.048
707.9 | 49.5 | 5.048
708 | 49.5 | 5.048
708.1 | 49.5 | 5.048
708.2 | 49.5 | 5.048
708.3 | 49.5 | 5.048
708.4 | 49.5 | 5.048
708.5 | 49.5 | 5.048
708.6 | 49.5 | 5.048
708.7 | 49.5 | 5.048
708.8 | 49.5 | 5.048
708.9 | 49.5 | 5.048
709 | 49.5 | 5.048
709.1 | 49.5 | 5.048
709.2 | 49.5 | 5.048
709.3 | 49.5 | 5.048
709.4 | 49.5 | 5.048
709.5 | 49.5 | 5.048
709.6 | 49.5 | 5.048
709.7 | 49.5 | 5.048
709.8 | 49.5 | 5.048
709.9 | 49.5 | 5.048
710 | 49.5 | 5.048
710.1 | 49.5 | 5.048
710.2 | 49.5 | 5.048
710.3 | 49.5 | 5.048
710.4 | 49.5 | 5.048
710.5 | 49.5 | 5.048
710.6 | 49.5 | 5.048
710.7 | 49.5 | 5.048
710.8 | 49.5 | 5.048
710.9 | 49.5 | 5.048
711 | 49.5 | 5.048
711.1 | 49.5 | 5.048
711.2 | 49.5 | 5.048
711.3 | 49.5 | 5.048
711.4 | 49.5 | 5.048
711.5 | 49.5 | 5.048
711.6 | 49.5 | 5.048
711.7 | 49.5 | 5.048
711.8 | 49.5 | 5.049
711.9 | 49.5 | 5.049
712 | 49.5 | 5.049
712.1 | 49.5 | 5.049
712.2 | 49.5 | 5.049
712.3 | 49.5 | 5.049
712.4 | 49.5 | 5.049
712.5 | 49.5 | 5.049
712.6 | 49.5 | 5.049
712.7 | 49.5 | 5.049
712.8 | 49.5 | 5.048
712.9 | 49.5 | 5.048
713 | 49.5 | 5.048
713.1 | 49.5 | 5.048
713.2 | 49.5 | 5.048
713.3 | 49.5 | 5.048
713.4 | 49.5 | 5.048
713.5 | 49.5 | 5.048
713.6 | 49.5 | 5.048
713.7 | 49.5 | 5.048
713.8 | 49.5 | 5.048
713.9 | 49.5 | 5.048
714 | 49.5 | 5.048
714.1 | 49.5 | 5.048
714.2 | 49.5 | 5.049
714.3 | 49.5 | 5.049
714.4 | 49.5 | 5.049
714.5 | 49.5 | 5.049
714.6 | 49.5 | 5.049
714.7 | 49.5 | 5.049
714.8 | 49.5 | 5.049
714.9 | 49.5 | 5.049
715 | 49.5 | 5.049
715.1 | 49.5 | 5.049
715.2 | 49.5 | 5.049
715.3 | 49.5 | 5.049
715.4 | 49.5 | 5.049
715.5 | 49.5 | 5.049
715.6 | 49.5 | 5.049
715.7 | 49.5 | 5.049
715.8 | 49.5 | 5.049
715.9 | 49.5 | 5.049
716 | 49.5 | 5.048
716.1 | 49.5 | 5.048
716.2 | 49.5 | 5.048
716.3 | 49.5 | 5.048
716.4 | 49.5 | 5.048
716.5 | 49.5 | 5.048
716.6 | 49.5 | 5.048
716.7 | 49.5 | 5.048
716.8 | 49.5 | 5.048
716.9 | 49.5 | 5.048
717 | 49.5 | 5.048
717.1 | 49.5 | 5.048
717.2 | 49.5 | 5.048
717.3 | 49.5 | 5.048
717.4 | 49.5 | 5.048
717.5 | 49.5 | 5.048
717.6 | 49.5 | 5.048
717.7 | 49.5 | 5.048
717.8 | 49.5 | 5.048
717.9 | 49.5 | 5.048
718 | 49.5 | 5.048
718.1 | 49.5 | 5.048
718.2 | 49.5 | 5.048
718.3 | 49.5 | 5.048
718.4 | 49.5 | 5.049
718.5 | 49.5 | 5.049
718.6 | 49.5 | 5.049
718.7 | 49.5 | 5.049
718.8 | 49.5 | 5.049
718.9 | 49.5 | 5.049
719 | 49.5 | 5.049
719.1 | 49.5 | 5.049
719.2 | 49.5 | 5.049
719.3 | 49.5 | 5.049
719.4 | 49.5 | 5.049
719.5 | 49.5 | 5.049
719.6 | 49.5 | 5.049
719.7 | 49.5 | 5.049
719.8 | 49.5 | 5.049
719.9 | 49.5 | 5.049
720 | 49.5 | 5.049
720.1 | 49.5 | 5.049
720.2 | 49.5 | 5.048
720.3 | 49.5 | 5.048
720.4 | 49.5 | 5.048
720.5 | 49.5 | 5.048
720.6 | 49.5 | 5.047
720.7 | 49.5 | 5.047
720.8 | 49.5 | 5.047
720.9 | 49.5 | 5.047
721 | 49.5 | 5.047
721.1 | 49.5 | 5.047
721.2 | 49.5 | 5.047
721.3 | 49.5 | 5.047
721.4 | 49.5 | 5.048
721.5 | 49.5 | 5.048
721.6 | 49.5 | 5.048
721.7 | 49.5 | 5.048
721.8 | 49.5 | 5.048
721.9 | 49.5 | 5.049
722 | 49.5 | 5.049
722.1 | 49.5 | 5.049
722.2 | 49.5 | 5.049
722.3 | 49.5 | 5.049
722.4 | 49.5 | 5.049
722.5 | 49.5 | 5.049
722.6 | 49.5 | 5.049
722.7 | 49.5 | 5.049
722.8 | 49.5 | 5.049
722.9 | 49.5 | 5.049
723 | 49.5 | 5.048
723.1 | 49.5 | 5.048
723.2 | 49.5 | 5.048
723.3 | 49.5 | 5.048
723.4 | 49.5 | 5.048
723.5 | 49.5 | 5.048
723.6 | 49.5 | 5.048
723.7 | 49.5 | 5.048
723.8 | 49.5 | 5.048
723.9 | 49.5 | 5.048
724 | 49.5 | 5.048
724.1 | 49.5 | 5.048
724.2 | 49.5 | 5.048
724.3 | 49.5 | 5.048
724.4 | 49.5 | 5.048
724.5 | 49.5 | 5.048
724.6 | 49.5 | 5.048
724.7 | 49.5 | 5.048
724.8 | 49.5 | 5.048
724.9 | 49.5 | 5.048
725 | 49.5 | 5.048
725.1 | 49.5 | 5.048
725.2 | 49.5 | 5.048
725.3 | 49.5 | 5.048
725.4 | 49.5 | 5.048
725.5 | 49.5 | 5.048
725.6 | 49.5 | 5.048
725.7 | 49.5 | 5.048
725.8 | 49.5 | 5.048
725.9 | 49.5 | 5.048
726 | 49.5 | 5.048
726.1 | 49.5 | 5.048
726.2 | 49.5 | 5.048
726.3 | 49.5 | 5.048
726.4 | 49.5 | 5.048
726.5 | 49.5 | 5.048
726.6 | 49.5 | 5.048
726.7 | 49.5 | 5.048
726.8 | 49.5 | 5.048
726.9 | 49.5 | 5.048
727 | 49.5 | 5.048
727.1 | 49.5 | 5.048
727.2 | 49.5 | 5.048
727.3 | 49.5 | 5.048
727.4 | 49.5 | 5.048
727.5 | 49.5 | 5.048
727.6 | 49.5 | 5.048
727.7 | 49.5 | 5.048
727.8 | 49.5 | 5.048
727.9 | 49.5 | 5.048
728 | 49.5 | 5.048
728.1 | 49.5 | 5.048
728.2 | 49.5 | 5.048
728.3 | 49.5 | 5.048
728.4 | 49.5 | 5.048
728.5 | 49.5 | 5.048
728.6 | 49.5 | 5.048
728.7 | 49.5 | 5.048
728.8 | 49.5 | 5.048
728.9 | 49.5 | 5.048
729 | 49.5 | 5.048
729.1 | 49.5 | 5.048
729.2 | 49.5 | 5.048
729.3 | 49.5 | 5.048
729.4 | 49.5 | 5.048
729.5 | 49.5 | 5.048
729.6 | 49.5 | 5.048
729.7 | 49.5 | 5.048
729.8 | 49.5 | 5.048
729.9 | 49.5 | 5.048
730 | 49.5 | 5.048
730.1 | 49.5 | 5.048
730.2 | 49.5 | 5.048
730.3 | 49.5 | 5.048
730.4 | 49.5 | 5.048
730.5 | 49.5 | 5.048
730.6 | 49.5 | 5.048
730.7 | 49.5 | 5.048
730.8 | 49.5 | 5.048
730.9 | 49.5 | 5.048
731 | 49.5 | 5.048
731.1 | 49.5 | 5.048
731.2 | 49.5 | 5.048
731.3 | 49.5 | 5.048
731.4 | 49.5 | 5.048
731.5 | 49.5 | 5.048
731.6 | 49.5 | 5.048
731.7 | 49.5 | 5.048
731.8 | 49.5 | 5.048
731.9 | 49.5 | 5.048
732 | 49.5 | 5.048
732.1 | 49.5 | 5.048
732.2 | 49.5 | 5.048
732.3 | 49.5 | 5.048
732.4 | 49.5 | 5.048
732.5 | 49.5 | 5.048
732.6 | 49.5 | 5.048
732.7 | 49.5 | 5.048
732.8 | 49.5 | 5.048
732.9 | 49.5 | 5.048
733 | 49.5 | 5.048
733.1 | 49.5 | 5.048
733.2 | 49.5 | 5.048
733.3 | 49.5 | 5.048
733.4 | 49.5 | 5.048
733.5 | 49.5 | 5.048
733.6 | 49.5 | 5.048
733.7 | 49.5 | 5.048
733.8 | 49.5 | 5.048
733.9 | 49.5 | 5.048
734 | 49.5 | 5.048
734.1 | 49.5 | 5.048
734.2 | 49.5 | 5.048
734.3 | 49.5 | 5.048
734.4 | 49.5 | 5.048
734.5 | 49.5 | 5.048
734.6 | 49.5 | 5.048
734.7 | 49.5 | 5.048
734.8 | 49.5 | 5.048
734.9 | 49.5 | 5.048
735 | 49.5 | 5.048
735.1 | 49.5 | 5.048
735.2 | 49.5 | 5.048
735.3 | 49.5 | 5.048
735.4 | 49.5 | 5.048
735.5 | 49.5 | 5.048
735.6 | 49.5 | 5.048
735.7 | 49.5 | 5.048
735.8 | 49.5 | 5.048
735.9 | 49.5 | 5.048
736 | 49.5 | 5.048
736.1 | 49.5 | 5.048
736.2 | 49.5 | 5.048
736.3 | 49.5 | 5.048
736.4 | 49.5 | 5.048
736.5 | 49.5 | 5.048
736.6 | 49.5 | 5.048
736.7 | 49.5 | 5.048
736.8 | 49.5 | 5.048
736.9 | 49.5 | 5.048
737 | 49.5 | 5.048
737.1 | 49.5 | 5.048
737.2 | 49.5 | 5.048
737.3 | 49.5 | 5.048
737.4 | 49.5 | 5.048
737.5 | 49.5 | 5.048
737.6 | 49.5 | 5.048
737.7 | 49.5 | 5.048
737.8 | 49.5 | 5.048
737.9 | 49.5 | 5.048
738 | 49.5 | 5.048
738.1 | 49.5 | 5.048
738.2 | 49.5 | 5.048
738.3 | 49.5 | 5.048
738.4 | 49.5 | 5.048
738.5 | 49.5 | 5.048
738.6 | 49.5 | 5.048
738.7 | 49.5 | 5.048
738.8 | 49.5 | 5.048
738.9 | 49.5 | 5.048
739 | 49.5 | 5.048
739.1 | 49.5 | 5.048
739.2 | 49.5 | 5.048
739.3 | 49.5 | 5.048
739.4 | 49.5 | 5.048
739.5 | 49.5 | 5.048
739.6 | 49.5 | 5.048
739.7 | 49.5 | 5.048
739.8 | 49.5 | 5.048
739.9 | 49.5 | 5.048
740 | 49.5 | 5.048
740.1 | 49.5 | 5.048
740.2 | 49.5 | 5.048
740.3 | 49.5 | 5.048
740.4 | 49.5 | 5.048
740.5 | 49.5 | 5.048
740.6 | 49.5 | 5.048
740.7 | 49.5 | 5.048
740.8 | 49.5 | 5.048
740.9 | 49.5 | 5.048
741 | 49.5 | 5.048
741.1 | 49.5 | 5.048
741.2 | 49.5 | 5.048
741.3 | 49.5 | 5.048
741.4 | 49.5 | 5.048
741.5 | 49.5 | 5.048
741.6 | 49.5 | 5.048
741.7 | 49.5 | 5.048
741.8 | 49.5 | 5.048
741.9 | 49.5 | 5.048
742 | 49.5 | 5.048
742.1 | 49.5 | 5.048
742.2 | 49.5 | 5.048
742.3 | 49.5 | 5.048
742.4 | 49.5 | 5.048
742.5 | 49.5 | 5.048
742.6 | 49.5 | 5.048
742.7 | 49.5 | 5.048
742.8 | 49.5 | 5.048
742.9 | 49.5 | 5.048
743 | 49.5 | 5.048
743.1 | 49.5 | 5.048
743.2 | 49.5 | 5.048
743.3 | 49.5 | 5.048
743.4 | 49.5 | 5.048
743.5 | 49.5 | 5.048
743.6 | 49.5 | 5.048
743.7 | 49.5 | 5.048
743.8 | 49.5 | 5.048
743.9 | 49.5 | 5.048
744 | 49.5 | 5.048
744.1 | 49.5 | 5.048
744.2 | 49.5 | 5.048
744.3 | 49.5 | 5.048
744.4 | 49.5 | 5.048
744.5 | 49.5 | 5.048
744.6 | 49.5 | 5.048
744.7 | 49.5 | 5.048
744.8 | 49.5 | 5.048
744.9 | 49.5 | 5.048
745 | 49.5 | 5.048
745.1 | 49.5 | 5.048
745.2 | 49.5 | 5.048
745.3 | 49.5 | 5.048
745.4 | 49.5 | 5.048
745.5 | 49.5 | 5.048
745.6 | 49.5 | 5.048
745.7 | 49.5 | 5.048
745.8 | 49.5 | 5.048
745.9 | 49.5 | 5.048
746 | 49.5 | 5.048
746.1 | 49.5 | 5.048
746.2 | 49.5 | 5.048
746.3 | 49.5 | 5.048
746.4 | 49.5 | 5.048
746.5 | 49.5 | 5.048
746.6 | 49.5 | 5.048
746.7 | 49.5 | 5.048
746.8 | 49.5 | 5.048
746.9 | 49.5 | 5.048
747 | 49.5 | 5.048
747.1 | 49.5 | 5.048
747.2 | 49.5 | 5.048
747.3 | 49.5 | 5.048
747.4 | 49.5 | 5.048
747.5 | 49.5 | 5.048
747.6 | 49.5 | 5.048
747.7 | 49.5 | 5.048
747.8 | 49.5 | 5.048
747.9 | 49.5 | 5.048
748 | 49.5 | 5.048
748.1 | 49.5 | 5.048
748.2 | 49.5 | 5.048
748.3 | 49.5 | 5.048
748.4 | 49.5 | 5.048
748.5 | 49.5 | 5.048
748.6 | 49.5 | 5.048
748.7 | 49.5 | 5.048
748.8 | 49.5 | 5.048
748.9 | 49.5 | 5.048
749 | 49.5 | 5.048
749.1 | 49.5 | 5.048
749.2 | 49.5 | 5.048
749.3 | 49.5 | 5.048
749.4 | 49.5 | 5.048
749.5 | 49.5 | 5.048
749.6 | 49.5 | 5.048
749.7 | 49.5 | 5.048
749.8 | 49.5 | 5.048
749.9 | 49.5 | 5.048
750 | 49.5 | 5.048
750.1 | 49.5 | 5.048
750.2 | 49.5 | 5.048
750.3 | 49.5 | 5.048
750.4 | 49.5 | 5.048
750.5 | 49.5 | 5.048
750.6 | 49.5 | 5.048
750.7 | 49.5 | 5.048
750.8 | 49.5 | 5.048
750.9 | 49.5 | 5.048
751 | 49.5 | 5.048
751.1 | 49.5 | 5.048
751.2 | 49.5 | 5.048
751.3 | 49.5 | 5.048
751.4 | 49.5 | 5.048
751.5 | 49.5 | 5.048
751.6 | 49.5 | 5.048
751.7 | 49.5 | 5.048
751.8 | 49.5 | 5.048
751.9 | 49.5 | 5.048
752 | 49.5 | 5.048
752.1 | 49.5 | 5.048
752.2 | 49.5 | 5.048
752.3 | 49.5 | 5.048
752.4 | 49.5 | 5.048
752.5 | 49.5 | 5.048
752.6 | 49.5 | 5.048
752.7 | 49.5 | 5.048
752.8 | 49.5 | 5.048
752.9 | 49.5 | 5.048
753 | 49.5 | 5.048
753.1 | 49.5 | 5.048
753.2 | 49.5 | 5.048
753.3 | 49.5 | 5.048
753.4 | 49.5 | 5.048
753.5 | 49.5 | 5.048
753.6 | 49.5 | 5.048
753.7 | 49.5 | 5.048
753.8 | 49.5 | 5.048
753.9 | 49.5 | 5.048
754 | 49.5 | 5.048
754.1 | 49.5 | 5.048
754.2 | 49.5 | 5.048
754.3 | 49.5 | 5.048
754.4 | 49.5 | 5.048
754.5 | 49.5 | 5.048
754.6 | 49.5 | 5.048
754.7 | 49.5 | 5.048
754.8 | 49.5 | 5.048
754.9 | 49.5 | 5.048
755 | 49.5 | 5.048
755.1 | 49.5 | 5.048
755.2 | 49.5 | 5.048
755.3 | 49.5 | 5.048
755.4 | 49.5 | 5.048
755.5 | 49.5 | 5.048
755.6 | 49.5 | 5.048
755.7 | 49.5 | 5.048
755.8 | 49.5 | 5.048
755.9 | 49.5 | 5.048
756 | 49.5 | 5.048
756.1 | 49.5 | 5.048
756.2 | 49.5 | 5.048
756.3 | 49.5 | 5.048
756.4 | 49.5 | 5.048
756.5 | 49.5 | 5.048
756.6 | 49.5 | 5.048
756.7 | 49.5 | 5.048
756.8 | 49.5 | 5.048
756.9 | 49.5 | 5.048
757 | 49.5 | 5.048
757.1 | 49.5 | 5.048
757.2 | 49.5 | 5.048
757.3 | 49.5 | 5.048
757.4 | 49.5 | 5.048
757.5 | 49.5 | 5.048
757.6 | 49.5 | 5.048
757.7 | 49.5 | 5.048
757.8 | 49.5 | 5.048
757.9 | 49.5 | 5.048
758 | 49.5 | 5.048
758.1 | 49.5 | 5.048
758.2 | 49.5 | 5.048
758.3 | 49.5 | 5.048
758.4 | 49.5 | 5.048
758.5 | 49.5 | 5.048
758.6 | 49.5 | 5.048
758.7 | 49.5 | 5.048
758.8 | 49.5 | 5.048
758.9 | 49.5 | 5.048
759 | 49.5 | 5.048
759.1 | 49.5 | 5.048
759.2 | 49.5 | 5.048
759.3 | 49.5 | 5.048
759.4 | 49.5 | 5.048
759.5 | 49.5 | 5.048
759.6 | 49.5 | 5.048
759.7 | 49.5 | 5.048
759.8 | 49.5 | 5.048
759.9 | 49.5 | 5.048
760 | 49.5 | 5.048
760.1 | 49.5 | 5.048
760.2 | 49.5 | 5.048
760.3 | 49.5 | 5.048
760.4 | 49.5 | 5.048
760.5 | 49.5 | 5.048
760.6 | 49.5 | 5.048
760.7 | 49.5 | 5.048
760.8 | 49.5 | 5.048
760.9 | 49.5 | 5.048
761 | 49.5 | 5.048
761.1 | 49.5 | 5.048
761.2 | 49.5 | 5.048
761.3 | 49.5 | 5.048
761.4 | 49.5 | 5.048
761.5 | 49.5 | 5.048
761.6 | 49.5 | 5.048
761.7 | 49.5 | 5.048
761.8 | 49.5 | 5.048
761.9 | 49.5 | 5.048
762 | 49.5 | 5.048
762.1 | 49.5 | 5.048
762.2 | 49.5 | 5.048
762.3 | 49.5 | 5.048
762.4 | 49.5 | 5.048
762.5 | 49.5 | 5.048
762.6 | 49.5 | 5.048
762.7 | 49.5 | 5.048
762.8 | 49.5 | 5.048
762.9 | 49.5 | 5.048
763 | 49.5 | 5.048
763.1 | 49.5 | 5.048
763.2 | 49.5 | 5.048
763.3 | 49.5 | 5.048
763.4 | 49.5 | 5.048
763.5 | 49.5 | 5.048
763.6 | 49.5 | 5.048
763.7 | 49.5 | 5.048
763.8 | 49.5 | 5.048
763.9 | 49.5 | 5.048
764 | 49.5 | 5.048
764.1 | 49.5 | 5.048
764.2 | 49.5 | 5.048
764.3 | 49.5 | 5.048
764.4 | 49.5 | 5.048
764.5 | 49.5 | 5.048
764.6 | 49.5 | 5.048
764.7 | 49.5 | 5.048
764.8 | 49.5 | 5.048
764.9 | 49.5 | 5.048
765 | 49.5 | 5.048
765.1 | 49.5 | 5.048
765.2 | 49.5 | 5.048
765.3 | 49.5 | 5.048
765.4 | 49.5 | 5.048
765.5 | 49.5 | 5.048
765.6 | 49.5 | 5.048
765.7 | 49.5 | 5.048
765.8 | 49.5 | 5.048
765.9 | 49.5 | 5.048
766 | 49.5 | 5.048
766.1 | 49.5 | 5.048
766.2 | 49.5 | 5.048
766.3 | 49.5 | 5.048
766.4 | 49.5 | 5.048
766.5 | 49.5 | 5.048
766.6 | 49.5 | 5.048
766.7 | 49.5 | 5.048
766.8 | 49.5 | 5.048
766.9 | 49.5 | 5.048
767 | 49.5 | 5.048
767.1 | 49.5 | 5.048
767.2 | 49.5 | 5.048
767.3 | 49.5 | 5.048
767.4 | 49.5 | 5.048
767.5 | 49.5 | 5.048
767.6 | 49.5 | 5.048
767.7 | 49.5 | 5.048
767.8 | 49.5 | 5.048
767.9 | 49.5 | 5.048
768 | 49.5 | 5.048
768.1 | 49.5 | 5.048
768.2 | 49.5 | 5.048
768.3 | 49.5 | 5.048
768.4 | 49.5 | 5.048
768.5 | 49.5 | 5.048
768.6 | 49.5 | 5.048
768.7 | 49.5 | 5.048
768.8 | 49.5 | 5.048
768.9 | 49.5 | 5.048
769 | 49.5 | 5.048
769.1 | 49.5 | 5.048
769.2 | 49.5 | 5.048
769.3 | 49.5 | 5.048
769.4 | 49.5 | 5.048
769.5 | 49.5 | 5.048
769.6 | 49.5 | 5.048
769.7 | 49.5 | 5.048
769.8 | 49.5 | 5.048
769.9 | 49.5 | 5.048
770 | 49.5 | 5.048
770.1 | 49.5 | 5.048
770.2 | 49.5 | 5.048
770.3 | 49.5 | 5.048
770.4 | 49.5 | 5.048
770.5 | 49.5 | 5.048
770.6 | 49.5 | 5.048
770.7 | 49.5 | 5.048
770.8 | 49.5 | 5.048
770.9 | 49.5 | 5.048
771 | 49.5 | 5.048
771.1 | 49.5 | 5.048
771.2 | 49.5 | 5.048
771.3 | 49.5 | 5.048
771.4 | 49.5 | 5.048
771.5 | 49.5 | 5.048
771.6 | 49.5 | 5.048
771.7 | 49.5 | 5.048
771.8 | 49.5 | 5.048
771.9 | 49.5 | 5.048
772 | 49.5 | 5.048
772.1 | 49.5 | 5.048
772.2 | 49.5 | 5.048
772.3 | 49.5 | 5.048
772.4 | 49.5 | 5.048
772.5 | 49.5 | 5.048
772.6 | 49.5 | 5.048
772.7 | 49.5 | 5.048
772.8 | 49.5 | 5.048
772.9 | 49.5 | 5.048
773 | 49.5 | 5.048
773.1 | 49.5 | 5.048
773.2 | 49.5 | 5.048
773.3 | 49.5 | 5.048
773.4 | 49.5 | 5.048
773.5 | 49.5 | 5.048
773.6 | 49.5 | 5.048
773.7 | 49.5 | 5.048
773.8 | 49.5 | 5.048
773.9 | 49.5 | 5.048
774 | 49.5 | 5.048
774.1 | 49.5 | 5.048
774.2 | 49.5 | 5.048
774.3 | 49.5 | 5.048
774.4 | 49.5 | 5.048
774.5 | 49.5 | 5.048
774.6 | 49.5 | 5.048
774.7 | 49.5 | 5.048
774.8 | 49.5 | 5.048
774.9 | 49.5 | 5.048
775 | 49.5 | 5.048
775.1 | 49.5 | 5.048
775.2 | 49.5 | 5.048
775.3 | 49.5 | 5.048
775.4 | 49.5 | 5.048
775.5 | 49.5 | 5.048
775.6 | 49.5 | 5.048
775.7 | 49.5 | 5.048
775.8 | 49.5 | 5.048
775.9 | 49.5 | 5.048
776 | 49.5 | 5.048
776.1 | 49.5 | 5.048
776.2 | 49.5 | 5.048
776.3 | 49.5 | 5.048
776.4 | 49.5 | 5.048
776.5 | 49.5 | 5.048
776.6 | 49.5 | 5.048
776.7 | 49.5 | 5.048
776.8 | 49.5 | 5.048
776.9 | 49.5 | 5.048
777 | 49.5 | 5.048
777.1 | 49.5 | 5.048
777.2 | 49.5 | 5.048
777.3 | 49.5 | 5.048
777.4 | 49.5 | 5.048
777.5 | 49.5 | 5.048
777.6 | 49.5 | 5.048
777.7 | 49.5 | 5.048
777.8 | 49.5 | 5.048
777.9 | 49.5 | 5.048
778 | 49.5 | 5.048
778.1 | 49.5 | 5.048
778.2 | 49.5 | 5.048
778.3 | 49.5 | 5.048
778.4 | 49.5 | 5.048
778.5 | 49.5 | 5.048
778.6 | 49.5 | 5.048
778.7 | 49.5 | 5.048
778.8 | 49.5 | 5.048
778.9 | 49.5 | 5.048
779 | 49.5 | 5.048
779.1 | 49.5 | 5.048
779.2 | 49.5 | 5.048
779.3 | 49.5 | 5.048
779.4 | 49.5 | 5.048
779.5 | 49.5 | 5.048
779.6 | 49.5 | 5.048
779.7 | 49.5 | 5.048
779.8 | 49.5 | 5.048
779.9 | 49.5 | 5.048
780 | 49.5 | 5.048
780.1 | 49.5 | 5.048
780.2 | 49.5 | 5.048
780.3 | 49.5 | 5.048
780.4 | 49.5 | 5.048
780.5 | 49.5 | 5.048
780.6 | 49.5 | 5.048
780.7 | 49.5 | 5.048
780.8 | 49.5 | 5.048
780.9 | 49.5 | 5.048
781 | 49.5 | 5.048
781.1 | 49.5 | 5.048
781.2 | 49.5 | 5.048
781.3 | 49.5 | 5.048
781.4 | 49.5 | 5.048
781.5 | 49.5 | 5.048
781.6 | 49.5 | 5.048
781.7 | 49.5 | 5.048
781.8 | 49.5 | 5.048
781.9 | 49.5 | 5.048
782 | 49.5 | 5.048
782.1 | 49.5 | 5.048
782.2 | 49.5 | 5.048
782.3 | 49.5 | 5.048
782.4 | 49.5 | 5.048
782.5 | 49.5 | 5.048
782.6 | 49.5 | 5.048
782.7 | 49.5 | 5.048
782.8 | 49.5 | 5.048
782.9 | 49.5 | 5.048
783 | 49.5 | 5.048
783.1 | 49.5 | 5.048
783.2 | 49.5 | 5.048
783.3 | 49.5 | 5.048
783.4 | 49.5 | 5.048
783.5 | 49.5 | 5.048
783.6 | 49.5 | 5.048
783.7 | 49.5 | 5.048
783.8 | 49.5 | 5.048
783.9 | 49.5 | 5.048
784 | 49.5 | 5.048
784.1 | 49.5 | 5.048
784.2 | 49.5 | 5.048
784.3 | 49.5 | 5.048
784.4 | 49.5 | 5.048
784.5 | 49.5 | 5.048
784.6 | 49.5 | 5.048
784.7 | 49.5 | 5.048
784.8 | 49.5 | 5.048
784.9 | 49.5 | 5.048
785 | 49.5 | 5.048
785.1 | 49.5 | 5.048
785.2 | 49.5 | 5.048
785.3 | 49.5 | 5.048
785.4 | 49.5 | 5.048
785.5 | 49.5 | 5.048
785.6 | 49.5 | 5.048
785.7 | 49.5 | 5.048
785.8 | 49.5 | 5.048
785.9 | 49.5 | 5.048
786 | 49.5 | 5.048
786.1 | 49.5 | 5.048
786.2 | 49.5 | 5.048
786.3 | 49.5 | 5.049
786.4 | 49.5 | 5.049
786.5 | 49.5 | 5.049
786.6 | 49.5 | 5.049
786.7 | 49.5 | 5.049
786.8 | 49.5 | 5.049
786.9 | 49.5 | 5.049
787 | 49.5 | 5.049
787.1 | 49.5 | 5.049
787.2 | 49.5 | 5.049
787.3 | 49.5 | 5.048
787.4 | 49.5 | 5.048
787.5 | 49.5 | 5.048
787.6 | 49.5 | 5.048
787.7 | 49.5 | 5.048
787.8 | 49.5 | 5.048
787.9 | 49.5 | 5.048
788 | 49.5 | 5.048
788.1 | 49.5 | 5.048
788.2 | 49.5 | 5.048
788.3 | 49.5 | 5.048
788.4 | 49.5 | 5.048
788.5 | 49.5 | 5.048
788.6 | 49.5 | 5.048
788.7 | 49.5 | 5.048
788.8 | 49.5 | 5.048
788.9 | 49.5 | 5.048
789 | 49.5 | 5.048
789.1 | 49.5 | 5.048
789.2 | 49.5 | 5.048
789.3 | 49.5 | 5.048
789.4 | 49.5 | 5.048
789.5 | 49.5 | 5.048
789.6 | 49.5 | 5.048
789.7 | 49.5 | 5.048
789.8 | 49.5 | 5.048
789.9 | 49.5 | 5.048
790 | 49.5 | 5.048
790.1 | 49.5 | 5.048
790.2 | 49.5 | 5.048
790.3 | 49.5 | 5.048
790.4 | 49.5 | 5.048
790.5 | 49.5 | 5.048
790.6 | 49.5 | 5.048
790.7 | 49.5 | 5.048
790.8 | 49.5 | 5.048
790.9 | 49.5 | 5.048
791 | 49.5 | 5.048
791.1 | 49.5 | 5.048
791.2 | 49.5 | 5.048
791.3 | 49.5 | 5.048
791.4 | 49.5 | 5.048
791.5 | 49.5 | 5.048
791.6 | 49.5 | 5.048
791.7 | 49.5 | 5.048
791.8 | 49.5 | 5.048
791.9 | 49.5 | 5.048
792 | 49.5 | 5.048
792.1 | 49.5 | 5.048
792.2 | 49.5 | 5.048
792.3 | 49.5 | 5.048
792.4 | 49.5 | 5.048
792.5 | 49.5 | 5.048
792.6 | 49.5 | 5.048
792.7 | 49.5 | 5.048
792.8 | 49.5 | 5.048
792.9 | 49.5 | 5.048
793 | 49.5 | 5.048
793.1 | 49.5 | 5.048
793.2 | 49.5 | 5.048
793.3 | 49.5 | 5.048
793.4 | 49.5 | 5.048
793.5 | 49.5 | 5.048
793.6 | 49.5 | 5.048
793.7 | 49.5 | 5.048
793.8 | 49.5 | 5.048
793.9 | 49.5 | 5.048
794 | 49.5 | 5.048
794.1 | 49.5 | 5.048
794.2 | 49.5 | 5.048
794.3 | 49.5 | 5.048
794.4 | 49.5 | 5.048
794.5 | 49.5 | 5.048
794.6 | 49.5 | 5.048
794.7 | 49.5 | 5.048
794.8 | 49.5 | 5.048
794.9 | 49.5 | 5.048
795 | 49.5 | 5.048
795.1 | 49.5 | 5.048
795.2 | 49.5 | 5.048
795.3 | 49.5 | 5.048
795.4 | 49.5 | 5.048
795.5 | 49.5 | 5.048
795.6 | 49.5 | 5.048
795.7 | 49.5 | 5.048
795.8 | 49.5 | 5.048
795.9 | 49.5 | 5.048
796 | 49.5 | 5.048
796.1 | 49.5 | 5.048
796.2 | 49.5 | 5.048
796.3 | 49.5 | 5.048
796.4 | 49.5 | 5.048
796.5 | 49.5 | 5.048
796.6 | 49.5 | 5.048
796.7 | 49.5 | 5.048
796.8 | 49.5 | 5.048
796.9 | 49.5 | 5.048
797 | 49.5 | 5.048
797.1 | 49.5 | 5.048
797.2 | 49.5 | 5.048
797.3 | 49.5 | 5.048
797.4 | 49.5 | 5.048
797.5 | 49.5 | 5.048
797.6 | 49.5 | 5.048
797.7 | 49.5 | 5.048
797.8 | 49.5 | 5.048
797.9 | 49.5 | 5.048
798 | 49.5 | 5.048
798.1 | 49.5 | 5.048
798.2 | 49.5 | 5.048
798.3 | 49.5 | 5.048
798.4 | 49.5 | 5.048
798.5 | 49.5 | 5.048
798.6 | 49.5 | 5.048
798.7 | 49.5 | 5.048
798.8 | 49.5 | 5.048
798.9 | 49.5 | 5.048
799 | 49.5 | 5.048
799.1 | 49.5 | 5.048
799.2 | 49.5 | 5.048
799.3 | 49.5 | 5.048
799.4 | 49.5 | 5.048
799.5 | 49.5 | 5.048
799.6 | 49.5 | 5.048
799.7 | 49.5 | 5.048
799.8 | 49.5 | 5.048
799.9 | 49.5 | 5.048
800 | 49.5 | 5.048
800.1 | 49.5 | 5.048
800.2 | 49.5 | 5.048
800.3 | 49.5 | 5.048
800.4 | 49.5 | 5.048
800.5 | 49.5 | 5.048
800.6 | 49.5 | 5.048
800.7 | 49.5 | 5.048
800.8 | 49.5 | 5.048
800.9 | 49.5 | 5.048
801 | 49.5 | 5.048
801.1 | 49.5 | 5.048
801.2 | 49.5 | 5.048
801.3 | 49.5 | 5.048
801.4 | 49.5 | 5.048
801.5 | 49.5 | 5.048
801.6 | 49.5 | 5.048
801.7 | 49.5 | 5.048
801.8 | 49.5 | 5.048
801.9 | 49.5 | 5.048
802 | 49.5 | 5.048
802.1 | 49.5 | 5.048
802.2 | 49.5 | 5.048
802.3 | 49.5 | 5.048
802.4 | 49.5 | 5.048
802.5 | 49.5 | 5.048
802.6 | 49.5 | 5.048
802.7 | 49.5 | 5.048
802.8 | 49.5 | 5.048
802.9 | 49.5 | 5.048
803 | 49.5 | 5.048
803.1 | 49.5 | 5.048
803.2 | 49.5 | 5.048
803.3 | 49.5 | 5.048
803.4 | 49.5 | 5.048
803.5 | 49.5 | 5.048
803.6 | 49.5 | 5.048
803.7 | 49.5 | 5.048
803.8 | 49.5 | 5.048
803.9 | 49.5 | 5.048
804 | 49.5 | 5.048
804.1 | 49.5 | 5.048
804.2 | 49.5 | 5.048
804.3 | 49.5 | 5.048
804.4 | 49.5 | 5.048
804.5 | 49.5 | 5.048
804.6 | 49.5 | 5.048
804.7 | 49.5 | 5.049
804.8 | 49.5 | 5.049
804.9 | 49.5 | 5.049
805 | 49.5 | 5.049
805.1 | 49.5 | 5.049
805.2 | 49.5 | 5.049
805.3 | 49.5 | 5.049
805.4 | 49.5 | 5.049
805.5 | 49.5 | 5.049
805.6 | 49.5 | 5.049
805.7 | 49.5 | 5.048
805.8 | 49.5 | 5.048
805.9 | 49.5 | 5.048
806 | 49.5 | 5.048
806.1 | 49.5 | 5.048
806.2 | 49.5 | 5.048
806.3 | 49.5 | 5.048
806.4 | 49.5 | 5.048
806.5 | 49.5 | 5.048
806.6 | 49.5 | 5.048
806.7 | 49.5 | 5.048
806.8 | 49.5 | 5.048
806.9 | 49.5 | 5.048
807 | 49.5 | 5.048
807.1 | 49.5 | 5.048
807.2 | 49.5 | 5.048
807.3 | 49.5 | 5.048
807.4 | 49.5 | 5.048
807.5 | 49.5 | 5.048
807.6 | 49.5 | 5.048
807.7 | 49.5 | 5.048
807.8 | 49.5 | 5.048
807.9 | 49.5 | 5.048
808 | 49.5 | 5.048
808.1 | 49.5 | 5.048
808.2 | 49.5 | 5.048
808.3 | 49.5 | 5.048
808.4 | 49.5 | 5.048
808.5 | 49.5 | 5.048
808.6 | 49.5 | 5.048
808.7 | 49.5 | 5.048
808.8 | 49.5 | 5.048
808.9 | 49.5 | 5.048
809 | 49.5 | 5.048
809.1 | 49.5 | 5.048
809.2 | 49.5 | 5.048
809.3 | 49.5 | 5.048
809.4 | 49.5 | 5.048
809.5 | 49.5 | 5.048
809.6 | 49.5 | 5.048
809.7 | 49.5 | 5.048
809.8 | 49.5 | 5.048
809.9 | 49.5 | 5.048
810 | 49.5 | 5.048
810.1 | 49.5 | 5.048
810.2 | 49.5 | 5.048
810.3 | 49.5 | 5.048
810.4 | 49.5 | 5.048
810.5 | 49.5 | 5.048
810.6 | 49.5 | 5.048
810.7 | 49.5 | 5.048
810.8 | 49.5 | 5.048
810.9 | 49.5 | 5.048
811 | 49.5 | 5.048
811.1 | 49.5 | 5.048
811.2 | 49.5 | 5.048
811.3 | 49.5 | 5.048
811.4 | 49.5 | 5.048
811.5 | 49.5 | 5.048
811.6 | 49.5 | 5.048
811.7 | 49.5 | 5.048
811.8 | 49.5 | 5.048
811.9 | 49.5 | 5.048
812 | 49.5 | 5.048
812.1 | 49.5 | 5.048
812.2 | 49.5 | 5.048
812.3 | 49.5 | 5.048
812.4 | 49.5 | 5.048
812.5 | 49.5 | 5.048
812.6 | 49.5 | 5.048
812.7 | 49.5 | 5.048
812.8 | 49.5 | 5.047
812.9 | 49.5 | 5.047
813 | 49.5 | 5.047
813.1 | 49.5 | 5.047
813.2 | 49.5 | 5.048
813.3 | 49.5 | 5.048
813.4 | 49.5 | 5.048
813.5 | 49.5 | 5.048
813.6 | 49.5 | 5.048
813.7 | 49.5 | 5.048
813.8 | 49.5 | 5.048
813.9 | 49.5 | 5.048
814 | 49.5 | 5.049
814.1 | 49.5 | 5.049
814.2 | 49.5 | 5.049
814.3 | 49.5 | 5.049
814.4 | 49.5 | 5.049
814.5 | 49.5 | 5.049
814.6 | 49.5 | 5.049
814.7 | 49.5 | 5.049
814.8 | 49.5 | 5.049
814.9 | 49.5 | 5.049
815 | 49.5 | 5.049
815.1 | 49.5 | 5.049
815.2 | 49.5 | 5.049
815.3 | 49.5 | 5.049
815.4 | 49.5 | 5.049
815.5 | 49.5 | 5.049
815.6 | 49.5 | 5.048
815.7 | 49.5 | 5.048
815.8 | 49.5 | 5.048
815.9 | 49.5 | 5.048
816 | 49.5 | 5.048
816.1 | 49.5 | 5.048
816.2 | 49.5 | 5.048
816.3 | 49.5 | 5.049
816.4 | 49.5 | 5.049
816.5 | 49.5 | 5.049
816.6 | 49.5 | 5.048
816.7 | 49.5 | 5.048
816.8 | 49.5 | 5.048
816.9 | 49.5 | 5.048
817 | 49.5 | 5.048
817.1 | 49.5 | 5.048
817.2 | 49.5 | 5.048
817.3 | 49.5 | 5.048
817.4 | 49.5 | 5.048
817.5 | 49.5 | 5.048
817.6 | 49.5 | 5.048
817.7 | 49.5 | 5.048
817.8 | 49.5 | 5.048
817.9 | 49.5 | 5.048
818 | 49.5 | 5.048
818.1 | 49.5 | 5.048
818.2 | 49.5 | 5.048
818.3 | 49.5 | 5.048
818.4 | 49.5 | 5.048
818.5 | 49.5 | 5.048
818.6 | 49.5 | 5.047
818.7 | 49.5 | 5.047
818.8 | 49.5 | 5.047
818.9 | 49.5 | 5.047
819 | 49.5 | 5.047
819.1 | 49.5 | 5.048
819.2 | 49.5 | 5.048
819.3 | 49.5 | 5.048
819.4 | 49.5 | 5.048
819.5 | 49.5 | 5.048
819.6 | 49.5 | 5.048
819.7 | 49.5 | 5.048
819.8 | 49.5 | 5.048
819.9 | 49.5 | 5.048
820 | 49.5 | 5.048
820.1 | 49.5 | 5.048
820.2 | 49.5 | 5.048
820.3 | 49.5 | 5.049
820.4 | 49.5 | 5.049
820.5 | 49.5 | 5.049
820.6 | 49.5 | 5.049
820.7 | 49.5 | 5.049
820.8 | 49.5 | 5.049
820.9 | 49.5 | 5.049
821 | 49.5 | 5.049
821.1 | 49.5 | 5.049
821.2 | 49.5 | 5.049
821.3 | 49.5 | 5.049
821.4 | 49.5 | 5.048
821.5 | 49.5 | 5.048
821.6 | 49.5 | 5.048
821.7 | 49.5 | 5.048
821.8 | 49.5 | 5.048
821.9 | 49.5 | 5.048
822 | 49.5 | 5.048
822.1 | 49.5 | 5.048
822.2 | 49.5 | 5.048
822.3 | 49.5 | 5.049
822.4 | 49.5 | 5.049
822.5 | 49.5 | 5.049
822.6 | 49.5 | 5.049
822.7 | 49.5 | 5.049
822.8 | 49.5 | 5.049
822.9 | 49.5 | 5.049
823 | 49.5 | 5.049
823.1 | 49.5 | 5.049
823.2 | 49.5 | 5.049
823.3 | 49.5 | 5.048
823.4 | 49.5 | 5.048
823.5 | 49.5 | 5.048
823.6 | 49.5 | 5.048
823.7 | 49.5 | 5.048
823.8 | 49.5 | 5.048
823.9 | 49.5 | 5.048
824 | 49.5 | 5.048
824.1 | 49.5 | 5.048
824.2 | 49.5 | 5.048
824.3 | 49.5 | 5.048
824.4 | 49.5 | 5.048
824.5 | 49.5 | 5.048
824.6 | 49.5 | 5.048
824.7 | 49.5 | 5.048
824.8 | 49.5 | 5.048
824.9 | 49.5 | 5.048
825 | 49.5 | 5.048
825.1 | 49.5 | 5.048
825.2 | 49.5 | 5.048
825.3 | 49.5 | 5.048
825.4 | 49.5 | 5.048
825.5 | 49.5 | 5.048
825.6 | 49.5 | 5.048
825.7 | 49.5 | 5.047
825.8 | 49.5 | 5.047
825.9 | 49.5 | 5.047
826 | 49.5 | 5.047
826.1 | 49.5 | 5.047
826.2 | 49.5 | 5.047
826.3 | 49.5 | 5.047
826.4 | 49.5 | 5.047
826.5 | 49.5 | 5.047
826.6 | 49.5 | 5.047
826.7 | 49.5 | 5.047
826.8 | 49.5 | 5.047
826.9 | 49.5 | 5.047
827 | 49.5 | 5.047
827.1 | 49.5 | 5.047
827.2 | 49.5 | 5.048
827.3 | 49.5 | 5.048
827.4 | 49.5 | 5.048
827.5 | 49.5 | 5.048
827.6 | 49.5 | 5.048
827.7 | 49.5 | 5.048
827.8 | 49.5 | 5.048
827.9 | 49.5 | 5.048
828 | 49.5 | 5.048
828.1 | 49.5 | 5.049
828.2 | 49.5 | 5.049
828.3 | 49.5 | 5.049
828.4 | 49.5 | 5.049
828.5 | 49.5 | 5.049
828.6 | 49.5 | 5.049
828.7 | 49.5 | 5.049
828.8 | 49.5 | 5.049
828.9 | 49.5 | 5.049
829 | 49.5 | 5.049
829.1 | 49.5 | 5.049
829.2 | 49.5 | 5.049
829.3 | 49.5 | 5.049
829.4 | 49.5 | 5.049
829.5 | 49.5 | 5.049
829.6 | 49.5 | 5.049
829.7 | 49.5 | 5.049
829.8 | 49.5 | 5.049
829.9 | 49.5 | 5.049
830 | 49.5 | 5.049
830.1 | 49.5 | 5.049
830.2 | 49.5 | 5.049
830.3 | 49.5 | 5.049
830.4 | 49.5 | 5.049
830.5 | 49.5 | 5.049
830.6 | 49.5 | 5.049
830.7 | 49.5 | 5.049
830.8 | 49.5 | 5.049
830.9 | 49.5 | 5.049
831 | 49.5 | 5.049
831.1 | 49.5 | 5.049
831.2 | 49.5 | 5.049
831.3 | 49.5 | 5.049
831.4 | 49.5 | 5.048
831.5 | 49.5 | 5.048
831.6 | 49.5 | 5.048
831.7 | 49.5 | 5.048
831.8 | 49.5 | 5.048
831.9 | 49.5 | 5.048
832 | 49.5 | 5.048
832.1 | 49.5 | 5.048
832.2 | 49.5 | 5.048
832.3 | 49.5 | 5.048
832.4 | 49.5 | 5.048
832.5 | 49.5 | 5.048
832.6 | 49.5 | 5.048
832.7 | 49.5 | 5.048
832.8 | 49.5 | 5.048
832.9 | 49.5 | 5.048
833 | 49.5 | 5.048
833.1 | 49.5 | 5.048
833.2 | 49.5 | 5.048
833.3 | 49.5 | 5.048
833.4 | 49.5 | 5.048
833.5 | 49.5 | 5.048
833.6 | 49.5 | 5.048
833.7 | 49.5 | 5.048
833.8 | 49.5 | 5.048
833.9 | 49.5 | 5.048
834 | 49.5 | 5.048
834.1 | 49.5 | 5.048
834.2 | 49.5 | 5.048
834.3 | 49.5 | 5.048
834.4 | 49.5 | 5.048
834.5 | 49.5 | 5.048
834.6 | 49.5 | 5.048
834.7 | 49.5 | 5.048
834.8 | 49.5 | 5.048
834.9 | 49.5 | 5.048
835 | 49.5 | 5.048
835.1 | 49.5 | 5.048
835.2 | 49.5 | 5.048
835.3 | 49.5 | 5.048
835.4 | 49.5 | 5.048
835.5 | 49.5 | 5.048
835.6 | 49.5 | 5.048
835.7 | 49.5 | 5.048
835.8 | 49.5 | 5.048
835.9 | 49.5 | 5.048
836 | 49.5 | 5.048
836.1 | 49.5 | 5.048
836.2 | 49.5 | 5.048
836.3 | 49.5 | 5.048
836.4 | 49.5 | 5.048
836.5 | 49.5 | 5.048
836.6 | 49.5 | 5.048
836.7 | 49.5 | 5.048
836.8 | 49.5 | 5.048
836.9 | 49.5 | 5.048
837 | 49.5 | 5.048
837.1 | 49.5 | 5.048
837.2 | 49.5 | 5.048
837.3 | 49.5 | 5.048
837.4 | 49.5 | 5.048
837.5 | 49.5 | 5.048
837.6 | 49.5 | 5.048
837.7 | 49.5 | 5.048
837.8 | 49.5 | 5.048
837.9 | 49.5 | 5.048
838 | 49.5 | 5.048
838.1 | 49.5 | 5.048
838.2 | 49.5 | 5.048
838.3 | 49.5 | 5.048
838.4 | 49.5 | 5.048
838.5 | 49.5 | 5.048
838.6 | 49.5 | 5.048
838.7 | 49.5 | 5.048
838.8 | 49.5 | 5.048
838.9 | 49.5 | 5.048
839 | 49.5 | 5.048
839.1 | 49.5 | 5.048
839.2 | 49.5 | 5.048
839.3 | 49.5 | 5.048
839.4 | 49.5 | 5.048
839.5 | 49.5 | 5.048
839.6 | 49.5 | 5.048
839.7 | 49.5 | 5.048
839.8 | 49.5 | 5.048
839.9 | 49.5 | 5.048
840 | 49.5 | 5.048
840.1 | 49.5 | 5.048
840.2 | 49.5 | 5.048
840.3 | 49.5 | 5.048
840.4 | 49.5 | 5.048
840.5 | 49.5 | 5.048
840.6 | 49.5 | 5.048
840.7 | 49.5 | 5.048
840.8 | 49.5 | 5.048
840.9 | 49.5 | 5.048
841 | 49.5 | 5.048
841.1 | 49.5 | 5.048
841.2 | 49.5 | 5.048
841.3 | 49.5 | 5.048
841.4 | 49.5 | 5.048
841.5 | 49.5 | 5.048
841.6 | 49.5 | 5.048
841.7 | 49.5 | 5.048
841.8 | 49.5 | 5.048
841.9 | 49.5 | 5.048
842 | 49.5 | 5.048
842.1 | 49.5 | 5.048
842.2 | 49.5 | 5.048
842.3 | 49.5 | 5.048
842.4 | 49.5 | 5.048
842.5 | 49.5 | 5.048
842.6 | 49.5 | 5.048
842.7 | 49.5 | 5.048
842.8 | 49.5 | 5.048
842.9 | 49.5 | 5.048
843 | 49.5 | 5.048
843.1 | 49.5 | 5.048
843.2 | 49.5 | 5.048
843.3 | 49.5 | 5.048
843.4 | 49.5 | 5.048
843.5 | 49.5 | 5.048
843.6 | 49.5 | 5.048
843.7 | 49.5 | 5.048
843.8 | 49.5 | 5.048
843.9 | 49.5 | 5.048
844 | 49.5 | 5.048
844.1 | 49.5 | 5.048
844.2 | 49.5 | 5.048
844.3 | 49.5 | 5.048
844.4 | 49.5 | 5.048
844.5 | 49.5 | 5.048
844.6 | 49.5 | 5.048
844.7 | 49.5 | 5.048
844.8 | 49.5 | 5.048
844.9 | 49.5 | 5.048
845 | 49.5 | 5.048
845.1 | 49.5 | 5.048
845.2 | 49.5 | 5.048
845.3 | 49.5 | 5.048
845.4 | 49.5 | 5.048
845.5 | 49.5 | 5.048
845.6 | 49.5 | 5.048
845.7 | 49.5 | 5.048
845.8 | 49.5 | 5.048
845.9 | 49.5 | 5.048
846 | 49.5 | 5.048
846.1 | 49.5 | 5.048
846.2 | 49.5 | 5.048
846.3 | 49.5 | 5.048
846.4 | 49.5 | 5.048
846.5 | 49.5 | 5.048
846.6 | 49.5 | 5.048
846.7 | 49.5 | 5.048
846.8 | 49.5 | 5.048
846.9 | 49.5 | 5.048
847 | 49.5 | 5.048
847.1 | 49.5 | 5.048
847.2 | 49.5 | 5.048
847.3 | 49.5 | 5.048
847.4 | 49.5 | 5.048
847.5 | 49.5 | 5.048
847.6 | 49.5 | 5.048
847.7 | 49.5 | 5.048
847.8 | 49.5 | 5.048
847.9 | 49.5 | 5.048
848 | 49.5 | 5.048
848.1 | 49.5 | 5.048
848.2 | 49.5 | 5.048
848.3 | 49.5 | 5.048
848.4 | 49.5 | 5.048
848.5 | 49.5 | 5.048
848.6 | 49.5 | 5.048
848.7 | 49.5 | 5.048
848.8 | 49.5 | 5.048
848.9 | 49.5 | 5.048
849 | 49.5 | 5.048
849.1 | 49.5 | 5.048
849.2 | 49.5 | 5.048
849.3 | 49.5 | 5.048
849.4 | 49.5 | 5.048
849.5 | 49.5 | 5.048
849.6 | 49.5 | 5.048
849.7 | 49.5 | 5.048
849.8 | 49.5 | 5.048
849.9 | 49.5 | 5.048
850 | 49.5 | 5.048
850.1 | 49.5 | 5.048
850.2 | 49.5 | 5.048
850.3 | 49.5 | 5.048
850.4 | 49.5 | 5.048
850.5 | 49.5 | 5.048
850.6 | 49.5 | 5.048
850.7 | 49.5 | 5.048
850.8 | 49.5 | 5.048
850.9 | 49.5 | 5.048
851 | 49.5 | 5.048
851.1 | 49.5 | 5.048
851.2 | 49.5 | 5.048
851.3 | 49.5 | 5.048
851.4 | 49.5 | 5.048
851.5 | 49.5 | 5.048
851.6 | 49.5 | 5.048
851.7 | 49.5 | 5.048
851.8 | 49.5 | 5.048
851.9 | 49.5 | 5.048
852 | 49.5 | 5.048
852.1 | 49.5 | 5.048
852.2 | 49.5 | 5.048
852.3 | 49.5 | 5.048
852.4 | 49.5 | 5.048
852.5 | 49.5 | 5.048
852.6 | 49.5 | 5.048
852.7 | 49.5 | 5.048
852.8 | 49.5 | 5.048
852.9 | 49.5 | 5.048
853 | 49.5 | 5.048
853.1 | 49.5 | 5.048
853.2 | 49.5 | 5.048
853.3 | 49.5 | 5.048
853.4 | 49.5 | 5.048
853.5 | 49.5 | 5.048
853.6 | 49.5 | 5.048
853.7 | 49.5 | 5.048
853.8 | 49.5 | 5.048
853.9 | 49.5 | 5.048
854 | 49.5 | 5.048
854.1 | 49.5 | 5.048
854.2 | 49.5 | 5.048
854.3 | 49.5 | 5.048
854.4 | 49.5 | 5.048
854.5 | 49.5 | 5.048
854.6 | 49.5 | 5.048
854.7 | 49.5 | 5.048
854.8 | 49.5 | 5.048
854.9 | 49.5 | 5.048
855 | 49.5 | 5.048
855.1 | 49.5 | 5.048
855.2 | 49.5 | 5.048
855.3 | 49.5 | 5.048
855.4 | 49.5 | 5.047
855.5 | 49.5 | 5.047
855.6 | 49.5 | 5.047
855.7 | 49.5 | 5.047
855.8 | 49.5 | 5.047
855.9 | 49.5 | 5.047
856 | 49.5 | 5.047
856.1 | 49.5 | 5.047
856.2 | 49.5 | 5.047
856.3 | 49.5 | 5.047
856.4 | 49.5 | 5.048
856.5 | 49.5 | 5.049
856.6 | 49.5 | 5.049
856.7 | 49.5 | 5.049
856.8 | 49.5 | 5.049
856.9 | 49.5 | 5.049
857 | 49.5 | 5.049
857.1 | 49.5 | 5.049
857.2 | 49.5 | 5.049
857.3 | 49.5 | 5.049
857.4 | 49.5 | 5.049
857.5 | 49.5 | 5.049
857.6 | 49.5 | 5.049
857.7 | 49.5 | 5.049
857.8 | 49.5 | 5.049
857.9 | 49.5 | 5.049
858 | 49.5 | 5.049
858.1 | 49.5 | 5.049
858.2 | 49.5 | 5.049
858.3 | 49.5 | 5.049
858.4 | 49.5 | 5.049
858.5 | 49.5 | 5.049
858.6 | 49.5 | 5.049
858.7 | 49.5 | 5.049
858.8 | 49.5 | 5.049
858.9 | 49.5 | 5.049
859 | 49.5 | 5.049
859.1 | 49.5 | 5.049
859.2 | 49.5 | 5.049
859.3 | 49.5 | 5.049
859.4 | 49.5 | 5.049
859.5 | 49.5 | 5.049
859.6 | 49.5 | 5.049
859.7 | 49.5 | 5.049
859.8 | 49.5 | 5.049
859.9 | 49.5 | 5.049
860 | 49.5 | 5.048
860.1 | 49.5 | 5.048
860.2 | 49.5 | 5.048
860.3 | 49.5 | 5.048
860.4 | 49.5 | 5.048
860.5 | 49.5 | 5.048
860.6 | 49.5 | 5.048
860.7 | 49.5 | 5.048
860.8 | 49.5 | 5.048
860.9 | 49.5 | 5.048
861 | 49.5 | 5.048
861.1 | 49.5 | 5.048
861.2 | 49.5 | 5.048
861.3 | 49.5 | 5.048
861.4 | 49.5 | 5.048
861.5 | 49.5 | 5.048
861.6 | 49.5 | 5.048
861.7 | 49.5 | 5.048
861.8 | 49.5 | 5.048
861.9 | 49.5 | 5.048
862 | 49.5 | 5.048
862.1 | 49.5 | 5.048
862.2 | 49.5 | 5.048
862.3 | 49.5 | 5.048
862.4 | 49.5 | 5.048
862.5 | 49.5 | 5.048
862.6 | 49.5 | 5.048
862.7 | 49.5 | 5.048
862.8 | 49.5 | 5.048
862.9 | 49.5 | 5.048
863 | 49.5 | 5.048
863.1 | 49.5 | 5.048
863.2 | 49.5 | 5.048
863.3 | 49.5 | 5.048
863.4 | 49.5 | 5.048
863.5 | 49.5 | 5.048
863.6 | 49.5 | 5.048
863.7 | 49.5 | 5.048
863.8 | 49.5 | 5.048
863.9 | 49.5 | 5.048
864 | 49.5 | 5.048
864.1 | 49.5 | 5.048
864.2 | 49.5 | 5.048
864.3 | 49.5 | 5.048
864.4 | 49.5 | 5.048
864.5 | 49.5 | 5.048
864.6 | 49.5 | 5.048
864.7 | 49.5 | 5.049
864.8 | 49.5 | 5.049
864.9 | 49.5 | 5.049
865 | 49.5 | 5.049
865.1 | 49.5 | 5.049
865.2 | 49.5 | 5.049
865.3 | 49.5 | 5.049
865.4 | 49.5 | 5.049
865.5 | 49.5 | 5.049
865.6 | 49.5 | 5.049
865.7 | 49.5 | 5.049
865.8 | 49.5 | 5.048
865.9 | 49.5 | 5.048
866 | 49.5 | 5.048
866.1 | 49.5 | 5.048
866.2 | 49.5 | 5.048
866.3 | 49.5 | 5.048
866.4 | 49.5 | 5.048
866.5 | 49.5 | 5.048
866.6 | 49.5 | 5.048
866.7 | 49.5 | 5.048
866.8 | 49.5 | 5.048
866.9 | 49.5 | 5.048
867 | 49.5 | 5.048
867.1 | 49.5 | 5.048
867.2 | 49.5 | 5.048
867.3 | 49.5 | 5.048
867.4 | 49.5 | 5.048
867.5 | 49.5 | 5.048
867.6 | 49.5 | 5.048
867.7 | 49.5 | 5.048
867.8 | 49.5 | 5.048
867.9 | 49.5 | 5.048
868 | 49.5 | 5.048
868.1 | 49.5 | 5.048
868.2 | 49.5 | 5.048
868.3 | 49.5 | 5.049
868.4 | 49.5 | 5.049
868.5 | 49.5 | 5.049
868.6 | 49.5 | 5.049
868.7 | 49.5 | 5.049
868.8 | 49.5 | 5.049
868.9 | 49.5 | 5.049
869 | 49.5 | 5.049
869.1 | 49.5 | 5.049
869.2 | 49.5 | 5.049
869.3 | 49.5 | 5.049
869.4 | 49.5 | 5.048
869.5 | 49.5 | 5.048
869.6 | 49.5 | 5.048
869.7 | 49.5 | 5.048
869.8 | 49.5 | 5.048
869.9 | 49.5 | 5.048
870 | 49.5 | 5.048
870.1 | 49.5 | 5.048
870.2 | 49.5 | 5.048
870.3 | 49.5 | 5.048
870.4 | 49.5 | 5.048
870.5 | 49.5 | 5.048
870.6 | 49.5 | 5.048
870.7 | 49.5 | 5.048
870.8 | 49.5 | 5.048
870.9 | 49.5 | 5.048
871 | 49.5 | 5.048
871.1 | 49.5 | 5.048
871.2 | 49.5 | 5.048
871.3 | 49.5 | 5.048
871.4 | 49.5 | 5.048
871.5 | 49.5 | 5.048
871.6 | 49.5 | 5.048
871.7 | 49.5 | 5.048
871.8 | 49.5 | 5.048
871.9 | 49.5 | 5.048
872 | 49.5 | 5.048
872.1 | 49.5 | 5.048
872.2 | 49.5 | 5.048
872.3 | 49.5 | 5.048
872.4 | 49.5 | 5.048
872.5 | 49.5 | 5.048
872.6 | 49.5 | 5.048
872.7 | 49.5 | 5.048
872.8 | 49.5 | 5.048
872.9 | 49.5 | 5.048
873 | 49.5 | 5.048
873.1 | 49.5 | 5.048
873.2 | 49.5 | 5.048
873.3 | 49.5 | 5.048
873.4 | 49.5 | 5.048
873.5 | 49.5 | 5.048
873.6 | 49.5 | 5.048
873.7 | 49.5 | 5.048
873.8 | 49.5 | 5.048
873.9 | 49.5 | 5.048
874 | 49.5 | 5.048
874.1 | 49.5 | 5.048
874.2 | 49.5 | 5.048
874.3 | 49.5 | 5.048
874.4 | 49.5 | 5.048
874.5 | 49.5 | 5.048
874.6 | 49.5 | 5.048
874.7 | 49.5 | 5.048
874.8 | 49.5 | 5.048
874.9 | 49.5 | 5.048
875 | 49.5 | 5.048
875.1 | 49.5 | 5.048
875.2 | 49.5 | 5.048
875.3 | 49.5 | 5.048
875.4 | 49.5 | 5.048
875.5 | 49.5 | 5.048
875.6 | 49.5 | 5.048
875.7 | 49.5 | 5.048
875.8 | 49.5 | 5.048
875.9 | 49.5 | 5.048
876 | 49.5 | 5.048
876.1 | 49.5 | 5.048
876.2 | 49.5 | 5.048
876.3 | 49.5 | 5.048
876.4 | 49.5 | 5.048
876.5 | 49.5 | 5.048
876.6 | 49.5 | 5.048
876.7 | 49.5 | 5.048
876.8 | 49.5 | 5.048
876.9 | 49.5 | 5.048
877 | 49.5 | 5.048
877.1 | 49.5 | 5.048
877.2 | 49.5 | 5.048
877.3 | 49.5 | 5.048
877.4 | 49.5 | 5.048
877.5 | 49.5 | 5.048
877.6 | 49.5 | 5.048
877.7 | 49.5 | 5.048
877.8 | 49.5 | 5.048
877.9 | 49.5 | 5.048
878 | 49.5 | 5.048
878.1 | 49.5 | 5.048
878.2 | 49.5 | 5.048
878.3 | 49.5 | 5.048
878.4 | 49.5 | 5.048
878.5 | 49.5 | 5.048
878.6 | 49.5 | 5.048
878.7 | 49.5 | 5.048
878.8 | 49.5 | 5.048
878.9 | 49.5 | 5.048
879 | 49.5 | 5.048
879.1 | 49.5 | 5.048
879.2 | 49.5 | 5.048
879.3 | 49.5 | 5.048
879.4 | 49.5 | 5.048
879.5 | 49.5 | 5.048
879.6 | 49.5 | 5.048
879.7 | 49.5 | 5.048
879.8 | 49.5 | 5.048
879.9 | 49.5 | 5.048
880 | 49.5 | 5.048
880.1 | 49.5 | 5.048
880.2 | 49.5 | 5.048
880.3 | 49.5 | 5.048
880.4 | 49.5 | 5.048
880.5 | 49.5 | 5.048
880.6 | 49.5 | 5.048
880.7 | 49.5 | 5.048
880.8 | 49.5 | 5.048
880.9 | 49.5 | 5.048
881 | 49.5 | 5.048
881.1 | 49.5 | 5.048
881.2 | 49.5 | 5.048
881.3 | 49.5 | 5.048
881.4 | 49.5 | 5.048
881.5 | 49.5 | 5.048
881.6 | 49.5 | 5.048
881.7 | 49.5 | 5.048
881.8 | 49.5 | 5.048
881.9 | 49.5 | 5.048
882 | 49.5 | 5.048
882.1 | 49.5 | 5.048
882.2 | 49.5 | 5.048
882.3 | 49.5 | 5.048
882.4 | 49.5 | 5.048
882.5 | 49.5 | 5.048
882.6 | 49.5 | 5.048
882.7 | 49.5 | 5.048
882.8 | 49.5 | 5.048
882.9 | 49.5 | 5.048
883 | 49.5 | 5.048
883.1 | 49.5 | 5.048
883.2 | 49.5 | 5.048
883.3 | 49.5 | 5.048
883.4 | 49.5 | 5.048
883.5 | 49.5 | 5.048
883.6 | 49.5 | 5.048
883.7 | 49.5 | 5.048
883.8 | 49.5 | 5.048
883.9 | 49.5 | 5.048
884 | 49.5 | 5.048
884.1 | 49.5 | 5.048
884.2 | 49.5 | 5.048
884.3 | 49.5 | 5.048
884.4 | 49.5 | 5.048
884.5 | 49.5 | 5.048
884.6 | 49.5 | 5.048
884.7 | 49.5 | 5.048
884.8 | 49.5 | 5.048
884.9 | 49.5 | 5.048
885 | 49.5 | 5.048
885.1 | 49.5 | 5.048
885.2 | 49.5 | 5.048
885.3 | 49.5 | 5.048
885.4 | 49.5 | 5.048
885.5 | 49.5 | 5.048
885.6 | 49.5 | 5.048
885.7 | 49.5 | 5.048
885.8 | 49.5 | 5.048
885.9 | 49.5 | 5.048
886 | 49.5 | 5.048
886.1 | 49.5 | 5.048
886.2 | 49.5 | 5.048
886.3 | 49.5 | 5.048
886.4 | 49.5 | 5.048
886.5 | 49.5 | 5.048
886.6 | 49.5 | 5.048
886.7 | 49.5 | 5.048
886.8 | 49.5 | 5.048
886.9 | 49.5 | 5.048
887 | 49.5 | 5.048
887.1 | 49.5 | 5.048
887.2 | 49.5 | 5.048
887.3 | 49.5 | 5.048
887.4 | 49.5 | 5.048
887.5 | 49.5 | 5.048
887.6 | 49.5 | 5.048
887.7 | 49.5 | 5.048
887.8 | 49.5 | 5.048
887.9 | 49.5 | 5.048
888 | 49.5 | 5.048
888.1 | 49.5 | 5.048
888.2 | 49.5 | 5.048
888.3 | 49.5 | 5.048
888.4 | 49.5 | 5.048
888.5 | 49.5 | 5.048
888.6 | 49.5 | 5.048
888.7 | 49.5 | 5.048
888.8 | 49.5 | 5.048
888.9 | 49.5 | 5.048
889 | 49.5 | 5.048
889.1 | 49.5 | 5.048
889.2 | 49.5 | 5.048
889.3 | 49.5 | 5.048
889.4 | 49.5 | 5.048
889.5 | 49.5 | 5.048
889.6 | 49.5 | 5.048
889.7 | 49.5 | 5.048
889.8 | 49.5 | 5.048
889.9 | 49.5 | 5.048
890 | 49.5 | 5.048
890.1 | 49.5 | 5.048
890.2 | 49.5 | 5.048
890.3 | 49.5 | 5.048
890.4 | 49.5 | 5.048
890.5 | 49.5 | 5.048
890.6 | 49.5 | 5.048
890.7 | 49.5 | 5.048
890.8 | 49.5 | 5.048
890.9 | 49.5 | 5.048
891 | 49.5 | 5.048
891.1 | 49.5 | 5.048
891.2 | 49.5 | 5.048
891.3 | 49.5 | 5.048
891.4 | 49.5 | 5.048
891.5 | 49.5 | 5.048
891.6 | 49.5 | 5.048
891.7 | 49.5 | 5.048
891.8 | 49.5 | 5.048
891.9 | 49.5 | 5.048
892 | 49.5 | 5.048
892.1 | 49.5 | 5.048
892.2 | 49.5 | 5.048
892.3 | 49.5 | 5.048
892.4 | 49.5 | 5.048
892.5 | 49.5 | 5.048
892.6 | 49.5 | 5.048
892.7 | 49.5 | 5.048
892.8 | 49.5 | 5.048
892.9 | 49.5 | 5.048
893 | 49.5 | 5.048
893.1 | 49.5 | 5.048
893.2 | 49.5 | 5.048
893.3 | 49.5 | 5.048
893.4 | 49.5 | 5.048
893.5 | 49.5 | 5.048
893.6 | 49.5 | 5.048
893.7 | 49.5 | 5.048
893.8 | 49.5 | 5.048
893.9 | 49.5 | 5.048
894 | 49.5 | 5.048
894.1 | 49.5 | 5.048
894.2 | 49.5 | 5.048
894.3 | 49.5 | 5.048
894.4 | 49.5 | 5.048
894.5 | 49.5 | 5.048
894.6 | 49.5 | 5.048
894.7 | 49.5 | 5.048
894.8 | 49.5 | 5.048
894.9 | 49.5 | 5.048
895 | 49.5 | 5.048
895.1 | 49.5 | 5.048
895.2 | 49.5 | 5.048
895.3 | 49.5 | 5.048
895.4 | 49.5 | 5.048
895.5 | 49.5 | 5.048
895.6 | 49.5 | 5.048
895.7 | 49.5 | 5.048
895.8 | 49.5 | 5.048
895.9 | 49.5 | 5.048
896 | 49.5 | 5.048
896.1 | 49.5 | 5.048
896.2 | 49.5 | 5.048
896.3 | 49.5 | 5.048
896.4 | 49.5 | 5.048
896.5 | 49.5 | 5.048
896.6 | 49.5 | 5.048
896.7 | 49.5 | 5.048
896.8 | 49.5 | 5.048
896.9 | 49.5 | 5.048
897 | 49.5 | 5.048
897.1 | 49.5 | 5.048
897.2 | 49.5 | 5.048
897.3 | 49.5 | 5.048
897.4 | 49.5 | 5.048
897.5 | 49.5 | 5.048
897.6 | 49.5 | 5.048
897.7 | 49.5 | 5.048
897.8 | 49.5 | 5.048
897.9 | 49.5 | 5.048
898 | 49.5 | 5.048
898.1 | 49.5 | 5.048
898.2 | 49.5 | 5.048
898.3 | 49.5 | 5.048
898.4 | 49.5 | 5.048
898.5 | 49.5 | 5.048
898.6 | 49.5 | 5.048
898.7 | 49.5 | 5.048
898.8 | 49.5 | 5.048
898.9 | 49.5 | 5.049
899 | 49.5 | 5.049
899.1 | 49.5 | 5.049
899.2 | 49.5 | 5.049
899.3 | 49.5 | 5.049
899.4 | 49.5 | 5.049
899.5 | 49.5 | 5.049
899.6 | 49.5 | 5.049
899.7 | 49.5 | 5.049
899.8 | 49.5 | 5.049
899.9 | 49.5 | 5.049
900 | 49.5 | 5.049
900.1 | 49.5 | 5.049
900.2 | 49.5 | 5.049
900.3 | 49.5 | 5.049
900.4 | 49.5 | 5.049
900.5 | 49.5 | 5.049
900.6 | 49.5 | 5.049
900.7 | 49.5 | 5.049
900.8 | 49.5 | 5.049
900.9 | 49.5 | 5.049
901 | 49.5 | 5.049
901.1 | 49.5 | 5.048
901.2 | 49.5 | 5.048
901.3 | 49.5 | 5.048
901.4 | 49.5 | 5.048
901.5 | 49.5 | 5.048
901.6 | 49.5 | 5.048
901.7 | 49.5 | 5.048
901.8 | 49.5 | 5.048
901.9 | 49.5 | 5.048
902 | 49.5 | 5.048
902.1 | 49.5 | 5.048
902.2 | 49.5 | 5.048
902.3 | 49.5 | 5.048
902.4 | 49.5 | 5.048
902.5 | 49.5 | 5.048
902.6 | 49.5 | 5.048
902.7 | 49.5 | 5.048
902.8 | 49.5 | 5.048
902.9 | 49.5 | 5.048
903 | 49.5 | 5.048
903.1 | 49.5 | 5.048
903.2 | 49.5 | 5.048
903.3 | 49.5 | 5.048
903.4 | 49.5 | 5.048
903.5 | 49.5 | 5.048
903.6 | 49.5 | 5.048
903.7 | 49.5 | 5.048
903.8 | 49.5 | 5.048
903.9 | 49.5 | 5.048
904 | 49.5 | 5.048
904.1 | 49.5 | 5.048
904.2 | 49.5 | 5.048
904.3 | 49.5 | 5.048
904.4 | 49.5 | 5.048
904.5 | 49.5 | 5.048
904.6 | 49.5 | 5.048
904.7 | 49.5 | 5.048
904.8 | 49.5 | 5.048
904.9 | 49.5 | 5.048
905 | 49.5 | 5.048
905.1 | 49.5 | 5.048
905.2 | 49.5 | 5.048
905.3 | 49.5 | 5.048
905.4 | 49.5 | 5.048
905.5 | 49.5 | 5.048
905.6 | 49.5 | 5.048
905.7 | 49.5 | 5.048
905.8 | 49.5 | 5.048
905.9 | 49.5 | 5.048
906 | 49.5 | 5.048
906.1 | 49.5 | 5.048
906.2 | 49.5 | 5.048
906.3 | 49.5 | 5.048
906.4 | 49.5 | 5.048
906.5 | 49.5 | 5.048
906.6 | 49.5 | 5.048
906.7 | 49.5 | 5.048
906.8 | 49.5 | 5.048
906.9 | 49.5 | 5.048
907 | 49.5 | 5.048
907.1 | 49.5 | 5.048
907.2 | 49.5 | 5.048
907.3 | 49.5 | 5.048
907.4 | 49.5 | 5.048
907.5 | 49.5 | 5.048
907.6 | 49.5 | 5.048
907.7 | 49.5 | 5.048
907.8 | 49.5 | 5.048
907.9 | 49.5 | 5.048
908 | 49.5 | 5.048
908.1 | 49.5 | 5.048
908.2 | 49.5 | 5.048
908.3 | 49.5 | 5.048
908.4 | 49.5 | 5.048
908.5 | 49.5 | 5.048
908.6 | 49.5 | 5.048
908.7 | 49.5 | 5.048
908.8 | 49.5 | 5.048
908.9 | 49.5 | 5.048
909 | 49.5 | 5.048
909.1 | 49.5 | 5.048
909.2 | 49.5 | 5.048
909.3 | 49.5 | 5.048
909.4 | 49.5 | 5.048
909.5 | 49.5 | 5.048
909.6 | 49.5 | 5.048
909.7 | 49.5 | 5.048
909.8 | 49.5 | 5.048
909.9 | 49.5 | 5.048
910 | 49.5 | 5.048
910.1 | 49.5 | 5.048
910.2 | 49.5 | 5.048
910.3 | 49.5 | 5.048
910.4 | 49.5 | 5.048
910.5 | 49.5 | 5.048
910.6 | 49.5 | 5.049
910.7 | 49.5 | 5.049
910.8 | 49.5 | 5.049
910.9 | 49.5 | 5.049
911 | 49.5 | 5.049
911.1 | 49.5 | 5.049
911.2 | 49.5 | 5.049
911.3 | 49.5 | 5.049
911.4 | 49.5 | 5.049
911.5 | 49.5 | 5.049
911.6 | 49.5 | 5.049
911.7 | 49.5 | 5.049
911.8 | 49.5 | 5.048
911.9 | 49.5 | 5.048
912 | 49.5 | 5.048
912.1 | 49.5 | 5.048
912.2 | 49.5 | 5.048
912.3 | 49.5 | 5.048
912.4 | 49.5 | 5.048
912.5 | 49.5 | 5.048
912.6 | 49.5 | 5.048
912.7 | 49.5 | 5.048
912.8 | 49.5 | 5.048
912.9 | 49.5 | 5.048
913 | 49.5 | 5.048
913.1 | 49.5 | 5.048
913.2 | 49.5 | 5.048
913.3 | 49.5 | 5.048
913.4 | 49.5 | 5.048
913.5 | 49.5 | 5.048
913.6 | 49.5 | 5.048
913.7 | 49.5 | 5.048
913.8 | 49.5 | 5.048
913.9 | 49.5 | 5.048
914 | 49.5 | 5.048
914.1 | 49.5 | 5.048
914.2 | 49.5 | 5.048
914.3 | 49.5 | 5.048
914.4 | 49.5 | 5.048
914.5 | 49.5 | 5.048
914.6 | 49.5 | 5.048
914.7 | 49.5 | 5.048
914.8 | 49.5 | 5.048
914.9 | 49.5 | 5.048
915 | 49.5 | 5.048
915.1 | 49.5 | 5.048
915.2 | 49.5 | 5.048
915.3 | 49.5 | 5.048
915.4 | 49.5 | 5.048
915.5 | 49.5 | 5.048
915.6 | 49.5 | 5.048
915.7 | 49.5 | 5.048
915.8 | 49.5 | 5.048
915.9 | 49.5 | 5.048
916 | 49.5 | 5.048
916.1 | 49.5 | 5.048
916.2 | 49.5 | 5.048
916.3 | 49.5 | 5.048
916.4 | 49.5 | 5.049
916.5 | 49.5 | 5.049
916.6 | 49.5 | 5.049
916.7 | 49.5 | 5.049
916.8 | 49.5 | 5.049
916.9 | 49.5 | 5.049
917 | 49.5 | 5.049
917.1 | 49.5 | 5.049
917.2 | 49.5 | 5.049
917.3 | 49.5 | 5.049
917.4 | 49.5 | 5.049
917.5 | 49.5 | 5.049
917.6 | 49.5 | 5.049
917.7 | 49.5 | 5.048
917.8 | 49.5 | 5.048
917.9 | 49.5 | 5.048
918 | 49.5 | 5.048
918.1 | 49.5 | 5.048
918.2 | 49.5 | 5.048
918.3 | 49.5 | 5.048
918.4 | 49.5 | 5.048
918.5 | 49.5 | 5.048
918.6 | 49.5 | 5.048
918.7 | 49.5 | 5.048
918.8 | 49.5 | 5.048
918.9 | 49.5 | 5.048
919 | 49.5 | 5.048
919.1 | 49.5 | 5.048
919.2 | 49.5 | 5.048
919.3 | 49.5 | 5.048
919.4 | 49.5 | 5.048
919.5 | 49.5 | 5.048
919.6 | 49.5 | 5.048
919.7 | 49.5 | 5.048
919.8 | 49.5 | 5.048
919.9 | 49.5 | 5.048
920 | 49.5 | 5.048
920.1 | 49.5 | 5.048
920.2 | 49.5 | 5.048
920.3 | 49.5 | 5.048
920.4 | 49.5 | 5.048
920.5 | 49.5 | 5.048
920.6 | 49.5 | 5.048
920.7 | 49.5 | 5.048
920.8 | 49.5 | 5.048
920.9 | 49.5 | 5.048
921 | 49.5 | 5.048
921.1 | 49.5 | 5.048
921.2 | 49.5 | 5.048
921.3 | 49.5 | 5.048
921.4 | 49.5 | 5.048
921.5 | 49.5 | 5.048
921.6 | 49.5 | 5.048
921.7 | 49.5 | 5.048
921.8 | 49.5 | 5.048
921.9 | 49.5 | 5.048
922 | 49.5 | 5.048
922.1 | 49.5 | 5.048
922.2 | 49.5 | 5.048
922.3 | 49.5 | 5.048
922.4 | 49.5 | 5.048
922.5 | 49.5 | 5.048
922.6 | 49.5 | 5.048
922.7 | 49.5 | 5.048
922.8 | 49.5 | 5.048
922.9 | 49.5 | 5.048
923 | 49.5 | 5.048
923.1 | 49.5 | 5.048
923.2 | 49.5 | 5.048
923.3 | 49.5 | 5.048
923.4 | 49.5 | 5.048
923.5 | 49.5 | 5.048
923.6 | 49.5 | 5.048
923.7 | 49.5 | 5.048
923.8 | 49.5 | 5.048
923.9 | 49.5 | 5.048
924 | 49.5 | 5.048
924.1 | 49.5 | 5.048
924.2 | 49.5 | 5.048
924.3 | 49.5 | 5.048
924.4 | 49.5 | 5.048
924.5 | 49.5 | 5.048
924.6 | 49.5 | 5.048
924.7 | 49.5 | 5.048
924.8 | 49.5 | 5.048
924.9 | 49.5 | 5.048
925 | 49.5 | 5.048
925.1 | 49.5 | 5.048
925.2 | 49.5 | 5.048
925.3 | 49.5 | 5.048
925.4 | 49.5 | 5.048
925.5 | 49.5 | 5.048
925.6 | 49.5 | 5.048
925.7 | 49.5 | 5.048
925.8 | 49.5 | 5.048
925.9 | 49.5 | 5.048
926 | 49.5 | 5.048
926.1 | 49.5 | 5.048
926.2 | 49.5 | 5.048
926.3 | 49.5 | 5.048
926.4 | 49.5 | 5.048
926.5 | 49.5 | 5.048
926.6 | 49.5 | 5.048
926.7 | 49.5 | 5.048
926.8 | 49.5 | 5.048
926.9 | 49.5 | 5.048
927 | 49.5 | 5.048
927.1 | 49.5 | 5.048
927.2 | 49.5 | 5.048
927.3 | 49.5 | 5.048
927.4 | 49.5 | 5.048
927.5 | 49.5 | 5.048
927.6 | 49.5 | 5.048
927.7 | 49.5 | 5.048
927.8 | 49.5 | 5.048
927.9 | 49.5 | 5.048
928 | 49.5 | 5.048
928.1 | 49.5 | 5.048
928.2 | 49.5 | 5.048
928.3 | 49.5 | 5.048
928.4 | 49.5 | 5.048
928.5 | 49.5 | 5.048
928.6 | 49.5 | 5.048
928.7 | 49.5 | 5.048
928.8 | 49.5 | 5.048
928.9 | 49.5 | 5.048
929 | 49.5 | 5.048
929.1 | 49.5 | 5.048
929.2 | 49.5 | 5.048
929.3 | 49.5 | 5.048
929.4 | 49.5 | 5.048
929.5 | 49.5 | 5.048
929.6 | 49.5 | 5.048
929.7 | 49.5 | 5.048
929.8 | 49.5 | 5.048
929.9 | 49.5 | 5.048
930 | 49.5 | 5.048
930.1 | 49.5 | 5.048
930.2 | 49.5 | 5.048
930.3 | 49.5 | 5.048
930.4 | 49.5 | 5.048
930.5 | 49.5 | 5.048
930.6 | 49.5 | 5.048
930.7 | 49.5 | 5.048
930.8 | 49.5 | 5.048
930.9 | 49.5 | 5.048
931 | 49.5 | 5.048
931.1 | 49.5 | 5.048
931.2 | 49.5 | 5.048
931.3 | 49.5 | 5.048
931.4 | 49.5 | 5.048
931.5 | 49.5 | 5.048
931.6 | 49.5 | 5.048
931.7 | 49.5 | 5.048
931.8 | 49.5 | 5.048
931.9 | 49.5 | 5.048
932 | 49.5 | 5.048
932.1 | 49.5 | 5.048
932.2 | 49.5 | 5.048
932.3 | 49.5 | 5.048
932.4 | 49.5 | 5.048
932.5 | 49.5 | 5.048
932.6 | 49.5 | 5.048
932.7 | 49.5 | 5.048
932.8 | 49.5 | 5.048
932.9 | 49.5 | 5.048
933 | 49.5 | 5.048
933.1 | 49.5 | 5.048
933.2 | 49.5 | 5.048
933.3 | 49.5 | 5.048
933.4 | 49.5 | 5.048
933.5 | 49.5 | 5.048
933.6 | 49.5 | 5.048
933.7 | 49.5 | 5.048
933.8 | 49.5 | 5.048
933.9 | 49.5 | 5.048
934 | 49.5 | 5.048
934.1 | 49.5 | 5.048
934.2 | 49.5 | 5.048
934.3 | 49.5 | 5.048
934.4 | 49.5 | 5.048
934.5 | 49.5 | 5.048
934.6 | 49.5 | 5.048
934.7 | 49.5 | 5.048
934.8 | 49.5 | 5.048
934.9 | 49.5 | 5.048
935 | 49.5 | 5.048
935.1 | 49.5 | 5.048
935.2 | 49.5 | 5.048
935.3 | 49.5 | 5.048
935.4 | 49.5 | 5.048
935.5 | 49.5 | 5.048
935.6 | 49.5 | 5.048
935.7 | 49.5 | 5.048
935.8 | 49.5 | 5.048
935.9 | 49.5 | 5.048
936 | 49.5 | 5.048
936.1 | 49.5 | 5.048
936.2 | 49.5 | 5.048
936.3 | 49.5 | 5.048
936.4 | 49.5 | 5.048
936.5 | 49.5 | 5.048
936.6 | 49.5 | 5.048
936.7 | 49.5 | 5.048
936.8 | 49.5 | 5.048
936.9 | 49.5 | 5.048
937 | 49.5 | 5.048
937.1 | 49.5 | 5.048
937.2 | 49.5 | 5.048
937.3 | 49.5 | 5.048
937.4 | 49.5 | 5.048
937.5 | 49.5 | 5.048
937.6 | 49.5 | 5.048
937.7 | 49.5 | 5.048
937.8 | 49.5 | 5.048
937.9 | 49.5 | 5.048
938 | 49.5 | 5.048
938.1 | 49.5 | 5.048
938.2 | 49.5 | 5.048
938.3 | 49.5 | 5.048
938.4 | 49.5 | 5.048
938.5 | 49.5 | 5.048
938.6 | 49.5 | 5.048
938.7 | 49.5 | 5.048
938.8 | 49.5 | 5.048
938.9 | 49.5 | 5.048
939 | 49.5 | 5.048
939.1 | 49.5 | 5.048
939.2 | 49.5 | 5.048
939.3 | 49.5 | 5.048
939.4 | 49.5 | 5.048
939.5 | 49.5 | 5.048
939.6 | 49.5 | 5.048
939.7 | 49.5 | 5.048
939.8 | 49.5 | 5.048
939.9 | 49.5 | 5.048
940 | 49.5 | 5.048
940.1 | 49.5 | 5.048
940.2 | 49.5 | 5.048
940.3 | 49.5 | 5.048
940.4 | 49.5 | 5.048
940.5 | 49.5 | 5.048
940.6 | 49.5 | 5.048
940.7 | 49.5 | 5.048
940.8 | 49.5 | 5.048
940.9 | 49.5 | 5.048
941 | 49.5 | 5.048
941.1 | 49.5 | 5.048
941.2 | 49.5 | 5.048
941.3 | 49.5 | 5.048
941.4 | 49.5 | 5.048
941.5 | 49.5 | 5.048
941.6 | 49.5 | 5.048
941.7 | 49.5 | 5.048
941.8 | 49.5 | 5.048
941.9 | 49.5 | 5.048
942 | 49.5 | 5.048
942.1 | 49.5 | 5.048
942.2 | 49.5 | 5.048
942.3 | 49.5 | 5.048
942.4 | 49.5 | 5.048
942.5 | 49.5 | 5.048
942.6 | 49.5 | 5.048
942.7 | 49.5 | 5.048
942.8 | 49.5 | 5.048
942.9 | 49.5 | 5.048
943 | 49.5 | 5.048
943.1 | 49.5 | 5.048
943.2 | 49.5 | 5.048
943.3 | 49.5 | 5.048
943.4 | 49.5 | 5.048
943.5 | 49.5 | 5.048
943.6 | 49.5 | 5.048
943.7 | 49.5 | 5.048
943.8 | 49.5 | 5.048
943.9 | 49.5 | 5.048
944 | 49.5 | 5.048
944.1 | 49.5 | 5.048
944.2 | 49.5 | 5.048
944.3 | 49.5 | 5.048
944.4 | 49.5 | 5.048
944.5 | 49.5 | 5.048
944.6 | 49.5 | 5.048
944.7 | 49.5 | 5.048
944.8 | 49.5 | 5.048
944.9 | 49.5 | 5.048
945 | 49.5 | 5.048
945.1 | 49.5 | 5.048
945.2 | 49.5 | 5.048
945.3 | 49.5 | 5.048
945.4 | 49.5 | 5.048
945.5 | 49.5 | 5.048
945.6 | 49.5 | 5.048
945.7 | 49.5 | 5.048
945.8 | 49.5 | 5.048
945.9 | 49.5 | 5.048
946 | 49.5 | 5.048
946.1 | 49.5 | 5.048
946.2 | 49.5 | 5.048
946.3 | 49.5 | 5.048
946.4 | 49.5 | 5.048
946.5 | 49.5 | 5.048
946.6 | 49.5 | 5.048
946.7 | 49.5 | 5.048
946.8 | 49.5 | 5.048
946.9 | 49.5 | 5.048
947 | 49.5 | 5.048
947.1 | 49.5 | 5.048
947.2 | 49.5 | 5.048
947.3 | 49.5 | 5.048
947.4 | 49.5 | 5.048
947.5 | 49.5 | 5.048
947.6 | 49.5 | 5.048
947.7 | 49.5 | 5.048
947.8 | 49.5 | 5.048
947.9 | 49.5 | 5.048
948 | 49.5 | 5.048
948.1 | 49.5 | 5.048
948.2 | 49.5 | 5.048
948.3 | 49.5 | 5.048
948.4 | 49.5 | 5.048
948.5 | 49.5 | 5.048
948.6 | 49.5 | 5.048
948.7 | 49.5 | 5.048
948.8 | 49.5 | 5.048
948.9 | 49.5 | 5.048
949 | 49.5 | 5.048
949.1 | 49.5 | 5.048
949.2 | 49.5 | 5.048
949.3 | 49.5 | 5.048
949.4 | 49.5 | 5.048
949.5 | 49.5 | 5.048
949.6 | 49.5 | 5.048
949.7 | 49.5 | 5.048
949.8 | 49.5 | 5.048
949.9 | 49.5 | 5.048
950 | 49.5 | 5.048
950.1 | 49.5 | 5.048
950.2 | 49.5 | 5.048
950.3 | 49.5 | 5.048
950.4 | 49.5 | 5.048
950.5 | 49.5 | 5.048
950.6 | 49.5 | 5.048
950.7 | 49.5 | 5.048
950.8 | 49.5 | 5.048
950.9 | 49.5 | 5.048
951 | 49.5 | 5.048
951.1 | 49.5 | 5.048
951.2 | 49.5 | 5.048
951.3 | 49.5 | 5.048
951.4 | 49.5 | 5.048
951.5 | 49.5 | 5.048
951.6 | 49.5 | 5.048
951.7 | 49.5 | 5.048
951.8 | 49.5 | 5.048
951.9 | 49.5 | 5.048
952 | 49.5 | 5.048
952.1 | 49.5 | 5.048
952.2 | 49.5 | 5.048
952.3 | 49.5 | 5.048
952.4 | 49.5 | 5.048
952.5 | 49.5 | 5.048
952.6 | 49.5 | 5.048
952.7 | 49.5 | 5.048
952.8 | 49.5 | 5.048
952.9 | 49.5 | 5.048
953 | 49.5 | 5.048
953.1 | 49.5 | 5.048
953.2 | 49.5 | 5.048
953.3 | 49.5 | 5.048
953.4 | 49.5 | 5.048
953.5 | 49.5 | 5.048
953.6 | 49.5 | 5.048
953.7 | 49.5 | 5.048
953.8 | 49.5 | 5.048
953.9 | 49.5 | 5.048
954 | 49.5 | 5.048
954.1 | 49.5 | 5.048
954.2 | 49.5 | 5.048
954.3 | 49.5 | 5.048
954.4 | 49.5 | 5.048
954.5 | 49.5 | 5.048
954.6 | 49.5 | 5.048
954.7 | 49.5 | 5.048
954.8 | 49.5 | 5.048
954.9 | 49.5 | 5.048
955 | 49.5 | 5.048
955.1 | 49.5 | 5.048
955.2 | 49.5 | 5.048
955.3 | 49.5 | 5.048
955.4 | 49.5 | 5.048
955.5 | 49.5 | 5.048
955.6 | 49.5 | 5.048
955.7 | 49.5 | 5.048
955.8 | 49.5 | 5.048
955.9 | 49.5 | 5.048
956 | 49.5 | 5.048
956.1 | 49.5 | 5.048
956.2 | 49.5 | 5.048
956.3 | 49.5 | 5.048
956.4 | 49.5 | 5.048
956.5 | 49.5 | 5.048
956.6 | 49.5 | 5.048
956.7 | 49.5 | 5.048
956.8 | 49.5 | 5.048
956.9 | 49.5 | 5.048
957 | 49.5 | 5.048
957.1 | 49.5 | 5.048
957.2 | 49.5 | 5.048
957.3 | 49.5 | 5.048
957.4 | 49.5 | 5.048
957.5 | 49.5 | 5.048
957.6 | 49.5 | 5.048
957.7 | 49.5 | 5.048
957.8 | 49.5 | 5.048
957.9 | 49.5 | 5.048
958 | 49.5 | 5.048
958.1 | 49.5 | 5.048
958.2 | 49.5 | 5.048
958.3 | 49.5 | 5.048
958.4 | 49.5 | 5.048
958.5 | 49.5 | 5.048
958.6 | 49.5 | 5.048
958.7 | 49.5 | 5.048
958.8 | 49.5 | 5.048
958.9 | 49.5 | 5.048
959 | 49.5 | 5.048
959.1 | 49.5 | 5.048
959.2 | 49.5 | 5.048
959.3 | 49.5 | 5.048
959.4 | 49.5 | 5.048
959.5 | 49.5 | 5.048
959.6 | 49.5 | 5.048
959.7 | 49.5 | 5.048
959.8 | 49.5 | 5.048
959.9 | 49.5 | 5.048
960 | 49.5 | 5.048
960.1 | 49.5 | 5.048
960.2 | 49.5 | 5.048
960.3 | 49.5 | 5.048
960.4 | 49.5 | 5.048
960.5 | 49.5 | 5.048
960.6 | 49.5 | 5.048
960.7 | 49.5 | 5.048
960.8 | 49.5 | 5.048
960.9 | 49.5 | 5.048
961 | 49.5 | 5.048
961.1 | 49.5 | 5.048
961.2 | 49.5 | 5.048
961.3 | 49.5 | 5.048
961.4 | 49.5 | 5.048
961.5 | 49.5 | 5.048
961.6 | 49.5 | 5.048
961.7 | 49.5 | 5.048
961.8 | 49.5 | 5.048
961.9 | 49.5 | 5.048
962 | 49.5 | 5.048
962.1 | 49.5 | 5.048
962.2 | 49.5 | 5.048
962.3 | 49.5 | 5.048
962.4 | 49.5 | 5.048
962.5 | 49.5 | 5.048
962.6 | 49.5 | 5.048
962.7 | 49.5 | 5.048
962.8 | 49.5 | 5.048
962.9 | 49.5 | 5.048
963 | 49.5 | 5.048
963.1 | 49.5 | 5.048
963.2 | 49.5 | 5.048
963.3 | 49.5 | 5.048
963.4 | 49.5 | 5.048
963.5 | 49.5 | 5.048
963.6 | 49.5 | 5.048
963.7 | 49.5 | 5.048
963.8 | 49.5 | 5.048
963.9 | 49.5 | 5.048
964 | 49.5 | 5.048
964.1 | 49.5 | 5.048
964.2 | 49.5 | 5.048
964.3 | 49.5 | 5.048
964.4 | 49.5 | 5.048
964.5 | 49.5 | 5.048
964.6 | 49.5 | 5.048
964.7 | 49.5 | 5.048
964.8 | 49.5 | 5.048
964.9 | 49.5 | 5.048
965 | 49.5 | 5.048
965.1 | 49.5 | 5.048
965.2 | 49.5 | 5.048
965.3 | 49.5 | 5.048
965.4 | 49.5 | 5.048
965.5 | 49.5 | 5.048
965.6 | 49.5 | 5.048
965.7 | 49.5 | 5.048
965.8 | 49.5 | 5.048
965.9 | 49.5 | 5.048
966 | 49.5 | 5.048
966.1 | 49.5 | 5.048
966.2 | 49.5 | 5.048
966.3 | 49.5 | 5.048
966.4 | 49.5 | 5.048
966.5 | 49.5 | 5.048
966.6 | 49.5 | 5.048
966.7 | 49.5 | 5.049
966.8 | 49.5 | 5.049
966.9 | 49.5 | 5.049
967 | 49.5 | 5.049
967.1 | 49.5 | 5.049
967.2 | 49.5 | 5.048
967.3 | 49.5 | 5.048
967.4 | 49.5 | 5.048
967.5 | 49.5 | 5.048
967.6 | 49.5 | 5.048
967.7 | 49.5 | 5.048
967.8 | 49.5 | 5.048
967.9 | 49.5 | 5.048
968 | 49.5 | 5.048
968.1 | 49.5 | 5.048
968.2 | 49.5 | 5.048
968.3 | 49.5 | 5.048
968.4 | 49.5 | 5.048
968.5 | 49.5 | 5.048
968.6 | 49.5 | 5.048
968.7 | 49.5 | 5.048
968.8 | 49.5 | 5.048
968.9 | 49.5 | 5.048
969 | 49.5 | 5.048
969.1 | 49.5 | 5.048
969.2 | 49.5 | 5.048
969.3 | 49.5 | 5.048
969.4 | 49.5 | 5.048
969.5 | 49.5 | 5.048
969.6 | 49.5 | 5.048
969.7 | 49.5 | 5.048
969.8 | 49.5 | 5.048
969.9 | 49.5 | 5.048
970 | 49.5 | 5.048
970.1 | 49.5 | 5.048
970.2 | 49.5 | 5.048
970.3 | 49.5 | 5.048
970.4 | 49.5 | 5.048
970.5 | 49.5 | 5.048
970.6 | 49.5 | 5.048
970.7 | 49.5 | 5.048
970.8 | 49.5 | 5.048
970.9 | 49.5 | 5.048
971 | 49.5 | 5.048
971.1 | 49.5 | 5.048
971.2 | 49.5 | 5.048
971.3 | 49.5 | 5.048
971.4 | 49.5 | 5.048
971.5 | 49.5 | 5.048
971.6 | 49.5 | 5.048
971.7 | 49.5 | 5.048
971.8 | 49.5 | 5.048
971.9 | 49.5 | 5.049
972 | 49.5 | 5.049
972.1 | 49.5 | 5.049
972.2 | 49.5 | 5.049
972.3 | 49.5 | 5.049
972.4 | 49.5 | 5.049
972.5 | 49.5 | 5.049
972.6 | 49.5 | 5.049
972.7 | 49.5 | 5.048
972.8 | 49.5 | 5.048
972.9 | 49.5 | 5.048
973 | 49.5 | 5.048
973.1 | 49.5 | 5.049
973.2 | 49.5 | 5.049
973.3 | 49.5 | 5.049
973.4 | 49.5 | 5.049
973.5 | 49.5 | 5.049
973.6 | 49.5 | 5.049
973.7 | 49.5 | 5.049
973.8 | 49.5 | 5.049
973.9 | 49.5 | 5.049
974 | 49.5 | 5.049
974.1 | 49.5 | 5.049
974.2 | 49.5 | 5.049
974.3 | 49.5 | 5.049
974.4 | 49.5 | 5.049
974.5 | 49.5 | 5.049
974.6 | 49.5 | 5.049
974.7 | 49.5 | 5.049
974.8 | 49.5 | 5.049
974.9 | 49.5 | 5.049
975 | 49.5 | 5.049
975.1 | 49.5 | 5.049
975.2 | 49.5 | 5.049
975.3 | 49.5 | 5.049
975.4 | 49.5 | 5.048
975.5 | 49.5 | 5.048
975.6 | 49.5 | 5.048
975.7 | 49.5 | 5.048
975.8 | 49.5 | 5.048
975.9 | 49.5 | 5.048
976 | 49.5 | 5.048
976.1 | 49.5 | 5.048
976.2 | 49.5 | 5.048
976.3 | 49.5 | 5.048
976.4 | 49.5 | 5.048
976.5 | 49.5 | 5.048
976.6 | 49.5 | 5.048
976.7 | 49.5 | 5.048
976.8 | 49.5 | 5.048
976.9 | 49.5 | 5.048
977 | 49.5 | 5.048
977.1 | 49.5 | 5.048
977.2 | 49.5 | 5.048
977.3 | 49.5 | 5.048
977.4 | 49.5 | 5.048
977.5 | 49.5 | 5.048
977.6 | 49.5 | 5.048
977.7 | 49.5 | 5.048
977.8 | 49.5 | 5.048
977.9 | 49.5 | 5.049
978 | 49.5 | 5.049
978.1 | 49.5 | 5.049
978.2 | 49.5 | 5.049
978.3 | 49.5 | 5.049
978.4 | 49.5 | 5.049
978.5 | 49.5 | 5.049
978.6 | 49.5 | 5.049
978.7 | 49.5 | 5.049
978.8 | 49.5 | 5.049
978.9 | 49.5 | 5.049
979 | 49.5 | 5.049
979.1 | 49.5 | 5.049
979.2 | 49.5 | 5.049
979.3 | 49.5 | 5.049
979.4 | 49.5 | 5.049
979.5 | 49.5 | 5.049
979.6 | 49.5 | 5.049
979.7 | 49.5 | 5.049
979.8 | 49.5 | 5.049
979.9 | 49.5 | 5.049
980 | 49.5 | 5.049
980.1 | 49.5 | 5.049
980.2 | 49.5 | 5.049
980.3 | 49.5 | 5.049
980.4 | 49.5 | 5.049
980.5 | 49.5 | 5.049
980.6 | 49.5 | 5.049
980.7 | 49.5 | 5.049
980.8 | 49.5 | 5.049
980.9 | 49.5 | 5.049
981 | 49.5 | 5.049
981.1 | 49.5 | 5.049
981.2 | 49.5 | 5.049
981.3 | 49.5 | 5.048
981.4 | 49.5 | 5.048
981.5 | 49.5 | 5.048
981.6 | 49.5 | 5.048
981.7 | 49.5 | 5.048
981.8 | 49.5 | 5.048
981.9 | 49.5 | 5.048
982 | 49.5 | 5.048
982.1 | 49.5 | 5.048
982.2 | 49.5 | 5.048
982.3 | 49.5 | 5.048
982.4 | 49.5 | 5.048
982.5 | 49.5 | 5.048
982.6 | 49.5 | 5.048
982.7 | 49.5 | 5.048
982.8 | 49.5 | 5.048
982.9 | 49.5 | 5.048
983 | 49.5 | 5.048
983.1 | 49.5 | 5.048
983.2 | 49.5 | 5.048
983.3 | 49.5 | 5.048
983.4 | 49.5 | 5.048
983.5 | 49.5 | 5.048
983.6 | 49.5 | 5.048
983.7 | 49.5 | 5.048
983.8 | 49.5 | 5.048
983.9 | 49.5 | 5.048
984 | 49.5 | 5.048
984.1 | 49.5 | 5.048
984.2 | 49.5 | 5.048
984.3 | 49.5 | 5.048
984.4 | 49.5 | 5.048
984.5 | 49.5 | 5.048
984.6 | 49.5 | 5.048
984.7 | 49.5 | 5.048
984.8 | 49.5 | 5.048
984.9 | 49.5 | 5.049
985 | 49.5 | 5.049
985.1 | 49.5 | 5.049
985.2 | 49.5 | 5.049
985.3 | 49.5 | 5.049
985.4 | 49.5 | 5.049
985.5 | 49.5 | 5.049
985.6 | 49.5 | 5.049
985.7 | 49.5 | 5.049
985.8 | 49.5 | 5.049
985.9 | 49.5 | 5.049
986 | 49.5 | 5.049
986.1 | 49.5 | 5.049
986.2 | 49.5 | 5.049
986.3 | 49.5 | 5.049
986.4 | 49.5 | 5.049
986.5 | 49.5 | 5.049
986.6 | 49.5 | 5.049
986.7 | 49.5 | 5.048
986.8 | 49.5 | 5.048
986.9 | 49.5 | 5.048
987 | 49.5 | 5.048
987.1 | 49.5 | 5.048
987.2 | 49.5 | 5.048
987.3 | 49.5 | 5.048
987.4 | 49.5 | 5.048
987.5 | 49.5 | 5.048
987.6 | 49.5 | 5.048
987.7 | 49.5 | 5.048
987.8 | 49.5 | 5.048
987.9 | 49.5 | 5.048
988 | 49.5 | 5.048
988.1 | 49.5 | 5.048
988.2 | 49.5 | 5.048
988.3 | 49.5 | 5.048
988.4 | 49.5 | 5.048
988.5 | 49.5 | 5.048
988.6 | 49.5 | 5.048
988.7 | 49.5 | 5.048
988.8 | 49.5 | 5.048
988.9 | 49.5 | 5.048
989 | 49.5 | 5.048
989.1 | 49.5 | 5.048
989.2 | 49.5 | 5.048
989.3 | 49.5 | 5.048
989.4 | 49.5 | 5.048
989.5 | 49.5 | 5.048
989.6 | 49.5 | 5.048
989.7 | 49.5 | 5.048
989.8 | 49.5 | 5.048
989.9 | 49.5 | 5.048
990 | 49.5 | 5.048
990.1 | 49.5 | 5.048
990.2 | 49.5 | 5.048
990.3 | 49.5 | 5.048
990.4 | 49.5 | 5.048
990.5 | 49.5 | 5.048
990.6 | 49.5 | 5.048
990.7 | 49.5 | 5.048
990.8 | 49.5 | 5.048
990.9 | 49.5 | 5.048
991 | 49.5 | 5.048
991.1 | 49.5 | 5.048
991.2 | 49.5 | 5.048
991.3 | 49.5 | 5.048
991.4 | 49.5 | 5.048
991.5 | 49.5 | 5.048
991.6 | 49.5 | 5.048
991.7 | 49.5 | 5.048
991.8 | 49.5 | 5.048
991.9 | 49.5 | 5.048
992 | 49.5 | 5.048
992.1 | 49.5 | 5.048
992.2 | 49.5 | 5.048
992.3 | 49.5 | 5.048
992.4 | 49.5 | 5.048
992.5 | 49.5 | 5.048
992.6 | 49.5 | 5.048
992.7 | 49.5 | 5.048
992.8 | 49.5 | 5.048
992.9 | 49.5 | 5.048
993 | 49.5 | 5.048
993.1 | 49.5 | 5.048
993.2 | 49.5 | 5.048
993.3 | 49.5 | 5.048
993.4 | 49.5 | 5.048
993.5 | 49.5 | 5.048
993.6 | 49.5 | 5.048
993.7 | 49.5 | 5.048
993.8 | 49.5 | 5.048
993.9 | 49.5 | 5.048
994 | 49.5 | 5.048
994.1 | 49.5 | 5.048
994.2 | 49.5 | 5.048
994.3 | 49.5 | 5.048
994.4 | 49.5 | 5.048
994.5 | 49.5 | 5.048
994.6 | 49.5 | 5.048
994.7 | 49.5 | 5.048
994.8 | 49.5 | 5.048
994.9 | 49.5 | 5.048
995 | 49.5 | 5.048
995.1 | 49.5 | 5.048
995.2 | 49.5 | 5.048
995.3 | 49.5 | 5.048
995.4 | 49.5 | 5.048
995.5 | 49.5 | 5.048
995.6 | 49.5 | 5.048
995.7 | 49.5 | 5.048
995.8 | 49.5 | 5.048
995.9 | 49.5 | 5.048
996 | 49.5 | 5.048
996.1 | 49.5 | 5.048
996.2 | 49.5 | 5.048
996.3 | 49.5 | 5.048
996.4 | 49.5 | 5.048
996.5 | 49.5 | 5.048
996.6 | 49.5 | 5.048
996.7 | 49.5 | 5.048
996.8 | 49.5 | 5.048
996.9 | 49.5 | 5.048
997 | 49.5 | 5.048
997.1 | 49.5 | 5.048
997.2 | 49.5 | 5.048
997.3 | 49.5 | 5.048
997.4 | 49.5 | 5.048
997.5 | 49.5 | 5.048
997.6 | 49.5 | 5.048
997.7 | 49.5 | 5.048
997.8 | 49.5 | 5.048
997.9 | 49.5 | 5.048
998 | 49.5 | 5.048
998.1 | 49.5 | 5.048
998.2 | 49.5 | 5.048
998.3 | 49.5 | 5.048
998.4 | 49.5 | 5.048
998.5 | 49.5 | 5.048
998.6 | 49.5 | 5.048
998.7 | 49.5 | 5.048
998.8 | 49.5 | 5.048
998.9 | 49.5 | 5.048
999 | 49.5 | 5.048
999.1 | 49.5 | 5.048
999.2 | 49.5 | 5.048
999.3 | 49.5 | 5.048
999.4 | 49.5 | 5.048
999.5 | 49.5 | 5.048
999.6 | 49.5 | 5.048
999.7 | 49.5 | 5.048
999.8 | 49.5 | 5.048
999.9 | 49.5 | 5.048
1000 | 49.5 | 5.048
1000.1 | 49.5 | 5.048
1000.2 | 49.5 | 5.048
1000.3 | 49.5 | 5.048
1000.4 | 49.5 | 5.048
1000.5 | 49.5 | 5.048
1000.6 | 49.5 | 5.048
1000.7 | 49.5 | 5.048
1000.8 | 49.5 | 5.048
1000.9 | 49.5 | 5.048
1001 | 49.5 | 5.048
1001.1 | 49.5 | 5.048
1001.2 | 49.5 | 5.048
1001.3 | 49.5 | 5.048
1001.4 | 49.5 | 5.048
1001.5 | 49.5 | 5.048
1001.6 | 49.5 | 5.048
1001.7 | 49.5 | 5.048
1001.8 | 49.5 | 5.048
1001.9 | 49.5 | 5.048
1002 | 49.5 | 5.048
1002.1 | 49.5 | 5.048
1002.2 | 49.5 | 5.048
1002.3 | 49.5 | 5.048
1002.4 | 49.5 | 5.048
1002.5 | 49.5 | 5.048
1002.6 | 49.5 | 5.048
1002.7 | 49.5 | 5.048
1002.8 | 49.5 | 5.048
1002.9 | 49.5 | 5.048
1003 | 49.5 | 5.048
1003.1 | 49.5 | 5.048
1003.2 | 49.5 | 5.048
1003.3 | 49.5 | 5.048
1003.4 | 49.5 | 5.048
1003.5 | 49.5 | 5.048
1003.6 | 49.5 | 5.048
1003.7 | 49.5 | 5.048
1003.8 | 49.5 | 5.048
1003.9 | 49.5 | 5.048
1004 | 49.5 | 5.048
1004.1 | 49.5 | 5.048
1004.2 | 49.5 | 5.048
1004.3 | 49.5 | 5.048
1004.4 | 49.5 | 5.048
1004.5 | 49.5 | 5.048
1004.6 | 49.5 | 5.048
1004.7 | 49.5 | 5.048
1004.8 | 49.5 | 5.048
1004.9 | 49.5 | 5.048
1005 | 49.5 | 5.048
1005.1 | 49.5 | 5.048
1005.2 | 49.5 | 5.048
1005.3 | 49.5 | 5.048
1005.4 | 49.5 | 5.048
1005.5 | 49.5 | 5.048
1005.6 | 49.5 | 5.048
1005.7 | 49.5 | 5.048
1005.8 | 49.5 | 5.048
1005.9 | 49.5 | 5.048
1006 | 49.5 | 5.048
1006.1 | 49.5 | 5.048
1006.2 | 49.5 | 5.048
1006.3 | 49.5 | 5.048
1006.4 | 49.5 | 5.048
1006.5 | 49.5 | 5.048
1006.6 | 49.5 | 5.048
1006.7 | 49.5 | 5.048
1006.8 | 49.5 | 5.048
1006.9 | 49.5 | 5.048
1007 | 49.5 | 5.048
1007.1 | 49.5 | 5.048
1007.2 | 49.5 | 5.048
1007.3 | 49.5 | 5.048
1007.4 | 49.5 | 5.048
1007.5 | 49.5 | 5.048
1007.6 | 49.5 | 5.048
1007.7 | 49.5 | 5.048
1007.8 | 49.5 | 5.048
1007.9 | 49.5 | 5.048
1008 | 49.5 | 5.048
1008.1 | 49.5 | 5.048
1008.2 | 49.5 | 5.048
1008.3 | 49.5 | 5.048
1008.4 | 49.5 | 5.048
1008.5 | 49.5 | 5.048
1008.6 | 49.5 | 5.048
1008.7 | 49.5 | 5.048
1008.8 | 49.5 | 5.048
1008.9 | 49.5 | 5.048
1009 | 49.5 | 5.048
1009.1 | 49.5 | 5.048
1009.2 | 49.5 | 5.048
1009.3 | 49.5 | 5.048
1009.4 | 49.5 | 5.048
1009.5 | 49.5 | 5.048
1009.6 | 49.5 | 5.048
1009.7 | 49.5 | 5.048
1009.8 | 49.5 | 5.048
1009.9 | 49.5 | 5.048
1010 | 49.5 | 5.048
1010.1 | 49.5 | 5.048
1010.2 | 49.5 | 5.048
1010.3 | 49.5 | 5.048
1010.4 | 49.5 | 5.048
1010.5 | 49.5 | 5.048
1010.6 | 49.5 | 5.048
1010.7 | 49.5 | 5.048
1010.8 | 49.5 | 5.048
1010.9 | 49.5 | 5.048
1011 | 49.5 | 5.048
1011.1 | 49.5 | 5.048
1011.2 | 49.5 | 5.048
1011.3 | 49.5 | 5.048
1011.4 | 49.5 | 5.048
1011.5 | 49.5 | 5.049
1011.6 | 49.5 | 5.049
1011.7 | 49.5 | 5.049
1011.8 | 49.5 | 5.049
1011.9 | 49.5 | 5.049
1012 | 49.5 | 5.049
1012.1 | 49.5 | 5.049
1012.2 | 49.5 | 5.049
1012.3 | 49.5 | 5.049
1012.4 | 49.5 | 5.049
1012.5 | 49.5 | 5.048
1012.6 | 49.5 | 5.048
1012.7 | 49.5 | 5.048
1012.8 | 49.5 | 5.048
1012.9 | 49.5 | 5.048
1013 | 49.5 | 5.048
1013.1 | 49.5 | 5.048
1013.2 | 49.5 | 5.048
1013.3 | 49.5 | 5.048
1013.4 | 49.5 | 5.048
1013.5 | 49.5 | 5.048
1013.6 | 49.5 | 5.048
1013.7 | 49.5 | 5.048
1013.8 | 49.5 | 5.048
1013.9 | 49.5 | 5.048
1014 | 49.5 | 5.048
1014.1 | 49.5 | 5.048
1014.2 | 49.5 | 5.048
1014.3 | 49.5 | 5.048
1014.4 | 49.5 | 5.048
1014.5 | 49.5 | 5.048
1014.6 | 49.5 | 5.048
1014.7 | 49.5 | 5.048
1014.8 | 49.5 | 5.048
1014.9 | 49.5 | 5.048
1015 | 49.5 | 5.048
1015.1 | 49.5 | 5.048
1015.2 | 49.5 | 5.048
1015.3 | 49.5 | 5.048
1015.4 | 49.5 | 5.048
1015.5 | 49.5 | 5.048
1015.6 | 49.5 | 5.048
1015.7 | 49.5 | 5.048
1015.8 | 49.5 | 5.048
1015.9 | 49.5 | 5.049
1016 | 49.5 | 5.049
1016.1 | 49.5 | 5.049
1016.2 | 49.5 | 5.049
1016.3 | 49.5 | 5.049
1016.4 | 49.5 | 5.049
1016.5 | 49.5 | 5.049
1016.6 | 49.5 | 5.049
1016.7 | 49.5 | 5.049
1016.8 | 49.5 | 5.049
1016.9 | 49.5 | 5.049
1017 | 49.5 | 5.049
1017.1 | 49.5 | 5.049
1017.2 | 49.5 | 5.049
1017.3 | 49.5 | 5.049
1017.4 | 49.5 | 5.049
1017.5 | 49.5 | 5.049
1017.6 | 49.5 | 5.049
1017.7 | 49.5 | 5.049
1017.8 | 49.5 | 5.049
1017.9 | 49.5 | 5.049
1018 | 49.5 | 5.049
1018.1 | 49.5 | 5.049
1018.2 | 49.5 | 5.048
1018.3 | 49.5 | 5.048
1018.4 | 49.5 | 5.048
1018.5 | 49.5 | 5.048
1018.6 | 49.5 | 5.048
1018.7 | 49.5 | 5.048
1018.8 | 49.5 | 5.048
1018.9 | 49.5 | 5.048
1019 | 49.5 | 5.048
1019.1 | 49.5 | 5.048
1019.2 | 49.5 | 5.048
1019.3 | 49.5 | 5.048
1019.4 | 49.5 | 5.048
1019.5 | 49.5 | 5.048
1019.6 | 49.5 | 5.048
1019.7 | 49.5 | 5.048
1019.8 | 49.5 | 5.048
1019.9 | 49.5 | 5.048
1020 | 49.5 | 5.048
1020.1 | 49.5 | 5.048
1020.2 | 49.5 | 5.048
1020.3 | 49.5 | 5.048
1020.4 | 49.5 | 5.048
1020.5 | 49.5 | 5.048
1020.6 | 49.5 | 5.048
1020.7 | 49.5 | 5.048
1020.8 | 49.5 | 5.048
1020.9 | 49.5 | 5.048
1021 | 49.5 | 5.048
1021.1 | 49.5 | 5.048
1021.2 | 49.5 | 5.048
1021.3 | 49.5 | 5.048
1021.4 | 49.5 | 5.048
1021.5 | 49.5 | 5.048
1021.6 | 49.5 | 5.048
1021.7 | 49.5 | 5.048
1021.8 | 49.5 | 5.049
1021.9 | 49.5 | 5.049
1022 | 49.5 | 5.049
1022.1 | 49.5 | 5.049
1022.2 | 49.5 | 5.049
1022.3 | 49.5 | 5.049
1022.4 | 49.5 | 5.049
1022.5 | 49.5 | 5.049
1022.6 | 49.5 | 5.049
1022.7 | 49.5 | 5.049
1022.8 | 49.5 | 5.049
1022.9 | 49.5 | 5.049
1023 | 49.5 | 5.049
1023.1 | 49.5 | 5.049
1023.2 | 49.5 | 5.049
1023.3 | 49.5 | 5.049
1023.4 | 49.5 | 5.049
1023.5 | 49.5 | 5.049
1023.6 | 49.5 | 5.049
1023.7 | 49.5 | 5.049
1023.8 | 49.5 | 5.049
1023.9 | 49.5 | 5.049
1024 | 49.5 | 5.048
1024.1 | 49.5 | 5.048
1024.2 | 49.5 | 5.048
1024.3 | 49.5 | 5.048
1024.4 | 49.5 | 5.048
1024.5 | 49.5 | 5.048
1024.6 | 49.5 | 5.048
1024.7 | 49.5 | 5.048
1024.8 | 49.5 | 5.048
1024.9 | 49.5 | 5.048
1025 | 49.5 | 5.048
1025.1 | 49.5 | 5.048
1025.2 | 49.5 | 5.048
1025.3 | 49.5 | 5.048
1025.4 | 49.5 | 5.048
1025.5 | 49.5 | 5.048
1025.6 | 49.5 | 5.048
1025.7 | 49.5 | 5.048
1025.8 | 49.5 | 5.048
1025.9 | 49.5 | 5.048
1026 | 49.5 | 5.048
1026.1 | 49.5 | 5.048
1026.2 | 49.5 | 5.048
1026.3 | 49.5 | 5.048
1026.4 | 49.5 | 5.048
1026.5 | 49.5 | 5.048
1026.6 | 49.5 | 5.047
1026.7 | 49.5 | 5.047
1026.8 | 49.5 | 5.047
1026.9 | 49.5 | 5.047
1027 | 49.5 | 5.047
1027.1 | 49.5 | 5.047
1027.2 | 49.5 | 5.047
1027.3 | 49.5 | 5.047
1027.4 | 49.5 | 5.047
1027.5 | 49.5 | 5.047
1027.6 | 49.5 | 5.048
1027.7 | 49.5 | 5.048
1027.8 | 49.5 | 5.048
1027.9 | 49.5 | 5.048
1028 | 49.5 | 5.048
1028.1 | 49.5 | 5.048
1028.2 | 49.5 | 5.048
1028.3 | 49.5 | 5.048
1028.4 | 49.5 | 5.048
1028.5 | 49.5 | 5.048
1028.6 | 49.5 | 5.048
1028.7 | 49.5 | 5.048
1028.8 | 49.5 | 5.048
1028.9 | 49.5 | 5.048
1029 | 49.5 | 5.049
1029.1 | 49.5 | 5.049
1029.2 | 49.5 | 5.049
1029.3 | 49.5 | 5.049
1029.4 | 49.5 | 5.049
1029.5 | 49.5 | 5.049
1029.6 | 49.5 | 5.049
1029.7 | 49.5 | 5.049
1029.8 | 49.5 | 5.048
1029.9 | 49.5 | 5.048
1030 | 49.5 | 5.048
1030.1 | 49.5 | 5.048
1030.2 | 49.5 | 5.049
1030.3 | 49.5 | 5.049
1030.4 | 49.5 | 5.049
1030.5 | 49.5 | 5.049
1030.6 | 49.5 | 5.049
1030.7 | 49.5 | 5.049
1030.8 | 49.5 | 5.049
1030.9 | 49.5 | 5.049
1031 | 49.5 | 5.048
1031.1 | 49.5 | 5.048
1031.2 | 49.5 | 5.048
1031.3 | 49.5 | 5.048
1031.4 | 49.5 | 5.048
1031.5 | 49.5 | 5.048
1031.6 | 49.5 | 5.048
1031.7 | 49.5 | 5.048
1031.8 | 49.5 | 5.048
1031.9 | 49.5 | 5.048
1032 | 49.5 | 5.048
1032.1 | 49.5 | 5.048
1032.2 | 49.5 | 5.048
1032.3 | 49.5 | 5.048
1032.4 | 49.5 | 5.048
1032.5 | 49.5 | 5.048
1032.6 | 49.5 | 5.048
1032.7 | 49.5 | 5.048
1032.8 | 49.5 | 5.048
1032.9 | 49.5 | 5.048
1033 | 49.5 | 5.048
1033.1 | 49.5 | 5.048
1033.2 | 49.5 | 5.048
1033.3 | 49.5 | 5.048
1033.4 | 49.5 | 5.048
1033.5 | 49.5 | 5.048
1033.6 | 49.5 | 5.048
1033.7 | 49.5 | 5.048
1033.8 | 49.5 | 5.048
1033.9 | 49.5 | 5.048
1034 | 49.5 | 5.048
1034.1 | 49.5 | 5.048
1034.2 | 49.5 | 5.048
1034.3 | 49.5 | 5.048
1034.4 | 49.5 | 5.048
1034.5 | 49.5 | 5.048
1034.6 | 49.5 | 5.049
1034.7 | 49.5 | 5.049
1034.8 | 49.5 | 5.049
1034.9 | 49.5 | 5.049
1035 | 49.5 | 5.048
1035.1 | 49.5 | 5.048
1035.2 | 49.5 | 5.048
1035.3 | 49.5 | 5.048
1035.4 | 49.5 | 5.048
1035.5 | 49.5 | 5.048
1035.6 | 49.5 | 5.048
1035.7 | 49.5 | 5.048
1035.8 | 49.5 | 5.048
1035.9 | 49.5 | 5.048
1036 | 49.5 | 5.048
1036.1 | 49.5 | 5.048
1036.2 | 49.5 | 5.048
1036.3 | 49.5 | 5.048
1036.4 | 49.5 | 5.048
1036.5 | 49.5 | 5.048
1036.6 | 49.5 | 5.048
1036.7 | 49.5 | 5.048
1036.8 | 49.5 | 5.048
1036.9 | 49.5 | 5.048
1037 | 49.5 | 5.048
1037.1 | 49.5 | 5.049
1037.2 | 49.5 | 5.049
1037.3 | 49.5 | 5.049
1037.4 | 49.5 | 5.049
1037.5 | 49.5 | 5.049
1037.6 | 49.5 | 5.049
1037.7 | 49.5 | 5.049
1037.8 | 49.5 | 5.049
1037.9 | 49.5 | 5.049
1038 | 49.5 | 5.048
1038.1 | 49.5 | 5.048
1038.2 | 49.5 | 5.048
1038.3 | 49.5 | 5.048
1038.4 | 49.5 | 5.048
1038.5 | 49.5 | 5.048
1038.6 | 49.5 | 5.048
1038.7 | 49.5 | 5.048
1038.8 | 49.5 | 5.048
1038.9 | 49.5 | 5.048
1039 | 49.5 | 5.048
1039.1 | 49.5 | 5.048
1039.2 | 49.5 | 5.048
1039.3 | 49.5 | 5.048
1039.4 | 49.5 | 5.048
1039.5 | 49.5 | 5.048
1039.6 | 49.5 | 5.048
1039.7 | 49.5 | 5.048
1039.8 | 49.5 | 5.048
1039.9 | 49.5 | 5.048
1040 | 49.5 | 5.048
1040.1 | 49.5 | 5.048
1040.2 | 49.5 | 5.048
1040.3 | 49.5 | 5.048
1040.4 | 49.5 | 5.048
1040.5 | 49.5 | 5.048
1040.6 | 49.5 | 5.048
1040.7 | 49.5 | 5.048
1040.8 | 49.5 | 5.048
1040.9 | 49.5 | 5.048
1041 | 49.5 | 5.048
1041.1 | 49.5 | 5.048
1041.2 | 49.5 | 5.048
1041.3 | 49.5 | 5.048
1041.4 | 49.5 | 5.048
1041.5 | 49.5 | 5.048
1041.6 | 49.5 | 5.048
1041.7 | 49.5 | 5.049
1041.8 | 49.5 | 5.049
1041.9 | 49.5 | 5.049
1042 | 49.5 | 5.049
1042.1 | 49.5 | 5.049
1042.2 | 49.5 | 5.049
1042.3 | 49.5 | 5.049
1042.4 | 49.5 | 5.049
1042.5 | 49.5 | 5.049
1042.6 | 49.5 | 5.049
1042.7 | 49.5 | 5.049
1042.8 | 49.5 | 5.048
1042.9 | 49.5 | 5.048
1043 | 49.5 | 5.048
1043.1 | 49.5 | 5.048
1043.2 | 49.5 | 5.048
1043.3 | 49.5 | 5.048
1043.4 | 49.5 | 5.048
1043.5 | 49.5 | 5.048
1043.6 | 49.5 | 5.048
1043.7 | 49.5 | 5.048
1043.8 | 49.5 | 5.048
1043.9 | 49.5 | 5.048
1044 | 49.5 | 5.048
1044.1 | 49.5 | 5.047
1044.2 | 49.5 | 5.047
1044.3 | 49.5 | 5.047
1044.4 | 49.5 | 5.047
1044.5 | 49.5 | 5.047
1044.6 | 49.5 | 5.047
1044.7 | 49.5 | 5.047
1044.8 | 49.5 | 5.047
1044.9 | 49.5 | 5.047
1045 | 49.5 | 5.047
1045.1 | 49.5 | 5.047
1045.2 | 49.5 | 5.047
1045.3 | 49.5 | 5.048
1045.4 | 49.5 | 5.048
1045.5 | 49.5 | 5.048
1045.6 | 49.5 | 5.048
1045.7 | 49.5 | 5.048
1045.8 | 49.5 | 5.048
1045.9 | 49.5 | 5.048
1046 | 49.5 | 5.048
1046.1 | 49.5 | 5.048
1046.2 | 49.5 | 5.048
1046.3 | 49.5 | 5.048
1046.4 | 49.5 | 5.048
1046.5 | 49.5 | 5.049
1046.6 | 49.5 | 5.049
1046.7 | 49.5 | 5.049
1046.8 | 49.5 | 5.049
1046.9 | 49.5 | 5.049
1047 | 49.5 | 5.049
1047.1 | 49.5 | 5.049
1047.2 | 49.5 | 5.049
1047.3 | 49.5 | 5.049
1047.4 | 49.5 | 5.049
1047.5 | 49.5 | 5.049
1047.6 | 49.5 | 5.049
1047.7 | 49.5 | 5.049
1047.8 | 49.5 | 5.049
1047.9 | 49.5 | 5.049
1048 | 49.5 | 5.049
1048.1 | 49.5 | 5.049
1048.2 | 49.5 | 5.049
1048.3 | 49.5 | 5.049
1048.4 | 49.5 | 5.049
1048.5 | 49.5 | 5.049
1048.6 | 49.5 | 5.049
1048.7 | 49.5 | 5.049
1048.8 | 49.5 | 5.048
1048.9 | 49.5 | 5.048
1049 | 49.5 | 5.048
1049.1 | 49.5 | 5.048
1049.2 | 49.5 | 5.048
1049.3 | 49.5 | 5.048
1049.4 | 49.5 | 5.048
1049.5 | 49.5 | 5.048
1049.6 | 49.5 | 5.048
1049.7 | 49.5 | 5.048
1049.8 | 49.5 | 5.048
1049.9 | 49.5 | 5.048
1050 | 49.5 | 5.048
1050.1 | 49.5 | 5.048
1050.2 | 49.5 | 5.048
1050.3 | 49.5 | 5.048
1050.4 | 49.5 | 5.048
1050.5 | 49.5 | 5.048
1050.6 | 49.5 | 5.048
1050.7 | 49.5 | 5.048
1050.8 | 49.5 | 5.048
1050.9 | 49.5 | 5.047
1051 | 49.5 | 5.047
1051.1 | 49.5 | 5.047
1051.2 | 49.5 | 5.047
1051.3 | 49.5 | 5.047
1051.4 | 49.5 | 5.047
1051.5 | 49.5 | 5.047
1051.6 | 49.5 | 5.047
1051.7 | 49.5 | 5.047
1051.8 | 49.5 | 5.047
1051.9 | 49.5 | 5.047
1052 | 49.5 | 5.047
1052.1 | 49.5 | 5.047
1052.2 | 49.5 | 5.047
1052.3 | 49.5 | 5.048
1052.4 | 49.5 | 5.048
1052.5 | 49.5 | 5.048
1052.6 | 49.5 | 5.048
1052.7 | 49.5 | 5.048
1052.8 | 49.5 | 5.049
1052.9 | 49.5 | 5.049
1053 | 49.5 | 5.049
1053.1 | 49.5 | 5.049
1053.2 | 49.5 | 5.049
1053.3 | 49.5 | 5.049
1053.4 | 49.5 | 5.049
1053.5 | 49.5 | 5.049
1053.6 | 49.5 | 5.049
1053.7 | 49.5 | 5.049
1053.8 | 49.5 | 5.049
1053.9 | 49.5 | 5.049
1054 | 49.5 | 5.049
1054.1 | 49.5 | 5.049
1054.2 | 49.5 | 5.049
1054.3 | 49.5 | 5.049
1054.4 | 49.5 | 5.049
1054.5 | 49.5 | 5.05
1054.6 | 49.5 | 5.05
1054.7 | 49.5 | 5.05
1054.8 | 49.5 | 5.05
1054.9 | 49.5 | 5.05
1055 | 49.5 | 5.05
1055.1 | 49.5 | 5.05
1055.2 | 49.5 | 5.049
1055.3 | 49.5 | 5.049
1055.4 | 49.5 | 5.049
1055.5 | 49.5 | 5.049
1055.6 | 49.5 | 5.049
1055.7 | 49.5 | 5.049
1055.8 | 49.5 | 5.049
1055.9 | 49.5 | 5.049
1056 | 49.5 | 5.049
1056.1 | 49.5 | 5.049
1056.2 | 49.5 | 5.048
1056.3 | 49.5 | 5.048
1056.4 | 49.5 | 5.048
1056.5 | 49.5 | 5.048
1056.6 | 49.5 | 5.048
1056.7 | 49.5 | 5.048
1056.8 | 49.5 | 5.048
1056.9 | 49.5 | 5.047
1057 | 49.5 | 5.047
1057.1 | 49.5 | 5.047
1057.2 | 49.5 | 5.047
1057.3 | 49.5 | 5.047
1057.4 | 49.5 | 5.047
1057.5 | 49.5 | 5.047
1057.6 | 49.5 | 5.047
1057.7 | 49.5 | 5.047
1057.8 | 49.5 | 5.047
1057.9 | 49.5 | 5.047
1058 | 49.5 | 5.047
1058.1 | 49.5 | 5.047
1058.2 | 49.5 | 5.047
1058.3 | 49.5 | 5.047
1058.4 | 49.5 | 5.047
1058.5 | 49.5 | 5.047
1058.6 | 49.5 | 5.047
1058.7 | 49.5 | 5.047
1058.8 | 49.5 | 5.047
1058.9 | 49.5 | 5.047
1059 | 49.5 | 5.047
1059.1 | 49.5 | 5.047
1059.2 | 49.5 | 5.048
1059.3 | 49.5 | 5.048
1059.4 | 49.5 | 5.048
1059.5 | 49.5 | 5.048
1059.6 | 49.5 | 5.048
1059.7 | 49.5 | 5.048
1059.8 | 49.5 | 5.048
1059.9 | 49.5 | 5.048
1060 | 49.5 | 5.048
1060.1 | 49.5 | 5.048
1060.2 | 49.5 | 5.048
1060.3 | 49.5 | 5.048
1060.4 | 49.5 | 5.049
1060.5 | 49.5 | 5.049
1060.6 | 49.5 | 5.049
1060.7 | 49.5 | 5.049
1060.8 | 49.5 | 5.049
1060.9 | 49.5 | 5.049
1061 | 49.5 | 5.049
1061.1 | 49.5 | 5.049
1061.2 | 49.5 | 5.049
1061.3 | 49.5 | 5.049
1061.4 | 49.5 | 5.049
1061.5 | 49.5 | 5.049
1061.6 | 49.5 | 5.049
1061.7 | 49.5 | 5.049
1061.8 | 49.5 | 5.049
1061.9 | 49.5 | 5.049
1062 | 49.5 | 5.049
1062.1 | 49.5 | 5.049
1062.2 | 49.5 | 5.049
1062.3 | 49.5 | 5.049
1062.4 | 49.5 | 5.049
1062.5 | 49.5 | 5.049
1062.6 | 49.5 | 5.049
1062.7 | 49.5 | 5.049
1062.8 | 49.5 | 5.049
1062.9 | 49.5 | 5.048
1063 | 49.5 | 5.048
1063.1 | 49.5 | 5.048
1063.2 | 49.5 | 5.048
1063.3 | 49.5 | 5.048
1063.4 | 49.5 | 5.048
1063.5 | 49.5 | 5.048
1063.6 | 49.5 | 5.048
1063.7 | 49.5 | 5.048
1063.8 | 49.5 | 5.048
1063.9 | 49.5 | 5.048
1064 | 49.5 | 5.048
1064.1 | 49.5 | 5.047
1064.2 | 49.5 | 5.047
1064.3 | 49.5 | 5.047
1064.4 | 49.5 | 5.047
1064.5 | 49.5 | 5.047
1064.6 | 49.5 | 5.047
1064.7 | 49.5 | 5.047
1064.8 | 49.5 | 5.047
1064.9 | 49.5 | 5.047
1065 | 49.5 | 5.048
1065.1 | 49.5 | 5.048
1065.2 | 49.5 | 5.048
1065.3 | 49.5 | 5.048
1065.4 | 49.5 | 5.048
1065.5 | 49.5 | 5.048
1065.6 | 49.5 | 5.048
1065.7 | 49.5 | 5.048
1065.8 | 49.5 | 5.048
1065.9 | 49.5 | 5.048
1066 | 49.5 | 5.048
1066.1 | 49.5 | 5.048
1066.2 | 49.5 | 5.049
1066.3 | 49.5 | 5.049
1066.4 | 49.5 | 5.049
1066.5 | 49.5 | 5.049
1066.6 | 49.5 | 5.049
1066.7 | 49.5 | 5.049
1066.8 | 49.5 | 5.049
1066.9 | 49.5 | 5.049
1067 | 49.5 | 5.049
1067.1 | 49.5 | 5.049
1067.2 | 49.5 | 5.049
1067.3 | 49.5 | 5.049
1067.4 | 49.5 | 5.049
1067.5 | 49.5 | 5.049
1067.6 | 49.5 | 5.049
1067.7 | 49.5 | 5.049
1067.8 | 49.5 | 5.049
1067.9 | 49.5 | 5.049
1068 | 49.5 | 5.049
1068.1 | 49.5 | 5.049
1068.2 | 49.5 | 5.049
1068.3 | 49.5 | 5.049
1068.4 | 49.5 | 5.049
1068.5 | 49.5 | 5.049
1068.6 | 49.5 | 5.049
1068.7 | 49.5 | 5.049
1068.8 | 49.5 | 5.049
1068.9 | 49.5 | 5.049
1069 | 49.5 | 5.048
1069.1 | 49.5 | 5.048
1069.2 | 49.5 | 5.048
1069.3 | 49.5 | 5.048
1069.4 | 49.5 | 5.048
1069.5 | 49.5 | 5.048
1069.6 | 49.5 | 5.048
1069.7 | 49.5 | 5.048
1069.8 | 49.5 | 5.048
1069.9 | 49.5 | 5.048
1070 | 49.5 | 5.048
1070.1 | 49.5 | 5.048
1070.2 | 49.5 | 5.048
1070.3 | 49.5 | 5.048
1070.4 | 49.5 | 5.048
1070.5 | 49.5 | 5.048
1070.6 | 49.5 | 5.048
1070.7 | 49.5 | 5.048
1070.8 | 49.5 | 5.048
1070.9 | 49.5 | 5.048
1071 | 49.5 | 5.048
1071.1 | 49.5 | 5.048
1071.2 | 49.5 | 5.048
1071.3 | 49.5 | 5.048
1071.4 | 49.5 | 5.048
1071.5 | 49.5 | 5.048
1071.6 | 49.5 | 5.048
1071.7 | 49.5 | 5.048
1071.8 | 49.5 | 5.048
1071.9 | 49.5 | 5.048
1072 | 49.5 | 5.048
1072.1 | 49.5 | 5.048
1072.2 | 49.5 | 5.048
1072.3 | 49.5 | 5.048
1072.4 | 49.5 | 5.048
1072.5 | 49.5 | 5.048
1072.6 | 49.5 | 5.048
1072.7 | 49.5 | 5.048
1072.8 | 49.5 | 5.048
1072.9 | 49.5 | 5.048
1073 | 49.5 | 5.048
1073.1 | 49.5 | 5.048
1073.2 | 49.5 | 5.048
1073.3 | 49.5 | 5.048
1073.4 | 49.5 | 5.048
1073.5 | 49.5 | 5.048
1073.6 | 49.5 | 5.048
1073.7 | 49.5 | 5.048
1073.8 | 49.5 | 5.048
1073.9 | 49.5 | 5.048
1074 | 49.5 | 5.048
1074.1 | 49.5 | 5.048
1074.2 | 49.5 | 5.048
1074.3 | 49.5 | 5.048
1074.4 | 49.5 | 5.048
1074.5 | 49.5 | 5.048
1074.6 | 49.5 | 5.048
1074.7 | 49.5 | 5.048
1074.8 | 49.5 | 5.048
1074.9 | 49.5 | 5.048
1075 | 49.5 | 5.048
1075.1 | 49.5 | 5.048
1075.2 | 49.5 | 5.048
1075.3 | 49.5 | 5.048
1075.4 | 49.5 | 5.048
1075.5 | 49.5 | 5.048
1075.6 | 49.5 | 5.048
1075.7 | 49.5 | 5.048
1075.8 | 49.5 | 5.048
1075.9 | 49.5 | 5.048
1076 | 49.5 | 5.048
1076.1 | 49.5 | 5.048
1076.2 | 49.5 | 5.048
1076.3 | 49.5 | 5.048
1076.4 | 49.5 | 5.048
1076.5 | 49.5 | 5.048
1076.6 | 49.5 | 5.048
1076.7 | 49.5 | 5.048
1076.8 | 49.5 | 5.048
1076.9 | 49.5 | 5.048
1077 | 49.5 | 5.048
1077.1 | 49.5 | 5.048
1077.2 | 49.5 | 5.048
1077.3 | 49.5 | 5.049
1077.4 | 49.5 | 5.049
1077.5 | 49.5 | 5.049
1077.6 | 49.5 | 5.049
1077.7 | 49.5 | 5.049
1077.8 | 49.5 | 5.049
1077.9 | 49.5 | 5.049
1078 | 49.5 | 5.049
1078.1 | 49.5 | 5.049
1078.2 | 49.5 | 5.049
1078.3 | 49.5 | 5.049
1078.4 | 49.5 | 5.049
1078.5 | 49.5 | 5.048
1078.6 | 49.5 | 5.048
1078.7 | 49.5 | 5.048
1078.8 | 49.5 | 5.048
1078.9 | 49.5 | 5.048
1079 | 49.5 | 5.048
1079.1 | 49.5 | 5.048
1079.2 | 49.5 | 5.048
1079.3 | 49.5 | 5.048
1079.4 | 49.5 | 5.048
1079.5 | 49.5 | 5.048
1079.6 | 49.5 | 5.048
1079.7 | 49.5 | 5.048
1079.8 | 49.5 | 5.048
1079.9 | 49.5 | 5.048
1080 | 49.5 | 5.048
1080.1 | 49.5 | 5.047
1080.2 | 49.5 | 5.047
1080.3 | 49.5 | 5.047
1080.4 | 49.5 | 5.047
1080.5 | 49.5 | 5.047
1080.6 | 49.5 | 5.047
1080.7 | 49.5 | 5.047
1080.8 | 49.5 | 5.047
1080.9 | 49.5 | 5.048
1081 | 49.5 | 5.048
1081.1 | 49.5 | 5.048
1081.2 | 49.5 | 5.048
1081.3 | 49.5 | 5.048
1081.4 | 49.5 | 5.048
1081.5 | 49.5 | 5.048
1081.6 | 49.5 | 5.048
1081.7 | 49.5 | 5.048
1081.8 | 49.5 | 5.048
1081.9 | 49.5 | 5.048
1082 | 49.5 | 5.048
1082.1 | 49.5 | 5.048
1082.2 | 49.5 | 5.048
1082.3 | 49.5 | 5.048
1082.4 | 49.5 | 5.048
1082.5 | 49.5 | 5.048
1082.6 | 49.5 | 5.048
1082.7 | 49.5 | 5.048
1082.8 | 49.5 | 5.048
1082.9 | 49.5 | 5.048
1083 | 49.5 | 5.048
1083.1 | 49.5 | 5.048
1083.2 | 49.5 | 5.048
1083.3 | 49.5 | 5.048
1083.4 | 49.5 | 5.048
1083.5 | 49.5 | 5.048
1083.6 | 49.5 | 5.048
1083.7 | 49.5 | 5.048
1083.8 | 49.5 | 5.048
1083.9 | 49.5 | 5.048
1084 | 49.5 | 5.048
1084.1 | 49.5 | 5.048
1084.2 | 49.5 | 5.048
1084.3 | 49.5 | 5.048
1084.4 | 49.5 | 5.048
1084.5 | 49.5 | 5.048
1084.6 | 49.5 | 5.048
1084.7 | 49.5 | 5.048
1084.8 | 49.5 | 5.048
1084.9 | 49.5 | 5.048
1085 | 49.5 | 5.048
1085.1 | 49.5 | 5.048
1085.2 | 49.5 | 5.048
1085.3 | 49.5 | 5.048
1085.4 | 49.5 | 5.048
1085.5 | 49.5 | 5.048
1085.6 | 49.5 | 5.048
1085.7 | 49.5 | 5.048
1085.8 | 49.5 | 5.048
1085.9 | 49.5 | 5.048
1086 | 49.5 | 5.048
1086.1 | 49.5 | 5.048
1086.2 | 49.5 | 5.048
1086.3 | 49.5 | 5.048
1086.4 | 49.5 | 5.048
1086.5 | 49.5 | 5.048
1086.6 | 49.5 | 5.048
1086.7 | 49.5 | 5.048
1086.8 | 49.5 | 5.048
1086.9 | 49.5 | 5.048
1087 | 49.5 | 5.048
1087.1 | 49.5 | 5.048
1087.2 | 49.5 | 5.048
1087.3 | 49.5 | 5.048
1087.4 | 49.5 | 5.048
1087.5 | 49.5 | 5.048
1087.6 | 49.5 | 5.048
1087.7 | 49.5 | 5.048
1087.8 | 49.5 | 5.048
1087.9 | 49.5 | 5.048
1088 | 49.5 | 5.048
1088.1 | 49.5 | 5.048
1088.2 | 49.5 | 5.048
1088.3 | 49.5 | 5.048
1088.4 | 49.5 | 5.048
1088.5 | 49.5 | 5.048
1088.6 | 49.5 | 5.048
1088.7 | 49.5 | 5.048
1088.8 | 49.5 | 5.048
1088.9 | 49.5 | 5.048
1089 | 49.5 | 5.048
1089.1 | 49.5 | 5.048
1089.2 | 49.5 | 5.048
1089.3 | 49.5 | 5.048
1089.4 | 49.5 | 5.048
1089.5 | 49.5 | 5.048
1089.6 | 49.5 | 5.049
1089.7 | 49.5 | 5.049
1089.8 | 49.5 | 5.049
1089.9 | 49.5 | 5.049
1090 | 49.5 | 5.049
1090.1 | 49.5 | 5.049
1090.2 | 49.5 | 5.049
1090.3 | 49.5 | 5.049
1090.4 | 49.5 | 5.049
1090.5 | 49.5 | 5.049
1090.6 | 49.5 | 5.049
1090.7 | 49.5 | 5.049
1090.8 | 49.5 | 5.048
1090.9 | 49.5 | 5.048
1091 | 49.5 | 5.048
1091.1 | 49.5 | 5.048
1091.2 | 49.5 | 5.048
1091.3 | 49.5 | 5.048
1091.4 | 49.5 | 5.048
1091.5 | 49.5 | 5.048
1091.6 | 49.5 | 5.048
1091.7 | 49.5 | 5.048
1091.8 | 49.5 | 5.048
1091.9 | 49.5 | 5.048
1092 | 49.5 | 5.048
1092.1 | 49.5 | 5.048
1092.2 | 49.5 | 5.048
1092.3 | 49.5 | 5.048
1092.4 | 49.5 | 5.048
1092.5 | 49.5 | 5.048
1092.6 | 49.5 | 5.048
1092.7 | 49.5 | 5.049
1092.8 | 49.5 | 5.049
1092.9 | 49.5 | 5.049
1093 | 49.5 | 5.049
1093.1 | 49.5 | 5.049
1093.2 | 49.5 | 5.049
1093.3 | 49.5 | 5.049
1093.4 | 49.5 | 5.049
1093.5 | 49.5 | 5.049
1093.6 | 49.5 | 5.049
1093.7 | 49.5 | 5.048
1093.8 | 49.5 | 5.048
1093.9 | 49.5 | 5.048
1094 | 49.5 | 5.048
1094.1 | 49.5 | 5.048
1094.2 | 49.5 | 5.048
1094.3 | 49.5 | 5.048
1094.4 | 49.5 | 5.048
1094.5 | 49.5 | 5.048
1094.6 | 49.5 | 5.048
1094.7 | 49.5 | 5.048
1094.8 | 49.5 | 5.048
1094.9 | 49.5 | 5.048
1095 | 49.5 | 5.048
1095.1 | 49.5 | 5.048
1095.2 | 49.5 | 5.048
1095.3 | 49.5 | 5.048
1095.4 | 49.5 | 5.048
1095.5 | 49.5 | 5.048
1095.6 | 49.5 | 5.048
1095.7 | 49.5 | 5.048
1095.8 | 49.5 | 5.048
1095.9 | 49.5 | 5.048
1096 | 49.5 | 5.048
1096.1 | 49.5 | 5.048
1096.2 | 49.5 | 5.048
1096.3 | 49.5 | 5.048
1096.4 | 49.5 | 5.048
1096.5 | 49.5 | 5.048
1096.6 | 49.5 | 5.048
1096.7 | 49.5 | 5.048
1096.8 | 49.5 | 5.048
1096.9 | 49.5 | 5.048
1097 | 49.5 | 5.048
1097.1 | 49.5 | 5.048
1097.2 | 49.5 | 5.048
1097.3 | 49.5 | 5.048
1097.4 | 49.5 | 5.048
1097.5 | 49.5 | 5.048
1097.6 | 49.5 | 5.048
1097.7 | 49.5 | 5.048
1097.8 | 49.5 | 5.048
1097.9 | 49.5 | 5.048
1098 | 49.5 | 5.048
1098.1 | 49.5 | 5.048
1098.2 | 49.5 | 5.048
1098.3 | 49.5 | 5.048
1098.4 | 49.5 | 5.048
1098.5 | 49.5 | 5.048
1098.6 | 49.5 | 5.048
1098.7 | 49.5 | 5.048
1098.8 | 49.5 | 5.048
1098.9 | 49.5 | 5.048
1099 | 49.5 | 5.048
1099.1 | 49.5 | 5.048
1099.2 | 49.5 | 5.048
1099.3 | 49.5 | 5.048
1099.4 | 49.5 | 5.048
1099.5 | 49.5 | 5.048
1099.6 | 49.5 | 5.048
1099.7 | 49.5 | 5.048
1099.8 | 49.5 | 5.048
1099.9 | 49.5 | 5.048
1100 | 49.5 | 5.048
1100.1 | 49.5 | 5.048
1100.2 | 49.5 | 5.048
1100.3 | 49.5 | 5.048
1100.4 | 49.5 | 5.048
1100.5 | 49.5 | 5.048
1100.6 | 49.5 | 5.048
1100.7 | 49.5 | 5.048
1100.8 | 49.5 | 5.048
1100.9 | 49.5 | 5.048
1101 | 49.5 | 5.048
1101.1 | 49.5 | 5.048
1101.2 | 49.5 | 5.048
1101.3 | 49.5 | 5.048
1101.4 | 49.5 | 5.048
1101.5 | 49.5 | 5.048
1101.6 | 49.5 | 5.048
1101.7 | 49.5 | 5.048
1101.8 | 49.5 | 5.048
1101.9 | 49.5 | 5.048
1102 | 49.5 | 5.048
1102.1 | 49.5 | 5.048
1102.2 | 49.5 | 5.048
1102.3 | 49.5 | 5.048
1102.4 | 49.5 | 5.048
1102.5 | 49.5 | 5.048
1102.6 | 49.5 | 5.048
1102.7 | 49.5 | 5.048
1102.8 | 49.5 | 5.048
1102.9 | 49.5 | 5.048
1103 | 49.5 | 5.048
1103.1 | 49.5 | 5.048
1103.2 | 49.5 | 5.048
1103.3 | 49.5 | 5.048
1103.4 | 49.5 | 5.048
1103.5 | 49.5 | 5.048
1103.6 | 49.5 | 5.048
1103.7 | 49.5 | 5.048
1103.8 | 49.5 | 5.048
1103.9 | 49.5 | 5.048
1104 | 49.5 | 5.048
1104.1 | 49.5 | 5.048
1104.2 | 49.5 | 5.048
1104.3 | 49.5 | 5.049
1104.4 | 49.5 | 5.049
1104.5 | 49.5 | 5.049
1104.6 | 49.5 | 5.049
1104.7 | 49.5 | 5.049
1104.8 | 49.5 | 5.049
1104.9 | 49.5 | 5.049
1105 | 49.5 | 5.049
1105.1 | 49.5 | 5.049
1105.2 | 49.5 | 5.049
1105.3 | 49.5 | 5.049
1105.4 | 49.5 | 5.049
1105.5 | 49.5 | 5.049
1105.6 | 49.5 | 5.049
1105.7 | 49.5 | 5.049
1105.8 | 49.5 | 5.049
1105.9 | 49.5 | 5.049
1106 | 49.5 | 5.049
1106.1 | 49.5 | 5.049
1106.2 | 49.5 | 5.049
1106.3 | 49.5 | 5.049
1106.4 | 49.5 | 5.049
1106.5 | 49.5 | 5.048
1106.6 | 49.5 | 5.048
1106.7 | 49.5 | 5.048
1106.8 | 49.5 | 5.048
1106.9 | 49.5 | 5.048
1107 | 49.5 | 5.048
1107.1 | 49.5 | 5.048
1107.2 | 49.5 | 5.048
1107.3 | 49.5 | 5.048
1107.4 | 49.5 | 5.048
1107.5 | 49.5 | 5.048
1107.6 | 49.5 | 5.048
1107.7 | 49.5 | 5.048
1107.8 | 49.5 | 5.048
1107.9 | 49.5 | 5.048
1108 | 49.5 | 5.048
1108.1 | 49.5 | 5.048
1108.2 | 49.5 | 5.048
1108.3 | 49.5 | 5.048
1108.4 | 49.5 | 5.048
1108.5 | 49.5 | 5.048
1108.6 | 49.5 | 5.048
1108.7 | 49.5 | 5.048
1108.8 | 49.5 | 5.048
1108.9 | 49.5 | 5.048
1109 | 49.5 | 5.048
1109.1 | 49.5 | 5.048
1109.2 | 49.5 | 5.048
1109.3 | 49.5 | 5.048
1109.4 | 49.5 | 5.048
1109.5 | 49.5 | 5.048
1109.6 | 49.5 | 5.048
1109.7 | 49.5 | 5.048
1109.8 | 49.5 | 5.048
1109.9 | 49.5 | 5.048
1110 | 49.5 | 5.048
1110.1 | 49.5 | 5.048
1110.2 | 49.5 | 5.048
1110.3 | 49.5 | 5.048
1110.4 | 49.5 | 5.048
1110.5 | 49.5 | 5.048
1110.6 | 49.5 | 5.048
1110.7 | 49.5 | 5.048
1110.8 | 49.5 | 5.048
1110.9 | 49.5 | 5.048
1111 | 49.5 | 5.048
1111.1 | 49.5 | 5.048
1111.2 | 49.5 | 5.048
1111.3 | 49.5 | 5.048
1111.4 | 49.5 | 5.048
1111.5 | 49.5 | 5.048
1111.6 | 49.5 | 5.048
1111.7 | 49.5 | 5.048
1111.8 | 49.5 | 5.048
1111.9 | 49.5 | 5.048
1112 | 49.5 | 5.048
1112.1 | 49.5 | 5.048
1112.2 | 49.5 | 5.048
1112.3 | 49.5 | 5.048
1112.4 | 49.5 | 5.048
1112.5 | 49.5 | 5.048
1112.6 | 49.5 | 5.048
1112.7 | 49.5 | 5.048
1112.8 | 49.5 | 5.048
1112.9 | 49.5 | 5.048
1113 | 49.5 | 5.048
1113.1 | 49.5 | 5.048
1113.2 | 49.5 | 5.048
1113.3 | 49.5 | 5.048
1113.4 | 49.5 | 5.048
1113.5 | 49.5 | 5.048
1113.6 | 49.5 | 5.048
1113.7 | 49.5 | 5.048
1113.8 | 49.5 | 5.048
1113.9 | 49.5 | 5.048
1114 | 49.5 | 5.048
1114.1 | 49.5 | 5.048
1114.2 | 49.5 | 5.048
1114.3 | 49.5 | 5.048
1114.4 | 49.5 | 5.048
1114.5 | 49.5 | 5.048
1114.6 | 49.5 | 5.048
1114.7 | 49.5 | 5.048
1114.8 | 49.5 | 5.048
1114.9 | 49.5 | 5.048
1115 | 49.5 | 5.048
1115.1 | 49.5 | 5.048
1115.2 | 49.5 | 5.048
1115.3 | 49.5 | 5.048
1115.4 | 49.5 | 5.048
1115.5 | 49.5 | 5.048
1115.6 | 49.5 | 5.048
1115.7 | 49.5 | 5.048
1115.8 | 49.5 | 5.048
1115.9 | 49.5 | 5.048
1116 | 49.5 | 5.048
1116.1 | 49.5 | 5.048
1116.2 | 49.5 | 5.048
1116.3 | 49.5 | 5.048
1116.4 | 49.5 | 5.048
1116.5 | 49.5 | 5.048
1116.6 | 49.5 | 5.048
1116.7 | 49.5 | 5.048
1116.8 | 49.5 | 5.048
1116.9 | 49.5 | 5.048
1117 | 49.5 | 5.048
1117.1 | 49.5 | 5.048
1117.2 | 49.5 | 5.048
1117.3 | 49.5 | 5.048
1117.4 | 49.5 | 5.048
1117.5 | 49.5 | 5.048
1117.6 | 49.5 | 5.048
1117.7 | 49.5 | 5.048
1117.8 | 49.5 | 5.048
1117.9 | 49.5 | 5.048
1118 | 49.5 | 5.048
1118.1 | 49.5 | 5.048
1118.2 | 49.5 | 5.048
1118.3 | 49.5 | 5.048
1118.4 | 49.5 | 5.048
1118.5 | 49.5 | 5.048
1118.6 | 49.5 | 5.048
1118.7 | 49.5 | 5.048
1118.8 | 49.5 | 5.048
1118.9 | 49.5 | 5.048
1119 | 49.5 | 5.048
1119.1 | 49.5 | 5.048
1119.2 | 49.5 | 5.048
1119.3 | 49.5 | 5.048
1119.4 | 49.5 | 5.048
1119.5 | 49.5 | 5.048
1119.6 | 49.5 | 5.048
1119.7 | 49.5 | 5.048
1119.8 | 49.5 | 5.048
1119.9 | 49.5 | 5.048
1120 | 49.5 | 5.048
1120.1 | 49.5 | 5.048
1120.2 | 49.5 | 5.048
1120.3 | 49.5 | 5.048
1120.4 | 49.5 | 5.048
1120.5 | 49.5 | 5.048
1120.6 | 49.5 | 5.048
1120.7 | 49.5 | 5.048
1120.8 | 49.5 | 5.048
1120.9 | 49.5 | 5.048
1121 | 49.5 | 5.048
1121.1 | 49.5 | 5.048
1121.2 | 49.5 | 5.048
1121.3 | 49.5 | 5.048
1121.4 | 49.5 | 5.048
1121.5 | 49.5 | 5.048
1121.6 | 49.5 | 5.048
1121.7 | 49.5 | 5.048
1121.8 | 49.5 | 5.048
1121.9 | 49.5 | 5.048
1122 | 49.5 | 5.048
1122.1 | 49.5 | 5.048
1122.2 | 49.5 | 5.048
1122.3 | 49.5 | 5.049
1122.4 | 49.5 | 5.049
1122.5 | 49.5 | 5.049
1122.6 | 49.5 | 5.049
1122.7 | 49.5 | 5.049
1122.8 | 49.5 | 5.049
1122.9 | 49.5 | 5.049
1123 | 49.5 | 5.049
1123.1 | 49.5 | 5.049
1123.2 | 49.5 | 5.049
1123.3 | 49.5 | 5.049
1123.4 | 49.5 | 5.048
1123.5 | 49.5 | 5.048
1123.6 | 49.5 | 5.048
1123.7 | 49.5 | 5.048
1123.8 | 49.5 | 5.048
1123.9 | 49.5 | 5.048
1124 | 49.5 | 5.048
1124.1 | 49.5 | 5.048
1124.2 | 49.5 | 5.048
1124.3 | 49.5 | 5.048
1124.4 | 49.5 | 5.048
1124.5 | 49.5 | 5.048
1124.6 | 49.5 | 5.048
1124.7 | 49.5 | 5.048
1124.8 | 49.5 | 5.048
1124.9 | 49.5 | 5.048
1125 | 49.5 | 5.048
1125.1 | 49.5 | 5.048
1125.2 | 49.5 | 5.048
1125.3 | 49.5 | 5.048
1125.4 | 49.5 | 5.048
1125.5 | 49.5 | 5.048
1125.6 | 49.5 | 5.048
1125.7 | 49.5 | 5.048
1125.8 | 49.5 | 5.048
1125.9 | 49.5 | 5.048
1126 | 49.5 | 5.048
1126.1 | 49.5 | 5.048
1126.2 | 49.5 | 5.048
1126.3 | 49.5 | 5.048
1126.4 | 49.5 | 5.048
1126.5 | 49.5 | 5.048
1126.6 | 49.5 | 5.048
1126.7 | 49.5 | 5.048
1126.8 | 49.5 | 5.048
1126.9 | 49.5 | 5.048
1127 | 49.5 | 5.048
1127.1 | 49.5 | 5.048
1127.2 | 49.5 | 5.048
1127.3 | 49.5 | 5.048
1127.4 | 49.5 | 5.048
1127.5 | 49.5 | 5.048
1127.6 | 49.5 | 5.048
1127.7 | 49.5 | 5.048
1127.8 | 49.5 | 5.048
1127.9 | 49.5 | 5.048
1128 | 49.5 | 5.048
1128.1 | 49.5 | 5.048
1128.2 | 49.5 | 5.048
1128.3 | 49.5 | 5.048
1128.4 | 49.5 | 5.048
1128.5 | 49.5 | 5.048
1128.6 | 49.5 | 5.048
1128.7 | 49.5 | 5.048
1128.8 | 49.5 | 5.048
1128.9 | 49.5 | 5.048
1129 | 49.5 | 5.048
1129.1 | 49.5 | 5.048
1129.2 | 49.5 | 5.048
1129.3 | 49.5 | 5.048
1129.4 | 49.5 | 5.048
1129.5 | 49.5 | 5.048
1129.6 | 49.5 | 5.048
1129.7 | 49.5 | 5.048
1129.8 | 49.5 | 5.048
1129.9 | 49.5 | 5.048
1130 | 49.5 | 5.048
1130.1 | 49.5 | 5.048
1130.2 | 49.5 | 5.048
1130.3 | 49.5 | 5.048
1130.4 | 49.5 | 5.048
1130.5 | 49.5 | 5.048
1130.6 | 49.5 | 5.048
1130.7 | 49.5 | 5.048
1130.8 | 49.5 | 5.048
1130.9 | 49.5 | 5.048
1131 | 49.5 | 5.048
1131.1 | 49.5 | 5.048
1131.2 | 49.5 | 5.048
1131.3 | 49.5 | 5.048
1131.4 | 49.5 | 5.048
1131.5 | 49.5 | 5.048
1131.6 | 49.5 | 5.048
1131.7 | 49.5 | 5.048
1131.8 | 49.5 | 5.048
1131.9 | 49.5 | 5.048
1132 | 49.5 | 5.048
1132.1 | 49.5 | 5.048
1132.2 | 49.5 | 5.048
1132.3 | 49.5 | 5.048
1132.4 | 49.5 | 5.048
1132.5 | 49.5 | 5.048
1132.6 | 49.5 | 5.048
1132.7 | 49.5 | 5.048
1132.8 | 49.5 | 5.048
1132.9 | 49.5 | 5.048
1133 | 49.5 | 5.048
1133.1 | 49.5 | 5.048
1133.2 | 49.5 | 5.048
1133.3 | 49.5 | 5.048
1133.4 | 49.5 | 5.048
1133.5 | 49.5 | 5.048
1133.6 | 49.5 | 5.048
1133.7 | 49.5 | 5.048
1133.8 | 49.5 | 5.048
1133.9 | 49.5 | 5.048
1134 | 49.5 | 5.048
1134.1 | 49.5 | 5.048
1134.2 | 49.5 | 5.048
1134.3 | 49.5 | 5.048
1134.4 | 49.5 | 5.048
1134.5 | 49.5 | 5.048
1134.6 | 49.5 | 5.048
1134.7 | 49.5 | 5.048
1134.8 | 49.5 | 5.048
1134.9 | 49.5 | 5.048
1135 | 49.5 | 5.048
1135.1 | 49.5 | 5.048
1135.2 | 49.5 | 5.048
1135.3 | 49.5 | 5.048
1135.4 | 49.5 | 5.048
1135.5 | 49.5 | 5.048
1135.6 | 49.5 | 5.048
1135.7 | 49.5 | 5.048
1135.8 | 49.5 | 5.048
1135.9 | 49.5 | 5.048
1136 | 49.5 | 5.048
1136.1 | 49.5 | 5.048
1136.2 | 49.5 | 5.048
1136.3 | 49.5 | 5.048
1136.4 | 49.5 | 5.048
1136.5 | 49.5 | 5.048
1136.6 | 49.5 | 5.048
1136.7 | 49.5 | 5.048
1136.8 | 49.5 | 5.048
1136.9 | 49.5 | 5.048
1137 | 49.5 | 5.048
1137.1 | 49.5 | 5.048
1137.2 | 49.5 | 5.048
1137.3 | 49.5 | 5.048
1137.4 | 49.5 | 5.048
1137.5 | 49.5 | 5.048
1137.6 | 49.5 | 5.048
1137.7 | 49.5 | 5.048
1137.8 | 49.5 | 5.048
1137.9 | 49.5 | 5.048
1138 | 49.5 | 5.048
1138.1 | 49.5 | 5.048
1138.2 | 49.5 | 5.048
1138.3 | 49.5 | 5.048
1138.4 | 49.5 | 5.048
1138.5 | 49.5 | 5.048
1138.6 | 49.5 | 5.048
1138.7 | 49.5 | 5.048
1138.8 | 49.5 | 5.048
1138.9 | 49.5 | 5.048
1139 | 49.5 | 5.048
1139.1 | 49.5 | 5.048
1139.2 | 49.5 | 5.048
1139.3 | 49.5 | 5.048
1139.4 | 49.5 | 5.048
1139.5 | 49.5 | 5.048
1139.6 | 49.5 | 5.048
1139.7 | 49.5 | 5.048
1139.8 | 49.5 | 5.048
1139.9 | 49.5 | 5.048
1140 | 49.5 | 5.048
1140.1 | 49.5 | 5.048
1140.2 | 49.5 | 5.048
1140.3 | 49.5 | 5.048
1140.4 | 49.5 | 5.048
1140.5 | 49.5 | 5.048
1140.6 | 49.5 | 5.048
1140.7 | 49.5 | 5.048
1140.8 | 49.5 | 5.048
1140.9 | 49.5 | 5.048
1141 | 49.5 | 5.048
1141.1 | 49.5 | 5.048
1141.2 | 49.5 | 5.048
1141.3 | 49.5 | 5.048
1141.4 | 49.5 | 5.048
1141.5 | 49.5 | 5.048
1141.6 | 49.5 | 5.048
1141.7 | 49.5 | 5.048
1141.8 | 49.5 | 5.048
1141.9 | 49.5 | 5.048
1142 | 49.5 | 5.048
1142.1 | 49.5 | 5.048
1142.2 | 49.5 | 5.048
1142.3 | 49.5 | 5.048
1142.4 | 49.5 | 5.048
1142.5 | 49.5 | 5.048
1142.6 | 49.5 | 5.048
1142.7 | 49.5 | 5.048
1142.8 | 49.5 | 5.048
1142.9 | 49.5 | 5.048
1143 | 49.5 | 5.048
1143.1 | 49.5 | 5.048
1143.2 | 49.5 | 5.048
1143.3 | 49.5 | 5.048
1143.4 | 49.5 | 5.048
1143.5 | 49.5 | 5.048
1143.6 | 49.5 | 5.048
1143.7 | 49.5 | 5.048
1143.8 | 49.5 | 5.048
1143.9 | 49.5 | 5.048
1144 | 49.5 | 5.048
1144.1 | 49.5 | 5.048
1144.2 | 49.5 | 5.048
1144.3 | 49.5 | 5.048
1144.4 | 49.5 | 5.048
1144.5 | 49.5 | 5.048
1144.6 | 49.5 | 5.048
1144.7 | 49.5 | 5.048
1144.8 | 49.5 | 5.048
1144.9 | 49.5 | 5.048
1145 | 49.5 | 5.048
1145.1 | 49.5 | 5.048
1145.2 | 49.5 | 5.048
1145.3 | 49.5 | 5.048
1145.4 | 49.5 | 5.048
1145.5 | 49.5 | 5.048
1145.6 | 49.5 | 5.048
1145.7 | 49.5 | 5.048
1145.8 | 49.5 | 5.048
1145.9 | 49.5 | 5.048
1146 | 49.5 | 5.048
1146.1 | 49.5 | 5.048
1146.2 | 49.5 | 5.048
1146.3 | 49.5 | 5.048
1146.4 | 49.5 | 5.048
1146.5 | 49.5 | 5.048
1146.6 | 49.5 | 5.048
1146.7 | 49.5 | 5.048
1146.8 | 49.5 | 5.048
1146.9 | 49.5 | 5.048
1147 | 49.5 | 5.048
1147.1 | 49.5 | 5.048
1147.2 | 49.5 | 5.048
1147.3 | 49.5 | 5.048
1147.4 | 49.5 | 5.048
1147.5 | 49.5 | 5.048
1147.6 | 49.5 | 5.048
1147.7 | 49.5 | 5.048
1147.8 | 49.5 | 5.048
1147.9 | 49.5 | 5.048
1148 | 49.5 | 5.048
1148.1 | 49.5 | 5.048
1148.2 | 49.5 | 5.048
1148.3 | 49.5 | 5.048
1148.4 | 49.5 | 5.048
1148.5 | 49.5 | 5.048
1148.6 | 49.5 | 5.048
1148.7 | 49.5 | 5.048
1148.8 | 49.5 | 5.048
1148.9 | 49.5 | 5.048
1149 | 49.5 | 5.048
1149.1 | 49.5 | 5.048
1149.2 | 49.5 | 5.048
1149.3 | 49.5 | 5.048
1149.4 | 49.5 | 5.048
1149.5 | 49.5 | 5.048
1149.6 | 49.5 | 5.048
1149.7 | 49.5 | 5.048
1149.8 | 49.5 | 5.048
1149.9 | 49.5 | 5.048
1150 | 49.5 | 5.048
1150.1 | 49.5 | 5.048
1150.2 | 49.5 | 5.048
1150.3 | 49.5 | 5.048
1150.4 | 49.5 | 5.048
1150.5 | 49.5 | 5.048
1150.6 | 49.5 | 5.048
1150.7 | 49.5 | 5.048
1150.8 | 49.5 | 5.048
1150.9 | 49.5 | 5.048
1151 | 49.5 | 5.048
1151.1 | 49.5 | 5.048
1151.2 | 49.5 | 5.048
1151.3 | 49.5 | 5.048
1151.4 | 49.5 | 5.048
1151.5 | 49.5 | 5.048
1151.6 | 49.5 | 5.048
1151.7 | 49.5 | 5.048
1151.8 | 49.5 | 5.048
1151.9 | 49.5 | 5.048
1152 | 49.5 | 5.048
1152.1 | 49.5 | 5.048
1152.2 | 49.5 | 5.048
1152.3 | 49.5 | 5.048
1152.4 | 49.5 | 5.048
1152.5 | 49.5 | 5.048
1152.6 | 49.5 | 5.048
1152.7 | 49.5 | 5.048
1152.8 | 49.5 | 5.048
1152.9 | 49.5 | 5.048
1153 | 49.5 | 5.048
1153.1 | 49.5 | 5.048
1153.2 | 49.5 | 5.048
1153.3 | 49.5 | 5.048
1153.4 | 49.5 | 5.048
1153.5 | 49.5 | 5.048
1153.6 | 49.5 | 5.048
1153.7 | 49.5 | 5.048
1153.8 | 49.5 | 5.048
1153.9 | 49.5 | 5.048
1154 | 49.5 | 5.048
1154.1 | 49.5 | 5.048
1154.2 | 49.5 | 5.048
1154.3 | 49.5 | 5.048
1154.4 | 49.5 | 5.048
1154.5 | 49.5 | 5.048
1154.6 | 49.5 | 5.048
1154.7 | 49.5 | 5.048
1154.8 | 49.5 | 5.048
1154.9 | 49.5 | 5.048
1155 | 49.5 | 5.048
1155.1 | 49.5 | 5.048
1155.2 | 49.5 | 5.048
1155.3 | 49.5 | 5.048
1155.4 | 49.5 | 5.048
1155.5 | 49.5 | 5.048
1155.6 | 49.5 | 5.048
1155.7 | 49.5 | 5.048
1155.8 | 49.5 | 5.048
1155.9 | 49.5 | 5.048
1156 | 49.5 | 5.048
1156.1 | 49.5 | 5.048
1156.2 | 49.5 | 5.048
1156.3 | 49.5 | 5.048
1156.4 | 49.5 | 5.048
1156.5 | 49.5 | 5.048
1156.6 | 49.5 | 5.048
1156.7 | 49.5 | 5.048
1156.8 | 49.5 | 5.048
1156.9 | 49.5 | 5.048
1157 | 49.5 | 5.048
1157.1 | 49.5 | 5.048
1157.2 | 49.5 | 5.048
1157.3 | 49.5 | 5.048
1157.4 | 49.5 | 5.048
1157.5 | 49.5 | 5.048
1157.6 | 49.5 | 5.048
1157.7 | 49.5 | 5.048
1157.8 | 49.5 | 5.048
1157.9 | 49.5 | 5.048
1158 | 49.5 | 5.048
1158.1 | 49.5 | 5.048
1158.2 | 49.5 | 5.048
1158.3 | 49.5 | 5.048
1158.4 | 49.5 | 5.048
1158.5 | 49.5 | 5.048
1158.6 | 49.5 | 5.048
1158.7 | 49.5 | 5.048
1158.8 | 49.5 | 5.048
1158.9 | 49.5 | 5.048
1159 | 49.5 | 5.048
1159.1 | 49.5 | 5.048
1159.2 | 49.5 | 5.048
1159.3 | 49.5 | 5.048
1159.4 | 49.5 | 5.048
1159.5 | 49.5 | 5.048
1159.6 | 49.5 | 5.048
1159.7 | 49.5 | 5.048
1159.8 | 49.5 | 5.048
1159.9 | 49.5 | 5.048
1160 | 49.5 | 5.048
1160.1 | 49.5 | 5.048
1160.2 | 49.5 | 5.048
1160.3 | 49.5 | 5.048
1160.4 | 49.5 | 5.048
1160.5 | 49.5 | 5.048
1160.6 | 49.5 | 5.048
1160.7 | 49.5 | 5.048
1160.8 | 49.5 | 5.048
1160.9 | 49.5 | 5.048
1161 | 49.5 | 5.048
1161.1 | 49.5 | 5.048
1161.2 | 49.5 | 5.048
1161.3 | 49.5 | 5.048
1161.4 | 49.5 | 5.048
1161.5 | 49.5 | 5.048
1161.6 | 49.5 | 5.048
1161.7 | 49.5 | 5.048
1161.8 | 49.5 | 5.048
1161.9 | 49.5 | 5.048
1162 | 49.5 | 5.048
1162.1 | 49.5 | 5.048
1162.2 | 49.5 | 5.048
1162.3 | 49.5 | 5.048
1162.4 | 49.5 | 5.049
1162.5 | 49.5 | 5.049
1162.6 | 49.5 | 5.049
1162.7 | 49.5 | 5.049
1162.8 | 49.5 | 5.049
1162.9 | 49.5 | 5.049
1163 | 49.5 | 5.049
1163.1 | 49.5 | 5.049
1163.2 | 49.5 | 5.048
1163.3 | 49.5 | 5.048
1163.4 | 49.5 | 5.048
1163.5 | 49.5 | 5.048
1163.6 | 49.5 | 5.048
1163.7 | 49.5 | 5.048
1163.8 | 49.5 | 5.048
1163.9 | 49.5 | 5.048
1164 | 49.5 | 5.048
1164.1 | 49.5 | 5.048
1164.2 | 49.5 | 5.048
1164.3 | 49.5 | 5.048
1164.4 | 49.5 | 5.048
1164.5 | 49.5 | 5.049
1164.6 | 49.5 | 5.049
1164.7 | 49.5 | 5.049
1164.8 | 49.5 | 5.048
1164.9 | 49.5 | 5.048
1165 | 49.5 | 5.048
1165.1 | 49.5 | 5.048
1165.2 | 49.5 | 5.048
1165.3 | 49.5 | 5.048
1165.4 | 49.5 | 5.048
1165.5 | 49.5 | 5.048
1165.6 | 49.5 | 5.049
1165.7 | 49.5 | 5.049
1165.8 | 49.5 | 5.049
1165.9 | 49.5 | 5.049
1166 | 49.5 | 5.049
1166.1 | 49.5 | 5.049
1166.2 | 49.5 | 5.049
1166.3 | 49.5 | 5.049
1166.4 | 49.5 | 5.049
1166.5 | 49.5 | 5.049
1166.6 | 49.5 | 5.049
1166.7 | 49.5 | 5.049
1166.8 | 49.5 | 5.049
1166.9 | 49.5 | 5.049
1167 | 49.5 | 5.049
1167.1 | 49.5 | 5.049
1167.2 | 49.5 | 5.049
1167.3 | 49.5 | 5.049
1167.4 | 49.5 | 5.049
1167.5 | 49.5 | 5.049
1167.6 | 49.5 | 5.049
1167.7 | 49.5 | 5.049
1167.8 | 49.5 | 5.049
1167.9 | 49.5 | 5.049
1168 | 49.5 | 5.048
1168.1 | 49.5 | 5.048
1168.2 | 49.5 | 5.048
1168.3 | 49.5 | 5.048
1168.4 | 49.5 | 5.048
1168.5 | 49.5 | 5.048
1168.6 | 49.5 | 5.048
1168.7 | 49.5 | 5.048
1168.8 | 49.5 | 5.048
1168.9 | 49.5 | 5.048
1169 | 49.5 | 5.048
1169.1 | 49.5 | 5.048
1169.2 | 49.5 | 5.048
1169.3 | 49.5 | 5.048
1169.4 | 49.5 | 5.048
1169.5 | 49.5 | 5.048
1169.6 | 49.5 | 5.048
1169.7 | 49.5 | 5.048
1169.8 | 49.5 | 5.048
1169.9 | 49.5 | 5.048
1170 | 49.5 | 5.048
1170.1 | 49.5 | 5.048
1170.2 | 49.5 | 5.048
1170.3 | 49.5 | 5.048
1170.4 | 49.5 | 5.048
1170.5 | 49.5 | 5.048
1170.6 | 49.5 | 5.048
1170.7 | 49.5 | 5.048
1170.8 | 49.5 | 5.048
1170.9 | 49.5 | 5.048
1171 | 49.5 | 5.048
1171.1 | 49.5 | 5.048
1171.2 | 49.5 | 5.048
1171.3 | 49.5 | 5.048
1171.4 | 49.5 | 5.048
1171.5 | 49.5 | 5.048
1171.6 | 49.5 | 5.048
1171.7 | 49.5 | 5.048
1171.8 | 49.5 | 5.048
1171.9 | 49.5 | 5.048
1172 | 49.5 | 5.048
1172.1 | 49.5 | 5.048
1172.2 | 49.5 | 5.048
1172.3 | 49.5 | 5.048
1172.4 | 49.5 | 5.048
1172.5 | 49.5 | 5.048
1172.6 | 49.5 | 5.048
1172.7 | 49.5 | 5.048
1172.8 | 49.5 | 5.049
1172.9 | 49.5 | 5.049
1173 | 49.5 | 5.049
1173.1 | 49.5 | 5.049
1173.2 | 49.5 | 5.049
1173.3 | 49.5 | 5.049
1173.4 | 49.5 | 5.049
1173.5 | 49.5 | 5.049
1173.6 | 49.5 | 5.049
1173.7 | 49.5 | 5.049
1173.8 | 49.5 | 5.049
1173.9 | 49.5 | 5.049
1174 | 49.5 | 5.049
1174.1 | 49.5 | 5.049
1174.2 | 49.5 | 5.049
1174.3 | 49.5 | 5.049
1174.4 | 49.5 | 5.049
1174.5 | 49.5 | 5.049
1174.6 | 49.5 | 5.049
1174.7 | 49.5 | 5.049
1174.8 | 49.5 | 5.049
1174.9 | 49.5 | 5.049
1175 | 49.5 | 5.048
1175.1 | 49.5 | 5.048
1175.2 | 49.5 | 5.048
1175.3 | 49.5 | 5.048
1175.4 | 49.5 | 5.048
1175.5 | 49.5 | 5.048
1175.6 | 49.5 | 5.048
1175.7 | 49.5 | 5.048
1175.8 | 49.5 | 5.048
1175.9 | 49.5 | 5.048
1176 | 49.5 | 5.048
1176.1 | 49.5 | 5.048
1176.2 | 49.5 | 5.048
1176.3 | 49.5 | 5.048
1176.4 | 49.5 | 5.048
1176.5 | 49.5 | 5.048
1176.6 | 49.5 | 5.048
1176.7 | 49.5 | 5.048
1176.8 | 49.5 | 5.048
1176.9 | 49.5 | 5.048
1177 | 49.5 | 5.048
1177.1 | 49.5 | 5.048
1177.2 | 49.5 | 5.048
1177.3 | 49.5 | 5.048
1177.4 | 49.5 | 5.048
1177.5 | 49.5 | 5.048
1177.6 | 49.5 | 5.048
1177.7 | 49.5 | 5.048
1177.8 | 49.5 | 5.048
1177.9 | 49.5 | 5.048
1178 | 49.5 | 5.048
1178.1 | 49.5 | 5.048
1178.2 | 49.5 | 5.048
1178.3 | 49.5 | 5.048
1178.4 | 49.5 | 5.048
1178.5 | 49.5 | 5.048
1178.6 | 49.5 | 5.048
1178.7 | 49.5 | 5.048
1178.8 | 49.5 | 5.048
1178.9 | 49.5 | 5.048
1179 | 49.5 | 5.048
1179.1 | 49.5 | 5.048
1179.2 | 49.5 | 5.048
1179.3 | 49.5 | 5.048
1179.4 | 49.5 | 5.048
1179.5 | 49.5 | 5.048
1179.6 | 49.5 | 5.048
1179.7 | 49.5 | 5.048
1179.8 | 49.5 | 5.048
1179.9 | 49.5 | 5.048
1180 | 49.5 | 5.048
1180.1 | 49.5 | 5.048
1180.2 | 49.5 | 5.048
1180.3 | 49.5 | 5.048
1180.4 | 49.5 | 5.048
1180.5 | 49.5 | 5.048
1180.6 | 49.5 | 5.048
1180.7 | 49.5 | 5.048
1180.8 | 49.5 | 5.048
1180.9 | 49.5 | 5.048
1181 | 49.5 | 5.048
1181.1 | 49.5 | 5.048
1181.2 | 49.5 | 5.048
1181.3 | 49.5 | 5.048
1181.4 | 49.5 | 5.048
1181.5 | 49.5 | 5.048
1181.6 | 49.5 | 5.048
1181.7 | 49.5 | 5.048
1181.8 | 49.5 | 5.048
1181.9 | 49.5 | 5.048
1182 | 49.5 | 5.048
1182.1 | 49.5 | 5.048
1182.2 | 49.5 | 5.048
1182.3 | 49.5 | 5.048
1182.4 | 49.5 | 5.048
1182.5 | 49.5 | 5.048
1182.6 | 49.5 | 5.048
1182.7 | 49.5 | 5.048
1182.8 | 49.5 | 5.048
1182.9 | 49.5 | 5.048
1183 | 49.5 | 5.048
1183.1 | 49.5 | 5.048
1183.2 | 49.5 | 5.048
1183.3 | 49.5 | 5.048
1183.4 | 49.5 | 5.048
1183.5 | 49.5 | 5.048
1183.6 | 49.5 | 5.048
1183.7 | 49.5 | 5.048
1183.8 | 49.5 | 5.048
1183.9 | 49.5 | 5.048
1184 | 49.5 | 5.048
1184.1 | 49.5 | 5.048
1184.2 | 49.5 | 5.048
1184.3 | 49.5 | 5.048
1184.4 | 49.5 | 5.048
1184.5 | 49.5 | 5.048
1184.6 | 49.5 | 5.048
1184.7 | 49.5 | 5.048
1184.8 | 49.5 | 5.048
1184.9 | 49.5 | 5.048
1185 | 49.5 | 5.048
1185.1 | 49.5 | 5.048
1185.2 | 49.5 | 5.048
1185.3 | 49.5 | 5.048
1185.4 | 49.5 | 5.048
1185.5 | 49.5 | 5.048
1185.6 | 49.5 | 5.048
1185.7 | 49.5 | 5.048
1185.8 | 49.5 | 5.048
1185.9 | 49.5 | 5.048
1186 | 49.5 | 5.048
1186.1 | 49.5 | 5.048
1186.2 | 49.5 | 5.048
1186.3 | 49.5 | 5.048
1186.4 | 49.5 | 5.048
1186.5 | 49.5 | 5.048
1186.6 | 49.5 | 5.048
1186.7 | 49.5 | 5.048
1186.8 | 49.5 | 5.048
1186.9 | 49.5 | 5.048
1187 | 49.5 | 5.048
1187.1 | 49.5 | 5.049
1187.2 | 49.5 | 5.049
1187.3 | 49.5 | 5.049
1187.4 | 49.5 | 5.049
1187.5 | 49.5 | 5.049
1187.6 | 49.5 | 5.049
1187.7 | 49.5 | 5.049
1187.8 | 49.5 | 5.049
1187.9 | 49.5 | 5.049
1188 | 49.5 | 5.049
1188.1 | 49.5 | 5.049
1188.2 | 49.5 | 5.048
1188.3 | 49.5 | 5.048
1188.4 | 49.5 | 5.048
1188.5 | 49.5 | 5.048
1188.6 | 49.5 | 5.049
1188.7 | 49.5 | 5.049
1188.8 | 49.5 | 5.049
1188.9 | 49.5 | 5.049
1189 | 49.5 | 5.049
1189.1 | 49.5 | 5.049
1189.2 | 49.5 | 5.049
1189.3 | 49.5 | 5.049
1189.4 | 49.5 | 5.049
1189.5 | 49.5 | 5.049
1189.6 | 49.5 | 5.049
1189.7 | 49.5 | 5.049
1189.8 | 49.5 | 5.048
1189.9 | 49.5 | 5.048
1190 | 49.5 | 5.048
1190.1 | 49.5 | 5.048
1190.2 | 49.5 | 5.048
1190.3 | 49.5 | 5.048
1190.4 | 49.5 | 5.048
1190.5 | 49.5 | 5.048
1190.6 | 49.5 | 5.048
1190.7 | 49.5 | 5.048
1190.8 | 49.5 | 5.048
1190.9 | 49.5 | 5.048
1191 | 49.5 | 5.048
1191.1 | 49.5 | 5.048
1191.2 | 49.5 | 5.048
1191.3 | 49.5 | 5.048
1191.4 | 49.5 | 5.048
1191.5 | 49.5 | 5.048
1191.6 | 49.5 | 5.048
1191.7 | 49.5 | 5.048
1191.8 | 49.5 | 5.048
1191.9 | 49.5 | 5.048
1192 | 49.5 | 5.048
1192.1 | 49.5 | 5.048
1192.2 | 49.5 | 5.048
1192.3 | 49.5 | 5.048
1192.4 | 49.5 | 5.048
1192.5 | 49.5 | 5.048
1192.6 | 49.5 | 5.048
1192.7 | 49.5 | 5.048
1192.8 | 49.5 | 5.048
1192.9 | 49.5 | 5.048
1193 | 49.5 | 5.048
1193.1 | 49.5 | 5.048
1193.2 | 49.5 | 5.048
1193.3 | 49.5 | 5.048
1193.4 | 49.5 | 5.048
1193.5 | 49.5 | 5.048
1193.6 | 49.5 | 5.048
1193.7 | 49.5 | 5.048
1193.8 | 49.5 | 5.048
1193.9 | 49.5 | 5.048
1194 | 49.5 | 5.048
1194.1 | 49.5 | 5.049
1194.2 | 49.5 | 5.049
1194.3 | 49.5 | 5.049
1194.4 | 49.5 | 5.049
1194.5 | 49.5 | 5.049
1194.6 | 49.5 | 5.049
1194.7 | 49.5 | 5.049
1194.8 | 49.5 | 5.049
1194.9 | 49.5 | 5.049
1195 | 49.5 | 5.049
1195.1 | 49.5 | 5.049
1195.2 | 49.5 | 5.049
1195.3 | 49.5 | 5.048
1195.4 | 49.5 | 5.048
1195.5 | 49.5 | 5.048
1195.6 | 49.5 | 5.048
1195.7 | 49.5 | 5.048
1195.8 | 49.5 | 5.048
1195.9 | 49.5 | 5.048
1196 | 49.5 | 5.048
1196.1 | 49.5 | 5.048
1196.2 | 49.5 | 5.048
1196.3 | 49.5 | 5.048
1196.4 | 49.5 | 5.048
1196.5 | 49.5 | 5.048
1196.6 | 49.5 | 5.048
1196.7 | 49.5 | 5.048
1196.8 | 49.5 | 5.048
1196.9 | 49.5 | 5.048
1197 | 49.5 | 5.048
1197.1 | 49.5 | 5.048
1197.2 | 49.5 | 5.048
1197.3 | 49.5 | 5.048
1197.4 | 49.5 | 5.048
1197.5 | 49.5 | 5.048
1197.6 | 49.5 | 5.048
1197.7 | 49.5 | 5.048
1197.8 | 49.5 | 5.048
1197.9 | 49.5 | 5.048
1198 | 49.5 | 5.048
1198.1 | 49.5 | 5.048
1198.2 | 49.5 | 5.048
1198.3 | 49.5 | 5.048
1198.4 | 49.5 | 5.048
1198.5 | 49.5 | 5.048
1198.6 | 49.5 | 5.048
1198.7 | 49.5 | 5.048
1198.8 | 49.5 | 5.048
1198.9 | 49.5 | 5.048
1199 | 49.5 | 5.048
1199.1 | 49.5 | 5.048
1199.2 | 49.5 | 5.048
1199.3 | 49.5 | 5.048
1199.4 | 49.5 | 5.048
1199.5 | 49.5 | 5.048
1199.6 | 49.5 | 5.048
1199.7 | 49.5 | 5.048
1199.8 | 49.5 | 5.048
1199.9 | 49.5 | 5.048
1200 | 49.5 | 5.048
1200.1 | 49.5 | 5.048
1200.2 | 49.5 | 5.048
1200.3 | 49.5 | 5.048
1200.4 | 49.5 | 5.048
1200.5 | 49.5 | 5.048
1200.6 | 49.5 | 5.048
1200.7 | 49.5 | 5.048
1200.8 | 49.5 | 5.048
1200.9 | 49.5 | 5.048
1201 | 49.5 | 5.048
1201.1 | 49.5 | 5.048
1201.2 | 49.5 | 5.048
1201.3 | 49.5 | 5.048
1201.4 | 49.5 | 5.048
1201.5 | 49.5 | 5.048
1201.6 | 49.5 | 5.048
1201.7 | 49.5 | 5.048
1201.8 | 49.5 | 5.048
1201.9 | 49.5 | 5.048
1202 | 49.5 | 5.048
1202.1 | 49.5 | 5.048
1202.2 | 49.5 | 5.048
1202.3 | 49.5 | 5.048
1202.4 | 49.5 | 5.048
1202.5 | 49.5 | 5.048
1202.6 | 49.5 | 5.048
1202.7 | 49.5 | 5.048
1202.8 | 49.5 | 5.048
1202.9 | 49.5 | 5.048
1203 | 49.5 | 5.048
1203.1 | 49.5 | 5.048
1203.2 | 49.5 | 5.048
1203.3 | 49.5 | 5.048
1203.4 | 49.5 | 5.048
1203.5 | 49.5 | 5.048
1203.6 | 49.5 | 5.048
1203.7 | 49.5 | 5.048
1203.8 | 49.5 | 5.048
1203.9 | 49.5 | 5.048
1204 | 49.5 | 5.048
1204.1 | 49.5 | 5.048
1204.2 | 49.5 | 5.048
1204.3 | 49.5 | 5.048
1204.4 | 49.5 | 5.048
1204.5 | 49.5 | 5.048
1204.6 | 49.5 | 5.048
1204.7 | 49.5 | 5.048
1204.8 | 49.5 | 5.048
1204.9 | 49.5 | 5.048
1205 | 49.5 | 5.048
1205.1 | 49.5 | 5.048
1205.2 | 49.5 | 5.048
1205.3 | 49.5 | 5.048
1205.4 | 49.5 | 5.048
1205.5 | 49.5 | 5.048
1205.6 | 49.5 | 5.048
1205.7 | 49.5 | 5.048
1205.8 | 49.5 | 5.048
1205.9 | 49.5 | 5.048
1206 | 49.5 | 5.048
1206.1 | 49.5 | 5.048
1206.2 | 49.5 | 5.048
1206.3 | 49.5 | 5.048
1206.4 | 49.5 | 5.048
1206.5 | 49.5 | 5.048
1206.6 | 49.5 | 5.048
1206.7 | 49.5 | 5.048
1206.8 | 49.5 | 5.048
1206.9 | 49.5 | 5.049
1207 | 49.5 | 5.049
1207.1 | 49.5 | 5.049
1207.2 | 49.5 | 5.049
1207.3 | 49.5 | 5.049
1207.4 | 49.5 | 5.049
1207.5 | 49.5 | 5.049
1207.6 | 49.5 | 5.049
1207.7 | 49.5 | 5.049
1207.8 | 49.5 | 5.049
1207.9 | 49.5 | 5.049
1208 | 49.5 | 5.049
1208.1 | 49.5 | 5.048
1208.2 | 49.5 | 5.048
1208.3 | 49.5 | 5.048
1208.4 | 49.5 | 5.048
1208.5 | 49.5 | 5.048
1208.6 | 49.5 | 5.048
1208.7 | 49.5 | 5.048
1208.8 | 49.5 | 5.048
1208.9 | 49.5 | 5.048
1209 | 49.5 | 5.048
1209.1 | 49.5 | 5.048
1209.2 | 49.5 | 5.048
1209.3 | 49.5 | 5.048
1209.4 | 49.5 | 5.048
1209.5 | 49.5 | 5.048
1209.6 | 49.5 | 5.048
1209.7 | 49.5 | 5.048
1209.8 | 49.5 | 5.048
1209.9 | 49.5 | 5.048
1210 | 49.5 | 5.048
1210.1 | 49.5 | 5.048
1210.2 | 49.5 | 5.048
1210.3 | 49.5 | 5.048
1210.4 | 49.5 | 5.048
1210.5 | 49.5 | 5.048
1210.6 | 49.5 | 5.048
1210.7 | 49.5 | 5.048
1210.8 | 49.5 | 5.048
1210.9 | 49.5 | 5.048
1211 | 49.5 | 5.048
1211.1 | 49.5 | 5.048
1211.2 | 49.5 | 5.048
1211.3 | 49.5 | 5.048
1211.4 | 49.5 | 5.048
1211.5 | 49.5 | 5.048
1211.6 | 49.5 | 5.048
1211.7 | 49.5 | 5.048
1211.8 | 49.5 | 5.048
1211.9 | 49.5 | 5.048
1212 | 49.5 | 5.048
1212.1 | 49.5 | 5.048
1212.2 | 49.5 | 5.048
1212.3 | 49.5 | 5.048
1212.4 | 49.5 | 5.048
1212.5 | 49.5 | 5.048
1212.6 | 49.5 | 5.048
1212.7 | 49.5 | 5.048
1212.8 | 49.5 | 5.049
1212.9 | 49.5 | 5.049
1213 | 49.5 | 5.049
1213.1 | 49.5 | 5.049
1213.2 | 49.5 | 5.049
1213.3 | 49.5 | 5.049
1213.4 | 49.5 | 5.049
1213.5 | 49.5 | 5.049
1213.6 | 49.5 | 5.049
1213.7 | 49.5 | 5.049
1213.8 | 49.5 | 5.049
1213.9 | 49.5 | 5.049
1214 | 49.5 | 5.048
1214.1 | 49.5 | 5.048
1214.2 | 49.5 | 5.049
1214.3 | 49.5 | 5.049
1214.4 | 49.5 | 5.049
1214.5 | 49.5 | 5.049
1214.6 | 49.5 | 5.049
1214.7 | 49.5 | 5.049
1214.8 | 49.5 | 5.048
1214.9 | 49.5 | 5.048
1215 | 49.5 | 5.048
1215.1 | 49.5 | 5.048
1215.2 | 49.5 | 5.048
1215.3 | 49.5 | 5.048
1215.4 | 49.5 | 5.048
1215.5 | 49.5 | 5.048
1215.6 | 49.5 | 5.048
1215.7 | 49.5 | 5.048
1215.8 | 49.5 | 5.048
1215.9 | 49.5 | 5.048
1216 | 49.5 | 5.049
1216.1 | 49.5 | 5.049
1216.2 | 49.5 | 5.049
1216.3 | 49.5 | 5.049
1216.4 | 49.5 | 5.049
1216.5 | 49.5 | 5.049
1216.6 | 49.5 | 5.048
1216.7 | 49.5 | 5.048
1216.8 | 49.5 | 5.048
1216.9 | 49.5 | 5.048
1217 | 49.5 | 5.048
1217.1 | 49.5 | 5.048
1217.2 | 49.5 | 5.048
1217.3 | 49.5 | 5.048
1217.4 | 49.5 | 5.047
1217.5 | 49.5 | 5.047
1217.6 | 49.5 | 5.047
1217.7 | 49.5 | 5.047
1217.8 | 49.5 | 5.047
1217.9 | 49.5 | 5.047
1218 | 49.5 | 5.047
1218.1 | 49.5 | 5.047
1218.2 | 49.5 | 5.047
1218.3 | 49.5 | 5.047
1218.4 | 49.5 | 5.047
1218.5 | 49.5 | 5.047
1218.6 | 49.5 | 5.047
1218.7 | 49.5 | 5.047
1218.8 | 49.5 | 5.047
1218.9 | 49.5 | 5.048
1219 | 49.5 | 5.048
1219.1 | 49.5 | 5.048
1219.2 | 49.5 | 5.048
1219.3 | 49.5 | 5.048
1219.4 | 49.5 | 5.048
1219.5 | 49.5 | 5.048
1219.6 | 49.5 | 5.048
1219.7 | 49.5 | 5.048
1219.8 | 49.5 | 5.048
1219.9 | 49.5 | 5.049
1220 | 49.5 | 5.049
1220.1 | 49.5 | 5.049
1220.2 | 49.5 | 5.049
1220.3 | 49.5 | 5.049
1220.4 | 49.5 | 5.049
1220.5 | 49.5 | 5.049
1220.6 | 49.5 | 5.049
1220.7 | 49.5 | 5.049
1220.8 | 49.5 | 5.048
1220.9 | 49.5 | 5.048
1221 | 49.5 | 5.048
1221.1 | 49.5 | 5.049
1221.2 | 49.5 | 5.049
1221.3 | 49.5 | 5.049
1221.4 | 49.5 | 5.049
1221.5 | 49.5 | 5.049
1221.6 | 49.5 | 5.049
1221.7 | 49.5 | 5.049
1221.8 | 49.5 | 5.049
1221.9 | 49.5 | 5.049
1222 | 49.5 | 5.049
1222.1 | 49.5 | 5.049
1222.2 | 49.5 | 5.049
1222.3 | 49.5 | 5.049
1222.4 | 49.5 | 5.049
1222.5 | 49.5 | 5.048
1222.6 | 49.5 | 5.048
1222.7 | 49.5 | 5.048
1222.8 | 49.5 | 5.048
1222.9 | 49.5 | 5.048
1223 | 49.5 | 5.048
1223.1 | 49.5 | 5.048
1223.2 | 49.5 | 5.048
1223.3 | 49.5 | 5.048
1223.4 | 49.5 | 5.048
1223.5 | 49.5 | 5.049
1223.6 | 49.5 | 5.048
1223.7 | 49.5 | 5.048
1223.8 | 49.5 | 5.048
1223.9 | 49.5 | 5.048
1224 | 49.5 | 5.048
1224.1 | 49.5 | 5.049
1224.2 | 49.5 | 5.049
1224.3 | 49.5 | 5.049
1224.4 | 49.5 | 5.049
1224.5 | 49.5 | 5.048
1224.6 | 49.5 | 5.048
1224.7 | 49.5 | 5.048
1224.8 | 49.5 | 5.048
1224.9 | 49.5 | 5.048
1225 | 49.5 | 5.048
1225.1 | 49.5 | 5.048
1225.2 | 49.5 | 5.048
1225.3 | 49.5 | 5.048
1225.4 | 49.5 | 5.048
1225.5 | 49.5 | 5.048
1225.6 | 49.5 | 5.048
1225.7 | 49.5 | 5.048
1225.8 | 49.5 | 5.048
1225.9 | 49.5 | 5.047
1226 | 49.5 | 5.047
1226.1 | 49.5 | 5.047
1226.2 | 49.5 | 5.047
1226.3 | 49.5 | 5.047
1226.4 | 49.5 | 5.047
1226.5 | 49.5 | 5.047
1226.6 | 49.5 | 5.047
1226.7 | 49.5 | 5.047
1226.8 | 49.5 | 5.047
1226.9 | 49.5 | 5.047
1227 | 49.5 | 5.047
1227.1 | 49.5 | 5.048
1227.2 | 49.5 | 5.048
1227.3 | 49.5 | 5.048
1227.4 | 49.5 | 5.048
1227.5 | 49.5 | 5.048
1227.6 | 49.5 | 5.048
1227.7 | 49.5 | 5.048
1227.8 | 49.5 | 5.048
1227.9 | 49.5 | 5.048
1228 | 49.5 | 5.048
1228.1 | 49.5 | 5.048
1228.2 | 49.5 | 5.048
1228.3 | 49.5 | 5.048
1228.4 | 49.5 | 5.048
1228.5 | 49.5 | 5.048
1228.6 | 49.5 | 5.048
1228.7 | 49.5 | 5.048
1228.8 | 49.5 | 5.048
1228.9 | 49.5 | 5.048
1229 | 49.5 | 5.048
1229.1 | 49.5 | 5.048
1229.2 | 49.5 | 5.048
1229.3 | 49.5 | 5.048
1229.4 | 49.5 | 5.049
1229.5 | 49.5 | 5.049
1229.6 | 49.5 | 5.049
1229.7 | 49.5 | 5.049
1229.8 | 49.5 | 5.049
1229.9 | 49.5 | 5.049
1230 | 49.5 | 5.048
1230.1 | 49.5 | 5.048
1230.2 | 49.5 | 5.048
1230.3 | 49.5 | 5.048
1230.4 | 49.5 | 5.048
1230.5 | 49.5 | 5.048
1230.6 | 49.5 | 5.048
1230.7 | 49.5 | 5.048
1230.8 | 49.5 | 5.048
1230.9 | 49.5 | 5.048
1231 | 49.5 | 5.048
1231.1 | 49.5 | 5.048
1231.2 | 49.5 | 5.048
1231.3 | 49.5 | 5.049
1231.4 | 49.5 | 5.049
1231.5 | 49.5 | 5.049
1231.6 | 49.5 | 5.048
1231.7 | 49.5 | 5.048
1231.8 | 49.5 | 5.048
1231.9 | 49.5 | 5.048
1232 | 49.5 | 5.048
1232.1 | 49.5 | 5.048
1232.2 | 49.5 | 5.048
1232.3 | 49.5 | 5.048
1232.4 | 49.5 | 5.048
1232.5 | 49.5 | 5.048
1232.6 | 49.5 | 5.048
1232.7 | 49.5 | 5.048
1232.8 | 49.5 | 5.047
1232.9 | 49.5 | 5.047
1233 | 49.5 | 5.047
1233.1 | 49.5 | 5.047
1233.2 | 49.5 | 5.047
1233.3 | 49.5 | 5.047
1233.4 | 49.5 | 5.047
1233.5 | 49.5 | 5.047
1233.6 | 49.5 | 5.047
1233.7 | 49.5 | 5.047
1233.8 | 49.5 | 5.047
1233.9 | 49.5 | 5.048
1234 | 49.5 | 5.048
1234.1 | 49.5 | 5.048
1234.2 | 49.5 | 5.048
1234.3 | 49.5 | 5.049
1234.4 | 49.5 | 5.049
1234.5 | 49.5 | 5.049
1234.6 | 49.5 | 5.049
1234.7 | 49.5 | 5.049
1234.8 | 49.5 | 5.049
1234.9 | 49.5 | 5.049
1235 | 49.5 | 5.049
1235.1 | 49.5 | 5.049
1235.2 | 49.5 | 5.049
1235.3 | 49.5 | 5.049
1235.4 | 49.5 | 5.049
1235.5 | 49.5 | 5.049
1235.6 | 49.5 | 5.049
1235.7 | 49.5 | 5.049
1235.8 | 49.5 | 5.049
1235.9 | 49.5 | 5.049
1236 | 49.5 | 5.049
1236.1 | 49.5 | 5.049
1236.2 | 49.5 | 5.049
1236.3 | 49.5 | 5.049
1236.4 | 49.5 | 5.049
1236.5 | 49.5 | 5.049
1236.6 | 49.5 | 5.049
1236.7 | 49.5 | 5.049
1236.8 | 49.5 | 5.049
1236.9 | 49.5 | 5.049
1237 | 49.5 | 5.049
1237.1 | 49.5 | 5.049
1237.2 | 49.5 | 5.049
1237.3 | 49.5 | 5.049
1237.4 | 49.5 | 5.049
1237.5 | 49.5 | 5.048
1237.6 | 49.5 | 5.048
1237.7 | 49.5 | 5.048
1237.8 | 49.5 | 5.048
1237.9 | 49.5 | 5.048
1238 | 49.5 | 5.048
1238.1 | 49.5 | 5.048
1238.2 | 49.5 | 5.048
1238.3 | 49.5 | 5.048
1238.4 | 49.5 | 5.048
1238.5 | 49.5 | 5.048
1238.6 | 49.5 | 5.048
1238.7 | 49.5 | 5.048
1238.8 | 49.5 | 5.047
1238.9 | 49.5 | 5.047
1239 | 49.5 | 5.047
1239.1 | 49.5 | 5.047
1239.2 | 49.5 | 5.047
1239.3 | 49.5 | 5.047
1239.4 | 49.5 | 5.047
1239.5 | 49.5 | 5.047
1239.6 | 49.5 | 5.047
1239.7 | 49.5 | 5.047
1239.8 | 49.5 | 5.048
1239.9 | 49.5 | 5.048
1240 | 49.5 | 5.048
1240.1 | 49.5 | 5.048
1240.2 | 49.5 | 5.048
1240.3 | 49.5 | 5.048
1240.4 | 49.5 | 5.048
1240.5 | 49.5 | 5.048
1240.6 | 49.5 | 5.048
1240.7 | 49.5 | 5.049
1240.8 | 49.5 | 5.049
1240.9 | 49.5 | 5.049
1241 | 49.5 | 5.049
1241.1 | 49.5 | 5.049
1241.2 | 49.5 | 5.049
1241.3 | 49.5 | 5.049
1241.4 | 49.5 | 5.049
1241.5 | 49.5 | 5.049
1241.6 | 49.5 | 5.049
1241.7 | 49.5 | 5.049
1241.8 | 49.5 | 5.049
1241.9 | 49.5 | 5.049
1242 | 49.5 | 5.049
1242.1 | 49.5 | 5.049
1242.2 | 49.5 | 5.049
1242.3 | 49.5 | 5.049
1242.4 | 49.5 | 5.049
1242.5 | 49.5 | 5.049
1242.6 | 49.5 | 5.049
1242.7 | 49.5 | 5.049
1242.8 | 49.5 | 5.049
1242.9 | 49.5 | 5.049
1243 | 49.5 | 5.049
1243.1 | 49.5 | 5.049
1243.2 | 49.5 | 5.049
1243.3 | 49.5 | 5.048
1243.4 | 49.5 | 5.048
1243.5 | 49.5 | 5.048
1243.6 | 49.5 | 5.048
1243.7 | 49.5 | 5.048
1243.8 | 49.5 | 5.048
1243.9 | 49.5 | 5.048
1244 | 49.5 | 5.048
1244.1 | 49.5 | 5.048
1244.2 | 49.5 | 5.048
1244.3 | 49.5 | 5.048
1244.4 | 49.5 | 5.048
1244.5 | 49.5 | 5.048
1244.6 | 49.5 | 5.048
1244.7 | 49.5 | 5.048
1244.8 | 49.5 | 5.048
1244.9 | 49.5 | 5.048
1245 | 49.5 | 5.048
1245.1 | 49.5 | 5.048
1245.2 | 49.5 | 5.048
1245.3 | 49.5 | 5.048
1245.4 | 49.5 | 5.048
1245.5 | 49.5 | 5.048
1245.6 | 49.5 | 5.048
1245.7 | 49.5 | 5.048
1245.8 | 49.5 | 5.048
1245.9 | 49.5 | 5.048
1246 | 49.5 | 5.048
1246.1 | 49.5 | 5.048
1246.2 | 49.5 | 5.048
1246.3 | 49.5 | 5.048
1246.4 | 49.5 | 5.048
1246.5 | 49.5 | 5.048
1246.6 | 49.5 | 5.048
1246.7 | 49.5 | 5.048
1246.8 | 49.5 | 5.048
1246.9 | 49.5 | 5.049
1247 | 49.5 | 5.049
1247.1 | 49.5 | 5.049
1247.2 | 49.5 | 5.049
1247.3 | 49.5 | 5.049
1247.4 | 49.5 | 5.049
1247.5 | 49.5 | 5.049
1247.6 | 49.5 | 5.049
1247.7 | 49.5 | 5.049
1247.8 | 49.5 | 5.049
1247.9 | 49.5 | 5.049
1248 | 49.5 | 5.049
1248.1 | 49.5 | 5.049
1248.2 | 49.5 | 5.049
1248.3 | 49.5 | 5.049
1248.4 | 49.5 | 5.049
1248.5 | 49.5 | 5.049
1248.6 | 49.5 | 5.049
1248.7 | 49.5 | 5.049
1248.8 | 49.5 | 5.049
1248.9 | 49.5 | 5.048
1249 | 49.5 | 5.048
1249.1 | 49.5 | 5.048
1249.2 | 49.5 | 5.048
1249.3 | 49.5 | 5.048
1249.4 | 49.5 | 5.048
1249.5 | 49.5 | 5.048
1249.6 | 49.5 | 5.048
1249.7 | 49.5 | 5.048
1249.8 | 49.5 | 5.048
1249.9 | 49.5 | 5.048
1250 | 49.5 | 5.048
1250.1 | 49.5 | 5.048
1250.2 | 49.5 | 5.048
1250.3 | 49.5 | 5.048
1250.4 | 49.5 | 5.048
1250.5 | 49.5 | 5.048
1250.6 | 49.5 | 5.048
1250.7 | 49.5 | 5.048
1250.8 | 49.5 | 5.048
1250.9 | 49.5 | 5.048
1251 | 49.5 | 5.048
1251.1 | 49.5 | 5.048
1251.2 | 49.5 | 5.048
1251.3 | 49.5 | 5.048
1251.4 | 49.5 | 5.048
1251.5 | 49.5 | 5.048
1251.6 | 49.5 | 5.048
1251.7 | 49.5 | 5.048
1251.8 | 49.5 | 5.048
1251.9 | 49.5 | 5.048
1252 | 49.5 | 5.048
1252.1 | 49.5 | 5.048
1252.2 | 49.5 | 5.048
1252.3 | 49.5 | 5.048
1252.4 | 49.5 | 5.048
1252.5 | 49.5 | 5.048
1252.6 | 49.5 | 5.048
1252.7 | 49.5 | 5.048
1252.8 | 49.5 | 5.048
1252.9 | 49.5 | 5.048
1253 | 49.5 | 5.048
1253.1 | 49.5 | 5.048
1253.2 | 49.5 | 5.048
1253.3 | 49.5 | 5.048
1253.4 | 49.5 | 5.048
1253.5 | 49.5 | 5.048
1253.6 | 49.5 | 5.048
1253.7 | 49.5 | 5.048
1253.8 | 49.5 | 5.048
1253.9 | 49.5 | 5.048
1254 | 49.5 | 5.048
1254.1 | 49.5 | 5.048
1254.2 | 49.5 | 5.048
1254.3 | 49.5 | 5.048
1254.4 | 49.5 | 5.048
1254.5 | 49.5 | 5.048
1254.6 | 49.5 | 5.048
1254.7 | 49.5 | 5.048
1254.8 | 49.5 | 5.048
1254.9 | 49.5 | 5.048
1255 | 49.5 | 5.048
1255.1 | 49.5 | 5.049
1255.2 | 49.5 | 5.049
1255.3 | 49.5 | 5.049
1255.4 | 49.5 | 5.049
1255.5 | 49.5 | 5.049
1255.6 | 49.5 | 5.049
1255.7 | 49.5 | 5.049
1255.8 | 49.5 | 5.049
1255.9 | 49.5 | 5.049
1256 | 49.5 | 5.049
1256.1 | 49.5 | 5.048
1256.2 | 49.5 | 5.048
1256.3 | 49.5 | 5.048
1256.4 | 49.5 | 5.048
1256.5 | 49.5 | 5.048
1256.6 | 49.5 | 5.048
1256.7 | 49.5 | 5.048
1256.8 | 49.5 | 5.048
1256.9 | 49.5 | 5.048
1257 | 49.5 | 5.048
1257.1 | 49.5 | 5.048
1257.2 | 49.5 | 5.048
1257.3 | 49.5 | 5.048
1257.4 | 49.5 | 5.048
1257.5 | 49.5 | 5.048
1257.6 | 49.5 | 5.048
1257.7 | 49.5 | 5.048
1257.8 | 49.5 | 5.048
1257.9 | 49.5 | 5.048
1258 | 49.5 | 5.048
1258.1 | 49.5 | 5.048
1258.2 | 49.5 | 5.048
1258.3 | 49.5 | 5.048
1258.4 | 49.5 | 5.048
1258.5 | 49.5 | 5.048
1258.6 | 49.5 | 5.048
1258.7 | 49.5 | 5.048
1258.8 | 49.5 | 5.048
1258.9 | 49.5 | 5.048
1259 | 49.5 | 5.048
1259.1 | 49.5 | 5.048
1259.2 | 49.5 | 5.048
1259.3 | 49.5 | 5.048
1259.4 | 49.5 | 5.048
1259.5 | 49.5 | 5.048
1259.6 | 49.5 | 5.048
1259.7 | 49.5 | 5.049
1259.8 | 49.5 | 5.049
1259.9 | 49.5 | 5.049
1260 | 49.5 | 5.048
1260.1 | 49.5 | 5.048
1260.2 | 49.5 | 5.048
1260.3 | 49.5 | 5.048
1260.4 | 49.5 | 5.048
1260.5 | 49.5 | 5.048
1260.6 | 49.5 | 5.048
1260.7 | 49.5 | 5.048
1260.8 | 49.5 | 5.048
1260.9 | 49.5 | 5.049
1261 | 49.5 | 5.049
1261.1 | 49.5 | 5.049
1261.2 | 49.5 | 5.049
1261.3 | 49.5 | 5.049
1261.4 | 49.5 | 5.049
1261.5 | 49.5 | 5.049
1261.6 | 49.5 | 5.049
1261.7 | 49.5 | 5.049
1261.8 | 49.5 | 5.049
1261.9 | 49.5 | 5.049
1262 | 49.5 | 5.049
1262.1 | 49.5 | 5.048
1262.2 | 49.5 | 5.048
1262.3 | 49.5 | 5.048
1262.4 | 49.5 | 5.048
1262.5 | 49.5 | 5.048
1262.6 | 49.5 | 5.048
1262.7 | 49.5 | 5.048
1262.8 | 49.5 | 5.048
1262.9 | 49.5 | 5.048
1263 | 49.5 | 5.048
1263.1 | 49.5 | 5.048
1263.2 | 49.5 | 5.048
1263.3 | 49.5 | 5.048
1263.4 | 49.5 | 5.048
1263.5 | 49.5 | 5.048
1263.6 | 49.5 | 5.048
1263.7 | 49.5 | 5.048
1263.8 | 49.5 | 5.048
1263.9 | 49.5 | 5.048
1264 | 49.5 | 5.048
1264.1 | 49.5 | 5.048
1264.2 | 49.5 | 5.048
1264.3 | 49.5 | 5.048
1264.4 | 49.5 | 5.048
1264.5 | 49.5 | 5.048
1264.6 | 49.5 | 5.048
1264.7 | 49.5 | 5.048
1264.8 | 49.5 | 5.048
1264.9 | 49.5 | 5.048
1265 | 49.5 | 5.048
1265.1 | 49.5 | 5.048
1265.2 | 49.5 | 5.048
1265.3 | 49.5 | 5.048
1265.4 | 49.5 | 5.048
1265.5 | 49.5 | 5.048
1265.6 | 49.5 | 5.048
1265.7 | 49.5 | 5.048
1265.8 | 49.5 | 5.048
1265.9 | 49.5 | 5.048
1266 | 49.5 | 5.048
1266.1 | 49.5 | 5.048
1266.2 | 49.5 | 5.048
1266.3 | 49.5 | 5.048
1266.4 | 49.5 | 5.048
1266.5 | 49.5 | 5.048
1266.6 | 49.5 | 5.048
1266.7 | 49.5 | 5.048
1266.8 | 49.5 | 5.048
1266.9 | 49.5 | 5.048
1267 | 49.5 | 5.048
1267.1 | 49.5 | 5.048
1267.2 | 49.5 | 5.048
1267.3 | 49.5 | 5.048
1267.4 | 49.5 | 5.048
1267.5 | 49.5 | 5.048
1267.6 | 49.5 | 5.048
1267.7 | 49.5 | 5.048
1267.8 | 49.5 | 5.048
1267.9 | 49.5 | 5.048
1268 | 49.5 | 5.048
1268.1 | 49.5 | 5.048
1268.2 | 49.5 | 5.048
1268.3 | 49.5 | 5.048
1268.4 | 49.5 | 5.048
1268.5 | 49.5 | 5.048
1268.6 | 49.5 | 5.048
1268.7 | 49.5 | 5.048
1268.8 | 49.5 | 5.048
1268.9 | 49.5 | 5.048
1269 | 49.5 | 5.048
1269.1 | 49.5 | 5.048
1269.2 | 49.5 | 5.048
1269.3 | 49.5 | 5.048
1269.4 | 49.5 | 5.048
1269.5 | 49.5 | 5.048
1269.6 | 49.5 | 5.048
1269.7 | 49.5 | 5.048
1269.8 | 49.5 | 5.048
1269.9 | 49.5 | 5.048
1270 | 49.5 | 5.048
1270.1 | 49.5 | 5.048
1270.2 | 49.5 | 5.048
1270.3 | 49.5 | 5.048
1270.4 | 49.5 | 5.048
1270.5 | 49.5 | 5.048
1270.6 | 49.5 | 5.048
1270.7 | 49.5 | 5.048
1270.8 | 49.5 | 5.048
1270.9 | 49.5 | 5.048
1271 | 49.5 | 5.048
1271.1 | 49.5 | 5.048
1271.2 | 49.5 | 5.048
1271.3 | 49.5 | 5.048
1271.4 | 49.5 | 5.048
1271.5 | 49.5 | 5.048
1271.6 | 49.5 | 5.048
1271.7 | 49.5 | 5.048
1271.8 | 49.5 | 5.048
1271.9 | 49.5 | 5.048
1272 | 49.5 | 5.048
1272.1 | 49.5 | 5.048
1272.2 | 49.5 | 5.048
1272.3 | 49.5 | 5.048
1272.4 | 49.5 | 5.048
1272.5 | 49.5 | 5.048
1272.6 | 49.5 | 5.048
1272.7 | 49.5 | 5.048
1272.8 | 49.5 | 5.048
1272.9 | 49.5 | 5.048
1273 | 49.5 | 5.048
1273.1 | 49.5 | 5.048
1273.2 | 49.5 | 5.048
1273.3 | 49.5 | 5.048
1273.4 | 49.5 | 5.048
1273.5 | 49.5 | 5.048
1273.6 | 49.5 | 5.048
1273.7 | 49.5 | 5.048
1273.8 | 49.5 | 5.048
1273.9 | 49.5 | 5.048
1274 | 49.5 | 5.048
1274.1 | 49.5 | 5.048
1274.2 | 49.5 | 5.048
1274.3 | 49.5 | 5.048
1274.4 | 49.5 | 5.048
1274.5 | 49.5 | 5.048
1274.6 | 49.5 | 5.048
1274.7 | 49.5 | 5.048
1274.8 | 49.5 | 5.048
1274.9 | 49.5 | 5.048
1275 | 49.5 | 5.048
1275.1 | 49.5 | 5.048
1275.2 | 49.5 | 5.048
1275.3 | 49.5 | 5.048
1275.4 | 49.5 | 5.048
1275.5 | 49.5 | 5.048
1275.6 | 49.5 | 5.048
1275.7 | 49.5 | 5.048
1275.8 | 49.5 | 5.048
1275.9 | 49.5 | 5.048
1276 | 49.5 | 5.048
1276.1 | 49.5 | 5.048
1276.2 | 49.5 | 5.048
1276.3 | 49.5 | 5.048
1276.4 | 49.5 | 5.048
1276.5 | 49.5 | 5.048
1276.6 | 49.5 | 5.048
1276.7 | 49.5 | 5.048
1276.8 | 49.5 | 5.048
1276.9 | 49.5 | 5.048
1277 | 49.5 | 5.048
1277.1 | 49.5 | 5.048
1277.2 | 49.5 | 5.048
1277.3 | 49.5 | 5.048
1277.4 | 49.5 | 5.048
1277.5 | 49.5 | 5.048
1277.6 | 49.5 | 5.048
1277.7 | 49.5 | 5.048
1277.8 | 49.5 | 5.048
1277.9 | 49.5 | 5.048
1278 | 49.5 | 5.048
1278.1 | 49.5 | 5.048
1278.2 | 49.5 | 5.048
1278.3 | 49.5 | 5.048
1278.4 | 49.5 | 5.048
1278.5 | 49.5 | 5.048
1278.6 | 49.5 | 5.048
1278.7 | 49.5 | 5.048
1278.8 | 49.5 | 5.048
1278.9 | 49.5 | 5.048
1279 | 49.5 | 5.048
1279.1 | 49.5 | 5.048
1279.2 | 49.5 | 5.048
1279.3 | 49.5 | 5.048
1279.4 | 49.5 | 5.048
1279.5 | 49.5 | 5.048
1279.6 | 49.5 | 5.048
1279.7 | 49.5 | 5.048
1279.8 | 49.5 | 5.048
1279.9 | 49.5 | 5.048
1280 | 49.5 | 5.048
1280.1 | 49.5 | 5.048
1280.2 | 49.5 | 5.048
1280.3 | 49.5 | 5.048
1280.4 | 49.5 | 5.048
1280.5 | 49.5 | 5.048
1280.6 | 49.5 | 5.048
1280.7 | 49.5 | 5.048
1280.8 | 49.5 | 5.048
1280.9 | 49.5 | 5.048
1281 | 49.5 | 5.048
1281.1 | 49.5 | 5.048
1281.2 | 49.5 | 5.048
1281.3 | 49.5 | 5.048
1281.4 | 49.5 | 5.048
1281.5 | 49.5 | 5.048
1281.6 | 49.5 | 5.048
1281.7 | 49.5 | 5.048
1281.8 | 49.5 | 5.048
1281.9 | 49.5 | 5.048
1282 | 49.5 | 5.048
1282.1 | 49.5 | 5.048
1282.2 | 49.5 | 5.048
1282.3 | 49.5 | 5.048
1282.4 | 49.5 | 5.048
1282.5 | 49.5 | 5.048
1282.6 | 49.5 | 5.048
1282.7 | 49.5 | 5.048
1282.8 | 49.5 | 5.048
1282.9 | 49.5 | 5.048
1283 | 49.5 | 5.048
1283.1 | 49.5 | 5.048
1283.2 | 49.5 | 5.048
1283.3 | 49.5 | 5.048
1283.4 | 49.5 | 5.048
1283.5 | 49.5 | 5.048
1283.6 | 49.5 | 5.048
1283.7 | 49.5 | 5.048
1283.8 | 49.5 | 5.048
1283.9 | 49.5 | 5.048
1284 | 49.5 | 5.048
1284.1 | 49.5 | 5.048
1284.2 | 49.5 | 5.048
1284.3 | 49.5 | 5.048
1284.4 | 49.5 | 5.048
1284.5 | 49.5 | 5.048
1284.6 | 49.5 | 5.048
1284.7 | 49.5 | 5.048
1284.8 | 49.5 | 5.048
1284.9 | 49.5 | 5.048
1285 | 49.5 | 5.048
1285.1 | 49.5 | 5.048
1285.2 | 49.5 | 5.049
1285.3 | 49.5 | 5.049
1285.4 | 49.5 | 5.049
1285.5 | 49.5 | 5.049
1285.6 | 49.5 | 5.049
1285.7 | 49.5 | 5.049
1285.8 | 49.5 | 5.049
1285.9 | 49.5 | 5.049
1286 | 49.5 | 5.049
1286.1 | 49.5 | 5.049
1286.2 | 49.5 | 5.049
1286.3 | 49.5 | 5.049
1286.4 | 49.5 | 5.049
1286.5 | 49.5 | 5.049
1286.6 | 49.5 | 5.049
1286.7 | 49.5 | 5.049
1286.8 | 49.5 | 5.049
1286.9 | 49.5 | 5.049
1287 | 49.5 | 5.049
1287.1 | 49.5 | 5.049
1287.2 | 49.5 | 5.049
1287.3 | 49.5 | 5.049
1287.4 | 49.5 | 5.049
1287.5 | 49.5 | 5.048
1287.6 | 49.5 | 5.048
1287.7 | 49.5 | 5.048
1287.8 | 49.5 | 5.048
1287.9 | 49.5 | 5.048
1288 | 49.5 | 5.048
1288.1 | 49.5 | 5.048
1288.2 | 49.5 | 5.048
1288.3 | 49.5 | 5.048
1288.4 | 49.5 | 5.048
1288.5 | 49.5 | 5.048
1288.6 | 49.5 | 5.048
1288.7 | 49.5 | 5.048
1288.8 | 49.5 | 5.048
1288.9 | 49.5 | 5.048
1289 | 49.5 | 5.048
1289.1 | 49.5 | 5.048
1289.2 | 49.5 | 5.048
1289.3 | 49.5 | 5.048
1289.4 | 49.5 | 5.048
1289.5 | 49.5 | 5.048
1289.6 | 49.5 | 5.048
1289.7 | 49.5 | 5.048
1289.8 | 49.5 | 5.048
1289.9 | 49.5 | 5.048
1290 | 49.5 | 5.048
1290.1 | 49.5 | 5.048
1290.2 | 49.5 | 5.048
1290.3 | 49.5 | 5.048
1290.4 | 49.5 | 5.048
1290.5 | 49.5 | 5.048
1290.6 | 49.5 | 5.048
1290.7 | 49.5 | 5.048
1290.8 | 49.5 | 5.048
1290.9 | 49.5 | 5.048
1291 | 49.5 | 5.048
1291.1 | 49.5 | 5.048
1291.2 | 49.5 | 5.048
1291.3 | 49.5 | 5.048
1291.4 | 49.5 | 5.048
1291.5 | 49.5 | 5.048
1291.6 | 49.5 | 5.048
1291.7 | 49.5 | 5.048
1291.8 | 49.5 | 5.048
1291.9 | 49.5 | 5.048
1292 | 49.5 | 5.048
1292.1 | 49.5 | 5.048
1292.2 | 49.5 | 5.048
1292.3 | 49.5 | 5.048
1292.4 | 49.5 | 5.048
1292.5 | 49.5 | 5.048
1292.6 | 49.5 | 5.048
1292.7 | 49.5 | 5.048
1292.8 | 49.5 | 5.048
1292.9 | 49.5 | 5.048
1293 | 49.5 | 5.048
1293.1 | 49.5 | 5.048
1293.2 | 49.5 | 5.048
1293.3 | 49.5 | 5.048
1293.4 | 49.5 | 5.048
1293.5 | 49.5 | 5.048
1293.6 | 49.5 | 5.048
1293.7 | 49.5 | 5.048
1293.8 | 49.5 | 5.048
1293.9 | 49.5 | 5.048
1294 | 49.5 | 5.048
1294.1 | 49.5 | 5.048
1294.2 | 49.5 | 5.048
1294.3 | 49.5 | 5.048
1294.4 | 49.5 | 5.048
1294.5 | 49.5 | 5.048
1294.6 | 49.5 | 5.048
1294.7 | 49.5 | 5.048
1294.8 | 49.5 | 5.048
1294.9 | 49.5 | 5.048
1295 | 49.5 | 5.048
1295.1 | 49.5 | 5.048
1295.2 | 49.5 | 5.048
1295.3 | 49.5 | 5.048
1295.4 | 49.5 | 5.048
1295.5 | 49.5 | 5.048
1295.6 | 49.5 | 5.048
1295.7 | 49.5 | 5.048
1295.8 | 49.5 | 5.048
1295.9 | 49.5 | 5.048
1296 | 49.5 | 5.048
1296.1 | 49.5 | 5.048
1296.2 | 49.5 | 5.048
1296.3 | 49.5 | 5.048
1296.4 | 49.5 | 5.048
1296.5 | 49.5 | 5.048
1296.6 | 49.5 | 5.048
1296.7 | 49.5 | 5.048
1296.8 | 49.5 | 5.048
1296.9 | 49.5 | 5.048
1297 | 49.5 | 5.048
1297.1 | 49.5 | 5.048
1297.2 | 49.5 | 5.048
1297.3 | 49.5 | 5.048
1297.4 | 49.5 | 5.048
1297.5 | 49.5 | 5.048
1297.6 | 49.5 | 5.048
1297.7 | 49.5 | 5.048
1297.8 | 49.5 | 5.048
1297.9 | 49.5 | 5.048
1298 | 49.5 | 5.048
1298.1 | 49.5 | 5.048
1298.2 | 49.5 | 5.048
1298.3 | 49.5 | 5.048
1298.4 | 49.5 | 5.048
1298.5 | 49.5 | 5.048
1298.6 | 49.5 | 5.048
1298.7 | 49.5 | 5.048
1298.8 | 49.5 | 5.048
1298.9 | 49.5 | 5.048
1299 | 49.5 | 5.048
1299.1 | 49.5 | 5.048
1299.2 | 49.5 | 5.048
1299.3 | 49.5 | 5.048
1299.4 | 49.5 | 5.048
1299.5 | 49.5 | 5.048
1299.6 | 49.5 | 5.048
1299.7 | 49.5 | 5.048
1299.8 | 49.5 | 5.048
1299.9 | 49.5 | 5.048
1300 | 49.5 | 5.048
1300.1 | 49.5 | 5.048
1300.2 | 49.5 | 5.048
1300.3 | 49.5 | 5.048
1300.4 | 49.5 | 5.048
1300.5 | 49.5 | 5.048
1300.6 | 49.5 | 5.048
1300.7 | 49.5 | 5.048
1300.8 | 49.5 | 5.048
1300.9 | 49.5 | 5.048
1301 | 49.5 | 5.048
1301.1 | 49.5 | 5.048
1301.2 | 49.5 | 5.048
1301.3 | 49.5 | 5.048
1301.4 | 49.5 | 5.048
1301.5 | 49.5 | 5.048
1301.6 | 49.5 | 5.048
1301.7 | 49.5 | 5.048
1301.8 | 49.5 | 5.048
1301.9 | 49.5 | 5.048
1302 | 49.5 | 5.048
1302.1 | 49.5 | 5.048
1302.2 | 49.5 | 5.048
1302.3 | 49.5 | 5.048
1302.4 | 49.5 | 5.048
1302.5 | 49.5 | 5.048
1302.6 | 49.5 | 5.048
1302.7 | 49.5 | 5.048
1302.8 | 49.5 | 5.048
1302.9 | 49.5 | 5.048
1303 | 49.5 | 5.048
1303.1 | 49.5 | 5.048
1303.2 | 49.5 | 5.048
1303.3 | 49.5 | 5.048
1303.4 | 49.5 | 5.048
1303.5 | 49.5 | 5.048
1303.6 | 49.5 | 5.048
1303.7 | 49.5 | 5.048
1303.8 | 49.5 | 5.048
1303.9 | 49.5 | 5.048
1304 | 49.5 | 5.048
1304.1 | 49.5 | 5.048
1304.2 | 49.5 | 5.048
1304.3 | 49.5 | 5.048
1304.4 | 49.5 | 5.048
1304.5 | 49.5 | 5.048
1304.6 | 49.5 | 5.048
1304.7 | 49.5 | 5.048
1304.8 | 49.5 | 5.048
1304.9 | 49.5 | 5.048
1305 | 49.5 | 5.048
1305.1 | 49.5 | 5.048
1305.2 | 49.5 | 5.048
1305.3 | 49.5 | 5.048
1305.4 | 49.5 | 5.048
1305.5 | 49.5 | 5.048
1305.6 | 49.5 | 5.048
1305.7 | 49.5 | 5.048
1305.8 | 49.5 | 5.048
1305.9 | 49.5 | 5.048
1306 | 49.5 | 5.048
1306.1 | 49.5 | 5.048
1306.2 | 49.5 | 5.048
1306.3 | 49.5 | 5.048
1306.4 | 49.5 | 5.048
1306.5 | 49.5 | 5.048
1306.6 | 49.5 | 5.048
1306.7 | 49.5 | 5.048
1306.8 | 49.5 | 5.048
1306.9 | 49.5 | 5.048
1307 | 49.5 | 5.048
1307.1 | 49.5 | 5.048
1307.2 | 49.5 | 5.048
1307.3 | 49.5 | 5.048
1307.4 | 49.5 | 5.048
1307.5 | 49.5 | 5.048
1307.6 | 49.5 | 5.048
1307.7 | 49.5 | 5.048
1307.8 | 49.5 | 5.048
1307.9 | 49.5 | 5.048
1308 | 49.5 | 5.048
1308.1 | 49.5 | 5.048
1308.2 | 49.5 | 5.048
1308.3 | 49.5 | 5.048
1308.4 | 49.5 | 5.048
1308.5 | 49.5 | 5.048
1308.6 | 49.5 | 5.048
1308.7 | 49.5 | 5.048
1308.8 | 49.5 | 5.048
1308.9 | 49.5 | 5.048
1309 | 49.5 | 5.048
1309.1 | 49.5 | 5.048
1309.2 | 49.5 | 5.048
1309.3 | 49.5 | 5.048
1309.4 | 49.5 | 5.048
1309.5 | 49.5 | 5.048
1309.6 | 49.5 | 5.048
1309.7 | 49.5 | 5.048
1309.8 | 49.5 | 5.048
1309.9 | 49.5 | 5.048
1310 | 49.5 | 5.048
1310.1 | 49.5 | 5.048
1310.2 | 49.5 | 5.048
1310.3 | 49.5 | 5.048
1310.4 | 49.5 | 5.048
1310.5 | 49.5 | 5.048
1310.6 | 49.5 | 5.048
1310.7 | 49.5 | 5.048
1310.8 | 49.5 | 5.048
1310.9 | 49.5 | 5.048
1311 | 49.5 | 5.048
1311.1 | 49.5 | 5.048
1311.2 | 49.5 | 5.048
1311.3 | 49.5 | 5.048
1311.4 | 49.5 | 5.048
1311.5 | 49.5 | 5.048
1311.6 | 49.5 | 5.048
1311.7 | 49.5 | 5.048
1311.8 | 49.5 | 5.048
1311.9 | 49.5 | 5.048
1312 | 49.5 | 5.048
1312.1 | 49.5 | 5.048
1312.2 | 49.5 | 5.048
1312.3 | 49.5 | 5.048
1312.4 | 49.5 | 5.048
1312.5 | 49.5 | 5.048
1312.6 | 49.5 | 5.048
1312.7 | 49.5 | 5.048
1312.8 | 49.5 | 5.048
1312.9 | 49.5 | 5.048
1313 | 49.5 | 5.048
1313.1 | 49.5 | 5.048
1313.2 | 49.5 | 5.048
1313.3 | 49.5 | 5.048
1313.4 | 49.5 | 5.048
1313.5 | 49.5 | 5.048
1313.6 | 49.5 | 5.048
1313.7 | 49.5 | 5.048
1313.8 | 49.5 | 5.048
1313.9 | 49.5 | 5.048
1314 | 49.5 | 5.048
1314.1 | 49.5 | 5.048
1314.2 | 49.5 | 5.048
1314.3 | 49.5 | 5.048
1314.4 | 49.5 | 5.048
1314.5 | 49.5 | 5.048
1314.6 | 49.5 | 5.048
1314.7 | 49.5 | 5.048
1314.8 | 49.5 | 5.048
1314.9 | 49.5 | 5.048
1315 | 49.5 | 5.048
1315.1 | 49.5 | 5.048
1315.2 | 49.5 | 5.048
1315.3 | 49.5 | 5.048
1315.4 | 49.5 | 5.048
1315.5 | 49.5 | 5.048
1315.6 | 49.5 | 5.048
1315.7 | 49.5 | 5.048
1315.8 | 49.5 | 5.048
1315.9 | 49.5 | 5.048
1316 | 49.5 | 5.048
1316.1 | 49.5 | 5.048
1316.2 | 49.5 | 5.048
1316.3 | 49.5 | 5.048
1316.4 | 49.5 | 5.048
1316.5 | 49.5 | 5.048
1316.6 | 49.5 | 5.048
1316.7 | 49.5 | 5.048
1316.8 | 49.5 | 5.048
1316.9 | 49.5 | 5.048
1317 | 49.5 | 5.048
1317.1 | 49.5 | 5.048
1317.2 | 49.5 | 5.048
1317.3 | 49.5 | 5.048
1317.4 | 49.5 | 5.048
1317.5 | 49.5 | 5.048
1317.6 | 49.5 | 5.048
1317.7 | 49.5 | 5.048
1317.8 | 49.5 | 5.048
1317.9 | 49.5 | 5.048
1318 | 49.5 | 5.048
1318.1 | 49.5 | 5.049
1318.2 | 49.5 | 5.049
1318.3 | 49.5 | 5.049
1318.4 | 49.5 | 5.049
1318.5 | 49.5 | 5.049
1318.6 | 49.5 | 5.049
1318.7 | 49.5 | 5.049
1318.8 | 49.5 | 5.049
1318.9 | 49.5 | 5.049
1319 | 49.5 | 5.049
1319.1 | 49.5 | 5.049
1319.2 | 49.5 | 5.049
1319.3 | 49.5 | 5.049
1319.4 | 49.5 | 5.048
1319.5 | 49.5 | 5.048
1319.6 | 49.5 | 5.048
1319.7 | 49.5 | 5.048
1319.8 | 49.5 | 5.048
1319.9 | 49.5 | 5.048
1320 | 49.5 | 5.048
1320.1 | 49.5 | 5.048
1320.2 | 49.5 | 5.048
1320.3 | 49.5 | 5.048
1320.4 | 49.5 | 5.048
1320.5 | 49.5 | 5.048
1320.6 | 49.5 | 5.048
1320.7 | 49.5 | 5.048
1320.8 | 49.5 | 5.048
1320.9 | 49.5 | 5.048
1321 | 49.5 | 5.048
1321.1 | 49.5 | 5.048
1321.2 | 49.5 | 5.048
1321.3 | 49.5 | 5.048
1321.4 | 49.5 | 5.048
1321.5 | 49.5 | 5.048
1321.6 | 49.5 | 5.048
1321.7 | 49.5 | 5.048
1321.8 | 49.5 | 5.048
1321.9 | 49.5 | 5.048
1322 | 49.5 | 5.048
1322.1 | 49.5 | 5.048
1322.2 | 49.5 | 5.048
1322.3 | 49.5 | 5.048
1322.4 | 49.5 | 5.048
1322.5 | 49.5 | 5.048
1322.6 | 49.5 | 5.048
1322.7 | 49.5 | 5.048
1322.8 | 49.5 | 5.048
1322.9 | 49.5 | 5.048
1323 | 49.5 | 5.048
1323.1 | 49.5 | 5.048
1323.2 | 49.5 | 5.048
1323.3 | 49.5 | 5.048
1323.4 | 49.5 | 5.048
1323.5 | 49.5 | 5.048
1323.6 | 49.5 | 5.048
1323.7 | 49.5 | 5.048
1323.8 | 49.5 | 5.048
1323.9 | 49.5 | 5.048
1324 | 49.5 | 5.048
1324.1 | 49.5 | 5.048
1324.2 | 49.5 | 5.048
1324.3 | 49.5 | 5.048
1324.4 | 49.5 | 5.048
1324.5 | 49.5 | 5.048
1324.6 | 49.5 | 5.048
1324.7 | 49.5 | 5.048
1324.8 | 49.5 | 5.048
1324.9 | 49.5 | 5.048
1325 | 49.5 | 5.048
1325.1 | 49.5 | 5.048
1325.2 | 49.5 | 5.048
1325.3 | 49.5 | 5.048
1325.4 | 49.5 | 5.048
1325.5 | 49.5 | 5.048
1325.6 | 49.5 | 5.048
1325.7 | 49.5 | 5.048
1325.8 | 49.5 | 5.048
1325.9 | 49.5 | 5.048
1326 | 49.5 | 5.048
1326.1 | 49.5 | 5.048
1326.2 | 49.5 | 5.048
1326.3 | 49.5 | 5.048
1326.4 | 49.5 | 5.048
1326.5 | 49.5 | 5.048
1326.6 | 49.5 | 5.048
1326.7 | 49.5 | 5.048
1326.8 | 49.5 | 5.048
1326.9 | 49.5 | 5.048
1327 | 49.5 | 5.048
1327.1 | 49.5 | 5.048
1327.2 | 49.5 | 5.048
1327.3 | 49.5 | 5.048
1327.4 | 49.5 | 5.048
1327.5 | 49.5 | 5.048
1327.6 | 49.5 | 5.048
1327.7 | 49.5 | 5.048
1327.8 | 49.5 | 5.048
1327.9 | 49.5 | 5.048
1328 | 49.5 | 5.048
1328.1 | 49.5 | 5.048
1328.2 | 49.5 | 5.048
1328.3 | 49.5 | 5.048
1328.4 | 49.5 | 5.048
1328.5 | 49.5 | 5.048
1328.6 | 49.5 | 5.048
1328.7 | 49.5 | 5.048
1328.8 | 49.5 | 5.048
1328.9 | 49.5 | 5.048
1329 | 49.5 | 5.048
1329.1 | 49.5 | 5.048
1329.2 | 49.5 | 5.048
1329.3 | 49.5 | 5.048
1329.4 | 49.5 | 5.048
1329.5 | 49.5 | 5.048
1329.6 | 49.5 | 5.048
1329.7 | 49.5 | 5.048
1329.8 | 49.5 | 5.048
1329.9 | 49.5 | 5.048
1330 | 49.5 | 5.048
1330.1 | 49.5 | 5.048
1330.2 | 49.5 | 5.048
1330.3 | 49.5 | 5.048
1330.4 | 49.5 | 5.048
1330.5 | 49.5 | 5.048
1330.6 | 49.5 | 5.048
1330.7 | 49.5 | 5.048
1330.8 | 49.5 | 5.048
1330.9 | 49.5 | 5.048
1331 | 49.5 | 5.048
1331.1 | 49.5 | 5.048
1331.2 | 49.5 | 5.048
1331.3 | 49.5 | 5.048
1331.4 | 49.5 | 5.048
1331.5 | 49.5 | 5.048
1331.6 | 49.5 | 5.048
1331.7 | 49.5 | 5.048
1331.8 | 49.5 | 5.048
1331.9 | 49.5 | 5.048
1332 | 49.5 | 5.048
1332.1 | 49.5 | 5.048
1332.2 | 49.5 | 5.048
1332.3 | 49.5 | 5.048
1332.4 | 49.5 | 5.048
1332.5 | 49.5 | 5.048
1332.6 | 49.5 | 5.048
1332.7 | 49.5 | 5.048
1332.8 | 49.5 | 5.048
1332.9 | 49.5 | 5.048
1333 | 49.5 | 5.048
1333.1 | 49.5 | 5.048
1333.2 | 49.5 | 5.048
1333.3 | 49.5 | 5.048
1333.4 | 49.5 | 5.048
1333.5 | 49.5 | 5.048
1333.6 | 49.5 | 5.048
1333.7 | 49.5 | 5.048
1333.8 | 49.5 | 5.048
1333.9 | 49.5 | 5.048
1334 | 49.5 | 5.048
1334.1 | 49.5 | 5.048
1334.2 | 49.5 | 5.048
1334.3 | 49.5 | 5.048
1334.4 | 49.5 | 5.048
1334.5 | 49.5 | 5.048
1334.6 | 49.5 | 5.048
1334.7 | 49.5 | 5.048
1334.8 | 49.5 | 5.048
1334.9 | 49.5 | 5.048
1335 | 49.5 | 5.048
1335.1 | 49.5 | 5.048
1335.2 | 49.5 | 5.048
1335.3 | 49.5 | 5.048
1335.4 | 49.5 | 5.048
1335.5 | 49.5 | 5.048
1335.6 | 49.5 | 5.048
1335.7 | 49.5 | 5.048
1335.8 | 49.5 | 5.048
1335.9 | 49.5 | 5.048
1336 | 49.5 | 5.048
1336.1 | 49.5 | 5.048
1336.2 | 49.5 | 5.048
1336.3 | 49.5 | 5.048
1336.4 | 49.5 | 5.048
1336.5 | 49.5 | 5.048
1336.6 | 49.5 | 5.048
1336.7 | 49.5 | 5.048
1336.8 | 49.5 | 5.048
1336.9 | 49.5 | 5.048
1337 | 49.5 | 5.048
1337.1 | 49.5 | 5.048
1337.2 | 49.5 | 5.048
1337.3 | 49.5 | 5.048
1337.4 | 49.5 | 5.048
1337.5 | 49.5 | 5.048
1337.6 | 49.5 | 5.048
1337.7 | 49.5 | 5.048
1337.8 | 49.5 | 5.048
1337.9 | 49.5 | 5.048
1338 | 49.5 | 5.048
1338.1 | 49.5 | 5.048
1338.2 | 49.5 | 5.048
1338.3 | 49.5 | 5.048
1338.4 | 49.5 | 5.048
1338.5 | 49.5 | 5.048
1338.6 | 49.5 | 5.048
1338.7 | 49.5 | 5.048
1338.8 | 49.5 | 5.048
1338.9 | 49.5 | 5.048
1339 | 49.5 | 5.048
1339.1 | 49.5 | 5.048
1339.2 | 49.5 | 5.048
1339.3 | 49.5 | 5.048
1339.4 | 49.5 | 5.048
1339.5 | 49.5 | 5.048
1339.6 | 49.5 | 5.048
1339.7 | 49.5 | 5.048
1339.8 | 49.5 | 5.048
1339.9 | 49.5 | 5.048
1340 | 49.5 | 5.048
1340.1 | 49.5 | 5.048
1340.2 | 49.5 | 5.048
1340.3 | 49.5 | 5.048
1340.4 | 49.5 | 5.048
1340.5 | 49.5 | 5.048
1340.6 | 49.5 | 5.048
1340.7 | 49.5 | 5.048
1340.8 | 49.5 | 5.048
1340.9 | 49.5 | 5.048
1341 | 49.5 | 5.048
1341.1 | 49.5 | 5.048
1341.2 | 49.5 | 5.048
1341.3 | 49.5 | 5.048
1341.4 | 49.5 | 5.048
1341.5 | 49.5 | 5.048
1341.6 | 49.5 | 5.048
1341.7 | 49.5 | 5.048
1341.8 | 49.5 | 5.048
1341.9 | 49.5 | 5.048
1342 | 49.5 | 5.048
1342.1 | 49.5 | 5.048
1342.2 | 49.5 | 5.048
1342.3 | 49.5 | 5.048
1342.4 | 49.5 | 5.048
1342.5 | 49.5 | 5.048
1342.6 | 49.5 | 5.048
1342.7 | 49.5 | 5.048
1342.8 | 49.5 | 5.048
1342.9 | 49.5 | 5.048
1343 | 49.5 | 5.048
1343.1 | 49.5 | 5.048
1343.2 | 49.5 | 5.048
1343.3 | 49.5 | 5.048
1343.4 | 49.5 | 5.048
1343.5 | 49.5 | 5.048
1343.6 | 49.5 | 5.048
1343.7 | 49.5 | 5.048
1343.8 | 49.5 | 5.048
1343.9 | 49.5 | 5.048
1344 | 49.5 | 5.048
1344.1 | 49.5 | 5.048
1344.2 | 49.5 | 5.048
1344.3 | 49.5 | 5.048
1344.4 | 49.5 | 5.048
1344.5 | 49.5 | 5.048
1344.6 | 49.5 | 5.048
1344.7 | 49.5 | 5.048
1344.8 | 49.5 | 5.048
1344.9 | 49.5 | 5.048
1345 | 49.5 | 5.048
1345.1 | 49.5 | 5.048
1345.2 | 49.5 | 5.048
1345.3 | 49.5 | 5.048
1345.4 | 49.5 | 5.048
1345.5 | 49.5 | 5.048
1345.6 | 49.5 | 5.048
1345.7 | 49.5 | 5.048
1345.8 | 49.5 | 5.048
1345.9 | 49.5 | 5.048
1346 | 49.5 | 5.048
1346.1 | 49.5 | 5.048
1346.2 | 49.5 | 5.048
1346.3 | 49.5 | 5.048
1346.4 | 49.5 | 5.048
1346.5 | 49.5 | 5.048
1346.6 | 49.5 | 5.048
1346.7 | 49.5 | 5.048
1346.8 | 49.5 | 5.048
1346.9 | 49.5 | 5.048
1347 | 49.5 | 5.048
1347.1 | 49.5 | 5.048
1347.2 | 49.5 | 5.048
1347.3 | 49.5 | 5.048
1347.4 | 49.5 | 5.048
1347.5 | 49.5 | 5.048
1347.6 | 49.5 | 5.048
1347.7 | 49.5 | 5.048
1347.8 | 49.5 | 5.048
1347.9 | 49.5 | 5.048
1348 | 49.5 | 5.048
1348.1 | 49.5 | 5.048
1348.2 | 49.5 | 5.048
1348.3 | 49.5 | 5.048
1348.4 | 49.5 | 5.048
1348.5 | 49.5 | 5.048
1348.6 | 49.5 | 5.048
1348.7 | 49.5 | 5.048
1348.8 | 49.5 | 5.048
1348.9 | 49.5 | 5.048
1349 | 49.5 | 5.048
1349.1 | 49.5 | 5.048
1349.2 | 49.5 | 5.048
1349.3 | 49.5 | 5.048
1349.4 | 49.5 | 5.048
1349.5 | 49.5 | 5.048
1349.6 | 49.5 | 5.048
1349.7 | 49.5 | 5.048
1349.8 | 49.5 | 5.048
1349.9 | 49.5 | 5.048
1350 | 49.5 | 5.048
1350.1 | 49.5 | 5.048
1350.2 | 49.5 | 5.048
1350.3 | 49.5 | 5.048
1350.4 | 49.5 | 5.048
1350.5 | 49.5 | 5.049
1350.6 | 49.5 | 5.049
1350.7 | 49.5 | 5.049
1350.8 | 49.5 | 5.049
1350.9 | 49.5 | 5.049
1351 | 49.5 | 5.049
1351.1 | 49.5 | 5.049
1351.2 | 49.5 | 5.049
1351.3 | 49.5 | 5.049
1351.4 | 49.5 | 5.049
1351.5 | 49.5 | 5.049
1351.6 | 49.5 | 5.049
1351.7 | 49.5 | 5.048
1351.8 | 49.5 | 5.048
1351.9 | 49.5 | 5.048
1352 | 49.5 | 5.048
1352.1 | 49.5 | 5.048
1352.2 | 49.5 | 5.048
1352.3 | 49.5 | 5.048
1352.4 | 49.5 | 5.048
1352.5 | 49.5 | 5.048
1352.6 | 49.5 | 5.048
1352.7 | 49.5 | 5.048
1352.8 | 49.5 | 5.048
1352.9 | 49.5 | 5.048
1353 | 49.5 | 5.048
1353.1 | 49.5 | 5.048
1353.2 | 49.5 | 5.048
1353.3 | 49.5 | 5.048
1353.4 | 49.5 | 5.048
1353.5 | 49.5 | 5.048
1353.6 | 49.5 | 5.048
1353.7 | 49.5 | 5.048
1353.8 | 49.5 | 5.048
1353.9 | 49.5 | 5.048
1354 | 49.5 | 5.048
1354.1 | 49.5 | 5.048
1354.2 | 49.5 | 5.048
1354.3 | 49.5 | 5.048
1354.4 | 49.5 | 5.048
1354.5 | 49.5 | 5.048
1354.6 | 49.5 | 5.048
1354.7 | 49.5 | 5.048
1354.8 | 49.5 | 5.048
1354.9 | 49.5 | 5.048
1355 | 49.5 | 5.048
1355.1 | 49.5 | 5.048
1355.2 | 49.5 | 5.048
1355.3 | 49.5 | 5.048
1355.4 | 49.5 | 5.048
1355.5 | 49.5 | 5.048
1355.6 | 49.5 | 5.048
1355.7 | 49.5 | 5.048
1355.8 | 49.5 | 5.048
1355.9 | 49.5 | 5.048
1356 | 49.5 | 5.048
1356.1 | 49.5 | 5.048
1356.2 | 49.5 | 5.048
1356.3 | 49.5 | 5.048
1356.4 | 49.5 | 5.048
1356.5 | 49.5 | 5.048
1356.6 | 49.5 | 5.048
1356.7 | 49.5 | 5.048
1356.8 | 49.5 | 5.048
1356.9 | 49.5 | 5.048
1357 | 49.5 | 5.048
1357.1 | 49.5 | 5.048
1357.2 | 49.5 | 5.048
1357.3 | 49.5 | 5.048
1357.4 | 49.5 | 5.048
1357.5 | 49.5 | 5.048
1357.6 | 49.5 | 5.048
1357.7 | 49.5 | 5.048
1357.8 | 49.5 | 5.048
1357.9 | 49.5 | 5.049
1358 | 49.5 | 5.049
1358.1 | 49.5 | 5.049
1358.2 | 49.5 | 5.049
1358.3 | 49.5 | 5.049
1358.4 | 49.5 | 5.049
1358.5 | 49.5 | 5.049
1358.6 | 49.5 | 5.049
1358.7 | 49.5 | 5.049
1358.8 | 49.5 | 5.049
1358.9 | 49.5 | 5.049
1359 | 49.5 | 5.048
1359.1 | 49.5 | 5.048
1359.2 | 49.5 | 5.048
1359.3 | 49.5 | 5.048
1359.4 | 49.5 | 5.048
1359.5 | 49.5 | 5.048
1359.6 | 49.5 | 5.048
1359.7 | 49.5 | 5.048
1359.8 | 49.5 | 5.048
1359.9 | 49.5 | 5.048
1360 | 49.5 | 5.048
1360.1 | 49.5 | 5.048
1360.2 | 49.5 | 5.048
1360.3 | 49.5 | 5.048
1360.4 | 49.5 | 5.048
1360.5 | 49.5 | 5.048
1360.6 | 49.5 | 5.048
1360.7 | 49.5 | 5.048
1360.8 | 49.5 | 5.048
1360.9 | 49.5 | 5.048
1361 | 49.5 | 5.048
1361.1 | 49.5 | 5.048
1361.2 | 49.5 | 5.048
1361.3 | 49.5 | 5.048
1361.4 | 49.5 | 5.048
1361.5 | 49.5 | 5.048
1361.6 | 49.5 | 5.048
1361.7 | 49.5 | 5.048
1361.8 | 49.5 | 5.048
1361.9 | 49.5 | 5.048
1362 | 49.5 | 5.048
1362.1 | 49.5 | 5.048
1362.2 | 49.5 | 5.048
1362.3 | 49.5 | 5.048
1362.4 | 49.5 | 5.048
1362.5 | 49.5 | 5.048
1362.6 | 49.5 | 5.048
1362.7 | 49.5 | 5.048
1362.8 | 49.5 | 5.048
1362.9 | 49.5 | 5.048
1363 | 49.5 | 5.048
1363.1 | 49.5 | 5.048
1363.2 | 49.5 | 5.048
1363.3 | 49.5 | 5.048
1363.4 | 49.5 | 5.048
1363.5 | 49.5 | 5.048
1363.6 | 49.5 | 5.048
1363.7 | 49.5 | 5.048
1363.8 | 49.5 | 5.048
1363.9 | 49.5 | 5.048
1364 | 49.5 | 5.048
1364.1 | 49.5 | 5.048
1364.2 | 49.5 | 5.048
1364.3 | 49.5 | 5.048
1364.4 | 49.5 | 5.048
1364.5 | 49.5 | 5.048
1364.6 | 49.5 | 5.048
1364.7 | 49.5 | 5.048
1364.8 | 49.5 | 5.048
1364.9 | 49.5 | 5.048
1365 | 49.5 | 5.048
1365.1 | 49.5 | 5.048
1365.2 | 49.5 | 5.048
1365.3 | 49.5 | 5.048
1365.4 | 49.5 | 5.048
1365.5 | 49.5 | 5.048
1365.6 | 49.5 | 5.048
1365.7 | 49.5 | 5.048
1365.8 | 49.5 | 5.048
1365.9 | 49.5 | 5.048
1366 | 49.5 | 5.048
1366.1 | 49.5 | 5.048
1366.2 | 49.5 | 5.048
1366.3 | 49.5 | 5.048
1366.4 | 49.5 | 5.048
1366.5 | 49.5 | 5.048
1366.6 | 49.5 | 5.048
1366.7 | 49.5 | 5.048
1366.8 | 49.5 | 5.048
1366.9 | 49.5 | 5.048
1367 | 49.5 | 5.048
1367.1 | 49.5 | 5.048
1367.2 | 49.5 | 5.048
1367.3 | 49.5 | 5.048
1367.4 | 49.5 | 5.048
1367.5 | 49.5 | 5.049
1367.6 | 49.5 | 5.049
1367.7 | 49.5 | 5.049
1367.8 | 49.5 | 5.049
1367.9 | 49.5 | 5.049
1368 | 49.5 | 5.049
1368.1 | 49.5 | 5.049
1368.2 | 49.5 | 5.049
1368.3 | 49.5 | 5.049
1368.4 | 49.5 | 5.049
1368.5 | 49.5 | 5.049
1368.6 | 49.5 | 5.049
1368.7 | 49.5 | 5.049
1368.8 | 49.5 | 5.049
1368.9 | 49.5 | 5.049
1369 | 49.5 | 5.049
1369.1 | 49.5 | 5.049
1369.2 | 49.5 | 5.049
1369.3 | 49.5 | 5.049
1369.4 | 49.5 | 5.049
1369.5 | 49.5 | 5.049
1369.6 | 49.5 | 5.048
1369.7 | 49.5 | 5.048
1369.8 | 49.5 | 5.048
1369.9 | 49.5 | 5.048
1370 | 49.5 | 5.048
1370.1 | 49.5 | 5.048
1370.2 | 49.5 | 5.048
1370.3 | 49.5 | 5.048
1370.4 | 49.5 | 5.048
1370.5 | 49.5 | 5.048
1370.6 | 49.5 | 5.048
1370.7 | 49.5 | 5.048
1370.8 | 49.5 | 5.048
1370.9 | 49.5 | 5.048
1371 | 49.5 | 5.048
1371.1 | 49.5 | 5.048
1371.2 | 49.5 | 5.048
1371.3 | 49.5 | 5.048
1371.4 | 49.5 | 5.048
1371.5 | 49.5 | 5.048
1371.6 | 49.5 | 5.048
1371.7 | 49.5 | 5.048
1371.8 | 49.5 | 5.048
1371.9 | 49.5 | 5.048
1372 | 49.5 | 5.048
1372.1 | 49.5 | 5.048
1372.2 | 49.5 | 5.048
1372.3 | 49.5 | 5.048
1372.4 | 49.5 | 5.048
1372.5 | 49.5 | 5.048
1372.6 | 49.5 | 5.048
1372.7 | 49.5 | 5.048
1372.8 | 49.5 | 5.048
1372.9 | 49.5 | 5.048
1373 | 49.5 | 5.048
1373.1 | 49.5 | 5.048
1373.2 | 49.5 | 5.048
1373.3 | 49.5 | 5.048
1373.4 | 49.5 | 5.048
1373.5 | 49.5 | 5.048
1373.6 | 49.5 | 5.048
1373.7 | 49.5 | 5.048
1373.8 | 49.5 | 5.048
1373.9 | 49.5 | 5.048
1374 | 49.5 | 5.048
1374.1 | 49.5 | 5.048
1374.2 | 49.5 | 5.048
1374.3 | 49.5 | 5.048
1374.4 | 49.5 | 5.048
1374.5 | 49.5 | 5.048
1374.6 | 49.5 | 5.048
1374.7 | 49.5 | 5.048
1374.8 | 49.5 | 5.048
1374.9 | 49.5 | 5.048
1375 | 49.5 | 5.048
1375.1 | 49.5 | 5.048
1375.2 | 49.5 | 5.048
1375.3 | 49.5 | 5.048
1375.4 | 49.5 | 5.048
1375.5 | 49.5 | 5.048
1375.6 | 49.5 | 5.048
1375.7 | 49.5 | 5.048
1375.8 | 49.5 | 5.048
1375.9 | 49.5 | 5.048
1376 | 49.5 | 5.048
1376.1 | 49.5 | 5.048
1376.2 | 49.5 | 5.048
1376.3 | 49.5 | 5.048
1376.4 | 49.5 | 5.048
1376.5 | 49.5 | 5.048
1376.6 | 49.5 | 5.048
1376.7 | 49.5 | 5.048
1376.8 | 49.5 | 5.048
1376.9 | 49.5 | 5.048
1377 | 49.5 | 5.048
1377.1 | 49.5 | 5.048
1377.2 | 49.5 | 5.048
1377.3 | 49.5 | 5.048
1377.4 | 49.5 | 5.048
1377.5 | 49.5 | 5.048
1377.6 | 49.5 | 5.048
1377.7 | 49.5 | 5.048
1377.8 | 49.5 | 5.048
1377.9 | 49.5 | 5.048
1378 | 49.5 | 5.048
1378.1 | 49.5 | 5.048
1378.2 | 49.5 | 5.048
1378.3 | 49.5 | 5.048
1378.4 | 49.5 | 5.048
1378.5 | 49.5 | 5.048
1378.6 | 49.5 | 5.048
1378.7 | 49.5 | 5.048
1378.8 | 49.5 | 5.048
1378.9 | 49.5 | 5.048
1379 | 49.5 | 5.048
1379.1 | 49.5 | 5.048
1379.2 | 49.5 | 5.048
1379.3 | 49.5 | 5.048
1379.4 | 49.5 | 5.048
1379.5 | 49.5 | 5.048
1379.6 | 49.5 | 5.048
1379.7 | 49.5 | 5.048
1379.8 | 49.5 | 5.048
1379.9 | 49.5 | 5.048
1380 | 49.5 | 5.048
1380.1 | 49.5 | 5.048
1380.2 | 49.5 | 5.048
1380.3 | 49.5 | 5.048
1380.4 | 49.5 | 5.048
1380.5 | 49.5 | 5.048
1380.6 | 49.5 | 5.048
1380.7 | 49.5 | 5.048
1380.8 | 49.5 | 5.048
1380.9 | 49.5 | 5.048
1381 | 49.5 | 5.048
1381.1 | 49.5 | 5.049
1381.2 | 49.5 | 5.049
1381.3 | 49.5 | 5.049
1381.4 | 49.5 | 5.049
1381.5 | 49.5 | 5.049
1381.6 | 49.5 | 5.049
1381.7 | 49.5 | 5.049
1381.8 | 49.5 | 5.049
1381.9 | 49.5 | 5.049
1382 | 49.5 | 5.049
1382.1 | 49.5 | 5.049
1382.2 | 49.5 | 5.049
1382.3 | 49.5 | 5.049
1382.4 | 49.5 | 5.049
1382.5 | 49.5 | 5.049
1382.6 | 49.5 | 5.049
1382.7 | 49.5 | 5.049
1382.8 | 49.5 | 5.049
1382.9 | 49.5 | 5.049
1383 | 49.5 | 5.049
1383.1 | 49.5 | 5.049
1383.2 | 49.5 | 5.049
1383.3 | 49.5 | 5.049
1383.4 | 49.5 | 5.049
1383.5 | 49.5 | 5.049
1383.6 | 49.5 | 5.048
1383.7 | 49.5 | 5.048
1383.8 | 49.5 | 5.048
1383.9 | 49.5 | 5.048
1384 | 49.5 | 5.048
1384.1 | 49.5 | 5.048
1384.2 | 49.5 | 5.048
1384.3 | 49.5 | 5.048
1384.4 | 49.5 | 5.048
1384.5 | 49.5 | 5.048
1384.6 | 49.5 | 5.048
1384.7 | 49.5 | 5.048
1384.8 | 49.5 | 5.048
1384.9 | 49.5 | 5.048
1385 | 49.5 | 5.048
1385.1 | 49.5 | 5.048
1385.2 | 49.5 | 5.048
1385.3 | 49.5 | 5.048
1385.4 | 49.5 | 5.048
1385.5 | 49.5 | 5.048
1385.6 | 49.5 | 5.048
1385.7 | 49.5 | 5.048
1385.8 | 49.5 | 5.048
1385.9 | 49.5 | 5.048
1386 | 49.5 | 5.048
1386.1 | 49.5 | 5.048
1386.2 | 49.5 | 5.048
1386.3 | 49.5 | 5.048
1386.4 | 49.5 | 5.048
1386.5 | 49.5 | 5.048
1386.6 | 49.5 | 5.048
1386.7 | 49.5 | 5.048
1386.8 | 49.5 | 5.048
1386.9 | 49.5 | 5.048
1387 | 49.5 | 5.048
1387.1 | 49.5 | 5.048
1387.2 | 49.5 | 5.048
1387.3 | 49.5 | 5.048
1387.4 | 49.5 | 5.048
1387.5 | 49.5 | 5.048
1387.6 | 49.5 | 5.048
1387.7 | 49.5 | 5.048
1387.8 | 49.5 | 5.048
1387.9 | 49.5 | 5.048
1388 | 49.5 | 5.048
1388.1 | 49.5 | 5.048
1388.2 | 49.5 | 5.048
1388.3 | 49.5 | 5.048
1388.4 | 49.5 | 5.048
1388.5 | 49.5 | 5.048
1388.6 | 49.5 | 5.048
1388.7 | 49.5 | 5.048
1388.8 | 49.5 | 5.048
1388.9 | 49.5 | 5.048
1389 | 49.5 | 5.048
1389.1 | 49.5 | 5.048
1389.2 | 49.5 | 5.048
1389.3 | 49.5 | 5.048
1389.4 | 49.5 | 5.048
1389.5 | 49.5 | 5.048
1389.6 | 49.5 | 5.048
1389.7 | 49.5 | 5.048
1389.8 | 49.5 | 5.048
1389.9 | 49.5 | 5.048
1390 | 49.5 | 5.048
1390.1 | 49.5 | 5.048
1390.2 | 49.5 | 5.048
1390.3 | 49.5 | 5.048
1390.4 | 49.5 | 5.048
1390.5 | 49.5 | 5.048
1390.6 | 49.5 | 5.048
1390.7 | 49.5 | 5.048
1390.8 | 49.5 | 5.048
1390.9 | 49.5 | 5.048
1391 | 49.5 | 5.048
1391.1 | 49.5 | 5.048
1391.2 | 49.5 | 5.048
1391.3 | 49.5 | 5.048
1391.4 | 49.5 | 5.048
1391.5 | 49.5 | 5.048
1391.6 | 49.5 | 5.048
1391.7 | 49.5 | 5.048
1391.8 | 49.5 | 5.048
1391.9 | 49.5 | 5.048
1392 | 49.5 | 5.048
1392.1 | 49.5 | 5.048
1392.2 | 49.5 | 5.048
1392.3 | 49.5 | 5.048
1392.4 | 49.5 | 5.048
1392.5 | 49.5 | 5.048
1392.6 | 49.5 | 5.048
1392.7 | 49.5 | 5.048
1392.8 | 49.5 | 5.048
1392.9 | 49.5 | 5.048
1393 | 49.5 | 5.048
1393.1 | 49.5 | 5.048
1393.2 | 49.5 | 5.048
1393.3 | 49.5 | 5.048
1393.4 | 49.5 | 5.048
1393.5 | 49.5 | 5.048
1393.6 | 49.5 | 5.048
1393.7 | 49.5 | 5.048
1393.8 | 49.5 | 5.048
1393.9 | 49.5 | 5.048
1394 | 49.5 | 5.048
1394.1 | 49.5 | 5.048
1394.2 | 49.5 | 5.048
1394.3 | 49.5 | 5.048
1394.4 | 49.5 | 5.048
1394.5 | 49.5 | 5.048
1394.6 | 49.5 | 5.048
1394.7 | 49.5 | 5.048
1394.8 | 49.5 | 5.048
1394.9 | 49.5 | 5.048
1395 | 49.5 | 5.048
1395.1 | 49.5 | 5.048
1395.2 | 49.5 | 5.048
1395.3 | 49.5 | 5.048
1395.4 | 49.5 | 5.048
1395.5 | 49.5 | 5.048
1395.6 | 49.5 | 5.048
1395.7 | 49.5 | 5.048
1395.8 | 49.5 | 5.048
1395.9 | 49.5 | 5.048
1396 | 49.5 | 5.048
1396.1 | 49.5 | 5.048
1396.2 | 49.5 | 5.048
1396.3 | 49.5 | 5.048
1396.4 | 49.5 | 5.048
1396.5 | 49.5 | 5.048
1396.6 | 49.5 | 5.048
1396.7 | 49.5 | 5.048
1396.8 | 49.5 | 5.048
1396.9 | 49.5 | 5.048
1397 | 49.5 | 5.048
1397.1 | 49.5 | 5.048
1397.2 | 49.5 | 5.048
1397.3 | 49.5 | 5.048
1397.4 | 49.5 | 5.048
1397.5 | 49.5 | 5.048
1397.6 | 49.5 | 5.048
1397.7 | 49.5 | 5.048
1397.8 | 49.5 | 5.048
1397.9 | 49.5 | 5.048
1398 | 49.5 | 5.048
1398.1 | 49.5 | 5.048
1398.2 | 49.5 | 5.048
1398.3 | 49.5 | 5.048
1398.4 | 49.5 | 5.048
1398.5 | 49.5 | 5.048
1398.6 | 49.5 | 5.048
1398.7 | 49.5 | 5.049
1398.8 | 49.5 | 5.049
1398.9 | 49.5 | 5.049
1399 | 49.5 | 5.049
1399.1 | 49.5 | 5.049
1399.2 | 49.5 | 5.049
1399.3 | 49.5 | 5.049
1399.4 | 49.5 | 5.049
1399.5 | 49.5 | 5.049
1399.6 | 49.5 | 5.049
1399.7 | 49.5 | 5.049
1399.8 | 49.5 | 5.049
1399.9 | 49.5 | 5.049
1400 | 49.5 | 5.049
1400.1 | 49.5 | 5.049
1400.2 | 49.5 | 5.049
1400.3 | 49.5 | 5.049
1400.4 | 49.5 | 5.049
1400.5 | 49.5 | 5.049
1400.6 | 49.5 | 5.049
1400.7 | 49.5 | 5.049
1400.8 | 49.5 | 5.049
1400.9 | 49.5 | 5.049
1401 | 49.5 | 5.048
1401.1 | 49.5 | 5.048
1401.2 | 49.5 | 5.048
1401.3 | 49.5 | 5.048
1401.4 | 49.5 | 5.048
1401.5 | 49.5 | 5.048
1401.6 | 49.5 | 5.048
1401.7 | 49.5 | 5.048
1401.8 | 49.5 | 5.048
1401.9 | 49.5 | 5.048
1402 | 49.5 | 5.048
1402.1 | 49.5 | 5.048
1402.2 | 49.5 | 5.048
1402.3 | 49.5 | 5.048
1402.4 | 49.5 | 5.048
1402.5 | 49.5 | 5.048
1402.6 | 49.5 | 5.048
1402.7 | 49.5 | 5.048
1402.8 | 49.5 | 5.048
1402.9 | 49.5 | 5.048
1403 | 49.5 | 5.048
1403.1 | 49.5 | 5.048
1403.2 | 49.5 | 5.048
1403.3 | 49.5 | 5.048
1403.4 | 49.5 | 5.048
1403.5 | 49.5 | 5.048
1403.6 | 49.5 | 5.048
1403.7 | 49.5 | 5.048
1403.8 | 49.5 | 5.048
1403.9 | 49.5 | 5.048
1404 | 49.5 | 5.048
1404.1 | 49.5 | 5.048
1404.2 | 49.5 | 5.048
1404.3 | 49.5 | 5.048
1404.4 | 49.5 | 5.048
1404.5 | 49.5 | 5.048
1404.6 | 49.5 | 5.048
1404.7 | 49.5 | 5.048
1404.8 | 49.5 | 5.048
1404.9 | 49.5 | 5.048
1405 | 49.5 | 5.048
1405.1 | 49.5 | 5.048
1405.2 | 49.5 | 5.048
1405.3 | 49.5 | 5.048
1405.4 | 49.5 | 5.048
1405.5 | 49.5 | 5.048
1405.6 | 49.5 | 5.048
1405.7 | 49.5 | 5.049
1405.8 | 49.5 | 5.049
1405.9 | 49.5 | 5.049
1406 | 49.5 | 5.049
1406.1 | 49.5 | 5.049
1406.2 | 49.5 | 5.049
1406.3 | 49.5 | 5.049
1406.4 | 49.5 | 5.049
1406.5 | 49.5 | 5.049
1406.6 | 49.5 | 5.049
1406.7 | 49.5 | 5.049
1406.8 | 49.5 | 5.049
1406.9 | 49.5 | 5.049
1407 | 49.5 | 5.049
1407.1 | 49.5 | 5.049
1407.2 | 49.5 | 5.049
1407.3 | 49.5 | 5.049
1407.4 | 49.5 | 5.049
1407.5 | 49.5 | 5.049
1407.6 | 49.5 | 5.049
1407.7 | 49.5 | 5.049
1407.8 | 49.5 | 5.049
1407.9 | 49.5 | 5.049
1408 | 49.5 | 5.049
1408.1 | 49.5 | 5.048
1408.2 | 49.5 | 5.048
1408.3 | 49.5 | 5.048
1408.4 | 49.5 | 5.048
1408.5 | 49.5 | 5.048
1408.6 | 49.5 | 5.048
1408.7 | 49.5 | 5.048
1408.8 | 49.5 | 5.048
1408.9 | 49.5 | 5.048
1409 | 49.5 | 5.048
1409.1 | 49.5 | 5.048
1409.2 | 49.5 | 5.048
1409.3 | 49.5 | 5.048
1409.4 | 49.5 | 5.048
1409.5 | 49.5 | 5.048
1409.6 | 49.5 | 5.048
1409.7 | 49.5 | 5.048
1409.8 | 49.5 | 5.048
1409.9 | 49.5 | 5.048
1410 | 49.5 | 5.048
1410.1 | 49.5 | 5.048
1410.2 | 49.5 | 5.048
1410.3 | 49.5 | 5.048
1410.4 | 49.5 | 5.048
1410.5 | 49.5 | 5.048
1410.6 | 49.5 | 5.048
1410.7 | 49.5 | 5.048
1410.8 | 49.5 | 5.048
1410.9 | 49.5 | 5.048
1411 | 49.5 | 5.048
1411.1 | 49.5 | 5.048
1411.2 | 49.5 | 5.048
1411.3 | 49.5 | 5.048
1411.4 | 49.5 | 5.048
1411.5 | 49.5 | 5.048
1411.6 | 49.5 | 5.048
1411.7 | 49.5 | 5.048
1411.8 | 49.5 | 5.048
1411.9 | 49.5 | 5.048
1412 | 49.5 | 5.048
1412.1 | 49.5 | 5.048
1412.2 | 49.5 | 5.048
1412.3 | 49.5 | 5.048
1412.4 | 49.5 | 5.048
1412.5 | 49.5 | 5.048
1412.6 | 49.5 | 5.048
1412.7 | 49.5 | 5.048
1412.8 | 49.5 | 5.048
1412.9 | 49.5 | 5.048
1413 | 49.5 | 5.048
1413.1 | 49.5 | 5.048
1413.2 | 49.5 | 5.048
1413.3 | 49.5 | 5.048
1413.4 | 49.5 | 5.048
1413.5 | 49.5 | 5.048
1413.6 | 49.5 | 5.048
1413.7 | 49.5 | 5.048
1413.8 | 49.5 | 5.048
1413.9 | 49.5 | 5.048
1414 | 49.5 | 5.048
1414.1 | 49.5 | 5.048
1414.2 | 49.5 | 5.048
1414.3 | 49.5 | 5.048
1414.4 | 49.5 | 5.048
1414.5 | 49.5 | 5.048
1414.6 | 49.5 | 5.048
1414.7 | 49.5 | 5.048
1414.8 | 49.5 | 5.048
1414.9 | 49.5 | 5.048
1415 | 49.5 | 5.048
1415.1 | 49.5 | 5.048
1415.2 | 49.5 | 5.048
1415.3 | 49.5 | 5.048
1415.4 | 49.5 | 5.048
1415.5 | 49.5 | 5.048
1415.6 | 49.5 | 5.048
1415.7 | 49.5 | 5.048
1415.8 | 49.5 | 5.048
1415.9 | 49.5 | 5.048
1416 | 49.5 | 5.048
1416.1 | 49.5 | 5.048
1416.2 | 49.5 | 5.048
1416.3 | 49.5 | 5.048
1416.4 | 49.5 | 5.048
1416.5 | 49.5 | 5.048
1416.6 | 49.5 | 5.048
1416.7 | 49.5 | 5.048
1416.8 | 49.5 | 5.048
1416.9 | 49.5 | 5.048
1417 | 49.5 | 5.048
1417.1 | 49.5 | 5.048
1417.2 | 49.5 | 5.048
1417.3 | 49.5 | 5.048
1417.4 | 49.5 | 5.048
1417.5 | 49.5 | 5.048
1417.6 | 49.5 | 5.048
1417.7 | 49.5 | 5.048
1417.8 | 49.5 | 5.048
1417.9 | 49.5 | 5.048
1418 | 49.5 | 5.048
1418.1 | 49.5 | 5.048
1418.2 | 49.5 | 5.048
1418.3 | 49.5 | 5.048
1418.4 | 49.5 | 5.048
1418.5 | 49.5 | 5.048
1418.6 | 49.5 | 5.048
1418.7 | 49.5 | 5.048
1418.8 | 49.5 | 5.048
1418.9 | 49.5 | 5.048
1419 | 49.5 | 5.048
1419.1 | 49.5 | 5.048
1419.2 | 49.5 | 5.048
1419.3 | 49.5 | 5.048
1419.4 | 49.5 | 5.048
1419.5 | 49.5 | 5.048
1419.6 | 49.5 | 5.048
1419.7 | 49.5 | 5.048
1419.8 | 49.5 | 5.048
1419.9 | 49.5 | 5.048
1420 | 49.5 | 5.048
1420.1 | 49.5 | 5.048
1420.2 | 49.5 | 5.048
1420.3 | 49.5 | 5.048
1420.4 | 49.5 | 5.048
1420.5 | 49.5 | 5.048
1420.6 | 49.5 | 5.048
1420.7 | 49.5 | 5.048
1420.8 | 49.5 | 5.048
1420.9 | 49.5 | 5.048
1421 | 49.5 | 5.048
1421.1 | 49.5 | 5.048
1421.2 | 49.5 | 5.048
1421.3 | 49.5 | 5.048
1421.4 | 49.5 | 5.048
1421.5 | 49.5 | 5.048
1421.6 | 49.5 | 5.048
1421.7 | 49.5 | 5.048
1421.8 | 49.5 | 5.048
1421.9 | 49.5 | 5.048
1422 | 49.5 | 5.048
1422.1 | 49.5 | 5.048
1422.2 | 49.5 | 5.048
1422.3 | 49.5 | 5.048
1422.4 | 49.5 | 5.048
1422.5 | 49.5 | 5.048
1422.6 | 49.5 | 5.048
1422.7 | 49.5 | 5.048
1422.8 | 49.5 | 5.048
1422.9 | 49.5 | 5.048
1423 | 49.5 | 5.048
1423.1 | 49.5 | 5.048
1423.2 | 49.5 | 5.048
1423.3 | 49.5 | 5.048
1423.4 | 49.5 | 5.048
1423.5 | 49.5 | 5.048
1423.6 | 49.5 | 5.048
1423.7 | 49.5 | 5.048
1423.8 | 49.5 | 5.048
1423.9 | 49.5 | 5.048
1424 | 49.5 | 5.048
1424.1 | 49.5 | 5.048
1424.2 | 49.5 | 5.048
1424.3 | 49.5 | 5.048
1424.4 | 49.5 | 5.048
1424.5 | 49.5 | 5.048
1424.6 | 49.5 | 5.048
1424.7 | 49.5 | 5.048
1424.8 | 49.5 | 5.048
1424.9 | 49.5 | 5.048
1425 | 49.5 | 5.048
1425.1 | 49.5 | 5.048
1425.2 | 49.5 | 5.048
1425.3 | 49.5 | 5.048
1425.4 | 49.5 | 5.048
1425.5 | 49.5 | 5.048
1425.6 | 49.5 | 5.048
1425.7 | 49.5 | 5.048
1425.8 | 49.5 | 5.048
1425.9 | 49.5 | 5.048
1426 | 49.5 | 5.048
1426.1 | 49.5 | 5.048
1426.2 | 49.5 | 5.048
1426.3 | 49.5 | 5.048
1426.4 | 49.5 | 5.048
1426.5 | 49.5 | 5.048
1426.6 | 49.5 | 5.048
1426.7 | 49.5 | 5.048
1426.8 | 49.5 | 5.048
1426.9 | 49.5 | 5.048
1427 | 49.5 | 5.048
1427.1 | 49.5 | 5.048
1427.2 | 49.5 | 5.048
1427.3 | 49.5 | 5.048
1427.4 | 49.5 | 5.048
1427.5 | 49.5 | 5.048
1427.6 | 49.5 | 5.048
1427.7 | 49.5 | 5.048
1427.8 | 49.5 | 5.048
1427.9 | 49.5 | 5.048
1428 | 49.5 | 5.048
1428.1 | 49.5 | 5.048
1428.2 | 49.5 | 5.048
1428.3 | 49.5 | 5.048
1428.4 | 49.5 | 5.048
1428.5 | 49.5 | 5.048
1428.6 | 49.5 | 5.048
1428.7 | 49.5 | 5.048
1428.8 | 49.5 | 5.048
1428.9 | 49.5 | 5.048
1429 | 49.5 | 5.048
1429.1 | 49.5 | 5.048
1429.2 | 49.5 | 5.048
1429.3 | 49.5 | 5.048
1429.4 | 49.5 | 5.048
1429.5 | 49.5 | 5.048
1429.6 | 49.5 | 5.048
1429.7 | 49.5 | 5.048
1429.8 | 49.5 | 5.048
1429.9 | 49.5 | 5.048
1430 | 49.5 | 5.048
1430.1 | 49.5 | 5.048
1430.2 | 49.5 | 5.048
1430.3 | 49.5 | 5.048
1430.4 | 49.5 | 5.048
1430.5 | 49.5 | 5.048
1430.6 | 49.5 | 5.048
1430.7 | 49.5 | 5.048
1430.8 | 49.5 | 5.048
1430.9 | 49.5 | 5.048
1431 | 49.5 | 5.048
1431.1 | 49.5 | 5.048
1431.2 | 49.5 | 5.048
1431.3 | 49.5 | 5.048
1431.4 | 49.5 | 5.048
1431.5 | 49.5 | 5.048
1431.6 | 49.5 | 5.048
1431.7 | 49.5 | 5.048
1431.8 | 49.5 | 5.048
1431.9 | 49.5 | 5.048
1432 | 49.5 | 5.048
1432.1 | 49.5 | 5.048
1432.2 | 49.5 | 5.048
1432.3 | 49.5 | 5.048
1432.4 | 49.5 | 5.048
1432.5 | 49.5 | 5.048
1432.6 | 49.5 | 5.048
1432.7 | 49.5 | 5.048
1432.8 | 49.5 | 5.048
1432.9 | 49.5 | 5.048
1433 | 49.5 | 5.048
1433.1 | 49.5 | 5.048
1433.2 | 49.5 | 5.048
1433.3 | 49.5 | 5.048
1433.4 | 49.5 | 5.048
1433.5 | 49.5 | 5.048
1433.6 | 49.5 | 5.048
1433.7 | 49.5 | 5.048
1433.8 | 49.5 | 5.048
1433.9 | 49.5 | 5.048
1434 | 49.5 | 5.048
1434.1 | 49.5 | 5.048
1434.2 | 49.5 | 5.048
1434.3 | 49.5 | 5.048
1434.4 | 49.5 | 5.048
1434.5 | 49.5 | 5.048
1434.6 | 49.5 | 5.048
1434.7 | 49.5 | 5.048
1434.8 | 49.5 | 5.048
1434.9 | 49.5 | 5.048
1435 | 49.5 | 5.048
1435.1 | 49.5 | 5.048
1435.2 | 49.5 | 5.048
1435.3 | 49.5 | 5.048
1435.4 | 49.5 | 5.048
1435.5 | 49.5 | 5.048
1435.6 | 49.5 | 5.048
1435.7 | 49.5 | 5.048
1435.8 | 49.5 | 5.048
1435.9 | 49.5 | 5.048
1436 | 49.5 | 5.048
1436.1 | 49.5 | 5.048
1436.2 | 49.5 | 5.048
1436.3 | 49.5 | 5.048
1436.4 | 49.5 | 5.048
1436.5 | 49.5 | 5.048
1436.6 | 49.5 | 5.048
1436.7 | 49.5 | 5.048
1436.8 | 49.5 | 5.048
1436.9 | 49.5 | 5.048
1437 | 49.5 | 5.048
1437.1 | 49.5 | 5.048
1437.2 | 49.5 | 5.048
1437.3 | 49.5 | 5.048
1437.4 | 49.5 | 5.048
1437.5 | 49.5 | 5.048
1437.6 | 49.5 | 5.048
1437.7 | 49.5 | 5.048
1437.8 | 49.5 | 5.048
1437.9 | 49.5 | 5.048
1438 | 49.5 | 5.048
1438.1 | 49.5 | 5.048
1438.2 | 49.5 | 5.048
1438.3 | 49.5 | 5.048
1438.4 | 49.5 | 5.048
1438.5 | 49.5 | 5.048
1438.6 | 49.5 | 5.048
1438.7 | 49.5 | 5.048
1438.8 | 49.5 | 5.048
1438.9 | 49.5 | 5.048
1439 | 49.5 | 5.048
1439.1 | 49.5 | 5.048
1439.2 | 49.5 | 5.048
1439.3 | 49.5 | 5.048
1439.4 | 49.5 | 5.048
1439.5 | 49.5 | 5.048
1439.6 | 49.5 | 5.048
1439.7 | 49.5 | 5.048
1439.8 | 49.5 | 5.048
1439.9 | 49.5 | 5.048
1440 | 49.5 | 5.048
1440.1 | 49.5 | 5.048
1440.2 | 49.5 | 5.048
1440.3 | 49.5 | 5.048
1440.4 | 49.5 | 5.048
1440.5 | 49.5 | 5.048
1440.6 | 49.5 | 5.048
1440.7 | 49.5 | 5.048
1440.8 | 49.5 | 5.048
1440.9 | 49.5 | 5.048
1441 | 49.5 | 5.048
1441.1 | 49.5 | 5.048
1441.2 | 49.5 | 5.048
1441.3 | 49.5 | 5.048
1441.4 | 49.5 | 5.048
1441.5 | 49.5 | 5.048
1441.6 | 49.5 | 5.048
1441.7 | 49.5 | 5.048
1441.8 | 49.5 | 5.048
1441.9 | 49.5 | 5.048
1442 | 49.5 | 5.048
1442.1 | 49.5 | 5.048
1442.2 | 49.5 | 5.048
1442.3 | 49.5 | 5.048
1442.4 | 49.5 | 5.048
1442.5 | 49.5 | 5.048
1442.6 | 49.5 | 5.048
1442.7 | 49.5 | 5.048
1442.8 | 49.5 | 5.048
1442.9 | 49.5 | 5.048
1443 | 49.5 | 5.048
1443.1 | 49.5 | 5.048
1443.2 | 49.5 | 5.048
1443.3 | 49.5 | 5.048
1443.4 | 49.5 | 5.048
1443.5 | 49.5 | 5.048
1443.6 | 49.5 | 5.048
1443.7 | 49.5 | 5.048
1443.8 | 49.5 | 5.048
1443.9 | 49.5 | 5.048
1444 | 49.5 | 5.048
1444.1 | 49.5 | 5.048
1444.2 | 49.5 | 5.048
1444.3 | 49.5 | 5.048
1444.4 | 49.5 | 5.048
1444.5 | 49.5 | 5.048
1444.6 | 49.5 | 5.048
1444.7 | 49.5 | 5.048
1444.8 | 49.5 | 5.048
1444.9 | 49.5 | 5.048
1445 | 49.5 | 5.048
1445.1 | 49.5 | 5.048
1445.2 | 49.5 | 5.048
1445.3 | 49.5 | 5.048
1445.4 | 49.5 | 5.048
1445.5 | 49.5 | 5.048
1445.6 | 49.5 | 5.048
1445.7 | 49.5 | 5.048
1445.8 | 49.5 | 5.048
1445.9 | 49.5 | 5.048
1446 | 49.5 | 5.048
1446.1 | 49.5 | 5.048
1446.2 | 49.5 | 5.048
1446.3 | 49.5 | 5.048
1446.4 | 49.5 | 5.048
1446.5 | 49.5 | 5.048
1446.6 | 49.5 | 5.048
1446.7 | 49.5 | 5.048
1446.8 | 49.5 | 5.048
1446.9 | 49.5 | 5.048
1447 | 49.5 | 5.048
1447.1 | 49.5 | 5.048
1447.2 | 49.5 | 5.048
1447.3 | 49.5 | 5.048
1447.4 | 49.5 | 5.048
1447.5 | 49.5 | 5.048
1447.6 | 49.5 | 5.048
1447.7 | 49.5 | 5.048
1447.8 | 49.5 | 5.048
1447.9 | 49.5 | 5.048
1448 | 49.5 | 5.048
1448.1 | 49.5 | 5.048
1448.2 | 49.5 | 5.048
1448.3 | 49.5 | 5.048
1448.4 | 49.5 | 5.048
1448.5 | 49.5 | 5.048
1448.6 | 49.5 | 5.048
1448.7 | 49.5 | 5.048
1448.8 | 49.5 | 5.048
1448.9 | 49.5 | 5.048
1449 | 49.5 | 5.048
1449.1 | 49.5 | 5.048
1449.2 | 49.5 | 5.048
1449.3 | 49.5 | 5.048
1449.4 | 49.5 | 5.048
1449.5 | 49.5 | 5.049
1449.6 | 49.5 | 5.049
1449.7 | 49.5 | 5.049
1449.8 | 49.5 | 5.049
1449.9 | 49.5 | 5.049
1450 | 49.5 | 5.049
1450.1 | 49.5 | 5.049
1450.2 | 49.5 | 5.049
1450.3 | 49.5 | 5.049
1450.4 | 49.5 | 5.049
1450.5 | 49.5 | 5.049
1450.6 | 49.5 | 5.049
1450.7 | 49.5 | 5.049
1450.8 | 49.5 | 5.049
1450.9 | 49.5 | 5.049
1451 | 49.5 | 5.049
1451.1 | 49.5 | 5.049
1451.2 | 49.5 | 5.049
1451.3 | 49.5 | 5.049
1451.4 | 49.5 | 5.049
1451.5 | 49.5 | 5.049
1451.6 | 49.5 | 5.049
1451.7 | 49.5 | 5.049
1451.8 | 49.5 | 5.049
1451.9 | 49.5 | 5.049
1452 | 49.5 | 5.049
1452.1 | 49.5 | 5.049
1452.2 | 49.5 | 5.049
1452.3 | 49.5 | 5.049
1452.4 | 49.5 | 5.049
1452.5 | 49.5 | 5.049
1452.6 | 49.5 | 5.049
1452.7 | 49.5 | 5.049
1452.8 | 49.5 | 5.049
1452.9 | 49.5 | 5.049
1453 | 49.5 | 5.048
1453.1 | 49.5 | 5.048
1453.2 | 49.5 | 5.048
1453.3 | 49.5 | 5.048
1453.4 | 49.5 | 5.048
1453.5 | 49.5 | 5.048
1453.6 | 49.5 | 5.048
1453.7 | 49.5 | 5.048
1453.8 | 49.5 | 5.048
1453.9 | 49.5 | 5.048
1454 | 49.5 | 5.048
1454.1 | 49.5 | 5.048
1454.2 | 49.5 | 5.048
1454.3 | 49.5 | 5.048
1454.4 | 49.5 | 5.048
1454.5 | 49.5 | 5.048
1454.6 | 49.5 | 5.048
1454.7 | 49.5 | 5.048
1454.8 | 49.5 | 5.048
1454.9 | 49.5 | 5.048
1455 | 49.5 | 5.048
1455.1 | 49.5 | 5.048
1455.2 | 49.5 | 5.048
1455.3 | 49.5 | 5.048
1455.4 | 49.5 | 5.048
1455.5 | 49.5 | 5.048
1455.6 | 49.5 | 5.048
1455.7 | 49.5 | 5.048
1455.8 | 49.5 | 5.048
1455.9 | 49.5 | 5.048
1456 | 49.5 | 5.048
1456.1 | 49.5 | 5.048
1456.2 | 49.5 | 5.048
1456.3 | 49.5 | 5.048
1456.4 | 49.5 | 5.048
1456.5 | 49.5 | 5.048
1456.6 | 49.5 | 5.048
1456.7 | 49.5 | 5.048
1456.8 | 49.5 | 5.048
1456.9 | 49.5 | 5.048
1457 | 49.5 | 5.048
1457.1 | 49.5 | 5.048
1457.2 | 49.5 | 5.048
1457.3 | 49.5 | 5.048
1457.4 | 49.5 | 5.048
1457.5 | 49.5 | 5.048
1457.6 | 49.5 | 5.048
1457.7 | 49.5 | 5.048
1457.8 | 49.5 | 5.048
1457.9 | 49.5 | 5.048
1458 | 49.5 | 5.048
1458.1 | 49.5 | 5.048
1458.2 | 49.5 | 5.048
1458.3 | 49.5 | 5.048
1458.4 | 49.5 | 5.048
1458.5 | 49.5 | 5.048
1458.6 | 49.5 | 5.048
1458.7 | 49.5 | 5.048
1458.8 | 49.5 | 5.048
1458.9 | 49.5 | 5.048
1459 | 49.5 | 5.048
1459.1 | 49.5 | 5.048
1459.2 | 49.5 | 5.048
1459.3 | 49.5 | 5.048
1459.4 | 49.5 | 5.048
1459.5 | 49.5 | 5.048
1459.6 | 49.5 | 5.048
1459.7 | 49.5 | 5.048
1459.8 | 49.5 | 5.048
1459.9 | 49.5 | 5.048
1460 | 49.5 | 5.048
1460.1 | 49.5 | 5.048
1460.2 | 49.5 | 5.048
1460.3 | 49.5 | 5.048
1460.4 | 49.5 | 5.048
1460.5 | 49.5 | 5.048
1460.6 | 49.5 | 5.048
1460.7 | 49.5 | 5.048
1460.8 | 49.5 | 5.048
1460.9 | 49.5 | 5.048
1461 | 49.5 | 5.048
1461.1 | 49.5 | 5.048
1461.2 | 49.5 | 5.048
1461.3 | 49.5 | 5.048
1461.4 | 49.5 | 5.048
1461.5 | 49.5 | 5.048
1461.6 | 49.5 | 5.048
1461.7 | 49.5 | 5.048
1461.8 | 49.5 | 5.048
1461.9 | 49.5 | 5.048
1462 | 49.5 | 5.048
1462.1 | 49.5 | 5.048
1462.2 | 49.5 | 5.048
1462.3 | 49.5 | 5.048
1462.4 | 49.5 | 5.048
1462.5 | 49.5 | 5.048
1462.6 | 49.5 | 5.048
1462.7 | 49.5 | 5.048
1462.8 | 49.5 | 5.048
1462.9 | 49.5 | 5.048
1463 | 49.5 | 5.048
1463.1 | 49.5 | 5.048
1463.2 | 49.5 | 5.048
1463.3 | 49.5 | 5.048
1463.4 | 49.5 | 5.048
1463.5 | 49.5 | 5.048
1463.6 | 49.5 | 5.048
1463.7 | 49.5 | 5.048
1463.8 | 49.5 | 5.048
1463.9 | 49.5 | 5.048
1464 | 49.5 | 5.048
1464.1 | 49.5 | 5.049
1464.2 | 49.5 | 5.049
1464.3 | 49.5 | 5.049
1464.4 | 49.5 | 5.049
1464.5 | 49.5 | 5.049
1464.6 | 49.5 | 5.049
1464.7 | 49.5 | 5.049
1464.8 | 49.5 | 5.049
1464.9 | 49.5 | 5.049
1465 | 49.5 | 5.049
1465.1 | 49.5 | 5.049
1465.2 | 49.5 | 5.049
1465.3 | 49.5 | 5.049
1465.4 | 49.5 | 5.049
1465.5 | 49.5 | 5.049
1465.6 | 49.5 | 5.049
1465.7 | 49.5 | 5.049
1465.8 | 49.5 | 5.049
1465.9 | 49.5 | 5.049
1466 | 49.5 | 5.049
1466.1 | 49.5 | 5.049
1466.2 | 49.5 | 5.049
1466.3 | 49.5 | 5.049
1466.4 | 49.5 | 5.049
1466.5 | 49.5 | 5.048
1466.6 | 49.5 | 5.048
1466.7 | 49.5 | 5.048
1466.8 | 49.5 | 5.048
1466.9 | 49.5 | 5.048
1467 | 49.5 | 5.048
1467.1 | 49.5 | 5.048
1467.2 | 49.5 | 5.048
1467.3 | 49.5 | 5.048
1467.4 | 49.5 | 5.048
1467.5 | 49.5 | 5.048
1467.6 | 49.5 | 5.048
1467.7 | 49.5 | 5.048
1467.8 | 49.5 | 5.048
1467.9 | 49.5 | 5.048
1468 | 49.5 | 5.048
1468.1 | 49.5 | 5.048
1468.2 | 49.5 | 5.048
1468.3 | 49.5 | 5.048
1468.4 | 49.5 | 5.048
1468.5 | 49.5 | 5.048
1468.6 | 49.5 | 5.048
1468.7 | 49.5 | 5.048
1468.8 | 49.5 | 5.048
1468.9 | 49.5 | 5.048
1469 | 49.5 | 5.048
1469.1 | 49.5 | 5.048
1469.2 | 49.5 | 5.049
1469.3 | 49.5 | 5.049
1469.4 | 49.5 | 5.049
1469.5 | 49.5 | 5.049
1469.6 | 49.5 | 5.049
1469.7 | 49.5 | 5.049
1469.8 | 49.5 | 5.049
1469.9 | 49.5 | 5.049
1470 | 49.5 | 5.049
1470.1 | 49.5 | 5.049
1470.2 | 49.5 | 5.049
1470.3 | 49.5 | 5.049
1470.4 | 49.5 | 5.049
1470.5 | 49.5 | 5.049
1470.6 | 49.5 | 5.049
1470.7 | 49.5 | 5.049
1470.8 | 49.5 | 5.049
1470.9 | 49.5 | 5.049
1471 | 49.5 | 5.049
1471.1 | 49.5 | 5.049
1471.2 | 49.5 | 5.049
1471.3 | 49.5 | 5.049
1471.4 | 49.5 | 5.048
1471.5 | 49.5 | 5.048
1471.6 | 49.5 | 5.048
1471.7 | 49.5 | 5.048
1471.8 | 49.5 | 5.048
1471.9 | 49.5 | 5.048
1472 | 49.5 | 5.048
1472.1 | 49.5 | 5.048
1472.2 | 49.5 | 5.048
1472.3 | 49.5 | 5.048
1472.4 | 49.5 | 5.048
1472.5 | 49.5 | 5.048
1472.6 | 49.5 | 5.048
1472.7 | 49.5 | 5.048
1472.8 | 49.5 | 5.048
1472.9 | 49.5 | 5.048
1473 | 49.5 | 5.048
1473.1 | 49.5 | 5.048
1473.2 | 49.5 | 5.048
1473.3 | 49.5 | 5.048
1473.4 | 49.5 | 5.048
1473.5 | 49.5 | 5.048
1473.6 | 49.5 | 5.048
1473.7 | 49.5 | 5.048
1473.8 | 49.5 | 5.048
1473.9 | 49.5 | 5.048
1474 | 49.5 | 5.048
1474.1 | 49.5 | 5.048
1474.2 | 49.5 | 5.048
1474.3 | 49.5 | 5.048
1474.4 | 49.5 | 5.048
1474.5 | 49.5 | 5.048
1474.6 | 49.5 | 5.048
1474.7 | 49.5 | 5.048
1474.8 | 49.5 | 5.048
1474.9 | 49.5 | 5.048
1475 | 49.5 | 5.048
1475.1 | 49.5 | 5.048
1475.2 | 49.5 | 5.049
1475.3 | 49.5 | 5.049
1475.4 | 49.5 | 5.049
1475.5 | 49.5 | 5.049
1475.6 | 49.5 | 5.049
1475.7 | 49.5 | 5.049
1475.8 | 49.5 | 5.049
1475.9 | 49.5 | 5.049
1476 | 49.5 | 5.049
1476.1 | 49.5 | 5.049
1476.2 | 49.5 | 5.049
1476.3 | 49.5 | 5.049
1476.4 | 49.5 | 5.049
1476.5 | 49.5 | 5.049
1476.6 | 49.5 | 5.049
1476.7 | 49.5 | 5.049
1476.8 | 49.5 | 5.049
1476.9 | 49.5 | 5.049
1477 | 49.5 | 5.049
1477.1 | 49.5 | 5.049
1477.2 | 49.5 | 5.049
1477.3 | 49.5 | 5.049
1477.4 | 49.5 | 5.049
1477.5 | 49.5 | 5.048
1477.6 | 49.5 | 5.048
1477.7 | 49.5 | 5.048
1477.8 | 49.5 | 5.048
1477.9 | 49.5 | 5.048
1478 | 49.5 | 5.048
1478.1 | 49.5 | 5.048
1478.2 | 49.5 | 5.048
1478.3 | 49.5 | 5.048
1478.4 | 49.5 | 5.048
1478.5 | 49.5 | 5.048
1478.6 | 49.5 | 5.048
1478.7 | 49.5 | 5.048
1478.8 | 49.5 | 5.048
1478.9 | 49.5 | 5.048
1479 | 49.5 | 5.048
1479.1 | 49.5 | 5.048
1479.2 | 49.5 | 5.048
1479.3 | 49.5 | 5.048
1479.4 | 49.5 | 5.048
1479.5 | 49.5 | 5.048
1479.6 | 49.5 | 5.048
1479.7 | 49.5 | 5.048
1479.8 | 49.5 | 5.048
1479.9 | 49.5 | 5.048
1480 | 49.5 | 5.048
1480.1 | 49.5 | 5.048
1480.2 | 49.5 | 5.048
1480.3 | 49.5 | 5.048
1480.4 | 49.5 | 5.048
1480.5 | 49.5 | 5.048
1480.6 | 49.5 | 5.048
1480.7 | 49.5 | 5.048
1480.8 | 49.5 | 5.048
1480.9 | 49.5 | 5.048
1481 | 49.5 | 5.048
1481.1 | 49.5 | 5.048
1481.2 | 49.5 | 5.048
1481.3 | 49.5 | 5.048
1481.4 | 49.5 | 5.048
1481.5 | 49.5 | 5.048
1481.6 | 49.5 | 5.048
1481.7 | 49.5 | 5.048
1481.8 | 49.5 | 5.048
1481.9 | 49.5 | 5.048
1482 | 49.5 | 5.048
1482.1 | 49.5 | 5.048
1482.2 | 49.5 | 5.048
1482.3 | 49.5 | 5.048
1482.4 | 49.5 | 5.048
1482.5 | 49.5 | 5.048
1482.6 | 49.5 | 5.048
1482.7 | 49.5 | 5.048
1482.8 | 49.5 | 5.048
1482.9 | 49.5 | 5.048
1483 | 49.5 | 5.048
1483.1 | 49.5 | 5.048
1483.2 | 49.5 | 5.048
1483.3 | 49.5 | 5.048
1483.4 | 49.5 | 5.048
1483.5 | 49.5 | 5.048
1483.6 | 49.5 | 5.048
1483.7 | 49.5 | 5.048
1483.8 | 49.5 | 5.048
1483.9 | 49.5 | 5.048
1484 | 49.5 | 5.048
1484.1 | 49.5 | 5.048
1484.2 | 49.5 | 5.048
1484.3 | 49.5 | 5.048
1484.4 | 49.5 | 5.048
1484.5 | 49.5 | 5.048
1484.6 | 49.5 | 5.048
1484.7 | 49.5 | 5.048
1484.8 | 49.5 | 5.048
1484.9 | 49.5 | 5.048
1485 | 49.5 | 5.048
1485.1 | 49.5 | 5.048
1485.2 | 49.5 | 5.048
1485.3 | 49.5 | 5.048
1485.4 | 49.5 | 5.048
1485.5 | 49.5 | 5.048
1485.6 | 49.5 | 5.048
1485.7 | 49.5 | 5.048
1485.8 | 49.5 | 5.048
1485.9 | 49.5 | 5.048
1486 | 49.5 | 5.048
1486.1 | 49.5 | 5.048
1486.2 | 49.5 | 5.048
1486.3 | 49.5 | 5.048
1486.4 | 49.5 | 5.048
1486.5 | 49.5 | 5.048
1486.6 | 49.5 | 5.048
1486.7 | 49.5 | 5.048
1486.8 | 49.5 | 5.048
1486.9 | 49.5 | 5.049
1487 | 49.5 | 5.049
1487.1 | 49.5 | 5.049
1487.2 | 49.5 | 5.048
1487.3 | 49.5 | 5.048
1487.4 | 49.5 | 5.048
1487.5 | 49.5 | 5.048
1487.6 | 49.5 | 5.048
1487.7 | 49.5 | 5.048
1487.8 | 49.5 | 5.048
1487.9 | 49.5 | 5.048
1488 | 49.5 | 5.048
1488.1 | 49.5 | 5.048
1488.2 | 49.5 | 5.048
1488.3 | 49.5 | 5.048
1488.4 | 49.5 | 5.048
1488.5 | 49.5 | 5.048
1488.6 | 49.5 | 5.048
1488.7 | 49.5 | 5.048
1488.8 | 49.5 | 5.048
1488.9 | 49.5 | 5.048
1489 | 49.5 | 5.048
1489.1 | 49.5 | 5.049
1489.2 | 49.5 | 5.049
1489.3 | 49.5 | 5.049
1489.4 | 49.5 | 5.049
1489.5 | 49.5 | 5.049
1489.6 | 49.5 | 5.049
1489.7 | 49.5 | 5.049
1489.8 | 49.5 | 5.049
1489.9 | 49.5 | 5.049
1490 | 49.5 | 5.049
1490.1 | 49.5 | 5.049
1490.2 | 49.5 | 5.049
1490.3 | 49.5 | 5.049
1490.4 | 49.5 | 5.049
1490.5 | 49.5 | 5.049
1490.6 | 49.5 | 5.049
1490.7 | 49.5 | 5.049
1490.8 | 49.5 | 5.049
1490.9 | 49.5 | 5.049
1491 | 49.5 | 5.049
1491.1 | 49.5 | 5.049
1491.2 | 49.5 | 5.049
1491.3 | 49.5 | 5.049
1491.4 | 49.5 | 5.049
1491.5 | 49.5 | 5.048
1491.6 | 49.5 | 5.048
1491.7 | 49.5 | 5.048
1491.8 | 49.5 | 5.048
1491.9 | 49.5 | 5.048
1492 | 49.5 | 5.048
1492.1 | 49.5 | 5.048
1492.2 | 49.5 | 5.048
1492.3 | 49.5 | 5.048
1492.4 | 49.5 | 5.048
1492.5 | 49.5 | 5.048
1492.6 | 49.5 | 5.048
1492.7 | 49.5 | 5.048
1492.8 | 49.5 | 5.048
1492.9 | 49.5 | 5.048
1493 | 49.5 | 5.048
1493.1 | 49.5 | 5.048
1493.2 | 49.5 | 5.048
1493.3 | 49.5 | 5.048
1493.4 | 49.5 | 5.048
1493.5 | 49.5 | 5.048
1493.6 | 49.5 | 5.048
1493.7 | 49.5 | 5.048
1493.8 | 49.5 | 5.048
1493.9 | 49.5 | 5.048
1494 | 49.5 | 5.048
1494.1 | 49.5 | 5.048
1494.2 | 49.5 | 5.048
1494.3 | 49.5 | 5.048
1494.4 | 49.5 | 5.048
1494.5 | 49.5 | 5.048
1494.6 | 49.5 | 5.048
1494.7 | 49.5 | 5.048
1494.8 | 49.5 | 5.048
1494.9 | 49.5 | 5.048
1495 | 49.5 | 5.048
1495.1 | 49.5 | 5.048
1495.2 | 49.5 | 5.048
1495.3 | 49.5 | 5.048
1495.4 | 49.5 | 5.048
1495.5 | 49.5 | 5.048
1495.6 | 49.5 | 5.048
1495.7 | 49.5 | 5.048
1495.8 | 49.5 | 5.048
1495.9 | 49.5 | 5.048
1496 | 49.5 | 5.048
1496.1 | 49.5 | 5.049
1496.2 | 49.5 | 5.049
1496.3 | 49.5 | 5.049
1496.4 | 49.5 | 5.049
1496.5 | 49.5 | 5.049
1496.6 | 49.5 | 5.049
1496.7 | 49.5 | 5.049
1496.8 | 49.5 | 5.049
1496.9 | 49.5 | 5.049
1497 | 49.5 | 5.049
1497.1 | 49.5 | 5.049
1497.2 | 49.5 | 5.049
1497.3 | 49.5 | 5.049
1497.4 | 49.5 | 5.049
1497.5 | 49.5 | 5.049
1497.6 | 49.5 | 5.049
1497.7 | 49.5 | 5.049
1497.8 | 49.5 | 5.049
1497.9 | 49.5 | 5.049
1498 | 49.5 | 5.049
1498.1 | 49.5 | 5.049
1498.2 | 49.5 | 5.049
1498.3 | 49.5 | 5.049
1498.4 | 49.5 | 5.049
1498.5 | 49.5 | 5.048
1498.6 | 49.5 | 5.048
1498.7 | 49.5 | 5.048
1498.8 | 49.5 | 5.048
1498.9 | 49.5 | 5.048
1499 | 49.5 | 5.048
1499.1 | 49.5 | 5.048
1499.2 | 49.5 | 5.048
1499.3 | 49.5 | 5.048
1499.4 | 49.5 | 5.048
1499.5 | 49.5 | 5.048
1499.6 | 49.5 | 5.048
1499.7 | 49.5 | 5.047
1499.8 | 49.5 | 5.047
1499.9 | 49.5 | 5.047
1500 | 49.5 | 5.047
1500.1 | 49.5 | 5.047
1500.2 | 49.5 | 5.047
1500.3 | 49.5 | 5.047
1500.4 | 49.5 | 5.047
1500.5 | 49.5 | 5.047
1500.6 | 49.5 | 5.047
1500.7 | 49.5 | 5.047
1500.8 | 49.5 | 5.047
1500.9 | 49.5 | 5.048
1501 | 49.5 | 5.048
1501.1 | 49.5 | 5.048
1501.2 | 49.5 | 5.048
1501.3 | 49.5 | 5.048
1501.4 | 49.5 | 5.048
1501.5 | 49.5 | 5.048
1501.6 | 49.5 | 5.048
1501.7 | 49.5 | 5.048
1501.8 | 49.5 | 5.048
1501.9 | 49.5 | 5.048
1502 | 49.5 | 5.049
1502.1 | 49.5 | 5.049
1502.2 | 49.5 | 5.049
1502.3 | 49.5 | 5.049
1502.4 | 49.5 | 5.049
1502.5 | 49.5 | 5.049
1502.6 | 49.5 | 5.049
1502.7 | 49.5 | 5.049
1502.8 | 49.5 | 5.049
1502.9 | 49.5 | 5.049
1503 | 49.5 | 5.049
1503.1 | 49.5 | 5.049
1503.2 | 49.5 | 5.049
1503.3 | 49.5 | 5.049
1503.4 | 49.5 | 5.049
1503.5 | 49.5 | 5.049
1503.6 | 49.5 | 5.049
1503.7 | 49.5 | 5.049
1503.8 | 49.5 | 5.049
1503.9 | 49.5 | 5.049
1504 | 49.5 | 5.049
1504.1 | 49.5 | 5.049
1504.2 | 49.5 | 5.049
1504.3 | 49.5 | 5.049
1504.4 | 49.5 | 5.049
1504.5 | 49.5 | 5.049
1504.6 | 49.5 | 5.049
1504.7 | 49.5 | 5.049
1504.8 | 49.5 | 5.049
1504.9 | 49.5 | 5.049
1505 | 49.5 | 5.049
1505.1 | 49.5 | 5.049
1505.2 | 49.5 | 5.049
1505.3 | 49.5 | 5.049
1505.4 | 49.5 | 5.048
1505.5 | 49.5 | 5.048
1505.6 | 49.5 | 5.048
1505.7 | 49.5 | 5.048
1505.8 | 49.5 | 5.048
1505.9 | 49.5 | 5.048
1506 | 49.5 | 5.048
1506.1 | 49.5 | 5.048
1506.2 | 49.5 | 5.048
1506.3 | 49.5 | 5.048
1506.4 | 49.5 | 5.048
1506.5 | 49.5 | 5.048
1506.6 | 49.5 | 5.048
1506.7 | 49.5 | 5.048
1506.8 | 49.5 | 5.048
1506.9 | 49.5 | 5.048
1507 | 49.5 | 5.048
1507.1 | 49.5 | 5.048
1507.2 | 49.5 | 5.048
1507.3 | 49.5 | 5.048
1507.4 | 49.5 | 5.048
1507.5 | 49.5 | 5.048
1507.6 | 49.5 | 5.048
1507.7 | 49.5 | 5.049
1507.8 | 49.5 | 5.049
1507.9 | 49.5 | 5.048
1508 | 49.5 | 5.048
1508.1 | 49.5 | 5.048
1508.2 | 49.5 | 5.048
1508.3 | 49.5 | 5.048
1508.4 | 49.5 | 5.048
1508.5 | 49.5 | 5.048
1508.6 | 49.5 | 5.048
1508.7 | 49.5 | 5.048
1508.8 | 49.5 | 5.048
1508.9 | 49.5 | 5.048
1509 | 49.5 | 5.048
1509.1 | 49.5 | 5.048
1509.2 | 49.5 | 5.048
1509.3 | 49.5 | 5.048
1509.4 | 49.5 | 5.048
1509.5 | 49.5 | 5.048
1509.6 | 49.5 | 5.048
1509.7 | 49.5 | 5.048
1509.8 | 49.5 | 5.048
1509.9 | 49.5 | 5.048
1510 | 49.5 | 5.048
1510.1 | 49.5 | 5.048
1510.2 | 49.5 | 5.048
1510.3 | 49.5 | 5.048
1510.4 | 49.5 | 5.048
1510.5 | 49.5 | 5.048
1510.6 | 49.5 | 5.048
1510.7 | 49.5 | 5.048
1510.8 | 49.5 | 5.048
1510.9 | 49.5 | 5.048
1511 | 49.5 | 5.048
1511.1 | 49.5 | 5.048
1511.2 | 49.5 | 5.048
1511.3 | 49.5 | 5.048
1511.4 | 49.5 | 5.048
1511.5 | 49.5 | 5.048
1511.6 | 49.5 | 5.048
1511.7 | 49.5 | 5.048
1511.8 | 49.5 | 5.048
1511.9 | 49.5 | 5.048
1512 | 49.5 | 5.048
1512.1 | 49.5 | 5.048
1512.2 | 49.5 | 5.048
1512.3 | 49.5 | 5.048
1512.4 | 49.5 | 5.048
1512.5 | 49.5 | 5.048
1512.6 | 49.5 | 5.048
1512.7 | 49.5 | 5.048
1512.8 | 49.5 | 5.048
1512.9 | 49.5 | 5.048
1513 | 49.5 | 5.048
1513.1 | 49.5 | 5.048
1513.2 | 49.5 | 5.048
1513.3 | 49.5 | 5.048
1513.4 | 49.5 | 5.048
1513.5 | 49.5 | 5.048
1513.6 | 49.5 | 5.048
1513.7 | 49.5 | 5.048
1513.8 | 49.5 | 5.048
1513.9 | 49.5 | 5.048
1514 | 49.5 | 5.048
1514.1 | 49.5 | 5.048
1514.2 | 49.5 | 5.048
1514.3 | 49.5 | 5.048
1514.4 | 49.5 | 5.048
1514.5 | 49.5 | 5.048
1514.6 | 49.5 | 5.048
1514.7 | 49.5 | 5.048
1514.8 | 49.5 | 5.048
1514.9 | 49.5 | 5.048
1515 | 49.5 | 5.048
1515.1 | 49.5 | 5.049
1515.2 | 49.5 | 5.049
1515.3 | 49.5 | 5.049
1515.4 | 49.5 | 5.049
1515.5 | 49.5 | 5.049
1515.6 | 49.5 | 5.049
1515.7 | 49.5 | 5.049
1515.8 | 49.5 | 5.049
1515.9 | 49.5 | 5.049
1516 | 49.5 | 5.048
1516.1 | 49.5 | 5.048
1516.2 | 49.5 | 5.048
1516.3 | 49.5 | 5.048
1516.4 | 49.5 | 5.048
1516.5 | 49.5 | 5.048
1516.6 | 49.5 | 5.048
1516.7 | 49.5 | 5.048
1516.8 | 49.5 | 5.048
1516.9 | 49.5 | 5.048
1517 | 49.5 | 5.048
1517.1 | 49.5 | 5.048
1517.2 | 49.5 | 5.048
1517.3 | 49.5 | 5.048
1517.4 | 49.5 | 5.048
1517.5 | 49.5 | 5.048
1517.6 | 49.5 | 5.048
1517.7 | 49.5 | 5.048
1517.8 | 49.5 | 5.048
1517.9 | 49.5 | 5.048
1518 | 49.5 | 5.048
1518.1 | 49.5 | 5.048
1518.2 | 49.5 | 5.048
1518.3 | 49.5 | 5.048
1518.4 | 49.5 | 5.048
1518.5 | 49.5 | 5.048
1518.6 | 49.5 | 5.048
1518.7 | 49.5 | 5.048
1518.8 | 49.5 | 5.048
1518.9 | 49.5 | 5.048
1519 | 49.5 | 5.048
1519.1 | 49.5 | 5.048
1519.2 | 49.5 | 5.048
1519.3 | 49.5 | 5.048
1519.4 | 49.5 | 5.048
1519.5 | 49.5 | 5.048
1519.6 | 49.5 | 5.048
1519.7 | 49.5 | 5.049
1519.8 | 49.5 | 5.049
1519.9 | 49.5 | 5.049
1520 | 49.5 | 5.049
1520.1 | 49.5 | 5.049
1520.2 | 49.5 | 5.049
1520.3 | 49.5 | 5.049
1520.4 | 49.5 | 5.049
1520.5 | 49.5 | 5.049
1520.6 | 49.5 | 5.049
1520.7 | 49.5 | 5.049
1520.8 | 49.5 | 5.049
1520.9 | 49.5 | 5.049
1521 | 49.5 | 5.049
1521.1 | 49.5 | 5.049
1521.2 | 49.5 | 5.049
1521.3 | 49.5 | 5.049
1521.4 | 49.5 | 5.049
1521.5 | 49.5 | 5.049
1521.6 | 49.5 | 5.049
1521.7 | 49.5 | 5.048
1521.8 | 49.5 | 5.048
1521.9 | 49.5 | 5.048
1522 | 49.5 | 5.047
1522.1 | 49.5 | 5.047
1522.2 | 49.5 | 5.047
1522.3 | 49.5 | 5.047
1522.4 | 49.5 | 5.047
1522.5 | 49.5 | 5.047
1522.6 | 49.5 | 5.047
1522.7 | 49.5 | 5.047
1522.8 | 49.5 | 5.047
1522.9 | 49.5 | 5.048
1523 | 49.5 | 5.048
1523.1 | 49.5 | 5.048
1523.2 | 49.5 | 5.048
1523.3 | 49.5 | 5.048
1523.4 | 49.5 | 5.048
1523.5 | 49.5 | 5.048
1523.6 | 49.5 | 5.048
1523.7 | 49.5 | 5.048
1523.8 | 49.5 | 5.048
1523.9 | 49.5 | 5.048
1524 | 49.5 | 5.048
1524.1 | 49.5 | 5.048
1524.2 | 49.5 | 5.048
1524.3 | 49.5 | 5.048
1524.4 | 49.5 | 5.048
1524.5 | 49.5 | 5.048
1524.6 | 49.5 | 5.048
1524.7 | 49.5 | 5.048
1524.8 | 49.5 | 5.048
1524.9 | 49.5 | 5.048
1525 | 49.5 | 5.048
1525.1 | 49.5 | 5.048
1525.2 | 49.5 | 5.048
1525.3 | 49.5 | 5.048
1525.4 | 49.5 | 5.048
1525.5 | 49.5 | 5.048
1525.6 | 49.5 | 5.048
1525.7 | 49.5 | 5.048
1525.8 | 49.5 | 5.048
1525.9 | 49.5 | 5.048
1526 | 49.5 | 5.048
1526.1 | 49.5 | 5.048
1526.2 | 49.5 | 5.048
1526.3 | 49.5 | 5.048
1526.4 | 49.5 | 5.048
1526.5 | 49.5 | 5.049
1526.6 | 49.5 | 5.049
1526.7 | 49.5 | 5.049
1526.8 | 49.5 | 5.049
1526.9 | 49.5 | 5.049
1527 | 49.5 | 5.049
1527.1 | 49.5 | 5.049
1527.2 | 49.5 | 5.049
1527.3 | 49.5 | 5.049
1527.4 | 49.5 | 5.049
1527.5 | 49.5 | 5.049
1527.6 | 49.5 | 5.049
1527.7 | 49.5 | 5.048
1527.8 | 49.5 | 5.048
1527.9 | 49.5 | 5.048
1528 | 49.5 | 5.048
1528.1 | 49.5 | 5.048
1528.2 | 49.5 | 5.048
1528.3 | 49.5 | 5.048
1528.4 | 49.5 | 5.048
1528.5 | 49.5 | 5.048
1528.6 | 49.5 | 5.048
1528.7 | 49.5 | 5.048
1528.8 | 49.5 | 5.048
1528.9 | 49.5 | 5.047
1529 | 49.5 | 5.047
1529.1 | 49.5 | 5.047
1529.2 | 49.5 | 5.047
1529.3 | 49.5 | 5.047
1529.4 | 49.5 | 5.047
1529.5 | 49.5 | 5.047
1529.6 | 49.5 | 5.047
1529.7 | 49.5 | 5.047
1529.8 | 49.5 | 5.047
1529.9 | 49.5 | 5.047
1530 | 49.5 | 5.047
1530.1 | 49.5 | 5.047
1530.2 | 49.5 | 5.047
1530.3 | 49.5 | 5.047
1530.4 | 49.5 | 5.047
1530.5 | 49.5 | 5.047
1530.6 | 49.5 | 5.047
1530.7 | 49.5 | 5.047
1530.8 | 49.5 | 5.047
1530.9 | 49.5 | 5.047
1531 | 49.5 | 5.047
1531.1 | 49.5 | 5.047
1531.2 | 49.5 | 5.048
1531.3 | 49.5 | 5.048
1531.4 | 49.5 | 5.048
1531.5 | 49.5 | 5.048
1531.6 | 49.5 | 5.048
1531.7 | 49.5 | 5.048
1531.8 | 49.5 | 5.048
1531.9 | 49.5 | 5.048
1532 | 49.5 | 5.048
1532.1 | 49.5 | 5.048
1532.2 | 49.5 | 5.048
1532.3 | 49.5 | 5.049
1532.4 | 49.5 | 5.049
1532.5 | 49.5 | 5.049
1532.6 | 49.5 | 5.049
1532.7 | 49.5 | 5.049
1532.8 | 49.5 | 5.049
1532.9 | 49.5 | 5.049
1533 | 49.5 | 5.049
1533.1 | 49.5 | 5.049
1533.2 | 49.5 | 5.049
1533.3 | 49.5 | 5.049
1533.4 | 49.5 | 5.049
1533.5 | 49.5 | 5.049
1533.6 | 49.5 | 5.049
1533.7 | 49.5 | 5.049
1533.8 | 49.5 | 5.049
1533.9 | 49.5 | 5.049
1534 | 49.5 | 5.049
1534.1 | 49.5 | 5.049
1534.2 | 49.5 | 5.049
1534.3 | 49.5 | 5.049
1534.4 | 49.5 | 5.049
1534.5 | 49.5 | 5.049
1534.6 | 49.5 | 5.049
1534.7 | 49.5 | 5.049
1534.8 | 49.5 | 5.048
1534.9 | 49.5 | 5.048
1535 | 49.5 | 5.048
1535.1 | 49.5 | 5.048
1535.2 | 49.5 | 5.048
1535.3 | 49.5 | 5.048
1535.4 | 49.5 | 5.048
1535.5 | 49.5 | 5.048
1535.6 | 49.5 | 5.048
1535.7 | 49.5 | 5.048
1535.8 | 49.5 | 5.048
1535.9 | 49.5 | 5.048
1536 | 49.5 | 5.048
1536.1 | 49.5 | 5.048
1536.2 | 49.5 | 5.048
1536.3 | 49.5 | 5.048
1536.4 | 49.5 | 5.048
1536.5 | 49.5 | 5.048
1536.6 | 49.5 | 5.048
1536.7 | 49.5 | 5.048
1536.8 | 49.5 | 5.048
1536.9 | 49.5 | 5.048
1537 | 49.5 | 5.048
1537.1 | 49.5 | 5.048
1537.2 | 49.5 | 5.048
1537.3 | 49.5 | 5.048
1537.4 | 49.5 | 5.048
1537.5 | 49.5 | 5.048
1537.6 | 49.5 | 5.048
1537.7 | 49.5 | 5.048
1537.8 | 49.5 | 5.048
1537.9 | 49.5 | 5.048
1538 | 49.5 | 5.048
1538.1 | 49.5 | 5.048
1538.2 | 49.5 | 5.048
1538.3 | 49.5 | 5.048
1538.4 | 49.5 | 5.048
1538.5 | 49.5 | 5.048
1538.6 | 49.5 | 5.048
1538.7 | 49.5 | 5.048
1538.8 | 49.5 | 5.048
1538.9 | 49.5 | 5.048
1539 | 49.5 | 5.048
1539.1 | 49.5 | 5.048
1539.2 | 49.5 | 5.048
1539.3 | 49.5 | 5.048
1539.4 | 49.5 | 5.048
1539.5 | 49.5 | 5.048
1539.6 | 49.5 | 5.048
1539.7 | 49.5 | 5.048
1539.8 | 49.5 | 5.048
1539.9 | 49.5 | 5.048
1540 | 49.5 | 5.048
1540.1 | 49.5 | 5.048
1540.2 | 49.5 | 5.048
1540.3 | 49.5 | 5.048
1540.4 | 49.5 | 5.048
1540.5 | 49.5 | 5.048
1540.6 | 49.5 | 5.048
1540.7 | 49.5 | 5.048
1540.8 | 49.5 | 5.048
1540.9 | 49.5 | 5.048
1541 | 49.5 | 5.048
1541.1 | 49.5 | 5.048
1541.2 | 49.5 | 5.048
1541.3 | 49.5 | 5.048
1541.4 | 49.5 | 5.048
1541.5 | 49.5 | 5.048
1541.6 | 49.5 | 5.048
1541.7 | 49.5 | 5.048
1541.8 | 49.5 | 5.048
1541.9 | 49.5 | 5.048
1542 | 49.5 | 5.048
1542.1 | 49.5 | 5.048
1542.2 | 49.5 | 5.048
1542.3 | 49.5 | 5.048
1542.4 | 49.5 | 5.048
1542.5 | 49.5 | 5.048
1542.6 | 49.5 | 5.048
1542.7 | 49.5 | 5.048
1542.8 | 49.5 | 5.048
1542.9 | 49.5 | 5.048
1543 | 49.5 | 5.048
1543.1 | 49.5 | 5.048
1543.2 | 49.5 | 5.048
1543.3 | 49.5 | 5.048
1543.4 | 49.5 | 5.048
1543.5 | 49.5 | 5.048
1543.6 | 49.5 | 5.048
1543.7 | 49.5 | 5.048
1543.8 | 49.5 | 5.048
1543.9 | 49.5 | 5.048
1544 | 49.5 | 5.048
1544.1 | 49.5 | 5.048
1544.2 | 49.5 | 5.048
1544.3 | 49.5 | 5.048
1544.4 | 49.5 | 5.048
1544.5 | 49.5 | 5.048
1544.6 | 49.5 | 5.048
1544.7 | 49.5 | 5.048
1544.8 | 49.5 | 5.048
1544.9 | 49.5 | 5.048
1545 | 49.5 | 5.048
1545.1 | 49.5 | 5.048
1545.2 | 49.5 | 5.048
1545.3 | 49.5 | 5.048
1545.4 | 49.5 | 5.048
1545.5 | 49.5 | 5.048
1545.6 | 49.5 | 5.048
1545.7 | 49.5 | 5.048
1545.8 | 49.5 | 5.048
1545.9 | 49.5 | 5.048
1546 | 49.5 | 5.048
1546.1 | 49.5 | 5.048
1546.2 | 49.5 | 5.048
1546.3 | 49.5 | 5.048
1546.4 | 49.5 | 5.048
1546.5 | 49.5 | 5.048
1546.6 | 49.5 | 5.048
1546.7 | 49.5 | 5.048
1546.8 | 49.5 | 5.048
1546.9 | 49.5 | 5.048
1547 | 49.5 | 5.048
1547.1 | 49.5 | 5.048
1547.2 | 49.5 | 5.048
1547.3 | 49.5 | 5.048
1547.4 | 49.5 | 5.048
1547.5 | 49.5 | 5.048
1547.6 | 49.5 | 5.048
1547.7 | 49.5 | 5.048
1547.8 | 49.5 | 5.048
1547.9 | 49.5 | 5.048
1548 | 49.5 | 5.048
1548.1 | 49.5 | 5.048
1548.2 | 49.5 | 5.048
1548.3 | 49.5 | 5.048
1548.4 | 49.5 | 5.048
1548.5 | 49.5 | 5.048
1548.6 | 49.5 | 5.048
1548.7 | 49.5 | 5.048
1548.8 | 49.5 | 5.048
1548.9 | 49.5 | 5.048
1549 | 49.5 | 5.048
1549.1 | 49.5 | 5.048
1549.2 | 49.5 | 5.048
1549.3 | 49.5 | 5.048
1549.4 | 49.5 | 5.048
1549.5 | 49.5 | 5.048
1549.6 | 49.5 | 5.048
1549.7 | 49.5 | 5.048
1549.8 | 49.5 | 5.048
1549.9 | 49.5 | 5.048
1550 | 49.5 | 5.048
1550.1 | 49.5 | 5.048
1550.2 | 49.5 | 5.048
1550.3 | 49.5 | 5.048
1550.4 | 49.5 | 5.048
1550.5 | 49.5 | 5.048
1550.6 | 49.5 | 5.048
1550.7 | 49.5 | 5.048
1550.8 | 49.5 | 5.048
1550.9 | 49.5 | 5.049
1551 | 49.5 | 5.049
1551.1 | 49.5 | 5.049
1551.2 | 49.5 | 5.049
1551.3 | 49.5 | 5.049
1551.4 | 49.5 | 5.049
1551.5 | 49.5 | 5.049
1551.6 | 49.5 | 5.049
1551.7 | 49.5 | 5.049
1551.8 | 49.5 | 5.049
1551.9 | 49.5 | 5.049
1552 | 49.5 | 5.049
1552.1 | 49.5 | 5.049
1552.2 | 49.5 | 5.049
1552.3 | 49.5 | 5.049
1552.4 | 49.5 | 5.049
1552.5 | 49.5 | 5.049
1552.6 | 49.5 | 5.049
1552.7 | 49.5 | 5.049
1552.8 | 49.5 | 5.049
1552.9 | 49.5 | 5.049
1553 | 49.5 | 5.049
1553.1 | 49.5 | 5.049
1553.2 | 49.5 | 5.049
1553.3 | 49.5 | 5.048
1553.4 | 49.5 | 5.048
1553.5 | 49.5 | 5.048
1553.6 | 49.5 | 5.048
1553.7 | 49.5 | 5.048
1553.8 | 49.5 | 5.048
1553.9 | 49.5 | 5.048
1554 | 49.5 | 5.048
1554.1 | 49.5 | 5.048
1554.2 | 49.5 | 5.048
1554.3 | 49.5 | 5.048
1554.4 | 49.5 | 5.048
1554.5 | 49.5 | 5.048
1554.6 | 49.5 | 5.048
1554.7 | 49.5 | 5.048
1554.8 | 49.5 | 5.048
1554.9 | 49.5 | 5.048
1555 | 49.5 | 5.048
1555.1 | 49.5 | 5.048
1555.2 | 49.5 | 5.048
1555.3 | 49.5 | 5.048
1555.4 | 49.5 | 5.048
1555.5 | 49.5 | 5.048
1555.6 | 49.5 | 5.048
1555.7 | 49.5 | 5.048
1555.8 | 49.5 | 5.048
1555.9 | 49.5 | 5.048
1556 | 49.5 | 5.048
1556.1 | 49.5 | 5.048
1556.2 | 49.5 | 5.048
1556.3 | 49.5 | 5.048
1556.4 | 49.5 | 5.048
1556.5 | 49.5 | 5.048
1556.6 | 49.5 | 5.048
1556.7 | 49.5 | 5.048
1556.8 | 49.5 | 5.048
1556.9 | 49.5 | 5.048
1557 | 49.5 | 5.048
1557.1 | 49.5 | 5.048
1557.2 | 49.5 | 5.048
1557.3 | 49.5 | 5.048
1557.4 | 49.5 | 5.048
1557.5 | 49.5 | 5.048
1557.6 | 49.5 | 5.048
1557.7 | 49.5 | 5.048
1557.8 | 49.5 | 5.048
1557.9 | 49.5 | 5.048
1558 | 49.5 | 5.048
1558.1 | 49.5 | 5.048
1558.2 | 49.5 | 5.048
1558.3 | 49.5 | 5.048
1558.4 | 49.5 | 5.048
1558.5 | 49.5 | 5.048
1558.6 | 49.5 | 5.048
1558.7 | 49.5 | 5.048
1558.8 | 49.5 | 5.048
1558.9 | 49.5 | 5.048
1559 | 49.5 | 5.048
1559.1 | 49.5 | 5.048
1559.2 | 49.5 | 5.048
1559.3 | 49.5 | 5.048
1559.4 | 49.5 | 5.048
1559.5 | 49.5 | 5.048
1559.6 | 49.5 | 5.048
1559.7 | 49.5 | 5.048
1559.8 | 49.5 | 5.048
1559.9 | 49.5 | 5.048
1560 | 49.5 | 5.048
1560.1 | 49.5 | 5.048
1560.2 | 49.5 | 5.048
1560.3 | 49.5 | 5.048
1560.4 | 49.5 | 5.048
1560.5 | 49.5 | 5.048
1560.6 | 49.5 | 5.048
1560.7 | 49.5 | 5.048
1560.8 | 49.5 | 5.048
1560.9 | 49.5 | 5.048
1561 | 49.5 | 5.048
1561.1 | 49.5 | 5.048
1561.2 | 49.5 | 5.048
1561.3 | 49.5 | 5.048
1561.4 | 49.5 | 5.048
1561.5 | 49.5 | 5.048
1561.6 | 49.5 | 5.048
1561.7 | 49.5 | 5.048
1561.8 | 49.5 | 5.048
1561.9 | 49.5 | 5.048
1562 | 49.5 | 5.048
1562.1 | 49.5 | 5.048
1562.2 | 49.5 | 5.048
1562.3 | 49.5 | 5.048
1562.4 | 49.5 | 5.048
1562.5 | 49.5 | 5.048
1562.6 | 49.5 | 5.048
1562.7 | 49.5 | 5.048
1562.8 | 49.5 | 5.048
1562.9 | 49.5 | 5.048
1563 | 49.5 | 5.048
1563.1 | 49.5 | 5.048
1563.2 | 49.5 | 5.048
1563.3 | 49.5 | 5.048
1563.4 | 49.5 | 5.048
1563.5 | 49.5 | 5.048
1563.6 | 49.5 | 5.048
1563.7 | 49.5 | 5.048
1563.8 | 49.5 | 5.048
1563.9 | 49.5 | 5.048
1564 | 49.5 | 5.048
1564.1 | 49.5 | 5.048
1564.2 | 49.5 | 5.048
1564.3 | 49.5 | 5.048
1564.4 | 49.5 | 5.048
1564.5 | 49.5 | 5.048
1564.6 | 49.5 | 5.048
1564.7 | 49.5 | 5.048
1564.8 | 49.5 | 5.048
1564.9 | 49.5 | 5.048
1565 | 49.5 | 5.048
1565.1 | 49.5 | 5.048
1565.2 | 49.5 | 5.048
1565.3 | 49.5 | 5.048
1565.4 | 49.5 | 5.048
1565.5 | 49.5 | 5.048
1565.6 | 49.5 | 5.048
1565.7 | 49.5 | 5.048
1565.8 | 49.5 | 5.048
1565.9 | 49.5 | 5.048
1566 | 49.5 | 5.048
1566.1 | 49.5 | 5.048
1566.2 | 49.5 | 5.048
1566.3 | 49.5 | 5.048
1566.4 | 49.5 | 5.048
1566.5 | 49.5 | 5.048
1566.6 | 49.5 | 5.048
1566.7 | 49.5 | 5.048
1566.8 | 49.5 | 5.048
1566.9 | 49.5 | 5.048
1567 | 49.5 | 5.048
1567.1 | 49.5 | 5.048
1567.2 | 49.5 | 5.048
1567.3 | 49.5 | 5.048
1567.4 | 49.5 | 5.048
1567.5 | 49.5 | 5.048
1567.6 | 49.5 | 5.048
1567.7 | 49.5 | 5.048
1567.8 | 49.5 | 5.048
1567.9 | 49.5 | 5.048
1568 | 49.5 | 5.048
1568.1 | 49.5 | 5.048
1568.2 | 49.5 | 5.048
1568.3 | 49.5 | 5.048
1568.4 | 49.5 | 5.048
1568.5 | 49.5 | 5.048
1568.6 | 49.5 | 5.048
1568.7 | 49.5 | 5.048
1568.8 | 49.5 | 5.048
1568.9 | 49.5 | 5.048
1569 | 49.5 | 5.048
1569.1 | 49.5 | 5.048
1569.2 | 49.5 | 5.048
1569.3 | 49.5 | 5.048
1569.4 | 49.5 | 5.048
1569.5 | 49.5 | 5.048
1569.6 | 49.5 | 5.048
1569.7 | 49.5 | 5.048
1569.8 | 49.5 | 5.048
1569.9 | 49.5 | 5.048
1570 | 49.5 | 5.048
1570.1 | 49.5 | 5.048
1570.2 | 49.5 | 5.048
1570.3 | 49.5 | 5.048
1570.4 | 49.5 | 5.048
1570.5 | 49.5 | 5.048
1570.6 | 49.5 | 5.048
1570.7 | 49.5 | 5.048
1570.8 | 49.5 | 5.048
1570.9 | 49.5 | 5.048
1571 | 49.5 | 5.048
1571.1 | 49.5 | 5.048
1571.2 | 49.5 | 5.048
1571.3 | 49.5 | 5.048
1571.4 | 49.5 | 5.048
1571.5 | 49.5 | 5.048
1571.6 | 49.5 | 5.048
1571.7 | 49.5 | 5.048
1571.8 | 49.5 | 5.048
1571.9 | 49.5 | 5.048
1572 | 49.5 | 5.048
1572.1 | 49.5 | 5.048
1572.2 | 49.5 | 5.048
1572.3 | 49.5 | 5.048
1572.4 | 49.5 | 5.048
1572.5 | 49.5 | 5.048
1572.6 | 49.5 | 5.048
1572.7 | 49.5 | 5.048
1572.8 | 49.5 | 5.048
1572.9 | 49.5 | 5.048
1573 | 49.5 | 5.048
1573.1 | 49.5 | 5.048
1573.2 | 49.5 | 5.048
1573.3 | 49.5 | 5.048
1573.4 | 49.5 | 5.048
1573.5 | 49.5 | 5.048
1573.6 | 49.5 | 5.048
1573.7 | 49.5 | 5.048
1573.8 | 49.5 | 5.048
1573.9 | 49.5 | 5.048
1574 | 49.5 | 5.048
1574.1 | 49.5 | 5.048
1574.2 | 49.5 | 5.048
1574.3 | 49.5 | 5.048
1574.4 | 49.5 | 5.048
1574.5 | 49.5 | 5.048
1574.6 | 49.5 | 5.048
1574.7 | 49.5 | 5.048
1574.8 | 49.5 | 5.048
1574.9 | 49.5 | 5.048
1575 | 49.5 | 5.048
1575.1 | 49.5 | 5.048
1575.2 | 49.5 | 5.048
1575.3 | 49.5 | 5.048
1575.4 | 49.5 | 5.048
1575.5 | 49.5 | 5.048
1575.6 | 49.5 | 5.048
1575.7 | 49.5 | 5.049
1575.8 | 49.5 | 5.049
1575.9 | 49.5 | 5.049
1576 | 49.5 | 5.049
1576.1 | 49.5 | 5.049
1576.2 | 49.5 | 5.049
1576.3 | 49.5 | 5.049
1576.4 | 49.5 | 5.049
1576.5 | 49.5 | 5.049
1576.6 | 49.5 | 5.049
1576.7 | 49.5 | 5.049
1576.8 | 49.5 | 5.048
1576.9 | 49.5 | 5.048
1577 | 49.5 | 5.048
1577.1 | 49.5 | 5.048
1577.2 | 49.5 | 5.048
1577.3 | 49.5 | 5.048
1577.4 | 49.5 | 5.048
1577.5 | 49.5 | 5.048
1577.6 | 49.5 | 5.048
1577.7 | 49.5 | 5.048
1577.8 | 49.5 | 5.048
1577.9 | 49.5 | 5.048
1578 | 49.5 | 5.048
1578.1 | 49.5 | 5.048
1578.2 | 49.5 | 5.048
1578.3 | 49.5 | 5.048
1578.4 | 49.5 | 5.048
1578.5 | 49.5 | 5.048
1578.6 | 49.5 | 5.048
1578.7 | 49.5 | 5.048
1578.8 | 49.5 | 5.048
1578.9 | 49.5 | 5.048
1579 | 49.5 | 5.048
1579.1 | 49.5 | 5.048
1579.2 | 49.5 | 5.048
1579.3 | 49.5 | 5.048
1579.4 | 49.5 | 5.048
1579.5 | 49.5 | 5.048
1579.6 | 49.5 | 5.048
1579.7 | 49.5 | 5.048
1579.8 | 49.5 | 5.048
1579.9 | 49.5 | 5.048
1580 | 49.5 | 5.048
1580.1 | 49.5 | 5.048
1580.2 | 49.5 | 5.048
1580.3 | 49.5 | 5.048
1580.4 | 49.5 | 5.048
1580.5 | 49.5 | 5.048
1580.6 | 49.5 | 5.048
1580.7 | 49.5 | 5.048
1580.8 | 49.5 | 5.048
1580.9 | 49.5 | 5.048
1581 | 49.5 | 5.048
1581.1 | 49.5 | 5.048
1581.2 | 49.5 | 5.048
1581.3 | 49.5 | 5.048
1581.4 | 49.5 | 5.048
1581.5 | 49.5 | 5.048
1581.6 | 49.5 | 5.048
1581.7 | 49.5 | 5.048
1581.8 | 49.5 | 5.048
1581.9 | 49.5 | 5.048
1582 | 49.5 | 5.048
1582.1 | 49.5 | 5.048
1582.2 | 49.5 | 5.048
1582.3 | 49.5 | 5.048
1582.4 | 49.5 | 5.048
1582.5 | 49.5 | 5.048
1582.6 | 49.5 | 5.048
1582.7 | 49.5 | 5.048
1582.8 | 49.5 | 5.048
1582.9 | 49.5 | 5.048
1583 | 49.5 | 5.048
1583.1 | 49.5 | 5.048
1583.2 | 49.5 | 5.048
1583.3 | 49.5 | 5.048
1583.4 | 49.5 | 5.048
1583.5 | 49.5 | 5.048
1583.6 | 49.5 | 5.048
1583.7 | 49.5 | 5.048
1583.8 | 49.5 | 5.048
1583.9 | 49.5 | 5.048
1584 | 49.5 | 5.048
1584.1 | 49.5 | 5.048
1584.2 | 49.5 | 5.048
1584.3 | 49.5 | 5.048
1584.4 | 49.5 | 5.048
1584.5 | 49.5 | 5.048
1584.6 | 49.5 | 5.048
1584.7 | 49.5 | 5.048
1584.8 | 49.5 | 5.048
1584.9 | 49.5 | 5.048
1585 | 49.5 | 5.048
1585.1 | 49.5 | 5.048
1585.2 | 49.5 | 5.048
1585.3 | 49.5 | 5.048
1585.4 | 49.5 | 5.048
1585.5 | 49.5 | 5.048
1585.6 | 49.5 | 5.048
1585.7 | 49.5 | 5.048
1585.8 | 49.5 | 5.048
1585.9 | 49.5 | 5.048
1586 | 49.5 | 5.048
1586.1 | 49.5 | 5.048
1586.2 | 49.5 | 5.048
1586.3 | 49.5 | 5.048
1586.4 | 49.5 | 5.048
1586.5 | 49.5 | 5.048
1586.6 | 49.5 | 5.048
1586.7 | 49.5 | 5.048
1586.8 | 49.5 | 5.048
1586.9 | 49.5 | 5.048
1587 | 49.5 | 5.048
1587.1 | 49.5 | 5.048
1587.2 | 49.5 | 5.048
1587.3 | 49.5 | 5.048
1587.4 | 49.5 | 5.048
1587.5 | 49.5 | 5.048
1587.6 | 49.5 | 5.048
1587.7 | 49.5 | 5.048
1587.8 | 49.5 | 5.048
1587.9 | 49.5 | 5.048
1588 | 49.5 | 5.048
1588.1 | 49.5 | 5.048
1588.2 | 49.5 | 5.048
1588.3 | 49.5 | 5.048
1588.4 | 49.5 | 5.048
1588.5 | 49.5 | 5.048
1588.6 | 49.5 | 5.048
1588.7 | 49.5 | 5.048
1588.8 | 49.5 | 5.048
1588.9 | 49.5 | 5.048
1589 | 49.5 | 5.048
1589.1 | 49.5 | 5.048
1589.2 | 49.5 | 5.048
1589.3 | 49.5 | 5.048
1589.4 | 49.5 | 5.048
1589.5 | 49.5 | 5.048
1589.6 | 49.5 | 5.048
1589.7 | 49.5 | 5.048
1589.8 | 49.5 | 5.048
1589.9 | 49.5 | 5.048
1590 | 49.5 | 5.048
1590.1 | 49.5 | 5.048
1590.2 | 49.5 | 5.048
1590.3 | 49.5 | 5.048
1590.4 | 49.5 | 5.048
1590.5 | 49.5 | 5.048
1590.6 | 49.5 | 5.048
1590.7 | 49.5 | 5.048
1590.8 | 49.5 | 5.048
1590.9 | 49.5 | 5.048
1591 | 49.5 | 5.048
1591.1 | 49.5 | 5.048
1591.2 | 49.5 | 5.048
1591.3 | 49.5 | 5.048
1591.4 | 49.5 | 5.048
1591.5 | 49.5 | 5.048
1591.6 | 49.5 | 5.048
1591.7 | 49.5 | 5.048
1591.8 | 49.5 | 5.048
1591.9 | 49.5 | 5.048
1592 | 49.5 | 5.048
1592.1 | 49.5 | 5.048
1592.2 | 49.5 | 5.048
1592.3 | 49.5 | 5.048
1592.4 | 49.5 | 5.048
1592.5 | 49.5 | 5.048
1592.6 | 49.5 | 5.048
1592.7 | 49.5 | 5.048
1592.8 | 49.5 | 5.048
1592.9 | 49.5 | 5.048
1593 | 49.5 | 5.048
1593.1 | 49.5 | 5.048
1593.2 | 49.5 | 5.048
1593.3 | 49.5 | 5.048
1593.4 | 49.5 | 5.048
1593.5 | 49.5 | 5.048
1593.6 | 49.5 | 5.048
1593.7 | 49.5 | 5.048
1593.8 | 49.5 | 5.048
1593.9 | 49.5 | 5.048
1594 | 49.5 | 5.048
1594.1 | 49.5 | 5.048
1594.2 | 49.5 | 5.048
1594.3 | 49.5 | 5.048
1594.4 | 49.5 | 5.048
1594.5 | 49.5 | 5.048
1594.6 | 49.5 | 5.048
1594.7 | 49.5 | 5.048
1594.8 | 49.5 | 5.048
1594.9 | 49.5 | 5.048
1595 | 49.5 | 5.048
1595.1 | 49.5 | 5.048
1595.2 | 49.5 | 5.048
1595.3 | 49.5 | 5.048
1595.4 | 49.5 | 5.048
1595.5 | 49.5 | 5.048
1595.6 | 49.5 | 5.048
1595.7 | 49.5 | 5.049
1595.8 | 49.5 | 5.049
1595.9 | 49.5 | 5.049
1596 | 49.5 | 5.049
1596.1 | 49.5 | 5.049
1596.2 | 49.5 | 5.049
1596.3 | 49.5 | 5.049
1596.4 | 49.5 | 5.049
1596.5 | 49.5 | 5.049
1596.6 | 49.5 | 5.049
1596.7 | 49.5 | 5.048
1596.8 | 49.5 | 5.048
1596.9 | 49.5 | 5.048
1597 | 49.5 | 5.048
1597.1 | 49.5 | 5.048
1597.2 | 49.5 | 5.048
1597.3 | 49.5 | 5.048
1597.4 | 49.5 | 5.048
1597.5 | 49.5 | 5.048
1597.6 | 49.5 | 5.048
1597.7 | 49.5 | 5.048
1597.8 | 49.5 | 5.048
1597.9 | 49.5 | 5.048
1598 | 49.5 | 5.048
1598.1 | 49.5 | 5.048
1598.2 | 49.5 | 5.048
1598.3 | 49.5 | 5.048
1598.4 | 49.5 | 5.048
1598.5 | 49.5 | 5.048
1598.6 | 49.5 | 5.048
1598.7 | 49.5 | 5.048
1598.8 | 49.5 | 5.048
1598.9 | 49.5 | 5.049
1599 | 49.5 | 5.049
1599.1 | 49.5 | 5.049
1599.2 | 49.5 | 5.049
1599.3 | 49.5 | 5.049
1599.4 | 49.5 | 5.049
1599.5 | 49.5 | 5.049
1599.6 | 49.5 | 5.049
1599.7 | 49.5 | 5.049
1599.8 | 49.5 | 5.049
1599.9 | 49.5 | 5.049
1600 | 49.5 | 5.049
1600.1 | 49.5 | 5.049
1600.2 | 49.5 | 5.049
1600.3 | 49.5 | 5.049
1600.4 | 49.5 | 5.049
1600.5 | 49.5 | 5.049
1600.6 | 49.5 | 5.049
1600.7 | 49.5 | 5.049
1600.8 | 49.5 | 5.049
1600.9 | 49.5 | 5.049
1601 | 49.5 | 5.049
1601.1 | 49.5 | 5.049
1601.2 | 49.5 | 5.049
1601.3 | 49.5 | 5.048
1601.4 | 49.5 | 5.048
1601.5 | 49.5 | 5.048
1601.6 | 49.5 | 5.048
1601.7 | 49.5 | 5.048
1601.8 | 49.5 | 5.048
1601.9 | 49.5 | 5.048
1602 | 49.5 | 5.048
1602.1 | 49.5 | 5.048
1602.2 | 49.5 | 5.048
1602.3 | 49.5 | 5.048
1602.4 | 49.5 | 5.048
1602.5 | 49.5 | 5.048
1602.6 | 49.5 | 5.048
1602.7 | 49.5 | 5.048
1602.8 | 49.5 | 5.048
1602.9 | 49.5 | 5.048
1603 | 49.5 | 5.048
1603.1 | 49.5 | 5.048
1603.2 | 49.5 | 5.048
1603.3 | 49.5 | 5.048
1603.4 | 49.5 | 5.048
1603.5 | 49.5 | 5.048
1603.6 | 49.5 | 5.048
1603.7 | 49.5 | 5.048
1603.8 | 49.5 | 5.048
1603.9 | 49.5 | 5.048
1604 | 49.5 | 5.048
1604.1 | 49.5 | 5.048
1604.2 | 49.5 | 5.048
1604.3 | 49.5 | 5.048
1604.4 | 49.5 | 5.048
1604.5 | 49.5 | 5.048
1604.6 | 49.5 | 5.048
1604.7 | 49.5 | 5.048
1604.8 | 49.5 | 5.048
1604.9 | 49.5 | 5.048
1605 | 49.5 | 5.048
1605.1 | 49.5 | 5.048
1605.2 | 49.5 | 5.048
1605.3 | 49.5 | 5.048
1605.4 | 49.5 | 5.048
1605.5 | 49.5 | 5.048
1605.6 | 49.5 | 5.048
1605.7 | 49.5 | 5.048
1605.8 | 49.5 | 5.048
1605.9 | 49.5 | 5.048
1606 | 49.5 | 5.048
1606.1 | 49.5 | 5.048
1606.2 | 49.5 | 5.048
1606.3 | 49.5 | 5.048
1606.4 | 49.5 | 5.048
1606.5 | 49.5 | 5.048
1606.6 | 49.5 | 5.048
1606.7 | 49.5 | 5.048
1606.8 | 49.5 | 5.048
1606.9 | 49.5 | 5.048
1607 | 49.5 | 5.048
1607.1 | 49.5 | 5.048
1607.2 | 49.5 | 5.048
1607.3 | 49.5 | 5.048
1607.4 | 49.5 | 5.048
1607.5 | 49.5 | 5.048
1607.6 | 49.5 | 5.048
1607.7 | 49.5 | 5.048
1607.8 | 49.5 | 5.048
1607.9 | 49.5 | 5.048
1608 | 49.5 | 5.048
1608.1 | 49.5 | 5.048
1608.2 | 49.5 | 5.048
1608.3 | 49.5 | 5.048
1608.4 | 49.5 | 5.048
1608.5 | 49.5 | 5.048
1608.6 | 49.5 | 5.048
1608.7 | 49.5 | 5.048
1608.8 | 49.5 | 5.048
1608.9 | 49.5 | 5.048
1609 | 49.5 | 5.048
1609.1 | 49.5 | 5.048
1609.2 | 49.5 | 5.048
1609.3 | 49.5 | 5.048
1609.4 | 49.5 | 5.048
1609.5 | 49.5 | 5.048
1609.6 | 49.5 | 5.048
1609.7 | 49.5 | 5.048
1609.8 | 49.5 | 5.048
1609.9 | 49.5 | 5.048
1610 | 49.5 | 5.048
1610.1 | 49.5 | 5.048
1610.2 | 49.5 | 5.048
1610.3 | 49.5 | 5.048
1610.4 | 49.5 | 5.048
1610.5 | 49.5 | 5.048
1610.6 | 49.5 | 5.049
1610.7 | 49.5 | 5.049
1610.8 | 49.5 | 5.049
1610.9 | 49.5 | 5.049
1611 | 49.5 | 5.049
1611.1 | 49.5 | 5.049
1611.2 | 49.5 | 5.049
1611.3 | 49.5 | 5.049
1611.4 | 49.5 | 5.049
1611.5 | 49.5 | 5.049
1611.6 | 49.5 | 5.049
1611.7 | 49.5 | 5.049
1611.8 | 49.5 | 5.049
1611.9 | 49.5 | 5.049
1612 | 49.5 | 5.049
1612.1 | 49.5 | 5.049
1612.2 | 49.5 | 5.049
1612.3 | 49.5 | 5.049
1612.4 | 49.5 | 5.049
1612.5 | 49.5 | 5.049
1612.6 | 49.5 | 5.049
1612.7 | 49.5 | 5.049
1612.8 | 49.5 | 5.049
1612.9 | 49.5 | 5.049
1613 | 49.5 | 5.048
1613.1 | 49.5 | 5.048
1613.2 | 49.5 | 5.048
1613.3 | 49.5 | 5.048
1613.4 | 49.5 | 5.048
1613.5 | 49.5 | 5.048
1613.6 | 49.5 | 5.048
1613.7 | 49.5 | 5.048
1613.8 | 49.5 | 5.048
1613.9 | 49.5 | 5.048
1614 | 49.5 | 5.048
1614.1 | 49.5 | 5.048
1614.2 | 49.5 | 5.048
1614.3 | 49.5 | 5.048
1614.4 | 49.5 | 5.048
1614.5 | 49.5 | 5.048
1614.6 | 49.5 | 5.048
1614.7 | 49.5 | 5.048
1614.8 | 49.5 | 5.048
1614.9 | 49.5 | 5.048
1615 | 49.5 | 5.048
1615.1 | 49.5 | 5.048
1615.2 | 49.5 | 5.048
1615.3 | 49.5 | 5.048
1615.4 | 49.5 | 5.048
1615.5 | 49.5 | 5.048
1615.6 | 49.5 | 5.048
1615.7 | 49.5 | 5.048
1615.8 | 49.5 | 5.048
1615.9 | 49.5 | 5.048
1616 | 49.5 | 5.048
1616.1 | 49.5 | 5.048
1616.2 | 49.5 | 5.048
1616.3 | 49.5 | 5.048
1616.4 | 49.5 | 5.048
1616.5 | 49.5 | 5.048
1616.6 | 49.5 | 5.048
1616.7 | 49.5 | 5.048
1616.8 | 49.5 | 5.048
1616.9 | 49.5 | 5.048
1617 | 49.5 | 5.048
1617.1 | 49.5 | 5.048
1617.2 | 49.5 | 5.048
1617.3 | 49.5 | 5.048
1617.4 | 49.5 | 5.048
1617.5 | 49.5 | 5.048
1617.6 | 49.5 | 5.048
1617.7 | 49.5 | 5.048
1617.8 | 49.5 | 5.048
1617.9 | 49.5 | 5.048
1618 | 49.5 | 5.048
1618.1 | 49.5 | 5.048
1618.2 | 49.5 | 5.048
1618.3 | 49.5 | 5.048
1618.4 | 49.5 | 5.048
1618.5 | 49.5 | 5.048
1618.6 | 49.5 | 5.048
1618.7 | 49.5 | 5.048
1618.8 | 49.5 | 5.048
1618.9 | 49.5 | 5.048
1619 | 49.5 | 5.048
1619.1 | 49.5 | 5.048
1619.2 | 49.5 | 5.048
1619.3 | 49.5 | 5.048
1619.4 | 49.5 | 5.048
1619.5 | 49.5 | 5.048
1619.6 | 49.5 | 5.048
1619.7 | 49.5 | 5.048
1619.8 | 49.5 | 5.048
1619.9 | 49.5 | 5.048
1620 | 49.5 | 5.048
1620.1 | 49.5 | 5.048
1620.2 | 49.5 | 5.048
1620.3 | 49.5 | 5.048
1620.4 | 49.5 | 5.048
1620.5 | 49.5 | 5.048
1620.6 | 49.5 | 5.048
1620.7 | 49.5 | 5.048
1620.8 | 49.5 | 5.048
1620.9 | 49.5 | 5.048
1621 | 49.5 | 5.048
1621.1 | 49.5 | 5.048
1621.2 | 49.5 | 5.048
1621.3 | 49.5 | 5.048
1621.4 | 49.5 | 5.048
1621.5 | 49.5 | 5.048
1621.6 | 49.5 | 5.048
1621.7 | 49.5 | 5.048
1621.8 | 49.5 | 5.048
1621.9 | 49.5 | 5.048
1622 | 49.5 | 5.048
1622.1 | 49.5 | 5.048
1622.2 | 49.5 | 5.048
1622.3 | 49.5 | 5.048
1622.4 | 49.5 | 5.048
1622.5 | 49.5 | 5.048
1622.6 | 49.5 | 5.048
1622.7 | 49.5 | 5.048
1622.8 | 49.5 | 5.048
1622.9 | 49.5 | 5.048
1623 | 49.5 | 5.048
1623.1 | 49.5 | 5.048
1623.2 | 49.5 | 5.048
1623.3 | 49.5 | 5.048
1623.4 | 49.5 | 5.048
1623.5 | 49.5 | 5.048
1623.6 | 49.5 | 5.048
1623.7 | 49.5 | 5.048
1623.8 | 49.5 | 5.048
1623.9 | 49.5 | 5.048
1624 | 49.5 | 5.048
1624.1 | 49.5 | 5.048
1624.2 | 49.5 | 5.048
1624.3 | 49.5 | 5.048
1624.4 | 49.5 | 5.048
1624.5 | 49.5 | 5.048
1624.6 | 49.5 | 5.048
1624.7 | 49.5 | 5.048
1624.8 | 49.5 | 5.048
1624.9 | 49.5 | 5.048
1625 | 49.5 | 5.048
1625.1 | 49.5 | 5.048
1625.2 | 49.5 | 5.048
1625.3 | 49.5 | 5.048
1625.4 | 49.5 | 5.048
1625.5 | 49.5 | 5.048
1625.6 | 49.5 | 5.048
1625.7 | 49.5 | 5.048
1625.8 | 49.5 | 5.048
1625.9 | 49.5 | 5.048
1626 | 49.5 | 5.048
1626.1 | 49.5 | 5.048
1626.2 | 49.5 | 5.048
1626.3 | 49.5 | 5.048
1626.4 | 49.5 | 5.048
1626.5 | 49.5 | 5.048
1626.6 | 49.5 | 5.048
1626.7 | 49.5 | 5.048
1626.8 | 49.5 | 5.048
1626.9 | 49.5 | 5.048
1627 | 49.5 | 5.048
1627.1 | 49.5 | 5.048
1627.2 | 49.5 | 5.048
1627.3 | 49.5 | 5.048
1627.4 | 49.5 | 5.048
1627.5 | 49.5 | 5.048
1627.6 | 49.5 | 5.048
1627.7 | 49.5 | 5.048
1627.8 | 49.5 | 5.048
1627.9 | 49.5 | 5.048
1628 | 49.5 | 5.048
1628.1 | 49.5 | 5.048
1628.2 | 49.5 | 5.048
1628.3 | 49.5 | 5.048
1628.4 | 49.5 | 5.048
1628.5 | 49.5 | 5.048
1628.6 | 49.5 | 5.048
1628.7 | 49.5 | 5.048
1628.8 | 49.5 | 5.048
1628.9 | 49.5 | 5.048
1629 | 49.5 | 5.048
1629.1 | 49.5 | 5.048
1629.2 | 49.5 | 5.048
1629.3 | 49.5 | 5.048
1629.4 | 49.5 | 5.048
1629.5 | 49.5 | 5.048
1629.6 | 49.5 | 5.048
1629.7 | 49.5 | 5.048
1629.8 | 49.5 | 5.048
1629.9 | 49.5 | 5.048
1630 | 49.5 | 5.048
1630.1 | 49.5 | 5.048
1630.2 | 49.5 | 5.048
1630.3 | 49.5 | 5.048
1630.4 | 49.5 | 5.048
1630.5 | 49.5 | 5.048
1630.6 | 49.5 | 5.048
1630.7 | 49.5 | 5.048
1630.8 | 49.5 | 5.048
1630.9 | 49.5 | 5.048
1631 | 49.5 | 5.048
1631.1 | 49.5 | 5.048
1631.2 | 49.5 | 5.048
1631.3 | 49.5 | 5.048
1631.4 | 49.5 | 5.048
1631.5 | 49.5 | 5.048
1631.6 | 49.5 | 5.048
1631.7 | 49.5 | 5.048
1631.8 | 49.5 | 5.048
1631.9 | 49.5 | 5.048
1632 | 49.5 | 5.048
1632.1 | 49.5 | 5.048
1632.2 | 49.5 | 5.048
1632.3 | 49.5 | 5.048
1632.4 | 49.5 | 5.048
1632.5 | 49.5 | 5.048
1632.6 | 49.5 | 5.048
1632.7 | 49.5 | 5.048
1632.8 | 49.5 | 5.048
1632.9 | 49.5 | 5.048
1633 | 49.5 | 5.048
1633.1 | 49.5 | 5.048
1633.2 | 49.5 | 5.048
1633.3 | 49.5 | 5.048
1633.4 | 49.5 | 5.048
1633.5 | 49.5 | 5.048
1633.6 | 49.5 | 5.048
1633.7 | 49.5 | 5.048
1633.8 | 49.5 | 5.048
1633.9 | 49.5 | 5.048
1634 | 49.5 | 5.048
1634.1 | 49.5 | 5.048
1634.2 | 49.5 | 5.048
1634.3 | 49.5 | 5.048
1634.4 | 49.5 | 5.048
1634.5 | 49.5 | 5.048
1634.6 | 49.5 | 5.048
1634.7 | 49.5 | 5.048
1634.8 | 49.5 | 5.048
1634.9 | 49.5 | 5.048
1635 | 49.5 | 5.048
1635.1 | 49.5 | 5.048
1635.2 | 49.5 | 5.048
1635.3 | 49.5 | 5.048
1635.4 | 49.5 | 5.048
1635.5 | 49.5 | 5.048
1635.6 | 49.5 | 5.048
1635.7 | 49.5 | 5.048
1635.8 | 49.5 | 5.048
1635.9 | 49.5 | 5.048
1636 | 49.5 | 5.048
1636.1 | 49.5 | 5.048
1636.2 | 49.5 | 5.048
1636.3 | 49.5 | 5.048
1636.4 | 49.5 | 5.048
1636.5 | 49.5 | 5.048
1636.6 | 49.5 | 5.048
1636.7 | 49.5 | 5.048
1636.8 | 49.5 | 5.048
1636.9 | 49.5 | 5.048
1637 | 49.5 | 5.048
1637.1 | 49.5 | 5.048
1637.2 | 49.5 | 5.048
1637.3 | 49.5 | 5.048
1637.4 | 49.5 | 5.048
1637.5 | 49.5 | 5.048
1637.6 | 49.5 | 5.048
1637.7 | 49.5 | 5.048
1637.8 | 49.5 | 5.048
1637.9 | 49.5 | 5.048
1638 | 49.5 | 5.048
1638.1 | 49.5 | 5.048
1638.2 | 49.5 | 5.048
1638.3 | 49.5 | 5.048
1638.4 | 49.5 | 5.048
1638.5 | 49.5 | 5.048
1638.6 | 49.5 | 5.048
1638.7 | 49.5 | 5.048
1638.8 | 49.5 | 5.048
1638.9 | 49.5 | 5.048
1639 | 49.5 | 5.048
1639.1 | 49.5 | 5.048
1639.2 | 49.5 | 5.048
1639.3 | 49.5 | 5.048
1639.4 | 49.5 | 5.048
1639.5 | 49.5 | 5.048
1639.6 | 49.5 | 5.048
1639.7 | 49.5 | 5.048
1639.8 | 49.5 | 5.048
1639.9 | 49.5 | 5.048
1640 | 49.5 | 5.048
1640.1 | 49.5 | 5.048
1640.2 | 49.5 | 5.048
1640.3 | 49.5 | 5.048
1640.4 | 49.5 | 5.048
1640.5 | 49.5 | 5.048
1640.6 | 49.5 | 5.048
1640.7 | 49.5 | 5.048
1640.8 | 49.5 | 5.048
1640.9 | 49.5 | 5.048
1641 | 49.5 | 5.048
1641.1 | 49.5 | 5.048
1641.2 | 49.5 | 5.048
1641.3 | 49.5 | 5.049
1641.4 | 49.5 | 5.049
1641.5 | 49.5 | 5.049
1641.6 | 49.5 | 5.049
1641.7 | 49.5 | 5.049
1641.8 | 49.5 | 5.049
1641.9 | 49.5 | 5.049
1642 | 49.5 | 5.049
1642.1 | 49.5 | 5.049
1642.2 | 49.5 | 5.049
1642.3 | 49.5 | 5.049
1642.4 | 49.5 | 5.049
1642.5 | 49.5 | 5.048
1642.6 | 49.5 | 5.048
1642.7 | 49.5 | 5.048
1642.8 | 49.5 | 5.048
1642.9 | 49.5 | 5.048
1643 | 49.5 | 5.048
1643.1 | 49.5 | 5.048
1643.2 | 49.5 | 5.048
1643.3 | 49.5 | 5.048
1643.4 | 49.5 | 5.048
1643.5 | 49.5 | 5.048
1643.6 | 49.5 | 5.048
1643.7 | 49.5 | 5.048
1643.8 | 49.5 | 5.048
1643.9 | 49.5 | 5.048
1644 | 49.5 | 5.048
1644.1 | 49.5 | 5.048
1644.2 | 49.5 | 5.048
1644.3 | 49.5 | 5.048
1644.4 | 49.5 | 5.048
1644.5 | 49.5 | 5.048
1644.6 | 49.5 | 5.048
1644.7 | 49.5 | 5.048
1644.8 | 49.5 | 5.048
1644.9 | 49.5 | 5.048
1645 | 49.5 | 5.048
1645.1 | 49.5 | 5.048
1645.2 | 49.5 | 5.048
1645.3 | 49.5 | 5.048
1645.4 | 49.5 | 5.048
1645.5 | 49.5 | 5.048
1645.6 | 49.5 | 5.048
1645.7 | 49.5 | 5.048
1645.8 | 49.5 | 5.048
1645.9 | 49.5 | 5.048
1646 | 49.5 | 5.048
1646.1 | 49.5 | 5.048
1646.2 | 49.5 | 5.048
1646.3 | 49.5 | 5.048
1646.4 | 49.5 | 5.048
1646.5 | 49.5 | 5.048
1646.6 | 49.5 | 5.048
1646.7 | 49.5 | 5.048
1646.8 | 49.5 | 5.048
1646.9 | 49.5 | 5.048
1647 | 49.5 | 5.048
1647.1 | 49.5 | 5.048
1647.2 | 49.5 | 5.048
1647.3 | 49.5 | 5.048
1647.4 | 49.5 | 5.048
1647.5 | 49.5 | 5.048
1647.6 | 49.5 | 5.048
1647.7 | 49.5 | 5.048
1647.8 | 49.5 | 5.048
1647.9 | 49.5 | 5.048
1648 | 49.5 | 5.048
1648.1 | 49.5 | 5.048
1648.2 | 49.5 | 5.048
1648.3 | 49.5 | 5.048
1648.4 | 49.5 | 5.048
1648.5 | 49.5 | 5.048
1648.6 | 49.5 | 5.048
1648.7 | 49.5 | 5.048
1648.8 | 49.5 | 5.048
1648.9 | 49.5 | 5.048
1649 | 49.5 | 5.048
1649.1 | 49.5 | 5.048
1649.2 | 49.5 | 5.048
1649.3 | 49.5 | 5.048
1649.4 | 49.5 | 5.048
1649.5 | 49.5 | 5.048
1649.6 | 49.5 | 5.048
1649.7 | 49.5 | 5.048
1649.8 | 49.5 | 5.048
1649.9 | 49.5 | 5.048
1650 | 49.5 | 5.048
1650.1 | 49.5 | 5.048
1650.2 | 49.5 | 5.048
1650.3 | 49.5 | 5.048
1650.4 | 49.5 | 5.048
1650.5 | 49.5 | 5.048
1650.6 | 49.5 | 5.048
1650.7 | 49.5 | 5.048
1650.8 | 49.5 | 5.048
1650.9 | 49.5 | 5.048
1651 | 49.5 | 5.048
1651.1 | 49.5 | 5.048
1651.2 | 49.5 | 5.048
1651.3 | 49.5 | 5.048
1651.4 | 49.5 | 5.048
1651.5 | 49.5 | 5.048
1651.6 | 49.5 | 5.047
1651.7 | 49.5 | 5.047
1651.8 | 49.5 | 5.047
1651.9 | 49.5 | 5.047
1652 | 49.5 | 5.047
1652.1 | 49.5 | 5.048
1652.2 | 49.5 | 5.048
1652.3 | 49.5 | 5.048
1652.4 | 49.5 | 5.048
1652.5 | 49.5 | 5.048
1652.6 | 49.5 | 5.048
1652.7 | 49.5 | 5.048
1652.8 | 49.5 | 5.048
1652.9 | 49.5 | 5.048
1653 | 49.5 | 5.048
1653.1 | 49.5 | 5.048
1653.2 | 49.5 | 5.048
1653.3 | 49.5 | 5.048
1653.4 | 49.5 | 5.048
1653.5 | 49.5 | 5.048
1653.6 | 49.5 | 5.048
1653.7 | 49.5 | 5.048
1653.8 | 49.5 | 5.048
1653.9 | 49.5 | 5.048
1654 | 49.5 | 5.048
1654.1 | 49.5 | 5.048
1654.2 | 49.5 | 5.048
1654.3 | 49.5 | 5.048
1654.4 | 49.5 | 5.048
1654.5 | 49.5 | 5.048
1654.6 | 49.5 | 5.048
1654.7 | 49.5 | 5.048
1654.8 | 49.5 | 5.048
1654.9 | 49.5 | 5.048
1655 | 49.5 | 5.048
1655.1 | 49.5 | 5.048
1655.2 | 49.5 | 5.048
1655.3 | 49.5 | 5.049
1655.4 | 49.5 | 5.049
1655.5 | 49.5 | 5.049
1655.6 | 49.5 | 5.049
1655.7 | 49.5 | 5.049
1655.8 | 49.5 | 5.049
1655.9 | 49.5 | 5.049
1656 | 49.5 | 5.049
1656.1 | 49.5 | 5.049
1656.2 | 49.5 | 5.049
1656.3 | 49.5 | 5.048
1656.4 | 49.5 | 5.048
1656.5 | 49.5 | 5.048
1656.6 | 49.5 | 5.048
1656.7 | 49.5 | 5.048
1656.8 | 49.5 | 5.048
1656.9 | 49.5 | 5.048
1657 | 49.5 | 5.048
1657.1 | 49.5 | 5.048
1657.2 | 49.5 | 5.048
1657.3 | 49.5 | 5.048
1657.4 | 49.5 | 5.048
1657.5 | 49.5 | 5.048
1657.6 | 49.5 | 5.048
1657.7 | 49.5 | 5.048
1657.8 | 49.5 | 5.048
1657.9 | 49.5 | 5.048
1658 | 49.5 | 5.048
1658.1 | 49.5 | 5.048
1658.2 | 49.5 | 5.048
1658.3 | 49.5 | 5.048
1658.4 | 49.5 | 5.048
1658.5 | 49.5 | 5.048
1658.6 | 49.5 | 5.048
1658.7 | 49.5 | 5.048
1658.8 | 49.5 | 5.048
1658.9 | 49.5 | 5.048
1659 | 49.5 | 5.048
1659.1 | 49.5 | 5.048
1659.2 | 49.5 | 5.048
1659.3 | 49.5 | 5.048
1659.4 | 49.5 | 5.048
1659.5 | 49.5 | 5.048
1659.6 | 49.5 | 5.048
1659.7 | 49.5 | 5.048
1659.8 | 49.5 | 5.048
1659.9 | 49.5 | 5.048
1660 | 49.5 | 5.048
1660.1 | 49.5 | 5.048
1660.2 | 49.5 | 5.048
1660.3 | 49.5 | 5.048
1660.4 | 49.5 | 5.048
1660.5 | 49.5 | 5.048
1660.6 | 49.5 | 5.048
1660.7 | 49.5 | 5.048
1660.8 | 49.5 | 5.048
1660.9 | 49.5 | 5.048
1661 | 49.5 | 5.048
1661.1 | 49.5 | 5.048
1661.2 | 49.5 | 5.048
1661.3 | 49.5 | 5.048
1661.4 | 49.5 | 5.048
1661.5 | 49.5 | 5.048
1661.6 | 49.5 | 5.048
1661.7 | 49.5 | 5.048
1661.8 | 49.5 | 5.048
1661.9 | 49.5 | 5.048
1662 | 49.5 | 5.048
1662.1 | 49.5 | 5.048
1662.2 | 49.5 | 5.048
1662.3 | 49.5 | 5.048
1662.4 | 49.5 | 5.048
1662.5 | 49.5 | 5.048
1662.6 | 49.5 | 5.048
1662.7 | 49.5 | 5.048
1662.8 | 49.5 | 5.048
1662.9 | 49.5 | 5.048
1663 | 49.5 | 5.048
1663.1 | 49.5 | 5.048
1663.2 | 49.5 | 5.048
1663.3 | 49.5 | 5.048
1663.4 | 49.5 | 5.048
1663.5 | 49.5 | 5.048
1663.6 | 49.5 | 5.048
1663.7 | 49.5 | 5.048
1663.8 | 49.5 | 5.048
1663.9 | 49.5 | 5.048
1664 | 49.5 | 5.048
1664.1 | 49.5 | 5.048
1664.2 | 49.5 | 5.048
1664.3 | 49.5 | 5.048
1664.4 | 49.5 | 5.048
1664.5 | 49.5 | 5.049
1664.6 | 49.5 | 5.049
1664.7 | 49.5 | 5.049
1664.8 | 49.5 | 5.049
1664.9 | 49.5 | 5.049
1665 | 49.5 | 5.049
1665.1 | 49.5 | 5.049
1665.2 | 49.5 | 5.049
1665.3 | 49.5 | 5.049
1665.4 | 49.5 | 5.049
1665.5 | 49.5 | 5.049
1665.6 | 49.5 | 5.049
1665.7 | 49.5 | 5.049
1665.8 | 49.5 | 5.049
1665.9 | 49.5 | 5.049
1666 | 49.5 | 5.049
1666.1 | 49.5 | 5.049
1666.2 | 49.5 | 5.049
1666.3 | 49.5 | 5.049
1666.4 | 49.5 | 5.049
1666.5 | 49.5 | 5.049
1666.6 | 49.5 | 5.049
1666.7 | 49.5 | 5.049
1666.8 | 49.5 | 5.049
1666.9 | 49.5 | 5.049
1667 | 49.5 | 5.049
1667.1 | 49.5 | 5.049
1667.2 | 49.5 | 5.049
1667.3 | 49.5 | 5.049
1667.4 | 49.5 | 5.049
1667.5 | 49.5 | 5.049
1667.6 | 49.5 | 5.049
1667.7 | 49.5 | 5.049
1667.8 | 49.5 | 5.049
1667.9 | 49.5 | 5.049
1668 | 49.5 | 5.049
1668.1 | 49.5 | 5.048
1668.2 | 49.5 | 5.048
1668.3 | 49.5 | 5.048
1668.4 | 49.5 | 5.048
1668.5 | 49.5 | 5.048
1668.6 | 49.5 | 5.048
1668.7 | 49.5 | 5.048
1668.8 | 49.5 | 5.048
1668.9 | 49.5 | 5.048
1669 | 49.5 | 5.048
1669.1 | 49.5 | 5.048
1669.2 | 49.5 | 5.048
1669.3 | 49.5 | 5.048
1669.4 | 49.5 | 5.048
1669.5 | 49.5 | 5.048
1669.6 | 49.5 | 5.048
1669.7 | 49.5 | 5.048
1669.8 | 49.5 | 5.048
1669.9 | 49.5 | 5.048
1670 | 49.5 | 5.048
1670.1 | 49.5 | 5.048
1670.2 | 49.5 | 5.048
1670.3 | 49.5 | 5.048
1670.4 | 49.5 | 5.048
1670.5 | 49.5 | 5.048
1670.6 | 49.5 | 5.048
1670.7 | 49.5 | 5.048
1670.8 | 49.5 | 5.048
1670.9 | 49.5 | 5.048
1671 | 49.5 | 5.048
1671.1 | 49.5 | 5.048
1671.2 | 49.5 | 5.048
1671.3 | 49.5 | 5.048
1671.4 | 49.5 | 5.048
1671.5 | 49.5 | 5.048
1671.6 | 49.5 | 5.048
1671.7 | 49.5 | 5.048
1671.8 | 49.5 | 5.048
1671.9 | 49.5 | 5.048
1672 | 49.5 | 5.048
1672.1 | 49.5 | 5.048
1672.2 | 49.5 | 5.048
1672.3 | 49.5 | 5.048
1672.4 | 49.5 | 5.048
1672.5 | 49.5 | 5.048
1672.6 | 49.5 | 5.048
1672.7 | 49.5 | 5.048
1672.8 | 49.5 | 5.048
1672.9 | 49.5 | 5.048
1673 | 49.5 | 5.048
1673.1 | 49.5 | 5.048
1673.2 | 49.5 | 5.048
1673.3 | 49.5 | 5.048
1673.4 | 49.5 | 5.048
1673.5 | 49.5 | 5.048
1673.6 | 49.5 | 5.048
1673.7 | 49.5 | 5.048
1673.8 | 49.5 | 5.048
1673.9 | 49.5 | 5.048
1674 | 49.5 | 5.048
1674.1 | 49.5 | 5.048
1674.2 | 49.5 | 5.048
1674.3 | 49.5 | 5.048
1674.4 | 49.5 | 5.048
1674.5 | 49.5 | 5.048
1674.6 | 49.5 | 5.048
1674.7 | 49.5 | 5.048
1674.8 | 49.5 | 5.048
1674.9 | 49.5 | 5.048
1675 | 49.5 | 5.048
1675.1 | 49.5 | 5.048
1675.2 | 49.5 | 5.048
1675.3 | 49.5 | 5.048
1675.4 | 49.5 | 5.048
1675.5 | 49.5 | 5.048
1675.6 | 49.5 | 5.048
1675.7 | 49.5 | 5.048
1675.8 | 49.5 | 5.048
1675.9 | 49.5 | 5.048
1676 | 49.5 | 5.048
1676.1 | 49.5 | 5.048
1676.2 | 49.5 | 5.048
1676.3 | 49.5 | 5.048
1676.4 | 49.5 | 5.048
1676.5 | 49.5 | 5.048
1676.6 | 49.5 | 5.048
1676.7 | 49.5 | 5.048
1676.8 | 49.5 | 5.048
1676.9 | 49.5 | 5.048
1677 | 49.5 | 5.048
1677.1 | 49.5 | 5.048
1677.2 | 49.5 | 5.048
1677.3 | 49.5 | 5.048
1677.4 | 49.5 | 5.048
1677.5 | 49.5 | 5.048
1677.6 | 49.5 | 5.048
1677.7 | 49.5 | 5.048
1677.8 | 49.5 | 5.048
1677.9 | 49.5 | 5.048
1678 | 49.5 | 5.048
1678.1 | 49.5 | 5.048
1678.2 | 49.5 | 5.048
1678.3 | 49.5 | 5.048
1678.4 | 49.5 | 5.048
1678.5 | 49.5 | 5.048
1678.6 | 49.5 | 5.048
1678.7 | 49.5 | 5.048
1678.8 | 49.5 | 5.048
1678.9 | 49.5 | 5.048
1679 | 49.5 | 5.048
1679.1 | 49.5 | 5.048
1679.2 | 49.5 | 5.048
1679.3 | 49.5 | 5.048
1679.4 | 49.5 | 5.048
1679.5 | 49.5 | 5.048
1679.6 | 49.5 | 5.048
1679.7 | 49.5 | 5.048
1679.8 | 49.5 | 5.048
1679.9 | 49.5 | 5.048
1680 | 49.5 | 5.048
1680.1 | 49.5 | 5.048
1680.2 | 49.5 | 5.048
1680.3 | 49.5 | 5.048
1680.4 | 49.5 | 5.048
1680.5 | 49.5 | 5.048
1680.6 | 49.5 | 5.048
1680.7 | 49.5 | 5.048
1680.8 | 49.5 | 5.048
1680.9 | 49.5 | 5.048
1681 | 49.5 | 5.048
1681.1 | 49.5 | 5.048
1681.2 | 49.5 | 5.048
1681.3 | 49.5 | 5.048
1681.4 | 49.5 | 5.048
1681.5 | 49.5 | 5.048
1681.6 | 49.5 | 5.048
1681.7 | 49.5 | 5.048
1681.8 | 49.5 | 5.048
1681.9 | 49.5 | 5.048
1682 | 49.5 | 5.048
1682.1 | 49.5 | 5.048
1682.2 | 49.5 | 5.048
1682.3 | 49.5 | 5.048
1682.4 | 49.5 | 5.048
1682.5 | 49.5 | 5.048
1682.6 | 49.5 | 5.048
1682.7 | 49.5 | 5.048
1682.8 | 49.5 | 5.048
1682.9 | 49.5 | 5.048
1683 | 49.5 | 5.048
1683.1 | 49.5 | 5.048
1683.2 | 49.5 | 5.048
1683.3 | 49.5 | 5.048
1683.4 | 49.5 | 5.048
1683.5 | 49.5 | 5.048
1683.6 | 49.5 | 5.048
1683.7 | 49.5 | 5.048
1683.8 | 49.5 | 5.048
1683.9 | 49.5 | 5.048
1684 | 49.5 | 5.048
1684.1 | 49.5 | 5.048
1684.2 | 49.5 | 5.048
1684.3 | 49.5 | 5.048
1684.4 | 49.5 | 5.048
1684.5 | 49.5 | 5.048
1684.6 | 49.5 | 5.048
1684.7 | 49.5 | 5.048
1684.8 | 49.5 | 5.048
1684.9 | 49.5 | 5.048
1685 | 49.5 | 5.048
1685.1 | 49.5 | 5.048
1685.2 | 49.5 | 5.048
1685.3 | 49.5 | 5.048
1685.4 | 49.5 | 5.048
1685.5 | 49.5 | 5.048
1685.6 | 49.5 | 5.048
1685.7 | 49.5 | 5.048
1685.8 | 49.5 | 5.048
1685.9 | 49.5 | 5.048
1686 | 49.5 | 5.048
1686.1 | 49.5 | 5.048
1686.2 | 49.5 | 5.048
1686.3 | 49.5 | 5.048
1686.4 | 49.5 | 5.048
1686.5 | 49.5 | 5.048
1686.6 | 49.5 | 5.048
1686.7 | 49.5 | 5.048
1686.8 | 49.5 | 5.048
1686.9 | 49.5 | 5.048
1687 | 49.5 | 5.048
1687.1 | 49.5 | 5.048
1687.2 | 49.5 | 5.048
1687.3 | 49.5 | 5.048
1687.4 | 49.5 | 5.048
1687.5 | 49.5 | 5.048
1687.6 | 49.5 | 5.048
1687.7 | 49.5 | 5.048
1687.8 | 49.5 | 5.048
1687.9 | 49.5 | 5.048
1688 | 49.5 | 5.048
1688.1 | 49.5 | 5.048
1688.2 | 49.5 | 5.048
1688.3 | 49.5 | 5.048
1688.4 | 49.5 | 5.048
1688.5 | 49.5 | 5.048
1688.6 | 49.5 | 5.048
1688.7 | 49.5 | 5.048
1688.8 | 49.5 | 5.048
1688.9 | 49.5 | 5.048
1689 | 49.5 | 5.048
1689.1 | 49.5 | 5.048
1689.2 | 49.5 | 5.048
1689.3 | 49.5 | 5.048
1689.4 | 49.5 | 5.048
1689.5 | 49.5 | 5.048
1689.6 | 49.5 | 5.048
1689.7 | 49.5 | 5.048
1689.8 | 49.5 | 5.048
1689.9 | 49.5 | 5.048
1690 | 49.5 | 5.048
1690.1 | 49.5 | 5.048
1690.2 | 49.5 | 5.048
1690.3 | 49.5 | 5.048
1690.4 | 49.5 | 5.048
1690.5 | 49.5 | 5.048
1690.6 | 49.5 | 5.048
1690.7 | 49.5 | 5.048
1690.8 | 49.5 | 5.048
1690.9 | 49.5 | 5.048
1691 | 49.5 | 5.048
1691.1 | 49.5 | 5.048
1691.2 | 49.5 | 5.048
1691.3 | 49.5 | 5.048
1691.4 | 49.5 | 5.048
1691.5 | 49.5 | 5.048
1691.6 | 49.5 | 5.048
1691.7 | 49.5 | 5.048
1691.8 | 49.5 | 5.048
1691.9 | 49.5 | 5.048
1692 | 49.5 | 5.048
1692.1 | 49.5 | 5.048
1692.2 | 49.5 | 5.048
1692.3 | 49.5 | 5.048
1692.4 | 49.5 | 5.048
1692.5 | 49.5 | 5.048
1692.6 | 49.5 | 5.048
1692.7 | 49.5 | 5.048
1692.8 | 49.5 | 5.048
1692.9 | 49.5 | 5.048
1693 | 49.5 | 5.048
1693.1 | 49.5 | 5.048
1693.2 | 49.5 | 5.048
1693.3 | 49.5 | 5.048
1693.4 | 49.5 | 5.048
1693.5 | 49.5 | 5.048
1693.6 | 49.5 | 5.048
1693.7 | 49.5 | 5.048
1693.8 | 49.5 | 5.048
1693.9 | 49.5 | 5.048
1694 | 49.5 | 5.048
1694.1 | 49.5 | 5.048
1694.2 | 49.5 | 5.048
1694.3 | 49.5 | 5.048
1694.4 | 49.5 | 5.048
1694.5 | 49.5 | 5.048
1694.6 | 49.5 | 5.048
1694.7 | 49.5 | 5.048
1694.8 | 49.5 | 5.048
1694.9 | 49.5 | 5.048
1695 | 49.5 | 5.048
1695.1 | 49.5 | 5.048
1695.2 | 49.5 | 5.048
1695.3 | 49.5 | 5.048
1695.4 | 49.5 | 5.048
1695.5 | 49.5 | 5.048
1695.6 | 49.5 | 5.048
1695.7 | 49.5 | 5.048
1695.8 | 49.5 | 5.048
1695.9 | 49.5 | 5.048
1696 | 49.5 | 5.048
1696.1 | 49.5 | 5.048
1696.2 | 49.5 | 5.048
1696.3 | 49.5 | 5.048
1696.4 | 49.5 | 5.048
1696.5 | 49.5 | 5.048
1696.6 | 49.5 | 5.048
1696.7 | 49.5 | 5.048
1696.8 | 49.5 | 5.048
1696.9 | 49.5 | 5.048
1697 | 49.5 | 5.048
1697.1 | 49.5 | 5.048
1697.2 | 49.5 | 5.048
1697.3 | 49.5 | 5.048
1697.4 | 49.5 | 5.048
1697.5 | 49.5 | 5.048
1697.6 | 49.5 | 5.048
1697.7 | 49.5 | 5.048
1697.8 | 49.5 | 5.048
1697.9 | 49.5 | 5.048
1698 | 49.5 | 5.048
1698.1 | 49.5 | 5.048
1698.2 | 49.5 | 5.048
1698.3 | 49.5 | 5.048
1698.4 | 49.5 | 5.048
1698.5 | 49.5 | 5.048
1698.6 | 49.5 | 5.048
1698.7 | 49.5 | 5.048
1698.8 | 49.5 | 5.048
1698.9 | 49.5 | 5.048
1699 | 49.5 | 5.048
1699.1 | 49.5 | 5.048
1699.2 | 49.5 | 5.048
1699.3 | 49.5 | 5.048
1699.4 | 49.5 | 5.048
1699.5 | 49.5 | 5.048
1699.6 | 49.5 | 5.048
1699.7 | 49.5 | 5.048
1699.8 | 49.5 | 5.048
1699.9 | 49.5 | 5.048
1700 | 49.5 | 5.048
1700.1 | 49.5 | 5.048
1700.2 | 49.5 | 5.048
1700.3 | 49.5 | 5.048
1700.4 | 49.5 | 5.048
1700.5 | 49.5 | 5.048
1700.6 | 49.5 | 5.048
1700.7 | 49.5 | 5.048
1700.8 | 49.5 | 5.048
1700.9 | 49.5 | 5.048
1701 | 49.5 | 5.048
1701.1 | 49.5 | 5.048
1701.2 | 49.5 | 5.048
1701.3 | 49.5 | 5.048
1701.4 | 49.5 | 5.048
1701.5 | 49.5 | 5.048
1701.6 | 49.5 | 5.048
1701.7 | 49.5 | 5.048
1701.8 | 49.5 | 5.048
1701.9 | 49.5 | 5.048
1702 | 49.5 | 5.048
1702.1 | 49.5 | 5.048
1702.2 | 49.5 | 5.048
1702.3 | 49.5 | 5.048
1702.4 | 49.5 | 5.048
1702.5 | 49.5 | 5.048
1702.6 | 49.5 | 5.048
1702.7 | 49.5 | 5.048
1702.8 | 49.5 | 5.048
1702.9 | 49.5 | 5.048
1703 | 49.5 | 5.048
1703.1 | 49.5 | 5.048
1703.2 | 49.5 | 5.048
1703.3 | 49.5 | 5.048
1703.4 | 49.5 | 5.048
1703.5 | 49.5 | 5.048
1703.6 | 49.5 | 5.048
1703.7 | 49.5 | 5.048
1703.8 | 49.5 | 5.048
1703.9 | 49.5 | 5.048
1704 | 49.5 | 5.048
1704.1 | 49.5 | 5.048
1704.2 | 49.5 | 5.048
1704.3 | 49.5 | 5.048
1704.4 | 49.5 | 5.048
1704.5 | 49.5 | 5.048
1704.6 | 49.5 | 5.048
1704.7 | 49.5 | 5.048
1704.8 | 49.5 | 5.048
1704.9 | 49.5 | 5.048
1705 | 49.5 | 5.048
1705.1 | 49.5 | 5.048
1705.2 | 49.5 | 5.048
1705.3 | 49.5 | 5.048
1705.4 | 49.5 | 5.048
1705.5 | 49.5 | 5.048
1705.6 | 49.5 | 5.048
1705.7 | 49.5 | 5.048
1705.8 | 49.5 | 5.048
1705.9 | 49.5 | 5.048
1706 | 49.5 | 5.048
1706.1 | 49.5 | 5.048
1706.2 | 49.5 | 5.048
1706.3 | 49.5 | 5.048
1706.4 | 49.5 | 5.048
1706.5 | 49.5 | 5.048
1706.6 | 49.5 | 5.048
1706.7 | 49.5 | 5.048
1706.8 | 49.5 | 5.048
1706.9 | 49.5 | 5.048
1707 | 49.5 | 5.048
1707.1 | 49.5 | 5.048
1707.2 | 49.5 | 5.048
1707.3 | 49.5 | 5.048
1707.4 | 49.5 | 5.048
1707.5 | 49.5 | 5.048
1707.6 | 49.5 | 5.048
1707.7 | 49.5 | 5.048
1707.8 | 49.5 | 5.048
1707.9 | 49.5 | 5.048
1708 | 49.5 | 5.048
1708.1 | 49.5 | 5.048
1708.2 | 49.5 | 5.048
1708.3 | 49.5 | 5.048
1708.4 | 49.5 | 5.048
1708.5 | 49.5 | 5.048
1708.6 | 49.5 | 5.048
1708.7 | 49.5 | 5.048
1708.8 | 49.5 | 5.048
1708.9 | 49.5 | 5.048
1709 | 49.5 | 5.048
1709.1 | 49.5 | 5.048
1709.2 | 49.5 | 5.048
1709.3 | 49.5 | 5.048
1709.4 | 49.5 | 5.048
1709.5 | 49.5 | 5.048
1709.6 | 49.5 | 5.048
1709.7 | 49.5 | 5.048
1709.8 | 49.5 | 5.048
1709.9 | 49.5 | 5.048
1710 | 49.5 | 5.048
1710.1 | 49.5 | 5.048
1710.2 | 49.5 | 5.048
1710.3 | 49.5 | 5.048
1710.4 | 49.5 | 5.048
1710.5 | 49.5 | 5.048
1710.6 | 49.5 | 5.048
1710.7 | 49.5 | 5.048
1710.8 | 49.5 | 5.048
1710.9 | 49.5 | 5.048
1711 | 49.5 | 5.048
1711.1 | 49.5 | 5.048
1711.2 | 49.5 | 5.048
1711.3 | 49.5 | 5.048
1711.4 | 49.5 | 5.048
1711.5 | 49.5 | 5.048
1711.6 | 49.5 | 5.048
1711.7 | 49.5 | 5.048
1711.8 | 49.5 | 5.048
1711.9 | 49.5 | 5.048
1712 | 49.5 | 5.048
1712.1 | 49.5 | 5.048
1712.2 | 49.5 | 5.048
1712.3 | 49.5 | 5.048
1712.4 | 49.5 | 5.048
1712.5 | 49.5 | 5.048
1712.6 | 49.5 | 5.048
1712.7 | 49.5 | 5.048
1712.8 | 49.5 | 5.048
1712.9 | 49.5 | 5.048
1713 | 49.5 | 5.048
1713.1 | 49.5 | 5.048
1713.2 | 49.5 | 5.048
1713.3 | 49.5 | 5.048
1713.4 | 49.5 | 5.048
1713.5 | 49.5 | 5.048
1713.6 | 49.5 | 5.048
1713.7 | 49.5 | 5.048
1713.8 | 49.5 | 5.048
1713.9 | 49.5 | 5.048
1714 | 49.5 | 5.048
1714.1 | 49.5 | 5.048
1714.2 | 49.5 | 5.048
1714.3 | 49.5 | 5.048
1714.4 | 49.5 | 5.048
1714.5 | 49.5 | 5.048
1714.6 | 49.5 | 5.048
1714.7 | 49.5 | 5.048
1714.8 | 49.5 | 5.048
1714.9 | 49.5 | 5.048
1715 | 49.5 | 5.048
1715.1 | 49.5 | 5.048
1715.2 | 49.5 | 5.048
1715.3 | 49.5 | 5.048
1715.4 | 49.5 | 5.048
1715.5 | 49.5 | 5.048
1715.6 | 49.5 | 5.048
1715.7 | 49.5 | 5.048
1715.8 | 49.5 | 5.048
1715.9 | 49.5 | 5.048
1716 | 49.5 | 5.048
1716.1 | 49.5 | 5.048
1716.2 | 49.5 | 5.048
1716.3 | 49.5 | 5.048
1716.4 | 49.5 | 5.048
1716.5 | 49.5 | 5.048
1716.6 | 49.5 | 5.048
1716.7 | 49.5 | 5.048
1716.8 | 49.5 | 5.048
1716.9 | 49.5 | 5.048
1717 | 49.5 | 5.048
1717.1 | 49.5 | 5.048
1717.2 | 49.5 | 5.048
1717.3 | 49.5 | 5.048
1717.4 | 49.5 | 5.048
1717.5 | 49.5 | 5.048
1717.6 | 49.5 | 5.048
1717.7 | 49.5 | 5.048
1717.8 | 49.5 | 5.048
1717.9 | 49.5 | 5.048
1718 | 49.5 | 5.048
1718.1 | 49.5 | 5.048
1718.2 | 49.5 | 5.048
1718.3 | 49.5 | 5.048
1718.4 | 49.5 | 5.048
1718.5 | 49.5 | 5.048
1718.6 | 49.5 | 5.048
1718.7 | 49.5 | 5.048
1718.8 | 49.5 | 5.048
1718.9 | 49.5 | 5.048
1719 | 49.5 | 5.048
1719.1 | 49.5 | 5.048
1719.2 | 49.5 | 5.048
1719.3 | 49.5 | 5.048
1719.4 | 49.5 | 5.048
1719.5 | 49.5 | 5.048
1719.6 | 49.5 | 5.048
1719.7 | 49.5 | 5.048
1719.8 | 49.5 | 5.048
1719.9 | 49.5 | 5.048
1720 | 49.5 | 5.048
1720.1 | 49.5 | 5.048
1720.2 | 49.5 | 5.048
1720.3 | 49.5 | 5.048
1720.4 | 49.5 | 5.048
1720.5 | 49.5 | 5.048
1720.6 | 49.5 | 5.048
1720.7 | 49.5 | 5.048
1720.8 | 49.5 | 5.048
1720.9 | 49.5 | 5.048
1721 | 49.5 | 5.048
1721.1 | 49.5 | 5.048
1721.2 | 49.5 | 5.048
1721.3 | 49.5 | 5.048
1721.4 | 49.5 | 5.048
1721.5 | 49.5 | 5.048
1721.6 | 49.5 | 5.048
1721.7 | 49.5 | 5.048
1721.8 | 49.5 | 5.048
1721.9 | 49.5 | 5.048
1722 | 49.5 | 5.048
1722.1 | 49.5 | 5.048
1722.2 | 49.5 | 5.048
1722.3 | 49.5 | 5.048
1722.4 | 49.5 | 5.048
1722.5 | 49.5 | 5.048
1722.6 | 49.5 | 5.048
1722.7 | 49.5 | 5.048
1722.8 | 49.5 | 5.048
1722.9 | 49.5 | 5.048
1723 | 49.5 | 5.048
1723.1 | 49.5 | 5.048
1723.2 | 49.5 | 5.048
1723.3 | 49.5 | 5.048
1723.4 | 49.5 | 5.048
1723.5 | 49.5 | 5.048
1723.6 | 49.5 | 5.048
1723.7 | 49.5 | 5.048
1723.8 | 49.5 | 5.048
1723.9 | 49.5 | 5.048
1724 | 49.5 | 5.048
1724.1 | 49.5 | 5.048
1724.2 | 49.5 | 5.048
1724.3 | 49.5 | 5.048
1724.4 | 49.5 | 5.048
1724.5 | 49.5 | 5.048
1724.6 | 49.5 | 5.048
1724.7 | 49.5 | 5.048
1724.8 | 49.5 | 5.048
1724.9 | 49.5 | 5.048
1725 | 49.5 | 5.048
1725.1 | 49.5 | 5.048
1725.2 | 49.5 | 5.048
1725.3 | 49.5 | 5.048
1725.4 | 49.5 | 5.048
1725.5 | 49.5 | 5.048
1725.6 | 49.5 | 5.048
1725.7 | 49.5 | 5.048
1725.8 | 49.5 | 5.048
1725.9 | 49.5 | 5.048
1726 | 49.5 | 5.048
1726.1 | 49.5 | 5.048
1726.2 | 49.5 | 5.048
1726.3 | 49.5 | 5.048
1726.4 | 49.5 | 5.048
1726.5 | 49.5 | 5.048
1726.6 | 49.5 | 5.048
1726.7 | 49.5 | 5.048
1726.8 | 49.5 | 5.048
1726.9 | 49.5 | 5.048
1727 | 49.5 | 5.048
1727.1 | 49.5 | 5.048
1727.2 | 49.5 | 5.048
1727.3 | 49.5 | 5.048
1727.4 | 49.5 | 5.048
1727.5 | 49.5 | 5.048
1727.6 | 49.5 | 5.048
1727.7 | 49.5 | 5.048
1727.8 | 49.5 | 5.048
1727.9 | 49.5 | 5.048
1728 | 49.5 | 5.048
1728.1 | 49.5 | 5.048
1728.2 | 49.5 | 5.048
1728.3 | 49.5 | 5.048
1728.4 | 49.5 | 5.048
1728.5 | 49.5 | 5.048
1728.6 | 49.5 | 5.048
1728.7 | 49.5 | 5.048
1728.8 | 49.5 | 5.048
1728.9 | 49.5 | 5.048
1729 | 49.5 | 5.048
1729.1 | 49.5 | 5.048
1729.2 | 49.5 | 5.048
1729.3 | 49.5 | 5.048
1729.4 | 49.5 | 5.048
1729.5 | 49.5 | 5.048
1729.6 | 49.5 | 5.048
1729.7 | 49.5 | 5.048
1729.8 | 49.5 | 5.048
1729.9 | 49.5 | 5.048
1730 | 49.5 | 5.048
1730.1 | 49.5 | 5.048
1730.2 | 49.5 | 5.048
1730.3 | 49.5 | 5.048
1730.4 | 49.5 | 5.048
1730.5 | 49.5 | 5.048
1730.6 | 49.5 | 5.048
1730.7 | 49.5 | 5.048
1730.8 | 49.5 | 5.048
1730.9 | 49.5 | 5.048
1731 | 49.5 | 5.048
1731.1 | 49.5 | 5.048
1731.2 | 49.5 | 5.048
1731.3 | 49.5 | 5.048
1731.4 | 49.5 | 5.048
1731.5 | 49.5 | 5.048
1731.6 | 49.5 | 5.048
1731.7 | 49.5 | 5.048
1731.8 | 49.5 | 5.048
1731.9 | 49.5 | 5.048
1732 | 49.5 | 5.048
1732.1 | 49.5 | 5.048
1732.2 | 49.5 | 5.048
1732.3 | 49.5 | 5.048
1732.4 | 49.5 | 5.048
1732.5 | 49.5 | 5.048
1732.6 | 49.5 | 5.048
1732.7 | 49.5 | 5.048
1732.8 | 49.5 | 5.048
1732.9 | 49.5 | 5.048
1733 | 49.5 | 5.048
1733.1 | 49.5 | 5.048
1733.2 | 49.5 | 5.048
1733.3 | 49.5 | 5.048
1733.4 | 49.5 | 5.048
1733.5 | 49.5 | 5.048
1733.6 | 49.5 | 5.048
1733.7 | 49.5 | 5.048
1733.8 | 49.5 | 5.048
1733.9 | 49.5 | 5.048
1734 | 49.5 | 5.048
1734.1 | 49.5 | 5.048
1734.2 | 49.5 | 5.048
1734.3 | 49.5 | 5.048
1734.4 | 49.5 | 5.048
1734.5 | 49.5 | 5.048
1734.6 | 49.5 | 5.048
1734.7 | 49.5 | 5.048
1734.8 | 49.5 | 5.048
1734.9 | 49.5 | 5.048
1735 | 49.5 | 5.048
1735.1 | 49.5 | 5.048
1735.2 | 49.5 | 5.048
1735.3 | 49.5 | 5.048
1735.4 | 49.5 | 5.048
1735.5 | 49.5 | 5.048
1735.6 | 49.5 | 5.048
1735.7 | 49.5 | 5.048
1735.8 | 49.5 | 5.048
1735.9 | 49.5 | 5.048
1736 | 49.5 | 5.048
1736.1 | 49.5 | 5.048
1736.2 | 49.5 | 5.048
1736.3 | 49.5 | 5.048
1736.4 | 49.5 | 5.048
1736.5 | 49.5 | 5.048
1736.6 | 49.5 | 5.048
1736.7 | 49.5 | 5.048
1736.8 | 49.5 | 5.048
1736.9 | 49.5 | 5.048
1737 | 49.5 | 5.048
1737.1 | 49.5 | 5.048
1737.2 | 49.5 | 5.048
1737.3 | 49.5 | 5.048
1737.4 | 49.5 | 5.048
1737.5 | 49.5 | 5.048
1737.6 | 49.5 | 5.048
1737.7 | 49.5 | 5.048
1737.8 | 49.5 | 5.048
1737.9 | 49.5 | 5.048
1738 | 49.5 | 5.048
1738.1 | 49.5 | 5.048
1738.2 | 49.5 | 5.048
1738.3 | 49.5 | 5.048
1738.4 | 49.5 | 5.048
1738.5 | 49.5 | 5.048
1738.6 | 49.5 | 5.048
1738.7 | 49.5 | 5.048
1738.8 | 49.5 | 5.048
1738.9 | 49.5 | 5.048
1739 | 49.5 | 5.048
1739.1 | 49.5 | 5.048
1739.2 | 49.5 | 5.048
1739.3 | 49.5 | 5.048
1739.4 | 49.5 | 5.048
1739.5 | 49.5 | 5.048
1739.6 | 49.5 | 5.048
1739.7 | 49.5 | 5.048
1739.8 | 49.5 | 5.048
1739.9 | 49.5 | 5.048
1740 | 49.5 | 5.048
1740.1 | 49.5 | 5.048
1740.2 | 49.5 | 5.048
1740.3 | 49.5 | 5.048
1740.4 | 49.5 | 5.048
1740.5 | 49.5 | 5.048
1740.6 | 49.5 | 5.048
1740.7 | 49.5 | 5.048
1740.8 | 49.5 | 5.048
1740.9 | 49.5 | 5.048
1741 | 49.5 | 5.048
1741.1 | 49.5 | 5.048
1741.2 | 49.5 | 5.048
1741.3 | 49.5 | 5.048
1741.4 | 49.5 | 5.048
1741.5 | 49.5 | 5.048
1741.6 | 49.5 | 5.048
1741.7 | 49.5 | 5.048
1741.8 | 49.5 | 5.048
1741.9 | 49.5 | 5.048
1742 | 49.5 | 5.048
1742.1 | 49.5 | 5.048
1742.2 | 49.5 | 5.048
1742.3 | 49.5 | 5.048
1742.4 | 49.5 | 5.048
1742.5 | 49.5 | 5.048
1742.6 | 49.5 | 5.048
1742.7 | 49.5 | 5.048
1742.8 | 49.5 | 5.048
1742.9 | 49.5 | 5.048
1743 | 49.5 | 5.048
1743.1 | 49.5 | 5.048
1743.2 | 49.5 | 5.048
1743.3 | 49.5 | 5.048
1743.4 | 49.5 | 5.048
1743.5 | 49.5 | 5.048
1743.6 | 49.5 | 5.048
1743.7 | 49.5 | 5.048
1743.8 | 49.5 | 5.048
1743.9 | 49.5 | 5.048
1744 | 49.5 | 5.048
1744.1 | 49.5 | 5.048
1744.2 | 49.5 | 5.048
1744.3 | 49.5 | 5.048
1744.4 | 49.5 | 5.048
1744.5 | 49.5 | 5.048
1744.6 | 49.5 | 5.048
1744.7 | 49.5 | 5.048
1744.8 | 49.5 | 5.048
1744.9 | 49.5 | 5.048
1745 | 49.5 | 5.048
1745.1 | 49.5 | 5.048
1745.2 | 49.5 | 5.048
1745.3 | 49.5 | 5.048
1745.4 | 49.5 | 5.048
1745.5 | 49.5 | 5.048
1745.6 | 49.5 | 5.048
1745.7 | 49.5 | 5.048
1745.8 | 49.5 | 5.048
1745.9 | 49.5 | 5.048
1746 | 49.5 | 5.048
1746.1 | 49.5 | 5.048
1746.2 | 49.5 | 5.048
1746.3 | 49.5 | 5.048
1746.4 | 49.5 | 5.048
1746.5 | 49.5 | 5.048
1746.6 | 49.5 | 5.048
1746.7 | 49.5 | 5.048
1746.8 | 49.5 | 5.048
1746.9 | 49.5 | 5.048
1747 | 49.5 | 5.048
1747.1 | 49.5 | 5.048
1747.2 | 49.5 | 5.048
1747.3 | 49.5 | 5.048
1747.4 | 49.5 | 5.048
1747.5 | 49.5 | 5.048
1747.6 | 49.5 | 5.048
1747.7 | 49.5 | 5.048
1747.8 | 49.5 | 5.048
1747.9 | 49.5 | 5.048
1748 | 49.5 | 5.048
1748.1 | 49.5 | 5.048
1748.2 | 49.5 | 5.048
1748.3 | 49.5 | 5.048
1748.4 | 49.5 | 5.048
1748.5 | 49.5 | 5.048
1748.6 | 49.5 | 5.048
1748.7 | 49.5 | 5.048
1748.8 | 49.5 | 5.048
1748.9 | 49.5 | 5.048
1749 | 49.5 | 5.048
1749.1 | 49.5 | 5.048
1749.2 | 49.5 | 5.048
1749.3 | 49.5 | 5.048
1749.4 | 49.5 | 5.048
1749.5 | 49.5 | 5.048
1749.6 | 49.5 | 5.048
1749.7 | 49.5 | 5.048
1749.8 | 49.5 | 5.048
1749.9 | 49.5 | 5.048
1750 | 49.5 | 5.048
1750.1 | 49.5 | 5.048
1750.2 | 49.5 | 5.048
1750.3 | 49.5 | 5.048
1750.4 | 49.5 | 5.049
1750.5 | 49.5 | 5.049
1750.6 | 49.5 | 5.049
1750.7 | 49.5 | 5.049
1750.8 | 49.5 | 5.049
1750.9 | 49.5 | 5.049
1751 | 49.5 | 5.049
1751.1 | 49.5 | 5.049
1751.2 | 49.5 | 5.049
1751.3 | 49.5 | 5.049
1751.4 | 49.5 | 5.048
1751.5 | 49.5 | 5.048
1751.6 | 49.5 | 5.048
1751.7 | 49.5 | 5.048
1751.8 | 49.5 | 5.048
1751.9 | 49.5 | 5.048
1752 | 49.5 | 5.048
1752.1 | 49.5 | 5.048
1752.2 | 49.5 | 5.048
1752.3 | 49.5 | 5.048
1752.4 | 49.5 | 5.048
1752.5 | 49.5 | 5.048
1752.6 | 49.5 | 5.048
1752.7 | 49.5 | 5.048
1752.8 | 49.5 | 5.048
1752.9 | 49.5 | 5.048
1753 | 49.5 | 5.048
1753.1 | 49.5 | 5.048
1753.2 | 49.5 | 5.048
1753.3 | 49.5 | 5.048
1753.4 | 49.5 | 5.048
1753.5 | 49.5 | 5.048
1753.6 | 49.5 | 5.048
1753.7 | 49.5 | 5.048
1753.8 | 49.5 | 5.048
1753.9 | 49.5 | 5.048
1754 | 49.5 | 5.048
1754.1 | 49.5 | 5.048
1754.2 | 49.5 | 5.048
1754.3 | 49.5 | 5.048
1754.4 | 49.5 | 5.048
1754.5 | 49.5 | 5.048
1754.6 | 49.5 | 5.048
1754.7 | 49.5 | 5.048
1754.8 | 49.5 | 5.048
1754.9 | 49.5 | 5.048
1755 | 49.5 | 5.048
1755.1 | 49.5 | 5.048
1755.2 | 49.5 | 5.048
1755.3 | 49.5 | 5.048
1755.4 | 49.5 | 5.048
1755.5 | 49.5 | 5.048
1755.6 | 49.5 | 5.048
1755.7 | 49.5 | 5.048
1755.8 | 49.5 | 5.048
1755.9 | 49.5 | 5.048
1756 | 49.5 | 5.048
1756.1 | 49.5 | 5.048
1756.2 | 49.5 | 5.048
1756.3 | 49.5 | 5.048
1756.4 | 49.5 | 5.048
1756.5 | 49.5 | 5.048
1756.6 | 49.5 | 5.048
1756.7 | 49.5 | 5.048
1756.8 | 49.5 | 5.048
1756.9 | 49.5 | 5.048
1757 | 49.5 | 5.048
1757.1 | 49.5 | 5.048
1757.2 | 49.5 | 5.048
1757.3 | 49.5 | 5.048
1757.4 | 49.5 | 5.048
1757.5 | 49.5 | 5.048
1757.6 | 49.5 | 5.048
1757.7 | 49.5 | 5.048
1757.8 | 49.5 | 5.048
1757.9 | 49.5 | 5.048
1758 | 49.5 | 5.048
1758.1 | 49.5 | 5.048
1758.2 | 49.5 | 5.048
1758.3 | 49.5 | 5.048
1758.4 | 49.5 | 5.048
1758.5 | 49.5 | 5.048
1758.6 | 49.5 | 5.048
1758.7 | 49.5 | 5.048
1758.8 | 49.5 | 5.048
1758.9 | 49.5 | 5.048
1759 | 49.5 | 5.048
1759.1 | 49.5 | 5.048
1759.2 | 49.5 | 5.048
1759.3 | 49.5 | 5.048
1759.4 | 49.5 | 5.048
1759.5 | 49.5 | 5.048
1759.6 | 49.5 | 5.048
1759.7 | 49.5 | 5.048
1759.8 | 49.5 | 5.048
1759.9 | 49.5 | 5.048
1760 | 49.5 | 5.048
1760.1 | 49.5 | 5.048
1760.2 | 49.5 | 5.048
1760.3 | 49.5 | 5.048
1760.4 | 49.5 | 5.048
1760.5 | 49.5 | 5.048
1760.6 | 49.5 | 5.048
1760.7 | 49.5 | 5.048
1760.8 | 49.5 | 5.048
1760.9 | 49.5 | 5.048
1761 | 49.5 | 5.048
1761.1 | 49.5 | 5.048
1761.2 | 49.5 | 5.048
1761.3 | 49.5 | 5.048
1761.4 | 49.5 | 5.048
1761.5 | 49.5 | 5.048
1761.6 | 49.5 | 5.048
1761.7 | 49.5 | 5.048
1761.8 | 49.5 | 5.048
1761.9 | 49.5 | 5.048
1762 | 49.5 | 5.048
1762.1 | 49.5 | 5.048
1762.2 | 49.5 | 5.048
1762.3 | 49.5 | 5.048
1762.4 | 49.5 | 5.048
1762.5 | 49.5 | 5.048
1762.6 | 49.5 | 5.048
1762.7 | 49.5 | 5.048
1762.8 | 49.5 | 5.048
1762.9 | 49.5 | 5.048
1763 | 49.5 | 5.048
1763.1 | 49.5 | 5.048
1763.2 | 49.5 | 5.048
1763.3 | 49.5 | 5.048
1763.4 | 49.5 | 5.048
1763.5 | 49.5 | 5.048
1763.6 | 49.5 | 5.048
1763.7 | 49.5 | 5.048
1763.8 | 49.5 | 5.048
1763.9 | 49.5 | 5.048
1764 | 49.5 | 5.048
1764.1 | 49.5 | 5.048
1764.2 | 49.5 | 5.048
1764.3 | 49.5 | 5.048
1764.4 | 49.5 | 5.048
1764.5 | 49.5 | 5.048
1764.6 | 49.5 | 5.048
1764.7 | 49.5 | 5.048
1764.8 | 49.5 | 5.048
1764.9 | 49.5 | 5.048
1765 | 49.5 | 5.048
1765.1 | 49.5 | 5.048
1765.2 | 49.5 | 5.048
1765.3 | 49.5 | 5.048
1765.4 | 49.5 | 5.048
1765.5 | 49.5 | 5.048
1765.6 | 49.5 | 5.048
1765.7 | 49.5 | 5.048
1765.8 | 49.5 | 5.048
1765.9 | 49.5 | 5.048
1766 | 49.5 | 5.048
1766.1 | 49.5 | 5.048
1766.2 | 49.5 | 5.048
1766.3 | 49.5 | 5.048
1766.4 | 49.5 | 5.048
1766.5 | 49.5 | 5.048
1766.6 | 49.5 | 5.048
1766.7 | 49.5 | 5.048
1766.8 | 49.5 | 5.048
1766.9 | 49.5 | 5.048
1767 | 49.5 | 5.048
1767.1 | 49.5 | 5.048
1767.2 | 49.5 | 5.048
1767.3 | 49.5 | 5.048
1767.4 | 49.5 | 5.048
1767.5 | 49.5 | 5.048
1767.6 | 49.5 | 5.048
1767.7 | 49.5 | 5.048
1767.8 | 49.5 | 5.048
1767.9 | 49.5 | 5.048
1768 | 49.5 | 5.048
1768.1 | 49.5 | 5.048
1768.2 | 49.5 | 5.048
1768.3 | 49.5 | 5.048
1768.4 | 49.5 | 5.048
1768.5 | 49.5 | 5.048
1768.6 | 49.5 | 5.048
1768.7 | 49.5 | 5.048
1768.8 | 49.5 | 5.048
1768.9 | 49.5 | 5.048
1769 | 49.5 | 5.048
1769.1 | 49.5 | 5.048
1769.2 | 49.5 | 5.048
1769.3 | 49.5 | 5.048
1769.4 | 49.5 | 5.048
1769.5 | 49.5 | 5.048
1769.6 | 49.5 | 5.048
1769.7 | 49.5 | 5.048
1769.8 | 49.5 | 5.048
1769.9 | 49.5 | 5.048
1770 | 49.5 | 5.048
1770.1 | 49.5 | 5.048
1770.2 | 49.5 | 5.048
1770.3 | 49.5 | 5.048
1770.4 | 49.5 | 5.048
1770.5 | 49.5 | 5.048
1770.6 | 49.5 | 5.048
1770.7 | 49.5 | 5.048
1770.8 | 49.5 | 5.048
1770.9 | 49.5 | 5.048
1771 | 49.5 | 5.048
1771.1 | 49.5 | 5.048
1771.2 | 49.5 | 5.048
1771.3 | 49.5 | 5.048
1771.4 | 49.5 | 5.048
1771.5 | 49.5 | 5.048
1771.6 | 49.5 | 5.048
1771.7 | 49.5 | 5.048
1771.8 | 49.5 | 5.048
1771.9 | 49.5 | 5.048
1772 | 49.5 | 5.048
1772.1 | 49.5 | 5.048
1772.2 | 49.5 | 5.048
1772.3 | 49.5 | 5.048
1772.4 | 49.5 | 5.048
1772.5 | 49.5 | 5.048
1772.6 | 49.5 | 5.048
1772.7 | 49.5 | 5.048
1772.8 | 49.5 | 5.048
1772.9 | 49.5 | 5.048
1773 | 49.5 | 5.048
1773.1 | 49.5 | 5.048
1773.2 | 49.5 | 5.048
1773.3 | 49.5 | 5.048
1773.4 | 49.5 | 5.048
1773.5 | 49.5 | 5.048
1773.6 | 49.5 | 5.048
1773.7 | 49.5 | 5.048
1773.8 | 49.5 | 5.048
1773.9 | 49.5 | 5.048
1774 | 49.5 | 5.048
1774.1 | 49.5 | 5.048
1774.2 | 49.5 | 5.048
1774.3 | 49.5 | 5.048
1774.4 | 49.5 | 5.048
1774.5 | 49.5 | 5.048
1774.6 | 49.5 | 5.048
1774.7 | 49.5 | 5.048
1774.8 | 49.5 | 5.048
1774.9 | 49.5 | 5.048
1775 | 49.5 | 5.048
1775.1 | 49.5 | 5.048
1775.2 | 49.5 | 5.048
1775.3 | 49.5 | 5.048
1775.4 | 49.5 | 5.048
1775.5 | 49.5 | 5.048
1775.6 | 49.5 | 5.048
1775.7 | 49.5 | 5.048
1775.8 | 49.5 | 5.048
1775.9 | 49.5 | 5.048
1776 | 49.5 | 5.048
1776.1 | 49.5 | 5.048
1776.2 | 49.5 | 5.048
1776.3 | 49.5 | 5.048
1776.4 | 49.5 | 5.048
1776.5 | 49.5 | 5.048
1776.6 | 49.5 | 5.048
1776.7 | 49.5 | 5.048
1776.8 | 49.5 | 5.048
1776.9 | 49.5 | 5.048
1777 | 49.5 | 5.048
1777.1 | 49.5 | 5.048
1777.2 | 49.5 | 5.048
1777.3 | 49.5 | 5.048
1777.4 | 49.5 | 5.048
1777.5 | 49.5 | 5.048
1777.6 | 49.5 | 5.048
1777.7 | 49.5 | 5.048
1777.8 | 49.5 | 5.048
1777.9 | 49.5 | 5.048
1778 | 49.5 | 5.048
1778.1 | 49.5 | 5.048
1778.2 | 49.5 | 5.048
1778.3 | 49.5 | 5.048
1778.4 | 49.5 | 5.048
1778.5 | 49.5 | 5.048
1778.6 | 49.5 | 5.048
1778.7 | 49.5 | 5.048
1778.8 | 49.5 | 5.048
1778.9 | 49.5 | 5.048
1779 | 49.5 | 5.048
1779.1 | 49.5 | 5.048
1779.2 | 49.5 | 5.048
1779.3 | 49.5 | 5.048
1779.4 | 49.5 | 5.048
1779.5 | 49.5 | 5.048
1779.6 | 49.5 | 5.048
1779.7 | 49.5 | 5.048
1779.8 | 49.5 | 5.048
1779.9 | 49.5 | 5.048
1780 | 49.5 | 5.048
1780.1 | 49.5 | 5.048
1780.2 | 49.5 | 5.048
1780.3 | 49.5 | 5.048
1780.4 | 49.5 | 5.048
1780.5 | 49.5 | 5.048
1780.6 | 49.5 | 5.048
1780.7 | 49.5 | 5.048
1780.8 | 49.5 | 5.048
1780.9 | 49.5 | 5.048
1781 | 49.5 | 5.048
1781.1 | 49.5 | 5.048
1781.2 | 49.5 | 5.048
1781.3 | 49.5 | 5.048
1781.4 | 49.5 | 5.048
1781.5 | 49.5 | 5.048
1781.6 | 49.5 | 5.048
1781.7 | 49.5 | 5.048
1781.8 | 49.5 | 5.048
1781.9 | 49.5 | 5.048
1782 | 49.5 | 5.048
1782.1 | 49.5 | 5.048
1782.2 | 49.5 | 5.048
1782.3 | 49.5 | 5.048
1782.4 | 49.5 | 5.048
1782.5 | 49.5 | 5.048
1782.6 | 49.5 | 5.048
1782.7 | 49.5 | 5.048
1782.8 | 49.5 | 5.048
1782.9 | 49.5 | 5.048
1783 | 49.5 | 5.049
1783.1 | 49.5 | 5.049
1783.2 | 49.5 | 5.049
1783.3 | 49.5 | 5.049
1783.4 | 49.5 | 5.049
1783.5 | 49.5 | 5.049
1783.6 | 49.5 | 5.049
1783.7 | 49.5 | 5.049
1783.8 | 49.5 | 5.049
1783.9 | 49.5 | 5.049
1784 | 49.5 | 5.049
1784.1 | 49.5 | 5.049
1784.2 | 49.5 | 5.049
1784.3 | 49.5 | 5.049
1784.4 | 49.5 | 5.049
1784.5 | 49.5 | 5.049
1784.6 | 49.5 | 5.049
1784.7 | 49.5 | 5.049
1784.8 | 49.5 | 5.049
1784.9 | 49.5 | 5.049
1785 | 49.5 | 5.049
1785.1 | 49.5 | 5.049
1785.2 | 49.5 | 5.049
1785.3 | 49.5 | 5.048
1785.4 | 49.5 | 5.048
1785.5 | 49.5 | 5.048
1785.6 | 49.5 | 5.048
1785.7 | 49.5 | 5.048
1785.8 | 49.5 | 5.048
1785.9 | 49.5 | 5.048
1786 | 49.5 | 5.048
1786.1 | 49.5 | 5.048
1786.2 | 49.5 | 5.048
1786.3 | 49.5 | 5.048
1786.4 | 49.5 | 5.048
1786.5 | 49.5 | 5.048
1786.6 | 49.5 | 5.048
1786.7 | 49.5 | 5.048
1786.8 | 49.5 | 5.048
1786.9 | 49.5 | 5.048
1787 | 49.5 | 5.048
1787.1 | 49.5 | 5.048
1787.2 | 49.5 | 5.048
1787.3 | 49.5 | 5.048
1787.4 | 49.5 | 5.048
1787.5 | 49.5 | 5.048
1787.6 | 49.5 | 5.048
1787.7 | 49.5 | 5.048
1787.8 | 49.5 | 5.048
1787.9 | 49.5 | 5.048
1788 | 49.5 | 5.048
1788.1 | 49.5 | 5.048
1788.2 | 49.5 | 5.048
1788.3 | 49.5 | 5.048
1788.4 | 49.5 | 5.048
1788.5 | 49.5 | 5.048
1788.6 | 49.5 | 5.048
1788.7 | 49.5 | 5.048
1788.8 | 49.5 | 5.048
1788.9 | 49.5 | 5.048
1789 | 49.5 | 5.048
1789.1 | 49.5 | 5.048
1789.2 | 49.5 | 5.048
1789.3 | 49.5 | 5.048
1789.4 | 49.5 | 5.048
1789.5 | 49.5 | 5.048
1789.6 | 49.5 | 5.048
1789.7 | 49.5 | 5.048
1789.8 | 49.5 | 5.048
1789.9 | 49.5 | 5.048
1790 | 49.5 | 5.048
1790.1 | 49.5 | 5.048
1790.2 | 49.5 | 5.048
1790.3 | 49.5 | 5.048
1790.4 | 49.5 | 5.048
1790.5 | 49.5 | 5.048
1790.6 | 49.5 | 5.048
1790.7 | 49.5 | 5.048
1790.8 | 49.5 | 5.048
1790.9 | 49.5 | 5.048
1791 | 49.5 | 5.048
1791.1 | 49.5 | 5.048
1791.2 | 49.5 | 5.048
1791.3 | 49.5 | 5.048
1791.4 | 49.5 | 5.048
1791.5 | 49.5 | 5.048
1791.6 | 49.5 | 5.048
1791.7 | 49.5 | 5.048
1791.8 | 49.5 | 5.048
1791.9 | 49.5 | 5.048
1792 | 49.5 | 5.048
1792.1 | 49.5 | 5.048
1792.2 | 49.5 | 5.048
1792.3 | 49.5 | 5.048
1792.4 | 49.5 | 5.048
1792.5 | 49.5 | 5.048
1792.6 | 49.5 | 5.048
1792.7 | 49.5 | 5.048
1792.8 | 49.5 | 5.048
1792.9 | 49.5 | 5.048
1793 | 49.5 | 5.048
1793.1 | 49.5 | 5.048
1793.2 | 49.5 | 5.048
1793.3 | 49.5 | 5.048
1793.4 | 49.5 | 5.048
1793.5 | 49.5 | 5.048
1793.6 | 49.5 | 5.048
1793.7 | 49.5 | 5.048
1793.8 | 49.5 | 5.048
1793.9 | 49.5 | 5.048
1794 | 49.5 | 5.048
1794.1 | 49.5 | 5.048
1794.2 | 49.5 | 5.048
1794.3 | 49.5 | 5.048
1794.4 | 49.5 | 5.048
1794.5 | 49.5 | 5.048
1794.6 | 49.5 | 5.048
1794.7 | 49.5 | 5.048
1794.8 | 49.5 | 5.048
1794.9 | 49.5 | 5.048
1795 | 49.5 | 5.048
1795.1 | 49.5 | 5.048
1795.2 | 49.5 | 5.048
1795.3 | 49.5 | 5.048
1795.4 | 49.5 | 5.048
1795.5 | 49.5 | 5.048
1795.6 | 49.5 | 5.048
1795.7 | 49.5 | 5.048
1795.8 | 49.5 | 5.048
1795.9 | 49.5 | 5.048
1796 | 49.5 | 5.048
1796.1 | 49.5 | 5.048
1796.2 | 49.5 | 5.048
1796.3 | 49.5 | 5.048
1796.4 | 49.5 | 5.048
1796.5 | 49.5 | 5.048
1796.6 | 49.5 | 5.048
1796.7 | 49.5 | 5.048
1796.8 | 49.5 | 5.048
1796.9 | 49.5 | 5.048
1797 | 49.5 | 5.048
1797.1 | 49.5 | 5.048
1797.2 | 49.5 | 5.048
1797.3 | 49.5 | 5.048
1797.4 | 49.5 | 5.048
1797.5 | 49.5 | 5.048
1797.6 | 49.5 | 5.048
1797.7 | 49.5 | 5.048
1797.8 | 49.5 | 5.048
1797.9 | 49.5 | 5.048
1798 | 49.5 | 5.048
1798.1 | 49.5 | 5.048
1798.2 | 49.5 | 5.048
1798.3 | 49.5 | 5.049
1798.4 | 49.5 | 5.049
1798.5 | 49.5 | 5.049
1798.6 | 49.5 | 5.049
1798.7 | 49.5 | 5.049
1798.8 | 49.5 | 5.049
1798.9 | 49.5 | 5.049
1799 | 49.5 | 5.049
1799.1 | 49.5 | 5.049
1799.2 | 49.5 | 5.049
1799.3 | 49.5 | 5.049
1799.4 | 49.5 | 5.049
1799.5 | 49.5 | 5.049
1799.6 | 49.5 | 5.049
1799.7 | 49.5 | 5.049
1799.8 | 49.5 | 5.049
1799.9 | 49.5 | 5.049
1800 | 49.5 | 5.049
1800.1 | 49.5 | 5.049
1800.2 | 49.5 | 5.049
1800.3 | 49.5 | 5.049
1800.4 | 49.5 | 5.049
1800.5 | 49.5 | 5.049
1800.6 | 49.5 | 5.048
1800.7 | 49.5 | 5.048
1800.8 | 49.5 | 5.048
1800.9 | 49.5 | 5.048
1801 | 49.5 | 5.048
1801.1 | 49.5 | 5.048
1801.2 | 49.5 | 5.048
1801.3 | 49.5 | 5.048
1801.4 | 49.5 | 5.048
1801.5 | 49.5 | 5.048
1801.6 | 49.5 | 5.048
1801.7 | 49.5 | 5.048
1801.8 | 49.5 | 5.048
1801.9 | 49.5 | 5.048
1802 | 49.5 | 5.048
1802.1 | 49.5 | 5.048
1802.2 | 49.5 | 5.048
1802.3 | 49.5 | 5.048
1802.4 | 49.5 | 5.048
1802.5 | 49.5 | 5.048
1802.6 | 49.5 | 5.048
1802.7 | 49.5 | 5.048
1802.8 | 49.5 | 5.048
1802.9 | 49.5 | 5.048
1803 | 49.5 | 5.048
1803.1 | 49.5 | 5.048
1803.2 | 49.5 | 5.048
1803.3 | 49.5 | 5.048
1803.4 | 49.5 | 5.048
1803.5 | 49.5 | 5.048
1803.6 | 49.5 | 5.048
1803.7 | 49.5 | 5.048
1803.8 | 49.5 | 5.048
1803.9 | 49.5 | 5.048
1804 | 49.5 | 5.048
1804.1 | 49.5 | 5.048
1804.2 | 49.5 | 5.048
1804.3 | 49.5 | 5.048
1804.4 | 49.5 | 5.048
1804.5 | 49.5 | 5.048
1804.6 | 49.5 | 5.048
1804.7 | 49.5 | 5.048
1804.8 | 49.5 | 5.048
1804.9 | 49.5 | 5.048
1805 | 49.5 | 5.048
1805.1 | 49.5 | 5.048
1805.2 | 49.5 | 5.048
1805.3 | 49.5 | 5.048
1805.4 | 49.5 | 5.048
1805.5 | 49.5 | 5.048
1805.6 | 49.5 | 5.048
1805.7 | 49.5 | 5.048
1805.8 | 49.5 | 5.048
1805.9 | 49.5 | 5.048
1806 | 49.5 | 5.048
1806.1 | 49.5 | 5.048
1806.2 | 49.5 | 5.048
1806.3 | 49.5 | 5.048
1806.4 | 49.5 | 5.048
1806.5 | 49.5 | 5.048
1806.6 | 49.5 | 5.048
1806.7 | 49.5 | 5.048
1806.8 | 49.5 | 5.048
1806.9 | 49.5 | 5.048
1807 | 49.5 | 5.048
1807.1 | 49.5 | 5.048
1807.2 | 49.5 | 5.048
1807.3 | 49.5 | 5.048
1807.4 | 49.5 | 5.048
1807.5 | 49.5 | 5.048
1807.6 | 49.5 | 5.048
1807.7 | 49.5 | 5.048
1807.8 | 49.5 | 5.048
1807.9 | 49.5 | 5.048
1808 | 49.5 | 5.048
1808.1 | 49.5 | 5.048
1808.2 | 49.5 | 5.048
1808.3 | 49.5 | 5.048
1808.4 | 49.5 | 5.048
1808.5 | 49.5 | 5.048
1808.6 | 49.5 | 5.048
1808.7 | 49.5 | 5.048
1808.8 | 49.5 | 5.049
1808.9 | 49.5 | 5.049
1809 | 49.5 | 5.049
1809.1 | 49.5 | 5.049
1809.2 | 49.5 | 5.049
1809.3 | 49.5 | 5.049
1809.4 | 49.5 | 5.049
1809.5 | 49.5 | 5.049
1809.6 | 49.5 | 5.049
1809.7 | 49.5 | 5.049
1809.8 | 49.5 | 5.049
1809.9 | 49.5 | 5.049
1810 | 49.5 | 5.048
1810.1 | 49.5 | 5.048
1810.2 | 49.5 | 5.048
1810.3 | 49.5 | 5.048
1810.4 | 49.5 | 5.048
1810.5 | 49.5 | 5.048
1810.6 | 49.5 | 5.048
1810.7 | 49.5 | 5.048
1810.8 | 49.5 | 5.048
1810.9 | 49.5 | 5.048
1811 | 49.5 | 5.048
1811.1 | 49.5 | 5.048
1811.2 | 49.5 | 5.048
1811.3 | 49.5 | 5.048
1811.4 | 49.5 | 5.048
1811.5 | 49.5 | 5.048
1811.6 | 49.5 | 5.048
1811.7 | 49.5 | 5.048
1811.8 | 49.5 | 5.048
1811.9 | 49.5 | 5.048
1812 | 49.5 | 5.048
1812.1 | 49.5 | 5.048
1812.2 | 49.5 | 5.048
1812.3 | 49.5 | 5.048
1812.4 | 49.5 | 5.048
1812.5 | 49.5 | 5.048
1812.6 | 49.5 | 5.048
1812.7 | 49.5 | 5.048
1812.8 | 49.5 | 5.048
1812.9 | 49.5 | 5.048
1813 | 49.5 | 5.048
1813.1 | 49.5 | 5.048
1813.2 | 49.5 | 5.048
1813.3 | 49.5 | 5.048
1813.4 | 49.5 | 5.048
1813.5 | 49.5 | 5.048
1813.6 | 49.5 | 5.048
1813.7 | 49.5 | 5.048
1813.8 | 49.5 | 5.048
1813.9 | 49.5 | 5.048
1814 | 49.5 | 5.048
1814.1 | 49.5 | 5.048
1814.2 | 49.5 | 5.048
1814.3 | 49.5 | 5.048
1814.4 | 49.5 | 5.048
1814.5 | 49.5 | 5.048
1814.6 | 49.5 | 5.048
1814.7 | 49.5 | 5.048
1814.8 | 49.5 | 5.048
1814.9 | 49.5 | 5.048
1815 | 49.5 | 5.048
1815.1 | 49.5 | 5.048
1815.2 | 49.5 | 5.048
1815.3 | 49.5 | 5.048
1815.4 | 49.5 | 5.048
1815.5 | 49.5 | 5.048
1815.6 | 49.5 | 5.048
1815.7 | 49.5 | 5.048
1815.8 | 49.5 | 5.048
1815.9 | 49.5 | 5.048
1816 | 49.5 | 5.048
1816.1 | 49.5 | 5.048
1816.2 | 49.5 | 5.048
1816.3 | 49.5 | 5.048
1816.4 | 49.5 | 5.048
1816.5 | 49.5 | 5.048
1816.6 | 49.5 | 5.048
1816.7 | 49.5 | 5.048
1816.8 | 49.5 | 5.048
1816.9 | 49.5 | 5.048
1817 | 49.5 | 5.048
1817.1 | 49.5 | 5.048
1817.2 | 49.5 | 5.048
1817.3 | 49.5 | 5.048
1817.4 | 49.5 | 5.048
1817.5 | 49.5 | 5.048
1817.6 | 49.5 | 5.048
1817.7 | 49.5 | 5.048
1817.8 | 49.5 | 5.048
1817.9 | 49.5 | 5.048
1818 | 49.5 | 5.048
1818.1 | 49.5 | 5.048
1818.2 | 49.5 | 5.048
1818.3 | 49.5 | 5.048
1818.4 | 49.5 | 5.048
1818.5 | 49.5 | 5.048
1818.6 | 49.5 | 5.048
1818.7 | 49.5 | 5.048
1818.8 | 49.5 | 5.048
1818.9 | 49.5 | 5.048
1819 | 49.5 | 5.048
1819.1 | 49.5 | 5.048
1819.2 | 49.5 | 5.048
1819.3 | 49.5 | 5.048
1819.4 | 49.5 | 5.048
1819.5 | 49.5 | 5.048
1819.6 | 49.5 | 5.048
1819.7 | 49.5 | 5.048
1819.8 | 49.5 | 5.048
1819.9 | 49.5 | 5.048
1820 | 49.5 | 5.048
1820.1 | 49.5 | 5.048
1820.2 | 49.5 | 5.048
1820.3 | 49.5 | 5.048
1820.4 | 49.5 | 5.048
1820.5 | 49.5 | 5.048
1820.6 | 49.5 | 5.048
1820.7 | 49.5 | 5.048
1820.8 | 49.5 | 5.048
1820.9 | 49.5 | 5.048
1821 | 49.5 | 5.048
1821.1 | 49.5 | 5.048
1821.2 | 49.5 | 5.048
1821.3 | 49.5 | 5.048
1821.4 | 49.5 | 5.048
1821.5 | 49.5 | 5.048
1821.6 | 49.5 | 5.048
1821.7 | 49.5 | 5.048
1821.8 | 49.5 | 5.048
1821.9 | 49.5 | 5.048
1822 | 49.5 | 5.048
1822.1 | 49.5 | 5.048
1822.2 | 49.5 | 5.048
1822.3 | 49.5 | 5.048
1822.4 | 49.5 | 5.048
1822.5 | 49.5 | 5.048
1822.6 | 49.5 | 5.048
1822.7 | 49.5 | 5.048
1822.8 | 49.5 | 5.048
1822.9 | 49.5 | 5.048
1823 | 49.5 | 5.048
1823.1 | 49.5 | 5.048
1823.2 | 49.5 | 5.048
1823.3 | 49.5 | 5.048
1823.4 | 49.5 | 5.048
1823.5 | 49.5 | 5.048
1823.6 | 49.5 | 5.048
1823.7 | 49.5 | 5.048
1823.8 | 49.5 | 5.048
1823.9 | 49.5 | 5.048
1824 | 49.5 | 5.048
1824.1 | 49.5 | 5.048
1824.2 | 49.5 | 5.048
1824.3 | 49.5 | 5.048
1824.4 | 49.5 | 5.048
1824.5 | 49.5 | 5.048
1824.6 | 49.5 | 5.048
1824.7 | 49.5 | 5.048
1824.8 | 49.5 | 5.048
1824.9 | 49.5 | 5.048
1825 | 49.5 | 5.048
1825.1 | 49.5 | 5.048
1825.2 | 49.5 | 5.048
1825.3 | 49.5 | 5.048
1825.4 | 49.5 | 5.048
1825.5 | 49.5 | 5.048
1825.6 | 49.5 | 5.048
1825.7 | 49.5 | 5.048
1825.8 | 49.5 | 5.048
1825.9 | 49.5 | 5.048
1826 | 49.5 | 5.048
1826.1 | 49.5 | 5.048
1826.2 | 49.5 | 5.048
1826.3 | 49.5 | 5.048
1826.4 | 49.5 | 5.048
1826.5 | 49.5 | 5.048
1826.6 | 49.5 | 5.048
1826.7 | 49.5 | 5.048
1826.8 | 49.5 | 5.048
1826.9 | 49.5 | 5.048
1827 | 49.5 | 5.048
1827.1 | 49.5 | 5.048
1827.2 | 49.5 | 5.048
1827.3 | 49.5 | 5.048
1827.4 | 49.5 | 5.048
1827.5 | 49.5 | 5.048
1827.6 | 49.5 | 5.048
1827.7 | 49.5 | 5.048
1827.8 | 49.5 | 5.048
1827.9 | 49.5 | 5.048
1828 | 49.5 | 5.048
1828.1 | 49.5 | 5.048
1828.2 | 49.5 | 5.048
1828.3 | 49.5 | 5.048
1828.4 | 49.5 | 5.048
1828.5 | 49.5 | 5.048
1828.6 | 49.5 | 5.048
1828.7 | 49.5 | 5.048
1828.8 | 49.5 | 5.048
1828.9 | 49.5 | 5.048
1829 | 49.5 | 5.048
1829.1 | 49.5 | 5.048
1829.2 | 49.5 | 5.048
1829.3 | 49.5 | 5.048
1829.4 | 49.5 | 5.048
1829.5 | 49.5 | 5.048
1829.6 | 49.5 | 5.048
1829.7 | 49.5 | 5.048
1829.8 | 49.5 | 5.048
1829.9 | 49.5 | 5.048
1830 | 50 | 5.048
1830.1 | 50 | 5.048
1830.2 | 50 | 5.048
1830.3 | 50 | 5.048
1830.4 | 50 | 5.048
1830.5 | 50 | 5.048
1830.6 | 50 | 5.048
1830.7 | 50 | 5.048
1830.8 | 50 | 5.048
1830.9 | 50 | 5.048
1831 | 50 | 5.048
1831.1 | 50 | 4.804
1831.2 | 50 | 3.54
1831.3 | 50 | 0.252
1831.4 | 50 | 0.09
1831.5 | 50 | -0.012
1831.6 | 50 | -0.011
1831.7 | 50 | -0.01
1831.8 | 50 | -0.009
1831.9 | 50 | -0.008
1832 | 50 | -0.008
1832.1 | 50 | -0.008
1832.2 | 50 | -0.008
1832.3 | 50 | -0.008
1832.4 | 50 | -0.008
1832.5 | 50 | -0.008
1832.6 | 50 | -0.008
1832.7 | 50 | -0.008
1832.8 | 50 | -0.008
1832.9 | 50 | -0.007
1833 | 50 | -0.007
1833.1 | 50 | -0.007
1833.2 | 50 | -0.007
1833.3 | 50 | -0.006
1833.4 | 50 | -0.006
1833.5 | 50 | -0.006
1833.6 | 50 | -0.005
1833.7 | 50 | -0.005
1833.8 | 50 | -0.005
1833.9 | 50 | -0.005
1834 | 50 | -0.005
1834.1 | 50 | -0.005
1834.2 | 50 | -0.005
1834.3 | 50 | -0.005
1834.4 | 50 | -0.005
1834.5 | 50 | -0.005
1834.6 | 50 | -0.005
1834.7 | 50 | -0.005
1834.8 | 50 | -0.005
1834.9 | 50 | -0.005
1835 | 50 | -0.005
1835.1 | 50 | -0.005
1835.2 | 50 | -0.005
1835.3 | 50 | -0.005
1835.4 | 50 | -0.005
1835.5 | 50 | -0.005
1835.6 | 50 | -0.005
1835.7 | 50 | -0.005
1835.8 | 50 | -0.005
1835.9 | 50 | -0.005
1836 | 50 | -0.005
1836.1 | 50 | -0.007
1836.2 | 50 | -0.007
1836.3 | 50 | -0.006
1836.4 | 50 | -0.006
1836.5 | 50 | -0.005
1836.6 | 50 | -0.005
1836.7 | 50 | -0.003
1836.8 | 50 | -0.002
1836.9 | 50 | -0.001
1837 | 50 | -0.001
1837.1 | 50 | -0.001
1837.2 | 50 | -0.001
1837.3 | 50 | -0.001
1837.4 | 50 | -0.001
1837.5 | 50 | -0.001
1837.6 | 50 | -0.001
1837.7 | 50 | -0.001
1837.8 | 50 | -0.001
1837.9 | 50 | -0.001
1838 | 50 | -0.002
1838.1 | 50 | -0.001
1838.2 | 50 | -0.001
1838.3 | 50 | -0.001
1838.4 | 50 | -0.001
1838.5 | 50 | -0.001
1838.6 | 50 | -0.001
1838.7 | 50 | -0.001
1838.8 | 50 | -0.001
1838.9 | 50 | -0.001
1839 | 50 | -0.001
1839.1 | 50 | -0.001
1839.2 | 50 | 0
1839.3 | 50 | 0
1839.4 | 50 | 0
1839.5 | 50 | 0
1839.6 | 50 | 0
1839.7 | 50 | 0
1839.8 | 50 | 0
1839.9 | 50 | 0
1840 | 50 | 0
1840.1 | 50 | 0
1840.2 | 50 | 0
1840.3 | 50 | 0
1840.4 | 50 | 0
1840.5 | 50 | 0
1840.6 | 50 | 0
1840.7 | 50 | 0
1840.8 | 50 | 0
1840.9 | 50 | 0
1841 | 50 | 0
1841.1 | 50 | 0
1841.2 | 50 | 0
1841.3 | 50 | 0
1841.4 | 50 | 0
1841.5 | 50 | 0
1841.6 | 50 | 0
1841.7 | 50 | 0
1841.8 | 50 | 0
1841.9 | 50 | 0
1842 | 50 | 0
1842.1 | 50 | 0
1842.2 | 50 | 0
1842.3 | 50 | 0
1842.4 | 50 | 0
1842.5 | 50 | 0
1842.6 | 50 | 0
1842.7 | 50 | 0
1842.8 | 50 | 0
1842.9 | 50 | 0
1843 | 50 | 0
1843.1 | 50 | 0
1843.2 | 50 | 0
1843.3 | 50 | 0
1843.4 | 50 | 0
1843.5 | 50 | 0
1843.6 | 50 | 0
1843.7 | 50 | 0
1843.8 | 50 | 0
1843.9 | 50 | 0
1844 | 50 | 0
1844.1 | 50 | 0
1844.2 | 50 | 0
1844.3 | 50 | 0
1844.4 | 50 | 0
1844.5 | 50 | 0
1844.6 | 50 | 0
1844.7 | 50 | 0
1844.8 | 50 | 0
1844.9 | 50 | 0
1845 | 50 | 0
1845.1 | 50 | 0
1845.2 | 50 | 0
1845.3 | 50 | 0
1845.4 | 50 | 0
1845.5 | 50 | 0
1845.6 | 50 | 0
1845.7 | 50 | 0
1845.8 | 50 | 0
1845.9 | 50 | 0
1846 | 50 | 0
1846.1 | 50 | 0
1846.2 | 50 | 0
1846.3 | 50 | 0
1846.4 | 50 | 0
1846.5 | 50 | 0
1846.6 | 50 | 0
1846.7 | 50 | 0
1846.8 | 50 | 0
1846.9 | 50 | 0
1847 | 50 | 0
1847.1 | 50 | 0
1847.2 | 50 | 0
1847.3 | 50 | 0
1847.4 | 50 | 0
1847.5 | 50 | 0
1847.6 | 50 | 0
1847.7 | 50 | 0
1847.8 | 50 | 0
1847.9 | 50 | 0
1848 | 50 | 0
1848.1 | 50 | 0
1848.2 | 50 | 0
1848.3 | 50 | 0
1848.4 | 50 | 0
1848.5 | 50 | 0
1848.6 | 50 | 0
1848.7 | 50 | 0
1848.8 | 50 | 0
1848.9 | 50 | 0
1849 | 50 | 0
1849.1 | 50 | 0
1849.2 | 50 | 0
1849.3 | 50 | 0
1849.4 | 50 | 0
1849.5 | 50 | 0
1849.6 | 50 | 0
1849.7 | 50 | 0
1849.8 | 50 | 0
1849.9 | 50 | 0
1850 | 50 | 0
1850.1 | 50 | 0
1850.2 | 50 | 0
1850.3 | 50 | 0
1850.4 | 50 | 0
1850.5 | 50 | 0
1850.6 | 50 | 0
1850.7 | 50 | 0
1850.8 | 50 | 0
1850.9 | 50 | 0
1851 | 50 | 0
1851.1 | 50 | 0
1851.2 | 50 | 0
1851.3 | 50 | 0
1851.4 | 50 | 0
1851.5 | 50 | 0
1851.6 | 50 | 0
1851.7 | 50 | 0
1851.8 | 50 | 0
1851.9 | 50 | 0
1852 | 50 | 0
1852.1 | 50 | 0
1852.2 | 50 | 0
1852.3 | 50 | 0
1852.4 | 50 | 0
1852.5 | 50 | 0
1852.6 | 50 | 0
1852.7 | 50 | 0
1852.8 | 50 | 0
1852.9 | 50 | 0
1853 | 50 | 0
1853.1 | 50 | 0
1853.2 | 50 | 0
1853.3 | 50 | 0
1853.4 | 50 | 0
1853.5 | 50 | 0
1853.6 | 50 | 0
1853.7 | 50 | 0
1853.8 | 50 | 0
1853.9 | 50 | 0
1854 | 50 | 0
1854.1 | 50 | 0
1854.2 | 50 | 0
1854.3 | 50 | 0
1854.4 | 50 | 0
1854.5 | 50 | 0
1854.6 | 50 | 0
1854.7 | 50 | 0
1854.8 | 50 | 0
1854.9 | 50 | 0
1855 | 50 | 0
1855.1 | 50 | 0
1855.2 | 50 | 0
1855.3 | 50 | 0
1855.4 | 50 | 0
1855.5 | 50 | 0
1855.6 | 50 | 0
1855.7 | 50 | 0
1855.8 | 50 | 0
1855.9 | 50 | 0
1856 | 50 | 0
1856.1 | 50 | 0
1856.2 | 50 | 0
1856.3 | 50 | 0
1856.4 | 50 | 0
1856.5 | 50 | 0
1856.6 | 50 | 0
1856.7 | 50 | 0
1856.8 | 50 | 0
1856.9 | 50 | 0
1857 | 50 | 0
1857.1 | 50 | 0
1857.2 | 50 | 0
1857.3 | 50 | 0
1857.4 | 50 | 0
1857.5 | 50 | 0
1857.6 | 50 | 0
1857.7 | 50 | 0
1857.8 | 50 | 0
1857.9 | 50 | 0
1858 | 50 | 0
1858.1 | 50 | 0
1858.2 | 50 | 0
1858.3 | 50 | 0
1858.4 | 50 | 0
1858.5 | 50 | 0
1858.6 | 50 | 0
1858.7 | 50 | 0
1858.8 | 50 | 0
1858.9 | 50 | 0
1859 | 50 | 0
1859.1 | 50 | 0
1859.2 | 50 | 0
1859.3 | 50 | 0
1859.4 | 50 | 0
1859.5 | 50 | 0
1859.6 | 50 | 0
1859.7 | 50 | 0
1859.8 | 50 | 0
1859.9 | 50 | 0
Note: SD calculation assumes Primary = Secondary.
If Primary ≠ Secondary then change cell J13 formula to =STDEV.P(INDIRECT(J9&":"&J10))

## Test 1.2 Single Asset
Time (s) | Frequency (Hz) | Active Power (MW)
0 | 50 | 0 | Asset/s Name/Ref
0.1 | 50 | 0 |  |  |  |  | Frequency Change
0.2 | 50 | 0 |  |  |  |  | High Start
0.3 | 50 | 0 | NewVol1 |  |  |  | 30
0.4 | 50 | 0 |  |  |  |  | 30
0.5 | 50 | 0 | Time Value at Which Frequency Changes |  |  |  | 40
0.6 | 50 | 0 |  |  |  | $C$402 | 40
0.7 | 50 | 0 |  |  |  | $C$18301 | 40
0.8 | 50 | 0 | 30 |  |  |  | 60
0.9 | 50 | 0 |  |  | High | -1.0092 | 2 Second Limit
1 | 50 | 0 | High Start |  | SD | 0.00011808 | 32
1.1 | 50 | 0 |  |  | % SD | 0.0023617 | 32
1.2 | 50 | 0 | 40
1.3 | 50 | 0
1.4 | 50 | 0 | High End | pre-Average | 0
1.5 | 50 | 0 |  | (edit range to average 10s before frequency change)
1.6 | 50 | 0 | 1829.9
1.7 | 50 | 0
1.8 | 50 | 0 | High Response
1.9 | 50 | 0
2 | 50 | 0 | -1.0092
2.1 | 50 | 0
2.2 | 50 | 0
2.3 | 50 | 0
2.4 | 50 | 0
2.5 | 50 | 0
2.6 | 50 | 0
2.7 | 50 | 0
2.8 | 50 | 0
2.9 | 50 | 0
3 | 50 | 0
3.1 | 50 | 0
3.2 | 50 | 0
3.3 | 50 | 0
3.4 | 50 | 0
3.5 | 50 | 0
3.6 | 50 | 0
3.7 | 50 | 0
3.8 | 50 | 0
3.9 | 50 | 0
4 | 50 | 0
4.1 | 50 | 0
4.2 | 50 | 0
4.3 | 50 | 0
4.4 | 50 | 0
4.5 | 50 | 0
4.6 | 50 | 0
4.7 | 50 | 0
4.8 | 50 | 0
4.9 | 50 | 0
5 | 50 | 0
5.1 | 50 | 0
5.2 | 50 | 0
5.3 | 50 | 0
5.4 | 50 | 0
5.5 | 50 | 0
5.6 | 50 | 0
5.7 | 50 | 0
5.8 | 50 | 0
5.9 | 50 | 0
6 | 50 | 0
6.1 | 50 | 0
6.2 | 50 | 0
6.3 | 50 | 0
6.4 | 50 | 0
6.5 | 50 | 0
6.6 | 50 | 0
6.7 | 50 | 0
6.8 | 50 | 0
6.9 | 50 | 0
7 | 50 | 0
7.1 | 50 | 0
7.2 | 50 | 0
7.3 | 50 | 0
7.4 | 50 | 0
7.5 | 50 | 0
7.6 | 50 | 0
7.7 | 50 | 0
7.8 | 50 | 0
7.9 | 50 | 0
8 | 50 | 0
8.1 | 50 | 0
8.2 | 50 | 0
8.3 | 50 | 0
8.4 | 50 | 0
8.5 | 50 | 0
8.6 | 50 | 0
8.7 | 50 | 0
8.8 | 50 | 0
8.9 | 50 | 0
9 | 50 | 0
9.1 | 50 | 0
9.2 | 50 | 0
9.3 | 50 | 0
9.4 | 50 | 0
9.5 | 50 | 0
9.6 | 50 | 0
9.7 | 50 | 0
9.8 | 50 | 0
9.9 | 50 | 0
10 | 50 | 0
10.1 | 50 | 0
10.2 | 50 | 0
10.3 | 50 | 0
10.4 | 50 | 0
10.5 | 50 | 0
10.6 | 50 | 0
10.7 | 50 | 0
10.8 | 50 | 0
10.9 | 50 | 0
11 | 50 | 0
11.1 | 50 | 0
11.2 | 50 | 0
11.3 | 50 | 0
11.4 | 50 | 0
11.5 | 50 | 0
11.6 | 50 | 0
11.7 | 50 | 0
11.8 | 50 | 0
11.9 | 50 | 0
12 | 50 | 0
12.1 | 50 | 0
12.2 | 50 | 0
12.3 | 50 | 0
12.4 | 50 | 0
12.5 | 50 | 0
12.6 | 50 | 0
12.7 | 50 | 0
12.8 | 50 | 0
12.9 | 50 | 0
13 | 50 | 0
13.1 | 50 | 0
13.2 | 50 | 0
13.3 | 50 | 0
13.4 | 50 | 0
13.5 | 50 | 0
13.6 | 50 | 0
13.7 | 50 | 0
13.8 | 50 | 0
13.9 | 50 | 0
14 | 50 | 0
14.1 | 50 | 0
14.2 | 50 | 0
14.3 | 50 | 0
14.4 | 50 | 0
14.5 | 50 | 0
14.6 | 50 | 0
14.7 | 50 | 0
14.8 | 50 | 0
14.9 | 50 | 0
15 | 50 | 0
15.1 | 50 | 0
15.2 | 50 | 0
15.3 | 50 | 0
15.4 | 50 | 0
15.5 | 50 | 0
15.6 | 50 | 0
15.7 | 50 | 0
15.8 | 50 | 0
15.9 | 50 | 0
16 | 50 | 0
16.1 | 50 | 0
16.2 | 50 | 0
16.3 | 50 | 0
16.4 | 50 | 0
16.5 | 50 | 0
16.6 | 50 | 0
16.7 | 50 | 0
16.8 | 50 | 0
16.9 | 50 | 0
17 | 50 | 0
17.1 | 50 | 0
17.2 | 50 | 0
17.3 | 50 | 0
17.4 | 50 | 0
17.5 | 50 | 0
17.6 | 50 | 0
17.7 | 50 | 0
17.8 | 50 | 0
17.9 | 50 | 0
18 | 50 | 0
18.1 | 50 | 0
18.2 | 50 | 0
18.3 | 50 | 0
18.4 | 50 | 0
18.5 | 50 | 0
18.6 | 50 | 0
18.7 | 50 | 0
18.8 | 50 | 0
18.9 | 50 | 0
19 | 50 | 0
19.1 | 50 | 0
19.2 | 50 | 0
19.3 | 50 | 0
19.4 | 50 | 0
19.5 | 50 | 0
19.6 | 50 | 0
19.7 | 50 | 0
19.8 | 50 | 0
19.9 | 50 | 0
20 | 50 | 0
20.1 | 50 | 0
20.2 | 50 | 0
20.3 | 50 | 0
20.4 | 50 | 0
20.5 | 50 | 0
20.6 | 50 | 0
20.7 | 50 | 0
20.8 | 50 | 0
20.9 | 50 | 0
21 | 50 | 0
21.1 | 50 | 0
21.2 | 50 | 0
21.3 | 50 | 0
21.4 | 50 | 0
21.5 | 50 | 0
21.6 | 50 | 0
21.7 | 50 | 0
21.8 | 50 | 0
21.9 | 50 | 0
22 | 50 | 0
22.1 | 50 | 0
22.2 | 50 | 0
22.3 | 50 | 0
22.4 | 50 | 0
22.5 | 50 | 0
22.6 | 50 | 0
22.7 | 50 | 0
22.8 | 50 | 0
22.9 | 50 | 0
23 | 50 | 0
23.1 | 50 | 0
23.2 | 50 | 0
23.3 | 50 | 0
23.4 | 50 | 0
23.5 | 50 | 0
23.6 | 50 | 0
23.7 | 50 | 0
23.8 | 50 | 0
23.9 | 50 | 0
24 | 50 | 0
24.1 | 50 | 0
24.2 | 50 | 0
24.3 | 50 | 0
24.4 | 50 | 0
24.5 | 50 | 0
24.6 | 50 | 0
24.7 | 50 | 0
24.8 | 50 | 0
24.9 | 50 | 0
25 | 50 | 0
25.1 | 50 | 0
25.2 | 50 | 0
25.3 | 50 | 0
25.4 | 50 | 0
25.5 | 50 | 0
25.6 | 50 | 0
25.7 | 50 | 0
25.8 | 50 | 0
25.9 | 50 | 0
26 | 50 | 0
26.1 | 50 | 0
26.2 | 50 | 0
26.3 | 50 | 0
26.4 | 50 | 0
26.5 | 50 | 0
26.6 | 50 | 0
26.7 | 50 | 0
26.8 | 50 | 0
26.9 | 50 | 0
27 | 50 | 0
27.1 | 50 | 0
27.2 | 50 | 0
27.3 | 50 | 0
27.4 | 50 | 0
27.5 | 50 | 0
27.6 | 50 | 0
27.7 | 50 | 0
27.8 | 50 | 0
27.9 | 50 | 0
28 | 50 | 0
28.1 | 50 | 0
28.2 | 50 | 0
28.3 | 50 | 0
28.4 | 50 | 0
28.5 | 50 | 0
28.6 | 50 | 0
28.7 | 50 | 0
28.8 | 50 | 0
28.9 | 50 | 0
29 | 50 | 0
29.1 | 50 | 0
29.2 | 50 | 0
29.3 | 50 | 0
29.4 | 50 | 0
29.5 | 50 | 0
29.6 | 50 | 0
29.7 | 50 | 0
29.8 | 50 | 0
29.9 | 50 | 0
30 | 50.5 | 0
30.1 | 50.5 | -0.005
30.2 | 50.5 | -0.0184
30.3 | 50.5 | -0.5958
30.4 | 50.5 | -0.982
30.5 | 50.5 | -1.0036
30.6 | 50.5 | -1.0166
30.7 | 50.5 | -1.0158
30.8 | 50.5 | -1.0156
30.9 | 50.5 | -1.0156
31 | 50.5 | -1.0156
31.1 | 50.5 | -1.0154
31.2 | 50.5 | -1.0156
31.3 | 50.5 | -1.0156
31.4 | 50.5 | -1.0156
31.5 | 50.5 | -1.0156
31.6 | 50.5 | -1.0158
31.7 | 50.5 | -1.0156
31.8 | 50.5 | -1.0156
31.9 | 50.5 | -1.0156
32 | 50.5 | -1.0158
32.1 | 50.5 | -1.0158
32.2 | 50.5 | -1.0158
32.3 | 50.5 | -1.0158
32.4 | 50.5 | -1.0158
32.5 | 50.5 | -1.0158
32.6 | 50.5 | -1.0158
32.7 | 50.5 | -1.0158
32.8 | 50.5 | -1.0158
32.9 | 50.5 | -1.0158
33 | 50.5 | -1.0158
33.1 | 50.5 | -1.0158
33.2 | 50.5 | -1.0158
33.3 | 50.5 | -1.0158
33.4 | 50.5 | -1.0158
33.5 | 50.5 | -1.0158
33.6 | 50.5 | -1.0158
33.7 | 50.5 | -1.0158
33.8 | 50.5 | -1.0158
33.9 | 50.5 | -1.0158
34 | 50.5 | -1.0158
34.1 | 50.5 | -1.0158
34.2 | 50.5 | -1.0158
34.3 | 50.5 | -1.0158
34.4 | 50.5 | -1.0158
34.5 | 50.5 | -1.0158
34.6 | 50.5 | -1.0156
34.7 | 50.5 | -1.0156
34.8 | 50.5 | -1.0156
34.9 | 50.5 | -1.0158
35 | 50.5 | -1.0158
35.1 | 50.5 | -1.0158
35.2 | 50.5 | -1.0158
35.3 | 50.5 | -1.016
35.4 | 50.5 | -1.016
35.5 | 50.5 | -1.016
35.6 | 50.5 | -1.016
35.7 | 50.5 | -1.016
35.8 | 50.5 | -1.0158
35.9 | 50.5 | -1.0158
36 | 50.5 | -1.0154
36.1 | 50.5 | -1.0152
36.2 | 50.5 | -1.015
36.3 | 50.5 | -1.015
36.4 | 50.5 | -1.015
36.5 | 50.5 | -1.015
36.6 | 50.5 | -1.015
36.7 | 50.5 | -1.015
36.8 | 50.5 | -1.015
36.9 | 50.5 | -1.015
37 | 50.5 | -1.0148
37.1 | 50.5 | -1.0146
37.2 | 50.5 | -1.0146
37.3 | 50.5 | -1.0146
37.4 | 50.5 | -1.0144
37.5 | 50.5 | -1.0144
37.6 | 50.5 | -1.0144
37.7 | 50.5 | -1.0144
37.8 | 50.5 | -1.0144
37.9 | 50.5 | -1.0144
38 | 50.5 | -1.0144
38.1 | 50.5 | -1.0144
38.2 | 50.5 | -1.014
38.3 | 50.5 | -1.014
38.4 | 50.5 | -1.0136
38.5 | 50.5 | -1.0134
38.6 | 50.5 | -1.0134
38.7 | 50.5 | -1.0134
38.8 | 50.5 | -1.0134
38.9 | 50.5 | -1.0134
39 | 50.5 | -1.0134
39.1 | 50.5 | -1.0134
39.2 | 50.5 | -1.0134
39.3 | 50.5 | -1.0134
39.4 | 50.5 | -1.0132
39.5 | 50.5 | -1.013
39.6 | 50.5 | -1.0128
39.7 | 50.5 | -1.0126
39.8 | 50.5 | -1.0124
39.9 | 50.5 | -1.0124
40 | 50.5 | -1.0124
40.1 | 50.5 | -1.0124
40.2 | 50.5 | -1.0124
40.3 | 50.5 | -1.0124
40.4 | 50.5 | -1.0124
40.5 | 50.5 | -1.0124
40.6 | 50.5 | -1.012
40.7 | 50.5 | -1.0118
40.8 | 50.5 | -1.0116
40.9 | 50.5 | -1.0114
41 | 50.5 | -1.0114
41.1 | 50.5 | -1.0114
41.2 | 50.5 | -1.0114
41.3 | 50.5 | -1.0114
41.4 | 50.5 | -1.0114
41.5 | 50.5 | -1.0114
41.6 | 50.5 | -1.0112
41.7 | 50.5 | -1.0112
41.8 | 50.5 | -1.0112
41.9 | 50.5 | -1.011
42 | 50.5 | -1.0108
42.1 | 50.5 | -1.0108
42.2 | 50.5 | -1.0108
42.3 | 50.5 | -1.0108
42.4 | 50.5 | -1.0108
42.5 | 50.5 | -1.0108
42.6 | 50.5 | -1.0108
42.7 | 50.5 | -1.0108
42.8 | 50.5 | -1.0104
42.9 | 50.5 | -1.0104
43 | 50.5 | -1.01
43.1 | 50.5 | -1.01
43.2 | 50.5 | -1.01
43.3 | 50.5 | -1.01
43.4 | 50.5 | -1.01
43.5 | 50.5 | -1.01
43.6 | 50.5 | -1.01
43.7 | 50.5 | -1.01
43.8 | 50.5 | -1.01
43.9 | 50.5 | -1.01
44 | 50.5 | -1.0098
44.1 | 50.5 | -1.0098
44.2 | 50.5 | -1.0098
44.3 | 50.5 | -1.0096
44.4 | 50.5 | -1.0096
44.5 | 50.5 | -1.0096
44.6 | 50.5 | -1.0096
44.7 | 50.5 | -1.0096
44.8 | 50.5 | -1.0096
44.9 | 50.5 | -1.0096
45 | 50.5 | -1.0096
45.1 | 50.5 | -1.0096
45.2 | 50.5 | -1.0096
45.3 | 50.5 | -1.0096
45.4 | 50.5 | -1.0094
45.5 | 50.5 | -1.0094
45.6 | 50.5 | -1.0094
45.7 | 50.5 | -1.0094
45.8 | 50.5 | -1.0094
45.9 | 50.5 | -1.0094
46 | 50.5 | -1.0094
46.1 | 50.5 | -1.0094
46.2 | 50.5 | -1.0094
46.3 | 50.5 | -1.0094
46.4 | 50.5 | -1.0094
46.5 | 50.5 | -1.0094
46.6 | 50.5 | -1.0094
46.7 | 50.5 | -1.0094
46.8 | 50.5 | -1.0094
46.9 | 50.5 | -1.0094
47 | 50.5 | -1.0094
47.1 | 50.5 | -1.0094
47.2 | 50.5 | -1.0094
47.3 | 50.5 | -1.0094
47.4 | 50.5 | -1.0094
47.5 | 50.5 | -1.0094
47.6 | 50.5 | -1.0094
47.7 | 50.5 | -1.0094
47.8 | 50.5 | -1.0094
47.9 | 50.5 | -1.0094
48 | 50.5 | -1.0094
48.1 | 50.5 | -1.0094
48.2 | 50.5 | -1.0094
48.3 | 50.5 | -1.0094
48.4 | 50.5 | -1.0094
48.5 | 50.5 | -1.0096
48.6 | 50.5 | -1.0096
48.7 | 50.5 | -1.0096
48.8 | 50.5 | -1.0096
48.9 | 50.5 | -1.0096
49 | 50.5 | -1.0096
49.1 | 50.5 | -1.0096
49.2 | 50.5 | -1.0096
49.3 | 50.5 | -1.0096
49.4 | 50.5 | -1.0096
49.5 | 50.5 | -1.0096
49.6 | 50.5 | -1.0096
49.7 | 50.5 | -1.0096
49.8 | 50.5 | -1.0094
49.9 | 50.5 | -1.0094
50 | 50.5 | -1.0094
50.1 | 50.5 | -1.0094
50.2 | 50.5 | -1.0094
50.3 | 50.5 | -1.0094
50.4 | 50.5 | -1.0094
50.5 | 50.5 | -1.0094
50.6 | 50.5 | -1.0094
50.7 | 50.5 | -1.0094
50.8 | 50.5 | -1.0094
50.9 | 50.5 | -1.0094
51 | 50.5 | -1.0094
51.1 | 50.5 | -1.0094
51.2 | 50.5 | -1.0094
51.3 | 50.5 | -1.0094
51.4 | 50.5 | -1.0094
51.5 | 50.5 | -1.0094
51.6 | 50.5 | -1.0094
51.7 | 50.5 | -1.0094
51.8 | 50.5 | -1.0094
51.9 | 50.5 | -1.0094
52 | 50.5 | -1.0094
52.1 | 50.5 | -1.0094
52.2 | 50.5 | -1.0094
52.3 | 50.5 | -1.0094
52.4 | 50.5 | -1.0094
52.5 | 50.5 | -1.0096
52.6 | 50.5 | -1.0096
52.7 | 50.5 | -1.0096
52.8 | 50.5 | -1.0096
52.9 | 50.5 | -1.0096
53 | 50.5 | -1.0096
53.1 | 50.5 | -1.0096
53.2 | 50.5 | -1.0096
53.3 | 50.5 | -1.0096
53.4 | 50.5 | -1.0096
53.5 | 50.5 | -1.0096
53.6 | 50.5 | -1.0098
53.7 | 50.5 | -1.0098
53.8 | 50.5 | -1.0096
53.9 | 50.5 | -1.0096
54 | 50.5 | -1.0096
54.1 | 50.5 | -1.0096
54.2 | 50.5 | -1.0096
54.3 | 50.5 | -1.0096
54.4 | 50.5 | -1.0096
54.5 | 50.5 | -1.0096
54.6 | 50.5 | -1.0096
54.7 | 50.5 | -1.0096
54.8 | 50.5 | -1.0096
54.9 | 50.5 | -1.0096
55 | 50.5 | -1.0094
55.1 | 50.5 | -1.0094
55.2 | 50.5 | -1.0094
55.3 | 50.5 | -1.0094
55.4 | 50.5 | -1.0094
55.5 | 50.5 | -1.0094
55.6 | 50.5 | -1.0094
55.7 | 50.5 | -1.0094
55.8 | 50.5 | -1.0094
55.9 | 50.5 | -1.0094
56 | 50.5 | -1.0094
56.1 | 50.5 | -1.0094
56.2 | 50.5 | -1.0094
56.3 | 50.5 | -1.0094
56.4 | 50.5 | -1.0094
56.5 | 50.5 | -1.0094
56.6 | 50.5 | -1.0094
56.7 | 50.5 | -1.0094
56.8 | 50.5 | -1.0094
56.9 | 50.5 | -1.0094
57 | 50.5 | -1.0094
57.1 | 50.5 | -1.0094
57.2 | 50.5 | -1.0094
57.3 | 50.5 | -1.0094
57.4 | 50.5 | -1.0094
57.5 | 50.5 | -1.0094
57.6 | 50.5 | -1.0094
57.7 | 50.5 | -1.0094
57.8 | 50.5 | -1.0094
57.9 | 50.5 | -1.0094
58 | 50.5 | -1.0096
58.1 | 50.5 | -1.0096
58.2 | 50.5 | -1.0096
58.3 | 50.5 | -1.0096
58.4 | 50.5 | -1.0096
58.5 | 50.5 | -1.0096
58.6 | 50.5 | -1.0096
58.7 | 50.5 | -1.0096
58.8 | 50.5 | -1.0096
58.9 | 50.5 | -1.0096
59 | 50.5 | -1.0096
59.1 | 50.5 | -1.0096
59.2 | 50.5 | -1.0096
59.3 | 50.5 | -1.0096
59.4 | 50.5 | -1.0096
59.5 | 50.5 | -1.0096
59.6 | 50.5 | -1.0096
59.7 | 50.5 | -1.0096
59.8 | 50.5 | -1.0096
59.9 | 50.5 | -1.0096
60 | 50.5 | -1.0096
60.1 | 50.5 | -1.0096
60.2 | 50.5 | -1.0096
60.3 | 50.5 | -1.0096
60.4 | 50.5 | -1.0096
60.5 | 50.5 | -1.0096
60.6 | 50.5 | -1.0096
60.7 | 50.5 | -1.0096
60.8 | 50.5 | -1.0096
60.9 | 50.5 | -1.0096
61 | 50.5 | -1.0096
61.1 | 50.5 | -1.0096
61.2 | 50.5 | -1.0096
61.3 | 50.5 | -1.0096
61.4 | 50.5 | -1.0096
61.5 | 50.5 | -1.0096
61.6 | 50.5 | -1.0096
61.7 | 50.5 | -1.0096
61.8 | 50.5 | -1.0096
61.9 | 50.5 | -1.0096
62 | 50.5 | -1.0096
62.1 | 50.5 | -1.0096
62.2 | 50.5 | -1.0096
62.3 | 50.5 | -1.0096
62.4 | 50.5 | -1.0096
62.5 | 50.5 | -1.0096
62.6 | 50.5 | -1.0096
62.7 | 50.5 | -1.0096
62.8 | 50.5 | -1.0096
62.9 | 50.5 | -1.0096
63 | 50.5 | -1.0096
63.1 | 50.5 | -1.0096
63.2 | 50.5 | -1.0096
63.3 | 50.5 | -1.0096
63.4 | 50.5 | -1.0096
63.5 | 50.5 | -1.0096
63.6 | 50.5 | -1.0096
63.7 | 50.5 | -1.0096
63.8 | 50.5 | -1.0096
63.9 | 50.5 | -1.0094
64 | 50.5 | -1.0094
64.1 | 50.5 | -1.0094
64.2 | 50.5 | -1.0094
64.3 | 50.5 | -1.0094
64.4 | 50.5 | -1.0094
64.5 | 50.5 | -1.0094
64.6 | 50.5 | -1.0094
64.7 | 50.5 | -1.0094
64.8 | 50.5 | -1.0094
64.9 | 50.5 | -1.0094
65 | 50.5 | -1.0094
65.1 | 50.5 | -1.0096
65.2 | 50.5 | -1.0096
65.3 | 50.5 | -1.0096
65.4 | 50.5 | -1.0096
65.5 | 50.5 | -1.0096
65.6 | 50.5 | -1.0096
65.7 | 50.5 | -1.0096
65.8 | 50.5 | -1.0096
65.9 | 50.5 | -1.0096
66 | 50.5 | -1.0096
66.1 | 50.5 | -1.0096
66.2 | 50.5 | -1.0096
66.3 | 50.5 | -1.0096
66.4 | 50.5 | -1.0096
66.5 | 50.5 | -1.0096
66.6 | 50.5 | -1.0096
66.7 | 50.5 | -1.0096
66.8 | 50.5 | -1.0096
66.9 | 50.5 | -1.0096
67 | 50.5 | -1.0096
67.1 | 50.5 | -1.0096
67.2 | 50.5 | -1.0096
67.3 | 50.5 | -1.0096
67.4 | 50.5 | -1.0096
67.5 | 50.5 | -1.0096
67.6 | 50.5 | -1.0096
67.7 | 50.5 | -1.0096
67.8 | 50.5 | -1.0096
67.9 | 50.5 | -1.0096
68 | 50.5 | -1.0096
68.1 | 50.5 | -1.0096
68.2 | 50.5 | -1.0096
68.3 | 50.5 | -1.0096
68.4 | 50.5 | -1.0096
68.5 | 50.5 | -1.0096
68.6 | 50.5 | -1.0096
68.7 | 50.5 | -1.0096
68.8 | 50.5 | -1.0096
68.9 | 50.5 | -1.0096
69 | 50.5 | -1.0096
69.1 | 50.5 | -1.0096
69.2 | 50.5 | -1.0096
69.3 | 50.5 | -1.0096
69.4 | 50.5 | -1.0096
69.5 | 50.5 | -1.0096
69.6 | 50.5 | -1.0096
69.7 | 50.5 | -1.0096
69.8 | 50.5 | -1.0096
69.9 | 50.5 | -1.0094
70 | 50.5 | -1.0094
70.1 | 50.5 | -1.0094
70.2 | 50.5 | -1.0094
70.3 | 50.5 | -1.0094
70.4 | 50.5 | -1.0094
70.5 | 50.5 | -1.0094
70.6 | 50.5 | -1.0094
70.7 | 50.5 | -1.0094
70.8 | 50.5 | -1.0094
70.9 | 50.5 | -1.0094
71 | 50.5 | -1.0094
71.1 | 50.5 | -1.0094
71.2 | 50.5 | -1.0094
71.3 | 50.5 | -1.0094
71.4 | 50.5 | -1.0094
71.5 | 50.5 | -1.0094
71.6 | 50.5 | -1.0094
71.7 | 50.5 | -1.0094
71.8 | 50.5 | -1.0094
71.9 | 50.5 | -1.0094
72 | 50.5 | -1.0096
72.1 | 50.5 | -1.0096
72.2 | 50.5 | -1.0096
72.3 | 50.5 | -1.0096
72.4 | 50.5 | -1.0096
72.5 | 50.5 | -1.0096
72.6 | 50.5 | -1.0096
72.7 | 50.5 | -1.0096
72.8 | 50.5 | -1.0096
72.9 | 50.5 | -1.0096
73 | 50.5 | -1.0096
73.1 | 50.5 | -1.0096
73.2 | 50.5 | -1.0096
73.3 | 50.5 | -1.0096
73.4 | 50.5 | -1.0096
73.5 | 50.5 | -1.0096
73.6 | 50.5 | -1.0096
73.7 | 50.5 | -1.0096
73.8 | 50.5 | -1.0096
73.9 | 50.5 | -1.0096
74 | 50.5 | -1.0096
74.1 | 50.5 | -1.0096
74.2 | 50.5 | -1.0096
74.3 | 50.5 | -1.0096
74.4 | 50.5 | -1.0096
74.5 | 50.5 | -1.0096
74.6 | 50.5 | -1.0096
74.7 | 50.5 | -1.0096
74.8 | 50.5 | -1.0096
74.9 | 50.5 | -1.0096
75 | 50.5 | -1.0096
75.1 | 50.5 | -1.0096
75.2 | 50.5 | -1.0096
75.3 | 50.5 | -1.0096
75.4 | 50.5 | -1.0096
75.5 | 50.5 | -1.0096
75.6 | 50.5 | -1.0096
75.7 | 50.5 | -1.0096
75.8 | 50.5 | -1.0096
75.9 | 50.5 | -1.0096
76 | 50.5 | -1.0096
76.1 | 50.5 | -1.0096
76.2 | 50.5 | -1.0096
76.3 | 50.5 | -1.0096
76.4 | 50.5 | -1.0096
76.5 | 50.5 | -1.0096
76.6 | 50.5 | -1.0096
76.7 | 50.5 | -1.0096
76.8 | 50.5 | -1.0096
76.9 | 50.5 | -1.0096
77 | 50.5 | -1.0096
77.1 | 50.5 | -1.0096
77.2 | 50.5 | -1.0096
77.3 | 50.5 | -1.0096
77.4 | 50.5 | -1.0096
77.5 | 50.5 | -1.0096
77.6 | 50.5 | -1.0096
77.7 | 50.5 | -1.0096
77.8 | 50.5 | -1.0096
77.9 | 50.5 | -1.0096
78 | 50.5 | -1.0096
78.1 | 50.5 | -1.0096
78.2 | 50.5 | -1.0096
78.3 | 50.5 | -1.0096
78.4 | 50.5 | -1.0096
78.5 | 50.5 | -1.0096
78.6 | 50.5 | -1.0096
78.7 | 50.5 | -1.0096
78.8 | 50.5 | -1.0096
78.9 | 50.5 | -1.0096
79 | 50.5 | -1.0096
79.1 | 50.5 | -1.0096
79.2 | 50.5 | -1.0094
79.3 | 50.5 | -1.0094
79.4 | 50.5 | -1.0094
79.5 | 50.5 | -1.0094
79.6 | 50.5 | -1.0094
79.7 | 50.5 | -1.0094
79.8 | 50.5 | -1.0094
79.9 | 50.5 | -1.0094
80 | 50.5 | -1.0094
80.1 | 50.5 | -1.0094
80.2 | 50.5 | -1.0094
80.3 | 50.5 | -1.0094
80.4 | 50.5 | -1.0096
80.5 | 50.5 | -1.0096
80.6 | 50.5 | -1.0096
80.7 | 50.5 | -1.0096
80.8 | 50.5 | -1.0096
80.9 | 50.5 | -1.0096
81 | 50.5 | -1.0096
81.1 | 50.5 | -1.0096
81.2 | 50.5 | -1.0096
81.3 | 50.5 | -1.0096
81.4 | 50.5 | -1.0096
81.5 | 50.5 | -1.0098
81.6 | 50.5 | -1.0096
81.7 | 50.5 | -1.0096
81.8 | 50.5 | -1.0096
81.9 | 50.5 | -1.0096
82 | 50.5 | -1.0096
82.1 | 50.5 | -1.0096
82.2 | 50.5 | -1.0096
82.3 | 50.5 | -1.0096
82.4 | 50.5 | -1.0096
82.5 | 50.5 | -1.0096
82.6 | 50.5 | -1.0096
82.7 | 50.5 | -1.0096
82.8 | 50.5 | -1.0096
82.9 | 50.5 | -1.0096
83 | 50.5 | -1.0096
83.1 | 50.5 | -1.0096
83.2 | 50.5 | -1.0096
83.3 | 50.5 | -1.0096
83.4 | 50.5 | -1.0096
83.5 | 50.5 | -1.0096
83.6 | 50.5 | -1.0096
83.7 | 50.5 | -1.0096
83.8 | 50.5 | -1.0096
83.9 | 50.5 | -1.0096
84 | 50.5 | -1.0096
84.1 | 50.5 | -1.0096
84.2 | 50.5 | -1.0094
84.3 | 50.5 | -1.0094
84.4 | 50.5 | -1.0094
84.5 | 50.5 | -1.0094
84.6 | 50.5 | -1.0094
84.7 | 50.5 | -1.0094
84.8 | 50.5 | -1.0096
84.9 | 50.5 | -1.0096
85 | 50.5 | -1.0096
85.1 | 50.5 | -1.0096
85.2 | 50.5 | -1.0096
85.3 | 50.5 | -1.0096
85.4 | 50.5 | -1.0096
85.5 | 50.5 | -1.0096
85.6 | 50.5 | -1.0096
85.7 | 50.5 | -1.0096
85.8 | 50.5 | -1.0096
85.9 | 50.5 | -1.0096
86 | 50.5 | -1.0096
86.1 | 50.5 | -1.0096
86.2 | 50.5 | -1.0094
86.3 | 50.5 | -1.0094
86.4 | 50.5 | -1.0094
86.5 | 50.5 | -1.0094
86.6 | 50.5 | -1.0094
86.7 | 50.5 | -1.0094
86.8 | 50.5 | -1.0094
86.9 | 50.5 | -1.0094
87 | 50.5 | -1.0094
87.1 | 50.5 | -1.0094
87.2 | 50.5 | -1.0094
87.3 | 50.5 | -1.0096
87.4 | 50.5 | -1.0096
87.5 | 50.5 | -1.0096
87.6 | 50.5 | -1.0096
87.7 | 50.5 | -1.0096
87.8 | 50.5 | -1.0096
87.9 | 50.5 | -1.0096
88 | 50.5 | -1.0096
88.1 | 50.5 | -1.0096
88.2 | 50.5 | -1.0096
88.3 | 50.5 | -1.0096
88.4 | 50.5 | -1.0096
88.5 | 50.5 | -1.0096
88.6 | 50.5 | -1.0096
88.7 | 50.5 | -1.0096
88.8 | 50.5 | -1.0096
88.9 | 50.5 | -1.0096
89 | 50.5 | -1.0096
89.1 | 50.5 | -1.0096
89.2 | 50.5 | -1.0096
89.3 | 50.5 | -1.0096
89.4 | 50.5 | -1.0096
89.5 | 50.5 | -1.0096
89.6 | 50.5 | -1.0096
89.7 | 50.5 | -1.0096
89.8 | 50.5 | -1.0096
89.9 | 50.5 | -1.0096
90 | 50.5 | -1.0096
90.1 | 50.5 | -1.0096
90.2 | 50.5 | -1.0096
90.3 | 50.5 | -1.0096
90.4 | 50.5 | -1.0096
90.5 | 50.5 | -1.0096
90.6 | 50.5 | -1.0096
90.7 | 50.5 | -1.0096
90.8 | 50.5 | -1.0096
90.9 | 50.5 | -1.0096
91 | 50.5 | -1.0096
91.1 | 50.5 | -1.0096
91.2 | 50.5 | -1.0096
91.3 | 50.5 | -1.0096
91.4 | 50.5 | -1.0096
91.5 | 50.5 | -1.0096
91.6 | 50.5 | -1.0096
91.7 | 50.5 | -1.0096
91.8 | 50.5 | -1.0096
91.9 | 50.5 | -1.0096
92 | 50.5 | -1.0096
92.1 | 50.5 | -1.0096
92.2 | 50.5 | -1.0096
92.3 | 50.5 | -1.0096
92.4 | 50.5 | -1.0096
92.5 | 50.5 | -1.0096
92.6 | 50.5 | -1.0096
92.7 | 50.5 | -1.0096
92.8 | 50.5 | -1.0096
92.9 | 50.5 | -1.0096
93 | 50.5 | -1.0096
93.1 | 50.5 | -1.0096
93.2 | 50.5 | -1.0094
93.3 | 50.5 | -1.0094
93.4 | 50.5 | -1.0094
93.5 | 50.5 | -1.0094
93.6 | 50.5 | -1.0094
93.7 | 50.5 | -1.0094
93.8 | 50.5 | -1.0094
93.9 | 50.5 | -1.0094
94 | 50.5 | -1.0094
94.1 | 50.5 | -1.0094
94.2 | 50.5 | -1.0094
94.3 | 50.5 | -1.0094
94.4 | 50.5 | -1.0094
94.5 | 50.5 | -1.0094
94.6 | 50.5 | -1.0094
94.7 | 50.5 | -1.0094
94.8 | 50.5 | -1.0094
94.9 | 50.5 | -1.0094
95 | 50.5 | -1.0094
95.1 | 50.5 | -1.0094
95.2 | 50.5 | -1.0094
95.3 | 50.5 | -1.0094
95.4 | 50.5 | -1.0094
95.5 | 50.5 | -1.0094
95.6 | 50.5 | -1.0094
95.7 | 50.5 | -1.0094
95.8 | 50.5 | -1.0094
95.9 | 50.5 | -1.0094
96 | 50.5 | -1.0094
96.1 | 50.5 | -1.0094
96.2 | 50.5 | -1.0094
96.3 | 50.5 | -1.0094
96.4 | 50.5 | -1.0094
96.5 | 50.5 | -1.0094
96.6 | 50.5 | -1.0094
96.7 | 50.5 | -1.0094
96.8 | 50.5 | -1.0096
96.9 | 50.5 | -1.0096
97 | 50.5 | -1.0096
97.1 | 50.5 | -1.0096
97.2 | 50.5 | -1.0096
97.3 | 50.5 | -1.0096
97.4 | 50.5 | -1.0096
97.5 | 50.5 | -1.0096
97.6 | 50.5 | -1.0096
97.7 | 50.5 | -1.0096
97.8 | 50.5 | -1.0096
97.9 | 50.5 | -1.0096
98 | 50.5 | -1.0096
98.1 | 50.5 | -1.0096
98.2 | 50.5 | -1.0096
98.3 | 50.5 | -1.0096
98.4 | 50.5 | -1.0096
98.5 | 50.5 | -1.0096
98.6 | 50.5 | -1.0096
98.7 | 50.5 | -1.0096
98.8 | 50.5 | -1.0096
98.9 | 50.5 | -1.0096
99 | 50.5 | -1.0096
99.1 | 50.5 | -1.0096
99.2 | 50.5 | -1.0096
99.3 | 50.5 | -1.0096
99.4 | 50.5 | -1.0096
99.5 | 50.5 | -1.0096
99.6 | 50.5 | -1.0096
99.7 | 50.5 | -1.0096
99.8 | 50.5 | -1.0096
99.9 | 50.5 | -1.0096
100 | 50.5 | -1.0096
100.1 | 50.5 | -1.0096
100.2 | 50.5 | -1.0096
100.3 | 50.5 | -1.0096
100.4 | 50.5 | -1.0096
100.5 | 50.5 | -1.0096
100.6 | 50.5 | -1.0096
100.7 | 50.5 | -1.0096
100.8 | 50.5 | -1.0096
100.9 | 50.5 | -1.0096
101 | 50.5 | -1.0096
101.1 | 50.5 | -1.0096
101.2 | 50.5 | -1.0096
101.3 | 50.5 | -1.0096
101.4 | 50.5 | -1.0096
101.5 | 50.5 | -1.0096
101.6 | 50.5 | -1.0096
101.7 | 50.5 | -1.0096
101.8 | 50.5 | -1.0096
101.9 | 50.5 | -1.0096
102 | 50.5 | -1.0096
102.1 | 50.5 | -1.0096
102.2 | 50.5 | -1.0096
102.3 | 50.5 | -1.0096
102.4 | 50.5 | -1.0096
102.5 | 50.5 | -1.0096
102.6 | 50.5 | -1.0094
102.7 | 50.5 | -1.0094
102.8 | 50.5 | -1.0094
102.9 | 50.5 | -1.0094
103 | 50.5 | -1.0094
103.1 | 50.5 | -1.0094
103.2 | 50.5 | -1.0094
103.3 | 50.5 | -1.0094
103.4 | 50.5 | -1.0094
103.5 | 50.5 | -1.0094
103.6 | 50.5 | -1.0096
103.7 | 50.5 | -1.0096
103.8 | 50.5 | -1.0096
103.9 | 50.5 | -1.0096
104 | 50.5 | -1.0096
104.1 | 50.5 | -1.0096
104.2 | 50.5 | -1.0096
104.3 | 50.5 | -1.0096
104.4 | 50.5 | -1.0096
104.5 | 50.5 | -1.0096
104.6 | 50.5 | -1.0096
104.7 | 50.5 | -1.0096
104.8 | 50.5 | -1.0096
104.9 | 50.5 | -1.0096
105 | 50.5 | -1.0096
105.1 | 50.5 | -1.0096
105.2 | 50.5 | -1.0096
105.3 | 50.5 | -1.0096
105.4 | 50.5 | -1.0096
105.5 | 50.5 | -1.0096
105.6 | 50.5 | -1.0096
105.7 | 50.5 | -1.0096
105.8 | 50.5 | -1.0096
105.9 | 50.5 | -1.0096
106 | 50.5 | -1.0096
106.1 | 50.5 | -1.0096
106.2 | 50.5 | -1.0096
106.3 | 50.5 | -1.0096
106.4 | 50.5 | -1.0096
106.5 | 50.5 | -1.0096
106.6 | 50.5 | -1.0096
106.7 | 50.5 | -1.0096
106.8 | 50.5 | -1.0096
106.9 | 50.5 | -1.0096
107 | 50.5 | -1.0096
107.1 | 50.5 | -1.0096
107.2 | 50.5 | -1.0096
107.3 | 50.5 | -1.0096
107.4 | 50.5 | -1.0096
107.5 | 50.5 | -1.0096
107.6 | 50.5 | -1.0096
107.7 | 50.5 | -1.0096
107.8 | 50.5 | -1.0096
107.9 | 50.5 | -1.0096
108 | 50.5 | -1.0096
108.1 | 50.5 | -1.0096
108.2 | 50.5 | -1.0096
108.3 | 50.5 | -1.0096
108.4 | 50.5 | -1.0096
108.5 | 50.5 | -1.0094
108.6 | 50.5 | -1.0094
108.7 | 50.5 | -1.0094
108.8 | 50.5 | -1.0094
108.9 | 50.5 | -1.0094
109 | 50.5 | -1.0094
109.1 | 50.5 | -1.0094
109.2 | 50.5 | -1.0094
109.3 | 50.5 | -1.0094
109.4 | 50.5 | -1.0094
109.5 | 50.5 | -1.0094
109.6 | 50.5 | -1.0094
109.7 | 50.5 | -1.0094
109.8 | 50.5 | -1.0094
109.9 | 50.5 | -1.0094
110 | 50.5 | -1.0094
110.1 | 50.5 | -1.0094
110.2 | 50.5 | -1.0094
110.3 | 50.5 | -1.0094
110.4 | 50.5 | -1.0094
110.5 | 50.5 | -1.0094
110.6 | 50.5 | -1.0094
110.7 | 50.5 | -1.0094
110.8 | 50.5 | -1.0094
110.9 | 50.5 | -1.0094
111 | 50.5 | -1.0094
111.1 | 50.5 | -1.0094
111.2 | 50.5 | -1.0094
111.3 | 50.5 | -1.0094
111.4 | 50.5 | -1.0094
111.5 | 50.5 | -1.0094
111.6 | 50.5 | -1.0094
111.7 | 50.5 | -1.0094
111.8 | 50.5 | -1.0094
111.9 | 50.5 | -1.0096
112 | 50.5 | -1.0096
112.1 | 50.5 | -1.0096
112.2 | 50.5 | -1.0096
112.3 | 50.5 | -1.0096
112.4 | 50.5 | -1.0096
112.5 | 50.5 | -1.0096
112.6 | 50.5 | -1.0096
112.7 | 50.5 | -1.0096
112.8 | 50.5 | -1.0096
112.9 | 50.5 | -1.0096
113 | 50.5 | -1.0096
113.1 | 50.5 | -1.0096
113.2 | 50.5 | -1.0096
113.3 | 50.5 | -1.0096
113.4 | 50.5 | -1.0096
113.5 | 50.5 | -1.0096
113.6 | 50.5 | -1.0096
113.7 | 50.5 | -1.0096
113.8 | 50.5 | -1.0096
113.9 | 50.5 | -1.0096
114 | 50.5 | -1.0096
114.1 | 50.5 | -1.0096
114.2 | 50.5 | -1.0096
114.3 | 50.5 | -1.0096
114.4 | 50.5 | -1.0096
114.5 | 50.5 | -1.0096
114.6 | 50.5 | -1.0096
114.7 | 50.5 | -1.0096
114.8 | 50.5 | -1.0096
114.9 | 50.5 | -1.0096
115 | 50.5 | -1.0096
115.1 | 50.5 | -1.0096
115.2 | 50.5 | -1.0096
115.3 | 50.5 | -1.0096
115.4 | 50.5 | -1.0096
115.5 | 50.5 | -1.0096
115.6 | 50.5 | -1.0096
115.7 | 50.5 | -1.0096
115.8 | 50.5 | -1.0096
115.9 | 50.5 | -1.0096
116 | 50.5 | -1.0096
116.1 | 50.5 | -1.0096
116.2 | 50.5 | -1.0096
116.3 | 50.5 | -1.0096
116.4 | 50.5 | -1.0096
116.5 | 50.5 | -1.0096
116.6 | 50.5 | -1.0096
116.7 | 50.5 | -1.0096
116.8 | 50.5 | -1.0096
116.9 | 50.5 | -1.0096
117 | 50.5 | -1.0096
117.1 | 50.5 | -1.0096
117.2 | 50.5 | -1.0096
117.3 | 50.5 | -1.0096
117.4 | 50.5 | -1.0096
117.5 | 50.5 | -1.0096
117.6 | 50.5 | -1.0096
117.7 | 50.5 | -1.0096
117.8 | 50.5 | -1.0096
117.9 | 50.5 | -1.0094
118 | 50.5 | -1.0094
118.1 | 50.5 | -1.0094
118.2 | 50.5 | -1.0094
118.3 | 50.5 | -1.0094
118.4 | 50.5 | -1.0094
118.5 | 50.5 | -1.0094
118.6 | 50.5 | -1.0094
118.7 | 50.5 | -1.0094
118.8 | 50.5 | -1.0096
118.9 | 50.5 | -1.0096
119 | 50.5 | -1.0096
119.1 | 50.5 | -1.0096
119.2 | 50.5 | -1.0096
119.3 | 50.5 | -1.0096
119.4 | 50.5 | -1.0096
119.5 | 50.5 | -1.0096
119.6 | 50.5 | -1.0096
119.7 | 50.5 | -1.0096
119.8 | 50.5 | -1.0096
119.9 | 50.5 | -1.0096
120 | 50.5 | -1.0098
120.1 | 50.5 | -1.0098
120.2 | 50.5 | -1.0098
120.3 | 50.5 | -1.0098
120.4 | 50.5 | -1.0098
120.5 | 50.5 | -1.0096
120.6 | 50.5 | -1.0096
120.7 | 50.5 | -1.0096
120.8 | 50.5 | -1.0096
120.9 | 50.5 | -1.0096
121 | 50.5 | -1.0096
121.1 | 50.5 | -1.0096
121.2 | 50.5 | -1.0096
121.3 | 50.5 | -1.0096
121.4 | 50.5 | -1.0096
121.5 | 50.5 | -1.0096
121.6 | 50.5 | -1.0096
121.7 | 50.5 | -1.0096
121.8 | 50.5 | -1.0096
121.9 | 50.5 | -1.0096
122 | 50.5 | -1.0096
122.1 | 50.5 | -1.0096
122.2 | 50.5 | -1.0096
122.3 | 50.5 | -1.0096
122.4 | 50.5 | -1.0096
122.5 | 50.5 | -1.0096
122.6 | 50.5 | -1.0096
122.7 | 50.5 | -1.0096
122.8 | 50.5 | -1.0096
122.9 | 50.5 | -1.0096
123 | 50.5 | -1.0096
123.1 | 50.5 | -1.0096
123.2 | 50.5 | -1.0096
123.3 | 50.5 | -1.0096
123.4 | 50.5 | -1.0096
123.5 | 50.5 | -1.0096
123.6 | 50.5 | -1.0096
123.7 | 50.5 | -1.0094
123.8 | 50.5 | -1.0094
123.9 | 50.5 | -1.0094
124 | 50.5 | -1.0094
124.1 | 50.5 | -1.0094
124.2 | 50.5 | -1.0094
124.3 | 50.5 | -1.0094
124.4 | 50.5 | -1.0094
124.5 | 50.5 | -1.0094
124.6 | 50.5 | -1.0094
124.7 | 50.5 | -1.0094
124.8 | 50.5 | -1.0094
124.9 | 50.5 | -1.0096
125 | 50.5 | -1.0096
125.1 | 50.5 | -1.0096
125.2 | 50.5 | -1.0096
125.3 | 50.5 | -1.0096
125.4 | 50.5 | -1.0096
125.5 | 50.5 | -1.0096
125.6 | 50.5 | -1.0096
125.7 | 50.5 | -1.0096
125.8 | 50.5 | -1.0096
125.9 | 50.5 | -1.0096
126 | 50.5 | -1.0096
126.1 | 50.5 | -1.0096
126.2 | 50.5 | -1.0094
126.3 | 50.5 | -1.0094
126.4 | 50.5 | -1.0094
126.5 | 50.5 | -1.0094
126.6 | 50.5 | -1.0094
126.7 | 50.5 | -1.0094
126.8 | 50.5 | -1.0094
126.9 | 50.5 | -1.0094
127 | 50.5 | -1.0094
127.1 | 50.5 | -1.0094
127.2 | 50.5 | -1.0094
127.3 | 50.5 | -1.0094
127.4 | 50.5 | -1.0094
127.5 | 50.5 | -1.0094
127.6 | 50.5 | -1.0094
127.7 | 50.5 | -1.0094
127.8 | 50.5 | -1.0094
127.9 | 50.5 | -1.0094
128 | 50.5 | -1.0094
128.1 | 50.5 | -1.0094
128.2 | 50.5 | -1.0094
128.3 | 50.5 | -1.0094
128.4 | 50.5 | -1.0096
128.5 | 50.5 | -1.0096
128.6 | 50.5 | -1.0096
128.7 | 50.5 | -1.0096
128.8 | 50.5 | -1.0096
128.9 | 50.5 | -1.0096
129 | 50.5 | -1.0096
129.1 | 50.5 | -1.0096
129.2 | 50.5 | -1.0096
129.3 | 50.5 | -1.0096
129.4 | 50.5 | -1.0096
129.5 | 50.5 | -1.0096
129.6 | 50.5 | -1.0096
129.7 | 50.5 | -1.0096
129.8 | 50.5 | -1.0096
129.9 | 50.5 | -1.0096
130 | 50.5 | -1.0096
130.1 | 50.5 | -1.0096
130.2 | 50.5 | -1.0096
130.3 | 50.5 | -1.0096
130.4 | 50.5 | -1.0096
130.5 | 50.5 | -1.0096
130.6 | 50.5 | -1.0096
130.7 | 50.5 | -1.0096
130.8 | 50.5 | -1.0096
130.9 | 50.5 | -1.0096
131 | 50.5 | -1.0096
131.1 | 50.5 | -1.0096
131.2 | 50.5 | -1.0096
131.3 | 50.5 | -1.0096
131.4 | 50.5 | -1.0096
131.5 | 50.5 | -1.0096
131.6 | 50.5 | -1.0096
131.7 | 50.5 | -1.0096
131.8 | 50.5 | -1.0096
131.9 | 50.5 | -1.0096
132 | 50.5 | -1.0096
132.1 | 50.5 | -1.0096
132.2 | 50.5 | -1.0096
132.3 | 50.5 | -1.0096
132.4 | 50.5 | -1.0096
132.5 | 50.5 | -1.0096
132.6 | 50.5 | -1.0096
132.7 | 50.5 | -1.0096
132.8 | 50.5 | -1.0096
132.9 | 50.5 | -1.0096
133 | 50.5 | -1.0094
133.1 | 50.5 | -1.0094
133.2 | 50.5 | -1.0094
133.3 | 50.5 | -1.0094
133.4 | 50.5 | -1.0094
133.5 | 50.5 | -1.0094
133.6 | 50.5 | -1.0094
133.7 | 50.5 | -1.0094
133.8 | 50.5 | -1.0094
133.9 | 50.5 | -1.0094
134 | 50.5 | -1.0094
134.1 | 50.5 | -1.0094
134.2 | 50.5 | -1.0094
134.3 | 50.5 | -1.0094
134.4 | 50.5 | -1.0094
134.5 | 50.5 | -1.0094
134.6 | 50.5 | -1.0094
134.7 | 50.5 | -1.0094
134.8 | 50.5 | -1.0094
134.9 | 50.5 | -1.0094
135 | 50.5 | -1.0094
135.1 | 50.5 | -1.0094
135.2 | 50.5 | -1.0096
135.3 | 50.5 | -1.0096
135.4 | 50.5 | -1.0096
135.5 | 50.5 | -1.0096
135.6 | 50.5 | -1.0096
135.7 | 50.5 | -1.0096
135.8 | 50.5 | -1.0096
135.9 | 50.5 | -1.0096
136 | 50.5 | -1.0096
136.1 | 50.5 | -1.0096
136.2 | 50.5 | -1.0096
136.3 | 50.5 | -1.0096
136.4 | 50.5 | -1.0096
136.5 | 50.5 | -1.0096
136.6 | 50.5 | -1.0096
136.7 | 50.5 | -1.0096
136.8 | 50.5 | -1.0096
136.9 | 50.5 | -1.0096
137 | 50.5 | -1.0096
137.1 | 50.5 | -1.0096
137.2 | 50.5 | -1.0096
137.3 | 50.5 | -1.0096
137.4 | 50.5 | -1.0096
137.5 | 50.5 | -1.0096
137.6 | 50.5 | -1.0096
137.7 | 50.5 | -1.0096
137.8 | 50.5 | -1.0096
137.9 | 50.5 | -1.0096
138 | 50.5 | -1.0096
138.1 | 50.5 | -1.0096
138.2 | 50.5 | -1.0096
138.3 | 50.5 | -1.0096
138.4 | 50.5 | -1.0096
138.5 | 50.5 | -1.0096
138.6 | 50.5 | -1.0096
138.7 | 50.5 | -1.0096
138.8 | 50.5 | -1.0096
138.9 | 50.5 | -1.0096
139 | 50.5 | -1.0096
139.1 | 50.5 | -1.0096
139.2 | 50.5 | -1.0096
139.3 | 50.5 | -1.0096
139.4 | 50.5 | -1.0096
139.5 | 50.5 | -1.0096
139.6 | 50.5 | -1.0096
139.7 | 50.5 | -1.0096
139.8 | 50.5 | -1.0096
139.9 | 50.5 | -1.0096
140 | 50.5 | -1.0096
140.1 | 50.5 | -1.0094
140.2 | 50.5 | -1.0094
140.3 | 50.5 | -1.0094
140.4 | 50.5 | -1.0094
140.5 | 50.5 | -1.0094
140.6 | 50.5 | -1.0094
140.7 | 50.5 | -1.0094
140.8 | 50.5 | -1.0094
140.9 | 50.5 | -1.0094
141 | 50.5 | -1.0094
141.1 | 50.5 | -1.0096
141.2 | 50.5 | -1.0096
141.3 | 50.5 | -1.0096
141.4 | 50.5 | -1.0096
141.5 | 50.5 | -1.0096
141.6 | 50.5 | -1.0096
141.7 | 50.5 | -1.0096
141.8 | 50.5 | -1.0096
141.9 | 50.5 | -1.0096
142 | 50.5 | -1.0096
142.1 | 50.5 | -1.0096
142.2 | 50.5 | -1.0096
142.3 | 50.5 | -1.0096
142.4 | 50.5 | -1.0096
142.5 | 50.5 | -1.0096
142.6 | 50.5 | -1.0096
142.7 | 50.5 | -1.0096
142.8 | 50.5 | -1.0096
142.9 | 50.5 | -1.0096
143 | 50.5 | -1.0096
143.1 | 50.5 | -1.0096
143.2 | 50.5 | -1.0096
143.3 | 50.5 | -1.0096
143.4 | 50.5 | -1.0096
143.5 | 50.5 | -1.0096
143.6 | 50.5 | -1.0096
143.7 | 50.5 | -1.0096
143.8 | 50.5 | -1.0096
143.9 | 50.5 | -1.0096
144 | 50.5 | -1.0096
144.1 | 50.5 | -1.0096
144.2 | 50.5 | -1.0096
144.3 | 50.5 | -1.0096
144.4 | 50.5 | -1.0096
144.5 | 50.5 | -1.0096
144.6 | 50.5 | -1.0096
144.7 | 50.5 | -1.0096
144.8 | 50.5 | -1.0096
144.9 | 50.5 | -1.0096
145 | 50.5 | -1.0096
145.1 | 50.5 | -1.0096
145.2 | 50.5 | -1.0096
145.3 | 50.5 | -1.0096
145.4 | 50.5 | -1.0096
145.5 | 50.5 | -1.0096
145.6 | 50.5 | -1.0096
145.7 | 50.5 | -1.0096
145.8 | 50.5 | -1.0096
145.9 | 50.5 | -1.0096
146 | 50.5 | -1.0096
146.1 | 50.5 | -1.0096
146.2 | 50.5 | -1.0096
146.3 | 50.5 | -1.0096
146.4 | 50.5 | -1.0096
146.5 | 50.5 | -1.0096
146.6 | 50.5 | -1.0096
146.7 | 50.5 | -1.0096
146.8 | 50.5 | -1.0096
146.9 | 50.5 | -1.0096
147 | 50.5 | -1.0096
147.1 | 50.5 | -1.0096
147.2 | 50.5 | -1.0096
147.3 | 50.5 | -1.0096
147.4 | 50.5 | -1.0096
147.5 | 50.5 | -1.0096
147.6 | 50.5 | -1.0096
147.7 | 50.5 | -1.0096
147.8 | 50.5 | -1.0096
147.9 | 50.5 | -1.0096
148 | 50.5 | -1.0096
148.1 | 50.5 | -1.0096
148.2 | 50.5 | -1.0096
148.3 | 50.5 | -1.0096
148.4 | 50.5 | -1.0096
148.5 | 50.5 | -1.0096
148.6 | 50.5 | -1.0096
148.7 | 50.5 | -1.0096
148.8 | 50.5 | -1.0096
148.9 | 50.5 | -1.0096
149 | 50.5 | -1.0096
149.1 | 50.5 | -1.0096
149.2 | 50.5 | -1.0096
149.3 | 50.5 | -1.0096
149.4 | 50.5 | -1.0096
149.5 | 50.5 | -1.0096
149.6 | 50.5 | -1.0094
149.7 | 50.5 | -1.0094
149.8 | 50.5 | -1.0094
149.9 | 50.5 | -1.0094
150 | 50.5 | -1.0094
150.1 | 50.5 | -1.0094
150.2 | 50.5 | -1.0094
150.3 | 50.5 | -1.0094
150.4 | 50.5 | -1.0096
150.5 | 50.5 | -1.0096
150.6 | 50.5 | -1.0096
150.7 | 50.5 | -1.0096
150.8 | 50.5 | -1.0096
150.9 | 50.5 | -1.0096
151 | 50.5 | -1.0096
151.1 | 50.5 | -1.0096
151.2 | 50.5 | -1.0096
151.3 | 50.5 | -1.0096
151.4 | 50.5 | -1.0096
151.5 | 50.5 | -1.0096
151.6 | 50.5 | -1.0096
151.7 | 50.5 | -1.0094
151.8 | 50.5 | -1.0094
151.9 | 50.5 | -1.0094
152 | 50.5 | -1.0094
152.1 | 50.5 | -1.0094
152.2 | 50.5 | -1.0094
152.3 | 50.5 | -1.0094
152.4 | 50.5 | -1.0094
152.5 | 50.5 | -1.0094
152.6 | 50.5 | -1.0094
152.7 | 50.5 | -1.0094
152.8 | 50.5 | -1.0094
152.9 | 50.5 | -1.0094
153 | 50.5 | -1.0094
153.1 | 50.5 | -1.0094
153.2 | 50.5 | -1.0096
153.3 | 50.5 | -1.0096
153.4 | 50.5 | -1.0096
153.5 | 50.5 | -1.0096
153.6 | 50.5 | -1.0096
153.7 | 50.5 | -1.0096
153.8 | 50.5 | -1.0096
153.9 | 50.5 | -1.0096
154 | 50.5 | -1.0096
154.1 | 50.5 | -1.0096
154.2 | 50.5 | -1.0096
154.3 | 50.5 | -1.0096
154.4 | 50.5 | -1.0096
154.5 | 50.5 | -1.0096
154.6 | 50.5 | -1.0096
154.7 | 50.5 | -1.0096
154.8 | 50.5 | -1.0096
154.9 | 50.5 | -1.0096
155 | 50.5 | -1.0096
155.1 | 50.5 | -1.0096
155.2 | 50.5 | -1.0096
155.3 | 50.5 | -1.0096
155.4 | 50.5 | -1.0096
155.5 | 50.5 | -1.0096
155.6 | 50.5 | -1.0096
155.7 | 50.5 | -1.0096
155.8 | 50.5 | -1.0096
155.9 | 50.5 | -1.0094
156 | 50.5 | -1.0094
156.1 | 50.5 | -1.0094
156.2 | 50.5 | -1.0094
156.3 | 50.5 | -1.0094
156.4 | 50.5 | -1.0096
156.5 | 50.5 | -1.0096
156.6 | 50.5 | -1.0096
156.7 | 50.5 | -1.0096
156.8 | 50.5 | -1.0096
156.9 | 50.5 | -1.0096
157 | 50.5 | -1.0096
157.1 | 50.5 | -1.0096
157.2 | 50.5 | -1.0096
157.3 | 50.5 | -1.0096
157.4 | 50.5 | -1.0096
157.5 | 50.5 | -1.0096
157.6 | 50.5 | -1.0096
157.7 | 50.5 | -1.0096
157.8 | 50.5 | -1.0096
157.9 | 50.5 | -1.0096
158 | 50.5 | -1.0096
158.1 | 50.5 | -1.0096
158.2 | 50.5 | -1.0096
158.3 | 50.5 | -1.0096
158.4 | 50.5 | -1.0096
158.5 | 50.5 | -1.0096
158.6 | 50.5 | -1.0096
158.7 | 50.5 | -1.0096
158.8 | 50.5 | -1.0096
158.9 | 50.5 | -1.0096
159 | 50.5 | -1.0096
159.1 | 50.5 | -1.0096
159.2 | 50.5 | -1.0096
159.3 | 50.5 | -1.0096
159.4 | 50.5 | -1.0096
159.5 | 50.5 | -1.0096
159.6 | 50.5 | -1.0096
159.7 | 50.5 | -1.0096
159.8 | 50.5 | -1.0096
159.9 | 50.5 | -1.0094
160 | 50.5 | -1.0096
160.1 | 50.5 | -1.0096
160.2 | 50.5 | -1.0096
160.3 | 50.5 | -1.0096
160.4 | 50.5 | -1.0096
160.5 | 50.5 | -1.0096
160.6 | 50.5 | -1.0096
160.7 | 50.5 | -1.0096
160.8 | 50.5 | -1.0096
160.9 | 50.5 | -1.0096
161 | 50.5 | -1.0096
161.1 | 50.5 | -1.0096
161.2 | 50.5 | -1.0096
161.3 | 50.5 | -1.0096
161.4 | 50.5 | -1.0096
161.5 | 50.5 | -1.0096
161.6 | 50.5 | -1.0096
161.7 | 50.5 | -1.0096
161.8 | 50.5 | -1.0096
161.9 | 50.5 | -1.0096
162 | 50.5 | -1.0096
162.1 | 50.5 | -1.0096
162.2 | 50.5 | -1.0098
162.3 | 50.5 | -1.0098
162.4 | 50.5 | -1.0096
162.5 | 50.5 | -1.0096
162.6 | 50.5 | -1.0096
162.7 | 50.5 | -1.0096
162.8 | 50.5 | -1.0096
162.9 | 50.5 | -1.0096
163 | 50.5 | -1.0096
163.1 | 50.5 | -1.0096
163.2 | 50.5 | -1.0096
163.3 | 50.5 | -1.0096
163.4 | 50.5 | -1.0096
163.5 | 50.5 | -1.0096
163.6 | 50.5 | -1.0096
163.7 | 50.5 | -1.0096
163.8 | 50.5 | -1.0096
163.9 | 50.5 | -1.0096
164 | 50.5 | -1.0096
164.1 | 50.5 | -1.0096
164.2 | 50.5 | -1.0096
164.3 | 50.5 | -1.0096
164.4 | 50.5 | -1.0096
164.5 | 50.5 | -1.0096
164.6 | 50.5 | -1.0096
164.7 | 50.5 | -1.0096
164.8 | 50.5 | -1.0096
164.9 | 50.5 | -1.0096
165 | 50.5 | -1.0096
165.1 | 50.5 | -1.0096
165.2 | 50.5 | -1.0096
165.3 | 50.5 | -1.0096
165.4 | 50.5 | -1.0096
165.5 | 50.5 | -1.0096
165.6 | 50.5 | -1.0096
165.7 | 50.5 | -1.0096
165.8 | 50.5 | -1.0096
165.9 | 50.5 | -1.0094
166 | 50.5 | -1.0094
166.1 | 50.5 | -1.0094
166.2 | 50.5 | -1.0094
166.3 | 50.5 | -1.0094
166.4 | 50.5 | -1.0094
166.5 | 50.5 | -1.0094
166.6 | 50.5 | -1.0094
166.7 | 50.5 | -1.0094
166.8 | 50.5 | -1.0094
166.9 | 50.5 | -1.0094
167 | 50.5 | -1.0094
167.1 | 50.5 | -1.0094
167.2 | 50.5 | -1.0094
167.3 | 50.5 | -1.0094
167.4 | 50.5 | -1.0094
167.5 | 50.5 | -1.0094
167.6 | 50.5 | -1.0094
167.7 | 50.5 | -1.0094
167.8 | 50.5 | -1.0094
167.9 | 50.5 | -1.0094
168 | 50.5 | -1.0096
168.1 | 50.5 | -1.0096
168.2 | 50.5 | -1.0096
168.3 | 50.5 | -1.0096
168.4 | 50.5 | -1.0096
168.5 | 50.5 | -1.0096
168.6 | 50.5 | -1.0096
168.7 | 50.5 | -1.0096
168.8 | 50.5 | -1.0096
168.9 | 50.5 | -1.0096
169 | 50.5 | -1.0096
169.1 | 50.5 | -1.0096
169.2 | 50.5 | -1.0096
169.3 | 50.5 | -1.0096
169.4 | 50.5 | -1.0096
169.5 | 50.5 | -1.0096
169.6 | 50.5 | -1.0096
169.7 | 50.5 | -1.0096
169.8 | 50.5 | -1.0096
169.9 | 50.5 | -1.0096
170 | 50.5 | -1.0096
170.1 | 50.5 | -1.0096
170.2 | 50.5 | -1.0096
170.3 | 50.5 | -1.0096
170.4 | 50.5 | -1.0096
170.5 | 50.5 | -1.0096
170.6 | 50.5 | -1.0096
170.7 | 50.5 | -1.0096
170.8 | 50.5 | -1.0096
170.9 | 50.5 | -1.0096
171 | 50.5 | -1.0096
171.1 | 50.5 | -1.0096
171.2 | 50.5 | -1.0096
171.3 | 50.5 | -1.0096
171.4 | 50.5 | -1.0096
171.5 | 50.5 | -1.0096
171.6 | 50.5 | -1.0096
171.7 | 50.5 | -1.0096
171.8 | 50.5 | -1.0096
171.9 | 50.5 | -1.0096
172 | 50.5 | -1.0096
172.1 | 50.5 | -1.0096
172.2 | 50.5 | -1.0096
172.3 | 50.5 | -1.0096
172.4 | 50.5 | -1.0096
172.5 | 50.5 | -1.0096
172.6 | 50.5 | -1.0096
172.7 | 50.5 | -1.0096
172.8 | 50.5 | -1.0096
172.9 | 50.5 | -1.0096
173 | 50.5 | -1.0096
173.1 | 50.5 | -1.0096
173.2 | 50.5 | -1.0096
173.3 | 50.5 | -1.0096
173.4 | 50.5 | -1.0096
173.5 | 50.5 | -1.0096
173.6 | 50.5 | -1.0096
173.7 | 50.5 | -1.0096
173.8 | 50.5 | -1.0096
173.9 | 50.5 | -1.0096
174 | 50.5 | -1.0096
174.1 | 50.5 | -1.0094
174.2 | 50.5 | -1.0094
174.3 | 50.5 | -1.0094
174.4 | 50.5 | -1.0094
174.5 | 50.5 | -1.0094
174.6 | 50.5 | -1.0094
174.7 | 50.5 | -1.0094
174.8 | 50.5 | -1.0094
174.9 | 50.5 | -1.0094
175 | 50.5 | -1.0094
175.1 | 50.5 | -1.0094
175.2 | 50.5 | -1.0094
175.3 | 50.5 | -1.0094
175.4 | 50.5 | -1.0094
175.5 | 50.5 | -1.0094
175.6 | 50.5 | -1.0094
175.7 | 50.5 | -1.0094
175.8 | 50.5 | -1.0094
175.9 | 50.5 | -1.0094
176 | 50.5 | -1.0094
176.1 | 50.5 | -1.0094
176.2 | 50.5 | -1.0094
176.3 | 50.5 | -1.0094
176.4 | 50.5 | -1.0096
176.5 | 50.5 | -1.0096
176.6 | 50.5 | -1.0096
176.7 | 50.5 | -1.0096
176.8 | 50.5 | -1.0096
176.9 | 50.5 | -1.0096
177 | 50.5 | -1.0096
177.1 | 50.5 | -1.0096
177.2 | 50.5 | -1.0096
177.3 | 50.5 | -1.0096
177.4 | 50.5 | -1.0096
177.5 | 50.5 | -1.0096
177.6 | 50.5 | -1.0096
177.7 | 50.5 | -1.0096
177.8 | 50.5 | -1.0096
177.9 | 50.5 | -1.0096
178 | 50.5 | -1.0096
178.1 | 50.5 | -1.0096
178.2 | 50.5 | -1.0096
178.3 | 50.5 | -1.0096
178.4 | 50.5 | -1.0096
178.5 | 50.5 | -1.0096
178.6 | 50.5 | -1.0096
178.7 | 50.5 | -1.0096
178.8 | 50.5 | -1.0096
178.9 | 50.5 | -1.0096
179 | 50.5 | -1.0096
179.1 | 50.5 | -1.0096
179.2 | 50.5 | -1.0096
179.3 | 50.5 | -1.0096
179.4 | 50.5 | -1.0096
179.5 | 50.5 | -1.0096
179.6 | 50.5 | -1.0096
179.7 | 50.5 | -1.0096
179.8 | 50.5 | -1.0094
179.9 | 50.5 | -1.0094
180 | 50.5 | -1.0094
180.1 | 50.5 | -1.0094
180.2 | 50.5 | -1.0094
180.3 | 50.5 | -1.0094
180.4 | 50.5 | -1.0094
180.5 | 50.5 | -1.0094
180.6 | 50.5 | -1.0094
180.7 | 50.5 | -1.0094
180.8 | 50.5 | -1.0094
180.9 | 50.5 | -1.0094
181 | 50.5 | -1.0094
181.1 | 50.5 | -1.0094
181.2 | 50.5 | -1.0094
181.3 | 50.5 | -1.0094
181.4 | 50.5 | -1.0094
181.5 | 50.5 | -1.0094
181.6 | 50.5 | -1.0094
181.7 | 50.5 | -1.0094
181.8 | 50.5 | -1.0094
181.9 | 50.5 | -1.0094
182 | 50.5 | -1.0094
182.1 | 50.5 | -1.0094
182.2 | 50.5 | -1.0096
182.3 | 50.5 | -1.0096
182.4 | 50.5 | -1.0096
182.5 | 50.5 | -1.0096
182.6 | 50.5 | -1.0096
182.7 | 50.5 | -1.0096
182.8 | 50.5 | -1.0096
182.9 | 50.5 | -1.0096
183 | 50.5 | -1.0096
183.1 | 50.5 | -1.0096
183.2 | 50.5 | -1.0096
183.3 | 50.5 | -1.0096
183.4 | 50.5 | -1.0096
183.5 | 50.5 | -1.0096
183.6 | 50.5 | -1.0096
183.7 | 50.5 | -1.0096
183.8 | 50.5 | -1.0096
183.9 | 50.5 | -1.0096
184 | 50.5 | -1.0096
184.1 | 50.5 | -1.0096
184.2 | 50.5 | -1.0096
184.3 | 50.5 | -1.0096
184.4 | 50.5 | -1.0096
184.5 | 50.5 | -1.0096
184.6 | 50.5 | -1.0096
184.7 | 50.5 | -1.0096
184.8 | 50.5 | -1.0096
184.9 | 50.5 | -1.0096
185 | 50.5 | -1.0096
185.1 | 50.5 | -1.0096
185.2 | 50.5 | -1.0096
185.3 | 50.5 | -1.0096
185.4 | 50.5 | -1.0096
185.5 | 50.5 | -1.0096
185.6 | 50.5 | -1.0096
185.7 | 50.5 | -1.0094
185.8 | 50.5 | -1.0094
185.9 | 50.5 | -1.0094
186 | 50.5 | -1.0094
186.1 | 50.5 | -1.0094
186.2 | 50.5 | -1.0094
186.3 | 50.5 | -1.0094
186.4 | 50.5 | -1.0094
186.5 | 50.5 | -1.0094
186.6 | 50.5 | -1.0094
186.7 | 50.5 | -1.0094
186.8 | 50.5 | -1.0094
186.9 | 50.5 | -1.0094
187 | 50.5 | -1.0094
187.1 | 50.5 | -1.0094
187.2 | 50.5 | -1.0094
187.3 | 50.5 | -1.0094
187.4 | 50.5 | -1.0094
187.5 | 50.5 | -1.0094
187.6 | 50.5 | -1.0094
187.7 | 50.5 | -1.0094
187.8 | 50.5 | -1.0094
187.9 | 50.5 | -1.0094
188 | 50.5 | -1.0096
188.1 | 50.5 | -1.0096
188.2 | 50.5 | -1.0096
188.3 | 50.5 | -1.0096
188.4 | 50.5 | -1.0096
188.5 | 50.5 | -1.0096
188.6 | 50.5 | -1.0096
188.7 | 50.5 | -1.0096
188.8 | 50.5 | -1.0096
188.9 | 50.5 | -1.0096
189 | 50.5 | -1.0096
189.1 | 50.5 | -1.0096
189.2 | 50.5 | -1.0096
189.3 | 50.5 | -1.0096
189.4 | 50.5 | -1.0096
189.5 | 50.5 | -1.0096
189.6 | 50.5 | -1.0096
189.7 | 50.5 | -1.0096
189.8 | 50.5 | -1.0096
189.9 | 50.5 | -1.0096
190 | 50.5 | -1.0096
190.1 | 50.5 | -1.0096
190.2 | 50.5 | -1.0096
190.3 | 50.5 | -1.0096
190.4 | 50.5 | -1.0096
190.5 | 50.5 | -1.0096
190.6 | 50.5 | -1.0096
190.7 | 50.5 | -1.0096
190.8 | 50.5 | -1.0096
190.9 | 50.5 | -1.0096
191 | 50.5 | -1.0096
191.1 | 50.5 | -1.0096
191.2 | 50.5 | -1.0096
191.3 | 50.5 | -1.0096
191.4 | 50.5 | -1.0096
191.5 | 50.5 | -1.0096
191.6 | 50.5 | -1.0096
191.7 | 50.5 | -1.0096
191.8 | 50.5 | -1.0096
191.9 | 50.5 | -1.0096
192 | 50.5 | -1.0096
192.1 | 50.5 | -1.0096
192.2 | 50.5 | -1.0096
192.3 | 50.5 | -1.0096
192.4 | 50.5 | -1.0096
192.5 | 50.5 | -1.0096
192.6 | 50.5 | -1.0096
192.7 | 50.5 | -1.0096
192.8 | 50.5 | -1.0096
192.9 | 50.5 | -1.0094
193 | 50.5 | -1.0094
193.1 | 50.5 | -1.0094
193.2 | 50.5 | -1.0094
193.3 | 50.5 | -1.0094
193.4 | 50.5 | -1.0094
193.5 | 50.5 | -1.0094
193.6 | 50.5 | -1.0094
193.7 | 50.5 | -1.0094
193.8 | 50.5 | -1.0094
193.9 | 50.5 | -1.0094
194 | 50.5 | -1.0094
194.1 | 50.5 | -1.0094
194.2 | 50.5 | -1.0094
194.3 | 50.5 | -1.0094
194.4 | 50.5 | -1.0094
194.5 | 50.5 | -1.0094
194.6 | 50.5 | -1.0094
194.7 | 50.5 | -1.0094
194.8 | 50.5 | -1.0094
194.9 | 50.5 | -1.0094
195 | 50.5 | -1.0096
195.1 | 50.5 | -1.0096
195.2 | 50.5 | -1.0096
195.3 | 50.5 | -1.0096
195.4 | 50.5 | -1.0096
195.5 | 50.5 | -1.0096
195.6 | 50.5 | -1.0096
195.7 | 50.5 | -1.0096
195.8 | 50.5 | -1.0096
195.9 | 50.5 | -1.0096
196 | 50.5 | -1.0096
196.1 | 50.5 | -1.0096
196.2 | 50.5 | -1.0096
196.3 | 50.5 | -1.0096
196.4 | 50.5 | -1.0096
196.5 | 50.5 | -1.0096
196.6 | 50.5 | -1.0096
196.7 | 50.5 | -1.0096
196.8 | 50.5 | -1.0096
196.9 | 50.5 | -1.0096
197 | 50.5 | -1.0096
197.1 | 50.5 | -1.0096
197.2 | 50.5 | -1.0096
197.3 | 50.5 | -1.0096
197.4 | 50.5 | -1.0096
197.5 | 50.5 | -1.0096
197.6 | 50.5 | -1.0094
197.7 | 50.5 | -1.0094
197.8 | 50.5 | -1.0094
197.9 | 50.5 | -1.0094
198 | 50.5 | -1.0094
198.1 | 50.5 | -1.0094
198.2 | 50.5 | -1.0094
198.3 | 50.5 | -1.0094
198.4 | 50.5 | -1.0094
198.5 | 50.5 | -1.0094
198.6 | 50.5 | -1.0094
198.7 | 50.5 | -1.0094
198.8 | 50.5 | -1.0094
198.9 | 50.5 | -1.0094
199 | 50.5 | -1.0094
199.1 | 50.5 | -1.0094
199.2 | 50.5 | -1.0094
199.3 | 50.5 | -1.0094
199.4 | 50.5 | -1.0094
199.5 | 50.5 | -1.0094
199.6 | 50.5 | -1.0094
199.7 | 50.5 | -1.0094
199.8 | 50.5 | -1.0094
199.9 | 50.5 | -1.0094
200 | 50.5 | -1.0094
200.1 | 50.5 | -1.0094
200.2 | 50.5 | -1.0094
200.3 | 50.5 | -1.0094
200.4 | 50.5 | -1.0094
200.5 | 50.5 | -1.0094
200.6 | 50.5 | -1.0094
200.7 | 50.5 | -1.0094
200.8 | 50.5 | -1.0096
200.9 | 50.5 | -1.0096
201 | 50.5 | -1.0096
201.1 | 50.5 | -1.0096
201.2 | 50.5 | -1.0096
201.3 | 50.5 | -1.0096
201.4 | 50.5 | -1.0096
201.5 | 50.5 | -1.0096
201.6 | 50.5 | -1.0096
201.7 | 50.5 | -1.0096
201.8 | 50.5 | -1.0096
201.9 | 50.5 | -1.0096
202 | 50.5 | -1.0096
202.1 | 50.5 | -1.0096
202.2 | 50.5 | -1.0096
202.3 | 50.5 | -1.0096
202.4 | 50.5 | -1.0096
202.5 | 50.5 | -1.0096
202.6 | 50.5 | -1.0096
202.7 | 50.5 | -1.0096
202.8 | 50.5 | -1.0096
202.9 | 50.5 | -1.0096
203 | 50.5 | -1.0096
203.1 | 50.5 | -1.0096
203.2 | 50.5 | -1.0096
203.3 | 50.5 | -1.0096
203.4 | 50.5 | -1.0096
203.5 | 50.5 | -1.0096
203.6 | 50.5 | -1.0096
203.7 | 50.5 | -1.0096
203.8 | 50.5 | -1.0096
203.9 | 50.5 | -1.0096
204 | 50.5 | -1.0096
204.1 | 50.5 | -1.0096
204.2 | 50.5 | -1.0096
204.3 | 50.5 | -1.0096
204.4 | 50.5 | -1.0096
204.5 | 50.5 | -1.0094
204.6 | 50.5 | -1.0094
204.7 | 50.5 | -1.0094
204.8 | 50.5 | -1.0094
204.9 | 50.5 | -1.0094
205 | 50.5 | -1.0094
205.1 | 50.5 | -1.0094
205.2 | 50.5 | -1.0094
205.3 | 50.5 | -1.0094
205.4 | 50.5 | -1.0094
205.5 | 50.5 | -1.0094
205.6 | 50.5 | -1.0094
205.7 | 50.5 | -1.0094
205.8 | 50.5 | -1.0096
205.9 | 50.5 | -1.0096
206 | 50.5 | -1.0096
206.1 | 50.5 | -1.0096
206.2 | 50.5 | -1.0096
206.3 | 50.5 | -1.0096
206.4 | 50.5 | -1.0096
206.5 | 50.5 | -1.0096
206.6 | 50.5 | -1.0096
206.7 | 50.5 | -1.0096
206.8 | 50.5 | -1.0096
206.9 | 50.5 | -1.0096
207 | 50.5 | -1.0096
207.1 | 50.5 | -1.0096
207.2 | 50.5 | -1.0096
207.3 | 50.5 | -1.0096
207.4 | 50.5 | -1.0096
207.5 | 50.5 | -1.0096
207.6 | 50.5 | -1.0096
207.7 | 50.5 | -1.0096
207.8 | 50.5 | -1.0096
207.9 | 50.5 | -1.0096
208 | 50.5 | -1.0096
208.1 | 50.5 | -1.0096
208.2 | 50.5 | -1.0096
208.3 | 50.5 | -1.0096
208.4 | 50.5 | -1.0096
208.5 | 50.5 | -1.0096
208.6 | 50.5 | -1.0096
208.7 | 50.5 | -1.0096
208.8 | 50.5 | -1.0096
208.9 | 50.5 | -1.0096
209 | 50.5 | -1.0096
209.1 | 50.5 | -1.0096
209.2 | 50.5 | -1.0096
209.3 | 50.5 | -1.0096
209.4 | 50.5 | -1.0096
209.5 | 50.5 | -1.0096
209.6 | 50.5 | -1.0096
209.7 | 50.5 | -1.0096
209.8 | 50.5 | -1.0096
209.9 | 50.5 | -1.0096
210 | 50.5 | -1.0096
210.1 | 50.5 | -1.0096
210.2 | 50.5 | -1.0094
210.3 | 50.5 | -1.0094
210.4 | 50.5 | -1.0094
210.5 | 50.5 | -1.0094
210.6 | 50.5 | -1.0094
210.7 | 50.5 | -1.0094
210.8 | 50.5 | -1.0094
210.9 | 50.5 | -1.0094
211 | 50.5 | -1.0094
211.1 | 50.5 | -1.0094
211.2 | 50.5 | -1.0094
211.3 | 50.5 | -1.0094
211.4 | 50.5 | -1.0094
211.5 | 50.5 | -1.0094
211.6 | 50.5 | -1.0094
211.7 | 50.5 | -1.0094
211.8 | 50.5 | -1.0094
211.9 | 50.5 | -1.0094
212 | 50.5 | -1.0094
212.1 | 50.5 | -1.0094
212.2 | 50.5 | -1.0094
212.3 | 50.5 | -1.0094
212.4 | 50.5 | -1.0094
212.5 | 50.5 | -1.0094
212.6 | 50.5 | -1.0096
212.7 | 50.5 | -1.0096
212.8 | 50.5 | -1.0096
212.9 | 50.5 | -1.0096
213 | 50.5 | -1.0096
213.1 | 50.5 | -1.0096
213.2 | 50.5 | -1.0096
213.3 | 50.5 | -1.0096
213.4 | 50.5 | -1.0096
213.5 | 50.5 | -1.0096
213.6 | 50.5 | -1.0096
213.7 | 50.5 | -1.0096
213.8 | 50.5 | -1.0096
213.9 | 50.5 | -1.0096
214 | 50.5 | -1.0096
214.1 | 50.5 | -1.0096
214.2 | 50.5 | -1.0096
214.3 | 50.5 | -1.0096
214.4 | 50.5 | -1.0096
214.5 | 50.5 | -1.0096
214.6 | 50.5 | -1.0096
214.7 | 50.5 | -1.0096
214.8 | 50.5 | -1.0098
214.9 | 50.5 | -1.0098
215 | 50.5 | -1.0098
215.1 | 50.5 | -1.0098
215.2 | 50.5 | -1.0098
215.3 | 50.5 | -1.0098
215.4 | 50.5 | -1.0098
215.5 | 50.5 | -1.0098
215.6 | 50.5 | -1.0098
215.7 | 50.5 | -1.0098
215.8 | 50.5 | -1.0098
215.9 | 50.5 | -1.0098
216 | 50.5 | -1.0098
216.1 | 50.5 | -1.0096
216.2 | 50.5 | -1.0096
216.3 | 50.5 | -1.0096
216.4 | 50.5 | -1.0096
216.5 | 50.5 | -1.0096
216.6 | 50.5 | -1.0096
216.7 | 50.5 | -1.0096
216.8 | 50.5 | -1.0096
216.9 | 50.5 | -1.0096
217 | 50.5 | -1.0096
217.1 | 50.5 | -1.0096
217.2 | 50.5 | -1.0096
217.3 | 50.5 | -1.0096
217.4 | 50.5 | -1.0096
217.5 | 50.5 | -1.0096
217.6 | 50.5 | -1.0096
217.7 | 50.5 | -1.0096
217.8 | 50.5 | -1.0096
217.9 | 50.5 | -1.0096
218 | 50.5 | -1.0096
218.1 | 50.5 | -1.0096
218.2 | 50.5 | -1.0096
218.3 | 50.5 | -1.0096
218.4 | 50.5 | -1.0096
218.5 | 50.5 | -1.0094
218.6 | 50.5 | -1.0094
218.7 | 50.5 | -1.0094
218.8 | 50.5 | -1.0094
218.9 | 50.5 | -1.0094
219 | 50.5 | -1.0094
219.1 | 50.5 | -1.0094
219.2 | 50.5 | -1.0094
219.3 | 50.5 | -1.0094
219.4 | 50.5 | -1.0094
219.5 | 50.5 | -1.0094
219.6 | 50.5 | -1.0096
219.7 | 50.5 | -1.0096
219.8 | 50.5 | -1.0096
219.9 | 50.5 | -1.0096
220 | 50.5 | -1.0096
220.1 | 50.5 | -1.0096
220.2 | 50.5 | -1.0096
220.3 | 50.5 | -1.0096
220.4 | 50.5 | -1.0096
220.5 | 50.5 | -1.0096
220.6 | 50.5 | -1.0096
220.7 | 50.5 | -1.0096
220.8 | 50.5 | -1.0096
220.9 | 50.5 | -1.0096
221 | 50.5 | -1.0096
221.1 | 50.5 | -1.0096
221.2 | 50.5 | -1.0096
221.3 | 50.5 | -1.0096
221.4 | 50.5 | -1.0096
221.5 | 50.5 | -1.0096
221.6 | 50.5 | -1.0096
221.7 | 50.5 | -1.0096
221.8 | 50.5 | -1.0096
221.9 | 50.5 | -1.0096
222 | 50.5 | -1.0096
222.1 | 50.5 | -1.0096
222.2 | 50.5 | -1.0096
222.3 | 50.5 | -1.0096
222.4 | 50.5 | -1.0096
222.5 | 50.5 | -1.0096
222.6 | 50.5 | -1.0096
222.7 | 50.5 | -1.0096
222.8 | 50.5 | -1.0096
222.9 | 50.5 | -1.0096
223 | 50.5 | -1.0096
223.1 | 50.5 | -1.0096
223.2 | 50.5 | -1.0096
223.3 | 50.5 | -1.0096
223.4 | 50.5 | -1.0096
223.5 | 50.5 | -1.0096
223.6 | 50.5 | -1.0096
223.7 | 50.5 | -1.0096
223.8 | 50.5 | -1.0096
223.9 | 50.5 | -1.0096
224 | 50.5 | -1.0096
224.1 | 50.5 | -1.0096
224.2 | 50.5 | -1.0096
224.3 | 50.5 | -1.0096
224.4 | 50.5 | -1.0096
224.5 | 50.5 | -1.0096
224.6 | 50.5 | -1.0096
224.7 | 50.5 | -1.0096
224.8 | 50.5 | -1.0096
224.9 | 50.5 | -1.0096
225 | 50.5 | -1.0096
225.1 | 50.5 | -1.0096
225.2 | 50.5 | -1.0096
225.3 | 50.5 | -1.0096
225.4 | 50.5 | -1.0096
225.5 | 50.5 | -1.0096
225.6 | 50.5 | -1.0096
225.7 | 50.5 | -1.0096
225.8 | 50.5 | -1.0096
225.9 | 50.5 | -1.0096
226 | 50.5 | -1.0096
226.1 | 50.5 | -1.0096
226.2 | 50.5 | -1.0096
226.3 | 50.5 | -1.0096
226.4 | 50.5 | -1.0096
226.5 | 50.5 | -1.0096
226.6 | 50.5 | -1.0096
226.7 | 50.5 | -1.0096
226.8 | 50.5 | -1.0096
226.9 | 50.5 | -1.0094
227 | 50.5 | -1.0094
227.1 | 50.5 | -1.0094
227.2 | 50.5 | -1.0094
227.3 | 50.5 | -1.0094
227.4 | 50.5 | -1.0094
227.5 | 50.5 | -1.0094
227.6 | 50.5 | -1.0094
227.7 | 50.5 | -1.0094
227.8 | 50.5 | -1.0094
227.9 | 50.5 | -1.0094
228 | 50.5 | -1.0094
228.1 | 50.5 | -1.0096
228.2 | 50.5 | -1.0096
228.3 | 50.5 | -1.0096
228.4 | 50.5 | -1.0096
228.5 | 50.5 | -1.0096
228.6 | 50.5 | -1.0096
228.7 | 50.5 | -1.0096
228.8 | 50.5 | -1.0096
228.9 | 50.5 | -1.0096
229 | 50.5 | -1.0096
229.1 | 50.5 | -1.0096
229.2 | 50.5 | -1.0096
229.3 | 50.5 | -1.0096
229.4 | 50.5 | -1.0096
229.5 | 50.5 | -1.0096
229.6 | 50.5 | -1.0096
229.7 | 50.5 | -1.0096
229.8 | 50.5 | -1.0096
229.9 | 50.5 | -1.0096
230 | 50.5 | -1.0096
230.1 | 50.5 | -1.0096
230.2 | 50.5 | -1.0096
230.3 | 50.5 | -1.0096
230.4 | 50.5 | -1.0096
230.5 | 50.5 | -1.0096
230.6 | 50.5 | -1.0096
230.7 | 50.5 | -1.0096
230.8 | 50.5 | -1.0096
230.9 | 50.5 | -1.0096
231 | 50.5 | -1.0096
231.1 | 50.5 | -1.0096
231.2 | 50.5 | -1.0096
231.3 | 50.5 | -1.0096
231.4 | 50.5 | -1.0096
231.5 | 50.5 | -1.0096
231.6 | 50.5 | -1.0096
231.7 | 50.5 | -1.0096
231.8 | 50.5 | -1.0096
231.9 | 50.5 | -1.0096
232 | 50.5 | -1.0096
232.1 | 50.5 | -1.0096
232.2 | 50.5 | -1.0096
232.3 | 50.5 | -1.0096
232.4 | 50.5 | -1.0096
232.5 | 50.5 | -1.0096
232.6 | 50.5 | -1.0096
232.7 | 50.5 | -1.0096
232.8 | 50.5 | -1.0096
232.9 | 50.5 | -1.0096
233 | 50.5 | -1.0096
233.1 | 50.5 | -1.0096
233.2 | 50.5 | -1.0096
233.3 | 50.5 | -1.0096
233.4 | 50.5 | -1.0096
233.5 | 50.5 | -1.0096
233.6 | 50.5 | -1.0096
233.7 | 50.5 | -1.0096
233.8 | 50.5 | -1.0096
233.9 | 50.5 | -1.0096
234 | 50.5 | -1.0096
234.1 | 50.5 | -1.0096
234.2 | 50.5 | -1.0096
234.3 | 50.5 | -1.0096
234.4 | 50.5 | -1.0096
234.5 | 50.5 | -1.0096
234.6 | 50.5 | -1.0096
234.7 | 50.5 | -1.0096
234.8 | 50.5 | -1.0096
234.9 | 50.5 | -1.0096
235 | 50.5 | -1.0096
235.1 | 50.5 | -1.0096
235.2 | 50.5 | -1.0096
235.3 | 50.5 | -1.0096
235.4 | 50.5 | -1.0096
235.5 | 50.5 | -1.0096
235.6 | 50.5 | -1.0096
235.7 | 50.5 | -1.0096
235.8 | 50.5 | -1.0096
235.9 | 50.5 | -1.0096
236 | 50.5 | -1.0096
236.1 | 50.5 | -1.0096
236.2 | 50.5 | -1.0096
236.3 | 50.5 | -1.0096
236.4 | 50.5 | -1.0096
236.5 | 50.5 | -1.0096
236.6 | 50.5 | -1.0096
236.7 | 50.5 | -1.0096
236.8 | 50.5 | -1.0096
236.9 | 50.5 | -1.0096
237 | 50.5 | -1.0096
237.1 | 50.5 | -1.0096
237.2 | 50.5 | -1.0096
237.3 | 50.5 | -1.0096
237.4 | 50.5 | -1.0096
237.5 | 50.5 | -1.0096
237.6 | 50.5 | -1.0096
237.7 | 50.5 | -1.0096
237.8 | 50.5 | -1.0096
237.9 | 50.5 | -1.0096
238 | 50.5 | -1.0096
238.1 | 50.5 | -1.0096
238.2 | 50.5 | -1.0096
238.3 | 50.5 | -1.0096
238.4 | 50.5 | -1.0096
238.5 | 50.5 | -1.0096
238.6 | 50.5 | -1.0096
238.7 | 50.5 | -1.0096
238.8 | 50.5 | -1.0096
238.9 | 50.5 | -1.0096
239 | 50.5 | -1.0096
239.1 | 50.5 | -1.0096
239.2 | 50.5 | -1.0096
239.3 | 50.5 | -1.0096
239.4 | 50.5 | -1.0096
239.5 | 50.5 | -1.0096
239.6 | 50.5 | -1.0096
239.7 | 50.5 | -1.0094
239.8 | 50.5 | -1.0094
239.9 | 50.5 | -1.0094
240 | 50.5 | -1.0094
240.1 | 50.5 | -1.0094
240.2 | 50.5 | -1.0094
240.3 | 50.5 | -1.0094
240.4 | 50.5 | -1.0094
240.5 | 50.5 | -1.0094
240.6 | 50.5 | -1.0094
240.7 | 50.5 | -1.0094
240.8 | 50.5 | -1.0094
240.9 | 50.5 | -1.0094
241 | 50.5 | -1.0094
241.1 | 50.5 | -1.0094
241.2 | 50.5 | -1.0094
241.3 | 50.5 | -1.0094
241.4 | 50.5 | -1.0094
241.5 | 50.5 | -1.0094
241.6 | 50.5 | -1.0094
241.7 | 50.5 | -1.0094
241.8 | 50.5 | -1.0094
241.9 | 50.5 | -1.0094
242 | 50.5 | -1.0096
242.1 | 50.5 | -1.0096
242.2 | 50.5 | -1.0096
242.3 | 50.5 | -1.0096
242.4 | 50.5 | -1.0096
242.5 | 50.5 | -1.0096
242.6 | 50.5 | -1.0096
242.7 | 50.5 | -1.0096
242.8 | 50.5 | -1.0096
242.9 | 50.5 | -1.0096
243 | 50.5 | -1.0096
243.1 | 50.5 | -1.0096
243.2 | 50.5 | -1.0096
243.3 | 50.5 | -1.0096
243.4 | 50.5 | -1.0096
243.5 | 50.5 | -1.0096
243.6 | 50.5 | -1.0096
243.7 | 50.5 | -1.0096
243.8 | 50.5 | -1.0096
243.9 | 50.5 | -1.0096
244 | 50.5 | -1.0096
244.1 | 50.5 | -1.0096
244.2 | 50.5 | -1.0096
244.3 | 50.5 | -1.0096
244.4 | 50.5 | -1.0096
244.5 | 50.5 | -1.0096
244.6 | 50.5 | -1.0096
244.7 | 50.5 | -1.0096
244.8 | 50.5 | -1.0096
244.9 | 50.5 | -1.0096
245 | 50.5 | -1.0096
245.1 | 50.5 | -1.0096
245.2 | 50.5 | -1.0096
245.3 | 50.5 | -1.0096
245.4 | 50.5 | -1.0096
245.5 | 50.5 | -1.0096
245.6 | 50.5 | -1.0096
245.7 | 50.5 | -1.0096
245.8 | 50.5 | -1.0096
245.9 | 50.5 | -1.0096
246 | 50.5 | -1.0096
246.1 | 50.5 | -1.0096
246.2 | 50.5 | -1.0096
246.3 | 50.5 | -1.0096
246.4 | 50.5 | -1.0096
246.5 | 50.5 | -1.0096
246.6 | 50.5 | -1.0096
246.7 | 50.5 | -1.0096
246.8 | 50.5 | -1.0096
246.9 | 50.5 | -1.0096
247 | 50.5 | -1.0096
247.1 | 50.5 | -1.0096
247.2 | 50.5 | -1.0096
247.3 | 50.5 | -1.0096
247.4 | 50.5 | -1.0096
247.5 | 50.5 | -1.0096
247.6 | 50.5 | -1.0096
247.7 | 50.5 | -1.0096
247.8 | 50.5 | -1.0096
247.9 | 50.5 | -1.0096
248 | 50.5 | -1.0096
248.1 | 50.5 | -1.0096
248.2 | 50.5 | -1.0096
248.3 | 50.5 | -1.0096
248.4 | 50.5 | -1.0096
248.5 | 50.5 | -1.0096
248.6 | 50.5 | -1.0096
248.7 | 50.5 | -1.0096
248.8 | 50.5 | -1.0096
248.9 | 50.5 | -1.0096
249 | 50.5 | -1.0096
249.1 | 50.5 | -1.0096
249.2 | 50.5 | -1.0096
249.3 | 50.5 | -1.0096
249.4 | 50.5 | -1.0096
249.5 | 50.5 | -1.0096
249.6 | 50.5 | -1.0096
249.7 | 50.5 | -1.0096
249.8 | 50.5 | -1.0096
249.9 | 50.5 | -1.0096
250 | 50.5 | -1.0096
250.1 | 50.5 | -1.0096
250.2 | 50.5 | -1.0096
250.3 | 50.5 | -1.0096
250.4 | 50.5 | -1.0096
250.5 | 50.5 | -1.0096
250.6 | 50.5 | -1.0096
250.7 | 50.5 | -1.0096
250.8 | 50.5 | -1.0096
250.9 | 50.5 | -1.0096
251 | 50.5 | -1.0096
251.1 | 50.5 | -1.0096
251.2 | 50.5 | -1.0096
251.3 | 50.5 | -1.0096
251.4 | 50.5 | -1.0096
251.5 | 50.5 | -1.0096
251.6 | 50.5 | -1.0096
251.7 | 50.5 | -1.0096
251.8 | 50.5 | -1.0096
251.9 | 50.5 | -1.0096
252 | 50.5 | -1.0096
252.1 | 50.5 | -1.0096
252.2 | 50.5 | -1.0096
252.3 | 50.5 | -1.0096
252.4 | 50.5 | -1.0096
252.5 | 50.5 | -1.0096
252.6 | 50.5 | -1.0096
252.7 | 50.5 | -1.0096
252.8 | 50.5 | -1.0096
252.9 | 50.5 | -1.0096
253 | 50.5 | -1.0096
253.1 | 50.5 | -1.0096
253.2 | 50.5 | -1.0096
253.3 | 50.5 | -1.0096
253.4 | 50.5 | -1.0096
253.5 | 50.5 | -1.0096
253.6 | 50.5 | -1.0096
253.7 | 50.5 | -1.0096
253.8 | 50.5 | -1.0096
253.9 | 50.5 | -1.0096
254 | 50.5 | -1.0096
254.1 | 50.5 | -1.0096
254.2 | 50.5 | -1.0096
254.3 | 50.5 | -1.0096
254.4 | 50.5 | -1.0096
254.5 | 50.5 | -1.0096
254.6 | 50.5 | -1.0096
254.7 | 50.5 | -1.0096
254.8 | 50.5 | -1.0096
254.9 | 50.5 | -1.0096
255 | 50.5 | -1.0096
255.1 | 50.5 | -1.0096
255.2 | 50.5 | -1.0096
255.3 | 50.5 | -1.0096
255.4 | 50.5 | -1.0096
255.5 | 50.5 | -1.0096
255.6 | 50.5 | -1.0096
255.7 | 50.5 | -1.0096
255.8 | 50.5 | -1.0096
255.9 | 50.5 | -1.0096
256 | 50.5 | -1.0096
256.1 | 50.5 | -1.0096
256.2 | 50.5 | -1.0096
256.3 | 50.5 | -1.0096
256.4 | 50.5 | -1.0096
256.5 | 50.5 | -1.0096
256.6 | 50.5 | -1.0096
256.7 | 50.5 | -1.0096
256.8 | 50.5 | -1.0096
256.9 | 50.5 | -1.0096
257 | 50.5 | -1.0096
257.1 | 50.5 | -1.0096
257.2 | 50.5 | -1.0096
257.3 | 50.5 | -1.0096
257.4 | 50.5 | -1.0096
257.5 | 50.5 | -1.0096
257.6 | 50.5 | -1.0096
257.7 | 50.5 | -1.0096
257.8 | 50.5 | -1.0096
257.9 | 50.5 | -1.0096
258 | 50.5 | -1.0096
258.1 | 50.5 | -1.0096
258.2 | 50.5 | -1.0096
258.3 | 50.5 | -1.0096
258.4 | 50.5 | -1.0094
258.5 | 50.5 | -1.0094
258.6 | 50.5 | -1.0094
258.7 | 50.5 | -1.0094
258.8 | 50.5 | -1.0094
258.9 | 50.5 | -1.0094
259 | 50.5 | -1.0094
259.1 | 50.5 | -1.0094
259.2 | 50.5 | -1.0094
259.3 | 50.5 | -1.0094
259.4 | 50.5 | -1.0094
259.5 | 50.5 | -1.0094
259.6 | 50.5 | -1.0094
259.7 | 50.5 | -1.0094
259.8 | 50.5 | -1.0094
259.9 | 50.5 | -1.0094
260 | 50.5 | -1.0094
260.1 | 50.5 | -1.0094
260.2 | 50.5 | -1.0094
260.3 | 50.5 | -1.0094
260.4 | 50.5 | -1.0094
260.5 | 50.5 | -1.0094
260.6 | 50.5 | -1.0094
260.7 | 50.5 | -1.0094
260.8 | 50.5 | -1.0096
260.9 | 50.5 | -1.0096
261 | 50.5 | -1.0096
261.1 | 50.5 | -1.0096
261.2 | 50.5 | -1.0096
261.3 | 50.5 | -1.0096
261.4 | 50.5 | -1.0096
261.5 | 50.5 | -1.0096
261.6 | 50.5 | -1.0096
261.7 | 50.5 | -1.0096
261.8 | 50.5 | -1.0096
261.9 | 50.5 | -1.0096
262 | 50.5 | -1.0096
262.1 | 50.5 | -1.0096
262.2 | 50.5 | -1.0096
262.3 | 50.5 | -1.0096
262.4 | 50.5 | -1.0096
262.5 | 50.5 | -1.0096
262.6 | 50.5 | -1.0096
262.7 | 50.5 | -1.0096
262.8 | 50.5 | -1.0096
262.9 | 50.5 | -1.0096
263 | 50.5 | -1.0096
263.1 | 50.5 | -1.0098
263.2 | 50.5 | -1.0098
263.3 | 50.5 | -1.0098
263.4 | 50.5 | -1.0098
263.5 | 50.5 | -1.0098
263.6 | 50.5 | -1.0098
263.7 | 50.5 | -1.0098
263.8 | 50.5 | -1.0098
263.9 | 50.5 | -1.0098
264 | 50.5 | -1.0098
264.1 | 50.5 | -1.0098
264.2 | 50.5 | -1.0098
264.3 | 50.5 | -1.0098
264.4 | 50.5 | -1.0098
264.5 | 50.5 | -1.0098
264.6 | 50.5 | -1.0098
264.7 | 50.5 | -1.0098
264.8 | 50.5 | -1.0098
264.9 | 50.5 | -1.0098
265 | 50.5 | -1.0098
265.1 | 50.5 | -1.0098
265.2 | 50.5 | -1.0098
265.3 | 50.5 | -1.0098
265.4 | 50.5 | -1.0096
265.5 | 50.5 | -1.0096
265.6 | 50.5 | -1.0096
265.7 | 50.5 | -1.0096
265.8 | 50.5 | -1.0096
265.9 | 50.5 | -1.0096
266 | 50.5 | -1.0096
266.1 | 50.5 | -1.0096
266.2 | 50.5 | -1.0096
266.3 | 50.5 | -1.0096
266.4 | 50.5 | -1.0096
266.5 | 50.5 | -1.0096
266.6 | 50.5 | -1.0096
266.7 | 50.5 | -1.0096
266.8 | 50.5 | -1.0096
266.9 | 50.5 | -1.0096
267 | 50.5 | -1.0096
267.1 | 50.5 | -1.0096
267.2 | 50.5 | -1.0096
267.3 | 50.5 | -1.0096
267.4 | 50.5 | -1.0096
267.5 | 50.5 | -1.0096
267.6 | 50.5 | -1.0096
267.7 | 50.5 | -1.0096
267.8 | 50.5 | -1.0096
267.9 | 50.5 | -1.0096
268 | 50.5 | -1.0096
268.1 | 50.5 | -1.0096
268.2 | 50.5 | -1.0096
268.3 | 50.5 | -1.0096
268.4 | 50.5 | -1.0096
268.5 | 50.5 | -1.0096
268.6 | 50.5 | -1.0096
268.7 | 50.5 | -1.0096
268.8 | 50.5 | -1.0096
268.9 | 50.5 | -1.0096
269 | 50.5 | -1.0096
269.1 | 50.5 | -1.0096
269.2 | 50.5 | -1.0096
269.3 | 50.5 | -1.0096
269.4 | 50.5 | -1.0096
269.5 | 50.5 | -1.0096
269.6 | 50.5 | -1.0096
269.7 | 50.5 | -1.0096
269.8 | 50.5 | -1.0096
269.9 | 50.5 | -1.0096
270 | 50.5 | -1.0096
270.1 | 50.5 | -1.0096
270.2 | 50.5 | -1.0096
270.3 | 50.5 | -1.0096
270.4 | 50.5 | -1.0096
270.5 | 50.5 | -1.0096
270.6 | 50.5 | -1.0096
270.7 | 50.5 | -1.0096
270.8 | 50.5 | -1.0096
270.9 | 50.5 | -1.0096
271 | 50.5 | -1.0096
271.1 | 50.5 | -1.0096
271.2 | 50.5 | -1.0096
271.3 | 50.5 | -1.0096
271.4 | 50.5 | -1.0096
271.5 | 50.5 | -1.0096
271.6 | 50.5 | -1.0096
271.7 | 50.5 | -1.0096
271.8 | 50.5 | -1.0096
271.9 | 50.5 | -1.0096
272 | 50.5 | -1.0096
272.1 | 50.5 | -1.0096
272.2 | 50.5 | -1.0096
272.3 | 50.5 | -1.0096
272.4 | 50.5 | -1.0096
272.5 | 50.5 | -1.0096
272.6 | 50.5 | -1.0096
272.7 | 50.5 | -1.0096
272.8 | 50.5 | -1.0096
272.9 | 50.5 | -1.0096
273 | 50.5 | -1.0096
273.1 | 50.5 | -1.0096
273.2 | 50.5 | -1.0096
273.3 | 50.5 | -1.0096
273.4 | 50.5 | -1.0096
273.5 | 50.5 | -1.0096
273.6 | 50.5 | -1.0096
273.7 | 50.5 | -1.0096
273.8 | 50.5 | -1.0096
273.9 | 50.5 | -1.0096
274 | 50.5 | -1.0096
274.1 | 50.5 | -1.0096
274.2 | 50.5 | -1.0096
274.3 | 50.5 | -1.0096
274.4 | 50.5 | -1.0096
274.5 | 50.5 | -1.0096
274.6 | 50.5 | -1.0096
274.7 | 50.5 | -1.0096
274.8 | 50.5 | -1.0096
274.9 | 50.5 | -1.0096
275 | 50.5 | -1.0096
275.1 | 50.5 | -1.0096
275.2 | 50.5 | -1.0096
275.3 | 50.5 | -1.0096
275.4 | 50.5 | -1.0096
275.5 | 50.5 | -1.0096
275.6 | 50.5 | -1.0096
275.7 | 50.5 | -1.0096
275.8 | 50.5 | -1.0096
275.9 | 50.5 | -1.0096
276 | 50.5 | -1.0096
276.1 | 50.5 | -1.0096
276.2 | 50.5 | -1.0096
276.3 | 50.5 | -1.0096
276.4 | 50.5 | -1.0096
276.5 | 50.5 | -1.0096
276.6 | 50.5 | -1.0096
276.7 | 50.5 | -1.0096
276.8 | 50.5 | -1.0096
276.9 | 50.5 | -1.0096
277 | 50.5 | -1.0096
277.1 | 50.5 | -1.0096
277.2 | 50.5 | -1.0096
277.3 | 50.5 | -1.0096
277.4 | 50.5 | -1.0096
277.5 | 50.5 | -1.0096
277.6 | 50.5 | -1.0096
277.7 | 50.5 | -1.0096
277.8 | 50.5 | -1.0096
277.9 | 50.5 | -1.0096
278 | 50.5 | -1.0096
278.1 | 50.5 | -1.0096
278.2 | 50.5 | -1.0096
278.3 | 50.5 | -1.0096
278.4 | 50.5 | -1.0096
278.5 | 50.5 | -1.0096
278.6 | 50.5 | -1.0096
278.7 | 50.5 | -1.0096
278.8 | 50.5 | -1.0096
278.9 | 50.5 | -1.0096
279 | 50.5 | -1.0096
279.1 | 50.5 | -1.0096
279.2 | 50.5 | -1.0096
279.3 | 50.5 | -1.0096
279.4 | 50.5 | -1.0096
279.5 | 50.5 | -1.0096
279.6 | 50.5 | -1.0096
279.7 | 50.5 | -1.0096
279.8 | 50.5 | -1.0096
279.9 | 50.5 | -1.0096
280 | 50.5 | -1.0096
280.1 | 50.5 | -1.0096
280.2 | 50.5 | -1.0096
280.3 | 50.5 | -1.0096
280.4 | 50.5 | -1.0096
280.5 | 50.5 | -1.0096
280.6 | 50.5 | -1.0096
280.7 | 50.5 | -1.0096
280.8 | 50.5 | -1.0096
280.9 | 50.5 | -1.0096
281 | 50.5 | -1.0096
281.1 | 50.5 | -1.0096
281.2 | 50.5 | -1.0096
281.3 | 50.5 | -1.0096
281.4 | 50.5 | -1.0096
281.5 | 50.5 | -1.0096
281.6 | 50.5 | -1.0096
281.7 | 50.5 | -1.0096
281.8 | 50.5 | -1.0096
281.9 | 50.5 | -1.0096
282 | 50.5 | -1.0096
282.1 | 50.5 | -1.0096
282.2 | 50.5 | -1.0096
282.3 | 50.5 | -1.0096
282.4 | 50.5 | -1.0096
282.5 | 50.5 | -1.0096
282.6 | 50.5 | -1.0096
282.7 | 50.5 | -1.0096
282.8 | 50.5 | -1.0096
282.9 | 50.5 | -1.0096
283 | 50.5 | -1.0096
283.1 | 50.5 | -1.0096
283.2 | 50.5 | -1.0096
283.3 | 50.5 | -1.0096
283.4 | 50.5 | -1.0096
283.5 | 50.5 | -1.0096
283.6 | 50.5 | -1.0096
283.7 | 50.5 | -1.0096
283.8 | 50.5 | -1.0096
283.9 | 50.5 | -1.0096
284 | 50.5 | -1.0096
284.1 | 50.5 | -1.0096
284.2 | 50.5 | -1.0096
284.3 | 50.5 | -1.0096
284.4 | 50.5 | -1.0096
284.5 | 50.5 | -1.0096
284.6 | 50.5 | -1.0096
284.7 | 50.5 | -1.0096
284.8 | 50.5 | -1.0096
284.9 | 50.5 | -1.0096
285 | 50.5 | -1.0096
285.1 | 50.5 | -1.0096
285.2 | 50.5 | -1.0096
285.3 | 50.5 | -1.0096
285.4 | 50.5 | -1.0096
285.5 | 50.5 | -1.0096
285.6 | 50.5 | -1.0096
285.7 | 50.5 | -1.0096
285.8 | 50.5 | -1.0096
285.9 | 50.5 | -1.0096
286 | 50.5 | -1.0096
286.1 | 50.5 | -1.0096
286.2 | 50.5 | -1.0096
286.3 | 50.5 | -1.0096
286.4 | 50.5 | -1.0096
286.5 | 50.5 | -1.0096
286.6 | 50.5 | -1.0096
286.7 | 50.5 | -1.0096
286.8 | 50.5 | -1.0096
286.9 | 50.5 | -1.0096
287 | 50.5 | -1.0096
287.1 | 50.5 | -1.0096
287.2 | 50.5 | -1.0096
287.3 | 50.5 | -1.0096
287.4 | 50.5 | -1.0096
287.5 | 50.5 | -1.0096
287.6 | 50.5 | -1.0096
287.7 | 50.5 | -1.0096
287.8 | 50.5 | -1.0096
287.9 | 50.5 | -1.0096
288 | 50.5 | -1.0096
288.1 | 50.5 | -1.0096
288.2 | 50.5 | -1.0096
288.3 | 50.5 | -1.0096
288.4 | 50.5 | -1.0096
288.5 | 50.5 | -1.0096
288.6 | 50.5 | -1.0096
288.7 | 50.5 | -1.0096
288.8 | 50.5 | -1.0096
288.9 | 50.5 | -1.0096
289 | 50.5 | -1.0096
289.1 | 50.5 | -1.0096
289.2 | 50.5 | -1.0096
289.3 | 50.5 | -1.0096
289.4 | 50.5 | -1.0096
289.5 | 50.5 | -1.0096
289.6 | 50.5 | -1.0096
289.7 | 50.5 | -1.0096
289.8 | 50.5 | -1.0096
289.9 | 50.5 | -1.0096
290 | 50.5 | -1.0096
290.1 | 50.5 | -1.0096
290.2 | 50.5 | -1.0096
290.3 | 50.5 | -1.0096
290.4 | 50.5 | -1.0096
290.5 | 50.5 | -1.0096
290.6 | 50.5 | -1.0096
290.7 | 50.5 | -1.0096
290.8 | 50.5 | -1.0096
290.9 | 50.5 | -1.0096
291 | 50.5 | -1.0096
291.1 | 50.5 | -1.0096
291.2 | 50.5 | -1.0096
291.3 | 50.5 | -1.0096
291.4 | 50.5 | -1.0096
291.5 | 50.5 | -1.0096
291.6 | 50.5 | -1.0096
291.7 | 50.5 | -1.0096
291.8 | 50.5 | -1.0096
291.9 | 50.5 | -1.0096
292 | 50.5 | -1.0096
292.1 | 50.5 | -1.0096
292.2 | 50.5 | -1.0096
292.3 | 50.5 | -1.0096
292.4 | 50.5 | -1.0096
292.5 | 50.5 | -1.0096
292.6 | 50.5 | -1.0096
292.7 | 50.5 | -1.0096
292.8 | 50.5 | -1.0096
292.9 | 50.5 | -1.0096
293 | 50.5 | -1.0096
293.1 | 50.5 | -1.0096
293.2 | 50.5 | -1.0096
293.3 | 50.5 | -1.0096
293.4 | 50.5 | -1.0096
293.5 | 50.5 | -1.0096
293.6 | 50.5 | -1.0096
293.7 | 50.5 | -1.0096
293.8 | 50.5 | -1.0096
293.9 | 50.5 | -1.0096
294 | 50.5 | -1.0096
294.1 | 50.5 | -1.0096
294.2 | 50.5 | -1.0096
294.3 | 50.5 | -1.0096
294.4 | 50.5 | -1.0096
294.5 | 50.5 | -1.0096
294.6 | 50.5 | -1.0096
294.7 | 50.5 | -1.0096
294.8 | 50.5 | -1.0096
294.9 | 50.5 | -1.0096
295 | 50.5 | -1.0096
295.1 | 50.5 | -1.0096
295.2 | 50.5 | -1.0096
295.3 | 50.5 | -1.0096
295.4 | 50.5 | -1.0096
295.5 | 50.5 | -1.0096
295.6 | 50.5 | -1.0096
295.7 | 50.5 | -1.0096
295.8 | 50.5 | -1.0096
295.9 | 50.5 | -1.0096
296 | 50.5 | -1.0096
296.1 | 50.5 | -1.0096
296.2 | 50.5 | -1.0096
296.3 | 50.5 | -1.0096
296.4 | 50.5 | -1.0096
296.5 | 50.5 | -1.0096
296.6 | 50.5 | -1.0096
296.7 | 50.5 | -1.0096
296.8 | 50.5 | -1.0096
296.9 | 50.5 | -1.0096
297 | 50.5 | -1.0096
297.1 | 50.5 | -1.0096
297.2 | 50.5 | -1.0096
297.3 | 50.5 | -1.0096
297.4 | 50.5 | -1.0096
297.5 | 50.5 | -1.0096
297.6 | 50.5 | -1.0096
297.7 | 50.5 | -1.0096
297.8 | 50.5 | -1.0096
297.9 | 50.5 | -1.0096
298 | 50.5 | -1.0096
298.1 | 50.5 | -1.0096
298.2 | 50.5 | -1.0096
298.3 | 50.5 | -1.0096
298.4 | 50.5 | -1.0096
298.5 | 50.5 | -1.0096
298.6 | 50.5 | -1.0096
298.7 | 50.5 | -1.0096
298.8 | 50.5 | -1.0096
298.9 | 50.5 | -1.0096
299 | 50.5 | -1.0096
299.1 | 50.5 | -1.0096
299.2 | 50.5 | -1.0096
299.3 | 50.5 | -1.0096
299.4 | 50.5 | -1.0096
299.5 | 50.5 | -1.0096
299.6 | 50.5 | -1.0096
299.7 | 50.5 | -1.0096
299.8 | 50.5 | -1.0096
299.9 | 50.5 | -1.0096
300 | 50.5 | -1.0096
300.1 | 50.5 | -1.0096
300.2 | 50.5 | -1.0096
300.3 | 50.5 | -1.0096
300.4 | 50.5 | -1.0096
300.5 | 50.5 | -1.0096
300.6 | 50.5 | -1.0096
300.7 | 50.5 | -1.0096
300.8 | 50.5 | -1.0096
300.9 | 50.5 | -1.0096
301 | 50.5 | -1.0096
301.1 | 50.5 | -1.0096
301.2 | 50.5 | -1.0096
301.3 | 50.5 | -1.0096
301.4 | 50.5 | -1.0096
301.5 | 50.5 | -1.0096
301.6 | 50.5 | -1.0096
301.7 | 50.5 | -1.0096
301.8 | 50.5 | -1.0096
301.9 | 50.5 | -1.0096
302 | 50.5 | -1.0096
302.1 | 50.5 | -1.0096
302.2 | 50.5 | -1.0096
302.3 | 50.5 | -1.0096
302.4 | 50.5 | -1.0096
302.5 | 50.5 | -1.0096
302.6 | 50.5 | -1.0096
302.7 | 50.5 | -1.0096
302.8 | 50.5 | -1.0096
302.9 | 50.5 | -1.0096
303 | 50.5 | -1.0096
303.1 | 50.5 | -1.0096
303.2 | 50.5 | -1.0096
303.3 | 50.5 | -1.0096
303.4 | 50.5 | -1.0096
303.5 | 50.5 | -1.0096
303.6 | 50.5 | -1.0096
303.7 | 50.5 | -1.0096
303.8 | 50.5 | -1.0096
303.9 | 50.5 | -1.0096
304 | 50.5 | -1.0096
304.1 | 50.5 | -1.0096
304.2 | 50.5 | -1.0096
304.3 | 50.5 | -1.0096
304.4 | 50.5 | -1.0096
304.5 | 50.5 | -1.0096
304.6 | 50.5 | -1.0096
304.7 | 50.5 | -1.0096
304.8 | 50.5 | -1.0096
304.9 | 50.5 | -1.0096
305 | 50.5 | -1.0096
305.1 | 50.5 | -1.0096
305.2 | 50.5 | -1.0096
305.3 | 50.5 | -1.0096
305.4 | 50.5 | -1.0096
305.5 | 50.5 | -1.0096
305.6 | 50.5 | -1.0096
305.7 | 50.5 | -1.0096
305.8 | 50.5 | -1.0096
305.9 | 50.5 | -1.0096
306 | 50.5 | -1.0096
306.1 | 50.5 | -1.0096
306.2 | 50.5 | -1.0096
306.3 | 50.5 | -1.0096
306.4 | 50.5 | -1.0096
306.5 | 50.5 | -1.0096
306.6 | 50.5 | -1.0096
306.7 | 50.5 | -1.0096
306.8 | 50.5 | -1.0096
306.9 | 50.5 | -1.0096
307 | 50.5 | -1.0096
307.1 | 50.5 | -1.0096
307.2 | 50.5 | -1.0096
307.3 | 50.5 | -1.0096
307.4 | 50.5 | -1.0096
307.5 | 50.5 | -1.0096
307.6 | 50.5 | -1.0096
307.7 | 50.5 | -1.0096
307.8 | 50.5 | -1.0096
307.9 | 50.5 | -1.0096
308 | 50.5 | -1.0096
308.1 | 50.5 | -1.0096
308.2 | 50.5 | -1.0096
308.3 | 50.5 | -1.0096
308.4 | 50.5 | -1.0096
308.5 | 50.5 | -1.0096
308.6 | 50.5 | -1.0096
308.7 | 50.5 | -1.0096
308.8 | 50.5 | -1.0096
308.9 | 50.5 | -1.0096
309 | 50.5 | -1.0096
309.1 | 50.5 | -1.0096
309.2 | 50.5 | -1.0096
309.3 | 50.5 | -1.0096
309.4 | 50.5 | -1.0096
309.5 | 50.5 | -1.0096
309.6 | 50.5 | -1.0096
309.7 | 50.5 | -1.0096
309.8 | 50.5 | -1.0096
309.9 | 50.5 | -1.0096
310 | 50.5 | -1.0096
310.1 | 50.5 | -1.0096
310.2 | 50.5 | -1.0096
310.3 | 50.5 | -1.0096
310.4 | 50.5 | -1.0096
310.5 | 50.5 | -1.0096
310.6 | 50.5 | -1.0096
310.7 | 50.5 | -1.0096
310.8 | 50.5 | -1.0096
310.9 | 50.5 | -1.0096
311 | 50.5 | -1.0096
311.1 | 50.5 | -1.0096
311.2 | 50.5 | -1.0096
311.3 | 50.5 | -1.0096
311.4 | 50.5 | -1.0096
311.5 | 50.5 | -1.0096
311.6 | 50.5 | -1.0096
311.7 | 50.5 | -1.0096
311.8 | 50.5 | -1.0096
311.9 | 50.5 | -1.0096
312 | 50.5 | -1.0096
312.1 | 50.5 | -1.0096
312.2 | 50.5 | -1.0096
312.3 | 50.5 | -1.0096
312.4 | 50.5 | -1.0096
312.5 | 50.5 | -1.0096
312.6 | 50.5 | -1.0096
312.7 | 50.5 | -1.0096
312.8 | 50.5 | -1.0096
312.9 | 50.5 | -1.0096
313 | 50.5 | -1.0096
313.1 | 50.5 | -1.0096
313.2 | 50.5 | -1.0096
313.3 | 50.5 | -1.0096
313.4 | 50.5 | -1.0096
313.5 | 50.5 | -1.0096
313.6 | 50.5 | -1.0096
313.7 | 50.5 | -1.0096
313.8 | 50.5 | -1.0096
313.9 | 50.5 | -1.0096
314 | 50.5 | -1.0096
314.1 | 50.5 | -1.0096
314.2 | 50.5 | -1.0096
314.3 | 50.5 | -1.0096
314.4 | 50.5 | -1.0096
314.5 | 50.5 | -1.0096
314.6 | 50.5 | -1.0096
314.7 | 50.5 | -1.0096
314.8 | 50.5 | -1.0096
314.9 | 50.5 | -1.0096
315 | 50.5 | -1.0096
315.1 | 50.5 | -1.0096
315.2 | 50.5 | -1.0096
315.3 | 50.5 | -1.0096
315.4 | 50.5 | -1.0096
315.5 | 50.5 | -1.0096
315.6 | 50.5 | -1.0096
315.7 | 50.5 | -1.0096
315.8 | 50.5 | -1.0096
315.9 | 50.5 | -1.0096
316 | 50.5 | -1.0096
316.1 | 50.5 | -1.0096
316.2 | 50.5 | -1.0096
316.3 | 50.5 | -1.0096
316.4 | 50.5 | -1.0096
316.5 | 50.5 | -1.0096
316.6 | 50.5 | -1.0096
316.7 | 50.5 | -1.0096
316.8 | 50.5 | -1.0096
316.9 | 50.5 | -1.0096
317 | 50.5 | -1.0096
317.1 | 50.5 | -1.0096
317.2 | 50.5 | -1.0096
317.3 | 50.5 | -1.0096
317.4 | 50.5 | -1.0096
317.5 | 50.5 | -1.0096
317.6 | 50.5 | -1.0096
317.7 | 50.5 | -1.0096
317.8 | 50.5 | -1.0096
317.9 | 50.5 | -1.0096
318 | 50.5 | -1.0096
318.1 | 50.5 | -1.0096
318.2 | 50.5 | -1.0096
318.3 | 50.5 | -1.0096
318.4 | 50.5 | -1.0096
318.5 | 50.5 | -1.0096
318.6 | 50.5 | -1.0096
318.7 | 50.5 | -1.0096
318.8 | 50.5 | -1.0096
318.9 | 50.5 | -1.0096
319 | 50.5 | -1.0094
319.1 | 50.5 | -1.0094
319.2 | 50.5 | -1.0094
319.3 | 50.5 | -1.0094
319.4 | 50.5 | -1.0094
319.5 | 50.5 | -1.0094
319.6 | 50.5 | -1.0094
319.7 | 50.5 | -1.0094
319.8 | 50.5 | -1.0094
319.9 | 50.5 | -1.0094
320 | 50.5 | -1.0094
320.1 | 50.5 | -1.0094
320.2 | 50.5 | -1.0094
320.3 | 50.5 | -1.0094
320.4 | 50.5 | -1.0094
320.5 | 50.5 | -1.0094
320.6 | 50.5 | -1.0094
320.7 | 50.5 | -1.0094
320.8 | 50.5 | -1.0094
320.9 | 50.5 | -1.0094
321 | 50.5 | -1.0094
321.1 | 50.5 | -1.0094
321.2 | 50.5 | -1.0094
321.3 | 50.5 | -1.0094
321.4 | 50.5 | -1.0096
321.5 | 50.5 | -1.0096
321.6 | 50.5 | -1.0096
321.7 | 50.5 | -1.0096
321.8 | 50.5 | -1.0096
321.9 | 50.5 | -1.0096
322 | 50.5 | -1.0096
322.1 | 50.5 | -1.0096
322.2 | 50.5 | -1.0096
322.3 | 50.5 | -1.0096
322.4 | 50.5 | -1.0096
322.5 | 50.5 | -1.0096
322.6 | 50.5 | -1.0096
322.7 | 50.5 | -1.0096
322.8 | 50.5 | -1.0096
322.9 | 50.5 | -1.0096
323 | 50.5 | -1.0096
323.1 | 50.5 | -1.0096
323.2 | 50.5 | -1.0096
323.3 | 50.5 | -1.0096
323.4 | 50.5 | -1.0096
323.5 | 50.5 | -1.0096
323.6 | 50.5 | -1.0096
323.7 | 50.5 | -1.0096
323.8 | 50.5 | -1.0096
323.9 | 50.5 | -1.0096
324 | 50.5 | -1.0096
324.1 | 50.5 | -1.0096
324.2 | 50.5 | -1.0096
324.3 | 50.5 | -1.0096
324.4 | 50.5 | -1.0096
324.5 | 50.5 | -1.0096
324.6 | 50.5 | -1.0096
324.7 | 50.5 | -1.0096
324.8 | 50.5 | -1.0096
324.9 | 50.5 | -1.0096
325 | 50.5 | -1.0094
325.1 | 50.5 | -1.0094
325.2 | 50.5 | -1.0094
325.3 | 50.5 | -1.0094
325.4 | 50.5 | -1.0094
325.5 | 50.5 | -1.0094
325.6 | 50.5 | -1.0094
325.7 | 50.5 | -1.0094
325.8 | 50.5 | -1.0094
325.9 | 50.5 | -1.0094
326 | 50.5 | -1.0094
326.1 | 50.5 | -1.0094
326.2 | 50.5 | -1.0094
326.3 | 50.5 | -1.0094
326.4 | 50.5 | -1.0094
326.5 | 50.5 | -1.0094
326.6 | 50.5 | -1.0094
326.7 | 50.5 | -1.0094
326.8 | 50.5 | -1.0094
326.9 | 50.5 | -1.0094
327 | 50.5 | -1.0094
327.1 | 50.5 | -1.0094
327.2 | 50.5 | -1.0096
327.3 | 50.5 | -1.0096
327.4 | 50.5 | -1.0096
327.5 | 50.5 | -1.0096
327.6 | 50.5 | -1.0096
327.7 | 50.5 | -1.0096
327.8 | 50.5 | -1.0096
327.9 | 50.5 | -1.0096
328 | 50.5 | -1.0096
328.1 | 50.5 | -1.0096
328.2 | 50.5 | -1.0096
328.3 | 50.5 | -1.0096
328.4 | 50.5 | -1.0096
328.5 | 50.5 | -1.0096
328.6 | 50.5 | -1.0096
328.7 | 50.5 | -1.0096
328.8 | 50.5 | -1.0096
328.9 | 50.5 | -1.0096
329 | 50.5 | -1.0096
329.1 | 50.5 | -1.0096
329.2 | 50.5 | -1.0096
329.3 | 50.5 | -1.0096
329.4 | 50.5 | -1.0096
329.5 | 50.5 | -1.0096
329.6 | 50.5 | -1.0096
329.7 | 50.5 | -1.0096
329.8 | 50.5 | -1.0096
329.9 | 50.5 | -1.0096
330 | 50.5 | -1.0096
330.1 | 50.5 | -1.0096
330.2 | 50.5 | -1.0096
330.3 | 50.5 | -1.0096
330.4 | 50.5 | -1.0096
330.5 | 50.5 | -1.0096
330.6 | 50.5 | -1.0096
330.7 | 50.5 | -1.0096
330.8 | 50.5 | -1.0096
330.9 | 50.5 | -1.0096
331 | 50.5 | -1.0096
331.1 | 50.5 | -1.0096
331.2 | 50.5 | -1.0096
331.3 | 50.5 | -1.0096
331.4 | 50.5 | -1.0096
331.5 | 50.5 | -1.0096
331.6 | 50.5 | -1.0096
331.7 | 50.5 | -1.0096
331.8 | 50.5 | -1.0096
331.9 | 50.5 | -1.0096
332 | 50.5 | -1.0096
332.1 | 50.5 | -1.0096
332.2 | 50.5 | -1.0096
332.3 | 50.5 | -1.0096
332.4 | 50.5 | -1.0096
332.5 | 50.5 | -1.0096
332.6 | 50.5 | -1.0096
332.7 | 50.5 | -1.0096
332.8 | 50.5 | -1.0096
332.9 | 50.5 | -1.0096
333 | 50.5 | -1.0096
333.1 | 50.5 | -1.0096
333.2 | 50.5 | -1.0096
333.3 | 50.5 | -1.0096
333.4 | 50.5 | -1.0096
333.5 | 50.5 | -1.0096
333.6 | 50.5 | -1.0096
333.7 | 50.5 | -1.0096
333.8 | 50.5 | -1.0096
333.9 | 50.5 | -1.0096
334 | 50.5 | -1.0096
334.1 | 50.5 | -1.0096
334.2 | 50.5 | -1.0096
334.3 | 50.5 | -1.0096
334.4 | 50.5 | -1.0096
334.5 | 50.5 | -1.0096
334.6 | 50.5 | -1.0096
334.7 | 50.5 | -1.0096
334.8 | 50.5 | -1.0096
334.9 | 50.5 | -1.0096
335 | 50.5 | -1.0096
335.1 | 50.5 | -1.0096
335.2 | 50.5 | -1.0096
335.3 | 50.5 | -1.0096
335.4 | 50.5 | -1.0096
335.5 | 50.5 | -1.0096
335.6 | 50.5 | -1.0096
335.7 | 50.5 | -1.0096
335.8 | 50.5 | -1.0096
335.9 | 50.5 | -1.0096
336 | 50.5 | -1.0096
336.1 | 50.5 | -1.0096
336.2 | 50.5 | -1.0096
336.3 | 50.5 | -1.0096
336.4 | 50.5 | -1.0096
336.5 | 50.5 | -1.0096
336.6 | 50.5 | -1.0096
336.7 | 50.5 | -1.0096
336.8 | 50.5 | -1.0096
336.9 | 50.5 | -1.0096
337 | 50.5 | -1.0096
337.1 | 50.5 | -1.0096
337.2 | 50.5 | -1.0096
337.3 | 50.5 | -1.0096
337.4 | 50.5 | -1.0096
337.5 | 50.5 | -1.0096
337.6 | 50.5 | -1.0096
337.7 | 50.5 | -1.0096
337.8 | 50.5 | -1.0096
337.9 | 50.5 | -1.0096
338 | 50.5 | -1.0096
338.1 | 50.5 | -1.0096
338.2 | 50.5 | -1.0096
338.3 | 50.5 | -1.0096
338.4 | 50.5 | -1.0096
338.5 | 50.5 | -1.0096
338.6 | 50.5 | -1.0096
338.7 | 50.5 | -1.0096
338.8 | 50.5 | -1.0096
338.9 | 50.5 | -1.0096
339 | 50.5 | -1.0096
339.1 | 50.5 | -1.0096
339.2 | 50.5 | -1.0096
339.3 | 50.5 | -1.0096
339.4 | 50.5 | -1.0096
339.5 | 50.5 | -1.0096
339.6 | 50.5 | -1.0096
339.7 | 50.5 | -1.0096
339.8 | 50.5 | -1.0096
339.9 | 50.5 | -1.0096
340 | 50.5 | -1.0096
340.1 | 50.5 | -1.0096
340.2 | 50.5 | -1.0096
340.3 | 50.5 | -1.0096
340.4 | 50.5 | -1.0096
340.5 | 50.5 | -1.0096
340.6 | 50.5 | -1.0096
340.7 | 50.5 | -1.0096
340.8 | 50.5 | -1.0096
340.9 | 50.5 | -1.0096
341 | 50.5 | -1.0096
341.1 | 50.5 | -1.0096
341.2 | 50.5 | -1.0096
341.3 | 50.5 | -1.0096
341.4 | 50.5 | -1.0096
341.5 | 50.5 | -1.0096
341.6 | 50.5 | -1.0096
341.7 | 50.5 | -1.0096
341.8 | 50.5 | -1.0096
341.9 | 50.5 | -1.0096
342 | 50.5 | -1.0096
342.1 | 50.5 | -1.0096
342.2 | 50.5 | -1.0096
342.3 | 50.5 | -1.0096
342.4 | 50.5 | -1.0096
342.5 | 50.5 | -1.0096
342.6 | 50.5 | -1.0096
342.7 | 50.5 | -1.0096
342.8 | 50.5 | -1.0096
342.9 | 50.5 | -1.0096
343 | 50.5 | -1.0096
343.1 | 50.5 | -1.0096
343.2 | 50.5 | -1.0096
343.3 | 50.5 | -1.0096
343.4 | 50.5 | -1.0096
343.5 | 50.5 | -1.0096
343.6 | 50.5 | -1.0096
343.7 | 50.5 | -1.0096
343.8 | 50.5 | -1.0096
343.9 | 50.5 | -1.0096
344 | 50.5 | -1.0096
344.1 | 50.5 | -1.0096
344.2 | 50.5 | -1.0096
344.3 | 50.5 | -1.0096
344.4 | 50.5 | -1.0096
344.5 | 50.5 | -1.0096
344.6 | 50.5 | -1.0096
344.7 | 50.5 | -1.0096
344.8 | 50.5 | -1.0096
344.9 | 50.5 | -1.0096
345 | 50.5 | -1.0096
345.1 | 50.5 | -1.0096
345.2 | 50.5 | -1.0096
345.3 | 50.5 | -1.0096
345.4 | 50.5 | -1.0096
345.5 | 50.5 | -1.0096
345.6 | 50.5 | -1.0096
345.7 | 50.5 | -1.0096
345.8 | 50.5 | -1.0096
345.9 | 50.5 | -1.0096
346 | 50.5 | -1.0096
346.1 | 50.5 | -1.0096
346.2 | 50.5 | -1.0096
346.3 | 50.5 | -1.0096
346.4 | 50.5 | -1.0096
346.5 | 50.5 | -1.0096
346.6 | 50.5 | -1.0096
346.7 | 50.5 | -1.0096
346.8 | 50.5 | -1.0096
346.9 | 50.5 | -1.0096
347 | 50.5 | -1.0096
347.1 | 50.5 | -1.0096
347.2 | 50.5 | -1.0096
347.3 | 50.5 | -1.0096
347.4 | 50.5 | -1.0096
347.5 | 50.5 | -1.0096
347.6 | 50.5 | -1.0096
347.7 | 50.5 | -1.0096
347.8 | 50.5 | -1.0096
347.9 | 50.5 | -1.0096
348 | 50.5 | -1.0096
348.1 | 50.5 | -1.0096
348.2 | 50.5 | -1.0096
348.3 | 50.5 | -1.0096
348.4 | 50.5 | -1.0096
348.5 | 50.5 | -1.0096
348.6 | 50.5 | -1.0096
348.7 | 50.5 | -1.0096
348.8 | 50.5 | -1.0096
348.9 | 50.5 | -1.0096
349 | 50.5 | -1.0096
349.1 | 50.5 | -1.0096
349.2 | 50.5 | -1.0096
349.3 | 50.5 | -1.0096
349.4 | 50.5 | -1.0096
349.5 | 50.5 | -1.0096
349.6 | 50.5 | -1.0096
349.7 | 50.5 | -1.0096
349.8 | 50.5 | -1.0096
349.9 | 50.5 | -1.0096
350 | 50.5 | -1.0096
350.1 | 50.5 | -1.0096
350.2 | 50.5 | -1.0096
350.3 | 50.5 | -1.0096
350.4 | 50.5 | -1.0096
350.5 | 50.5 | -1.0096
350.6 | 50.5 | -1.0096
350.7 | 50.5 | -1.0096
350.8 | 50.5 | -1.0096
350.9 | 50.5 | -1.0096
351 | 50.5 | -1.0096
351.1 | 50.5 | -1.0096
351.2 | 50.5 | -1.0096
351.3 | 50.5 | -1.0096
351.4 | 50.5 | -1.0096
351.5 | 50.5 | -1.0096
351.6 | 50.5 | -1.0096
351.7 | 50.5 | -1.0096
351.8 | 50.5 | -1.0096
351.9 | 50.5 | -1.0096
352 | 50.5 | -1.0096
352.1 | 50.5 | -1.0094
352.2 | 50.5 | -1.0094
352.3 | 50.5 | -1.0094
352.4 | 50.5 | -1.0094
352.5 | 50.5 | -1.0094
352.6 | 50.5 | -1.0094
352.7 | 50.5 | -1.0094
352.8 | 50.5 | -1.0094
352.9 | 50.5 | -1.0094
353 | 50.5 | -1.0094
353.1 | 50.5 | -1.0094
353.2 | 50.5 | -1.0094
353.3 | 50.5 | -1.0094
353.4 | 50.5 | -1.0094
353.5 | 50.5 | -1.0094
353.6 | 50.5 | -1.0094
353.7 | 50.5 | -1.0094
353.8 | 50.5 | -1.0094
353.9 | 50.5 | -1.0094
354 | 50.5 | -1.0094
354.1 | 50.5 | -1.0094
354.2 | 50.5 | -1.0094
354.3 | 50.5 | -1.0096
354.4 | 50.5 | -1.0096
354.5 | 50.5 | -1.0096
354.6 | 50.5 | -1.0096
354.7 | 50.5 | -1.0096
354.8 | 50.5 | -1.0096
354.9 | 50.5 | -1.0096
355 | 50.5 | -1.0096
355.1 | 50.5 | -1.0096
355.2 | 50.5 | -1.0096
355.3 | 50.5 | -1.0096
355.4 | 50.5 | -1.0096
355.5 | 50.5 | -1.0094
355.6 | 50.5 | -1.0094
355.7 | 50.5 | -1.0094
355.8 | 50.5 | -1.0094
355.9 | 50.5 | -1.0094
356 | 50.5 | -1.0094
356.1 | 50.5 | -1.0094
356.2 | 50.5 | -1.0094
356.3 | 50.5 | -1.0094
356.4 | 50.5 | -1.0094
356.5 | 50.5 | -1.0094
356.6 | 50.5 | -1.0096
356.7 | 50.5 | -1.0096
356.8 | 50.5 | -1.0096
356.9 | 50.5 | -1.0096
357 | 50.5 | -1.0096
357.1 | 50.5 | -1.0096
357.2 | 50.5 | -1.0096
357.3 | 50.5 | -1.0096
357.4 | 50.5 | -1.0096
357.5 | 50.5 | -1.0096
357.6 | 50.5 | -1.0096
357.7 | 50.5 | -1.0096
357.8 | 50.5 | -1.0096
357.9 | 50.5 | -1.0096
358 | 50.5 | -1.0096
358.1 | 50.5 | -1.0096
358.2 | 50.5 | -1.0096
358.3 | 50.5 | -1.0096
358.4 | 50.5 | -1.0096
358.5 | 50.5 | -1.0096
358.6 | 50.5 | -1.0096
358.7 | 50.5 | -1.0096
358.8 | 50.5 | -1.0096
358.9 | 50.5 | -1.0096
359 | 50.5 | -1.0096
359.1 | 50.5 | -1.0096
359.2 | 50.5 | -1.0096
359.3 | 50.5 | -1.0096
359.4 | 50.5 | -1.0096
359.5 | 50.5 | -1.0096
359.6 | 50.5 | -1.0096
359.7 | 50.5 | -1.0096
359.8 | 50.5 | -1.0096
359.9 | 50.5 | -1.0096
360 | 50.5 | -1.0096
360.1 | 50.5 | -1.0096
360.2 | 50.5 | -1.0096
360.3 | 50.5 | -1.0096
360.4 | 50.5 | -1.0096
360.5 | 50.5 | -1.0096
360.6 | 50.5 | -1.0096
360.7 | 50.5 | -1.0096
360.8 | 50.5 | -1.0096
360.9 | 50.5 | -1.0096
361 | 50.5 | -1.0096
361.1 | 50.5 | -1.0096
361.2 | 50.5 | -1.0096
361.3 | 50.5 | -1.0096
361.4 | 50.5 | -1.0094
361.5 | 50.5 | -1.0094
361.6 | 50.5 | -1.0094
361.7 | 50.5 | -1.0094
361.8 | 50.5 | -1.0094
361.9 | 50.5 | -1.0094
362 | 50.5 | -1.0094
362.1 | 50.5 | -1.0094
362.2 | 50.5 | -1.0094
362.3 | 50.5 | -1.0094
362.4 | 50.5 | -1.0094
362.5 | 50.5 | -1.0096
362.6 | 50.5 | -1.0096
362.7 | 50.5 | -1.0096
362.8 | 50.5 | -1.0096
362.9 | 50.5 | -1.0096
363 | 50.5 | -1.0096
363.1 | 50.5 | -1.0096
363.2 | 50.5 | -1.0096
363.3 | 50.5 | -1.0096
363.4 | 50.5 | -1.0096
363.5 | 50.5 | -1.0096
363.6 | 50.5 | -1.0096
363.7 | 50.5 | -1.0096
363.8 | 50.5 | -1.0096
363.9 | 50.5 | -1.0096
364 | 50.5 | -1.0096
364.1 | 50.5 | -1.0096
364.2 | 50.5 | -1.0096
364.3 | 50.5 | -1.0096
364.4 | 50.5 | -1.0096
364.5 | 50.5 | -1.0096
364.6 | 50.5 | -1.0096
364.7 | 50.5 | -1.0096
364.8 | 50.5 | -1.0096
364.9 | 50.5 | -1.0096
365 | 50.5 | -1.0096
365.1 | 50.5 | -1.0096
365.2 | 50.5 | -1.0096
365.3 | 50.5 | -1.0096
365.4 | 50.5 | -1.0096
365.5 | 50.5 | -1.0096
365.6 | 50.5 | -1.0096
365.7 | 50.5 | -1.0096
365.8 | 50.5 | -1.0096
365.9 | 50.5 | -1.0096
366 | 50.5 | -1.0096
366.1 | 50.5 | -1.0096
366.2 | 50.5 | -1.0096
366.3 | 50.5 | -1.0096
366.4 | 50.5 | -1.0096
366.5 | 50.5 | -1.0096
366.6 | 50.5 | -1.0096
366.7 | 50.5 | -1.0096
366.8 | 50.5 | -1.0096
366.9 | 50.5 | -1.0096
367 | 50.5 | -1.0096
367.1 | 50.5 | -1.0096
367.2 | 50.5 | -1.0096
367.3 | 50.5 | -1.0096
367.4 | 50.5 | -1.0096
367.5 | 50.5 | -1.0096
367.6 | 50.5 | -1.0096
367.7 | 50.5 | -1.0096
367.8 | 50.5 | -1.0096
367.9 | 50.5 | -1.0096
368 | 50.5 | -1.0096
368.1 | 50.5 | -1.0096
368.2 | 50.5 | -1.0096
368.3 | 50.5 | -1.0096
368.4 | 50.5 | -1.0096
368.5 | 50.5 | -1.0096
368.6 | 50.5 | -1.0096
368.7 | 50.5 | -1.0096
368.8 | 50.5 | -1.0096
368.9 | 50.5 | -1.0096
369 | 50.5 | -1.0096
369.1 | 50.5 | -1.0096
369.2 | 50.5 | -1.0096
369.3 | 50.5 | -1.0096
369.4 | 50.5 | -1.0096
369.5 | 50.5 | -1.0096
369.6 | 50.5 | -1.0096
369.7 | 50.5 | -1.0096
369.8 | 50.5 | -1.0096
369.9 | 50.5 | -1.0094
370 | 50.5 | -1.0094
370.1 | 50.5 | -1.0094
370.2 | 50.5 | -1.0094
370.3 | 50.5 | -1.0094
370.4 | 50.5 | -1.0094
370.5 | 50.5 | -1.0094
370.6 | 50.5 | -1.0094
370.7 | 50.5 | -1.0094
370.8 | 50.5 | -1.0094
370.9 | 50.5 | -1.0094
371 | 50.5 | -1.0094
371.1 | 50.5 | -1.0096
371.2 | 50.5 | -1.0096
371.3 | 50.5 | -1.0096
371.4 | 50.5 | -1.0096
371.5 | 50.5 | -1.0096
371.6 | 50.5 | -1.0096
371.7 | 50.5 | -1.0096
371.8 | 50.5 | -1.0096
371.9 | 50.5 | -1.0096
372 | 50.5 | -1.0096
372.1 | 50.5 | -1.0096
372.2 | 50.5 | -1.0096
372.3 | 50.5 | -1.0096
372.4 | 50.5 | -1.0096
372.5 | 50.5 | -1.0094
372.6 | 50.5 | -1.0094
372.7 | 50.5 | -1.0094
372.8 | 50.5 | -1.0094
372.9 | 50.5 | -1.0094
373 | 50.5 | -1.0094
373.1 | 50.5 | -1.0094
373.2 | 50.5 | -1.0094
373.3 | 50.5 | -1.0094
373.4 | 50.5 | -1.0096
373.5 | 50.5 | -1.0096
373.6 | 50.5 | -1.0096
373.7 | 50.5 | -1.0096
373.8 | 50.5 | -1.0096
373.9 | 50.5 | -1.0096
374 | 50.5 | -1.0096
374.1 | 50.5 | -1.0096
374.2 | 50.5 | -1.0096
374.3 | 50.5 | -1.0096
374.4 | 50.5 | -1.0096
374.5 | 50.5 | -1.0096
374.6 | 50.5 | -1.0096
374.7 | 50.5 | -1.0096
374.8 | 50.5 | -1.0096
374.9 | 50.5 | -1.0096
375 | 50.5 | -1.0096
375.1 | 50.5 | -1.0096
375.2 | 50.5 | -1.0096
375.3 | 50.5 | -1.0096
375.4 | 50.5 | -1.0096
375.5 | 50.5 | -1.0096
375.6 | 50.5 | -1.0096
375.7 | 50.5 | -1.0096
375.8 | 50.5 | -1.0096
375.9 | 50.5 | -1.0096
376 | 50.5 | -1.0096
376.1 | 50.5 | -1.0096
376.2 | 50.5 | -1.0096
376.3 | 50.5 | -1.0096
376.4 | 50.5 | -1.0096
376.5 | 50.5 | -1.0096
376.6 | 50.5 | -1.0096
376.7 | 50.5 | -1.0096
376.8 | 50.5 | -1.0096
376.9 | 50.5 | -1.0096
377 | 50.5 | -1.0096
377.1 | 50.5 | -1.0096
377.2 | 50.5 | -1.0096
377.3 | 50.5 | -1.0096
377.4 | 50.5 | -1.0096
377.5 | 50.5 | -1.0096
377.6 | 50.5 | -1.0096
377.7 | 50.5 | -1.0096
377.8 | 50.5 | -1.0096
377.9 | 50.5 | -1.0096
378 | 50.5 | -1.0096
378.1 | 50.5 | -1.0096
378.2 | 50.5 | -1.0096
378.3 | 50.5 | -1.0096
378.4 | 50.5 | -1.0096
378.5 | 50.5 | -1.0096
378.6 | 50.5 | -1.0096
378.7 | 50.5 | -1.0096
378.8 | 50.5 | -1.0096
378.9 | 50.5 | -1.0096
379 | 50.5 | -1.0096
379.1 | 50.5 | -1.0096
379.2 | 50.5 | -1.0096
379.3 | 50.5 | -1.0096
379.4 | 50.5 | -1.0096
379.5 | 50.5 | -1.0096
379.6 | 50.5 | -1.0096
379.7 | 50.5 | -1.0096
379.8 | 50.5 | -1.0096
379.9 | 50.5 | -1.0096
380 | 50.5 | -1.0096
380.1 | 50.5 | -1.0096
380.2 | 50.5 | -1.0096
380.3 | 50.5 | -1.0096
380.4 | 50.5 | -1.0096
380.5 | 50.5 | -1.0096
380.6 | 50.5 | -1.0096
380.7 | 50.5 | -1.0096
380.8 | 50.5 | -1.0096
380.9 | 50.5 | -1.0096
381 | 50.5 | -1.0096
381.1 | 50.5 | -1.0096
381.2 | 50.5 | -1.0096
381.3 | 50.5 | -1.0096
381.4 | 50.5 | -1.0096
381.5 | 50.5 | -1.0096
381.6 | 50.5 | -1.0096
381.7 | 50.5 | -1.0096
381.8 | 50.5 | -1.0096
381.9 | 50.5 | -1.0096
382 | 50.5 | -1.0096
382.1 | 50.5 | -1.0096
382.2 | 50.5 | -1.0096
382.3 | 50.5 | -1.0096
382.4 | 50.5 | -1.0096
382.5 | 50.5 | -1.0096
382.6 | 50.5 | -1.0096
382.7 | 50.5 | -1.0096
382.8 | 50.5 | -1.0096
382.9 | 50.5 | -1.0096
383 | 50.5 | -1.0096
383.1 | 50.5 | -1.0096
383.2 | 50.5 | -1.0096
383.3 | 50.5 | -1.0096
383.4 | 50.5 | -1.0096
383.5 | 50.5 | -1.0096
383.6 | 50.5 | -1.0096
383.7 | 50.5 | -1.0096
383.8 | 50.5 | -1.0096
383.9 | 50.5 | -1.0096
384 | 50.5 | -1.0096
384.1 | 50.5 | -1.0096
384.2 | 50.5 | -1.0096
384.3 | 50.5 | -1.0096
384.4 | 50.5 | -1.0096
384.5 | 50.5 | -1.0096
384.6 | 50.5 | -1.0096
384.7 | 50.5 | -1.0096
384.8 | 50.5 | -1.0096
384.9 | 50.5 | -1.0096
385 | 50.5 | -1.0096
385.1 | 50.5 | -1.0096
385.2 | 50.5 | -1.0096
385.3 | 50.5 | -1.0096
385.4 | 50.5 | -1.0096
385.5 | 50.5 | -1.0096
385.6 | 50.5 | -1.0096
385.7 | 50.5 | -1.0096
385.8 | 50.5 | -1.0096
385.9 | 50.5 | -1.0096
386 | 50.5 | -1.0096
386.1 | 50.5 | -1.0096
386.2 | 50.5 | -1.0096
386.3 | 50.5 | -1.0096
386.4 | 50.5 | -1.0096
386.5 | 50.5 | -1.0096
386.6 | 50.5 | -1.0096
386.7 | 50.5 | -1.0096
386.8 | 50.5 | -1.0096
386.9 | 50.5 | -1.0096
387 | 50.5 | -1.0096
387.1 | 50.5 | -1.0096
387.2 | 50.5 | -1.0096
387.3 | 50.5 | -1.0096
387.4 | 50.5 | -1.0096
387.5 | 50.5 | -1.0096
387.6 | 50.5 | -1.0096
387.7 | 50.5 | -1.0096
387.8 | 50.5 | -1.0096
387.9 | 50.5 | -1.0096
388 | 50.5 | -1.0096
388.1 | 50.5 | -1.0096
388.2 | 50.5 | -1.0096
388.3 | 50.5 | -1.0096
388.4 | 50.5 | -1.0096
388.5 | 50.5 | -1.0096
388.6 | 50.5 | -1.0096
388.7 | 50.5 | -1.0096
388.8 | 50.5 | -1.0096
388.9 | 50.5 | -1.0096
389 | 50.5 | -1.0096
389.1 | 50.5 | -1.0096
389.2 | 50.5 | -1.0096
389.3 | 50.5 | -1.0096
389.4 | 50.5 | -1.0096
389.5 | 50.5 | -1.0096
389.6 | 50.5 | -1.0096
389.7 | 50.5 | -1.0096
389.8 | 50.5 | -1.0096
389.9 | 50.5 | -1.0096
390 | 50.5 | -1.0096
390.1 | 50.5 | -1.0096
390.2 | 50.5 | -1.0096
390.3 | 50.5 | -1.0096
390.4 | 50.5 | -1.0096
390.5 | 50.5 | -1.0096
390.6 | 50.5 | -1.0094
390.7 | 50.5 | -1.0094
390.8 | 50.5 | -1.0094
390.9 | 50.5 | -1.0094
391 | 50.5 | -1.0094
391.1 | 50.5 | -1.0094
391.2 | 50.5 | -1.0094
391.3 | 50.5 | -1.0094
391.4 | 50.5 | -1.0094
391.5 | 50.5 | -1.0094
391.6 | 50.5 | -1.0094
391.7 | 50.5 | -1.0094
391.8 | 50.5 | -1.0094
391.9 | 50.5 | -1.0094
392 | 50.5 | -1.0094
392.1 | 50.5 | -1.0094
392.2 | 50.5 | -1.0094
392.3 | 50.5 | -1.0094
392.4 | 50.5 | -1.0094
392.5 | 50.5 | -1.0094
392.6 | 50.5 | -1.0094
392.7 | 50.5 | -1.0094
392.8 | 50.5 | -1.0094
392.9 | 50.5 | -1.0096
393 | 50.5 | -1.0096
393.1 | 50.5 | -1.0096
393.2 | 50.5 | -1.0096
393.3 | 50.5 | -1.0096
393.4 | 50.5 | -1.0096
393.5 | 50.5 | -1.0096
393.6 | 50.5 | -1.0096
393.7 | 50.5 | -1.0096
393.8 | 50.5 | -1.0096
393.9 | 50.5 | -1.0096
394 | 50.5 | -1.0096
394.1 | 50.5 | -1.0096
394.2 | 50.5 | -1.0096
394.3 | 50.5 | -1.0096
394.4 | 50.5 | -1.0096
394.5 | 50.5 | -1.0096
394.6 | 50.5 | -1.0096
394.7 | 50.5 | -1.0096
394.8 | 50.5 | -1.0096
394.9 | 50.5 | -1.0096
395 | 50.5 | -1.0096
395.1 | 50.5 | -1.0096
395.2 | 50.5 | -1.0096
395.3 | 50.5 | -1.0096
395.4 | 50.5 | -1.0096
395.5 | 50.5 | -1.0096
395.6 | 50.5 | -1.0096
395.7 | 50.5 | -1.0096
395.8 | 50.5 | -1.0096
395.9 | 50.5 | -1.0096
396 | 50.5 | -1.0096
396.1 | 50.5 | -1.0096
396.2 | 50.5 | -1.0096
396.3 | 50.5 | -1.0096
396.4 | 50.5 | -1.0096
396.5 | 50.5 | -1.0096
396.6 | 50.5 | -1.0096
396.7 | 50.5 | -1.0096
396.8 | 50.5 | -1.0096
396.9 | 50.5 | -1.0096
397 | 50.5 | -1.0096
397.1 | 50.5 | -1.0096
397.2 | 50.5 | -1.0096
397.3 | 50.5 | -1.0096
397.4 | 50.5 | -1.0096
397.5 | 50.5 | -1.0096
397.6 | 50.5 | -1.0096
397.7 | 50.5 | -1.0096
397.8 | 50.5 | -1.0096
397.9 | 50.5 | -1.0096
398 | 50.5 | -1.0096
398.1 | 50.5 | -1.0096
398.2 | 50.5 | -1.0096
398.3 | 50.5 | -1.0096
398.4 | 50.5 | -1.0096
398.5 | 50.5 | -1.0096
398.6 | 50.5 | -1.0096
398.7 | 50.5 | -1.0096
398.8 | 50.5 | -1.0096
398.9 | 50.5 | -1.0096
399 | 50.5 | -1.0096
399.1 | 50.5 | -1.0096
399.2 | 50.5 | -1.0096
399.3 | 50.5 | -1.0096
399.4 | 50.5 | -1.0096
399.5 | 50.5 | -1.0096
399.6 | 50.5 | -1.0096
399.7 | 50.5 | -1.0096
399.8 | 50.5 | -1.0096
399.9 | 50.5 | -1.0096
400 | 50.5 | -1.0096
400.1 | 50.5 | -1.0096
400.2 | 50.5 | -1.0096
400.3 | 50.5 | -1.0096
400.4 | 50.5 | -1.0096
400.5 | 50.5 | -1.0096
400.6 | 50.5 | -1.0096
400.7 | 50.5 | -1.0096
400.8 | 50.5 | -1.0096
400.9 | 50.5 | -1.0096
401 | 50.5 | -1.0096
401.1 | 50.5 | -1.0096
401.2 | 50.5 | -1.0096
401.3 | 50.5 | -1.0096
401.4 | 50.5 | -1.0096
401.5 | 50.5 | -1.0096
401.6 | 50.5 | -1.0096
401.7 | 50.5 | -1.0096
401.8 | 50.5 | -1.0096
401.9 | 50.5 | -1.0096
402 | 50.5 | -1.0096
402.1 | 50.5 | -1.0096
402.2 | 50.5 | -1.0096
402.3 | 50.5 | -1.0096
402.4 | 50.5 | -1.0096
402.5 | 50.5 | -1.0096
402.6 | 50.5 | -1.0096
402.7 | 50.5 | -1.0096
402.8 | 50.5 | -1.0096
402.9 | 50.5 | -1.0096
403 | 50.5 | -1.0096
403.1 | 50.5 | -1.0096
403.2 | 50.5 | -1.0096
403.3 | 50.5 | -1.0096
403.4 | 50.5 | -1.0096
403.5 | 50.5 | -1.0096
403.6 | 50.5 | -1.0096
403.7 | 50.5 | -1.0096
403.8 | 50.5 | -1.0096
403.9 | 50.5 | -1.0096
404 | 50.5 | -1.0096
404.1 | 50.5 | -1.0096
404.2 | 50.5 | -1.0096
404.3 | 50.5 | -1.0096
404.4 | 50.5 | -1.0096
404.5 | 50.5 | -1.0096
404.6 | 50.5 | -1.0096
404.7 | 50.5 | -1.0096
404.8 | 50.5 | -1.0096
404.9 | 50.5 | -1.0096
405 | 50.5 | -1.0098
405.1 | 50.5 | -1.0098
405.2 | 50.5 | -1.0098
405.3 | 50.5 | -1.0098
405.4 | 50.5 | -1.0098
405.5 | 50.5 | -1.0098
405.6 | 50.5 | -1.0098
405.7 | 50.5 | -1.0098
405.8 | 50.5 | -1.0098
405.9 | 50.5 | -1.0098
406 | 50.5 | -1.0098
406.1 | 50.5 | -1.0096
406.2 | 50.5 | -1.0096
406.3 | 50.5 | -1.0096
406.4 | 50.5 | -1.0096
406.5 | 50.5 | -1.0096
406.6 | 50.5 | -1.0096
406.7 | 50.5 | -1.0096
406.8 | 50.5 | -1.0096
406.9 | 50.5 | -1.0096
407 | 50.5 | -1.0096
407.1 | 50.5 | -1.0096
407.2 | 50.5 | -1.0096
407.3 | 50.5 | -1.0096
407.4 | 50.5 | -1.0096
407.5 | 50.5 | -1.0096
407.6 | 50.5 | -1.0096
407.7 | 50.5 | -1.0096
407.8 | 50.5 | -1.0096
407.9 | 50.5 | -1.0096
408 | 50.5 | -1.0096
408.1 | 50.5 | -1.0094
408.2 | 50.5 | -1.0094
408.3 | 50.5 | -1.0094
408.4 | 50.5 | -1.0094
408.5 | 50.5 | -1.0094
408.6 | 50.5 | -1.0094
408.7 | 50.5 | -1.0094
408.8 | 50.5 | -1.0094
408.9 | 50.5 | -1.0094
409 | 50.5 | -1.0094
409.1 | 50.5 | -1.0094
409.2 | 50.5 | -1.0096
409.3 | 50.5 | -1.0096
409.4 | 50.5 | -1.0096
409.5 | 50.5 | -1.0096
409.6 | 50.5 | -1.0096
409.7 | 50.5 | -1.0096
409.8 | 50.5 | -1.0096
409.9 | 50.5 | -1.0096
410 | 50.5 | -1.0096
410.1 | 50.5 | -1.0096
410.2 | 50.5 | -1.0096
410.3 | 50.5 | -1.0096
410.4 | 50.5 | -1.0098
410.5 | 50.5 | -1.0098
410.6 | 50.5 | -1.0098
410.7 | 50.5 | -1.0098
410.8 | 50.5 | -1.0098
410.9 | 50.5 | -1.0098
411 | 50.5 | -1.0098
411.1 | 50.5 | -1.0098
411.2 | 50.5 | -1.0098
411.3 | 50.5 | -1.0098
411.4 | 50.5 | -1.0098
411.5 | 50.5 | -1.0098
411.6 | 50.5 | -1.0096
411.7 | 50.5 | -1.0096
411.8 | 50.5 | -1.0096
411.9 | 50.5 | -1.0096
412 | 50.5 | -1.0096
412.1 | 50.5 | -1.0096
412.2 | 50.5 | -1.0096
412.3 | 50.5 | -1.0096
412.4 | 50.5 | -1.0096
412.5 | 50.5 | -1.0096
412.6 | 50.5 | -1.0096
412.7 | 50.5 | -1.0096
412.8 | 50.5 | -1.0096
412.9 | 50.5 | -1.0094
413 | 50.5 | -1.0094
413.1 | 50.5 | -1.0094
413.2 | 50.5 | -1.0094
413.3 | 50.5 | -1.0094
413.4 | 50.5 | -1.0094
413.5 | 50.5 | -1.0094
413.6 | 50.5 | -1.0096
413.7 | 50.5 | -1.0096
413.8 | 50.5 | -1.0096
413.9 | 50.5 | -1.0096
414 | 50.5 | -1.0096
414.1 | 50.5 | -1.0096
414.2 | 50.5 | -1.0096
414.3 | 50.5 | -1.0096
414.4 | 50.5 | -1.0096
414.5 | 50.5 | -1.0096
414.6 | 50.5 | -1.0096
414.7 | 50.5 | -1.0096
414.8 | 50.5 | -1.0096
414.9 | 50.5 | -1.0096
415 | 50.5 | -1.0096
415.1 | 50.5 | -1.0096
415.2 | 50.5 | -1.0096
415.3 | 50.5 | -1.0096
415.4 | 50.5 | -1.0096
415.5 | 50.5 | -1.0096
415.6 | 50.5 | -1.0096
415.7 | 50.5 | -1.0096
415.8 | 50.5 | -1.0096
415.9 | 50.5 | -1.0096
416 | 50.5 | -1.0098
416.1 | 50.5 | -1.0098
416.2 | 50.5 | -1.0098
416.3 | 50.5 | -1.0098
416.4 | 50.5 | -1.0098
416.5 | 50.5 | -1.0096
416.6 | 50.5 | -1.0096
416.7 | 50.5 | -1.0096
416.8 | 50.5 | -1.0096
416.9 | 50.5 | -1.0096
417 | 50.5 | -1.0096
417.1 | 50.5 | -1.0096
417.2 | 50.5 | -1.0096
417.3 | 50.5 | -1.0096
417.4 | 50.5 | -1.0096
417.5 | 50.5 | -1.0096
417.6 | 50.5 | -1.0096
417.7 | 50.5 | -1.0094
417.8 | 50.5 | -1.0094
417.9 | 50.5 | -1.0094
418 | 50.5 | -1.0094
418.1 | 50.5 | -1.0094
418.2 | 50.5 | -1.0094
418.3 | 50.5 | -1.0094
418.4 | 50.5 | -1.0094
418.5 | 50.5 | -1.0094
418.6 | 50.5 | -1.0094
418.7 | 50.5 | -1.0094
418.8 | 50.5 | -1.0094
418.9 | 50.5 | -1.0094
419 | 50.5 | -1.0094
419.1 | 50.5 | -1.0094
419.2 | 50.5 | -1.0094
419.3 | 50.5 | -1.0094
419.4 | 50.5 | -1.0094
419.5 | 50.5 | -1.0094
419.6 | 50.5 | -1.0096
419.7 | 50.5 | -1.0096
419.8 | 50.5 | -1.0096
419.9 | 50.5 | -1.0096
420 | 50.5 | -1.0096
420.1 | 50.5 | -1.0096
420.2 | 50.5 | -1.0096
420.3 | 50.5 | -1.0096
420.4 | 50.5 | -1.0096
420.5 | 50.5 | -1.0096
420.6 | 50.5 | -1.0096
420.7 | 50.5 | -1.0096
420.8 | 50.5 | -1.0096
420.9 | 50.5 | -1.0096
421 | 50.5 | -1.0096
421.1 | 50.5 | -1.0096
421.2 | 50.5 | -1.0096
421.3 | 50.5 | -1.0096
421.4 | 50.5 | -1.0096
421.5 | 50.5 | -1.0096
421.6 | 50.5 | -1.0096
421.7 | 50.5 | -1.0096
421.8 | 50.5 | -1.0096
421.9 | 50.5 | -1.0096
422 | 50.5 | -1.0096
422.1 | 50.5 | -1.0096
422.2 | 50.5 | -1.0098
422.3 | 50.5 | -1.0098
422.4 | 50.5 | -1.0098
422.5 | 50.5 | -1.0098
422.6 | 50.5 | -1.0098
422.7 | 50.5 | -1.0098
422.8 | 50.5 | -1.0098
422.9 | 50.5 | -1.0098
423 | 50.5 | -1.0098
423.1 | 50.5 | -1.0098
423.2 | 50.5 | -1.0098
423.3 | 50.5 | -1.0098
423.4 | 50.5 | -1.0094
423.5 | 50.5 | -1.0094
423.6 | 50.5 | -1.0094
423.7 | 50.5 | -1.0094
423.8 | 50.5 | -1.0094
423.9 | 50.5 | -1.0094
424 | 50.5 | -1.0094
424.1 | 50.5 | -1.0094
424.2 | 50.5 | -1.0094
424.3 | 50.5 | -1.0094
424.4 | 50.5 | -1.0094
424.5 | 50.5 | -1.0094
424.6 | 50.5 | -1.0094
424.7 | 50.5 | -1.0094
424.8 | 50.5 | -1.0094
424.9 | 50.5 | -1.0094
425 | 50.5 | -1.0094
425.1 | 50.5 | -1.0094
425.2 | 50.5 | -1.0094
425.3 | 50.5 | -1.0094
425.4 | 50.5 | -1.0094
425.5 | 50.5 | -1.0096
425.6 | 50.5 | -1.0096
425.7 | 50.5 | -1.0096
425.8 | 50.5 | -1.0096
425.9 | 50.5 | -1.0094
426 | 50.5 | -1.0094
426.1 | 50.5 | -1.0094
426.2 | 50.5 | -1.0094
426.3 | 50.5 | -1.0094
426.4 | 50.5 | -1.0094
426.5 | 50.5 | -1.0094
426.6 | 50.5 | -1.0094
426.7 | 50.5 | -1.0096
426.8 | 50.5 | -1.0096
426.9 | 50.5 | -1.0094
427 | 50.5 | -1.0094
427.1 | 50.5 | -1.0094
427.2 | 50.5 | -1.0094
427.3 | 50.5 | -1.0094
427.4 | 50.5 | -1.0094
427.5 | 50.5 | -1.0094
427.6 | 50.5 | -1.0094
427.7 | 50.5 | -1.0094
427.8 | 50.5 | -1.0094
427.9 | 50.5 | -1.0094
428 | 50.5 | -1.0096
428.1 | 50.5 | -1.0096
428.2 | 50.5 | -1.0096
428.3 | 50.5 | -1.0096
428.4 | 50.5 | -1.0096
428.5 | 50.5 | -1.0096
428.6 | 50.5 | -1.0096
428.7 | 50.5 | -1.0096
428.8 | 50.5 | -1.0096
428.9 | 50.5 | -1.0096
429 | 50.5 | -1.0096
429.1 | 50.5 | -1.0096
429.2 | 50.5 | -1.0096
429.3 | 50.5 | -1.0096
429.4 | 50.5 | -1.0096
429.5 | 50.5 | -1.0096
429.6 | 50.5 | -1.0096
429.7 | 50.5 | -1.0096
429.8 | 50.5 | -1.0096
429.9 | 50.5 | -1.0096
430 | 50.5 | -1.0096
430.1 | 50.5 | -1.0096
430.2 | 50.5 | -1.0096
430.3 | 50.5 | -1.0096
430.4 | 50.5 | -1.0096
430.5 | 50.5 | -1.0096
430.6 | 50.5 | -1.0096
430.7 | 50.5 | -1.0096
430.8 | 50.5 | -1.0096
430.9 | 50.5 | -1.0096
431 | 50.5 | -1.0096
431.1 | 50.5 | -1.0096
431.2 | 50.5 | -1.0096
431.3 | 50.5 | -1.0096
431.4 | 50.5 | -1.0096
431.5 | 50.5 | -1.0096
431.6 | 50.5 | -1.0096
431.7 | 50.5 | -1.0096
431.8 | 50.5 | -1.0096
431.9 | 50.5 | -1.0096
432 | 50.5 | -1.0096
432.1 | 50.5 | -1.0096
432.2 | 50.5 | -1.0096
432.3 | 50.5 | -1.0096
432.4 | 50.5 | -1.0096
432.5 | 50.5 | -1.0096
432.6 | 50.5 | -1.0096
432.7 | 50.5 | -1.0096
432.8 | 50.5 | -1.0094
432.9 | 50.5 | -1.0094
433 | 50.5 | -1.0094
433.1 | 50.5 | -1.0094
433.2 | 50.5 | -1.0094
433.3 | 50.5 | -1.0094
433.4 | 50.5 | -1.0094
433.5 | 50.5 | -1.0094
433.6 | 50.5 | -1.0094
433.7 | 50.5 | -1.0094
433.8 | 50.5 | -1.0094
433.9 | 50.5 | -1.0094
434 | 50.5 | -1.0096
434.1 | 50.5 | -1.0096
434.2 | 50.5 | -1.0096
434.3 | 50.5 | -1.0096
434.4 | 50.5 | -1.0096
434.5 | 50.5 | -1.0096
434.6 | 50.5 | -1.0096
434.7 | 50.5 | -1.0096
434.8 | 50.5 | -1.0096
434.9 | 50.5 | -1.0096
435 | 50.5 | -1.0096
435.1 | 50.5 | -1.0096
435.2 | 50.5 | -1.0096
435.3 | 50.5 | -1.0096
435.4 | 50.5 | -1.0096
435.5 | 50.5 | -1.0096
435.6 | 50.5 | -1.0096
435.7 | 50.5 | -1.0096
435.8 | 50.5 | -1.0096
435.9 | 50.5 | -1.0096
436 | 50.5 | -1.0096
436.1 | 50.5 | -1.0096
436.2 | 50.5 | -1.0096
436.3 | 50.5 | -1.0096
436.4 | 50.5 | -1.0096
436.5 | 50.5 | -1.0096
436.6 | 50.5 | -1.0096
436.7 | 50.5 | -1.0096
436.8 | 50.5 | -1.0096
436.9 | 50.5 | -1.0096
437 | 50.5 | -1.0096
437.1 | 50.5 | -1.0096
437.2 | 50.5 | -1.0096
437.3 | 50.5 | -1.0094
437.4 | 50.5 | -1.0094
437.5 | 50.5 | -1.0096
437.6 | 50.5 | -1.0096
437.7 | 50.5 | -1.0096
437.8 | 50.5 | -1.0096
437.9 | 50.5 | -1.0096
438 | 50.5 | -1.0096
438.1 | 50.5 | -1.0096
438.2 | 50.5 | -1.0096
438.3 | 50.5 | -1.0096
438.4 | 50.5 | -1.0096
438.5 | 50.5 | -1.0096
438.6 | 50.5 | -1.0096
438.7 | 50.5 | -1.0096
438.8 | 50.5 | -1.0096
438.9 | 50.5 | -1.0096
439 | 50.5 | -1.0096
439.1 | 50.5 | -1.0096
439.2 | 50.5 | -1.0096
439.3 | 50.5 | -1.0096
439.4 | 50.5 | -1.0096
439.5 | 50.5 | -1.0096
439.6 | 50.5 | -1.0096
439.7 | 50.5 | -1.0096
439.8 | 50.5 | -1.0096
439.9 | 50.5 | -1.0096
440 | 50.5 | -1.0096
440.1 | 50.5 | -1.0096
440.2 | 50.5 | -1.0096
440.3 | 50.5 | -1.0096
440.4 | 50.5 | -1.0096
440.5 | 50.5 | -1.0096
440.6 | 50.5 | -1.0096
440.7 | 50.5 | -1.0096
440.8 | 50.5 | -1.0096
440.9 | 50.5 | -1.0096
441 | 50.5 | -1.0096
441.1 | 50.5 | -1.0096
441.2 | 50.5 | -1.0096
441.3 | 50.5 | -1.0096
441.4 | 50.5 | -1.0096
441.5 | 50.5 | -1.0096
441.6 | 50.5 | -1.0096
441.7 | 50.5 | -1.0096
441.8 | 50.5 | -1.0096
441.9 | 50.5 | -1.0096
442 | 50.5 | -1.0096
442.1 | 50.5 | -1.0096
442.2 | 50.5 | -1.0096
442.3 | 50.5 | -1.0096
442.4 | 50.5 | -1.0096
442.5 | 50.5 | -1.0096
442.6 | 50.5 | -1.0096
442.7 | 50.5 | -1.0096
442.8 | 50.5 | -1.0096
442.9 | 50.5 | -1.0096
443 | 50.5 | -1.0096
443.1 | 50.5 | -1.0096
443.2 | 50.5 | -1.0096
443.3 | 50.5 | -1.0096
443.4 | 50.5 | -1.0096
443.5 | 50.5 | -1.0096
443.6 | 50.5 | -1.0096
443.7 | 50.5 | -1.0096
443.8 | 50.5 | -1.0096
443.9 | 50.5 | -1.0096
444 | 50.5 | -1.0096
444.1 | 50.5 | -1.0096
444.2 | 50.5 | -1.0096
444.3 | 50.5 | -1.0096
444.4 | 50.5 | -1.0096
444.5 | 50.5 | -1.0096
444.6 | 50.5 | -1.0096
444.7 | 50.5 | -1.0096
444.8 | 50.5 | -1.0096
444.9 | 50.5 | -1.0096
445 | 50.5 | -1.0096
445.1 | 50.5 | -1.0096
445.2 | 50.5 | -1.0096
445.3 | 50.5 | -1.0096
445.4 | 50.5 | -1.0096
445.5 | 50.5 | -1.0096
445.6 | 50.5 | -1.0096
445.7 | 50.5 | -1.0096
445.8 | 50.5 | -1.0096
445.9 | 50.5 | -1.0096
446 | 50.5 | -1.0096
446.1 | 50.5 | -1.0096
446.2 | 50.5 | -1.0096
446.3 | 50.5 | -1.0096
446.4 | 50.5 | -1.0096
446.5 | 50.5 | -1.0096
446.6 | 50.5 | -1.0096
446.7 | 50.5 | -1.0096
446.8 | 50.5 | -1.0096
446.9 | 50.5 | -1.0096
447 | 50.5 | -1.0096
447.1 | 50.5 | -1.0096
447.2 | 50.5 | -1.0096
447.3 | 50.5 | -1.0096
447.4 | 50.5 | -1.0096
447.5 | 50.5 | -1.0096
447.6 | 50.5 | -1.0096
447.7 | 50.5 | -1.0096
447.8 | 50.5 | -1.0096
447.9 | 50.5 | -1.0096
448 | 50.5 | -1.0096
448.1 | 50.5 | -1.0096
448.2 | 50.5 | -1.0096
448.3 | 50.5 | -1.0096
448.4 | 50.5 | -1.0096
448.5 | 50.5 | -1.0096
448.6 | 50.5 | -1.0096
448.7 | 50.5 | -1.0096
448.8 | 50.5 | -1.0096
448.9 | 50.5 | -1.0096
449 | 50.5 | -1.0096
449.1 | 50.5 | -1.0096
449.2 | 50.5 | -1.0096
449.3 | 50.5 | -1.0096
449.4 | 50.5 | -1.0096
449.5 | 50.5 | -1.0096
449.6 | 50.5 | -1.0096
449.7 | 50.5 | -1.0096
449.8 | 50.5 | -1.0096
449.9 | 50.5 | -1.0096
450 | 50.5 | -1.0096
450.1 | 50.5 | -1.0096
450.2 | 50.5 | -1.0096
450.3 | 50.5 | -1.0096
450.4 | 50.5 | -1.0096
450.5 | 50.5 | -1.0096
450.6 | 50.5 | -1.0096
450.7 | 50.5 | -1.0096
450.8 | 50.5 | -1.0096
450.9 | 50.5 | -1.0096
451 | 50.5 | -1.0096
451.1 | 50.5 | -1.0096
451.2 | 50.5 | -1.0096
451.3 | 50.5 | -1.0096
451.4 | 50.5 | -1.0096
451.5 | 50.5 | -1.0096
451.6 | 50.5 | -1.0096
451.7 | 50.5 | -1.0096
451.8 | 50.5 | -1.0096
451.9 | 50.5 | -1.0096
452 | 50.5 | -1.0096
452.1 | 50.5 | -1.0096
452.2 | 50.5 | -1.0096
452.3 | 50.5 | -1.0096
452.4 | 50.5 | -1.0096
452.5 | 50.5 | -1.0096
452.6 | 50.5 | -1.0096
452.7 | 50.5 | -1.0096
452.8 | 50.5 | -1.0096
452.9 | 50.5 | -1.0096
453 | 50.5 | -1.0096
453.1 | 50.5 | -1.0096
453.2 | 50.5 | -1.0096
453.3 | 50.5 | -1.0096
453.4 | 50.5 | -1.0096
453.5 | 50.5 | -1.0096
453.6 | 50.5 | -1.0096
453.7 | 50.5 | -1.0096
453.8 | 50.5 | -1.0096
453.9 | 50.5 | -1.0096
454 | 50.5 | -1.0096
454.1 | 50.5 | -1.0096
454.2 | 50.5 | -1.0096
454.3 | 50.5 | -1.0096
454.4 | 50.5 | -1.0096
454.5 | 50.5 | -1.0096
454.6 | 50.5 | -1.0096
454.7 | 50.5 | -1.0096
454.8 | 50.5 | -1.0096
454.9 | 50.5 | -1.0096
455 | 50.5 | -1.0096
455.1 | 50.5 | -1.0096
455.2 | 50.5 | -1.0096
455.3 | 50.5 | -1.0096
455.4 | 50.5 | -1.0096
455.5 | 50.5 | -1.0096
455.6 | 50.5 | -1.0096
455.7 | 50.5 | -1.0096
455.8 | 50.5 | -1.0096
455.9 | 50.5 | -1.0096
456 | 50.5 | -1.0096
456.1 | 50.5 | -1.0096
456.2 | 50.5 | -1.0094
456.3 | 50.5 | -1.0094
456.4 | 50.5 | -1.0094
456.5 | 50.5 | -1.0094
456.6 | 50.5 | -1.0094
456.7 | 50.5 | -1.0094
456.8 | 50.5 | -1.0094
456.9 | 50.5 | -1.0094
457 | 50.5 | -1.0094
457.1 | 50.5 | -1.0094
457.2 | 50.5 | -1.0096
457.3 | 50.5 | -1.0096
457.4 | 50.5 | -1.0096
457.5 | 50.5 | -1.0096
457.6 | 50.5 | -1.0096
457.7 | 50.5 | -1.0096
457.8 | 50.5 | -1.0096
457.9 | 50.5 | -1.0096
458 | 50.5 | -1.0096
458.1 | 50.5 | -1.0096
458.2 | 50.5 | -1.0096
458.3 | 50.5 | -1.0096
458.4 | 50.5 | -1.0096
458.5 | 50.5 | -1.0094
458.6 | 50.5 | -1.0094
458.7 | 50.5 | -1.0094
458.8 | 50.5 | -1.0094
458.9 | 50.5 | -1.0094
459 | 50.5 | -1.0094
459.1 | 50.5 | -1.0094
459.2 | 50.5 | -1.0094
459.3 | 50.5 | -1.0094
459.4 | 50.5 | -1.0094
459.5 | 50.5 | -1.0094
459.6 | 50.5 | -1.0094
459.7 | 50.5 | -1.0094
459.8 | 50.5 | -1.0094
459.9 | 50.5 | -1.0094
460 | 50.5 | -1.0094
460.1 | 50.5 | -1.0094
460.2 | 50.5 | -1.0094
460.3 | 50.5 | -1.0094
460.4 | 50.5 | -1.0094
460.5 | 50.5 | -1.0094
460.6 | 50.5 | -1.0094
460.7 | 50.5 | -1.0094
460.8 | 50.5 | -1.0094
460.9 | 50.5 | -1.0094
461 | 50.5 | -1.0094
461.1 | 50.5 | -1.0094
461.2 | 50.5 | -1.0094
461.3 | 50.5 | -1.0094
461.4 | 50.5 | -1.0094
461.5 | 50.5 | -1.0094
461.6 | 50.5 | -1.0094
461.7 | 50.5 | -1.0094
461.8 | 50.5 | -1.0094
461.9 | 50.5 | -1.0096
462 | 50.5 | -1.0096
462.1 | 50.5 | -1.0096
462.2 | 50.5 | -1.0096
462.3 | 50.5 | -1.0096
462.4 | 50.5 | -1.0096
462.5 | 50.5 | -1.0096
462.6 | 50.5 | -1.0096
462.7 | 50.5 | -1.0096
462.8 | 50.5 | -1.0098
462.9 | 50.5 | -1.0098
463 | 50.5 | -1.0098
463.1 | 50.5 | -1.0098
463.2 | 50.5 | -1.0098
463.3 | 50.5 | -1.0098
463.4 | 50.5 | -1.0098
463.5 | 50.5 | -1.0098
463.6 | 50.5 | -1.0098
463.7 | 50.5 | -1.0098
463.8 | 50.5 | -1.0098
463.9 | 50.5 | -1.0098
464 | 50.5 | -1.0098
464.1 | 50.5 | -1.0098
464.2 | 50.5 | -1.0098
464.3 | 50.5 | -1.0096
464.4 | 50.5 | -1.0096
464.5 | 50.5 | -1.0096
464.6 | 50.5 | -1.0096
464.7 | 50.5 | -1.0096
464.8 | 50.5 | -1.0096
464.9 | 50.5 | -1.0096
465 | 50.5 | -1.0096
465.1 | 50.5 | -1.0096
465.2 | 50.5 | -1.0094
465.3 | 50.5 | -1.0094
465.4 | 50.5 | -1.0094
465.5 | 50.5 | -1.0094
465.6 | 50.5 | -1.0094
465.7 | 50.5 | -1.0094
465.8 | 50.5 | -1.0094
465.9 | 50.5 | -1.0094
466 | 50.5 | -1.0094
466.1 | 50.5 | -1.0094
466.2 | 50.5 | -1.0094
466.3 | 50.5 | -1.0094
466.4 | 50.5 | -1.0094
466.5 | 50.5 | -1.0094
466.6 | 50.5 | -1.0092
466.7 | 50.5 | -1.0094
466.8 | 50.5 | -1.0094
466.9 | 50.5 | -1.0094
467 | 50.5 | -1.0094
467.1 | 50.5 | -1.0094
467.2 | 50.5 | -1.0094
467.3 | 50.5 | -1.0094
467.4 | 50.5 | -1.0094
467.5 | 50.5 | -1.0094
467.6 | 50.5 | -1.0094
467.7 | 50.5 | -1.0096
467.8 | 50.5 | -1.0098
467.9 | 50.5 | -1.0098
468 | 50.5 | -1.0098
468.1 | 50.5 | -1.0098
468.2 | 50.5 | -1.0098
468.3 | 50.5 | -1.0098
468.4 | 50.5 | -1.0098
468.5 | 50.5 | -1.0098
468.6 | 50.5 | -1.0098
468.7 | 50.5 | -1.0098
468.8 | 50.5 | -1.0098
468.9 | 50.5 | -1.0098
469 | 50.5 | -1.0096
469.1 | 50.5 | -1.0096
469.2 | 50.5 | -1.0096
469.3 | 50.5 | -1.0096
469.4 | 50.5 | -1.0096
469.5 | 50.5 | -1.0096
469.6 | 50.5 | -1.0096
469.7 | 50.5 | -1.0096
469.8 | 50.5 | -1.0096
469.9 | 50.5 | -1.0098
470 | 50.5 | -1.0098
470.1 | 50.5 | -1.0098
470.2 | 50.5 | -1.0098
470.3 | 50.5 | -1.0098
470.4 | 50.5 | -1.0098
470.5 | 50.5 | -1.0098
470.6 | 50.5 | -1.0098
470.7 | 50.5 | -1.0098
470.8 | 50.5 | -1.0098
470.9 | 50.5 | -1.0098
471 | 50.5 | -1.0098
471.1 | 50.5 | -1.0098
471.2 | 50.5 | -1.0098
471.3 | 50.5 | -1.0098
471.4 | 50.5 | -1.0096
471.5 | 50.5 | -1.0096
471.6 | 50.5 | -1.0096
471.7 | 50.5 | -1.0096
471.8 | 50.5 | -1.0096
471.9 | 50.5 | -1.0096
472 | 50.5 | -1.0096
472.1 | 50.5 | -1.0096
472.2 | 50.5 | -1.0094
472.3 | 50.5 | -1.0094
472.4 | 50.5 | -1.0094
472.5 | 50.5 | -1.0094
472.6 | 50.5 | -1.0094
472.7 | 50.5 | -1.0094
472.8 | 50.5 | -1.0094
472.9 | 50.5 | -1.0094
473 | 50.5 | -1.0094
473.1 | 50.5 | -1.0094
473.2 | 50.5 | -1.0094
473.3 | 50.5 | -1.0094
473.4 | 50.5 | -1.0094
473.5 | 50.5 | -1.0094
473.6 | 50.5 | -1.0094
473.7 | 50.5 | -1.0096
473.8 | 50.5 | -1.0096
473.9 | 50.5 | -1.0096
474 | 50.5 | -1.0096
474.1 | 50.5 | -1.0096
474.2 | 50.5 | -1.0096
474.3 | 50.5 | -1.0096
474.4 | 50.5 | -1.0096
474.5 | 50.5 | -1.0096
474.6 | 50.5 | -1.0096
474.7 | 50.5 | -1.0096
474.8 | 50.5 | -1.0096
474.9 | 50.5 | -1.0096
475 | 50.5 | -1.0096
475.1 | 50.5 | -1.0096
475.2 | 50.5 | -1.0096
475.3 | 50.5 | -1.0096
475.4 | 50.5 | -1.0096
475.5 | 50.5 | -1.0096
475.6 | 50.5 | -1.0096
475.7 | 50.5 | -1.0096
475.8 | 50.5 | -1.0096
475.9 | 50.5 | -1.0096
476 | 50.5 | -1.0096
476.1 | 50.5 | -1.0096
476.2 | 50.5 | -1.0096
476.3 | 50.5 | -1.0096
476.4 | 50.5 | -1.0096
476.5 | 50.5 | -1.0096
476.6 | 50.5 | -1.0096
476.7 | 50.5 | -1.0096
476.8 | 50.5 | -1.0096
476.9 | 50.5 | -1.0096
477 | 50.5 | -1.0098
477.1 | 50.5 | -1.0098
477.2 | 50.5 | -1.0098
477.3 | 50.5 | -1.0096
477.4 | 50.5 | -1.0096
477.5 | 50.5 | -1.0096
477.6 | 50.5 | -1.0096
477.7 | 50.5 | -1.0096
477.8 | 50.5 | -1.0096
477.9 | 50.5 | -1.0096
478 | 50.5 | -1.0096
478.1 | 50.5 | -1.0096
478.2 | 50.5 | -1.0098
478.3 | 50.5 | -1.0098
478.4 | 50.5 | -1.0098
478.5 | 50.5 | -1.0096
478.6 | 50.5 | -1.0096
478.7 | 50.5 | -1.0096
478.8 | 50.5 | -1.0096
478.9 | 50.5 | -1.0096
479 | 50.5 | -1.0096
479.1 | 50.5 | -1.0096
479.2 | 50.5 | -1.0096
479.3 | 50.5 | -1.0096
479.4 | 50.5 | -1.0096
479.5 | 50.5 | -1.0096
479.6 | 50.5 | -1.0096
479.7 | 50.5 | -1.0096
479.8 | 50.5 | -1.0096
479.9 | 50.5 | -1.0096
480 | 50.5 | -1.0096
480.1 | 50.5 | -1.0096
480.2 | 50.5 | -1.0096
480.3 | 50.5 | -1.0096
480.4 | 50.5 | -1.0096
480.5 | 50.5 | -1.0096
480.6 | 50.5 | -1.0094
480.7 | 50.5 | -1.0094
480.8 | 50.5 | -1.0094
480.9 | 50.5 | -1.0094
481 | 50.5 | -1.0094
481.1 | 50.5 | -1.0094
481.2 | 50.5 | -1.0094
481.3 | 50.5 | -1.0094
481.4 | 50.5 | -1.0094
481.5 | 50.5 | -1.0094
481.6 | 50.5 | -1.0094
481.7 | 50.5 | -1.0094
481.8 | 50.5 | -1.0094
481.9 | 50.5 | -1.0094
482 | 50.5 | -1.0094
482.1 | 50.5 | -1.0094
482.2 | 50.5 | -1.0094
482.3 | 50.5 | -1.0094
482.4 | 50.5 | -1.0094
482.5 | 50.5 | -1.0094
482.6 | 50.5 | -1.0094
482.7 | 50.5 | -1.0096
482.8 | 50.5 | -1.0096
482.9 | 50.5 | -1.0094
483 | 50.5 | -1.0096
483.1 | 50.5 | -1.0096
483.2 | 50.5 | -1.0096
483.3 | 50.5 | -1.0096
483.4 | 50.5 | -1.0096
483.5 | 50.5 | -1.0096
483.6 | 50.5 | -1.0096
483.7 | 50.5 | -1.0096
483.8 | 50.5 | -1.0096
483.9 | 50.5 | -1.0096
484 | 50.5 | -1.0096
484.1 | 50.5 | -1.0096
484.2 | 50.5 | -1.0096
484.3 | 50.5 | -1.0094
484.4 | 50.5 | -1.0094
484.5 | 50.5 | -1.0094
484.6 | 50.5 | -1.0094
484.7 | 50.5 | -1.0094
484.8 | 50.5 | -1.0094
484.9 | 50.5 | -1.0094
485 | 50.5 | -1.0094
485.1 | 50.5 | -1.0094
485.2 | 50.5 | -1.0094
485.3 | 50.5 | -1.0094
485.4 | 50.5 | -1.0094
485.5 | 50.5 | -1.0094
485.6 | 50.5 | -1.0094
485.7 | 50.5 | -1.0094
485.8 | 50.5 | -1.0094
485.9 | 50.5 | -1.0094
486 | 50.5 | -1.0094
486.1 | 50.5 | -1.0094
486.2 | 50.5 | -1.0094
486.3 | 50.5 | -1.0096
486.4 | 50.5 | -1.0096
486.5 | 50.5 | -1.0096
486.6 | 50.5 | -1.0096
486.7 | 50.5 | -1.0096
486.8 | 50.5 | -1.0096
486.9 | 50.5 | -1.0096
487 | 50.5 | -1.0096
487.1 | 50.5 | -1.0096
487.2 | 50.5 | -1.0096
487.3 | 50.5 | -1.0096
487.4 | 50.5 | -1.0096
487.5 | 50.5 | -1.0096
487.6 | 50.5 | -1.0096
487.7 | 50.5 | -1.0096
487.8 | 50.5 | -1.0098
487.9 | 50.5 | -1.0098
488 | 50.5 | -1.0098
488.1 | 50.5 | -1.0098
488.2 | 50.5 | -1.0098
488.3 | 50.5 | -1.0098
488.4 | 50.5 | -1.0098
488.5 | 50.5 | -1.0098
488.6 | 50.5 | -1.0096
488.7 | 50.5 | -1.0096
488.8 | 50.5 | -1.0096
488.9 | 50.5 | -1.0096
489 | 50.5 | -1.0096
489.1 | 50.5 | -1.0096
489.2 | 50.5 | -1.0096
489.3 | 50.5 | -1.0096
489.4 | 50.5 | -1.0096
489.5 | 50.5 | -1.0096
489.6 | 50.5 | -1.0096
489.7 | 50.5 | -1.0096
489.8 | 50.5 | -1.0094
489.9 | 50.5 | -1.0094
490 | 50.5 | -1.0094
490.1 | 50.5 | -1.0094
490.2 | 50.5 | -1.0092
490.3 | 50.5 | -1.0092
490.4 | 50.5 | -1.0092
490.5 | 50.5 | -1.0092
490.6 | 50.5 | -1.0092
490.7 | 50.5 | -1.0092
490.8 | 50.5 | -1.0092
490.9 | 50.5 | -1.0092
491 | 50.5 | -1.0092
491.1 | 50.5 | -1.0092
491.2 | 50.5 | -1.0092
491.3 | 50.5 | -1.0092
491.4 | 50.5 | -1.0092
491.5 | 50.5 | -1.0092
491.6 | 50.5 | -1.0092
491.7 | 50.5 | -1.0092
491.8 | 50.5 | -1.0092
491.9 | 50.5 | -1.0092
492 | 50.5 | -1.0094
492.1 | 50.5 | -1.0094
492.2 | 50.5 | -1.0094
492.3 | 50.5 | -1.0094
492.4 | 50.5 | -1.0096
492.5 | 50.5 | -1.0096
492.6 | 50.5 | -1.0096
492.7 | 50.5 | -1.0096
492.8 | 50.5 | -1.0096
492.9 | 50.5 | -1.0096
493 | 50.5 | -1.0096
493.1 | 50.5 | -1.0096
493.2 | 50.5 | -1.0096
493.3 | 50.5 | -1.0096
493.4 | 50.5 | -1.0096
493.5 | 50.5 | -1.0096
493.6 | 50.5 | -1.0096
493.7 | 50.5 | -1.0096
493.8 | 50.5 | -1.0096
493.9 | 50.5 | -1.0096
494 | 50.5 | -1.0096
494.1 | 50.5 | -1.0096
494.2 | 50.5 | -1.0096
494.3 | 50.5 | -1.0096
494.4 | 50.5 | -1.0096
494.5 | 50.5 | -1.0096
494.6 | 50.5 | -1.0096
494.7 | 50.5 | -1.0096
494.8 | 50.5 | -1.0096
494.9 | 50.5 | -1.0096
495 | 50.5 | -1.0096
495.1 | 50.5 | -1.0096
495.2 | 50.5 | -1.0096
495.3 | 50.5 | -1.0096
495.4 | 50.5 | -1.0096
495.5 | 50.5 | -1.0096
495.6 | 50.5 | -1.0096
495.7 | 50.5 | -1.0096
495.8 | 50.5 | -1.0096
495.9 | 50.5 | -1.0096
496 | 50.5 | -1.0096
496.1 | 50.5 | -1.0094
496.2 | 50.5 | -1.0094
496.3 | 50.5 | -1.0094
496.4 | 50.5 | -1.0094
496.5 | 50.5 | -1.0094
496.6 | 50.5 | -1.0094
496.7 | 50.5 | -1.0094
496.8 | 50.5 | -1.0094
496.9 | 50.5 | -1.0094
497 | 50.5 | -1.0094
497.1 | 50.5 | -1.0094
497.2 | 50.5 | -1.0094
497.3 | 50.5 | -1.0094
497.4 | 50.5 | -1.0094
497.5 | 50.5 | -1.0094
497.6 | 50.5 | -1.0094
497.7 | 50.5 | -1.0094
497.8 | 50.5 | -1.0094
497.9 | 50.5 | -1.0096
498 | 50.5 | -1.0096
498.1 | 50.5 | -1.0096
498.2 | 50.5 | -1.0096
498.3 | 50.5 | -1.0096
498.4 | 50.5 | -1.0096
498.5 | 50.5 | -1.0096
498.6 | 50.5 | -1.0096
498.7 | 50.5 | -1.0096
498.8 | 50.5 | -1.0096
498.9 | 50.5 | -1.0096
499 | 50.5 | -1.0096
499.1 | 50.5 | -1.0096
499.2 | 50.5 | -1.0096
499.3 | 50.5 | -1.0096
499.4 | 50.5 | -1.0096
499.5 | 50.5 | -1.0096
499.6 | 50.5 | -1.0096
499.7 | 50.5 | -1.0098
499.8 | 50.5 | -1.0098
499.9 | 50.5 | -1.0098
500 | 50.5 | -1.0098
500.1 | 50.5 | -1.0098
500.2 | 50.5 | -1.0098
500.3 | 50.5 | -1.0096
500.4 | 50.5 | -1.0096
500.5 | 50.5 | -1.0096
500.6 | 50.5 | -1.0096
500.7 | 50.5 | -1.0096
500.8 | 50.5 | -1.0096
500.9 | 50.5 | -1.0096
501 | 50.5 | -1.0096
501.1 | 50.5 | -1.0096
501.2 | 50.5 | -1.0096
501.3 | 50.5 | -1.0096
501.4 | 50.5 | -1.0096
501.5 | 50.5 | -1.0096
501.6 | 50.5 | -1.0096
501.7 | 50.5 | -1.0094
501.8 | 50.5 | -1.0094
501.9 | 50.5 | -1.0094
502 | 50.5 | -1.0094
502.1 | 50.5 | -1.0094
502.2 | 50.5 | -1.0094
502.3 | 50.5 | -1.0094
502.4 | 50.5 | -1.0094
502.5 | 50.5 | -1.0094
502.6 | 50.5 | -1.0094
502.7 | 50.5 | -1.0094
502.8 | 50.5 | -1.0094
502.9 | 50.5 | -1.0094
503 | 50.5 | -1.0094
503.1 | 50.5 | -1.0094
503.2 | 50.5 | -1.0094
503.3 | 50.5 | -1.0094
503.4 | 50.5 | -1.0094
503.5 | 50.5 | -1.0094
503.6 | 50.5 | -1.0094
503.7 | 50.5 | -1.0094
503.8 | 50.5 | -1.0094
503.9 | 50.5 | -1.0094
504 | 50.5 | -1.0096
504.1 | 50.5 | -1.0096
504.2 | 50.5 | -1.0096
504.3 | 50.5 | -1.0096
504.4 | 50.5 | -1.0096
504.5 | 50.5 | -1.0096
504.6 | 50.5 | -1.0096
504.7 | 50.5 | -1.0096
504.8 | 50.5 | -1.0096
504.9 | 50.5 | -1.0096
505 | 50.5 | -1.0096
505.1 | 50.5 | -1.0096
505.2 | 50.5 | -1.0096
505.3 | 50.5 | -1.0096
505.4 | 50.5 | -1.0098
505.5 | 50.5 | -1.0098
505.6 | 50.5 | -1.0098
505.7 | 50.5 | -1.0098
505.8 | 50.5 | -1.0098
505.9 | 50.5 | -1.0098
506 | 50.5 | -1.0098
506.1 | 50.5 | -1.0098
506.2 | 50.5 | -1.0098
506.3 | 50.5 | -1.0098
506.4 | 50.5 | -1.0098
506.5 | 50.5 | -1.0098
506.6 | 50.5 | -1.0098
506.7 | 50.5 | -1.0098
506.8 | 50.5 | -1.0098
506.9 | 50.5 | -1.0098
507 | 50.5 | -1.0098
507.1 | 50.5 | -1.0098
507.2 | 50.5 | -1.0098
507.3 | 50.5 | -1.0098
507.4 | 50.5 | -1.0096
507.5 | 50.5 | -1.0096
507.6 | 50.5 | -1.0096
507.7 | 50.5 | -1.0094
507.8 | 50.5 | -1.0094
507.9 | 50.5 | -1.0094
508 | 50.5 | -1.0094
508.1 | 50.5 | -1.0094
508.2 | 50.5 | -1.0094
508.3 | 50.5 | -1.0094
508.4 | 50.5 | -1.0094
508.5 | 50.5 | -1.0094
508.6 | 50.5 | -1.0094
508.7 | 50.5 | -1.0094
508.8 | 50.5 | -1.0094
508.9 | 50.5 | -1.0094
509 | 50.5 | -1.0094
509.1 | 50.5 | -1.0094
509.2 | 50.5 | -1.0094
509.3 | 50.5 | -1.0094
509.4 | 50.5 | -1.0094
509.5 | 50.5 | -1.0094
509.6 | 50.5 | -1.0094
509.7 | 50.5 | -1.0094
509.8 | 50.5 | -1.0094
509.9 | 50.5 | -1.0094
510 | 50.5 | -1.0094
510.1 | 50.5 | -1.0094
510.2 | 50.5 | -1.0094
510.3 | 50.5 | -1.0094
510.4 | 50.5 | -1.0094
510.5 | 50.5 | -1.0094
510.6 | 50.5 | -1.0094
510.7 | 50.5 | -1.0096
510.8 | 50.5 | -1.0096
510.9 | 50.5 | -1.0096
511 | 50.5 | -1.0096
511.1 | 50.5 | -1.0096
511.2 | 50.5 | -1.0096
511.3 | 50.5 | -1.0098
511.4 | 50.5 | -1.0098
511.5 | 50.5 | -1.0098
511.6 | 50.5 | -1.0098
511.7 | 50.5 | -1.0098
511.8 | 50.5 | -1.0098
511.9 | 50.5 | -1.0098
512 | 50.5 | -1.0098
512.1 | 50.5 | -1.0098
512.2 | 50.5 | -1.0098
512.3 | 50.5 | -1.0096
512.4 | 50.5 | -1.0096
512.5 | 50.5 | -1.0096
512.6 | 50.5 | -1.0096
512.7 | 50.5 | -1.0096
512.8 | 50.5 | -1.0096
512.9 | 50.5 | -1.0096
513 | 50.5 | -1.0096
513.1 | 50.5 | -1.0096
513.2 | 50.5 | -1.0096
513.3 | 50.5 | -1.0096
513.4 | 50.5 | -1.0096
513.5 | 50.5 | -1.0096
513.6 | 50.5 | -1.0096
513.7 | 50.5 | -1.0096
513.8 | 50.5 | -1.0096
513.9 | 50.5 | -1.0096
514 | 50.5 | -1.0096
514.1 | 50.5 | -1.0096
514.2 | 50.5 | -1.0096
514.3 | 50.5 | -1.0096
514.4 | 50.5 | -1.0096
514.5 | 50.5 | -1.0096
514.6 | 50.5 | -1.0096
514.7 | 50.5 | -1.0096
514.8 | 50.5 | -1.0096
514.9 | 50.5 | -1.0096
515 | 50.5 | -1.0096
515.1 | 50.5 | -1.0096
515.2 | 50.5 | -1.0096
515.3 | 50.5 | -1.0096
515.4 | 50.5 | -1.0096
515.5 | 50.5 | -1.0096
515.6 | 50.5 | -1.0096
515.7 | 50.5 | -1.0096
515.8 | 50.5 | -1.0096
515.9 | 50.5 | -1.0096
516 | 50.5 | -1.0096
516.1 | 50.5 | -1.0096
516.2 | 50.5 | -1.0096
516.3 | 50.5 | -1.0096
516.4 | 50.5 | -1.0096
516.5 | 50.5 | -1.0096
516.6 | 50.5 | -1.0094
516.7 | 50.5 | -1.0094
516.8 | 50.5 | -1.0094
516.9 | 50.5 | -1.0094
517 | 50.5 | -1.0094
517.1 | 50.5 | -1.0094
517.2 | 50.5 | -1.0094
517.3 | 50.5 | -1.0094
517.4 | 50.5 | -1.0094
517.5 | 50.5 | -1.0094
517.6 | 50.5 | -1.0096
517.7 | 50.5 | -1.0096
517.8 | 50.5 | -1.0096
517.9 | 50.5 | -1.0096
518 | 50.5 | -1.0096
518.1 | 50.5 | -1.0096
518.2 | 50.5 | -1.0096
518.3 | 50.5 | -1.0096
518.4 | 50.5 | -1.0096
518.5 | 50.5 | -1.0096
518.6 | 50.5 | -1.0096
518.7 | 50.5 | -1.0096
518.8 | 50.5 | -1.0096
518.9 | 50.5 | -1.0096
519 | 50.5 | -1.0096
519.1 | 50.5 | -1.0096
519.2 | 50.5 | -1.0096
519.3 | 50.5 | -1.0096
519.4 | 50.5 | -1.0096
519.5 | 50.5 | -1.0096
519.6 | 50.5 | -1.0096
519.7 | 50.5 | -1.0096
519.8 | 50.5 | -1.0096
519.9 | 50.5 | -1.0096
520 | 50.5 | -1.0096
520.1 | 50.5 | -1.0096
520.2 | 50.5 | -1.0096
520.3 | 50.5 | -1.0096
520.4 | 50.5 | -1.0096
520.5 | 50.5 | -1.0096
520.6 | 50.5 | -1.0096
520.7 | 50.5 | -1.0096
520.8 | 50.5 | -1.0096
520.9 | 50.5 | -1.0096
521 | 50.5 | -1.0096
521.1 | 50.5 | -1.0096
521.2 | 50.5 | -1.0096
521.3 | 50.5 | -1.0096
521.4 | 50.5 | -1.0096
521.5 | 50.5 | -1.0096
521.6 | 50.5 | -1.0096
521.7 | 50.5 | -1.0096
521.8 | 50.5 | -1.0096
521.9 | 50.5 | -1.0096
522 | 50.5 | -1.0096
522.1 | 50.5 | -1.0096
522.2 | 50.5 | -1.0096
522.3 | 50.5 | -1.0096
522.4 | 50.5 | -1.0096
522.5 | 50.5 | -1.0096
522.6 | 50.5 | -1.0096
522.7 | 50.5 | -1.0096
522.8 | 50.5 | -1.0096
522.9 | 50.5 | -1.0096
523 | 50.5 | -1.0096
523.1 | 50.5 | -1.0096
523.2 | 50.5 | -1.0096
523.3 | 50.5 | -1.0096
523.4 | 50.5 | -1.0096
523.5 | 50.5 | -1.0096
523.6 | 50.5 | -1.0096
523.7 | 50.5 | -1.0096
523.8 | 50.5 | -1.0096
523.9 | 50.5 | -1.0096
524 | 50.5 | -1.0096
524.1 | 50.5 | -1.0094
524.2 | 50.5 | -1.0094
524.3 | 50.5 | -1.0094
524.4 | 50.5 | -1.0094
524.5 | 50.5 | -1.0094
524.6 | 50.5 | -1.0094
524.7 | 50.5 | -1.0094
524.8 | 50.5 | -1.0094
524.9 | 50.5 | -1.0094
525 | 50.5 | -1.0094
525.1 | 50.5 | -1.0094
525.2 | 50.5 | -1.0094
525.3 | 50.5 | -1.0094
525.4 | 50.5 | -1.0094
525.5 | 50.5 | -1.0094
525.6 | 50.5 | -1.0094
525.7 | 50.5 | -1.0094
525.8 | 50.5 | -1.0094
525.9 | 50.5 | -1.0094
526 | 50.5 | -1.0094
526.1 | 50.5 | -1.0094
526.2 | 50.5 | -1.0094
526.3 | 50.5 | -1.0094
526.4 | 50.5 | -1.0096
526.5 | 50.5 | -1.0096
526.6 | 50.5 | -1.0096
526.7 | 50.5 | -1.0096
526.8 | 50.5 | -1.0096
526.9 | 50.5 | -1.0096
527 | 50.5 | -1.0096
527.1 | 50.5 | -1.0096
527.2 | 50.5 | -1.0096
527.3 | 50.5 | -1.0096
527.4 | 50.5 | -1.0096
527.5 | 50.5 | -1.0096
527.6 | 50.5 | -1.0096
527.7 | 50.5 | -1.0096
527.8 | 50.5 | -1.0096
527.9 | 50.5 | -1.0096
528 | 50.5 | -1.0096
528.1 | 50.5 | -1.0096
528.2 | 50.5 | -1.0096
528.3 | 50.5 | -1.0096
528.4 | 50.5 | -1.0096
528.5 | 50.5 | -1.0096
528.6 | 50.5 | -1.0096
528.7 | 50.5 | -1.0096
528.8 | 50.5 | -1.0096
528.9 | 50.5 | -1.0096
529 | 50.5 | -1.0096
529.1 | 50.5 | -1.0096
529.2 | 50.5 | -1.0096
529.3 | 50.5 | -1.0096
529.4 | 50.5 | -1.0096
529.5 | 50.5 | -1.0096
529.6 | 50.5 | -1.0096
529.7 | 50.5 | -1.0096
529.8 | 50.5 | -1.0096
529.9 | 50.5 | -1.0096
530 | 50.5 | -1.0096
530.1 | 50.5 | -1.0096
530.2 | 50.5 | -1.0096
530.3 | 50.5 | -1.0096
530.4 | 50.5 | -1.0096
530.5 | 50.5 | -1.0096
530.6 | 50.5 | -1.0096
530.7 | 50.5 | -1.0096
530.8 | 50.5 | -1.0096
530.9 | 50.5 | -1.0096
531 | 50.5 | -1.0096
531.1 | 50.5 | -1.0096
531.2 | 50.5 | -1.0096
531.3 | 50.5 | -1.0096
531.4 | 50.5 | -1.0096
531.5 | 50.5 | -1.0096
531.6 | 50.5 | -1.0096
531.7 | 50.5 | -1.0096
531.8 | 50.5 | -1.0096
531.9 | 50.5 | -1.0096
532 | 50.5 | -1.0096
532.1 | 50.5 | -1.0096
532.2 | 50.5 | -1.0096
532.3 | 50.5 | -1.0096
532.4 | 50.5 | -1.0096
532.5 | 50.5 | -1.0096
532.6 | 50.5 | -1.0096
532.7 | 50.5 | -1.0096
532.8 | 50.5 | -1.0096
532.9 | 50.5 | -1.0096
533 | 50.5 | -1.0096
533.1 | 50.5 | -1.0096
533.2 | 50.5 | -1.0096
533.3 | 50.5 | -1.0096
533.4 | 50.5 | -1.0096
533.5 | 50.5 | -1.0096
533.6 | 50.5 | -1.0096
533.7 | 50.5 | -1.0096
533.8 | 50.5 | -1.0096
533.9 | 50.5 | -1.0096
534 | 50.5 | -1.0096
534.1 | 50.5 | -1.0096
534.2 | 50.5 | -1.0096
534.3 | 50.5 | -1.0096
534.4 | 50.5 | -1.0096
534.5 | 50.5 | -1.0096
534.6 | 50.5 | -1.0096
534.7 | 50.5 | -1.0096
534.8 | 50.5 | -1.0096
534.9 | 50.5 | -1.0096
535 | 50.5 | -1.0096
535.1 | 50.5 | -1.0096
535.2 | 50.5 | -1.0096
535.3 | 50.5 | -1.0096
535.4 | 50.5 | -1.0096
535.5 | 50.5 | -1.0096
535.6 | 50.5 | -1.0096
535.7 | 50.5 | -1.0096
535.8 | 50.5 | -1.0096
535.9 | 50.5 | -1.0096
536 | 50.5 | -1.0096
536.1 | 50.5 | -1.0096
536.2 | 50.5 | -1.0096
536.3 | 50.5 | -1.0096
536.4 | 50.5 | -1.0096
536.5 | 50.5 | -1.0096
536.6 | 50.5 | -1.0096
536.7 | 50.5 | -1.0096
536.8 | 50.5 | -1.0096
536.9 | 50.5 | -1.0096
537 | 50.5 | -1.0096
537.1 | 50.5 | -1.0096
537.2 | 50.5 | -1.0096
537.3 | 50.5 | -1.0096
537.4 | 50.5 | -1.0096
537.5 | 50.5 | -1.0096
537.6 | 50.5 | -1.0096
537.7 | 50.5 | -1.0096
537.8 | 50.5 | -1.0096
537.9 | 50.5 | -1.0096
538 | 50.5 | -1.0096
538.1 | 50.5 | -1.0096
538.2 | 50.5 | -1.0096
538.3 | 50.5 | -1.0096
538.4 | 50.5 | -1.0096
538.5 | 50.5 | -1.0096
538.6 | 50.5 | -1.0096
538.7 | 50.5 | -1.0096
538.8 | 50.5 | -1.0096
538.9 | 50.5 | -1.0096
539 | 50.5 | -1.0096
539.1 | 50.5 | -1.0096
539.2 | 50.5 | -1.0098
539.3 | 50.5 | -1.0098
539.4 | 50.5 | -1.0096
539.5 | 50.5 | -1.0096
539.6 | 50.5 | -1.0096
539.7 | 50.5 | -1.0096
539.8 | 50.5 | -1.0096
539.9 | 50.5 | -1.0096
540 | 50.5 | -1.0096
540.1 | 50.5 | -1.0096
540.2 | 50.5 | -1.0096
540.3 | 50.5 | -1.0096
540.4 | 50.5 | -1.0096
540.5 | 50.5 | -1.0096
540.6 | 50.5 | -1.0096
540.7 | 50.5 | -1.0096
540.8 | 50.5 | -1.0096
540.9 | 50.5 | -1.0096
541 | 50.5 | -1.0096
541.1 | 50.5 | -1.0096
541.2 | 50.5 | -1.0096
541.3 | 50.5 | -1.0096
541.4 | 50.5 | -1.0096
541.5 | 50.5 | -1.0096
541.6 | 50.5 | -1.0096
541.7 | 50.5 | -1.0094
541.8 | 50.5 | -1.0094
541.9 | 50.5 | -1.0094
542 | 50.5 | -1.0094
542.1 | 50.5 | -1.0094
542.2 | 50.5 | -1.0094
542.3 | 50.5 | -1.0094
542.4 | 50.5 | -1.0094
542.5 | 50.5 | -1.0094
542.6 | 50.5 | -1.0094
542.7 | 50.5 | -1.0094
542.8 | 50.5 | -1.0094
542.9 | 50.5 | -1.0094
543 | 50.5 | -1.0094
543.1 | 50.5 | -1.0094
543.2 | 50.5 | -1.0094
543.3 | 50.5 | -1.0094
543.4 | 50.5 | -1.0094
543.5 | 50.5 | -1.0094
543.6 | 50.5 | -1.0094
543.7 | 50.5 | -1.0094
543.8 | 50.5 | -1.0094
543.9 | 50.5 | -1.0094
544 | 50.5 | -1.0096
544.1 | 50.5 | -1.0096
544.2 | 50.5 | -1.0096
544.3 | 50.5 | -1.0096
544.4 | 50.5 | -1.0096
544.5 | 50.5 | -1.0096
544.6 | 50.5 | -1.0096
544.7 | 50.5 | -1.0096
544.8 | 50.5 | -1.0096
544.9 | 50.5 | -1.0096
545 | 50.5 | -1.0096
545.1 | 50.5 | -1.0096
545.2 | 50.5 | -1.0096
545.3 | 50.5 | -1.0096
545.4 | 50.5 | -1.0096
545.5 | 50.5 | -1.0096
545.6 | 50.5 | -1.0096
545.7 | 50.5 | -1.0096
545.8 | 50.5 | -1.0096
545.9 | 50.5 | -1.0096
546 | 50.5 | -1.0096
546.1 | 50.5 | -1.0096
546.2 | 50.5 | -1.0096
546.3 | 50.5 | -1.0096
546.4 | 50.5 | -1.0096
546.5 | 50.5 | -1.0096
546.6 | 50.5 | -1.0096
546.7 | 50.5 | -1.0096
546.8 | 50.5 | -1.0096
546.9 | 50.5 | -1.0098
547 | 50.5 | -1.0098
547.1 | 50.5 | -1.0098
547.2 | 50.5 | -1.0098
547.3 | 50.5 | -1.0098
547.4 | 50.5 | -1.0096
547.5 | 50.5 | -1.0096
547.6 | 50.5 | -1.0096
547.7 | 50.5 | -1.0096
547.8 | 50.5 | -1.0096
547.9 | 50.5 | -1.0096
548 | 50.5 | -1.0096
548.1 | 50.5 | -1.0096
548.2 | 50.5 | -1.0096
548.3 | 50.5 | -1.0096
548.4 | 50.5 | -1.0096
548.5 | 50.5 | -1.0096
548.6 | 50.5 | -1.0096
548.7 | 50.5 | -1.0096
548.8 | 50.5 | -1.0096
548.9 | 50.5 | -1.0096
549 | 50.5 | -1.0096
549.1 | 50.5 | -1.0096
549.2 | 50.5 | -1.0096
549.3 | 50.5 | -1.0096
549.4 | 50.5 | -1.0096
549.5 | 50.5 | -1.0096
549.6 | 50.5 | -1.0096
549.7 | 50.5 | -1.0096
549.8 | 50.5 | -1.0096
549.9 | 50.5 | -1.0096
550 | 50.5 | -1.0096
550.1 | 50.5 | -1.0096
550.2 | 50.5 | -1.0096
550.3 | 50.5 | -1.0096
550.4 | 50.5 | -1.0096
550.5 | 50.5 | -1.0096
550.6 | 50.5 | -1.0096
550.7 | 50.5 | -1.0096
550.8 | 50.5 | -1.0096
550.9 | 50.5 | -1.0096
551 | 50.5 | -1.0096
551.1 | 50.5 | -1.0096
551.2 | 50.5 | -1.0096
551.3 | 50.5 | -1.0096
551.4 | 50.5 | -1.0096
551.5 | 50.5 | -1.0096
551.6 | 50.5 | -1.0096
551.7 | 50.5 | -1.0096
551.8 | 50.5 | -1.0096
551.9 | 50.5 | -1.0096
552 | 50.5 | -1.0096
552.1 | 50.5 | -1.0094
552.2 | 50.5 | -1.0094
552.3 | 50.5 | -1.0094
552.4 | 50.5 | -1.0094
552.5 | 50.5 | -1.0094
552.6 | 50.5 | -1.0096
552.7 | 50.5 | -1.0096
552.8 | 50.5 | -1.0096
552.9 | 50.5 | -1.0096
553 | 50.5 | -1.0096
553.1 | 50.5 | -1.0096
553.2 | 50.5 | -1.0096
553.3 | 50.5 | -1.0096
553.4 | 50.5 | -1.0094
553.5 | 50.5 | -1.0094
553.6 | 50.5 | -1.0094
553.7 | 50.5 | -1.0094
553.8 | 50.5 | -1.0094
553.9 | 50.5 | -1.0094
554 | 50.5 | -1.0094
554.1 | 50.5 | -1.0094
554.2 | 50.5 | -1.0094
554.3 | 50.5 | -1.0094
554.4 | 50.5 | -1.0096
554.5 | 50.5 | -1.0096
554.6 | 50.5 | -1.0096
554.7 | 50.5 | -1.0096
554.8 | 50.5 | -1.0096
554.9 | 50.5 | -1.0096
555 | 50.5 | -1.0096
555.1 | 50.5 | -1.0096
555.2 | 50.5 | -1.0096
555.3 | 50.5 | -1.0096
555.4 | 50.5 | -1.0096
555.5 | 50.5 | -1.0096
555.6 | 50.5 | -1.0096
555.7 | 50.5 | -1.0096
555.8 | 50.5 | -1.0096
555.9 | 50.5 | -1.0096
556 | 50.5 | -1.0096
556.1 | 50.5 | -1.0096
556.2 | 50.5 | -1.0096
556.3 | 50.5 | -1.0096
556.4 | 50.5 | -1.0096
556.5 | 50.5 | -1.0096
556.6 | 50.5 | -1.0096
556.7 | 50.5 | -1.0096
556.8 | 50.5 | -1.0096
556.9 | 50.5 | -1.0096
557 | 50.5 | -1.0096
557.1 | 50.5 | -1.0096
557.2 | 50.5 | -1.0096
557.3 | 50.5 | -1.0096
557.4 | 50.5 | -1.0096
557.5 | 50.5 | -1.0096
557.6 | 50.5 | -1.0096
557.7 | 50.5 | -1.0096
557.8 | 50.5 | -1.0096
557.9 | 50.5 | -1.0096
558 | 50.5 | -1.0096
558.1 | 50.5 | -1.0096
558.2 | 50.5 | -1.0096
558.3 | 50.5 | -1.0096
558.4 | 50.5 | -1.0096
558.5 | 50.5 | -1.0096
558.6 | 50.5 | -1.0096
558.7 | 50.5 | -1.0096
558.8 | 50.5 | -1.0096
558.9 | 50.5 | -1.0096
559 | 50.5 | -1.0096
559.1 | 50.5 | -1.0096
559.2 | 50.5 | -1.0096
559.3 | 50.5 | -1.0094
559.4 | 50.5 | -1.0094
559.5 | 50.5 | -1.0094
559.6 | 50.5 | -1.0094
559.7 | 50.5 | -1.0094
559.8 | 50.5 | -1.0094
559.9 | 50.5 | -1.0094
560 | 50.5 | -1.0094
560.1 | 50.5 | -1.0094
560.2 | 50.5 | -1.0094
560.3 | 50.5 | -1.0096
560.4 | 50.5 | -1.0096
560.5 | 50.5 | -1.0096
560.6 | 50.5 | -1.0096
560.7 | 50.5 | -1.0096
560.8 | 50.5 | -1.0096
560.9 | 50.5 | -1.0096
561 | 50.5 | -1.0096
561.1 | 50.5 | -1.0096
561.2 | 50.5 | -1.0096
561.3 | 50.5 | -1.0096
561.4 | 50.5 | -1.0096
561.5 | 50.5 | -1.0096
561.6 | 50.5 | -1.0096
561.7 | 50.5 | -1.0096
561.8 | 50.5 | -1.0096
561.9 | 50.5 | -1.0096
562 | 50.5 | -1.0096
562.1 | 50.5 | -1.0096
562.2 | 50.5 | -1.0096
562.3 | 50.5 | -1.0096
562.4 | 50.5 | -1.0096
562.5 | 50.5 | -1.0096
562.6 | 50.5 | -1.0096
562.7 | 50.5 | -1.0096
562.8 | 50.5 | -1.0096
562.9 | 50.5 | -1.0096
563 | 50.5 | -1.0096
563.1 | 50.5 | -1.0096
563.2 | 50.5 | -1.0096
563.3 | 50.5 | -1.0096
563.4 | 50.5 | -1.0096
563.5 | 50.5 | -1.0096
563.6 | 50.5 | -1.0096
563.7 | 50.5 | -1.0096
563.8 | 50.5 | -1.0096
563.9 | 50.5 | -1.0096
564 | 50.5 | -1.0096
564.1 | 50.5 | -1.0096
564.2 | 50.5 | -1.0096
564.3 | 50.5 | -1.0096
564.4 | 50.5 | -1.0096
564.5 | 50.5 | -1.0096
564.6 | 50.5 | -1.0096
564.7 | 50.5 | -1.0096
564.8 | 50.5 | -1.0096
564.9 | 50.5 | -1.0096
565 | 50.5 | -1.0094
565.1 | 50.5 | -1.0094
565.2 | 50.5 | -1.0094
565.3 | 50.5 | -1.0094
565.4 | 50.5 | -1.0094
565.5 | 50.5 | -1.0094
565.6 | 50.5 | -1.0094
565.7 | 50.5 | -1.0094
565.8 | 50.5 | -1.0094
565.9 | 50.5 | -1.0094
566 | 50.5 | -1.0094
566.1 | 50.5 | -1.0094
566.2 | 50.5 | -1.0094
566.3 | 50.5 | -1.0094
566.4 | 50.5 | -1.0094
566.5 | 50.5 | -1.0094
566.6 | 50.5 | -1.0094
566.7 | 50.5 | -1.0094
566.8 | 50.5 | -1.0094
566.9 | 50.5 | -1.0094
567 | 50.5 | -1.0094
567.1 | 50.5 | -1.0094
567.2 | 50.5 | -1.0094
567.3 | 50.5 | -1.0094
567.4 | 50.5 | -1.0094
567.5 | 50.5 | -1.0094
567.6 | 50.5 | -1.0094
567.7 | 50.5 | -1.0094
567.8 | 50.5 | -1.0094
567.9 | 50.5 | -1.0094
568 | 50.5 | -1.0094
568.1 | 50.5 | -1.0094
568.2 | 50.5 | -1.0094
568.3 | 50.5 | -1.0094
568.4 | 50.5 | -1.0096
568.5 | 50.5 | -1.0096
568.6 | 50.5 | -1.0096
568.7 | 50.5 | -1.0096
568.8 | 50.5 | -1.0096
568.9 | 50.5 | -1.0096
569 | 50.5 | -1.0096
569.1 | 50.5 | -1.0096
569.2 | 50.5 | -1.0096
569.3 | 50.5 | -1.0096
569.4 | 50.5 | -1.0096
569.5 | 50.5 | -1.0096
569.6 | 50.5 | -1.0096
569.7 | 50.5 | -1.0096
569.8 | 50.5 | -1.0096
569.9 | 50.5 | -1.0096
570 | 50.5 | -1.0096
570.1 | 50.5 | -1.0096
570.2 | 50.5 | -1.0096
570.3 | 50.5 | -1.0096
570.4 | 50.5 | -1.0096
570.5 | 50.5 | -1.0096
570.6 | 50.5 | -1.0096
570.7 | 50.5 | -1.0096
570.8 | 50.5 | -1.0096
570.9 | 50.5 | -1.0094
571 | 50.5 | -1.0094
571.1 | 50.5 | -1.0094
571.2 | 50.5 | -1.0094
571.3 | 50.5 | -1.0094
571.4 | 50.5 | -1.0094
571.5 | 50.5 | -1.0094
571.6 | 50.5 | -1.0094
571.7 | 50.5 | -1.0094
571.8 | 50.5 | -1.0094
571.9 | 50.5 | -1.0094
572 | 50.5 | -1.0094
572.1 | 50.5 | -1.0096
572.2 | 50.5 | -1.0096
572.3 | 50.5 | -1.0096
572.4 | 50.5 | -1.0096
572.5 | 50.5 | -1.0096
572.6 | 50.5 | -1.0096
572.7 | 50.5 | -1.0096
572.8 | 50.5 | -1.0096
572.9 | 50.5 | -1.0096
573 | 50.5 | -1.0096
573.1 | 50.5 | -1.0096
573.2 | 50.5 | -1.0096
573.3 | 50.5 | -1.0096
573.4 | 50.5 | -1.0096
573.5 | 50.5 | -1.0096
573.6 | 50.5 | -1.0096
573.7 | 50.5 | -1.0096
573.8 | 50.5 | -1.0096
573.9 | 50.5 | -1.0096
574 | 50.5 | -1.0096
574.1 | 50.5 | -1.0096
574.2 | 50.5 | -1.0096
574.3 | 50.5 | -1.0096
574.4 | 50.5 | -1.0096
574.5 | 50.5 | -1.0096
574.6 | 50.5 | -1.0096
574.7 | 50.5 | -1.0096
574.8 | 50.5 | -1.0096
574.9 | 50.5 | -1.0096
575 | 50.5 | -1.0096
575.1 | 50.5 | -1.0096
575.2 | 50.5 | -1.0096
575.3 | 50.5 | -1.0096
575.4 | 50.5 | -1.0096
575.5 | 50.5 | -1.0096
575.6 | 50.5 | -1.0096
575.7 | 50.5 | -1.0096
575.8 | 50.5 | -1.0096
575.9 | 50.5 | -1.0096
576 | 50.5 | -1.0096
576.1 | 50.5 | -1.0096
576.2 | 50.5 | -1.0096
576.3 | 50.5 | -1.0096
576.4 | 50.5 | -1.0096
576.5 | 50.5 | -1.0096
576.6 | 50.5 | -1.0096
576.7 | 50.5 | -1.0096
576.8 | 50.5 | -1.0096
576.9 | 50.5 | -1.0094
577 | 50.5 | -1.0094
577.1 | 50.5 | -1.0094
577.2 | 50.5 | -1.0094
577.3 | 50.5 | -1.0094
577.4 | 50.5 | -1.0094
577.5 | 50.5 | -1.0094
577.6 | 50.5 | -1.0094
577.7 | 50.5 | -1.0094
577.8 | 50.5 | -1.0094
577.9 | 50.5 | -1.0096
578 | 50.5 | -1.0096
578.1 | 50.5 | -1.0096
578.2 | 50.5 | -1.0096
578.3 | 50.5 | -1.0096
578.4 | 50.5 | -1.0096
578.5 | 50.5 | -1.0096
578.6 | 50.5 | -1.0096
578.7 | 50.5 | -1.0096
578.8 | 50.5 | -1.0096
578.9 | 50.5 | -1.0096
579 | 50.5 | -1.0096
579.1 | 50.5 | -1.0096
579.2 | 50.5 | -1.0096
579.3 | 50.5 | -1.0096
579.4 | 50.5 | -1.0096
579.5 | 50.5 | -1.0096
579.6 | 50.5 | -1.0096
579.7 | 50.5 | -1.0096
579.8 | 50.5 | -1.0096
579.9 | 50.5 | -1.0096
580 | 50.5 | -1.0096
580.1 | 50.5 | -1.0096
580.2 | 50.5 | -1.0094
580.3 | 50.5 | -1.0096
580.4 | 50.5 | -1.0096
580.5 | 50.5 | -1.0096
580.6 | 50.5 | -1.0096
580.7 | 50.5 | -1.0096
580.8 | 50.5 | -1.0096
580.9 | 50.5 | -1.0096
581 | 50.5 | -1.0096
581.1 | 50.5 | -1.0096
581.2 | 50.5 | -1.0096
581.3 | 50.5 | -1.0096
581.4 | 50.5 | -1.0096
581.5 | 50.5 | -1.0096
581.6 | 50.5 | -1.0096
581.7 | 50.5 | -1.0096
581.8 | 50.5 | -1.0096
581.9 | 50.5 | -1.0096
582 | 50.5 | -1.0096
582.1 | 50.5 | -1.0096
582.2 | 50.5 | -1.0096
582.3 | 50.5 | -1.0096
582.4 | 50.5 | -1.0096
582.5 | 50.5 | -1.0096
582.6 | 50.5 | -1.0096
582.7 | 50.5 | -1.0096
582.8 | 50.5 | -1.0096
582.9 | 50.5 | -1.0096
583 | 50.5 | -1.0096
583.1 | 50.5 | -1.0096
583.2 | 50.5 | -1.0096
583.3 | 50.5 | -1.0096
583.4 | 50.5 | -1.0096
583.5 | 50.5 | -1.0096
583.6 | 50.5 | -1.0096
583.7 | 50.5 | -1.0094
583.8 | 50.5 | -1.0094
583.9 | 50.5 | -1.0094
584 | 50.5 | -1.0094
584.1 | 50.5 | -1.0094
584.2 | 50.5 | -1.0094
584.3 | 50.5 | -1.0094
584.4 | 50.5 | -1.0094
584.5 | 50.5 | -1.0094
584.6 | 50.5 | -1.0094
584.7 | 50.5 | -1.0094
584.8 | 50.5 | -1.0096
584.9 | 50.5 | -1.0096
585 | 50.5 | -1.0096
585.1 | 50.5 | -1.0094
585.2 | 50.5 | -1.0094
585.3 | 50.5 | -1.0094
585.4 | 50.5 | -1.0094
585.5 | 50.5 | -1.0094
585.6 | 50.5 | -1.0094
585.7 | 50.5 | -1.0094
585.8 | 50.5 | -1.0094
585.9 | 50.5 | -1.0094
586 | 50.5 | -1.0094
586.1 | 50.5 | -1.0096
586.2 | 50.5 | -1.0096
586.3 | 50.5 | -1.0096
586.4 | 50.5 | -1.0096
586.5 | 50.5 | -1.0096
586.6 | 50.5 | -1.0096
586.7 | 50.5 | -1.0096
586.8 | 50.5 | -1.0096
586.9 | 50.5 | -1.0096
587 | 50.5 | -1.0096
587.1 | 50.5 | -1.0096
587.2 | 50.5 | -1.0096
587.3 | 50.5 | -1.0096
587.4 | 50.5 | -1.0096
587.5 | 50.5 | -1.0096
587.6 | 50.5 | -1.0096
587.7 | 50.5 | -1.0096
587.8 | 50.5 | -1.0096
587.9 | 50.5 | -1.0096
588 | 50.5 | -1.0096
588.1 | 50.5 | -1.0096
588.2 | 50.5 | -1.0096
588.3 | 50.5 | -1.0096
588.4 | 50.5 | -1.0096
588.5 | 50.5 | -1.0096
588.6 | 50.5 | -1.0096
588.7 | 50.5 | -1.0096
588.8 | 50.5 | -1.0096
588.9 | 50.5 | -1.0096
589 | 50.5 | -1.0096
589.1 | 50.5 | -1.0096
589.2 | 50.5 | -1.0096
589.3 | 50.5 | -1.0096
589.4 | 50.5 | -1.0096
589.5 | 50.5 | -1.0096
589.6 | 50.5 | -1.0096
589.7 | 50.5 | -1.0094
589.8 | 50.5 | -1.0094
589.9 | 50.5 | -1.0094
590 | 50.5 | -1.0094
590.1 | 50.5 | -1.0094
590.2 | 50.5 | -1.0094
590.3 | 50.5 | -1.0094
590.4 | 50.5 | -1.0094
590.5 | 50.5 | -1.0094
590.6 | 50.5 | -1.0094
590.7 | 50.5 | -1.0094
590.8 | 50.5 | -1.0096
590.9 | 50.5 | -1.0096
591 | 50.5 | -1.0096
591.1 | 50.5 | -1.0096
591.2 | 50.5 | -1.0096
591.3 | 50.5 | -1.0096
591.4 | 50.5 | -1.0096
591.5 | 50.5 | -1.0096
591.6 | 50.5 | -1.0096
591.7 | 50.5 | -1.0096
591.8 | 50.5 | -1.0096
591.9 | 50.5 | -1.0096
592 | 50.5 | -1.0096
592.1 | 50.5 | -1.0096
592.2 | 50.5 | -1.0096
592.3 | 50.5 | -1.0096
592.4 | 50.5 | -1.0096
592.5 | 50.5 | -1.0096
592.6 | 50.5 | -1.0096
592.7 | 50.5 | -1.0096
592.8 | 50.5 | -1.0096
592.9 | 50.5 | -1.0096
593 | 50.5 | -1.0096
593.1 | 50.5 | -1.0096
593.2 | 50.5 | -1.0096
593.3 | 50.5 | -1.0096
593.4 | 50.5 | -1.0096
593.5 | 50.5 | -1.0096
593.6 | 50.5 | -1.0096
593.7 | 50.5 | -1.0096
593.8 | 50.5 | -1.0096
593.9 | 50.5 | -1.0096
594 | 50.5 | -1.0096
594.1 | 50.5 | -1.0096
594.2 | 50.5 | -1.0096
594.3 | 50.5 | -1.0096
594.4 | 50.5 | -1.0096
594.5 | 50.5 | -1.0096
594.6 | 50.5 | -1.0096
594.7 | 50.5 | -1.0096
594.8 | 50.5 | -1.0096
594.9 | 50.5 | -1.0096
595 | 50.5 | -1.0096
595.1 | 50.5 | -1.0096
595.2 | 50.5 | -1.0096
595.3 | 50.5 | -1.0096
595.4 | 50.5 | -1.0096
595.5 | 50.5 | -1.0096
595.6 | 50.5 | -1.0096
595.7 | 50.5 | -1.0096
595.8 | 50.5 | -1.0096
595.9 | 50.5 | -1.0096
596 | 50.5 | -1.0096
596.1 | 50.5 | -1.0096
596.2 | 50.5 | -1.0096
596.3 | 50.5 | -1.0096
596.4 | 50.5 | -1.0096
596.5 | 50.5 | -1.0096
596.6 | 50.5 | -1.0096
596.7 | 50.5 | -1.0096
596.8 | 50.5 | -1.0096
596.9 | 50.5 | -1.0096
597 | 50.5 | -1.0096
597.1 | 50.5 | -1.0096
597.2 | 50.5 | -1.0096
597.3 | 50.5 | -1.0096
597.4 | 50.5 | -1.0096
597.5 | 50.5 | -1.0096
597.6 | 50.5 | -1.0096
597.7 | 50.5 | -1.0096
597.8 | 50.5 | -1.0094
597.9 | 50.5 | -1.0094
598 | 50.5 | -1.0094
598.1 | 50.5 | -1.0094
598.2 | 50.5 | -1.0094
598.3 | 50.5 | -1.0094
598.4 | 50.5 | -1.0094
598.5 | 50.5 | -1.0094
598.6 | 50.5 | -1.0094
598.7 | 50.5 | -1.0094
598.8 | 50.5 | -1.0094
598.9 | 50.5 | -1.0094
599 | 50.5 | -1.0096
599.1 | 50.5 | -1.0096
599.2 | 50.5 | -1.0096
599.3 | 50.5 | -1.0096
599.4 | 50.5 | -1.0096
599.5 | 50.5 | -1.0096
599.6 | 50.5 | -1.0096
599.7 | 50.5 | -1.0096
599.8 | 50.5 | -1.0096
599.9 | 50.5 | -1.0096
600 | 50.5 | -1.0096
600.1 | 50.5 | -1.0094
600.2 | 50.5 | -1.0094
600.3 | 50.5 | -1.0094
600.4 | 50.5 | -1.0094
600.5 | 50.5 | -1.0094
600.6 | 50.5 | -1.0094
600.7 | 50.5 | -1.0094
600.8 | 50.5 | -1.0094
600.9 | 50.5 | -1.0094
601 | 50.5 | -1.0094
601.1 | 50.5 | -1.0094
601.2 | 50.5 | -1.0096
601.3 | 50.5 | -1.0096
601.4 | 50.5 | -1.0096
601.5 | 50.5 | -1.0096
601.6 | 50.5 | -1.0096
601.7 | 50.5 | -1.0096
601.8 | 50.5 | -1.0096
601.9 | 50.5 | -1.0096
602 | 50.5 | -1.0096
602.1 | 50.5 | -1.0096
602.2 | 50.5 | -1.0096
602.3 | 50.5 | -1.0096
602.4 | 50.5 | -1.0096
602.5 | 50.5 | -1.0096
602.6 | 50.5 | -1.0096
602.7 | 50.5 | -1.0096
602.8 | 50.5 | -1.0096
602.9 | 50.5 | -1.0096
603 | 50.5 | -1.0096
603.1 | 50.5 | -1.0096
603.2 | 50.5 | -1.0096
603.3 | 50.5 | -1.0096
603.4 | 50.5 | -1.0096
603.5 | 50.5 | -1.0096
603.6 | 50.5 | -1.0096
603.7 | 50.5 | -1.0096
603.8 | 50.5 | -1.0096
603.9 | 50.5 | -1.0096
604 | 50.5 | -1.0096
604.1 | 50.5 | -1.0096
604.2 | 50.5 | -1.0096
604.3 | 50.5 | -1.0096
604.4 | 50.5 | -1.0096
604.5 | 50.5 | -1.0096
604.6 | 50.5 | -1.0096
604.7 | 50.5 | -1.0096
604.8 | 50.5 | -1.0096
604.9 | 50.5 | -1.0096
605 | 50.5 | -1.0096
605.1 | 50.5 | -1.0096
605.2 | 50.5 | -1.0096
605.3 | 50.5 | -1.0096
605.4 | 50.5 | -1.0096
605.5 | 50.5 | -1.0096
605.6 | 50.5 | -1.0096
605.7 | 50.5 | -1.0096
605.8 | 50.5 | -1.0096
605.9 | 50.5 | -1.0096
606 | 50.5 | -1.0096
606.1 | 50.5 | -1.0096
606.2 | 50.5 | -1.0096
606.3 | 50.5 | -1.0096
606.4 | 50.5 | -1.0096
606.5 | 50.5 | -1.0096
606.6 | 50.5 | -1.0096
606.7 | 50.5 | -1.0096
606.8 | 50.5 | -1.0096
606.9 | 50.5 | -1.0096
607 | 50.5 | -1.0096
607.1 | 50.5 | -1.0096
607.2 | 50.5 | -1.0096
607.3 | 50.5 | -1.0096
607.4 | 50.5 | -1.0096
607.5 | 50.5 | -1.0096
607.6 | 50.5 | -1.0096
607.7 | 50.5 | -1.0096
607.8 | 50.5 | -1.0096
607.9 | 50.5 | -1.0096
608 | 50.5 | -1.0096
608.1 | 50.5 | -1.0096
608.2 | 50.5 | -1.0096
608.3 | 50.5 | -1.0096
608.4 | 50.5 | -1.0096
608.5 | 50.5 | -1.0096
608.6 | 50.5 | -1.0096
608.7 | 50.5 | -1.0096
608.8 | 50.5 | -1.0096
608.9 | 50.5 | -1.0096
609 | 50.5 | -1.0096
609.1 | 50.5 | -1.0096
609.2 | 50.5 | -1.0096
609.3 | 50.5 | -1.0096
609.4 | 50.5 | -1.0096
609.5 | 50.5 | -1.0096
609.6 | 50.5 | -1.0096
609.7 | 50.5 | -1.0096
609.8 | 50.5 | -1.0096
609.9 | 50.5 | -1.0096
610 | 50.5 | -1.0096
610.1 | 50.5 | -1.0096
610.2 | 50.5 | -1.0096
610.3 | 50.5 | -1.0096
610.4 | 50.5 | -1.0096
610.5 | 50.5 | -1.0096
610.6 | 50.5 | -1.0096
610.7 | 50.5 | -1.0096
610.8 | 50.5 | -1.0096
610.9 | 50.5 | -1.0096
611 | 50.5 | -1.0096
611.1 | 50.5 | -1.0096
611.2 | 50.5 | -1.0096
611.3 | 50.5 | -1.0096
611.4 | 50.5 | -1.0096
611.5 | 50.5 | -1.0096
611.6 | 50.5 | -1.0096
611.7 | 50.5 | -1.0096
611.8 | 50.5 | -1.0096
611.9 | 50.5 | -1.0096
612 | 50.5 | -1.0096
612.1 | 50.5 | -1.0096
612.2 | 50.5 | -1.0096
612.3 | 50.5 | -1.0096
612.4 | 50.5 | -1.0096
612.5 | 50.5 | -1.0096
612.6 | 50.5 | -1.0096
612.7 | 50.5 | -1.0096
612.8 | 50.5 | -1.0096
612.9 | 50.5 | -1.0096
613 | 50.5 | -1.0096
613.1 | 50.5 | -1.0096
613.2 | 50.5 | -1.0096
613.3 | 50.5 | -1.0096
613.4 | 50.5 | -1.0096
613.5 | 50.5 | -1.0096
613.6 | 50.5 | -1.0096
613.7 | 50.5 | -1.0096
613.8 | 50.5 | -1.0096
613.9 | 50.5 | -1.0096
614 | 50.5 | -1.0096
614.1 | 50.5 | -1.0096
614.2 | 50.5 | -1.0096
614.3 | 50.5 | -1.0096
614.4 | 50.5 | -1.0096
614.5 | 50.5 | -1.0096
614.6 | 50.5 | -1.0096
614.7 | 50.5 | -1.0096
614.8 | 50.5 | -1.0096
614.9 | 50.5 | -1.0096
615 | 50.5 | -1.0096
615.1 | 50.5 | -1.0096
615.2 | 50.5 | -1.0096
615.3 | 50.5 | -1.0096
615.4 | 50.5 | -1.0096
615.5 | 50.5 | -1.0096
615.6 | 50.5 | -1.0096
615.7 | 50.5 | -1.0096
615.8 | 50.5 | -1.0096
615.9 | 50.5 | -1.0096
616 | 50.5 | -1.0096
616.1 | 50.5 | -1.0096
616.2 | 50.5 | -1.0096
616.3 | 50.5 | -1.0096
616.4 | 50.5 | -1.0096
616.5 | 50.5 | -1.0096
616.6 | 50.5 | -1.0096
616.7 | 50.5 | -1.0096
616.8 | 50.5 | -1.0096
616.9 | 50.5 | -1.0096
617 | 50.5 | -1.0096
617.1 | 50.5 | -1.0096
617.2 | 50.5 | -1.0096
617.3 | 50.5 | -1.0096
617.4 | 50.5 | -1.0096
617.5 | 50.5 | -1.0096
617.6 | 50.5 | -1.0096
617.7 | 50.5 | -1.0094
617.8 | 50.5 | -1.0094
617.9 | 50.5 | -1.0094
618 | 50.5 | -1.0094
618.1 | 50.5 | -1.0094
618.2 | 50.5 | -1.0094
618.3 | 50.5 | -1.0094
618.4 | 50.5 | -1.0094
618.5 | 50.5 | -1.0094
618.6 | 50.5 | -1.0094
618.7 | 50.5 | -1.0096
618.8 | 50.5 | -1.0094
618.9 | 50.5 | -1.0094
619 | 50.5 | -1.0094
619.1 | 50.5 | -1.0094
619.2 | 50.5 | -1.0094
619.3 | 50.5 | -1.0094
619.4 | 50.5 | -1.0094
619.5 | 50.5 | -1.0094
619.6 | 50.5 | -1.0094
619.7 | 50.5 | -1.0094
619.8 | 50.5 | -1.0094
619.9 | 50.5 | -1.0094
620 | 50.5 | -1.0094
620.1 | 50.5 | -1.0094
620.2 | 50.5 | -1.0094
620.3 | 50.5 | -1.0094
620.4 | 50.5 | -1.0094
620.5 | 50.5 | -1.0094
620.6 | 50.5 | -1.0094
620.7 | 50.5 | -1.0094
620.8 | 50.5 | -1.0094
620.9 | 50.5 | -1.0094
621 | 50.5 | -1.0096
621.1 | 50.5 | -1.0096
621.2 | 50.5 | -1.0096
621.3 | 50.5 | -1.0096
621.4 | 50.5 | -1.0096
621.5 | 50.5 | -1.0096
621.6 | 50.5 | -1.0096
621.7 | 50.5 | -1.0096
621.8 | 50.5 | -1.0096
621.9 | 50.5 | -1.0096
622 | 50.5 | -1.0096
622.1 | 50.5 | -1.0096
622.2 | 50.5 | -1.0096
622.3 | 50.5 | -1.0096
622.4 | 50.5 | -1.0096
622.5 | 50.5 | -1.0096
622.6 | 50.5 | -1.0096
622.7 | 50.5 | -1.0096
622.8 | 50.5 | -1.0096
622.9 | 50.5 | -1.0096
623 | 50.5 | -1.0096
623.1 | 50.5 | -1.0096
623.2 | 50.5 | -1.0096
623.3 | 50.5 | -1.0096
623.4 | 50.5 | -1.0096
623.5 | 50.5 | -1.0096
623.6 | 50.5 | -1.0096
623.7 | 50.5 | -1.0094
623.8 | 50.5 | -1.0094
623.9 | 50.5 | -1.0094
624 | 50.5 | -1.0094
624.1 | 50.5 | -1.0094
624.2 | 50.5 | -1.0094
624.3 | 50.5 | -1.0094
624.4 | 50.5 | -1.0094
624.5 | 50.5 | -1.0094
624.6 | 50.5 | -1.0094
624.7 | 50.5 | -1.0094
624.8 | 50.5 | -1.0096
624.9 | 50.5 | -1.0096
625 | 50.5 | -1.0096
625.1 | 50.5 | -1.0096
625.2 | 50.5 | -1.0096
625.3 | 50.5 | -1.0096
625.4 | 50.5 | -1.0096
625.5 | 50.5 | -1.0096
625.6 | 50.5 | -1.0096
625.7 | 50.5 | -1.0096
625.8 | 50.5 | -1.0096
625.9 | 50.5 | -1.0096
626 | 50.5 | -1.0096
626.1 | 50.5 | -1.0096
626.2 | 50.5 | -1.0096
626.3 | 50.5 | -1.0096
626.4 | 50.5 | -1.0096
626.5 | 50.5 | -1.0096
626.6 | 50.5 | -1.0096
626.7 | 50.5 | -1.0096
626.8 | 50.5 | -1.0096
626.9 | 50.5 | -1.0096
627 | 50.5 | -1.0096
627.1 | 50.5 | -1.0096
627.2 | 50.5 | -1.0096
627.3 | 50.5 | -1.0096
627.4 | 50.5 | -1.0096
627.5 | 50.5 | -1.0096
627.6 | 50.5 | -1.0096
627.7 | 50.5 | -1.0096
627.8 | 50.5 | -1.0096
627.9 | 50.5 | -1.0096
628 | 50.5 | -1.0096
628.1 | 50.5 | -1.0096
628.2 | 50.5 | -1.0096
628.3 | 50.5 | -1.0096
628.4 | 50.5 | -1.0096
628.5 | 50.5 | -1.0096
628.6 | 50.5 | -1.0096
628.7 | 50.5 | -1.0096
628.8 | 50.5 | -1.0096
628.9 | 50.5 | -1.0096
629 | 50.5 | -1.0096
629.1 | 50.5 | -1.0096
629.2 | 50.5 | -1.0096
629.3 | 50.5 | -1.0096
629.4 | 50.5 | -1.0096
629.5 | 50.5 | -1.0096
629.6 | 50.5 | -1.0096
629.7 | 50.5 | -1.0096
629.8 | 50.5 | -1.0096
629.9 | 50.5 | -1.0096
630 | 50.5 | -1.0096
630.1 | 50.5 | -1.0096
630.2 | 50.5 | -1.0096
630.3 | 50.5 | -1.0096
630.4 | 50.5 | -1.0096
630.5 | 50.5 | -1.0096
630.6 | 50.5 | -1.0096
630.7 | 50.5 | -1.0096
630.8 | 50.5 | -1.0096
630.9 | 50.5 | -1.0096
631 | 50.5 | -1.0096
631.1 | 50.5 | -1.0096
631.2 | 50.5 | -1.0096
631.3 | 50.5 | -1.0096
631.4 | 50.5 | -1.0096
631.5 | 50.5 | -1.0096
631.6 | 50.5 | -1.0096
631.7 | 50.5 | -1.0096
631.8 | 50.5 | -1.0096
631.9 | 50.5 | -1.0096
632 | 50.5 | -1.0096
632.1 | 50.5 | -1.0096
632.2 | 50.5 | -1.0096
632.3 | 50.5 | -1.0096
632.4 | 50.5 | -1.0096
632.5 | 50.5 | -1.0096
632.6 | 50.5 | -1.0096
632.7 | 50.5 | -1.0096
632.8 | 50.5 | -1.0096
632.9 | 50.5 | -1.0096
633 | 50.5 | -1.0096
633.1 | 50.5 | -1.0096
633.2 | 50.5 | -1.0096
633.3 | 50.5 | -1.0096
633.4 | 50.5 | -1.0096
633.5 | 50.5 | -1.0096
633.6 | 50.5 | -1.0096
633.7 | 50.5 | -1.0096
633.8 | 50.5 | -1.0096
633.9 | 50.5 | -1.0096
634 | 50.5 | -1.0096
634.1 | 50.5 | -1.0096
634.2 | 50.5 | -1.0096
634.3 | 50.5 | -1.0096
634.4 | 50.5 | -1.0096
634.5 | 50.5 | -1.0096
634.6 | 50.5 | -1.0096
634.7 | 50.5 | -1.0096
634.8 | 50.5 | -1.0096
634.9 | 50.5 | -1.0096
635 | 50.5 | -1.0096
635.1 | 50.5 | -1.0096
635.2 | 50.5 | -1.0096
635.3 | 50.5 | -1.0096
635.4 | 50.5 | -1.0096
635.5 | 50.5 | -1.0096
635.6 | 50.5 | -1.0096
635.7 | 50.5 | -1.0096
635.8 | 50.5 | -1.0096
635.9 | 50.5 | -1.0096
636 | 50.5 | -1.0096
636.1 | 50.5 | -1.0096
636.2 | 50.5 | -1.0096
636.3 | 50.5 | -1.0096
636.4 | 50.5 | -1.0096
636.5 | 50.5 | -1.0096
636.6 | 50.5 | -1.0096
636.7 | 50.5 | -1.0096
636.8 | 50.5 | -1.0096
636.9 | 50.5 | -1.0096
637 | 50.5 | -1.0096
637.1 | 50.5 | -1.0096
637.2 | 50.5 | -1.0096
637.3 | 50.5 | -1.0096
637.4 | 50.5 | -1.0096
637.5 | 50.5 | -1.0096
637.6 | 50.5 | -1.0096
637.7 | 50.5 | -1.0096
637.8 | 50.5 | -1.0096
637.9 | 50.5 | -1.0096
638 | 50.5 | -1.0096
638.1 | 50.5 | -1.0096
638.2 | 50.5 | -1.0096
638.3 | 50.5 | -1.0096
638.4 | 50.5 | -1.0096
638.5 | 50.5 | -1.0096
638.6 | 50.5 | -1.0096
638.7 | 50.5 | -1.0096
638.8 | 50.5 | -1.0096
638.9 | 50.5 | -1.0096
639 | 50.5 | -1.0096
639.1 | 50.5 | -1.0096
639.2 | 50.5 | -1.0096
639.3 | 50.5 | -1.0096
639.4 | 50.5 | -1.0096
639.5 | 50.5 | -1.0096
639.6 | 50.5 | -1.0096
639.7 | 50.5 | -1.0096
639.8 | 50.5 | -1.0096
639.9 | 50.5 | -1.0096
640 | 50.5 | -1.0096
640.1 | 50.5 | -1.0096
640.2 | 50.5 | -1.0096
640.3 | 50.5 | -1.0096
640.4 | 50.5 | -1.0096
640.5 | 50.5 | -1.0096
640.6 | 50.5 | -1.0096
640.7 | 50.5 | -1.0096
640.8 | 50.5 | -1.0096
640.9 | 50.5 | -1.0096
641 | 50.5 | -1.0096
641.1 | 50.5 | -1.0096
641.2 | 50.5 | -1.0096
641.3 | 50.5 | -1.0096
641.4 | 50.5 | -1.0096
641.5 | 50.5 | -1.0096
641.6 | 50.5 | -1.0096
641.7 | 50.5 | -1.0096
641.8 | 50.5 | -1.0096
641.9 | 50.5 | -1.0096
642 | 50.5 | -1.0096
642.1 | 50.5 | -1.0096
642.2 | 50.5 | -1.0096
642.3 | 50.5 | -1.0096
642.4 | 50.5 | -1.0096
642.5 | 50.5 | -1.0096
642.6 | 50.5 | -1.0096
642.7 | 50.5 | -1.0096
642.8 | 50.5 | -1.0096
642.9 | 50.5 | -1.0096
643 | 50.5 | -1.0096
643.1 | 50.5 | -1.0096
643.2 | 50.5 | -1.0096
643.3 | 50.5 | -1.0096
643.4 | 50.5 | -1.0096
643.5 | 50.5 | -1.0096
643.6 | 50.5 | -1.0096
643.7 | 50.5 | -1.0096
643.8 | 50.5 | -1.0096
643.9 | 50.5 | -1.0096
644 | 50.5 | -1.0096
644.1 | 50.5 | -1.0096
644.2 | 50.5 | -1.0096
644.3 | 50.5 | -1.0096
644.4 | 50.5 | -1.0096
644.5 | 50.5 | -1.0096
644.6 | 50.5 | -1.0096
644.7 | 50.5 | -1.0096
644.8 | 50.5 | -1.0096
644.9 | 50.5 | -1.0096
645 | 50.5 | -1.0096
645.1 | 50.5 | -1.0096
645.2 | 50.5 | -1.0096
645.3 | 50.5 | -1.0096
645.4 | 50.5 | -1.0096
645.5 | 50.5 | -1.0096
645.6 | 50.5 | -1.0096
645.7 | 50.5 | -1.0096
645.8 | 50.5 | -1.0096
645.9 | 50.5 | -1.0096
646 | 50.5 | -1.0096
646.1 | 50.5 | -1.0096
646.2 | 50.5 | -1.0096
646.3 | 50.5 | -1.0096
646.4 | 50.5 | -1.0096
646.5 | 50.5 | -1.0096
646.6 | 50.5 | -1.0096
646.7 | 50.5 | -1.0096
646.8 | 50.5 | -1.0096
646.9 | 50.5 | -1.0096
647 | 50.5 | -1.0096
647.1 | 50.5 | -1.0096
647.2 | 50.5 | -1.0096
647.3 | 50.5 | -1.0096
647.4 | 50.5 | -1.0096
647.5 | 50.5 | -1.0096
647.6 | 50.5 | -1.0096
647.7 | 50.5 | -1.0096
647.8 | 50.5 | -1.0096
647.9 | 50.5 | -1.0096
648 | 50.5 | -1.0096
648.1 | 50.5 | -1.0096
648.2 | 50.5 | -1.0096
648.3 | 50.5 | -1.0096
648.4 | 50.5 | -1.0096
648.5 | 50.5 | -1.0096
648.6 | 50.5 | -1.0096
648.7 | 50.5 | -1.0096
648.8 | 50.5 | -1.0096
648.9 | 50.5 | -1.0096
649 | 50.5 | -1.0096
649.1 | 50.5 | -1.0096
649.2 | 50.5 | -1.0096
649.3 | 50.5 | -1.0096
649.4 | 50.5 | -1.0096
649.5 | 50.5 | -1.0096
649.6 | 50.5 | -1.0096
649.7 | 50.5 | -1.0096
649.8 | 50.5 | -1.0096
649.9 | 50.5 | -1.0096
650 | 50.5 | -1.0096
650.1 | 50.5 | -1.0096
650.2 | 50.5 | -1.0096
650.3 | 50.5 | -1.0096
650.4 | 50.5 | -1.0096
650.5 | 50.5 | -1.0096
650.6 | 50.5 | -1.0096
650.7 | 50.5 | -1.0096
650.8 | 50.5 | -1.0096
650.9 | 50.5 | -1.0096
651 | 50.5 | -1.0096
651.1 | 50.5 | -1.0096
651.2 | 50.5 | -1.0096
651.3 | 50.5 | -1.0096
651.4 | 50.5 | -1.0096
651.5 | 50.5 | -1.0096
651.6 | 50.5 | -1.0096
651.7 | 50.5 | -1.0096
651.8 | 50.5 | -1.0096
651.9 | 50.5 | -1.0096
652 | 50.5 | -1.0096
652.1 | 50.5 | -1.0096
652.2 | 50.5 | -1.0096
652.3 | 50.5 | -1.0096
652.4 | 50.5 | -1.0096
652.5 | 50.5 | -1.0096
652.6 | 50.5 | -1.0096
652.7 | 50.5 | -1.0096
652.8 | 50.5 | -1.0096
652.9 | 50.5 | -1.0096
653 | 50.5 | -1.0096
653.1 | 50.5 | -1.0096
653.2 | 50.5 | -1.0096
653.3 | 50.5 | -1.0096
653.4 | 50.5 | -1.0096
653.5 | 50.5 | -1.0096
653.6 | 50.5 | -1.0096
653.7 | 50.5 | -1.0096
653.8 | 50.5 | -1.0096
653.9 | 50.5 | -1.0096
654 | 50.5 | -1.0096
654.1 | 50.5 | -1.0096
654.2 | 50.5 | -1.0096
654.3 | 50.5 | -1.0096
654.4 | 50.5 | -1.0096
654.5 | 50.5 | -1.0096
654.6 | 50.5 | -1.0096
654.7 | 50.5 | -1.0096
654.8 | 50.5 | -1.0096
654.9 | 50.5 | -1.0096
655 | 50.5 | -1.0096
655.1 | 50.5 | -1.0096
655.2 | 50.5 | -1.0096
655.3 | 50.5 | -1.0096
655.4 | 50.5 | -1.0096
655.5 | 50.5 | -1.0096
655.6 | 50.5 | -1.0096
655.7 | 50.5 | -1.0096
655.8 | 50.5 | -1.0096
655.9 | 50.5 | -1.0096
656 | 50.5 | -1.0096
656.1 | 50.5 | -1.0096
656.2 | 50.5 | -1.0096
656.3 | 50.5 | -1.0096
656.4 | 50.5 | -1.0096
656.5 | 50.5 | -1.0096
656.6 | 50.5 | -1.0096
656.7 | 50.5 | -1.0096
656.8 | 50.5 | -1.0096
656.9 | 50.5 | -1.0096
657 | 50.5 | -1.0096
657.1 | 50.5 | -1.0096
657.2 | 50.5 | -1.0096
657.3 | 50.5 | -1.0096
657.4 | 50.5 | -1.0096
657.5 | 50.5 | -1.0096
657.6 | 50.5 | -1.0096
657.7 | 50.5 | -1.0096
657.8 | 50.5 | -1.0096
657.9 | 50.5 | -1.0096
658 | 50.5 | -1.0096
658.1 | 50.5 | -1.0096
658.2 | 50.5 | -1.0096
658.3 | 50.5 | -1.0096
658.4 | 50.5 | -1.0096
658.5 | 50.5 | -1.0096
658.6 | 50.5 | -1.0096
658.7 | 50.5 | -1.0096
658.8 | 50.5 | -1.0096
658.9 | 50.5 | -1.0096
659 | 50.5 | -1.0096
659.1 | 50.5 | -1.0096
659.2 | 50.5 | -1.0096
659.3 | 50.5 | -1.0096
659.4 | 50.5 | -1.0096
659.5 | 50.5 | -1.0096
659.6 | 50.5 | -1.0096
659.7 | 50.5 | -1.0096
659.8 | 50.5 | -1.0096
659.9 | 50.5 | -1.0096
660 | 50.5 | -1.0096
660.1 | 50.5 | -1.0096
660.2 | 50.5 | -1.0096
660.3 | 50.5 | -1.0096
660.4 | 50.5 | -1.0096
660.5 | 50.5 | -1.0096
660.6 | 50.5 | -1.0096
660.7 | 50.5 | -1.0096
660.8 | 50.5 | -1.0096
660.9 | 50.5 | -1.0096
661 | 50.5 | -1.0096
661.1 | 50.5 | -1.0096
661.2 | 50.5 | -1.0096
661.3 | 50.5 | -1.0096
661.4 | 50.5 | -1.0096
661.5 | 50.5 | -1.0096
661.6 | 50.5 | -1.0096
661.7 | 50.5 | -1.0096
661.8 | 50.5 | -1.0096
661.9 | 50.5 | -1.0096
662 | 50.5 | -1.0096
662.1 | 50.5 | -1.0096
662.2 | 50.5 | -1.0096
662.3 | 50.5 | -1.0096
662.4 | 50.5 | -1.0096
662.5 | 50.5 | -1.0096
662.6 | 50.5 | -1.0096
662.7 | 50.5 | -1.0096
662.8 | 50.5 | -1.0096
662.9 | 50.5 | -1.0096
663 | 50.5 | -1.0096
663.1 | 50.5 | -1.0096
663.2 | 50.5 | -1.0096
663.3 | 50.5 | -1.0096
663.4 | 50.5 | -1.0096
663.5 | 50.5 | -1.0096
663.6 | 50.5 | -1.0096
663.7 | 50.5 | -1.0096
663.8 | 50.5 | -1.0096
663.9 | 50.5 | -1.0096
664 | 50.5 | -1.0096
664.1 | 50.5 | -1.0096
664.2 | 50.5 | -1.0096
664.3 | 50.5 | -1.0096
664.4 | 50.5 | -1.0096
664.5 | 50.5 | -1.0096
664.6 | 50.5 | -1.0096
664.7 | 50.5 | -1.0096
664.8 | 50.5 | -1.0096
664.9 | 50.5 | -1.0096
665 | 50.5 | -1.0096
665.1 | 50.5 | -1.0096
665.2 | 50.5 | -1.0096
665.3 | 50.5 | -1.0096
665.4 | 50.5 | -1.0096
665.5 | 50.5 | -1.0096
665.6 | 50.5 | -1.0096
665.7 | 50.5 | -1.0096
665.8 | 50.5 | -1.0096
665.9 | 50.5 | -1.0096
666 | 50.5 | -1.0096
666.1 | 50.5 | -1.0096
666.2 | 50.5 | -1.0096
666.3 | 50.5 | -1.0096
666.4 | 50.5 | -1.0096
666.5 | 50.5 | -1.0096
666.6 | 50.5 | -1.0096
666.7 | 50.5 | -1.0096
666.8 | 50.5 | -1.0096
666.9 | 50.5 | -1.0096
667 | 50.5 | -1.0096
667.1 | 50.5 | -1.0096
667.2 | 50.5 | -1.0096
667.3 | 50.5 | -1.0096
667.4 | 50.5 | -1.0096
667.5 | 50.5 | -1.0096
667.6 | 50.5 | -1.0096
667.7 | 50.5 | -1.0096
667.8 | 50.5 | -1.0096
667.9 | 50.5 | -1.0096
668 | 50.5 | -1.0096
668.1 | 50.5 | -1.0096
668.2 | 50.5 | -1.0096
668.3 | 50.5 | -1.0096
668.4 | 50.5 | -1.0096
668.5 | 50.5 | -1.0096
668.6 | 50.5 | -1.0096
668.7 | 50.5 | -1.0096
668.8 | 50.5 | -1.0096
668.9 | 50.5 | -1.0096
669 | 50.5 | -1.0096
669.1 | 50.5 | -1.0096
669.2 | 50.5 | -1.0096
669.3 | 50.5 | -1.0096
669.4 | 50.5 | -1.0096
669.5 | 50.5 | -1.0096
669.6 | 50.5 | -1.0096
669.7 | 50.5 | -1.0096
669.8 | 50.5 | -1.0096
669.9 | 50.5 | -1.0096
670 | 50.5 | -1.0096
670.1 | 50.5 | -1.0096
670.2 | 50.5 | -1.0096
670.3 | 50.5 | -1.0096
670.4 | 50.5 | -1.0096
670.5 | 50.5 | -1.0096
670.6 | 50.5 | -1.0096
670.7 | 50.5 | -1.0096
670.8 | 50.5 | -1.0096
670.9 | 50.5 | -1.0096
671 | 50.5 | -1.0096
671.1 | 50.5 | -1.0096
671.2 | 50.5 | -1.0096
671.3 | 50.5 | -1.0096
671.4 | 50.5 | -1.0096
671.5 | 50.5 | -1.0096
671.6 | 50.5 | -1.0096
671.7 | 50.5 | -1.0096
671.8 | 50.5 | -1.0096
671.9 | 50.5 | -1.0096
672 | 50.5 | -1.0096
672.1 | 50.5 | -1.0096
672.2 | 50.5 | -1.0096
672.3 | 50.5 | -1.0096
672.4 | 50.5 | -1.0096
672.5 | 50.5 | -1.0096
672.6 | 50.5 | -1.0096
672.7 | 50.5 | -1.0096
672.8 | 50.5 | -1.0096
672.9 | 50.5 | -1.0096
673 | 50.5 | -1.0096
673.1 | 50.5 | -1.0096
673.2 | 50.5 | -1.0096
673.3 | 50.5 | -1.0096
673.4 | 50.5 | -1.0096
673.5 | 50.5 | -1.0096
673.6 | 50.5 | -1.0096
673.7 | 50.5 | -1.0096
673.8 | 50.5 | -1.0096
673.9 | 50.5 | -1.0096
674 | 50.5 | -1.0096
674.1 | 50.5 | -1.0096
674.2 | 50.5 | -1.0096
674.3 | 50.5 | -1.0096
674.4 | 50.5 | -1.0096
674.5 | 50.5 | -1.0096
674.6 | 50.5 | -1.0096
674.7 | 50.5 | -1.0096
674.8 | 50.5 | -1.0096
674.9 | 50.5 | -1.0096
675 | 50.5 | -1.0096
675.1 | 50.5 | -1.0096
675.2 | 50.5 | -1.0096
675.3 | 50.5 | -1.0096
675.4 | 50.5 | -1.0096
675.5 | 50.5 | -1.0096
675.6 | 50.5 | -1.0096
675.7 | 50.5 | -1.0096
675.8 | 50.5 | -1.0096
675.9 | 50.5 | -1.0096
676 | 50.5 | -1.0096
676.1 | 50.5 | -1.0096
676.2 | 50.5 | -1.0094
676.3 | 50.5 | -1.0094
676.4 | 50.5 | -1.0094
676.5 | 50.5 | -1.0094
676.6 | 50.5 | -1.0094
676.7 | 50.5 | -1.0094
676.8 | 50.5 | -1.0094
676.9 | 50.5 | -1.0094
677 | 50.5 | -1.0094
677.1 | 50.5 | -1.0094
677.2 | 50.5 | -1.0094
677.3 | 50.5 | -1.0094
677.4 | 50.5 | -1.0094
677.5 | 50.5 | -1.0094
677.6 | 50.5 | -1.0094
677.7 | 50.5 | -1.0094
677.8 | 50.5 | -1.0094
677.9 | 50.5 | -1.0094
678 | 50.5 | -1.0094
678.1 | 50.5 | -1.0094
678.2 | 50.5 | -1.0094
678.3 | 50.5 | -1.0094
678.4 | 50.5 | -1.0096
678.5 | 50.5 | -1.0096
678.6 | 50.5 | -1.0096
678.7 | 50.5 | -1.0096
678.8 | 50.5 | -1.0096
678.9 | 50.5 | -1.0096
679 | 50.5 | -1.0096
679.1 | 50.5 | -1.0096
679.2 | 50.5 | -1.0096
679.3 | 50.5 | -1.0096
679.4 | 50.5 | -1.0096
679.5 | 50.5 | -1.0096
679.6 | 50.5 | -1.0096
679.7 | 50.5 | -1.0096
679.8 | 50.5 | -1.0096
679.9 | 50.5 | -1.0096
680 | 50.5 | -1.0096
680.1 | 50.5 | -1.0096
680.2 | 50.5 | -1.0096
680.3 | 50.5 | -1.0096
680.4 | 50.5 | -1.0096
680.5 | 50.5 | -1.0096
680.6 | 50.5 | -1.0096
680.7 | 50.5 | -1.0096
680.8 | 50.5 | -1.0096
680.9 | 50.5 | -1.0096
681 | 50.5 | -1.0096
681.1 | 50.5 | -1.0096
681.2 | 50.5 | -1.0096
681.3 | 50.5 | -1.0096
681.4 | 50.5 | -1.0096
681.5 | 50.5 | -1.0096
681.6 | 50.5 | -1.0096
681.7 | 50.5 | -1.0096
681.8 | 50.5 | -1.0096
681.9 | 50.5 | -1.0096
682 | 50.5 | -1.0096
682.1 | 50.5 | -1.0096
682.2 | 50.5 | -1.0096
682.3 | 50.5 | -1.0096
682.4 | 50.5 | -1.0096
682.5 | 50.5 | -1.0096
682.6 | 50.5 | -1.0096
682.7 | 50.5 | -1.0096
682.8 | 50.5 | -1.0096
682.9 | 50.5 | -1.0096
683 | 50.5 | -1.0096
683.1 | 50.5 | -1.0096
683.2 | 50.5 | -1.0096
683.3 | 50.5 | -1.0096
683.4 | 50.5 | -1.0096
683.5 | 50.5 | -1.0096
683.6 | 50.5 | -1.0096
683.7 | 50.5 | -1.0096
683.8 | 50.5 | -1.0096
683.9 | 50.5 | -1.0096
684 | 50.5 | -1.0096
684.1 | 50.5 | -1.0096
684.2 | 50.5 | -1.0096
684.3 | 50.5 | -1.0096
684.4 | 50.5 | -1.0096
684.5 | 50.5 | -1.0096
684.6 | 50.5 | -1.0096
684.7 | 50.5 | -1.0096
684.8 | 50.5 | -1.0096
684.9 | 50.5 | -1.0096
685 | 50.5 | -1.0096
685.1 | 50.5 | -1.0096
685.2 | 50.5 | -1.0096
685.3 | 50.5 | -1.0096
685.4 | 50.5 | -1.0096
685.5 | 50.5 | -1.0096
685.6 | 50.5 | -1.0096
685.7 | 50.5 | -1.0096
685.8 | 50.5 | -1.0096
685.9 | 50.5 | -1.0096
686 | 50.5 | -1.0096
686.1 | 50.5 | -1.0096
686.2 | 50.5 | -1.0096
686.3 | 50.5 | -1.0096
686.4 | 50.5 | -1.0096
686.5 | 50.5 | -1.0096
686.6 | 50.5 | -1.0096
686.7 | 50.5 | -1.0096
686.8 | 50.5 | -1.0096
686.9 | 50.5 | -1.0096
687 | 50.5 | -1.0096
687.1 | 50.5 | -1.0096
687.2 | 50.5 | -1.0096
687.3 | 50.5 | -1.0096
687.4 | 50.5 | -1.0096
687.5 | 50.5 | -1.0096
687.6 | 50.5 | -1.0096
687.7 | 50.5 | -1.0096
687.8 | 50.5 | -1.0096
687.9 | 50.5 | -1.0096
688 | 50.5 | -1.0096
688.1 | 50.5 | -1.0096
688.2 | 50.5 | -1.0096
688.3 | 50.5 | -1.0096
688.4 | 50.5 | -1.0096
688.5 | 50.5 | -1.0096
688.6 | 50.5 | -1.0096
688.7 | 50.5 | -1.0096
688.8 | 50.5 | -1.0096
688.9 | 50.5 | -1.0096
689 | 50.5 | -1.0096
689.1 | 50.5 | -1.0096
689.2 | 50.5 | -1.0096
689.3 | 50.5 | -1.0096
689.4 | 50.5 | -1.0096
689.5 | 50.5 | -1.0096
689.6 | 50.5 | -1.0096
689.7 | 50.5 | -1.0096
689.8 | 50.5 | -1.0096
689.9 | 50.5 | -1.0096
690 | 50.5 | -1.0096
690.1 | 50.5 | -1.0096
690.2 | 50.5 | -1.0096
690.3 | 50.5 | -1.0096
690.4 | 50.5 | -1.0096
690.5 | 50.5 | -1.0096
690.6 | 50.5 | -1.0096
690.7 | 50.5 | -1.0096
690.8 | 50.5 | -1.0096
690.9 | 50.5 | -1.0096
691 | 50.5 | -1.0096
691.1 | 50.5 | -1.0096
691.2 | 50.5 | -1.0096
691.3 | 50.5 | -1.0096
691.4 | 50.5 | -1.0096
691.5 | 50.5 | -1.0096
691.6 | 50.5 | -1.0096
691.7 | 50.5 | -1.0096
691.8 | 50.5 | -1.0096
691.9 | 50.5 | -1.0096
692 | 50.5 | -1.0096
692.1 | 50.5 | -1.0096
692.2 | 50.5 | -1.0096
692.3 | 50.5 | -1.0096
692.4 | 50.5 | -1.0096
692.5 | 50.5 | -1.0096
692.6 | 50.5 | -1.0096
692.7 | 50.5 | -1.0096
692.8 | 50.5 | -1.0096
692.9 | 50.5 | -1.0096
693 | 50.5 | -1.0096
693.1 | 50.5 | -1.0096
693.2 | 50.5 | -1.0096
693.3 | 50.5 | -1.0096
693.4 | 50.5 | -1.0096
693.5 | 50.5 | -1.0096
693.6 | 50.5 | -1.0096
693.7 | 50.5 | -1.0096
693.8 | 50.5 | -1.0096
693.9 | 50.5 | -1.0096
694 | 50.5 | -1.0096
694.1 | 50.5 | -1.0096
694.2 | 50.5 | -1.0096
694.3 | 50.5 | -1.0096
694.4 | 50.5 | -1.0096
694.5 | 50.5 | -1.0096
694.6 | 50.5 | -1.0096
694.7 | 50.5 | -1.0096
694.8 | 50.5 | -1.0096
694.9 | 50.5 | -1.0096
695 | 50.5 | -1.0096
695.1 | 50.5 | -1.0096
695.2 | 50.5 | -1.0096
695.3 | 50.5 | -1.0096
695.4 | 50.5 | -1.0096
695.5 | 50.5 | -1.0096
695.6 | 50.5 | -1.0096
695.7 | 50.5 | -1.0096
695.8 | 50.5 | -1.0094
695.9 | 50.5 | -1.0094
696 | 50.5 | -1.0094
696.1 | 50.5 | -1.0094
696.2 | 50.5 | -1.0094
696.3 | 50.5 | -1.0094
696.4 | 50.5 | -1.0094
696.5 | 50.5 | -1.0094
696.6 | 50.5 | -1.0094
696.7 | 50.5 | -1.0094
696.8 | 50.5 | -1.0094
696.9 | 50.5 | -1.0096
697 | 50.5 | -1.0096
697.1 | 50.5 | -1.0096
697.2 | 50.5 | -1.0096
697.3 | 50.5 | -1.0096
697.4 | 50.5 | -1.0096
697.5 | 50.5 | -1.0096
697.6 | 50.5 | -1.0096
697.7 | 50.5 | -1.0096
697.8 | 50.5 | -1.0096
697.9 | 50.5 | -1.0096
698 | 50.5 | -1.0096
698.1 | 50.5 | -1.0096
698.2 | 50.5 | -1.0096
698.3 | 50.5 | -1.0096
698.4 | 50.5 | -1.0096
698.5 | 50.5 | -1.0096
698.6 | 50.5 | -1.0096
698.7 | 50.5 | -1.0096
698.8 | 50.5 | -1.0096
698.9 | 50.5 | -1.0096
699 | 50.5 | -1.0096
699.1 | 50.5 | -1.0096
699.2 | 50.5 | -1.0096
699.3 | 50.5 | -1.0096
699.4 | 50.5 | -1.0096
699.5 | 50.5 | -1.0096
699.6 | 50.5 | -1.0096
699.7 | 50.5 | -1.0096
699.8 | 50.5 | -1.0096
699.9 | 50.5 | -1.0096
700 | 50.5 | -1.0096
700.1 | 50.5 | -1.0096
700.2 | 50.5 | -1.0096
700.3 | 50.5 | -1.0096
700.4 | 50.5 | -1.0096
700.5 | 50.5 | -1.0096
700.6 | 50.5 | -1.0096
700.7 | 50.5 | -1.0096
700.8 | 50.5 | -1.0096
700.9 | 50.5 | -1.0096
701 | 50.5 | -1.0096
701.1 | 50.5 | -1.0096
701.2 | 50.5 | -1.0096
701.3 | 50.5 | -1.0096
701.4 | 50.5 | -1.0096
701.5 | 50.5 | -1.0096
701.6 | 50.5 | -1.0096
701.7 | 50.5 | -1.0094
701.8 | 50.5 | -1.0094
701.9 | 50.5 | -1.0094
702 | 50.5 | -1.0094
702.1 | 50.5 | -1.0094
702.2 | 50.5 | -1.0094
702.3 | 50.5 | -1.0094
702.4 | 50.5 | -1.0094
702.5 | 50.5 | -1.0094
702.6 | 50.5 | -1.0094
702.7 | 50.5 | -1.0094
702.8 | 50.5 | -1.0094
702.9 | 50.5 | -1.0096
703 | 50.5 | -1.0096
703.1 | 50.5 | -1.0096
703.2 | 50.5 | -1.0096
703.3 | 50.5 | -1.0096
703.4 | 50.5 | -1.0096
703.5 | 50.5 | -1.0096
703.6 | 50.5 | -1.0096
703.7 | 50.5 | -1.0096
703.8 | 50.5 | -1.0096
703.9 | 50.5 | -1.0096
704 | 50.5 | -1.0096
704.1 | 50.5 | -1.0096
704.2 | 50.5 | -1.0096
704.3 | 50.5 | -1.0096
704.4 | 50.5 | -1.0096
704.5 | 50.5 | -1.0096
704.6 | 50.5 | -1.0096
704.7 | 50.5 | -1.0096
704.8 | 50.5 | -1.0096
704.9 | 50.5 | -1.0096
705 | 50.5 | -1.0096
705.1 | 50.5 | -1.0096
705.2 | 50.5 | -1.0096
705.3 | 50.5 | -1.0096
705.4 | 50.5 | -1.0096
705.5 | 50.5 | -1.0096
705.6 | 50.5 | -1.0096
705.7 | 50.5 | -1.0096
705.8 | 50.5 | -1.0096
705.9 | 50.5 | -1.0096
706 | 50.5 | -1.0096
706.1 | 50.5 | -1.0096
706.2 | 50.5 | -1.0096
706.3 | 50.5 | -1.0096
706.4 | 50.5 | -1.0096
706.5 | 50.5 | -1.0096
706.6 | 50.5 | -1.0096
706.7 | 50.5 | -1.0096
706.8 | 50.5 | -1.0096
706.9 | 50.5 | -1.0096
707 | 50.5 | -1.0096
707.1 | 50.5 | -1.0096
707.2 | 50.5 | -1.0096
707.3 | 50.5 | -1.0096
707.4 | 50.5 | -1.0096
707.5 | 50.5 | -1.0096
707.6 | 50.5 | -1.0096
707.7 | 50.5 | -1.0096
707.8 | 50.5 | -1.0096
707.9 | 50.5 | -1.0096
708 | 50.5 | -1.0096
708.1 | 50.5 | -1.0096
708.2 | 50.5 | -1.0096
708.3 | 50.5 | -1.0096
708.4 | 50.5 | -1.0096
708.5 | 50.5 | -1.0096
708.6 | 50.5 | -1.0096
708.7 | 50.5 | -1.0094
708.8 | 50.5 | -1.0094
708.9 | 50.5 | -1.0094
709 | 50.5 | -1.0094
709.1 | 50.5 | -1.0094
709.2 | 50.5 | -1.0094
709.3 | 50.5 | -1.0094
709.4 | 50.5 | -1.0094
709.5 | 50.5 | -1.0094
709.6 | 50.5 | -1.0094
709.7 | 50.5 | -1.0094
709.8 | 50.5 | -1.0094
709.9 | 50.5 | -1.0094
710 | 50.5 | -1.0094
710.1 | 50.5 | -1.0094
710.2 | 50.5 | -1.0094
710.3 | 50.5 | -1.0094
710.4 | 50.5 | -1.0094
710.5 | 50.5 | -1.0094
710.6 | 50.5 | -1.0094
710.7 | 50.5 | -1.0094
710.8 | 50.5 | -1.0094
710.9 | 50.5 | -1.0094
711 | 50.5 | -1.0094
711.1 | 50.5 | -1.0094
711.2 | 50.5 | -1.0096
711.3 | 50.5 | -1.0096
711.4 | 50.5 | -1.0096
711.5 | 50.5 | -1.0096
711.6 | 50.5 | -1.0096
711.7 | 50.5 | -1.0096
711.8 | 50.5 | -1.0096
711.9 | 50.5 | -1.0096
712 | 50.5 | -1.0096
712.1 | 50.5 | -1.0096
712.2 | 50.5 | -1.0096
712.3 | 50.5 | -1.0096
712.4 | 50.5 | -1.0096
712.5 | 50.5 | -1.0096
712.6 | 50.5 | -1.0096
712.7 | 50.5 | -1.0096
712.8 | 50.5 | -1.0096
712.9 | 50.5 | -1.0096
713 | 50.5 | -1.0096
713.1 | 50.5 | -1.0096
713.2 | 50.5 | -1.0096
713.3 | 50.5 | -1.0096
713.4 | 50.5 | -1.0096
713.5 | 50.5 | -1.0096
713.6 | 50.5 | -1.0096
713.7 | 50.5 | -1.0096
713.8 | 50.5 | -1.0096
713.9 | 50.5 | -1.0096
714 | 50.5 | -1.0096
714.1 | 50.5 | -1.0096
714.2 | 50.5 | -1.0096
714.3 | 50.5 | -1.0096
714.4 | 50.5 | -1.0096
714.5 | 50.5 | -1.0096
714.6 | 50.5 | -1.0096
714.7 | 50.5 | -1.0096
714.8 | 50.5 | -1.0096
714.9 | 50.5 | -1.0096
715 | 50.5 | -1.0096
715.1 | 50.5 | -1.0096
715.2 | 50.5 | -1.0096
715.3 | 50.5 | -1.0096
715.4 | 50.5 | -1.0096
715.5 | 50.5 | -1.0096
715.6 | 50.5 | -1.0096
715.7 | 50.5 | -1.0094
715.8 | 50.5 | -1.0094
715.9 | 50.5 | -1.0094
716 | 50.5 | -1.0094
716.1 | 50.5 | -1.0094
716.2 | 50.5 | -1.0094
716.3 | 50.5 | -1.0094
716.4 | 50.5 | -1.0094
716.5 | 50.5 | -1.0094
716.6 | 50.5 | -1.0094
716.7 | 50.5 | -1.0094
716.8 | 50.5 | -1.0094
716.9 | 50.5 | -1.0094
717 | 50.5 | -1.0094
717.1 | 50.5 | -1.0096
717.2 | 50.5 | -1.0096
717.3 | 50.5 | -1.0096
717.4 | 50.5 | -1.0096
717.5 | 50.5 | -1.0096
717.6 | 50.5 | -1.0096
717.7 | 50.5 | -1.0096
717.8 | 50.5 | -1.0096
717.9 | 50.5 | -1.0096
718 | 50.5 | -1.0096
718.1 | 50.5 | -1.0098
718.2 | 50.5 | -1.0098
718.3 | 50.5 | -1.0098
718.4 | 50.5 | -1.0098
718.5 | 50.5 | -1.0098
718.6 | 50.5 | -1.0098
718.7 | 50.5 | -1.0098
718.8 | 50.5 | -1.0098
718.9 | 50.5 | -1.0098
719 | 50.5 | -1.0098
719.1 | 50.5 | -1.0098
719.2 | 50.5 | -1.0098
719.3 | 50.5 | -1.0096
719.4 | 50.5 | -1.0096
719.5 | 50.5 | -1.0096
719.6 | 50.5 | -1.0096
719.7 | 50.5 | -1.0096
719.8 | 50.5 | -1.0096
719.9 | 50.5 | -1.0096
720 | 50.5 | -1.0096
720.1 | 50.5 | -1.0096
720.2 | 50.5 | -1.0096
720.3 | 50.5 | -1.0096
720.4 | 50.5 | -1.0096
720.5 | 50.5 | -1.0096
720.6 | 50.5 | -1.0096
720.7 | 50.5 | -1.0096
720.8 | 50.5 | -1.0096
720.9 | 50.5 | -1.0096
721 | 50.5 | -1.0096
721.1 | 50.5 | -1.0096
721.2 | 50.5 | -1.0096
721.3 | 50.5 | -1.0096
721.4 | 50.5 | -1.0096
721.5 | 50.5 | -1.0096
721.6 | 50.5 | -1.0096
721.7 | 50.5 | -1.0096
721.8 | 50.5 | -1.0096
721.9 | 50.5 | -1.0096
722 | 50.5 | -1.0096
722.1 | 50.5 | -1.0096
722.2 | 50.5 | -1.0096
722.3 | 50.5 | -1.0096
722.4 | 50.5 | -1.0096
722.5 | 50.5 | -1.0096
722.6 | 50.5 | -1.0096
722.7 | 50.5 | -1.0096
722.8 | 50.5 | -1.0096
722.9 | 50.5 | -1.0096
723 | 50.5 | -1.0096
723.1 | 50.5 | -1.0096
723.2 | 50.5 | -1.0096
723.3 | 50.5 | -1.0096
723.4 | 50.5 | -1.0096
723.5 | 50.5 | -1.0096
723.6 | 50.5 | -1.0096
723.7 | 50.5 | -1.0096
723.8 | 50.5 | -1.0096
723.9 | 50.5 | -1.0096
724 | 50.5 | -1.0096
724.1 | 50.5 | -1.0096
724.2 | 50.5 | -1.0096
724.3 | 50.5 | -1.0096
724.4 | 50.5 | -1.0096
724.5 | 50.5 | -1.0096
724.6 | 50.5 | -1.0096
724.7 | 50.5 | -1.0096
724.8 | 50.5 | -1.0096
724.9 | 50.5 | -1.0096
725 | 50.5 | -1.0096
725.1 | 50.5 | -1.0096
725.2 | 50.5 | -1.0096
725.3 | 50.5 | -1.0096
725.4 | 50.5 | -1.0096
725.5 | 50.5 | -1.0096
725.6 | 50.5 | -1.0096
725.7 | 50.5 | -1.0096
725.8 | 50.5 | -1.0096
725.9 | 50.5 | -1.0096
726 | 50.5 | -1.0096
726.1 | 50.5 | -1.0096
726.2 | 50.5 | -1.0096
726.3 | 50.5 | -1.0096
726.4 | 50.5 | -1.0096
726.5 | 50.5 | -1.0096
726.6 | 50.5 | -1.0096
726.7 | 50.5 | -1.0096
726.8 | 50.5 | -1.0096
726.9 | 50.5 | -1.0096
727 | 50.5 | -1.0096
727.1 | 50.5 | -1.0096
727.2 | 50.5 | -1.0096
727.3 | 50.5 | -1.0096
727.4 | 50.5 | -1.0096
727.5 | 50.5 | -1.0096
727.6 | 50.5 | -1.0096
727.7 | 50.5 | -1.0096
727.8 | 50.5 | -1.0096
727.9 | 50.5 | -1.0096
728 | 50.5 | -1.0096
728.1 | 50.5 | -1.0096
728.2 | 50.5 | -1.0096
728.3 | 50.5 | -1.0096
728.4 | 50.5 | -1.0096
728.5 | 50.5 | -1.0096
728.6 | 50.5 | -1.0096
728.7 | 50.5 | -1.0096
728.8 | 50.5 | -1.0096
728.9 | 50.5 | -1.0096
729 | 50.5 | -1.0096
729.1 | 50.5 | -1.0096
729.2 | 50.5 | -1.0096
729.3 | 50.5 | -1.0096
729.4 | 50.5 | -1.0096
729.5 | 50.5 | -1.0096
729.6 | 50.5 | -1.0096
729.7 | 50.5 | -1.0096
729.8 | 50.5 | -1.0096
729.9 | 50.5 | -1.0096
730 | 50.5 | -1.0096
730.1 | 50.5 | -1.0096
730.2 | 50.5 | -1.0096
730.3 | 50.5 | -1.0096
730.4 | 50.5 | -1.0096
730.5 | 50.5 | -1.0096
730.6 | 50.5 | -1.0096
730.7 | 50.5 | -1.0096
730.8 | 50.5 | -1.0096
730.9 | 50.5 | -1.0096
731 | 50.5 | -1.0096
731.1 | 50.5 | -1.0096
731.2 | 50.5 | -1.0096
731.3 | 50.5 | -1.0096
731.4 | 50.5 | -1.0096
731.5 | 50.5 | -1.0096
731.6 | 50.5 | -1.0096
731.7 | 50.5 | -1.0096
731.8 | 50.5 | -1.0096
731.9 | 50.5 | -1.0096
732 | 50.5 | -1.0096
732.1 | 50.5 | -1.0096
732.2 | 50.5 | -1.0096
732.3 | 50.5 | -1.0096
732.4 | 50.5 | -1.0096
732.5 | 50.5 | -1.0096
732.6 | 50.5 | -1.0096
732.7 | 50.5 | -1.0096
732.8 | 50.5 | -1.0096
732.9 | 50.5 | -1.0096
733 | 50.5 | -1.0096
733.1 | 50.5 | -1.0096
733.2 | 50.5 | -1.0096
733.3 | 50.5 | -1.0096
733.4 | 50.5 | -1.0096
733.5 | 50.5 | -1.0096
733.6 | 50.5 | -1.0096
733.7 | 50.5 | -1.0096
733.8 | 50.5 | -1.0096
733.9 | 50.5 | -1.0096
734 | 50.5 | -1.0096
734.1 | 50.5 | -1.0096
734.2 | 50.5 | -1.0096
734.3 | 50.5 | -1.0096
734.4 | 50.5 | -1.0096
734.5 | 50.5 | -1.0096
734.6 | 50.5 | -1.0096
734.7 | 50.5 | -1.0096
734.8 | 50.5 | -1.0096
734.9 | 50.5 | -1.0096
735 | 50.5 | -1.0096
735.1 | 50.5 | -1.0096
735.2 | 50.5 | -1.0096
735.3 | 50.5 | -1.0096
735.4 | 50.5 | -1.0096
735.5 | 50.5 | -1.0096
735.6 | 50.5 | -1.0096
735.7 | 50.5 | -1.0096
735.8 | 50.5 | -1.0094
735.9 | 50.5 | -1.0094
736 | 50.5 | -1.0094
736.1 | 50.5 | -1.0094
736.2 | 50.5 | -1.0094
736.3 | 50.5 | -1.0094
736.4 | 50.5 | -1.0094
736.5 | 50.5 | -1.0094
736.6 | 50.5 | -1.0094
736.7 | 50.5 | -1.0094
736.8 | 50.5 | -1.0094
736.9 | 50.5 | -1.0096
737 | 50.5 | -1.0096
737.1 | 50.5 | -1.0096
737.2 | 50.5 | -1.0096
737.3 | 50.5 | -1.0096
737.4 | 50.5 | -1.0096
737.5 | 50.5 | -1.0096
737.6 | 50.5 | -1.0096
737.7 | 50.5 | -1.0096
737.8 | 50.5 | -1.0096
737.9 | 50.5 | -1.0096
738 | 50.5 | -1.0096
738.1 | 50.5 | -1.0096
738.2 | 50.5 | -1.0096
738.3 | 50.5 | -1.0096
738.4 | 50.5 | -1.0096
738.5 | 50.5 | -1.0096
738.6 | 50.5 | -1.0096
738.7 | 50.5 | -1.0096
738.8 | 50.5 | -1.0096
738.9 | 50.5 | -1.0096
739 | 50.5 | -1.0096
739.1 | 50.5 | -1.0096
739.2 | 50.5 | -1.0096
739.3 | 50.5 | -1.0096
739.4 | 50.5 | -1.0096
739.5 | 50.5 | -1.0096
739.6 | 50.5 | -1.0096
739.7 | 50.5 | -1.0096
739.8 | 50.5 | -1.0096
739.9 | 50.5 | -1.0096
740 | 50.5 | -1.0096
740.1 | 50.5 | -1.0096
740.2 | 50.5 | -1.0096
740.3 | 50.5 | -1.0096
740.4 | 50.5 | -1.0098
740.5 | 50.5 | -1.0098
740.6 | 50.5 | -1.0098
740.7 | 50.5 | -1.0098
740.8 | 50.5 | -1.0098
740.9 | 50.5 | -1.0098
741 | 50.5 | -1.0098
741.1 | 50.5 | -1.0098
741.2 | 50.5 | -1.0098
741.3 | 50.5 | -1.0098
741.4 | 50.5 | -1.0098
741.5 | 50.5 | -1.0096
741.6 | 50.5 | -1.0096
741.7 | 50.5 | -1.0096
741.8 | 50.5 | -1.0096
741.9 | 50.5 | -1.0096
742 | 50.5 | -1.0096
742.1 | 50.5 | -1.0096
742.2 | 50.5 | -1.0096
742.3 | 50.5 | -1.0096
742.4 | 50.5 | -1.0096
742.5 | 50.5 | -1.0096
742.6 | 50.5 | -1.0094
742.7 | 50.5 | -1.0094
742.8 | 50.5 | -1.0094
742.9 | 50.5 | -1.0094
743 | 50.5 | -1.0094
743.1 | 50.5 | -1.0094
743.2 | 50.5 | -1.0094
743.3 | 50.5 | -1.0094
743.4 | 50.5 | -1.0094
743.5 | 50.5 | -1.0094
743.6 | 50.5 | -1.0096
743.7 | 50.5 | -1.0096
743.8 | 50.5 | -1.0094
743.9 | 50.5 | -1.0094
744 | 50.5 | -1.0094
744.1 | 50.5 | -1.0094
744.2 | 50.5 | -1.0094
744.3 | 50.5 | -1.0094
744.4 | 50.5 | -1.0094
744.5 | 50.5 | -1.0094
744.6 | 50.5 | -1.0094
744.7 | 50.5 | -1.0094
744.8 | 50.5 | -1.0094
744.9 | 50.5 | -1.0094
745 | 50.5 | -1.0094
745.1 | 50.5 | -1.0094
745.2 | 50.5 | -1.0094
745.3 | 50.5 | -1.0094
745.4 | 50.5 | -1.0094
745.5 | 50.5 | -1.0094
745.6 | 50.5 | -1.0094
745.7 | 50.5 | -1.0094
745.8 | 50.5 | -1.0094
745.9 | 50.5 | -1.0094
746 | 50.5 | -1.0094
746.1 | 50.5 | -1.0094
746.2 | 50.5 | -1.0096
746.3 | 50.5 | -1.0096
746.4 | 50.5 | -1.0096
746.5 | 50.5 | -1.0096
746.6 | 50.5 | -1.0096
746.7 | 50.5 | -1.0096
746.8 | 50.5 | -1.0096
746.9 | 50.5 | -1.0096
747 | 50.5 | -1.0096
747.1 | 50.5 | -1.0096
747.2 | 50.5 | -1.0096
747.3 | 50.5 | -1.0096
747.4 | 50.5 | -1.0096
747.5 | 50.5 | -1.0096
747.6 | 50.5 | -1.0096
747.7 | 50.5 | -1.0096
747.8 | 50.5 | -1.0096
747.9 | 50.5 | -1.0096
748 | 50.5 | -1.0096
748.1 | 50.5 | -1.0096
748.2 | 50.5 | -1.0096
748.3 | 50.5 | -1.0096
748.4 | 50.5 | -1.0096
748.5 | 50.5 | -1.0096
748.6 | 50.5 | -1.0094
748.7 | 50.5 | -1.0094
748.8 | 50.5 | -1.0094
748.9 | 50.5 | -1.0094
749 | 50.5 | -1.0094
749.1 | 50.5 | -1.0094
749.2 | 50.5 | -1.0094
749.3 | 50.5 | -1.0094
749.4 | 50.5 | -1.0094
749.5 | 50.5 | -1.0094
749.6 | 50.5 | -1.0094
749.7 | 50.5 | -1.0094
749.8 | 50.5 | -1.0094
749.9 | 50.5 | -1.0096
750 | 50.5 | -1.0096
750.1 | 50.5 | -1.0096
750.2 | 50.5 | -1.0096
750.3 | 50.5 | -1.0096
750.4 | 50.5 | -1.0096
750.5 | 50.5 | -1.0096
750.6 | 50.5 | -1.0096
750.7 | 50.5 | -1.0096
750.8 | 50.5 | -1.0096
750.9 | 50.5 | -1.0096
751 | 50.5 | -1.0096
751.1 | 50.5 | -1.0096
751.2 | 50.5 | -1.0096
751.3 | 50.5 | -1.0096
751.4 | 50.5 | -1.0096
751.5 | 50.5 | -1.0096
751.6 | 50.5 | -1.0096
751.7 | 50.5 | -1.0096
751.8 | 50.5 | -1.0096
751.9 | 50.5 | -1.0096
752 | 50.5 | -1.0096
752.1 | 50.5 | -1.0096
752.2 | 50.5 | -1.0096
752.3 | 50.5 | -1.0096
752.4 | 50.5 | -1.0096
752.5 | 50.5 | -1.0096
752.6 | 50.5 | -1.0096
752.7 | 50.5 | -1.0096
752.8 | 50.5 | -1.0096
752.9 | 50.5 | -1.0096
753 | 50.5 | -1.0096
753.1 | 50.5 | -1.0096
753.2 | 50.5 | -1.0096
753.3 | 50.5 | -1.0096
753.4 | 50.5 | -1.0096
753.5 | 50.5 | -1.0096
753.6 | 50.5 | -1.0096
753.7 | 50.5 | -1.0096
753.8 | 50.5 | -1.0096
753.9 | 50.5 | -1.0096
754 | 50.5 | -1.0096
754.1 | 50.5 | -1.0096
754.2 | 50.5 | -1.0096
754.3 | 50.5 | -1.0096
754.4 | 50.5 | -1.0096
754.5 | 50.5 | -1.0096
754.6 | 50.5 | -1.0096
754.7 | 50.5 | -1.0096
754.8 | 50.5 | -1.0096
754.9 | 50.5 | -1.0096
755 | 50.5 | -1.0096
755.1 | 50.5 | -1.0096
755.2 | 50.5 | -1.0096
755.3 | 50.5 | -1.0096
755.4 | 50.5 | -1.0096
755.5 | 50.5 | -1.0094
755.6 | 50.5 | -1.0094
755.7 | 50.5 | -1.0094
755.8 | 50.5 | -1.0094
755.9 | 50.5 | -1.0094
756 | 50.5 | -1.0094
756.1 | 50.5 | -1.0094
756.2 | 50.5 | -1.0094
756.3 | 50.5 | -1.0094
756.4 | 50.5 | -1.0094
756.5 | 50.5 | -1.0094
756.6 | 50.5 | -1.0094
756.7 | 50.5 | -1.0096
756.8 | 50.5 | -1.0096
756.9 | 50.5 | -1.0096
757 | 50.5 | -1.0096
757.1 | 50.5 | -1.0096
757.2 | 50.5 | -1.0096
757.3 | 50.5 | -1.0096
757.4 | 50.5 | -1.0096
757.5 | 50.5 | -1.0096
757.6 | 50.5 | -1.0096
757.7 | 50.5 | -1.0096
757.8 | 50.5 | -1.0096
757.9 | 50.5 | -1.0096
758 | 50.5 | -1.0096
758.1 | 50.5 | -1.0096
758.2 | 50.5 | -1.0096
758.3 | 50.5 | -1.0096
758.4 | 50.5 | -1.0096
758.5 | 50.5 | -1.0096
758.6 | 50.5 | -1.0096
758.7 | 50.5 | -1.0096
758.8 | 50.5 | -1.0096
758.9 | 50.5 | -1.0096
759 | 50.5 | -1.0096
759.1 | 50.5 | -1.0096
759.2 | 50.5 | -1.0096
759.3 | 50.5 | -1.0096
759.4 | 50.5 | -1.0096
759.5 | 50.5 | -1.0096
759.6 | 50.5 | -1.0096
759.7 | 50.5 | -1.0096
759.8 | 50.5 | -1.0096
759.9 | 50.5 | -1.0096
760 | 50.5 | -1.0096
760.1 | 50.5 | -1.0096
760.2 | 50.5 | -1.0096
760.3 | 50.5 | -1.0096
760.4 | 50.5 | -1.0096
760.5 | 50.5 | -1.0096
760.6 | 50.5 | -1.0096
760.7 | 50.5 | -1.0096
760.8 | 50.5 | -1.0096
760.9 | 50.5 | -1.0096
761 | 50.5 | -1.0096
761.1 | 50.5 | -1.0096
761.2 | 50.5 | -1.0096
761.3 | 50.5 | -1.0096
761.4 | 50.5 | -1.0094
761.5 | 50.5 | -1.0094
761.6 | 50.5 | -1.0094
761.7 | 50.5 | -1.0094
761.8 | 50.5 | -1.0094
761.9 | 50.5 | -1.0094
762 | 50.5 | -1.0094
762.1 | 50.5 | -1.0094
762.2 | 50.5 | -1.0094
762.3 | 50.5 | -1.0094
762.4 | 50.5 | -1.0094
762.5 | 50.5 | -1.0096
762.6 | 50.5 | -1.0096
762.7 | 50.5 | -1.0096
762.8 | 50.5 | -1.0096
762.9 | 50.5 | -1.0096
763 | 50.5 | -1.0096
763.1 | 50.5 | -1.0096
763.2 | 50.5 | -1.0096
763.3 | 50.5 | -1.0096
763.4 | 50.5 | -1.0096
763.5 | 50.5 | -1.0096
763.6 | 50.5 | -1.0096
763.7 | 50.5 | -1.0096
763.8 | 50.5 | -1.0096
763.9 | 50.5 | -1.0096
764 | 50.5 | -1.0096
764.1 | 50.5 | -1.0096
764.2 | 50.5 | -1.0096
764.3 | 50.5 | -1.0096
764.4 | 50.5 | -1.0096
764.5 | 50.5 | -1.0096
764.6 | 50.5 | -1.0096
764.7 | 50.5 | -1.0096
764.8 | 50.5 | -1.0096
764.9 | 50.5 | -1.0096
765 | 50.5 | -1.0096
765.1 | 50.5 | -1.0098
765.2 | 50.5 | -1.0098
765.3 | 50.5 | -1.0098
765.4 | 50.5 | -1.0098
765.5 | 50.5 | -1.0098
765.6 | 50.5 | -1.0098
765.7 | 50.5 | -1.0098
765.8 | 50.5 | -1.0098
765.9 | 50.5 | -1.0098
766 | 50.5 | -1.0096
766.1 | 50.5 | -1.0096
766.2 | 50.5 | -1.0096
766.3 | 50.5 | -1.0096
766.4 | 50.5 | -1.0096
766.5 | 50.5 | -1.0096
766.6 | 50.5 | -1.0096
766.7 | 50.5 | -1.0096
766.8 | 50.5 | -1.0096
766.9 | 50.5 | -1.0096
767 | 50.5 | -1.0096
767.1 | 50.5 | -1.0096
767.2 | 50.5 | -1.0094
767.3 | 50.5 | -1.0094
767.4 | 50.5 | -1.0094
767.5 | 50.5 | -1.0094
767.6 | 50.5 | -1.0094
767.7 | 50.5 | -1.0094
767.8 | 50.5 | -1.0094
767.9 | 50.5 | -1.0094
768 | 50.5 | -1.0094
768.1 | 50.5 | -1.0094
768.2 | 50.5 | -1.0094
768.3 | 50.5 | -1.0096
768.4 | 50.5 | -1.0096
768.5 | 50.5 | -1.0096
768.6 | 50.5 | -1.0096
768.7 | 50.5 | -1.0096
768.8 | 50.5 | -1.0096
768.9 | 50.5 | -1.0096
769 | 50.5 | -1.0096
769.1 | 50.5 | -1.0096
769.2 | 50.5 | -1.0096
769.3 | 50.5 | -1.0096
769.4 | 50.5 | -1.0096
769.5 | 50.5 | -1.0096
769.6 | 50.5 | -1.0096
769.7 | 50.5 | -1.0096
769.8 | 50.5 | -1.0096
769.9 | 50.5 | -1.0096
770 | 50.5 | -1.0096
770.1 | 50.5 | -1.0096
770.2 | 50.5 | -1.0096
770.3 | 50.5 | -1.0096
770.4 | 50.5 | -1.0096
770.5 | 50.5 | -1.0096
770.6 | 50.5 | -1.0096
770.7 | 50.5 | -1.0096
770.8 | 50.5 | -1.0096
770.9 | 50.5 | -1.0096
771 | 50.5 | -1.0096
771.1 | 50.5 | -1.0096
771.2 | 50.5 | -1.0096
771.3 | 50.5 | -1.0096
771.4 | 50.5 | -1.0096
771.5 | 50.5 | -1.0096
771.6 | 50.5 | -1.0096
771.7 | 50.5 | -1.0096
771.8 | 50.5 | -1.0096
771.9 | 50.5 | -1.0096
772 | 50.5 | -1.0096
772.1 | 50.5 | -1.0096
772.2 | 50.5 | -1.0096
772.3 | 50.5 | -1.0096
772.4 | 50.5 | -1.0096
772.5 | 50.5 | -1.0096
772.6 | 50.5 | -1.0096
772.7 | 50.5 | -1.0096
772.8 | 50.5 | -1.0096
772.9 | 50.5 | -1.0096
773 | 50.5 | -1.0096
773.1 | 50.5 | -1.0096
773.2 | 50.5 | -1.0096
773.3 | 50.5 | -1.0096
773.4 | 50.5 | -1.0096
773.5 | 50.5 | -1.0096
773.6 | 50.5 | -1.0096
773.7 | 50.5 | -1.0096
773.8 | 50.5 | -1.0096
773.9 | 50.5 | -1.0096
774 | 50.5 | -1.0096
774.1 | 50.5 | -1.0096
774.2 | 50.5 | -1.0096
774.3 | 50.5 | -1.0096
774.4 | 50.5 | -1.0096
774.5 | 50.5 | -1.0096
774.6 | 50.5 | -1.0096
774.7 | 50.5 | -1.0096
774.8 | 50.5 | -1.0096
774.9 | 50.5 | -1.0096
775 | 50.5 | -1.0096
775.1 | 50.5 | -1.0096
775.2 | 50.5 | -1.0096
775.3 | 50.5 | -1.0096
775.4 | 50.5 | -1.0096
775.5 | 50.5 | -1.0096
775.6 | 50.5 | -1.0096
775.7 | 50.5 | -1.0096
775.8 | 50.5 | -1.0096
775.9 | 50.5 | -1.0096
776 | 50.5 | -1.0096
776.1 | 50.5 | -1.0096
776.2 | 50.5 | -1.0094
776.3 | 50.5 | -1.0094
776.4 | 50.5 | -1.0094
776.5 | 50.5 | -1.0094
776.6 | 50.5 | -1.0094
776.7 | 50.5 | -1.0094
776.8 | 50.5 | -1.0094
776.9 | 50.5 | -1.0094
777 | 50.5 | -1.0094
777.1 | 50.5 | -1.0094
777.2 | 50.5 | -1.0094
777.3 | 50.5 | -1.0094
777.4 | 50.5 | -1.0094
777.5 | 50.5 | -1.0094
777.6 | 50.5 | -1.0094
777.7 | 50.5 | -1.0094
777.8 | 50.5 | -1.0094
777.9 | 50.5 | -1.0094
778 | 50.5 | -1.0094
778.1 | 50.5 | -1.0094
778.2 | 50.5 | -1.0094
778.3 | 50.5 | -1.0094
778.4 | 50.5 | -1.0094
778.5 | 50.5 | -1.0094
778.6 | 50.5 | -1.0094
778.7 | 50.5 | -1.0094
778.8 | 50.5 | -1.0094
778.9 | 50.5 | -1.0094
779 | 50.5 | -1.0094
779.1 | 50.5 | -1.0094
779.2 | 50.5 | -1.0094
779.3 | 50.5 | -1.0094
779.4 | 50.5 | -1.0094
779.5 | 50.5 | -1.0094
779.6 | 50.5 | -1.0096
779.7 | 50.5 | -1.0096
779.8 | 50.5 | -1.0096
779.9 | 50.5 | -1.0096
780 | 50.5 | -1.0096
780.1 | 50.5 | -1.0096
780.2 | 50.5 | -1.0096
780.3 | 50.5 | -1.0096
780.4 | 50.5 | -1.0096
780.5 | 50.5 | -1.0096
780.6 | 50.5 | -1.0096
780.7 | 50.5 | -1.0096
780.8 | 50.5 | -1.0096
780.9 | 50.5 | -1.0096
781 | 50.5 | -1.0096
781.1 | 50.5 | -1.0096
781.2 | 50.5 | -1.0096
781.3 | 50.5 | -1.0096
781.4 | 50.5 | -1.0096
781.5 | 50.5 | -1.0096
781.6 | 50.5 | -1.0096
781.7 | 50.5 | -1.0096
781.8 | 50.5 | -1.0096
781.9 | 50.5 | -1.0096
782 | 50.5 | -1.0096
782.1 | 50.5 | -1.0096
782.2 | 50.5 | -1.0096
782.3 | 50.5 | -1.0096
782.4 | 50.5 | -1.0096
782.5 | 50.5 | -1.0096
782.6 | 50.5 | -1.0096
782.7 | 50.5 | -1.0096
782.8 | 50.5 | -1.0096
782.9 | 50.5 | -1.0096
783 | 50.5 | -1.0096
783.1 | 50.5 | -1.0096
783.2 | 50.5 | -1.0096
783.3 | 50.5 | -1.0096
783.4 | 50.5 | -1.0096
783.5 | 50.5 | -1.0096
783.6 | 50.5 | -1.0096
783.7 | 50.5 | -1.0096
783.8 | 50.5 | -1.0096
783.9 | 50.5 | -1.0096
784 | 50.5 | -1.0096
784.1 | 50.5 | -1.0096
784.2 | 50.5 | -1.0096
784.3 | 50.5 | -1.0094
784.4 | 50.5 | -1.0094
784.5 | 50.5 | -1.0094
784.6 | 50.5 | -1.0094
784.7 | 50.5 | -1.0094
784.8 | 50.5 | -1.0094
784.9 | 50.5 | -1.0094
785 | 50.5 | -1.0094
785.1 | 50.5 | -1.0094
785.2 | 50.5 | -1.0094
785.3 | 50.5 | -1.0094
785.4 | 50.5 | -1.0094
785.5 | 50.5 | -1.0094
785.6 | 50.5 | -1.0094
785.7 | 50.5 | -1.0094
785.8 | 50.5 | -1.0094
785.9 | 50.5 | -1.0094
786 | 50.5 | -1.0094
786.1 | 50.5 | -1.0094
786.2 | 50.5 | -1.0094
786.3 | 50.5 | -1.0094
786.4 | 50.5 | -1.0094
786.5 | 50.5 | -1.0094
786.6 | 50.5 | -1.0094
786.7 | 50.5 | -1.0094
786.8 | 50.5 | -1.0094
786.9 | 50.5 | -1.0094
787 | 50.5 | -1.0094
787.1 | 50.5 | -1.0094
787.2 | 50.5 | -1.0094
787.3 | 50.5 | -1.0094
787.4 | 50.5 | -1.0094
787.5 | 50.5 | -1.0094
787.6 | 50.5 | -1.0094
787.7 | 50.5 | -1.0094
787.8 | 50.5 | -1.0094
787.9 | 50.5 | -1.0094
788 | 50.5 | -1.0094
788.1 | 50.5 | -1.0094
788.2 | 50.5 | -1.0094
788.3 | 50.5 | -1.0096
788.4 | 50.5 | -1.0096
788.5 | 50.5 | -1.0096
788.6 | 50.5 | -1.0096
788.7 | 50.5 | -1.0096
788.8 | 50.5 | -1.0096
788.9 | 50.5 | -1.0096
789 | 50.5 | -1.0096
789.1 | 50.5 | -1.0096
789.2 | 50.5 | -1.0096
789.3 | 50.5 | -1.0096
789.4 | 50.5 | -1.0096
789.5 | 50.5 | -1.0096
789.6 | 50.5 | -1.0096
789.7 | 50.5 | -1.0096
789.8 | 50.5 | -1.0096
789.9 | 50.5 | -1.0096
790 | 50.5 | -1.0096
790.1 | 50.5 | -1.0096
790.2 | 50.5 | -1.0096
790.3 | 50.5 | -1.0096
790.4 | 50.5 | -1.0096
790.5 | 50.5 | -1.0096
790.6 | 50.5 | -1.0096
790.7 | 50.5 | -1.0096
790.8 | 50.5 | -1.0096
790.9 | 50.5 | -1.0096
791 | 50.5 | -1.0096
791.1 | 50.5 | -1.0096
791.2 | 50.5 | -1.0096
791.3 | 50.5 | -1.0096
791.4 | 50.5 | -1.0096
791.5 | 50.5 | -1.0096
791.6 | 50.5 | -1.0096
791.7 | 50.5 | -1.0096
791.8 | 50.5 | -1.0094
791.9 | 50.5 | -1.0094
792 | 50.5 | -1.0094
792.1 | 50.5 | -1.0094
792.2 | 50.5 | -1.0094
792.3 | 50.5 | -1.0094
792.4 | 50.5 | -1.0094
792.5 | 50.5 | -1.0094
792.6 | 50.5 | -1.0094
792.7 | 50.5 | -1.0094
792.8 | 50.5 | -1.0094
792.9 | 50.5 | -1.0094
793 | 50.5 | -1.0094
793.1 | 50.5 | -1.0094
793.2 | 50.5 | -1.0094
793.3 | 50.5 | -1.0094
793.4 | 50.5 | -1.0094
793.5 | 50.5 | -1.0094
793.6 | 50.5 | -1.0094
793.7 | 50.5 | -1.0094
793.8 | 50.5 | -1.0094
793.9 | 50.5 | -1.0094
794 | 50.5 | -1.0094
794.1 | 50.5 | -1.0094
794.2 | 50.5 | -1.0096
794.3 | 50.5 | -1.0096
794.4 | 50.5 | -1.0096
794.5 | 50.5 | -1.0096
794.6 | 50.5 | -1.0096
794.7 | 50.5 | -1.0096
794.8 | 50.5 | -1.0096
794.9 | 50.5 | -1.0096
795 | 50.5 | -1.0096
795.1 | 50.5 | -1.0096
795.2 | 50.5 | -1.0096
795.3 | 50.5 | -1.0096
795.4 | 50.5 | -1.0096
795.5 | 50.5 | -1.0096
795.6 | 50.5 | -1.0096
795.7 | 50.5 | -1.0096
795.8 | 50.5 | -1.0096
795.9 | 50.5 | -1.0096
796 | 50.5 | -1.0096
796.1 | 50.5 | -1.0096
796.2 | 50.5 | -1.0096
796.3 | 50.5 | -1.0096
796.4 | 50.5 | -1.0096
796.5 | 50.5 | -1.0096
796.6 | 50.5 | -1.0096
796.7 | 50.5 | -1.0096
796.8 | 50.5 | -1.0096
796.9 | 50.5 | -1.0096
797 | 50.5 | -1.0096
797.1 | 50.5 | -1.0096
797.2 | 50.5 | -1.0096
797.3 | 50.5 | -1.0096
797.4 | 50.5 | -1.0096
797.5 | 50.5 | -1.0096
797.6 | 50.5 | -1.0096
797.7 | 50.5 | -1.0096
797.8 | 50.5 | -1.0096
797.9 | 50.5 | -1.0096
798 | 50.5 | -1.0096
798.1 | 50.5 | -1.0096
798.2 | 50.5 | -1.0096
798.3 | 50.5 | -1.0096
798.4 | 50.5 | -1.0096
798.5 | 50.5 | -1.0096
798.6 | 50.5 | -1.0096
798.7 | 50.5 | -1.0096
798.8 | 50.5 | -1.0096
798.9 | 50.5 | -1.0096
799 | 50.5 | -1.0096
799.1 | 50.5 | -1.0096
799.2 | 50.5 | -1.0096
799.3 | 50.5 | -1.0096
799.4 | 50.5 | -1.0096
799.5 | 50.5 | -1.0096
799.6 | 50.5 | -1.0096
799.7 | 50.5 | -1.0096
799.8 | 50.5 | -1.0096
799.9 | 50.5 | -1.0096
800 | 50.5 | -1.0096
800.1 | 50.5 | -1.0096
800.2 | 50.5 | -1.0096
800.3 | 50.5 | -1.0096
800.4 | 50.5 | -1.0096
800.5 | 50.5 | -1.0096
800.6 | 50.5 | -1.0096
800.7 | 50.5 | -1.0096
800.8 | 50.5 | -1.0096
800.9 | 50.5 | -1.0096
801 | 50.5 | -1.0096
801.1 | 50.5 | -1.0096
801.2 | 50.5 | -1.0096
801.3 | 50.5 | -1.0096
801.4 | 50.5 | -1.0096
801.5 | 50.5 | -1.0096
801.6 | 50.5 | -1.0096
801.7 | 50.5 | -1.0096
801.8 | 50.5 | -1.0096
801.9 | 50.5 | -1.0096
802 | 50.5 | -1.0096
802.1 | 50.5 | -1.0096
802.2 | 50.5 | -1.0096
802.3 | 50.5 | -1.0096
802.4 | 50.5 | -1.0096
802.5 | 50.5 | -1.0096
802.6 | 50.5 | -1.0096
802.7 | 50.5 | -1.0096
802.8 | 50.5 | -1.0096
802.9 | 50.5 | -1.0096
803 | 50.5 | -1.0096
803.1 | 50.5 | -1.0096
803.2 | 50.5 | -1.0096
803.3 | 50.5 | -1.0096
803.4 | 50.5 | -1.0096
803.5 | 50.5 | -1.0096
803.6 | 50.5 | -1.0094
803.7 | 50.5 | -1.0094
803.8 | 50.5 | -1.0094
803.9 | 50.5 | -1.0094
804 | 50.5 | -1.0094
804.1 | 50.5 | -1.0094
804.2 | 50.5 | -1.0094
804.3 | 50.5 | -1.0094
804.4 | 50.5 | -1.0094
804.5 | 50.5 | -1.0094
804.6 | 50.5 | -1.0094
804.7 | 50.5 | -1.0094
804.8 | 50.5 | -1.0096
804.9 | 50.5 | -1.0096
805 | 50.5 | -1.0096
805.1 | 50.5 | -1.0096
805.2 | 50.5 | -1.0096
805.3 | 50.5 | -1.0096
805.4 | 50.5 | -1.0096
805.5 | 50.5 | -1.0096
805.6 | 50.5 | -1.0096
805.7 | 50.5 | -1.0096
805.8 | 50.5 | -1.0096
805.9 | 50.5 | -1.0096
806 | 50.5 | -1.0096
806.1 | 50.5 | -1.0096
806.2 | 50.5 | -1.0096
806.3 | 50.5 | -1.0096
806.4 | 50.5 | -1.0096
806.5 | 50.5 | -1.0096
806.6 | 50.5 | -1.0096
806.7 | 50.5 | -1.0096
806.8 | 50.5 | -1.0096
806.9 | 50.5 | -1.0096
807 | 50.5 | -1.0096
807.1 | 50.5 | -1.0096
807.2 | 50.5 | -1.0096
807.3 | 50.5 | -1.0096
807.4 | 50.5 | -1.0096
807.5 | 50.5 | -1.0096
807.6 | 50.5 | -1.0096
807.7 | 50.5 | -1.0096
807.8 | 50.5 | -1.0096
807.9 | 50.5 | -1.0096
808 | 50.5 | -1.0096
808.1 | 50.5 | -1.0096
808.2 | 50.5 | -1.0096
808.3 | 50.5 | -1.0096
808.4 | 50.5 | -1.0096
808.5 | 50.5 | -1.0096
808.6 | 50.5 | -1.0096
808.7 | 50.5 | -1.0096
808.8 | 50.5 | -1.0096
808.9 | 50.5 | -1.0096
809 | 50.5 | -1.0096
809.1 | 50.5 | -1.0096
809.2 | 50.5 | -1.0096
809.3 | 50.5 | -1.0096
809.4 | 50.5 | -1.0096
809.5 | 50.5 | -1.0096
809.6 | 50.5 | -1.0096
809.7 | 50.5 | -1.0096
809.8 | 50.5 | -1.0096
809.9 | 50.5 | -1.0096
810 | 50.5 | -1.0096
810.1 | 50.5 | -1.0096
810.2 | 50.5 | -1.0096
810.3 | 50.5 | -1.0096
810.4 | 50.5 | -1.0096
810.5 | 50.5 | -1.0096
810.6 | 50.5 | -1.0096
810.7 | 50.5 | -1.0096
810.8 | 50.5 | -1.0096
810.9 | 50.5 | -1.0096
811 | 50.5 | -1.0096
811.1 | 50.5 | -1.0096
811.2 | 50.5 | -1.0096
811.3 | 50.5 | -1.0096
811.4 | 50.5 | -1.0096
811.5 | 50.5 | -1.0096
811.6 | 50.5 | -1.0096
811.7 | 50.5 | -1.0096
811.8 | 50.5 | -1.0096
811.9 | 50.5 | -1.0096
812 | 50.5 | -1.0096
812.1 | 50.5 | -1.0096
812.2 | 50.5 | -1.0096
812.3 | 50.5 | -1.0096
812.4 | 50.5 | -1.0096
812.5 | 50.5 | -1.0096
812.6 | 50.5 | -1.0096
812.7 | 50.5 | -1.0096
812.8 | 50.5 | -1.0096
812.9 | 50.5 | -1.0096
813 | 50.5 | -1.0096
813.1 | 50.5 | -1.0096
813.2 | 50.5 | -1.0096
813.3 | 50.5 | -1.0096
813.4 | 50.5 | -1.0096
813.5 | 50.5 | -1.0096
813.6 | 50.5 | -1.0096
813.7 | 50.5 | -1.0096
813.8 | 50.5 | -1.0096
813.9 | 50.5 | -1.0096
814 | 50.5 | -1.0096
814.1 | 50.5 | -1.0096
814.2 | 50.5 | -1.0096
814.3 | 50.5 | -1.0096
814.4 | 50.5 | -1.0096
814.5 | 50.5 | -1.0096
814.6 | 50.5 | -1.0096
814.7 | 50.5 | -1.0096
814.8 | 50.5 | -1.0096
814.9 | 50.5 | -1.0096
815 | 50.5 | -1.0096
815.1 | 50.5 | -1.0096
815.2 | 50.5 | -1.0096
815.3 | 50.5 | -1.0096
815.4 | 50.5 | -1.0096
815.5 | 50.5 | -1.0096
815.6 | 50.5 | -1.0096
815.7 | 50.5 | -1.0096
815.8 | 50.5 | -1.0096
815.9 | 50.5 | -1.0096
816 | 50.5 | -1.0096
816.1 | 50.5 | -1.0096
816.2 | 50.5 | -1.0096
816.3 | 50.5 | -1.0096
816.4 | 50.5 | -1.0096
816.5 | 50.5 | -1.0096
816.6 | 50.5 | -1.0096
816.7 | 50.5 | -1.0096
816.8 | 50.5 | -1.0096
816.9 | 50.5 | -1.0096
817 | 50.5 | -1.0096
817.1 | 50.5 | -1.0096
817.2 | 50.5 | -1.0096
817.3 | 50.5 | -1.0096
817.4 | 50.5 | -1.0096
817.5 | 50.5 | -1.0096
817.6 | 50.5 | -1.0096
817.7 | 50.5 | -1.0096
817.8 | 50.5 | -1.0094
817.9 | 50.5 | -1.0094
818 | 50.5 | -1.0094
818.1 | 50.5 | -1.0094
818.2 | 50.5 | -1.0094
818.3 | 50.5 | -1.0094
818.4 | 50.5 | -1.0094
818.5 | 50.5 | -1.0094
818.6 | 50.5 | -1.0094
818.7 | 50.5 | -1.0094
818.8 | 50.5 | -1.0094
818.9 | 50.5 | -1.0094
819 | 50.5 | -1.0094
819.1 | 50.5 | -1.0094
819.2 | 50.5 | -1.0094
819.3 | 50.5 | -1.0094
819.4 | 50.5 | -1.0094
819.5 | 50.5 | -1.0094
819.6 | 50.5 | -1.0094
819.7 | 50.5 | -1.0094
819.8 | 50.5 | -1.0094
819.9 | 50.5 | -1.0094
820 | 50.5 | -1.0096
820.1 | 50.5 | -1.0096
820.2 | 50.5 | -1.0096
820.3 | 50.5 | -1.0096
820.4 | 50.5 | -1.0096
820.5 | 50.5 | -1.0096
820.6 | 50.5 | -1.0096
820.7 | 50.5 | -1.0096
820.8 | 50.5 | -1.0096
820.9 | 50.5 | -1.0096
821 | 50.5 | -1.0096
821.1 | 50.5 | -1.0096
821.2 | 50.5 | -1.0096
821.3 | 50.5 | -1.0096
821.4 | 50.5 | -1.0096
821.5 | 50.5 | -1.0096
821.6 | 50.5 | -1.0096
821.7 | 50.5 | -1.0096
821.8 | 50.5 | -1.0096
821.9 | 50.5 | -1.0096
822 | 50.5 | -1.0096
822.1 | 50.5 | -1.0096
822.2 | 50.5 | -1.0096
822.3 | 50.5 | -1.0096
822.4 | 50.5 | -1.0096
822.5 | 50.5 | -1.0096
822.6 | 50.5 | -1.0096
822.7 | 50.5 | -1.0096
822.8 | 50.5 | -1.0096
822.9 | 50.5 | -1.0096
823 | 50.5 | -1.0096
823.1 | 50.5 | -1.0096
823.2 | 50.5 | -1.0096
823.3 | 50.5 | -1.0096
823.4 | 50.5 | -1.0096
823.5 | 50.5 | -1.0096
823.6 | 50.5 | -1.0096
823.7 | 50.5 | -1.0096
823.8 | 50.5 | -1.0096
823.9 | 50.5 | -1.0096
824 | 50.5 | -1.0096
824.1 | 50.5 | -1.0096
824.2 | 50.5 | -1.0096
824.3 | 50.5 | -1.0096
824.4 | 50.5 | -1.0096
824.5 | 50.5 | -1.0096
824.6 | 50.5 | -1.0096
824.7 | 50.5 | -1.0096
824.8 | 50.5 | -1.0096
824.9 | 50.5 | -1.0096
825 | 50.5 | -1.0096
825.1 | 50.5 | -1.0096
825.2 | 50.5 | -1.0096
825.3 | 50.5 | -1.0096
825.4 | 50.5 | -1.0096
825.5 | 50.5 | -1.0096
825.6 | 50.5 | -1.0096
825.7 | 50.5 | -1.0096
825.8 | 50.5 | -1.0096
825.9 | 50.5 | -1.0096
826 | 50.5 | -1.0096
826.1 | 50.5 | -1.0096
826.2 | 50.5 | -1.0096
826.3 | 50.5 | -1.0096
826.4 | 50.5 | -1.0096
826.5 | 50.5 | -1.0096
826.6 | 50.5 | -1.0096
826.7 | 50.5 | -1.0096
826.8 | 50.5 | -1.0096
826.9 | 50.5 | -1.0096
827 | 50.5 | -1.0096
827.1 | 50.5 | -1.0096
827.2 | 50.5 | -1.0096
827.3 | 50.5 | -1.0096
827.4 | 50.5 | -1.0096
827.5 | 50.5 | -1.0096
827.6 | 50.5 | -1.0096
827.7 | 50.5 | -1.0096
827.8 | 50.5 | -1.0096
827.9 | 50.5 | -1.0096
828 | 50.5 | -1.0096
828.1 | 50.5 | -1.0096
828.2 | 50.5 | -1.0096
828.3 | 50.5 | -1.0096
828.4 | 50.5 | -1.0096
828.5 | 50.5 | -1.0096
828.6 | 50.5 | -1.0094
828.7 | 50.5 | -1.0094
828.8 | 50.5 | -1.0094
828.9 | 50.5 | -1.0094
829 | 50.5 | -1.0094
829.1 | 50.5 | -1.0094
829.2 | 50.5 | -1.0094
829.3 | 50.5 | -1.0094
829.4 | 50.5 | -1.0094
829.5 | 50.5 | -1.0094
829.6 | 50.5 | -1.0096
829.7 | 50.5 | -1.0096
829.8 | 50.5 | -1.0096
829.9 | 50.5 | -1.0096
830 | 50.5 | -1.0096
830.1 | 50.5 | -1.0096
830.2 | 50.5 | -1.0096
830.3 | 50.5 | -1.0096
830.4 | 50.5 | -1.0096
830.5 | 50.5 | -1.0096
830.6 | 50.5 | -1.0096
830.7 | 50.5 | -1.0096
830.8 | 50.5 | -1.0096
830.9 | 50.5 | -1.0096
831 | 50.5 | -1.0096
831.1 | 50.5 | -1.0096
831.2 | 50.5 | -1.0096
831.3 | 50.5 | -1.0096
831.4 | 50.5 | -1.0096
831.5 | 50.5 | -1.0096
831.6 | 50.5 | -1.0096
831.7 | 50.5 | -1.0096
831.8 | 50.5 | -1.0096
831.9 | 50.5 | -1.0096
832 | 50.5 | -1.0096
832.1 | 50.5 | -1.0096
832.2 | 50.5 | -1.0096
832.3 | 50.5 | -1.0096
832.4 | 50.5 | -1.0096
832.5 | 50.5 | -1.0096
832.6 | 50.5 | -1.0096
832.7 | 50.5 | -1.0096
832.8 | 50.5 | -1.0096
832.9 | 50.5 | -1.0096
833 | 50.5 | -1.0096
833.1 | 50.5 | -1.0096
833.2 | 50.5 | -1.0096
833.3 | 50.5 | -1.0096
833.4 | 50.5 | -1.0096
833.5 | 50.5 | -1.0096
833.6 | 50.5 | -1.0096
833.7 | 50.5 | -1.0096
833.8 | 50.5 | -1.0096
833.9 | 50.5 | -1.0096
834 | 50.5 | -1.0096
834.1 | 50.5 | -1.0096
834.2 | 50.5 | -1.0096
834.3 | 50.5 | -1.0096
834.4 | 50.5 | -1.0096
834.5 | 50.5 | -1.0096
834.6 | 50.5 | -1.0096
834.7 | 50.5 | -1.0096
834.8 | 50.5 | -1.0096
834.9 | 50.5 | -1.0096
835 | 50.5 | -1.0094
835.1 | 50.5 | -1.0094
835.2 | 50.5 | -1.0094
835.3 | 50.5 | -1.0094
835.4 | 50.5 | -1.0094
835.5 | 50.5 | -1.0094
835.6 | 50.5 | -1.0094
835.7 | 50.5 | -1.0094
835.8 | 50.5 | -1.0094
835.9 | 50.5 | -1.0094
836 | 50.5 | -1.0096
836.1 | 50.5 | -1.0096
836.2 | 50.5 | -1.0096
836.3 | 50.5 | -1.0096
836.4 | 50.5 | -1.0096
836.5 | 50.5 | -1.0096
836.6 | 50.5 | -1.0096
836.7 | 50.5 | -1.0096
836.8 | 50.5 | -1.0096
836.9 | 50.5 | -1.0096
837 | 50.5 | -1.0096
837.1 | 50.5 | -1.0096
837.2 | 50.5 | -1.0096
837.3 | 50.5 | -1.0096
837.4 | 50.5 | -1.0096
837.5 | 50.5 | -1.0096
837.6 | 50.5 | -1.0096
837.7 | 50.5 | -1.0096
837.8 | 50.5 | -1.0096
837.9 | 50.5 | -1.0096
838 | 50.5 | -1.0096
838.1 | 50.5 | -1.0096
838.2 | 50.5 | -1.0096
838.3 | 50.5 | -1.0096
838.4 | 50.5 | -1.0096
838.5 | 50.5 | -1.0096
838.6 | 50.5 | -1.0096
838.7 | 50.5 | -1.0096
838.8 | 50.5 | -1.0096
838.9 | 50.5 | -1.0096
839 | 50.5 | -1.0096
839.1 | 50.5 | -1.0096
839.2 | 50.5 | -1.0096
839.3 | 50.5 | -1.0096
839.4 | 50.5 | -1.0096
839.5 | 50.5 | -1.0096
839.6 | 50.5 | -1.0096
839.7 | 50.5 | -1.0096
839.8 | 50.5 | -1.0096
839.9 | 50.5 | -1.0096
840 | 50.5 | -1.0096
840.1 | 50.5 | -1.0096
840.2 | 50.5 | -1.0096
840.3 | 50.5 | -1.0096
840.4 | 50.5 | -1.0096
840.5 | 50.5 | -1.0096
840.6 | 50.5 | -1.0096
840.7 | 50.5 | -1.0096
840.8 | 50.5 | -1.0096
840.9 | 50.5 | -1.0096
841 | 50.5 | -1.0096
841.1 | 50.5 | -1.0096
841.2 | 50.5 | -1.0096
841.3 | 50.5 | -1.0096
841.4 | 50.5 | -1.0096
841.5 | 50.5 | -1.0096
841.6 | 50.5 | -1.0096
841.7 | 50.5 | -1.0096
841.8 | 50.5 | -1.0096
841.9 | 50.5 | -1.0096
842 | 50.5 | -1.0096
842.1 | 50.5 | -1.0096
842.2 | 50.5 | -1.0096
842.3 | 50.5 | -1.0096
842.4 | 50.5 | -1.0096
842.5 | 50.5 | -1.0096
842.6 | 50.5 | -1.0096
842.7 | 50.5 | -1.0096
842.8 | 50.5 | -1.0096
842.9 | 50.5 | -1.0096
843 | 50.5 | -1.0096
843.1 | 50.5 | -1.0096
843.2 | 50.5 | -1.0096
843.3 | 50.5 | -1.0096
843.4 | 50.5 | -1.0096
843.5 | 50.5 | -1.0096
843.6 | 50.5 | -1.0094
843.7 | 50.5 | -1.0094
843.8 | 50.5 | -1.0094
843.9 | 50.5 | -1.0094
844 | 50.5 | -1.0094
844.1 | 50.5 | -1.0094
844.2 | 50.5 | -1.0094
844.3 | 50.5 | -1.0094
844.4 | 50.5 | -1.0094
844.5 | 50.5 | -1.0094
844.6 | 50.5 | -1.0094
844.7 | 50.5 | -1.0094
844.8 | 50.5 | -1.0096
844.9 | 50.5 | -1.0096
845 | 50.5 | -1.0094
845.1 | 50.5 | -1.0094
845.2 | 50.5 | -1.0094
845.3 | 50.5 | -1.0094
845.4 | 50.5 | -1.0094
845.5 | 50.5 | -1.0094
845.6 | 50.5 | -1.0094
845.7 | 50.5 | -1.0094
845.8 | 50.5 | -1.0094
845.9 | 50.5 | -1.0094
846 | 50.5 | -1.0094
846.1 | 50.5 | -1.0094
846.2 | 50.5 | -1.0094
846.3 | 50.5 | -1.0094
846.4 | 50.5 | -1.0094
846.5 | 50.5 | -1.0094
846.6 | 50.5 | -1.0094
846.7 | 50.5 | -1.0094
846.8 | 50.5 | -1.0094
846.9 | 50.5 | -1.0094
847 | 50.5 | -1.0094
847.1 | 50.5 | -1.0094
847.2 | 50.5 | -1.0096
847.3 | 50.5 | -1.0096
847.4 | 50.5 | -1.0096
847.5 | 50.5 | -1.0096
847.6 | 50.5 | -1.0096
847.7 | 50.5 | -1.0096
847.8 | 50.5 | -1.0096
847.9 | 50.5 | -1.0096
848 | 50.5 | -1.0096
848.1 | 50.5 | -1.0096
848.2 | 50.5 | -1.0096
848.3 | 50.5 | -1.0096
848.4 | 50.5 | -1.0096
848.5 | 50.5 | -1.0096
848.6 | 50.5 | -1.0096
848.7 | 50.5 | -1.0096
848.8 | 50.5 | -1.0096
848.9 | 50.5 | -1.0096
849 | 50.5 | -1.0096
849.1 | 50.5 | -1.0096
849.2 | 50.5 | -1.0096
849.3 | 50.5 | -1.0096
849.4 | 50.5 | -1.0096
849.5 | 50.5 | -1.0096
849.6 | 50.5 | -1.0096
849.7 | 50.5 | -1.0096
849.8 | 50.5 | -1.0096
849.9 | 50.5 | -1.0096
850 | 50.5 | -1.0096
850.1 | 50.5 | -1.0096
850.2 | 50.5 | -1.0096
850.3 | 50.5 | -1.0096
850.4 | 50.5 | -1.0096
850.5 | 50.5 | -1.0096
850.6 | 50.5 | -1.0096
850.7 | 50.5 | -1.0096
850.8 | 50.5 | -1.0096
850.9 | 50.5 | -1.0096
851 | 50.5 | -1.0096
851.1 | 50.5 | -1.0096
851.2 | 50.5 | -1.0096
851.3 | 50.5 | -1.0096
851.4 | 50.5 | -1.0096
851.5 | 50.5 | -1.0096
851.6 | 50.5 | -1.0096
851.7 | 50.5 | -1.0096
851.8 | 50.5 | -1.0096
851.9 | 50.5 | -1.0096
852 | 50.5 | -1.0096
852.1 | 50.5 | -1.0096
852.2 | 50.5 | -1.0096
852.3 | 50.5 | -1.0096
852.4 | 50.5 | -1.0096
852.5 | 50.5 | -1.0096
852.6 | 50.5 | -1.0096
852.7 | 50.5 | -1.0096
852.8 | 50.5 | -1.0096
852.9 | 50.5 | -1.0096
853 | 50.5 | -1.0094
853.1 | 50.5 | -1.0094
853.2 | 50.5 | -1.0094
853.3 | 50.5 | -1.0094
853.4 | 50.5 | -1.0094
853.5 | 50.5 | -1.0094
853.6 | 50.5 | -1.0094
853.7 | 50.5 | -1.0094
853.8 | 50.5 | -1.0094
853.9 | 50.5 | -1.0094
854 | 50.5 | -1.0094
854.1 | 50.5 | -1.0094
854.2 | 50.5 | -1.0094
854.3 | 50.5 | -1.0096
854.4 | 50.5 | -1.0096
854.5 | 50.5 | -1.0096
854.6 | 50.5 | -1.0096
854.7 | 50.5 | -1.0096
854.8 | 50.5 | -1.0096
854.9 | 50.5 | -1.0096
855 | 50.5 | -1.0096
855.1 | 50.5 | -1.0096
855.2 | 50.5 | -1.0096
855.3 | 50.5 | -1.0096
855.4 | 50.5 | -1.0096
855.5 | 50.5 | -1.0096
855.6 | 50.5 | -1.0096
855.7 | 50.5 | -1.0096
855.8 | 50.5 | -1.0096
855.9 | 50.5 | -1.0096
856 | 50.5 | -1.0096
856.1 | 50.5 | -1.0096
856.2 | 50.5 | -1.0096
856.3 | 50.5 | -1.0096
856.4 | 50.5 | -1.0096
856.5 | 50.5 | -1.0096
856.6 | 50.5 | -1.0096
856.7 | 50.5 | -1.0096
856.8 | 50.5 | -1.0096
856.9 | 50.5 | -1.0096
857 | 50.5 | -1.0096
857.1 | 50.5 | -1.0096
857.2 | 50.5 | -1.0096
857.3 | 50.5 | -1.0096
857.4 | 50.5 | -1.0096
857.5 | 50.5 | -1.0096
857.6 | 50.5 | -1.0096
857.7 | 50.5 | -1.0096
857.8 | 50.5 | -1.0096
857.9 | 50.5 | -1.0096
858 | 50.5 | -1.0096
858.1 | 50.5 | -1.0096
858.2 | 50.5 | -1.0096
858.3 | 50.5 | -1.0096
858.4 | 50.5 | -1.0096
858.5 | 50.5 | -1.0096
858.6 | 50.5 | -1.0096
858.7 | 50.5 | -1.0096
858.8 | 50.5 | -1.0096
858.9 | 50.5 | -1.0094
859 | 50.5 | -1.0094
859.1 | 50.5 | -1.0094
859.2 | 50.5 | -1.0094
859.3 | 50.5 | -1.0094
859.4 | 50.5 | -1.0094
859.5 | 50.5 | -1.0094
859.6 | 50.5 | -1.0094
859.7 | 50.5 | -1.0094
859.8 | 50.5 | -1.0094
859.9 | 50.5 | -1.0094
860 | 50.5 | -1.0096
860.1 | 50.5 | -1.0096
860.2 | 50.5 | -1.0096
860.3 | 50.5 | -1.0096
860.4 | 50.5 | -1.0096
860.5 | 50.5 | -1.0096
860.6 | 50.5 | -1.0096
860.7 | 50.5 | -1.0096
860.8 | 50.5 | -1.0096
860.9 | 50.5 | -1.0096
861 | 50.5 | -1.0096
861.1 | 50.5 | -1.0096
861.2 | 50.5 | -1.0096
861.3 | 50.5 | -1.0096
861.4 | 50.5 | -1.0096
861.5 | 50.5 | -1.0096
861.6 | 50.5 | -1.0096
861.7 | 50.5 | -1.0096
861.8 | 50.5 | -1.0096
861.9 | 50.5 | -1.0096
862 | 50.5 | -1.0096
862.1 | 50.5 | -1.0096
862.2 | 50.5 | -1.0096
862.3 | 50.5 | -1.0096
862.4 | 50.5 | -1.0096
862.5 | 50.5 | -1.0096
862.6 | 50.5 | -1.0096
862.7 | 50.5 | -1.0096
862.8 | 50.5 | -1.0096
862.9 | 50.5 | -1.0096
863 | 50.5 | -1.0096
863.1 | 50.5 | -1.0096
863.2 | 50.5 | -1.0096
863.3 | 50.5 | -1.0096
863.4 | 50.5 | -1.0096
863.5 | 50.5 | -1.0096
863.6 | 50.5 | -1.0096
863.7 | 50.5 | -1.0096
863.8 | 50.5 | -1.0096
863.9 | 50.5 | -1.0096
864 | 50.5 | -1.0096
864.1 | 50.5 | -1.0096
864.2 | 50.5 | -1.0096
864.3 | 50.5 | -1.0096
864.4 | 50.5 | -1.0096
864.5 | 50.5 | -1.0096
864.6 | 50.5 | -1.0096
864.7 | 50.5 | -1.0096
864.8 | 50.5 | -1.0096
864.9 | 50.5 | -1.0096
865 | 50.5 | -1.0096
865.1 | 50.5 | -1.0096
865.2 | 50.5 | -1.0096
865.3 | 50.5 | -1.0096
865.4 | 50.5 | -1.0096
865.5 | 50.5 | -1.0096
865.6 | 50.5 | -1.0096
865.7 | 50.5 | -1.0096
865.8 | 50.5 | -1.0096
865.9 | 50.5 | -1.0096
866 | 50.5 | -1.0096
866.1 | 50.5 | -1.0096
866.2 | 50.5 | -1.0096
866.3 | 50.5 | -1.0096
866.4 | 50.5 | -1.0096
866.5 | 50.5 | -1.0096
866.6 | 50.5 | -1.0096
866.7 | 50.5 | -1.0096
866.8 | 50.5 | -1.0096
866.9 | 50.5 | -1.0096
867 | 50.5 | -1.0094
867.1 | 50.5 | -1.0094
867.2 | 50.5 | -1.0094
867.3 | 50.5 | -1.0094
867.4 | 50.5 | -1.0094
867.5 | 50.5 | -1.0094
867.6 | 50.5 | -1.0094
867.7 | 50.5 | -1.0094
867.8 | 50.5 | -1.0094
867.9 | 50.5 | -1.0094
868 | 50.5 | -1.0094
868.1 | 50.5 | -1.0094
868.2 | 50.5 | -1.0094
868.3 | 50.5 | -1.0094
868.4 | 50.5 | -1.0094
868.5 | 50.5 | -1.0094
868.6 | 50.5 | -1.0094
868.7 | 50.5 | -1.0094
868.8 | 50.5 | -1.0094
868.9 | 50.5 | -1.0094
869 | 50.5 | -1.0094
869.1 | 50.5 | -1.0094
869.2 | 50.5 | -1.0096
869.3 | 50.5 | -1.0096
869.4 | 50.5 | -1.0096
869.5 | 50.5 | -1.0096
869.6 | 50.5 | -1.0096
869.7 | 50.5 | -1.0096
869.8 | 50.5 | -1.0096
869.9 | 50.5 | -1.0096
870 | 50.5 | -1.0096
870.1 | 50.5 | -1.0096
870.2 | 50.5 | -1.0096
870.3 | 50.5 | -1.0096
870.4 | 50.5 | -1.0096
870.5 | 50.5 | -1.0096
870.6 | 50.5 | -1.0096
870.7 | 50.5 | -1.0096
870.8 | 50.5 | -1.0096
870.9 | 50.5 | -1.0096
871 | 50.5 | -1.0096
871.1 | 50.5 | -1.0096
871.2 | 50.5 | -1.0096
871.3 | 50.5 | -1.0096
871.4 | 50.5 | -1.0096
871.5 | 50.5 | -1.0096
871.6 | 50.5 | -1.0096
871.7 | 50.5 | -1.0096
871.8 | 50.5 | -1.0096
871.9 | 50.5 | -1.0096
872 | 50.5 | -1.0096
872.1 | 50.5 | -1.0096
872.2 | 50.5 | -1.0096
872.3 | 50.5 | -1.0096
872.4 | 50.5 | -1.0096
872.5 | 50.5 | -1.0096
872.6 | 50.5 | -1.0096
872.7 | 50.5 | -1.0096
872.8 | 50.5 | -1.0096
872.9 | 50.5 | -1.0096
873 | 50.5 | -1.0096
873.1 | 50.5 | -1.0096
873.2 | 50.5 | -1.0096
873.3 | 50.5 | -1.0096
873.4 | 50.5 | -1.0096
873.5 | 50.5 | -1.0096
873.6 | 50.5 | -1.0096
873.7 | 50.5 | -1.0096
873.8 | 50.5 | -1.0096
873.9 | 50.5 | -1.0094
874 | 50.5 | -1.0094
874.1 | 50.5 | -1.0094
874.2 | 50.5 | -1.0094
874.3 | 50.5 | -1.0094
874.4 | 50.5 | -1.0094
874.5 | 50.5 | -1.0094
874.6 | 50.5 | -1.0094
874.7 | 50.5 | -1.0094
874.8 | 50.5 | -1.0094
874.9 | 50.5 | -1.0094
875 | 50.5 | -1.0094
875.1 | 50.5 | -1.0094
875.2 | 50.5 | -1.0094
875.3 | 50.5 | -1.0094
875.4 | 50.5 | -1.0094
875.5 | 50.5 | -1.0094
875.6 | 50.5 | -1.0094
875.7 | 50.5 | -1.0094
875.8 | 50.5 | -1.0094
875.9 | 50.5 | -1.0094
876 | 50.5 | -1.0094
876.1 | 50.5 | -1.0094
876.2 | 50.5 | -1.0094
876.3 | 50.5 | -1.0094
876.4 | 50.5 | -1.0096
876.5 | 50.5 | -1.0096
876.6 | 50.5 | -1.0096
876.7 | 50.5 | -1.0096
876.8 | 50.5 | -1.0096
876.9 | 50.5 | -1.0096
877 | 50.5 | -1.0096
877.1 | 50.5 | -1.0096
877.2 | 50.5 | -1.0096
877.3 | 50.5 | -1.0096
877.4 | 50.5 | -1.0096
877.5 | 50.5 | -1.0096
877.6 | 50.5 | -1.0096
877.7 | 50.5 | -1.0096
877.8 | 50.5 | -1.0096
877.9 | 50.5 | -1.0096
878 | 50.5 | -1.0096
878.1 | 50.5 | -1.0096
878.2 | 50.5 | -1.0096
878.3 | 50.5 | -1.0096
878.4 | 50.5 | -1.0096
878.5 | 50.5 | -1.0096
878.6 | 50.5 | -1.0096
878.7 | 50.5 | -1.0096
878.8 | 50.5 | -1.0096
878.9 | 50.5 | -1.0096
879 | 50.5 | -1.0096
879.1 | 50.5 | -1.0096
879.2 | 50.5 | -1.0096
879.3 | 50.5 | -1.0096
879.4 | 50.5 | -1.0096
879.5 | 50.5 | -1.0096
879.6 | 50.5 | -1.0096
879.7 | 50.5 | -1.0096
879.8 | 50.5 | -1.0096
879.9 | 50.5 | -1.0096
880 | 50.5 | -1.0096
880.1 | 50.5 | -1.0096
880.2 | 50.5 | -1.0096
880.3 | 50.5 | -1.0096
880.4 | 50.5 | -1.0096
880.5 | 50.5 | -1.0096
880.6 | 50.5 | -1.0096
880.7 | 50.5 | -1.0096
880.8 | 50.5 | -1.0096
880.9 | 50.5 | -1.0096
881 | 50.5 | -1.0094
881.1 | 50.5 | -1.0094
881.2 | 50.5 | -1.0094
881.3 | 50.5 | -1.0094
881.4 | 50.5 | -1.0094
881.5 | 50.5 | -1.0094
881.6 | 50.5 | -1.0094
881.7 | 50.5 | -1.0094
881.8 | 50.5 | -1.0094
881.9 | 50.5 | -1.0094
882 | 50.5 | -1.0094
882.1 | 50.5 | -1.0094
882.2 | 50.5 | -1.0096
882.3 | 50.5 | -1.0096
882.4 | 50.5 | -1.0096
882.5 | 50.5 | -1.0096
882.6 | 50.5 | -1.0096
882.7 | 50.5 | -1.0096
882.8 | 50.5 | -1.0096
882.9 | 50.5 | -1.0096
883 | 50.5 | -1.0096
883.1 | 50.5 | -1.0096
883.2 | 50.5 | -1.0096
883.3 | 50.5 | -1.0096
883.4 | 50.5 | -1.0096
883.5 | 50.5 | -1.0096
883.6 | 50.5 | -1.0096
883.7 | 50.5 | -1.0096
883.8 | 50.5 | -1.0096
883.9 | 50.5 | -1.0096
884 | 50.5 | -1.0096
884.1 | 50.5 | -1.0096
884.2 | 50.5 | -1.0096
884.3 | 50.5 | -1.0096
884.4 | 50.5 | -1.0096
884.5 | 50.5 | -1.0094
884.6 | 50.5 | -1.0094
884.7 | 50.5 | -1.0094
884.8 | 50.5 | -1.0094
884.9 | 50.5 | -1.0094
885 | 50.5 | -1.0094
885.1 | 50.5 | -1.0094
885.2 | 50.5 | -1.0094
885.3 | 50.5 | -1.0094
885.4 | 50.5 | -1.0094
885.5 | 50.5 | -1.0094
885.6 | 50.5 | -1.0094
885.7 | 50.5 | -1.0094
885.8 | 50.5 | -1.0094
885.9 | 50.5 | -1.0094
886 | 50.5 | -1.0094
886.1 | 50.5 | -1.0094
886.2 | 50.5 | -1.0094
886.3 | 50.5 | -1.0094
886.4 | 50.5 | -1.0094
886.5 | 50.5 | -1.0094
886.6 | 50.5 | -1.0094
886.7 | 50.5 | -1.0094
886.8 | 50.5 | -1.0094
886.9 | 50.5 | -1.0094
887 | 50.5 | -1.0094
887.1 | 50.5 | -1.0094
887.2 | 50.5 | -1.0094
887.3 | 50.5 | -1.0094
887.4 | 50.5 | -1.0094
887.5 | 50.5 | -1.0094
887.6 | 50.5 | -1.0094
887.7 | 50.5 | -1.0094
887.8 | 50.5 | -1.0094
887.9 | 50.5 | -1.0094
888 | 50.5 | -1.0094
888.1 | 50.5 | -1.0094
888.2 | 50.5 | -1.0094
888.3 | 50.5 | -1.0094
888.4 | 50.5 | -1.0094
888.5 | 50.5 | -1.0094
888.6 | 50.5 | -1.0094
888.7 | 50.5 | -1.0094
888.8 | 50.5 | -1.0094
888.9 | 50.5 | -1.0094
889 | 50.5 | -1.0094
889.1 | 50.5 | -1.0096
889.2 | 50.5 | -1.0096
889.3 | 50.5 | -1.0096
889.4 | 50.5 | -1.0096
889.5 | 50.5 | -1.0096
889.6 | 50.5 | -1.0096
889.7 | 50.5 | -1.0096
889.8 | 50.5 | -1.0096
889.9 | 50.5 | -1.0096
890 | 50.5 | -1.0096
890.1 | 50.5 | -1.0096
890.2 | 50.5 | -1.0098
890.3 | 50.5 | -1.0096
890.4 | 50.5 | -1.0096
890.5 | 50.5 | -1.0096
890.6 | 50.5 | -1.0096
890.7 | 50.5 | -1.0096
890.8 | 50.5 | -1.0096
890.9 | 50.5 | -1.0096
891 | 50.5 | -1.0096
891.1 | 50.5 | -1.0096
891.2 | 50.5 | -1.0096
891.3 | 50.5 | -1.0096
891.4 | 50.5 | -1.0096
891.5 | 50.5 | -1.0094
891.6 | 50.5 | -1.0094
891.7 | 50.5 | -1.0094
891.8 | 50.5 | -1.0094
891.9 | 50.5 | -1.0094
892 | 50.5 | -1.0094
892.1 | 50.5 | -1.0094
892.2 | 50.5 | -1.0094
892.3 | 50.5 | -1.0094
892.4 | 50.5 | -1.0094
892.5 | 50.5 | -1.0094
892.6 | 50.5 | -1.0094
892.7 | 50.5 | -1.0094
892.8 | 50.5 | -1.0096
892.9 | 50.5 | -1.0096
893 | 50.5 | -1.0096
893.1 | 50.5 | -1.0096
893.2 | 50.5 | -1.0096
893.3 | 50.5 | -1.0096
893.4 | 50.5 | -1.0096
893.5 | 50.5 | -1.0096
893.6 | 50.5 | -1.0096
893.7 | 50.5 | -1.0096
893.8 | 50.5 | -1.0096
893.9 | 50.5 | -1.0096
894 | 50.5 | -1.0096
894.1 | 50.5 | -1.0096
894.2 | 50.5 | -1.0096
894.3 | 50.5 | -1.0096
894.4 | 50.5 | -1.0096
894.5 | 50.5 | -1.0096
894.6 | 50.5 | -1.0096
894.7 | 50.5 | -1.0096
894.8 | 50.5 | -1.0096
894.9 | 50.5 | -1.0096
895 | 50.5 | -1.0096
895.1 | 50.5 | -1.0096
895.2 | 50.5 | -1.0096
895.3 | 50.5 | -1.0096
895.4 | 50.5 | -1.0096
895.5 | 50.5 | -1.0096
895.6 | 50.5 | -1.0096
895.7 | 50.5 | -1.0096
895.8 | 50.5 | -1.0096
895.9 | 50.5 | -1.0096
896 | 50.5 | -1.0096
896.1 | 50.5 | -1.0096
896.2 | 50.5 | -1.0094
896.3 | 50.5 | -1.0094
896.4 | 50.5 | -1.0094
896.5 | 50.5 | -1.0094
896.6 | 50.5 | -1.0094
896.7 | 50.5 | -1.0094
896.8 | 50.5 | -1.0094
896.9 | 50.5 | -1.0094
897 | 50.5 | -1.0094
897.1 | 50.5 | -1.0094
897.2 | 50.5 | -1.0094
897.3 | 50.5 | -1.0094
897.4 | 50.5 | -1.0094
897.5 | 50.5 | -1.0094
897.6 | 50.5 | -1.0094
897.7 | 50.5 | -1.0094
897.8 | 50.5 | -1.0094
897.9 | 50.5 | -1.0094
898 | 50.5 | -1.0094
898.1 | 50.5 | -1.0094
898.2 | 50.5 | -1.0094
898.3 | 50.5 | -1.0094
898.4 | 50.5 | -1.0094
898.5 | 50.5 | -1.0096
898.6 | 50.5 | -1.0096
898.7 | 50.5 | -1.0096
898.8 | 50.5 | -1.0096
898.9 | 50.5 | -1.0096
899 | 50.5 | -1.0096
899.1 | 50.5 | -1.0096
899.2 | 50.5 | -1.0096
899.3 | 50.5 | -1.0096
899.4 | 50.5 | -1.0096
899.5 | 50.5 | -1.0096
899.6 | 50.5 | -1.0096
899.7 | 50.5 | -1.0096
899.8 | 50.5 | -1.0096
899.9 | 50.5 | -1.0096
900 | 50.5 | -1.0096
900.1 | 50.5 | -1.0096
900.2 | 50.5 | -1.0096
900.3 | 50.5 | -1.0096
900.4 | 50.5 | -1.0096
900.5 | 50.5 | -1.0096
900.6 | 50.5 | -1.0096
900.7 | 50.5 | -1.0096
900.8 | 50.5 | -1.0096
900.9 | 50.5 | -1.0096
901 | 50.5 | -1.0096
901.1 | 50.5 | -1.0096
901.2 | 50.5 | -1.0096
901.3 | 50.5 | -1.0096
901.4 | 50.5 | -1.0096
901.5 | 50.5 | -1.0096
901.6 | 50.5 | -1.0096
901.7 | 50.5 | -1.0096
901.8 | 50.5 | -1.0096
901.9 | 50.5 | -1.0094
902 | 50.5 | -1.0094
902.1 | 50.5 | -1.0094
902.2 | 50.5 | -1.0094
902.3 | 50.5 | -1.0094
902.4 | 50.5 | -1.0094
902.5 | 50.5 | -1.0094
902.6 | 50.5 | -1.0094
902.7 | 50.5 | -1.0094
902.8 | 50.5 | -1.0094
902.9 | 50.5 | -1.0094
903 | 50.5 | -1.0094
903.1 | 50.5 | -1.0094
903.2 | 50.5 | -1.0094
903.3 | 50.5 | -1.0094
903.4 | 50.5 | -1.0094
903.5 | 50.5 | -1.0094
903.6 | 50.5 | -1.0094
903.7 | 50.5 | -1.0094
903.8 | 50.5 | -1.0094
903.9 | 50.5 | -1.0094
904 | 50.5 | -1.0094
904.1 | 50.5 | -1.0094
904.2 | 50.5 | -1.0096
904.3 | 50.5 | -1.0096
904.4 | 50.5 | -1.0096
904.5 | 50.5 | -1.0096
904.6 | 50.5 | -1.0096
904.7 | 50.5 | -1.0096
904.8 | 50.5 | -1.0096
904.9 | 50.5 | -1.0096
905 | 50.5 | -1.0096
905.1 | 50.5 | -1.0096
905.2 | 50.5 | -1.0096
905.3 | 50.5 | -1.0096
905.4 | 50.5 | -1.0096
905.5 | 50.5 | -1.0096
905.6 | 50.5 | -1.0096
905.7 | 50.5 | -1.0096
905.8 | 50.5 | -1.0096
905.9 | 50.5 | -1.0096
906 | 50.5 | -1.0096
906.1 | 50.5 | -1.0096
906.2 | 50.5 | -1.0096
906.3 | 50.5 | -1.0096
906.4 | 50.5 | -1.0096
906.5 | 50.5 | -1.0096
906.6 | 50.5 | -1.0096
906.7 | 50.5 | -1.0096
906.8 | 50.5 | -1.0096
906.9 | 50.5 | -1.0096
907 | 50.5 | -1.0096
907.1 | 50.5 | -1.0096
907.2 | 50.5 | -1.0096
907.3 | 50.5 | -1.0096
907.4 | 50.5 | -1.0096
907.5 | 50.5 | -1.0096
907.6 | 50.5 | -1.0096
907.7 | 50.5 | -1.0096
907.8 | 50.5 | -1.0096
907.9 | 50.5 | -1.0096
908 | 50.5 | -1.0096
908.1 | 50.5 | -1.0096
908.2 | 50.5 | -1.0096
908.3 | 50.5 | -1.0096
908.4 | 50.5 | -1.0096
908.5 | 50.5 | -1.0096
908.6 | 50.5 | -1.0096
908.7 | 50.5 | -1.0096
908.8 | 50.5 | -1.0096
908.9 | 50.5 | -1.0096
909 | 50.5 | -1.0096
909.1 | 50.5 | -1.0096
909.2 | 50.5 | -1.0096
909.3 | 50.5 | -1.0096
909.4 | 50.5 | -1.0096
909.5 | 50.5 | -1.0096
909.6 | 50.5 | -1.0096
909.7 | 50.5 | -1.0096
909.8 | 50.5 | -1.0096
909.9 | 50.5 | -1.0096
910 | 50.5 | -1.0096
910.1 | 50.5 | -1.0094
910.2 | 50.5 | -1.0094
910.3 | 50.5 | -1.0094
910.4 | 50.5 | -1.0094
910.5 | 50.5 | -1.0094
910.6 | 50.5 | -1.0094
910.7 | 50.5 | -1.0094
910.8 | 50.5 | -1.0094
910.9 | 50.5 | -1.0094
911 | 50.5 | -1.0094
911.1 | 50.5 | -1.0094
911.2 | 50.5 | -1.0094
911.3 | 50.5 | -1.0094
911.4 | 50.5 | -1.0094
911.5 | 50.5 | -1.0094
911.6 | 50.5 | -1.0094
911.7 | 50.5 | -1.0094
911.8 | 50.5 | -1.0094
911.9 | 50.5 | -1.0094
912 | 50.5 | -1.0094
912.1 | 50.5 | -1.0094
912.2 | 50.5 | -1.0094
912.3 | 50.5 | -1.0096
912.4 | 50.5 | -1.0096
912.5 | 50.5 | -1.0096
912.6 | 50.5 | -1.0096
912.7 | 50.5 | -1.0096
912.8 | 50.5 | -1.0096
912.9 | 50.5 | -1.0096
913 | 50.5 | -1.0096
913.1 | 50.5 | -1.0096
913.2 | 50.5 | -1.0096
913.3 | 50.5 | -1.0096
913.4 | 50.5 | -1.0096
913.5 | 50.5 | -1.0096
913.6 | 50.5 | -1.0096
913.7 | 50.5 | -1.0096
913.8 | 50.5 | -1.0096
913.9 | 50.5 | -1.0096
914 | 50.5 | -1.0096
914.1 | 50.5 | -1.0096
914.2 | 50.5 | -1.0096
914.3 | 50.5 | -1.0096
914.4 | 50.5 | -1.0096
914.5 | 50.5 | -1.0096
914.6 | 50.5 | -1.0096
914.7 | 50.5 | -1.0096
914.8 | 50.5 | -1.0096
914.9 | 50.5 | -1.0096
915 | 50.5 | -1.0096
915.1 | 50.5 | -1.0096
915.2 | 50.5 | -1.0096
915.3 | 50.5 | -1.0096
915.4 | 50.5 | -1.0096
915.5 | 50.5 | -1.0096
915.6 | 50.5 | -1.0096
915.7 | 50.5 | -1.0096
915.8 | 50.5 | -1.0094
915.9 | 50.5 | -1.0094
916 | 50.5 | -1.0094
916.1 | 50.5 | -1.0094
916.2 | 50.5 | -1.0094
916.3 | 50.5 | -1.0094
916.4 | 50.5 | -1.0094
916.5 | 50.5 | -1.0094
916.6 | 50.5 | -1.0094
916.7 | 50.5 | -1.0094
916.8 | 50.5 | -1.0094
916.9 | 50.5 | -1.0094
917 | 50.5 | -1.0094
917.1 | 50.5 | -1.0094
917.2 | 50.5 | -1.0094
917.3 | 50.5 | -1.0094
917.4 | 50.5 | -1.0094
917.5 | 50.5 | -1.0094
917.6 | 50.5 | -1.0094
917.7 | 50.5 | -1.0094
917.8 | 50.5 | -1.0094
917.9 | 50.5 | -1.0094
918 | 50.5 | -1.0094
918.1 | 50.5 | -1.0094
918.2 | 50.5 | -1.0094
918.3 | 50.5 | -1.0094
918.4 | 50.5 | -1.0094
918.5 | 50.5 | -1.0094
918.6 | 50.5 | -1.0094
918.7 | 50.5 | -1.0094
918.8 | 50.5 | -1.0094
918.9 | 50.5 | -1.0094
919 | 50.5 | -1.0094
919.1 | 50.5 | -1.0094
919.2 | 50.5 | -1.0096
919.3 | 50.5 | -1.0096
919.4 | 50.5 | -1.0096
919.5 | 50.5 | -1.0096
919.6 | 50.5 | -1.0096
919.7 | 50.5 | -1.0096
919.8 | 50.5 | -1.0096
919.9 | 50.5 | -1.0096
920 | 50.5 | -1.0096
920.1 | 50.5 | -1.0096
920.2 | 50.5 | -1.0096
920.3 | 50.5 | -1.0096
920.4 | 50.5 | -1.0096
920.5 | 50.5 | -1.0096
920.6 | 50.5 | -1.0096
920.7 | 50.5 | -1.0096
920.8 | 50.5 | -1.0096
920.9 | 50.5 | -1.0096
921 | 50.5 | -1.0096
921.1 | 50.5 | -1.0096
921.2 | 50.5 | -1.0096
921.3 | 50.5 | -1.0096
921.4 | 50.5 | -1.0096
921.5 | 50.5 | -1.0096
921.6 | 50.5 | -1.0096
921.7 | 50.5 | -1.0096
921.8 | 50.5 | -1.0096
921.9 | 50.5 | -1.0096
922 | 50.5 | -1.0096
922.1 | 50.5 | -1.0096
922.2 | 50.5 | -1.0096
922.3 | 50.5 | -1.0096
922.4 | 50.5 | -1.0096
922.5 | 50.5 | -1.0096
922.6 | 50.5 | -1.0096
922.7 | 50.5 | -1.0096
922.8 | 50.5 | -1.0096
922.9 | 50.5 | -1.0096
923 | 50.5 | -1.0096
923.1 | 50.5 | -1.0096
923.2 | 50.5 | -1.0096
923.3 | 50.5 | -1.0096
923.4 | 50.5 | -1.0096
923.5 | 50.5 | -1.0096
923.6 | 50.5 | -1.0096
923.7 | 50.5 | -1.0096
923.8 | 50.5 | -1.0096
923.9 | 50.5 | -1.0096
924 | 50.5 | -1.0096
924.1 | 50.5 | -1.0096
924.2 | 50.5 | -1.0096
924.3 | 50.5 | -1.0096
924.4 | 50.5 | -1.0096
924.5 | 50.5 | -1.0096
924.6 | 50.5 | -1.0096
924.7 | 50.5 | -1.0096
924.8 | 50.5 | -1.0096
924.9 | 50.5 | -1.0096
925 | 50.5 | -1.0096
925.1 | 50.5 | -1.0096
925.2 | 50.5 | -1.0096
925.3 | 50.5 | -1.0096
925.4 | 50.5 | -1.0096
925.5 | 50.5 | -1.0096
925.6 | 50.5 | -1.0096
925.7 | 50.5 | -1.0096
925.8 | 50.5 | -1.0096
925.9 | 50.5 | -1.0096
926 | 50.5 | -1.0096
926.1 | 50.5 | -1.0096
926.2 | 50.5 | -1.0094
926.3 | 50.5 | -1.0094
926.4 | 50.5 | -1.0094
926.5 | 50.5 | -1.0094
926.6 | 50.5 | -1.0094
926.7 | 50.5 | -1.0094
926.8 | 50.5 | -1.0094
926.9 | 50.5 | -1.0094
927 | 50.5 | -1.0094
927.1 | 50.5 | -1.0094
927.2 | 50.5 | -1.0094
927.3 | 50.5 | -1.0094
927.4 | 50.5 | -1.0094
927.5 | 50.5 | -1.0096
927.6 | 50.5 | -1.0096
927.7 | 50.5 | -1.0096
927.8 | 50.5 | -1.0096
927.9 | 50.5 | -1.0096
928 | 50.5 | -1.0096
928.1 | 50.5 | -1.0096
928.2 | 50.5 | -1.0096
928.3 | 50.5 | -1.0096
928.4 | 50.5 | -1.0096
928.5 | 50.5 | -1.0096
928.6 | 50.5 | -1.0096
928.7 | 50.5 | -1.0096
928.8 | 50.5 | -1.0096
928.9 | 50.5 | -1.0096
929 | 50.5 | -1.0096
929.1 | 50.5 | -1.0096
929.2 | 50.5 | -1.0096
929.3 | 50.5 | -1.0096
929.4 | 50.5 | -1.0096
929.5 | 50.5 | -1.0096
929.6 | 50.5 | -1.0096
929.7 | 50.5 | -1.0096
929.8 | 50.5 | -1.0096
929.9 | 50.5 | -1.0096
930 | 50.5 | -1.0096
930.1 | 50.5 | -1.0096
930.2 | 50.5 | -1.0096
930.3 | 50.5 | -1.0096
930.4 | 50.5 | -1.0096
930.5 | 50.5 | -1.0096
930.6 | 50.5 | -1.0096
930.7 | 50.5 | -1.0096
930.8 | 50.5 | -1.0096
930.9 | 50.5 | -1.0096
931 | 50.5 | -1.0094
931.1 | 50.5 | -1.0096
931.2 | 50.5 | -1.0096
931.3 | 50.5 | -1.0096
931.4 | 50.5 | -1.0096
931.5 | 50.5 | -1.0096
931.6 | 50.5 | -1.0096
931.7 | 50.5 | -1.0096
931.8 | 50.5 | -1.0096
931.9 | 50.5 | -1.0096
932 | 50.5 | -1.0096
932.1 | 50.5 | -1.0096
932.2 | 50.5 | -1.0096
932.3 | 50.5 | -1.0096
932.4 | 50.5 | -1.0096
932.5 | 50.5 | -1.0096
932.6 | 50.5 | -1.0096
932.7 | 50.5 | -1.0096
932.8 | 50.5 | -1.0096
932.9 | 50.5 | -1.0096
933 | 50.5 | -1.0096
933.1 | 50.5 | -1.0096
933.2 | 50.5 | -1.0096
933.3 | 50.5 | -1.0096
933.4 | 50.5 | -1.0098
933.5 | 50.5 | -1.0098
933.6 | 50.5 | -1.0098
933.7 | 50.5 | -1.0098
933.8 | 50.5 | -1.0098
933.9 | 50.5 | -1.0098
934 | 50.5 | -1.0098
934.1 | 50.5 | -1.0098
934.2 | 50.5 | -1.0098
934.3 | 50.5 | -1.0098
934.4 | 50.5 | -1.0098
934.5 | 50.5 | -1.0098
934.6 | 50.5 | -1.0096
934.7 | 50.5 | -1.0096
934.8 | 50.5 | -1.0096
934.9 | 50.5 | -1.0096
935 | 50.5 | -1.0096
935.1 | 50.5 | -1.0096
935.2 | 50.5 | -1.0096
935.3 | 50.5 | -1.0096
935.4 | 50.5 | -1.0096
935.5 | 50.5 | -1.0096
935.6 | 50.5 | -1.0096
935.7 | 50.5 | -1.0096
935.8 | 50.5 | -1.0096
935.9 | 50.5 | -1.0096
936 | 50.5 | -1.0096
936.1 | 50.5 | -1.0096
936.2 | 50.5 | -1.0096
936.3 | 50.5 | -1.0096
936.4 | 50.5 | -1.0096
936.5 | 50.5 | -1.0096
936.6 | 50.5 | -1.0096
936.7 | 50.5 | -1.0096
936.8 | 50.5 | -1.0096
936.9 | 50.5 | -1.0094
937 | 50.5 | -1.0094
937.1 | 50.5 | -1.0094
937.2 | 50.5 | -1.0094
937.3 | 50.5 | -1.0094
937.4 | 50.5 | -1.0094
937.5 | 50.5 | -1.0094
937.6 | 50.5 | -1.0094
937.7 | 50.5 | -1.0094
937.8 | 50.5 | -1.0094
937.9 | 50.5 | -1.0094
938 | 50.5 | -1.0094
938.1 | 50.5 | -1.0094
938.2 | 50.5 | -1.0094
938.3 | 50.5 | -1.0094
938.4 | 50.5 | -1.0094
938.5 | 50.5 | -1.0094
938.6 | 50.5 | -1.0094
938.7 | 50.5 | -1.0094
938.8 | 50.5 | -1.0094
938.9 | 50.5 | -1.0094
939 | 50.5 | -1.0094
939.1 | 50.5 | -1.0096
939.2 | 50.5 | -1.0096
939.3 | 50.5 | -1.0096
939.4 | 50.5 | -1.0096
939.5 | 50.5 | -1.0096
939.6 | 50.5 | -1.0096
939.7 | 50.5 | -1.0096
939.8 | 50.5 | -1.0096
939.9 | 50.5 | -1.0096
940 | 50.5 | -1.0096
940.1 | 50.5 | -1.0096
940.2 | 50.5 | -1.0096
940.3 | 50.5 | -1.0096
940.4 | 50.5 | -1.0096
940.5 | 50.5 | -1.0096
940.6 | 50.5 | -1.0096
940.7 | 50.5 | -1.0096
940.8 | 50.5 | -1.0096
940.9 | 50.5 | -1.0096
941 | 50.5 | -1.0096
941.1 | 50.5 | -1.0096
941.2 | 50.5 | -1.0096
941.3 | 50.5 | -1.0096
941.4 | 50.5 | -1.0096
941.5 | 50.5 | -1.0096
941.6 | 50.5 | -1.0096
941.7 | 50.5 | -1.0096
941.8 | 50.5 | -1.0096
941.9 | 50.5 | -1.0096
942 | 50.5 | -1.0096
942.1 | 50.5 | -1.0096
942.2 | 50.5 | -1.0096
942.3 | 50.5 | -1.0096
942.4 | 50.5 | -1.0096
942.5 | 50.5 | -1.0096
942.6 | 50.5 | -1.0096
942.7 | 50.5 | -1.0096
942.8 | 50.5 | -1.0096
942.9 | 50.5 | -1.0096
943 | 50.5 | -1.0096
943.1 | 50.5 | -1.0096
943.2 | 50.5 | -1.0096
943.3 | 50.5 | -1.0096
943.4 | 50.5 | -1.0096
943.5 | 50.5 | -1.0096
943.6 | 50.5 | -1.0096
943.7 | 50.5 | -1.0096
943.8 | 50.5 | -1.0094
943.9 | 50.5 | -1.0094
944 | 50.5 | -1.0094
944.1 | 50.5 | -1.0094
944.2 | 50.5 | -1.0094
944.3 | 50.5 | -1.0094
944.4 | 50.5 | -1.0094
944.5 | 50.5 | -1.0094
944.6 | 50.5 | -1.0094
944.7 | 50.5 | -1.0094
944.8 | 50.5 | -1.0094
944.9 | 50.5 | -1.0094
945 | 50.5 | -1.0094
945.1 | 50.5 | -1.0094
945.2 | 50.5 | -1.0094
945.3 | 50.5 | -1.0094
945.4 | 50.5 | -1.0094
945.5 | 50.5 | -1.0094
945.6 | 50.5 | -1.0094
945.7 | 50.5 | -1.0094
945.8 | 50.5 | -1.0094
945.9 | 50.5 | -1.0094
946 | 50.5 | -1.0096
946.1 | 50.5 | -1.0096
946.2 | 50.5 | -1.0096
946.3 | 50.5 | -1.0096
946.4 | 50.5 | -1.0096
946.5 | 50.5 | -1.0096
946.6 | 50.5 | -1.0096
946.7 | 50.5 | -1.0096
946.8 | 50.5 | -1.0096
946.9 | 50.5 | -1.0096
947 | 50.5 | -1.0096
947.1 | 50.5 | -1.0096
947.2 | 50.5 | -1.0096
947.3 | 50.5 | -1.0096
947.4 | 50.5 | -1.0096
947.5 | 50.5 | -1.0096
947.6 | 50.5 | -1.0096
947.7 | 50.5 | -1.0096
947.8 | 50.5 | -1.0096
947.9 | 50.5 | -1.0096
948 | 50.5 | -1.0096
948.1 | 50.5 | -1.0096
948.2 | 50.5 | -1.0096
948.3 | 50.5 | -1.0096
948.4 | 50.5 | -1.0096
948.5 | 50.5 | -1.0096
948.6 | 50.5 | -1.0096
948.7 | 50.5 | -1.0096
948.8 | 50.5 | -1.0096
948.9 | 50.5 | -1.0096
949 | 50.5 | -1.0096
949.1 | 50.5 | -1.0096
949.2 | 50.5 | -1.0096
949.3 | 50.5 | -1.0096
949.4 | 50.5 | -1.0096
949.5 | 50.5 | -1.0096
949.6 | 50.5 | -1.0096
949.7 | 50.5 | -1.0096
949.8 | 50.5 | -1.0096
949.9 | 50.5 | -1.0096
950 | 50.5 | -1.0096
950.1 | 50.5 | -1.0096
950.2 | 50.5 | -1.0096
950.3 | 50.5 | -1.0096
950.4 | 50.5 | -1.0096
950.5 | 50.5 | -1.0096
950.6 | 50.5 | -1.0096
950.7 | 50.5 | -1.0096
950.8 | 50.5 | -1.0096
950.9 | 50.5 | -1.0096
951 | 50.5 | -1.0096
951.1 | 50.5 | -1.0096
951.2 | 50.5 | -1.0096
951.3 | 50.5 | -1.0096
951.4 | 50.5 | -1.0096
951.5 | 50.5 | -1.0096
951.6 | 50.5 | -1.0096
951.7 | 50.5 | -1.0096
951.8 | 50.5 | -1.0096
951.9 | 50.5 | -1.0096
952 | 50.5 | -1.0096
952.1 | 50.5 | -1.0096
952.2 | 50.5 | -1.0096
952.3 | 50.5 | -1.0096
952.4 | 50.5 | -1.0096
952.5 | 50.5 | -1.0096
952.6 | 50.5 | -1.0096
952.7 | 50.5 | -1.0096
952.8 | 50.5 | -1.0096
952.9 | 50.5 | -1.0096
953 | 50.5 | -1.0096
953.1 | 50.5 | -1.0096
953.2 | 50.5 | -1.0096
953.3 | 50.5 | -1.0096
953.4 | 50.5 | -1.0096
953.5 | 50.5 | -1.0096
953.6 | 50.5 | -1.0096
953.7 | 50.5 | -1.0096
953.8 | 50.5 | -1.0096
953.9 | 50.5 | -1.0096
954 | 50.5 | -1.0096
954.1 | 50.5 | -1.0096
954.2 | 50.5 | -1.0096
954.3 | 50.5 | -1.0096
954.4 | 50.5 | -1.0096
954.5 | 50.5 | -1.0096
954.6 | 50.5 | -1.0096
954.7 | 50.5 | -1.0096
954.8 | 50.5 | -1.0096
954.9 | 50.5 | -1.0096
955 | 50.5 | -1.0096
955.1 | 50.5 | -1.0096
955.2 | 50.5 | -1.0096
955.3 | 50.5 | -1.0096
955.4 | 50.5 | -1.0096
955.5 | 50.5 | -1.0096
955.6 | 50.5 | -1.0096
955.7 | 50.5 | -1.0096
955.8 | 50.5 | -1.0096
955.9 | 50.5 | -1.0096
956 | 50.5 | -1.0096
956.1 | 50.5 | -1.0096
956.2 | 50.5 | -1.0096
956.3 | 50.5 | -1.0096
956.4 | 50.5 | -1.0096
956.5 | 50.5 | -1.0096
956.6 | 50.5 | -1.0096
956.7 | 50.5 | -1.0096
956.8 | 50.5 | -1.0096
956.9 | 50.5 | -1.0096
957 | 50.5 | -1.0096
957.1 | 50.5 | -1.0096
957.2 | 50.5 | -1.0096
957.3 | 50.5 | -1.0096
957.4 | 50.5 | -1.0096
957.5 | 50.5 | -1.0096
957.6 | 50.5 | -1.0096
957.7 | 50.5 | -1.0096
957.8 | 50.5 | -1.0096
957.9 | 50.5 | -1.0096
958 | 50.5 | -1.0096
958.1 | 50.5 | -1.0096
958.2 | 50.5 | -1.0096
958.3 | 50.5 | -1.0096
958.4 | 50.5 | -1.0096
958.5 | 50.5 | -1.0096
958.6 | 50.5 | -1.0096
958.7 | 50.5 | -1.0096
958.8 | 50.5 | -1.0096
958.9 | 50.5 | -1.0096
959 | 50.5 | -1.0096
959.1 | 50.5 | -1.0096
959.2 | 50.5 | -1.0096
959.3 | 50.5 | -1.0096
959.4 | 50.5 | -1.0096
959.5 | 50.5 | -1.0096
959.6 | 50.5 | -1.0096
959.7 | 50.5 | -1.0096
959.8 | 50.5 | -1.0096
959.9 | 50.5 | -1.0096
960 | 50.5 | -1.0096
960.1 | 50.5 | -1.0096
960.2 | 50.5 | -1.0096
960.3 | 50.5 | -1.0096
960.4 | 50.5 | -1.0096
960.5 | 50.5 | -1.0096
960.6 | 50.5 | -1.0096
960.7 | 50.5 | -1.0096
960.8 | 50.5 | -1.0096
960.9 | 50.5 | -1.0096
961 | 50.5 | -1.0096
961.1 | 50.5 | -1.0096
961.2 | 50.5 | -1.0096
961.3 | 50.5 | -1.0096
961.4 | 50.5 | -1.0096
961.5 | 50.5 | -1.0094
961.6 | 50.5 | -1.0094
961.7 | 50.5 | -1.0094
961.8 | 50.5 | -1.0094
961.9 | 50.5 | -1.0094
962 | 50.5 | -1.0094
962.1 | 50.5 | -1.0094
962.2 | 50.5 | -1.0094
962.3 | 50.5 | -1.0094
962.4 | 50.5 | -1.0094
962.5 | 50.5 | -1.0094
962.6 | 50.5 | -1.0094
962.7 | 50.5 | -1.0096
962.8 | 50.5 | -1.0096
962.9 | 50.5 | -1.0096
963 | 50.5 | -1.0096
963.1 | 50.5 | -1.0096
963.2 | 50.5 | -1.0096
963.3 | 50.5 | -1.0096
963.4 | 50.5 | -1.0096
963.5 | 50.5 | -1.0096
963.6 | 50.5 | -1.0096
963.7 | 50.5 | -1.0096
963.8 | 50.5 | -1.0096
963.9 | 50.5 | -1.0096
964 | 50.5 | -1.0096
964.1 | 50.5 | -1.0096
964.2 | 50.5 | -1.0096
964.3 | 50.5 | -1.0096
964.4 | 50.5 | -1.0096
964.5 | 50.5 | -1.0096
964.6 | 50.5 | -1.0096
964.7 | 50.5 | -1.0096
964.8 | 50.5 | -1.0096
964.9 | 50.5 | -1.0096
965 | 50.5 | -1.0096
965.1 | 50.5 | -1.0096
965.2 | 50.5 | -1.0096
965.3 | 50.5 | -1.0096
965.4 | 50.5 | -1.0096
965.5 | 50.5 | -1.0096
965.6 | 50.5 | -1.0096
965.7 | 50.5 | -1.0096
965.8 | 50.5 | -1.0096
965.9 | 50.5 | -1.0096
966 | 50.5 | -1.0096
966.1 | 50.5 | -1.0096
966.2 | 50.5 | -1.0096
966.3 | 50.5 | -1.0096
966.4 | 50.5 | -1.0096
966.5 | 50.5 | -1.0096
966.6 | 50.5 | -1.0096
966.7 | 50.5 | -1.0096
966.8 | 50.5 | -1.0096
966.9 | 50.5 | -1.0096
967 | 50.5 | -1.0096
967.1 | 50.5 | -1.0096
967.2 | 50.5 | -1.0096
967.3 | 50.5 | -1.0096
967.4 | 50.5 | -1.0096
967.5 | 50.5 | -1.0096
967.6 | 50.5 | -1.0096
967.7 | 50.5 | -1.0096
967.8 | 50.5 | -1.0096
967.9 | 50.5 | -1.0096
968 | 50.5 | -1.0096
968.1 | 50.5 | -1.0096
968.2 | 50.5 | -1.0096
968.3 | 50.5 | -1.0096
968.4 | 50.5 | -1.0096
968.5 | 50.5 | -1.0096
968.6 | 50.5 | -1.0096
968.7 | 50.5 | -1.0096
968.8 | 50.5 | -1.0096
968.9 | 50.5 | -1.0096
969 | 50.5 | -1.0096
969.1 | 50.5 | -1.0096
969.2 | 50.5 | -1.0096
969.3 | 50.5 | -1.0096
969.4 | 50.5 | -1.0096
969.5 | 50.5 | -1.0096
969.6 | 50.5 | -1.0096
969.7 | 50.5 | -1.0096
969.8 | 50.5 | -1.0096
969.9 | 50.5 | -1.0096
970 | 50.5 | -1.0096
970.1 | 50.5 | -1.0096
970.2 | 50.5 | -1.0096
970.3 | 50.5 | -1.0096
970.4 | 50.5 | -1.0096
970.5 | 50.5 | -1.0096
970.6 | 50.5 | -1.0096
970.7 | 50.5 | -1.0096
970.8 | 50.5 | -1.0096
970.9 | 50.5 | -1.0096
971 | 50.5 | -1.0096
971.1 | 50.5 | -1.0096
971.2 | 50.5 | -1.0096
971.3 | 50.5 | -1.0096
971.4 | 50.5 | -1.0096
971.5 | 50.5 | -1.0096
971.6 | 50.5 | -1.0096
971.7 | 50.5 | -1.0096
971.8 | 50.5 | -1.0094
971.9 | 50.5 | -1.0094
972 | 50.5 | -1.0094
972.1 | 50.5 | -1.0094
972.2 | 50.5 | -1.0094
972.3 | 50.5 | -1.0094
972.4 | 50.5 | -1.0094
972.5 | 50.5 | -1.0094
972.6 | 50.5 | -1.0094
972.7 | 50.5 | -1.0094
972.8 | 50.5 | -1.0096
972.9 | 50.5 | -1.0096
973 | 50.5 | -1.0096
973.1 | 50.5 | -1.0096
973.2 | 50.5 | -1.0096
973.3 | 50.5 | -1.0096
973.4 | 50.5 | -1.0096
973.5 | 50.5 | -1.0096
973.6 | 50.5 | -1.0096
973.7 | 50.5 | -1.0096
973.8 | 50.5 | -1.0096
973.9 | 50.5 | -1.0096
974 | 50.5 | -1.0096
974.1 | 50.5 | -1.0096
974.2 | 50.5 | -1.0096
974.3 | 50.5 | -1.0096
974.4 | 50.5 | -1.0096
974.5 | 50.5 | -1.0094
974.6 | 50.5 | -1.0094
974.7 | 50.5 | -1.0094
974.8 | 50.5 | -1.0094
974.9 | 50.5 | -1.0094
975 | 50.5 | -1.0094
975.1 | 50.5 | -1.0094
975.2 | 50.5 | -1.0096
975.3 | 50.5 | -1.0096
975.4 | 50.5 | -1.0096
975.5 | 50.5 | -1.0096
975.6 | 50.5 | -1.0096
975.7 | 50.5 | -1.0096
975.8 | 50.5 | -1.0096
975.9 | 50.5 | -1.0096
976 | 50.5 | -1.0096
976.1 | 50.5 | -1.0096
976.2 | 50.5 | -1.0096
976.3 | 50.5 | -1.0094
976.4 | 50.5 | -1.0094
976.5 | 50.5 | -1.0094
976.6 | 50.5 | -1.0094
976.7 | 50.5 | -1.0094
976.8 | 50.5 | -1.0094
976.9 | 50.5 | -1.0096
977 | 50.5 | -1.0096
977.1 | 50.5 | -1.0096
977.2 | 50.5 | -1.0096
977.3 | 50.5 | -1.0096
977.4 | 50.5 | -1.0096
977.5 | 50.5 | -1.0094
977.6 | 50.5 | -1.0094
977.7 | 50.5 | -1.0094
977.8 | 50.5 | -1.0094
977.9 | 50.5 | -1.0094
978 | 50.5 | -1.0094
978.1 | 50.5 | -1.0094
978.2 | 50.5 | -1.0094
978.3 | 50.5 | -1.0094
978.4 | 50.5 | -1.0094
978.5 | 50.5 | -1.0094
978.6 | 50.5 | -1.0094
978.7 | 50.5 | -1.0096
978.8 | 50.5 | -1.0096
978.9 | 50.5 | -1.0096
979 | 50.5 | -1.0096
979.1 | 50.5 | -1.0096
979.2 | 50.5 | -1.0096
979.3 | 50.5 | -1.0094
979.4 | 50.5 | -1.0094
979.5 | 50.5 | -1.0094
979.6 | 50.5 | -1.0094
979.7 | 50.5 | -1.0094
979.8 | 50.5 | -1.0096
979.9 | 50.5 | -1.0096
980 | 50.5 | -1.0096
980.1 | 50.5 | -1.0096
980.2 | 50.5 | -1.0096
980.3 | 50.5 | -1.0096
980.4 | 50.5 | -1.0096
980.5 | 50.5 | -1.0096
980.6 | 50.5 | -1.0096
980.7 | 50.5 | -1.0096
980.8 | 50.5 | -1.0096
980.9 | 50.5 | -1.0096
981 | 50.5 | -1.0094
981.1 | 50.5 | -1.0094
981.2 | 50.5 | -1.0094
981.3 | 50.5 | -1.0094
981.4 | 50.5 | -1.0094
981.5 | 50.5 | -1.0094
981.6 | 50.5 | -1.0094
981.7 | 50.5 | -1.0094
981.8 | 50.5 | -1.0094
981.9 | 50.5 | -1.0094
982 | 50.5 | -1.0094
982.1 | 50.5 | -1.0094
982.2 | 50.5 | -1.0096
982.3 | 50.5 | -1.0096
982.4 | 50.5 | -1.0096
982.5 | 50.5 | -1.0096
982.6 | 50.5 | -1.0096
982.7 | 50.5 | -1.0096
982.8 | 50.5 | -1.0096
982.9 | 50.5 | -1.0096
983 | 50.5 | -1.0096
983.1 | 50.5 | -1.0096
983.2 | 50.5 | -1.0096
983.3 | 50.5 | -1.0096
983.4 | 50.5 | -1.0096
983.5 | 50.5 | -1.0096
983.6 | 50.5 | -1.0096
983.7 | 50.5 | -1.0096
983.8 | 50.5 | -1.0096
983.9 | 50.5 | -1.0096
984 | 50.5 | -1.0096
984.1 | 50.5 | -1.0096
984.2 | 50.5 | -1.0096
984.3 | 50.5 | -1.0096
984.4 | 50.5 | -1.0096
984.5 | 50.5 | -1.0096
984.6 | 50.5 | -1.0096
984.7 | 50.5 | -1.0096
984.8 | 50.5 | -1.0096
984.9 | 50.5 | -1.0096
985 | 50.5 | -1.0096
985.1 | 50.5 | -1.0096
985.2 | 50.5 | -1.0096
985.3 | 50.5 | -1.0096
985.4 | 50.5 | -1.0096
985.5 | 50.5 | -1.0096
985.6 | 50.5 | -1.0096
985.7 | 50.5 | -1.0096
985.8 | 50.5 | -1.0096
985.9 | 50.5 | -1.0096
986 | 50.5 | -1.0096
986.1 | 50.5 | -1.0094
986.2 | 50.5 | -1.0094
986.3 | 50.5 | -1.0094
986.4 | 50.5 | -1.0094
986.5 | 50.5 | -1.0094
986.6 | 50.5 | -1.0094
986.7 | 50.5 | -1.0094
986.8 | 50.5 | -1.0096
986.9 | 50.5 | -1.0096
987 | 50.5 | -1.0096
987.1 | 50.5 | -1.0096
987.2 | 50.5 | -1.0096
987.3 | 50.5 | -1.0096
987.4 | 50.5 | -1.0096
987.5 | 50.5 | -1.0096
987.6 | 50.5 | -1.0096
987.7 | 50.5 | -1.0096
987.8 | 50.5 | -1.0096
987.9 | 50.5 | -1.0096
988 | 50.5 | -1.0096
988.1 | 50.5 | -1.0096
988.2 | 50.5 | -1.0096
988.3 | 50.5 | -1.0096
988.4 | 50.5 | -1.0096
988.5 | 50.5 | -1.0096
988.6 | 50.5 | -1.0096
988.7 | 50.5 | -1.0096
988.8 | 50.5 | -1.0096
988.9 | 50.5 | -1.0096
989 | 50.5 | -1.0096
989.1 | 50.5 | -1.0096
989.2 | 50.5 | -1.0096
989.3 | 50.5 | -1.0096
989.4 | 50.5 | -1.0096
989.5 | 50.5 | -1.0096
989.6 | 50.5 | -1.0096
989.7 | 50.5 | -1.0096
989.8 | 50.5 | -1.0096
989.9 | 50.5 | -1.0096
990 | 50.5 | -1.0096
990.1 | 50.5 | -1.0096
990.2 | 50.5 | -1.0096
990.3 | 50.5 | -1.0096
990.4 | 50.5 | -1.0096
990.5 | 50.5 | -1.0096
990.6 | 50.5 | -1.0096
990.7 | 50.5 | -1.0096
990.8 | 50.5 | -1.0096
990.9 | 50.5 | -1.0096
991 | 50.5 | -1.0096
991.1 | 50.5 | -1.0096
991.2 | 50.5 | -1.0096
991.3 | 50.5 | -1.0096
991.4 | 50.5 | -1.0096
991.5 | 50.5 | -1.0096
991.6 | 50.5 | -1.0096
991.7 | 50.5 | -1.0096
991.8 | 50.5 | -1.0096
991.9 | 50.5 | -1.0096
992 | 50.5 | -1.0096
992.1 | 50.5 | -1.0096
992.2 | 50.5 | -1.0096
992.3 | 50.5 | -1.0096
992.4 | 50.5 | -1.0096
992.5 | 50.5 | -1.0096
992.6 | 50.5 | -1.0094
992.7 | 50.5 | -1.0094
992.8 | 50.5 | -1.0094
992.9 | 50.5 | -1.0094
993 | 50.5 | -1.0094
993.1 | 50.5 | -1.0094
993.2 | 50.5 | -1.0094
993.3 | 50.5 | -1.0094
993.4 | 50.5 | -1.0094
993.5 | 50.5 | -1.0094
993.6 | 50.5 | -1.0094
993.7 | 50.5 | -1.0094
993.8 | 50.5 | -1.0094
993.9 | 50.5 | -1.0094
994 | 50.5 | -1.0094
994.1 | 50.5 | -1.0094
994.2 | 50.5 | -1.0094
994.3 | 50.5 | -1.0094
994.4 | 50.5 | -1.0094
994.5 | 50.5 | -1.0094
994.6 | 50.5 | -1.0094
994.7 | 50.5 | -1.0094
994.8 | 50.5 | -1.0094
994.9 | 50.5 | -1.0094
995 | 50.5 | -1.0096
995.1 | 50.5 | -1.0096
995.2 | 50.5 | -1.0096
995.3 | 50.5 | -1.0096
995.4 | 50.5 | -1.0096
995.5 | 50.5 | -1.0096
995.6 | 50.5 | -1.0096
995.7 | 50.5 | -1.0096
995.8 | 50.5 | -1.0096
995.9 | 50.5 | -1.0096
996 | 50.5 | -1.0096
996.1 | 50.5 | -1.0096
996.2 | 50.5 | -1.0096
996.3 | 50.5 | -1.0096
996.4 | 50.5 | -1.0096
996.5 | 50.5 | -1.0096
996.6 | 50.5 | -1.0096
996.7 | 50.5 | -1.0096
996.8 | 50.5 | -1.0096
996.9 | 50.5 | -1.0096
997 | 50.5 | -1.0096
997.1 | 50.5 | -1.0096
997.2 | 50.5 | -1.0096
997.3 | 50.5 | -1.0096
997.4 | 50.5 | -1.0096
997.5 | 50.5 | -1.0096
997.6 | 50.5 | -1.0096
997.7 | 50.5 | -1.0096
997.8 | 50.5 | -1.0096
997.9 | 50.5 | -1.0096
998 | 50.5 | -1.0096
998.1 | 50.5 | -1.0096
998.2 | 50.5 | -1.0096
998.3 | 50.5 | -1.0096
998.4 | 50.5 | -1.0096
998.5 | 50.5 | -1.0096
998.6 | 50.5 | -1.0096
998.7 | 50.5 | -1.0096
998.8 | 50.5 | -1.0096
998.9 | 50.5 | -1.0096
999 | 50.5 | -1.0096
999.1 | 50.5 | -1.0096
999.2 | 50.5 | -1.0096
999.3 | 50.5 | -1.0096
999.4 | 50.5 | -1.0096
999.5 | 50.5 | -1.0096
999.6 | 50.5 | -1.0096
999.7 | 50.5 | -1.0096
999.8 | 50.5 | -1.0096
999.9 | 50.5 | -1.0096
1000 | 50.5 | -1.0096
1000.1 | 50.5 | -1.0096
1000.2 | 50.5 | -1.0096
1000.3 | 50.5 | -1.0096
1000.4 | 50.5 | -1.0096
1000.5 | 50.5 | -1.0096
1000.6 | 50.5 | -1.0096
1000.7 | 50.5 | -1.0096
1000.8 | 50.5 | -1.0096
1000.9 | 50.5 | -1.0094
1001 | 50.5 | -1.0094
1001.1 | 50.5 | -1.0094
1001.2 | 50.5 | -1.0094
1001.3 | 50.5 | -1.0094
1001.4 | 50.5 | -1.0094
1001.5 | 50.5 | -1.0094
1001.6 | 50.5 | -1.0094
1001.7 | 50.5 | -1.0094
1001.8 | 50.5 | -1.0094
1001.9 | 50.5 | -1.0096
1002 | 50.5 | -1.0096
1002.1 | 50.5 | -1.0096
1002.2 | 50.5 | -1.0096
1002.3 | 50.5 | -1.0096
1002.4 | 50.5 | -1.0096
1002.5 | 50.5 | -1.0096
1002.6 | 50.5 | -1.0096
1002.7 | 50.5 | -1.0096
1002.8 | 50.5 | -1.0096
1002.9 | 50.5 | -1.0096
1003 | 50.5 | -1.0096
1003.1 | 50.5 | -1.0096
1003.2 | 50.5 | -1.0096
1003.3 | 50.5 | -1.0096
1003.4 | 50.5 | -1.0096
1003.5 | 50.5 | -1.0096
1003.6 | 50.5 | -1.0096
1003.7 | 50.5 | -1.0096
1003.8 | 50.5 | -1.0094
1003.9 | 50.5 | -1.0094
1004 | 50.5 | -1.0094
1004.1 | 50.5 | -1.0094
1004.2 | 50.5 | -1.0094
1004.3 | 50.5 | -1.0096
1004.4 | 50.5 | -1.0096
1004.5 | 50.5 | -1.0096
1004.6 | 50.5 | -1.0096
1004.7 | 50.5 | -1.0096
1004.8 | 50.5 | -1.0096
1004.9 | 50.5 | -1.0096
1005 | 50.5 | -1.0096
1005.1 | 50.5 | -1.0096
1005.2 | 50.5 | -1.0096
1005.3 | 50.5 | -1.0096
1005.4 | 50.5 | -1.0096
1005.5 | 50.5 | -1.0096
1005.6 | 50.5 | -1.0096
1005.7 | 50.5 | -1.0096
1005.8 | 50.5 | -1.0096
1005.9 | 50.5 | -1.0096
1006 | 50.5 | -1.0096
1006.1 | 50.5 | -1.0096
1006.2 | 50.5 | -1.0096
1006.3 | 50.5 | -1.0096
1006.4 | 50.5 | -1.0096
1006.5 | 50.5 | -1.0096
1006.6 | 50.5 | -1.0096
1006.7 | 50.5 | -1.0096
1006.8 | 50.5 | -1.0096
1006.9 | 50.5 | -1.0096
1007 | 50.5 | -1.0096
1007.1 | 50.5 | -1.0096
1007.2 | 50.5 | -1.0096
1007.3 | 50.5 | -1.0096
1007.4 | 50.5 | -1.0096
1007.5 | 50.5 | -1.0096
1007.6 | 50.5 | -1.0096
1007.7 | 50.5 | -1.0096
1007.8 | 50.5 | -1.0096
1007.9 | 50.5 | -1.0094
1008 | 50.5 | -1.0094
1008.1 | 50.5 | -1.0094
1008.2 | 50.5 | -1.0094
1008.3 | 50.5 | -1.0094
1008.4 | 50.5 | -1.0094
1008.5 | 50.5 | -1.0094
1008.6 | 50.5 | -1.0094
1008.7 | 50.5 | -1.0094
1008.8 | 50.5 | -1.0096
1008.9 | 50.5 | -1.0096
1009 | 50.5 | -1.0096
1009.1 | 50.5 | -1.0096
1009.2 | 50.5 | -1.0096
1009.3 | 50.5 | -1.0096
1009.4 | 50.5 | -1.0096
1009.5 | 50.5 | -1.0096
1009.6 | 50.5 | -1.0096
1009.7 | 50.5 | -1.0096
1009.8 | 50.5 | -1.0096
1009.9 | 50.5 | -1.0096
1010 | 50.5 | -1.0096
1010.1 | 50.5 | -1.0096
1010.2 | 50.5 | -1.0096
1010.3 | 50.5 | -1.0096
1010.4 | 50.5 | -1.0096
1010.5 | 50.5 | -1.0096
1010.6 | 50.5 | -1.0096
1010.7 | 50.5 | -1.0096
1010.8 | 50.5 | -1.0096
1010.9 | 50.5 | -1.0096
1011 | 50.5 | -1.0096
1011.1 | 50.5 | -1.0096
1011.2 | 50.5 | -1.0096
1011.3 | 50.5 | -1.0096
1011.4 | 50.5 | -1.0096
1011.5 | 50.5 | -1.0096
1011.6 | 50.5 | -1.0096
1011.7 | 50.5 | -1.0096
1011.8 | 50.5 | -1.0096
1011.9 | 50.5 | -1.0096
1012 | 50.5 | -1.0096
1012.1 | 50.5 | -1.0096
1012.2 | 50.5 | -1.0096
1012.3 | 50.5 | -1.0096
1012.4 | 50.5 | -1.0096
1012.5 | 50.5 | -1.0096
1012.6 | 50.5 | -1.0096
1012.7 | 50.5 | -1.0096
1012.8 | 50.5 | -1.0096
1012.9 | 50.5 | -1.0096
1013 | 50.5 | -1.0096
1013.1 | 50.5 | -1.0096
1013.2 | 50.5 | -1.0096
1013.3 | 50.5 | -1.0096
1013.4 | 50.5 | -1.0096
1013.5 | 50.5 | -1.0096
1013.6 | 50.5 | -1.0096
1013.7 | 50.5 | -1.0096
1013.8 | 50.5 | -1.0096
1013.9 | 50.5 | -1.0096
1014 | 50.5 | -1.0096
1014.1 | 50.5 | -1.0096
1014.2 | 50.5 | -1.0096
1014.3 | 50.5 | -1.0096
1014.4 | 50.5 | -1.0096
1014.5 | 50.5 | -1.0096
1014.6 | 50.5 | -1.0096
1014.7 | 50.5 | -1.0094
1014.8 | 50.5 | -1.0094
1014.9 | 50.5 | -1.0094
1015 | 50.5 | -1.0094
1015.1 | 50.5 | -1.0094
1015.2 | 50.5 | -1.0094
1015.3 | 50.5 | -1.0094
1015.4 | 50.5 | -1.0094
1015.5 | 50.5 | -1.0094
1015.6 | 50.5 | -1.0094
1015.7 | 50.5 | -1.0094
1015.8 | 50.5 | -1.0094
1015.9 | 50.5 | -1.0094
1016 | 50.5 | -1.0094
1016.1 | 50.5 | -1.0094
1016.2 | 50.5 | -1.0094
1016.3 | 50.5 | -1.0094
1016.4 | 50.5 | -1.0094
1016.5 | 50.5 | -1.0094
1016.6 | 50.5 | -1.0094
1016.7 | 50.5 | -1.0094
1016.8 | 50.5 | -1.0094
1016.9 | 50.5 | -1.0094
1017 | 50.5 | -1.0094
1017.1 | 50.5 | -1.0096
1017.2 | 50.5 | -1.0096
1017.3 | 50.5 | -1.0096
1017.4 | 50.5 | -1.0096
1017.5 | 50.5 | -1.0096
1017.6 | 50.5 | -1.0096
1017.7 | 50.5 | -1.0096
1017.8 | 50.5 | -1.0096
1017.9 | 50.5 | -1.0096
1018 | 50.5 | -1.0096
1018.1 | 50.5 | -1.0096
1018.2 | 50.5 | -1.0096
1018.3 | 50.5 | -1.0096
1018.4 | 50.5 | -1.0096
1018.5 | 50.5 | -1.0096
1018.6 | 50.5 | -1.0096
1018.7 | 50.5 | -1.0096
1018.8 | 50.5 | -1.0096
1018.9 | 50.5 | -1.0096
1019 | 50.5 | -1.0096
1019.1 | 50.5 | -1.0096
1019.2 | 50.5 | -1.0096
1019.3 | 50.5 | -1.0096
1019.4 | 50.5 | -1.0096
1019.5 | 50.5 | -1.0096
1019.6 | 50.5 | -1.0096
1019.7 | 50.5 | -1.0096
1019.8 | 50.5 | -1.0096
1019.9 | 50.5 | -1.0096
1020 | 50.5 | -1.0096
1020.1 | 50.5 | -1.0096
1020.2 | 50.5 | -1.0096
1020.3 | 50.5 | -1.0096
1020.4 | 50.5 | -1.0096
1020.5 | 50.5 | -1.0096
1020.6 | 50.5 | -1.0096
1020.7 | 50.5 | -1.0096
1020.8 | 50.5 | -1.0096
1020.9 | 50.5 | -1.0096
1021 | 50.5 | -1.0096
1021.1 | 50.5 | -1.0096
1021.2 | 50.5 | -1.0096
1021.3 | 50.5 | -1.0096
1021.4 | 50.5 | -1.0096
1021.5 | 50.5 | -1.0096
1021.6 | 50.5 | -1.0096
1021.7 | 50.5 | -1.0096
1021.8 | 50.5 | -1.0094
1021.9 | 50.5 | -1.0094
1022 | 50.5 | -1.0094
1022.1 | 50.5 | -1.0094
1022.2 | 50.5 | -1.0094
1022.3 | 50.5 | -1.0094
1022.4 | 50.5 | -1.0094
1022.5 | 50.5 | -1.0094
1022.6 | 50.5 | -1.0094
1022.7 | 50.5 | -1.0094
1022.8 | 50.5 | -1.0094
1022.9 | 50.5 | -1.0094
1023 | 50.5 | -1.0094
1023.1 | 50.5 | -1.0094
1023.2 | 50.5 | -1.0094
1023.3 | 50.5 | -1.0094
1023.4 | 50.5 | -1.0094
1023.5 | 50.5 | -1.0094
1023.6 | 50.5 | -1.0094
1023.7 | 50.5 | -1.0094
1023.8 | 50.5 | -1.0094
1023.9 | 50.5 | -1.0094
1024 | 50.5 | -1.0094
1024.1 | 50.5 | -1.0094
1024.2 | 50.5 | -1.0096
1024.3 | 50.5 | -1.0096
1024.4 | 50.5 | -1.0096
1024.5 | 50.5 | -1.0096
1024.6 | 50.5 | -1.0096
1024.7 | 50.5 | -1.0096
1024.8 | 50.5 | -1.0096
1024.9 | 50.5 | -1.0096
1025 | 50.5 | -1.0096
1025.1 | 50.5 | -1.0096
1025.2 | 50.5 | -1.0096
1025.3 | 50.5 | -1.0096
1025.4 | 50.5 | -1.0096
1025.5 | 50.5 | -1.0096
1025.6 | 50.5 | -1.0096
1025.7 | 50.5 | -1.0096
1025.8 | 50.5 | -1.0096
1025.9 | 50.5 | -1.0096
1026 | 50.5 | -1.0096
1026.1 | 50.5 | -1.0096
1026.2 | 50.5 | -1.0096
1026.3 | 50.5 | -1.0096
1026.4 | 50.5 | -1.0096
1026.5 | 50.5 | -1.0096
1026.6 | 50.5 | -1.0096
1026.7 | 50.5 | -1.0096
1026.8 | 50.5 | -1.0096
1026.9 | 50.5 | -1.0096
1027 | 50.5 | -1.0096
1027.1 | 50.5 | -1.0096
1027.2 | 50.5 | -1.0096
1027.3 | 50.5 | -1.0096
1027.4 | 50.5 | -1.0096
1027.5 | 50.5 | -1.0096
1027.6 | 50.5 | -1.0096
1027.7 | 50.5 | -1.0096
1027.8 | 50.5 | -1.0096
1027.9 | 50.5 | -1.0096
1028 | 50.5 | -1.0096
1028.1 | 50.5 | -1.0098
1028.2 | 50.5 | -1.0098
1028.3 | 50.5 | -1.0098
1028.4 | 50.5 | -1.0098
1028.5 | 50.5 | -1.0098
1028.6 | 50.5 | -1.0098
1028.7 | 50.5 | -1.0098
1028.8 | 50.5 | -1.0096
1028.9 | 50.5 | -1.0096
1029 | 50.5 | -1.0096
1029.1 | 50.5 | -1.0096
1029.2 | 50.5 | -1.0096
1029.3 | 50.5 | -1.0094
1029.4 | 50.5 | -1.0096
1029.5 | 50.5 | -1.0096
1029.6 | 50.5 | -1.0096
1029.7 | 50.5 | -1.0096
1029.8 | 50.5 | -1.0096
1029.9 | 50.5 | -1.0096
1030 | 50.5 | -1.0096
1030.1 | 50.5 | -1.0096
1030.2 | 50.5 | -1.0096
1030.3 | 50.5 | -1.0096
1030.4 | 50.5 | -1.0096
1030.5 | 50.5 | -1.0094
1030.6 | 50.5 | -1.0094
1030.7 | 50.5 | -1.0094
1030.8 | 50.5 | -1.0094
1030.9 | 50.5 | -1.0094
1031 | 50.5 | -1.0094
1031.1 | 50.5 | -1.0094
1031.2 | 50.5 | -1.0094
1031.3 | 50.5 | -1.0094
1031.4 | 50.5 | -1.0094
1031.5 | 50.5 | -1.0094
1031.6 | 50.5 | -1.0094
1031.7 | 50.5 | -1.0094
1031.8 | 50.5 | -1.0094
1031.9 | 50.5 | -1.0094
1032 | 50.5 | -1.0094
1032.1 | 50.5 | -1.0094
1032.2 | 50.5 | -1.0094
1032.3 | 50.5 | -1.0094
1032.4 | 50.5 | -1.0094
1032.5 | 50.5 | -1.0094
1032.6 | 50.5 | -1.0094
1032.7 | 50.5 | -1.0094
1032.8 | 50.5 | -1.0094
1032.9 | 50.5 | -1.0094
1033 | 50.5 | -1.0094
1033.1 | 50.5 | -1.0094
1033.2 | 50.5 | -1.0094
1033.3 | 50.5 | -1.0094
1033.4 | 50.5 | -1.0094
1033.5 | 50.5 | -1.0094
1033.6 | 50.5 | -1.0094
1033.7 | 50.5 | -1.0094
1033.8 | 50.5 | -1.0094
1033.9 | 50.5 | -1.0094
1034 | 50.5 | -1.0094
1034.1 | 50.5 | -1.0096
1034.2 | 50.5 | -1.0096
1034.3 | 50.5 | -1.0096
1034.4 | 50.5 | -1.0096
1034.5 | 50.5 | -1.0096
1034.6 | 50.5 | -1.0096
1034.7 | 50.5 | -1.0096
1034.8 | 50.5 | -1.0096
1034.9 | 50.5 | -1.0096
1035 | 50.5 | -1.0096
1035.1 | 50.5 | -1.0096
1035.2 | 50.5 | -1.0096
1035.3 | 50.5 | -1.0096
1035.4 | 50.5 | -1.0096
1035.5 | 50.5 | -1.0096
1035.6 | 50.5 | -1.0096
1035.7 | 50.5 | -1.0096
1035.8 | 50.5 | -1.0096
1035.9 | 50.5 | -1.0096
1036 | 50.5 | -1.0096
1036.1 | 50.5 | -1.0096
1036.2 | 50.5 | -1.0096
1036.3 | 50.5 | -1.0096
1036.4 | 50.5 | -1.0096
1036.5 | 50.5 | -1.0096
1036.6 | 50.5 | -1.0096
1036.7 | 50.5 | -1.0096
1036.8 | 50.5 | -1.0096
1036.9 | 50.5 | -1.0096
1037 | 50.5 | -1.0096
1037.1 | 50.5 | -1.0096
1037.2 | 50.5 | -1.0096
1037.3 | 50.5 | -1.0096
1037.4 | 50.5 | -1.0096
1037.5 | 50.5 | -1.0096
1037.6 | 50.5 | -1.0094
1037.7 | 50.5 | -1.0094
1037.8 | 50.5 | -1.0094
1037.9 | 50.5 | -1.0094
1038 | 50.5 | -1.0094
1038.1 | 50.5 | -1.0094
1038.2 | 50.5 | -1.0094
1038.3 | 50.5 | -1.0094
1038.4 | 50.5 | -1.0094
1038.5 | 50.5 | -1.0094
1038.6 | 50.5 | -1.0094
1038.7 | 50.5 | -1.0096
1038.8 | 50.5 | -1.0096
1038.9 | 50.5 | -1.0096
1039 | 50.5 | -1.0096
1039.1 | 50.5 | -1.0096
1039.2 | 50.5 | -1.0096
1039.3 | 50.5 | -1.0096
1039.4 | 50.5 | -1.0096
1039.5 | 50.5 | -1.0096
1039.6 | 50.5 | -1.0096
1039.7 | 50.5 | -1.0096
1039.8 | 50.5 | -1.0096
1039.9 | 50.5 | -1.0096
1040 | 50.5 | -1.0096
1040.1 | 50.5 | -1.0096
1040.2 | 50.5 | -1.0096
1040.3 | 50.5 | -1.0096
1040.4 | 50.5 | -1.0096
1040.5 | 50.5 | -1.0096
1040.6 | 50.5 | -1.0096
1040.7 | 50.5 | -1.0096
1040.8 | 50.5 | -1.0096
1040.9 | 50.5 | -1.0096
1041 | 50.5 | -1.0096
1041.1 | 50.5 | -1.0096
1041.2 | 50.5 | -1.0096
1041.3 | 50.5 | -1.0096
1041.4 | 50.5 | -1.0096
1041.5 | 50.5 | -1.0096
1041.6 | 50.5 | -1.0096
1041.7 | 50.5 | -1.0096
1041.8 | 50.5 | -1.0096
1041.9 | 50.5 | -1.0096
1042 | 50.5 | -1.0096
1042.1 | 50.5 | -1.0096
1042.2 | 50.5 | -1.0096
1042.3 | 50.5 | -1.0096
1042.4 | 50.5 | -1.0094
1042.5 | 50.5 | -1.0094
1042.6 | 50.5 | -1.0094
1042.7 | 50.5 | -1.0094
1042.8 | 50.5 | -1.0094
1042.9 | 50.5 | -1.0094
1043 | 50.5 | -1.0094
1043.1 | 50.5 | -1.0094
1043.2 | 50.5 | -1.0094
1043.3 | 50.5 | -1.0094
1043.4 | 50.5 | -1.0094
1043.5 | 50.5 | -1.0094
1043.6 | 50.5 | -1.0094
1043.7 | 50.5 | -1.0094
1043.8 | 50.5 | -1.0094
1043.9 | 50.5 | -1.0094
1044 | 50.5 | -1.0094
1044.1 | 50.5 | -1.0094
1044.2 | 50.5 | -1.0094
1044.3 | 50.5 | -1.0094
1044.4 | 50.5 | -1.0094
1044.5 | 50.5 | -1.0094
1044.6 | 50.5 | -1.0096
1044.7 | 50.5 | -1.0096
1044.8 | 50.5 | -1.0096
1044.9 | 50.5 | -1.0096
1045 | 50.5 | -1.0096
1045.1 | 50.5 | -1.0096
1045.2 | 50.5 | -1.0096
1045.3 | 50.5 | -1.0096
1045.4 | 50.5 | -1.0096
1045.5 | 50.5 | -1.0096
1045.6 | 50.5 | -1.0096
1045.7 | 50.5 | -1.0096
1045.8 | 50.5 | -1.0096
1045.9 | 50.5 | -1.0096
1046 | 50.5 | -1.0096
1046.1 | 50.5 | -1.0096
1046.2 | 50.5 | -1.0096
1046.3 | 50.5 | -1.0096
1046.4 | 50.5 | -1.0096
1046.5 | 50.5 | -1.0096
1046.6 | 50.5 | -1.0096
1046.7 | 50.5 | -1.0096
1046.8 | 50.5 | -1.0096
1046.9 | 50.5 | -1.0096
1047 | 50.5 | -1.0096
1047.1 | 50.5 | -1.0096
1047.2 | 50.5 | -1.0096
1047.3 | 50.5 | -1.0096
1047.4 | 50.5 | -1.0096
1047.5 | 50.5 | -1.0096
1047.6 | 50.5 | -1.0096
1047.7 | 50.5 | -1.0096
1047.8 | 50.5 | -1.0096
1047.9 | 50.5 | -1.0096
1048 | 50.5 | -1.0096
1048.1 | 50.5 | -1.0096
1048.2 | 50.5 | -1.0096
1048.3 | 50.5 | -1.0096
1048.4 | 50.5 | -1.0096
1048.5 | 50.5 | -1.0096
1048.6 | 50.5 | -1.0096
1048.7 | 50.5 | -1.0096
1048.8 | 50.5 | -1.0096
1048.9 | 50.5 | -1.0096
1049 | 50.5 | -1.0096
1049.1 | 50.5 | -1.0096
1049.2 | 50.5 | -1.0096
1049.3 | 50.5 | -1.0096
1049.4 | 50.5 | -1.0096
1049.5 | 50.5 | -1.0096
1049.6 | 50.5 | -1.0096
1049.7 | 50.5 | -1.0096
1049.8 | 50.5 | -1.0096
1049.9 | 50.5 | -1.0096
1050 | 50.5 | -1.0096
1050.1 | 50.5 | -1.0096
1050.2 | 50.5 | -1.0096
1050.3 | 50.5 | -1.0096
1050.4 | 50.5 | -1.0096
1050.5 | 50.5 | -1.0096
1050.6 | 50.5 | -1.0096
1050.7 | 50.5 | -1.0096
1050.8 | 50.5 | -1.0096
1050.9 | 50.5 | -1.0096
1051 | 50.5 | -1.0096
1051.1 | 50.5 | -1.0096
1051.2 | 50.5 | -1.0096
1051.3 | 50.5 | -1.0096
1051.4 | 50.5 | -1.0096
1051.5 | 50.5 | -1.0096
1051.6 | 50.5 | -1.0096
1051.7 | 50.5 | -1.0096
1051.8 | 50.5 | -1.0096
1051.9 | 50.5 | -1.0096
1052 | 50.5 | -1.0096
1052.1 | 50.5 | -1.0096
1052.2 | 50.5 | -1.0096
1052.3 | 50.5 | -1.0096
1052.4 | 50.5 | -1.0096
1052.5 | 50.5 | -1.0096
1052.6 | 50.5 | -1.0096
1052.7 | 50.5 | -1.0096
1052.8 | 50.5 | -1.0096
1052.9 | 50.5 | -1.0096
1053 | 50.5 | -1.0096
1053.1 | 50.5 | -1.0096
1053.2 | 50.5 | -1.0096
1053.3 | 50.5 | -1.0096
1053.4 | 50.5 | -1.0096
1053.5 | 50.5 | -1.0096
1053.6 | 50.5 | -1.0096
1053.7 | 50.5 | -1.0096
1053.8 | 50.5 | -1.0096
1053.9 | 50.5 | -1.0096
1054 | 50.5 | -1.0096
1054.1 | 50.5 | -1.0096
1054.2 | 50.5 | -1.0096
1054.3 | 50.5 | -1.0096
1054.4 | 50.5 | -1.0096
1054.5 | 50.5 | -1.0096
1054.6 | 50.5 | -1.0096
1054.7 | 50.5 | -1.0096
1054.8 | 50.5 | -1.0096
1054.9 | 50.5 | -1.0096
1055 | 50.5 | -1.0096
1055.1 | 50.5 | -1.0096
1055.2 | 50.5 | -1.0096
1055.3 | 50.5 | -1.0096
1055.4 | 50.5 | -1.0096
1055.5 | 50.5 | -1.0096
1055.6 | 50.5 | -1.0096
1055.7 | 50.5 | -1.0096
1055.8 | 50.5 | -1.0096
1055.9 | 50.5 | -1.0096
1056 | 50.5 | -1.0096
1056.1 | 50.5 | -1.0096
1056.2 | 50.5 | -1.0096
1056.3 | 50.5 | -1.0096
1056.4 | 50.5 | -1.0096
1056.5 | 50.5 | -1.0096
1056.6 | 50.5 | -1.0096
1056.7 | 50.5 | -1.0096
1056.8 | 50.5 | -1.0096
1056.9 | 50.5 | -1.0096
1057 | 50.5 | -1.0096
1057.1 | 50.5 | -1.0096
1057.2 | 50.5 | -1.0096
1057.3 | 50.5 | -1.0096
1057.4 | 50.5 | -1.0096
1057.5 | 50.5 | -1.0096
1057.6 | 50.5 | -1.0096
1057.7 | 50.5 | -1.0096
1057.8 | 50.5 | -1.0096
1057.9 | 50.5 | -1.0096
1058 | 50.5 | -1.0096
1058.1 | 50.5 | -1.0096
1058.2 | 50.5 | -1.0096
1058.3 | 50.5 | -1.0096
1058.4 | 50.5 | -1.0096
1058.5 | 50.5 | -1.0096
1058.6 | 50.5 | -1.0096
1058.7 | 50.5 | -1.0096
1058.8 | 50.5 | -1.0096
1058.9 | 50.5 | -1.0096
1059 | 50.5 | -1.0096
1059.1 | 50.5 | -1.0096
1059.2 | 50.5 | -1.0096
1059.3 | 50.5 | -1.0096
1059.4 | 50.5 | -1.0096
1059.5 | 50.5 | -1.0096
1059.6 | 50.5 | -1.0096
1059.7 | 50.5 | -1.0096
1059.8 | 50.5 | -1.0096
1059.9 | 50.5 | -1.0096
1060 | 50.5 | -1.0096
1060.1 | 50.5 | -1.0096
1060.2 | 50.5 | -1.0094
1060.3 | 50.5 | -1.0094
1060.4 | 50.5 | -1.0094
1060.5 | 50.5 | -1.0094
1060.6 | 50.5 | -1.0094
1060.7 | 50.5 | -1.0094
1060.8 | 50.5 | -1.0094
1060.9 | 50.5 | -1.0094
1061 | 50.5 | -1.0094
1061.1 | 50.5 | -1.0094
1061.2 | 50.5 | -1.0094
1061.3 | 50.5 | -1.0094
1061.4 | 50.5 | -1.0094
1061.5 | 50.5 | -1.0094
1061.6 | 50.5 | -1.0094
1061.7 | 50.5 | -1.0094
1061.8 | 50.5 | -1.0094
1061.9 | 50.5 | -1.0094
1062 | 50.5 | -1.0094
1062.1 | 50.5 | -1.0094
1062.2 | 50.5 | -1.0094
1062.3 | 50.5 | -1.0094
1062.4 | 50.5 | -1.0094
1062.5 | 50.5 | -1.0094
1062.6 | 50.5 | -1.0096
1062.7 | 50.5 | -1.0096
1062.8 | 50.5 | -1.0096
1062.9 | 50.5 | -1.0096
1063 | 50.5 | -1.0096
1063.1 | 50.5 | -1.0096
1063.2 | 50.5 | -1.0096
1063.3 | 50.5 | -1.0096
1063.4 | 50.5 | -1.0096
1063.5 | 50.5 | -1.0096
1063.6 | 50.5 | -1.0096
1063.7 | 50.5 | -1.0096
1063.8 | 50.5 | -1.0096
1063.9 | 50.5 | -1.0096
1064 | 50.5 | -1.0096
1064.1 | 50.5 | -1.0096
1064.2 | 50.5 | -1.0096
1064.3 | 50.5 | -1.0096
1064.4 | 50.5 | -1.0096
1064.5 | 50.5 | -1.0096
1064.6 | 50.5 | -1.0096
1064.7 | 50.5 | -1.0096
1064.8 | 50.5 | -1.0096
1064.9 | 50.5 | -1.0096
1065 | 50.5 | -1.0096
1065.1 | 50.5 | -1.0096
1065.2 | 50.5 | -1.0096
1065.3 | 50.5 | -1.0096
1065.4 | 50.5 | -1.0096
1065.5 | 50.5 | -1.0096
1065.6 | 50.5 | -1.0096
1065.7 | 50.5 | -1.0096
1065.8 | 50.5 | -1.0096
1065.9 | 50.5 | -1.0096
1066 | 50.5 | -1.0096
1066.1 | 50.5 | -1.0096
1066.2 | 50.5 | -1.0096
1066.3 | 50.5 | -1.0096
1066.4 | 50.5 | -1.0096
1066.5 | 50.5 | -1.0096
1066.6 | 50.5 | -1.0096
1066.7 | 50.5 | -1.0096
1066.8 | 50.5 | -1.0096
1066.9 | 50.5 | -1.0096
1067 | 50.5 | -1.0096
1067.1 | 50.5 | -1.0096
1067.2 | 50.5 | -1.0096
1067.3 | 50.5 | -1.0096
1067.4 | 50.5 | -1.0096
1067.5 | 50.5 | -1.0096
1067.6 | 50.5 | -1.0096
1067.7 | 50.5 | -1.0096
1067.8 | 50.5 | -1.0096
1067.9 | 50.5 | -1.0096
1068 | 50.5 | -1.0096
1068.1 | 50.5 | -1.0096
1068.2 | 50.5 | -1.0096
1068.3 | 50.5 | -1.0096
1068.4 | 50.5 | -1.0096
1068.5 | 50.5 | -1.0096
1068.6 | 50.5 | -1.0096
1068.7 | 50.5 | -1.0096
1068.8 | 50.5 | -1.0096
1068.9 | 50.5 | -1.0096
1069 | 50.5 | -1.0096
1069.1 | 50.5 | -1.0096
1069.2 | 50.5 | -1.0096
1069.3 | 50.5 | -1.0096
1069.4 | 50.5 | -1.0096
1069.5 | 50.5 | -1.0096
1069.6 | 50.5 | -1.0096
1069.7 | 50.5 | -1.0096
1069.8 | 50.5 | -1.0096
1069.9 | 50.5 | -1.0096
1070 | 50.5 | -1.0096
1070.1 | 50.5 | -1.0096
1070.2 | 50.5 | -1.0096
1070.3 | 50.5 | -1.0096
1070.4 | 50.5 | -1.0096
1070.5 | 50.5 | -1.0096
1070.6 | 50.5 | -1.0096
1070.7 | 50.5 | -1.0096
1070.8 | 50.5 | -1.0096
1070.9 | 50.5 | -1.0096
1071 | 50.5 | -1.0096
1071.1 | 50.5 | -1.0096
1071.2 | 50.5 | -1.0096
1071.3 | 50.5 | -1.0096
1071.4 | 50.5 | -1.0096
1071.5 | 50.5 | -1.0096
1071.6 | 50.5 | -1.0096
1071.7 | 50.5 | -1.0096
1071.8 | 50.5 | -1.0096
1071.9 | 50.5 | -1.0096
1072 | 50.5 | -1.0096
1072.1 | 50.5 | -1.0096
1072.2 | 50.5 | -1.0096
1072.3 | 50.5 | -1.0096
1072.4 | 50.5 | -1.0096
1072.5 | 50.5 | -1.0096
1072.6 | 50.5 | -1.0096
1072.7 | 50.5 | -1.0096
1072.8 | 50.5 | -1.0096
1072.9 | 50.5 | -1.0096
1073 | 50.5 | -1.0096
1073.1 | 50.5 | -1.0096
1073.2 | 50.5 | -1.0096
1073.3 | 50.5 | -1.0096
1073.4 | 50.5 | -1.0096
1073.5 | 50.5 | -1.0096
1073.6 | 50.5 | -1.0096
1073.7 | 50.5 | -1.0096
1073.8 | 50.5 | -1.0096
1073.9 | 50.5 | -1.0096
1074 | 50.5 | -1.0096
1074.1 | 50.5 | -1.0096
1074.2 | 50.5 | -1.0096
1074.3 | 50.5 | -1.0096
1074.4 | 50.5 | -1.0096
1074.5 | 50.5 | -1.0096
1074.6 | 50.5 | -1.0096
1074.7 | 50.5 | -1.0096
1074.8 | 50.5 | -1.0096
1074.9 | 50.5 | -1.0096
1075 | 50.5 | -1.0096
1075.1 | 50.5 | -1.0096
1075.2 | 50.5 | -1.0096
1075.3 | 50.5 | -1.0096
1075.4 | 50.5 | -1.0094
1075.5 | 50.5 | -1.0094
1075.6 | 50.5 | -1.0094
1075.7 | 50.5 | -1.0094
1075.8 | 50.5 | -1.0094
1075.9 | 50.5 | -1.0094
1076 | 50.5 | -1.0094
1076.1 | 50.5 | -1.0094
1076.2 | 50.5 | -1.0094
1076.3 | 50.5 | -1.0094
1076.4 | 50.5 | -1.0096
1076.5 | 50.5 | -1.0096
1076.6 | 50.5 | -1.0096
1076.7 | 50.5 | -1.0096
1076.8 | 50.5 | -1.0096
1076.9 | 50.5 | -1.0096
1077 | 50.5 | -1.0096
1077.1 | 50.5 | -1.0096
1077.2 | 50.5 | -1.0096
1077.3 | 50.5 | -1.0096
1077.4 | 50.5 | -1.0096
1077.5 | 50.5 | -1.0096
1077.6 | 50.5 | -1.0096
1077.7 | 50.5 | -1.0096
1077.8 | 50.5 | -1.0096
1077.9 | 50.5 | -1.0096
1078 | 50.5 | -1.0096
1078.1 | 50.5 | -1.0096
1078.2 | 50.5 | -1.0096
1078.3 | 50.5 | -1.0096
1078.4 | 50.5 | -1.0096
1078.5 | 50.5 | -1.0096
1078.6 | 50.5 | -1.0096
1078.7 | 50.5 | -1.0096
1078.8 | 50.5 | -1.0096
1078.9 | 50.5 | -1.0096
1079 | 50.5 | -1.0096
1079.1 | 50.5 | -1.0096
1079.2 | 50.5 | -1.0096
1079.3 | 50.5 | -1.0096
1079.4 | 50.5 | -1.0096
1079.5 | 50.5 | -1.0096
1079.6 | 50.5 | -1.0096
1079.7 | 50.5 | -1.0096
1079.8 | 50.5 | -1.0096
1079.9 | 50.5 | -1.0096
1080 | 50.5 | -1.0096
1080.1 | 50.5 | -1.0096
1080.2 | 50.5 | -1.0096
1080.3 | 50.5 | -1.0096
1080.4 | 50.5 | -1.0096
1080.5 | 50.5 | -1.0096
1080.6 | 50.5 | -1.0096
1080.7 | 50.5 | -1.0096
1080.8 | 50.5 | -1.0096
1080.9 | 50.5 | -1.0096
1081 | 50.5 | -1.0096
1081.1 | 50.5 | -1.0096
1081.2 | 50.5 | -1.0096
1081.3 | 50.5 | -1.0096
1081.4 | 50.5 | -1.0096
1081.5 | 50.5 | -1.0096
1081.6 | 50.5 | -1.0096
1081.7 | 50.5 | -1.0096
1081.8 | 50.5 | -1.0096
1081.9 | 50.5 | -1.0096
1082 | 50.5 | -1.0096
1082.1 | 50.5 | -1.0096
1082.2 | 50.5 | -1.0094
1082.3 | 50.5 | -1.0094
1082.4 | 50.5 | -1.0094
1082.5 | 50.5 | -1.0094
1082.6 | 50.5 | -1.0094
1082.7 | 50.5 | -1.0094
1082.8 | 50.5 | -1.0094
1082.9 | 50.5 | -1.0094
1083 | 50.5 | -1.0094
1083.1 | 50.5 | -1.0094
1083.2 | 50.5 | -1.0094
1083.3 | 50.5 | -1.0094
1083.4 | 50.5 | -1.0096
1083.5 | 50.5 | -1.0096
1083.6 | 50.5 | -1.0096
1083.7 | 50.5 | -1.0096
1083.8 | 50.5 | -1.0096
1083.9 | 50.5 | -1.0096
1084 | 50.5 | -1.0096
1084.1 | 50.5 | -1.0096
1084.2 | 50.5 | -1.0096
1084.3 | 50.5 | -1.0096
1084.4 | 50.5 | -1.0096
1084.5 | 50.5 | -1.0096
1084.6 | 50.5 | -1.0096
1084.7 | 50.5 | -1.0096
1084.8 | 50.5 | -1.0096
1084.9 | 50.5 | -1.0096
1085 | 50.5 | -1.0096
1085.1 | 50.5 | -1.0096
1085.2 | 50.5 | -1.0096
1085.3 | 50.5 | -1.0096
1085.4 | 50.5 | -1.0096
1085.5 | 50.5 | -1.0096
1085.6 | 50.5 | -1.0096
1085.7 | 50.5 | -1.0096
1085.8 | 50.5 | -1.0096
1085.9 | 50.5 | -1.0096
1086 | 50.5 | -1.0096
1086.1 | 50.5 | -1.0096
1086.2 | 50.5 | -1.0096
1086.3 | 50.5 | -1.0096
1086.4 | 50.5 | -1.0096
1086.5 | 50.5 | -1.0096
1086.6 | 50.5 | -1.0096
1086.7 | 50.5 | -1.0096
1086.8 | 50.5 | -1.0096
1086.9 | 50.5 | -1.0096
1087 | 50.5 | -1.0096
1087.1 | 50.5 | -1.0096
1087.2 | 50.5 | -1.0096
1087.3 | 50.5 | -1.0096
1087.4 | 50.5 | -1.0096
1087.5 | 50.5 | -1.0096
1087.6 | 50.5 | -1.0096
1087.7 | 50.5 | -1.0096
1087.8 | 50.5 | -1.0096
1087.9 | 50.5 | -1.0096
1088 | 50.5 | -1.0096
1088.1 | 50.5 | -1.0096
1088.2 | 50.5 | -1.0096
1088.3 | 50.5 | -1.0096
1088.4 | 50.5 | -1.0096
1088.5 | 50.5 | -1.0096
1088.6 | 50.5 | -1.0096
1088.7 | 50.5 | -1.0096
1088.8 | 50.5 | -1.0096
1088.9 | 50.5 | -1.0096
1089 | 50.5 | -1.0096
1089.1 | 50.5 | -1.0096
1089.2 | 50.5 | -1.0096
1089.3 | 50.5 | -1.0096
1089.4 | 50.5 | -1.0096
1089.5 | 50.5 | -1.0096
1089.6 | 50.5 | -1.0096
1089.7 | 50.5 | -1.0096
1089.8 | 50.5 | -1.0096
1089.9 | 50.5 | -1.0096
1090 | 50.5 | -1.0096
1090.1 | 50.5 | -1.0096
1090.2 | 50.5 | -1.0096
1090.3 | 50.5 | -1.0096
1090.4 | 50.5 | -1.0096
1090.5 | 50.5 | -1.0096
1090.6 | 50.5 | -1.0096
1090.7 | 50.5 | -1.0096
1090.8 | 50.5 | -1.0096
1090.9 | 50.5 | -1.0096
1091 | 50.5 | -1.0096
1091.1 | 50.5 | -1.0096
1091.2 | 50.5 | -1.0096
1091.3 | 50.5 | -1.0096
1091.4 | 50.5 | -1.0096
1091.5 | 50.5 | -1.0096
1091.6 | 50.5 | -1.0096
1091.7 | 50.5 | -1.0096
1091.8 | 50.5 | -1.0096
1091.9 | 50.5 | -1.0096
1092 | 50.5 | -1.0096
1092.1 | 50.5 | -1.0096
1092.2 | 50.5 | -1.0096
1092.3 | 50.5 | -1.0096
1092.4 | 50.5 | -1.0096
1092.5 | 50.5 | -1.0096
1092.6 | 50.5 | -1.0096
1092.7 | 50.5 | -1.0096
1092.8 | 50.5 | -1.0096
1092.9 | 50.5 | -1.0096
1093 | 50.5 | -1.0096
1093.1 | 50.5 | -1.0096
1093.2 | 50.5 | -1.0096
1093.3 | 50.5 | -1.0096
1093.4 | 50.5 | -1.0096
1093.5 | 50.5 | -1.0096
1093.6 | 50.5 | -1.0096
1093.7 | 50.5 | -1.0096
1093.8 | 50.5 | -1.0096
1093.9 | 50.5 | -1.0096
1094 | 50.5 | -1.0096
1094.1 | 50.5 | -1.0096
1094.2 | 50.5 | -1.0096
1094.3 | 50.5 | -1.0096
1094.4 | 50.5 | -1.0096
1094.5 | 50.5 | -1.0096
1094.6 | 50.5 | -1.0096
1094.7 | 50.5 | -1.0096
1094.8 | 50.5 | -1.0096
1094.9 | 50.5 | -1.0096
1095 | 50.5 | -1.0096
1095.1 | 50.5 | -1.0096
1095.2 | 50.5 | -1.0096
1095.3 | 50.5 | -1.0096
1095.4 | 50.5 | -1.0096
1095.5 | 50.5 | -1.0096
1095.6 | 50.5 | -1.0096
1095.7 | 50.5 | -1.0096
1095.8 | 50.5 | -1.0096
1095.9 | 50.5 | -1.0096
1096 | 50.5 | -1.0096
1096.1 | 50.5 | -1.0096
1096.2 | 50.5 | -1.0096
1096.3 | 50.5 | -1.0096
1096.4 | 50.5 | -1.0096
1096.5 | 50.5 | -1.0096
1096.6 | 50.5 | -1.0096
1096.7 | 50.5 | -1.0096
1096.8 | 50.5 | -1.0096
1096.9 | 50.5 | -1.0096
1097 | 50.5 | -1.0096
1097.1 | 50.5 | -1.0096
1097.2 | 50.5 | -1.0096
1097.3 | 50.5 | -1.0096
1097.4 | 50.5 | -1.0096
1097.5 | 50.5 | -1.0096
1097.6 | 50.5 | -1.0096
1097.7 | 50.5 | -1.0096
1097.8 | 50.5 | -1.0096
1097.9 | 50.5 | -1.0096
1098 | 50.5 | -1.0096
1098.1 | 50.5 | -1.0096
1098.2 | 50.5 | -1.0096
1098.3 | 50.5 | -1.0096
1098.4 | 50.5 | -1.0096
1098.5 | 50.5 | -1.0096
1098.6 | 50.5 | -1.0096
1098.7 | 50.5 | -1.0096
1098.8 | 50.5 | -1.0096
1098.9 | 50.5 | -1.0096
1099 | 50.5 | -1.0096
1099.1 | 50.5 | -1.0096
1099.2 | 50.5 | -1.0096
1099.3 | 50.5 | -1.0096
1099.4 | 50.5 | -1.0096
1099.5 | 50.5 | -1.0096
1099.6 | 50.5 | -1.0096
1099.7 | 50.5 | -1.0096
1099.8 | 50.5 | -1.0096
1099.9 | 50.5 | -1.0096
1100 | 50.5 | -1.0096
1100.1 | 50.5 | -1.0096
1100.2 | 50.5 | -1.0096
1100.3 | 50.5 | -1.0096
1100.4 | 50.5 | -1.0096
1100.5 | 50.5 | -1.0096
1100.6 | 50.5 | -1.0096
1100.7 | 50.5 | -1.0096
1100.8 | 50.5 | -1.0096
1100.9 | 50.5 | -1.0096
1101 | 50.5 | -1.0096
1101.1 | 50.5 | -1.0096
1101.2 | 50.5 | -1.0096
1101.3 | 50.5 | -1.0096
1101.4 | 50.5 | -1.0096
1101.5 | 50.5 | -1.0096
1101.6 | 50.5 | -1.0096
1101.7 | 50.5 | -1.0096
1101.8 | 50.5 | -1.0096
1101.9 | 50.5 | -1.0096
1102 | 50.5 | -1.0096
1102.1 | 50.5 | -1.0096
1102.2 | 50.5 | -1.0096
1102.3 | 50.5 | -1.0096
1102.4 | 50.5 | -1.0096
1102.5 | 50.5 | -1.0096
1102.6 | 50.5 | -1.0096
1102.7 | 50.5 | -1.0096
1102.8 | 50.5 | -1.0096
1102.9 | 50.5 | -1.0096
1103 | 50.5 | -1.0096
1103.1 | 50.5 | -1.0096
1103.2 | 50.5 | -1.0096
1103.3 | 50.5 | -1.0096
1103.4 | 50.5 | -1.0096
1103.5 | 50.5 | -1.0096
1103.6 | 50.5 | -1.0096
1103.7 | 50.5 | -1.0096
1103.8 | 50.5 | -1.0096
1103.9 | 50.5 | -1.0096
1104 | 50.5 | -1.0096
1104.1 | 50.5 | -1.0096
1104.2 | 50.5 | -1.0096
1104.3 | 50.5 | -1.0096
1104.4 | 50.5 | -1.0096
1104.5 | 50.5 | -1.0096
1104.6 | 50.5 | -1.0096
1104.7 | 50.5 | -1.0096
1104.8 | 50.5 | -1.0096
1104.9 | 50.5 | -1.0096
1105 | 50.5 | -1.0096
1105.1 | 50.5 | -1.0096
1105.2 | 50.5 | -1.0096
1105.3 | 50.5 | -1.0096
1105.4 | 50.5 | -1.0096
1105.5 | 50.5 | -1.0096
1105.6 | 50.5 | -1.0096
1105.7 | 50.5 | -1.0096
1105.8 | 50.5 | -1.0096
1105.9 | 50.5 | -1.0096
1106 | 50.5 | -1.0096
1106.1 | 50.5 | -1.0096
1106.2 | 50.5 | -1.0096
1106.3 | 50.5 | -1.0096
1106.4 | 50.5 | -1.0096
1106.5 | 50.5 | -1.0096
1106.6 | 50.5 | -1.0096
1106.7 | 50.5 | -1.0096
1106.8 | 50.5 | -1.0096
1106.9 | 50.5 | -1.0096
1107 | 50.5 | -1.0096
1107.1 | 50.5 | -1.0096
1107.2 | 50.5 | -1.0096
1107.3 | 50.5 | -1.0096
1107.4 | 50.5 | -1.0096
1107.5 | 50.5 | -1.0096
1107.6 | 50.5 | -1.0096
1107.7 | 50.5 | -1.0096
1107.8 | 50.5 | -1.0096
1107.9 | 50.5 | -1.0096
1108 | 50.5 | -1.0096
1108.1 | 50.5 | -1.0096
1108.2 | 50.5 | -1.0096
1108.3 | 50.5 | -1.0096
1108.4 | 50.5 | -1.0096
1108.5 | 50.5 | -1.0096
1108.6 | 50.5 | -1.0096
1108.7 | 50.5 | -1.0096
1108.8 | 50.5 | -1.0096
1108.9 | 50.5 | -1.0096
1109 | 50.5 | -1.0096
1109.1 | 50.5 | -1.0096
1109.2 | 50.5 | -1.0096
1109.3 | 50.5 | -1.0096
1109.4 | 50.5 | -1.0096
1109.5 | 50.5 | -1.0096
1109.6 | 50.5 | -1.0096
1109.7 | 50.5 | -1.0096
1109.8 | 50.5 | -1.0096
1109.9 | 50.5 | -1.0096
1110 | 50.5 | -1.0096
1110.1 | 50.5 | -1.0096
1110.2 | 50.5 | -1.0096
1110.3 | 50.5 | -1.0096
1110.4 | 50.5 | -1.0096
1110.5 | 50.5 | -1.0096
1110.6 | 50.5 | -1.0096
1110.7 | 50.5 | -1.0096
1110.8 | 50.5 | -1.0096
1110.9 | 50.5 | -1.0096
1111 | 50.5 | -1.0096
1111.1 | 50.5 | -1.0096
1111.2 | 50.5 | -1.0096
1111.3 | 50.5 | -1.0096
1111.4 | 50.5 | -1.0096
1111.5 | 50.5 | -1.0096
1111.6 | 50.5 | -1.0096
1111.7 | 50.5 | -1.0096
1111.8 | 50.5 | -1.0096
1111.9 | 50.5 | -1.0096
1112 | 50.5 | -1.0096
1112.1 | 50.5 | -1.0096
1112.2 | 50.5 | -1.0096
1112.3 | 50.5 | -1.0096
1112.4 | 50.5 | -1.0096
1112.5 | 50.5 | -1.0096
1112.6 | 50.5 | -1.0096
1112.7 | 50.5 | -1.0096
1112.8 | 50.5 | -1.0096
1112.9 | 50.5 | -1.0096
1113 | 50.5 | -1.0096
1113.1 | 50.5 | -1.0096
1113.2 | 50.5 | -1.0096
1113.3 | 50.5 | -1.0096
1113.4 | 50.5 | -1.0096
1113.5 | 50.5 | -1.0096
1113.6 | 50.5 | -1.0096
1113.7 | 50.5 | -1.0096
1113.8 | 50.5 | -1.0096
1113.9 | 50.5 | -1.0096
1114 | 50.5 | -1.0096
1114.1 | 50.5 | -1.0096
1114.2 | 50.5 | -1.0096
1114.3 | 50.5 | -1.0096
1114.4 | 50.5 | -1.0096
1114.5 | 50.5 | -1.0096
1114.6 | 50.5 | -1.0096
1114.7 | 50.5 | -1.0096
1114.8 | 50.5 | -1.0096
1114.9 | 50.5 | -1.0096
1115 | 50.5 | -1.0096
1115.1 | 50.5 | -1.0096
1115.2 | 50.5 | -1.0096
1115.3 | 50.5 | -1.0096
1115.4 | 50.5 | -1.0096
1115.5 | 50.5 | -1.0096
1115.6 | 50.5 | -1.0096
1115.7 | 50.5 | -1.0096
1115.8 | 50.5 | -1.0096
1115.9 | 50.5 | -1.0096
1116 | 50.5 | -1.0096
1116.1 | 50.5 | -1.0096
1116.2 | 50.5 | -1.0096
1116.3 | 50.5 | -1.0096
1116.4 | 50.5 | -1.0096
1116.5 | 50.5 | -1.0096
1116.6 | 50.5 | -1.0096
1116.7 | 50.5 | -1.0096
1116.8 | 50.5 | -1.0096
1116.9 | 50.5 | -1.0096
1117 | 50.5 | -1.0096
1117.1 | 50.5 | -1.0096
1117.2 | 50.5 | -1.0096
1117.3 | 50.5 | -1.0096
1117.4 | 50.5 | -1.0096
1117.5 | 50.5 | -1.0096
1117.6 | 50.5 | -1.0096
1117.7 | 50.5 | -1.0096
1117.8 | 50.5 | -1.0096
1117.9 | 50.5 | -1.0096
1118 | 50.5 | -1.0096
1118.1 | 50.5 | -1.0096
1118.2 | 50.5 | -1.0096
1118.3 | 50.5 | -1.0096
1118.4 | 50.5 | -1.0096
1118.5 | 50.5 | -1.0096
1118.6 | 50.5 | -1.0096
1118.7 | 50.5 | -1.0096
1118.8 | 50.5 | -1.0096
1118.9 | 50.5 | -1.0096
1119 | 50.5 | -1.0096
1119.1 | 50.5 | -1.0096
1119.2 | 50.5 | -1.0096
1119.3 | 50.5 | -1.0096
1119.4 | 50.5 | -1.0096
1119.5 | 50.5 | -1.0096
1119.6 | 50.5 | -1.0096
1119.7 | 50.5 | -1.0096
1119.8 | 50.5 | -1.0096
1119.9 | 50.5 | -1.0096
1120 | 50.5 | -1.0096
1120.1 | 50.5 | -1.0096
1120.2 | 50.5 | -1.0096
1120.3 | 50.5 | -1.0096
1120.4 | 50.5 | -1.0096
1120.5 | 50.5 | -1.0096
1120.6 | 50.5 | -1.0096
1120.7 | 50.5 | -1.0096
1120.8 | 50.5 | -1.0096
1120.9 | 50.5 | -1.0096
1121 | 50.5 | -1.0096
1121.1 | 50.5 | -1.0096
1121.2 | 50.5 | -1.0096
1121.3 | 50.5 | -1.0096
1121.4 | 50.5 | -1.0096
1121.5 | 50.5 | -1.0096
1121.6 | 50.5 | -1.0096
1121.7 | 50.5 | -1.0096
1121.8 | 50.5 | -1.0094
1121.9 | 50.5 | -1.0094
1122 | 50.5 | -1.0094
1122.1 | 50.5 | -1.0094
1122.2 | 50.5 | -1.0094
1122.3 | 50.5 | -1.0094
1122.4 | 50.5 | -1.0094
1122.5 | 50.5 | -1.0094
1122.6 | 50.5 | -1.0094
1122.7 | 50.5 | -1.0094
1122.8 | 50.5 | -1.0094
1122.9 | 50.5 | -1.0094
1123 | 50.5 | -1.0096
1123.1 | 50.5 | -1.0096
1123.2 | 50.5 | -1.0096
1123.3 | 50.5 | -1.0096
1123.4 | 50.5 | -1.0096
1123.5 | 50.5 | -1.0096
1123.6 | 50.5 | -1.0096
1123.7 | 50.5 | -1.0096
1123.8 | 50.5 | -1.0096
1123.9 | 50.5 | -1.0096
1124 | 50.5 | -1.0096
1124.1 | 50.5 | -1.0096
1124.2 | 50.5 | -1.0096
1124.3 | 50.5 | -1.0096
1124.4 | 50.5 | -1.0096
1124.5 | 50.5 | -1.0096
1124.6 | 50.5 | -1.0096
1124.7 | 50.5 | -1.0096
1124.8 | 50.5 | -1.0096
1124.9 | 50.5 | -1.0096
1125 | 50.5 | -1.0096
1125.1 | 50.5 | -1.0096
1125.2 | 50.5 | -1.0096
1125.3 | 50.5 | -1.0096
1125.4 | 50.5 | -1.0096
1125.5 | 50.5 | -1.0096
1125.6 | 50.5 | -1.0096
1125.7 | 50.5 | -1.0096
1125.8 | 50.5 | -1.0096
1125.9 | 50.5 | -1.0096
1126 | 50.5 | -1.0096
1126.1 | 50.5 | -1.0096
1126.2 | 50.5 | -1.0096
1126.3 | 50.5 | -1.0096
1126.4 | 50.5 | -1.0096
1126.5 | 50.5 | -1.0096
1126.6 | 50.5 | -1.0096
1126.7 | 50.5 | -1.0096
1126.8 | 50.5 | -1.0096
1126.9 | 50.5 | -1.0096
1127 | 50.5 | -1.0096
1127.1 | 50.5 | -1.0096
1127.2 | 50.5 | -1.0096
1127.3 | 50.5 | -1.0096
1127.4 | 50.5 | -1.0096
1127.5 | 50.5 | -1.0096
1127.6 | 50.5 | -1.0094
1127.7 | 50.5 | -1.0094
1127.8 | 50.5 | -1.0094
1127.9 | 50.5 | -1.0094
1128 | 50.5 | -1.0094
1128.1 | 50.5 | -1.0094
1128.2 | 50.5 | -1.0094
1128.3 | 50.5 | -1.0094
1128.4 | 50.5 | -1.0094
1128.5 | 50.5 | -1.0094
1128.6 | 50.5 | -1.0094
1128.7 | 50.5 | -1.0094
1128.8 | 50.5 | -1.0096
1128.9 | 50.5 | -1.0096
1129 | 50.5 | -1.0096
1129.1 | 50.5 | -1.0096
1129.2 | 50.5 | -1.0096
1129.3 | 50.5 | -1.0096
1129.4 | 50.5 | -1.0096
1129.5 | 50.5 | -1.0096
1129.6 | 50.5 | -1.0096
1129.7 | 50.5 | -1.0096
1129.8 | 50.5 | -1.0096
1129.9 | 50.5 | -1.0096
1130 | 50.5 | -1.0096
1130.1 | 50.5 | -1.0096
1130.2 | 50.5 | -1.0096
1130.3 | 50.5 | -1.0096
1130.4 | 50.5 | -1.0096
1130.5 | 50.5 | -1.0096
1130.6 | 50.5 | -1.0096
1130.7 | 50.5 | -1.0096
1130.8 | 50.5 | -1.0096
1130.9 | 50.5 | -1.0096
1131 | 50.5 | -1.0096
1131.1 | 50.5 | -1.0096
1131.2 | 50.5 | -1.0096
1131.3 | 50.5 | -1.0096
1131.4 | 50.5 | -1.0096
1131.5 | 50.5 | -1.0096
1131.6 | 50.5 | -1.0096
1131.7 | 50.5 | -1.0096
1131.8 | 50.5 | -1.0096
1131.9 | 50.5 | -1.0096
1132 | 50.5 | -1.0096
1132.1 | 50.5 | -1.0096
1132.2 | 50.5 | -1.0096
1132.3 | 50.5 | -1.0096
1132.4 | 50.5 | -1.0096
1132.5 | 50.5 | -1.0096
1132.6 | 50.5 | -1.0096
1132.7 | 50.5 | -1.0096
1132.8 | 50.5 | -1.0096
1132.9 | 50.5 | -1.0096
1133 | 50.5 | -1.0096
1133.1 | 50.5 | -1.0096
1133.2 | 50.5 | -1.0096
1133.3 | 50.5 | -1.0096
1133.4 | 50.5 | -1.0096
1133.5 | 50.5 | -1.0096
1133.6 | 50.5 | -1.0094
1133.7 | 50.5 | -1.0094
1133.8 | 50.5 | -1.0094
1133.9 | 50.5 | -1.0094
1134 | 50.5 | -1.0094
1134.1 | 50.5 | -1.0094
1134.2 | 50.5 | -1.0094
1134.3 | 50.5 | -1.0094
1134.4 | 50.5 | -1.0094
1134.5 | 50.5 | -1.0094
1134.6 | 50.5 | -1.0096
1134.7 | 50.5 | -1.0096
1134.8 | 50.5 | -1.0096
1134.9 | 50.5 | -1.0096
1135 | 50.5 | -1.0096
1135.1 | 50.5 | -1.0096
1135.2 | 50.5 | -1.0096
1135.3 | 50.5 | -1.0096
1135.4 | 50.5 | -1.0096
1135.5 | 50.5 | -1.0096
1135.6 | 50.5 | -1.0096
1135.7 | 50.5 | -1.0096
1135.8 | 50.5 | -1.0096
1135.9 | 50.5 | -1.0096
1136 | 50.5 | -1.0096
1136.1 | 50.5 | -1.0096
1136.2 | 50.5 | -1.0096
1136.3 | 50.5 | -1.0096
1136.4 | 50.5 | -1.0096
1136.5 | 50.5 | -1.0096
1136.6 | 50.5 | -1.0096
1136.7 | 50.5 | -1.0096
1136.8 | 50.5 | -1.0096
1136.9 | 50.5 | -1.0096
1137 | 50.5 | -1.0096
1137.1 | 50.5 | -1.0096
1137.2 | 50.5 | -1.0096
1137.3 | 50.5 | -1.0098
1137.4 | 50.5 | -1.0098
1137.5 | 50.5 | -1.0098
1137.6 | 50.5 | -1.0098
1137.7 | 50.5 | -1.0098
1137.8 | 50.5 | -1.0098
1137.9 | 50.5 | -1.0098
1138 | 50.5 | -1.0098
1138.1 | 50.5 | -1.0096
1138.2 | 50.5 | -1.0096
1138.3 | 50.5 | -1.0096
1138.4 | 50.5 | -1.0096
1138.5 | 50.5 | -1.0096
1138.6 | 50.5 | -1.0096
1138.7 | 50.5 | -1.0096
1138.8 | 50.5 | -1.0096
1138.9 | 50.5 | -1.0096
1139 | 50.5 | -1.0096
1139.1 | 50.5 | -1.0096
1139.2 | 50.5 | -1.0096
1139.3 | 50.5 | -1.0094
1139.4 | 50.5 | -1.0094
1139.5 | 50.5 | -1.0094
1139.6 | 50.5 | -1.0094
1139.7 | 50.5 | -1.0094
1139.8 | 50.5 | -1.0094
1139.9 | 50.5 | -1.0094
1140 | 50.5 | -1.0094
1140.1 | 50.5 | -1.0094
1140.2 | 50.5 | -1.0094
1140.3 | 50.5 | -1.0094
1140.4 | 50.5 | -1.0094
1140.5 | 50.5 | -1.0094
1140.6 | 50.5 | -1.0094
1140.7 | 50.5 | -1.0094
1140.8 | 50.5 | -1.0096
1140.9 | 50.5 | -1.0096
1141 | 50.5 | -1.0096
1141.1 | 50.5 | -1.0096
1141.2 | 50.5 | -1.0096
1141.3 | 50.5 | -1.0096
1141.4 | 50.5 | -1.0096
1141.5 | 50.5 | -1.0096
1141.6 | 50.5 | -1.0096
1141.7 | 50.5 | -1.0096
1141.8 | 50.5 | -1.0096
1141.9 | 50.5 | -1.0096
1142 | 50.5 | -1.0096
1142.1 | 50.5 | -1.0096
1142.2 | 50.5 | -1.0096
1142.3 | 50.5 | -1.0096
1142.4 | 50.5 | -1.0096
1142.5 | 50.5 | -1.0096
1142.6 | 50.5 | -1.0096
1142.7 | 50.5 | -1.0096
1142.8 | 50.5 | -1.0096
1142.9 | 50.5 | -1.0096
1143 | 50.5 | -1.0096
1143.1 | 50.5 | -1.0096
1143.2 | 50.5 | -1.0096
1143.3 | 50.5 | -1.0096
1143.4 | 50.5 | -1.0096
1143.5 | 50.5 | -1.0096
1143.6 | 50.5 | -1.0096
1143.7 | 50.5 | -1.0096
1143.8 | 50.5 | -1.0096
1143.9 | 50.5 | -1.0096
1144 | 50.5 | -1.0096
1144.1 | 50.5 | -1.0096
1144.2 | 50.5 | -1.0096
1144.3 | 50.5 | -1.0096
1144.4 | 50.5 | -1.0096
1144.5 | 50.5 | -1.0096
1144.6 | 50.5 | -1.0096
1144.7 | 50.5 | -1.0096
1144.8 | 50.5 | -1.0096
1144.9 | 50.5 | -1.0096
1145 | 50.5 | -1.0096
1145.1 | 50.5 | -1.0096
1145.2 | 50.5 | -1.0096
1145.3 | 50.5 | -1.0096
1145.4 | 50.5 | -1.0096
1145.5 | 50.5 | -1.0096
1145.6 | 50.5 | -1.0096
1145.7 | 50.5 | -1.0096
1145.8 | 50.5 | -1.0096
1145.9 | 50.5 | -1.0096
1146 | 50.5 | -1.0096
1146.1 | 50.5 | -1.0096
1146.2 | 50.5 | -1.0096
1146.3 | 50.5 | -1.0096
1146.4 | 50.5 | -1.0096
1146.5 | 50.5 | -1.0096
1146.6 | 50.5 | -1.0094
1146.7 | 50.5 | -1.0094
1146.8 | 50.5 | -1.0094
1146.9 | 50.5 | -1.0094
1147 | 50.5 | -1.0094
1147.1 | 50.5 | -1.0094
1147.2 | 50.5 | -1.0094
1147.3 | 50.5 | -1.0094
1147.4 | 50.5 | -1.0094
1147.5 | 50.5 | -1.0094
1147.6 | 50.5 | -1.0094
1147.7 | 50.5 | -1.0094
1147.8 | 50.5 | -1.0096
1147.9 | 50.5 | -1.0096
1148 | 50.5 | -1.0096
1148.1 | 50.5 | -1.0096
1148.2 | 50.5 | -1.0096
1148.3 | 50.5 | -1.0096
1148.4 | 50.5 | -1.0096
1148.5 | 50.5 | -1.0096
1148.6 | 50.5 | -1.0096
1148.7 | 50.5 | -1.0096
1148.8 | 50.5 | -1.0096
1148.9 | 50.5 | -1.0096
1149 | 50.5 | -1.0096
1149.1 | 50.5 | -1.0096
1149.2 | 50.5 | -1.0096
1149.3 | 50.5 | -1.0096
1149.4 | 50.5 | -1.0096
1149.5 | 50.5 | -1.0096
1149.6 | 50.5 | -1.0096
1149.7 | 50.5 | -1.0096
1149.8 | 50.5 | -1.0096
1149.9 | 50.5 | -1.0096
1150 | 50.5 | -1.0096
1150.1 | 50.5 | -1.0096
1150.2 | 50.5 | -1.0096
1150.3 | 50.5 | -1.0096
1150.4 | 50.5 | -1.0096
1150.5 | 50.5 | -1.0096
1150.6 | 50.5 | -1.0096
1150.7 | 50.5 | -1.0096
1150.8 | 50.5 | -1.0096
1150.9 | 50.5 | -1.0096
1151 | 50.5 | -1.0096
1151.1 | 50.5 | -1.0096
1151.2 | 50.5 | -1.0096
1151.3 | 50.5 | -1.0096
1151.4 | 50.5 | -1.0096
1151.5 | 50.5 | -1.0096
1151.6 | 50.5 | -1.0096
1151.7 | 50.5 | -1.0096
1151.8 | 50.5 | -1.0096
1151.9 | 50.5 | -1.0096
1152 | 50.5 | -1.0096
1152.1 | 50.5 | -1.0096
1152.2 | 50.5 | -1.0096
1152.3 | 50.5 | -1.0096
1152.4 | 50.5 | -1.0096
1152.5 | 50.5 | -1.0096
1152.6 | 50.5 | -1.0094
1152.7 | 50.5 | -1.0094
1152.8 | 50.5 | -1.0094
1152.9 | 50.5 | -1.0094
1153 | 50.5 | -1.0094
1153.1 | 50.5 | -1.0094
1153.2 | 50.5 | -1.0094
1153.3 | 50.5 | -1.0094
1153.4 | 50.5 | -1.0094
1153.5 | 50.5 | -1.0094
1153.6 | 50.5 | -1.0094
1153.7 | 50.5 | -1.0096
1153.8 | 50.5 | -1.0096
1153.9 | 50.5 | -1.0096
1154 | 50.5 | -1.0096
1154.1 | 50.5 | -1.0096
1154.2 | 50.5 | -1.0096
1154.3 | 50.5 | -1.0096
1154.4 | 50.5 | -1.0096
1154.5 | 50.5 | -1.0096
1154.6 | 50.5 | -1.0096
1154.7 | 50.5 | -1.0096
1154.8 | 50.5 | -1.0096
1154.9 | 50.5 | -1.0096
1155 | 50.5 | -1.0096
1155.1 | 50.5 | -1.0096
1155.2 | 50.5 | -1.0096
1155.3 | 50.5 | -1.0096
1155.4 | 50.5 | -1.0096
1155.5 | 50.5 | -1.0096
1155.6 | 50.5 | -1.0096
1155.7 | 50.5 | -1.0096
1155.8 | 50.5 | -1.0096
1155.9 | 50.5 | -1.0096
1156 | 50.5 | -1.0096
1156.1 | 50.5 | -1.0096
1156.2 | 50.5 | -1.0096
1156.3 | 50.5 | -1.0096
1156.4 | 50.5 | -1.0096
1156.5 | 50.5 | -1.0096
1156.6 | 50.5 | -1.0096
1156.7 | 50.5 | -1.0096
1156.8 | 50.5 | -1.0096
1156.9 | 50.5 | -1.0096
1157 | 50.5 | -1.0096
1157.1 | 50.5 | -1.0096
1157.2 | 50.5 | -1.0096
1157.3 | 50.5 | -1.0096
1157.4 | 50.5 | -1.0096
1157.5 | 50.5 | -1.0096
1157.6 | 50.5 | -1.0096
1157.7 | 50.5 | -1.0096
1157.8 | 50.5 | -1.0096
1157.9 | 50.5 | -1.0096
1158 | 50.5 | -1.0096
1158.1 | 50.5 | -1.0096
1158.2 | 50.5 | -1.0096
1158.3 | 50.5 | -1.0096
1158.4 | 50.5 | -1.0094
1158.5 | 50.5 | -1.0094
1158.6 | 50.5 | -1.0094
1158.7 | 50.5 | -1.0094
1158.8 | 50.5 | -1.0094
1158.9 | 50.5 | -1.0094
1159 | 50.5 | -1.0094
1159.1 | 50.5 | -1.0094
1159.2 | 50.5 | -1.0094
1159.3 | 50.5 | -1.0094
1159.4 | 50.5 | -1.0096
1159.5 | 50.5 | -1.0096
1159.6 | 50.5 | -1.0096
1159.7 | 50.5 | -1.0096
1159.8 | 50.5 | -1.0096
1159.9 | 50.5 | -1.0096
1160 | 50.5 | -1.0096
1160.1 | 50.5 | -1.0096
1160.2 | 50.5 | -1.0096
1160.3 | 50.5 | -1.0096
1160.4 | 50.5 | -1.0096
1160.5 | 50.5 | -1.0096
1160.6 | 50.5 | -1.0096
1160.7 | 50.5 | -1.0096
1160.8 | 50.5 | -1.0096
1160.9 | 50.5 | -1.0096
1161 | 50.5 | -1.0096
1161.1 | 50.5 | -1.0096
1161.2 | 50.5 | -1.0096
1161.3 | 50.5 | -1.0096
1161.4 | 50.5 | -1.0096
1161.5 | 50.5 | -1.0096
1161.6 | 50.5 | -1.0096
1161.7 | 50.5 | -1.0096
1161.8 | 50.5 | -1.0096
1161.9 | 50.5 | -1.0096
1162 | 50.5 | -1.0096
1162.1 | 50.5 | -1.0096
1162.2 | 50.5 | -1.0096
1162.3 | 50.5 | -1.0096
1162.4 | 50.5 | -1.0096
1162.5 | 50.5 | -1.0096
1162.6 | 50.5 | -1.0096
1162.7 | 50.5 | -1.0096
1162.8 | 50.5 | -1.0096
1162.9 | 50.5 | -1.0096
1163 | 50.5 | -1.0096
1163.1 | 50.5 | -1.0096
1163.2 | 50.5 | -1.0096
1163.3 | 50.5 | -1.0096
1163.4 | 50.5 | -1.0096
1163.5 | 50.5 | -1.0096
1163.6 | 50.5 | -1.0096
1163.7 | 50.5 | -1.0096
1163.8 | 50.5 | -1.0096
1163.9 | 50.5 | -1.0096
1164 | 50.5 | -1.0096
1164.1 | 50.5 | -1.0096
1164.2 | 50.5 | -1.0096
1164.3 | 50.5 | -1.0096
1164.4 | 50.5 | -1.0096
1164.5 | 50.5 | -1.0096
1164.6 | 50.5 | -1.0096
1164.7 | 50.5 | -1.0096
1164.8 | 50.5 | -1.0096
1164.9 | 50.5 | -1.0096
1165 | 50.5 | -1.0096
1165.1 | 50.5 | -1.0096
1165.2 | 50.5 | -1.0096
1165.3 | 50.5 | -1.0096
1165.4 | 50.5 | -1.0096
1165.5 | 50.5 | -1.0096
1165.6 | 50.5 | -1.0096
1165.7 | 50.5 | -1.0096
1165.8 | 50.5 | -1.0096
1165.9 | 50.5 | -1.0096
1166 | 50.5 | -1.0096
1166.1 | 50.5 | -1.0096
1166.2 | 50.5 | -1.0096
1166.3 | 50.5 | -1.0096
1166.4 | 50.5 | -1.0096
1166.5 | 50.5 | -1.0096
1166.6 | 50.5 | -1.0096
1166.7 | 50.5 | -1.0096
1166.8 | 50.5 | -1.0096
1166.9 | 50.5 | -1.0096
1167 | 50.5 | -1.0096
1167.1 | 50.5 | -1.0096
1167.2 | 50.5 | -1.0096
1167.3 | 50.5 | -1.0096
1167.4 | 50.5 | -1.0096
1167.5 | 50.5 | -1.0096
1167.6 | 50.5 | -1.0096
1167.7 | 50.5 | -1.0096
1167.8 | 50.5 | -1.0096
1167.9 | 50.5 | -1.0096
1168 | 50.5 | -1.0096
1168.1 | 50.5 | -1.0096
1168.2 | 50.5 | -1.0096
1168.3 | 50.5 | -1.0096
1168.4 | 50.5 | -1.0096
1168.5 | 50.5 | -1.0096
1168.6 | 50.5 | -1.0096
1168.7 | 50.5 | -1.0096
1168.8 | 50.5 | -1.0096
1168.9 | 50.5 | -1.0096
1169 | 50.5 | -1.0096
1169.1 | 50.5 | -1.0096
1169.2 | 50.5 | -1.0096
1169.3 | 50.5 | -1.0096
1169.4 | 50.5 | -1.0096
1169.5 | 50.5 | -1.0096
1169.6 | 50.5 | -1.0096
1169.7 | 50.5 | -1.0094
1169.8 | 50.5 | -1.0094
1169.9 | 50.5 | -1.0094
1170 | 50.5 | -1.0094
1170.1 | 50.5 | -1.0094
1170.2 | 50.5 | -1.0094
1170.3 | 50.5 | -1.0094
1170.4 | 50.5 | -1.0094
1170.5 | 50.5 | -1.0094
1170.6 | 50.5 | -1.0094
1170.7 | 50.5 | -1.0094
1170.8 | 50.5 | -1.0094
1170.9 | 50.5 | -1.0094
1171 | 50.5 | -1.0096
1171.1 | 50.5 | -1.0096
1171.2 | 50.5 | -1.0096
1171.3 | 50.5 | -1.0096
1171.4 | 50.5 | -1.0096
1171.5 | 50.5 | -1.0096
1171.6 | 50.5 | -1.0096
1171.7 | 50.5 | -1.0096
1171.8 | 50.5 | -1.0096
1171.9 | 50.5 | -1.0096
1172 | 50.5 | -1.0096
1172.1 | 50.5 | -1.0096
1172.2 | 50.5 | -1.0096
1172.3 | 50.5 | -1.0096
1172.4 | 50.5 | -1.0096
1172.5 | 50.5 | -1.0096
1172.6 | 50.5 | -1.0096
1172.7 | 50.5 | -1.0096
1172.8 | 50.5 | -1.0096
1172.9 | 50.5 | -1.0096
1173 | 50.5 | -1.0096
1173.1 | 50.5 | -1.0096
1173.2 | 50.5 | -1.0096
1173.3 | 50.5 | -1.0094
1173.4 | 50.5 | -1.0094
1173.5 | 50.5 | -1.0096
1173.6 | 50.5 | -1.0096
1173.7 | 50.5 | -1.0096
1173.8 | 50.5 | -1.0096
1173.9 | 50.5 | -1.0096
1174 | 50.5 | -1.0096
1174.1 | 50.5 | -1.0096
1174.2 | 50.5 | -1.0096
1174.3 | 50.5 | -1.0096
1174.4 | 50.5 | -1.0096
1174.5 | 50.5 | -1.0096
1174.6 | 50.5 | -1.0096
1174.7 | 50.5 | -1.0096
1174.8 | 50.5 | -1.0096
1174.9 | 50.5 | -1.0096
1175 | 50.5 | -1.0096
1175.1 | 50.5 | -1.0096
1175.2 | 50.5 | -1.0096
1175.3 | 50.5 | -1.0096
1175.4 | 50.5 | -1.0096
1175.5 | 50.5 | -1.0096
1175.6 | 50.5 | -1.0094
1175.7 | 50.5 | -1.0094
1175.8 | 50.5 | -1.0094
1175.9 | 50.5 | -1.0094
1176 | 50.5 | -1.0094
1176.1 | 50.5 | -1.0094
1176.2 | 50.5 | -1.0094
1176.3 | 50.5 | -1.0094
1176.4 | 50.5 | -1.0094
1176.5 | 50.5 | -1.0094
1176.6 | 50.5 | -1.0094
1176.7 | 50.5 | -1.0094
1176.8 | 50.5 | -1.0094
1176.9 | 50.5 | -1.0094
1177 | 50.5 | -1.0094
1177.1 | 50.5 | -1.0094
1177.2 | 50.5 | -1.0094
1177.3 | 50.5 | -1.0094
1177.4 | 50.5 | -1.0094
1177.5 | 50.5 | -1.0094
1177.6 | 50.5 | -1.0094
1177.7 | 50.5 | -1.0094
1177.8 | 50.5 | -1.0094
1177.9 | 50.5 | -1.0094
1178 | 50.5 | -1.0094
1178.1 | 50.5 | -1.0094
1178.2 | 50.5 | -1.0096
1178.3 | 50.5 | -1.0096
1178.4 | 50.5 | -1.0096
1178.5 | 50.5 | -1.0096
1178.6 | 50.5 | -1.0096
1178.7 | 50.5 | -1.0096
1178.8 | 50.5 | -1.0096
1178.9 | 50.5 | -1.0096
1179 | 50.5 | -1.0096
1179.1 | 50.5 | -1.0096
1179.2 | 50.5 | -1.0096
1179.3 | 50.5 | -1.0096
1179.4 | 50.5 | -1.0096
1179.5 | 50.5 | -1.0096
1179.6 | 50.5 | -1.0096
1179.7 | 50.5 | -1.0096
1179.8 | 50.5 | -1.0096
1179.9 | 50.5 | -1.0096
1180 | 50.5 | -1.0096
1180.1 | 50.5 | -1.0096
1180.2 | 50.5 | -1.0096
1180.3 | 50.5 | -1.0096
1180.4 | 50.5 | -1.0096
1180.5 | 50.5 | -1.0096
1180.6 | 50.5 | -1.0096
1180.7 | 50.5 | -1.0096
1180.8 | 50.5 | -1.0096
1180.9 | 50.5 | -1.0096
1181 | 50.5 | -1.0096
1181.1 | 50.5 | -1.0096
1181.2 | 50.5 | -1.0096
1181.3 | 50.5 | -1.0096
1181.4 | 50.5 | -1.0096
1181.5 | 50.5 | -1.0096
1181.6 | 50.5 | -1.0094
1181.7 | 50.5 | -1.0094
1181.8 | 50.5 | -1.0094
1181.9 | 50.5 | -1.0094
1182 | 50.5 | -1.0094
1182.1 | 50.5 | -1.0094
1182.2 | 50.5 | -1.0094
1182.3 | 50.5 | -1.0094
1182.4 | 50.5 | -1.0094
1182.5 | 50.5 | -1.0094
1182.6 | 50.5 | -1.0096
1182.7 | 50.5 | -1.0096
1182.8 | 50.5 | -1.0096
1182.9 | 50.5 | -1.0096
1183 | 50.5 | -1.0096
1183.1 | 50.5 | -1.0096
1183.2 | 50.5 | -1.0096
1183.3 | 50.5 | -1.0096
1183.4 | 50.5 | -1.0096
1183.5 | 50.5 | -1.0096
1183.6 | 50.5 | -1.0096
1183.7 | 50.5 | -1.0096
1183.8 | 50.5 | -1.0096
1183.9 | 50.5 | -1.0096
1184 | 50.5 | -1.0096
1184.1 | 50.5 | -1.0094
1184.2 | 50.5 | -1.0094
1184.3 | 50.5 | -1.0094
1184.4 | 50.5 | -1.0094
1184.5 | 50.5 | -1.0094
1184.6 | 50.5 | -1.0094
1184.7 | 50.5 | -1.0094
1184.8 | 50.5 | -1.0094
1184.9 | 50.5 | -1.0096
1185 | 50.5 | -1.0096
1185.1 | 50.5 | -1.0096
1185.2 | 50.5 | -1.0096
1185.3 | 50.5 | -1.0096
1185.4 | 50.5 | -1.0096
1185.5 | 50.5 | -1.0096
1185.6 | 50.5 | -1.0096
1185.7 | 50.5 | -1.0096
1185.8 | 50.5 | -1.0096
1185.9 | 50.5 | -1.0096
1186 | 50.5 | -1.0096
1186.1 | 50.5 | -1.0094
1186.2 | 50.5 | -1.0094
1186.3 | 50.5 | -1.0094
1186.4 | 50.5 | -1.0096
1186.5 | 50.5 | -1.0096
1186.6 | 50.5 | -1.0096
1186.7 | 50.5 | -1.0096
1186.8 | 50.5 | -1.0096
1186.9 | 50.5 | -1.0096
1187 | 50.5 | -1.0096
1187.1 | 50.5 | -1.0096
1187.2 | 50.5 | -1.0096
1187.3 | 50.5 | -1.0094
1187.4 | 50.5 | -1.0094
1187.5 | 50.5 | -1.0094
1187.6 | 50.5 | -1.0094
1187.7 | 50.5 | -1.0094
1187.8 | 50.5 | -1.0094
1187.9 | 50.5 | -1.0094
1188 | 50.5 | -1.0094
1188.1 | 50.5 | -1.0094
1188.2 | 50.5 | -1.0094
1188.3 | 50.5 | -1.0094
1188.4 | 50.5 | -1.0094
1188.5 | 50.5 | -1.0096
1188.6 | 50.5 | -1.0096
1188.7 | 50.5 | -1.0096
1188.8 | 50.5 | -1.0096
1188.9 | 50.5 | -1.0096
1189 | 50.5 | -1.0096
1189.1 | 50.5 | -1.0096
1189.2 | 50.5 | -1.0096
1189.3 | 50.5 | -1.0096
1189.4 | 50.5 | -1.0096
1189.5 | 50.5 | -1.0096
1189.6 | 50.5 | -1.0096
1189.7 | 50.5 | -1.0096
1189.8 | 50.5 | -1.0096
1189.9 | 50.5 | -1.0096
1190 | 50.5 | -1.0096
1190.1 | 50.5 | -1.0096
1190.2 | 50.5 | -1.0096
1190.3 | 50.5 | -1.0096
1190.4 | 50.5 | -1.0096
1190.5 | 50.5 | -1.0096
1190.6 | 50.5 | -1.0096
1190.7 | 50.5 | -1.0096
1190.8 | 50.5 | -1.0096
1190.9 | 50.5 | -1.0096
1191 | 50.5 | -1.0096
1191.1 | 50.5 | -1.0096
1191.2 | 50.5 | -1.0096
1191.3 | 50.5 | -1.0096
1191.4 | 50.5 | -1.0096
1191.5 | 50.5 | -1.0096
1191.6 | 50.5 | -1.0096
1191.7 | 50.5 | -1.0096
1191.8 | 50.5 | -1.0096
1191.9 | 50.5 | -1.0096
1192 | 50.5 | -1.0096
1192.1 | 50.5 | -1.0096
1192.2 | 50.5 | -1.0096
1192.3 | 50.5 | -1.0096
1192.4 | 50.5 | -1.0096
1192.5 | 50.5 | -1.0096
1192.6 | 50.5 | -1.0096
1192.7 | 50.5 | -1.0096
1192.8 | 50.5 | -1.0096
1192.9 | 50.5 | -1.0096
1193 | 50.5 | -1.0096
1193.1 | 50.5 | -1.0096
1193.2 | 50.5 | -1.0094
1193.3 | 50.5 | -1.0094
1193.4 | 50.5 | -1.0094
1193.5 | 50.5 | -1.0094
1193.6 | 50.5 | -1.0094
1193.7 | 50.5 | -1.0094
1193.8 | 50.5 | -1.0094
1193.9 | 50.5 | -1.0094
1194 | 50.5 | -1.0096
1194.1 | 50.5 | -1.0096
1194.2 | 50.5 | -1.0096
1194.3 | 50.5 | -1.0096
1194.4 | 50.5 | -1.0096
1194.5 | 50.5 | -1.0096
1194.6 | 50.5 | -1.0096
1194.7 | 50.5 | -1.0096
1194.8 | 50.5 | -1.0096
1194.9 | 50.5 | -1.0096
1195 | 50.5 | -1.0096
1195.1 | 50.5 | -1.0096
1195.2 | 50.5 | -1.0096
1195.3 | 50.5 | -1.0096
1195.4 | 50.5 | -1.0096
1195.5 | 50.5 | -1.0096
1195.6 | 50.5 | -1.0096
1195.7 | 50.5 | -1.0096
1195.8 | 50.5 | -1.0096
1195.9 | 50.5 | -1.0096
1196 | 50.5 | -1.0096
1196.1 | 50.5 | -1.0096
1196.2 | 50.5 | -1.0096
1196.3 | 50.5 | -1.0096
1196.4 | 50.5 | -1.0096
1196.5 | 50.5 | -1.0096
1196.6 | 50.5 | -1.0096
1196.7 | 50.5 | -1.0096
1196.8 | 50.5 | -1.0096
1196.9 | 50.5 | -1.0096
1197 | 50.5 | -1.0096
1197.1 | 50.5 | -1.0096
1197.2 | 50.5 | -1.0096
1197.3 | 50.5 | -1.0096
1197.4 | 50.5 | -1.0096
1197.5 | 50.5 | -1.0096
1197.6 | 50.5 | -1.0096
1197.7 | 50.5 | -1.0096
1197.8 | 50.5 | -1.0096
1197.9 | 50.5 | -1.0094
1198 | 50.5 | -1.0094
1198.1 | 50.5 | -1.0094
1198.2 | 50.5 | -1.0094
1198.3 | 50.5 | -1.0094
1198.4 | 50.5 | -1.0094
1198.5 | 50.5 | -1.0094
1198.6 | 50.5 | -1.0094
1198.7 | 50.5 | -1.0094
1198.8 | 50.5 | -1.0094
1198.9 | 50.5 | -1.0094
1199 | 50.5 | -1.0094
1199.1 | 50.5 | -1.0094
1199.2 | 50.5 | -1.0096
1199.3 | 50.5 | -1.0096
1199.4 | 50.5 | -1.0096
1199.5 | 50.5 | -1.0096
1199.6 | 50.5 | -1.0096
1199.7 | 50.5 | -1.0096
1199.8 | 50.5 | -1.0096
1199.9 | 50.5 | -1.0096
1200 | 50.5 | -1.0096
1200.1 | 50.5 | -1.0096
1200.2 | 50.5 | -1.0096
1200.3 | 50.5 | -1.0096
1200.4 | 50.5 | -1.0096
1200.5 | 50.5 | -1.0096
1200.6 | 50.5 | -1.0096
1200.7 | 50.5 | -1.0096
1200.8 | 50.5 | -1.0096
1200.9 | 50.5 | -1.0096
1201 | 50.5 | -1.0096
1201.1 | 50.5 | -1.0096
1201.2 | 50.5 | -1.0096
1201.3 | 50.5 | -1.0096
1201.4 | 50.5 | -1.0096
1201.5 | 50.5 | -1.0096
1201.6 | 50.5 | -1.0096
1201.7 | 50.5 | -1.0096
1201.8 | 50.5 | -1.0096
1201.9 | 50.5 | -1.0096
1202 | 50.5 | -1.0098
1202.1 | 50.5 | -1.0098
1202.2 | 50.5 | -1.0098
1202.3 | 50.5 | -1.0098
1202.4 | 50.5 | -1.0098
1202.5 | 50.5 | -1.0098
1202.6 | 50.5 | -1.0098
1202.7 | 50.5 | -1.0098
1202.8 | 50.5 | -1.0098
1202.9 | 50.5 | -1.0098
1203 | 50.5 | -1.0098
1203.1 | 50.5 | -1.0098
1203.2 | 50.5 | -1.0098
1203.3 | 50.5 | -1.0098
1203.4 | 50.5 | -1.0098
1203.5 | 50.5 | -1.0098
1203.6 | 50.5 | -1.0098
1203.7 | 50.5 | -1.0096
1203.8 | 50.5 | -1.0096
1203.9 | 50.5 | -1.0096
1204 | 50.5 | -1.0096
1204.1 | 50.5 | -1.0096
1204.2 | 50.5 | -1.0096
1204.3 | 50.5 | -1.0096
1204.4 | 50.5 | -1.0094
1204.5 | 50.5 | -1.0094
1204.6 | 50.5 | -1.0094
1204.7 | 50.5 | -1.0094
1204.8 | 50.5 | -1.0092
1204.9 | 50.5 | -1.0092
1205 | 50.5 | -1.0092
1205.1 | 50.5 | -1.0094
1205.2 | 50.5 | -1.0094
1205.3 | 50.5 | -1.0094
1205.4 | 50.5 | -1.0094
1205.5 | 50.5 | -1.0094
1205.6 | 50.5 | -1.0094
1205.7 | 50.5 | -1.0094
1205.8 | 50.5 | -1.0094
1205.9 | 50.5 | -1.0094
1206 | 50.5 | -1.0094
1206.1 | 50.5 | -1.0094
1206.2 | 50.5 | -1.0094
1206.3 | 50.5 | -1.0094
1206.4 | 50.5 | -1.0094
1206.5 | 50.5 | -1.0094
1206.6 | 50.5 | -1.0094
1206.7 | 50.5 | -1.0094
1206.8 | 50.5 | -1.0096
1206.9 | 50.5 | -1.0096
1207 | 50.5 | -1.0096
1207.1 | 50.5 | -1.0096
1207.2 | 50.5 | -1.0096
1207.3 | 50.5 | -1.0096
1207.4 | 50.5 | -1.0096
1207.5 | 50.5 | -1.0096
1207.6 | 50.5 | -1.0096
1207.7 | 50.5 | -1.0096
1207.8 | 50.5 | -1.0096
1207.9 | 50.5 | -1.0096
1208 | 50.5 | -1.0096
1208.1 | 50.5 | -1.0096
1208.2 | 50.5 | -1.0096
1208.3 | 50.5 | -1.0096
1208.4 | 50.5 | -1.0096
1208.5 | 50.5 | -1.0096
1208.6 | 50.5 | -1.0096
1208.7 | 50.5 | -1.0096
1208.8 | 50.5 | -1.0096
1208.9 | 50.5 | -1.0096
1209 | 50.5 | -1.0096
1209.1 | 50.5 | -1.0096
1209.2 | 50.5 | -1.0096
1209.3 | 50.5 | -1.0096
1209.4 | 50.5 | -1.0096
1209.5 | 50.5 | -1.0096
1209.6 | 50.5 | -1.0096
1209.7 | 50.5 | -1.0096
1209.8 | 50.5 | -1.0096
1209.9 | 50.5 | -1.0096
1210 | 50.5 | -1.0096
1210.1 | 50.5 | -1.0096
1210.2 | 50.5 | -1.0096
1210.3 | 50.5 | -1.0096
1210.4 | 50.5 | -1.0096
1210.5 | 50.5 | -1.0096
1210.6 | 50.5 | -1.0096
1210.7 | 50.5 | -1.0094
1210.8 | 50.5 | -1.0094
1210.9 | 50.5 | -1.0094
1211 | 50.5 | -1.0094
1211.1 | 50.5 | -1.0094
1211.2 | 50.5 | -1.0094
1211.3 | 50.5 | -1.0094
1211.4 | 50.5 | -1.0094
1211.5 | 50.5 | -1.0094
1211.6 | 50.5 | -1.0094
1211.7 | 50.5 | -1.0094
1211.8 | 50.5 | -1.0094
1211.9 | 50.5 | -1.0094
1212 | 50.5 | -1.0094
1212.1 | 50.5 | -1.0094
1212.2 | 50.5 | -1.0094
1212.3 | 50.5 | -1.0094
1212.4 | 50.5 | -1.0094
1212.5 | 50.5 | -1.0094
1212.6 | 50.5 | -1.0094
1212.7 | 50.5 | -1.0094
1212.8 | 50.5 | -1.0094
1212.9 | 50.5 | -1.0094
1213 | 50.5 | -1.0096
1213.1 | 50.5 | -1.0096
1213.2 | 50.5 | -1.0096
1213.3 | 50.5 | -1.0096
1213.4 | 50.5 | -1.0096
1213.5 | 50.5 | -1.0096
1213.6 | 50.5 | -1.0096
1213.7 | 50.5 | -1.0096
1213.8 | 50.5 | -1.0094
1213.9 | 50.5 | -1.0094
1214 | 50.5 | -1.0094
1214.1 | 50.5 | -1.0094
1214.2 | 50.5 | -1.0094
1214.3 | 50.5 | -1.0094
1214.4 | 50.5 | -1.0094
1214.5 | 50.5 | -1.0094
1214.6 | 50.5 | -1.0094
1214.7 | 50.5 | -1.0094
1214.8 | 50.5 | -1.0096
1214.9 | 50.5 | -1.0096
1215 | 50.5 | -1.0096
1215.1 | 50.5 | -1.0096
1215.2 | 50.5 | -1.0096
1215.3 | 50.5 | -1.0096
1215.4 | 50.5 | -1.0096
1215.5 | 50.5 | -1.0096
1215.6 | 50.5 | -1.0096
1215.7 | 50.5 | -1.0096
1215.8 | 50.5 | -1.0096
1215.9 | 50.5 | -1.0096
1216 | 50.5 | -1.0096
1216.1 | 50.5 | -1.0096
1216.2 | 50.5 | -1.0096
1216.3 | 50.5 | -1.0096
1216.4 | 50.5 | -1.0096
1216.5 | 50.5 | -1.0096
1216.6 | 50.5 | -1.0096
1216.7 | 50.5 | -1.0096
1216.8 | 50.5 | -1.0096
1216.9 | 50.5 | -1.0096
1217 | 50.5 | -1.0096
1217.1 | 50.5 | -1.0096
1217.2 | 50.5 | -1.0096
1217.3 | 50.5 | -1.0096
1217.4 | 50.5 | -1.0096
1217.5 | 50.5 | -1.0096
1217.6 | 50.5 | -1.0096
1217.7 | 50.5 | -1.0096
1217.8 | 50.5 | -1.0096
1217.9 | 50.5 | -1.0096
1218 | 50.5 | -1.0096
1218.1 | 50.5 | -1.0096
1218.2 | 50.5 | -1.0096
1218.3 | 50.5 | -1.0096
1218.4 | 50.5 | -1.0096
1218.5 | 50.5 | -1.0096
1218.6 | 50.5 | -1.0096
1218.7 | 50.5 | -1.0096
1218.8 | 50.5 | -1.0096
1218.9 | 50.5 | -1.0096
1219 | 50.5 | -1.0096
1219.1 | 50.5 | -1.0096
1219.2 | 50.5 | -1.0096
1219.3 | 50.5 | -1.0096
1219.4 | 50.5 | -1.0096
1219.5 | 50.5 | -1.0096
1219.6 | 50.5 | -1.0096
1219.7 | 50.5 | -1.0096
1219.8 | 50.5 | -1.0096
1219.9 | 50.5 | -1.0096
1220 | 50.5 | -1.0096
1220.1 | 50.5 | -1.0096
1220.2 | 50.5 | -1.0096
1220.3 | 50.5 | -1.0096
1220.4 | 50.5 | -1.0096
1220.5 | 50.5 | -1.0096
1220.6 | 50.5 | -1.0096
1220.7 | 50.5 | -1.0096
1220.8 | 50.5 | -1.0096
1220.9 | 50.5 | -1.0096
1221 | 50.5 | -1.0096
1221.1 | 50.5 | -1.0096
1221.2 | 50.5 | -1.0096
1221.3 | 50.5 | -1.0096
1221.4 | 50.5 | -1.0096
1221.5 | 50.5 | -1.0096
1221.6 | 50.5 | -1.0096
1221.7 | 50.5 | -1.0096
1221.8 | 50.5 | -1.0096
1221.9 | 50.5 | -1.0096
1222 | 50.5 | -1.0096
1222.1 | 50.5 | -1.0096
1222.2 | 50.5 | -1.0096
1222.3 | 50.5 | -1.0096
1222.4 | 50.5 | -1.0096
1222.5 | 50.5 | -1.0096
1222.6 | 50.5 | -1.0096
1222.7 | 50.5 | -1.0096
1222.8 | 50.5 | -1.0096
1222.9 | 50.5 | -1.0096
1223 | 50.5 | -1.0096
1223.1 | 50.5 | -1.0096
1223.2 | 50.5 | -1.0096
1223.3 | 50.5 | -1.0096
1223.4 | 50.5 | -1.0096
1223.5 | 50.5 | -1.0096
1223.6 | 50.5 | -1.0096
1223.7 | 50.5 | -1.0096
1223.8 | 50.5 | -1.0096
1223.9 | 50.5 | -1.0096
1224 | 50.5 | -1.0096
1224.1 | 50.5 | -1.0096
1224.2 | 50.5 | -1.0096
1224.3 | 50.5 | -1.0096
1224.4 | 50.5 | -1.0096
1224.5 | 50.5 | -1.0096
1224.6 | 50.5 | -1.0096
1224.7 | 50.5 | -1.0096
1224.8 | 50.5 | -1.0096
1224.9 | 50.5 | -1.0096
1225 | 50.5 | -1.0096
1225.1 | 50.5 | -1.0096
1225.2 | 50.5 | -1.0096
1225.3 | 50.5 | -1.0096
1225.4 | 50.5 | -1.0096
1225.5 | 50.5 | -1.0096
1225.6 | 50.5 | -1.0096
1225.7 | 50.5 | -1.0096
1225.8 | 50.5 | -1.0096
1225.9 | 50.5 | -1.0094
1226 | 50.5 | -1.0094
1226.1 | 50.5 | -1.0094
1226.2 | 50.5 | -1.0094
1226.3 | 50.5 | -1.0094
1226.4 | 50.5 | -1.0094
1226.5 | 50.5 | -1.0094
1226.6 | 50.5 | -1.0094
1226.7 | 50.5 | -1.0094
1226.8 | 50.5 | -1.0094
1226.9 | 50.5 | -1.0094
1227 | 50.5 | -1.0094
1227.1 | 50.5 | -1.0096
1227.2 | 50.5 | -1.0096
1227.3 | 50.5 | -1.0096
1227.4 | 50.5 | -1.0096
1227.5 | 50.5 | -1.0096
1227.6 | 50.5 | -1.0096
1227.7 | 50.5 | -1.0096
1227.8 | 50.5 | -1.0096
1227.9 | 50.5 | -1.0096
1228 | 50.5 | -1.0096
1228.1 | 50.5 | -1.0096
1228.2 | 50.5 | -1.0096
1228.3 | 50.5 | -1.0096
1228.4 | 50.5 | -1.0096
1228.5 | 50.5 | -1.0096
1228.6 | 50.5 | -1.0096
1228.7 | 50.5 | -1.0096
1228.8 | 50.5 | -1.0096
1228.9 | 50.5 | -1.0096
1229 | 50.5 | -1.0096
1229.1 | 50.5 | -1.0096
1229.2 | 50.5 | -1.0096
1229.3 | 50.5 | -1.0096
1229.4 | 50.5 | -1.0096
1229.5 | 50.5 | -1.0096
1229.6 | 50.5 | -1.0096
1229.7 | 50.5 | -1.0096
1229.8 | 50.5 | -1.0096
1229.9 | 50.5 | -1.0096
1230 | 50.5 | -1.0096
1230.1 | 50.5 | -1.0096
1230.2 | 50.5 | -1.0096
1230.3 | 50.5 | -1.0096
1230.4 | 50.5 | -1.0096
1230.5 | 50.5 | -1.0096
1230.6 | 50.5 | -1.0096
1230.7 | 50.5 | -1.0096
1230.8 | 50.5 | -1.0096
1230.9 | 50.5 | -1.0096
1231 | 50.5 | -1.0096
1231.1 | 50.5 | -1.0096
1231.2 | 50.5 | -1.0096
1231.3 | 50.5 | -1.0096
1231.4 | 50.5 | -1.0096
1231.5 | 50.5 | -1.0096
1231.6 | 50.5 | -1.0096
1231.7 | 50.5 | -1.0096
1231.8 | 50.5 | -1.0094
1231.9 | 50.5 | -1.0094
1232 | 50.5 | -1.0094
1232.1 | 50.5 | -1.0094
1232.2 | 50.5 | -1.0094
1232.3 | 50.5 | -1.0094
1232.4 | 50.5 | -1.0094
1232.5 | 50.5 | -1.0094
1232.6 | 50.5 | -1.0094
1232.7 | 50.5 | -1.0094
1232.8 | 50.5 | -1.0094
1232.9 | 50.5 | -1.0094
1233 | 50.5 | -1.0094
1233.1 | 50.5 | -1.0094
1233.2 | 50.5 | -1.0094
1233.3 | 50.5 | -1.0094
1233.4 | 50.5 | -1.0094
1233.5 | 50.5 | -1.0094
1233.6 | 50.5 | -1.0094
1233.7 | 50.5 | -1.0094
1233.8 | 50.5 | -1.0094
1233.9 | 50.5 | -1.0094
1234 | 50.5 | -1.0094
1234.1 | 50.5 | -1.0096
1234.2 | 50.5 | -1.0096
1234.3 | 50.5 | -1.0096
1234.4 | 50.5 | -1.0096
1234.5 | 50.5 | -1.0096
1234.6 | 50.5 | -1.0096
1234.7 | 50.5 | -1.0096
1234.8 | 50.5 | -1.0096
1234.9 | 50.5 | -1.0096
1235 | 50.5 | -1.0096
1235.1 | 50.5 | -1.0096
1235.2 | 50.5 | -1.0096
1235.3 | 50.5 | -1.0096
1235.4 | 50.5 | -1.0096
1235.5 | 50.5 | -1.0096
1235.6 | 50.5 | -1.0096
1235.7 | 50.5 | -1.0096
1235.8 | 50.5 | -1.0096
1235.9 | 50.5 | -1.0096
1236 | 50.5 | -1.0096
1236.1 | 50.5 | -1.0096
1236.2 | 50.5 | -1.0096
1236.3 | 50.5 | -1.0096
1236.4 | 50.5 | -1.0096
1236.5 | 50.5 | -1.0096
1236.6 | 50.5 | -1.0096
1236.7 | 50.5 | -1.0096
1236.8 | 50.5 | -1.0096
1236.9 | 50.5 | -1.0096
1237 | 50.5 | -1.0096
1237.1 | 50.5 | -1.0096
1237.2 | 50.5 | -1.0096
1237.3 | 50.5 | -1.0096
1237.4 | 50.5 | -1.0096
1237.5 | 50.5 | -1.0096
1237.6 | 50.5 | -1.0096
1237.7 | 50.5 | -1.0096
1237.8 | 50.5 | -1.0096
1237.9 | 50.5 | -1.0096
1238 | 50.5 | -1.0096
1238.1 | 50.5 | -1.0096
1238.2 | 50.5 | -1.0096
1238.3 | 50.5 | -1.0096
1238.4 | 50.5 | -1.0096
1238.5 | 50.5 | -1.0096
1238.6 | 50.5 | -1.0096
1238.7 | 50.5 | -1.0094
1238.8 | 50.5 | -1.0094
1238.9 | 50.5 | -1.0094
1239 | 50.5 | -1.0094
1239.1 | 50.5 | -1.0094
1239.2 | 50.5 | -1.0094
1239.3 | 50.5 | -1.0094
1239.4 | 50.5 | -1.0094
1239.5 | 50.5 | -1.0094
1239.6 | 50.5 | -1.0094
1239.7 | 50.5 | -1.0094
1239.8 | 50.5 | -1.0094
1239.9 | 50.5 | -1.0094
1240 | 50.5 | -1.0094
1240.1 | 50.5 | -1.0094
1240.2 | 50.5 | -1.0094
1240.3 | 50.5 | -1.0094
1240.4 | 50.5 | -1.0094
1240.5 | 50.5 | -1.0094
1240.6 | 50.5 | -1.0094
1240.7 | 50.5 | -1.0094
1240.8 | 50.5 | -1.0094
1240.9 | 50.5 | -1.0094
1241 | 50.5 | -1.0094
1241.1 | 50.5 | -1.0096
1241.2 | 50.5 | -1.0096
1241.3 | 50.5 | -1.0096
1241.4 | 50.5 | -1.0096
1241.5 | 50.5 | -1.0096
1241.6 | 50.5 | -1.0096
1241.7 | 50.5 | -1.0096
1241.8 | 50.5 | -1.0096
1241.9 | 50.5 | -1.0096
1242 | 50.5 | -1.0096
1242.1 | 50.5 | -1.0096
1242.2 | 50.5 | -1.0096
1242.3 | 50.5 | -1.0096
1242.4 | 50.5 | -1.0096
1242.5 | 50.5 | -1.0096
1242.6 | 50.5 | -1.0096
1242.7 | 50.5 | -1.0096
1242.8 | 50.5 | -1.0096
1242.9 | 50.5 | -1.0096
1243 | 50.5 | -1.0096
1243.1 | 50.5 | -1.0096
1243.2 | 50.5 | -1.0096
1243.3 | 50.5 | -1.0096
1243.4 | 50.5 | -1.0096
1243.5 | 50.5 | -1.0096
1243.6 | 50.5 | -1.0096
1243.7 | 50.5 | -1.0096
1243.8 | 50.5 | -1.0096
1243.9 | 50.5 | -1.0096
1244 | 50.5 | -1.0096
1244.1 | 50.5 | -1.0094
1244.2 | 50.5 | -1.0094
1244.3 | 50.5 | -1.0094
1244.4 | 50.5 | -1.0094
1244.5 | 50.5 | -1.0094
1244.6 | 50.5 | -1.0094
1244.7 | 50.5 | -1.0094
1244.8 | 50.5 | -1.0094
1244.9 | 50.5 | -1.0092
1245 | 50.5 | -1.0092
1245.1 | 50.5 | -1.0092
1245.2 | 50.5 | -1.0092
1245.3 | 50.5 | -1.0092
1245.4 | 50.5 | -1.0092
1245.5 | 50.5 | -1.0092
1245.6 | 50.5 | -1.0092
1245.7 | 50.5 | -1.0092
1245.8 | 50.5 | -1.0092
1245.9 | 50.5 | -1.0092
1246 | 50.5 | -1.0092
1246.1 | 50.5 | -1.0096
1246.2 | 50.5 | -1.0096
1246.3 | 50.5 | -1.0096
1246.4 | 50.5 | -1.0096
1246.5 | 50.5 | -1.0094
1246.6 | 50.5 | -1.0094
1246.7 | 50.5 | -1.0094
1246.8 | 50.5 | -1.0094
1246.9 | 50.5 | -1.0096
1247 | 50.5 | -1.0096
1247.1 | 50.5 | -1.0096
1247.2 | 50.5 | -1.0096
1247.3 | 50.5 | -1.0096
1247.4 | 50.5 | -1.0096
1247.5 | 50.5 | -1.0096
1247.6 | 50.5 | -1.0096
1247.7 | 50.5 | -1.0096
1247.8 | 50.5 | -1.0096
1247.9 | 50.5 | -1.0096
1248 | 50.5 | -1.0096
1248.1 | 50.5 | -1.0098
1248.2 | 50.5 | -1.0098
1248.3 | 50.5 | -1.0098
1248.4 | 50.5 | -1.0096
1248.5 | 50.5 | -1.0096
1248.6 | 50.5 | -1.0096
1248.7 | 50.5 | -1.0096
1248.8 | 50.5 | -1.0096
1248.9 | 50.5 | -1.0096
1249 | 50.5 | -1.0096
1249.1 | 50.5 | -1.0096
1249.2 | 50.5 | -1.0096
1249.3 | 50.5 | -1.0094
1249.4 | 50.5 | -1.0094
1249.5 | 50.5 | -1.0094
1249.6 | 50.5 | -1.0094
1249.7 | 50.5 | -1.0094
1249.8 | 50.5 | -1.0094
1249.9 | 50.5 | -1.0094
1250 | 50.5 | -1.0094
1250.1 | 50.5 | -1.0094
1250.2 | 50.5 | -1.0094
1250.3 | 50.5 | -1.0094
1250.4 | 50.5 | -1.0094
1250.5 | 50.5 | -1.0094
1250.6 | 50.5 | -1.0094
1250.7 | 50.5 | -1.0094
1250.8 | 50.5 | -1.0094
1250.9 | 50.5 | -1.0094
1251 | 50.5 | -1.0094
1251.1 | 50.5 | -1.0094
1251.2 | 50.5 | -1.0094
1251.3 | 50.5 | -1.0094
1251.4 | 50.5 | -1.0094
1251.5 | 50.5 | -1.0094
1251.6 | 50.5 | -1.0094
1251.7 | 50.5 | -1.0094
1251.8 | 50.5 | -1.0094
1251.9 | 50.5 | -1.0094
1252 | 50.5 | -1.0094
1252.1 | 50.5 | -1.0094
1252.2 | 50.5 | -1.0094
1252.3 | 50.5 | -1.0094
1252.4 | 50.5 | -1.0094
1252.5 | 50.5 | -1.0094
1252.6 | 50.5 | -1.0094
1252.7 | 50.5 | -1.0094
1252.8 | 50.5 | -1.0096
1252.9 | 50.5 | -1.0096
1253 | 50.5 | -1.0096
1253.1 | 50.5 | -1.0096
1253.2 | 50.5 | -1.0096
1253.3 | 50.5 | -1.0096
1253.4 | 50.5 | -1.0096
1253.5 | 50.5 | -1.0096
1253.6 | 50.5 | -1.0096
1253.7 | 50.5 | -1.0096
1253.8 | 50.5 | -1.0096
1253.9 | 50.5 | -1.0096
1254 | 50.5 | -1.0098
1254.1 | 50.5 | -1.0098
1254.2 | 50.5 | -1.0098
1254.3 | 50.5 | -1.0098
1254.4 | 50.5 | -1.0098
1254.5 | 50.5 | -1.0098
1254.6 | 50.5 | -1.0098
1254.7 | 50.5 | -1.0098
1254.8 | 50.5 | -1.0098
1254.9 | 50.5 | -1.0098
1255 | 50.5 | -1.0098
1255.1 | 50.5 | -1.0098
1255.2 | 50.5 | -1.0096
1255.3 | 50.5 | -1.0096
1255.4 | 50.5 | -1.0094
1255.5 | 50.5 | -1.0094
1255.6 | 50.5 | -1.0094
1255.7 | 50.5 | -1.0094
1255.8 | 50.5 | -1.0094
1255.9 | 50.5 | -1.0094
1256 | 50.5 | -1.0094
1256.1 | 50.5 | -1.0094
1256.2 | 50.5 | -1.0094
1256.3 | 50.5 | -1.0094
1256.4 | 50.5 | -1.0094
1256.5 | 50.5 | -1.0094
1256.6 | 50.5 | -1.0094
1256.7 | 50.5 | -1.0094
1256.8 | 50.5 | -1.0094
1256.9 | 50.5 | -1.0094
1257 | 50.5 | -1.0094
1257.1 | 50.5 | -1.0094
1257.2 | 50.5 | -1.0094
1257.3 | 50.5 | -1.0094
1257.4 | 50.5 | -1.0094
1257.5 | 50.5 | -1.0094
1257.6 | 50.5 | -1.0094
1257.7 | 50.5 | -1.0096
1257.8 | 50.5 | -1.0096
1257.9 | 50.5 | -1.0096
1258 | 50.5 | -1.0096
1258.1 | 50.5 | -1.0096
1258.2 | 50.5 | -1.0096
1258.3 | 50.5 | -1.0096
1258.4 | 50.5 | -1.0096
1258.5 | 50.5 | -1.0096
1258.6 | 50.5 | -1.0096
1258.7 | 50.5 | -1.0096
1258.8 | 50.5 | -1.0096
1258.9 | 50.5 | -1.0096
1259 | 50.5 | -1.0096
1259.1 | 50.5 | -1.0096
1259.2 | 50.5 | -1.0096
1259.3 | 50.5 | -1.0096
1259.4 | 50.5 | -1.0096
1259.5 | 50.5 | -1.0096
1259.6 | 50.5 | -1.0096
1259.7 | 50.5 | -1.0096
1259.8 | 50.5 | -1.0096
1259.9 | 50.5 | -1.0096
1260 | 50.5 | -1.0096
1260.1 | 50.5 | -1.0096
1260.2 | 50.5 | -1.0096
1260.3 | 50.5 | -1.0096
1260.4 | 50.5 | -1.0096
1260.5 | 50.5 | -1.0096
1260.6 | 50.5 | -1.0096
1260.7 | 50.5 | -1.0096
1260.8 | 50.5 | -1.0096
1260.9 | 50.5 | -1.0096
1261 | 50.5 | -1.0096
1261.1 | 50.5 | -1.0096
1261.2 | 50.5 | -1.0096
1261.3 | 50.5 | -1.0096
1261.4 | 50.5 | -1.0096
1261.5 | 50.5 | -1.0096
1261.6 | 50.5 | -1.0096
1261.7 | 50.5 | -1.0096
1261.8 | 50.5 | -1.0096
1261.9 | 50.5 | -1.0096
1262 | 50.5 | -1.0096
1262.1 | 50.5 | -1.0096
1262.2 | 50.5 | -1.0096
1262.3 | 50.5 | -1.0096
1262.4 | 50.5 | -1.0094
1262.5 | 50.5 | -1.0094
1262.6 | 50.5 | -1.0094
1262.7 | 50.5 | -1.0094
1262.8 | 50.5 | -1.0094
1262.9 | 50.5 | -1.0094
1263 | 50.5 | -1.0094
1263.1 | 50.5 | -1.0094
1263.2 | 50.5 | -1.0094
1263.3 | 50.5 | -1.0094
1263.4 | 50.5 | -1.0094
1263.5 | 50.5 | -1.0096
1263.6 | 50.5 | -1.0096
1263.7 | 50.5 | -1.0096
1263.8 | 50.5 | -1.0096
1263.9 | 50.5 | -1.0096
1264 | 50.5 | -1.0096
1264.1 | 50.5 | -1.0096
1264.2 | 50.5 | -1.0096
1264.3 | 50.5 | -1.0096
1264.4 | 50.5 | -1.0096
1264.5 | 50.5 | -1.0096
1264.6 | 50.5 | -1.0096
1264.7 | 50.5 | -1.0096
1264.8 | 50.5 | -1.0096
1264.9 | 50.5 | -1.0096
1265 | 50.5 | -1.0096
1265.1 | 50.5 | -1.0096
1265.2 | 50.5 | -1.0096
1265.3 | 50.5 | -1.0096
1265.4 | 50.5 | -1.0096
1265.5 | 50.5 | -1.0096
1265.6 | 50.5 | -1.0096
1265.7 | 50.5 | -1.0096
1265.8 | 50.5 | -1.0096
1265.9 | 50.5 | -1.0096
1266 | 50.5 | -1.0096
1266.1 | 50.5 | -1.0096
1266.2 | 50.5 | -1.0096
1266.3 | 50.5 | -1.0096
1266.4 | 50.5 | -1.0096
1266.5 | 50.5 | -1.0096
1266.6 | 50.5 | -1.0096
1266.7 | 50.5 | -1.0096
1266.8 | 50.5 | -1.0096
1266.9 | 50.5 | -1.0096
1267 | 50.5 | -1.0096
1267.1 | 50.5 | -1.0096
1267.2 | 50.5 | -1.0096
1267.3 | 50.5 | -1.0096
1267.4 | 50.5 | -1.0096
1267.5 | 50.5 | -1.0096
1267.6 | 50.5 | -1.0096
1267.7 | 50.5 | -1.0096
1267.8 | 50.5 | -1.0096
1267.9 | 50.5 | -1.0096
1268 | 50.5 | -1.0096
1268.1 | 50.5 | -1.0096
1268.2 | 50.5 | -1.0096
1268.3 | 50.5 | -1.0096
1268.4 | 50.5 | -1.0096
1268.5 | 50.5 | -1.0096
1268.6 | 50.5 | -1.0096
1268.7 | 50.5 | -1.0096
1268.8 | 50.5 | -1.0096
1268.9 | 50.5 | -1.0096
1269 | 50.5 | -1.0096
1269.1 | 50.5 | -1.0096
1269.2 | 50.5 | -1.0096
1269.3 | 50.5 | -1.0096
1269.4 | 50.5 | -1.0096
1269.5 | 50.5 | -1.0096
1269.6 | 50.5 | -1.0096
1269.7 | 50.5 | -1.0096
1269.8 | 50.5 | -1.0096
1269.9 | 50.5 | -1.0096
1270 | 50.5 | -1.0096
1270.1 | 50.5 | -1.0096
1270.2 | 50.5 | -1.0096
1270.3 | 50.5 | -1.0096
1270.4 | 50.5 | -1.0096
1270.5 | 50.5 | -1.0096
1270.6 | 50.5 | -1.0096
1270.7 | 50.5 | -1.0096
1270.8 | 50.5 | -1.0096
1270.9 | 50.5 | -1.0096
1271 | 50.5 | -1.0096
1271.1 | 50.5 | -1.0096
1271.2 | 50.5 | -1.0096
1271.3 | 50.5 | -1.0096
1271.4 | 50.5 | -1.0096
1271.5 | 50.5 | -1.0096
1271.6 | 50.5 | -1.0096
1271.7 | 50.5 | -1.0094
1271.8 | 50.5 | -1.0094
1271.9 | 50.5 | -1.0094
1272 | 50.5 | -1.0094
1272.1 | 50.5 | -1.0094
1272.2 | 50.5 | -1.0094
1272.3 | 50.5 | -1.0094
1272.4 | 50.5 | -1.0094
1272.5 | 50.5 | -1.0094
1272.6 | 50.5 | -1.0094
1272.7 | 50.5 | -1.0094
1272.8 | 50.5 | -1.0096
1272.9 | 50.5 | -1.0096
1273 | 50.5 | -1.0096
1273.1 | 50.5 | -1.0096
1273.2 | 50.5 | -1.0096
1273.3 | 50.5 | -1.0096
1273.4 | 50.5 | -1.0096
1273.5 | 50.5 | -1.0096
1273.6 | 50.5 | -1.0096
1273.7 | 50.5 | -1.0096
1273.8 | 50.5 | -1.0096
1273.9 | 50.5 | -1.0096
1274 | 50.5 | -1.0096
1274.1 | 50.5 | -1.0096
1274.2 | 50.5 | -1.0096
1274.3 | 50.5 | -1.0096
1274.4 | 50.5 | -1.0096
1274.5 | 50.5 | -1.0096
1274.6 | 50.5 | -1.0096
1274.7 | 50.5 | -1.0096
1274.8 | 50.5 | -1.0096
1274.9 | 50.5 | -1.0096
1275 | 50.5 | -1.0096
1275.1 | 50.5 | -1.0096
1275.2 | 50.5 | -1.0096
1275.3 | 50.5 | -1.0096
1275.4 | 50.5 | -1.0096
1275.5 | 50.5 | -1.0096
1275.6 | 50.5 | -1.0096
1275.7 | 50.5 | -1.0096
1275.8 | 50.5 | -1.0096
1275.9 | 50.5 | -1.0096
1276 | 50.5 | -1.0096
1276.1 | 50.5 | -1.0096
1276.2 | 50.5 | -1.0096
1276.3 | 50.5 | -1.0096
1276.4 | 50.5 | -1.0096
1276.5 | 50.5 | -1.0096
1276.6 | 50.5 | -1.0096
1276.7 | 50.5 | -1.0096
1276.8 | 50.5 | -1.0096
1276.9 | 50.5 | -1.0096
1277 | 50.5 | -1.0096
1277.1 | 50.5 | -1.0096
1277.2 | 50.5 | -1.0096
1277.3 | 50.5 | -1.0096
1277.4 | 50.5 | -1.0096
1277.5 | 50.5 | -1.0096
1277.6 | 50.5 | -1.0096
1277.7 | 50.5 | -1.0094
1277.8 | 50.5 | -1.0094
1277.9 | 50.5 | -1.0094
1278 | 50.5 | -1.0094
1278.1 | 50.5 | -1.0094
1278.2 | 50.5 | -1.0094
1278.3 | 50.5 | -1.0094
1278.4 | 50.5 | -1.0094
1278.5 | 50.5 | -1.0094
1278.6 | 50.5 | -1.0094
1278.7 | 50.5 | -1.0094
1278.8 | 50.5 | -1.0096
1278.9 | 50.5 | -1.0096
1279 | 50.5 | -1.0096
1279.1 | 50.5 | -1.0096
1279.2 | 50.5 | -1.0096
1279.3 | 50.5 | -1.0096
1279.4 | 50.5 | -1.0096
1279.5 | 50.5 | -1.0096
1279.6 | 50.5 | -1.0096
1279.7 | 50.5 | -1.0096
1279.8 | 50.5 | -1.0096
1279.9 | 50.5 | -1.0096
1280 | 50.5 | -1.0096
1280.1 | 50.5 | -1.0096
1280.2 | 50.5 | -1.0096
1280.3 | 50.5 | -1.0096
1280.4 | 50.5 | -1.0096
1280.5 | 50.5 | -1.0096
1280.6 | 50.5 | -1.0096
1280.7 | 50.5 | -1.0096
1280.8 | 50.5 | -1.0096
1280.9 | 50.5 | -1.0094
1281 | 50.5 | -1.0094
1281.1 | 50.5 | -1.0094
1281.2 | 50.5 | -1.0094
1281.3 | 50.5 | -1.0094
1281.4 | 50.5 | -1.0094
1281.5 | 50.5 | -1.0094
1281.6 | 50.5 | -1.0094
1281.7 | 50.5 | -1.0094
1281.8 | 50.5 | -1.0094
1281.9 | 50.5 | -1.0094
1282 | 50.5 | -1.0094
1282.1 | 50.5 | -1.0096
1282.2 | 50.5 | -1.0096
1282.3 | 50.5 | -1.0094
1282.4 | 50.5 | -1.0094
1282.5 | 50.5 | -1.0094
1282.6 | 50.5 | -1.0094
1282.7 | 50.5 | -1.0094
1282.8 | 50.5 | -1.0094
1282.9 | 50.5 | -1.0094
1283 | 50.5 | -1.0094
1283.1 | 50.5 | -1.0094
1283.2 | 50.5 | -1.0094
1283.3 | 50.5 | -1.0096
1283.4 | 50.5 | -1.0096
1283.5 | 50.5 | -1.0096
1283.6 | 50.5 | -1.0096
1283.7 | 50.5 | -1.0096
1283.8 | 50.5 | -1.0096
1283.9 | 50.5 | -1.0096
1284 | 50.5 | -1.0096
1284.1 | 50.5 | -1.0096
1284.2 | 50.5 | -1.0096
1284.3 | 50.5 | -1.0096
1284.4 | 50.5 | -1.0094
1284.5 | 50.5 | -1.0094
1284.6 | 50.5 | -1.0094
1284.7 | 50.5 | -1.0094
1284.8 | 50.5 | -1.0094
1284.9 | 50.5 | -1.0094
1285 | 50.5 | -1.0094
1285.1 | 50.5 | -1.0094
1285.2 | 50.5 | -1.0094
1285.3 | 50.5 | -1.0094
1285.4 | 50.5 | -1.0094
1285.5 | 50.5 | -1.0094
1285.6 | 50.5 | -1.0094
1285.7 | 50.5 | -1.0094
1285.8 | 50.5 | -1.0096
1285.9 | 50.5 | -1.0096
1286 | 50.5 | -1.0096
1286.1 | 50.5 | -1.0096
1286.2 | 50.5 | -1.0096
1286.3 | 50.5 | -1.0096
1286.4 | 50.5 | -1.0096
1286.5 | 50.5 | -1.0096
1286.6 | 50.5 | -1.0096
1286.7 | 50.5 | -1.0094
1286.8 | 50.5 | -1.0094
1286.9 | 50.5 | -1.0094
1287 | 50.5 | -1.0094
1287.1 | 50.5 | -1.0094
1287.2 | 50.5 | -1.0094
1287.3 | 50.5 | -1.0094
1287.4 | 50.5 | -1.0094
1287.5 | 50.5 | -1.0094
1287.6 | 50.5 | -1.0094
1287.7 | 50.5 | -1.0094
1287.8 | 50.5 | -1.0094
1287.9 | 50.5 | -1.0096
1288 | 50.5 | -1.0096
1288.1 | 50.5 | -1.0096
1288.2 | 50.5 | -1.0096
1288.3 | 50.5 | -1.0096
1288.4 | 50.5 | -1.0096
1288.5 | 50.5 | -1.0096
1288.6 | 50.5 | -1.0096
1288.7 | 50.5 | -1.0096
1288.8 | 50.5 | -1.0096
1288.9 | 50.5 | -1.0096
1289 | 50.5 | -1.0096
1289.1 | 50.5 | -1.0096
1289.2 | 50.5 | -1.0096
1289.3 | 50.5 | -1.0096
1289.4 | 50.5 | -1.0096
1289.5 | 50.5 | -1.0096
1289.6 | 50.5 | -1.0096
1289.7 | 50.5 | -1.0096
1289.8 | 50.5 | -1.0096
1289.9 | 50.5 | -1.0096
1290 | 50.5 | -1.0096
1290.1 | 50.5 | -1.0096
1290.2 | 50.5 | -1.0096
1290.3 | 50.5 | -1.0096
1290.4 | 50.5 | -1.0096
1290.5 | 50.5 | -1.0096
1290.6 | 50.5 | -1.0096
1290.7 | 50.5 | -1.0096
1290.8 | 50.5 | -1.0096
1290.9 | 50.5 | -1.0096
1291 | 50.5 | -1.0096
1291.1 | 50.5 | -1.0096
1291.2 | 50.5 | -1.0096
1291.3 | 50.5 | -1.0096
1291.4 | 50.5 | -1.0096
1291.5 | 50.5 | -1.0096
1291.6 | 50.5 | -1.0096
1291.7 | 50.5 | -1.0096
1291.8 | 50.5 | -1.0096
1291.9 | 50.5 | -1.0096
1292 | 50.5 | -1.0096
1292.1 | 50.5 | -1.0096
1292.2 | 50.5 | -1.0096
1292.3 | 50.5 | -1.0096
1292.4 | 50.5 | -1.0096
1292.5 | 50.5 | -1.0096
1292.6 | 50.5 | -1.0094
1292.7 | 50.5 | -1.0094
1292.8 | 50.5 | -1.0094
1292.9 | 50.5 | -1.0094
1293 | 50.5 | -1.0094
1293.1 | 50.5 | -1.0094
1293.2 | 50.5 | -1.0094
1293.3 | 50.5 | -1.0094
1293.4 | 50.5 | -1.0094
1293.5 | 50.5 | -1.0094
1293.6 | 50.5 | -1.0094
1293.7 | 50.5 | -1.0094
1293.8 | 50.5 | -1.0094
1293.9 | 50.5 | -1.0096
1294 | 50.5 | -1.0096
1294.1 | 50.5 | -1.0096
1294.2 | 50.5 | -1.0096
1294.3 | 50.5 | -1.0096
1294.4 | 50.5 | -1.0096
1294.5 | 50.5 | -1.0096
1294.6 | 50.5 | -1.0096
1294.7 | 50.5 | -1.0096
1294.8 | 50.5 | -1.0096
1294.9 | 50.5 | -1.0096
1295 | 50.5 | -1.0096
1295.1 | 50.5 | -1.0096
1295.2 | 50.5 | -1.0096
1295.3 | 50.5 | -1.0096
1295.4 | 50.5 | -1.0096
1295.5 | 50.5 | -1.0096
1295.6 | 50.5 | -1.0096
1295.7 | 50.5 | -1.0096
1295.8 | 50.5 | -1.0096
1295.9 | 50.5 | -1.0096
1296 | 50.5 | -1.0096
1296.1 | 50.5 | -1.0096
1296.2 | 50.5 | -1.0096
1296.3 | 50.5 | -1.0096
1296.4 | 50.5 | -1.0096
1296.5 | 50.5 | -1.0096
1296.6 | 50.5 | -1.0096
1296.7 | 50.5 | -1.0096
1296.8 | 50.5 | -1.0096
1296.9 | 50.5 | -1.0096
1297 | 50.5 | -1.0096
1297.1 | 50.5 | -1.0096
1297.2 | 50.5 | -1.0096
1297.3 | 50.5 | -1.0096
1297.4 | 50.5 | -1.0096
1297.5 | 50.5 | -1.0096
1297.6 | 50.5 | -1.0096
1297.7 | 50.5 | -1.0096
1297.8 | 50.5 | -1.0096
1297.9 | 50.5 | -1.0096
1298 | 50.5 | -1.0096
1298.1 | 50.5 | -1.0096
1298.2 | 50.5 | -1.0096
1298.3 | 50.5 | -1.0096
1298.4 | 50.5 | -1.0096
1298.5 | 50.5 | -1.0096
1298.6 | 50.5 | -1.0096
1298.7 | 50.5 | -1.0096
1298.8 | 50.5 | -1.0096
1298.9 | 50.5 | -1.0096
1299 | 50.5 | -1.0096
1299.1 | 50.5 | -1.0096
1299.2 | 50.5 | -1.0096
1299.3 | 50.5 | -1.0096
1299.4 | 50.5 | -1.0096
1299.5 | 50.5 | -1.0096
1299.6 | 50.5 | -1.0096
1299.7 | 50.5 | -1.0096
1299.8 | 50.5 | -1.0096
1299.9 | 50.5 | -1.0096
1300 | 50.5 | -1.0096
1300.1 | 50.5 | -1.0096
1300.2 | 50.5 | -1.0096
1300.3 | 50.5 | -1.0096
1300.4 | 50.5 | -1.0096
1300.5 | 50.5 | -1.0096
1300.6 | 50.5 | -1.0096
1300.7 | 50.5 | -1.0096
1300.8 | 50.5 | -1.0096
1300.9 | 50.5 | -1.0096
1301 | 50.5 | -1.0096
1301.1 | 50.5 | -1.0096
1301.2 | 50.5 | -1.0096
1301.3 | 50.5 | -1.0096
1301.4 | 50.5 | -1.0096
1301.5 | 50.5 | -1.0096
1301.6 | 50.5 | -1.0096
1301.7 | 50.5 | -1.0096
1301.8 | 50.5 | -1.0096
1301.9 | 50.5 | -1.0096
1302 | 50.5 | -1.0096
1302.1 | 50.5 | -1.0096
1302.2 | 50.5 | -1.0096
1302.3 | 50.5 | -1.0096
1302.4 | 50.5 | -1.0096
1302.5 | 50.5 | -1.0096
1302.6 | 50.5 | -1.0096
1302.7 | 50.5 | -1.0096
1302.8 | 50.5 | -1.0096
1302.9 | 50.5 | -1.0096
1303 | 50.5 | -1.0096
1303.1 | 50.5 | -1.0096
1303.2 | 50.5 | -1.0096
1303.3 | 50.5 | -1.0094
1303.4 | 50.5 | -1.0094
1303.5 | 50.5 | -1.0094
1303.6 | 50.5 | -1.0094
1303.7 | 50.5 | -1.0094
1303.8 | 50.5 | -1.0094
1303.9 | 50.5 | -1.0094
1304 | 50.5 | -1.0094
1304.1 | 50.5 | -1.0094
1304.2 | 50.5 | -1.0094
1304.3 | 50.5 | -1.0094
1304.4 | 50.5 | -1.0094
1304.5 | 50.5 | -1.0096
1304.6 | 50.5 | -1.0096
1304.7 | 50.5 | -1.0096
1304.8 | 50.5 | -1.0096
1304.9 | 50.5 | -1.0096
1305 | 50.5 | -1.0096
1305.1 | 50.5 | -1.0096
1305.2 | 50.5 | -1.0096
1305.3 | 50.5 | -1.0096
1305.4 | 50.5 | -1.0096
1305.5 | 50.5 | -1.0094
1305.6 | 50.5 | -1.0094
1305.7 | 50.5 | -1.0096
1305.8 | 50.5 | -1.0096
1305.9 | 50.5 | -1.0096
1306 | 50.5 | -1.0096
1306.1 | 50.5 | -1.0096
1306.2 | 50.5 | -1.0096
1306.3 | 50.5 | -1.0096
1306.4 | 50.5 | -1.0096
1306.5 | 50.5 | -1.0096
1306.6 | 50.5 | -1.0096
1306.7 | 50.5 | -1.0096
1306.8 | 50.5 | -1.0096
1306.9 | 50.5 | -1.0096
1307 | 50.5 | -1.0096
1307.1 | 50.5 | -1.0096
1307.2 | 50.5 | -1.0096
1307.3 | 50.5 | -1.0096
1307.4 | 50.5 | -1.0096
1307.5 | 50.5 | -1.0096
1307.6 | 50.5 | -1.0096
1307.7 | 50.5 | -1.0096
1307.8 | 50.5 | -1.0096
1307.9 | 50.5 | -1.0096
1308 | 50.5 | -1.0096
1308.1 | 50.5 | -1.0096
1308.2 | 50.5 | -1.0096
1308.3 | 50.5 | -1.0096
1308.4 | 50.5 | -1.0096
1308.5 | 50.5 | -1.0096
1308.6 | 50.5 | -1.0096
1308.7 | 50.5 | -1.0096
1308.8 | 50.5 | -1.0096
1308.9 | 50.5 | -1.0096
1309 | 50.5 | -1.0096
1309.1 | 50.5 | -1.0096
1309.2 | 50.5 | -1.0096
1309.3 | 50.5 | -1.0096
1309.4 | 50.5 | -1.0096
1309.5 | 50.5 | -1.0096
1309.6 | 50.5 | -1.0096
1309.7 | 50.5 | -1.0096
1309.8 | 50.5 | -1.0096
1309.9 | 50.5 | -1.0096
1310 | 50.5 | -1.0096
1310.1 | 50.5 | -1.0096
1310.2 | 50.5 | -1.0096
1310.3 | 50.5 | -1.0096
1310.4 | 50.5 | -1.0094
1310.5 | 50.5 | -1.0094
1310.6 | 50.5 | -1.0094
1310.7 | 50.5 | -1.0094
1310.8 | 50.5 | -1.0094
1310.9 | 50.5 | -1.0094
1311 | 50.5 | -1.0094
1311.1 | 50.5 | -1.0094
1311.2 | 50.5 | -1.0094
1311.3 | 50.5 | -1.0094
1311.4 | 50.5 | -1.0094
1311.5 | 50.5 | -1.0096
1311.6 | 50.5 | -1.0096
1311.7 | 50.5 | -1.0096
1311.8 | 50.5 | -1.0096
1311.9 | 50.5 | -1.0096
1312 | 50.5 | -1.0096
1312.1 | 50.5 | -1.0096
1312.2 | 50.5 | -1.0096
1312.3 | 50.5 | -1.0096
1312.4 | 50.5 | -1.0096
1312.5 | 50.5 | -1.0096
1312.6 | 50.5 | -1.0096
1312.7 | 50.5 | -1.0096
1312.8 | 50.5 | -1.0096
1312.9 | 50.5 | -1.0096
1313 | 50.5 | -1.0096
1313.1 | 50.5 | -1.0096
1313.2 | 50.5 | -1.0096
1313.3 | 50.5 | -1.0096
1313.4 | 50.5 | -1.0096
1313.5 | 50.5 | -1.0096
1313.6 | 50.5 | -1.0096
1313.7 | 50.5 | -1.0096
1313.8 | 50.5 | -1.0096
1313.9 | 50.5 | -1.0096
1314 | 50.5 | -1.0096
1314.1 | 50.5 | -1.0096
1314.2 | 50.5 | -1.0096
1314.3 | 50.5 | -1.0096
1314.4 | 50.5 | -1.0096
1314.5 | 50.5 | -1.0096
1314.6 | 50.5 | -1.0096
1314.7 | 50.5 | -1.0096
1314.8 | 50.5 | -1.0096
1314.9 | 50.5 | -1.0096
1315 | 50.5 | -1.0096
1315.1 | 50.5 | -1.0096
1315.2 | 50.5 | -1.0096
1315.3 | 50.5 | -1.0096
1315.4 | 50.5 | -1.0096
1315.5 | 50.5 | -1.0096
1315.6 | 50.5 | -1.0096
1315.7 | 50.5 | -1.0096
1315.8 | 50.5 | -1.0096
1315.9 | 50.5 | -1.0096
1316 | 50.5 | -1.0096
1316.1 | 50.5 | -1.0096
1316.2 | 50.5 | -1.0096
1316.3 | 50.5 | -1.0096
1316.4 | 50.5 | -1.0096
1316.5 | 50.5 | -1.0096
1316.6 | 50.5 | -1.0096
1316.7 | 50.5 | -1.0096
1316.8 | 50.5 | -1.0096
1316.9 | 50.5 | -1.0096
1317 | 50.5 | -1.0096
1317.1 | 50.5 | -1.0096
1317.2 | 50.5 | -1.0096
1317.3 | 50.5 | -1.0096
1317.4 | 50.5 | -1.0096
1317.5 | 50.5 | -1.0096
1317.6 | 50.5 | -1.0096
1317.7 | 50.5 | -1.0096
1317.8 | 50.5 | -1.0096
1317.9 | 50.5 | -1.0096
1318 | 50.5 | -1.0096
1318.1 | 50.5 | -1.0096
1318.2 | 50.5 | -1.0096
1318.3 | 50.5 | -1.0096
1318.4 | 50.5 | -1.0096
1318.5 | 50.5 | -1.0096
1318.6 | 50.5 | -1.0096
1318.7 | 50.5 | -1.0096
1318.8 | 50.5 | -1.0096
1318.9 | 50.5 | -1.0096
1319 | 50.5 | -1.0096
1319.1 | 50.5 | -1.0096
1319.2 | 50.5 | -1.0096
1319.3 | 50.5 | -1.0096
1319.4 | 50.5 | -1.0096
1319.5 | 50.5 | -1.0096
1319.6 | 50.5 | -1.0096
1319.7 | 50.5 | -1.0096
1319.8 | 50.5 | -1.0096
1319.9 | 50.5 | -1.0096
1320 | 50.5 | -1.0096
1320.1 | 50.5 | -1.0096
1320.2 | 50.5 | -1.0096
1320.3 | 50.5 | -1.0096
1320.4 | 50.5 | -1.0096
1320.5 | 50.5 | -1.0096
1320.6 | 50.5 | -1.0096
1320.7 | 50.5 | -1.0096
1320.8 | 50.5 | -1.0096
1320.9 | 50.5 | -1.0096
1321 | 50.5 | -1.0096
1321.1 | 50.5 | -1.0096
1321.2 | 50.5 | -1.0096
1321.3 | 50.5 | -1.0096
1321.4 | 50.5 | -1.0096
1321.5 | 50.5 | -1.0096
1321.6 | 50.5 | -1.0096
1321.7 | 50.5 | -1.0096
1321.8 | 50.5 | -1.0094
1321.9 | 50.5 | -1.0094
1322 | 50.5 | -1.0094
1322.1 | 50.5 | -1.0094
1322.2 | 50.5 | -1.0094
1322.3 | 50.5 | -1.0094
1322.4 | 50.5 | -1.0094
1322.5 | 50.5 | -1.0094
1322.6 | 50.5 | -1.0094
1322.7 | 50.5 | -1.0094
1322.8 | 50.5 | -1.0094
1322.9 | 50.5 | -1.0096
1323 | 50.5 | -1.0096
1323.1 | 50.5 | -1.0096
1323.2 | 50.5 | -1.0096
1323.3 | 50.5 | -1.0096
1323.4 | 50.5 | -1.0096
1323.5 | 50.5 | -1.0096
1323.6 | 50.5 | -1.0096
1323.7 | 50.5 | -1.0096
1323.8 | 50.5 | -1.0096
1323.9 | 50.5 | -1.0096
1324 | 50.5 | -1.0096
1324.1 | 50.5 | -1.0096
1324.2 | 50.5 | -1.0096
1324.3 | 50.5 | -1.0096
1324.4 | 50.5 | -1.0096
1324.5 | 50.5 | -1.0096
1324.6 | 50.5 | -1.0096
1324.7 | 50.5 | -1.0096
1324.8 | 50.5 | -1.0096
1324.9 | 50.5 | -1.0096
1325 | 50.5 | -1.0096
1325.1 | 50.5 | -1.0096
1325.2 | 50.5 | -1.0096
1325.3 | 50.5 | -1.0096
1325.4 | 50.5 | -1.0096
1325.5 | 50.5 | -1.0096
1325.6 | 50.5 | -1.0096
1325.7 | 50.5 | -1.0096
1325.8 | 50.5 | -1.0096
1325.9 | 50.5 | -1.0096
1326 | 50.5 | -1.0096
1326.1 | 50.5 | -1.0096
1326.2 | 50.5 | -1.0096
1326.3 | 50.5 | -1.0096
1326.4 | 50.5 | -1.0096
1326.5 | 50.5 | -1.0096
1326.6 | 50.5 | -1.0096
1326.7 | 50.5 | -1.0096
1326.8 | 50.5 | -1.0096
1326.9 | 50.5 | -1.0096
1327 | 50.5 | -1.0096
1327.1 | 50.5 | -1.0096
1327.2 | 50.5 | -1.0096
1327.3 | 50.5 | -1.0096
1327.4 | 50.5 | -1.0096
1327.5 | 50.5 | -1.0096
1327.6 | 50.5 | -1.0096
1327.7 | 50.5 | -1.0096
1327.8 | 50.5 | -1.0096
1327.9 | 50.5 | -1.0096
1328 | 50.5 | -1.0096
1328.1 | 50.5 | -1.0096
1328.2 | 50.5 | -1.0096
1328.3 | 50.5 | -1.0096
1328.4 | 50.5 | -1.0096
1328.5 | 50.5 | -1.0096
1328.6 | 50.5 | -1.0096
1328.7 | 50.5 | -1.0096
1328.8 | 50.5 | -1.0096
1328.9 | 50.5 | -1.0096
1329 | 50.5 | -1.0096
1329.1 | 50.5 | -1.0096
1329.2 | 50.5 | -1.0096
1329.3 | 50.5 | -1.0096
1329.4 | 50.5 | -1.0096
1329.5 | 50.5 | -1.0096
1329.6 | 50.5 | -1.0096
1329.7 | 50.5 | -1.0096
1329.8 | 50.5 | -1.0096
1329.9 | 50.5 | -1.0096
1330 | 50.5 | -1.0096
1330.1 | 50.5 | -1.0096
1330.2 | 50.5 | -1.0096
1330.3 | 50.5 | -1.0096
1330.4 | 50.5 | -1.0096
1330.5 | 50.5 | -1.0096
1330.6 | 50.5 | -1.0096
1330.7 | 50.5 | -1.0096
1330.8 | 50.5 | -1.0096
1330.9 | 50.5 | -1.0096
1331 | 50.5 | -1.0096
1331.1 | 50.5 | -1.0096
1331.2 | 50.5 | -1.0096
1331.3 | 50.5 | -1.0096
1331.4 | 50.5 | -1.0096
1331.5 | 50.5 | -1.0096
1331.6 | 50.5 | -1.0096
1331.7 | 50.5 | -1.0096
1331.8 | 50.5 | -1.0096
1331.9 | 50.5 | -1.0096
1332 | 50.5 | -1.0096
1332.1 | 50.5 | -1.0096
1332.2 | 50.5 | -1.0096
1332.3 | 50.5 | -1.0096
1332.4 | 50.5 | -1.0096
1332.5 | 50.5 | -1.0096
1332.6 | 50.5 | -1.0096
1332.7 | 50.5 | -1.0096
1332.8 | 50.5 | -1.0096
1332.9 | 50.5 | -1.0096
1333 | 50.5 | -1.0096
1333.1 | 50.5 | -1.0096
1333.2 | 50.5 | -1.0096
1333.3 | 50.5 | -1.0096
1333.4 | 50.5 | -1.0096
1333.5 | 50.5 | -1.0096
1333.6 | 50.5 | -1.0096
1333.7 | 50.5 | -1.0096
1333.8 | 50.5 | -1.0096
1333.9 | 50.5 | -1.0096
1334 | 50.5 | -1.0096
1334.1 | 50.5 | -1.0096
1334.2 | 50.5 | -1.0096
1334.3 | 50.5 | -1.0096
1334.4 | 50.5 | -1.0096
1334.5 | 50.5 | -1.0096
1334.6 | 50.5 | -1.0096
1334.7 | 50.5 | -1.0096
1334.8 | 50.5 | -1.0096
1334.9 | 50.5 | -1.0096
1335 | 50.5 | -1.0096
1335.1 | 50.5 | -1.0096
1335.2 | 50.5 | -1.0096
1335.3 | 50.5 | -1.0096
1335.4 | 50.5 | -1.0096
1335.5 | 50.5 | -1.0096
1335.6 | 50.5 | -1.0096
1335.7 | 50.5 | -1.0096
1335.8 | 50.5 | -1.0096
1335.9 | 50.5 | -1.0096
1336 | 50.5 | -1.0096
1336.1 | 50.5 | -1.0096
1336.2 | 50.5 | -1.0096
1336.3 | 50.5 | -1.0096
1336.4 | 50.5 | -1.0096
1336.5 | 50.5 | -1.0096
1336.6 | 50.5 | -1.0096
1336.7 | 50.5 | -1.0096
1336.8 | 50.5 | -1.0096
1336.9 | 50.5 | -1.0096
1337 | 50.5 | -1.0096
1337.1 | 50.5 | -1.0096
1337.2 | 50.5 | -1.0096
1337.3 | 50.5 | -1.0096
1337.4 | 50.5 | -1.0096
1337.5 | 50.5 | -1.0096
1337.6 | 50.5 | -1.0096
1337.7 | 50.5 | -1.0096
1337.8 | 50.5 | -1.0096
1337.9 | 50.5 | -1.0096
1338 | 50.5 | -1.0096
1338.1 | 50.5 | -1.0096
1338.2 | 50.5 | -1.0096
1338.3 | 50.5 | -1.0096
1338.4 | 50.5 | -1.0096
1338.5 | 50.5 | -1.0096
1338.6 | 50.5 | -1.0096
1338.7 | 50.5 | -1.0096
1338.8 | 50.5 | -1.0096
1338.9 | 50.5 | -1.0096
1339 | 50.5 | -1.0096
1339.1 | 50.5 | -1.0096
1339.2 | 50.5 | -1.0096
1339.3 | 50.5 | -1.0096
1339.4 | 50.5 | -1.0096
1339.5 | 50.5 | -1.0096
1339.6 | 50.5 | -1.0096
1339.7 | 50.5 | -1.0096
1339.8 | 50.5 | -1.0096
1339.9 | 50.5 | -1.0096
1340 | 50.5 | -1.0096
1340.1 | 50.5 | -1.0096
1340.2 | 50.5 | -1.0096
1340.3 | 50.5 | -1.0096
1340.4 | 50.5 | -1.0098
1340.5 | 50.5 | -1.0098
1340.6 | 50.5 | -1.0096
1340.7 | 50.5 | -1.0096
1340.8 | 50.5 | -1.0096
1340.9 | 50.5 | -1.0096
1341 | 50.5 | -1.0096
1341.1 | 50.5 | -1.0096
1341.2 | 50.5 | -1.0096
1341.3 | 50.5 | -1.0096
1341.4 | 50.5 | -1.0096
1341.5 | 50.5 | -1.0096
1341.6 | 50.5 | -1.0096
1341.7 | 50.5 | -1.0096
1341.8 | 50.5 | -1.0096
1341.9 | 50.5 | -1.0096
1342 | 50.5 | -1.0096
1342.1 | 50.5 | -1.0096
1342.2 | 50.5 | -1.0096
1342.3 | 50.5 | -1.0096
1342.4 | 50.5 | -1.0096
1342.5 | 50.5 | -1.0096
1342.6 | 50.5 | -1.0096
1342.7 | 50.5 | -1.0096
1342.8 | 50.5 | -1.0096
1342.9 | 50.5 | -1.0094
1343 | 50.5 | -1.0094
1343.1 | 50.5 | -1.0094
1343.2 | 50.5 | -1.0094
1343.3 | 50.5 | -1.0094
1343.4 | 50.5 | -1.0094
1343.5 | 50.5 | -1.0094
1343.6 | 50.5 | -1.0094
1343.7 | 50.5 | -1.0094
1343.8 | 50.5 | -1.0094
1343.9 | 50.5 | -1.0094
1344 | 50.5 | -1.0094
1344.1 | 50.5 | -1.0096
1344.2 | 50.5 | -1.0096
1344.3 | 50.5 | -1.0096
1344.4 | 50.5 | -1.0096
1344.5 | 50.5 | -1.0096
1344.6 | 50.5 | -1.0096
1344.7 | 50.5 | -1.0096
1344.8 | 50.5 | -1.0096
1344.9 | 50.5 | -1.0096
1345 | 50.5 | -1.0096
1345.1 | 50.5 | -1.0096
1345.2 | 50.5 | -1.0096
1345.3 | 50.5 | -1.0096
1345.4 | 50.5 | -1.0096
1345.5 | 50.5 | -1.0096
1345.6 | 50.5 | -1.0096
1345.7 | 50.5 | -1.0096
1345.8 | 50.5 | -1.0096
1345.9 | 50.5 | -1.0096
1346 | 50.5 | -1.0096
1346.1 | 50.5 | -1.0096
1346.2 | 50.5 | -1.0096
1346.3 | 50.5 | -1.0096
1346.4 | 50.5 | -1.0096
1346.5 | 50.5 | -1.0096
1346.6 | 50.5 | -1.0096
1346.7 | 50.5 | -1.0096
1346.8 | 50.5 | -1.0096
1346.9 | 50.5 | -1.0096
1347 | 50.5 | -1.0096
1347.1 | 50.5 | -1.0096
1347.2 | 50.5 | -1.0096
1347.3 | 50.5 | -1.0096
1347.4 | 50.5 | -1.0096
1347.5 | 50.5 | -1.0096
1347.6 | 50.5 | -1.0096
1347.7 | 50.5 | -1.0096
1347.8 | 50.5 | -1.0096
1347.9 | 50.5 | -1.0096
1348 | 50.5 | -1.0096
1348.1 | 50.5 | -1.0096
1348.2 | 50.5 | -1.0096
1348.3 | 50.5 | -1.0096
1348.4 | 50.5 | -1.0096
1348.5 | 50.5 | -1.0096
1348.6 | 50.5 | -1.0096
1348.7 | 50.5 | -1.0096
1348.8 | 50.5 | -1.0096
1348.9 | 50.5 | -1.0096
1349 | 50.5 | -1.0096
1349.1 | 50.5 | -1.0096
1349.2 | 50.5 | -1.0096
1349.3 | 50.5 | -1.0096
1349.4 | 50.5 | -1.0096
1349.5 | 50.5 | -1.0096
1349.6 | 50.5 | -1.0096
1349.7 | 50.5 | -1.0096
1349.8 | 50.5 | -1.0096
1349.9 | 50.5 | -1.0096
1350 | 50.5 | -1.0096
1350.1 | 50.5 | -1.0096
1350.2 | 50.5 | -1.0096
1350.3 | 50.5 | -1.0096
1350.4 | 50.5 | -1.0096
1350.5 | 50.5 | -1.0096
1350.6 | 50.5 | -1.0096
1350.7 | 50.5 | -1.0096
1350.8 | 50.5 | -1.0096
1350.9 | 50.5 | -1.0096
1351 | 50.5 | -1.0096
1351.1 | 50.5 | -1.0096
1351.2 | 50.5 | -1.0096
1351.3 | 50.5 | -1.0096
1351.4 | 50.5 | -1.0096
1351.5 | 50.5 | -1.0096
1351.6 | 50.5 | -1.0096
1351.7 | 50.5 | -1.0096
1351.8 | 50.5 | -1.0096
1351.9 | 50.5 | -1.0096
1352 | 50.5 | -1.0096
1352.1 | 50.5 | -1.0096
1352.2 | 50.5 | -1.0096
1352.3 | 50.5 | -1.0096
1352.4 | 50.5 | -1.0096
1352.5 | 50.5 | -1.0096
1352.6 | 50.5 | -1.0096
1352.7 | 50.5 | -1.0096
1352.8 | 50.5 | -1.0096
1352.9 | 50.5 | -1.0096
1353 | 50.5 | -1.0096
1353.1 | 50.5 | -1.0096
1353.2 | 50.5 | -1.0096
1353.3 | 50.5 | -1.0096
1353.4 | 50.5 | -1.0096
1353.5 | 50.5 | -1.0096
1353.6 | 50.5 | -1.0096
1353.7 | 50.5 | -1.0096
1353.8 | 50.5 | -1.0096
1353.9 | 50.5 | -1.0096
1354 | 50.5 | -1.0096
1354.1 | 50.5 | -1.0096
1354.2 | 50.5 | -1.0096
1354.3 | 50.5 | -1.0096
1354.4 | 50.5 | -1.0096
1354.5 | 50.5 | -1.0096
1354.6 | 50.5 | -1.0096
1354.7 | 50.5 | -1.0096
1354.8 | 50.5 | -1.0096
1354.9 | 50.5 | -1.0096
1355 | 50.5 | -1.0096
1355.1 | 50.5 | -1.0096
1355.2 | 50.5 | -1.0096
1355.3 | 50.5 | -1.0096
1355.4 | 50.5 | -1.0096
1355.5 | 50.5 | -1.0096
1355.6 | 50.5 | -1.0096
1355.7 | 50.5 | -1.0096
1355.8 | 50.5 | -1.0096
1355.9 | 50.5 | -1.0096
1356 | 50.5 | -1.0096
1356.1 | 50.5 | -1.0096
1356.2 | 50.5 | -1.0096
1356.3 | 50.5 | -1.0096
1356.4 | 50.5 | -1.0096
1356.5 | 50.5 | -1.0096
1356.6 | 50.5 | -1.0096
1356.7 | 50.5 | -1.0096
1356.8 | 50.5 | -1.0096
1356.9 | 50.5 | -1.0096
1357 | 50.5 | -1.0096
1357.1 | 50.5 | -1.0096
1357.2 | 50.5 | -1.0096
1357.3 | 50.5 | -1.0096
1357.4 | 50.5 | -1.0096
1357.5 | 50.5 | -1.0096
1357.6 | 50.5 | -1.0096
1357.7 | 50.5 | -1.0096
1357.8 | 50.5 | -1.0096
1357.9 | 50.5 | -1.0096
1358 | 50.5 | -1.0096
1358.1 | 50.5 | -1.0096
1358.2 | 50.5 | -1.0096
1358.3 | 50.5 | -1.0096
1358.4 | 50.5 | -1.0096
1358.5 | 50.5 | -1.0096
1358.6 | 50.5 | -1.0096
1358.7 | 50.5 | -1.0096
1358.8 | 50.5 | -1.0096
1358.9 | 50.5 | -1.0096
1359 | 50.5 | -1.0096
1359.1 | 50.5 | -1.0096
1359.2 | 50.5 | -1.0096
1359.3 | 50.5 | -1.0096
1359.4 | 50.5 | -1.0094
1359.5 | 50.5 | -1.0094
1359.6 | 50.5 | -1.0094
1359.7 | 50.5 | -1.0094
1359.8 | 50.5 | -1.0094
1359.9 | 50.5 | -1.0094
1360 | 50.5 | -1.0094
1360.1 | 50.5 | -1.0094
1360.2 | 50.5 | -1.0094
1360.3 | 50.5 | -1.0094
1360.4 | 50.5 | -1.0094
1360.5 | 50.5 | -1.0094
1360.6 | 50.5 | -1.0094
1360.7 | 50.5 | -1.0094
1360.8 | 50.5 | -1.0094
1360.9 | 50.5 | -1.0094
1361 | 50.5 | -1.0094
1361.1 | 50.5 | -1.0094
1361.2 | 50.5 | -1.0094
1361.3 | 50.5 | -1.0094
1361.4 | 50.5 | -1.0094
1361.5 | 50.5 | -1.0094
1361.6 | 50.5 | -1.0096
1361.7 | 50.5 | -1.0096
1361.8 | 50.5 | -1.0096
1361.9 | 50.5 | -1.0096
1362 | 50.5 | -1.0096
1362.1 | 50.5 | -1.0096
1362.2 | 50.5 | -1.0096
1362.3 | 50.5 | -1.0096
1362.4 | 50.5 | -1.0096
1362.5 | 50.5 | -1.0096
1362.6 | 50.5 | -1.0096
1362.7 | 50.5 | -1.0096
1362.8 | 50.5 | -1.0096
1362.9 | 50.5 | -1.0096
1363 | 50.5 | -1.0096
1363.1 | 50.5 | -1.0096
1363.2 | 50.5 | -1.0096
1363.3 | 50.5 | -1.0096
1363.4 | 50.5 | -1.0096
1363.5 | 50.5 | -1.0096
1363.6 | 50.5 | -1.0096
1363.7 | 50.5 | -1.0096
1363.8 | 50.5 | -1.0096
1363.9 | 50.5 | -1.0096
1364 | 50.5 | -1.0096
1364.1 | 50.5 | -1.0096
1364.2 | 50.5 | -1.0096
1364.3 | 50.5 | -1.0096
1364.4 | 50.5 | -1.0096
1364.5 | 50.5 | -1.0096
1364.6 | 50.5 | -1.0096
1364.7 | 50.5 | -1.0096
1364.8 | 50.5 | -1.0096
1364.9 | 50.5 | -1.0096
1365 | 50.5 | -1.0096
1365.1 | 50.5 | -1.0096
1365.2 | 50.5 | -1.0096
1365.3 | 50.5 | -1.0096
1365.4 | 50.5 | -1.0096
1365.5 | 50.5 | -1.0096
1365.6 | 50.5 | -1.0096
1365.7 | 50.5 | -1.0096
1365.8 | 50.5 | -1.0096
1365.9 | 50.5 | -1.0096
1366 | 50.5 | -1.0096
1366.1 | 50.5 | -1.0096
1366.2 | 50.5 | -1.0094
1366.3 | 50.5 | -1.0094
1366.4 | 50.5 | -1.0094
1366.5 | 50.5 | -1.0094
1366.6 | 50.5 | -1.0094
1366.7 | 50.5 | -1.0094
1366.8 | 50.5 | -1.0094
1366.9 | 50.5 | -1.0094
1367 | 50.5 | -1.0094
1367.1 | 50.5 | -1.0094
1367.2 | 50.5 | -1.0094
1367.3 | 50.5 | -1.0094
1367.4 | 50.5 | -1.0094
1367.5 | 50.5 | -1.0094
1367.6 | 50.5 | -1.0094
1367.7 | 50.5 | -1.0094
1367.8 | 50.5 | -1.0094
1367.9 | 50.5 | -1.0094
1368 | 50.5 | -1.0094
1368.1 | 50.5 | -1.0094
1368.2 | 50.5 | -1.0094
1368.3 | 50.5 | -1.0094
1368.4 | 50.5 | -1.0094
1368.5 | 50.5 | -1.0096
1368.6 | 50.5 | -1.0096
1368.7 | 50.5 | -1.0096
1368.8 | 50.5 | -1.0096
1368.9 | 50.5 | -1.0094
1369 | 50.5 | -1.0094
1369.1 | 50.5 | -1.0094
1369.2 | 50.5 | -1.0094
1369.3 | 50.5 | -1.0094
1369.4 | 50.5 | -1.0094
1369.5 | 50.5 | -1.0094
1369.6 | 50.5 | -1.0094
1369.7 | 50.5 | -1.0096
1369.8 | 50.5 | -1.0096
1369.9 | 50.5 | -1.0096
1370 | 50.5 | -1.0096
1370.1 | 50.5 | -1.0096
1370.2 | 50.5 | -1.0096
1370.3 | 50.5 | -1.0096
1370.4 | 50.5 | -1.0096
1370.5 | 50.5 | -1.0096
1370.6 | 50.5 | -1.0096
1370.7 | 50.5 | -1.0096
1370.8 | 50.5 | -1.0096
1370.9 | 50.5 | -1.0096
1371 | 50.5 | -1.0096
1371.1 | 50.5 | -1.0096
1371.2 | 50.5 | -1.0096
1371.3 | 50.5 | -1.0096
1371.4 | 50.5 | -1.0096
1371.5 | 50.5 | -1.0096
1371.6 | 50.5 | -1.0096
1371.7 | 50.5 | -1.0096
1371.8 | 50.5 | -1.0096
1371.9 | 50.5 | -1.0096
1372 | 50.5 | -1.0096
1372.1 | 50.5 | -1.0096
1372.2 | 50.5 | -1.0094
1372.3 | 50.5 | -1.0094
1372.4 | 50.5 | -1.0094
1372.5 | 50.5 | -1.0094
1372.6 | 50.5 | -1.0094
1372.7 | 50.5 | -1.0094
1372.8 | 50.5 | -1.0094
1372.9 | 50.5 | -1.0094
1373 | 50.5 | -1.0094
1373.1 | 50.5 | -1.0094
1373.2 | 50.5 | -1.0094
1373.3 | 50.5 | -1.0094
1373.4 | 50.5 | -1.0094
1373.5 | 50.5 | -1.0094
1373.6 | 50.5 | -1.0094
1373.7 | 50.5 | -1.0094
1373.8 | 50.5 | -1.0094
1373.9 | 50.5 | -1.0094
1374 | 50.5 | -1.0094
1374.1 | 50.5 | -1.0094
1374.2 | 50.5 | -1.0094
1374.3 | 50.5 | -1.0094
1374.4 | 50.5 | -1.0096
1374.5 | 50.5 | -1.0096
1374.6 | 50.5 | -1.0096
1374.7 | 50.5 | -1.0096
1374.8 | 50.5 | -1.0096
1374.9 | 50.5 | -1.0096
1375 | 50.5 | -1.0096
1375.1 | 50.5 | -1.0096
1375.2 | 50.5 | -1.0096
1375.3 | 50.5 | -1.0096
1375.4 | 50.5 | -1.0096
1375.5 | 50.5 | -1.0096
1375.6 | 50.5 | -1.0096
1375.7 | 50.5 | -1.0096
1375.8 | 50.5 | -1.0096
1375.9 | 50.5 | -1.0096
1376 | 50.5 | -1.0096
1376.1 | 50.5 | -1.0096
1376.2 | 50.5 | -1.0096
1376.3 | 50.5 | -1.0096
1376.4 | 50.5 | -1.0096
1376.5 | 50.5 | -1.0096
1376.6 | 50.5 | -1.0096
1376.7 | 50.5 | -1.0096
1376.8 | 50.5 | -1.0096
1376.9 | 50.5 | -1.0096
1377 | 50.5 | -1.0096
1377.1 | 50.5 | -1.0096
1377.2 | 50.5 | -1.0096
1377.3 | 50.5 | -1.0096
1377.4 | 50.5 | -1.0096
1377.5 | 50.5 | -1.0096
1377.6 | 50.5 | -1.0096
1377.7 | 50.5 | -1.0096
1377.8 | 50.5 | -1.0096
1377.9 | 50.5 | -1.0096
1378 | 50.5 | -1.0096
1378.1 | 50.5 | -1.0096
1378.2 | 50.5 | -1.0096
1378.3 | 50.5 | -1.0096
1378.4 | 50.5 | -1.0096
1378.5 | 50.5 | -1.0096
1378.6 | 50.5 | -1.0096
1378.7 | 50.5 | -1.0096
1378.8 | 50.5 | -1.0096
1378.9 | 50.5 | -1.0096
1379 | 50.5 | -1.0096
1379.1 | 50.5 | -1.0096
1379.2 | 50.5 | -1.0096
1379.3 | 50.5 | -1.0096
1379.4 | 50.5 | -1.0096
1379.5 | 50.5 | -1.0096
1379.6 | 50.5 | -1.0096
1379.7 | 50.5 | -1.0096
1379.8 | 50.5 | -1.0096
1379.9 | 50.5 | -1.0096
1380 | 50.5 | -1.0096
1380.1 | 50.5 | -1.0096
1380.2 | 50.5 | -1.0096
1380.3 | 50.5 | -1.0096
1380.4 | 50.5 | -1.0096
1380.5 | 50.5 | -1.0096
1380.6 | 50.5 | -1.0096
1380.7 | 50.5 | -1.0096
1380.8 | 50.5 | -1.0096
1380.9 | 50.5 | -1.0096
1381 | 50.5 | -1.0096
1381.1 | 50.5 | -1.0096
1381.2 | 50.5 | -1.0096
1381.3 | 50.5 | -1.0096
1381.4 | 50.5 | -1.0096
1381.5 | 50.5 | -1.0096
1381.6 | 50.5 | -1.0096
1381.7 | 50.5 | -1.0096
1381.8 | 50.5 | -1.0096
1381.9 | 50.5 | -1.0096
1382 | 50.5 | -1.0096
1382.1 | 50.5 | -1.0096
1382.2 | 50.5 | -1.0096
1382.3 | 50.5 | -1.0096
1382.4 | 50.5 | -1.0096
1382.5 | 50.5 | -1.0096
1382.6 | 50.5 | -1.0096
1382.7 | 50.5 | -1.0096
1382.8 | 50.5 | -1.0096
1382.9 | 50.5 | -1.0096
1383 | 50.5 | -1.0096
1383.1 | 50.5 | -1.0096
1383.2 | 50.5 | -1.0096
1383.3 | 50.5 | -1.0096
1383.4 | 50.5 | -1.0096
1383.5 | 50.5 | -1.0096
1383.6 | 50.5 | -1.0096
1383.7 | 50.5 | -1.0096
1383.8 | 50.5 | -1.0096
1383.9 | 50.5 | -1.0094
1384 | 50.5 | -1.0094
1384.1 | 50.5 | -1.0094
1384.2 | 50.5 | -1.0094
1384.3 | 50.5 | -1.0094
1384.4 | 50.5 | -1.0094
1384.5 | 50.5 | -1.0094
1384.6 | 50.5 | -1.0094
1384.7 | 50.5 | -1.0094
1384.8 | 50.5 | -1.0094
1384.9 | 50.5 | -1.0094
1385 | 50.5 | -1.0094
1385.1 | 50.5 | -1.0094
1385.2 | 50.5 | -1.0094
1385.3 | 50.5 | -1.0094
1385.4 | 50.5 | -1.0094
1385.5 | 50.5 | -1.0094
1385.6 | 50.5 | -1.0094
1385.7 | 50.5 | -1.0094
1385.8 | 50.5 | -1.0094
1385.9 | 50.5 | -1.0094
1386 | 50.5 | -1.0094
1386.1 | 50.5 | -1.0096
1386.2 | 50.5 | -1.0096
1386.3 | 50.5 | -1.0096
1386.4 | 50.5 | -1.0096
1386.5 | 50.5 | -1.0096
1386.6 | 50.5 | -1.0096
1386.7 | 50.5 | -1.0096
1386.8 | 50.5 | -1.0096
1386.9 | 50.5 | -1.0096
1387 | 50.5 | -1.0096
1387.1 | 50.5 | -1.0096
1387.2 | 50.5 | -1.0096
1387.3 | 50.5 | -1.0096
1387.4 | 50.5 | -1.0096
1387.5 | 50.5 | -1.0096
1387.6 | 50.5 | -1.0096
1387.7 | 50.5 | -1.0096
1387.8 | 50.5 | -1.0096
1387.9 | 50.5 | -1.0096
1388 | 50.5 | -1.0096
1388.1 | 50.5 | -1.0096
1388.2 | 50.5 | -1.0096
1388.3 | 50.5 | -1.0096
1388.4 | 50.5 | -1.0096
1388.5 | 50.5 | -1.0096
1388.6 | 50.5 | -1.0096
1388.7 | 50.5 | -1.0096
1388.8 | 50.5 | -1.0096
1388.9 | 50.5 | -1.0096
1389 | 50.5 | -1.0096
1389.1 | 50.5 | -1.0096
1389.2 | 50.5 | -1.0096
1389.3 | 50.5 | -1.0096
1389.4 | 50.5 | -1.0096
1389.5 | 50.5 | -1.0096
1389.6 | 50.5 | -1.0096
1389.7 | 50.5 | -1.0096
1389.8 | 50.5 | -1.0096
1389.9 | 50.5 | -1.0096
1390 | 50.5 | -1.0096
1390.1 | 50.5 | -1.0094
1390.2 | 50.5 | -1.0094
1390.3 | 50.5 | -1.0094
1390.4 | 50.5 | -1.0094
1390.5 | 50.5 | -1.0094
1390.6 | 50.5 | -1.0094
1390.7 | 50.5 | -1.0094
1390.8 | 50.5 | -1.0094
1390.9 | 50.5 | -1.0094
1391 | 50.5 | -1.0094
1391.1 | 50.5 | -1.0094
1391.2 | 50.5 | -1.0096
1391.3 | 50.5 | -1.0096
1391.4 | 50.5 | -1.0096
1391.5 | 50.5 | -1.0096
1391.6 | 50.5 | -1.0096
1391.7 | 50.5 | -1.0096
1391.8 | 50.5 | -1.0096
1391.9 | 50.5 | -1.0096
1392 | 50.5 | -1.0096
1392.1 | 50.5 | -1.0096
1392.2 | 50.5 | -1.0096
1392.3 | 50.5 | -1.0096
1392.4 | 50.5 | -1.0096
1392.5 | 50.5 | -1.0096
1392.6 | 50.5 | -1.0096
1392.7 | 50.5 | -1.0096
1392.8 | 50.5 | -1.0096
1392.9 | 50.5 | -1.0096
1393 | 50.5 | -1.0096
1393.1 | 50.5 | -1.0096
1393.2 | 50.5 | -1.0096
1393.3 | 50.5 | -1.0096
1393.4 | 50.5 | -1.0096
1393.5 | 50.5 | -1.0096
1393.6 | 50.5 | -1.0096
1393.7 | 50.5 | -1.0096
1393.8 | 50.5 | -1.0096
1393.9 | 50.5 | -1.0096
1394 | 50.5 | -1.0096
1394.1 | 50.5 | -1.0096
1394.2 | 50.5 | -1.0096
1394.3 | 50.5 | -1.0096
1394.4 | 50.5 | -1.0096
1394.5 | 50.5 | -1.0096
1394.6 | 50.5 | -1.0096
1394.7 | 50.5 | -1.0096
1394.8 | 50.5 | -1.0096
1394.9 | 50.5 | -1.0096
1395 | 50.5 | -1.0096
1395.1 | 50.5 | -1.0096
1395.2 | 50.5 | -1.0096
1395.3 | 50.5 | -1.0096
1395.4 | 50.5 | -1.0096
1395.5 | 50.5 | -1.0096
1395.6 | 50.5 | -1.0096
1395.7 | 50.5 | -1.0096
1395.8 | 50.5 | -1.0096
1395.9 | 50.5 | -1.0096
1396 | 50.5 | -1.0096
1396.1 | 50.5 | -1.0096
1396.2 | 50.5 | -1.0096
1396.3 | 50.5 | -1.0096
1396.4 | 50.5 | -1.0096
1396.5 | 50.5 | -1.0096
1396.6 | 50.5 | -1.0096
1396.7 | 50.5 | -1.0096
1396.8 | 50.5 | -1.0096
1396.9 | 50.5 | -1.0096
1397 | 50.5 | -1.0096
1397.1 | 50.5 | -1.0096
1397.2 | 50.5 | -1.0096
1397.3 | 50.5 | -1.0096
1397.4 | 50.5 | -1.0096
1397.5 | 50.5 | -1.0096
1397.6 | 50.5 | -1.0096
1397.7 | 50.5 | -1.0096
1397.8 | 50.5 | -1.0096
1397.9 | 50.5 | -1.0096
1398 | 50.5 | -1.0096
1398.1 | 50.5 | -1.0096
1398.2 | 50.5 | -1.0096
1398.3 | 50.5 | -1.0096
1398.4 | 50.5 | -1.0096
1398.5 | 50.5 | -1.0096
1398.6 | 50.5 | -1.0096
1398.7 | 50.5 | -1.0096
1398.8 | 50.5 | -1.0096
1398.9 | 50.5 | -1.0096
1399 | 50.5 | -1.0096
1399.1 | 50.5 | -1.0096
1399.2 | 50.5 | -1.0096
1399.3 | 50.5 | -1.0096
1399.4 | 50.5 | -1.0096
1399.5 | 50.5 | -1.0096
1399.6 | 50.5 | -1.0096
1399.7 | 50.5 | -1.0096
1399.8 | 50.5 | -1.0096
1399.9 | 50.5 | -1.0096
1400 | 50.5 | -1.0096
1400.1 | 50.5 | -1.0096
1400.2 | 50.5 | -1.0096
1400.3 | 50.5 | -1.0096
1400.4 | 50.5 | -1.0096
1400.5 | 50.5 | -1.0096
1400.6 | 50.5 | -1.0096
1400.7 | 50.5 | -1.0096
1400.8 | 50.5 | -1.0096
1400.9 | 50.5 | -1.0096
1401 | 50.5 | -1.0096
1401.1 | 50.5 | -1.0096
1401.2 | 50.5 | -1.0096
1401.3 | 50.5 | -1.0096
1401.4 | 50.5 | -1.0096
1401.5 | 50.5 | -1.0096
1401.6 | 50.5 | -1.0096
1401.7 | 50.5 | -1.0096
1401.8 | 50.5 | -1.0096
1401.9 | 50.5 | -1.0096
1402 | 50.5 | -1.0096
1402.1 | 50.5 | -1.0096
1402.2 | 50.5 | -1.0096
1402.3 | 50.5 | -1.0096
1402.4 | 50.5 | -1.0096
1402.5 | 50.5 | -1.0096
1402.6 | 50.5 | -1.0096
1402.7 | 50.5 | -1.0096
1402.8 | 50.5 | -1.0096
1402.9 | 50.5 | -1.0094
1403 | 50.5 | -1.0094
1403.1 | 50.5 | -1.0094
1403.2 | 50.5 | -1.0094
1403.3 | 50.5 | -1.0094
1403.4 | 50.5 | -1.0094
1403.5 | 50.5 | -1.0094
1403.6 | 50.5 | -1.0094
1403.7 | 50.5 | -1.0096
1403.8 | 50.5 | -1.0096
1403.9 | 50.5 | -1.0096
1404 | 50.5 | -1.0096
1404.1 | 50.5 | -1.0096
1404.2 | 50.5 | -1.0096
1404.3 | 50.5 | -1.0096
1404.4 | 50.5 | -1.0096
1404.5 | 50.5 | -1.0096
1404.6 | 50.5 | -1.0096
1404.7 | 50.5 | -1.0096
1404.8 | 50.5 | -1.0096
1404.9 | 50.5 | -1.0096
1405 | 50.5 | -1.0096
1405.1 | 50.5 | -1.0096
1405.2 | 50.5 | -1.0096
1405.3 | 50.5 | -1.0096
1405.4 | 50.5 | -1.0096
1405.5 | 50.5 | -1.0096
1405.6 | 50.5 | -1.0096
1405.7 | 50.5 | -1.0096
1405.8 | 50.5 | -1.0096
1405.9 | 50.5 | -1.0096
1406 | 50.5 | -1.0096
1406.1 | 50.5 | -1.0096
1406.2 | 50.5 | -1.0096
1406.3 | 50.5 | -1.0096
1406.4 | 50.5 | -1.0096
1406.5 | 50.5 | -1.0096
1406.6 | 50.5 | -1.0096
1406.7 | 50.5 | -1.0096
1406.8 | 50.5 | -1.0096
1406.9 | 50.5 | -1.0096
1407 | 50.5 | -1.0096
1407.1 | 50.5 | -1.0096
1407.2 | 50.5 | -1.0096
1407.3 | 50.5 | -1.0096
1407.4 | 50.5 | -1.0096
1407.5 | 50.5 | -1.0096
1407.6 | 50.5 | -1.0096
1407.7 | 50.5 | -1.0096
1407.8 | 50.5 | -1.0096
1407.9 | 50.5 | -1.0096
1408 | 50.5 | -1.0096
1408.1 | 50.5 | -1.0096
1408.2 | 50.5 | -1.0096
1408.3 | 50.5 | -1.0096
1408.4 | 50.5 | -1.0096
1408.5 | 50.5 | -1.0096
1408.6 | 50.5 | -1.0096
1408.7 | 50.5 | -1.0096
1408.8 | 50.5 | -1.0096
1408.9 | 50.5 | -1.0096
1409 | 50.5 | -1.0096
1409.1 | 50.5 | -1.0096
1409.2 | 50.5 | -1.0096
1409.3 | 50.5 | -1.0096
1409.4 | 50.5 | -1.0096
1409.5 | 50.5 | -1.0096
1409.6 | 50.5 | -1.0096
1409.7 | 50.5 | -1.0096
1409.8 | 50.5 | -1.0096
1409.9 | 50.5 | -1.0096
1410 | 50.5 | -1.0096
1410.1 | 50.5 | -1.0096
1410.2 | 50.5 | -1.0096
1410.3 | 50.5 | -1.0096
1410.4 | 50.5 | -1.0096
1410.5 | 50.5 | -1.0096
1410.6 | 50.5 | -1.0096
1410.7 | 50.5 | -1.0096
1410.8 | 50.5 | -1.0096
1410.9 | 50.5 | -1.0096
1411 | 50.5 | -1.0096
1411.1 | 50.5 | -1.0096
1411.2 | 50.5 | -1.0096
1411.3 | 50.5 | -1.0096
1411.4 | 50.5 | -1.0096
1411.5 | 50.5 | -1.0096
1411.6 | 50.5 | -1.0096
1411.7 | 50.5 | -1.0096
1411.8 | 50.5 | -1.0096
1411.9 | 50.5 | -1.0096
1412 | 50.5 | -1.0096
1412.1 | 50.5 | -1.0096
1412.2 | 50.5 | -1.0096
1412.3 | 50.5 | -1.0096
1412.4 | 50.5 | -1.0096
1412.5 | 50.5 | -1.0096
1412.6 | 50.5 | -1.0096
1412.7 | 50.5 | -1.0096
1412.8 | 50.5 | -1.0096
1412.9 | 50.5 | -1.0096
1413 | 50.5 | -1.0096
1413.1 | 50.5 | -1.0096
1413.2 | 50.5 | -1.0096
1413.3 | 50.5 | -1.0096
1413.4 | 50.5 | -1.0096
1413.5 | 50.5 | -1.0096
1413.6 | 50.5 | -1.0096
1413.7 | 50.5 | -1.0096
1413.8 | 50.5 | -1.0096
1413.9 | 50.5 | -1.0096
1414 | 50.5 | -1.0096
1414.1 | 50.5 | -1.0096
1414.2 | 50.5 | -1.0096
1414.3 | 50.5 | -1.0096
1414.4 | 50.5 | -1.0096
1414.5 | 50.5 | -1.0096
1414.6 | 50.5 | -1.0096
1414.7 | 50.5 | -1.0096
1414.8 | 50.5 | -1.0096
1414.9 | 50.5 | -1.0096
1415 | 50.5 | -1.0096
1415.1 | 50.5 | -1.0096
1415.2 | 50.5 | -1.0096
1415.3 | 50.5 | -1.0096
1415.4 | 50.5 | -1.0096
1415.5 | 50.5 | -1.0096
1415.6 | 50.5 | -1.0096
1415.7 | 50.5 | -1.0096
1415.8 | 50.5 | -1.0096
1415.9 | 50.5 | -1.0096
1416 | 50.5 | -1.0096
1416.1 | 50.5 | -1.0096
1416.2 | 50.5 | -1.0096
1416.3 | 50.5 | -1.0096
1416.4 | 50.5 | -1.0096
1416.5 | 50.5 | -1.0096
1416.6 | 50.5 | -1.0096
1416.7 | 50.5 | -1.0096
1416.8 | 50.5 | -1.0096
1416.9 | 50.5 | -1.0096
1417 | 50.5 | -1.0096
1417.1 | 50.5 | -1.0096
1417.2 | 50.5 | -1.0096
1417.3 | 50.5 | -1.0096
1417.4 | 50.5 | -1.0096
1417.5 | 50.5 | -1.0096
1417.6 | 50.5 | -1.0096
1417.7 | 50.5 | -1.0096
1417.8 | 50.5 | -1.0096
1417.9 | 50.5 | -1.0096
1418 | 50.5 | -1.0096
1418.1 | 50.5 | -1.0096
1418.2 | 50.5 | -1.0096
1418.3 | 50.5 | -1.0096
1418.4 | 50.5 | -1.0096
1418.5 | 50.5 | -1.0096
1418.6 | 50.5 | -1.0096
1418.7 | 50.5 | -1.0096
1418.8 | 50.5 | -1.0096
1418.9 | 50.5 | -1.0096
1419 | 50.5 | -1.0096
1419.1 | 50.5 | -1.0096
1419.2 | 50.5 | -1.0096
1419.3 | 50.5 | -1.0096
1419.4 | 50.5 | -1.0096
1419.5 | 50.5 | -1.0096
1419.6 | 50.5 | -1.0096
1419.7 | 50.5 | -1.0096
1419.8 | 50.5 | -1.0096
1419.9 | 50.5 | -1.0096
1420 | 50.5 | -1.0096
1420.1 | 50.5 | -1.0096
1420.2 | 50.5 | -1.0096
1420.3 | 50.5 | -1.0096
1420.4 | 50.5 | -1.0096
1420.5 | 50.5 | -1.0096
1420.6 | 50.5 | -1.0096
1420.7 | 50.5 | -1.0096
1420.8 | 50.5 | -1.0096
1420.9 | 50.5 | -1.0096
1421 | 50.5 | -1.0096
1421.1 | 50.5 | -1.0096
1421.2 | 50.5 | -1.0096
1421.3 | 50.5 | -1.0096
1421.4 | 50.5 | -1.0096
1421.5 | 50.5 | -1.0096
1421.6 | 50.5 | -1.0096
1421.7 | 50.5 | -1.0096
1421.8 | 50.5 | -1.0096
1421.9 | 50.5 | -1.0096
1422 | 50.5 | -1.0096
1422.1 | 50.5 | -1.0096
1422.2 | 50.5 | -1.0096
1422.3 | 50.5 | -1.0096
1422.4 | 50.5 | -1.0096
1422.5 | 50.5 | -1.0096
1422.6 | 50.5 | -1.0096
1422.7 | 50.5 | -1.0096
1422.8 | 50.5 | -1.0096
1422.9 | 50.5 | -1.0096
1423 | 50.5 | -1.0096
1423.1 | 50.5 | -1.0096
1423.2 | 50.5 | -1.0096
1423.3 | 50.5 | -1.0096
1423.4 | 50.5 | -1.0096
1423.5 | 50.5 | -1.0096
1423.6 | 50.5 | -1.0096
1423.7 | 50.5 | -1.0096
1423.8 | 50.5 | -1.0096
1423.9 | 50.5 | -1.0096
1424 | 50.5 | -1.0096
1424.1 | 50.5 | -1.0096
1424.2 | 50.5 | -1.0096
1424.3 | 50.5 | -1.0096
1424.4 | 50.5 | -1.0096
1424.5 | 50.5 | -1.0096
1424.6 | 50.5 | -1.0096
1424.7 | 50.5 | -1.0096
1424.8 | 50.5 | -1.0096
1424.9 | 50.5 | -1.0094
1425 | 50.5 | -1.0094
1425.1 | 50.5 | -1.0094
1425.2 | 50.5 | -1.0094
1425.3 | 50.5 | -1.0094
1425.4 | 50.5 | -1.0094
1425.5 | 50.5 | -1.0094
1425.6 | 50.5 | -1.0094
1425.7 | 50.5 | -1.0094
1425.8 | 50.5 | -1.0094
1425.9 | 50.5 | -1.0094
1426 | 50.5 | -1.0094
1426.1 | 50.5 | -1.0096
1426.2 | 50.5 | -1.0096
1426.3 | 50.5 | -1.0096
1426.4 | 50.5 | -1.0096
1426.5 | 50.5 | -1.0096
1426.6 | 50.5 | -1.0096
1426.7 | 50.5 | -1.0096
1426.8 | 50.5 | -1.0096
1426.9 | 50.5 | -1.0096
1427 | 50.5 | -1.0096
1427.1 | 50.5 | -1.0096
1427.2 | 50.5 | -1.0096
1427.3 | 50.5 | -1.0096
1427.4 | 50.5 | -1.0096
1427.5 | 50.5 | -1.0096
1427.6 | 50.5 | -1.0096
1427.7 | 50.5 | -1.0096
1427.8 | 50.5 | -1.0096
1427.9 | 50.5 | -1.0096
1428 | 50.5 | -1.0096
1428.1 | 50.5 | -1.0096
1428.2 | 50.5 | -1.0096
1428.3 | 50.5 | -1.0096
1428.4 | 50.5 | -1.0096
1428.5 | 50.5 | -1.0096
1428.6 | 50.5 | -1.0096
1428.7 | 50.5 | -1.0096
1428.8 | 50.5 | -1.0096
1428.9 | 50.5 | -1.0096
1429 | 50.5 | -1.0096
1429.1 | 50.5 | -1.0096
1429.2 | 50.5 | -1.0096
1429.3 | 50.5 | -1.0096
1429.4 | 50.5 | -1.0096
1429.5 | 50.5 | -1.0096
1429.6 | 50.5 | -1.0096
1429.7 | 50.5 | -1.0096
1429.8 | 50.5 | -1.0096
1429.9 | 50.5 | -1.0096
1430 | 50.5 | -1.0096
1430.1 | 50.5 | -1.0096
1430.2 | 50.5 | -1.0096
1430.3 | 50.5 | -1.0096
1430.4 | 50.5 | -1.0096
1430.5 | 50.5 | -1.0096
1430.6 | 50.5 | -1.0098
1430.7 | 50.5 | -1.0098
1430.8 | 50.5 | -1.0098
1430.9 | 50.5 | -1.0098
1431 | 50.5 | -1.0098
1431.1 | 50.5 | -1.0098
1431.2 | 50.5 | -1.0098
1431.3 | 50.5 | -1.0098
1431.4 | 50.5 | -1.0096
1431.5 | 50.5 | -1.0096
1431.6 | 50.5 | -1.0096
1431.7 | 50.5 | -1.0096
1431.8 | 50.5 | -1.0096
1431.9 | 50.5 | -1.0096
1432 | 50.5 | -1.0096
1432.1 | 50.5 | -1.0096
1432.2 | 50.5 | -1.0096
1432.3 | 50.5 | -1.0096
1432.4 | 50.5 | -1.0096
1432.5 | 50.5 | -1.0096
1432.6 | 50.5 | -1.0096
1432.7 | 50.5 | -1.0096
1432.8 | 50.5 | -1.0096
1432.9 | 50.5 | -1.0096
1433 | 50.5 | -1.0096
1433.1 | 50.5 | -1.0096
1433.2 | 50.5 | -1.0096
1433.3 | 50.5 | -1.0096
1433.4 | 50.5 | -1.0096
1433.5 | 50.5 | -1.0096
1433.6 | 50.5 | -1.0096
1433.7 | 50.5 | -1.0096
1433.8 | 50.5 | -1.0096
1433.9 | 50.5 | -1.0096
1434 | 50.5 | -1.0096
1434.1 | 50.5 | -1.0096
1434.2 | 50.5 | -1.0096
1434.3 | 50.5 | -1.0096
1434.4 | 50.5 | -1.0096
1434.5 | 50.5 | -1.0096
1434.6 | 50.5 | -1.0096
1434.7 | 50.5 | -1.0096
1434.8 | 50.5 | -1.0096
1434.9 | 50.5 | -1.0096
1435 | 50.5 | -1.0096
1435.1 | 50.5 | -1.0096
1435.2 | 50.5 | -1.0096
1435.3 | 50.5 | -1.0096
1435.4 | 50.5 | -1.0096
1435.5 | 50.5 | -1.0094
1435.6 | 50.5 | -1.0094
1435.7 | 50.5 | -1.0094
1435.8 | 50.5 | -1.0094
1435.9 | 50.5 | -1.0094
1436 | 50.5 | -1.0094
1436.1 | 50.5 | -1.0094
1436.2 | 50.5 | -1.0094
1436.3 | 50.5 | -1.0094
1436.4 | 50.5 | -1.0094
1436.5 | 50.5 | -1.0094
1436.6 | 50.5 | -1.0096
1436.7 | 50.5 | -1.0096
1436.8 | 50.5 | -1.0096
1436.9 | 50.5 | -1.0096
1437 | 50.5 | -1.0096
1437.1 | 50.5 | -1.0096
1437.2 | 50.5 | -1.0096
1437.3 | 50.5 | -1.0096
1437.4 | 50.5 | -1.0096
1437.5 | 50.5 | -1.0096
1437.6 | 50.5 | -1.0096
1437.7 | 50.5 | -1.0096
1437.8 | 50.5 | -1.0096
1437.9 | 50.5 | -1.0096
1438 | 50.5 | -1.0096
1438.1 | 50.5 | -1.0096
1438.2 | 50.5 | -1.0096
1438.3 | 50.5 | -1.0096
1438.4 | 50.5 | -1.0096
1438.5 | 50.5 | -1.0094
1438.6 | 50.5 | -1.0094
1438.7 | 50.5 | -1.0094
1438.8 | 50.5 | -1.0094
1438.9 | 50.5 | -1.0094
1439 | 50.5 | -1.0094
1439.1 | 50.5 | -1.0094
1439.2 | 50.5 | -1.0094
1439.3 | 50.5 | -1.0094
1439.4 | 50.5 | -1.0094
1439.5 | 50.5 | -1.0094
1439.6 | 50.5 | -1.0096
1439.7 | 50.5 | -1.0096
1439.8 | 50.5 | -1.0096
1439.9 | 50.5 | -1.0096
1440 | 50.5 | -1.0096
1440.1 | 50.5 | -1.0096
1440.2 | 50.5 | -1.0096
1440.3 | 50.5 | -1.0096
1440.4 | 50.5 | -1.0096
1440.5 | 50.5 | -1.0096
1440.6 | 50.5 | -1.0096
1440.7 | 50.5 | -1.0096
1440.8 | 50.5 | -1.0096
1440.9 | 50.5 | -1.0096
1441 | 50.5 | -1.0096
1441.1 | 50.5 | -1.0096
1441.2 | 50.5 | -1.0096
1441.3 | 50.5 | -1.0096
1441.4 | 50.5 | -1.0096
1441.5 | 50.5 | -1.0096
1441.6 | 50.5 | -1.0096
1441.7 | 50.5 | -1.0096
1441.8 | 50.5 | -1.0096
1441.9 | 50.5 | -1.0096
1442 | 50.5 | -1.0096
1442.1 | 50.5 | -1.0096
1442.2 | 50.5 | -1.0096
1442.3 | 50.5 | -1.0096
1442.4 | 50.5 | -1.0096
1442.5 | 50.5 | -1.0096
1442.6 | 50.5 | -1.0096
1442.7 | 50.5 | -1.0096
1442.8 | 50.5 | -1.0096
1442.9 | 50.5 | -1.0096
1443 | 50.5 | -1.0096
1443.1 | 50.5 | -1.0096
1443.2 | 50.5 | -1.0096
1443.3 | 50.5 | -1.0096
1443.4 | 50.5 | -1.0096
1443.5 | 50.5 | -1.0096
1443.6 | 50.5 | -1.0096
1443.7 | 50.5 | -1.0096
1443.8 | 50.5 | -1.0096
1443.9 | 50.5 | -1.0096
1444 | 50.5 | -1.0096
1444.1 | 50.5 | -1.0096
1444.2 | 50.5 | -1.0096
1444.3 | 50.5 | -1.0096
1444.4 | 50.5 | -1.0096
1444.5 | 50.5 | -1.0096
1444.6 | 50.5 | -1.0096
1444.7 | 50.5 | -1.0096
1444.8 | 50.5 | -1.0096
1444.9 | 50.5 | -1.0096
1445 | 50.5 | -1.0096
1445.1 | 50.5 | -1.0096
1445.2 | 50.5 | -1.0096
1445.3 | 50.5 | -1.0094
1445.4 | 50.5 | -1.0094
1445.5 | 50.5 | -1.0094
1445.6 | 50.5 | -1.0094
1445.7 | 50.5 | -1.0094
1445.8 | 50.5 | -1.0094
1445.9 | 50.5 | -1.0094
1446 | 50.5 | -1.0094
1446.1 | 50.5 | -1.0094
1446.2 | 50.5 | -1.0094
1446.3 | 50.5 | -1.0094
1446.4 | 50.5 | -1.0094
1446.5 | 50.5 | -1.0094
1446.6 | 50.5 | -1.0094
1446.7 | 50.5 | -1.0094
1446.8 | 50.5 | -1.0094
1446.9 | 50.5 | -1.0094
1447 | 50.5 | -1.0094
1447.1 | 50.5 | -1.0094
1447.2 | 50.5 | -1.0094
1447.3 | 50.5 | -1.0094
1447.4 | 50.5 | -1.0094
1447.5 | 50.5 | -1.0094
1447.6 | 50.5 | -1.0096
1447.7 | 50.5 | -1.0096
1447.8 | 50.5 | -1.0096
1447.9 | 50.5 | -1.0096
1448 | 50.5 | -1.0096
1448.1 | 50.5 | -1.0096
1448.2 | 50.5 | -1.0096
1448.3 | 50.5 | -1.0096
1448.4 | 50.5 | -1.0096
1448.5 | 50.5 | -1.0096
1448.6 | 50.5 | -1.0096
1448.7 | 50.5 | -1.0096
1448.8 | 50.5 | -1.0096
1448.9 | 50.5 | -1.0096
1449 | 50.5 | -1.0096
1449.1 | 50.5 | -1.0096
1449.2 | 50.5 | -1.0096
1449.3 | 50.5 | -1.0096
1449.4 | 50.5 | -1.0096
1449.5 | 50.5 | -1.0096
1449.6 | 50.5 | -1.0096
1449.7 | 50.5 | -1.0096
1449.8 | 50.5 | -1.0096
1449.9 | 50.5 | -1.0096
1450 | 50.5 | -1.0096
1450.1 | 50.5 | -1.0096
1450.2 | 50.5 | -1.0096
1450.3 | 50.5 | -1.0096
1450.4 | 50.5 | -1.0096
1450.5 | 50.5 | -1.0096
1450.6 | 50.5 | -1.0096
1450.7 | 50.5 | -1.0096
1450.8 | 50.5 | -1.0096
1450.9 | 50.5 | -1.0096
1451 | 50.5 | -1.0096
1451.1 | 50.5 | -1.0096
1451.2 | 50.5 | -1.0096
1451.3 | 50.5 | -1.0094
1451.4 | 50.5 | -1.0094
1451.5 | 50.5 | -1.0094
1451.6 | 50.5 | -1.0096
1451.7 | 50.5 | -1.0096
1451.8 | 50.5 | -1.0096
1451.9 | 50.5 | -1.0096
1452 | 50.5 | -1.0096
1452.1 | 50.5 | -1.0096
1452.2 | 50.5 | -1.0096
1452.3 | 50.5 | -1.0096
1452.4 | 50.5 | -1.0096
1452.5 | 50.5 | -1.0096
1452.6 | 50.5 | -1.0096
1452.7 | 50.5 | -1.0096
1452.8 | 50.5 | -1.0094
1452.9 | 50.5 | -1.0094
1453 | 50.5 | -1.0094
1453.1 | 50.5 | -1.0094
1453.2 | 50.5 | -1.0094
1453.3 | 50.5 | -1.0094
1453.4 | 50.5 | -1.0096
1453.5 | 50.5 | -1.0096
1453.6 | 50.5 | -1.0096
1453.7 | 50.5 | -1.0096
1453.8 | 50.5 | -1.0096
1453.9 | 50.5 | -1.0096
1454 | 50.5 | -1.0096
1454.1 | 50.5 | -1.0096
1454.2 | 50.5 | -1.0096
1454.3 | 50.5 | -1.0096
1454.4 | 50.5 | -1.0096
1454.5 | 50.5 | -1.0096
1454.6 | 50.5 | -1.0096
1454.7 | 50.5 | -1.0096
1454.8 | 50.5 | -1.0096
1454.9 | 50.5 | -1.0096
1455 | 50.5 | -1.0096
1455.1 | 50.5 | -1.0096
1455.2 | 50.5 | -1.0096
1455.3 | 50.5 | -1.0096
1455.4 | 50.5 | -1.0096
1455.5 | 50.5 | -1.0096
1455.6 | 50.5 | -1.0096
1455.7 | 50.5 | -1.0096
1455.8 | 50.5 | -1.0096
1455.9 | 50.5 | -1.0096
1456 | 50.5 | -1.0096
1456.1 | 50.5 | -1.0096
1456.2 | 50.5 | -1.0096
1456.3 | 50.5 | -1.0096
1456.4 | 50.5 | -1.0096
1456.5 | 50.5 | -1.0096
1456.6 | 50.5 | -1.0096
1456.7 | 50.5 | -1.0096
1456.8 | 50.5 | -1.0096
1456.9 | 50.5 | -1.0096
1457 | 50.5 | -1.0096
1457.1 | 50.5 | -1.0096
1457.2 | 50.5 | -1.0096
1457.3 | 50.5 | -1.0096
1457.4 | 50.5 | -1.0096
1457.5 | 50.5 | -1.0096
1457.6 | 50.5 | -1.0096
1457.7 | 50.5 | -1.0096
1457.8 | 50.5 | -1.0096
1457.9 | 50.5 | -1.0096
1458 | 50.5 | -1.0096
1458.1 | 50.5 | -1.0096
1458.2 | 50.5 | -1.0096
1458.3 | 50.5 | -1.0096
1458.4 | 50.5 | -1.0096
1458.5 | 50.5 | -1.0096
1458.6 | 50.5 | -1.0096
1458.7 | 50.5 | -1.0096
1458.8 | 50.5 | -1.0096
1458.9 | 50.5 | -1.0096
1459 | 50.5 | -1.0096
1459.1 | 50.5 | -1.0096
1459.2 | 50.5 | -1.0096
1459.3 | 50.5 | -1.0096
1459.4 | 50.5 | -1.0096
1459.5 | 50.5 | -1.0096
1459.6 | 50.5 | -1.0096
1459.7 | 50.5 | -1.0096
1459.8 | 50.5 | -1.0096
1459.9 | 50.5 | -1.0096
1460 | 50.5 | -1.0096
1460.1 | 50.5 | -1.0096
1460.2 | 50.5 | -1.0096
1460.3 | 50.5 | -1.0096
1460.4 | 50.5 | -1.0096
1460.5 | 50.5 | -1.0096
1460.6 | 50.5 | -1.0096
1460.7 | 50.5 | -1.0096
1460.8 | 50.5 | -1.0096
1460.9 | 50.5 | -1.0096
1461 | 50.5 | -1.0094
1461.1 | 50.5 | -1.0094
1461.2 | 50.5 | -1.0094
1461.3 | 50.5 | -1.0094
1461.4 | 50.5 | -1.0094
1461.5 | 50.5 | -1.0094
1461.6 | 50.5 | -1.0094
1461.7 | 50.5 | -1.0094
1461.8 | 50.5 | -1.0094
1461.9 | 50.5 | -1.0094
1462 | 50.5 | -1.0094
1462.1 | 50.5 | -1.0096
1462.2 | 50.5 | -1.0096
1462.3 | 50.5 | -1.0096
1462.4 | 50.5 | -1.0096
1462.5 | 50.5 | -1.0096
1462.6 | 50.5 | -1.0096
1462.7 | 50.5 | -1.0096
1462.8 | 50.5 | -1.0096
1462.9 | 50.5 | -1.0096
1463 | 50.5 | -1.0096
1463.1 | 50.5 | -1.0096
1463.2 | 50.5 | -1.0096
1463.3 | 50.5 | -1.0096
1463.4 | 50.5 | -1.0096
1463.5 | 50.5 | -1.0096
1463.6 | 50.5 | -1.0096
1463.7 | 50.5 | -1.0096
1463.8 | 50.5 | -1.0096
1463.9 | 50.5 | -1.0096
1464 | 50.5 | -1.0096
1464.1 | 50.5 | -1.0096
1464.2 | 50.5 | -1.0096
1464.3 | 50.5 | -1.0096
1464.4 | 50.5 | -1.0096
1464.5 | 50.5 | -1.0096
1464.6 | 50.5 | -1.0096
1464.7 | 50.5 | -1.0096
1464.8 | 50.5 | -1.0096
1464.9 | 50.5 | -1.0096
1465 | 50.5 | -1.0096
1465.1 | 50.5 | -1.0096
1465.2 | 50.5 | -1.0096
1465.3 | 50.5 | -1.0096
1465.4 | 50.5 | -1.0096
1465.5 | 50.5 | -1.0096
1465.6 | 50.5 | -1.0096
1465.7 | 50.5 | -1.0096
1465.8 | 50.5 | -1.0096
1465.9 | 50.5 | -1.0096
1466 | 50.5 | -1.0096
1466.1 | 50.5 | -1.0096
1466.2 | 50.5 | -1.0096
1466.3 | 50.5 | -1.0096
1466.4 | 50.5 | -1.0096
1466.5 | 50.5 | -1.0096
1466.6 | 50.5 | -1.0096
1466.7 | 50.5 | -1.0096
1466.8 | 50.5 | -1.0096
1466.9 | 50.5 | -1.0096
1467 | 50.5 | -1.0096
1467.1 | 50.5 | -1.0096
1467.2 | 50.5 | -1.0096
1467.3 | 50.5 | -1.0096
1467.4 | 50.5 | -1.0096
1467.5 | 50.5 | -1.0096
1467.6 | 50.5 | -1.0096
1467.7 | 50.5 | -1.0096
1467.8 | 50.5 | -1.0096
1467.9 | 50.5 | -1.0096
1468 | 50.5 | -1.0096
1468.1 | 50.5 | -1.0096
1468.2 | 50.5 | -1.0096
1468.3 | 50.5 | -1.0096
1468.4 | 50.5 | -1.0096
1468.5 | 50.5 | -1.0096
1468.6 | 50.5 | -1.0096
1468.7 | 50.5 | -1.0094
1468.8 | 50.5 | -1.0094
1468.9 | 50.5 | -1.0094
1469 | 50.5 | -1.0094
1469.1 | 50.5 | -1.0094
1469.2 | 50.5 | -1.0094
1469.3 | 50.5 | -1.0094
1469.4 | 50.5 | -1.0094
1469.5 | 50.5 | -1.0094
1469.6 | 50.5 | -1.0094
1469.7 | 50.5 | -1.0094
1469.8 | 50.5 | -1.0094
1469.9 | 50.5 | -1.0094
1470 | 50.5 | -1.0094
1470.1 | 50.5 | -1.0094
1470.2 | 50.5 | -1.0094
1470.3 | 50.5 | -1.0094
1470.4 | 50.5 | -1.0094
1470.5 | 50.5 | -1.0094
1470.6 | 50.5 | -1.0094
1470.7 | 50.5 | -1.0094
1470.8 | 50.5 | -1.0094
1470.9 | 50.5 | -1.0094
1471 | 50.5 | -1.0094
1471.1 | 50.5 | -1.0094
1471.2 | 50.5 | -1.0094
1471.3 | 50.5 | -1.0094
1471.4 | 50.5 | -1.0094
1471.5 | 50.5 | -1.0094
1471.6 | 50.5 | -1.0094
1471.7 | 50.5 | -1.0094
1471.8 | 50.5 | -1.0094
1471.9 | 50.5 | -1.0094
1472 | 50.5 | -1.0096
1472.1 | 50.5 | -1.0096
1472.2 | 50.5 | -1.0096
1472.3 | 50.5 | -1.0096
1472.4 | 50.5 | -1.0096
1472.5 | 50.5 | -1.0096
1472.6 | 50.5 | -1.0096
1472.7 | 50.5 | -1.0096
1472.8 | 50.5 | -1.0096
1472.9 | 50.5 | -1.0096
1473 | 50.5 | -1.0096
1473.1 | 50.5 | -1.0096
1473.2 | 50.5 | -1.0096
1473.3 | 50.5 | -1.0096
1473.4 | 50.5 | -1.0096
1473.5 | 50.5 | -1.0096
1473.6 | 50.5 | -1.0096
1473.7 | 50.5 | -1.0096
1473.8 | 50.5 | -1.0096
1473.9 | 50.5 | -1.0096
1474 | 50.5 | -1.0096
1474.1 | 50.5 | -1.0096
1474.2 | 50.5 | -1.0096
1474.3 | 50.5 | -1.0096
1474.4 | 50.5 | -1.0096
1474.5 | 50.5 | -1.0094
1474.6 | 50.5 | -1.0094
1474.7 | 50.5 | -1.0094
1474.8 | 50.5 | -1.0094
1474.9 | 50.5 | -1.0094
1475 | 50.5 | -1.0094
1475.1 | 50.5 | -1.0094
1475.2 | 50.5 | -1.0094
1475.3 | 50.5 | -1.0094
1475.4 | 50.5 | -1.0094
1475.5 | 50.5 | -1.0094
1475.6 | 50.5 | -1.0094
1475.7 | 50.5 | -1.0094
1475.8 | 50.5 | -1.0094
1475.9 | 50.5 | -1.0094
1476 | 50.5 | -1.0094
1476.1 | 50.5 | -1.0094
1476.2 | 50.5 | -1.0094
1476.3 | 50.5 | -1.0094
1476.4 | 50.5 | -1.0094
1476.5 | 50.5 | -1.0094
1476.6 | 50.5 | -1.0094
1476.7 | 50.5 | -1.0094
1476.8 | 50.5 | -1.0094
1476.9 | 50.5 | -1.0094
1477 | 50.5 | -1.0094
1477.1 | 50.5 | -1.0094
1477.2 | 50.5 | -1.0094
1477.3 | 50.5 | -1.0094
1477.4 | 50.5 | -1.0094
1477.5 | 50.5 | -1.0094
1477.6 | 50.5 | -1.0094
1477.7 | 50.5 | -1.0094
1477.8 | 50.5 | -1.0094
1477.9 | 50.5 | -1.0094
1478 | 50.5 | -1.0096
1478.1 | 50.5 | -1.0096
1478.2 | 50.5 | -1.0096
1478.3 | 50.5 | -1.0096
1478.4 | 50.5 | -1.0096
1478.5 | 50.5 | -1.0096
1478.6 | 50.5 | -1.0096
1478.7 | 50.5 | -1.0096
1478.8 | 50.5 | -1.0096
1478.9 | 50.5 | -1.0096
1479 | 50.5 | -1.0096
1479.1 | 50.5 | -1.0096
1479.2 | 50.5 | -1.0096
1479.3 | 50.5 | -1.0096
1479.4 | 50.5 | -1.0096
1479.5 | 50.5 | -1.0096
1479.6 | 50.5 | -1.0096
1479.7 | 50.5 | -1.0096
1479.8 | 50.5 | -1.0096
1479.9 | 50.5 | -1.0096
1480 | 50.5 | -1.0096
1480.1 | 50.5 | -1.0096
1480.2 | 50.5 | -1.0096
1480.3 | 50.5 | -1.0096
1480.4 | 50.5 | -1.0096
1480.5 | 50.5 | -1.0096
1480.6 | 50.5 | -1.0096
1480.7 | 50.5 | -1.0096
1480.8 | 50.5 | -1.0096
1480.9 | 50.5 | -1.0096
1481 | 50.5 | -1.0096
1481.1 | 50.5 | -1.0096
1481.2 | 50.5 | -1.0096
1481.3 | 50.5 | -1.0096
1481.4 | 50.5 | -1.0096
1481.5 | 50.5 | -1.0096
1481.6 | 50.5 | -1.0096
1481.7 | 50.5 | -1.0096
1481.8 | 50.5 | -1.0096
1481.9 | 50.5 | -1.0096
1482 | 50.5 | -1.0096
1482.1 | 50.5 | -1.0096
1482.2 | 50.5 | -1.0096
1482.3 | 50.5 | -1.0096
1482.4 | 50.5 | -1.0096
1482.5 | 50.5 | -1.0096
1482.6 | 50.5 | -1.0096
1482.7 | 50.5 | -1.0096
1482.8 | 50.5 | -1.0096
1482.9 | 50.5 | -1.0096
1483 | 50.5 | -1.0096
1483.1 | 50.5 | -1.0096
1483.2 | 50.5 | -1.0096
1483.3 | 50.5 | -1.0096
1483.4 | 50.5 | -1.0096
1483.5 | 50.5 | -1.0096
1483.6 | 50.5 | -1.0096
1483.7 | 50.5 | -1.0096
1483.8 | 50.5 | -1.0096
1483.9 | 50.5 | -1.0096
1484 | 50.5 | -1.0096
1484.1 | 50.5 | -1.0096
1484.2 | 50.5 | -1.0096
1484.3 | 50.5 | -1.0096
1484.4 | 50.5 | -1.0094
1484.5 | 50.5 | -1.0094
1484.6 | 50.5 | -1.0094
1484.7 | 50.5 | -1.0094
1484.8 | 50.5 | -1.0094
1484.9 | 50.5 | -1.0094
1485 | 50.5 | -1.0094
1485.1 | 50.5 | -1.0094
1485.2 | 50.5 | -1.0094
1485.3 | 50.5 | -1.0094
1485.4 | 50.5 | -1.0094
1485.5 | 50.5 | -1.0094
1485.6 | 50.5 | -1.0094
1485.7 | 50.5 | -1.0094
1485.8 | 50.5 | -1.0094
1485.9 | 50.5 | -1.0094
1486 | 50.5 | -1.0094
1486.1 | 50.5 | -1.0094
1486.2 | 50.5 | -1.0094
1486.3 | 50.5 | -1.0094
1486.4 | 50.5 | -1.0094
1486.5 | 50.5 | -1.0094
1486.6 | 50.5 | -1.0094
1486.7 | 50.5 | -1.0096
1486.8 | 50.5 | -1.0096
1486.9 | 50.5 | -1.0096
1487 | 50.5 | -1.0096
1487.1 | 50.5 | -1.0096
1487.2 | 50.5 | -1.0096
1487.3 | 50.5 | -1.0096
1487.4 | 50.5 | -1.0096
1487.5 | 50.5 | -1.0096
1487.6 | 50.5 | -1.0096
1487.7 | 50.5 | -1.0096
1487.8 | 50.5 | -1.0096
1487.9 | 50.5 | -1.0096
1488 | 50.5 | -1.0096
1488.1 | 50.5 | -1.0096
1488.2 | 50.5 | -1.0096
1488.3 | 50.5 | -1.0094
1488.4 | 50.5 | -1.0094
1488.5 | 50.5 | -1.0094
1488.6 | 50.5 | -1.0094
1488.7 | 50.5 | -1.0094
1488.8 | 50.5 | -1.0094
1488.9 | 50.5 | -1.0094
1489 | 50.5 | -1.0094
1489.1 | 50.5 | -1.0094
1489.2 | 50.5 | -1.0094
1489.3 | 50.5 | -1.0094
1489.4 | 50.5 | -1.0094
1489.5 | 50.5 | -1.0094
1489.6 | 50.5 | -1.0094
1489.7 | 50.5 | -1.0094
1489.8 | 50.5 | -1.0094
1489.9 | 50.5 | -1.0094
1490 | 50.5 | -1.0094
1490.1 | 50.5 | -1.0094
1490.2 | 50.5 | -1.0094
1490.3 | 50.5 | -1.0094
1490.4 | 50.5 | -1.0096
1490.5 | 50.5 | -1.0096
1490.6 | 50.5 | -1.0096
1490.7 | 50.5 | -1.0096
1490.8 | 50.5 | -1.0096
1490.9 | 50.5 | -1.0096
1491 | 50.5 | -1.0096
1491.1 | 50.5 | -1.0096
1491.2 | 50.5 | -1.0096
1491.3 | 50.5 | -1.0096
1491.4 | 50.5 | -1.0096
1491.5 | 50.5 | -1.0096
1491.6 | 50.5 | -1.0096
1491.7 | 50.5 | -1.0096
1491.8 | 50.5 | -1.0096
1491.9 | 50.5 | -1.0096
1492 | 50.5 | -1.0096
1492.1 | 50.5 | -1.0096
1492.2 | 50.5 | -1.0096
1492.3 | 50.5 | -1.0096
1492.4 | 50.5 | -1.0096
1492.5 | 50.5 | -1.0096
1492.6 | 50.5 | -1.0096
1492.7 | 50.5 | -1.0096
1492.8 | 50.5 | -1.0096
1492.9 | 50.5 | -1.0096
1493 | 50.5 | -1.0096
1493.1 | 50.5 | -1.0096
1493.2 | 50.5 | -1.0096
1493.3 | 50.5 | -1.0096
1493.4 | 50.5 | -1.0096
1493.5 | 50.5 | -1.0096
1493.6 | 50.5 | -1.0096
1493.7 | 50.5 | -1.0096
1493.8 | 50.5 | -1.0096
1493.9 | 50.5 | -1.0096
1494 | 50.5 | -1.0096
1494.1 | 50.5 | -1.0096
1494.2 | 50.5 | -1.0096
1494.3 | 50.5 | -1.0096
1494.4 | 50.5 | -1.0096
1494.5 | 50.5 | -1.0096
1494.6 | 50.5 | -1.0096
1494.7 | 50.5 | -1.0096
1494.8 | 50.5 | -1.0096
1494.9 | 50.5 | -1.0096
1495 | 50.5 | -1.0094
1495.1 | 50.5 | -1.0094
1495.2 | 50.5 | -1.0094
1495.3 | 50.5 | -1.0094
1495.4 | 50.5 | -1.0094
1495.5 | 50.5 | -1.0094
1495.6 | 50.5 | -1.0094
1495.7 | 50.5 | -1.0094
1495.8 | 50.5 | -1.0094
1495.9 | 50.5 | -1.0094
1496 | 50.5 | -1.0094
1496.1 | 50.5 | -1.0094
1496.2 | 50.5 | -1.0094
1496.3 | 50.5 | -1.0094
1496.4 | 50.5 | -1.0096
1496.5 | 50.5 | -1.0096
1496.6 | 50.5 | -1.0096
1496.7 | 50.5 | -1.0096
1496.8 | 50.5 | -1.0096
1496.9 | 50.5 | -1.0096
1497 | 50.5 | -1.0096
1497.1 | 50.5 | -1.0096
1497.2 | 50.5 | -1.0096
1497.3 | 50.5 | -1.0096
1497.4 | 50.5 | -1.0096
1497.5 | 50.5 | -1.0096
1497.6 | 50.5 | -1.0096
1497.7 | 50.5 | -1.0096
1497.8 | 50.5 | -1.0096
1497.9 | 50.5 | -1.0096
1498 | 50.5 | -1.0096
1498.1 | 50.5 | -1.0096
1498.2 | 50.5 | -1.0096
1498.3 | 50.5 | -1.0096
1498.4 | 50.5 | -1.0096
1498.5 | 50.5 | -1.0096
1498.6 | 50.5 | -1.0096
1498.7 | 50.5 | -1.0096
1498.8 | 50.5 | -1.0096
1498.9 | 50.5 | -1.0096
1499 | 50.5 | -1.0096
1499.1 | 50.5 | -1.0096
1499.2 | 50.5 | -1.0096
1499.3 | 50.5 | -1.0096
1499.4 | 50.5 | -1.0096
1499.5 | 50.5 | -1.0096
1499.6 | 50.5 | -1.0096
1499.7 | 50.5 | -1.0096
1499.8 | 50.5 | -1.0096
1499.9 | 50.5 | -1.0096
1500 | 50.5 | -1.0096
1500.1 | 50.5 | -1.0096
1500.2 | 50.5 | -1.0096
1500.3 | 50.5 | -1.0096
1500.4 | 50.5 | -1.0096
1500.5 | 50.5 | -1.0096
1500.6 | 50.5 | -1.0096
1500.7 | 50.5 | -1.0096
1500.8 | 50.5 | -1.0096
1500.9 | 50.5 | -1.0096
1501 | 50.5 | -1.0096
1501.1 | 50.5 | -1.0096
1501.2 | 50.5 | -1.0096
1501.3 | 50.5 | -1.0096
1501.4 | 50.5 | -1.0096
1501.5 | 50.5 | -1.0096
1501.6 | 50.5 | -1.0096
1501.7 | 50.5 | -1.0096
1501.8 | 50.5 | -1.0096
1501.9 | 50.5 | -1.0096
1502 | 50.5 | -1.0096
1502.1 | 50.5 | -1.0096
1502.2 | 50.5 | -1.0096
1502.3 | 50.5 | -1.0096
1502.4 | 50.5 | -1.0096
1502.5 | 50.5 | -1.0096
1502.6 | 50.5 | -1.0096
1502.7 | 50.5 | -1.0096
1502.8 | 50.5 | -1.0096
1502.9 | 50.5 | -1.0096
1503 | 50.5 | -1.0096
1503.1 | 50.5 | -1.0096
1503.2 | 50.5 | -1.0096
1503.3 | 50.5 | -1.0096
1503.4 | 50.5 | -1.0096
1503.5 | 50.5 | -1.0096
1503.6 | 50.5 | -1.0096
1503.7 | 50.5 | -1.0096
1503.8 | 50.5 | -1.0096
1503.9 | 50.5 | -1.0096
1504 | 50.5 | -1.0096
1504.1 | 50.5 | -1.0096
1504.2 | 50.5 | -1.0096
1504.3 | 50.5 | -1.0096
1504.4 | 50.5 | -1.0096
1504.5 | 50.5 | -1.0096
1504.6 | 50.5 | -1.0096
1504.7 | 50.5 | -1.0096
1504.8 | 50.5 | -1.0096
1504.9 | 50.5 | -1.0096
1505 | 50.5 | -1.0096
1505.1 | 50.5 | -1.0096
1505.2 | 50.5 | -1.0096
1505.3 | 50.5 | -1.0096
1505.4 | 50.5 | -1.0096
1505.5 | 50.5 | -1.0096
1505.6 | 50.5 | -1.0096
1505.7 | 50.5 | -1.0096
1505.8 | 50.5 | -1.0096
1505.9 | 50.5 | -1.0096
1506 | 50.5 | -1.0096
1506.1 | 50.5 | -1.0096
1506.2 | 50.5 | -1.0096
1506.3 | 50.5 | -1.0096
1506.4 | 50.5 | -1.0096
1506.5 | 50.5 | -1.0096
1506.6 | 50.5 | -1.0096
1506.7 | 50.5 | -1.0096
1506.8 | 50.5 | -1.0096
1506.9 | 50.5 | -1.0096
1507 | 50.5 | -1.0096
1507.1 | 50.5 | -1.0096
1507.2 | 50.5 | -1.0096
1507.3 | 50.5 | -1.0096
1507.4 | 50.5 | -1.0096
1507.5 | 50.5 | -1.0096
1507.6 | 50.5 | -1.0096
1507.7 | 50.5 | -1.0096
1507.8 | 50.5 | -1.0096
1507.9 | 50.5 | -1.0096
1508 | 50.5 | -1.0096
1508.1 | 50.5 | -1.0096
1508.2 | 50.5 | -1.0096
1508.3 | 50.5 | -1.0096
1508.4 | 50.5 | -1.0096
1508.5 | 50.5 | -1.0096
1508.6 | 50.5 | -1.0096
1508.7 | 50.5 | -1.0096
1508.8 | 50.5 | -1.0096
1508.9 | 50.5 | -1.0096
1509 | 50.5 | -1.0096
1509.1 | 50.5 | -1.0096
1509.2 | 50.5 | -1.0098
1509.3 | 50.5 | -1.0096
1509.4 | 50.5 | -1.0096
1509.5 | 50.5 | -1.0096
1509.6 | 50.5 | -1.0096
1509.7 | 50.5 | -1.0096
1509.8 | 50.5 | -1.0096
1509.9 | 50.5 | -1.0096
1510 | 50.5 | -1.0096
1510.1 | 50.5 | -1.0096
1510.2 | 50.5 | -1.0096
1510.3 | 50.5 | -1.0096
1510.4 | 50.5 | -1.0096
1510.5 | 50.5 | -1.0096
1510.6 | 50.5 | -1.0096
1510.7 | 50.5 | -1.0096
1510.8 | 50.5 | -1.0096
1510.9 | 50.5 | -1.0096
1511 | 50.5 | -1.0096
1511.1 | 50.5 | -1.0096
1511.2 | 50.5 | -1.0096
1511.3 | 50.5 | -1.0096
1511.4 | 50.5 | -1.0096
1511.5 | 50.5 | -1.0096
1511.6 | 50.5 | -1.0096
1511.7 | 50.5 | -1.0094
1511.8 | 50.5 | -1.0094
1511.9 | 50.5 | -1.0094
1512 | 50.5 | -1.0094
1512.1 | 50.5 | -1.0094
1512.2 | 50.5 | -1.0094
1512.3 | 50.5 | -1.0094
1512.4 | 50.5 | -1.0094
1512.5 | 50.5 | -1.0094
1512.6 | 50.5 | -1.0094
1512.7 | 50.5 | -1.0094
1512.8 | 50.5 | -1.0094
1512.9 | 50.5 | -1.0094
1513 | 50.5 | -1.0094
1513.1 | 50.5 | -1.0094
1513.2 | 50.5 | -1.0094
1513.3 | 50.5 | -1.0094
1513.4 | 50.5 | -1.0094
1513.5 | 50.5 | -1.0094
1513.6 | 50.5 | -1.0094
1513.7 | 50.5 | -1.0094
1513.8 | 50.5 | -1.0094
1513.9 | 50.5 | -1.0094
1514 | 50.5 | -1.0096
1514.1 | 50.5 | -1.0096
1514.2 | 50.5 | -1.0096
1514.3 | 50.5 | -1.0096
1514.4 | 50.5 | -1.0096
1514.5 | 50.5 | -1.0096
1514.6 | 50.5 | -1.0096
1514.7 | 50.5 | -1.0096
1514.8 | 50.5 | -1.0096
1514.9 | 50.5 | -1.0096
1515 | 50.5 | -1.0096
1515.1 | 50.5 | -1.0096
1515.2 | 50.5 | -1.0096
1515.3 | 50.5 | -1.0096
1515.4 | 50.5 | -1.0096
1515.5 | 50.5 | -1.0096
1515.6 | 50.5 | -1.0096
1515.7 | 50.5 | -1.0096
1515.8 | 50.5 | -1.0096
1515.9 | 50.5 | -1.0096
1516 | 50.5 | -1.0096
1516.1 | 50.5 | -1.0096
1516.2 | 50.5 | -1.0096
1516.3 | 50.5 | -1.0096
1516.4 | 50.5 | -1.0096
1516.5 | 50.5 | -1.0096
1516.6 | 50.5 | -1.0096
1516.7 | 50.5 | -1.0096
1516.8 | 50.5 | -1.0096
1516.9 | 50.5 | -1.0096
1517 | 50.5 | -1.0096
1517.1 | 50.5 | -1.0096
1517.2 | 50.5 | -1.0096
1517.3 | 50.5 | -1.0096
1517.4 | 50.5 | -1.0096
1517.5 | 50.5 | -1.0096
1517.6 | 50.5 | -1.0096
1517.7 | 50.5 | -1.0096
1517.8 | 50.5 | -1.0096
1517.9 | 50.5 | -1.0096
1518 | 50.5 | -1.0096
1518.1 | 50.5 | -1.0096
1518.2 | 50.5 | -1.0096
1518.3 | 50.5 | -1.0096
1518.4 | 50.5 | -1.0096
1518.5 | 50.5 | -1.0096
1518.6 | 50.5 | -1.0094
1518.7 | 50.5 | -1.0094
1518.8 | 50.5 | -1.0094
1518.9 | 50.5 | -1.0094
1519 | 50.5 | -1.0094
1519.1 | 50.5 | -1.0094
1519.2 | 50.5 | -1.0094
1519.3 | 50.5 | -1.0094
1519.4 | 50.5 | -1.0094
1519.5 | 50.5 | -1.0094
1519.6 | 50.5 | -1.0094
1519.7 | 50.5 | -1.0094
1519.8 | 50.5 | -1.0094
1519.9 | 50.5 | -1.0094
1520 | 50.5 | -1.0094
1520.1 | 50.5 | -1.0094
1520.2 | 50.5 | -1.0094
1520.3 | 50.5 | -1.0094
1520.4 | 50.5 | -1.0094
1520.5 | 50.5 | -1.0094
1520.6 | 50.5 | -1.0094
1520.7 | 50.5 | -1.0094
1520.8 | 50.5 | -1.0096
1520.9 | 50.5 | -1.0096
1521 | 50.5 | -1.0096
1521.1 | 50.5 | -1.0096
1521.2 | 50.5 | -1.0096
1521.3 | 50.5 | -1.0096
1521.4 | 50.5 | -1.0096
1521.5 | 50.5 | -1.0096
1521.6 | 50.5 | -1.0096
1521.7 | 50.5 | -1.0096
1521.8 | 50.5 | -1.0096
1521.9 | 50.5 | -1.0096
1522 | 50.5 | -1.0096
1522.1 | 50.5 | -1.0096
1522.2 | 50.5 | -1.0096
1522.3 | 50.5 | -1.0096
1522.4 | 50.5 | -1.0096
1522.5 | 50.5 | -1.0096
1522.6 | 50.5 | -1.0096
1522.7 | 50.5 | -1.0096
1522.8 | 50.5 | -1.0096
1522.9 | 50.5 | -1.0096
1523 | 50.5 | -1.0096
1523.1 | 50.5 | -1.0096
1523.2 | 50.5 | -1.0096
1523.3 | 50.5 | -1.0096
1523.4 | 50.5 | -1.0096
1523.5 | 50.5 | -1.0096
1523.6 | 50.5 | -1.0096
1523.7 | 50.5 | -1.0096
1523.8 | 50.5 | -1.0096
1523.9 | 50.5 | -1.0096
1524 | 50.5 | -1.0096
1524.1 | 50.5 | -1.0096
1524.2 | 50.5 | -1.0096
1524.3 | 50.5 | -1.0096
1524.4 | 50.5 | -1.0096
1524.5 | 50.5 | -1.0096
1524.6 | 50.5 | -1.0096
1524.7 | 50.5 | -1.0096
1524.8 | 50.5 | -1.0096
1524.9 | 50.5 | -1.0096
1525 | 50.5 | -1.0096
1525.1 | 50.5 | -1.0096
1525.2 | 50.5 | -1.0096
1525.3 | 50.5 | -1.0096
1525.4 | 50.5 | -1.0096
1525.5 | 50.5 | -1.0096
1525.6 | 50.5 | -1.0096
1525.7 | 50.5 | -1.0094
1525.8 | 50.5 | -1.0094
1525.9 | 50.5 | -1.0094
1526 | 50.5 | -1.0094
1526.1 | 50.5 | -1.0094
1526.2 | 50.5 | -1.0094
1526.3 | 50.5 | -1.0094
1526.4 | 50.5 | -1.0094
1526.5 | 50.5 | -1.0094
1526.6 | 50.5 | -1.0094
1526.7 | 50.5 | -1.0094
1526.8 | 50.5 | -1.0094
1526.9 | 50.5 | -1.0094
1527 | 50.5 | -1.0094
1527.1 | 50.5 | -1.0094
1527.2 | 50.5 | -1.0094
1527.3 | 50.5 | -1.0094
1527.4 | 50.5 | -1.0094
1527.5 | 50.5 | -1.0094
1527.6 | 50.5 | -1.0094
1527.7 | 50.5 | -1.0094
1527.8 | 50.5 | -1.0094
1527.9 | 50.5 | -1.0094
1528 | 50.5 | -1.0096
1528.1 | 50.5 | -1.0096
1528.2 | 50.5 | -1.0096
1528.3 | 50.5 | -1.0096
1528.4 | 50.5 | -1.0096
1528.5 | 50.5 | -1.0096
1528.6 | 50.5 | -1.0096
1528.7 | 50.5 | -1.0096
1528.8 | 50.5 | -1.0096
1528.9 | 50.5 | -1.0096
1529 | 50.5 | -1.0096
1529.1 | 50.5 | -1.0096
1529.2 | 50.5 | -1.0096
1529.3 | 50.5 | -1.0096
1529.4 | 50.5 | -1.0094
1529.5 | 50.5 | -1.0094
1529.6 | 50.5 | -1.0094
1529.7 | 50.5 | -1.0094
1529.8 | 50.5 | -1.0094
1529.9 | 50.5 | -1.0094
1530 | 50.5 | -1.0094
1530.1 | 50.5 | -1.0094
1530.2 | 50.5 | -1.0094
1530.3 | 50.5 | -1.0094
1530.4 | 50.5 | -1.0096
1530.5 | 50.5 | -1.0096
1530.6 | 50.5 | -1.0096
1530.7 | 50.5 | -1.0096
1530.8 | 50.5 | -1.0096
1530.9 | 50.5 | -1.0096
1531 | 50.5 | -1.0096
1531.1 | 50.5 | -1.0096
1531.2 | 50.5 | -1.0096
1531.3 | 50.5 | -1.0096
1531.4 | 50.5 | -1.0096
1531.5 | 50.5 | -1.0094
1531.6 | 50.5 | -1.0094
1531.7 | 50.5 | -1.0094
1531.8 | 50.5 | -1.0094
1531.9 | 50.5 | -1.0094
1532 | 50.5 | -1.0094
1532.1 | 50.5 | -1.0094
1532.2 | 50.5 | -1.0094
1532.3 | 50.5 | -1.0094
1532.4 | 50.5 | -1.0094
1532.5 | 50.5 | -1.0094
1532.6 | 50.5 | -1.0096
1532.7 | 50.5 | -1.0096
1532.8 | 50.5 | -1.0096
1532.9 | 50.5 | -1.0096
1533 | 50.5 | -1.0096
1533.1 | 50.5 | -1.0096
1533.2 | 50.5 | -1.0096
1533.3 | 50.5 | -1.0096
1533.4 | 50.5 | -1.0096
1533.5 | 50.5 | -1.0096
1533.6 | 50.5 | -1.0096
1533.7 | 50.5 | -1.0096
1533.8 | 50.5 | -1.0096
1533.9 | 50.5 | -1.0096
1534 | 50.5 | -1.0096
1534.1 | 50.5 | -1.0096
1534.2 | 50.5 | -1.0096
1534.3 | 50.5 | -1.0096
1534.4 | 50.5 | -1.0096
1534.5 | 50.5 | -1.0096
1534.6 | 50.5 | -1.0096
1534.7 | 50.5 | -1.0096
1534.8 | 50.5 | -1.0096
1534.9 | 50.5 | -1.0096
1535 | 50.5 | -1.0094
1535.1 | 50.5 | -1.0094
1535.2 | 50.5 | -1.0094
1535.3 | 50.5 | -1.0094
1535.4 | 50.5 | -1.0094
1535.5 | 50.5 | -1.0094
1535.6 | 50.5 | -1.0094
1535.7 | 50.5 | -1.0094
1535.8 | 50.5 | -1.0094
1535.9 | 50.5 | -1.0094
1536 | 50.5 | -1.0094
1536.1 | 50.5 | -1.0094
1536.2 | 50.5 | -1.0094
1536.3 | 50.5 | -1.0094
1536.4 | 50.5 | -1.0094
1536.5 | 50.5 | -1.0094
1536.6 | 50.5 | -1.0094
1536.7 | 50.5 | -1.0094
1536.8 | 50.5 | -1.0094
1536.9 | 50.5 | -1.0094
1537 | 50.5 | -1.0094
1537.1 | 50.5 | -1.0094
1537.2 | 50.5 | -1.0094
1537.3 | 50.5 | -1.0094
1537.4 | 50.5 | -1.0094
1537.5 | 50.5 | -1.0094
1537.6 | 50.5 | -1.0094
1537.7 | 50.5 | -1.0094
1537.8 | 50.5 | -1.0094
1537.9 | 50.5 | -1.0094
1538 | 50.5 | -1.0094
1538.1 | 50.5 | -1.0094
1538.2 | 50.5 | -1.0094
1538.3 | 50.5 | -1.0094
1538.4 | 50.5 | -1.0096
1538.5 | 50.5 | -1.0096
1538.6 | 50.5 | -1.0096
1538.7 | 50.5 | -1.0096
1538.8 | 50.5 | -1.0096
1538.9 | 50.5 | -1.0096
1539 | 50.5 | -1.0096
1539.1 | 50.5 | -1.0096
1539.2 | 50.5 | -1.0096
1539.3 | 50.5 | -1.0096
1539.4 | 50.5 | -1.0096
1539.5 | 50.5 | -1.0096
1539.6 | 50.5 | -1.0096
1539.7 | 50.5 | -1.0096
1539.8 | 50.5 | -1.0096
1539.9 | 50.5 | -1.0096
1540 | 50.5 | -1.0096
1540.1 | 50.5 | -1.0096
1540.2 | 50.5 | -1.0096
1540.3 | 50.5 | -1.0096
1540.4 | 50.5 | -1.0096
1540.5 | 50.5 | -1.0096
1540.6 | 50.5 | -1.0096
1540.7 | 50.5 | -1.0096
1540.8 | 50.5 | -1.0096
1540.9 | 50.5 | -1.0096
1541 | 50.5 | -1.0096
1541.1 | 50.5 | -1.0096
1541.2 | 50.5 | -1.0096
1541.3 | 50.5 | -1.0096
1541.4 | 50.5 | -1.0096
1541.5 | 50.5 | -1.0096
1541.6 | 50.5 | -1.0096
1541.7 | 50.5 | -1.0096
1541.8 | 50.5 | -1.0096
1541.9 | 50.5 | -1.0096
1542 | 50.5 | -1.0096
1542.1 | 50.5 | -1.0094
1542.2 | 50.5 | -1.0094
1542.3 | 50.5 | -1.0094
1542.4 | 50.5 | -1.0094
1542.5 | 50.5 | -1.0094
1542.6 | 50.5 | -1.0094
1542.7 | 50.5 | -1.0094
1542.8 | 50.5 | -1.0094
1542.9 | 50.5 | -1.0094
1543 | 50.5 | -1.0094
1543.1 | 50.5 | -1.0094
1543.2 | 50.5 | -1.0094
1543.3 | 50.5 | -1.0094
1543.4 | 50.5 | -1.0094
1543.5 | 50.5 | -1.0094
1543.6 | 50.5 | -1.0094
1543.7 | 50.5 | -1.0094
1543.8 | 50.5 | -1.0094
1543.9 | 50.5 | -1.0094
1544 | 50.5 | -1.0094
1544.1 | 50.5 | -1.0094
1544.2 | 50.5 | -1.0094
1544.3 | 50.5 | -1.0096
1544.4 | 50.5 | -1.0096
1544.5 | 50.5 | -1.0096
1544.6 | 50.5 | -1.0096
1544.7 | 50.5 | -1.0096
1544.8 | 50.5 | -1.0096
1544.9 | 50.5 | -1.0096
1545 | 50.5 | -1.0096
1545.1 | 50.5 | -1.0096
1545.2 | 50.5 | -1.0096
1545.3 | 50.5 | -1.0096
1545.4 | 50.5 | -1.0096
1545.5 | 50.5 | -1.0096
1545.6 | 50.5 | -1.0096
1545.7 | 50.5 | -1.0096
1545.8 | 50.5 | -1.0096
1545.9 | 50.5 | -1.0096
1546 | 50.5 | -1.0096
1546.1 | 50.5 | -1.0096
1546.2 | 50.5 | -1.0096
1546.3 | 50.5 | -1.0096
1546.4 | 50.5 | -1.0096
1546.5 | 50.5 | -1.0096
1546.6 | 50.5 | -1.0096
1546.7 | 50.5 | -1.0096
1546.8 | 50.5 | -1.0096
1546.9 | 50.5 | -1.0096
1547 | 50.5 | -1.0096
1547.1 | 50.5 | -1.0096
1547.2 | 50.5 | -1.0096
1547.3 | 50.5 | -1.0096
1547.4 | 50.5 | -1.0096
1547.5 | 50.5 | -1.0096
1547.6 | 50.5 | -1.0096
1547.7 | 50.5 | -1.0094
1547.8 | 50.5 | -1.0094
1547.9 | 50.5 | -1.0094
1548 | 50.5 | -1.0094
1548.1 | 50.5 | -1.0094
1548.2 | 50.5 | -1.0094
1548.3 | 50.5 | -1.0094
1548.4 | 50.5 | -1.0094
1548.5 | 50.5 | -1.0094
1548.6 | 50.5 | -1.0094
1548.7 | 50.5 | -1.0094
1548.8 | 50.5 | -1.0094
1548.9 | 50.5 | -1.0094
1549 | 50.5 | -1.0094
1549.1 | 50.5 | -1.0094
1549.2 | 50.5 | -1.0094
1549.3 | 50.5 | -1.0094
1549.4 | 50.5 | -1.0094
1549.5 | 50.5 | -1.0094
1549.6 | 50.5 | -1.0094
1549.7 | 50.5 | -1.0094
1549.8 | 50.5 | -1.0094
1549.9 | 50.5 | -1.0094
1550 | 50.5 | -1.0096
1550.1 | 50.5 | -1.0096
1550.2 | 50.5 | -1.0096
1550.3 | 50.5 | -1.0096
1550.4 | 50.5 | -1.0096
1550.5 | 50.5 | -1.0096
1550.6 | 50.5 | -1.0096
1550.7 | 50.5 | -1.0096
1550.8 | 50.5 | -1.0096
1550.9 | 50.5 | -1.0096
1551 | 50.5 | -1.0096
1551.1 | 50.5 | -1.0096
1551.2 | 50.5 | -1.0096
1551.3 | 50.5 | -1.0096
1551.4 | 50.5 | -1.0096
1551.5 | 50.5 | -1.0096
1551.6 | 50.5 | -1.0096
1551.7 | 50.5 | -1.0096
1551.8 | 50.5 | -1.0096
1551.9 | 50.5 | -1.0096
1552 | 50.5 | -1.0096
1552.1 | 50.5 | -1.0096
1552.2 | 50.5 | -1.0096
1552.3 | 50.5 | -1.0096
1552.4 | 50.5 | -1.0096
1552.5 | 50.5 | -1.0096
1552.6 | 50.5 | -1.0096
1552.7 | 50.5 | -1.0096
1552.8 | 50.5 | -1.0096
1552.9 | 50.5 | -1.0096
1553 | 50.5 | -1.0096
1553.1 | 50.5 | -1.0096
1553.2 | 50.5 | -1.0096
1553.3 | 50.5 | -1.0096
1553.4 | 50.5 | -1.0096
1553.5 | 50.5 | -1.0096
1553.6 | 50.5 | -1.0096
1553.7 | 50.5 | -1.0096
1553.8 | 50.5 | -1.0096
1553.9 | 50.5 | -1.0096
1554 | 50.5 | -1.0096
1554.1 | 50.5 | -1.0096
1554.2 | 50.5 | -1.0096
1554.3 | 50.5 | -1.0096
1554.4 | 50.5 | -1.0096
1554.5 | 50.5 | -1.0096
1554.6 | 50.5 | -1.0096
1554.7 | 50.5 | -1.0096
1554.8 | 50.5 | -1.0096
1554.9 | 50.5 | -1.0094
1555 | 50.5 | -1.0094
1555.1 | 50.5 | -1.0094
1555.2 | 50.5 | -1.0094
1555.3 | 50.5 | -1.0094
1555.4 | 50.5 | -1.0094
1555.5 | 50.5 | -1.0094
1555.6 | 50.5 | -1.0094
1555.7 | 50.5 | -1.0094
1555.8 | 50.5 | -1.0094
1555.9 | 50.5 | -1.0094
1556 | 50.5 | -1.0096
1556.1 | 50.5 | -1.0096
1556.2 | 50.5 | -1.0096
1556.3 | 50.5 | -1.0096
1556.4 | 50.5 | -1.0096
1556.5 | 50.5 | -1.0096
1556.6 | 50.5 | -1.0096
1556.7 | 50.5 | -1.0096
1556.8 | 50.5 | -1.0096
1556.9 | 50.5 | -1.0096
1557 | 50.5 | -1.0096
1557.1 | 50.5 | -1.0096
1557.2 | 50.5 | -1.0096
1557.3 | 50.5 | -1.0096
1557.4 | 50.5 | -1.0096
1557.5 | 50.5 | -1.0096
1557.6 | 50.5 | -1.0096
1557.7 | 50.5 | -1.0096
1557.8 | 50.5 | -1.0096
1557.9 | 50.5 | -1.0096
1558 | 50.5 | -1.0096
1558.1 | 50.5 | -1.0096
1558.2 | 50.5 | -1.0096
1558.3 | 50.5 | -1.0096
1558.4 | 50.5 | -1.0096
1558.5 | 50.5 | -1.0096
1558.6 | 50.5 | -1.0096
1558.7 | 50.5 | -1.0096
1558.8 | 50.5 | -1.0096
1558.9 | 50.5 | -1.0096
1559 | 50.5 | -1.0096
1559.1 | 50.5 | -1.0096
1559.2 | 50.5 | -1.0096
1559.3 | 50.5 | -1.0096
1559.4 | 50.5 | -1.0096
1559.5 | 50.5 | -1.0096
1559.6 | 50.5 | -1.0096
1559.7 | 50.5 | -1.0096
1559.8 | 50.5 | -1.0096
1559.9 | 50.5 | -1.0096
1560 | 50.5 | -1.0096
1560.1 | 50.5 | -1.0096
1560.2 | 50.5 | -1.0096
1560.3 | 50.5 | -1.0096
1560.4 | 50.5 | -1.0096
1560.5 | 50.5 | -1.0096
1560.6 | 50.5 | -1.0096
1560.7 | 50.5 | -1.0096
1560.8 | 50.5 | -1.0096
1560.9 | 50.5 | -1.0096
1561 | 50.5 | -1.0096
1561.1 | 50.5 | -1.0096
1561.2 | 50.5 | -1.0096
1561.3 | 50.5 | -1.0096
1561.4 | 50.5 | -1.0096
1561.5 | 50.5 | -1.0096
1561.6 | 50.5 | -1.0096
1561.7 | 50.5 | -1.0096
1561.8 | 50.5 | -1.0096
1561.9 | 50.5 | -1.0096
1562 | 50.5 | -1.0096
1562.1 | 50.5 | -1.0096
1562.2 | 50.5 | -1.0096
1562.3 | 50.5 | -1.0096
1562.4 | 50.5 | -1.0096
1562.5 | 50.5 | -1.0096
1562.6 | 50.5 | -1.0096
1562.7 | 50.5 | -1.0096
1562.8 | 50.5 | -1.0096
1562.9 | 50.5 | -1.0096
1563 | 50.5 | -1.0096
1563.1 | 50.5 | -1.0096
1563.2 | 50.5 | -1.0096
1563.3 | 50.5 | -1.0096
1563.4 | 50.5 | -1.0096
1563.5 | 50.5 | -1.0096
1563.6 | 50.5 | -1.0096
1563.7 | 50.5 | -1.0096
1563.8 | 50.5 | -1.0096
1563.9 | 50.5 | -1.0096
1564 | 50.5 | -1.0096
1564.1 | 50.5 | -1.0096
1564.2 | 50.5 | -1.0096
1564.3 | 50.5 | -1.0096
1564.4 | 50.5 | -1.0096
1564.5 | 50.5 | -1.0096
1564.6 | 50.5 | -1.0096
1564.7 | 50.5 | -1.0096
1564.8 | 50.5 | -1.0096
1564.9 | 50.5 | -1.0096
1565 | 50.5 | -1.0096
1565.1 | 50.5 | -1.0096
1565.2 | 50.5 | -1.0096
1565.3 | 50.5 | -1.0096
1565.4 | 50.5 | -1.0096
1565.5 | 50.5 | -1.0096
1565.6 | 50.5 | -1.0096
1565.7 | 50.5 | -1.0096
1565.8 | 50.5 | -1.0096
1565.9 | 50.5 | -1.0096
1566 | 50.5 | -1.0096
1566.1 | 50.5 | -1.0096
1566.2 | 50.5 | -1.0096
1566.3 | 50.5 | -1.0096
1566.4 | 50.5 | -1.0096
1566.5 | 50.5 | -1.0096
1566.6 | 50.5 | -1.0096
1566.7 | 50.5 | -1.0096
1566.8 | 50.5 | -1.0096
1566.9 | 50.5 | -1.0096
1567 | 50.5 | -1.0096
1567.1 | 50.5 | -1.0096
1567.2 | 50.5 | -1.0096
1567.3 | 50.5 | -1.0096
1567.4 | 50.5 | -1.0096
1567.5 | 50.5 | -1.0096
1567.6 | 50.5 | -1.0096
1567.7 | 50.5 | -1.0096
1567.8 | 50.5 | -1.0096
1567.9 | 50.5 | -1.0096
1568 | 50.5 | -1.0096
1568.1 | 50.5 | -1.0096
1568.2 | 50.5 | -1.0096
1568.3 | 50.5 | -1.0096
1568.4 | 50.5 | -1.0096
1568.5 | 50.5 | -1.0096
1568.6 | 50.5 | -1.0096
1568.7 | 50.5 | -1.0094
1568.8 | 50.5 | -1.0094
1568.9 | 50.5 | -1.0094
1569 | 50.5 | -1.0094
1569.1 | 50.5 | -1.0094
1569.2 | 50.5 | -1.0094
1569.3 | 50.5 | -1.0094
1569.4 | 50.5 | -1.0094
1569.5 | 50.5 | -1.0094
1569.6 | 50.5 | -1.0094
1569.7 | 50.5 | -1.0094
1569.8 | 50.5 | -1.0094
1569.9 | 50.5 | -1.0094
1570 | 50.5 | -1.0094
1570.1 | 50.5 | -1.0094
1570.2 | 50.5 | -1.0094
1570.3 | 50.5 | -1.0094
1570.4 | 50.5 | -1.0094
1570.5 | 50.5 | -1.0094
1570.6 | 50.5 | -1.0094
1570.7 | 50.5 | -1.0094
1570.8 | 50.5 | -1.0094
1570.9 | 50.5 | -1.0094
1571 | 50.5 | -1.0094
1571.1 | 50.5 | -1.0094
1571.2 | 50.5 | -1.0096
1571.3 | 50.5 | -1.0096
1571.4 | 50.5 | -1.0096
1571.5 | 50.5 | -1.0096
1571.6 | 50.5 | -1.0096
1571.7 | 50.5 | -1.0096
1571.8 | 50.5 | -1.0096
1571.9 | 50.5 | -1.0096
1572 | 50.5 | -1.0096
1572.1 | 50.5 | -1.0096
1572.2 | 50.5 | -1.0096
1572.3 | 50.5 | -1.0096
1572.4 | 50.5 | -1.0096
1572.5 | 50.5 | -1.0096
1572.6 | 50.5 | -1.0096
1572.7 | 50.5 | -1.0096
1572.8 | 50.5 | -1.0096
1572.9 | 50.5 | -1.0096
1573 | 50.5 | -1.0096
1573.1 | 50.5 | -1.0096
1573.2 | 50.5 | -1.0096
1573.3 | 50.5 | -1.0096
1573.4 | 50.5 | -1.0096
1573.5 | 50.5 | -1.0096
1573.6 | 50.5 | -1.0096
1573.7 | 50.5 | -1.0096
1573.8 | 50.5 | -1.0096
1573.9 | 50.5 | -1.0096
1574 | 50.5 | -1.0096
1574.1 | 50.5 | -1.0096
1574.2 | 50.5 | -1.0096
1574.3 | 50.5 | -1.0096
1574.4 | 50.5 | -1.0096
1574.5 | 50.5 | -1.0096
1574.6 | 50.5 | -1.0096
1574.7 | 50.5 | -1.0096
1574.8 | 50.5 | -1.0096
1574.9 | 50.5 | -1.0096
1575 | 50.5 | -1.0096
1575.1 | 50.5 | -1.0096
1575.2 | 50.5 | -1.0096
1575.3 | 50.5 | -1.0096
1575.4 | 50.5 | -1.0096
1575.5 | 50.5 | -1.0096
1575.6 | 50.5 | -1.0096
1575.7 | 50.5 | -1.0096
1575.8 | 50.5 | -1.0096
1575.9 | 50.5 | -1.0096
1576 | 50.5 | -1.0096
1576.1 | 50.5 | -1.0096
1576.2 | 50.5 | -1.0096
1576.3 | 50.5 | -1.0096
1576.4 | 50.5 | -1.0096
1576.5 | 50.5 | -1.0096
1576.6 | 50.5 | -1.0096
1576.7 | 50.5 | -1.0096
1576.8 | 50.5 | -1.0096
1576.9 | 50.5 | -1.0096
1577 | 50.5 | -1.0096
1577.1 | 50.5 | -1.0096
1577.2 | 50.5 | -1.0096
1577.3 | 50.5 | -1.0096
1577.4 | 50.5 | -1.0096
1577.5 | 50.5 | -1.0096
1577.6 | 50.5 | -1.0096
1577.7 | 50.5 | -1.0096
1577.8 | 50.5 | -1.0096
1577.9 | 50.5 | -1.0096
1578 | 50.5 | -1.0096
1578.1 | 50.5 | -1.0096
1578.2 | 50.5 | -1.0096
1578.3 | 50.5 | -1.0096
1578.4 | 50.5 | -1.0096
1578.5 | 50.5 | -1.0096
1578.6 | 50.5 | -1.0096
1578.7 | 50.5 | -1.0096
1578.8 | 50.5 | -1.0096
1578.9 | 50.5 | -1.0096
1579 | 50.5 | -1.0096
1579.1 | 50.5 | -1.0096
1579.2 | 50.5 | -1.0096
1579.3 | 50.5 | -1.0096
1579.4 | 50.5 | -1.0096
1579.5 | 50.5 | -1.0096
1579.6 | 50.5 | -1.0096
1579.7 | 50.5 | -1.0096
1579.8 | 50.5 | -1.0096
1579.9 | 50.5 | -1.0096
1580 | 50.5 | -1.0096
1580.1 | 50.5 | -1.0096
1580.2 | 50.5 | -1.0096
1580.3 | 50.5 | -1.0096
1580.4 | 50.5 | -1.0096
1580.5 | 50.5 | -1.0096
1580.6 | 50.5 | -1.0096
1580.7 | 50.5 | -1.0096
1580.8 | 50.5 | -1.0096
1580.9 | 50.5 | -1.0096
1581 | 50.5 | -1.0096
1581.1 | 50.5 | -1.0096
1581.2 | 50.5 | -1.0096
1581.3 | 50.5 | -1.0096
1581.4 | 50.5 | -1.0096
1581.5 | 50.5 | -1.0096
1581.6 | 50.5 | -1.0096
1581.7 | 50.5 | -1.0096
1581.8 | 50.5 | -1.0096
1581.9 | 50.5 | -1.0094
1582 | 50.5 | -1.0094
1582.1 | 50.5 | -1.0094
1582.2 | 50.5 | -1.0094
1582.3 | 50.5 | -1.0094
1582.4 | 50.5 | -1.0094
1582.5 | 50.5 | -1.0094
1582.6 | 50.5 | -1.0094
1582.7 | 50.5 | -1.0094
1582.8 | 50.5 | -1.0094
1582.9 | 50.5 | -1.0094
1583 | 50.5 | -1.0094
1583.1 | 50.5 | -1.0094
1583.2 | 50.5 | -1.0094
1583.3 | 50.5 | -1.0094
1583.4 | 50.5 | -1.0094
1583.5 | 50.5 | -1.0094
1583.6 | 50.5 | -1.0094
1583.7 | 50.5 | -1.0094
1583.8 | 50.5 | -1.0094
1583.9 | 50.5 | -1.0094
1584 | 50.5 | -1.0096
1584.1 | 50.5 | -1.0096
1584.2 | 50.5 | -1.0096
1584.3 | 50.5 | -1.0096
1584.4 | 50.5 | -1.0096
1584.5 | 50.5 | -1.0096
1584.6 | 50.5 | -1.0096
1584.7 | 50.5 | -1.0096
1584.8 | 50.5 | -1.0096
1584.9 | 50.5 | -1.0096
1585 | 50.5 | -1.0096
1585.1 | 50.5 | -1.0096
1585.2 | 50.5 | -1.0096
1585.3 | 50.5 | -1.0096
1585.4 | 50.5 | -1.0096
1585.5 | 50.5 | -1.0096
1585.6 | 50.5 | -1.0096
1585.7 | 50.5 | -1.0096
1585.8 | 50.5 | -1.0096
1585.9 | 50.5 | -1.0096
1586 | 50.5 | -1.0096
1586.1 | 50.5 | -1.0096
1586.2 | 50.5 | -1.0096
1586.3 | 50.5 | -1.0096
1586.4 | 50.5 | -1.0096
1586.5 | 50.5 | -1.0096
1586.6 | 50.5 | -1.0096
1586.7 | 50.5 | -1.0096
1586.8 | 50.5 | -1.0096
1586.9 | 50.5 | -1.0096
1587 | 50.5 | -1.0096
1587.1 | 50.5 | -1.0096
1587.2 | 50.5 | -1.0096
1587.3 | 50.5 | -1.0096
1587.4 | 50.5 | -1.0096
1587.5 | 50.5 | -1.0096
1587.6 | 50.5 | -1.0096
1587.7 | 50.5 | -1.0096
1587.8 | 50.5 | -1.0096
1587.9 | 50.5 | -1.0096
1588 | 50.5 | -1.0096
1588.1 | 50.5 | -1.0096
1588.2 | 50.5 | -1.0096
1588.3 | 50.5 | -1.0096
1588.4 | 50.5 | -1.0096
1588.5 | 50.5 | -1.0098
1588.6 | 50.5 | -1.0098
1588.7 | 50.5 | -1.0098
1588.8 | 50.5 | -1.0096
1588.9 | 50.5 | -1.0096
1589 | 50.5 | -1.0096
1589.1 | 50.5 | -1.0096
1589.2 | 50.5 | -1.0096
1589.3 | 50.5 | -1.0096
1589.4 | 50.5 | -1.0096
1589.5 | 50.5 | -1.0096
1589.6 | 50.5 | -1.0096
1589.7 | 50.5 | -1.0094
1589.8 | 50.5 | -1.0094
1589.9 | 50.5 | -1.0094
1590 | 50.5 | -1.0096
1590.1 | 50.5 | -1.0096
1590.2 | 50.5 | -1.0096
1590.3 | 50.5 | -1.0096
1590.4 | 50.5 | -1.0096
1590.5 | 50.5 | -1.0096
1590.6 | 50.5 | -1.0096
1590.7 | 50.5 | -1.0096
1590.8 | 50.5 | -1.0096
1590.9 | 50.5 | -1.0096
1591 | 50.5 | -1.0096
1591.1 | 50.5 | -1.0096
1591.2 | 50.5 | -1.0096
1591.3 | 50.5 | -1.0096
1591.4 | 50.5 | -1.0096
1591.5 | 50.5 | -1.0096
1591.6 | 50.5 | -1.0096
1591.7 | 50.5 | -1.0096
1591.8 | 50.5 | -1.0096
1591.9 | 50.5 | -1.0096
1592 | 50.5 | -1.0096
1592.1 | 50.5 | -1.0096
1592.2 | 50.5 | -1.0096
1592.3 | 50.5 | -1.0096
1592.4 | 50.5 | -1.0096
1592.5 | 50.5 | -1.0096
1592.6 | 50.5 | -1.0096
1592.7 | 50.5 | -1.0096
1592.8 | 50.5 | -1.0096
1592.9 | 50.5 | -1.0096
1593 | 50.5 | -1.0096
1593.1 | 50.5 | -1.0096
1593.2 | 50.5 | -1.0096
1593.3 | 50.5 | -1.0096
1593.4 | 50.5 | -1.0096
1593.5 | 50.5 | -1.0096
1593.6 | 50.5 | -1.0096
1593.7 | 50.5 | -1.0098
1593.8 | 50.5 | -1.0098
1593.9 | 50.5 | -1.0098
1594 | 50.5 | -1.0098
1594.1 | 50.5 | -1.0098
1594.2 | 50.5 | -1.0098
1594.3 | 50.5 | -1.0098
1594.4 | 50.5 | -1.0098
1594.5 | 50.5 | -1.0098
1594.6 | 50.5 | -1.0098
1594.7 | 50.5 | -1.0096
1594.8 | 50.5 | -1.0096
1594.9 | 50.5 | -1.0096
1595 | 50.5 | -1.0096
1595.1 | 50.5 | -1.0096
1595.2 | 50.5 | -1.0096
1595.3 | 50.5 | -1.0096
1595.4 | 50.5 | -1.0096
1595.5 | 50.5 | -1.0096
1595.6 | 50.5 | -1.0096
1595.7 | 50.5 | -1.0096
1595.8 | 50.5 | -1.0096
1595.9 | 50.5 | -1.0096
1596 | 50.5 | -1.0096
1596.1 | 50.5 | -1.0094
1596.2 | 50.5 | -1.0094
1596.3 | 50.5 | -1.0094
1596.4 | 50.5 | -1.0094
1596.5 | 50.5 | -1.0094
1596.6 | 50.5 | -1.0094
1596.7 | 50.5 | -1.0094
1596.8 | 50.5 | -1.0094
1596.9 | 50.5 | -1.0094
1597 | 50.5 | -1.0094
1597.1 | 50.5 | -1.0094
1597.2 | 50.5 | -1.0094
1597.3 | 50.5 | -1.0094
1597.4 | 50.5 | -1.0094
1597.5 | 50.5 | -1.0094
1597.6 | 50.5 | -1.0094
1597.7 | 50.5 | -1.0094
1597.8 | 50.5 | -1.0094
1597.9 | 50.5 | -1.0094
1598 | 50.5 | -1.0094
1598.1 | 50.5 | -1.0094
1598.2 | 50.5 | -1.0094
1598.3 | 50.5 | -1.0094
1598.4 | 50.5 | -1.0094
1598.5 | 50.5 | -1.0094
1598.6 | 50.5 | -1.0094
1598.7 | 50.5 | -1.0094
1598.8 | 50.5 | -1.0094
1598.9 | 50.5 | -1.0094
1599 | 50.5 | -1.0094
1599.1 | 50.5 | -1.0094
1599.2 | 50.5 | -1.0094
1599.3 | 50.5 | -1.0094
1599.4 | 50.5 | -1.0094
1599.5 | 50.5 | -1.0096
1599.6 | 50.5 | -1.0096
1599.7 | 50.5 | -1.0096
1599.8 | 50.5 | -1.0096
1599.9 | 50.5 | -1.0096
1600 | 50.5 | -1.0096
1600.1 | 50.5 | -1.0096
1600.2 | 50.5 | -1.0096
1600.3 | 50.5 | -1.0096
1600.4 | 50.5 | -1.0096
1600.5 | 50.5 | -1.0096
1600.6 | 50.5 | -1.0096
1600.7 | 50.5 | -1.0094
1600.8 | 50.5 | -1.0094
1600.9 | 50.5 | -1.0094
1601 | 50.5 | -1.0094
1601.1 | 50.5 | -1.0094
1601.2 | 50.5 | -1.0094
1601.3 | 50.5 | -1.0094
1601.4 | 50.5 | -1.0094
1601.5 | 50.5 | -1.0094
1601.6 | 50.5 | -1.0096
1601.7 | 50.5 | -1.0096
1601.8 | 50.5 | -1.0096
1601.9 | 50.5 | -1.0096
1602 | 50.5 | -1.0096
1602.1 | 50.5 | -1.0096
1602.2 | 50.5 | -1.0096
1602.3 | 50.5 | -1.0096
1602.4 | 50.5 | -1.0096
1602.5 | 50.5 | -1.0096
1602.6 | 50.5 | -1.0096
1602.7 | 50.5 | -1.0096
1602.8 | 50.5 | -1.0096
1602.9 | 50.5 | -1.0096
1603 | 50.5 | -1.0096
1603.1 | 50.5 | -1.0096
1603.2 | 50.5 | -1.0096
1603.3 | 50.5 | -1.0096
1603.4 | 50.5 | -1.0096
1603.5 | 50.5 | -1.0096
1603.6 | 50.5 | -1.0096
1603.7 | 50.5 | -1.0096
1603.8 | 50.5 | -1.0096
1603.9 | 50.5 | -1.0096
1604 | 50.5 | -1.0096
1604.1 | 50.5 | -1.0096
1604.2 | 50.5 | -1.0096
1604.3 | 50.5 | -1.0096
1604.4 | 50.5 | -1.0096
1604.5 | 50.5 | -1.0096
1604.6 | 50.5 | -1.0096
1604.7 | 50.5 | -1.0096
1604.8 | 50.5 | -1.0096
1604.9 | 50.5 | -1.0096
1605 | 50.5 | -1.0096
1605.1 | 50.5 | -1.0096
1605.2 | 50.5 | -1.0094
1605.3 | 50.5 | -1.0096
1605.4 | 50.5 | -1.0096
1605.5 | 50.5 | -1.0096
1605.6 | 50.5 | -1.0096
1605.7 | 50.5 | -1.0096
1605.8 | 50.5 | -1.0096
1605.9 | 50.5 | -1.0096
1606 | 50.5 | -1.0096
1606.1 | 50.5 | -1.0096
1606.2 | 50.5 | -1.0096
1606.3 | 50.5 | -1.0096
1606.4 | 50.5 | -1.0096
1606.5 | 50.5 | -1.0096
1606.6 | 50.5 | -1.0096
1606.7 | 50.5 | -1.0096
1606.8 | 50.5 | -1.0096
1606.9 | 50.5 | -1.0096
1607 | 50.5 | -1.0096
1607.1 | 50.5 | -1.0096
1607.2 | 50.5 | -1.0096
1607.3 | 50.5 | -1.0096
1607.4 | 50.5 | -1.0096
1607.5 | 50.5 | -1.0096
1607.6 | 50.5 | -1.0096
1607.7 | 50.5 | -1.0096
1607.8 | 50.5 | -1.0096
1607.9 | 50.5 | -1.0096
1608 | 50.5 | -1.0096
1608.1 | 50.5 | -1.0096
1608.2 | 50.5 | -1.0096
1608.3 | 50.5 | -1.0096
1608.4 | 50.5 | -1.0096
1608.5 | 50.5 | -1.0096
1608.6 | 50.5 | -1.0096
1608.7 | 50.5 | -1.0096
1608.8 | 50.5 | -1.0096
1608.9 | 50.5 | -1.0094
1609 | 50.5 | -1.0094
1609.1 | 50.5 | -1.0094
1609.2 | 50.5 | -1.0094
1609.3 | 50.5 | -1.0094
1609.4 | 50.5 | -1.0094
1609.5 | 50.5 | -1.0094
1609.6 | 50.5 | -1.0094
1609.7 | 50.5 | -1.0092
1609.8 | 50.5 | -1.0094
1609.9 | 50.5 | -1.0094
1610 | 50.5 | -1.0094
1610.1 | 50.5 | -1.0094
1610.2 | 50.5 | -1.0094
1610.3 | 50.5 | -1.0094
1610.4 | 50.5 | -1.0094
1610.5 | 50.5 | -1.0094
1610.6 | 50.5 | -1.0094
1610.7 | 50.5 | -1.0094
1610.8 | 50.5 | -1.0094
1610.9 | 50.5 | -1.0096
1611 | 50.5 | -1.0096
1611.1 | 50.5 | -1.0096
1611.2 | 50.5 | -1.0096
1611.3 | 50.5 | -1.0096
1611.4 | 50.5 | -1.0096
1611.5 | 50.5 | -1.0096
1611.6 | 50.5 | -1.0096
1611.7 | 50.5 | -1.0096
1611.8 | 50.5 | -1.0096
1611.9 | 50.5 | -1.0096
1612 | 50.5 | -1.0096
1612.1 | 50.5 | -1.0094
1612.2 | 50.5 | -1.0094
1612.3 | 50.5 | -1.0094
1612.4 | 50.5 | -1.0094
1612.5 | 50.5 | -1.0094
1612.6 | 50.5 | -1.0094
1612.7 | 50.5 | -1.0094
1612.8 | 50.5 | -1.0094
1612.9 | 50.5 | -1.0094
1613 | 50.5 | -1.0094
1613.1 | 50.5 | -1.0094
1613.2 | 50.5 | -1.0094
1613.3 | 50.5 | -1.0096
1613.4 | 50.5 | -1.0096
1613.5 | 50.5 | -1.0096
1613.6 | 50.5 | -1.0096
1613.7 | 50.5 | -1.0096
1613.8 | 50.5 | -1.0096
1613.9 | 50.5 | -1.0096
1614 | 50.5 | -1.0096
1614.1 | 50.5 | -1.0096
1614.2 | 50.5 | -1.0096
1614.3 | 50.5 | -1.0096
1614.4 | 50.5 | -1.0096
1614.5 | 50.5 | -1.0096
1614.6 | 50.5 | -1.0096
1614.7 | 50.5 | -1.0096
1614.8 | 50.5 | -1.0096
1614.9 | 50.5 | -1.0096
1615 | 50.5 | -1.0096
1615.1 | 50.5 | -1.0096
1615.2 | 50.5 | -1.0096
1615.3 | 50.5 | -1.0096
1615.4 | 50.5 | -1.0096
1615.5 | 50.5 | -1.0096
1615.6 | 50.5 | -1.0096
1615.7 | 50.5 | -1.0096
1615.8 | 50.5 | -1.0096
1615.9 | 50.5 | -1.0096
1616 | 50.5 | -1.0096
1616.1 | 50.5 | -1.0096
1616.2 | 50.5 | -1.0096
1616.3 | 50.5 | -1.0096
1616.4 | 50.5 | -1.0096
1616.5 | 50.5 | -1.0096
1616.6 | 50.5 | -1.0096
1616.7 | 50.5 | -1.0096
1616.8 | 50.5 | -1.0096
1616.9 | 50.5 | -1.0096
1617 | 50.5 | -1.0096
1617.1 | 50.5 | -1.0096
1617.2 | 50.5 | -1.0096
1617.3 | 50.5 | -1.0096
1617.4 | 50.5 | -1.0096
1617.5 | 50.5 | -1.0096
1617.6 | 50.5 | -1.0096
1617.7 | 50.5 | -1.0096
1617.8 | 50.5 | -1.0096
1617.9 | 50.5 | -1.0096
1618 | 50.5 | -1.0096
1618.1 | 50.5 | -1.0096
1618.2 | 50.5 | -1.0094
1618.3 | 50.5 | -1.0094
1618.4 | 50.5 | -1.0094
1618.5 | 50.5 | -1.0094
1618.6 | 50.5 | -1.0094
1618.7 | 50.5 | -1.0094
1618.8 | 50.5 | -1.0094
1618.9 | 50.5 | -1.0094
1619 | 50.5 | -1.0094
1619.1 | 50.5 | -1.0094
1619.2 | 50.5 | -1.0094
1619.3 | 50.5 | -1.0096
1619.4 | 50.5 | -1.0096
1619.5 | 50.5 | -1.0096
1619.6 | 50.5 | -1.0096
1619.7 | 50.5 | -1.0096
1619.8 | 50.5 | -1.0096
1619.9 | 50.5 | -1.0096
1620 | 50.5 | -1.0096
1620.1 | 50.5 | -1.0096
1620.2 | 50.5 | -1.0096
1620.3 | 50.5 | -1.0096
1620.4 | 50.5 | -1.0096
1620.5 | 50.5 | -1.0096
1620.6 | 50.5 | -1.0096
1620.7 | 50.5 | -1.0096
1620.8 | 50.5 | -1.0096
1620.9 | 50.5 | -1.0096
1621 | 50.5 | -1.0096
1621.1 | 50.5 | -1.0096
1621.2 | 50.5 | -1.0096
1621.3 | 50.5 | -1.0096
1621.4 | 50.5 | -1.0096
1621.5 | 50.5 | -1.0096
1621.6 | 50.5 | -1.0096
1621.7 | 50.5 | -1.0096
1621.8 | 50.5 | -1.0096
1621.9 | 50.5 | -1.0096
1622 | 50.5 | -1.0096
1622.1 | 50.5 | -1.0096
1622.2 | 50.5 | -1.0096
1622.3 | 50.5 | -1.0096
1622.4 | 50.5 | -1.0096
1622.5 | 50.5 | -1.0096
1622.6 | 50.5 | -1.0096
1622.7 | 50.5 | -1.0096
1622.8 | 50.5 | -1.0096
1622.9 | 50.5 | -1.0096
1623 | 50.5 | -1.0096
1623.1 | 50.5 | -1.0096
1623.2 | 50.5 | -1.0096
1623.3 | 50.5 | -1.0096
1623.4 | 50.5 | -1.0096
1623.5 | 50.5 | -1.0096
1623.6 | 50.5 | -1.0096
1623.7 | 50.5 | -1.0096
1623.8 | 50.5 | -1.0096
1623.9 | 50.5 | -1.0096
1624 | 50.5 | -1.0096
1624.1 | 50.5 | -1.0094
1624.2 | 50.5 | -1.0094
1624.3 | 50.5 | -1.0094
1624.4 | 50.5 | -1.0094
1624.5 | 50.5 | -1.0094
1624.6 | 50.5 | -1.0094
1624.7 | 50.5 | -1.0094
1624.8 | 50.5 | -1.0094
1624.9 | 50.5 | -1.0094
1625 | 50.5 | -1.0094
1625.1 | 50.5 | -1.0094
1625.2 | 50.5 | -1.0094
1625.3 | 50.5 | -1.0096
1625.4 | 50.5 | -1.0096
1625.5 | 50.5 | -1.0096
1625.6 | 50.5 | -1.0096
1625.7 | 50.5 | -1.0096
1625.8 | 50.5 | -1.0096
1625.9 | 50.5 | -1.0096
1626 | 50.5 | -1.0096
1626.1 | 50.5 | -1.0096
1626.2 | 50.5 | -1.0096
1626.3 | 50.5 | -1.0096
1626.4 | 50.5 | -1.0096
1626.5 | 50.5 | -1.0096
1626.6 | 50.5 | -1.0096
1626.7 | 50.5 | -1.0096
1626.8 | 50.5 | -1.0096
1626.9 | 50.5 | -1.0096
1627 | 50.5 | -1.0096
1627.1 | 50.5 | -1.0096
1627.2 | 50.5 | -1.0096
1627.3 | 50.5 | -1.0096
1627.4 | 50.5 | -1.0096
1627.5 | 50.5 | -1.0096
1627.6 | 50.5 | -1.0096
1627.7 | 50.5 | -1.0096
1627.8 | 50.5 | -1.0096
1627.9 | 50.5 | -1.0096
1628 | 50.5 | -1.0096
1628.1 | 50.5 | -1.0096
1628.2 | 50.5 | -1.0096
1628.3 | 50.5 | -1.0096
1628.4 | 50.5 | -1.0096
1628.5 | 50.5 | -1.0096
1628.6 | 50.5 | -1.0096
1628.7 | 50.5 | -1.0096
1628.8 | 50.5 | -1.0096
1628.9 | 50.5 | -1.0096
1629 | 50.5 | -1.0096
1629.1 | 50.5 | -1.0096
1629.2 | 50.5 | -1.0096
1629.3 | 50.5 | -1.0096
1629.4 | 50.5 | -1.0096
1629.5 | 50.5 | -1.0096
1629.6 | 50.5 | -1.0096
1629.7 | 50.5 | -1.0096
1629.8 | 50.5 | -1.0096
1629.9 | 50.5 | -1.0096
1630 | 50.5 | -1.0096
1630.1 | 50.5 | -1.0096
1630.2 | 50.5 | -1.0096
1630.3 | 50.5 | -1.0096
1630.4 | 50.5 | -1.0096
1630.5 | 50.5 | -1.0096
1630.6 | 50.5 | -1.0096
1630.7 | 50.5 | -1.0096
1630.8 | 50.5 | -1.0096
1630.9 | 50.5 | -1.0096
1631 | 50.5 | -1.0096
1631.1 | 50.5 | -1.0096
1631.2 | 50.5 | -1.0096
1631.3 | 50.5 | -1.0096
1631.4 | 50.5 | -1.0096
1631.5 | 50.5 | -1.0096
1631.6 | 50.5 | -1.0096
1631.7 | 50.5 | -1.0096
1631.8 | 50.5 | -1.0096
1631.9 | 50.5 | -1.0096
1632 | 50.5 | -1.0096
1632.1 | 50.5 | -1.0096
1632.2 | 50.5 | -1.0096
1632.3 | 50.5 | -1.0096
1632.4 | 50.5 | -1.0096
1632.5 | 50.5 | -1.0096
1632.6 | 50.5 | -1.0096
1632.7 | 50.5 | -1.0096
1632.8 | 50.5 | -1.0096
1632.9 | 50.5 | -1.0096
1633 | 50.5 | -1.0096
1633.1 | 50.5 | -1.0096
1633.2 | 50.5 | -1.0096
1633.3 | 50.5 | -1.0096
1633.4 | 50.5 | -1.0096
1633.5 | 50.5 | -1.0096
1633.6 | 50.5 | -1.0096
1633.7 | 50.5 | -1.0096
1633.8 | 50.5 | -1.0096
1633.9 | 50.5 | -1.0096
1634 | 50.5 | -1.0096
1634.1 | 50.5 | -1.0096
1634.2 | 50.5 | -1.0096
1634.3 | 50.5 | -1.0096
1634.4 | 50.5 | -1.0096
1634.5 | 50.5 | -1.0096
1634.6 | 50.5 | -1.0096
1634.7 | 50.5 | -1.0096
1634.8 | 50.5 | -1.0096
1634.9 | 50.5 | -1.0096
1635 | 50.5 | -1.0096
1635.1 | 50.5 | -1.0096
1635.2 | 50.5 | -1.0096
1635.3 | 50.5 | -1.0096
1635.4 | 50.5 | -1.0096
1635.5 | 50.5 | -1.0096
1635.6 | 50.5 | -1.0096
1635.7 | 50.5 | -1.0096
1635.8 | 50.5 | -1.0096
1635.9 | 50.5 | -1.0096
1636 | 50.5 | -1.0096
1636.1 | 50.5 | -1.0096
1636.2 | 50.5 | -1.0096
1636.3 | 50.5 | -1.0096
1636.4 | 50.5 | -1.0096
1636.5 | 50.5 | -1.0096
1636.6 | 50.5 | -1.0096
1636.7 | 50.5 | -1.0096
1636.8 | 50.5 | -1.0096
1636.9 | 50.5 | -1.0096
1637 | 50.5 | -1.0096
1637.1 | 50.5 | -1.0096
1637.2 | 50.5 | -1.0096
1637.3 | 50.5 | -1.0096
1637.4 | 50.5 | -1.0096
1637.5 | 50.5 | -1.0096
1637.6 | 50.5 | -1.0096
1637.7 | 50.5 | -1.0096
1637.8 | 50.5 | -1.0096
1637.9 | 50.5 | -1.0096
1638 | 50.5 | -1.0096
1638.1 | 50.5 | -1.0096
1638.2 | 50.5 | -1.0096
1638.3 | 50.5 | -1.0096
1638.4 | 50.5 | -1.0096
1638.5 | 50.5 | -1.0096
1638.6 | 50.5 | -1.0096
1638.7 | 50.5 | -1.0096
1638.8 | 50.5 | -1.0096
1638.9 | 50.5 | -1.0096
1639 | 50.5 | -1.0096
1639.1 | 50.5 | -1.0096
1639.2 | 50.5 | -1.0096
1639.3 | 50.5 | -1.0096
1639.4 | 50.5 | -1.0094
1639.5 | 50.5 | -1.0094
1639.6 | 50.5 | -1.0094
1639.7 | 50.5 | -1.0094
1639.8 | 50.5 | -1.0094
1639.9 | 50.5 | -1.0094
1640 | 50.5 | -1.0094
1640.1 | 50.5 | -1.0094
1640.2 | 50.5 | -1.0094
1640.3 | 50.5 | -1.0094
1640.4 | 50.5 | -1.0094
1640.5 | 50.5 | -1.0096
1640.6 | 50.5 | -1.0096
1640.7 | 50.5 | -1.0096
1640.8 | 50.5 | -1.0096
1640.9 | 50.5 | -1.0096
1641 | 50.5 | -1.0096
1641.1 | 50.5 | -1.0096
1641.2 | 50.5 | -1.0096
1641.3 | 50.5 | -1.0096
1641.4 | 50.5 | -1.0096
1641.5 | 50.5 | -1.0096
1641.6 | 50.5 | -1.0096
1641.7 | 50.5 | -1.0096
1641.8 | 50.5 | -1.0096
1641.9 | 50.5 | -1.0096
1642 | 50.5 | -1.0096
1642.1 | 50.5 | -1.0096
1642.2 | 50.5 | -1.0096
1642.3 | 50.5 | -1.0096
1642.4 | 50.5 | -1.0096
1642.5 | 50.5 | -1.0096
1642.6 | 50.5 | -1.0096
1642.7 | 50.5 | -1.0096
1642.8 | 50.5 | -1.0096
1642.9 | 50.5 | -1.0096
1643 | 50.5 | -1.0096
1643.1 | 50.5 | -1.0096
1643.2 | 50.5 | -1.0096
1643.3 | 50.5 | -1.0096
1643.4 | 50.5 | -1.0096
1643.5 | 50.5 | -1.0096
1643.6 | 50.5 | -1.0096
1643.7 | 50.5 | -1.0096
1643.8 | 50.5 | -1.0096
1643.9 | 50.5 | -1.0096
1644 | 50.5 | -1.0096
1644.1 | 50.5 | -1.0096
1644.2 | 50.5 | -1.0096
1644.3 | 50.5 | -1.0096
1644.4 | 50.5 | -1.0096
1644.5 | 50.5 | -1.0096
1644.6 | 50.5 | -1.0096
1644.7 | 50.5 | -1.0096
1644.8 | 50.5 | -1.0096
1644.9 | 50.5 | -1.0096
1645 | 50.5 | -1.0096
1645.1 | 50.5 | -1.0096
1645.2 | 50.5 | -1.0096
1645.3 | 50.5 | -1.0096
1645.4 | 50.5 | -1.0096
1645.5 | 50.5 | -1.0096
1645.6 | 50.5 | -1.0096
1645.7 | 50.5 | -1.0096
1645.8 | 50.5 | -1.0096
1645.9 | 50.5 | -1.0096
1646 | 50.5 | -1.0096
1646.1 | 50.5 | -1.0096
1646.2 | 50.5 | -1.0096
1646.3 | 50.5 | -1.0096
1646.4 | 50.5 | -1.0096
1646.5 | 50.5 | -1.0096
1646.6 | 50.5 | -1.0096
1646.7 | 50.5 | -1.0096
1646.8 | 50.5 | -1.0096
1646.9 | 50.5 | -1.0096
1647 | 50.5 | -1.0096
1647.1 | 50.5 | -1.0096
1647.2 | 50.5 | -1.0096
1647.3 | 50.5 | -1.0096
1647.4 | 50.5 | -1.0096
1647.5 | 50.5 | -1.0096
1647.6 | 50.5 | -1.0096
1647.7 | 50.5 | -1.0096
1647.8 | 50.5 | -1.0096
1647.9 | 50.5 | -1.0096
1648 | 50.5 | -1.0096
1648.1 | 50.5 | -1.0096
1648.2 | 50.5 | -1.0096
1648.3 | 50.5 | -1.0096
1648.4 | 50.5 | -1.0096
1648.5 | 50.5 | -1.0096
1648.6 | 50.5 | -1.0096
1648.7 | 50.5 | -1.0096
1648.8 | 50.5 | -1.0096
1648.9 | 50.5 | -1.0096
1649 | 50.5 | -1.0096
1649.1 | 50.5 | -1.0096
1649.2 | 50.5 | -1.0096
1649.3 | 50.5 | -1.0096
1649.4 | 50.5 | -1.0096
1649.5 | 50.5 | -1.0096
1649.6 | 50.5 | -1.0096
1649.7 | 50.5 | -1.0096
1649.8 | 50.5 | -1.0096
1649.9 | 50.5 | -1.0096
1650 | 50.5 | -1.0096
1650.1 | 50.5 | -1.0096
1650.2 | 50.5 | -1.0096
1650.3 | 50.5 | -1.0096
1650.4 | 50.5 | -1.0096
1650.5 | 50.5 | -1.0096
1650.6 | 50.5 | -1.0096
1650.7 | 50.5 | -1.0096
1650.8 | 50.5 | -1.0096
1650.9 | 50.5 | -1.0096
1651 | 50.5 | -1.0096
1651.1 | 50.5 | -1.0096
1651.2 | 50.5 | -1.0096
1651.3 | 50.5 | -1.0096
1651.4 | 50.5 | -1.0096
1651.5 | 50.5 | -1.0096
1651.6 | 50.5 | -1.0096
1651.7 | 50.5 | -1.0096
1651.8 | 50.5 | -1.0096
1651.9 | 50.5 | -1.0096
1652 | 50.5 | -1.0096
1652.1 | 50.5 | -1.0096
1652.2 | 50.5 | -1.0096
1652.3 | 50.5 | -1.0096
1652.4 | 50.5 | -1.0096
1652.5 | 50.5 | -1.0096
1652.6 | 50.5 | -1.0096
1652.7 | 50.5 | -1.0096
1652.8 | 50.5 | -1.0096
1652.9 | 50.5 | -1.0096
1653 | 50.5 | -1.0096
1653.1 | 50.5 | -1.0096
1653.2 | 50.5 | -1.0096
1653.3 | 50.5 | -1.0096
1653.4 | 50.5 | -1.0096
1653.5 | 50.5 | -1.0096
1653.6 | 50.5 | -1.0096
1653.7 | 50.5 | -1.0096
1653.8 | 50.5 | -1.0096
1653.9 | 50.5 | -1.0096
1654 | 50.5 | -1.0096
1654.1 | 50.5 | -1.0096
1654.2 | 50.5 | -1.0096
1654.3 | 50.5 | -1.0096
1654.4 | 50.5 | -1.0096
1654.5 | 50.5 | -1.0096
1654.6 | 50.5 | -1.0096
1654.7 | 50.5 | -1.0096
1654.8 | 50.5 | -1.0096
1654.9 | 50.5 | -1.0096
1655 | 50.5 | -1.0096
1655.1 | 50.5 | -1.0096
1655.2 | 50.5 | -1.0096
1655.3 | 50.5 | -1.0096
1655.4 | 50.5 | -1.0096
1655.5 | 50.5 | -1.0096
1655.6 | 50.5 | -1.0096
1655.7 | 50.5 | -1.0096
1655.8 | 50.5 | -1.0096
1655.9 | 50.5 | -1.0096
1656 | 50.5 | -1.0096
1656.1 | 50.5 | -1.0096
1656.2 | 50.5 | -1.0096
1656.3 | 50.5 | -1.0096
1656.4 | 50.5 | -1.0096
1656.5 | 50.5 | -1.0096
1656.6 | 50.5 | -1.0096
1656.7 | 50.5 | -1.0096
1656.8 | 50.5 | -1.0096
1656.9 | 50.5 | -1.0096
1657 | 50.5 | -1.0096
1657.1 | 50.5 | -1.0096
1657.2 | 50.5 | -1.0096
1657.3 | 50.5 | -1.0096
1657.4 | 50.5 | -1.0096
1657.5 | 50.5 | -1.0096
1657.6 | 50.5 | -1.0096
1657.7 | 50.5 | -1.0096
1657.8 | 50.5 | -1.0096
1657.9 | 50.5 | -1.0096
1658 | 50.5 | -1.0096
1658.1 | 50.5 | -1.0096
1658.2 | 50.5 | -1.0096
1658.3 | 50.5 | -1.0096
1658.4 | 50.5 | -1.0096
1658.5 | 50.5 | -1.0096
1658.6 | 50.5 | -1.0096
1658.7 | 50.5 | -1.0096
1658.8 | 50.5 | -1.0096
1658.9 | 50.5 | -1.0096
1659 | 50.5 | -1.0096
1659.1 | 50.5 | -1.0096
1659.2 | 50.5 | -1.0096
1659.3 | 50.5 | -1.0096
1659.4 | 50.5 | -1.0096
1659.5 | 50.5 | -1.0096
1659.6 | 50.5 | -1.0096
1659.7 | 50.5 | -1.0096
1659.8 | 50.5 | -1.0096
1659.9 | 50.5 | -1.0096
1660 | 50.5 | -1.0096
1660.1 | 50.5 | -1.0096
1660.2 | 50.5 | -1.0096
1660.3 | 50.5 | -1.0096
1660.4 | 50.5 | -1.0096
1660.5 | 50.5 | -1.0096
1660.6 | 50.5 | -1.0096
1660.7 | 50.5 | -1.0096
1660.8 | 50.5 | -1.0096
1660.9 | 50.5 | -1.0096
1661 | 50.5 | -1.0096
1661.1 | 50.5 | -1.0096
1661.2 | 50.5 | -1.0096
1661.3 | 50.5 | -1.0096
1661.4 | 50.5 | -1.0096
1661.5 | 50.5 | -1.0096
1661.6 | 50.5 | -1.0096
1661.7 | 50.5 | -1.0096
1661.8 | 50.5 | -1.0094
1661.9 | 50.5 | -1.0094
1662 | 50.5 | -1.0094
1662.1 | 50.5 | -1.0094
1662.2 | 50.5 | -1.0094
1662.3 | 50.5 | -1.0094
1662.4 | 50.5 | -1.0094
1662.5 | 50.5 | -1.0094
1662.6 | 50.5 | -1.0094
1662.7 | 50.5 | -1.0094
1662.8 | 50.5 | -1.0096
1662.9 | 50.5 | -1.0096
1663 | 50.5 | -1.0096
1663.1 | 50.5 | -1.0096
1663.2 | 50.5 | -1.0096
1663.3 | 50.5 | -1.0096
1663.4 | 50.5 | -1.0096
1663.5 | 50.5 | -1.0096
1663.6 | 50.5 | -1.0096
1663.7 | 50.5 | -1.0096
1663.8 | 50.5 | -1.0096
1663.9 | 50.5 | -1.0096
1664 | 50.5 | -1.0096
1664.1 | 50.5 | -1.0096
1664.2 | 50.5 | -1.0096
1664.3 | 50.5 | -1.0096
1664.4 | 50.5 | -1.0096
1664.5 | 50.5 | -1.0096
1664.6 | 50.5 | -1.0096
1664.7 | 50.5 | -1.0096
1664.8 | 50.5 | -1.0096
1664.9 | 50.5 | -1.0096
1665 | 50.5 | -1.0096
1665.1 | 50.5 | -1.0096
1665.2 | 50.5 | -1.0096
1665.3 | 50.5 | -1.0096
1665.4 | 50.5 | -1.0096
1665.5 | 50.5 | -1.0096
1665.6 | 50.5 | -1.0096
1665.7 | 50.5 | -1.0096
1665.8 | 50.5 | -1.0096
1665.9 | 50.5 | -1.0096
1666 | 50.5 | -1.0096
1666.1 | 50.5 | -1.0096
1666.2 | 50.5 | -1.0096
1666.3 | 50.5 | -1.0096
1666.4 | 50.5 | -1.0096
1666.5 | 50.5 | -1.0096
1666.6 | 50.5 | -1.0096
1666.7 | 50.5 | -1.0096
1666.8 | 50.5 | -1.0096
1666.9 | 50.5 | -1.0096
1667 | 50.5 | -1.0096
1667.1 | 50.5 | -1.0096
1667.2 | 50.5 | -1.0096
1667.3 | 50.5 | -1.0096
1667.4 | 50.5 | -1.0096
1667.5 | 50.5 | -1.0096
1667.6 | 50.5 | -1.0096
1667.7 | 50.5 | -1.0096
1667.8 | 50.5 | -1.0096
1667.9 | 50.5 | -1.0096
1668 | 50.5 | -1.0096
1668.1 | 50.5 | -1.0096
1668.2 | 50.5 | -1.0096
1668.3 | 50.5 | -1.0096
1668.4 | 50.5 | -1.0096
1668.5 | 50.5 | -1.0096
1668.6 | 50.5 | -1.0096
1668.7 | 50.5 | -1.0096
1668.8 | 50.5 | -1.0096
1668.9 | 50.5 | -1.0096
1669 | 50.5 | -1.0096
1669.1 | 50.5 | -1.0096
1669.2 | 50.5 | -1.0096
1669.3 | 50.5 | -1.0096
1669.4 | 50.5 | -1.0096
1669.5 | 50.5 | -1.0096
1669.6 | 50.5 | -1.0096
1669.7 | 50.5 | -1.0096
1669.8 | 50.5 | -1.0096
1669.9 | 50.5 | -1.0096
1670 | 50.5 | -1.0096
1670.1 | 50.5 | -1.0096
1670.2 | 50.5 | -1.0096
1670.3 | 50.5 | -1.0096
1670.4 | 50.5 | -1.0096
1670.5 | 50.5 | -1.0096
1670.6 | 50.5 | -1.0096
1670.7 | 50.5 | -1.0096
1670.8 | 50.5 | -1.0096
1670.9 | 50.5 | -1.0096
1671 | 50.5 | -1.0096
1671.1 | 50.5 | -1.0096
1671.2 | 50.5 | -1.0096
1671.3 | 50.5 | -1.0096
1671.4 | 50.5 | -1.0096
1671.5 | 50.5 | -1.0096
1671.6 | 50.5 | -1.0096
1671.7 | 50.5 | -1.0096
1671.8 | 50.5 | -1.0096
1671.9 | 50.5 | -1.0096
1672 | 50.5 | -1.0096
1672.1 | 50.5 | -1.0096
1672.2 | 50.5 | -1.0096
1672.3 | 50.5 | -1.0096
1672.4 | 50.5 | -1.0096
1672.5 | 50.5 | -1.0096
1672.6 | 50.5 | -1.0096
1672.7 | 50.5 | -1.0096
1672.8 | 50.5 | -1.0096
1672.9 | 50.5 | -1.0096
1673 | 50.5 | -1.0096
1673.1 | 50.5 | -1.0096
1673.2 | 50.5 | -1.0096
1673.3 | 50.5 | -1.0096
1673.4 | 50.5 | -1.0096
1673.5 | 50.5 | -1.0096
1673.6 | 50.5 | -1.0096
1673.7 | 50.5 | -1.0096
1673.8 | 50.5 | -1.0096
1673.9 | 50.5 | -1.0096
1674 | 50.5 | -1.0096
1674.1 | 50.5 | -1.0096
1674.2 | 50.5 | -1.0096
1674.3 | 50.5 | -1.0096
1674.4 | 50.5 | -1.0094
1674.5 | 50.5 | -1.0094
1674.6 | 50.5 | -1.0094
1674.7 | 50.5 | -1.0094
1674.8 | 50.5 | -1.0094
1674.9 | 50.5 | -1.0094
1675 | 50.5 | -1.0094
1675.1 | 50.5 | -1.0094
1675.2 | 50.5 | -1.0094
1675.3 | 50.5 | -1.0094
1675.4 | 50.5 | -1.0094
1675.5 | 50.5 | -1.0094
1675.6 | 50.5 | -1.0094
1675.7 | 50.5 | -1.0094
1675.8 | 50.5 | -1.0094
1675.9 | 50.5 | -1.0094
1676 | 50.5 | -1.0094
1676.1 | 50.5 | -1.0094
1676.2 | 50.5 | -1.0094
1676.3 | 50.5 | -1.0094
1676.4 | 50.5 | -1.0094
1676.5 | 50.5 | -1.0094
1676.6 | 50.5 | -1.0094
1676.7 | 50.5 | -1.0094
1676.8 | 50.5 | -1.0096
1676.9 | 50.5 | -1.0096
1677 | 50.5 | -1.0096
1677.1 | 50.5 | -1.0096
1677.2 | 50.5 | -1.0096
1677.3 | 50.5 | -1.0096
1677.4 | 50.5 | -1.0096
1677.5 | 50.5 | -1.0096
1677.6 | 50.5 | -1.0096
1677.7 | 50.5 | -1.0096
1677.8 | 50.5 | -1.0096
1677.9 | 50.5 | -1.0096
1678 | 50.5 | -1.0096
1678.1 | 50.5 | -1.0096
1678.2 | 50.5 | -1.0096
1678.3 | 50.5 | -1.0096
1678.4 | 50.5 | -1.0096
1678.5 | 50.5 | -1.0096
1678.6 | 50.5 | -1.0096
1678.7 | 50.5 | -1.0096
1678.8 | 50.5 | -1.0096
1678.9 | 50.5 | -1.0096
1679 | 50.5 | -1.0096
1679.1 | 50.5 | -1.0096
1679.2 | 50.5 | -1.0096
1679.3 | 50.5 | -1.0096
1679.4 | 50.5 | -1.0096
1679.5 | 50.5 | -1.0096
1679.6 | 50.5 | -1.0096
1679.7 | 50.5 | -1.0096
1679.8 | 50.5 | -1.0096
1679.9 | 50.5 | -1.0096
1680 | 50.5 | -1.0096
1680.1 | 50.5 | -1.0096
1680.2 | 50.5 | -1.0096
1680.3 | 50.5 | -1.0096
1680.4 | 50.5 | -1.0096
1680.5 | 50.5 | -1.0096
1680.6 | 50.5 | -1.0096
1680.7 | 50.5 | -1.0096
1680.8 | 50.5 | -1.0096
1680.9 | 50.5 | -1.0096
1681 | 50.5 | -1.0096
1681.1 | 50.5 | -1.0096
1681.2 | 50.5 | -1.0096
1681.3 | 50.5 | -1.0096
1681.4 | 50.5 | -1.0096
1681.5 | 50.5 | -1.0096
1681.6 | 50.5 | -1.0094
1681.7 | 50.5 | -1.0094
1681.8 | 50.5 | -1.0094
1681.9 | 50.5 | -1.0094
1682 | 50.5 | -1.0094
1682.1 | 50.5 | -1.0094
1682.2 | 50.5 | -1.0094
1682.3 | 50.5 | -1.0094
1682.4 | 50.5 | -1.0094
1682.5 | 50.5 | -1.0094
1682.6 | 50.5 | -1.0096
1682.7 | 50.5 | -1.0096
1682.8 | 50.5 | -1.0096
1682.9 | 50.5 | -1.0096
1683 | 50.5 | -1.0096
1683.1 | 50.5 | -1.0096
1683.2 | 50.5 | -1.0096
1683.3 | 50.5 | -1.0096
1683.4 | 50.5 | -1.0096
1683.5 | 50.5 | -1.0096
1683.6 | 50.5 | -1.0096
1683.7 | 50.5 | -1.0096
1683.8 | 50.5 | -1.0096
1683.9 | 50.5 | -1.0096
1684 | 50.5 | -1.0096
1684.1 | 50.5 | -1.0096
1684.2 | 50.5 | -1.0096
1684.3 | 50.5 | -1.0096
1684.4 | 50.5 | -1.0096
1684.5 | 50.5 | -1.0096
1684.6 | 50.5 | -1.0096
1684.7 | 50.5 | -1.0096
1684.8 | 50.5 | -1.0096
1684.9 | 50.5 | -1.0096
1685 | 50.5 | -1.0096
1685.1 | 50.5 | -1.0096
1685.2 | 50.5 | -1.0096
1685.3 | 50.5 | -1.0096
1685.4 | 50.5 | -1.0096
1685.5 | 50.5 | -1.0096
1685.6 | 50.5 | -1.0096
1685.7 | 50.5 | -1.0096
1685.8 | 50.5 | -1.0096
1685.9 | 50.5 | -1.0096
1686 | 50.5 | -1.0096
1686.1 | 50.5 | -1.0096
1686.2 | 50.5 | -1.0096
1686.3 | 50.5 | -1.0096
1686.4 | 50.5 | -1.0096
1686.5 | 50.5 | -1.0096
1686.6 | 50.5 | -1.0096
1686.7 | 50.5 | -1.0096
1686.8 | 50.5 | -1.0096
1686.9 | 50.5 | -1.0096
1687 | 50.5 | -1.0096
1687.1 | 50.5 | -1.0096
1687.2 | 50.5 | -1.0096
1687.3 | 50.5 | -1.0096
1687.4 | 50.5 | -1.0096
1687.5 | 50.5 | -1.0096
1687.6 | 50.5 | -1.0096
1687.7 | 50.5 | -1.0096
1687.8 | 50.5 | -1.0096
1687.9 | 50.5 | -1.0096
1688 | 50.5 | -1.0096
1688.1 | 50.5 | -1.0096
1688.2 | 50.5 | -1.0096
1688.3 | 50.5 | -1.0096
1688.4 | 50.5 | -1.0096
1688.5 | 50.5 | -1.0096
1688.6 | 50.5 | -1.0096
1688.7 | 50.5 | -1.0096
1688.8 | 50.5 | -1.0096
1688.9 | 50.5 | -1.0096
1689 | 50.5 | -1.0096
1689.1 | 50.5 | -1.0096
1689.2 | 50.5 | -1.0096
1689.3 | 50.5 | -1.0096
1689.4 | 50.5 | -1.0096
1689.5 | 50.5 | -1.0096
1689.6 | 50.5 | -1.0096
1689.7 | 50.5 | -1.0096
1689.8 | 50.5 | -1.0096
1689.9 | 50.5 | -1.0096
1690 | 50.5 | -1.0096
1690.1 | 50.5 | -1.0096
1690.2 | 50.5 | -1.0096
1690.3 | 50.5 | -1.0096
1690.4 | 50.5 | -1.0096
1690.5 | 50.5 | -1.0096
1690.6 | 50.5 | -1.0096
1690.7 | 50.5 | -1.0096
1690.8 | 50.5 | -1.0096
1690.9 | 50.5 | -1.0096
1691 | 50.5 | -1.0096
1691.1 | 50.5 | -1.0096
1691.2 | 50.5 | -1.0096
1691.3 | 50.5 | -1.0096
1691.4 | 50.5 | -1.0096
1691.5 | 50.5 | -1.0096
1691.6 | 50.5 | -1.0096
1691.7 | 50.5 | -1.0096
1691.8 | 50.5 | -1.0096
1691.9 | 50.5 | -1.0096
1692 | 50.5 | -1.0096
1692.1 | 50.5 | -1.0096
1692.2 | 50.5 | -1.0096
1692.3 | 50.5 | -1.0096
1692.4 | 50.5 | -1.0096
1692.5 | 50.5 | -1.0096
1692.6 | 50.5 | -1.0096
1692.7 | 50.5 | -1.0096
1692.8 | 50.5 | -1.0096
1692.9 | 50.5 | -1.0096
1693 | 50.5 | -1.0096
1693.1 | 50.5 | -1.0096
1693.2 | 50.5 | -1.0096
1693.3 | 50.5 | -1.0096
1693.4 | 50.5 | -1.0096
1693.5 | 50.5 | -1.0096
1693.6 | 50.5 | -1.0096
1693.7 | 50.5 | -1.0096
1693.8 | 50.5 | -1.0096
1693.9 | 50.5 | -1.0096
1694 | 50.5 | -1.0096
1694.1 | 50.5 | -1.0096
1694.2 | 50.5 | -1.0096
1694.3 | 50.5 | -1.0096
1694.4 | 50.5 | -1.0096
1694.5 | 50.5 | -1.0096
1694.6 | 50.5 | -1.0096
1694.7 | 50.5 | -1.0096
1694.8 | 50.5 | -1.0096
1694.9 | 50.5 | -1.0096
1695 | 50.5 | -1.0096
1695.1 | 50.5 | -1.0096
1695.2 | 50.5 | -1.0096
1695.3 | 50.5 | -1.0096
1695.4 | 50.5 | -1.0096
1695.5 | 50.5 | -1.0096
1695.6 | 50.5 | -1.0096
1695.7 | 50.5 | -1.0096
1695.8 | 50.5 | -1.0096
1695.9 | 50.5 | -1.0096
1696 | 50.5 | -1.0096
1696.1 | 50.5 | -1.0096
1696.2 | 50.5 | -1.0096
1696.3 | 50.5 | -1.0096
1696.4 | 50.5 | -1.0096
1696.5 | 50.5 | -1.0096
1696.6 | 50.5 | -1.0096
1696.7 | 50.5 | -1.0096
1696.8 | 50.5 | -1.0096
1696.9 | 50.5 | -1.0096
1697 | 50.5 | -1.0096
1697.1 | 50.5 | -1.0096
1697.2 | 50.5 | -1.0096
1697.3 | 50.5 | -1.0096
1697.4 | 50.5 | -1.0096
1697.5 | 50.5 | -1.0096
1697.6 | 50.5 | -1.0096
1697.7 | 50.5 | -1.0096
1697.8 | 50.5 | -1.0096
1697.9 | 50.5 | -1.0096
1698 | 50.5 | -1.0096
1698.1 | 50.5 | -1.0096
1698.2 | 50.5 | -1.0096
1698.3 | 50.5 | -1.0096
1698.4 | 50.5 | -1.0096
1698.5 | 50.5 | -1.0096
1698.6 | 50.5 | -1.0096
1698.7 | 50.5 | -1.0094
1698.8 | 50.5 | -1.0094
1698.9 | 50.5 | -1.0094
1699 | 50.5 | -1.0096
1699.1 | 50.5 | -1.0096
1699.2 | 50.5 | -1.0096
1699.3 | 50.5 | -1.0096
1699.4 | 50.5 | -1.0096
1699.5 | 50.5 | -1.0096
1699.6 | 50.5 | -1.0096
1699.7 | 50.5 | -1.0096
1699.8 | 50.5 | -1.0096
1699.9 | 50.5 | -1.0096
1700 | 50.5 | -1.0094
1700.1 | 50.5 | -1.0094
1700.2 | 50.5 | -1.0094
1700.3 | 50.5 | -1.0094
1700.4 | 50.5 | -1.0094
1700.5 | 50.5 | -1.0094
1700.6 | 50.5 | -1.0094
1700.7 | 50.5 | -1.0094
1700.8 | 50.5 | -1.0094
1700.9 | 50.5 | -1.0094
1701 | 50.5 | -1.0094
1701.1 | 50.5 | -1.0094
1701.2 | 50.5 | -1.0094
1701.3 | 50.5 | -1.0094
1701.4 | 50.5 | -1.0094
1701.5 | 50.5 | -1.0094
1701.6 | 50.5 | -1.0094
1701.7 | 50.5 | -1.0094
1701.8 | 50.5 | -1.0094
1701.9 | 50.5 | -1.0094
1702 | 50.5 | -1.0094
1702.1 | 50.5 | -1.0096
1702.2 | 50.5 | -1.0096
1702.3 | 50.5 | -1.0096
1702.4 | 50.5 | -1.0096
1702.5 | 50.5 | -1.0096
1702.6 | 50.5 | -1.0096
1702.7 | 50.5 | -1.0096
1702.8 | 50.5 | -1.0096
1702.9 | 50.5 | -1.0096
1703 | 50.5 | -1.0096
1703.1 | 50.5 | -1.0096
1703.2 | 50.5 | -1.0096
1703.3 | 50.5 | -1.0096
1703.4 | 50.5 | -1.0096
1703.5 | 50.5 | -1.0096
1703.6 | 50.5 | -1.0096
1703.7 | 50.5 | -1.0096
1703.8 | 50.5 | -1.0096
1703.9 | 50.5 | -1.0096
1704 | 50.5 | -1.0096
1704.1 | 50.5 | -1.0096
1704.2 | 50.5 | -1.0096
1704.3 | 50.5 | -1.0096
1704.4 | 50.5 | -1.0096
1704.5 | 50.5 | -1.0096
1704.6 | 50.5 | -1.0096
1704.7 | 50.5 | -1.0096
1704.8 | 50.5 | -1.0096
1704.9 | 50.5 | -1.0096
1705 | 50.5 | -1.0096
1705.1 | 50.5 | -1.0096
1705.2 | 50.5 | -1.0096
1705.3 | 50.5 | -1.0096
1705.4 | 50.5 | -1.0096
1705.5 | 50.5 | -1.0096
1705.6 | 50.5 | -1.0096
1705.7 | 50.5 | -1.0096
1705.8 | 50.5 | -1.0096
1705.9 | 50.5 | -1.0096
1706 | 50.5 | -1.0096
1706.1 | 50.5 | -1.0096
1706.2 | 50.5 | -1.0096
1706.3 | 50.5 | -1.0096
1706.4 | 50.5 | -1.0096
1706.5 | 50.5 | -1.0096
1706.6 | 50.5 | -1.0096
1706.7 | 50.5 | -1.0096
1706.8 | 50.5 | -1.0096
1706.9 | 50.5 | -1.0096
1707 | 50.5 | -1.0096
1707.1 | 50.5 | -1.0096
1707.2 | 50.5 | -1.0096
1707.3 | 50.5 | -1.0096
1707.4 | 50.5 | -1.0096
1707.5 | 50.5 | -1.0096
1707.6 | 50.5 | -1.0096
1707.7 | 50.5 | -1.0096
1707.8 | 50.5 | -1.0096
1707.9 | 50.5 | -1.0096
1708 | 50.5 | -1.0096
1708.1 | 50.5 | -1.0096
1708.2 | 50.5 | -1.0096
1708.3 | 50.5 | -1.0096
1708.4 | 50.5 | -1.0096
1708.5 | 50.5 | -1.0096
1708.6 | 50.5 | -1.0096
1708.7 | 50.5 | -1.0096
1708.8 | 50.5 | -1.0096
1708.9 | 50.5 | -1.0096
1709 | 50.5 | -1.0096
1709.1 | 50.5 | -1.0096
1709.2 | 50.5 | -1.0096
1709.3 | 50.5 | -1.0096
1709.4 | 50.5 | -1.0096
1709.5 | 50.5 | -1.0096
1709.6 | 50.5 | -1.0096
1709.7 | 50.5 | -1.0096
1709.8 | 50.5 | -1.0096
1709.9 | 50.5 | -1.0096
1710 | 50.5 | -1.0096
1710.1 | 50.5 | -1.0096
1710.2 | 50.5 | -1.0096
1710.3 | 50.5 | -1.0096
1710.4 | 50.5 | -1.0096
1710.5 | 50.5 | -1.0096
1710.6 | 50.5 | -1.0096
1710.7 | 50.5 | -1.0096
1710.8 | 50.5 | -1.0096
1710.9 | 50.5 | -1.0096
1711 | 50.5 | -1.0096
1711.1 | 50.5 | -1.0096
1711.2 | 50.5 | -1.0096
1711.3 | 50.5 | -1.0096
1711.4 | 50.5 | -1.0096
1711.5 | 50.5 | -1.0096
1711.6 | 50.5 | -1.0096
1711.7 | 50.5 | -1.0096
1711.8 | 50.5 | -1.0094
1711.9 | 50.5 | -1.0094
1712 | 50.5 | -1.0094
1712.1 | 50.5 | -1.0094
1712.2 | 50.5 | -1.0094
1712.3 | 50.5 | -1.0094
1712.4 | 50.5 | -1.0094
1712.5 | 50.5 | -1.0094
1712.6 | 50.5 | -1.0094
1712.7 | 50.5 | -1.0094
1712.8 | 50.5 | -1.0094
1712.9 | 50.5 | -1.0094
1713 | 50.5 | -1.0096
1713.1 | 50.5 | -1.0096
1713.2 | 50.5 | -1.0096
1713.3 | 50.5 | -1.0096
1713.4 | 50.5 | -1.0096
1713.5 | 50.5 | -1.0096
1713.6 | 50.5 | -1.0096
1713.7 | 50.5 | -1.0096
1713.8 | 50.5 | -1.0096
1713.9 | 50.5 | -1.0096
1714 | 50.5 | -1.0096
1714.1 | 50.5 | -1.0096
1714.2 | 50.5 | -1.0096
1714.3 | 50.5 | -1.0096
1714.4 | 50.5 | -1.0096
1714.5 | 50.5 | -1.0096
1714.6 | 50.5 | -1.0096
1714.7 | 50.5 | -1.0096
1714.8 | 50.5 | -1.0096
1714.9 | 50.5 | -1.0096
1715 | 50.5 | -1.0096
1715.1 | 50.5 | -1.0096
1715.2 | 50.5 | -1.0096
1715.3 | 50.5 | -1.0096
1715.4 | 50.5 | -1.0096
1715.5 | 50.5 | -1.0096
1715.6 | 50.5 | -1.0096
1715.7 | 50.5 | -1.0096
1715.8 | 50.5 | -1.0096
1715.9 | 50.5 | -1.0096
1716 | 50.5 | -1.0096
1716.1 | 50.5 | -1.0096
1716.2 | 50.5 | -1.0096
1716.3 | 50.5 | -1.0096
1716.4 | 50.5 | -1.0096
1716.5 | 50.5 | -1.0096
1716.6 | 50.5 | -1.0096
1716.7 | 50.5 | -1.0096
1716.8 | 50.5 | -1.0096
1716.9 | 50.5 | -1.0096
1717 | 50.5 | -1.0096
1717.1 | 50.5 | -1.0096
1717.2 | 50.5 | -1.0096
1717.3 | 50.5 | -1.0096
1717.4 | 50.5 | -1.0096
1717.5 | 50.5 | -1.0096
1717.6 | 50.5 | -1.0096
1717.7 | 50.5 | -1.0096
1717.8 | 50.5 | -1.0096
1717.9 | 50.5 | -1.0096
1718 | 50.5 | -1.0096
1718.1 | 50.5 | -1.0096
1718.2 | 50.5 | -1.0096
1718.3 | 50.5 | -1.0096
1718.4 | 50.5 | -1.0096
1718.5 | 50.5 | -1.0096
1718.6 | 50.5 | -1.0096
1718.7 | 50.5 | -1.0096
1718.8 | 50.5 | -1.0096
1718.9 | 50.5 | -1.0096
1719 | 50.5 | -1.0096
1719.1 | 50.5 | -1.0096
1719.2 | 50.5 | -1.0096
1719.3 | 50.5 | -1.0096
1719.4 | 50.5 | -1.0096
1719.5 | 50.5 | -1.0096
1719.6 | 50.5 | -1.0096
1719.7 | 50.5 | -1.0096
1719.8 | 50.5 | -1.0096
1719.9 | 50.5 | -1.0096
1720 | 50.5 | -1.0096
1720.1 | 50.5 | -1.0096
1720.2 | 50.5 | -1.0096
1720.3 | 50.5 | -1.0096
1720.4 | 50.5 | -1.0096
1720.5 | 50.5 | -1.0096
1720.6 | 50.5 | -1.0096
1720.7 | 50.5 | -1.0096
1720.8 | 50.5 | -1.0096
1720.9 | 50.5 | -1.0096
1721 | 50.5 | -1.0096
1721.1 | 50.5 | -1.0096
1721.2 | 50.5 | -1.0096
1721.3 | 50.5 | -1.0096
1721.4 | 50.5 | -1.0096
1721.5 | 50.5 | -1.0096
1721.6 | 50.5 | -1.0096
1721.7 | 50.5 | -1.0096
1721.8 | 50.5 | -1.0096
1721.9 | 50.5 | -1.0096
1722 | 50.5 | -1.0096
1722.1 | 50.5 | -1.0096
1722.2 | 50.5 | -1.0096
1722.3 | 50.5 | -1.0096
1722.4 | 50.5 | -1.0096
1722.5 | 50.5 | -1.0096
1722.6 | 50.5 | -1.0096
1722.7 | 50.5 | -1.0096
1722.8 | 50.5 | -1.0096
1722.9 | 50.5 | -1.0096
1723 | 50.5 | -1.0096
1723.1 | 50.5 | -1.0096
1723.2 | 50.5 | -1.0096
1723.3 | 50.5 | -1.0096
1723.4 | 50.5 | -1.0096
1723.5 | 50.5 | -1.0096
1723.6 | 50.5 | -1.0096
1723.7 | 50.5 | -1.0096
1723.8 | 50.5 | -1.0096
1723.9 | 50.5 | -1.0096
1724 | 50.5 | -1.0096
1724.1 | 50.5 | -1.0096
1724.2 | 50.5 | -1.0096
1724.3 | 50.5 | -1.0096
1724.4 | 50.5 | -1.0096
1724.5 | 50.5 | -1.0096
1724.6 | 50.5 | -1.0096
1724.7 | 50.5 | -1.0096
1724.8 | 50.5 | -1.0096
1724.9 | 50.5 | -1.0096
1725 | 50.5 | -1.0096
1725.1 | 50.5 | -1.0096
1725.2 | 50.5 | -1.0096
1725.3 | 50.5 | -1.0096
1725.4 | 50.5 | -1.0096
1725.5 | 50.5 | -1.0096
1725.6 | 50.5 | -1.0096
1725.7 | 50.5 | -1.0096
1725.8 | 50.5 | -1.0096
1725.9 | 50.5 | -1.0096
1726 | 50.5 | -1.0096
1726.1 | 50.5 | -1.0096
1726.2 | 50.5 | -1.0096
1726.3 | 50.5 | -1.0096
1726.4 | 50.5 | -1.0096
1726.5 | 50.5 | -1.0096
1726.6 | 50.5 | -1.0096
1726.7 | 50.5 | -1.0096
1726.8 | 50.5 | -1.0096
1726.9 | 50.5 | -1.0096
1727 | 50.5 | -1.0096
1727.1 | 50.5 | -1.0096
1727.2 | 50.5 | -1.0096
1727.3 | 50.5 | -1.0096
1727.4 | 50.5 | -1.0096
1727.5 | 50.5 | -1.0096
1727.6 | 50.5 | -1.0096
1727.7 | 50.5 | -1.0096
1727.8 | 50.5 | -1.0096
1727.9 | 50.5 | -1.0096
1728 | 50.5 | -1.0096
1728.1 | 50.5 | -1.0096
1728.2 | 50.5 | -1.0096
1728.3 | 50.5 | -1.0096
1728.4 | 50.5 | -1.0096
1728.5 | 50.5 | -1.0096
1728.6 | 50.5 | -1.0096
1728.7 | 50.5 | -1.0096
1728.8 | 50.5 | -1.0096
1728.9 | 50.5 | -1.0096
1729 | 50.5 | -1.0096
1729.1 | 50.5 | -1.0096
1729.2 | 50.5 | -1.0096
1729.3 | 50.5 | -1.0096
1729.4 | 50.5 | -1.0096
1729.5 | 50.5 | -1.0096
1729.6 | 50.5 | -1.0096
1729.7 | 50.5 | -1.0096
1729.8 | 50.5 | -1.0096
1729.9 | 50.5 | -1.0096
1730 | 50.5 | -1.0096
1730.1 | 50.5 | -1.0096
1730.2 | 50.5 | -1.0096
1730.3 | 50.5 | -1.0096
1730.4 | 50.5 | -1.0096
1730.5 | 50.5 | -1.0096
1730.6 | 50.5 | -1.0096
1730.7 | 50.5 | -1.0096
1730.8 | 50.5 | -1.0096
1730.9 | 50.5 | -1.0096
1731 | 50.5 | -1.0096
1731.1 | 50.5 | -1.0096
1731.2 | 50.5 | -1.0096
1731.3 | 50.5 | -1.0096
1731.4 | 50.5 | -1.0096
1731.5 | 50.5 | -1.0096
1731.6 | 50.5 | -1.0096
1731.7 | 50.5 | -1.0096
1731.8 | 50.5 | -1.0096
1731.9 | 50.5 | -1.0096
1732 | 50.5 | -1.0096
1732.1 | 50.5 | -1.0096
1732.2 | 50.5 | -1.0096
1732.3 | 50.5 | -1.0096
1732.4 | 50.5 | -1.0096
1732.5 | 50.5 | -1.0096
1732.6 | 50.5 | -1.0096
1732.7 | 50.5 | -1.0096
1732.8 | 50.5 | -1.0096
1732.9 | 50.5 | -1.0096
1733 | 50.5 | -1.0096
1733.1 | 50.5 | -1.0096
1733.2 | 50.5 | -1.0096
1733.3 | 50.5 | -1.0096
1733.4 | 50.5 | -1.0096
1733.5 | 50.5 | -1.0096
1733.6 | 50.5 | -1.0096
1733.7 | 50.5 | -1.0096
1733.8 | 50.5 | -1.0096
1733.9 | 50.5 | -1.0096
1734 | 50.5 | -1.0096
1734.1 | 50.5 | -1.0096
1734.2 | 50.5 | -1.0096
1734.3 | 50.5 | -1.0096
1734.4 | 50.5 | -1.0096
1734.5 | 50.5 | -1.0096
1734.6 | 50.5 | -1.0096
1734.7 | 50.5 | -1.0096
1734.8 | 50.5 | -1.0096
1734.9 | 50.5 | -1.0096
1735 | 50.5 | -1.0096
1735.1 | 50.5 | -1.0096
1735.2 | 50.5 | -1.0096
1735.3 | 50.5 | -1.0096
1735.4 | 50.5 | -1.0096
1735.5 | 50.5 | -1.0096
1735.6 | 50.5 | -1.0096
1735.7 | 50.5 | -1.0096
1735.8 | 50.5 | -1.0096
1735.9 | 50.5 | -1.0096
1736 | 50.5 | -1.0096
1736.1 | 50.5 | -1.0096
1736.2 | 50.5 | -1.0096
1736.3 | 50.5 | -1.0096
1736.4 | 50.5 | -1.0096
1736.5 | 50.5 | -1.0096
1736.6 | 50.5 | -1.0096
1736.7 | 50.5 | -1.0096
1736.8 | 50.5 | -1.0096
1736.9 | 50.5 | -1.0096
1737 | 50.5 | -1.0096
1737.1 | 50.5 | -1.0096
1737.2 | 50.5 | -1.0096
1737.3 | 50.5 | -1.0096
1737.4 | 50.5 | -1.0096
1737.5 | 50.5 | -1.0096
1737.6 | 50.5 | -1.0096
1737.7 | 50.5 | -1.0096
1737.8 | 50.5 | -1.0096
1737.9 | 50.5 | -1.0096
1738 | 50.5 | -1.0096
1738.1 | 50.5 | -1.0096
1738.2 | 50.5 | -1.0096
1738.3 | 50.5 | -1.0096
1738.4 | 50.5 | -1.0096
1738.5 | 50.5 | -1.0096
1738.6 | 50.5 | -1.0096
1738.7 | 50.5 | -1.0096
1738.8 | 50.5 | -1.0096
1738.9 | 50.5 | -1.0096
1739 | 50.5 | -1.0096
1739.1 | 50.5 | -1.0096
1739.2 | 50.5 | -1.0096
1739.3 | 50.5 | -1.0096
1739.4 | 50.5 | -1.0096
1739.5 | 50.5 | -1.0096
1739.6 | 50.5 | -1.0096
1739.7 | 50.5 | -1.0096
1739.8 | 50.5 | -1.0096
1739.9 | 50.5 | -1.0096
1740 | 50.5 | -1.0096
1740.1 | 50.5 | -1.0096
1740.2 | 50.5 | -1.0096
1740.3 | 50.5 | -1.0096
1740.4 | 50.5 | -1.0096
1740.5 | 50.5 | -1.0096
1740.6 | 50.5 | -1.0096
1740.7 | 50.5 | -1.0096
1740.8 | 50.5 | -1.0096
1740.9 | 50.5 | -1.0096
1741 | 50.5 | -1.0096
1741.1 | 50.5 | -1.0096
1741.2 | 50.5 | -1.0096
1741.3 | 50.5 | -1.0096
1741.4 | 50.5 | -1.0096
1741.5 | 50.5 | -1.0096
1741.6 | 50.5 | -1.0096
1741.7 | 50.5 | -1.0096
1741.8 | 50.5 | -1.0096
1741.9 | 50.5 | -1.0096
1742 | 50.5 | -1.0096
1742.1 | 50.5 | -1.0096
1742.2 | 50.5 | -1.0096
1742.3 | 50.5 | -1.0096
1742.4 | 50.5 | -1.0096
1742.5 | 50.5 | -1.0096
1742.6 | 50.5 | -1.0096
1742.7 | 50.5 | -1.0096
1742.8 | 50.5 | -1.0096
1742.9 | 50.5 | -1.0096
1743 | 50.5 | -1.0096
1743.1 | 50.5 | -1.0096
1743.2 | 50.5 | -1.0096
1743.3 | 50.5 | -1.0096
1743.4 | 50.5 | -1.0096
1743.5 | 50.5 | -1.0096
1743.6 | 50.5 | -1.0096
1743.7 | 50.5 | -1.0096
1743.8 | 50.5 | -1.0096
1743.9 | 50.5 | -1.0096
1744 | 50.5 | -1.0096
1744.1 | 50.5 | -1.0096
1744.2 | 50.5 | -1.0096
1744.3 | 50.5 | -1.0096
1744.4 | 50.5 | -1.0096
1744.5 | 50.5 | -1.0096
1744.6 | 50.5 | -1.0096
1744.7 | 50.5 | -1.0096
1744.8 | 50.5 | -1.0096
1744.9 | 50.5 | -1.0096
1745 | 50.5 | -1.0096
1745.1 | 50.5 | -1.0096
1745.2 | 50.5 | -1.0096
1745.3 | 50.5 | -1.0096
1745.4 | 50.5 | -1.0096
1745.5 | 50.5 | -1.0096
1745.6 | 50.5 | -1.0096
1745.7 | 50.5 | -1.0096
1745.8 | 50.5 | -1.0096
1745.9 | 50.5 | -1.0096
1746 | 50.5 | -1.0096
1746.1 | 50.5 | -1.0096
1746.2 | 50.5 | -1.0096
1746.3 | 50.5 | -1.0096
1746.4 | 50.5 | -1.0096
1746.5 | 50.5 | -1.0096
1746.6 | 50.5 | -1.0096
1746.7 | 50.5 | -1.0096
1746.8 | 50.5 | -1.0096
1746.9 | 50.5 | -1.0096
1747 | 50.5 | -1.0096
1747.1 | 50.5 | -1.0096
1747.2 | 50.5 | -1.0096
1747.3 | 50.5 | -1.0096
1747.4 | 50.5 | -1.0096
1747.5 | 50.5 | -1.0096
1747.6 | 50.5 | -1.0096
1747.7 | 50.5 | -1.0096
1747.8 | 50.5 | -1.0096
1747.9 | 50.5 | -1.0096
1748 | 50.5 | -1.0096
1748.1 | 50.5 | -1.0096
1748.2 | 50.5 | -1.0096
1748.3 | 50.5 | -1.0096
1748.4 | 50.5 | -1.0096
1748.5 | 50.5 | -1.0096
1748.6 | 50.5 | -1.0096
1748.7 | 50.5 | -1.0096
1748.8 | 50.5 | -1.0096
1748.9 | 50.5 | -1.0096
1749 | 50.5 | -1.0096
1749.1 | 50.5 | -1.0096
1749.2 | 50.5 | -1.0096
1749.3 | 50.5 | -1.0096
1749.4 | 50.5 | -1.0096
1749.5 | 50.5 | -1.0096
1749.6 | 50.5 | -1.0096
1749.7 | 50.5 | -1.0096
1749.8 | 50.5 | -1.0096
1749.9 | 50.5 | -1.0096
1750 | 50.5 | -1.0096
1750.1 | 50.5 | -1.0096
1750.2 | 50.5 | -1.0096
1750.3 | 50.5 | -1.0096
1750.4 | 50.5 | -1.0096
1750.5 | 50.5 | -1.0096
1750.6 | 50.5 | -1.0096
1750.7 | 50.5 | -1.0096
1750.8 | 50.5 | -1.0096
1750.9 | 50.5 | -1.0096
1751 | 50.5 | -1.0096
1751.1 | 50.5 | -1.0096
1751.2 | 50.5 | -1.0096
1751.3 | 50.5 | -1.0096
1751.4 | 50.5 | -1.0096
1751.5 | 50.5 | -1.0096
1751.6 | 50.5 | -1.0096
1751.7 | 50.5 | -1.0096
1751.8 | 50.5 | -1.0096
1751.9 | 50.5 | -1.0096
1752 | 50.5 | -1.0096
1752.1 | 50.5 | -1.0096
1752.2 | 50.5 | -1.0096
1752.3 | 50.5 | -1.0096
1752.4 | 50.5 | -1.0096
1752.5 | 50.5 | -1.0096
1752.6 | 50.5 | -1.0096
1752.7 | 50.5 | -1.0096
1752.8 | 50.5 | -1.0096
1752.9 | 50.5 | -1.0096
1753 | 50.5 | -1.0096
1753.1 | 50.5 | -1.0096
1753.2 | 50.5 | -1.0096
1753.3 | 50.5 | -1.0096
1753.4 | 50.5 | -1.0096
1753.5 | 50.5 | -1.0096
1753.6 | 50.5 | -1.0096
1753.7 | 50.5 | -1.0096
1753.8 | 50.5 | -1.0096
1753.9 | 50.5 | -1.0096
1754 | 50.5 | -1.0096
1754.1 | 50.5 | -1.0096
1754.2 | 50.5 | -1.0096
1754.3 | 50.5 | -1.0096
1754.4 | 50.5 | -1.0096
1754.5 | 50.5 | -1.0096
1754.6 | 50.5 | -1.0096
1754.7 | 50.5 | -1.0096
1754.8 | 50.5 | -1.0096
1754.9 | 50.5 | -1.0096
1755 | 50.5 | -1.0096
1755.1 | 50.5 | -1.0096
1755.2 | 50.5 | -1.0096
1755.3 | 50.5 | -1.0096
1755.4 | 50.5 | -1.0096
1755.5 | 50.5 | -1.0096
1755.6 | 50.5 | -1.0096
1755.7 | 50.5 | -1.0096
1755.8 | 50.5 | -1.0096
1755.9 | 50.5 | -1.0096
1756 | 50.5 | -1.0096
1756.1 | 50.5 | -1.0096
1756.2 | 50.5 | -1.0096
1756.3 | 50.5 | -1.0096
1756.4 | 50.5 | -1.0096
1756.5 | 50.5 | -1.0096
1756.6 | 50.5 | -1.0096
1756.7 | 50.5 | -1.0096
1756.8 | 50.5 | -1.0096
1756.9 | 50.5 | -1.0096
1757 | 50.5 | -1.0096
1757.1 | 50.5 | -1.0096
1757.2 | 50.5 | -1.0096
1757.3 | 50.5 | -1.0096
1757.4 | 50.5 | -1.0096
1757.5 | 50.5 | -1.0096
1757.6 | 50.5 | -1.0096
1757.7 | 50.5 | -1.0096
1757.8 | 50.5 | -1.0096
1757.9 | 50.5 | -1.0096
1758 | 50.5 | -1.0096
1758.1 | 50.5 | -1.0096
1758.2 | 50.5 | -1.0096
1758.3 | 50.5 | -1.0096
1758.4 | 50.5 | -1.0096
1758.5 | 50.5 | -1.0096
1758.6 | 50.5 | -1.0096
1758.7 | 50.5 | -1.0096
1758.8 | 50.5 | -1.0096
1758.9 | 50.5 | -1.0096
1759 | 50.5 | -1.0096
1759.1 | 50.5 | -1.0096
1759.2 | 50.5 | -1.0096
1759.3 | 50.5 | -1.0096
1759.4 | 50.5 | -1.0096
1759.5 | 50.5 | -1.0096
1759.6 | 50.5 | -1.0096
1759.7 | 50.5 | -1.0096
1759.8 | 50.5 | -1.0096
1759.9 | 50.5 | -1.0096
1760 | 50.5 | -1.0096
1760.1 | 50.5 | -1.0096
1760.2 | 50.5 | -1.0096
1760.3 | 50.5 | -1.0096
1760.4 | 50.5 | -1.0096
1760.5 | 50.5 | -1.0096
1760.6 | 50.5 | -1.0096
1760.7 | 50.5 | -1.0096
1760.8 | 50.5 | -1.0096
1760.9 | 50.5 | -1.0096
1761 | 50.5 | -1.0096
1761.1 | 50.5 | -1.0096
1761.2 | 50.5 | -1.0096
1761.3 | 50.5 | -1.0096
1761.4 | 50.5 | -1.0096
1761.5 | 50.5 | -1.0096
1761.6 | 50.5 | -1.0096
1761.7 | 50.5 | -1.0096
1761.8 | 50.5 | -1.0096
1761.9 | 50.5 | -1.0096
1762 | 50.5 | -1.0094
1762.1 | 50.5 | -1.0094
1762.2 | 50.5 | -1.0094
1762.3 | 50.5 | -1.0094
1762.4 | 50.5 | -1.0094
1762.5 | 50.5 | -1.0094
1762.6 | 50.5 | -1.0094
1762.7 | 50.5 | -1.0094
1762.8 | 50.5 | -1.0096
1762.9 | 50.5 | -1.0096
1763 | 50.5 | -1.0096
1763.1 | 50.5 | -1.0096
1763.2 | 50.5 | -1.0096
1763.3 | 50.5 | -1.0096
1763.4 | 50.5 | -1.0096
1763.5 | 50.5 | -1.0096
1763.6 | 50.5 | -1.0096
1763.7 | 50.5 | -1.0096
1763.8 | 50.5 | -1.0096
1763.9 | 50.5 | -1.0096
1764 | 50.5 | -1.0096
1764.1 | 50.5 | -1.0096
1764.2 | 50.5 | -1.0094
1764.3 | 50.5 | -1.0094
1764.4 | 50.5 | -1.0096
1764.5 | 50.5 | -1.0096
1764.6 | 50.5 | -1.0096
1764.7 | 50.5 | -1.0096
1764.8 | 50.5 | -1.0096
1764.9 | 50.5 | -1.0096
1765 | 50.5 | -1.0096
1765.1 | 50.5 | -1.0096
1765.2 | 50.5 | -1.0096
1765.3 | 50.5 | -1.0096
1765.4 | 50.5 | -1.0096
1765.5 | 50.5 | -1.0096
1765.6 | 50.5 | -1.0096
1765.7 | 50.5 | -1.0096
1765.8 | 50.5 | -1.0096
1765.9 | 50.5 | -1.0096
1766 | 50.5 | -1.0096
1766.1 | 50.5 | -1.0096
1766.2 | 50.5 | -1.0096
1766.3 | 50.5 | -1.0096
1766.4 | 50.5 | -1.0096
1766.5 | 50.5 | -1.0096
1766.6 | 50.5 | -1.0096
1766.7 | 50.5 | -1.0096
1766.8 | 50.5 | -1.0096
1766.9 | 50.5 | -1.0096
1767 | 50.5 | -1.0096
1767.1 | 50.5 | -1.0096
1767.2 | 50.5 | -1.0096
1767.3 | 50.5 | -1.0096
1767.4 | 50.5 | -1.0096
1767.5 | 50.5 | -1.0096
1767.6 | 50.5 | -1.0096
1767.7 | 50.5 | -1.0096
1767.8 | 50.5 | -1.0096
1767.9 | 50.5 | -1.0094
1768 | 50.5 | -1.0094
1768.1 | 50.5 | -1.0094
1768.2 | 50.5 | -1.0094
1768.3 | 50.5 | -1.0094
1768.4 | 50.5 | -1.0094
1768.5 | 50.5 | -1.0094
1768.6 | 50.5 | -1.0094
1768.7 | 50.5 | -1.0094
1768.8 | 50.5 | -1.0094
1768.9 | 50.5 | -1.0094
1769 | 50.5 | -1.0094
1769.1 | 50.5 | -1.0094
1769.2 | 50.5 | -1.0094
1769.3 | 50.5 | -1.0094
1769.4 | 50.5 | -1.0094
1769.5 | 50.5 | -1.0094
1769.6 | 50.5 | -1.0094
1769.7 | 50.5 | -1.0094
1769.8 | 50.5 | -1.0094
1769.9 | 50.5 | -1.0094
1770 | 50.5 | -1.0094
1770.1 | 50.5 | -1.0094
1770.2 | 50.5 | -1.0096
1770.3 | 50.5 | -1.0096
1770.4 | 50.5 | -1.0096
1770.5 | 50.5 | -1.0096
1770.6 | 50.5 | -1.0096
1770.7 | 50.5 | -1.0096
1770.8 | 50.5 | -1.0096
1770.9 | 50.5 | -1.0096
1771 | 50.5 | -1.0096
1771.1 | 50.5 | -1.0096
1771.2 | 50.5 | -1.0096
1771.3 | 50.5 | -1.0096
1771.4 | 50.5 | -1.0096
1771.5 | 50.5 | -1.0096
1771.6 | 50.5 | -1.0096
1771.7 | 50.5 | -1.0096
1771.8 | 50.5 | -1.0096
1771.9 | 50.5 | -1.0096
1772 | 50.5 | -1.0096
1772.1 | 50.5 | -1.0096
1772.2 | 50.5 | -1.0096
1772.3 | 50.5 | -1.0096
1772.4 | 50.5 | -1.0096
1772.5 | 50.5 | -1.0096
1772.6 | 50.5 | -1.0096
1772.7 | 50.5 | -1.0096
1772.8 | 50.5 | -1.0096
1772.9 | 50.5 | -1.0096
1773 | 50.5 | -1.0096
1773.1 | 50.5 | -1.0096
1773.2 | 50.5 | -1.0096
1773.3 | 50.5 | -1.0096
1773.4 | 50.5 | -1.0096
1773.5 | 50.5 | -1.0096
1773.6 | 50.5 | -1.0096
1773.7 | 50.5 | -1.0096
1773.8 | 50.5 | -1.0096
1773.9 | 50.5 | -1.0096
1774 | 50.5 | -1.0096
1774.1 | 50.5 | -1.0096
1774.2 | 50.5 | -1.0096
1774.3 | 50.5 | -1.0096
1774.4 | 50.5 | -1.0096
1774.5 | 50.5 | -1.0096
1774.6 | 50.5 | -1.0096
1774.7 | 50.5 | -1.0096
1774.8 | 50.5 | -1.0096
1774.9 | 50.5 | -1.0096
1775 | 50.5 | -1.0096
1775.1 | 50.5 | -1.0096
1775.2 | 50.5 | -1.0096
1775.3 | 50.5 | -1.0096
1775.4 | 50.5 | -1.0096
1775.5 | 50.5 | -1.0096
1775.6 | 50.5 | -1.0096
1775.7 | 50.5 | -1.0096
1775.8 | 50.5 | -1.0096
1775.9 | 50.5 | -1.0096
1776 | 50.5 | -1.0096
1776.1 | 50.5 | -1.0096
1776.2 | 50.5 | -1.0096
1776.3 | 50.5 | -1.0096
1776.4 | 50.5 | -1.0096
1776.5 | 50.5 | -1.0096
1776.6 | 50.5 | -1.0096
1776.7 | 50.5 | -1.0096
1776.8 | 50.5 | -1.0096
1776.9 | 50.5 | -1.0096
1777 | 50.5 | -1.0096
1777.1 | 50.5 | -1.0096
1777.2 | 50.5 | -1.0096
1777.3 | 50.5 | -1.0096
1777.4 | 50.5 | -1.0096
1777.5 | 50.5 | -1.0096
1777.6 | 50.5 | -1.0096
1777.7 | 50.5 | -1.0096
1777.8 | 50.5 | -1.0096
1777.9 | 50.5 | -1.0096
1778 | 50.5 | -1.0096
1778.1 | 50.5 | -1.0096
1778.2 | 50.5 | -1.0096
1778.3 | 50.5 | -1.0096
1778.4 | 50.5 | -1.0096
1778.5 | 50.5 | -1.0096
1778.6 | 50.5 | -1.0096
1778.7 | 50.5 | -1.0096
1778.8 | 50.5 | -1.0096
1778.9 | 50.5 | -1.0096
1779 | 50.5 | -1.0096
1779.1 | 50.5 | -1.0096
1779.2 | 50.5 | -1.0096
1779.3 | 50.5 | -1.0096
1779.4 | 50.5 | -1.0096
1779.5 | 50.5 | -1.0096
1779.6 | 50.5 | -1.0096
1779.7 | 50.5 | -1.0096
1779.8 | 50.5 | -1.0096
1779.9 | 50.5 | -1.0096
1780 | 50.5 | -1.0096
1780.1 | 50.5 | -1.0096
1780.2 | 50.5 | -1.0096
1780.3 | 50.5 | -1.0096
1780.4 | 50.5 | -1.0096
1780.5 | 50.5 | -1.0096
1780.6 | 50.5 | -1.0096
1780.7 | 50.5 | -1.0096
1780.8 | 50.5 | -1.0096
1780.9 | 50.5 | -1.0096
1781 | 50.5 | -1.0096
1781.1 | 50.5 | -1.0096
1781.2 | 50.5 | -1.0096
1781.3 | 50.5 | -1.0096
1781.4 | 50.5 | -1.0096
1781.5 | 50.5 | -1.0096
1781.6 | 50.5 | -1.0096
1781.7 | 50.5 | -1.0096
1781.8 | 50.5 | -1.0096
1781.9 | 50.5 | -1.0096
1782 | 50.5 | -1.0096
1782.1 | 50.5 | -1.0096
1782.2 | 50.5 | -1.0096
1782.3 | 50.5 | -1.0096
1782.4 | 50.5 | -1.0096
1782.5 | 50.5 | -1.0096
1782.6 | 50.5 | -1.0096
1782.7 | 50.5 | -1.0096
1782.8 | 50.5 | -1.0096
1782.9 | 50.5 | -1.0096
1783 | 50.5 | -1.0096
1783.1 | 50.5 | -1.0096
1783.2 | 50.5 | -1.0096
1783.3 | 50.5 | -1.0096
1783.4 | 50.5 | -1.0096
1783.5 | 50.5 | -1.0096
1783.6 | 50.5 | -1.0096
1783.7 | 50.5 | -1.0096
1783.8 | 50.5 | -1.0096
1783.9 | 50.5 | -1.0096
1784 | 50.5 | -1.0096
1784.1 | 50.5 | -1.0096
1784.2 | 50.5 | -1.0096
1784.3 | 50.5 | -1.0096
1784.4 | 50.5 | -1.0096
1784.5 | 50.5 | -1.0096
1784.6 | 50.5 | -1.0096
1784.7 | 50.5 | -1.0096
1784.8 | 50.5 | -1.0096
1784.9 | 50.5 | -1.0096
1785 | 50.5 | -1.0096
1785.1 | 50.5 | -1.0096
1785.2 | 50.5 | -1.0096
1785.3 | 50.5 | -1.0096
1785.4 | 50.5 | -1.0094
1785.5 | 50.5 | -1.0094
1785.6 | 50.5 | -1.0094
1785.7 | 50.5 | -1.0094
1785.8 | 50.5 | -1.0094
1785.9 | 50.5 | -1.0094
1786 | 50.5 | -1.0094
1786.1 | 50.5 | -1.0094
1786.2 | 50.5 | -1.0094
1786.3 | 50.5 | -1.0094
1786.4 | 50.5 | -1.0096
1786.5 | 50.5 | -1.0096
1786.6 | 50.5 | -1.0096
1786.7 | 50.5 | -1.0096
1786.8 | 50.5 | -1.0096
1786.9 | 50.5 | -1.0096
1787 | 50.5 | -1.0096
1787.1 | 50.5 | -1.0096
1787.2 | 50.5 | -1.0096
1787.3 | 50.5 | -1.0096
1787.4 | 50.5 | -1.0094
1787.5 | 50.5 | -1.0094
1787.6 | 50.5 | -1.0094
1787.7 | 50.5 | -1.0094
1787.8 | 50.5 | -1.0094
1787.9 | 50.5 | -1.0094
1788 | 50.5 | -1.0094
1788.1 | 50.5 | -1.0094
1788.2 | 50.5 | -1.0094
1788.3 | 50.5 | -1.0094
1788.4 | 50.5 | -1.0094
1788.5 | 50.5 | -1.0094
1788.6 | 50.5 | -1.0094
1788.7 | 50.5 | -1.0094
1788.8 | 50.5 | -1.0094
1788.9 | 50.5 | -1.0094
1789 | 50.5 | -1.0094
1789.1 | 50.5 | -1.0094
1789.2 | 50.5 | -1.0094
1789.3 | 50.5 | -1.0094
1789.4 | 50.5 | -1.0094
1789.5 | 50.5 | -1.0094
1789.6 | 50.5 | -1.0094
1789.7 | 50.5 | -1.0096
1789.8 | 50.5 | -1.0096
1789.9 | 50.5 | -1.0096
1790 | 50.5 | -1.0096
1790.1 | 50.5 | -1.0096
1790.2 | 50.5 | -1.0096
1790.3 | 50.5 | -1.0096
1790.4 | 50.5 | -1.0096
1790.5 | 50.5 | -1.0096
1790.6 | 50.5 | -1.0096
1790.7 | 50.5 | -1.0096
1790.8 | 50.5 | -1.0096
1790.9 | 50.5 | -1.0096
1791 | 50.5 | -1.0096
1791.1 | 50.5 | -1.0096
1791.2 | 50.5 | -1.0096
1791.3 | 50.5 | -1.0096
1791.4 | 50.5 | -1.0096
1791.5 | 50.5 | -1.0096
1791.6 | 50.5 | -1.0096
1791.7 | 50.5 | -1.0096
1791.8 | 50.5 | -1.0096
1791.9 | 50.5 | -1.0096
1792 | 50.5 | -1.0096
1792.1 | 50.5 | -1.0096
1792.2 | 50.5 | -1.0094
1792.3 | 50.5 | -1.0094
1792.4 | 50.5 | -1.0094
1792.5 | 50.5 | -1.0094
1792.6 | 50.5 | -1.0094
1792.7 | 50.5 | -1.0094
1792.8 | 50.5 | -1.0094
1792.9 | 50.5 | -1.0094
1793 | 50.5 | -1.0094
1793.1 | 50.5 | -1.0094
1793.2 | 50.5 | -1.0094
1793.3 | 50.5 | -1.0094
1793.4 | 50.5 | -1.0094
1793.5 | 50.5 | -1.0094
1793.6 | 50.5 | -1.0094
1793.7 | 50.5 | -1.0094
1793.8 | 50.5 | -1.0094
1793.9 | 50.5 | -1.0094
1794 | 50.5 | -1.0094
1794.1 | 50.5 | -1.0094
1794.2 | 50.5 | -1.0094
1794.3 | 50.5 | -1.0094
1794.4 | 50.5 | -1.0094
1794.5 | 50.5 | -1.0094
1794.6 | 50.5 | -1.0094
1794.7 | 50.5 | -1.0094
1794.8 | 50.5 | -1.0094
1794.9 | 50.5 | -1.0094
1795 | 50.5 | -1.0094
1795.1 | 50.5 | -1.0094
1795.2 | 50.5 | -1.0094
1795.3 | 50.5 | -1.0094
1795.4 | 50.5 | -1.0094
1795.5 | 50.5 | -1.0094
1795.6 | 50.5 | -1.0096
1795.7 | 50.5 | -1.0096
1795.8 | 50.5 | -1.0096
1795.9 | 50.5 | -1.0096
1796 | 50.5 | -1.0096
1796.1 | 50.5 | -1.0096
1796.2 | 50.5 | -1.0096
1796.3 | 50.5 | -1.0096
1796.4 | 50.5 | -1.0096
1796.5 | 50.5 | -1.0096
1796.6 | 50.5 | -1.0096
1796.7 | 50.5 | -1.0096
1796.8 | 50.5 | -1.0096
1796.9 | 50.5 | -1.0096
1797 | 50.5 | -1.0096
1797.1 | 50.5 | -1.0096
1797.2 | 50.5 | -1.0096
1797.3 | 50.5 | -1.0096
1797.4 | 50.5 | -1.0096
1797.5 | 50.5 | -1.0096
1797.6 | 50.5 | -1.0096
1797.7 | 50.5 | -1.0096
1797.8 | 50.5 | -1.0096
1797.9 | 50.5 | -1.0096
1798 | 50.5 | -1.0096
1798.1 | 50.5 | -1.0096
1798.2 | 50.5 | -1.0096
1798.3 | 50.5 | -1.0096
1798.4 | 50.5 | -1.0096
1798.5 | 50.5 | -1.0096
1798.6 | 50.5 | -1.0096
1798.7 | 50.5 | -1.0096
1798.8 | 50.5 | -1.0096
1798.9 | 50.5 | -1.0096
1799 | 50.5 | -1.0096
1799.1 | 50.5 | -1.0096
1799.2 | 50.5 | -1.0096
1799.3 | 50.5 | -1.0096
1799.4 | 50.5 | -1.0096
1799.5 | 50.5 | -1.0096
1799.6 | 50.5 | -1.0096
1799.7 | 50.5 | -1.0096
1799.8 | 50.5 | -1.0096
1799.9 | 50.5 | -1.0096
1800 | 50.5 | -1.0096
1800.1 | 50.5 | -1.0096
1800.2 | 50.5 | -1.0096
1800.3 | 50.5 | -1.0096
1800.4 | 50.5 | -1.0096
1800.5 | 50.5 | -1.0096
1800.6 | 50.5 | -1.0096
1800.7 | 50.5 | -1.0096
1800.8 | 50.5 | -1.0096
1800.9 | 50.5 | -1.0096
1801 | 50.5 | -1.0096
1801.1 | 50.5 | -1.0096
1801.2 | 50.5 | -1.0096
1801.3 | 50.5 | -1.0096
1801.4 | 50.5 | -1.0096
1801.5 | 50.5 | -1.0096
1801.6 | 50.5 | -1.0096
1801.7 | 50.5 | -1.0096
1801.8 | 50.5 | -1.0096
1801.9 | 50.5 | -1.0096
1802 | 50.5 | -1.0096
1802.1 | 50.5 | -1.0096
1802.2 | 50.5 | -1.0096
1802.3 | 50.5 | -1.0096
1802.4 | 50.5 | -1.0096
1802.5 | 50.5 | -1.0096
1802.6 | 50.5 | -1.0096
1802.7 | 50.5 | -1.0096
1802.8 | 50.5 | -1.0096
1802.9 | 50.5 | -1.0096
1803 | 50.5 | -1.0096
1803.1 | 50.5 | -1.0096
1803.2 | 50.5 | -1.0096
1803.3 | 50.5 | -1.0096
1803.4 | 50.5 | -1.0096
1803.5 | 50.5 | -1.0096
1803.6 | 50.5 | -1.0096
1803.7 | 50.5 | -1.0096
1803.8 | 50.5 | -1.0096
1803.9 | 50.5 | -1.0096
1804 | 50.5 | -1.0096
1804.1 | 50.5 | -1.0096
1804.2 | 50.5 | -1.0096
1804.3 | 50.5 | -1.0096
1804.4 | 50.5 | -1.0096
1804.5 | 50.5 | -1.0096
1804.6 | 50.5 | -1.0096
1804.7 | 50.5 | -1.0096
1804.8 | 50.5 | -1.0096
1804.9 | 50.5 | -1.0096
1805 | 50.5 | -1.0096
1805.1 | 50.5 | -1.0096
1805.2 | 50.5 | -1.0096
1805.3 | 50.5 | -1.0096
1805.4 | 50.5 | -1.0096
1805.5 | 50.5 | -1.0096
1805.6 | 50.5 | -1.0096
1805.7 | 50.5 | -1.0096
1805.8 | 50.5 | -1.0096
1805.9 | 50.5 | -1.0096
1806 | 50.5 | -1.0096
1806.1 | 50.5 | -1.0096
1806.2 | 50.5 | -1.0096
1806.3 | 50.5 | -1.0096
1806.4 | 50.5 | -1.0096
1806.5 | 50.5 | -1.0096
1806.6 | 50.5 | -1.0096
1806.7 | 50.5 | -1.0096
1806.8 | 50.5 | -1.0096
1806.9 | 50.5 | -1.0096
1807 | 50.5 | -1.0096
1807.1 | 50.5 | -1.0096
1807.2 | 50.5 | -1.0096
1807.3 | 50.5 | -1.0096
1807.4 | 50.5 | -1.0096
1807.5 | 50.5 | -1.0096
1807.6 | 50.5 | -1.0096
1807.7 | 50.5 | -1.0096
1807.8 | 50.5 | -1.0096
1807.9 | 50.5 | -1.0096
1808 | 50.5 | -1.0096
1808.1 | 50.5 | -1.0096
1808.2 | 50.5 | -1.0096
1808.3 | 50.5 | -1.0096
1808.4 | 50.5 | -1.0096
1808.5 | 50.5 | -1.0096
1808.6 | 50.5 | -1.0096
1808.7 | 50.5 | -1.0096
1808.8 | 50.5 | -1.0096
1808.9 | 50.5 | -1.0096
1809 | 50.5 | -1.0096
1809.1 | 50.5 | -1.0096
1809.2 | 50.5 | -1.0096
1809.3 | 50.5 | -1.0096
1809.4 | 50.5 | -1.0096
1809.5 | 50.5 | -1.0096
1809.6 | 50.5 | -1.0096
1809.7 | 50.5 | -1.0096
1809.8 | 50.5 | -1.0094
1809.9 | 50.5 | -1.0094
1810 | 50.5 | -1.0094
1810.1 | 50.5 | -1.0094
1810.2 | 50.5 | -1.0094
1810.3 | 50.5 | -1.0094
1810.4 | 50.5 | -1.0094
1810.5 | 50.5 | -1.0094
1810.6 | 50.5 | -1.0094
1810.7 | 50.5 | -1.0094
1810.8 | 50.5 | -1.0094
1810.9 | 50.5 | -1.0094
1811 | 50.5 | -1.0094
1811.1 | 50.5 | -1.0094
1811.2 | 50.5 | -1.0094
1811.3 | 50.5 | -1.0094
1811.4 | 50.5 | -1.0094
1811.5 | 50.5 | -1.0094
1811.6 | 50.5 | -1.0094
1811.7 | 50.5 | -1.0094
1811.8 | 50.5 | -1.0094
1811.9 | 50.5 | -1.0094
1812 | 50.5 | -1.0096
1812.1 | 50.5 | -1.0096
1812.2 | 50.5 | -1.0096
1812.3 | 50.5 | -1.0096
1812.4 | 50.5 | -1.0096
1812.5 | 50.5 | -1.0096
1812.6 | 50.5 | -1.0096
1812.7 | 50.5 | -1.0096
1812.8 | 50.5 | -1.0096
1812.9 | 50.5 | -1.0096
1813 | 50.5 | -1.0096
1813.1 | 50.5 | -1.0096
1813.2 | 50.5 | -1.0096
1813.3 | 50.5 | -1.0096
1813.4 | 50.5 | -1.0096
1813.5 | 50.5 | -1.0096
1813.6 | 50.5 | -1.0096
1813.7 | 50.5 | -1.0096
1813.8 | 50.5 | -1.0096
1813.9 | 50.5 | -1.0096
1814 | 50.5 | -1.0096
1814.1 | 50.5 | -1.0096
1814.2 | 50.5 | -1.0096
1814.3 | 50.5 | -1.0096
1814.4 | 50.5 | -1.0096
1814.5 | 50.5 | -1.0096
1814.6 | 50.5 | -1.0096
1814.7 | 50.5 | -1.0096
1814.8 | 50.5 | -1.0096
1814.9 | 50.5 | -1.0096
1815 | 50.5 | -1.0096
1815.1 | 50.5 | -1.0096
1815.2 | 50.5 | -1.0096
1815.3 | 50.5 | -1.0096
1815.4 | 50.5 | -1.0096
1815.5 | 50.5 | -1.0096
1815.6 | 50.5 | -1.0096
1815.7 | 50.5 | -1.0096
1815.8 | 50.5 | -1.0096
1815.9 | 50.5 | -1.0096
1816 | 50.5 | -1.0096
1816.1 | 50.5 | -1.0096
1816.2 | 50.5 | -1.0096
1816.3 | 50.5 | -1.0096
1816.4 | 50.5 | -1.0096
1816.5 | 50.5 | -1.0096
1816.6 | 50.5 | -1.0094
1816.7 | 50.5 | -1.0094
1816.8 | 50.5 | -1.0094
1816.9 | 50.5 | -1.0094
1817 | 50.5 | -1.0094
1817.1 | 50.5 | -1.0094
1817.2 | 50.5 | -1.0094
1817.3 | 50.5 | -1.0094
1817.4 | 50.5 | -1.0094
1817.5 | 50.5 | -1.0094
1817.6 | 50.5 | -1.0094
1817.7 | 50.5 | -1.0094
1817.8 | 50.5 | -1.0094
1817.9 | 50.5 | -1.0094
1818 | 50.5 | -1.0094
1818.1 | 50.5 | -1.0094
1818.2 | 50.5 | -1.0094
1818.3 | 50.5 | -1.0094
1818.4 | 50.5 | -1.0094
1818.5 | 50.5 | -1.0094
1818.6 | 50.5 | -1.0094
1818.7 | 50.5 | -1.0094
1818.8 | 50.5 | -1.0094
1818.9 | 50.5 | -1.0096
1819 | 50.5 | -1.0096
1819.1 | 50.5 | -1.0096
1819.2 | 50.5 | -1.0096
1819.3 | 50.5 | -1.0096
1819.4 | 50.5 | -1.0094
1819.5 | 50.5 | -1.0094
1819.6 | 50.5 | -1.0094
1819.7 | 50.5 | -1.0094
1819.8 | 50.5 | -1.0094
1819.9 | 50.5 | -1.0094
1820 | 50.5 | -1.0094
1820.1 | 50.5 | -1.0094
1820.2 | 50.5 | -1.0094
1820.3 | 50.5 | -1.0096
1820.4 | 50.5 | -1.0096
1820.5 | 50.5 | -1.0096
1820.6 | 50.5 | -1.0096
1820.7 | 50.5 | -1.0096
1820.8 | 50.5 | -1.0096
1820.9 | 50.5 | -1.0096
1821 | 50.5 | -1.0096
1821.1 | 50.5 | -1.0096
1821.2 | 50.5 | -1.0096
1821.3 | 50.5 | -1.0096
1821.4 | 50.5 | -1.0094
1821.5 | 50.5 | -1.0094
1821.6 | 50.5 | -1.0096
1821.7 | 50.5 | -1.0096
1821.8 | 50.5 | -1.0096
1821.9 | 50.5 | -1.0096
1822 | 50.5 | -1.0096
1822.1 | 50.5 | -1.0096
1822.2 | 50.5 | -1.0096
1822.3 | 50.5 | -1.0096
1822.4 | 50.5 | -1.0096
1822.5 | 50.5 | -1.0096
1822.6 | 50.5 | -1.0096
1822.7 | 50.5 | -1.0096
1822.8 | 50.5 | -1.0096
1822.9 | 50.5 | -1.0096
1823 | 50.5 | -1.0096
1823.1 | 50.5 | -1.0096
1823.2 | 50.5 | -1.0096
1823.3 | 50.5 | -1.0096
1823.4 | 50.5 | -1.0096
1823.5 | 50.5 | -1.0096
1823.6 | 50.5 | -1.0096
1823.7 | 50.5 | -1.0096
1823.8 | 50.5 | -1.0094
1823.9 | 50.5 | -1.0094
1824 | 50.5 | -1.0094
1824.1 | 50.5 | -1.0094
1824.2 | 50.5 | -1.0094
1824.3 | 50.5 | -1.0094
1824.4 | 50.5 | -1.0094
1824.5 | 50.5 | -1.0094
1824.6 | 50.5 | -1.0094
1824.7 | 50.5 | -1.0094
1824.8 | 50.5 | -1.0096
1824.9 | 50.5 | -1.0096
1825 | 50.5 | -1.0096
1825.1 | 50.5 | -1.0096
1825.2 | 50.5 | -1.0096
1825.3 | 50.5 | -1.0096
1825.4 | 50.5 | -1.0096
1825.5 | 50.5 | -1.0096
1825.6 | 50.5 | -1.0096
1825.7 | 50.5 | -1.0096
1825.8 | 50.5 | -1.0096
1825.9 | 50.5 | -1.0096
1826 | 50.5 | -1.0096
1826.1 | 50.5 | -1.0096
1826.2 | 50.5 | -1.0096
1826.3 | 50.5 | -1.0096
1826.4 | 50.5 | -1.0096
1826.5 | 50.5 | -1.0096
1826.6 | 50.5 | -1.0096
1826.7 | 50.5 | -1.0096
1826.8 | 50.5 | -1.0096
1826.9 | 50.5 | -1.0096
1827 | 50.5 | -1.0096
1827.1 | 50.5 | -1.0096
1827.2 | 50.5 | -1.0096
1827.3 | 50.5 | -1.0094
1827.4 | 50.5 | -1.0094
1827.5 | 50.5 | -1.0094
1827.6 | 50.5 | -1.0094
1827.7 | 50.5 | -1.0094
1827.8 | 50.5 | -1.0094
1827.9 | 50.5 | -1.0094
1828 | 50.5 | -1.0094
1828.1 | 50.5 | -1.0094
1828.2 | 50.5 | -1.0094
1828.3 | 50.5 | -1.0094
1828.4 | 50.5 | -1.0094
1828.5 | 50.5 | -1.0094
1828.6 | 50.5 | -1.0094
1828.7 | 50.5 | -1.0094
1828.8 | 50.5 | -1.0094
1828.9 | 50.5 | -1.0094
1829 | 50.5 | -1.0094
1829.1 | 50.5 | -1.0094
1829.2 | 50.5 | -1.0094
1829.3 | 50.5 | -1.0094
1829.4 | 50.5 | -1.0094
1829.5 | 50.5 | -1.0094
1829.6 | 50.5 | -1.0094
1829.7 | 50.5 | -1.0096
1829.8 | 50.5 | -1.0096
1829.9 | 50.5 | -1.0096
1830 | 50 | -1.0096
1830.1 | 50 | -1.0096
1830.2 | 50 | -1.0096
1830.3 | 50 | -1.0096
1830.4 | 50 | -1.0096
1830.5 | 50 | -1.0096
1830.6 | 50 | -1.0096
1830.7 | 50 | -1.0096
1830.8 | 50 | -1.0096
1830.9 | 50 | -1.0096
1831 | 50 | -1.0096
1831.1 | 50 | -1.0096
1831.2 | 50 | -0.8156
1831.3 | 50 | -0.22
1831.4 | 50 | -0.0296
1831.5 | 50 | -0.0102
1831.6 | 50 | -0.0006
1831.7 | 50 | -0.0002
1831.8 | 50 | -0.0002
1831.9 | 50 | -0.0002
1832 | 50 | -0.0002
1832.1 | 50 | -0.0002
1832.2 | 50 | -0.0002
1832.3 | 50 | -0.0002
1832.4 | 50 | -0.0002
1832.5 | 50 | -0.0002
1832.6 | 50 | -0.0002
1832.7 | 50 | -0.0002
1832.8 | 50 | -0.0002
1832.9 | 50 | -0.0002
1833 | 50 | -0.0002
1833.1 | 50 | -0.0002
1833.2 | 50 | -0.0002
1833.3 | 50 | -0.0004
1833.4 | 50 | -0.0004
1833.5 | 50 | -0.0006
1833.6 | 50 | -0.0006
1833.7 | 50 | -0.0008
1833.8 | 50 | -0.0008
1833.9 | 50 | -0.0008
1834 | 50 | -0.0008
1834.1 | 50 | -0.0008
1834.2 | 50 | -0.0008
1834.3 | 50 | -0.001
1834.4 | 50 | -0.001
1834.5 | 50 | -0.001
1834.6 | 50 | -0.001
1834.7 | 50 | -0.001
1834.8 | 50 | -0.001
1834.9 | 50 | -0.001
1835 | 50 | -0.0008
1835.1 | 50 | -0.0008
1835.2 | 50 | -0.0008
1835.3 | 50 | -0.0008
1835.4 | 50 | -0.0008
1835.5 | 50 | -0.0008
1835.6 | 50 | -0.0008
1835.7 | 50 | -0.0008
1835.8 | 50 | -0.0008
1835.9 | 50 | -0.0008
1836 | 50 | -0.0008
1836.1 | 50 | -0.0006
1836.2 | 50 | -0.0002
1836.3 | 50 | -0.0002
1836.4 | 50 | -0.0002
1836.5 | 50 | -0.0002
1836.6 | 50 | -0.0002
1836.7 | 50 | -0.0002
1836.8 | 50 | -0.0004
1836.9 | 50 | -0.0004
1837 | 50 | -0.0004
1837.1 | 50 | -0.0004
1837.2 | 50 | -0.0004
1837.3 | 50 | -0.0004
1837.4 | 50 | -0.0004
1837.5 | 50 | -0.0004
1837.6 | 50 | -0.0002
1837.7 | 50 | -0.0002
1837.8 | 50 | -0.0002
1837.9 | 50 | 0
1838 | 50 | -0.0002
1838.1 | 50 | -0.0002
1838.2 | 50 | 0
1838.3 | 50 | 0
1838.4 | 50 | 0
1838.5 | 50 | 0
1838.6 | 50 | 0
1838.7 | 50 | 0
1838.8 | 50 | 0
1838.9 | 50 | 0
1839 | 50 | 0
1839.1 | 50 | 0
1839.2 | 50 | 0
1839.3 | 50 | 0
1839.4 | 50 | 0
1839.5 | 50 | 0
1839.6 | 50 | 0
1839.7 | 50 | 0
1839.8 | 50 | 0
1839.9 | 50 | 0
1840 | 50 | 0
1840.1 | 50 | 0
1840.2 | 50 | 0
1840.3 | 50 | 0
1840.4 | 50 | 0
1840.5 | 50 | 0
1840.6 | 50 | 0
1840.7 | 50 | 0
1840.8 | 50 | 0
1840.9 | 50 | 0
1841 | 50 | 0
1841.1 | 50 | 0
1841.2 | 50 | 0
1841.3 | 50 | 0
1841.4 | 50 | 0
1841.5 | 50 | 0
1841.6 | 50 | 0
1841.7 | 50 | 0
1841.8 | 50 | 0
1841.9 | 50 | 0
1842 | 50 | 0
1842.1 | 50 | 0
1842.2 | 50 | 0
1842.3 | 50 | 0
1842.4 | 50 | 0
1842.5 | 50 | 0
1842.6 | 50 | 0
1842.7 | 50 | 0
1842.8 | 50 | 0
1842.9 | 50 | 0
1843 | 50 | 0
1843.1 | 50 | 0
1843.2 | 50 | 0
1843.3 | 50 | 0
1843.4 | 50 | 0
1843.5 | 50 | 0
1843.6 | 50 | 0
1843.7 | 50 | 0
1843.8 | 50 | 0
1843.9 | 50 | 0
1844 | 50 | 0
1844.1 | 50 | 0
1844.2 | 50 | 0
1844.3 | 50 | 0
1844.4 | 50 | 0
1844.5 | 50 | 0
1844.6 | 50 | 0
1844.7 | 50 | 0
1844.8 | 50 | 0
1844.9 | 50 | 0
1845 | 50 | 0
1845.1 | 50 | 0
1845.2 | 50 | 0
1845.3 | 50 | 0
1845.4 | 50 | 0
1845.5 | 50 | 0
1845.6 | 50 | 0
1845.7 | 50 | 0
1845.8 | 50 | 0
1845.9 | 50 | 0
1846 | 50 | 0
1846.1 | 50 | 0
1846.2 | 50 | 0
1846.3 | 50 | 0
1846.4 | 50 | 0
1846.5 | 50 | 0
1846.6 | 50 | 0
1846.7 | 50 | 0
1846.8 | 50 | 0
1846.9 | 50 | 0
1847 | 50 | 0
1847.1 | 50 | 0
1847.2 | 50 | 0
1847.3 | 50 | 0
1847.4 | 50 | 0
1847.5 | 50 | 0
1847.6 | 50 | 0
1847.7 | 50 | 0
1847.8 | 50 | 0
1847.9 | 50 | 0
1848 | 50 | 0
1848.1 | 50 | 0
1848.2 | 50 | 0
1848.3 | 50 | 0
1848.4 | 50 | 0
1848.5 | 50 | 0
1848.6 | 50 | 0
1848.7 | 50 | 0
1848.8 | 50 | 0
1848.9 | 50 | 0
1849 | 50 | 0
1849.1 | 50 | 0
1849.2 | 50 | 0
1849.3 | 50 | 0
1849.4 | 50 | 0
1849.5 | 50 | 0
1849.6 | 50 | 0
1849.7 | 50 | 0
1849.8 | 50 | 0
1849.9 | 50 | 0
1850 | 50 | 0
1850.1 | 50 | 0
1850.2 | 50 | 0
1850.3 | 50 | 0
1850.4 | 50 | 0
1850.5 | 50 | 0
1850.6 | 50 | 0
1850.7 | 50 | 0
1850.8 | 50 | 0
1850.9 | 50 | 0
1851 | 50 | 0
1851.1 | 50 | 0
1851.2 | 50 | 0
1851.3 | 50 | 0
1851.4 | 50 | 0
1851.5 | 50 | 0
1851.6 | 50 | 0
1851.7 | 50 | 0
1851.8 | 50 | 0
1851.9 | 50 | 0
1852 | 50 | 0
1852.1 | 50 | 0
1852.2 | 50 | 0
1852.3 | 50 | 0
1852.4 | 50 | 0
1852.5 | 50 | 0
1852.6 | 50 | 0
1852.7 | 50 | 0
1852.8 | 50 | 0
1852.9 | 50 | 0
1853 | 50 | 0
1853.1 | 50 | 0
1853.2 | 50 | 0
1853.3 | 50 | 0
1853.4 | 50 | 0
1853.5 | 50 | 0
1853.6 | 50 | 0
1853.7 | 50 | 0
1853.8 | 50 | 0
1853.9 | 50 | 0
1854 | 50 | 0
1854.1 | 50 | 0
1854.2 | 50 | 0
1854.3 | 50 | 0
1854.4 | 50 | 0
1854.5 | 50 | 0
1854.6 | 50 | 0
1854.7 | 50 | 0
1854.8 | 50 | 0
1854.9 | 50 | 0
1855 | 50 | 0
1855.1 | 50 | 0
1855.2 | 50 | 0
1855.3 | 50 | 0
1855.4 | 50 | 0
1855.5 | 50 | 0
1855.6 | 50 | 0
1855.7 | 50 | 0
1855.8 | 50 | 0
1855.9 | 50 | 0
1856 | 50 | 0
1856.1 | 50 | 0
1856.2 | 50 | 0
1856.3 | 50 | 0
1856.4 | 50 | 0
1856.5 | 50 | 0
1856.6 | 50 | 0
1856.7 | 50 | 0
1856.8 | 50 | 0
1856.9 | 50 | 0
1857 | 50 | 0
1857.1 | 50 | 0
1857.2 | 50 | 0
1857.3 | 50 | 0
1857.4 | 50 | 0
1857.5 | 50 | 0
1857.6 | 50 | 0
1857.7 | 50 | 0
1857.8 | 50 | 0
1857.9 | 50 | 0
1858 | 50 | 0
1858.1 | 50 | 0
1858.2 | 50 | 0
1858.3 | 50 | 0
1858.4 | 50 | 0
1858.5 | 50 | 0
1858.6 | 50 | 0
1858.7 | 50 | 0
1858.8 | 50 | 0
1858.9 | 50 | 0
1859 | 50 | 0
1859.1 | 50 | 0
1859.2 | 50 | 0
1859.3 | 50 | 0
1859.4 | 50 | 0
1859.5 | 50 | 0
1859.6 | 50 | 0
1859.7 | 50 | 0
1859.8 | 50 | 0
1859.9 | 50 | 0
1860 | 50 | 0
This sheet to be used for single or group of assets which are a subgroup of overall test.
In example shown, this is a 1MW asset which will be assessed as part of a 5MW Unit.
Example assumes this asset can sustain maximum response for 30 minutes. It not the case, adjust cell E13 'High End' accordingly and clearly state in test report.

## Test 1.2 Total
Time (s) | Frequency (Hz) | Active Power (MW)
0 | 50 | 0 | Time Value at Which Frequency Changes
0.1 | 50 | 0 |  |  |  |  | Frequency Change
0.2 | 50 | 0 |  |  |  |  | High Start
0.3 | 50 | 0 | 30 |  |  |  | 30
0.4 | 50 | 0 |  |  |  |  | 30
0.5 | 50 | 0 | High Start |  |  |  | 40
0.6 | 50 | 0 |  |  |  | $C$402 | 40
0.7 | 50 | 0 | 40 |  |  | $C$18301 | 40
0.8 | 50 | 0 |  |  |  |  | 60
0.9 | 50 | 0 | High End |  | High | -5.046 | 2 Second Limit
1 | 50 | 0 |  |  | SD | 0.00059041 | 32
1.1 | 50 | 0 | 1829.9 |  | % SD | 0.011808 | 32
1.2 | 50 | 0
1.3 | 50 | 0 | High Response
1.4 | 50 | 0 |  | pre-Average | 0
1.5 | 50 | 0 | -5.046 | (edit range to average 10s before frequency change)
1.6 | 50 | 0
1.7 | 50 | 0
1.8 | 50 | 0
1.9 | 50 | 0
2 | 50 | 0
2.1 | 50 | 0
2.2 | 50 | 0
2.3 | 50 | 0
2.4 | 50 | 0
2.5 | 50 | 0
2.6 | 50 | 0
2.7 | 50 | 0
2.8 | 50 | 0
2.9 | 50 | 0
3 | 50 | 0
3.1 | 50 | 0
3.2 | 50 | 0
3.3 | 50 | 0
3.4 | 50 | 0
3.5 | 50 | 0
3.6 | 50 | 0
3.7 | 50 | 0
3.8 | 50 | 0
3.9 | 50 | 0
4 | 50 | 0
4.1 | 50 | 0
4.2 | 50 | 0
4.3 | 50 | 0
4.4 | 50 | 0
4.5 | 50 | 0
4.6 | 50 | 0
4.7 | 50 | 0
4.8 | 50 | 0
4.9 | 50 | 0
5 | 50 | 0
5.1 | 50 | 0
5.2 | 50 | 0
5.3 | 50 | 0
5.4 | 50 | 0
5.5 | 50 | 0
5.6 | 50 | 0
5.7 | 50 | 0
5.8 | 50 | 0
5.9 | 50 | 0
6 | 50 | 0
6.1 | 50 | 0
6.2 | 50 | 0
6.3 | 50 | 0
6.4 | 50 | 0
6.5 | 50 | 0
6.6 | 50 | 0
6.7 | 50 | 0
6.8 | 50 | 0
6.9 | 50 | 0
7 | 50 | 0
7.1 | 50 | 0
7.2 | 50 | 0
7.3 | 50 | 0
7.4 | 50 | 0
7.5 | 50 | 0
7.6 | 50 | 0
7.7 | 50 | 0
7.8 | 50 | 0
7.9 | 50 | 0
8 | 50 | 0
8.1 | 50 | 0
8.2 | 50 | 0
8.3 | 50 | 0
8.4 | 50 | 0
8.5 | 50 | 0
8.6 | 50 | 0
8.7 | 50 | 0
8.8 | 50 | 0
8.9 | 50 | 0
9 | 50 | 0
9.1 | 50 | 0
9.2 | 50 | 0
9.3 | 50 | 0
9.4 | 50 | 0
9.5 | 50 | 0
9.6 | 50 | 0
9.7 | 50 | 0
9.8 | 50 | 0
9.9 | 50 | 0
10 | 50 | 0
10.1 | 50 | 0
10.2 | 50 | 0
10.3 | 50 | 0
10.4 | 50 | 0
10.5 | 50 | 0
10.6 | 50 | 0
10.7 | 50 | 0
10.8 | 50 | 0
10.9 | 50 | 0
11 | 50 | 0
11.1 | 50 | 0
11.2 | 50 | 0
11.3 | 50 | 0
11.4 | 50 | 0
11.5 | 50 | 0
11.6 | 50 | 0
11.7 | 50 | 0
11.8 | 50 | 0
11.9 | 50 | 0
12 | 50 | 0
12.1 | 50 | 0
12.2 | 50 | 0
12.3 | 50 | 0
12.4 | 50 | 0
12.5 | 50 | 0
12.6 | 50 | 0
12.7 | 50 | 0
12.8 | 50 | 0
12.9 | 50 | 0
13 | 50 | 0
13.1 | 50 | 0
13.2 | 50 | 0
13.3 | 50 | 0
13.4 | 50 | 0
13.5 | 50 | 0
13.6 | 50 | 0
13.7 | 50 | 0
13.8 | 50 | 0
13.9 | 50 | 0
14 | 50 | 0
14.1 | 50 | 0
14.2 | 50 | 0
14.3 | 50 | 0
14.4 | 50 | 0
14.5 | 50 | 0
14.6 | 50 | 0
14.7 | 50 | 0
14.8 | 50 | 0
14.9 | 50 | 0
15 | 50 | 0
15.1 | 50 | 0
15.2 | 50 | 0
15.3 | 50 | 0
15.4 | 50 | 0
15.5 | 50 | 0
15.6 | 50 | 0
15.7 | 50 | 0
15.8 | 50 | 0
15.9 | 50 | 0
16 | 50 | 0
16.1 | 50 | 0
16.2 | 50 | 0
16.3 | 50 | 0
16.4 | 50 | 0
16.5 | 50 | 0
16.6 | 50 | 0
16.7 | 50 | 0
16.8 | 50 | 0
16.9 | 50 | 0
17 | 50 | 0
17.1 | 50 | 0
17.2 | 50 | 0
17.3 | 50 | 0
17.4 | 50 | 0
17.5 | 50 | 0
17.6 | 50 | 0
17.7 | 50 | 0
17.8 | 50 | 0
17.9 | 50 | 0
18 | 50 | 0
18.1 | 50 | 0
18.2 | 50 | 0
18.3 | 50 | 0
18.4 | 50 | 0
18.5 | 50 | 0
18.6 | 50 | 0
18.7 | 50 | 0
18.8 | 50 | 0
18.9 | 50 | 0
19 | 50 | 0
19.1 | 50 | 0
19.2 | 50 | 0
19.3 | 50 | 0
19.4 | 50 | 0
19.5 | 50 | 0
19.6 | 50 | 0
19.7 | 50 | 0
19.8 | 50 | 0
19.9 | 50 | 0
20 | 50 | 0
20.1 | 50 | 0
20.2 | 50 | 0
20.3 | 50 | 0
20.4 | 50 | 0
20.5 | 50 | 0
20.6 | 50 | 0
20.7 | 50 | 0
20.8 | 50 | 0
20.9 | 50 | 0
21 | 50 | 0
21.1 | 50 | 0
21.2 | 50 | 0
21.3 | 50 | 0
21.4 | 50 | 0
21.5 | 50 | 0
21.6 | 50 | 0
21.7 | 50 | 0
21.8 | 50 | 0
21.9 | 50 | 0
22 | 50 | 0
22.1 | 50 | 0
22.2 | 50 | 0
22.3 | 50 | 0
22.4 | 50 | 0
22.5 | 50 | 0
22.6 | 50 | 0
22.7 | 50 | 0
22.8 | 50 | 0
22.9 | 50 | 0
23 | 50 | 0
23.1 | 50 | 0
23.2 | 50 | 0
23.3 | 50 | 0
23.4 | 50 | 0
23.5 | 50 | 0
23.6 | 50 | 0
23.7 | 50 | 0
23.8 | 50 | 0
23.9 | 50 | 0
24 | 50 | 0
24.1 | 50 | 0
24.2 | 50 | 0
24.3 | 50 | 0
24.4 | 50 | 0
24.5 | 50 | 0
24.6 | 50 | 0
24.7 | 50 | 0
24.8 | 50 | 0
24.9 | 50 | 0
25 | 50 | 0
25.1 | 50 | 0
25.2 | 50 | 0
25.3 | 50 | 0
25.4 | 50 | 0
25.5 | 50 | 0
25.6 | 50 | 0
25.7 | 50 | 0
25.8 | 50 | 0
25.9 | 50 | 0
26 | 50 | 0
26.1 | 50 | 0
26.2 | 50 | 0
26.3 | 50 | 0
26.4 | 50 | 0
26.5 | 50 | 0
26.6 | 50 | 0
26.7 | 50 | 0
26.8 | 50 | 0
26.9 | 50 | 0
27 | 50 | 0
27.1 | 50 | 0
27.2 | 50 | 0
27.3 | 50 | 0
27.4 | 50 | 0
27.5 | 50 | 0
27.6 | 50 | 0
27.7 | 50 | 0
27.8 | 50 | 0
27.9 | 50 | 0
28 | 50 | 0
28.1 | 50 | 0
28.2 | 50 | 0
28.3 | 50 | 0
28.4 | 50 | 0
28.5 | 50 | 0
28.6 | 50 | 0
28.7 | 50 | 0
28.8 | 50 | 0
28.9 | 50 | 0
29 | 50 | 0
29.1 | 50 | 0
29.2 | 50 | 0
29.3 | 50 | 0
29.4 | 50 | 0
29.5 | 50 | 0
29.6 | 50 | 0
29.7 | 50 | 0
29.8 | 50 | 0
29.9 | 50 | 0
30 | 50.5 | 0
30.1 | 50.5 | -0.025
30.2 | 50.5 | -0.092
30.3 | 50.5 | -2.979
30.4 | 50.5 | -4.91
30.5 | 50.5 | -5.018
30.6 | 50.5 | -5.083
30.7 | 50.5 | -5.079
30.8 | 50.5 | -5.078
30.9 | 50.5 | -5.078
31 | 50.5 | -5.078
31.1 | 50.5 | -5.077
31.2 | 50.5 | -5.078
31.3 | 50.5 | -5.078
31.4 | 50.5 | -5.078
31.5 | 50.5 | -5.078
31.6 | 50.5 | -5.079
31.7 | 50.5 | -5.078
31.8 | 50.5 | -5.078
31.9 | 50.5 | -5.078
32 | 50.5 | -5.079
32.1 | 50.5 | -5.079
32.2 | 50.5 | -5.079
32.3 | 50.5 | -5.079
32.4 | 50.5 | -5.079
32.5 | 50.5 | -5.079
32.6 | 50.5 | -5.079
32.7 | 50.5 | -5.079
32.8 | 50.5 | -5.079
32.9 | 50.5 | -5.079
33 | 50.5 | -5.079
33.1 | 50.5 | -5.079
33.2 | 50.5 | -5.079
33.3 | 50.5 | -5.079
33.4 | 50.5 | -5.079
33.5 | 50.5 | -5.079
33.6 | 50.5 | -5.079
33.7 | 50.5 | -5.079
33.8 | 50.5 | -5.079
33.9 | 50.5 | -5.079
34 | 50.5 | -5.079
34.1 | 50.5 | -5.079
34.2 | 50.5 | -5.079
34.3 | 50.5 | -5.079
34.4 | 50.5 | -5.079
34.5 | 50.5 | -5.079
34.6 | 50.5 | -5.078
34.7 | 50.5 | -5.078
34.8 | 50.5 | -5.078
34.9 | 50.5 | -5.079
35 | 50.5 | -5.079
35.1 | 50.5 | -5.079
35.2 | 50.5 | -5.079
35.3 | 50.5 | -5.08
35.4 | 50.5 | -5.08
35.5 | 50.5 | -5.08
35.6 | 50.5 | -5.08
35.7 | 50.5 | -5.08
35.8 | 50.5 | -5.079
35.9 | 50.5 | -5.079
36 | 50.5 | -5.077
36.1 | 50.5 | -5.076
36.2 | 50.5 | -5.075
36.3 | 50.5 | -5.075
36.4 | 50.5 | -5.075
36.5 | 50.5 | -5.075
36.6 | 50.5 | -5.075
36.7 | 50.5 | -5.075
36.8 | 50.5 | -5.075
36.9 | 50.5 | -5.075
37 | 50.5 | -5.074
37.1 | 50.5 | -5.073
37.2 | 50.5 | -5.073
37.3 | 50.5 | -5.073
37.4 | 50.5 | -5.072
37.5 | 50.5 | -5.072
37.6 | 50.5 | -5.072
37.7 | 50.5 | -5.072
37.8 | 50.5 | -5.072
37.9 | 50.5 | -5.072
38 | 50.5 | -5.072
38.1 | 50.5 | -5.072
38.2 | 50.5 | -5.07
38.3 | 50.5 | -5.07
38.4 | 50.5 | -5.068
38.5 | 50.5 | -5.067
38.6 | 50.5 | -5.067
38.7 | 50.5 | -5.067
38.8 | 50.5 | -5.067
38.9 | 50.5 | -5.067
39 | 50.5 | -5.067
39.1 | 50.5 | -5.067
39.2 | 50.5 | -5.067
39.3 | 50.5 | -5.067
39.4 | 50.5 | -5.066
39.5 | 50.5 | -5.065
39.6 | 50.5 | -5.064
39.7 | 50.5 | -5.063
39.8 | 50.5 | -5.062
39.9 | 50.5 | -5.062
40 | 50.5 | -5.062
40.1 | 50.5 | -5.062
40.2 | 50.5 | -5.062
40.3 | 50.5 | -5.062
40.4 | 50.5 | -5.062
40.5 | 50.5 | -5.062
40.6 | 50.5 | -5.06
40.7 | 50.5 | -5.059
40.8 | 50.5 | -5.058
40.9 | 50.5 | -5.057
41 | 50.5 | -5.057
41.1 | 50.5 | -5.057
41.2 | 50.5 | -5.057
41.3 | 50.5 | -5.057
41.4 | 50.5 | -5.057
41.5 | 50.5 | -5.057
41.6 | 50.5 | -5.056
41.7 | 50.5 | -5.056
41.8 | 50.5 | -5.056
41.9 | 50.5 | -5.055
42 | 50.5 | -5.054
42.1 | 50.5 | -5.054
42.2 | 50.5 | -5.054
42.3 | 50.5 | -5.054
42.4 | 50.5 | -5.054
42.5 | 50.5 | -5.054
42.6 | 50.5 | -5.054
42.7 | 50.5 | -5.054
42.8 | 50.5 | -5.052
42.9 | 50.5 | -5.052
43 | 50.5 | -5.05
43.1 | 50.5 | -5.05
43.2 | 50.5 | -5.05
43.3 | 50.5 | -5.05
43.4 | 50.5 | -5.05
43.5 | 50.5 | -5.05
43.6 | 50.5 | -5.05
43.7 | 50.5 | -5.05
43.8 | 50.5 | -5.05
43.9 | 50.5 | -5.05
44 | 50.5 | -5.049
44.1 | 50.5 | -5.049
44.2 | 50.5 | -5.049
44.3 | 50.5 | -5.048
44.4 | 50.5 | -5.048
44.5 | 50.5 | -5.048
44.6 | 50.5 | -5.048
44.7 | 50.5 | -5.048
44.8 | 50.5 | -5.048
44.9 | 50.5 | -5.048
45 | 50.5 | -5.048
45.1 | 50.5 | -5.048
45.2 | 50.5 | -5.048
45.3 | 50.5 | -5.048
45.4 | 50.5 | -5.047
45.5 | 50.5 | -5.047
45.6 | 50.5 | -5.047
45.7 | 50.5 | -5.047
45.8 | 50.5 | -5.047
45.9 | 50.5 | -5.047
46 | 50.5 | -5.047
46.1 | 50.5 | -5.047
46.2 | 50.5 | -5.047
46.3 | 50.5 | -5.047
46.4 | 50.5 | -5.047
46.5 | 50.5 | -5.047
46.6 | 50.5 | -5.047
46.7 | 50.5 | -5.047
46.8 | 50.5 | -5.047
46.9 | 50.5 | -5.047
47 | 50.5 | -5.047
47.1 | 50.5 | -5.047
47.2 | 50.5 | -5.047
47.3 | 50.5 | -5.047
47.4 | 50.5 | -5.047
47.5 | 50.5 | -5.047
47.6 | 50.5 | -5.047
47.7 | 50.5 | -5.047
47.8 | 50.5 | -5.047
47.9 | 50.5 | -5.047
48 | 50.5 | -5.047
48.1 | 50.5 | -5.047
48.2 | 50.5 | -5.047
48.3 | 50.5 | -5.047
48.4 | 50.5 | -5.047
48.5 | 50.5 | -5.048
48.6 | 50.5 | -5.048
48.7 | 50.5 | -5.048
48.8 | 50.5 | -5.048
48.9 | 50.5 | -5.048
49 | 50.5 | -5.048
49.1 | 50.5 | -5.048
49.2 | 50.5 | -5.048
49.3 | 50.5 | -5.048
49.4 | 50.5 | -5.048
49.5 | 50.5 | -5.048
49.6 | 50.5 | -5.048
49.7 | 50.5 | -5.048
49.8 | 50.5 | -5.047
49.9 | 50.5 | -5.047
50 | 50.5 | -5.047
50.1 | 50.5 | -5.047
50.2 | 50.5 | -5.047
50.3 | 50.5 | -5.047
50.4 | 50.5 | -5.047
50.5 | 50.5 | -5.047
50.6 | 50.5 | -5.047
50.7 | 50.5 | -5.047
50.8 | 50.5 | -5.047
50.9 | 50.5 | -5.047
51 | 50.5 | -5.047
51.1 | 50.5 | -5.047
51.2 | 50.5 | -5.047
51.3 | 50.5 | -5.047
51.4 | 50.5 | -5.047
51.5 | 50.5 | -5.047
51.6 | 50.5 | -5.047
51.7 | 50.5 | -5.047
51.8 | 50.5 | -5.047
51.9 | 50.5 | -5.047
52 | 50.5 | -5.047
52.1 | 50.5 | -5.047
52.2 | 50.5 | -5.047
52.3 | 50.5 | -5.047
52.4 | 50.5 | -5.047
52.5 | 50.5 | -5.048
52.6 | 50.5 | -5.048
52.7 | 50.5 | -5.048
52.8 | 50.5 | -5.048
52.9 | 50.5 | -5.048
53 | 50.5 | -5.048
53.1 | 50.5 | -5.048
53.2 | 50.5 | -5.048
53.3 | 50.5 | -5.048
53.4 | 50.5 | -5.048
53.5 | 50.5 | -5.048
53.6 | 50.5 | -5.049
53.7 | 50.5 | -5.049
53.8 | 50.5 | -5.048
53.9 | 50.5 | -5.048
54 | 50.5 | -5.048
54.1 | 50.5 | -5.048
54.2 | 50.5 | -5.048
54.3 | 50.5 | -5.048
54.4 | 50.5 | -5.048
54.5 | 50.5 | -5.048
54.6 | 50.5 | -5.048
54.7 | 50.5 | -5.048
54.8 | 50.5 | -5.048
54.9 | 50.5 | -5.048
55 | 50.5 | -5.047
55.1 | 50.5 | -5.047
55.2 | 50.5 | -5.047
55.3 | 50.5 | -5.047
55.4 | 50.5 | -5.047
55.5 | 50.5 | -5.047
55.6 | 50.5 | -5.047
55.7 | 50.5 | -5.047
55.8 | 50.5 | -5.047
55.9 | 50.5 | -5.047
56 | 50.5 | -5.047
56.1 | 50.5 | -5.047
56.2 | 50.5 | -5.047
56.3 | 50.5 | -5.047
56.4 | 50.5 | -5.047
56.5 | 50.5 | -5.047
56.6 | 50.5 | -5.047
56.7 | 50.5 | -5.047
56.8 | 50.5 | -5.047
56.9 | 50.5 | -5.047
57 | 50.5 | -5.047
57.1 | 50.5 | -5.047
57.2 | 50.5 | -5.047
57.3 | 50.5 | -5.047
57.4 | 50.5 | -5.047
57.5 | 50.5 | -5.047
57.6 | 50.5 | -5.047
57.7 | 50.5 | -5.047
57.8 | 50.5 | -5.047
57.9 | 50.5 | -5.047
58 | 50.5 | -5.048
58.1 | 50.5 | -5.048
58.2 | 50.5 | -5.048
58.3 | 50.5 | -5.048
58.4 | 50.5 | -5.048
58.5 | 50.5 | -5.048
58.6 | 50.5 | -5.048
58.7 | 50.5 | -5.048
58.8 | 50.5 | -5.048
58.9 | 50.5 | -5.048
59 | 50.5 | -5.048
59.1 | 50.5 | -5.048
59.2 | 50.5 | -5.048
59.3 | 50.5 | -5.048
59.4 | 50.5 | -5.048
59.5 | 50.5 | -5.048
59.6 | 50.5 | -5.048
59.7 | 50.5 | -5.048
59.8 | 50.5 | -5.048
59.9 | 50.5 | -5.048
60 | 50.5 | -5.048
60.1 | 50.5 | -5.048
60.2 | 50.5 | -5.048
60.3 | 50.5 | -5.048
60.4 | 50.5 | -5.048
60.5 | 50.5 | -5.048
60.6 | 50.5 | -5.048
60.7 | 50.5 | -5.048
60.8 | 50.5 | -5.048
60.9 | 50.5 | -5.048
61 | 50.5 | -5.048
61.1 | 50.5 | -5.048
61.2 | 50.5 | -5.048
61.3 | 50.5 | -5.048
61.4 | 50.5 | -5.048
61.5 | 50.5 | -5.048
61.6 | 50.5 | -5.048
61.7 | 50.5 | -5.048
61.8 | 50.5 | -5.048
61.9 | 50.5 | -5.048
62 | 50.5 | -5.048
62.1 | 50.5 | -5.048
62.2 | 50.5 | -5.048
62.3 | 50.5 | -5.048
62.4 | 50.5 | -5.048
62.5 | 50.5 | -5.048
62.6 | 50.5 | -5.048
62.7 | 50.5 | -5.048
62.8 | 50.5 | -5.048
62.9 | 50.5 | -5.048
63 | 50.5 | -5.048
63.1 | 50.5 | -5.048
63.2 | 50.5 | -5.048
63.3 | 50.5 | -5.048
63.4 | 50.5 | -5.048
63.5 | 50.5 | -5.048
63.6 | 50.5 | -5.048
63.7 | 50.5 | -5.048
63.8 | 50.5 | -5.048
63.9 | 50.5 | -5.047
64 | 50.5 | -5.047
64.1 | 50.5 | -5.047
64.2 | 50.5 | -5.047
64.3 | 50.5 | -5.047
64.4 | 50.5 | -5.047
64.5 | 50.5 | -5.047
64.6 | 50.5 | -5.047
64.7 | 50.5 | -5.047
64.8 | 50.5 | -5.047
64.9 | 50.5 | -5.047
65 | 50.5 | -5.047
65.1 | 50.5 | -5.048
65.2 | 50.5 | -5.048
65.3 | 50.5 | -5.048
65.4 | 50.5 | -5.048
65.5 | 50.5 | -5.048
65.6 | 50.5 | -5.048
65.7 | 50.5 | -5.048
65.8 | 50.5 | -5.048
65.9 | 50.5 | -5.048
66 | 50.5 | -5.048
66.1 | 50.5 | -5.048
66.2 | 50.5 | -5.048
66.3 | 50.5 | -5.048
66.4 | 50.5 | -5.048
66.5 | 50.5 | -5.048
66.6 | 50.5 | -5.048
66.7 | 50.5 | -5.048
66.8 | 50.5 | -5.048
66.9 | 50.5 | -5.048
67 | 50.5 | -5.048
67.1 | 50.5 | -5.048
67.2 | 50.5 | -5.048
67.3 | 50.5 | -5.048
67.4 | 50.5 | -5.048
67.5 | 50.5 | -5.048
67.6 | 50.5 | -5.048
67.7 | 50.5 | -5.048
67.8 | 50.5 | -5.048
67.9 | 50.5 | -5.048
68 | 50.5 | -5.048
68.1 | 50.5 | -5.048
68.2 | 50.5 | -5.048
68.3 | 50.5 | -5.048
68.4 | 50.5 | -5.048
68.5 | 50.5 | -5.048
68.6 | 50.5 | -5.048
68.7 | 50.5 | -5.048
68.8 | 50.5 | -5.048
68.9 | 50.5 | -5.048
69 | 50.5 | -5.048
69.1 | 50.5 | -5.048
69.2 | 50.5 | -5.048
69.3 | 50.5 | -5.048
69.4 | 50.5 | -5.048
69.5 | 50.5 | -5.048
69.6 | 50.5 | -5.048
69.7 | 50.5 | -5.048
69.8 | 50.5 | -5.048
69.9 | 50.5 | -5.047
70 | 50.5 | -5.047
70.1 | 50.5 | -5.047
70.2 | 50.5 | -5.047
70.3 | 50.5 | -5.047
70.4 | 50.5 | -5.047
70.5 | 50.5 | -5.047
70.6 | 50.5 | -5.047
70.7 | 50.5 | -5.047
70.8 | 50.5 | -5.047
70.9 | 50.5 | -5.047
71 | 50.5 | -5.047
71.1 | 50.5 | -5.047
71.2 | 50.5 | -5.047
71.3 | 50.5 | -5.047
71.4 | 50.5 | -5.047
71.5 | 50.5 | -5.047
71.6 | 50.5 | -5.047
71.7 | 50.5 | -5.047
71.8 | 50.5 | -5.047
71.9 | 50.5 | -5.047
72 | 50.5 | -5.048
72.1 | 50.5 | -5.048
72.2 | 50.5 | -5.048
72.3 | 50.5 | -5.048
72.4 | 50.5 | -5.048
72.5 | 50.5 | -5.048
72.6 | 50.5 | -5.048
72.7 | 50.5 | -5.048
72.8 | 50.5 | -5.048
72.9 | 50.5 | -5.048
73 | 50.5 | -5.048
73.1 | 50.5 | -5.048
73.2 | 50.5 | -5.048
73.3 | 50.5 | -5.048
73.4 | 50.5 | -5.048
73.5 | 50.5 | -5.048
73.6 | 50.5 | -5.048
73.7 | 50.5 | -5.048
73.8 | 50.5 | -5.048
73.9 | 50.5 | -5.048
74 | 50.5 | -5.048
74.1 | 50.5 | -5.048
74.2 | 50.5 | -5.048
74.3 | 50.5 | -5.048
74.4 | 50.5 | -5.048
74.5 | 50.5 | -5.048
74.6 | 50.5 | -5.048
74.7 | 50.5 | -5.048
74.8 | 50.5 | -5.048
74.9 | 50.5 | -5.048
75 | 50.5 | -5.048
75.1 | 50.5 | -5.048
75.2 | 50.5 | -5.048
75.3 | 50.5 | -5.048
75.4 | 50.5 | -5.048
75.5 | 50.5 | -5.048
75.6 | 50.5 | -5.048
75.7 | 50.5 | -5.048
75.8 | 50.5 | -5.048
75.9 | 50.5 | -5.048
76 | 50.5 | -5.048
76.1 | 50.5 | -5.048
76.2 | 50.5 | -5.048
76.3 | 50.5 | -5.048
76.4 | 50.5 | -5.048
76.5 | 50.5 | -5.048
76.6 | 50.5 | -5.048
76.7 | 50.5 | -5.048
76.8 | 50.5 | -5.048
76.9 | 50.5 | -5.048
77 | 50.5 | -5.048
77.1 | 50.5 | -5.048
77.2 | 50.5 | -5.048
77.3 | 50.5 | -5.048
77.4 | 50.5 | -5.048
77.5 | 50.5 | -5.048
77.6 | 50.5 | -5.048
77.7 | 50.5 | -5.048
77.8 | 50.5 | -5.048
77.9 | 50.5 | -5.048
78 | 50.5 | -5.048
78.1 | 50.5 | -5.048
78.2 | 50.5 | -5.048
78.3 | 50.5 | -5.048
78.4 | 50.5 | -5.048
78.5 | 50.5 | -5.048
78.6 | 50.5 | -5.048
78.7 | 50.5 | -5.048
78.8 | 50.5 | -5.048
78.9 | 50.5 | -5.048
79 | 50.5 | -5.048
79.1 | 50.5 | -5.048
79.2 | 50.5 | -5.047
79.3 | 50.5 | -5.047
79.4 | 50.5 | -5.047
79.5 | 50.5 | -5.047
79.6 | 50.5 | -5.047
79.7 | 50.5 | -5.047
79.8 | 50.5 | -5.047
79.9 | 50.5 | -5.047
80 | 50.5 | -5.047
80.1 | 50.5 | -5.047
80.2 | 50.5 | -5.047
80.3 | 50.5 | -5.047
80.4 | 50.5 | -5.048
80.5 | 50.5 | -5.048
80.6 | 50.5 | -5.048
80.7 | 50.5 | -5.048
80.8 | 50.5 | -5.048
80.9 | 50.5 | -5.048
81 | 50.5 | -5.048
81.1 | 50.5 | -5.048
81.2 | 50.5 | -5.048
81.3 | 50.5 | -5.048
81.4 | 50.5 | -5.048
81.5 | 50.5 | -5.049
81.6 | 50.5 | -5.048
81.7 | 50.5 | -5.048
81.8 | 50.5 | -5.048
81.9 | 50.5 | -5.048
82 | 50.5 | -5.048
82.1 | 50.5 | -5.048
82.2 | 50.5 | -5.048
82.3 | 50.5 | -5.048
82.4 | 50.5 | -5.048
82.5 | 50.5 | -5.048
82.6 | 50.5 | -5.048
82.7 | 50.5 | -5.048
82.8 | 50.5 | -5.048
82.9 | 50.5 | -5.048
83 | 50.5 | -5.048
83.1 | 50.5 | -5.048
83.2 | 50.5 | -5.048
83.3 | 50.5 | -5.048
83.4 | 50.5 | -5.048
83.5 | 50.5 | -5.048
83.6 | 50.5 | -5.048
83.7 | 50.5 | -5.048
83.8 | 50.5 | -5.048
83.9 | 50.5 | -5.048
84 | 50.5 | -5.048
84.1 | 50.5 | -5.048
84.2 | 50.5 | -5.047
84.3 | 50.5 | -5.047
84.4 | 50.5 | -5.047
84.5 | 50.5 | -5.047
84.6 | 50.5 | -5.047
84.7 | 50.5 | -5.047
84.8 | 50.5 | -5.048
84.9 | 50.5 | -5.048
85 | 50.5 | -5.048
85.1 | 50.5 | -5.048
85.2 | 50.5 | -5.048
85.3 | 50.5 | -5.048
85.4 | 50.5 | -5.048
85.5 | 50.5 | -5.048
85.6 | 50.5 | -5.048
85.7 | 50.5 | -5.048
85.8 | 50.5 | -5.048
85.9 | 50.5 | -5.048
86 | 50.5 | -5.048
86.1 | 50.5 | -5.048
86.2 | 50.5 | -5.047
86.3 | 50.5 | -5.047
86.4 | 50.5 | -5.047
86.5 | 50.5 | -5.047
86.6 | 50.5 | -5.047
86.7 | 50.5 | -5.047
86.8 | 50.5 | -5.047
86.9 | 50.5 | -5.047
87 | 50.5 | -5.047
87.1 | 50.5 | -5.047
87.2 | 50.5 | -5.047
87.3 | 50.5 | -5.048
87.4 | 50.5 | -5.048
87.5 | 50.5 | -5.048
87.6 | 50.5 | -5.048
87.7 | 50.5 | -5.048
87.8 | 50.5 | -5.048
87.9 | 50.5 | -5.048
88 | 50.5 | -5.048
88.1 | 50.5 | -5.048
88.2 | 50.5 | -5.048
88.3 | 50.5 | -5.048
88.4 | 50.5 | -5.048
88.5 | 50.5 | -5.048
88.6 | 50.5 | -5.048
88.7 | 50.5 | -5.048
88.8 | 50.5 | -5.048
88.9 | 50.5 | -5.048
89 | 50.5 | -5.048
89.1 | 50.5 | -5.048
89.2 | 50.5 | -5.048
89.3 | 50.5 | -5.048
89.4 | 50.5 | -5.048
89.5 | 50.5 | -5.048
89.6 | 50.5 | -5.048
89.7 | 50.5 | -5.048
89.8 | 50.5 | -5.048
89.9 | 50.5 | -5.048
90 | 50.5 | -5.048
90.1 | 50.5 | -5.048
90.2 | 50.5 | -5.048
90.3 | 50.5 | -5.048
90.4 | 50.5 | -5.048
90.5 | 50.5 | -5.048
90.6 | 50.5 | -5.048
90.7 | 50.5 | -5.048
90.8 | 50.5 | -5.048
90.9 | 50.5 | -5.048
91 | 50.5 | -5.048
91.1 | 50.5 | -5.048
91.2 | 50.5 | -5.048
91.3 | 50.5 | -5.048
91.4 | 50.5 | -5.048
91.5 | 50.5 | -5.048
91.6 | 50.5 | -5.048
91.7 | 50.5 | -5.048
91.8 | 50.5 | -5.048
91.9 | 50.5 | -5.048
92 | 50.5 | -5.048
92.1 | 50.5 | -5.048
92.2 | 50.5 | -5.048
92.3 | 50.5 | -5.048
92.4 | 50.5 | -5.048
92.5 | 50.5 | -5.048
92.6 | 50.5 | -5.048
92.7 | 50.5 | -5.048
92.8 | 50.5 | -5.048
92.9 | 50.5 | -5.048
93 | 50.5 | -5.048
93.1 | 50.5 | -5.048
93.2 | 50.5 | -5.047
93.3 | 50.5 | -5.047
93.4 | 50.5 | -5.047
93.5 | 50.5 | -5.047
93.6 | 50.5 | -5.047
93.7 | 50.5 | -5.047
93.8 | 50.5 | -5.047
93.9 | 50.5 | -5.047
94 | 50.5 | -5.047
94.1 | 50.5 | -5.047
94.2 | 50.5 | -5.047
94.3 | 50.5 | -5.047
94.4 | 50.5 | -5.047
94.5 | 50.5 | -5.047
94.6 | 50.5 | -5.047
94.7 | 50.5 | -5.047
94.8 | 50.5 | -5.047
94.9 | 50.5 | -5.047
95 | 50.5 | -5.047
95.1 | 50.5 | -5.047
95.2 | 50.5 | -5.047
95.3 | 50.5 | -5.047
95.4 | 50.5 | -5.047
95.5 | 50.5 | -5.047
95.6 | 50.5 | -5.047
95.7 | 50.5 | -5.047
95.8 | 50.5 | -5.047
95.9 | 50.5 | -5.047
96 | 50.5 | -5.047
96.1 | 50.5 | -5.047
96.2 | 50.5 | -5.047
96.3 | 50.5 | -5.047
96.4 | 50.5 | -5.047
96.5 | 50.5 | -5.047
96.6 | 50.5 | -5.047
96.7 | 50.5 | -5.047
96.8 | 50.5 | -5.048
96.9 | 50.5 | -5.048
97 | 50.5 | -5.048
97.1 | 50.5 | -5.048
97.2 | 50.5 | -5.048
97.3 | 50.5 | -5.048
97.4 | 50.5 | -5.048
97.5 | 50.5 | -5.048
97.6 | 50.5 | -5.048
97.7 | 50.5 | -5.048
97.8 | 50.5 | -5.048
97.9 | 50.5 | -5.048
98 | 50.5 | -5.048
98.1 | 50.5 | -5.048
98.2 | 50.5 | -5.048
98.3 | 50.5 | -5.048
98.4 | 50.5 | -5.048
98.5 | 50.5 | -5.048
98.6 | 50.5 | -5.048
98.7 | 50.5 | -5.048
98.8 | 50.5 | -5.048
98.9 | 50.5 | -5.048
99 | 50.5 | -5.048
99.1 | 50.5 | -5.048
99.2 | 50.5 | -5.048
99.3 | 50.5 | -5.048
99.4 | 50.5 | -5.048
99.5 | 50.5 | -5.048
99.6 | 50.5 | -5.048
99.7 | 50.5 | -5.048
99.8 | 50.5 | -5.048
99.9 | 50.5 | -5.048
100 | 50.5 | -5.048
100.1 | 50.5 | -5.048
100.2 | 50.5 | -5.048
100.3 | 50.5 | -5.048
100.4 | 50.5 | -5.048
100.5 | 50.5 | -5.048
100.6 | 50.5 | -5.048
100.7 | 50.5 | -5.048
100.8 | 50.5 | -5.048
100.9 | 50.5 | -5.048
101 | 50.5 | -5.048
101.1 | 50.5 | -5.048
101.2 | 50.5 | -5.048
101.3 | 50.5 | -5.048
101.4 | 50.5 | -5.048
101.5 | 50.5 | -5.048
101.6 | 50.5 | -5.048
101.7 | 50.5 | -5.048
101.8 | 50.5 | -5.048
101.9 | 50.5 | -5.048
102 | 50.5 | -5.048
102.1 | 50.5 | -5.048
102.2 | 50.5 | -5.048
102.3 | 50.5 | -5.048
102.4 | 50.5 | -5.048
102.5 | 50.5 | -5.048
102.6 | 50.5 | -5.047
102.7 | 50.5 | -5.047
102.8 | 50.5 | -5.047
102.9 | 50.5 | -5.047
103 | 50.5 | -5.047
103.1 | 50.5 | -5.047
103.2 | 50.5 | -5.047
103.3 | 50.5 | -5.047
103.4 | 50.5 | -5.047
103.5 | 50.5 | -5.047
103.6 | 50.5 | -5.048
103.7 | 50.5 | -5.048
103.8 | 50.5 | -5.048
103.9 | 50.5 | -5.048
104 | 50.5 | -5.048
104.1 | 50.5 | -5.048
104.2 | 50.5 | -5.048
104.3 | 50.5 | -5.048
104.4 | 50.5 | -5.048
104.5 | 50.5 | -5.048
104.6 | 50.5 | -5.048
104.7 | 50.5 | -5.048
104.8 | 50.5 | -5.048
104.9 | 50.5 | -5.048
105 | 50.5 | -5.048
105.1 | 50.5 | -5.048
105.2 | 50.5 | -5.048
105.3 | 50.5 | -5.048
105.4 | 50.5 | -5.048
105.5 | 50.5 | -5.048
105.6 | 50.5 | -5.048
105.7 | 50.5 | -5.048
105.8 | 50.5 | -5.048
105.9 | 50.5 | -5.048
106 | 50.5 | -5.048
106.1 | 50.5 | -5.048
106.2 | 50.5 | -5.048
106.3 | 50.5 | -5.048
106.4 | 50.5 | -5.048
106.5 | 50.5 | -5.048
106.6 | 50.5 | -5.048
106.7 | 50.5 | -5.048
106.8 | 50.5 | -5.048
106.9 | 50.5 | -5.048
107 | 50.5 | -5.048
107.1 | 50.5 | -5.048
107.2 | 50.5 | -5.048
107.3 | 50.5 | -5.048
107.4 | 50.5 | -5.048
107.5 | 50.5 | -5.048
107.6 | 50.5 | -5.048
107.7 | 50.5 | -5.048
107.8 | 50.5 | -5.048
107.9 | 50.5 | -5.048
108 | 50.5 | -5.048
108.1 | 50.5 | -5.048
108.2 | 50.5 | -5.048
108.3 | 50.5 | -5.048
108.4 | 50.5 | -5.048
108.5 | 50.5 | -5.047
108.6 | 50.5 | -5.047
108.7 | 50.5 | -5.047
108.8 | 50.5 | -5.047
108.9 | 50.5 | -5.047
109 | 50.5 | -5.047
109.1 | 50.5 | -5.047
109.2 | 50.5 | -5.047
109.3 | 50.5 | -5.047
109.4 | 50.5 | -5.047
109.5 | 50.5 | -5.047
109.6 | 50.5 | -5.047
109.7 | 50.5 | -5.047
109.8 | 50.5 | -5.047
109.9 | 50.5 | -5.047
110 | 50.5 | -5.047
110.1 | 50.5 | -5.047
110.2 | 50.5 | -5.047
110.3 | 50.5 | -5.047
110.4 | 50.5 | -5.047
110.5 | 50.5 | -5.047
110.6 | 50.5 | -5.047
110.7 | 50.5 | -5.047
110.8 | 50.5 | -5.047
110.9 | 50.5 | -5.047
111 | 50.5 | -5.047
111.1 | 50.5 | -5.047
111.2 | 50.5 | -5.047
111.3 | 50.5 | -5.047
111.4 | 50.5 | -5.047
111.5 | 50.5 | -5.047
111.6 | 50.5 | -5.047
111.7 | 50.5 | -5.047
111.8 | 50.5 | -5.047
111.9 | 50.5 | -5.048
112 | 50.5 | -5.048
112.1 | 50.5 | -5.048
112.2 | 50.5 | -5.048
112.3 | 50.5 | -5.048
112.4 | 50.5 | -5.048
112.5 | 50.5 | -5.048
112.6 | 50.5 | -5.048
112.7 | 50.5 | -5.048
112.8 | 50.5 | -5.048
112.9 | 50.5 | -5.048
113 | 50.5 | -5.048
113.1 | 50.5 | -5.048
113.2 | 50.5 | -5.048
113.3 | 50.5 | -5.048
113.4 | 50.5 | -5.048
113.5 | 50.5 | -5.048
113.6 | 50.5 | -5.048
113.7 | 50.5 | -5.048
113.8 | 50.5 | -5.048
113.9 | 50.5 | -5.048
114 | 50.5 | -5.048
114.1 | 50.5 | -5.048
114.2 | 50.5 | -5.048
114.3 | 50.5 | -5.048
114.4 | 50.5 | -5.048
114.5 | 50.5 | -5.048
114.6 | 50.5 | -5.048
114.7 | 50.5 | -5.048
114.8 | 50.5 | -5.048
114.9 | 50.5 | -5.048
115 | 50.5 | -5.048
115.1 | 50.5 | -5.048
115.2 | 50.5 | -5.048
115.3 | 50.5 | -5.048
115.4 | 50.5 | -5.048
115.5 | 50.5 | -5.048
115.6 | 50.5 | -5.048
115.7 | 50.5 | -5.048
115.8 | 50.5 | -5.048
115.9 | 50.5 | -5.048
116 | 50.5 | -5.048
116.1 | 50.5 | -5.048
116.2 | 50.5 | -5.048
116.3 | 50.5 | -5.048
116.4 | 50.5 | -5.048
116.5 | 50.5 | -5.048
116.6 | 50.5 | -5.048
116.7 | 50.5 | -5.048
116.8 | 50.5 | -5.048
116.9 | 50.5 | -5.048
117 | 50.5 | -5.048
117.1 | 50.5 | -5.048
117.2 | 50.5 | -5.048
117.3 | 50.5 | -5.048
117.4 | 50.5 | -5.048
117.5 | 50.5 | -5.048
117.6 | 50.5 | -5.048
117.7 | 50.5 | -5.048
117.8 | 50.5 | -5.048
117.9 | 50.5 | -5.047
118 | 50.5 | -5.047
118.1 | 50.5 | -5.047
118.2 | 50.5 | -5.047
118.3 | 50.5 | -5.047
118.4 | 50.5 | -5.047
118.5 | 50.5 | -5.047
118.6 | 50.5 | -5.047
118.7 | 50.5 | -5.047
118.8 | 50.5 | -5.048
118.9 | 50.5 | -5.048
119 | 50.5 | -5.048
119.1 | 50.5 | -5.048
119.2 | 50.5 | -5.048
119.3 | 50.5 | -5.048
119.4 | 50.5 | -5.048
119.5 | 50.5 | -5.048
119.6 | 50.5 | -5.048
119.7 | 50.5 | -5.048
119.8 | 50.5 | -5.048
119.9 | 50.5 | -5.048
120 | 50.5 | -5.049
120.1 | 50.5 | -5.049
120.2 | 50.5 | -5.049
120.3 | 50.5 | -5.049
120.4 | 50.5 | -5.049
120.5 | 50.5 | -5.048
120.6 | 50.5 | -5.048
120.7 | 50.5 | -5.048
120.8 | 50.5 | -5.048
120.9 | 50.5 | -5.048
121 | 50.5 | -5.048
121.1 | 50.5 | -5.048
121.2 | 50.5 | -5.048
121.3 | 50.5 | -5.048
121.4 | 50.5 | -5.048
121.5 | 50.5 | -5.048
121.6 | 50.5 | -5.048
121.7 | 50.5 | -5.048
121.8 | 50.5 | -5.048
121.9 | 50.5 | -5.048
122 | 50.5 | -5.048
122.1 | 50.5 | -5.048
122.2 | 50.5 | -5.048
122.3 | 50.5 | -5.048
122.4 | 50.5 | -5.048
122.5 | 50.5 | -5.048
122.6 | 50.5 | -5.048
122.7 | 50.5 | -5.048
122.8 | 50.5 | -5.048
122.9 | 50.5 | -5.048
123 | 50.5 | -5.048
123.1 | 50.5 | -5.048
123.2 | 50.5 | -5.048
123.3 | 50.5 | -5.048
123.4 | 50.5 | -5.048
123.5 | 50.5 | -5.048
123.6 | 50.5 | -5.048
123.7 | 50.5 | -5.047
123.8 | 50.5 | -5.047
123.9 | 50.5 | -5.047
124 | 50.5 | -5.047
124.1 | 50.5 | -5.047
124.2 | 50.5 | -5.047
124.3 | 50.5 | -5.047
124.4 | 50.5 | -5.047
124.5 | 50.5 | -5.047
124.6 | 50.5 | -5.047
124.7 | 50.5 | -5.047
124.8 | 50.5 | -5.047
124.9 | 50.5 | -5.048
125 | 50.5 | -5.048
125.1 | 50.5 | -5.048
125.2 | 50.5 | -5.048
125.3 | 50.5 | -5.048
125.4 | 50.5 | -5.048
125.5 | 50.5 | -5.048
125.6 | 50.5 | -5.048
125.7 | 50.5 | -5.048
125.8 | 50.5 | -5.048
125.9 | 50.5 | -5.048
126 | 50.5 | -5.048
126.1 | 50.5 | -5.048
126.2 | 50.5 | -5.047
126.3 | 50.5 | -5.047
126.4 | 50.5 | -5.047
126.5 | 50.5 | -5.047
126.6 | 50.5 | -5.047
126.7 | 50.5 | -5.047
126.8 | 50.5 | -5.047
126.9 | 50.5 | -5.047
127 | 50.5 | -5.047
127.1 | 50.5 | -5.047
127.2 | 50.5 | -5.047
127.3 | 50.5 | -5.047
127.4 | 50.5 | -5.047
127.5 | 50.5 | -5.047
127.6 | 50.5 | -5.047
127.7 | 50.5 | -5.047
127.8 | 50.5 | -5.047
127.9 | 50.5 | -5.047
128 | 50.5 | -5.047
128.1 | 50.5 | -5.047
128.2 | 50.5 | -5.047
128.3 | 50.5 | -5.047
128.4 | 50.5 | -5.048
128.5 | 50.5 | -5.048
128.6 | 50.5 | -5.048
128.7 | 50.5 | -5.048
128.8 | 50.5 | -5.048
128.9 | 50.5 | -5.048
129 | 50.5 | -5.048
129.1 | 50.5 | -5.048
129.2 | 50.5 | -5.048
129.3 | 50.5 | -5.048
129.4 | 50.5 | -5.048
129.5 | 50.5 | -5.048
129.6 | 50.5 | -5.048
129.7 | 50.5 | -5.048
129.8 | 50.5 | -5.048
129.9 | 50.5 | -5.048
130 | 50.5 | -5.048
130.1 | 50.5 | -5.048
130.2 | 50.5 | -5.048
130.3 | 50.5 | -5.048
130.4 | 50.5 | -5.048
130.5 | 50.5 | -5.048
130.6 | 50.5 | -5.048
130.7 | 50.5 | -5.048
130.8 | 50.5 | -5.048
130.9 | 50.5 | -5.048
131 | 50.5 | -5.048
131.1 | 50.5 | -5.048
131.2 | 50.5 | -5.048
131.3 | 50.5 | -5.048
131.4 | 50.5 | -5.048
131.5 | 50.5 | -5.048
131.6 | 50.5 | -5.048
131.7 | 50.5 | -5.048
131.8 | 50.5 | -5.048
131.9 | 50.5 | -5.048
132 | 50.5 | -5.048
132.1 | 50.5 | -5.048
132.2 | 50.5 | -5.048
132.3 | 50.5 | -5.048
132.4 | 50.5 | -5.048
132.5 | 50.5 | -5.048
132.6 | 50.5 | -5.048
132.7 | 50.5 | -5.048
132.8 | 50.5 | -5.048
132.9 | 50.5 | -5.048
133 | 50.5 | -5.047
133.1 | 50.5 | -5.047
133.2 | 50.5 | -5.047
133.3 | 50.5 | -5.047
133.4 | 50.5 | -5.047
133.5 | 50.5 | -5.047
133.6 | 50.5 | -5.047
133.7 | 50.5 | -5.047
133.8 | 50.5 | -5.047
133.9 | 50.5 | -5.047
134 | 50.5 | -5.047
134.1 | 50.5 | -5.047
134.2 | 50.5 | -5.047
134.3 | 50.5 | -5.047
134.4 | 50.5 | -5.047
134.5 | 50.5 | -5.047
134.6 | 50.5 | -5.047
134.7 | 50.5 | -5.047
134.8 | 50.5 | -5.047
134.9 | 50.5 | -5.047
135 | 50.5 | -5.047
135.1 | 50.5 | -5.047
135.2 | 50.5 | -5.048
135.3 | 50.5 | -5.048
135.4 | 50.5 | -5.048
135.5 | 50.5 | -5.048
135.6 | 50.5 | -5.048
135.7 | 50.5 | -5.048
135.8 | 50.5 | -5.048
135.9 | 50.5 | -5.048
136 | 50.5 | -5.048
136.1 | 50.5 | -5.048
136.2 | 50.5 | -5.048
136.3 | 50.5 | -5.048
136.4 | 50.5 | -5.048
136.5 | 50.5 | -5.048
136.6 | 50.5 | -5.048
136.7 | 50.5 | -5.048
136.8 | 50.5 | -5.048
136.9 | 50.5 | -5.048
137 | 50.5 | -5.048
137.1 | 50.5 | -5.048
137.2 | 50.5 | -5.048
137.3 | 50.5 | -5.048
137.4 | 50.5 | -5.048
137.5 | 50.5 | -5.048
137.6 | 50.5 | -5.048
137.7 | 50.5 | -5.048
137.8 | 50.5 | -5.048
137.9 | 50.5 | -5.048
138 | 50.5 | -5.048
138.1 | 50.5 | -5.048
138.2 | 50.5 | -5.048
138.3 | 50.5 | -5.048
138.4 | 50.5 | -5.048
138.5 | 50.5 | -5.048
138.6 | 50.5 | -5.048
138.7 | 50.5 | -5.048
138.8 | 50.5 | -5.048
138.9 | 50.5 | -5.048
139 | 50.5 | -5.048
139.1 | 50.5 | -5.048
139.2 | 50.5 | -5.048
139.3 | 50.5 | -5.048
139.4 | 50.5 | -5.048
139.5 | 50.5 | -5.048
139.6 | 50.5 | -5.048
139.7 | 50.5 | -5.048
139.8 | 50.5 | -5.048
139.9 | 50.5 | -5.048
140 | 50.5 | -5.048
140.1 | 50.5 | -5.047
140.2 | 50.5 | -5.047
140.3 | 50.5 | -5.047
140.4 | 50.5 | -5.047
140.5 | 50.5 | -5.047
140.6 | 50.5 | -5.047
140.7 | 50.5 | -5.047
140.8 | 50.5 | -5.047
140.9 | 50.5 | -5.047
141 | 50.5 | -5.047
141.1 | 50.5 | -5.048
141.2 | 50.5 | -5.048
141.3 | 50.5 | -5.048
141.4 | 50.5 | -5.048
141.5 | 50.5 | -5.048
141.6 | 50.5 | -5.048
141.7 | 50.5 | -5.048
141.8 | 50.5 | -5.048
141.9 | 50.5 | -5.048
142 | 50.5 | -5.048
142.1 | 50.5 | -5.048
142.2 | 50.5 | -5.048
142.3 | 50.5 | -5.048
142.4 | 50.5 | -5.048
142.5 | 50.5 | -5.048
142.6 | 50.5 | -5.048
142.7 | 50.5 | -5.048
142.8 | 50.5 | -5.048
142.9 | 50.5 | -5.048
143 | 50.5 | -5.048
143.1 | 50.5 | -5.048
143.2 | 50.5 | -5.048
143.3 | 50.5 | -5.048
143.4 | 50.5 | -5.048
143.5 | 50.5 | -5.048
143.6 | 50.5 | -5.048
143.7 | 50.5 | -5.048
143.8 | 50.5 | -5.048
143.9 | 50.5 | -5.048
144 | 50.5 | -5.048
144.1 | 50.5 | -5.048
144.2 | 50.5 | -5.048
144.3 | 50.5 | -5.048
144.4 | 50.5 | -5.048
144.5 | 50.5 | -5.048
144.6 | 50.5 | -5.048
144.7 | 50.5 | -5.048
144.8 | 50.5 | -5.048
144.9 | 50.5 | -5.048
145 | 50.5 | -5.048
145.1 | 50.5 | -5.048
145.2 | 50.5 | -5.048
145.3 | 50.5 | -5.048
145.4 | 50.5 | -5.048
145.5 | 50.5 | -5.048
145.6 | 50.5 | -5.048
145.7 | 50.5 | -5.048
145.8 | 50.5 | -5.048
145.9 | 50.5 | -5.048
146 | 50.5 | -5.048
146.1 | 50.5 | -5.048
146.2 | 50.5 | -5.048
146.3 | 50.5 | -5.048
146.4 | 50.5 | -5.048
146.5 | 50.5 | -5.048
146.6 | 50.5 | -5.048
146.7 | 50.5 | -5.048
146.8 | 50.5 | -5.048
146.9 | 50.5 | -5.048
147 | 50.5 | -5.048
147.1 | 50.5 | -5.048
147.2 | 50.5 | -5.048
147.3 | 50.5 | -5.048
147.4 | 50.5 | -5.048
147.5 | 50.5 | -5.048
147.6 | 50.5 | -5.048
147.7 | 50.5 | -5.048
147.8 | 50.5 | -5.048
147.9 | 50.5 | -5.048
148 | 50.5 | -5.048
148.1 | 50.5 | -5.048
148.2 | 50.5 | -5.048
148.3 | 50.5 | -5.048
148.4 | 50.5 | -5.048
148.5 | 50.5 | -5.048
148.6 | 50.5 | -5.048
148.7 | 50.5 | -5.048
148.8 | 50.5 | -5.048
148.9 | 50.5 | -5.048
149 | 50.5 | -5.048
149.1 | 50.5 | -5.048
149.2 | 50.5 | -5.048
149.3 | 50.5 | -5.048
149.4 | 50.5 | -5.048
149.5 | 50.5 | -5.048
149.6 | 50.5 | -5.047
149.7 | 50.5 | -5.047
149.8 | 50.5 | -5.047
149.9 | 50.5 | -5.047
150 | 50.5 | -5.047
150.1 | 50.5 | -5.047
150.2 | 50.5 | -5.047
150.3 | 50.5 | -5.047
150.4 | 50.5 | -5.048
150.5 | 50.5 | -5.048
150.6 | 50.5 | -5.048
150.7 | 50.5 | -5.048
150.8 | 50.5 | -5.048
150.9 | 50.5 | -5.048
151 | 50.5 | -5.048
151.1 | 50.5 | -5.048
151.2 | 50.5 | -5.048
151.3 | 50.5 | -5.048
151.4 | 50.5 | -5.048
151.5 | 50.5 | -5.048
151.6 | 50.5 | -5.048
151.7 | 50.5 | -5.047
151.8 | 50.5 | -5.047
151.9 | 50.5 | -5.047
152 | 50.5 | -5.047
152.1 | 50.5 | -5.047
152.2 | 50.5 | -5.047
152.3 | 50.5 | -5.047
152.4 | 50.5 | -5.047
152.5 | 50.5 | -5.047
152.6 | 50.5 | -5.047
152.7 | 50.5 | -5.047
152.8 | 50.5 | -5.047
152.9 | 50.5 | -5.047
153 | 50.5 | -5.047
153.1 | 50.5 | -5.047
153.2 | 50.5 | -5.048
153.3 | 50.5 | -5.048
153.4 | 50.5 | -5.048
153.5 | 50.5 | -5.048
153.6 | 50.5 | -5.048
153.7 | 50.5 | -5.048
153.8 | 50.5 | -5.048
153.9 | 50.5 | -5.048
154 | 50.5 | -5.048
154.1 | 50.5 | -5.048
154.2 | 50.5 | -5.048
154.3 | 50.5 | -5.048
154.4 | 50.5 | -5.048
154.5 | 50.5 | -5.048
154.6 | 50.5 | -5.048
154.7 | 50.5 | -5.048
154.8 | 50.5 | -5.048
154.9 | 50.5 | -5.048
155 | 50.5 | -5.048
155.1 | 50.5 | -5.048
155.2 | 50.5 | -5.048
155.3 | 50.5 | -5.048
155.4 | 50.5 | -5.048
155.5 | 50.5 | -5.048
155.6 | 50.5 | -5.048
155.7 | 50.5 | -5.048
155.8 | 50.5 | -5.048
155.9 | 50.5 | -5.047
156 | 50.5 | -5.047
156.1 | 50.5 | -5.047
156.2 | 50.5 | -5.047
156.3 | 50.5 | -5.047
156.4 | 50.5 | -5.048
156.5 | 50.5 | -5.048
156.6 | 50.5 | -5.048
156.7 | 50.5 | -5.048
156.8 | 50.5 | -5.048
156.9 | 50.5 | -5.048
157 | 50.5 | -5.048
157.1 | 50.5 | -5.048
157.2 | 50.5 | -5.048
157.3 | 50.5 | -5.048
157.4 | 50.5 | -5.048
157.5 | 50.5 | -5.048
157.6 | 50.5 | -5.048
157.7 | 50.5 | -5.048
157.8 | 50.5 | -5.048
157.9 | 50.5 | -5.048
158 | 50.5 | -5.048
158.1 | 50.5 | -5.048
158.2 | 50.5 | -5.048
158.3 | 50.5 | -5.048
158.4 | 50.5 | -5.048
158.5 | 50.5 | -5.048
158.6 | 50.5 | -5.048
158.7 | 50.5 | -5.048
158.8 | 50.5 | -5.048
158.9 | 50.5 | -5.048
159 | 50.5 | -5.048
159.1 | 50.5 | -5.048
159.2 | 50.5 | -5.048
159.3 | 50.5 | -5.048
159.4 | 50.5 | -5.048
159.5 | 50.5 | -5.048
159.6 | 50.5 | -5.048
159.7 | 50.5 | -5.048
159.8 | 50.5 | -5.048
159.9 | 50.5 | -5.047
160 | 50.5 | -5.048
160.1 | 50.5 | -5.048
160.2 | 50.5 | -5.048
160.3 | 50.5 | -5.048
160.4 | 50.5 | -5.048
160.5 | 50.5 | -5.048
160.6 | 50.5 | -5.048
160.7 | 50.5 | -5.048
160.8 | 50.5 | -5.048
160.9 | 50.5 | -5.048
161 | 50.5 | -5.048
161.1 | 50.5 | -5.048
161.2 | 50.5 | -5.048
161.3 | 50.5 | -5.048
161.4 | 50.5 | -5.048
161.5 | 50.5 | -5.048
161.6 | 50.5 | -5.048
161.7 | 50.5 | -5.048
161.8 | 50.5 | -5.048
161.9 | 50.5 | -5.048
162 | 50.5 | -5.048
162.1 | 50.5 | -5.048
162.2 | 50.5 | -5.049
162.3 | 50.5 | -5.049
162.4 | 50.5 | -5.048
162.5 | 50.5 | -5.048
162.6 | 50.5 | -5.048
162.7 | 50.5 | -5.048
162.8 | 50.5 | -5.048
162.9 | 50.5 | -5.048
163 | 50.5 | -5.048
163.1 | 50.5 | -5.048
163.2 | 50.5 | -5.048
163.3 | 50.5 | -5.048
163.4 | 50.5 | -5.048
163.5 | 50.5 | -5.048
163.6 | 50.5 | -5.048
163.7 | 50.5 | -5.048
163.8 | 50.5 | -5.048
163.9 | 50.5 | -5.048
164 | 50.5 | -5.048
164.1 | 50.5 | -5.048
164.2 | 50.5 | -5.048
164.3 | 50.5 | -5.048
164.4 | 50.5 | -5.048
164.5 | 50.5 | -5.048
164.6 | 50.5 | -5.048
164.7 | 50.5 | -5.048
164.8 | 50.5 | -5.048
164.9 | 50.5 | -5.048
165 | 50.5 | -5.048
165.1 | 50.5 | -5.048
165.2 | 50.5 | -5.048
165.3 | 50.5 | -5.048
165.4 | 50.5 | -5.048
165.5 | 50.5 | -5.048
165.6 | 50.5 | -5.048
165.7 | 50.5 | -5.048
165.8 | 50.5 | -5.048
165.9 | 50.5 | -5.047
166 | 50.5 | -5.047
166.1 | 50.5 | -5.047
166.2 | 50.5 | -5.047
166.3 | 50.5 | -5.047
166.4 | 50.5 | -5.047
166.5 | 50.5 | -5.047
166.6 | 50.5 | -5.047
166.7 | 50.5 | -5.047
166.8 | 50.5 | -5.047
166.9 | 50.5 | -5.047
167 | 50.5 | -5.047
167.1 | 50.5 | -5.047
167.2 | 50.5 | -5.047
167.3 | 50.5 | -5.047
167.4 | 50.5 | -5.047
167.5 | 50.5 | -5.047
167.6 | 50.5 | -5.047
167.7 | 50.5 | -5.047
167.8 | 50.5 | -5.047
167.9 | 50.5 | -5.047
168 | 50.5 | -5.048
168.1 | 50.5 | -5.048
168.2 | 50.5 | -5.048
168.3 | 50.5 | -5.048
168.4 | 50.5 | -5.048
168.5 | 50.5 | -5.048
168.6 | 50.5 | -5.048
168.7 | 50.5 | -5.048
168.8 | 50.5 | -5.048
168.9 | 50.5 | -5.048
169 | 50.5 | -5.048
169.1 | 50.5 | -5.048
169.2 | 50.5 | -5.048
169.3 | 50.5 | -5.048
169.4 | 50.5 | -5.048
169.5 | 50.5 | -5.048
169.6 | 50.5 | -5.048
169.7 | 50.5 | -5.048
169.8 | 50.5 | -5.048
169.9 | 50.5 | -5.048
170 | 50.5 | -5.048
170.1 | 50.5 | -5.048
170.2 | 50.5 | -5.048
170.3 | 50.5 | -5.048
170.4 | 50.5 | -5.048
170.5 | 50.5 | -5.048
170.6 | 50.5 | -5.048
170.7 | 50.5 | -5.048
170.8 | 50.5 | -5.048
170.9 | 50.5 | -5.048
171 | 50.5 | -5.048
171.1 | 50.5 | -5.048
171.2 | 50.5 | -5.048
171.3 | 50.5 | -5.048
171.4 | 50.5 | -5.048
171.5 | 50.5 | -5.048
171.6 | 50.5 | -5.048
171.7 | 50.5 | -5.048
171.8 | 50.5 | -5.048
171.9 | 50.5 | -5.048
172 | 50.5 | -5.048
172.1 | 50.5 | -5.048
172.2 | 50.5 | -5.048
172.3 | 50.5 | -5.048
172.4 | 50.5 | -5.048
172.5 | 50.5 | -5.048
172.6 | 50.5 | -5.048
172.7 | 50.5 | -5.048
172.8 | 50.5 | -5.048
172.9 | 50.5 | -5.048
173 | 50.5 | -5.048
173.1 | 50.5 | -5.048
173.2 | 50.5 | -5.048
173.3 | 50.5 | -5.048
173.4 | 50.5 | -5.048
173.5 | 50.5 | -5.048
173.6 | 50.5 | -5.048
173.7 | 50.5 | -5.048
173.8 | 50.5 | -5.048
173.9 | 50.5 | -5.048
174 | 50.5 | -5.048
174.1 | 50.5 | -5.047
174.2 | 50.5 | -5.047
174.3 | 50.5 | -5.047
174.4 | 50.5 | -5.047
174.5 | 50.5 | -5.047
174.6 | 50.5 | -5.047
174.7 | 50.5 | -5.047
174.8 | 50.5 | -5.047
174.9 | 50.5 | -5.047
175 | 50.5 | -5.047
175.1 | 50.5 | -5.047
175.2 | 50.5 | -5.047
175.3 | 50.5 | -5.047
175.4 | 50.5 | -5.047
175.5 | 50.5 | -5.047
175.6 | 50.5 | -5.047
175.7 | 50.5 | -5.047
175.8 | 50.5 | -5.047
175.9 | 50.5 | -5.047
176 | 50.5 | -5.047
176.1 | 50.5 | -5.047
176.2 | 50.5 | -5.047
176.3 | 50.5 | -5.047
176.4 | 50.5 | -5.048
176.5 | 50.5 | -5.048
176.6 | 50.5 | -5.048
176.7 | 50.5 | -5.048
176.8 | 50.5 | -5.048
176.9 | 50.5 | -5.048
177 | 50.5 | -5.048
177.1 | 50.5 | -5.048
177.2 | 50.5 | -5.048
177.3 | 50.5 | -5.048
177.4 | 50.5 | -5.048
177.5 | 50.5 | -5.048
177.6 | 50.5 | -5.048
177.7 | 50.5 | -5.048
177.8 | 50.5 | -5.048
177.9 | 50.5 | -5.048
178 | 50.5 | -5.048
178.1 | 50.5 | -5.048
178.2 | 50.5 | -5.048
178.3 | 50.5 | -5.048
178.4 | 50.5 | -5.048
178.5 | 50.5 | -5.048
178.6 | 50.5 | -5.048
178.7 | 50.5 | -5.048
178.8 | 50.5 | -5.048
178.9 | 50.5 | -5.048
179 | 50.5 | -5.048
179.1 | 50.5 | -5.048
179.2 | 50.5 | -5.048
179.3 | 50.5 | -5.048
179.4 | 50.5 | -5.048
179.5 | 50.5 | -5.048
179.6 | 50.5 | -5.048
179.7 | 50.5 | -5.048
179.8 | 50.5 | -5.047
179.9 | 50.5 | -5.047
180 | 50.5 | -5.047
180.1 | 50.5 | -5.047
180.2 | 50.5 | -5.047
180.3 | 50.5 | -5.047
180.4 | 50.5 | -5.047
180.5 | 50.5 | -5.047
180.6 | 50.5 | -5.047
180.7 | 50.5 | -5.047
180.8 | 50.5 | -5.047
180.9 | 50.5 | -5.047
181 | 50.5 | -5.047
181.1 | 50.5 | -5.047
181.2 | 50.5 | -5.047
181.3 | 50.5 | -5.047
181.4 | 50.5 | -5.047
181.5 | 50.5 | -5.047
181.6 | 50.5 | -5.047
181.7 | 50.5 | -5.047
181.8 | 50.5 | -5.047
181.9 | 50.5 | -5.047
182 | 50.5 | -5.047
182.1 | 50.5 | -5.047
182.2 | 50.5 | -5.048
182.3 | 50.5 | -5.048
182.4 | 50.5 | -5.048
182.5 | 50.5 | -5.048
182.6 | 50.5 | -5.048
182.7 | 50.5 | -5.048
182.8 | 50.5 | -5.048
182.9 | 50.5 | -5.048
183 | 50.5 | -5.048
183.1 | 50.5 | -5.048
183.2 | 50.5 | -5.048
183.3 | 50.5 | -5.048
183.4 | 50.5 | -5.048
183.5 | 50.5 | -5.048
183.6 | 50.5 | -5.048
183.7 | 50.5 | -5.048
183.8 | 50.5 | -5.048
183.9 | 50.5 | -5.048
184 | 50.5 | -5.048
184.1 | 50.5 | -5.048
184.2 | 50.5 | -5.048
184.3 | 50.5 | -5.048
184.4 | 50.5 | -5.048
184.5 | 50.5 | -5.048
184.6 | 50.5 | -5.048
184.7 | 50.5 | -5.048
184.8 | 50.5 | -5.048
184.9 | 50.5 | -5.048
185 | 50.5 | -5.048
185.1 | 50.5 | -5.048
185.2 | 50.5 | -5.048
185.3 | 50.5 | -5.048
185.4 | 50.5 | -5.048
185.5 | 50.5 | -5.048
185.6 | 50.5 | -5.048
185.7 | 50.5 | -5.047
185.8 | 50.5 | -5.047
185.9 | 50.5 | -5.047
186 | 50.5 | -5.047
186.1 | 50.5 | -5.047
186.2 | 50.5 | -5.047
186.3 | 50.5 | -5.047
186.4 | 50.5 | -5.047
186.5 | 50.5 | -5.047
186.6 | 50.5 | -5.047
186.7 | 50.5 | -5.047
186.8 | 50.5 | -5.047
186.9 | 50.5 | -5.047
187 | 50.5 | -5.047
187.1 | 50.5 | -5.047
187.2 | 50.5 | -5.047
187.3 | 50.5 | -5.047
187.4 | 50.5 | -5.047
187.5 | 50.5 | -5.047
187.6 | 50.5 | -5.047
187.7 | 50.5 | -5.047
187.8 | 50.5 | -5.047
187.9 | 50.5 | -5.047
188 | 50.5 | -5.048
188.1 | 50.5 | -5.048
188.2 | 50.5 | -5.048
188.3 | 50.5 | -5.048
188.4 | 50.5 | -5.048
188.5 | 50.5 | -5.048
188.6 | 50.5 | -5.048
188.7 | 50.5 | -5.048
188.8 | 50.5 | -5.048
188.9 | 50.5 | -5.048
189 | 50.5 | -5.048
189.1 | 50.5 | -5.048
189.2 | 50.5 | -5.048
189.3 | 50.5 | -5.048
189.4 | 50.5 | -5.048
189.5 | 50.5 | -5.048
189.6 | 50.5 | -5.048
189.7 | 50.5 | -5.048
189.8 | 50.5 | -5.048
189.9 | 50.5 | -5.048
190 | 50.5 | -5.048
190.1 | 50.5 | -5.048
190.2 | 50.5 | -5.048
190.3 | 50.5 | -5.048
190.4 | 50.5 | -5.048
190.5 | 50.5 | -5.048
190.6 | 50.5 | -5.048
190.7 | 50.5 | -5.048
190.8 | 50.5 | -5.048
190.9 | 50.5 | -5.048
191 | 50.5 | -5.048
191.1 | 50.5 | -5.048
191.2 | 50.5 | -5.048
191.3 | 50.5 | -5.048
191.4 | 50.5 | -5.048
191.5 | 50.5 | -5.048
191.6 | 50.5 | -5.048
191.7 | 50.5 | -5.048
191.8 | 50.5 | -5.048
191.9 | 50.5 | -5.048
192 | 50.5 | -5.048
192.1 | 50.5 | -5.048
192.2 | 50.5 | -5.048
192.3 | 50.5 | -5.048
192.4 | 50.5 | -5.048
192.5 | 50.5 | -5.048
192.6 | 50.5 | -5.048
192.7 | 50.5 | -5.048
192.8 | 50.5 | -5.048
192.9 | 50.5 | -5.047
193 | 50.5 | -5.047
193.1 | 50.5 | -5.047
193.2 | 50.5 | -5.047
193.3 | 50.5 | -5.047
193.4 | 50.5 | -5.047
193.5 | 50.5 | -5.047
193.6 | 50.5 | -5.047
193.7 | 50.5 | -5.047
193.8 | 50.5 | -5.047
193.9 | 50.5 | -5.047
194 | 50.5 | -5.047
194.1 | 50.5 | -5.047
194.2 | 50.5 | -5.047
194.3 | 50.5 | -5.047
194.4 | 50.5 | -5.047
194.5 | 50.5 | -5.047
194.6 | 50.5 | -5.047
194.7 | 50.5 | -5.047
194.8 | 50.5 | -5.047
194.9 | 50.5 | -5.047
195 | 50.5 | -5.048
195.1 | 50.5 | -5.048
195.2 | 50.5 | -5.048
195.3 | 50.5 | -5.048
195.4 | 50.5 | -5.048
195.5 | 50.5 | -5.048
195.6 | 50.5 | -5.048
195.7 | 50.5 | -5.048
195.8 | 50.5 | -5.048
195.9 | 50.5 | -5.048
196 | 50.5 | -5.048
196.1 | 50.5 | -5.048
196.2 | 50.5 | -5.048
196.3 | 50.5 | -5.048
196.4 | 50.5 | -5.048
196.5 | 50.5 | -5.048
196.6 | 50.5 | -5.048
196.7 | 50.5 | -5.048
196.8 | 50.5 | -5.048
196.9 | 50.5 | -5.048
197 | 50.5 | -5.048
197.1 | 50.5 | -5.048
197.2 | 50.5 | -5.048
197.3 | 50.5 | -5.048
197.4 | 50.5 | -5.048
197.5 | 50.5 | -5.048
197.6 | 50.5 | -5.047
197.7 | 50.5 | -5.047
197.8 | 50.5 | -5.047
197.9 | 50.5 | -5.047
198 | 50.5 | -5.047
198.1 | 50.5 | -5.047
198.2 | 50.5 | -5.047
198.3 | 50.5 | -5.047
198.4 | 50.5 | -5.047
198.5 | 50.5 | -5.047
198.6 | 50.5 | -5.047
198.7 | 50.5 | -5.047
198.8 | 50.5 | -5.047
198.9 | 50.5 | -5.047
199 | 50.5 | -5.047
199.1 | 50.5 | -5.047
199.2 | 50.5 | -5.047
199.3 | 50.5 | -5.047
199.4 | 50.5 | -5.047
199.5 | 50.5 | -5.047
199.6 | 50.5 | -5.047
199.7 | 50.5 | -5.047
199.8 | 50.5 | -5.047
199.9 | 50.5 | -5.047
200 | 50.5 | -5.047
200.1 | 50.5 | -5.047
200.2 | 50.5 | -5.047
200.3 | 50.5 | -5.047
200.4 | 50.5 | -5.047
200.5 | 50.5 | -5.047
200.6 | 50.5 | -5.047
200.7 | 50.5 | -5.047
200.8 | 50.5 | -5.048
200.9 | 50.5 | -5.048
201 | 50.5 | -5.048
201.1 | 50.5 | -5.048
201.2 | 50.5 | -5.048
201.3 | 50.5 | -5.048
201.4 | 50.5 | -5.048
201.5 | 50.5 | -5.048
201.6 | 50.5 | -5.048
201.7 | 50.5 | -5.048
201.8 | 50.5 | -5.048
201.9 | 50.5 | -5.048
202 | 50.5 | -5.048
202.1 | 50.5 | -5.048
202.2 | 50.5 | -5.048
202.3 | 50.5 | -5.048
202.4 | 50.5 | -5.048
202.5 | 50.5 | -5.048
202.6 | 50.5 | -5.048
202.7 | 50.5 | -5.048
202.8 | 50.5 | -5.048
202.9 | 50.5 | -5.048
203 | 50.5 | -5.048
203.1 | 50.5 | -5.048
203.2 | 50.5 | -5.048
203.3 | 50.5 | -5.048
203.4 | 50.5 | -5.048
203.5 | 50.5 | -5.048
203.6 | 50.5 | -5.048
203.7 | 50.5 | -5.048
203.8 | 50.5 | -5.048
203.9 | 50.5 | -5.048
204 | 50.5 | -5.048
204.1 | 50.5 | -5.048
204.2 | 50.5 | -5.048
204.3 | 50.5 | -5.048
204.4 | 50.5 | -5.048
204.5 | 50.5 | -5.047
204.6 | 50.5 | -5.047
204.7 | 50.5 | -5.047
204.8 | 50.5 | -5.047
204.9 | 50.5 | -5.047
205 | 50.5 | -5.047
205.1 | 50.5 | -5.047
205.2 | 50.5 | -5.047
205.3 | 50.5 | -5.047
205.4 | 50.5 | -5.047
205.5 | 50.5 | -5.047
205.6 | 50.5 | -5.047
205.7 | 50.5 | -5.047
205.8 | 50.5 | -5.048
205.9 | 50.5 | -5.048
206 | 50.5 | -5.048
206.1 | 50.5 | -5.048
206.2 | 50.5 | -5.048
206.3 | 50.5 | -5.048
206.4 | 50.5 | -5.048
206.5 | 50.5 | -5.048
206.6 | 50.5 | -5.048
206.7 | 50.5 | -5.048
206.8 | 50.5 | -5.048
206.9 | 50.5 | -5.048
207 | 50.5 | -5.048
207.1 | 50.5 | -5.048
207.2 | 50.5 | -5.048
207.3 | 50.5 | -5.048
207.4 | 50.5 | -5.048
207.5 | 50.5 | -5.048
207.6 | 50.5 | -5.048
207.7 | 50.5 | -5.048
207.8 | 50.5 | -5.048
207.9 | 50.5 | -5.048
208 | 50.5 | -5.048
208.1 | 50.5 | -5.048
208.2 | 50.5 | -5.048
208.3 | 50.5 | -5.048
208.4 | 50.5 | -5.048
208.5 | 50.5 | -5.048
208.6 | 50.5 | -5.048
208.7 | 50.5 | -5.048
208.8 | 50.5 | -5.048
208.9 | 50.5 | -5.048
209 | 50.5 | -5.048
209.1 | 50.5 | -5.048
209.2 | 50.5 | -5.048
209.3 | 50.5 | -5.048
209.4 | 50.5 | -5.048
209.5 | 50.5 | -5.048
209.6 | 50.5 | -5.048
209.7 | 50.5 | -5.048
209.8 | 50.5 | -5.048
209.9 | 50.5 | -5.048
210 | 50.5 | -5.048
210.1 | 50.5 | -5.048
210.2 | 50.5 | -5.047
210.3 | 50.5 | -5.047
210.4 | 50.5 | -5.047
210.5 | 50.5 | -5.047
210.6 | 50.5 | -5.047
210.7 | 50.5 | -5.047
210.8 | 50.5 | -5.047
210.9 | 50.5 | -5.047
211 | 50.5 | -5.047
211.1 | 50.5 | -5.047
211.2 | 50.5 | -5.047
211.3 | 50.5 | -5.047
211.4 | 50.5 | -5.047
211.5 | 50.5 | -5.047
211.6 | 50.5 | -5.047
211.7 | 50.5 | -5.047
211.8 | 50.5 | -5.047
211.9 | 50.5 | -5.047
212 | 50.5 | -5.047
212.1 | 50.5 | -5.047
212.2 | 50.5 | -5.047
212.3 | 50.5 | -5.047
212.4 | 50.5 | -5.047
212.5 | 50.5 | -5.047
212.6 | 50.5 | -5.048
212.7 | 50.5 | -5.048
212.8 | 50.5 | -5.048
212.9 | 50.5 | -5.048
213 | 50.5 | -5.048
213.1 | 50.5 | -5.048
213.2 | 50.5 | -5.048
213.3 | 50.5 | -5.048
213.4 | 50.5 | -5.048
213.5 | 50.5 | -5.048
213.6 | 50.5 | -5.048
213.7 | 50.5 | -5.048
213.8 | 50.5 | -5.048
213.9 | 50.5 | -5.048
214 | 50.5 | -5.048
214.1 | 50.5 | -5.048
214.2 | 50.5 | -5.048
214.3 | 50.5 | -5.048
214.4 | 50.5 | -5.048
214.5 | 50.5 | -5.048
214.6 | 50.5 | -5.048
214.7 | 50.5 | -5.048
214.8 | 50.5 | -5.049
214.9 | 50.5 | -5.049
215 | 50.5 | -5.049
215.1 | 50.5 | -5.049
215.2 | 50.5 | -5.049
215.3 | 50.5 | -5.049
215.4 | 50.5 | -5.049
215.5 | 50.5 | -5.049
215.6 | 50.5 | -5.049
215.7 | 50.5 | -5.049
215.8 | 50.5 | -5.049
215.9 | 50.5 | -5.049
216 | 50.5 | -5.049
216.1 | 50.5 | -5.048
216.2 | 50.5 | -5.048
216.3 | 50.5 | -5.048
216.4 | 50.5 | -5.048
216.5 | 50.5 | -5.048
216.6 | 50.5 | -5.048
216.7 | 50.5 | -5.048
216.8 | 50.5 | -5.048
216.9 | 50.5 | -5.048
217 | 50.5 | -5.048
217.1 | 50.5 | -5.048
217.2 | 50.5 | -5.048
217.3 | 50.5 | -5.048
217.4 | 50.5 | -5.048
217.5 | 50.5 | -5.048
217.6 | 50.5 | -5.048
217.7 | 50.5 | -5.048
217.8 | 50.5 | -5.048
217.9 | 50.5 | -5.048
218 | 50.5 | -5.048
218.1 | 50.5 | -5.048
218.2 | 50.5 | -5.048
218.3 | 50.5 | -5.048
218.4 | 50.5 | -5.048
218.5 | 50.5 | -5.047
218.6 | 50.5 | -5.047
218.7 | 50.5 | -5.047
218.8 | 50.5 | -5.047
218.9 | 50.5 | -5.047
219 | 50.5 | -5.047
219.1 | 50.5 | -5.047
219.2 | 50.5 | -5.047
219.3 | 50.5 | -5.047
219.4 | 50.5 | -5.047
219.5 | 50.5 | -5.047
219.6 | 50.5 | -5.048
219.7 | 50.5 | -5.048
219.8 | 50.5 | -5.048
219.9 | 50.5 | -5.048
220 | 50.5 | -5.048
220.1 | 50.5 | -5.048
220.2 | 50.5 | -5.048
220.3 | 50.5 | -5.048
220.4 | 50.5 | -5.048
220.5 | 50.5 | -5.048
220.6 | 50.5 | -5.048
220.7 | 50.5 | -5.048
220.8 | 50.5 | -5.048
220.9 | 50.5 | -5.048
221 | 50.5 | -5.048
221.1 | 50.5 | -5.048
221.2 | 50.5 | -5.048
221.3 | 50.5 | -5.048
221.4 | 50.5 | -5.048
221.5 | 50.5 | -5.048
221.6 | 50.5 | -5.048
221.7 | 50.5 | -5.048
221.8 | 50.5 | -5.048
221.9 | 50.5 | -5.048
222 | 50.5 | -5.048
222.1 | 50.5 | -5.048
222.2 | 50.5 | -5.048
222.3 | 50.5 | -5.048
222.4 | 50.5 | -5.048
222.5 | 50.5 | -5.048
222.6 | 50.5 | -5.048
222.7 | 50.5 | -5.048
222.8 | 50.5 | -5.048
222.9 | 50.5 | -5.048
223 | 50.5 | -5.048
223.1 | 50.5 | -5.048
223.2 | 50.5 | -5.048
223.3 | 50.5 | -5.048
223.4 | 50.5 | -5.048
223.5 | 50.5 | -5.048
223.6 | 50.5 | -5.048
223.7 | 50.5 | -5.048
223.8 | 50.5 | -5.048
223.9 | 50.5 | -5.048
224 | 50.5 | -5.048
224.1 | 50.5 | -5.048
224.2 | 50.5 | -5.048
224.3 | 50.5 | -5.048
224.4 | 50.5 | -5.048
224.5 | 50.5 | -5.048
224.6 | 50.5 | -5.048
224.7 | 50.5 | -5.048
224.8 | 50.5 | -5.048
224.9 | 50.5 | -5.048
225 | 50.5 | -5.048
225.1 | 50.5 | -5.048
225.2 | 50.5 | -5.048
225.3 | 50.5 | -5.048
225.4 | 50.5 | -5.048
225.5 | 50.5 | -5.048
225.6 | 50.5 | -5.048
225.7 | 50.5 | -5.048
225.8 | 50.5 | -5.048
225.9 | 50.5 | -5.048
226 | 50.5 | -5.048
226.1 | 50.5 | -5.048
226.2 | 50.5 | -5.048
226.3 | 50.5 | -5.048
226.4 | 50.5 | -5.048
226.5 | 50.5 | -5.048
226.6 | 50.5 | -5.048
226.7 | 50.5 | -5.048
226.8 | 50.5 | -5.048
226.9 | 50.5 | -5.047
227 | 50.5 | -5.047
227.1 | 50.5 | -5.047
227.2 | 50.5 | -5.047
227.3 | 50.5 | -5.047
227.4 | 50.5 | -5.047
227.5 | 50.5 | -5.047
227.6 | 50.5 | -5.047
227.7 | 50.5 | -5.047
227.8 | 50.5 | -5.047
227.9 | 50.5 | -5.047
228 | 50.5 | -5.047
228.1 | 50.5 | -5.048
228.2 | 50.5 | -5.048
228.3 | 50.5 | -5.048
228.4 | 50.5 | -5.048
228.5 | 50.5 | -5.048
228.6 | 50.5 | -5.048
228.7 | 50.5 | -5.048
228.8 | 50.5 | -5.048
228.9 | 50.5 | -5.048
229 | 50.5 | -5.048
229.1 | 50.5 | -5.048
229.2 | 50.5 | -5.048
229.3 | 50.5 | -5.048
229.4 | 50.5 | -5.048
229.5 | 50.5 | -5.048
229.6 | 50.5 | -5.048
229.7 | 50.5 | -5.048
229.8 | 50.5 | -5.048
229.9 | 50.5 | -5.048
230 | 50.5 | -5.048
230.1 | 50.5 | -5.048
230.2 | 50.5 | -5.048
230.3 | 50.5 | -5.048
230.4 | 50.5 | -5.048
230.5 | 50.5 | -5.048
230.6 | 50.5 | -5.048
230.7 | 50.5 | -5.048
230.8 | 50.5 | -5.048
230.9 | 50.5 | -5.048
231 | 50.5 | -5.048
231.1 | 50.5 | -5.048
231.2 | 50.5 | -5.048
231.3 | 50.5 | -5.048
231.4 | 50.5 | -5.048
231.5 | 50.5 | -5.048
231.6 | 50.5 | -5.048
231.7 | 50.5 | -5.048
231.8 | 50.5 | -5.048
231.9 | 50.5 | -5.048
232 | 50.5 | -5.048
232.1 | 50.5 | -5.048
232.2 | 50.5 | -5.048
232.3 | 50.5 | -5.048
232.4 | 50.5 | -5.048
232.5 | 50.5 | -5.048
232.6 | 50.5 | -5.048
232.7 | 50.5 | -5.048
232.8 | 50.5 | -5.048
232.9 | 50.5 | -5.048
233 | 50.5 | -5.048
233.1 | 50.5 | -5.048
233.2 | 50.5 | -5.048
233.3 | 50.5 | -5.048
233.4 | 50.5 | -5.048
233.5 | 50.5 | -5.048
233.6 | 50.5 | -5.048
233.7 | 50.5 | -5.048
233.8 | 50.5 | -5.048
233.9 | 50.5 | -5.048
234 | 50.5 | -5.048
234.1 | 50.5 | -5.048
234.2 | 50.5 | -5.048
234.3 | 50.5 | -5.048
234.4 | 50.5 | -5.048
234.5 | 50.5 | -5.048
234.6 | 50.5 | -5.048
234.7 | 50.5 | -5.048
234.8 | 50.5 | -5.048
234.9 | 50.5 | -5.048
235 | 50.5 | -5.048
235.1 | 50.5 | -5.048
235.2 | 50.5 | -5.048
235.3 | 50.5 | -5.048
235.4 | 50.5 | -5.048
235.5 | 50.5 | -5.048
235.6 | 50.5 | -5.048
235.7 | 50.5 | -5.048
235.8 | 50.5 | -5.048
235.9 | 50.5 | -5.048
236 | 50.5 | -5.048
236.1 | 50.5 | -5.048
236.2 | 50.5 | -5.048
236.3 | 50.5 | -5.048
236.4 | 50.5 | -5.048
236.5 | 50.5 | -5.048
236.6 | 50.5 | -5.048
236.7 | 50.5 | -5.048
236.8 | 50.5 | -5.048
236.9 | 50.5 | -5.048
237 | 50.5 | -5.048
237.1 | 50.5 | -5.048
237.2 | 50.5 | -5.048
237.3 | 50.5 | -5.048
237.4 | 50.5 | -5.048
237.5 | 50.5 | -5.048
237.6 | 50.5 | -5.048
237.7 | 50.5 | -5.048
237.8 | 50.5 | -5.048
237.9 | 50.5 | -5.048
238 | 50.5 | -5.048
238.1 | 50.5 | -5.048
238.2 | 50.5 | -5.048
238.3 | 50.5 | -5.048
238.4 | 50.5 | -5.048
238.5 | 50.5 | -5.048
238.6 | 50.5 | -5.048
238.7 | 50.5 | -5.048
238.8 | 50.5 | -5.048
238.9 | 50.5 | -5.048
239 | 50.5 | -5.048
239.1 | 50.5 | -5.048
239.2 | 50.5 | -5.048
239.3 | 50.5 | -5.048
239.4 | 50.5 | -5.048
239.5 | 50.5 | -5.048
239.6 | 50.5 | -5.048
239.7 | 50.5 | -5.047
239.8 | 50.5 | -5.047
239.9 | 50.5 | -5.047
240 | 50.5 | -5.047
240.1 | 50.5 | -5.047
240.2 | 50.5 | -5.047
240.3 | 50.5 | -5.047
240.4 | 50.5 | -5.047
240.5 | 50.5 | -5.047
240.6 | 50.5 | -5.047
240.7 | 50.5 | -5.047
240.8 | 50.5 | -5.047
240.9 | 50.5 | -5.047
241 | 50.5 | -5.047
241.1 | 50.5 | -5.047
241.2 | 50.5 | -5.047
241.3 | 50.5 | -5.047
241.4 | 50.5 | -5.047
241.5 | 50.5 | -5.047
241.6 | 50.5 | -5.047
241.7 | 50.5 | -5.047
241.8 | 50.5 | -5.047
241.9 | 50.5 | -5.047
242 | 50.5 | -5.048
242.1 | 50.5 | -5.048
242.2 | 50.5 | -5.048
242.3 | 50.5 | -5.048
242.4 | 50.5 | -5.048
242.5 | 50.5 | -5.048
242.6 | 50.5 | -5.048
242.7 | 50.5 | -5.048
242.8 | 50.5 | -5.048
242.9 | 50.5 | -5.048
243 | 50.5 | -5.048
243.1 | 50.5 | -5.048
243.2 | 50.5 | -5.048
243.3 | 50.5 | -5.048
243.4 | 50.5 | -5.048
243.5 | 50.5 | -5.048
243.6 | 50.5 | -5.048
243.7 | 50.5 | -5.048
243.8 | 50.5 | -5.048
243.9 | 50.5 | -5.048
244 | 50.5 | -5.048
244.1 | 50.5 | -5.048
244.2 | 50.5 | -5.048
244.3 | 50.5 | -5.048
244.4 | 50.5 | -5.048
244.5 | 50.5 | -5.048
244.6 | 50.5 | -5.048
244.7 | 50.5 | -5.048
244.8 | 50.5 | -5.048
244.9 | 50.5 | -5.048
245 | 50.5 | -5.048
245.1 | 50.5 | -5.048
245.2 | 50.5 | -5.048
245.3 | 50.5 | -5.048
245.4 | 50.5 | -5.048
245.5 | 50.5 | -5.048
245.6 | 50.5 | -5.048
245.7 | 50.5 | -5.048
245.8 | 50.5 | -5.048
245.9 | 50.5 | -5.048
246 | 50.5 | -5.048
246.1 | 50.5 | -5.048
246.2 | 50.5 | -5.048
246.3 | 50.5 | -5.048
246.4 | 50.5 | -5.048
246.5 | 50.5 | -5.048
246.6 | 50.5 | -5.048
246.7 | 50.5 | -5.048
246.8 | 50.5 | -5.048
246.9 | 50.5 | -5.048
247 | 50.5 | -5.048
247.1 | 50.5 | -5.048
247.2 | 50.5 | -5.048
247.3 | 50.5 | -5.048
247.4 | 50.5 | -5.048
247.5 | 50.5 | -5.048
247.6 | 50.5 | -5.048
247.7 | 50.5 | -5.048
247.8 | 50.5 | -5.048
247.9 | 50.5 | -5.048
248 | 50.5 | -5.048
248.1 | 50.5 | -5.048
248.2 | 50.5 | -5.048
248.3 | 50.5 | -5.048
248.4 | 50.5 | -5.048
248.5 | 50.5 | -5.048
248.6 | 50.5 | -5.048
248.7 | 50.5 | -5.048
248.8 | 50.5 | -5.048
248.9 | 50.5 | -5.048
249 | 50.5 | -5.048
249.1 | 50.5 | -5.048
249.2 | 50.5 | -5.048
249.3 | 50.5 | -5.048
249.4 | 50.5 | -5.048
249.5 | 50.5 | -5.048
249.6 | 50.5 | -5.048
249.7 | 50.5 | -5.048
249.8 | 50.5 | -5.048
249.9 | 50.5 | -5.048
250 | 50.5 | -5.048
250.1 | 50.5 | -5.048
250.2 | 50.5 | -5.048
250.3 | 50.5 | -5.048
250.4 | 50.5 | -5.048
250.5 | 50.5 | -5.048
250.6 | 50.5 | -5.048
250.7 | 50.5 | -5.048
250.8 | 50.5 | -5.048
250.9 | 50.5 | -5.048
251 | 50.5 | -5.048
251.1 | 50.5 | -5.048
251.2 | 50.5 | -5.048
251.3 | 50.5 | -5.048
251.4 | 50.5 | -5.048
251.5 | 50.5 | -5.048
251.6 | 50.5 | -5.048
251.7 | 50.5 | -5.048
251.8 | 50.5 | -5.048
251.9 | 50.5 | -5.048
252 | 50.5 | -5.048
252.1 | 50.5 | -5.048
252.2 | 50.5 | -5.048
252.3 | 50.5 | -5.048
252.4 | 50.5 | -5.048
252.5 | 50.5 | -5.048
252.6 | 50.5 | -5.048
252.7 | 50.5 | -5.048
252.8 | 50.5 | -5.048
252.9 | 50.5 | -5.048
253 | 50.5 | -5.048
253.1 | 50.5 | -5.048
253.2 | 50.5 | -5.048
253.3 | 50.5 | -5.048
253.4 | 50.5 | -5.048
253.5 | 50.5 | -5.048
253.6 | 50.5 | -5.048
253.7 | 50.5 | -5.048
253.8 | 50.5 | -5.048
253.9 | 50.5 | -5.048
254 | 50.5 | -5.048
254.1 | 50.5 | -5.048
254.2 | 50.5 | -5.048
254.3 | 50.5 | -5.048
254.4 | 50.5 | -5.048
254.5 | 50.5 | -5.048
254.6 | 50.5 | -5.048
254.7 | 50.5 | -5.048
254.8 | 50.5 | -5.048
254.9 | 50.5 | -5.048
255 | 50.5 | -5.048
255.1 | 50.5 | -5.048
255.2 | 50.5 | -5.048
255.3 | 50.5 | -5.048
255.4 | 50.5 | -5.048
255.5 | 50.5 | -5.048
255.6 | 50.5 | -5.048
255.7 | 50.5 | -5.048
255.8 | 50.5 | -5.048
255.9 | 50.5 | -5.048
256 | 50.5 | -5.048
256.1 | 50.5 | -5.048
256.2 | 50.5 | -5.048
256.3 | 50.5 | -5.048
256.4 | 50.5 | -5.048
256.5 | 50.5 | -5.048
256.6 | 50.5 | -5.048
256.7 | 50.5 | -5.048
256.8 | 50.5 | -5.048
256.9 | 50.5 | -5.048
257 | 50.5 | -5.048
257.1 | 50.5 | -5.048
257.2 | 50.5 | -5.048
257.3 | 50.5 | -5.048
257.4 | 50.5 | -5.048
257.5 | 50.5 | -5.048
257.6 | 50.5 | -5.048
257.7 | 50.5 | -5.048
257.8 | 50.5 | -5.048
257.9 | 50.5 | -5.048
258 | 50.5 | -5.048
258.1 | 50.5 | -5.048
258.2 | 50.5 | -5.048
258.3 | 50.5 | -5.048
258.4 | 50.5 | -5.047
258.5 | 50.5 | -5.047
258.6 | 50.5 | -5.047
258.7 | 50.5 | -5.047
258.8 | 50.5 | -5.047
258.9 | 50.5 | -5.047
259 | 50.5 | -5.047
259.1 | 50.5 | -5.047
259.2 | 50.5 | -5.047
259.3 | 50.5 | -5.047
259.4 | 50.5 | -5.047
259.5 | 50.5 | -5.047
259.6 | 50.5 | -5.047
259.7 | 50.5 | -5.047
259.8 | 50.5 | -5.047
259.9 | 50.5 | -5.047
260 | 50.5 | -5.047
260.1 | 50.5 | -5.047
260.2 | 50.5 | -5.047
260.3 | 50.5 | -5.047
260.4 | 50.5 | -5.047
260.5 | 50.5 | -5.047
260.6 | 50.5 | -5.047
260.7 | 50.5 | -5.047
260.8 | 50.5 | -5.048
260.9 | 50.5 | -5.048
261 | 50.5 | -5.048
261.1 | 50.5 | -5.048
261.2 | 50.5 | -5.048
261.3 | 50.5 | -5.048
261.4 | 50.5 | -5.048
261.5 | 50.5 | -5.048
261.6 | 50.5 | -5.048
261.7 | 50.5 | -5.048
261.8 | 50.5 | -5.048
261.9 | 50.5 | -5.048
262 | 50.5 | -5.048
262.1 | 50.5 | -5.048
262.2 | 50.5 | -5.048
262.3 | 50.5 | -5.048
262.4 | 50.5 | -5.048
262.5 | 50.5 | -5.048
262.6 | 50.5 | -5.048
262.7 | 50.5 | -5.048
262.8 | 50.5 | -5.048
262.9 | 50.5 | -5.048
263 | 50.5 | -5.048
263.1 | 50.5 | -5.049
263.2 | 50.5 | -5.049
263.3 | 50.5 | -5.049
263.4 | 50.5 | -5.049
263.5 | 50.5 | -5.049
263.6 | 50.5 | -5.049
263.7 | 50.5 | -5.049
263.8 | 50.5 | -5.049
263.9 | 50.5 | -5.049
264 | 50.5 | -5.049
264.1 | 50.5 | -5.049
264.2 | 50.5 | -5.049
264.3 | 50.5 | -5.049
264.4 | 50.5 | -5.049
264.5 | 50.5 | -5.049
264.6 | 50.5 | -5.049
264.7 | 50.5 | -5.049
264.8 | 50.5 | -5.049
264.9 | 50.5 | -5.049
265 | 50.5 | -5.049
265.1 | 50.5 | -5.049
265.2 | 50.5 | -5.049
265.3 | 50.5 | -5.049
265.4 | 50.5 | -5.048
265.5 | 50.5 | -5.048
265.6 | 50.5 | -5.048
265.7 | 50.5 | -5.048
265.8 | 50.5 | -5.048
265.9 | 50.5 | -5.048
266 | 50.5 | -5.048
266.1 | 50.5 | -5.048
266.2 | 50.5 | -5.048
266.3 | 50.5 | -5.048
266.4 | 50.5 | -5.048
266.5 | 50.5 | -5.048
266.6 | 50.5 | -5.048
266.7 | 50.5 | -5.048
266.8 | 50.5 | -5.048
266.9 | 50.5 | -5.048
267 | 50.5 | -5.048
267.1 | 50.5 | -5.048
267.2 | 50.5 | -5.048
267.3 | 50.5 | -5.048
267.4 | 50.5 | -5.048
267.5 | 50.5 | -5.048
267.6 | 50.5 | -5.048
267.7 | 50.5 | -5.048
267.8 | 50.5 | -5.048
267.9 | 50.5 | -5.048
268 | 50.5 | -5.048
268.1 | 50.5 | -5.048
268.2 | 50.5 | -5.048
268.3 | 50.5 | -5.048
268.4 | 50.5 | -5.048
268.5 | 50.5 | -5.048
268.6 | 50.5 | -5.048
268.7 | 50.5 | -5.048
268.8 | 50.5 | -5.048
268.9 | 50.5 | -5.048
269 | 50.5 | -5.048
269.1 | 50.5 | -5.048
269.2 | 50.5 | -5.048
269.3 | 50.5 | -5.048
269.4 | 50.5 | -5.048
269.5 | 50.5 | -5.048
269.6 | 50.5 | -5.048
269.7 | 50.5 | -5.048
269.8 | 50.5 | -5.048
269.9 | 50.5 | -5.048
270 | 50.5 | -5.048
270.1 | 50.5 | -5.048
270.2 | 50.5 | -5.048
270.3 | 50.5 | -5.048
270.4 | 50.5 | -5.048
270.5 | 50.5 | -5.048
270.6 | 50.5 | -5.048
270.7 | 50.5 | -5.048
270.8 | 50.5 | -5.048
270.9 | 50.5 | -5.048
271 | 50.5 | -5.048
271.1 | 50.5 | -5.048
271.2 | 50.5 | -5.048
271.3 | 50.5 | -5.048
271.4 | 50.5 | -5.048
271.5 | 50.5 | -5.048
271.6 | 50.5 | -5.048
271.7 | 50.5 | -5.048
271.8 | 50.5 | -5.048
271.9 | 50.5 | -5.048
272 | 50.5 | -5.048
272.1 | 50.5 | -5.048
272.2 | 50.5 | -5.048
272.3 | 50.5 | -5.048
272.4 | 50.5 | -5.048
272.5 | 50.5 | -5.048
272.6 | 50.5 | -5.048
272.7 | 50.5 | -5.048
272.8 | 50.5 | -5.048
272.9 | 50.5 | -5.048
273 | 50.5 | -5.048
273.1 | 50.5 | -5.048
273.2 | 50.5 | -5.048
273.3 | 50.5 | -5.048
273.4 | 50.5 | -5.048
273.5 | 50.5 | -5.048
273.6 | 50.5 | -5.048
273.7 | 50.5 | -5.048
273.8 | 50.5 | -5.048
273.9 | 50.5 | -5.048
274 | 50.5 | -5.048
274.1 | 50.5 | -5.048
274.2 | 50.5 | -5.048
274.3 | 50.5 | -5.048
274.4 | 50.5 | -5.048
274.5 | 50.5 | -5.048
274.6 | 50.5 | -5.048
274.7 | 50.5 | -5.048
274.8 | 50.5 | -5.048
274.9 | 50.5 | -5.048
275 | 50.5 | -5.048
275.1 | 50.5 | -5.048
275.2 | 50.5 | -5.048
275.3 | 50.5 | -5.048
275.4 | 50.5 | -5.048
275.5 | 50.5 | -5.048
275.6 | 50.5 | -5.048
275.7 | 50.5 | -5.048
275.8 | 50.5 | -5.048
275.9 | 50.5 | -5.048
276 | 50.5 | -5.048
276.1 | 50.5 | -5.048
276.2 | 50.5 | -5.048
276.3 | 50.5 | -5.048
276.4 | 50.5 | -5.048
276.5 | 50.5 | -5.048
276.6 | 50.5 | -5.048
276.7 | 50.5 | -5.048
276.8 | 50.5 | -5.048
276.9 | 50.5 | -5.048
277 | 50.5 | -5.048
277.1 | 50.5 | -5.048
277.2 | 50.5 | -5.048
277.3 | 50.5 | -5.048
277.4 | 50.5 | -5.048
277.5 | 50.5 | -5.048
277.6 | 50.5 | -5.048
277.7 | 50.5 | -5.048
277.8 | 50.5 | -5.048
277.9 | 50.5 | -5.048
278 | 50.5 | -5.048
278.1 | 50.5 | -5.048
278.2 | 50.5 | -5.048
278.3 | 50.5 | -5.048
278.4 | 50.5 | -5.048
278.5 | 50.5 | -5.048
278.6 | 50.5 | -5.048
278.7 | 50.5 | -5.048
278.8 | 50.5 | -5.048
278.9 | 50.5 | -5.048
279 | 50.5 | -5.048
279.1 | 50.5 | -5.048
279.2 | 50.5 | -5.048
279.3 | 50.5 | -5.048
279.4 | 50.5 | -5.048
279.5 | 50.5 | -5.048
279.6 | 50.5 | -5.048
279.7 | 50.5 | -5.048
279.8 | 50.5 | -5.048
279.9 | 50.5 | -5.048
280 | 50.5 | -5.048
280.1 | 50.5 | -5.048
280.2 | 50.5 | -5.048
280.3 | 50.5 | -5.048
280.4 | 50.5 | -5.048
280.5 | 50.5 | -5.048
280.6 | 50.5 | -5.048
280.7 | 50.5 | -5.048
280.8 | 50.5 | -5.048
280.9 | 50.5 | -5.048
281 | 50.5 | -5.048
281.1 | 50.5 | -5.048
281.2 | 50.5 | -5.048
281.3 | 50.5 | -5.048
281.4 | 50.5 | -5.048
281.5 | 50.5 | -5.048
281.6 | 50.5 | -5.048
281.7 | 50.5 | -5.048
281.8 | 50.5 | -5.048
281.9 | 50.5 | -5.048
282 | 50.5 | -5.048
282.1 | 50.5 | -5.048
282.2 | 50.5 | -5.048
282.3 | 50.5 | -5.048
282.4 | 50.5 | -5.048
282.5 | 50.5 | -5.048
282.6 | 50.5 | -5.048
282.7 | 50.5 | -5.048
282.8 | 50.5 | -5.048
282.9 | 50.5 | -5.048
283 | 50.5 | -5.048
283.1 | 50.5 | -5.048
283.2 | 50.5 | -5.048
283.3 | 50.5 | -5.048
283.4 | 50.5 | -5.048
283.5 | 50.5 | -5.048
283.6 | 50.5 | -5.048
283.7 | 50.5 | -5.048
283.8 | 50.5 | -5.048
283.9 | 50.5 | -5.048
284 | 50.5 | -5.048
284.1 | 50.5 | -5.048
284.2 | 50.5 | -5.048
284.3 | 50.5 | -5.048
284.4 | 50.5 | -5.048
284.5 | 50.5 | -5.048
284.6 | 50.5 | -5.048
284.7 | 50.5 | -5.048
284.8 | 50.5 | -5.048
284.9 | 50.5 | -5.048
285 | 50.5 | -5.048
285.1 | 50.5 | -5.048
285.2 | 50.5 | -5.048
285.3 | 50.5 | -5.048
285.4 | 50.5 | -5.048
285.5 | 50.5 | -5.048
285.6 | 50.5 | -5.048
285.7 | 50.5 | -5.048
285.8 | 50.5 | -5.048
285.9 | 50.5 | -5.048
286 | 50.5 | -5.048
286.1 | 50.5 | -5.048
286.2 | 50.5 | -5.048
286.3 | 50.5 | -5.048
286.4 | 50.5 | -5.048
286.5 | 50.5 | -5.048
286.6 | 50.5 | -5.048
286.7 | 50.5 | -5.048
286.8 | 50.5 | -5.048
286.9 | 50.5 | -5.048
287 | 50.5 | -5.048
287.1 | 50.5 | -5.048
287.2 | 50.5 | -5.048
287.3 | 50.5 | -5.048
287.4 | 50.5 | -5.048
287.5 | 50.5 | -5.048
287.6 | 50.5 | -5.048
287.7 | 50.5 | -5.048
287.8 | 50.5 | -5.048
287.9 | 50.5 | -5.048
288 | 50.5 | -5.048
288.1 | 50.5 | -5.048
288.2 | 50.5 | -5.048
288.3 | 50.5 | -5.048
288.4 | 50.5 | -5.048
288.5 | 50.5 | -5.048
288.6 | 50.5 | -5.048
288.7 | 50.5 | -5.048
288.8 | 50.5 | -5.048
288.9 | 50.5 | -5.048
289 | 50.5 | -5.048
289.1 | 50.5 | -5.048
289.2 | 50.5 | -5.048
289.3 | 50.5 | -5.048
289.4 | 50.5 | -5.048
289.5 | 50.5 | -5.048
289.6 | 50.5 | -5.048
289.7 | 50.5 | -5.048
289.8 | 50.5 | -5.048
289.9 | 50.5 | -5.048
290 | 50.5 | -5.048
290.1 | 50.5 | -5.048
290.2 | 50.5 | -5.048
290.3 | 50.5 | -5.048
290.4 | 50.5 | -5.048
290.5 | 50.5 | -5.048
290.6 | 50.5 | -5.048
290.7 | 50.5 | -5.048
290.8 | 50.5 | -5.048
290.9 | 50.5 | -5.048
291 | 50.5 | -5.048
291.1 | 50.5 | -5.048
291.2 | 50.5 | -5.048
291.3 | 50.5 | -5.048
291.4 | 50.5 | -5.048
291.5 | 50.5 | -5.048
291.6 | 50.5 | -5.048
291.7 | 50.5 | -5.048
291.8 | 50.5 | -5.048
291.9 | 50.5 | -5.048
292 | 50.5 | -5.048
292.1 | 50.5 | -5.048
292.2 | 50.5 | -5.048
292.3 | 50.5 | -5.048
292.4 | 50.5 | -5.048
292.5 | 50.5 | -5.048
292.6 | 50.5 | -5.048
292.7 | 50.5 | -5.048
292.8 | 50.5 | -5.048
292.9 | 50.5 | -5.048
293 | 50.5 | -5.048
293.1 | 50.5 | -5.048
293.2 | 50.5 | -5.048
293.3 | 50.5 | -5.048
293.4 | 50.5 | -5.048
293.5 | 50.5 | -5.048
293.6 | 50.5 | -5.048
293.7 | 50.5 | -5.048
293.8 | 50.5 | -5.048
293.9 | 50.5 | -5.048
294 | 50.5 | -5.048
294.1 | 50.5 | -5.048
294.2 | 50.5 | -5.048
294.3 | 50.5 | -5.048
294.4 | 50.5 | -5.048
294.5 | 50.5 | -5.048
294.6 | 50.5 | -5.048
294.7 | 50.5 | -5.048
294.8 | 50.5 | -5.048
294.9 | 50.5 | -5.048
295 | 50.5 | -5.048
295.1 | 50.5 | -5.048
295.2 | 50.5 | -5.048
295.3 | 50.5 | -5.048
295.4 | 50.5 | -5.048
295.5 | 50.5 | -5.048
295.6 | 50.5 | -5.048
295.7 | 50.5 | -5.048
295.8 | 50.5 | -5.048
295.9 | 50.5 | -5.048
296 | 50.5 | -5.048
296.1 | 50.5 | -5.048
296.2 | 50.5 | -5.048
296.3 | 50.5 | -5.048
296.4 | 50.5 | -5.048
296.5 | 50.5 | -5.048
296.6 | 50.5 | -5.048
296.7 | 50.5 | -5.048
296.8 | 50.5 | -5.048
296.9 | 50.5 | -5.048
297 | 50.5 | -5.048
297.1 | 50.5 | -5.048
297.2 | 50.5 | -5.048
297.3 | 50.5 | -5.048
297.4 | 50.5 | -5.048
297.5 | 50.5 | -5.048
297.6 | 50.5 | -5.048
297.7 | 50.5 | -5.048
297.8 | 50.5 | -5.048
297.9 | 50.5 | -5.048
298 | 50.5 | -5.048
298.1 | 50.5 | -5.048
298.2 | 50.5 | -5.048
298.3 | 50.5 | -5.048
298.4 | 50.5 | -5.048
298.5 | 50.5 | -5.048
298.6 | 50.5 | -5.048
298.7 | 50.5 | -5.048
298.8 | 50.5 | -5.048
298.9 | 50.5 | -5.048
299 | 50.5 | -5.048
299.1 | 50.5 | -5.048
299.2 | 50.5 | -5.048
299.3 | 50.5 | -5.048
299.4 | 50.5 | -5.048
299.5 | 50.5 | -5.048
299.6 | 50.5 | -5.048
299.7 | 50.5 | -5.048
299.8 | 50.5 | -5.048
299.9 | 50.5 | -5.048
300 | 50.5 | -5.048
300.1 | 50.5 | -5.048
300.2 | 50.5 | -5.048
300.3 | 50.5 | -5.048
300.4 | 50.5 | -5.048
300.5 | 50.5 | -5.048
300.6 | 50.5 | -5.048
300.7 | 50.5 | -5.048
300.8 | 50.5 | -5.048
300.9 | 50.5 | -5.048
301 | 50.5 | -5.048
301.1 | 50.5 | -5.048
301.2 | 50.5 | -5.048
301.3 | 50.5 | -5.048
301.4 | 50.5 | -5.048
301.5 | 50.5 | -5.048
301.6 | 50.5 | -5.048
301.7 | 50.5 | -5.048
301.8 | 50.5 | -5.048
301.9 | 50.5 | -5.048
302 | 50.5 | -5.048
302.1 | 50.5 | -5.048
302.2 | 50.5 | -5.048
302.3 | 50.5 | -5.048
302.4 | 50.5 | -5.048
302.5 | 50.5 | -5.048
302.6 | 50.5 | -5.048
302.7 | 50.5 | -5.048
302.8 | 50.5 | -5.048
302.9 | 50.5 | -5.048
303 | 50.5 | -5.048
303.1 | 50.5 | -5.048
303.2 | 50.5 | -5.048
303.3 | 50.5 | -5.048
303.4 | 50.5 | -5.048
303.5 | 50.5 | -5.048
303.6 | 50.5 | -5.048
303.7 | 50.5 | -5.048
303.8 | 50.5 | -5.048
303.9 | 50.5 | -5.048
304 | 50.5 | -5.048
304.1 | 50.5 | -5.048
304.2 | 50.5 | -5.048
304.3 | 50.5 | -5.048
304.4 | 50.5 | -5.048
304.5 | 50.5 | -5.048
304.6 | 50.5 | -5.048
304.7 | 50.5 | -5.048
304.8 | 50.5 | -5.048
304.9 | 50.5 | -5.048
305 | 50.5 | -5.048
305.1 | 50.5 | -5.048
305.2 | 50.5 | -5.048
305.3 | 50.5 | -5.048
305.4 | 50.5 | -5.048
305.5 | 50.5 | -5.048
305.6 | 50.5 | -5.048
305.7 | 50.5 | -5.048
305.8 | 50.5 | -5.048
305.9 | 50.5 | -5.048
306 | 50.5 | -5.048
306.1 | 50.5 | -5.048
306.2 | 50.5 | -5.048
306.3 | 50.5 | -5.048
306.4 | 50.5 | -5.048
306.5 | 50.5 | -5.048
306.6 | 50.5 | -5.048
306.7 | 50.5 | -5.048
306.8 | 50.5 | -5.048
306.9 | 50.5 | -5.048
307 | 50.5 | -5.048
307.1 | 50.5 | -5.048
307.2 | 50.5 | -5.048
307.3 | 50.5 | -5.048
307.4 | 50.5 | -5.048
307.5 | 50.5 | -5.048
307.6 | 50.5 | -5.048
307.7 | 50.5 | -5.048
307.8 | 50.5 | -5.048
307.9 | 50.5 | -5.048
308 | 50.5 | -5.048
308.1 | 50.5 | -5.048
308.2 | 50.5 | -5.048
308.3 | 50.5 | -5.048
308.4 | 50.5 | -5.048
308.5 | 50.5 | -5.048
308.6 | 50.5 | -5.048
308.7 | 50.5 | -5.048
308.8 | 50.5 | -5.048
308.9 | 50.5 | -5.048
309 | 50.5 | -5.048
309.1 | 50.5 | -5.048
309.2 | 50.5 | -5.048
309.3 | 50.5 | -5.048
309.4 | 50.5 | -5.048
309.5 | 50.5 | -5.048
309.6 | 50.5 | -5.048
309.7 | 50.5 | -5.048
309.8 | 50.5 | -5.048
309.9 | 50.5 | -5.048
310 | 50.5 | -5.048
310.1 | 50.5 | -5.048
310.2 | 50.5 | -5.048
310.3 | 50.5 | -5.048
310.4 | 50.5 | -5.048
310.5 | 50.5 | -5.048
310.6 | 50.5 | -5.048
310.7 | 50.5 | -5.048
310.8 | 50.5 | -5.048
310.9 | 50.5 | -5.048
311 | 50.5 | -5.048
311.1 | 50.5 | -5.048
311.2 | 50.5 | -5.048
311.3 | 50.5 | -5.048
311.4 | 50.5 | -5.048
311.5 | 50.5 | -5.048
311.6 | 50.5 | -5.048
311.7 | 50.5 | -5.048
311.8 | 50.5 | -5.048
311.9 | 50.5 | -5.048
312 | 50.5 | -5.048
312.1 | 50.5 | -5.048
312.2 | 50.5 | -5.048
312.3 | 50.5 | -5.048
312.4 | 50.5 | -5.048
312.5 | 50.5 | -5.048
312.6 | 50.5 | -5.048
312.7 | 50.5 | -5.048
312.8 | 50.5 | -5.048
312.9 | 50.5 | -5.048
313 | 50.5 | -5.048
313.1 | 50.5 | -5.048
313.2 | 50.5 | -5.048
313.3 | 50.5 | -5.048
313.4 | 50.5 | -5.048
313.5 | 50.5 | -5.048
313.6 | 50.5 | -5.048
313.7 | 50.5 | -5.048
313.8 | 50.5 | -5.048
313.9 | 50.5 | -5.048
314 | 50.5 | -5.048
314.1 | 50.5 | -5.048
314.2 | 50.5 | -5.048
314.3 | 50.5 | -5.048
314.4 | 50.5 | -5.048
314.5 | 50.5 | -5.048
314.6 | 50.5 | -5.048
314.7 | 50.5 | -5.048
314.8 | 50.5 | -5.048
314.9 | 50.5 | -5.048
315 | 50.5 | -5.048
315.1 | 50.5 | -5.048
315.2 | 50.5 | -5.048
315.3 | 50.5 | -5.048
315.4 | 50.5 | -5.048
315.5 | 50.5 | -5.048
315.6 | 50.5 | -5.048
315.7 | 50.5 | -5.048
315.8 | 50.5 | -5.048
315.9 | 50.5 | -5.048
316 | 50.5 | -5.048
316.1 | 50.5 | -5.048
316.2 | 50.5 | -5.048
316.3 | 50.5 | -5.048
316.4 | 50.5 | -5.048
316.5 | 50.5 | -5.048
316.6 | 50.5 | -5.048
316.7 | 50.5 | -5.048
316.8 | 50.5 | -5.048
316.9 | 50.5 | -5.048
317 | 50.5 | -5.048
317.1 | 50.5 | -5.048
317.2 | 50.5 | -5.048
317.3 | 50.5 | -5.048
317.4 | 50.5 | -5.048
317.5 | 50.5 | -5.048
317.6 | 50.5 | -5.048
317.7 | 50.5 | -5.048
317.8 | 50.5 | -5.048
317.9 | 50.5 | -5.048
318 | 50.5 | -5.048
318.1 | 50.5 | -5.048
318.2 | 50.5 | -5.048
318.3 | 50.5 | -5.048
318.4 | 50.5 | -5.048
318.5 | 50.5 | -5.048
318.6 | 50.5 | -5.048
318.7 | 50.5 | -5.048
318.8 | 50.5 | -5.048
318.9 | 50.5 | -5.048
319 | 50.5 | -5.047
319.1 | 50.5 | -5.047
319.2 | 50.5 | -5.047
319.3 | 50.5 | -5.047
319.4 | 50.5 | -5.047
319.5 | 50.5 | -5.047
319.6 | 50.5 | -5.047
319.7 | 50.5 | -5.047
319.8 | 50.5 | -5.047
319.9 | 50.5 | -5.047
320 | 50.5 | -5.047
320.1 | 50.5 | -5.047
320.2 | 50.5 | -5.047
320.3 | 50.5 | -5.047
320.4 | 50.5 | -5.047
320.5 | 50.5 | -5.047
320.6 | 50.5 | -5.047
320.7 | 50.5 | -5.047
320.8 | 50.5 | -5.047
320.9 | 50.5 | -5.047
321 | 50.5 | -5.047
321.1 | 50.5 | -5.047
321.2 | 50.5 | -5.047
321.3 | 50.5 | -5.047
321.4 | 50.5 | -5.048
321.5 | 50.5 | -5.048
321.6 | 50.5 | -5.048
321.7 | 50.5 | -5.048
321.8 | 50.5 | -5.048
321.9 | 50.5 | -5.048
322 | 50.5 | -5.048
322.1 | 50.5 | -5.048
322.2 | 50.5 | -5.048
322.3 | 50.5 | -5.048
322.4 | 50.5 | -5.048
322.5 | 50.5 | -5.048
322.6 | 50.5 | -5.048
322.7 | 50.5 | -5.048
322.8 | 50.5 | -5.048
322.9 | 50.5 | -5.048
323 | 50.5 | -5.048
323.1 | 50.5 | -5.048
323.2 | 50.5 | -5.048
323.3 | 50.5 | -5.048
323.4 | 50.5 | -5.048
323.5 | 50.5 | -5.048
323.6 | 50.5 | -5.048
323.7 | 50.5 | -5.048
323.8 | 50.5 | -5.048
323.9 | 50.5 | -5.048
324 | 50.5 | -5.048
324.1 | 50.5 | -5.048
324.2 | 50.5 | -5.048
324.3 | 50.5 | -5.048
324.4 | 50.5 | -5.048
324.5 | 50.5 | -5.048
324.6 | 50.5 | -5.048
324.7 | 50.5 | -5.048
324.8 | 50.5 | -5.048
324.9 | 50.5 | -5.048
325 | 50.5 | -5.047
325.1 | 50.5 | -5.047
325.2 | 50.5 | -5.047
325.3 | 50.5 | -5.047
325.4 | 50.5 | -5.047
325.5 | 50.5 | -5.047
325.6 | 50.5 | -5.047
325.7 | 50.5 | -5.047
325.8 | 50.5 | -5.047
325.9 | 50.5 | -5.047
326 | 50.5 | -5.047
326.1 | 50.5 | -5.047
326.2 | 50.5 | -5.047
326.3 | 50.5 | -5.047
326.4 | 50.5 | -5.047
326.5 | 50.5 | -5.047
326.6 | 50.5 | -5.047
326.7 | 50.5 | -5.047
326.8 | 50.5 | -5.047
326.9 | 50.5 | -5.047
327 | 50.5 | -5.047
327.1 | 50.5 | -5.047
327.2 | 50.5 | -5.048
327.3 | 50.5 | -5.048
327.4 | 50.5 | -5.048
327.5 | 50.5 | -5.048
327.6 | 50.5 | -5.048
327.7 | 50.5 | -5.048
327.8 | 50.5 | -5.048
327.9 | 50.5 | -5.048
328 | 50.5 | -5.048
328.1 | 50.5 | -5.048
328.2 | 50.5 | -5.048
328.3 | 50.5 | -5.048
328.4 | 50.5 | -5.048
328.5 | 50.5 | -5.048
328.6 | 50.5 | -5.048
328.7 | 50.5 | -5.048
328.8 | 50.5 | -5.048
328.9 | 50.5 | -5.048
329 | 50.5 | -5.048
329.1 | 50.5 | -5.048
329.2 | 50.5 | -5.048
329.3 | 50.5 | -5.048
329.4 | 50.5 | -5.048
329.5 | 50.5 | -5.048
329.6 | 50.5 | -5.048
329.7 | 50.5 | -5.048
329.8 | 50.5 | -5.048
329.9 | 50.5 | -5.048
330 | 50.5 | -5.048
330.1 | 50.5 | -5.048
330.2 | 50.5 | -5.048
330.3 | 50.5 | -5.048
330.4 | 50.5 | -5.048
330.5 | 50.5 | -5.048
330.6 | 50.5 | -5.048
330.7 | 50.5 | -5.048
330.8 | 50.5 | -5.048
330.9 | 50.5 | -5.048
331 | 50.5 | -5.048
331.1 | 50.5 | -5.048
331.2 | 50.5 | -5.048
331.3 | 50.5 | -5.048
331.4 | 50.5 | -5.048
331.5 | 50.5 | -5.048
331.6 | 50.5 | -5.048
331.7 | 50.5 | -5.048
331.8 | 50.5 | -5.048
331.9 | 50.5 | -5.048
332 | 50.5 | -5.048
332.1 | 50.5 | -5.048
332.2 | 50.5 | -5.048
332.3 | 50.5 | -5.048
332.4 | 50.5 | -5.048
332.5 | 50.5 | -5.048
332.6 | 50.5 | -5.048
332.7 | 50.5 | -5.048
332.8 | 50.5 | -5.048
332.9 | 50.5 | -5.048
333 | 50.5 | -5.048
333.1 | 50.5 | -5.048
333.2 | 50.5 | -5.048
333.3 | 50.5 | -5.048
333.4 | 50.5 | -5.048
333.5 | 50.5 | -5.048
333.6 | 50.5 | -5.048
333.7 | 50.5 | -5.048
333.8 | 50.5 | -5.048
333.9 | 50.5 | -5.048
334 | 50.5 | -5.048
334.1 | 50.5 | -5.048
334.2 | 50.5 | -5.048
334.3 | 50.5 | -5.048
334.4 | 50.5 | -5.048
334.5 | 50.5 | -5.048
334.6 | 50.5 | -5.048
334.7 | 50.5 | -5.048
334.8 | 50.5 | -5.048
334.9 | 50.5 | -5.048
335 | 50.5 | -5.048
335.1 | 50.5 | -5.048
335.2 | 50.5 | -5.048
335.3 | 50.5 | -5.048
335.4 | 50.5 | -5.048
335.5 | 50.5 | -5.048
335.6 | 50.5 | -5.048
335.7 | 50.5 | -5.048
335.8 | 50.5 | -5.048
335.9 | 50.5 | -5.048
336 | 50.5 | -5.048
336.1 | 50.5 | -5.048
336.2 | 50.5 | -5.048
336.3 | 50.5 | -5.048
336.4 | 50.5 | -5.048
336.5 | 50.5 | -5.048
336.6 | 50.5 | -5.048
336.7 | 50.5 | -5.048
336.8 | 50.5 | -5.048
336.9 | 50.5 | -5.048
337 | 50.5 | -5.048
337.1 | 50.5 | -5.048
337.2 | 50.5 | -5.048
337.3 | 50.5 | -5.048
337.4 | 50.5 | -5.048
337.5 | 50.5 | -5.048
337.6 | 50.5 | -5.048
337.7 | 50.5 | -5.048
337.8 | 50.5 | -5.048
337.9 | 50.5 | -5.048
338 | 50.5 | -5.048
338.1 | 50.5 | -5.048
338.2 | 50.5 | -5.048
338.3 | 50.5 | -5.048
338.4 | 50.5 | -5.048
338.5 | 50.5 | -5.048
338.6 | 50.5 | -5.048
338.7 | 50.5 | -5.048
338.8 | 50.5 | -5.048
338.9 | 50.5 | -5.048
339 | 50.5 | -5.048
339.1 | 50.5 | -5.048
339.2 | 50.5 | -5.048
339.3 | 50.5 | -5.048
339.4 | 50.5 | -5.048
339.5 | 50.5 | -5.048
339.6 | 50.5 | -5.048
339.7 | 50.5 | -5.048
339.8 | 50.5 | -5.048
339.9 | 50.5 | -5.048
340 | 50.5 | -5.048
340.1 | 50.5 | -5.048
340.2 | 50.5 | -5.048
340.3 | 50.5 | -5.048
340.4 | 50.5 | -5.048
340.5 | 50.5 | -5.048
340.6 | 50.5 | -5.048
340.7 | 50.5 | -5.048
340.8 | 50.5 | -5.048
340.9 | 50.5 | -5.048
341 | 50.5 | -5.048
341.1 | 50.5 | -5.048
341.2 | 50.5 | -5.048
341.3 | 50.5 | -5.048
341.4 | 50.5 | -5.048
341.5 | 50.5 | -5.048
341.6 | 50.5 | -5.048
341.7 | 50.5 | -5.048
341.8 | 50.5 | -5.048
341.9 | 50.5 | -5.048
342 | 50.5 | -5.048
342.1 | 50.5 | -5.048
342.2 | 50.5 | -5.048
342.3 | 50.5 | -5.048
342.4 | 50.5 | -5.048
342.5 | 50.5 | -5.048
342.6 | 50.5 | -5.048
342.7 | 50.5 | -5.048
342.8 | 50.5 | -5.048
342.9 | 50.5 | -5.048
343 | 50.5 | -5.048
343.1 | 50.5 | -5.048
343.2 | 50.5 | -5.048
343.3 | 50.5 | -5.048
343.4 | 50.5 | -5.048
343.5 | 50.5 | -5.048
343.6 | 50.5 | -5.048
343.7 | 50.5 | -5.048
343.8 | 50.5 | -5.048
343.9 | 50.5 | -5.048
344 | 50.5 | -5.048
344.1 | 50.5 | -5.048
344.2 | 50.5 | -5.048
344.3 | 50.5 | -5.048
344.4 | 50.5 | -5.048
344.5 | 50.5 | -5.048
344.6 | 50.5 | -5.048
344.7 | 50.5 | -5.048
344.8 | 50.5 | -5.048
344.9 | 50.5 | -5.048
345 | 50.5 | -5.048
345.1 | 50.5 | -5.048
345.2 | 50.5 | -5.048
345.3 | 50.5 | -5.048
345.4 | 50.5 | -5.048
345.5 | 50.5 | -5.048
345.6 | 50.5 | -5.048
345.7 | 50.5 | -5.048
345.8 | 50.5 | -5.048
345.9 | 50.5 | -5.048
346 | 50.5 | -5.048
346.1 | 50.5 | -5.048
346.2 | 50.5 | -5.048
346.3 | 50.5 | -5.048
346.4 | 50.5 | -5.048
346.5 | 50.5 | -5.048
346.6 | 50.5 | -5.048
346.7 | 50.5 | -5.048
346.8 | 50.5 | -5.048
346.9 | 50.5 | -5.048
347 | 50.5 | -5.048
347.1 | 50.5 | -5.048
347.2 | 50.5 | -5.048
347.3 | 50.5 | -5.048
347.4 | 50.5 | -5.048
347.5 | 50.5 | -5.048
347.6 | 50.5 | -5.048
347.7 | 50.5 | -5.048
347.8 | 50.5 | -5.048
347.9 | 50.5 | -5.048
348 | 50.5 | -5.048
348.1 | 50.5 | -5.048
348.2 | 50.5 | -5.048
348.3 | 50.5 | -5.048
348.4 | 50.5 | -5.048
348.5 | 50.5 | -5.048
348.6 | 50.5 | -5.048
348.7 | 50.5 | -5.048
348.8 | 50.5 | -5.048
348.9 | 50.5 | -5.048
349 | 50.5 | -5.048
349.1 | 50.5 | -5.048
349.2 | 50.5 | -5.048
349.3 | 50.5 | -5.048
349.4 | 50.5 | -5.048
349.5 | 50.5 | -5.048
349.6 | 50.5 | -5.048
349.7 | 50.5 | -5.048
349.8 | 50.5 | -5.048
349.9 | 50.5 | -5.048
350 | 50.5 | -5.048
350.1 | 50.5 | -5.048
350.2 | 50.5 | -5.048
350.3 | 50.5 | -5.048
350.4 | 50.5 | -5.048
350.5 | 50.5 | -5.048
350.6 | 50.5 | -5.048
350.7 | 50.5 | -5.048
350.8 | 50.5 | -5.048
350.9 | 50.5 | -5.048
351 | 50.5 | -5.048
351.1 | 50.5 | -5.048
351.2 | 50.5 | -5.048
351.3 | 50.5 | -5.048
351.4 | 50.5 | -5.048
351.5 | 50.5 | -5.048
351.6 | 50.5 | -5.048
351.7 | 50.5 | -5.048
351.8 | 50.5 | -5.048
351.9 | 50.5 | -5.048
352 | 50.5 | -5.048
352.1 | 50.5 | -5.047
352.2 | 50.5 | -5.047
352.3 | 50.5 | -5.047
352.4 | 50.5 | -5.047
352.5 | 50.5 | -5.047
352.6 | 50.5 | -5.047
352.7 | 50.5 | -5.047
352.8 | 50.5 | -5.047
352.9 | 50.5 | -5.047
353 | 50.5 | -5.047
353.1 | 50.5 | -5.047
353.2 | 50.5 | -5.047
353.3 | 50.5 | -5.047
353.4 | 50.5 | -5.047
353.5 | 50.5 | -5.047
353.6 | 50.5 | -5.047
353.7 | 50.5 | -5.047
353.8 | 50.5 | -5.047
353.9 | 50.5 | -5.047
354 | 50.5 | -5.047
354.1 | 50.5 | -5.047
354.2 | 50.5 | -5.047
354.3 | 50.5 | -5.048
354.4 | 50.5 | -5.048
354.5 | 50.5 | -5.048
354.6 | 50.5 | -5.048
354.7 | 50.5 | -5.048
354.8 | 50.5 | -5.048
354.9 | 50.5 | -5.048
355 | 50.5 | -5.048
355.1 | 50.5 | -5.048
355.2 | 50.5 | -5.048
355.3 | 50.5 | -5.048
355.4 | 50.5 | -5.048
355.5 | 50.5 | -5.047
355.6 | 50.5 | -5.047
355.7 | 50.5 | -5.047
355.8 | 50.5 | -5.047
355.9 | 50.5 | -5.047
356 | 50.5 | -5.047
356.1 | 50.5 | -5.047
356.2 | 50.5 | -5.047
356.3 | 50.5 | -5.047
356.4 | 50.5 | -5.047
356.5 | 50.5 | -5.047
356.6 | 50.5 | -5.048
356.7 | 50.5 | -5.048
356.8 | 50.5 | -5.048
356.9 | 50.5 | -5.048
357 | 50.5 | -5.048
357.1 | 50.5 | -5.048
357.2 | 50.5 | -5.048
357.3 | 50.5 | -5.048
357.4 | 50.5 | -5.048
357.5 | 50.5 | -5.048
357.6 | 50.5 | -5.048
357.7 | 50.5 | -5.048
357.8 | 50.5 | -5.048
357.9 | 50.5 | -5.048
358 | 50.5 | -5.048
358.1 | 50.5 | -5.048
358.2 | 50.5 | -5.048
358.3 | 50.5 | -5.048
358.4 | 50.5 | -5.048
358.5 | 50.5 | -5.048
358.6 | 50.5 | -5.048
358.7 | 50.5 | -5.048
358.8 | 50.5 | -5.048
358.9 | 50.5 | -5.048
359 | 50.5 | -5.048
359.1 | 50.5 | -5.048
359.2 | 50.5 | -5.048
359.3 | 50.5 | -5.048
359.4 | 50.5 | -5.048
359.5 | 50.5 | -5.048
359.6 | 50.5 | -5.048
359.7 | 50.5 | -5.048
359.8 | 50.5 | -5.048
359.9 | 50.5 | -5.048
360 | 50.5 | -5.048
360.1 | 50.5 | -5.048
360.2 | 50.5 | -5.048
360.3 | 50.5 | -5.048
360.4 | 50.5 | -5.048
360.5 | 50.5 | -5.048
360.6 | 50.5 | -5.048
360.7 | 50.5 | -5.048
360.8 | 50.5 | -5.048
360.9 | 50.5 | -5.048
361 | 50.5 | -5.048
361.1 | 50.5 | -5.048
361.2 | 50.5 | -5.048
361.3 | 50.5 | -5.048
361.4 | 50.5 | -5.047
361.5 | 50.5 | -5.047
361.6 | 50.5 | -5.047
361.7 | 50.5 | -5.047
361.8 | 50.5 | -5.047
361.9 | 50.5 | -5.047
362 | 50.5 | -5.047
362.1 | 50.5 | -5.047
362.2 | 50.5 | -5.047
362.3 | 50.5 | -5.047
362.4 | 50.5 | -5.047
362.5 | 50.5 | -5.048
362.6 | 50.5 | -5.048
362.7 | 50.5 | -5.048
362.8 | 50.5 | -5.048
362.9 | 50.5 | -5.048
363 | 50.5 | -5.048
363.1 | 50.5 | -5.048
363.2 | 50.5 | -5.048
363.3 | 50.5 | -5.048
363.4 | 50.5 | -5.048
363.5 | 50.5 | -5.048
363.6 | 50.5 | -5.048
363.7 | 50.5 | -5.048
363.8 | 50.5 | -5.048
363.9 | 50.5 | -5.048
364 | 50.5 | -5.048
364.1 | 50.5 | -5.048
364.2 | 50.5 | -5.048
364.3 | 50.5 | -5.048
364.4 | 50.5 | -5.048
364.5 | 50.5 | -5.048
364.6 | 50.5 | -5.048
364.7 | 50.5 | -5.048
364.8 | 50.5 | -5.048
364.9 | 50.5 | -5.048
365 | 50.5 | -5.048
365.1 | 50.5 | -5.048
365.2 | 50.5 | -5.048
365.3 | 50.5 | -5.048
365.4 | 50.5 | -5.048
365.5 | 50.5 | -5.048
365.6 | 50.5 | -5.048
365.7 | 50.5 | -5.048
365.8 | 50.5 | -5.048
365.9 | 50.5 | -5.048
366 | 50.5 | -5.048
366.1 | 50.5 | -5.048
366.2 | 50.5 | -5.048
366.3 | 50.5 | -5.048
366.4 | 50.5 | -5.048
366.5 | 50.5 | -5.048
366.6 | 50.5 | -5.048
366.7 | 50.5 | -5.048
366.8 | 50.5 | -5.048
366.9 | 50.5 | -5.048
367 | 50.5 | -5.048
367.1 | 50.5 | -5.048
367.2 | 50.5 | -5.048
367.3 | 50.5 | -5.048
367.4 | 50.5 | -5.048
367.5 | 50.5 | -5.048
367.6 | 50.5 | -5.048
367.7 | 50.5 | -5.048
367.8 | 50.5 | -5.048
367.9 | 50.5 | -5.048
368 | 50.5 | -5.048
368.1 | 50.5 | -5.048
368.2 | 50.5 | -5.048
368.3 | 50.5 | -5.048
368.4 | 50.5 | -5.048
368.5 | 50.5 | -5.048
368.6 | 50.5 | -5.048
368.7 | 50.5 | -5.048
368.8 | 50.5 | -5.048
368.9 | 50.5 | -5.048
369 | 50.5 | -5.048
369.1 | 50.5 | -5.048
369.2 | 50.5 | -5.048
369.3 | 50.5 | -5.048
369.4 | 50.5 | -5.048
369.5 | 50.5 | -5.048
369.6 | 50.5 | -5.048
369.7 | 50.5 | -5.048
369.8 | 50.5 | -5.048
369.9 | 50.5 | -5.047
370 | 50.5 | -5.047
370.1 | 50.5 | -5.047
370.2 | 50.5 | -5.047
370.3 | 50.5 | -5.047
370.4 | 50.5 | -5.047
370.5 | 50.5 | -5.047
370.6 | 50.5 | -5.047
370.7 | 50.5 | -5.047
370.8 | 50.5 | -5.047
370.9 | 50.5 | -5.047
371 | 50.5 | -5.047
371.1 | 50.5 | -5.048
371.2 | 50.5 | -5.048
371.3 | 50.5 | -5.048
371.4 | 50.5 | -5.048
371.5 | 50.5 | -5.048
371.6 | 50.5 | -5.048
371.7 | 50.5 | -5.048
371.8 | 50.5 | -5.048
371.9 | 50.5 | -5.048
372 | 50.5 | -5.048
372.1 | 50.5 | -5.048
372.2 | 50.5 | -5.048
372.3 | 50.5 | -5.048
372.4 | 50.5 | -5.048
372.5 | 50.5 | -5.047
372.6 | 50.5 | -5.047
372.7 | 50.5 | -5.047
372.8 | 50.5 | -5.047
372.9 | 50.5 | -5.047
373 | 50.5 | -5.047
373.1 | 50.5 | -5.047
373.2 | 50.5 | -5.047
373.3 | 50.5 | -5.047
373.4 | 50.5 | -5.048
373.5 | 50.5 | -5.048
373.6 | 50.5 | -5.048
373.7 | 50.5 | -5.048
373.8 | 50.5 | -5.048
373.9 | 50.5 | -5.048
374 | 50.5 | -5.048
374.1 | 50.5 | -5.048
374.2 | 50.5 | -5.048
374.3 | 50.5 | -5.048
374.4 | 50.5 | -5.048
374.5 | 50.5 | -5.048
374.6 | 50.5 | -5.048
374.7 | 50.5 | -5.048
374.8 | 50.5 | -5.048
374.9 | 50.5 | -5.048
375 | 50.5 | -5.048
375.1 | 50.5 | -5.048
375.2 | 50.5 | -5.048
375.3 | 50.5 | -5.048
375.4 | 50.5 | -5.048
375.5 | 50.5 | -5.048
375.6 | 50.5 | -5.048
375.7 | 50.5 | -5.048
375.8 | 50.5 | -5.048
375.9 | 50.5 | -5.048
376 | 50.5 | -5.048
376.1 | 50.5 | -5.048
376.2 | 50.5 | -5.048
376.3 | 50.5 | -5.048
376.4 | 50.5 | -5.048
376.5 | 50.5 | -5.048
376.6 | 50.5 | -5.048
376.7 | 50.5 | -5.048
376.8 | 50.5 | -5.048
376.9 | 50.5 | -5.048
377 | 50.5 | -5.048
377.1 | 50.5 | -5.048
377.2 | 50.5 | -5.048
377.3 | 50.5 | -5.048
377.4 | 50.5 | -5.048
377.5 | 50.5 | -5.048
377.6 | 50.5 | -5.048
377.7 | 50.5 | -5.048
377.8 | 50.5 | -5.048
377.9 | 50.5 | -5.048
378 | 50.5 | -5.048
378.1 | 50.5 | -5.048
378.2 | 50.5 | -5.048
378.3 | 50.5 | -5.048
378.4 | 50.5 | -5.048
378.5 | 50.5 | -5.048
378.6 | 50.5 | -5.048
378.7 | 50.5 | -5.048
378.8 | 50.5 | -5.048
378.9 | 50.5 | -5.048
379 | 50.5 | -5.048
379.1 | 50.5 | -5.048
379.2 | 50.5 | -5.048
379.3 | 50.5 | -5.048
379.4 | 50.5 | -5.048
379.5 | 50.5 | -5.048
379.6 | 50.5 | -5.048
379.7 | 50.5 | -5.048
379.8 | 50.5 | -5.048
379.9 | 50.5 | -5.048
380 | 50.5 | -5.048
380.1 | 50.5 | -5.048
380.2 | 50.5 | -5.048
380.3 | 50.5 | -5.048
380.4 | 50.5 | -5.048
380.5 | 50.5 | -5.048
380.6 | 50.5 | -5.048
380.7 | 50.5 | -5.048
380.8 | 50.5 | -5.048
380.9 | 50.5 | -5.048
381 | 50.5 | -5.048
381.1 | 50.5 | -5.048
381.2 | 50.5 | -5.048
381.3 | 50.5 | -5.048
381.4 | 50.5 | -5.048
381.5 | 50.5 | -5.048
381.6 | 50.5 | -5.048
381.7 | 50.5 | -5.048
381.8 | 50.5 | -5.048
381.9 | 50.5 | -5.048
382 | 50.5 | -5.048
382.1 | 50.5 | -5.048
382.2 | 50.5 | -5.048
382.3 | 50.5 | -5.048
382.4 | 50.5 | -5.048
382.5 | 50.5 | -5.048
382.6 | 50.5 | -5.048
382.7 | 50.5 | -5.048
382.8 | 50.5 | -5.048
382.9 | 50.5 | -5.048
383 | 50.5 | -5.048
383.1 | 50.5 | -5.048
383.2 | 50.5 | -5.048
383.3 | 50.5 | -5.048
383.4 | 50.5 | -5.048
383.5 | 50.5 | -5.048
383.6 | 50.5 | -5.048
383.7 | 50.5 | -5.048
383.8 | 50.5 | -5.048
383.9 | 50.5 | -5.048
384 | 50.5 | -5.048
384.1 | 50.5 | -5.048
384.2 | 50.5 | -5.048
384.3 | 50.5 | -5.048
384.4 | 50.5 | -5.048
384.5 | 50.5 | -5.048
384.6 | 50.5 | -5.048
384.7 | 50.5 | -5.048
384.8 | 50.5 | -5.048
384.9 | 50.5 | -5.048
385 | 50.5 | -5.048
385.1 | 50.5 | -5.048
385.2 | 50.5 | -5.048
385.3 | 50.5 | -5.048
385.4 | 50.5 | -5.048
385.5 | 50.5 | -5.048
385.6 | 50.5 | -5.048
385.7 | 50.5 | -5.048
385.8 | 50.5 | -5.048
385.9 | 50.5 | -5.048
386 | 50.5 | -5.048
386.1 | 50.5 | -5.048
386.2 | 50.5 | -5.048
386.3 | 50.5 | -5.048
386.4 | 50.5 | -5.048
386.5 | 50.5 | -5.048
386.6 | 50.5 | -5.048
386.7 | 50.5 | -5.048
386.8 | 50.5 | -5.048
386.9 | 50.5 | -5.048
387 | 50.5 | -5.048
387.1 | 50.5 | -5.048
387.2 | 50.5 | -5.048
387.3 | 50.5 | -5.048
387.4 | 50.5 | -5.048
387.5 | 50.5 | -5.048
387.6 | 50.5 | -5.048
387.7 | 50.5 | -5.048
387.8 | 50.5 | -5.048
387.9 | 50.5 | -5.048
388 | 50.5 | -5.048
388.1 | 50.5 | -5.048
388.2 | 50.5 | -5.048
388.3 | 50.5 | -5.048
388.4 | 50.5 | -5.048
388.5 | 50.5 | -5.048
388.6 | 50.5 | -5.048
388.7 | 50.5 | -5.048
388.8 | 50.5 | -5.048
388.9 | 50.5 | -5.048
389 | 50.5 | -5.048
389.1 | 50.5 | -5.048
389.2 | 50.5 | -5.048
389.3 | 50.5 | -5.048
389.4 | 50.5 | -5.048
389.5 | 50.5 | -5.048
389.6 | 50.5 | -5.048
389.7 | 50.5 | -5.048
389.8 | 50.5 | -5.048
389.9 | 50.5 | -5.048
390 | 50.5 | -5.048
390.1 | 50.5 | -5.048
390.2 | 50.5 | -5.048
390.3 | 50.5 | -5.048
390.4 | 50.5 | -5.048
390.5 | 50.5 | -5.048
390.6 | 50.5 | -5.047
390.7 | 50.5 | -5.047
390.8 | 50.5 | -5.047
390.9 | 50.5 | -5.047
391 | 50.5 | -5.047
391.1 | 50.5 | -5.047
391.2 | 50.5 | -5.047
391.3 | 50.5 | -5.047
391.4 | 50.5 | -5.047
391.5 | 50.5 | -5.047
391.6 | 50.5 | -5.047
391.7 | 50.5 | -5.047
391.8 | 50.5 | -5.047
391.9 | 50.5 | -5.047
392 | 50.5 | -5.047
392.1 | 50.5 | -5.047
392.2 | 50.5 | -5.047
392.3 | 50.5 | -5.047
392.4 | 50.5 | -5.047
392.5 | 50.5 | -5.047
392.6 | 50.5 | -5.047
392.7 | 50.5 | -5.047
392.8 | 50.5 | -5.047
392.9 | 50.5 | -5.048
393 | 50.5 | -5.048
393.1 | 50.5 | -5.048
393.2 | 50.5 | -5.048
393.3 | 50.5 | -5.048
393.4 | 50.5 | -5.048
393.5 | 50.5 | -5.048
393.6 | 50.5 | -5.048
393.7 | 50.5 | -5.048
393.8 | 50.5 | -5.048
393.9 | 50.5 | -5.048
394 | 50.5 | -5.048
394.1 | 50.5 | -5.048
394.2 | 50.5 | -5.048
394.3 | 50.5 | -5.048
394.4 | 50.5 | -5.048
394.5 | 50.5 | -5.048
394.6 | 50.5 | -5.048
394.7 | 50.5 | -5.048
394.8 | 50.5 | -5.048
394.9 | 50.5 | -5.048
395 | 50.5 | -5.048
395.1 | 50.5 | -5.048
395.2 | 50.5 | -5.048
395.3 | 50.5 | -5.048
395.4 | 50.5 | -5.048
395.5 | 50.5 | -5.048
395.6 | 50.5 | -5.048
395.7 | 50.5 | -5.048
395.8 | 50.5 | -5.048
395.9 | 50.5 | -5.048
396 | 50.5 | -5.048
396.1 | 50.5 | -5.048
396.2 | 50.5 | -5.048
396.3 | 50.5 | -5.048
396.4 | 50.5 | -5.048
396.5 | 50.5 | -5.048
396.6 | 50.5 | -5.048
396.7 | 50.5 | -5.048
396.8 | 50.5 | -5.048
396.9 | 50.5 | -5.048
397 | 50.5 | -5.048
397.1 | 50.5 | -5.048
397.2 | 50.5 | -5.048
397.3 | 50.5 | -5.048
397.4 | 50.5 | -5.048
397.5 | 50.5 | -5.048
397.6 | 50.5 | -5.048
397.7 | 50.5 | -5.048
397.8 | 50.5 | -5.048
397.9 | 50.5 | -5.048
398 | 50.5 | -5.048
398.1 | 50.5 | -5.048
398.2 | 50.5 | -5.048
398.3 | 50.5 | -5.048
398.4 | 50.5 | -5.048
398.5 | 50.5 | -5.048
398.6 | 50.5 | -5.048
398.7 | 50.5 | -5.048
398.8 | 50.5 | -5.048
398.9 | 50.5 | -5.048
399 | 50.5 | -5.048
399.1 | 50.5 | -5.048
399.2 | 50.5 | -5.048
399.3 | 50.5 | -5.048
399.4 | 50.5 | -5.048
399.5 | 50.5 | -5.048
399.6 | 50.5 | -5.048
399.7 | 50.5 | -5.048
399.8 | 50.5 | -5.048
399.9 | 50.5 | -5.048
400 | 50.5 | -5.048
400.1 | 50.5 | -5.048
400.2 | 50.5 | -5.048
400.3 | 50.5 | -5.048
400.4 | 50.5 | -5.048
400.5 | 50.5 | -5.048
400.6 | 50.5 | -5.048
400.7 | 50.5 | -5.048
400.8 | 50.5 | -5.048
400.9 | 50.5 | -5.048
401 | 50.5 | -5.048
401.1 | 50.5 | -5.048
401.2 | 50.5 | -5.048
401.3 | 50.5 | -5.048
401.4 | 50.5 | -5.048
401.5 | 50.5 | -5.048
401.6 | 50.5 | -5.048
401.7 | 50.5 | -5.048
401.8 | 50.5 | -5.048
401.9 | 50.5 | -5.048
402 | 50.5 | -5.048
402.1 | 50.5 | -5.048
402.2 | 50.5 | -5.048
402.3 | 50.5 | -5.048
402.4 | 50.5 | -5.048
402.5 | 50.5 | -5.048
402.6 | 50.5 | -5.048
402.7 | 50.5 | -5.048
402.8 | 50.5 | -5.048
402.9 | 50.5 | -5.048
403 | 50.5 | -5.048
403.1 | 50.5 | -5.048
403.2 | 50.5 | -5.048
403.3 | 50.5 | -5.048
403.4 | 50.5 | -5.048
403.5 | 50.5 | -5.048
403.6 | 50.5 | -5.048
403.7 | 50.5 | -5.048
403.8 | 50.5 | -5.048
403.9 | 50.5 | -5.048
404 | 50.5 | -5.048
404.1 | 50.5 | -5.048
404.2 | 50.5 | -5.048
404.3 | 50.5 | -5.048
404.4 | 50.5 | -5.048
404.5 | 50.5 | -5.048
404.6 | 50.5 | -5.048
404.7 | 50.5 | -5.048
404.8 | 50.5 | -5.048
404.9 | 50.5 | -5.048
405 | 50.5 | -5.049
405.1 | 50.5 | -5.049
405.2 | 50.5 | -5.049
405.3 | 50.5 | -5.049
405.4 | 50.5 | -5.049
405.5 | 50.5 | -5.049
405.6 | 50.5 | -5.049
405.7 | 50.5 | -5.049
405.8 | 50.5 | -5.049
405.9 | 50.5 | -5.049
406 | 50.5 | -5.049
406.1 | 50.5 | -5.048
406.2 | 50.5 | -5.048
406.3 | 50.5 | -5.048
406.4 | 50.5 | -5.048
406.5 | 50.5 | -5.048
406.6 | 50.5 | -5.048
406.7 | 50.5 | -5.048
406.8 | 50.5 | -5.048
406.9 | 50.5 | -5.048
407 | 50.5 | -5.048
407.1 | 50.5 | -5.048
407.2 | 50.5 | -5.048
407.3 | 50.5 | -5.048
407.4 | 50.5 | -5.048
407.5 | 50.5 | -5.048
407.6 | 50.5 | -5.048
407.7 | 50.5 | -5.048
407.8 | 50.5 | -5.048
407.9 | 50.5 | -5.048
408 | 50.5 | -5.048
408.1 | 50.5 | -5.047
408.2 | 50.5 | -5.047
408.3 | 50.5 | -5.047
408.4 | 50.5 | -5.047
408.5 | 50.5 | -5.047
408.6 | 50.5 | -5.047
408.7 | 50.5 | -5.047
408.8 | 50.5 | -5.047
408.9 | 50.5 | -5.047
409 | 50.5 | -5.047
409.1 | 50.5 | -5.047
409.2 | 50.5 | -5.048
409.3 | 50.5 | -5.048
409.4 | 50.5 | -5.048
409.5 | 50.5 | -5.048
409.6 | 50.5 | -5.048
409.7 | 50.5 | -5.048
409.8 | 50.5 | -5.048
409.9 | 50.5 | -5.048
410 | 50.5 | -5.048
410.1 | 50.5 | -5.048
410.2 | 50.5 | -5.048
410.3 | 50.5 | -5.048
410.4 | 50.5 | -5.049
410.5 | 50.5 | -5.049
410.6 | 50.5 | -5.049
410.7 | 50.5 | -5.049
410.8 | 50.5 | -5.049
410.9 | 50.5 | -5.049
411 | 50.5 | -5.049
411.1 | 50.5 | -5.049
411.2 | 50.5 | -5.049
411.3 | 50.5 | -5.049
411.4 | 50.5 | -5.049
411.5 | 50.5 | -5.049
411.6 | 50.5 | -5.048
411.7 | 50.5 | -5.048
411.8 | 50.5 | -5.048
411.9 | 50.5 | -5.048
412 | 50.5 | -5.048
412.1 | 50.5 | -5.048
412.2 | 50.5 | -5.048
412.3 | 50.5 | -5.048
412.4 | 50.5 | -5.048
412.5 | 50.5 | -5.048
412.6 | 50.5 | -5.048
412.7 | 50.5 | -5.048
412.8 | 50.5 | -5.048
412.9 | 50.5 | -5.047
413 | 50.5 | -5.047
413.1 | 50.5 | -5.047
413.2 | 50.5 | -5.047
413.3 | 50.5 | -5.047
413.4 | 50.5 | -5.047
413.5 | 50.5 | -5.047
413.6 | 50.5 | -5.048
413.7 | 50.5 | -5.048
413.8 | 50.5 | -5.048
413.9 | 50.5 | -5.048
414 | 50.5 | -5.048
414.1 | 50.5 | -5.048
414.2 | 50.5 | -5.048
414.3 | 50.5 | -5.048
414.4 | 50.5 | -5.048
414.5 | 50.5 | -5.048
414.6 | 50.5 | -5.048
414.7 | 50.5 | -5.048
414.8 | 50.5 | -5.048
414.9 | 50.5 | -5.048
415 | 50.5 | -5.048
415.1 | 50.5 | -5.048
415.2 | 50.5 | -5.048
415.3 | 50.5 | -5.048
415.4 | 50.5 | -5.048
415.5 | 50.5 | -5.048
415.6 | 50.5 | -5.048
415.7 | 50.5 | -5.048
415.8 | 50.5 | -5.048
415.9 | 50.5 | -5.048
416 | 50.5 | -5.049
416.1 | 50.5 | -5.049
416.2 | 50.5 | -5.049
416.3 | 50.5 | -5.049
416.4 | 50.5 | -5.049
416.5 | 50.5 | -5.048
416.6 | 50.5 | -5.048
416.7 | 50.5 | -5.048
416.8 | 50.5 | -5.048
416.9 | 50.5 | -5.048
417 | 50.5 | -5.048
417.1 | 50.5 | -5.048
417.2 | 50.5 | -5.048
417.3 | 50.5 | -5.048
417.4 | 50.5 | -5.048
417.5 | 50.5 | -5.048
417.6 | 50.5 | -5.048
417.7 | 50.5 | -5.047
417.8 | 50.5 | -5.047
417.9 | 50.5 | -5.047
418 | 50.5 | -5.047
418.1 | 50.5 | -5.047
418.2 | 50.5 | -5.047
418.3 | 50.5 | -5.047
418.4 | 50.5 | -5.047
418.5 | 50.5 | -5.047
418.6 | 50.5 | -5.047
418.7 | 50.5 | -5.047
418.8 | 50.5 | -5.047
418.9 | 50.5 | -5.047
419 | 50.5 | -5.047
419.1 | 50.5 | -5.047
419.2 | 50.5 | -5.047
419.3 | 50.5 | -5.047
419.4 | 50.5 | -5.047
419.5 | 50.5 | -5.047
419.6 | 50.5 | -5.048
419.7 | 50.5 | -5.048
419.8 | 50.5 | -5.048
419.9 | 50.5 | -5.048
420 | 50.5 | -5.048
420.1 | 50.5 | -5.048
420.2 | 50.5 | -5.048
420.3 | 50.5 | -5.048
420.4 | 50.5 | -5.048
420.5 | 50.5 | -5.048
420.6 | 50.5 | -5.048
420.7 | 50.5 | -5.048
420.8 | 50.5 | -5.048
420.9 | 50.5 | -5.048
421 | 50.5 | -5.048
421.1 | 50.5 | -5.048
421.2 | 50.5 | -5.048
421.3 | 50.5 | -5.048
421.4 | 50.5 | -5.048
421.5 | 50.5 | -5.048
421.6 | 50.5 | -5.048
421.7 | 50.5 | -5.048
421.8 | 50.5 | -5.048
421.9 | 50.5 | -5.048
422 | 50.5 | -5.048
422.1 | 50.5 | -5.048
422.2 | 50.5 | -5.049
422.3 | 50.5 | -5.049
422.4 | 50.5 | -5.049
422.5 | 50.5 | -5.049
422.6 | 50.5 | -5.049
422.7 | 50.5 | -5.049
422.8 | 50.5 | -5.049
422.9 | 50.5 | -5.049
423 | 50.5 | -5.049
423.1 | 50.5 | -5.049
423.2 | 50.5 | -5.049
423.3 | 50.5 | -5.049
423.4 | 50.5 | -5.047
423.5 | 50.5 | -5.047
423.6 | 50.5 | -5.047
423.7 | 50.5 | -5.047
423.8 | 50.5 | -5.047
423.9 | 50.5 | -5.047
424 | 50.5 | -5.047
424.1 | 50.5 | -5.047
424.2 | 50.5 | -5.047
424.3 | 50.5 | -5.047
424.4 | 50.5 | -5.047
424.5 | 50.5 | -5.047
424.6 | 50.5 | -5.047
424.7 | 50.5 | -5.047
424.8 | 50.5 | -5.047
424.9 | 50.5 | -5.047
425 | 50.5 | -5.047
425.1 | 50.5 | -5.047
425.2 | 50.5 | -5.047
425.3 | 50.5 | -5.047
425.4 | 50.5 | -5.047
425.5 | 50.5 | -5.048
425.6 | 50.5 | -5.048
425.7 | 50.5 | -5.048
425.8 | 50.5 | -5.048
425.9 | 50.5 | -5.047
426 | 50.5 | -5.047
426.1 | 50.5 | -5.047
426.2 | 50.5 | -5.047
426.3 | 50.5 | -5.047
426.4 | 50.5 | -5.047
426.5 | 50.5 | -5.047
426.6 | 50.5 | -5.047
426.7 | 50.5 | -5.048
426.8 | 50.5 | -5.048
426.9 | 50.5 | -5.047
427 | 50.5 | -5.047
427.1 | 50.5 | -5.047
427.2 | 50.5 | -5.047
427.3 | 50.5 | -5.047
427.4 | 50.5 | -5.047
427.5 | 50.5 | -5.047
427.6 | 50.5 | -5.047
427.7 | 50.5 | -5.047
427.8 | 50.5 | -5.047
427.9 | 50.5 | -5.047
428 | 50.5 | -5.048
428.1 | 50.5 | -5.048
428.2 | 50.5 | -5.048
428.3 | 50.5 | -5.048
428.4 | 50.5 | -5.048
428.5 | 50.5 | -5.048
428.6 | 50.5 | -5.048
428.7 | 50.5 | -5.048
428.8 | 50.5 | -5.048
428.9 | 50.5 | -5.048
429 | 50.5 | -5.048
429.1 | 50.5 | -5.048
429.2 | 50.5 | -5.048
429.3 | 50.5 | -5.048
429.4 | 50.5 | -5.048
429.5 | 50.5 | -5.048
429.6 | 50.5 | -5.048
429.7 | 50.5 | -5.048
429.8 | 50.5 | -5.048
429.9 | 50.5 | -5.048
430 | 50.5 | -5.048
430.1 | 50.5 | -5.048
430.2 | 50.5 | -5.048
430.3 | 50.5 | -5.048
430.4 | 50.5 | -5.048
430.5 | 50.5 | -5.048
430.6 | 50.5 | -5.048
430.7 | 50.5 | -5.048
430.8 | 50.5 | -5.048
430.9 | 50.5 | -5.048
431 | 50.5 | -5.048
431.1 | 50.5 | -5.048
431.2 | 50.5 | -5.048
431.3 | 50.5 | -5.048
431.4 | 50.5 | -5.048
431.5 | 50.5 | -5.048
431.6 | 50.5 | -5.048
431.7 | 50.5 | -5.048
431.8 | 50.5 | -5.048
431.9 | 50.5 | -5.048
432 | 50.5 | -5.048
432.1 | 50.5 | -5.048
432.2 | 50.5 | -5.048
432.3 | 50.5 | -5.048
432.4 | 50.5 | -5.048
432.5 | 50.5 | -5.048
432.6 | 50.5 | -5.048
432.7 | 50.5 | -5.048
432.8 | 50.5 | -5.047
432.9 | 50.5 | -5.047
433 | 50.5 | -5.047
433.1 | 50.5 | -5.047
433.2 | 50.5 | -5.047
433.3 | 50.5 | -5.047
433.4 | 50.5 | -5.047
433.5 | 50.5 | -5.047
433.6 | 50.5 | -5.047
433.7 | 50.5 | -5.047
433.8 | 50.5 | -5.047
433.9 | 50.5 | -5.047
434 | 50.5 | -5.048
434.1 | 50.5 | -5.048
434.2 | 50.5 | -5.048
434.3 | 50.5 | -5.048
434.4 | 50.5 | -5.048
434.5 | 50.5 | -5.048
434.6 | 50.5 | -5.048
434.7 | 50.5 | -5.048
434.8 | 50.5 | -5.048
434.9 | 50.5 | -5.048
435 | 50.5 | -5.048
435.1 | 50.5 | -5.048
435.2 | 50.5 | -5.048
435.3 | 50.5 | -5.048
435.4 | 50.5 | -5.048
435.5 | 50.5 | -5.048
435.6 | 50.5 | -5.048
435.7 | 50.5 | -5.048
435.8 | 50.5 | -5.048
435.9 | 50.5 | -5.048
436 | 50.5 | -5.048
436.1 | 50.5 | -5.048
436.2 | 50.5 | -5.048
436.3 | 50.5 | -5.048
436.4 | 50.5 | -5.048
436.5 | 50.5 | -5.048
436.6 | 50.5 | -5.048
436.7 | 50.5 | -5.048
436.8 | 50.5 | -5.048
436.9 | 50.5 | -5.048
437 | 50.5 | -5.048
437.1 | 50.5 | -5.048
437.2 | 50.5 | -5.048
437.3 | 50.5 | -5.047
437.4 | 50.5 | -5.047
437.5 | 50.5 | -5.048
437.6 | 50.5 | -5.048
437.7 | 50.5 | -5.048
437.8 | 50.5 | -5.048
437.9 | 50.5 | -5.048
438 | 50.5 | -5.048
438.1 | 50.5 | -5.048
438.2 | 50.5 | -5.048
438.3 | 50.5 | -5.048
438.4 | 50.5 | -5.048
438.5 | 50.5 | -5.048
438.6 | 50.5 | -5.048
438.7 | 50.5 | -5.048
438.8 | 50.5 | -5.048
438.9 | 50.5 | -5.048
439 | 50.5 | -5.048
439.1 | 50.5 | -5.048
439.2 | 50.5 | -5.048
439.3 | 50.5 | -5.048
439.4 | 50.5 | -5.048
439.5 | 50.5 | -5.048
439.6 | 50.5 | -5.048
439.7 | 50.5 | -5.048
439.8 | 50.5 | -5.048
439.9 | 50.5 | -5.048
440 | 50.5 | -5.048
440.1 | 50.5 | -5.048
440.2 | 50.5 | -5.048
440.3 | 50.5 | -5.048
440.4 | 50.5 | -5.048
440.5 | 50.5 | -5.048
440.6 | 50.5 | -5.048
440.7 | 50.5 | -5.048
440.8 | 50.5 | -5.048
440.9 | 50.5 | -5.048
441 | 50.5 | -5.048
441.1 | 50.5 | -5.048
441.2 | 50.5 | -5.048
441.3 | 50.5 | -5.048
441.4 | 50.5 | -5.048
441.5 | 50.5 | -5.048
441.6 | 50.5 | -5.048
441.7 | 50.5 | -5.048
441.8 | 50.5 | -5.048
441.9 | 50.5 | -5.048
442 | 50.5 | -5.048
442.1 | 50.5 | -5.048
442.2 | 50.5 | -5.048
442.3 | 50.5 | -5.048
442.4 | 50.5 | -5.048
442.5 | 50.5 | -5.048
442.6 | 50.5 | -5.048
442.7 | 50.5 | -5.048
442.8 | 50.5 | -5.048
442.9 | 50.5 | -5.048
443 | 50.5 | -5.048
443.1 | 50.5 | -5.048
443.2 | 50.5 | -5.048
443.3 | 50.5 | -5.048
443.4 | 50.5 | -5.048
443.5 | 50.5 | -5.048
443.6 | 50.5 | -5.048
443.7 | 50.5 | -5.048
443.8 | 50.5 | -5.048
443.9 | 50.5 | -5.048
444 | 50.5 | -5.048
444.1 | 50.5 | -5.048
444.2 | 50.5 | -5.048
444.3 | 50.5 | -5.048
444.4 | 50.5 | -5.048
444.5 | 50.5 | -5.048
444.6 | 50.5 | -5.048
444.7 | 50.5 | -5.048
444.8 | 50.5 | -5.048
444.9 | 50.5 | -5.048
445 | 50.5 | -5.048
445.1 | 50.5 | -5.048
445.2 | 50.5 | -5.048
445.3 | 50.5 | -5.048
445.4 | 50.5 | -5.048
445.5 | 50.5 | -5.048
445.6 | 50.5 | -5.048
445.7 | 50.5 | -5.048
445.8 | 50.5 | -5.048
445.9 | 50.5 | -5.048
446 | 50.5 | -5.048
446.1 | 50.5 | -5.048
446.2 | 50.5 | -5.048
446.3 | 50.5 | -5.048
446.4 | 50.5 | -5.048
446.5 | 50.5 | -5.048
446.6 | 50.5 | -5.048
446.7 | 50.5 | -5.048
446.8 | 50.5 | -5.048
446.9 | 50.5 | -5.048
447 | 50.5 | -5.048
447.1 | 50.5 | -5.048
447.2 | 50.5 | -5.048
447.3 | 50.5 | -5.048
447.4 | 50.5 | -5.048
447.5 | 50.5 | -5.048
447.6 | 50.5 | -5.048
447.7 | 50.5 | -5.048
447.8 | 50.5 | -5.048
447.9 | 50.5 | -5.048
448 | 50.5 | -5.048
448.1 | 50.5 | -5.048
448.2 | 50.5 | -5.048
448.3 | 50.5 | -5.048
448.4 | 50.5 | -5.048
448.5 | 50.5 | -5.048
448.6 | 50.5 | -5.048
448.7 | 50.5 | -5.048
448.8 | 50.5 | -5.048
448.9 | 50.5 | -5.048
449 | 50.5 | -5.048
449.1 | 50.5 | -5.048
449.2 | 50.5 | -5.048
449.3 | 50.5 | -5.048
449.4 | 50.5 | -5.048
449.5 | 50.5 | -5.048
449.6 | 50.5 | -5.048
449.7 | 50.5 | -5.048
449.8 | 50.5 | -5.048
449.9 | 50.5 | -5.048
450 | 50.5 | -5.048
450.1 | 50.5 | -5.048
450.2 | 50.5 | -5.048
450.3 | 50.5 | -5.048
450.4 | 50.5 | -5.048
450.5 | 50.5 | -5.048
450.6 | 50.5 | -5.048
450.7 | 50.5 | -5.048
450.8 | 50.5 | -5.048
450.9 | 50.5 | -5.048
451 | 50.5 | -5.048
451.1 | 50.5 | -5.048
451.2 | 50.5 | -5.048
451.3 | 50.5 | -5.048
451.4 | 50.5 | -5.048
451.5 | 50.5 | -5.048
451.6 | 50.5 | -5.048
451.7 | 50.5 | -5.048
451.8 | 50.5 | -5.048
451.9 | 50.5 | -5.048
452 | 50.5 | -5.048
452.1 | 50.5 | -5.048
452.2 | 50.5 | -5.048
452.3 | 50.5 | -5.048
452.4 | 50.5 | -5.048
452.5 | 50.5 | -5.048
452.6 | 50.5 | -5.048
452.7 | 50.5 | -5.048
452.8 | 50.5 | -5.048
452.9 | 50.5 | -5.048
453 | 50.5 | -5.048
453.1 | 50.5 | -5.048
453.2 | 50.5 | -5.048
453.3 | 50.5 | -5.048
453.4 | 50.5 | -5.048
453.5 | 50.5 | -5.048
453.6 | 50.5 | -5.048
453.7 | 50.5 | -5.048
453.8 | 50.5 | -5.048
453.9 | 50.5 | -5.048
454 | 50.5 | -5.048
454.1 | 50.5 | -5.048
454.2 | 50.5 | -5.048
454.3 | 50.5 | -5.048
454.4 | 50.5 | -5.048
454.5 | 50.5 | -5.048
454.6 | 50.5 | -5.048
454.7 | 50.5 | -5.048
454.8 | 50.5 | -5.048
454.9 | 50.5 | -5.048
455 | 50.5 | -5.048
455.1 | 50.5 | -5.048
455.2 | 50.5 | -5.048
455.3 | 50.5 | -5.048
455.4 | 50.5 | -5.048
455.5 | 50.5 | -5.048
455.6 | 50.5 | -5.048
455.7 | 50.5 | -5.048
455.8 | 50.5 | -5.048
455.9 | 50.5 | -5.048
456 | 50.5 | -5.048
456.1 | 50.5 | -5.048
456.2 | 50.5 | -5.047
456.3 | 50.5 | -5.047
456.4 | 50.5 | -5.047
456.5 | 50.5 | -5.047
456.6 | 50.5 | -5.047
456.7 | 50.5 | -5.047
456.8 | 50.5 | -5.047
456.9 | 50.5 | -5.047
457 | 50.5 | -5.047
457.1 | 50.5 | -5.047
457.2 | 50.5 | -5.048
457.3 | 50.5 | -5.048
457.4 | 50.5 | -5.048
457.5 | 50.5 | -5.048
457.6 | 50.5 | -5.048
457.7 | 50.5 | -5.048
457.8 | 50.5 | -5.048
457.9 | 50.5 | -5.048
458 | 50.5 | -5.048
458.1 | 50.5 | -5.048
458.2 | 50.5 | -5.048
458.3 | 50.5 | -5.048
458.4 | 50.5 | -5.048
458.5 | 50.5 | -5.047
458.6 | 50.5 | -5.047
458.7 | 50.5 | -5.047
458.8 | 50.5 | -5.047
458.9 | 50.5 | -5.047
459 | 50.5 | -5.047
459.1 | 50.5 | -5.047
459.2 | 50.5 | -5.047
459.3 | 50.5 | -5.047
459.4 | 50.5 | -5.047
459.5 | 50.5 | -5.047
459.6 | 50.5 | -5.047
459.7 | 50.5 | -5.047
459.8 | 50.5 | -5.047
459.9 | 50.5 | -5.047
460 | 50.5 | -5.047
460.1 | 50.5 | -5.047
460.2 | 50.5 | -5.047
460.3 | 50.5 | -5.047
460.4 | 50.5 | -5.047
460.5 | 50.5 | -5.047
460.6 | 50.5 | -5.047
460.7 | 50.5 | -5.047
460.8 | 50.5 | -5.047
460.9 | 50.5 | -5.047
461 | 50.5 | -5.047
461.1 | 50.5 | -5.047
461.2 | 50.5 | -5.047
461.3 | 50.5 | -5.047
461.4 | 50.5 | -5.047
461.5 | 50.5 | -5.047
461.6 | 50.5 | -5.047
461.7 | 50.5 | -5.047
461.8 | 50.5 | -5.047
461.9 | 50.5 | -5.048
462 | 50.5 | -5.048
462.1 | 50.5 | -5.048
462.2 | 50.5 | -5.048
462.3 | 50.5 | -5.048
462.4 | 50.5 | -5.048
462.5 | 50.5 | -5.048
462.6 | 50.5 | -5.048
462.7 | 50.5 | -5.048
462.8 | 50.5 | -5.049
462.9 | 50.5 | -5.049
463 | 50.5 | -5.049
463.1 | 50.5 | -5.049
463.2 | 50.5 | -5.049
463.3 | 50.5 | -5.049
463.4 | 50.5 | -5.049
463.5 | 50.5 | -5.049
463.6 | 50.5 | -5.049
463.7 | 50.5 | -5.049
463.8 | 50.5 | -5.049
463.9 | 50.5 | -5.049
464 | 50.5 | -5.049
464.1 | 50.5 | -5.049
464.2 | 50.5 | -5.049
464.3 | 50.5 | -5.048
464.4 | 50.5 | -5.048
464.5 | 50.5 | -5.048
464.6 | 50.5 | -5.048
464.7 | 50.5 | -5.048
464.8 | 50.5 | -5.048
464.9 | 50.5 | -5.048
465 | 50.5 | -5.048
465.1 | 50.5 | -5.048
465.2 | 50.5 | -5.047
465.3 | 50.5 | -5.047
465.4 | 50.5 | -5.047
465.5 | 50.5 | -5.047
465.6 | 50.5 | -5.047
465.7 | 50.5 | -5.047
465.8 | 50.5 | -5.047
465.9 | 50.5 | -5.047
466 | 50.5 | -5.047
466.1 | 50.5 | -5.047
466.2 | 50.5 | -5.047
466.3 | 50.5 | -5.047
466.4 | 50.5 | -5.047
466.5 | 50.5 | -5.047
466.6 | 50.5 | -5.046
466.7 | 50.5 | -5.047
466.8 | 50.5 | -5.047
466.9 | 50.5 | -5.047
467 | 50.5 | -5.047
467.1 | 50.5 | -5.047
467.2 | 50.5 | -5.047
467.3 | 50.5 | -5.047
467.4 | 50.5 | -5.047
467.5 | 50.5 | -5.047
467.6 | 50.5 | -5.047
467.7 | 50.5 | -5.048
467.8 | 50.5 | -5.049
467.9 | 50.5 | -5.049
468 | 50.5 | -5.049
468.1 | 50.5 | -5.049
468.2 | 50.5 | -5.049
468.3 | 50.5 | -5.049
468.4 | 50.5 | -5.049
468.5 | 50.5 | -5.049
468.6 | 50.5 | -5.049
468.7 | 50.5 | -5.049
468.8 | 50.5 | -5.049
468.9 | 50.5 | -5.049
469 | 50.5 | -5.048
469.1 | 50.5 | -5.048
469.2 | 50.5 | -5.048
469.3 | 50.5 | -5.048
469.4 | 50.5 | -5.048
469.5 | 50.5 | -5.048
469.6 | 50.5 | -5.048
469.7 | 50.5 | -5.048
469.8 | 50.5 | -5.048
469.9 | 50.5 | -5.049
470 | 50.5 | -5.049
470.1 | 50.5 | -5.049
470.2 | 50.5 | -5.049
470.3 | 50.5 | -5.049
470.4 | 50.5 | -5.049
470.5 | 50.5 | -5.049
470.6 | 50.5 | -5.049
470.7 | 50.5 | -5.049
470.8 | 50.5 | -5.049
470.9 | 50.5 | -5.049
471 | 50.5 | -5.049
471.1 | 50.5 | -5.049
471.2 | 50.5 | -5.049
471.3 | 50.5 | -5.049
471.4 | 50.5 | -5.048
471.5 | 50.5 | -5.048
471.6 | 50.5 | -5.048
471.7 | 50.5 | -5.048
471.8 | 50.5 | -5.048
471.9 | 50.5 | -5.048
472 | 50.5 | -5.048
472.1 | 50.5 | -5.048
472.2 | 50.5 | -5.047
472.3 | 50.5 | -5.047
472.4 | 50.5 | -5.047
472.5 | 50.5 | -5.047
472.6 | 50.5 | -5.047
472.7 | 50.5 | -5.047
472.8 | 50.5 | -5.047
472.9 | 50.5 | -5.047
473 | 50.5 | -5.047
473.1 | 50.5 | -5.047
473.2 | 50.5 | -5.047
473.3 | 50.5 | -5.047
473.4 | 50.5 | -5.047
473.5 | 50.5 | -5.047
473.6 | 50.5 | -5.047
473.7 | 50.5 | -5.048
473.8 | 50.5 | -5.048
473.9 | 50.5 | -5.048
474 | 50.5 | -5.048
474.1 | 50.5 | -5.048
474.2 | 50.5 | -5.048
474.3 | 50.5 | -5.048
474.4 | 50.5 | -5.048
474.5 | 50.5 | -5.048
474.6 | 50.5 | -5.048
474.7 | 50.5 | -5.048
474.8 | 50.5 | -5.048
474.9 | 50.5 | -5.048
475 | 50.5 | -5.048
475.1 | 50.5 | -5.048
475.2 | 50.5 | -5.048
475.3 | 50.5 | -5.048
475.4 | 50.5 | -5.048
475.5 | 50.5 | -5.048
475.6 | 50.5 | -5.048
475.7 | 50.5 | -5.048
475.8 | 50.5 | -5.048
475.9 | 50.5 | -5.048
476 | 50.5 | -5.048
476.1 | 50.5 | -5.048
476.2 | 50.5 | -5.048
476.3 | 50.5 | -5.048
476.4 | 50.5 | -5.048
476.5 | 50.5 | -5.048
476.6 | 50.5 | -5.048
476.7 | 50.5 | -5.048
476.8 | 50.5 | -5.048
476.9 | 50.5 | -5.048
477 | 50.5 | -5.049
477.1 | 50.5 | -5.049
477.2 | 50.5 | -5.049
477.3 | 50.5 | -5.048
477.4 | 50.5 | -5.048
477.5 | 50.5 | -5.048
477.6 | 50.5 | -5.048
477.7 | 50.5 | -5.048
477.8 | 50.5 | -5.048
477.9 | 50.5 | -5.048
478 | 50.5 | -5.048
478.1 | 50.5 | -5.048
478.2 | 50.5 | -5.049
478.3 | 50.5 | -5.049
478.4 | 50.5 | -5.049
478.5 | 50.5 | -5.048
478.6 | 50.5 | -5.048
478.7 | 50.5 | -5.048
478.8 | 50.5 | -5.048
478.9 | 50.5 | -5.048
479 | 50.5 | -5.048
479.1 | 50.5 | -5.048
479.2 | 50.5 | -5.048
479.3 | 50.5 | -5.048
479.4 | 50.5 | -5.048
479.5 | 50.5 | -5.048
479.6 | 50.5 | -5.048
479.7 | 50.5 | -5.048
479.8 | 50.5 | -5.048
479.9 | 50.5 | -5.048
480 | 50.5 | -5.048
480.1 | 50.5 | -5.048
480.2 | 50.5 | -5.048
480.3 | 50.5 | -5.048
480.4 | 50.5 | -5.048
480.5 | 50.5 | -5.048
480.6 | 50.5 | -5.047
480.7 | 50.5 | -5.047
480.8 | 50.5 | -5.047
480.9 | 50.5 | -5.047
481 | 50.5 | -5.047
481.1 | 50.5 | -5.047
481.2 | 50.5 | -5.047
481.3 | 50.5 | -5.047
481.4 | 50.5 | -5.047
481.5 | 50.5 | -5.047
481.6 | 50.5 | -5.047
481.7 | 50.5 | -5.047
481.8 | 50.5 | -5.047
481.9 | 50.5 | -5.047
482 | 50.5 | -5.047
482.1 | 50.5 | -5.047
482.2 | 50.5 | -5.047
482.3 | 50.5 | -5.047
482.4 | 50.5 | -5.047
482.5 | 50.5 | -5.047
482.6 | 50.5 | -5.047
482.7 | 50.5 | -5.048
482.8 | 50.5 | -5.048
482.9 | 50.5 | -5.047
483 | 50.5 | -5.048
483.1 | 50.5 | -5.048
483.2 | 50.5 | -5.048
483.3 | 50.5 | -5.048
483.4 | 50.5 | -5.048
483.5 | 50.5 | -5.048
483.6 | 50.5 | -5.048
483.7 | 50.5 | -5.048
483.8 | 50.5 | -5.048
483.9 | 50.5 | -5.048
484 | 50.5 | -5.048
484.1 | 50.5 | -5.048
484.2 | 50.5 | -5.048
484.3 | 50.5 | -5.047
484.4 | 50.5 | -5.047
484.5 | 50.5 | -5.047
484.6 | 50.5 | -5.047
484.7 | 50.5 | -5.047
484.8 | 50.5 | -5.047
484.9 | 50.5 | -5.047
485 | 50.5 | -5.047
485.1 | 50.5 | -5.047
485.2 | 50.5 | -5.047
485.3 | 50.5 | -5.047
485.4 | 50.5 | -5.047
485.5 | 50.5 | -5.047
485.6 | 50.5 | -5.047
485.7 | 50.5 | -5.047
485.8 | 50.5 | -5.047
485.9 | 50.5 | -5.047
486 | 50.5 | -5.047
486.1 | 50.5 | -5.047
486.2 | 50.5 | -5.047
486.3 | 50.5 | -5.048
486.4 | 50.5 | -5.048
486.5 | 50.5 | -5.048
486.6 | 50.5 | -5.048
486.7 | 50.5 | -5.048
486.8 | 50.5 | -5.048
486.9 | 50.5 | -5.048
487 | 50.5 | -5.048
487.1 | 50.5 | -5.048
487.2 | 50.5 | -5.048
487.3 | 50.5 | -5.048
487.4 | 50.5 | -5.048
487.5 | 50.5 | -5.048
487.6 | 50.5 | -5.048
487.7 | 50.5 | -5.048
487.8 | 50.5 | -5.049
487.9 | 50.5 | -5.049
488 | 50.5 | -5.049
488.1 | 50.5 | -5.049
488.2 | 50.5 | -5.049
488.3 | 50.5 | -5.049
488.4 | 50.5 | -5.049
488.5 | 50.5 | -5.049
488.6 | 50.5 | -5.048
488.7 | 50.5 | -5.048
488.8 | 50.5 | -5.048
488.9 | 50.5 | -5.048
489 | 50.5 | -5.048
489.1 | 50.5 | -5.048
489.2 | 50.5 | -5.048
489.3 | 50.5 | -5.048
489.4 | 50.5 | -5.048
489.5 | 50.5 | -5.048
489.6 | 50.5 | -5.048
489.7 | 50.5 | -5.048
489.8 | 50.5 | -5.047
489.9 | 50.5 | -5.047
490 | 50.5 | -5.047
490.1 | 50.5 | -5.047
490.2 | 50.5 | -5.046
490.3 | 50.5 | -5.046
490.4 | 50.5 | -5.046
490.5 | 50.5 | -5.046
490.6 | 50.5 | -5.046
490.7 | 50.5 | -5.046
490.8 | 50.5 | -5.046
490.9 | 50.5 | -5.046
491 | 50.5 | -5.046
491.1 | 50.5 | -5.046
491.2 | 50.5 | -5.046
491.3 | 50.5 | -5.046
491.4 | 50.5 | -5.046
491.5 | 50.5 | -5.046
491.6 | 50.5 | -5.046
491.7 | 50.5 | -5.046
491.8 | 50.5 | -5.046
491.9 | 50.5 | -5.046
492 | 50.5 | -5.047
492.1 | 50.5 | -5.047
492.2 | 50.5 | -5.047
492.3 | 50.5 | -5.047
492.4 | 50.5 | -5.048
492.5 | 50.5 | -5.048
492.6 | 50.5 | -5.048
492.7 | 50.5 | -5.048
492.8 | 50.5 | -5.048
492.9 | 50.5 | -5.048
493 | 50.5 | -5.048
493.1 | 50.5 | -5.048
493.2 | 50.5 | -5.048
493.3 | 50.5 | -5.048
493.4 | 50.5 | -5.048
493.5 | 50.5 | -5.048
493.6 | 50.5 | -5.048
493.7 | 50.5 | -5.048
493.8 | 50.5 | -5.048
493.9 | 50.5 | -5.048
494 | 50.5 | -5.048
494.1 | 50.5 | -5.048
494.2 | 50.5 | -5.048
494.3 | 50.5 | -5.048
494.4 | 50.5 | -5.048
494.5 | 50.5 | -5.048
494.6 | 50.5 | -5.048
494.7 | 50.5 | -5.048
494.8 | 50.5 | -5.048
494.9 | 50.5 | -5.048
495 | 50.5 | -5.048
495.1 | 50.5 | -5.048
495.2 | 50.5 | -5.048
495.3 | 50.5 | -5.048
495.4 | 50.5 | -5.048
495.5 | 50.5 | -5.048
495.6 | 50.5 | -5.048
495.7 | 50.5 | -5.048
495.8 | 50.5 | -5.048
495.9 | 50.5 | -5.048
496 | 50.5 | -5.048
496.1 | 50.5 | -5.047
496.2 | 50.5 | -5.047
496.3 | 50.5 | -5.047
496.4 | 50.5 | -5.047
496.5 | 50.5 | -5.047
496.6 | 50.5 | -5.047
496.7 | 50.5 | -5.047
496.8 | 50.5 | -5.047
496.9 | 50.5 | -5.047
497 | 50.5 | -5.047
497.1 | 50.5 | -5.047
497.2 | 50.5 | -5.047
497.3 | 50.5 | -5.047
497.4 | 50.5 | -5.047
497.5 | 50.5 | -5.047
497.6 | 50.5 | -5.047
497.7 | 50.5 | -5.047
497.8 | 50.5 | -5.047
497.9 | 50.5 | -5.048
498 | 50.5 | -5.048
498.1 | 50.5 | -5.048
498.2 | 50.5 | -5.048
498.3 | 50.5 | -5.048
498.4 | 50.5 | -5.048
498.5 | 50.5 | -5.048
498.6 | 50.5 | -5.048
498.7 | 50.5 | -5.048
498.8 | 50.5 | -5.048
498.9 | 50.5 | -5.048
499 | 50.5 | -5.048
499.1 | 50.5 | -5.048
499.2 | 50.5 | -5.048
499.3 | 50.5 | -5.048
499.4 | 50.5 | -5.048
499.5 | 50.5 | -5.048
499.6 | 50.5 | -5.048
499.7 | 50.5 | -5.049
499.8 | 50.5 | -5.049
499.9 | 50.5 | -5.049
500 | 50.5 | -5.049
500.1 | 50.5 | -5.049
500.2 | 50.5 | -5.049
500.3 | 50.5 | -5.048
500.4 | 50.5 | -5.048
500.5 | 50.5 | -5.048
500.6 | 50.5 | -5.048
500.7 | 50.5 | -5.048
500.8 | 50.5 | -5.048
500.9 | 50.5 | -5.048
501 | 50.5 | -5.048
501.1 | 50.5 | -5.048
501.2 | 50.5 | -5.048
501.3 | 50.5 | -5.048
501.4 | 50.5 | -5.048
501.5 | 50.5 | -5.048
501.6 | 50.5 | -5.048
501.7 | 50.5 | -5.047
501.8 | 50.5 | -5.047
501.9 | 50.5 | -5.047
502 | 50.5 | -5.047
502.1 | 50.5 | -5.047
502.2 | 50.5 | -5.047
502.3 | 50.5 | -5.047
502.4 | 50.5 | -5.047
502.5 | 50.5 | -5.047
502.6 | 50.5 | -5.047
502.7 | 50.5 | -5.047
502.8 | 50.5 | -5.047
502.9 | 50.5 | -5.047
503 | 50.5 | -5.047
503.1 | 50.5 | -5.047
503.2 | 50.5 | -5.047
503.3 | 50.5 | -5.047
503.4 | 50.5 | -5.047
503.5 | 50.5 | -5.047
503.6 | 50.5 | -5.047
503.7 | 50.5 | -5.047
503.8 | 50.5 | -5.047
503.9 | 50.5 | -5.047
504 | 50.5 | -5.048
504.1 | 50.5 | -5.048
504.2 | 50.5 | -5.048
504.3 | 50.5 | -5.048
504.4 | 50.5 | -5.048
504.5 | 50.5 | -5.048
504.6 | 50.5 | -5.048
504.7 | 50.5 | -5.048
504.8 | 50.5 | -5.048
504.9 | 50.5 | -5.048
505 | 50.5 | -5.048
505.1 | 50.5 | -5.048
505.2 | 50.5 | -5.048
505.3 | 50.5 | -5.048
505.4 | 50.5 | -5.049
505.5 | 50.5 | -5.049
505.6 | 50.5 | -5.049
505.7 | 50.5 | -5.049
505.8 | 50.5 | -5.049
505.9 | 50.5 | -5.049
506 | 50.5 | -5.049
506.1 | 50.5 | -5.049
506.2 | 50.5 | -5.049
506.3 | 50.5 | -5.049
506.4 | 50.5 | -5.049
506.5 | 50.5 | -5.049
506.6 | 50.5 | -5.049
506.7 | 50.5 | -5.049
506.8 | 50.5 | -5.049
506.9 | 50.5 | -5.049
507 | 50.5 | -5.049
507.1 | 50.5 | -5.049
507.2 | 50.5 | -5.049
507.3 | 50.5 | -5.049
507.4 | 50.5 | -5.048
507.5 | 50.5 | -5.048
507.6 | 50.5 | -5.048
507.7 | 50.5 | -5.047
507.8 | 50.5 | -5.047
507.9 | 50.5 | -5.047
508 | 50.5 | -5.047
508.1 | 50.5 | -5.047
508.2 | 50.5 | -5.047
508.3 | 50.5 | -5.047
508.4 | 50.5 | -5.047
508.5 | 50.5 | -5.047
508.6 | 50.5 | -5.047
508.7 | 50.5 | -5.047
508.8 | 50.5 | -5.047
508.9 | 50.5 | -5.047
509 | 50.5 | -5.047
509.1 | 50.5 | -5.047
509.2 | 50.5 | -5.047
509.3 | 50.5 | -5.047
509.4 | 50.5 | -5.047
509.5 | 50.5 | -5.047
509.6 | 50.5 | -5.047
509.7 | 50.5 | -5.047
509.8 | 50.5 | -5.047
509.9 | 50.5 | -5.047
510 | 50.5 | -5.047
510.1 | 50.5 | -5.047
510.2 | 50.5 | -5.047
510.3 | 50.5 | -5.047
510.4 | 50.5 | -5.047
510.5 | 50.5 | -5.047
510.6 | 50.5 | -5.047
510.7 | 50.5 | -5.048
510.8 | 50.5 | -5.048
510.9 | 50.5 | -5.048
511 | 50.5 | -5.048
511.1 | 50.5 | -5.048
511.2 | 50.5 | -5.048
511.3 | 50.5 | -5.049
511.4 | 50.5 | -5.049
511.5 | 50.5 | -5.049
511.6 | 50.5 | -5.049
511.7 | 50.5 | -5.049
511.8 | 50.5 | -5.049
511.9 | 50.5 | -5.049
512 | 50.5 | -5.049
512.1 | 50.5 | -5.049
512.2 | 50.5 | -5.049
512.3 | 50.5 | -5.048
512.4 | 50.5 | -5.048
512.5 | 50.5 | -5.048
512.6 | 50.5 | -5.048
512.7 | 50.5 | -5.048
512.8 | 50.5 | -5.048
512.9 | 50.5 | -5.048
513 | 50.5 | -5.048
513.1 | 50.5 | -5.048
513.2 | 50.5 | -5.048
513.3 | 50.5 | -5.048
513.4 | 50.5 | -5.048
513.5 | 50.5 | -5.048
513.6 | 50.5 | -5.048
513.7 | 50.5 | -5.048
513.8 | 50.5 | -5.048
513.9 | 50.5 | -5.048
514 | 50.5 | -5.048
514.1 | 50.5 | -5.048
514.2 | 50.5 | -5.048
514.3 | 50.5 | -5.048
514.4 | 50.5 | -5.048
514.5 | 50.5 | -5.048
514.6 | 50.5 | -5.048
514.7 | 50.5 | -5.048
514.8 | 50.5 | -5.048
514.9 | 50.5 | -5.048
515 | 50.5 | -5.048
515.1 | 50.5 | -5.048
515.2 | 50.5 | -5.048
515.3 | 50.5 | -5.048
515.4 | 50.5 | -5.048
515.5 | 50.5 | -5.048
515.6 | 50.5 | -5.048
515.7 | 50.5 | -5.048
515.8 | 50.5 | -5.048
515.9 | 50.5 | -5.048
516 | 50.5 | -5.048
516.1 | 50.5 | -5.048
516.2 | 50.5 | -5.048
516.3 | 50.5 | -5.048
516.4 | 50.5 | -5.048
516.5 | 50.5 | -5.048
516.6 | 50.5 | -5.047
516.7 | 50.5 | -5.047
516.8 | 50.5 | -5.047
516.9 | 50.5 | -5.047
517 | 50.5 | -5.047
517.1 | 50.5 | -5.047
517.2 | 50.5 | -5.047
517.3 | 50.5 | -5.047
517.4 | 50.5 | -5.047
517.5 | 50.5 | -5.047
517.6 | 50.5 | -5.048
517.7 | 50.5 | -5.048
517.8 | 50.5 | -5.048
517.9 | 50.5 | -5.048
518 | 50.5 | -5.048
518.1 | 50.5 | -5.048
518.2 | 50.5 | -5.048
518.3 | 50.5 | -5.048
518.4 | 50.5 | -5.048
518.5 | 50.5 | -5.048
518.6 | 50.5 | -5.048
518.7 | 50.5 | -5.048
518.8 | 50.5 | -5.048
518.9 | 50.5 | -5.048
519 | 50.5 | -5.048
519.1 | 50.5 | -5.048
519.2 | 50.5 | -5.048
519.3 | 50.5 | -5.048
519.4 | 50.5 | -5.048
519.5 | 50.5 | -5.048
519.6 | 50.5 | -5.048
519.7 | 50.5 | -5.048
519.8 | 50.5 | -5.048
519.9 | 50.5 | -5.048
520 | 50.5 | -5.048
520.1 | 50.5 | -5.048
520.2 | 50.5 | -5.048
520.3 | 50.5 | -5.048
520.4 | 50.5 | -5.048
520.5 | 50.5 | -5.048
520.6 | 50.5 | -5.048
520.7 | 50.5 | -5.048
520.8 | 50.5 | -5.048
520.9 | 50.5 | -5.048
521 | 50.5 | -5.048
521.1 | 50.5 | -5.048
521.2 | 50.5 | -5.048
521.3 | 50.5 | -5.048
521.4 | 50.5 | -5.048
521.5 | 50.5 | -5.048
521.6 | 50.5 | -5.048
521.7 | 50.5 | -5.048
521.8 | 50.5 | -5.048
521.9 | 50.5 | -5.048
522 | 50.5 | -5.048
522.1 | 50.5 | -5.048
522.2 | 50.5 | -5.048
522.3 | 50.5 | -5.048
522.4 | 50.5 | -5.048
522.5 | 50.5 | -5.048
522.6 | 50.5 | -5.048
522.7 | 50.5 | -5.048
522.8 | 50.5 | -5.048
522.9 | 50.5 | -5.048
523 | 50.5 | -5.048
523.1 | 50.5 | -5.048
523.2 | 50.5 | -5.048
523.3 | 50.5 | -5.048
523.4 | 50.5 | -5.048
523.5 | 50.5 | -5.048
523.6 | 50.5 | -5.048
523.7 | 50.5 | -5.048
523.8 | 50.5 | -5.048
523.9 | 50.5 | -5.048
524 | 50.5 | -5.048
524.1 | 50.5 | -5.047
524.2 | 50.5 | -5.047
524.3 | 50.5 | -5.047
524.4 | 50.5 | -5.047
524.5 | 50.5 | -5.047
524.6 | 50.5 | -5.047
524.7 | 50.5 | -5.047
524.8 | 50.5 | -5.047
524.9 | 50.5 | -5.047
525 | 50.5 | -5.047
525.1 | 50.5 | -5.047
525.2 | 50.5 | -5.047
525.3 | 50.5 | -5.047
525.4 | 50.5 | -5.047
525.5 | 50.5 | -5.047
525.6 | 50.5 | -5.047
525.7 | 50.5 | -5.047
525.8 | 50.5 | -5.047
525.9 | 50.5 | -5.047
526 | 50.5 | -5.047
526.1 | 50.5 | -5.047
526.2 | 50.5 | -5.047
526.3 | 50.5 | -5.047
526.4 | 50.5 | -5.048
526.5 | 50.5 | -5.048
526.6 | 50.5 | -5.048
526.7 | 50.5 | -5.048
526.8 | 50.5 | -5.048
526.9 | 50.5 | -5.048
527 | 50.5 | -5.048
527.1 | 50.5 | -5.048
527.2 | 50.5 | -5.048
527.3 | 50.5 | -5.048
527.4 | 50.5 | -5.048
527.5 | 50.5 | -5.048
527.6 | 50.5 | -5.048
527.7 | 50.5 | -5.048
527.8 | 50.5 | -5.048
527.9 | 50.5 | -5.048
528 | 50.5 | -5.048
528.1 | 50.5 | -5.048
528.2 | 50.5 | -5.048
528.3 | 50.5 | -5.048
528.4 | 50.5 | -5.048
528.5 | 50.5 | -5.048
528.6 | 50.5 | -5.048
528.7 | 50.5 | -5.048
528.8 | 50.5 | -5.048
528.9 | 50.5 | -5.048
529 | 50.5 | -5.048
529.1 | 50.5 | -5.048
529.2 | 50.5 | -5.048
529.3 | 50.5 | -5.048
529.4 | 50.5 | -5.048
529.5 | 50.5 | -5.048
529.6 | 50.5 | -5.048
529.7 | 50.5 | -5.048
529.8 | 50.5 | -5.048
529.9 | 50.5 | -5.048
530 | 50.5 | -5.048
530.1 | 50.5 | -5.048
530.2 | 50.5 | -5.048
530.3 | 50.5 | -5.048
530.4 | 50.5 | -5.048
530.5 | 50.5 | -5.048
530.6 | 50.5 | -5.048
530.7 | 50.5 | -5.048
530.8 | 50.5 | -5.048
530.9 | 50.5 | -5.048
531 | 50.5 | -5.048
531.1 | 50.5 | -5.048
531.2 | 50.5 | -5.048
531.3 | 50.5 | -5.048
531.4 | 50.5 | -5.048
531.5 | 50.5 | -5.048
531.6 | 50.5 | -5.048
531.7 | 50.5 | -5.048
531.8 | 50.5 | -5.048
531.9 | 50.5 | -5.048
532 | 50.5 | -5.048
532.1 | 50.5 | -5.048
532.2 | 50.5 | -5.048
532.3 | 50.5 | -5.048
532.4 | 50.5 | -5.048
532.5 | 50.5 | -5.048
532.6 | 50.5 | -5.048
532.7 | 50.5 | -5.048
532.8 | 50.5 | -5.048
532.9 | 50.5 | -5.048
533 | 50.5 | -5.048
533.1 | 50.5 | -5.048
533.2 | 50.5 | -5.048
533.3 | 50.5 | -5.048
533.4 | 50.5 | -5.048
533.5 | 50.5 | -5.048
533.6 | 50.5 | -5.048
533.7 | 50.5 | -5.048
533.8 | 50.5 | -5.048
533.9 | 50.5 | -5.048
534 | 50.5 | -5.048
534.1 | 50.5 | -5.048
534.2 | 50.5 | -5.048
534.3 | 50.5 | -5.048
534.4 | 50.5 | -5.048
534.5 | 50.5 | -5.048
534.6 | 50.5 | -5.048
534.7 | 50.5 | -5.048
534.8 | 50.5 | -5.048
534.9 | 50.5 | -5.048
535 | 50.5 | -5.048
535.1 | 50.5 | -5.048
535.2 | 50.5 | -5.048
535.3 | 50.5 | -5.048
535.4 | 50.5 | -5.048
535.5 | 50.5 | -5.048
535.6 | 50.5 | -5.048
535.7 | 50.5 | -5.048
535.8 | 50.5 | -5.048
535.9 | 50.5 | -5.048
536 | 50.5 | -5.048
536.1 | 50.5 | -5.048
536.2 | 50.5 | -5.048
536.3 | 50.5 | -5.048
536.4 | 50.5 | -5.048
536.5 | 50.5 | -5.048
536.6 | 50.5 | -5.048
536.7 | 50.5 | -5.048
536.8 | 50.5 | -5.048
536.9 | 50.5 | -5.048
537 | 50.5 | -5.048
537.1 | 50.5 | -5.048
537.2 | 50.5 | -5.048
537.3 | 50.5 | -5.048
537.4 | 50.5 | -5.048
537.5 | 50.5 | -5.048
537.6 | 50.5 | -5.048
537.7 | 50.5 | -5.048
537.8 | 50.5 | -5.048
537.9 | 50.5 | -5.048
538 | 50.5 | -5.048
538.1 | 50.5 | -5.048
538.2 | 50.5 | -5.048
538.3 | 50.5 | -5.048
538.4 | 50.5 | -5.048
538.5 | 50.5 | -5.048
538.6 | 50.5 | -5.048
538.7 | 50.5 | -5.048
538.8 | 50.5 | -5.048
538.9 | 50.5 | -5.048
539 | 50.5 | -5.048
539.1 | 50.5 | -5.048
539.2 | 50.5 | -5.049
539.3 | 50.5 | -5.049
539.4 | 50.5 | -5.048
539.5 | 50.5 | -5.048
539.6 | 50.5 | -5.048
539.7 | 50.5 | -5.048
539.8 | 50.5 | -5.048
539.9 | 50.5 | -5.048
540 | 50.5 | -5.048
540.1 | 50.5 | -5.048
540.2 | 50.5 | -5.048
540.3 | 50.5 | -5.048
540.4 | 50.5 | -5.048
540.5 | 50.5 | -5.048
540.6 | 50.5 | -5.048
540.7 | 50.5 | -5.048
540.8 | 50.5 | -5.048
540.9 | 50.5 | -5.048
541 | 50.5 | -5.048
541.1 | 50.5 | -5.048
541.2 | 50.5 | -5.048
541.3 | 50.5 | -5.048
541.4 | 50.5 | -5.048
541.5 | 50.5 | -5.048
541.6 | 50.5 | -5.048
541.7 | 50.5 | -5.047
541.8 | 50.5 | -5.047
541.9 | 50.5 | -5.047
542 | 50.5 | -5.047
542.1 | 50.5 | -5.047
542.2 | 50.5 | -5.047
542.3 | 50.5 | -5.047
542.4 | 50.5 | -5.047
542.5 | 50.5 | -5.047
542.6 | 50.5 | -5.047
542.7 | 50.5 | -5.047
542.8 | 50.5 | -5.047
542.9 | 50.5 | -5.047
543 | 50.5 | -5.047
543.1 | 50.5 | -5.047
543.2 | 50.5 | -5.047
543.3 | 50.5 | -5.047
543.4 | 50.5 | -5.047
543.5 | 50.5 | -5.047
543.6 | 50.5 | -5.047
543.7 | 50.5 | -5.047
543.8 | 50.5 | -5.047
543.9 | 50.5 | -5.047
544 | 50.5 | -5.048
544.1 | 50.5 | -5.048
544.2 | 50.5 | -5.048
544.3 | 50.5 | -5.048
544.4 | 50.5 | -5.048
544.5 | 50.5 | -5.048
544.6 | 50.5 | -5.048
544.7 | 50.5 | -5.048
544.8 | 50.5 | -5.048
544.9 | 50.5 | -5.048
545 | 50.5 | -5.048
545.1 | 50.5 | -5.048
545.2 | 50.5 | -5.048
545.3 | 50.5 | -5.048
545.4 | 50.5 | -5.048
545.5 | 50.5 | -5.048
545.6 | 50.5 | -5.048
545.7 | 50.5 | -5.048
545.8 | 50.5 | -5.048
545.9 | 50.5 | -5.048
546 | 50.5 | -5.048
546.1 | 50.5 | -5.048
546.2 | 50.5 | -5.048
546.3 | 50.5 | -5.048
546.4 | 50.5 | -5.048
546.5 | 50.5 | -5.048
546.6 | 50.5 | -5.048
546.7 | 50.5 | -5.048
546.8 | 50.5 | -5.048
546.9 | 50.5 | -5.049
547 | 50.5 | -5.049
547.1 | 50.5 | -5.049
547.2 | 50.5 | -5.049
547.3 | 50.5 | -5.049
547.4 | 50.5 | -5.048
547.5 | 50.5 | -5.048
547.6 | 50.5 | -5.048
547.7 | 50.5 | -5.048
547.8 | 50.5 | -5.048
547.9 | 50.5 | -5.048
548 | 50.5 | -5.048
548.1 | 50.5 | -5.048
548.2 | 50.5 | -5.048
548.3 | 50.5 | -5.048
548.4 | 50.5 | -5.048
548.5 | 50.5 | -5.048
548.6 | 50.5 | -5.048
548.7 | 50.5 | -5.048
548.8 | 50.5 | -5.048
548.9 | 50.5 | -5.048
549 | 50.5 | -5.048
549.1 | 50.5 | -5.048
549.2 | 50.5 | -5.048
549.3 | 50.5 | -5.048
549.4 | 50.5 | -5.048
549.5 | 50.5 | -5.048
549.6 | 50.5 | -5.048
549.7 | 50.5 | -5.048
549.8 | 50.5 | -5.048
549.9 | 50.5 | -5.048
550 | 50.5 | -5.048
550.1 | 50.5 | -5.048
550.2 | 50.5 | -5.048
550.3 | 50.5 | -5.048
550.4 | 50.5 | -5.048
550.5 | 50.5 | -5.048
550.6 | 50.5 | -5.048
550.7 | 50.5 | -5.048
550.8 | 50.5 | -5.048
550.9 | 50.5 | -5.048
551 | 50.5 | -5.048
551.1 | 50.5 | -5.048
551.2 | 50.5 | -5.048
551.3 | 50.5 | -5.048
551.4 | 50.5 | -5.048
551.5 | 50.5 | -5.048
551.6 | 50.5 | -5.048
551.7 | 50.5 | -5.048
551.8 | 50.5 | -5.048
551.9 | 50.5 | -5.048
552 | 50.5 | -5.048
552.1 | 50.5 | -5.047
552.2 | 50.5 | -5.047
552.3 | 50.5 | -5.047
552.4 | 50.5 | -5.047
552.5 | 50.5 | -5.047
552.6 | 50.5 | -5.048
552.7 | 50.5 | -5.048
552.8 | 50.5 | -5.048
552.9 | 50.5 | -5.048
553 | 50.5 | -5.048
553.1 | 50.5 | -5.048
553.2 | 50.5 | -5.048
553.3 | 50.5 | -5.048
553.4 | 50.5 | -5.047
553.5 | 50.5 | -5.047
553.6 | 50.5 | -5.047
553.7 | 50.5 | -5.047
553.8 | 50.5 | -5.047
553.9 | 50.5 | -5.047
554 | 50.5 | -5.047
554.1 | 50.5 | -5.047
554.2 | 50.5 | -5.047
554.3 | 50.5 | -5.047
554.4 | 50.5 | -5.048
554.5 | 50.5 | -5.048
554.6 | 50.5 | -5.048
554.7 | 50.5 | -5.048
554.8 | 50.5 | -5.048
554.9 | 50.5 | -5.048
555 | 50.5 | -5.048
555.1 | 50.5 | -5.048
555.2 | 50.5 | -5.048
555.3 | 50.5 | -5.048
555.4 | 50.5 | -5.048
555.5 | 50.5 | -5.048
555.6 | 50.5 | -5.048
555.7 | 50.5 | -5.048
555.8 | 50.5 | -5.048
555.9 | 50.5 | -5.048
556 | 50.5 | -5.048
556.1 | 50.5 | -5.048
556.2 | 50.5 | -5.048
556.3 | 50.5 | -5.048
556.4 | 50.5 | -5.048
556.5 | 50.5 | -5.048
556.6 | 50.5 | -5.048
556.7 | 50.5 | -5.048
556.8 | 50.5 | -5.048
556.9 | 50.5 | -5.048
557 | 50.5 | -5.048
557.1 | 50.5 | -5.048
557.2 | 50.5 | -5.048
557.3 | 50.5 | -5.048
557.4 | 50.5 | -5.048
557.5 | 50.5 | -5.048
557.6 | 50.5 | -5.048
557.7 | 50.5 | -5.048
557.8 | 50.5 | -5.048
557.9 | 50.5 | -5.048
558 | 50.5 | -5.048
558.1 | 50.5 | -5.048
558.2 | 50.5 | -5.048
558.3 | 50.5 | -5.048
558.4 | 50.5 | -5.048
558.5 | 50.5 | -5.048
558.6 | 50.5 | -5.048
558.7 | 50.5 | -5.048
558.8 | 50.5 | -5.048
558.9 | 50.5 | -5.048
559 | 50.5 | -5.048
559.1 | 50.5 | -5.048
559.2 | 50.5 | -5.048
559.3 | 50.5 | -5.047
559.4 | 50.5 | -5.047
559.5 | 50.5 | -5.047
559.6 | 50.5 | -5.047
559.7 | 50.5 | -5.047
559.8 | 50.5 | -5.047
559.9 | 50.5 | -5.047
560 | 50.5 | -5.047
560.1 | 50.5 | -5.047
560.2 | 50.5 | -5.047
560.3 | 50.5 | -5.048
560.4 | 50.5 | -5.048
560.5 | 50.5 | -5.048
560.6 | 50.5 | -5.048
560.7 | 50.5 | -5.048
560.8 | 50.5 | -5.048
560.9 | 50.5 | -5.048
561 | 50.5 | -5.048
561.1 | 50.5 | -5.048
561.2 | 50.5 | -5.048
561.3 | 50.5 | -5.048
561.4 | 50.5 | -5.048
561.5 | 50.5 | -5.048
561.6 | 50.5 | -5.048
561.7 | 50.5 | -5.048
561.8 | 50.5 | -5.048
561.9 | 50.5 | -5.048
562 | 50.5 | -5.048
562.1 | 50.5 | -5.048
562.2 | 50.5 | -5.048
562.3 | 50.5 | -5.048
562.4 | 50.5 | -5.048
562.5 | 50.5 | -5.048
562.6 | 50.5 | -5.048
562.7 | 50.5 | -5.048
562.8 | 50.5 | -5.048
562.9 | 50.5 | -5.048
563 | 50.5 | -5.048
563.1 | 50.5 | -5.048
563.2 | 50.5 | -5.048
563.3 | 50.5 | -5.048
563.4 | 50.5 | -5.048
563.5 | 50.5 | -5.048
563.6 | 50.5 | -5.048
563.7 | 50.5 | -5.048
563.8 | 50.5 | -5.048
563.9 | 50.5 | -5.048
564 | 50.5 | -5.048
564.1 | 50.5 | -5.048
564.2 | 50.5 | -5.048
564.3 | 50.5 | -5.048
564.4 | 50.5 | -5.048
564.5 | 50.5 | -5.048
564.6 | 50.5 | -5.048
564.7 | 50.5 | -5.048
564.8 | 50.5 | -5.048
564.9 | 50.5 | -5.048
565 | 50.5 | -5.047
565.1 | 50.5 | -5.047
565.2 | 50.5 | -5.047
565.3 | 50.5 | -5.047
565.4 | 50.5 | -5.047
565.5 | 50.5 | -5.047
565.6 | 50.5 | -5.047
565.7 | 50.5 | -5.047
565.8 | 50.5 | -5.047
565.9 | 50.5 | -5.047
566 | 50.5 | -5.047
566.1 | 50.5 | -5.047
566.2 | 50.5 | -5.047
566.3 | 50.5 | -5.047
566.4 | 50.5 | -5.047
566.5 | 50.5 | -5.047
566.6 | 50.5 | -5.047
566.7 | 50.5 | -5.047
566.8 | 50.5 | -5.047
566.9 | 50.5 | -5.047
567 | 50.5 | -5.047
567.1 | 50.5 | -5.047
567.2 | 50.5 | -5.047
567.3 | 50.5 | -5.047
567.4 | 50.5 | -5.047
567.5 | 50.5 | -5.047
567.6 | 50.5 | -5.047
567.7 | 50.5 | -5.047
567.8 | 50.5 | -5.047
567.9 | 50.5 | -5.047
568 | 50.5 | -5.047
568.1 | 50.5 | -5.047
568.2 | 50.5 | -5.047
568.3 | 50.5 | -5.047
568.4 | 50.5 | -5.048
568.5 | 50.5 | -5.048
568.6 | 50.5 | -5.048
568.7 | 50.5 | -5.048
568.8 | 50.5 | -5.048
568.9 | 50.5 | -5.048
569 | 50.5 | -5.048
569.1 | 50.5 | -5.048
569.2 | 50.5 | -5.048
569.3 | 50.5 | -5.048
569.4 | 50.5 | -5.048
569.5 | 50.5 | -5.048
569.6 | 50.5 | -5.048
569.7 | 50.5 | -5.048
569.8 | 50.5 | -5.048
569.9 | 50.5 | -5.048
570 | 50.5 | -5.048
570.1 | 50.5 | -5.048
570.2 | 50.5 | -5.048
570.3 | 50.5 | -5.048
570.4 | 50.5 | -5.048
570.5 | 50.5 | -5.048
570.6 | 50.5 | -5.048
570.7 | 50.5 | -5.048
570.8 | 50.5 | -5.048
570.9 | 50.5 | -5.047
571 | 50.5 | -5.047
571.1 | 50.5 | -5.047
571.2 | 50.5 | -5.047
571.3 | 50.5 | -5.047
571.4 | 50.5 | -5.047
571.5 | 50.5 | -5.047
571.6 | 50.5 | -5.047
571.7 | 50.5 | -5.047
571.8 | 50.5 | -5.047
571.9 | 50.5 | -5.047
572 | 50.5 | -5.047
572.1 | 50.5 | -5.048
572.2 | 50.5 | -5.048
572.3 | 50.5 | -5.048
572.4 | 50.5 | -5.048
572.5 | 50.5 | -5.048
572.6 | 50.5 | -5.048
572.7 | 50.5 | -5.048
572.8 | 50.5 | -5.048
572.9 | 50.5 | -5.048
573 | 50.5 | -5.048
573.1 | 50.5 | -5.048
573.2 | 50.5 | -5.048
573.3 | 50.5 | -5.048
573.4 | 50.5 | -5.048
573.5 | 50.5 | -5.048
573.6 | 50.5 | -5.048
573.7 | 50.5 | -5.048
573.8 | 50.5 | -5.048
573.9 | 50.5 | -5.048
574 | 50.5 | -5.048
574.1 | 50.5 | -5.048
574.2 | 50.5 | -5.048
574.3 | 50.5 | -5.048
574.4 | 50.5 | -5.048
574.5 | 50.5 | -5.048
574.6 | 50.5 | -5.048
574.7 | 50.5 | -5.048
574.8 | 50.5 | -5.048
574.9 | 50.5 | -5.048
575 | 50.5 | -5.048
575.1 | 50.5 | -5.048
575.2 | 50.5 | -5.048
575.3 | 50.5 | -5.048
575.4 | 50.5 | -5.048
575.5 | 50.5 | -5.048
575.6 | 50.5 | -5.048
575.7 | 50.5 | -5.048
575.8 | 50.5 | -5.048
575.9 | 50.5 | -5.048
576 | 50.5 | -5.048
576.1 | 50.5 | -5.048
576.2 | 50.5 | -5.048
576.3 | 50.5 | -5.048
576.4 | 50.5 | -5.048
576.5 | 50.5 | -5.048
576.6 | 50.5 | -5.048
576.7 | 50.5 | -5.048
576.8 | 50.5 | -5.048
576.9 | 50.5 | -5.047
577 | 50.5 | -5.047
577.1 | 50.5 | -5.047
577.2 | 50.5 | -5.047
577.3 | 50.5 | -5.047
577.4 | 50.5 | -5.047
577.5 | 50.5 | -5.047
577.6 | 50.5 | -5.047
577.7 | 50.5 | -5.047
577.8 | 50.5 | -5.047
577.9 | 50.5 | -5.048
578 | 50.5 | -5.048
578.1 | 50.5 | -5.048
578.2 | 50.5 | -5.048
578.3 | 50.5 | -5.048
578.4 | 50.5 | -5.048
578.5 | 50.5 | -5.048
578.6 | 50.5 | -5.048
578.7 | 50.5 | -5.048
578.8 | 50.5 | -5.048
578.9 | 50.5 | -5.048
579 | 50.5 | -5.048
579.1 | 50.5 | -5.048
579.2 | 50.5 | -5.048
579.3 | 50.5 | -5.048
579.4 | 50.5 | -5.048
579.5 | 50.5 | -5.048
579.6 | 50.5 | -5.048
579.7 | 50.5 | -5.048
579.8 | 50.5 | -5.048
579.9 | 50.5 | -5.048
580 | 50.5 | -5.048
580.1 | 50.5 | -5.048
580.2 | 50.5 | -5.047
580.3 | 50.5 | -5.048
580.4 | 50.5 | -5.048
580.5 | 50.5 | -5.048
580.6 | 50.5 | -5.048
580.7 | 50.5 | -5.048
580.8 | 50.5 | -5.048
580.9 | 50.5 | -5.048
581 | 50.5 | -5.048
581.1 | 50.5 | -5.048
581.2 | 50.5 | -5.048
581.3 | 50.5 | -5.048
581.4 | 50.5 | -5.048
581.5 | 50.5 | -5.048
581.6 | 50.5 | -5.048
581.7 | 50.5 | -5.048
581.8 | 50.5 | -5.048
581.9 | 50.5 | -5.048
582 | 50.5 | -5.048
582.1 | 50.5 | -5.048
582.2 | 50.5 | -5.048
582.3 | 50.5 | -5.048
582.4 | 50.5 | -5.048
582.5 | 50.5 | -5.048
582.6 | 50.5 | -5.048
582.7 | 50.5 | -5.048
582.8 | 50.5 | -5.048
582.9 | 50.5 | -5.048
583 | 50.5 | -5.048
583.1 | 50.5 | -5.048
583.2 | 50.5 | -5.048
583.3 | 50.5 | -5.048
583.4 | 50.5 | -5.048
583.5 | 50.5 | -5.048
583.6 | 50.5 | -5.048
583.7 | 50.5 | -5.047
583.8 | 50.5 | -5.047
583.9 | 50.5 | -5.047
584 | 50.5 | -5.047
584.1 | 50.5 | -5.047
584.2 | 50.5 | -5.047
584.3 | 50.5 | -5.047
584.4 | 50.5 | -5.047
584.5 | 50.5 | -5.047
584.6 | 50.5 | -5.047
584.7 | 50.5 | -5.047
584.8 | 50.5 | -5.048
584.9 | 50.5 | -5.048
585 | 50.5 | -5.048
585.1 | 50.5 | -5.047
585.2 | 50.5 | -5.047
585.3 | 50.5 | -5.047
585.4 | 50.5 | -5.047
585.5 | 50.5 | -5.047
585.6 | 50.5 | -5.047
585.7 | 50.5 | -5.047
585.8 | 50.5 | -5.047
585.9 | 50.5 | -5.047
586 | 50.5 | -5.047
586.1 | 50.5 | -5.048
586.2 | 50.5 | -5.048
586.3 | 50.5 | -5.048
586.4 | 50.5 | -5.048
586.5 | 50.5 | -5.048
586.6 | 50.5 | -5.048
586.7 | 50.5 | -5.048
586.8 | 50.5 | -5.048
586.9 | 50.5 | -5.048
587 | 50.5 | -5.048
587.1 | 50.5 | -5.048
587.2 | 50.5 | -5.048
587.3 | 50.5 | -5.048
587.4 | 50.5 | -5.048
587.5 | 50.5 | -5.048
587.6 | 50.5 | -5.048
587.7 | 50.5 | -5.048
587.8 | 50.5 | -5.048
587.9 | 50.5 | -5.048
588 | 50.5 | -5.048
588.1 | 50.5 | -5.048
588.2 | 50.5 | -5.048
588.3 | 50.5 | -5.048
588.4 | 50.5 | -5.048
588.5 | 50.5 | -5.048
588.6 | 50.5 | -5.048
588.7 | 50.5 | -5.048
588.8 | 50.5 | -5.048
588.9 | 50.5 | -5.048
589 | 50.5 | -5.048
589.1 | 50.5 | -5.048
589.2 | 50.5 | -5.048
589.3 | 50.5 | -5.048
589.4 | 50.5 | -5.048
589.5 | 50.5 | -5.048
589.6 | 50.5 | -5.048
589.7 | 50.5 | -5.047
589.8 | 50.5 | -5.047
589.9 | 50.5 | -5.047
590 | 50.5 | -5.047
590.1 | 50.5 | -5.047
590.2 | 50.5 | -5.047
590.3 | 50.5 | -5.047
590.4 | 50.5 | -5.047
590.5 | 50.5 | -5.047
590.6 | 50.5 | -5.047
590.7 | 50.5 | -5.047
590.8 | 50.5 | -5.048
590.9 | 50.5 | -5.048
591 | 50.5 | -5.048
591.1 | 50.5 | -5.048
591.2 | 50.5 | -5.048
591.3 | 50.5 | -5.048
591.4 | 50.5 | -5.048
591.5 | 50.5 | -5.048
591.6 | 50.5 | -5.048
591.7 | 50.5 | -5.048
591.8 | 50.5 | -5.048
591.9 | 50.5 | -5.048
592 | 50.5 | -5.048
592.1 | 50.5 | -5.048
592.2 | 50.5 | -5.048
592.3 | 50.5 | -5.048
592.4 | 50.5 | -5.048
592.5 | 50.5 | -5.048
592.6 | 50.5 | -5.048
592.7 | 50.5 | -5.048
592.8 | 50.5 | -5.048
592.9 | 50.5 | -5.048
593 | 50.5 | -5.048
593.1 | 50.5 | -5.048
593.2 | 50.5 | -5.048
593.3 | 50.5 | -5.048
593.4 | 50.5 | -5.048
593.5 | 50.5 | -5.048
593.6 | 50.5 | -5.048
593.7 | 50.5 | -5.048
593.8 | 50.5 | -5.048
593.9 | 50.5 | -5.048
594 | 50.5 | -5.048
594.1 | 50.5 | -5.048
594.2 | 50.5 | -5.048
594.3 | 50.5 | -5.048
594.4 | 50.5 | -5.048
594.5 | 50.5 | -5.048
594.6 | 50.5 | -5.048
594.7 | 50.5 | -5.048
594.8 | 50.5 | -5.048
594.9 | 50.5 | -5.048
595 | 50.5 | -5.048
595.1 | 50.5 | -5.048
595.2 | 50.5 | -5.048
595.3 | 50.5 | -5.048
595.4 | 50.5 | -5.048
595.5 | 50.5 | -5.048
595.6 | 50.5 | -5.048
595.7 | 50.5 | -5.048
595.8 | 50.5 | -5.048
595.9 | 50.5 | -5.048
596 | 50.5 | -5.048
596.1 | 50.5 | -5.048
596.2 | 50.5 | -5.048
596.3 | 50.5 | -5.048
596.4 | 50.5 | -5.048
596.5 | 50.5 | -5.048
596.6 | 50.5 | -5.048
596.7 | 50.5 | -5.048
596.8 | 50.5 | -5.048
596.9 | 50.5 | -5.048
597 | 50.5 | -5.048
597.1 | 50.5 | -5.048
597.2 | 50.5 | -5.048
597.3 | 50.5 | -5.048
597.4 | 50.5 | -5.048
597.5 | 50.5 | -5.048
597.6 | 50.5 | -5.048
597.7 | 50.5 | -5.048
597.8 | 50.5 | -5.047
597.9 | 50.5 | -5.047
598 | 50.5 | -5.047
598.1 | 50.5 | -5.047
598.2 | 50.5 | -5.047
598.3 | 50.5 | -5.047
598.4 | 50.5 | -5.047
598.5 | 50.5 | -5.047
598.6 | 50.5 | -5.047
598.7 | 50.5 | -5.047
598.8 | 50.5 | -5.047
598.9 | 50.5 | -5.047
599 | 50.5 | -5.048
599.1 | 50.5 | -5.048
599.2 | 50.5 | -5.048
599.3 | 50.5 | -5.048
599.4 | 50.5 | -5.048
599.5 | 50.5 | -5.048
599.6 | 50.5 | -5.048
599.7 | 50.5 | -5.048
599.8 | 50.5 | -5.048
599.9 | 50.5 | -5.048
600 | 50.5 | -5.048
600.1 | 50.5 | -5.047
600.2 | 50.5 | -5.047
600.3 | 50.5 | -5.047
600.4 | 50.5 | -5.047
600.5 | 50.5 | -5.047
600.6 | 50.5 | -5.047
600.7 | 50.5 | -5.047
600.8 | 50.5 | -5.047
600.9 | 50.5 | -5.047
601 | 50.5 | -5.047
601.1 | 50.5 | -5.047
601.2 | 50.5 | -5.048
601.3 | 50.5 | -5.048
601.4 | 50.5 | -5.048
601.5 | 50.5 | -5.048
601.6 | 50.5 | -5.048
601.7 | 50.5 | -5.048
601.8 | 50.5 | -5.048
601.9 | 50.5 | -5.048
602 | 50.5 | -5.048
602.1 | 50.5 | -5.048
602.2 | 50.5 | -5.048
602.3 | 50.5 | -5.048
602.4 | 50.5 | -5.048
602.5 | 50.5 | -5.048
602.6 | 50.5 | -5.048
602.7 | 50.5 | -5.048
602.8 | 50.5 | -5.048
602.9 | 50.5 | -5.048
603 | 50.5 | -5.048
603.1 | 50.5 | -5.048
603.2 | 50.5 | -5.048
603.3 | 50.5 | -5.048
603.4 | 50.5 | -5.048
603.5 | 50.5 | -5.048
603.6 | 50.5 | -5.048
603.7 | 50.5 | -5.048
603.8 | 50.5 | -5.048
603.9 | 50.5 | -5.048
604 | 50.5 | -5.048
604.1 | 50.5 | -5.048
604.2 | 50.5 | -5.048
604.3 | 50.5 | -5.048
604.4 | 50.5 | -5.048
604.5 | 50.5 | -5.048
604.6 | 50.5 | -5.048
604.7 | 50.5 | -5.048
604.8 | 50.5 | -5.048
604.9 | 50.5 | -5.048
605 | 50.5 | -5.048
605.1 | 50.5 | -5.048
605.2 | 50.5 | -5.048
605.3 | 50.5 | -5.048
605.4 | 50.5 | -5.048
605.5 | 50.5 | -5.048
605.6 | 50.5 | -5.048
605.7 | 50.5 | -5.048
605.8 | 50.5 | -5.048
605.9 | 50.5 | -5.048
606 | 50.5 | -5.048
606.1 | 50.5 | -5.048
606.2 | 50.5 | -5.048
606.3 | 50.5 | -5.048
606.4 | 50.5 | -5.048
606.5 | 50.5 | -5.048
606.6 | 50.5 | -5.048
606.7 | 50.5 | -5.048
606.8 | 50.5 | -5.048
606.9 | 50.5 | -5.048
607 | 50.5 | -5.048
607.1 | 50.5 | -5.048
607.2 | 50.5 | -5.048
607.3 | 50.5 | -5.048
607.4 | 50.5 | -5.048
607.5 | 50.5 | -5.048
607.6 | 50.5 | -5.048
607.7 | 50.5 | -5.048
607.8 | 50.5 | -5.048
607.9 | 50.5 | -5.048
608 | 50.5 | -5.048
608.1 | 50.5 | -5.048
608.2 | 50.5 | -5.048
608.3 | 50.5 | -5.048
608.4 | 50.5 | -5.048
608.5 | 50.5 | -5.048
608.6 | 50.5 | -5.048
608.7 | 50.5 | -5.048
608.8 | 50.5 | -5.048
608.9 | 50.5 | -5.048
609 | 50.5 | -5.048
609.1 | 50.5 | -5.048
609.2 | 50.5 | -5.048
609.3 | 50.5 | -5.048
609.4 | 50.5 | -5.048
609.5 | 50.5 | -5.048
609.6 | 50.5 | -5.048
609.7 | 50.5 | -5.048
609.8 | 50.5 | -5.048
609.9 | 50.5 | -5.048
610 | 50.5 | -5.048
610.1 | 50.5 | -5.048
610.2 | 50.5 | -5.048
610.3 | 50.5 | -5.048
610.4 | 50.5 | -5.048
610.5 | 50.5 | -5.048
610.6 | 50.5 | -5.048
610.7 | 50.5 | -5.048
610.8 | 50.5 | -5.048
610.9 | 50.5 | -5.048
611 | 50.5 | -5.048
611.1 | 50.5 | -5.048
611.2 | 50.5 | -5.048
611.3 | 50.5 | -5.048
611.4 | 50.5 | -5.048
611.5 | 50.5 | -5.048
611.6 | 50.5 | -5.048
611.7 | 50.5 | -5.048
611.8 | 50.5 | -5.048
611.9 | 50.5 | -5.048
612 | 50.5 | -5.048
612.1 | 50.5 | -5.048
612.2 | 50.5 | -5.048
612.3 | 50.5 | -5.048
612.4 | 50.5 | -5.048
612.5 | 50.5 | -5.048
612.6 | 50.5 | -5.048
612.7 | 50.5 | -5.048
612.8 | 50.5 | -5.048
612.9 | 50.5 | -5.048
613 | 50.5 | -5.048
613.1 | 50.5 | -5.048
613.2 | 50.5 | -5.048
613.3 | 50.5 | -5.048
613.4 | 50.5 | -5.048
613.5 | 50.5 | -5.048
613.6 | 50.5 | -5.048
613.7 | 50.5 | -5.048
613.8 | 50.5 | -5.048
613.9 | 50.5 | -5.048
614 | 50.5 | -5.048
614.1 | 50.5 | -5.048
614.2 | 50.5 | -5.048
614.3 | 50.5 | -5.048
614.4 | 50.5 | -5.048
614.5 | 50.5 | -5.048
614.6 | 50.5 | -5.048
614.7 | 50.5 | -5.048
614.8 | 50.5 | -5.048
614.9 | 50.5 | -5.048
615 | 50.5 | -5.048
615.1 | 50.5 | -5.048
615.2 | 50.5 | -5.048
615.3 | 50.5 | -5.048
615.4 | 50.5 | -5.048
615.5 | 50.5 | -5.048
615.6 | 50.5 | -5.048
615.7 | 50.5 | -5.048
615.8 | 50.5 | -5.048
615.9 | 50.5 | -5.048
616 | 50.5 | -5.048
616.1 | 50.5 | -5.048
616.2 | 50.5 | -5.048
616.3 | 50.5 | -5.048
616.4 | 50.5 | -5.048
616.5 | 50.5 | -5.048
616.6 | 50.5 | -5.048
616.7 | 50.5 | -5.048
616.8 | 50.5 | -5.048
616.9 | 50.5 | -5.048
617 | 50.5 | -5.048
617.1 | 50.5 | -5.048
617.2 | 50.5 | -5.048
617.3 | 50.5 | -5.048
617.4 | 50.5 | -5.048
617.5 | 50.5 | -5.048
617.6 | 50.5 | -5.048
617.7 | 50.5 | -5.047
617.8 | 50.5 | -5.047
617.9 | 50.5 | -5.047
618 | 50.5 | -5.047
618.1 | 50.5 | -5.047
618.2 | 50.5 | -5.047
618.3 | 50.5 | -5.047
618.4 | 50.5 | -5.047
618.5 | 50.5 | -5.047
618.6 | 50.5 | -5.047
618.7 | 50.5 | -5.048
618.8 | 50.5 | -5.047
618.9 | 50.5 | -5.047
619 | 50.5 | -5.047
619.1 | 50.5 | -5.047
619.2 | 50.5 | -5.047
619.3 | 50.5 | -5.047
619.4 | 50.5 | -5.047
619.5 | 50.5 | -5.047
619.6 | 50.5 | -5.047
619.7 | 50.5 | -5.047
619.8 | 50.5 | -5.047
619.9 | 50.5 | -5.047
620 | 50.5 | -5.047
620.1 | 50.5 | -5.047
620.2 | 50.5 | -5.047
620.3 | 50.5 | -5.047
620.4 | 50.5 | -5.047
620.5 | 50.5 | -5.047
620.6 | 50.5 | -5.047
620.7 | 50.5 | -5.047
620.8 | 50.5 | -5.047
620.9 | 50.5 | -5.047
621 | 50.5 | -5.048
621.1 | 50.5 | -5.048
621.2 | 50.5 | -5.048
621.3 | 50.5 | -5.048
621.4 | 50.5 | -5.048
621.5 | 50.5 | -5.048
621.6 | 50.5 | -5.048
621.7 | 50.5 | -5.048
621.8 | 50.5 | -5.048
621.9 | 50.5 | -5.048
622 | 50.5 | -5.048
622.1 | 50.5 | -5.048
622.2 | 50.5 | -5.048
622.3 | 50.5 | -5.048
622.4 | 50.5 | -5.048
622.5 | 50.5 | -5.048
622.6 | 50.5 | -5.048
622.7 | 50.5 | -5.048
622.8 | 50.5 | -5.048
622.9 | 50.5 | -5.048
623 | 50.5 | -5.048
623.1 | 50.5 | -5.048
623.2 | 50.5 | -5.048
623.3 | 50.5 | -5.048
623.4 | 50.5 | -5.048
623.5 | 50.5 | -5.048
623.6 | 50.5 | -5.048
623.7 | 50.5 | -5.047
623.8 | 50.5 | -5.047
623.9 | 50.5 | -5.047
624 | 50.5 | -5.047
624.1 | 50.5 | -5.047
624.2 | 50.5 | -5.047
624.3 | 50.5 | -5.047
624.4 | 50.5 | -5.047
624.5 | 50.5 | -5.047
624.6 | 50.5 | -5.047
624.7 | 50.5 | -5.047
624.8 | 50.5 | -5.048
624.9 | 50.5 | -5.048
625 | 50.5 | -5.048
625.1 | 50.5 | -5.048
625.2 | 50.5 | -5.048
625.3 | 50.5 | -5.048
625.4 | 50.5 | -5.048
625.5 | 50.5 | -5.048
625.6 | 50.5 | -5.048
625.7 | 50.5 | -5.048
625.8 | 50.5 | -5.048
625.9 | 50.5 | -5.048
626 | 50.5 | -5.048
626.1 | 50.5 | -5.048
626.2 | 50.5 | -5.048
626.3 | 50.5 | -5.048
626.4 | 50.5 | -5.048
626.5 | 50.5 | -5.048
626.6 | 50.5 | -5.048
626.7 | 50.5 | -5.048
626.8 | 50.5 | -5.048
626.9 | 50.5 | -5.048
627 | 50.5 | -5.048
627.1 | 50.5 | -5.048
627.2 | 50.5 | -5.048
627.3 | 50.5 | -5.048
627.4 | 50.5 | -5.048
627.5 | 50.5 | -5.048
627.6 | 50.5 | -5.048
627.7 | 50.5 | -5.048
627.8 | 50.5 | -5.048
627.9 | 50.5 | -5.048
628 | 50.5 | -5.048
628.1 | 50.5 | -5.048
628.2 | 50.5 | -5.048
628.3 | 50.5 | -5.048
628.4 | 50.5 | -5.048
628.5 | 50.5 | -5.048
628.6 | 50.5 | -5.048
628.7 | 50.5 | -5.048
628.8 | 50.5 | -5.048
628.9 | 50.5 | -5.048
629 | 50.5 | -5.048
629.1 | 50.5 | -5.048
629.2 | 50.5 | -5.048
629.3 | 50.5 | -5.048
629.4 | 50.5 | -5.048
629.5 | 50.5 | -5.048
629.6 | 50.5 | -5.048
629.7 | 50.5 | -5.048
629.8 | 50.5 | -5.048
629.9 | 50.5 | -5.048
630 | 50.5 | -5.048
630.1 | 50.5 | -5.048
630.2 | 50.5 | -5.048
630.3 | 50.5 | -5.048
630.4 | 50.5 | -5.048
630.5 | 50.5 | -5.048
630.6 | 50.5 | -5.048
630.7 | 50.5 | -5.048
630.8 | 50.5 | -5.048
630.9 | 50.5 | -5.048
631 | 50.5 | -5.048
631.1 | 50.5 | -5.048
631.2 | 50.5 | -5.048
631.3 | 50.5 | -5.048
631.4 | 50.5 | -5.048
631.5 | 50.5 | -5.048
631.6 | 50.5 | -5.048
631.7 | 50.5 | -5.048
631.8 | 50.5 | -5.048
631.9 | 50.5 | -5.048
632 | 50.5 | -5.048
632.1 | 50.5 | -5.048
632.2 | 50.5 | -5.048
632.3 | 50.5 | -5.048
632.4 | 50.5 | -5.048
632.5 | 50.5 | -5.048
632.6 | 50.5 | -5.048
632.7 | 50.5 | -5.048
632.8 | 50.5 | -5.048
632.9 | 50.5 | -5.048
633 | 50.5 | -5.048
633.1 | 50.5 | -5.048
633.2 | 50.5 | -5.048
633.3 | 50.5 | -5.048
633.4 | 50.5 | -5.048
633.5 | 50.5 | -5.048
633.6 | 50.5 | -5.048
633.7 | 50.5 | -5.048
633.8 | 50.5 | -5.048
633.9 | 50.5 | -5.048
634 | 50.5 | -5.048
634.1 | 50.5 | -5.048
634.2 | 50.5 | -5.048
634.3 | 50.5 | -5.048
634.4 | 50.5 | -5.048
634.5 | 50.5 | -5.048
634.6 | 50.5 | -5.048
634.7 | 50.5 | -5.048
634.8 | 50.5 | -5.048
634.9 | 50.5 | -5.048
635 | 50.5 | -5.048
635.1 | 50.5 | -5.048
635.2 | 50.5 | -5.048
635.3 | 50.5 | -5.048
635.4 | 50.5 | -5.048
635.5 | 50.5 | -5.048
635.6 | 50.5 | -5.048
635.7 | 50.5 | -5.048
635.8 | 50.5 | -5.048
635.9 | 50.5 | -5.048
636 | 50.5 | -5.048
636.1 | 50.5 | -5.048
636.2 | 50.5 | -5.048
636.3 | 50.5 | -5.048
636.4 | 50.5 | -5.048
636.5 | 50.5 | -5.048
636.6 | 50.5 | -5.048
636.7 | 50.5 | -5.048
636.8 | 50.5 | -5.048
636.9 | 50.5 | -5.048
637 | 50.5 | -5.048
637.1 | 50.5 | -5.048
637.2 | 50.5 | -5.048
637.3 | 50.5 | -5.048
637.4 | 50.5 | -5.048
637.5 | 50.5 | -5.048
637.6 | 50.5 | -5.048
637.7 | 50.5 | -5.048
637.8 | 50.5 | -5.048
637.9 | 50.5 | -5.048
638 | 50.5 | -5.048
638.1 | 50.5 | -5.048
638.2 | 50.5 | -5.048
638.3 | 50.5 | -5.048
638.4 | 50.5 | -5.048
638.5 | 50.5 | -5.048
638.6 | 50.5 | -5.048
638.7 | 50.5 | -5.048
638.8 | 50.5 | -5.048
638.9 | 50.5 | -5.048
639 | 50.5 | -5.048
639.1 | 50.5 | -5.048
639.2 | 50.5 | -5.048
639.3 | 50.5 | -5.048
639.4 | 50.5 | -5.048
639.5 | 50.5 | -5.048
639.6 | 50.5 | -5.048
639.7 | 50.5 | -5.048
639.8 | 50.5 | -5.048
639.9 | 50.5 | -5.048
640 | 50.5 | -5.048
640.1 | 50.5 | -5.048
640.2 | 50.5 | -5.048
640.3 | 50.5 | -5.048
640.4 | 50.5 | -5.048
640.5 | 50.5 | -5.048
640.6 | 50.5 | -5.048
640.7 | 50.5 | -5.048
640.8 | 50.5 | -5.048
640.9 | 50.5 | -5.048
641 | 50.5 | -5.048
641.1 | 50.5 | -5.048
641.2 | 50.5 | -5.048
641.3 | 50.5 | -5.048
641.4 | 50.5 | -5.048
641.5 | 50.5 | -5.048
641.6 | 50.5 | -5.048
641.7 | 50.5 | -5.048
641.8 | 50.5 | -5.048
641.9 | 50.5 | -5.048
642 | 50.5 | -5.048
642.1 | 50.5 | -5.048
642.2 | 50.5 | -5.048
642.3 | 50.5 | -5.048
642.4 | 50.5 | -5.048
642.5 | 50.5 | -5.048
642.6 | 50.5 | -5.048
642.7 | 50.5 | -5.048
642.8 | 50.5 | -5.048
642.9 | 50.5 | -5.048
643 | 50.5 | -5.048
643.1 | 50.5 | -5.048
643.2 | 50.5 | -5.048
643.3 | 50.5 | -5.048
643.4 | 50.5 | -5.048
643.5 | 50.5 | -5.048
643.6 | 50.5 | -5.048
643.7 | 50.5 | -5.048
643.8 | 50.5 | -5.048
643.9 | 50.5 | -5.048
644 | 50.5 | -5.048
644.1 | 50.5 | -5.048
644.2 | 50.5 | -5.048
644.3 | 50.5 | -5.048
644.4 | 50.5 | -5.048
644.5 | 50.5 | -5.048
644.6 | 50.5 | -5.048
644.7 | 50.5 | -5.048
644.8 | 50.5 | -5.048
644.9 | 50.5 | -5.048
645 | 50.5 | -5.048
645.1 | 50.5 | -5.048
645.2 | 50.5 | -5.048
645.3 | 50.5 | -5.048
645.4 | 50.5 | -5.048
645.5 | 50.5 | -5.048
645.6 | 50.5 | -5.048
645.7 | 50.5 | -5.048
645.8 | 50.5 | -5.048
645.9 | 50.5 | -5.048
646 | 50.5 | -5.048
646.1 | 50.5 | -5.048
646.2 | 50.5 | -5.048
646.3 | 50.5 | -5.048
646.4 | 50.5 | -5.048
646.5 | 50.5 | -5.048
646.6 | 50.5 | -5.048
646.7 | 50.5 | -5.048
646.8 | 50.5 | -5.048
646.9 | 50.5 | -5.048
647 | 50.5 | -5.048
647.1 | 50.5 | -5.048
647.2 | 50.5 | -5.048
647.3 | 50.5 | -5.048
647.4 | 50.5 | -5.048
647.5 | 50.5 | -5.048
647.6 | 50.5 | -5.048
647.7 | 50.5 | -5.048
647.8 | 50.5 | -5.048
647.9 | 50.5 | -5.048
648 | 50.5 | -5.048
648.1 | 50.5 | -5.048
648.2 | 50.5 | -5.048
648.3 | 50.5 | -5.048
648.4 | 50.5 | -5.048
648.5 | 50.5 | -5.048
648.6 | 50.5 | -5.048
648.7 | 50.5 | -5.048
648.8 | 50.5 | -5.048
648.9 | 50.5 | -5.048
649 | 50.5 | -5.048
649.1 | 50.5 | -5.048
649.2 | 50.5 | -5.048
649.3 | 50.5 | -5.048
649.4 | 50.5 | -5.048
649.5 | 50.5 | -5.048
649.6 | 50.5 | -5.048
649.7 | 50.5 | -5.048
649.8 | 50.5 | -5.048
649.9 | 50.5 | -5.048
650 | 50.5 | -5.048
650.1 | 50.5 | -5.048
650.2 | 50.5 | -5.048
650.3 | 50.5 | -5.048
650.4 | 50.5 | -5.048
650.5 | 50.5 | -5.048
650.6 | 50.5 | -5.048
650.7 | 50.5 | -5.048
650.8 | 50.5 | -5.048
650.9 | 50.5 | -5.048
651 | 50.5 | -5.048
651.1 | 50.5 | -5.048
651.2 | 50.5 | -5.048
651.3 | 50.5 | -5.048
651.4 | 50.5 | -5.048
651.5 | 50.5 | -5.048
651.6 | 50.5 | -5.048
651.7 | 50.5 | -5.048
651.8 | 50.5 | -5.048
651.9 | 50.5 | -5.048
652 | 50.5 | -5.048
652.1 | 50.5 | -5.048
652.2 | 50.5 | -5.048
652.3 | 50.5 | -5.048
652.4 | 50.5 | -5.048
652.5 | 50.5 | -5.048
652.6 | 50.5 | -5.048
652.7 | 50.5 | -5.048
652.8 | 50.5 | -5.048
652.9 | 50.5 | -5.048
653 | 50.5 | -5.048
653.1 | 50.5 | -5.048
653.2 | 50.5 | -5.048
653.3 | 50.5 | -5.048
653.4 | 50.5 | -5.048
653.5 | 50.5 | -5.048
653.6 | 50.5 | -5.048
653.7 | 50.5 | -5.048
653.8 | 50.5 | -5.048
653.9 | 50.5 | -5.048
654 | 50.5 | -5.048
654.1 | 50.5 | -5.048
654.2 | 50.5 | -5.048
654.3 | 50.5 | -5.048
654.4 | 50.5 | -5.048
654.5 | 50.5 | -5.048
654.6 | 50.5 | -5.048
654.7 | 50.5 | -5.048
654.8 | 50.5 | -5.048
654.9 | 50.5 | -5.048
655 | 50.5 | -5.048
655.1 | 50.5 | -5.048
655.2 | 50.5 | -5.048
655.3 | 50.5 | -5.048
655.4 | 50.5 | -5.048
655.5 | 50.5 | -5.048
655.6 | 50.5 | -5.048
655.7 | 50.5 | -5.048
655.8 | 50.5 | -5.048
655.9 | 50.5 | -5.048
656 | 50.5 | -5.048
656.1 | 50.5 | -5.048
656.2 | 50.5 | -5.048
656.3 | 50.5 | -5.048
656.4 | 50.5 | -5.048
656.5 | 50.5 | -5.048
656.6 | 50.5 | -5.048
656.7 | 50.5 | -5.048
656.8 | 50.5 | -5.048
656.9 | 50.5 | -5.048
657 | 50.5 | -5.048
657.1 | 50.5 | -5.048
657.2 | 50.5 | -5.048
657.3 | 50.5 | -5.048
657.4 | 50.5 | -5.048
657.5 | 50.5 | -5.048
657.6 | 50.5 | -5.048
657.7 | 50.5 | -5.048
657.8 | 50.5 | -5.048
657.9 | 50.5 | -5.048
658 | 50.5 | -5.048
658.1 | 50.5 | -5.048
658.2 | 50.5 | -5.048
658.3 | 50.5 | -5.048
658.4 | 50.5 | -5.048
658.5 | 50.5 | -5.048
658.6 | 50.5 | -5.048
658.7 | 50.5 | -5.048
658.8 | 50.5 | -5.048
658.9 | 50.5 | -5.048
659 | 50.5 | -5.048
659.1 | 50.5 | -5.048
659.2 | 50.5 | -5.048
659.3 | 50.5 | -5.048
659.4 | 50.5 | -5.048
659.5 | 50.5 | -5.048
659.6 | 50.5 | -5.048
659.7 | 50.5 | -5.048
659.8 | 50.5 | -5.048
659.9 | 50.5 | -5.048
660 | 50.5 | -5.048
660.1 | 50.5 | -5.048
660.2 | 50.5 | -5.048
660.3 | 50.5 | -5.048
660.4 | 50.5 | -5.048
660.5 | 50.5 | -5.048
660.6 | 50.5 | -5.048
660.7 | 50.5 | -5.048
660.8 | 50.5 | -5.048
660.9 | 50.5 | -5.048
661 | 50.5 | -5.048
661.1 | 50.5 | -5.048
661.2 | 50.5 | -5.048
661.3 | 50.5 | -5.048
661.4 | 50.5 | -5.048
661.5 | 50.5 | -5.048
661.6 | 50.5 | -5.048
661.7 | 50.5 | -5.048
661.8 | 50.5 | -5.048
661.9 | 50.5 | -5.048
662 | 50.5 | -5.048
662.1 | 50.5 | -5.048
662.2 | 50.5 | -5.048
662.3 | 50.5 | -5.048
662.4 | 50.5 | -5.048
662.5 | 50.5 | -5.048
662.6 | 50.5 | -5.048
662.7 | 50.5 | -5.048
662.8 | 50.5 | -5.048
662.9 | 50.5 | -5.048
663 | 50.5 | -5.048
663.1 | 50.5 | -5.048
663.2 | 50.5 | -5.048
663.3 | 50.5 | -5.048
663.4 | 50.5 | -5.048
663.5 | 50.5 | -5.048
663.6 | 50.5 | -5.048
663.7 | 50.5 | -5.048
663.8 | 50.5 | -5.048
663.9 | 50.5 | -5.048
664 | 50.5 | -5.048
664.1 | 50.5 | -5.048
664.2 | 50.5 | -5.048
664.3 | 50.5 | -5.048
664.4 | 50.5 | -5.048
664.5 | 50.5 | -5.048
664.6 | 50.5 | -5.048
664.7 | 50.5 | -5.048
664.8 | 50.5 | -5.048
664.9 | 50.5 | -5.048
665 | 50.5 | -5.048
665.1 | 50.5 | -5.048
665.2 | 50.5 | -5.048
665.3 | 50.5 | -5.048
665.4 | 50.5 | -5.048
665.5 | 50.5 | -5.048
665.6 | 50.5 | -5.048
665.7 | 50.5 | -5.048
665.8 | 50.5 | -5.048
665.9 | 50.5 | -5.048
666 | 50.5 | -5.048
666.1 | 50.5 | -5.048
666.2 | 50.5 | -5.048
666.3 | 50.5 | -5.048
666.4 | 50.5 | -5.048
666.5 | 50.5 | -5.048
666.6 | 50.5 | -5.048
666.7 | 50.5 | -5.048
666.8 | 50.5 | -5.048
666.9 | 50.5 | -5.048
667 | 50.5 | -5.048
667.1 | 50.5 | -5.048
667.2 | 50.5 | -5.048
667.3 | 50.5 | -5.048
667.4 | 50.5 | -5.048
667.5 | 50.5 | -5.048
667.6 | 50.5 | -5.048
667.7 | 50.5 | -5.048
667.8 | 50.5 | -5.048
667.9 | 50.5 | -5.048
668 | 50.5 | -5.048
668.1 | 50.5 | -5.048
668.2 | 50.5 | -5.048
668.3 | 50.5 | -5.048
668.4 | 50.5 | -5.048
668.5 | 50.5 | -5.048
668.6 | 50.5 | -5.048
668.7 | 50.5 | -5.048
668.8 | 50.5 | -5.048
668.9 | 50.5 | -5.048
669 | 50.5 | -5.048
669.1 | 50.5 | -5.048
669.2 | 50.5 | -5.048
669.3 | 50.5 | -5.048
669.4 | 50.5 | -5.048
669.5 | 50.5 | -5.048
669.6 | 50.5 | -5.048
669.7 | 50.5 | -5.048
669.8 | 50.5 | -5.048
669.9 | 50.5 | -5.048
670 | 50.5 | -5.048
670.1 | 50.5 | -5.048
670.2 | 50.5 | -5.048
670.3 | 50.5 | -5.048
670.4 | 50.5 | -5.048
670.5 | 50.5 | -5.048
670.6 | 50.5 | -5.048
670.7 | 50.5 | -5.048
670.8 | 50.5 | -5.048
670.9 | 50.5 | -5.048
671 | 50.5 | -5.048
671.1 | 50.5 | -5.048
671.2 | 50.5 | -5.048
671.3 | 50.5 | -5.048
671.4 | 50.5 | -5.048
671.5 | 50.5 | -5.048
671.6 | 50.5 | -5.048
671.7 | 50.5 | -5.048
671.8 | 50.5 | -5.048
671.9 | 50.5 | -5.048
672 | 50.5 | -5.048
672.1 | 50.5 | -5.048
672.2 | 50.5 | -5.048
672.3 | 50.5 | -5.048
672.4 | 50.5 | -5.048
672.5 | 50.5 | -5.048
672.6 | 50.5 | -5.048
672.7 | 50.5 | -5.048
672.8 | 50.5 | -5.048
672.9 | 50.5 | -5.048
673 | 50.5 | -5.048
673.1 | 50.5 | -5.048
673.2 | 50.5 | -5.048
673.3 | 50.5 | -5.048
673.4 | 50.5 | -5.048
673.5 | 50.5 | -5.048
673.6 | 50.5 | -5.048
673.7 | 50.5 | -5.048
673.8 | 50.5 | -5.048
673.9 | 50.5 | -5.048
674 | 50.5 | -5.048
674.1 | 50.5 | -5.048
674.2 | 50.5 | -5.048
674.3 | 50.5 | -5.048
674.4 | 50.5 | -5.048
674.5 | 50.5 | -5.048
674.6 | 50.5 | -5.048
674.7 | 50.5 | -5.048
674.8 | 50.5 | -5.048
674.9 | 50.5 | -5.048
675 | 50.5 | -5.048
675.1 | 50.5 | -5.048
675.2 | 50.5 | -5.048
675.3 | 50.5 | -5.048
675.4 | 50.5 | -5.048
675.5 | 50.5 | -5.048
675.6 | 50.5 | -5.048
675.7 | 50.5 | -5.048
675.8 | 50.5 | -5.048
675.9 | 50.5 | -5.048
676 | 50.5 | -5.048
676.1 | 50.5 | -5.048
676.2 | 50.5 | -5.047
676.3 | 50.5 | -5.047
676.4 | 50.5 | -5.047
676.5 | 50.5 | -5.047
676.6 | 50.5 | -5.047
676.7 | 50.5 | -5.047
676.8 | 50.5 | -5.047
676.9 | 50.5 | -5.047
677 | 50.5 | -5.047
677.1 | 50.5 | -5.047
677.2 | 50.5 | -5.047
677.3 | 50.5 | -5.047
677.4 | 50.5 | -5.047
677.5 | 50.5 | -5.047
677.6 | 50.5 | -5.047
677.7 | 50.5 | -5.047
677.8 | 50.5 | -5.047
677.9 | 50.5 | -5.047
678 | 50.5 | -5.047
678.1 | 50.5 | -5.047
678.2 | 50.5 | -5.047
678.3 | 50.5 | -5.047
678.4 | 50.5 | -5.048
678.5 | 50.5 | -5.048
678.6 | 50.5 | -5.048
678.7 | 50.5 | -5.048
678.8 | 50.5 | -5.048
678.9 | 50.5 | -5.048
679 | 50.5 | -5.048
679.1 | 50.5 | -5.048
679.2 | 50.5 | -5.048
679.3 | 50.5 | -5.048
679.4 | 50.5 | -5.048
679.5 | 50.5 | -5.048
679.6 | 50.5 | -5.048
679.7 | 50.5 | -5.048
679.8 | 50.5 | -5.048
679.9 | 50.5 | -5.048
680 | 50.5 | -5.048
680.1 | 50.5 | -5.048
680.2 | 50.5 | -5.048
680.3 | 50.5 | -5.048
680.4 | 50.5 | -5.048
680.5 | 50.5 | -5.048
680.6 | 50.5 | -5.048
680.7 | 50.5 | -5.048
680.8 | 50.5 | -5.048
680.9 | 50.5 | -5.048
681 | 50.5 | -5.048
681.1 | 50.5 | -5.048
681.2 | 50.5 | -5.048
681.3 | 50.5 | -5.048
681.4 | 50.5 | -5.048
681.5 | 50.5 | -5.048
681.6 | 50.5 | -5.048
681.7 | 50.5 | -5.048
681.8 | 50.5 | -5.048
681.9 | 50.5 | -5.048
682 | 50.5 | -5.048
682.1 | 50.5 | -5.048
682.2 | 50.5 | -5.048
682.3 | 50.5 | -5.048
682.4 | 50.5 | -5.048
682.5 | 50.5 | -5.048
682.6 | 50.5 | -5.048
682.7 | 50.5 | -5.048
682.8 | 50.5 | -5.048
682.9 | 50.5 | -5.048
683 | 50.5 | -5.048
683.1 | 50.5 | -5.048
683.2 | 50.5 | -5.048
683.3 | 50.5 | -5.048
683.4 | 50.5 | -5.048
683.5 | 50.5 | -5.048
683.6 | 50.5 | -5.048
683.7 | 50.5 | -5.048
683.8 | 50.5 | -5.048
683.9 | 50.5 | -5.048
684 | 50.5 | -5.048
684.1 | 50.5 | -5.048
684.2 | 50.5 | -5.048
684.3 | 50.5 | -5.048
684.4 | 50.5 | -5.048
684.5 | 50.5 | -5.048
684.6 | 50.5 | -5.048
684.7 | 50.5 | -5.048
684.8 | 50.5 | -5.048
684.9 | 50.5 | -5.048
685 | 50.5 | -5.048
685.1 | 50.5 | -5.048
685.2 | 50.5 | -5.048
685.3 | 50.5 | -5.048
685.4 | 50.5 | -5.048
685.5 | 50.5 | -5.048
685.6 | 50.5 | -5.048
685.7 | 50.5 | -5.048
685.8 | 50.5 | -5.048
685.9 | 50.5 | -5.048
686 | 50.5 | -5.048
686.1 | 50.5 | -5.048
686.2 | 50.5 | -5.048
686.3 | 50.5 | -5.048
686.4 | 50.5 | -5.048
686.5 | 50.5 | -5.048
686.6 | 50.5 | -5.048
686.7 | 50.5 | -5.048
686.8 | 50.5 | -5.048
686.9 | 50.5 | -5.048
687 | 50.5 | -5.048
687.1 | 50.5 | -5.048
687.2 | 50.5 | -5.048
687.3 | 50.5 | -5.048
687.4 | 50.5 | -5.048
687.5 | 50.5 | -5.048
687.6 | 50.5 | -5.048
687.7 | 50.5 | -5.048
687.8 | 50.5 | -5.048
687.9 | 50.5 | -5.048
688 | 50.5 | -5.048
688.1 | 50.5 | -5.048
688.2 | 50.5 | -5.048
688.3 | 50.5 | -5.048
688.4 | 50.5 | -5.048
688.5 | 50.5 | -5.048
688.6 | 50.5 | -5.048
688.7 | 50.5 | -5.048
688.8 | 50.5 | -5.048
688.9 | 50.5 | -5.048
689 | 50.5 | -5.048
689.1 | 50.5 | -5.048
689.2 | 50.5 | -5.048
689.3 | 50.5 | -5.048
689.4 | 50.5 | -5.048
689.5 | 50.5 | -5.048
689.6 | 50.5 | -5.048
689.7 | 50.5 | -5.048
689.8 | 50.5 | -5.048
689.9 | 50.5 | -5.048
690 | 50.5 | -5.048
690.1 | 50.5 | -5.048
690.2 | 50.5 | -5.048
690.3 | 50.5 | -5.048
690.4 | 50.5 | -5.048
690.5 | 50.5 | -5.048
690.6 | 50.5 | -5.048
690.7 | 50.5 | -5.048
690.8 | 50.5 | -5.048
690.9 | 50.5 | -5.048
691 | 50.5 | -5.048
691.1 | 50.5 | -5.048
691.2 | 50.5 | -5.048
691.3 | 50.5 | -5.048
691.4 | 50.5 | -5.048
691.5 | 50.5 | -5.048
691.6 | 50.5 | -5.048
691.7 | 50.5 | -5.048
691.8 | 50.5 | -5.048
691.9 | 50.5 | -5.048
692 | 50.5 | -5.048
692.1 | 50.5 | -5.048
692.2 | 50.5 | -5.048
692.3 | 50.5 | -5.048
692.4 | 50.5 | -5.048
692.5 | 50.5 | -5.048
692.6 | 50.5 | -5.048
692.7 | 50.5 | -5.048
692.8 | 50.5 | -5.048
692.9 | 50.5 | -5.048
693 | 50.5 | -5.048
693.1 | 50.5 | -5.048
693.2 | 50.5 | -5.048
693.3 | 50.5 | -5.048
693.4 | 50.5 | -5.048
693.5 | 50.5 | -5.048
693.6 | 50.5 | -5.048
693.7 | 50.5 | -5.048
693.8 | 50.5 | -5.048
693.9 | 50.5 | -5.048
694 | 50.5 | -5.048
694.1 | 50.5 | -5.048
694.2 | 50.5 | -5.048
694.3 | 50.5 | -5.048
694.4 | 50.5 | -5.048
694.5 | 50.5 | -5.048
694.6 | 50.5 | -5.048
694.7 | 50.5 | -5.048
694.8 | 50.5 | -5.048
694.9 | 50.5 | -5.048
695 | 50.5 | -5.048
695.1 | 50.5 | -5.048
695.2 | 50.5 | -5.048
695.3 | 50.5 | -5.048
695.4 | 50.5 | -5.048
695.5 | 50.5 | -5.048
695.6 | 50.5 | -5.048
695.7 | 50.5 | -5.048
695.8 | 50.5 | -5.047
695.9 | 50.5 | -5.047
696 | 50.5 | -5.047
696.1 | 50.5 | -5.047
696.2 | 50.5 | -5.047
696.3 | 50.5 | -5.047
696.4 | 50.5 | -5.047
696.5 | 50.5 | -5.047
696.6 | 50.5 | -5.047
696.7 | 50.5 | -5.047
696.8 | 50.5 | -5.047
696.9 | 50.5 | -5.048
697 | 50.5 | -5.048
697.1 | 50.5 | -5.048
697.2 | 50.5 | -5.048
697.3 | 50.5 | -5.048
697.4 | 50.5 | -5.048
697.5 | 50.5 | -5.048
697.6 | 50.5 | -5.048
697.7 | 50.5 | -5.048
697.8 | 50.5 | -5.048
697.9 | 50.5 | -5.048
698 | 50.5 | -5.048
698.1 | 50.5 | -5.048
698.2 | 50.5 | -5.048
698.3 | 50.5 | -5.048
698.4 | 50.5 | -5.048
698.5 | 50.5 | -5.048
698.6 | 50.5 | -5.048
698.7 | 50.5 | -5.048
698.8 | 50.5 | -5.048
698.9 | 50.5 | -5.048
699 | 50.5 | -5.048
699.1 | 50.5 | -5.048
699.2 | 50.5 | -5.048
699.3 | 50.5 | -5.048
699.4 | 50.5 | -5.048
699.5 | 50.5 | -5.048
699.6 | 50.5 | -5.048
699.7 | 50.5 | -5.048
699.8 | 50.5 | -5.048
699.9 | 50.5 | -5.048
700 | 50.5 | -5.048
700.1 | 50.5 | -5.048
700.2 | 50.5 | -5.048
700.3 | 50.5 | -5.048
700.4 | 50.5 | -5.048
700.5 | 50.5 | -5.048
700.6 | 50.5 | -5.048
700.7 | 50.5 | -5.048
700.8 | 50.5 | -5.048
700.9 | 50.5 | -5.048
701 | 50.5 | -5.048
701.1 | 50.5 | -5.048
701.2 | 50.5 | -5.048
701.3 | 50.5 | -5.048
701.4 | 50.5 | -5.048
701.5 | 50.5 | -5.048
701.6 | 50.5 | -5.048
701.7 | 50.5 | -5.047
701.8 | 50.5 | -5.047
701.9 | 50.5 | -5.047
702 | 50.5 | -5.047
702.1 | 50.5 | -5.047
702.2 | 50.5 | -5.047
702.3 | 50.5 | -5.047
702.4 | 50.5 | -5.047
702.5 | 50.5 | -5.047
702.6 | 50.5 | -5.047
702.7 | 50.5 | -5.047
702.8 | 50.5 | -5.047
702.9 | 50.5 | -5.048
703 | 50.5 | -5.048
703.1 | 50.5 | -5.048
703.2 | 50.5 | -5.048
703.3 | 50.5 | -5.048
703.4 | 50.5 | -5.048
703.5 | 50.5 | -5.048
703.6 | 50.5 | -5.048
703.7 | 50.5 | -5.048
703.8 | 50.5 | -5.048
703.9 | 50.5 | -5.048
704 | 50.5 | -5.048
704.1 | 50.5 | -5.048
704.2 | 50.5 | -5.048
704.3 | 50.5 | -5.048
704.4 | 50.5 | -5.048
704.5 | 50.5 | -5.048
704.6 | 50.5 | -5.048
704.7 | 50.5 | -5.048
704.8 | 50.5 | -5.048
704.9 | 50.5 | -5.048
705 | 50.5 | -5.048
705.1 | 50.5 | -5.048
705.2 | 50.5 | -5.048
705.3 | 50.5 | -5.048
705.4 | 50.5 | -5.048
705.5 | 50.5 | -5.048
705.6 | 50.5 | -5.048
705.7 | 50.5 | -5.048
705.8 | 50.5 | -5.048
705.9 | 50.5 | -5.048
706 | 50.5 | -5.048
706.1 | 50.5 | -5.048
706.2 | 50.5 | -5.048
706.3 | 50.5 | -5.048
706.4 | 50.5 | -5.048
706.5 | 50.5 | -5.048
706.6 | 50.5 | -5.048
706.7 | 50.5 | -5.048
706.8 | 50.5 | -5.048
706.9 | 50.5 | -5.048
707 | 50.5 | -5.048
707.1 | 50.5 | -5.048
707.2 | 50.5 | -5.048
707.3 | 50.5 | -5.048
707.4 | 50.5 | -5.048
707.5 | 50.5 | -5.048
707.6 | 50.5 | -5.048
707.7 | 50.5 | -5.048
707.8 | 50.5 | -5.048
707.9 | 50.5 | -5.048
708 | 50.5 | -5.048
708.1 | 50.5 | -5.048
708.2 | 50.5 | -5.048
708.3 | 50.5 | -5.048
708.4 | 50.5 | -5.048
708.5 | 50.5 | -5.048
708.6 | 50.5 | -5.048
708.7 | 50.5 | -5.047
708.8 | 50.5 | -5.047
708.9 | 50.5 | -5.047
709 | 50.5 | -5.047
709.1 | 50.5 | -5.047
709.2 | 50.5 | -5.047
709.3 | 50.5 | -5.047
709.4 | 50.5 | -5.047
709.5 | 50.5 | -5.047
709.6 | 50.5 | -5.047
709.7 | 50.5 | -5.047
709.8 | 50.5 | -5.047
709.9 | 50.5 | -5.047
710 | 50.5 | -5.047
710.1 | 50.5 | -5.047
710.2 | 50.5 | -5.047
710.3 | 50.5 | -5.047
710.4 | 50.5 | -5.047
710.5 | 50.5 | -5.047
710.6 | 50.5 | -5.047
710.7 | 50.5 | -5.047
710.8 | 50.5 | -5.047
710.9 | 50.5 | -5.047
711 | 50.5 | -5.047
711.1 | 50.5 | -5.047
711.2 | 50.5 | -5.048
711.3 | 50.5 | -5.048
711.4 | 50.5 | -5.048
711.5 | 50.5 | -5.048
711.6 | 50.5 | -5.048
711.7 | 50.5 | -5.048
711.8 | 50.5 | -5.048
711.9 | 50.5 | -5.048
712 | 50.5 | -5.048
712.1 | 50.5 | -5.048
712.2 | 50.5 | -5.048
712.3 | 50.5 | -5.048
712.4 | 50.5 | -5.048
712.5 | 50.5 | -5.048
712.6 | 50.5 | -5.048
712.7 | 50.5 | -5.048
712.8 | 50.5 | -5.048
712.9 | 50.5 | -5.048
713 | 50.5 | -5.048
713.1 | 50.5 | -5.048
713.2 | 50.5 | -5.048
713.3 | 50.5 | -5.048
713.4 | 50.5 | -5.048
713.5 | 50.5 | -5.048
713.6 | 50.5 | -5.048
713.7 | 50.5 | -5.048
713.8 | 50.5 | -5.048
713.9 | 50.5 | -5.048
714 | 50.5 | -5.048
714.1 | 50.5 | -5.048
714.2 | 50.5 | -5.048
714.3 | 50.5 | -5.048
714.4 | 50.5 | -5.048
714.5 | 50.5 | -5.048
714.6 | 50.5 | -5.048
714.7 | 50.5 | -5.048
714.8 | 50.5 | -5.048
714.9 | 50.5 | -5.048
715 | 50.5 | -5.048
715.1 | 50.5 | -5.048
715.2 | 50.5 | -5.048
715.3 | 50.5 | -5.048
715.4 | 50.5 | -5.048
715.5 | 50.5 | -5.048
715.6 | 50.5 | -5.048
715.7 | 50.5 | -5.047
715.8 | 50.5 | -5.047
715.9 | 50.5 | -5.047
716 | 50.5 | -5.047
716.1 | 50.5 | -5.047
716.2 | 50.5 | -5.047
716.3 | 50.5 | -5.047
716.4 | 50.5 | -5.047
716.5 | 50.5 | -5.047
716.6 | 50.5 | -5.047
716.7 | 50.5 | -5.047
716.8 | 50.5 | -5.047
716.9 | 50.5 | -5.047
717 | 50.5 | -5.047
717.1 | 50.5 | -5.048
717.2 | 50.5 | -5.048
717.3 | 50.5 | -5.048
717.4 | 50.5 | -5.048
717.5 | 50.5 | -5.048
717.6 | 50.5 | -5.048
717.7 | 50.5 | -5.048
717.8 | 50.5 | -5.048
717.9 | 50.5 | -5.048
718 | 50.5 | -5.048
718.1 | 50.5 | -5.049
718.2 | 50.5 | -5.049
718.3 | 50.5 | -5.049
718.4 | 50.5 | -5.049
718.5 | 50.5 | -5.049
718.6 | 50.5 | -5.049
718.7 | 50.5 | -5.049
718.8 | 50.5 | -5.049
718.9 | 50.5 | -5.049
719 | 50.5 | -5.049
719.1 | 50.5 | -5.049
719.2 | 50.5 | -5.049
719.3 | 50.5 | -5.048
719.4 | 50.5 | -5.048
719.5 | 50.5 | -5.048
719.6 | 50.5 | -5.048
719.7 | 50.5 | -5.048
719.8 | 50.5 | -5.048
719.9 | 50.5 | -5.048
720 | 50.5 | -5.048
720.1 | 50.5 | -5.048
720.2 | 50.5 | -5.048
720.3 | 50.5 | -5.048
720.4 | 50.5 | -5.048
720.5 | 50.5 | -5.048
720.6 | 50.5 | -5.048
720.7 | 50.5 | -5.048
720.8 | 50.5 | -5.048
720.9 | 50.5 | -5.048
721 | 50.5 | -5.048
721.1 | 50.5 | -5.048
721.2 | 50.5 | -5.048
721.3 | 50.5 | -5.048
721.4 | 50.5 | -5.048
721.5 | 50.5 | -5.048
721.6 | 50.5 | -5.048
721.7 | 50.5 | -5.048
721.8 | 50.5 | -5.048
721.9 | 50.5 | -5.048
722 | 50.5 | -5.048
722.1 | 50.5 | -5.048
722.2 | 50.5 | -5.048
722.3 | 50.5 | -5.048
722.4 | 50.5 | -5.048
722.5 | 50.5 | -5.048
722.6 | 50.5 | -5.048
722.7 | 50.5 | -5.048
722.8 | 50.5 | -5.048
722.9 | 50.5 | -5.048
723 | 50.5 | -5.048
723.1 | 50.5 | -5.048
723.2 | 50.5 | -5.048
723.3 | 50.5 | -5.048
723.4 | 50.5 | -5.048
723.5 | 50.5 | -5.048
723.6 | 50.5 | -5.048
723.7 | 50.5 | -5.048
723.8 | 50.5 | -5.048
723.9 | 50.5 | -5.048
724 | 50.5 | -5.048
724.1 | 50.5 | -5.048
724.2 | 50.5 | -5.048
724.3 | 50.5 | -5.048
724.4 | 50.5 | -5.048
724.5 | 50.5 | -5.048
724.6 | 50.5 | -5.048
724.7 | 50.5 | -5.048
724.8 | 50.5 | -5.048
724.9 | 50.5 | -5.048
725 | 50.5 | -5.048
725.1 | 50.5 | -5.048
725.2 | 50.5 | -5.048
725.3 | 50.5 | -5.048
725.4 | 50.5 | -5.048
725.5 | 50.5 | -5.048
725.6 | 50.5 | -5.048
725.7 | 50.5 | -5.048
725.8 | 50.5 | -5.048
725.9 | 50.5 | -5.048
726 | 50.5 | -5.048
726.1 | 50.5 | -5.048
726.2 | 50.5 | -5.048
726.3 | 50.5 | -5.048
726.4 | 50.5 | -5.048
726.5 | 50.5 | -5.048
726.6 | 50.5 | -5.048
726.7 | 50.5 | -5.048
726.8 | 50.5 | -5.048
726.9 | 50.5 | -5.048
727 | 50.5 | -5.048
727.1 | 50.5 | -5.048
727.2 | 50.5 | -5.048
727.3 | 50.5 | -5.048
727.4 | 50.5 | -5.048
727.5 | 50.5 | -5.048
727.6 | 50.5 | -5.048
727.7 | 50.5 | -5.048
727.8 | 50.5 | -5.048
727.9 | 50.5 | -5.048
728 | 50.5 | -5.048
728.1 | 50.5 | -5.048
728.2 | 50.5 | -5.048
728.3 | 50.5 | -5.048
728.4 | 50.5 | -5.048
728.5 | 50.5 | -5.048
728.6 | 50.5 | -5.048
728.7 | 50.5 | -5.048
728.8 | 50.5 | -5.048
728.9 | 50.5 | -5.048
729 | 50.5 | -5.048
729.1 | 50.5 | -5.048
729.2 | 50.5 | -5.048
729.3 | 50.5 | -5.048
729.4 | 50.5 | -5.048
729.5 | 50.5 | -5.048
729.6 | 50.5 | -5.048
729.7 | 50.5 | -5.048
729.8 | 50.5 | -5.048
729.9 | 50.5 | -5.048
730 | 50.5 | -5.048
730.1 | 50.5 | -5.048
730.2 | 50.5 | -5.048
730.3 | 50.5 | -5.048
730.4 | 50.5 | -5.048
730.5 | 50.5 | -5.048
730.6 | 50.5 | -5.048
730.7 | 50.5 | -5.048
730.8 | 50.5 | -5.048
730.9 | 50.5 | -5.048
731 | 50.5 | -5.048
731.1 | 50.5 | -5.048
731.2 | 50.5 | -5.048
731.3 | 50.5 | -5.048
731.4 | 50.5 | -5.048
731.5 | 50.5 | -5.048
731.6 | 50.5 | -5.048
731.7 | 50.5 | -5.048
731.8 | 50.5 | -5.048
731.9 | 50.5 | -5.048
732 | 50.5 | -5.048
732.1 | 50.5 | -5.048
732.2 | 50.5 | -5.048
732.3 | 50.5 | -5.048
732.4 | 50.5 | -5.048
732.5 | 50.5 | -5.048
732.6 | 50.5 | -5.048
732.7 | 50.5 | -5.048
732.8 | 50.5 | -5.048
732.9 | 50.5 | -5.048
733 | 50.5 | -5.048
733.1 | 50.5 | -5.048
733.2 | 50.5 | -5.048
733.3 | 50.5 | -5.048
733.4 | 50.5 | -5.048
733.5 | 50.5 | -5.048
733.6 | 50.5 | -5.048
733.7 | 50.5 | -5.048
733.8 | 50.5 | -5.048
733.9 | 50.5 | -5.048
734 | 50.5 | -5.048
734.1 | 50.5 | -5.048
734.2 | 50.5 | -5.048
734.3 | 50.5 | -5.048
734.4 | 50.5 | -5.048
734.5 | 50.5 | -5.048
734.6 | 50.5 | -5.048
734.7 | 50.5 | -5.048
734.8 | 50.5 | -5.048
734.9 | 50.5 | -5.048
735 | 50.5 | -5.048
735.1 | 50.5 | -5.048
735.2 | 50.5 | -5.048
735.3 | 50.5 | -5.048
735.4 | 50.5 | -5.048
735.5 | 50.5 | -5.048
735.6 | 50.5 | -5.048
735.7 | 50.5 | -5.048
735.8 | 50.5 | -5.047
735.9 | 50.5 | -5.047
736 | 50.5 | -5.047
736.1 | 50.5 | -5.047
736.2 | 50.5 | -5.047
736.3 | 50.5 | -5.047
736.4 | 50.5 | -5.047
736.5 | 50.5 | -5.047
736.6 | 50.5 | -5.047
736.7 | 50.5 | -5.047
736.8 | 50.5 | -5.047
736.9 | 50.5 | -5.048
737 | 50.5 | -5.048
737.1 | 50.5 | -5.048
737.2 | 50.5 | -5.048
737.3 | 50.5 | -5.048
737.4 | 50.5 | -5.048
737.5 | 50.5 | -5.048
737.6 | 50.5 | -5.048
737.7 | 50.5 | -5.048
737.8 | 50.5 | -5.048
737.9 | 50.5 | -5.048
738 | 50.5 | -5.048
738.1 | 50.5 | -5.048
738.2 | 50.5 | -5.048
738.3 | 50.5 | -5.048
738.4 | 50.5 | -5.048
738.5 | 50.5 | -5.048
738.6 | 50.5 | -5.048
738.7 | 50.5 | -5.048
738.8 | 50.5 | -5.048
738.9 | 50.5 | -5.048
739 | 50.5 | -5.048
739.1 | 50.5 | -5.048
739.2 | 50.5 | -5.048
739.3 | 50.5 | -5.048
739.4 | 50.5 | -5.048
739.5 | 50.5 | -5.048
739.6 | 50.5 | -5.048
739.7 | 50.5 | -5.048
739.8 | 50.5 | -5.048
739.9 | 50.5 | -5.048
740 | 50.5 | -5.048
740.1 | 50.5 | -5.048
740.2 | 50.5 | -5.048
740.3 | 50.5 | -5.048
740.4 | 50.5 | -5.049
740.5 | 50.5 | -5.049
740.6 | 50.5 | -5.049
740.7 | 50.5 | -5.049
740.8 | 50.5 | -5.049
740.9 | 50.5 | -5.049
741 | 50.5 | -5.049
741.1 | 50.5 | -5.049
741.2 | 50.5 | -5.049
741.3 | 50.5 | -5.049
741.4 | 50.5 | -5.049
741.5 | 50.5 | -5.048
741.6 | 50.5 | -5.048
741.7 | 50.5 | -5.048
741.8 | 50.5 | -5.048
741.9 | 50.5 | -5.048
742 | 50.5 | -5.048
742.1 | 50.5 | -5.048
742.2 | 50.5 | -5.048
742.3 | 50.5 | -5.048
742.4 | 50.5 | -5.048
742.5 | 50.5 | -5.048
742.6 | 50.5 | -5.047
742.7 | 50.5 | -5.047
742.8 | 50.5 | -5.047
742.9 | 50.5 | -5.047
743 | 50.5 | -5.047
743.1 | 50.5 | -5.047
743.2 | 50.5 | -5.047
743.3 | 50.5 | -5.047
743.4 | 50.5 | -5.047
743.5 | 50.5 | -5.047
743.6 | 50.5 | -5.048
743.7 | 50.5 | -5.048
743.8 | 50.5 | -5.047
743.9 | 50.5 | -5.047
744 | 50.5 | -5.047
744.1 | 50.5 | -5.047
744.2 | 50.5 | -5.047
744.3 | 50.5 | -5.047
744.4 | 50.5 | -5.047
744.5 | 50.5 | -5.047
744.6 | 50.5 | -5.047
744.7 | 50.5 | -5.047
744.8 | 50.5 | -5.047
744.9 | 50.5 | -5.047
745 | 50.5 | -5.047
745.1 | 50.5 | -5.047
745.2 | 50.5 | -5.047
745.3 | 50.5 | -5.047
745.4 | 50.5 | -5.047
745.5 | 50.5 | -5.047
745.6 | 50.5 | -5.047
745.7 | 50.5 | -5.047
745.8 | 50.5 | -5.047
745.9 | 50.5 | -5.047
746 | 50.5 | -5.047
746.1 | 50.5 | -5.047
746.2 | 50.5 | -5.048
746.3 | 50.5 | -5.048
746.4 | 50.5 | -5.048
746.5 | 50.5 | -5.048
746.6 | 50.5 | -5.048
746.7 | 50.5 | -5.048
746.8 | 50.5 | -5.048
746.9 | 50.5 | -5.048
747 | 50.5 | -5.048
747.1 | 50.5 | -5.048
747.2 | 50.5 | -5.048
747.3 | 50.5 | -5.048
747.4 | 50.5 | -5.048
747.5 | 50.5 | -5.048
747.6 | 50.5 | -5.048
747.7 | 50.5 | -5.048
747.8 | 50.5 | -5.048
747.9 | 50.5 | -5.048
748 | 50.5 | -5.048
748.1 | 50.5 | -5.048
748.2 | 50.5 | -5.048
748.3 | 50.5 | -5.048
748.4 | 50.5 | -5.048
748.5 | 50.5 | -5.048
748.6 | 50.5 | -5.047
748.7 | 50.5 | -5.047
748.8 | 50.5 | -5.047
748.9 | 50.5 | -5.047
749 | 50.5 | -5.047
749.1 | 50.5 | -5.047
749.2 | 50.5 | -5.047
749.3 | 50.5 | -5.047
749.4 | 50.5 | -5.047
749.5 | 50.5 | -5.047
749.6 | 50.5 | -5.047
749.7 | 50.5 | -5.047
749.8 | 50.5 | -5.047
749.9 | 50.5 | -5.048
750 | 50.5 | -5.048
750.1 | 50.5 | -5.048
750.2 | 50.5 | -5.048
750.3 | 50.5 | -5.048
750.4 | 50.5 | -5.048
750.5 | 50.5 | -5.048
750.6 | 50.5 | -5.048
750.7 | 50.5 | -5.048
750.8 | 50.5 | -5.048
750.9 | 50.5 | -5.048
751 | 50.5 | -5.048
751.1 | 50.5 | -5.048
751.2 | 50.5 | -5.048
751.3 | 50.5 | -5.048
751.4 | 50.5 | -5.048
751.5 | 50.5 | -5.048
751.6 | 50.5 | -5.048
751.7 | 50.5 | -5.048
751.8 | 50.5 | -5.048
751.9 | 50.5 | -5.048
752 | 50.5 | -5.048
752.1 | 50.5 | -5.048
752.2 | 50.5 | -5.048
752.3 | 50.5 | -5.048
752.4 | 50.5 | -5.048
752.5 | 50.5 | -5.048
752.6 | 50.5 | -5.048
752.7 | 50.5 | -5.048
752.8 | 50.5 | -5.048
752.9 | 50.5 | -5.048
753 | 50.5 | -5.048
753.1 | 50.5 | -5.048
753.2 | 50.5 | -5.048
753.3 | 50.5 | -5.048
753.4 | 50.5 | -5.048
753.5 | 50.5 | -5.048
753.6 | 50.5 | -5.048
753.7 | 50.5 | -5.048
753.8 | 50.5 | -5.048
753.9 | 50.5 | -5.048
754 | 50.5 | -5.048
754.1 | 50.5 | -5.048
754.2 | 50.5 | -5.048
754.3 | 50.5 | -5.048
754.4 | 50.5 | -5.048
754.5 | 50.5 | -5.048
754.6 | 50.5 | -5.048
754.7 | 50.5 | -5.048
754.8 | 50.5 | -5.048
754.9 | 50.5 | -5.048
755 | 50.5 | -5.048
755.1 | 50.5 | -5.048
755.2 | 50.5 | -5.048
755.3 | 50.5 | -5.048
755.4 | 50.5 | -5.048
755.5 | 50.5 | -5.047
755.6 | 50.5 | -5.047
755.7 | 50.5 | -5.047
755.8 | 50.5 | -5.047
755.9 | 50.5 | -5.047
756 | 50.5 | -5.047
756.1 | 50.5 | -5.047
756.2 | 50.5 | -5.047
756.3 | 50.5 | -5.047
756.4 | 50.5 | -5.047
756.5 | 50.5 | -5.047
756.6 | 50.5 | -5.047
756.7 | 50.5 | -5.048
756.8 | 50.5 | -5.048
756.9 | 50.5 | -5.048
757 | 50.5 | -5.048
757.1 | 50.5 | -5.048
757.2 | 50.5 | -5.048
757.3 | 50.5 | -5.048
757.4 | 50.5 | -5.048
757.5 | 50.5 | -5.048
757.6 | 50.5 | -5.048
757.7 | 50.5 | -5.048
757.8 | 50.5 | -5.048
757.9 | 50.5 | -5.048
758 | 50.5 | -5.048
758.1 | 50.5 | -5.048
758.2 | 50.5 | -5.048
758.3 | 50.5 | -5.048
758.4 | 50.5 | -5.048
758.5 | 50.5 | -5.048
758.6 | 50.5 | -5.048
758.7 | 50.5 | -5.048
758.8 | 50.5 | -5.048
758.9 | 50.5 | -5.048
759 | 50.5 | -5.048
759.1 | 50.5 | -5.048
759.2 | 50.5 | -5.048
759.3 | 50.5 | -5.048
759.4 | 50.5 | -5.048
759.5 | 50.5 | -5.048
759.6 | 50.5 | -5.048
759.7 | 50.5 | -5.048
759.8 | 50.5 | -5.048
759.9 | 50.5 | -5.048
760 | 50.5 | -5.048
760.1 | 50.5 | -5.048
760.2 | 50.5 | -5.048
760.3 | 50.5 | -5.048
760.4 | 50.5 | -5.048
760.5 | 50.5 | -5.048
760.6 | 50.5 | -5.048
760.7 | 50.5 | -5.048
760.8 | 50.5 | -5.048
760.9 | 50.5 | -5.048
761 | 50.5 | -5.048
761.1 | 50.5 | -5.048
761.2 | 50.5 | -5.048
761.3 | 50.5 | -5.048
761.4 | 50.5 | -5.047
761.5 | 50.5 | -5.047
761.6 | 50.5 | -5.047
761.7 | 50.5 | -5.047
761.8 | 50.5 | -5.047
761.9 | 50.5 | -5.047
762 | 50.5 | -5.047
762.1 | 50.5 | -5.047
762.2 | 50.5 | -5.047
762.3 | 50.5 | -5.047
762.4 | 50.5 | -5.047
762.5 | 50.5 | -5.048
762.6 | 50.5 | -5.048
762.7 | 50.5 | -5.048
762.8 | 50.5 | -5.048
762.9 | 50.5 | -5.048
763 | 50.5 | -5.048
763.1 | 50.5 | -5.048
763.2 | 50.5 | -5.048
763.3 | 50.5 | -5.048
763.4 | 50.5 | -5.048
763.5 | 50.5 | -5.048
763.6 | 50.5 | -5.048
763.7 | 50.5 | -5.048
763.8 | 50.5 | -5.048
763.9 | 50.5 | -5.048
764 | 50.5 | -5.048
764.1 | 50.5 | -5.048
764.2 | 50.5 | -5.048
764.3 | 50.5 | -5.048
764.4 | 50.5 | -5.048
764.5 | 50.5 | -5.048
764.6 | 50.5 | -5.048
764.7 | 50.5 | -5.048
764.8 | 50.5 | -5.048
764.9 | 50.5 | -5.048
765 | 50.5 | -5.048
765.1 | 50.5 | -5.049
765.2 | 50.5 | -5.049
765.3 | 50.5 | -5.049
765.4 | 50.5 | -5.049
765.5 | 50.5 | -5.049
765.6 | 50.5 | -5.049
765.7 | 50.5 | -5.049
765.8 | 50.5 | -5.049
765.9 | 50.5 | -5.049
766 | 50.5 | -5.048
766.1 | 50.5 | -5.048
766.2 | 50.5 | -5.048
766.3 | 50.5 | -5.048
766.4 | 50.5 | -5.048
766.5 | 50.5 | -5.048
766.6 | 50.5 | -5.048
766.7 | 50.5 | -5.048
766.8 | 50.5 | -5.048
766.9 | 50.5 | -5.048
767 | 50.5 | -5.048
767.1 | 50.5 | -5.048
767.2 | 50.5 | -5.047
767.3 | 50.5 | -5.047
767.4 | 50.5 | -5.047
767.5 | 50.5 | -5.047
767.6 | 50.5 | -5.047
767.7 | 50.5 | -5.047
767.8 | 50.5 | -5.047
767.9 | 50.5 | -5.047
768 | 50.5 | -5.047
768.1 | 50.5 | -5.047
768.2 | 50.5 | -5.047
768.3 | 50.5 | -5.048
768.4 | 50.5 | -5.048
768.5 | 50.5 | -5.048
768.6 | 50.5 | -5.048
768.7 | 50.5 | -5.048
768.8 | 50.5 | -5.048
768.9 | 50.5 | -5.048
769 | 50.5 | -5.048
769.1 | 50.5 | -5.048
769.2 | 50.5 | -5.048
769.3 | 50.5 | -5.048
769.4 | 50.5 | -5.048
769.5 | 50.5 | -5.048
769.6 | 50.5 | -5.048
769.7 | 50.5 | -5.048
769.8 | 50.5 | -5.048
769.9 | 50.5 | -5.048
770 | 50.5 | -5.048
770.1 | 50.5 | -5.048
770.2 | 50.5 | -5.048
770.3 | 50.5 | -5.048
770.4 | 50.5 | -5.048
770.5 | 50.5 | -5.048
770.6 | 50.5 | -5.048
770.7 | 50.5 | -5.048
770.8 | 50.5 | -5.048
770.9 | 50.5 | -5.048
771 | 50.5 | -5.048
771.1 | 50.5 | -5.048
771.2 | 50.5 | -5.048
771.3 | 50.5 | -5.048
771.4 | 50.5 | -5.048
771.5 | 50.5 | -5.048
771.6 | 50.5 | -5.048
771.7 | 50.5 | -5.048
771.8 | 50.5 | -5.048
771.9 | 50.5 | -5.048
772 | 50.5 | -5.048
772.1 | 50.5 | -5.048
772.2 | 50.5 | -5.048
772.3 | 50.5 | -5.048
772.4 | 50.5 | -5.048
772.5 | 50.5 | -5.048
772.6 | 50.5 | -5.048
772.7 | 50.5 | -5.048
772.8 | 50.5 | -5.048
772.9 | 50.5 | -5.048
773 | 50.5 | -5.048
773.1 | 50.5 | -5.048
773.2 | 50.5 | -5.048
773.3 | 50.5 | -5.048
773.4 | 50.5 | -5.048
773.5 | 50.5 | -5.048
773.6 | 50.5 | -5.048
773.7 | 50.5 | -5.048
773.8 | 50.5 | -5.048
773.9 | 50.5 | -5.048
774 | 50.5 | -5.048
774.1 | 50.5 | -5.048
774.2 | 50.5 | -5.048
774.3 | 50.5 | -5.048
774.4 | 50.5 | -5.048
774.5 | 50.5 | -5.048
774.6 | 50.5 | -5.048
774.7 | 50.5 | -5.048
774.8 | 50.5 | -5.048
774.9 | 50.5 | -5.048
775 | 50.5 | -5.048
775.1 | 50.5 | -5.048
775.2 | 50.5 | -5.048
775.3 | 50.5 | -5.048
775.4 | 50.5 | -5.048
775.5 | 50.5 | -5.048
775.6 | 50.5 | -5.048
775.7 | 50.5 | -5.048
775.8 | 50.5 | -5.048
775.9 | 50.5 | -5.048
776 | 50.5 | -5.048
776.1 | 50.5 | -5.048
776.2 | 50.5 | -5.047
776.3 | 50.5 | -5.047
776.4 | 50.5 | -5.047
776.5 | 50.5 | -5.047
776.6 | 50.5 | -5.047
776.7 | 50.5 | -5.047
776.8 | 50.5 | -5.047
776.9 | 50.5 | -5.047
777 | 50.5 | -5.047
777.1 | 50.5 | -5.047
777.2 | 50.5 | -5.047
777.3 | 50.5 | -5.047
777.4 | 50.5 | -5.047
777.5 | 50.5 | -5.047
777.6 | 50.5 | -5.047
777.7 | 50.5 | -5.047
777.8 | 50.5 | -5.047
777.9 | 50.5 | -5.047
778 | 50.5 | -5.047
778.1 | 50.5 | -5.047
778.2 | 50.5 | -5.047
778.3 | 50.5 | -5.047
778.4 | 50.5 | -5.047
778.5 | 50.5 | -5.047
778.6 | 50.5 | -5.047
778.7 | 50.5 | -5.047
778.8 | 50.5 | -5.047
778.9 | 50.5 | -5.047
779 | 50.5 | -5.047
779.1 | 50.5 | -5.047
779.2 | 50.5 | -5.047
779.3 | 50.5 | -5.047
779.4 | 50.5 | -5.047
779.5 | 50.5 | -5.047
779.6 | 50.5 | -5.048
779.7 | 50.5 | -5.048
779.8 | 50.5 | -5.048
779.9 | 50.5 | -5.048
780 | 50.5 | -5.048
780.1 | 50.5 | -5.048
780.2 | 50.5 | -5.048
780.3 | 50.5 | -5.048
780.4 | 50.5 | -5.048
780.5 | 50.5 | -5.048
780.6 | 50.5 | -5.048
780.7 | 50.5 | -5.048
780.8 | 50.5 | -5.048
780.9 | 50.5 | -5.048
781 | 50.5 | -5.048
781.1 | 50.5 | -5.048
781.2 | 50.5 | -5.048
781.3 | 50.5 | -5.048
781.4 | 50.5 | -5.048
781.5 | 50.5 | -5.048
781.6 | 50.5 | -5.048
781.7 | 50.5 | -5.048
781.8 | 50.5 | -5.048
781.9 | 50.5 | -5.048
782 | 50.5 | -5.048
782.1 | 50.5 | -5.048
782.2 | 50.5 | -5.048
782.3 | 50.5 | -5.048
782.4 | 50.5 | -5.048
782.5 | 50.5 | -5.048
782.6 | 50.5 | -5.048
782.7 | 50.5 | -5.048
782.8 | 50.5 | -5.048
782.9 | 50.5 | -5.048
783 | 50.5 | -5.048
783.1 | 50.5 | -5.048
783.2 | 50.5 | -5.048
783.3 | 50.5 | -5.048
783.4 | 50.5 | -5.048
783.5 | 50.5 | -5.048
783.6 | 50.5 | -5.048
783.7 | 50.5 | -5.048
783.8 | 50.5 | -5.048
783.9 | 50.5 | -5.048
784 | 50.5 | -5.048
784.1 | 50.5 | -5.048
784.2 | 50.5 | -5.048
784.3 | 50.5 | -5.047
784.4 | 50.5 | -5.047
784.5 | 50.5 | -5.047
784.6 | 50.5 | -5.047
784.7 | 50.5 | -5.047
784.8 | 50.5 | -5.047
784.9 | 50.5 | -5.047
785 | 50.5 | -5.047
785.1 | 50.5 | -5.047
785.2 | 50.5 | -5.047
785.3 | 50.5 | -5.047
785.4 | 50.5 | -5.047
785.5 | 50.5 | -5.047
785.6 | 50.5 | -5.047
785.7 | 50.5 | -5.047
785.8 | 50.5 | -5.047
785.9 | 50.5 | -5.047
786 | 50.5 | -5.047
786.1 | 50.5 | -5.047
786.2 | 50.5 | -5.047
786.3 | 50.5 | -5.047
786.4 | 50.5 | -5.047
786.5 | 50.5 | -5.047
786.6 | 50.5 | -5.047
786.7 | 50.5 | -5.047
786.8 | 50.5 | -5.047
786.9 | 50.5 | -5.047
787 | 50.5 | -5.047
787.1 | 50.5 | -5.047
787.2 | 50.5 | -5.047
787.3 | 50.5 | -5.047
787.4 | 50.5 | -5.047
787.5 | 50.5 | -5.047
787.6 | 50.5 | -5.047
787.7 | 50.5 | -5.047
787.8 | 50.5 | -5.047
787.9 | 50.5 | -5.047
788 | 50.5 | -5.047
788.1 | 50.5 | -5.047
788.2 | 50.5 | -5.047
788.3 | 50.5 | -5.048
788.4 | 50.5 | -5.048
788.5 | 50.5 | -5.048
788.6 | 50.5 | -5.048
788.7 | 50.5 | -5.048
788.8 | 50.5 | -5.048
788.9 | 50.5 | -5.048
789 | 50.5 | -5.048
789.1 | 50.5 | -5.048
789.2 | 50.5 | -5.048
789.3 | 50.5 | -5.048
789.4 | 50.5 | -5.048
789.5 | 50.5 | -5.048
789.6 | 50.5 | -5.048
789.7 | 50.5 | -5.048
789.8 | 50.5 | -5.048
789.9 | 50.5 | -5.048
790 | 50.5 | -5.048
790.1 | 50.5 | -5.048
790.2 | 50.5 | -5.048
790.3 | 50.5 | -5.048
790.4 | 50.5 | -5.048
790.5 | 50.5 | -5.048
790.6 | 50.5 | -5.048
790.7 | 50.5 | -5.048
790.8 | 50.5 | -5.048
790.9 | 50.5 | -5.048
791 | 50.5 | -5.048
791.1 | 50.5 | -5.048
791.2 | 50.5 | -5.048
791.3 | 50.5 | -5.048
791.4 | 50.5 | -5.048
791.5 | 50.5 | -5.048
791.6 | 50.5 | -5.048
791.7 | 50.5 | -5.048
791.8 | 50.5 | -5.047
791.9 | 50.5 | -5.047
792 | 50.5 | -5.047
792.1 | 50.5 | -5.047
792.2 | 50.5 | -5.047
792.3 | 50.5 | -5.047
792.4 | 50.5 | -5.047
792.5 | 50.5 | -5.047
792.6 | 50.5 | -5.047
792.7 | 50.5 | -5.047
792.8 | 50.5 | -5.047
792.9 | 50.5 | -5.047
793 | 50.5 | -5.047
793.1 | 50.5 | -5.047
793.2 | 50.5 | -5.047
793.3 | 50.5 | -5.047
793.4 | 50.5 | -5.047
793.5 | 50.5 | -5.047
793.6 | 50.5 | -5.047
793.7 | 50.5 | -5.047
793.8 | 50.5 | -5.047
793.9 | 50.5 | -5.047
794 | 50.5 | -5.047
794.1 | 50.5 | -5.047
794.2 | 50.5 | -5.048
794.3 | 50.5 | -5.048
794.4 | 50.5 | -5.048
794.5 | 50.5 | -5.048
794.6 | 50.5 | -5.048
794.7 | 50.5 | -5.048
794.8 | 50.5 | -5.048
794.9 | 50.5 | -5.048
795 | 50.5 | -5.048
795.1 | 50.5 | -5.048
795.2 | 50.5 | -5.048
795.3 | 50.5 | -5.048
795.4 | 50.5 | -5.048
795.5 | 50.5 | -5.048
795.6 | 50.5 | -5.048
795.7 | 50.5 | -5.048
795.8 | 50.5 | -5.048
795.9 | 50.5 | -5.048
796 | 50.5 | -5.048
796.1 | 50.5 | -5.048
796.2 | 50.5 | -5.048
796.3 | 50.5 | -5.048
796.4 | 50.5 | -5.048
796.5 | 50.5 | -5.048
796.6 | 50.5 | -5.048
796.7 | 50.5 | -5.048
796.8 | 50.5 | -5.048
796.9 | 50.5 | -5.048
797 | 50.5 | -5.048
797.1 | 50.5 | -5.048
797.2 | 50.5 | -5.048
797.3 | 50.5 | -5.048
797.4 | 50.5 | -5.048
797.5 | 50.5 | -5.048
797.6 | 50.5 | -5.048
797.7 | 50.5 | -5.048
797.8 | 50.5 | -5.048
797.9 | 50.5 | -5.048
798 | 50.5 | -5.048
798.1 | 50.5 | -5.048
798.2 | 50.5 | -5.048
798.3 | 50.5 | -5.048
798.4 | 50.5 | -5.048
798.5 | 50.5 | -5.048
798.6 | 50.5 | -5.048
798.7 | 50.5 | -5.048
798.8 | 50.5 | -5.048
798.9 | 50.5 | -5.048
799 | 50.5 | -5.048
799.1 | 50.5 | -5.048
799.2 | 50.5 | -5.048
799.3 | 50.5 | -5.048
799.4 | 50.5 | -5.048
799.5 | 50.5 | -5.048
799.6 | 50.5 | -5.048
799.7 | 50.5 | -5.048
799.8 | 50.5 | -5.048
799.9 | 50.5 | -5.048
800 | 50.5 | -5.048
800.1 | 50.5 | -5.048
800.2 | 50.5 | -5.048
800.3 | 50.5 | -5.048
800.4 | 50.5 | -5.048
800.5 | 50.5 | -5.048
800.6 | 50.5 | -5.048
800.7 | 50.5 | -5.048
800.8 | 50.5 | -5.048
800.9 | 50.5 | -5.048
801 | 50.5 | -5.048
801.1 | 50.5 | -5.048
801.2 | 50.5 | -5.048
801.3 | 50.5 | -5.048
801.4 | 50.5 | -5.048
801.5 | 50.5 | -5.048
801.6 | 50.5 | -5.048
801.7 | 50.5 | -5.048
801.8 | 50.5 | -5.048
801.9 | 50.5 | -5.048
802 | 50.5 | -5.048
802.1 | 50.5 | -5.048
802.2 | 50.5 | -5.048
802.3 | 50.5 | -5.048
802.4 | 50.5 | -5.048
802.5 | 50.5 | -5.048
802.6 | 50.5 | -5.048
802.7 | 50.5 | -5.048
802.8 | 50.5 | -5.048
802.9 | 50.5 | -5.048
803 | 50.5 | -5.048
803.1 | 50.5 | -5.048
803.2 | 50.5 | -5.048
803.3 | 50.5 | -5.048
803.4 | 50.5 | -5.048
803.5 | 50.5 | -5.048
803.6 | 50.5 | -5.047
803.7 | 50.5 | -5.047
803.8 | 50.5 | -5.047
803.9 | 50.5 | -5.047
804 | 50.5 | -5.047
804.1 | 50.5 | -5.047
804.2 | 50.5 | -5.047
804.3 | 50.5 | -5.047
804.4 | 50.5 | -5.047
804.5 | 50.5 | -5.047
804.6 | 50.5 | -5.047
804.7 | 50.5 | -5.047
804.8 | 50.5 | -5.048
804.9 | 50.5 | -5.048
805 | 50.5 | -5.048
805.1 | 50.5 | -5.048
805.2 | 50.5 | -5.048
805.3 | 50.5 | -5.048
805.4 | 50.5 | -5.048
805.5 | 50.5 | -5.048
805.6 | 50.5 | -5.048
805.7 | 50.5 | -5.048
805.8 | 50.5 | -5.048
805.9 | 50.5 | -5.048
806 | 50.5 | -5.048
806.1 | 50.5 | -5.048
806.2 | 50.5 | -5.048
806.3 | 50.5 | -5.048
806.4 | 50.5 | -5.048
806.5 | 50.5 | -5.048
806.6 | 50.5 | -5.048
806.7 | 50.5 | -5.048
806.8 | 50.5 | -5.048
806.9 | 50.5 | -5.048
807 | 50.5 | -5.048
807.1 | 50.5 | -5.048
807.2 | 50.5 | -5.048
807.3 | 50.5 | -5.048
807.4 | 50.5 | -5.048
807.5 | 50.5 | -5.048
807.6 | 50.5 | -5.048
807.7 | 50.5 | -5.048
807.8 | 50.5 | -5.048
807.9 | 50.5 | -5.048
808 | 50.5 | -5.048
808.1 | 50.5 | -5.048
808.2 | 50.5 | -5.048
808.3 | 50.5 | -5.048
808.4 | 50.5 | -5.048
808.5 | 50.5 | -5.048
808.6 | 50.5 | -5.048
808.7 | 50.5 | -5.048
808.8 | 50.5 | -5.048
808.9 | 50.5 | -5.048
809 | 50.5 | -5.048
809.1 | 50.5 | -5.048
809.2 | 50.5 | -5.048
809.3 | 50.5 | -5.048
809.4 | 50.5 | -5.048
809.5 | 50.5 | -5.048
809.6 | 50.5 | -5.048
809.7 | 50.5 | -5.048
809.8 | 50.5 | -5.048
809.9 | 50.5 | -5.048
810 | 50.5 | -5.048
810.1 | 50.5 | -5.048
810.2 | 50.5 | -5.048
810.3 | 50.5 | -5.048
810.4 | 50.5 | -5.048
810.5 | 50.5 | -5.048
810.6 | 50.5 | -5.048
810.7 | 50.5 | -5.048
810.8 | 50.5 | -5.048
810.9 | 50.5 | -5.048
811 | 50.5 | -5.048
811.1 | 50.5 | -5.048
811.2 | 50.5 | -5.048
811.3 | 50.5 | -5.048
811.4 | 50.5 | -5.048
811.5 | 50.5 | -5.048
811.6 | 50.5 | -5.048
811.7 | 50.5 | -5.048
811.8 | 50.5 | -5.048
811.9 | 50.5 | -5.048
812 | 50.5 | -5.048
812.1 | 50.5 | -5.048
812.2 | 50.5 | -5.048
812.3 | 50.5 | -5.048
812.4 | 50.5 | -5.048
812.5 | 50.5 | -5.048
812.6 | 50.5 | -5.048
812.7 | 50.5 | -5.048
812.8 | 50.5 | -5.048
812.9 | 50.5 | -5.048
813 | 50.5 | -5.048
813.1 | 50.5 | -5.048
813.2 | 50.5 | -5.048
813.3 | 50.5 | -5.048
813.4 | 50.5 | -5.048
813.5 | 50.5 | -5.048
813.6 | 50.5 | -5.048
813.7 | 50.5 | -5.048
813.8 | 50.5 | -5.048
813.9 | 50.5 | -5.048
814 | 50.5 | -5.048
814.1 | 50.5 | -5.048
814.2 | 50.5 | -5.048
814.3 | 50.5 | -5.048
814.4 | 50.5 | -5.048
814.5 | 50.5 | -5.048
814.6 | 50.5 | -5.048
814.7 | 50.5 | -5.048
814.8 | 50.5 | -5.048
814.9 | 50.5 | -5.048
815 | 50.5 | -5.048
815.1 | 50.5 | -5.048
815.2 | 50.5 | -5.048
815.3 | 50.5 | -5.048
815.4 | 50.5 | -5.048
815.5 | 50.5 | -5.048
815.6 | 50.5 | -5.048
815.7 | 50.5 | -5.048
815.8 | 50.5 | -5.048
815.9 | 50.5 | -5.048
816 | 50.5 | -5.048
816.1 | 50.5 | -5.048
816.2 | 50.5 | -5.048
816.3 | 50.5 | -5.048
816.4 | 50.5 | -5.048
816.5 | 50.5 | -5.048
816.6 | 50.5 | -5.048
816.7 | 50.5 | -5.048
816.8 | 50.5 | -5.048
816.9 | 50.5 | -5.048
817 | 50.5 | -5.048
817.1 | 50.5 | -5.048
817.2 | 50.5 | -5.048
817.3 | 50.5 | -5.048
817.4 | 50.5 | -5.048
817.5 | 50.5 | -5.048
817.6 | 50.5 | -5.048
817.7 | 50.5 | -5.048
817.8 | 50.5 | -5.047
817.9 | 50.5 | -5.047
818 | 50.5 | -5.047
818.1 | 50.5 | -5.047
818.2 | 50.5 | -5.047
818.3 | 50.5 | -5.047
818.4 | 50.5 | -5.047
818.5 | 50.5 | -5.047
818.6 | 50.5 | -5.047
818.7 | 50.5 | -5.047
818.8 | 50.5 | -5.047
818.9 | 50.5 | -5.047
819 | 50.5 | -5.047
819.1 | 50.5 | -5.047
819.2 | 50.5 | -5.047
819.3 | 50.5 | -5.047
819.4 | 50.5 | -5.047
819.5 | 50.5 | -5.047
819.6 | 50.5 | -5.047
819.7 | 50.5 | -5.047
819.8 | 50.5 | -5.047
819.9 | 50.5 | -5.047
820 | 50.5 | -5.048
820.1 | 50.5 | -5.048
820.2 | 50.5 | -5.048
820.3 | 50.5 | -5.048
820.4 | 50.5 | -5.048
820.5 | 50.5 | -5.048
820.6 | 50.5 | -5.048
820.7 | 50.5 | -5.048
820.8 | 50.5 | -5.048
820.9 | 50.5 | -5.048
821 | 50.5 | -5.048
821.1 | 50.5 | -5.048
821.2 | 50.5 | -5.048
821.3 | 50.5 | -5.048
821.4 | 50.5 | -5.048
821.5 | 50.5 | -5.048
821.6 | 50.5 | -5.048
821.7 | 50.5 | -5.048
821.8 | 50.5 | -5.048
821.9 | 50.5 | -5.048
822 | 50.5 | -5.048
822.1 | 50.5 | -5.048
822.2 | 50.5 | -5.048
822.3 | 50.5 | -5.048
822.4 | 50.5 | -5.048
822.5 | 50.5 | -5.048
822.6 | 50.5 | -5.048
822.7 | 50.5 | -5.048
822.8 | 50.5 | -5.048
822.9 | 50.5 | -5.048
823 | 50.5 | -5.048
823.1 | 50.5 | -5.048
823.2 | 50.5 | -5.048
823.3 | 50.5 | -5.048
823.4 | 50.5 | -5.048
823.5 | 50.5 | -5.048
823.6 | 50.5 | -5.048
823.7 | 50.5 | -5.048
823.8 | 50.5 | -5.048
823.9 | 50.5 | -5.048
824 | 50.5 | -5.048
824.1 | 50.5 | -5.048
824.2 | 50.5 | -5.048
824.3 | 50.5 | -5.048
824.4 | 50.5 | -5.048
824.5 | 50.5 | -5.048
824.6 | 50.5 | -5.048
824.7 | 50.5 | -5.048
824.8 | 50.5 | -5.048
824.9 | 50.5 | -5.048
825 | 50.5 | -5.048
825.1 | 50.5 | -5.048
825.2 | 50.5 | -5.048
825.3 | 50.5 | -5.048
825.4 | 50.5 | -5.048
825.5 | 50.5 | -5.048
825.6 | 50.5 | -5.048
825.7 | 50.5 | -5.048
825.8 | 50.5 | -5.048
825.9 | 50.5 | -5.048
826 | 50.5 | -5.048
826.1 | 50.5 | -5.048
826.2 | 50.5 | -5.048
826.3 | 50.5 | -5.048
826.4 | 50.5 | -5.048
826.5 | 50.5 | -5.048
826.6 | 50.5 | -5.048
826.7 | 50.5 | -5.048
826.8 | 50.5 | -5.048
826.9 | 50.5 | -5.048
827 | 50.5 | -5.048
827.1 | 50.5 | -5.048
827.2 | 50.5 | -5.048
827.3 | 50.5 | -5.048
827.4 | 50.5 | -5.048
827.5 | 50.5 | -5.048
827.6 | 50.5 | -5.048
827.7 | 50.5 | -5.048
827.8 | 50.5 | -5.048
827.9 | 50.5 | -5.048
828 | 50.5 | -5.048
828.1 | 50.5 | -5.048
828.2 | 50.5 | -5.048
828.3 | 50.5 | -5.048
828.4 | 50.5 | -5.048
828.5 | 50.5 | -5.048
828.6 | 50.5 | -5.047
828.7 | 50.5 | -5.047
828.8 | 50.5 | -5.047
828.9 | 50.5 | -5.047
829 | 50.5 | -5.047
829.1 | 50.5 | -5.047
829.2 | 50.5 | -5.047
829.3 | 50.5 | -5.047
829.4 | 50.5 | -5.047
829.5 | 50.5 | -5.047
829.6 | 50.5 | -5.048
829.7 | 50.5 | -5.048
829.8 | 50.5 | -5.048
829.9 | 50.5 | -5.048
830 | 50.5 | -5.048
830.1 | 50.5 | -5.048
830.2 | 50.5 | -5.048
830.3 | 50.5 | -5.048
830.4 | 50.5 | -5.048
830.5 | 50.5 | -5.048
830.6 | 50.5 | -5.048
830.7 | 50.5 | -5.048
830.8 | 50.5 | -5.048
830.9 | 50.5 | -5.048
831 | 50.5 | -5.048
831.1 | 50.5 | -5.048
831.2 | 50.5 | -5.048
831.3 | 50.5 | -5.048
831.4 | 50.5 | -5.048
831.5 | 50.5 | -5.048
831.6 | 50.5 | -5.048
831.7 | 50.5 | -5.048
831.8 | 50.5 | -5.048
831.9 | 50.5 | -5.048
832 | 50.5 | -5.048
832.1 | 50.5 | -5.048
832.2 | 50.5 | -5.048
832.3 | 50.5 | -5.048
832.4 | 50.5 | -5.048
832.5 | 50.5 | -5.048
832.6 | 50.5 | -5.048
832.7 | 50.5 | -5.048
832.8 | 50.5 | -5.048
832.9 | 50.5 | -5.048
833 | 50.5 | -5.048
833.1 | 50.5 | -5.048
833.2 | 50.5 | -5.048
833.3 | 50.5 | -5.048
833.4 | 50.5 | -5.048
833.5 | 50.5 | -5.048
833.6 | 50.5 | -5.048
833.7 | 50.5 | -5.048
833.8 | 50.5 | -5.048
833.9 | 50.5 | -5.048
834 | 50.5 | -5.048
834.1 | 50.5 | -5.048
834.2 | 50.5 | -5.048
834.3 | 50.5 | -5.048
834.4 | 50.5 | -5.048
834.5 | 50.5 | -5.048
834.6 | 50.5 | -5.048
834.7 | 50.5 | -5.048
834.8 | 50.5 | -5.048
834.9 | 50.5 | -5.048
835 | 50.5 | -5.047
835.1 | 50.5 | -5.047
835.2 | 50.5 | -5.047
835.3 | 50.5 | -5.047
835.4 | 50.5 | -5.047
835.5 | 50.5 | -5.047
835.6 | 50.5 | -5.047
835.7 | 50.5 | -5.047
835.8 | 50.5 | -5.047
835.9 | 50.5 | -5.047
836 | 50.5 | -5.048
836.1 | 50.5 | -5.048
836.2 | 50.5 | -5.048
836.3 | 50.5 | -5.048
836.4 | 50.5 | -5.048
836.5 | 50.5 | -5.048
836.6 | 50.5 | -5.048
836.7 | 50.5 | -5.048
836.8 | 50.5 | -5.048
836.9 | 50.5 | -5.048
837 | 50.5 | -5.048
837.1 | 50.5 | -5.048
837.2 | 50.5 | -5.048
837.3 | 50.5 | -5.048
837.4 | 50.5 | -5.048
837.5 | 50.5 | -5.048
837.6 | 50.5 | -5.048
837.7 | 50.5 | -5.048
837.8 | 50.5 | -5.048
837.9 | 50.5 | -5.048
838 | 50.5 | -5.048
838.1 | 50.5 | -5.048
838.2 | 50.5 | -5.048
838.3 | 50.5 | -5.048
838.4 | 50.5 | -5.048
838.5 | 50.5 | -5.048
838.6 | 50.5 | -5.048
838.7 | 50.5 | -5.048
838.8 | 50.5 | -5.048
838.9 | 50.5 | -5.048
839 | 50.5 | -5.048
839.1 | 50.5 | -5.048
839.2 | 50.5 | -5.048
839.3 | 50.5 | -5.048
839.4 | 50.5 | -5.048
839.5 | 50.5 | -5.048
839.6 | 50.5 | -5.048
839.7 | 50.5 | -5.048
839.8 | 50.5 | -5.048
839.9 | 50.5 | -5.048
840 | 50.5 | -5.048
840.1 | 50.5 | -5.048
840.2 | 50.5 | -5.048
840.3 | 50.5 | -5.048
840.4 | 50.5 | -5.048
840.5 | 50.5 | -5.048
840.6 | 50.5 | -5.048
840.7 | 50.5 | -5.048
840.8 | 50.5 | -5.048
840.9 | 50.5 | -5.048
841 | 50.5 | -5.048
841.1 | 50.5 | -5.048
841.2 | 50.5 | -5.048
841.3 | 50.5 | -5.048
841.4 | 50.5 | -5.048
841.5 | 50.5 | -5.048
841.6 | 50.5 | -5.048
841.7 | 50.5 | -5.048
841.8 | 50.5 | -5.048
841.9 | 50.5 | -5.048
842 | 50.5 | -5.048
842.1 | 50.5 | -5.048
842.2 | 50.5 | -5.048
842.3 | 50.5 | -5.048
842.4 | 50.5 | -5.048
842.5 | 50.5 | -5.048
842.6 | 50.5 | -5.048
842.7 | 50.5 | -5.048
842.8 | 50.5 | -5.048
842.9 | 50.5 | -5.048
843 | 50.5 | -5.048
843.1 | 50.5 | -5.048
843.2 | 50.5 | -5.048
843.3 | 50.5 | -5.048
843.4 | 50.5 | -5.048
843.5 | 50.5 | -5.048
843.6 | 50.5 | -5.047
843.7 | 50.5 | -5.047
843.8 | 50.5 | -5.047
843.9 | 50.5 | -5.047
844 | 50.5 | -5.047
844.1 | 50.5 | -5.047
844.2 | 50.5 | -5.047
844.3 | 50.5 | -5.047
844.4 | 50.5 | -5.047
844.5 | 50.5 | -5.047
844.6 | 50.5 | -5.047
844.7 | 50.5 | -5.047
844.8 | 50.5 | -5.048
844.9 | 50.5 | -5.048
845 | 50.5 | -5.047
845.1 | 50.5 | -5.047
845.2 | 50.5 | -5.047
845.3 | 50.5 | -5.047
845.4 | 50.5 | -5.047
845.5 | 50.5 | -5.047
845.6 | 50.5 | -5.047
845.7 | 50.5 | -5.047
845.8 | 50.5 | -5.047
845.9 | 50.5 | -5.047
846 | 50.5 | -5.047
846.1 | 50.5 | -5.047
846.2 | 50.5 | -5.047
846.3 | 50.5 | -5.047
846.4 | 50.5 | -5.047
846.5 | 50.5 | -5.047
846.6 | 50.5 | -5.047
846.7 | 50.5 | -5.047
846.8 | 50.5 | -5.047
846.9 | 50.5 | -5.047
847 | 50.5 | -5.047
847.1 | 50.5 | -5.047
847.2 | 50.5 | -5.048
847.3 | 50.5 | -5.048
847.4 | 50.5 | -5.048
847.5 | 50.5 | -5.048
847.6 | 50.5 | -5.048
847.7 | 50.5 | -5.048
847.8 | 50.5 | -5.048
847.9 | 50.5 | -5.048
848 | 50.5 | -5.048
848.1 | 50.5 | -5.048
848.2 | 50.5 | -5.048
848.3 | 50.5 | -5.048
848.4 | 50.5 | -5.048
848.5 | 50.5 | -5.048
848.6 | 50.5 | -5.048
848.7 | 50.5 | -5.048
848.8 | 50.5 | -5.048
848.9 | 50.5 | -5.048
849 | 50.5 | -5.048
849.1 | 50.5 | -5.048
849.2 | 50.5 | -5.048
849.3 | 50.5 | -5.048
849.4 | 50.5 | -5.048
849.5 | 50.5 | -5.048
849.6 | 50.5 | -5.048
849.7 | 50.5 | -5.048
849.8 | 50.5 | -5.048
849.9 | 50.5 | -5.048
850 | 50.5 | -5.048
850.1 | 50.5 | -5.048
850.2 | 50.5 | -5.048
850.3 | 50.5 | -5.048
850.4 | 50.5 | -5.048
850.5 | 50.5 | -5.048
850.6 | 50.5 | -5.048
850.7 | 50.5 | -5.048
850.8 | 50.5 | -5.048
850.9 | 50.5 | -5.048
851 | 50.5 | -5.048
851.1 | 50.5 | -5.048
851.2 | 50.5 | -5.048
851.3 | 50.5 | -5.048
851.4 | 50.5 | -5.048
851.5 | 50.5 | -5.048
851.6 | 50.5 | -5.048
851.7 | 50.5 | -5.048
851.8 | 50.5 | -5.048
851.9 | 50.5 | -5.048
852 | 50.5 | -5.048
852.1 | 50.5 | -5.048
852.2 | 50.5 | -5.048
852.3 | 50.5 | -5.048
852.4 | 50.5 | -5.048
852.5 | 50.5 | -5.048
852.6 | 50.5 | -5.048
852.7 | 50.5 | -5.048
852.8 | 50.5 | -5.048
852.9 | 50.5 | -5.048
853 | 50.5 | -5.047
853.1 | 50.5 | -5.047
853.2 | 50.5 | -5.047
853.3 | 50.5 | -5.047
853.4 | 50.5 | -5.047
853.5 | 50.5 | -5.047
853.6 | 50.5 | -5.047
853.7 | 50.5 | -5.047
853.8 | 50.5 | -5.047
853.9 | 50.5 | -5.047
854 | 50.5 | -5.047
854.1 | 50.5 | -5.047
854.2 | 50.5 | -5.047
854.3 | 50.5 | -5.048
854.4 | 50.5 | -5.048
854.5 | 50.5 | -5.048
854.6 | 50.5 | -5.048
854.7 | 50.5 | -5.048
854.8 | 50.5 | -5.048
854.9 | 50.5 | -5.048
855 | 50.5 | -5.048
855.1 | 50.5 | -5.048
855.2 | 50.5 | -5.048
855.3 | 50.5 | -5.048
855.4 | 50.5 | -5.048
855.5 | 50.5 | -5.048
855.6 | 50.5 | -5.048
855.7 | 50.5 | -5.048
855.8 | 50.5 | -5.048
855.9 | 50.5 | -5.048
856 | 50.5 | -5.048
856.1 | 50.5 | -5.048
856.2 | 50.5 | -5.048
856.3 | 50.5 | -5.048
856.4 | 50.5 | -5.048
856.5 | 50.5 | -5.048
856.6 | 50.5 | -5.048
856.7 | 50.5 | -5.048
856.8 | 50.5 | -5.048
856.9 | 50.5 | -5.048
857 | 50.5 | -5.048
857.1 | 50.5 | -5.048
857.2 | 50.5 | -5.048
857.3 | 50.5 | -5.048
857.4 | 50.5 | -5.048
857.5 | 50.5 | -5.048
857.6 | 50.5 | -5.048
857.7 | 50.5 | -5.048
857.8 | 50.5 | -5.048
857.9 | 50.5 | -5.048
858 | 50.5 | -5.048
858.1 | 50.5 | -5.048
858.2 | 50.5 | -5.048
858.3 | 50.5 | -5.048
858.4 | 50.5 | -5.048
858.5 | 50.5 | -5.048
858.6 | 50.5 | -5.048
858.7 | 50.5 | -5.048
858.8 | 50.5 | -5.048
858.9 | 50.5 | -5.047
859 | 50.5 | -5.047
859.1 | 50.5 | -5.047
859.2 | 50.5 | -5.047
859.3 | 50.5 | -5.047
859.4 | 50.5 | -5.047
859.5 | 50.5 | -5.047
859.6 | 50.5 | -5.047
859.7 | 50.5 | -5.047
859.8 | 50.5 | -5.047
859.9 | 50.5 | -5.047
860 | 50.5 | -5.048
860.1 | 50.5 | -5.048
860.2 | 50.5 | -5.048
860.3 | 50.5 | -5.048
860.4 | 50.5 | -5.048
860.5 | 50.5 | -5.048
860.6 | 50.5 | -5.048
860.7 | 50.5 | -5.048
860.8 | 50.5 | -5.048
860.9 | 50.5 | -5.048
861 | 50.5 | -5.048
861.1 | 50.5 | -5.048
861.2 | 50.5 | -5.048
861.3 | 50.5 | -5.048
861.4 | 50.5 | -5.048
861.5 | 50.5 | -5.048
861.6 | 50.5 | -5.048
861.7 | 50.5 | -5.048
861.8 | 50.5 | -5.048
861.9 | 50.5 | -5.048
862 | 50.5 | -5.048
862.1 | 50.5 | -5.048
862.2 | 50.5 | -5.048
862.3 | 50.5 | -5.048
862.4 | 50.5 | -5.048
862.5 | 50.5 | -5.048
862.6 | 50.5 | -5.048
862.7 | 50.5 | -5.048
862.8 | 50.5 | -5.048
862.9 | 50.5 | -5.048
863 | 50.5 | -5.048
863.1 | 50.5 | -5.048
863.2 | 50.5 | -5.048
863.3 | 50.5 | -5.048
863.4 | 50.5 | -5.048
863.5 | 50.5 | -5.048
863.6 | 50.5 | -5.048
863.7 | 50.5 | -5.048
863.8 | 50.5 | -5.048
863.9 | 50.5 | -5.048
864 | 50.5 | -5.048
864.1 | 50.5 | -5.048
864.2 | 50.5 | -5.048
864.3 | 50.5 | -5.048
864.4 | 50.5 | -5.048
864.5 | 50.5 | -5.048
864.6 | 50.5 | -5.048
864.7 | 50.5 | -5.048
864.8 | 50.5 | -5.048
864.9 | 50.5 | -5.048
865 | 50.5 | -5.048
865.1 | 50.5 | -5.048
865.2 | 50.5 | -5.048
865.3 | 50.5 | -5.048
865.4 | 50.5 | -5.048
865.5 | 50.5 | -5.048
865.6 | 50.5 | -5.048
865.7 | 50.5 | -5.048
865.8 | 50.5 | -5.048
865.9 | 50.5 | -5.048
866 | 50.5 | -5.048
866.1 | 50.5 | -5.048
866.2 | 50.5 | -5.048
866.3 | 50.5 | -5.048
866.4 | 50.5 | -5.048
866.5 | 50.5 | -5.048
866.6 | 50.5 | -5.048
866.7 | 50.5 | -5.048
866.8 | 50.5 | -5.048
866.9 | 50.5 | -5.048
867 | 50.5 | -5.047
867.1 | 50.5 | -5.047
867.2 | 50.5 | -5.047
867.3 | 50.5 | -5.047
867.4 | 50.5 | -5.047
867.5 | 50.5 | -5.047
867.6 | 50.5 | -5.047
867.7 | 50.5 | -5.047
867.8 | 50.5 | -5.047
867.9 | 50.5 | -5.047
868 | 50.5 | -5.047
868.1 | 50.5 | -5.047
868.2 | 50.5 | -5.047
868.3 | 50.5 | -5.047
868.4 | 50.5 | -5.047
868.5 | 50.5 | -5.047
868.6 | 50.5 | -5.047
868.7 | 50.5 | -5.047
868.8 | 50.5 | -5.047
868.9 | 50.5 | -5.047
869 | 50.5 | -5.047
869.1 | 50.5 | -5.047
869.2 | 50.5 | -5.048
869.3 | 50.5 | -5.048
869.4 | 50.5 | -5.048
869.5 | 50.5 | -5.048
869.6 | 50.5 | -5.048
869.7 | 50.5 | -5.048
869.8 | 50.5 | -5.048
869.9 | 50.5 | -5.048
870 | 50.5 | -5.048
870.1 | 50.5 | -5.048
870.2 | 50.5 | -5.048
870.3 | 50.5 | -5.048
870.4 | 50.5 | -5.048
870.5 | 50.5 | -5.048
870.6 | 50.5 | -5.048
870.7 | 50.5 | -5.048
870.8 | 50.5 | -5.048
870.9 | 50.5 | -5.048
871 | 50.5 | -5.048
871.1 | 50.5 | -5.048
871.2 | 50.5 | -5.048
871.3 | 50.5 | -5.048
871.4 | 50.5 | -5.048
871.5 | 50.5 | -5.048
871.6 | 50.5 | -5.048
871.7 | 50.5 | -5.048
871.8 | 50.5 | -5.048
871.9 | 50.5 | -5.048
872 | 50.5 | -5.048
872.1 | 50.5 | -5.048
872.2 | 50.5 | -5.048
872.3 | 50.5 | -5.048
872.4 | 50.5 | -5.048
872.5 | 50.5 | -5.048
872.6 | 50.5 | -5.048
872.7 | 50.5 | -5.048
872.8 | 50.5 | -5.048
872.9 | 50.5 | -5.048
873 | 50.5 | -5.048
873.1 | 50.5 | -5.048
873.2 | 50.5 | -5.048
873.3 | 50.5 | -5.048
873.4 | 50.5 | -5.048
873.5 | 50.5 | -5.048
873.6 | 50.5 | -5.048
873.7 | 50.5 | -5.048
873.8 | 50.5 | -5.048
873.9 | 50.5 | -5.047
874 | 50.5 | -5.047
874.1 | 50.5 | -5.047
874.2 | 50.5 | -5.047
874.3 | 50.5 | -5.047
874.4 | 50.5 | -5.047
874.5 | 50.5 | -5.047
874.6 | 50.5 | -5.047
874.7 | 50.5 | -5.047
874.8 | 50.5 | -5.047
874.9 | 50.5 | -5.047
875 | 50.5 | -5.047
875.1 | 50.5 | -5.047
875.2 | 50.5 | -5.047
875.3 | 50.5 | -5.047
875.4 | 50.5 | -5.047
875.5 | 50.5 | -5.047
875.6 | 50.5 | -5.047
875.7 | 50.5 | -5.047
875.8 | 50.5 | -5.047
875.9 | 50.5 | -5.047
876 | 50.5 | -5.047
876.1 | 50.5 | -5.047
876.2 | 50.5 | -5.047
876.3 | 50.5 | -5.047
876.4 | 50.5 | -5.048
876.5 | 50.5 | -5.048
876.6 | 50.5 | -5.048
876.7 | 50.5 | -5.048
876.8 | 50.5 | -5.048
876.9 | 50.5 | -5.048
877 | 50.5 | -5.048
877.1 | 50.5 | -5.048
877.2 | 50.5 | -5.048
877.3 | 50.5 | -5.048
877.4 | 50.5 | -5.048
877.5 | 50.5 | -5.048
877.6 | 50.5 | -5.048
877.7 | 50.5 | -5.048
877.8 | 50.5 | -5.048
877.9 | 50.5 | -5.048
878 | 50.5 | -5.048
878.1 | 50.5 | -5.048
878.2 | 50.5 | -5.048
878.3 | 50.5 | -5.048
878.4 | 50.5 | -5.048
878.5 | 50.5 | -5.048
878.6 | 50.5 | -5.048
878.7 | 50.5 | -5.048
878.8 | 50.5 | -5.048
878.9 | 50.5 | -5.048
879 | 50.5 | -5.048
879.1 | 50.5 | -5.048
879.2 | 50.5 | -5.048
879.3 | 50.5 | -5.048
879.4 | 50.5 | -5.048
879.5 | 50.5 | -5.048
879.6 | 50.5 | -5.048
879.7 | 50.5 | -5.048
879.8 | 50.5 | -5.048
879.9 | 50.5 | -5.048
880 | 50.5 | -5.048
880.1 | 50.5 | -5.048
880.2 | 50.5 | -5.048
880.3 | 50.5 | -5.048
880.4 | 50.5 | -5.048
880.5 | 50.5 | -5.048
880.6 | 50.5 | -5.048
880.7 | 50.5 | -5.048
880.8 | 50.5 | -5.048
880.9 | 50.5 | -5.048
881 | 50.5 | -5.047
881.1 | 50.5 | -5.047
881.2 | 50.5 | -5.047
881.3 | 50.5 | -5.047
881.4 | 50.5 | -5.047
881.5 | 50.5 | -5.047
881.6 | 50.5 | -5.047
881.7 | 50.5 | -5.047
881.8 | 50.5 | -5.047
881.9 | 50.5 | -5.047
882 | 50.5 | -5.047
882.1 | 50.5 | -5.047
882.2 | 50.5 | -5.048
882.3 | 50.5 | -5.048
882.4 | 50.5 | -5.048
882.5 | 50.5 | -5.048
882.6 | 50.5 | -5.048
882.7 | 50.5 | -5.048
882.8 | 50.5 | -5.048
882.9 | 50.5 | -5.048
883 | 50.5 | -5.048
883.1 | 50.5 | -5.048
883.2 | 50.5 | -5.048
883.3 | 50.5 | -5.048
883.4 | 50.5 | -5.048
883.5 | 50.5 | -5.048
883.6 | 50.5 | -5.048
883.7 | 50.5 | -5.048
883.8 | 50.5 | -5.048
883.9 | 50.5 | -5.048
884 | 50.5 | -5.048
884.1 | 50.5 | -5.048
884.2 | 50.5 | -5.048
884.3 | 50.5 | -5.048
884.4 | 50.5 | -5.048
884.5 | 50.5 | -5.047
884.6 | 50.5 | -5.047
884.7 | 50.5 | -5.047
884.8 | 50.5 | -5.047
884.9 | 50.5 | -5.047
885 | 50.5 | -5.047
885.1 | 50.5 | -5.047
885.2 | 50.5 | -5.047
885.3 | 50.5 | -5.047
885.4 | 50.5 | -5.047
885.5 | 50.5 | -5.047
885.6 | 50.5 | -5.047
885.7 | 50.5 | -5.047
885.8 | 50.5 | -5.047
885.9 | 50.5 | -5.047
886 | 50.5 | -5.047
886.1 | 50.5 | -5.047
886.2 | 50.5 | -5.047
886.3 | 50.5 | -5.047
886.4 | 50.5 | -5.047
886.5 | 50.5 | -5.047
886.6 | 50.5 | -5.047
886.7 | 50.5 | -5.047
886.8 | 50.5 | -5.047
886.9 | 50.5 | -5.047
887 | 50.5 | -5.047
887.1 | 50.5 | -5.047
887.2 | 50.5 | -5.047
887.3 | 50.5 | -5.047
887.4 | 50.5 | -5.047
887.5 | 50.5 | -5.047
887.6 | 50.5 | -5.047
887.7 | 50.5 | -5.047
887.8 | 50.5 | -5.047
887.9 | 50.5 | -5.047
888 | 50.5 | -5.047
888.1 | 50.5 | -5.047
888.2 | 50.5 | -5.047
888.3 | 50.5 | -5.047
888.4 | 50.5 | -5.047
888.5 | 50.5 | -5.047
888.6 | 50.5 | -5.047
888.7 | 50.5 | -5.047
888.8 | 50.5 | -5.047
888.9 | 50.5 | -5.047
889 | 50.5 | -5.047
889.1 | 50.5 | -5.048
889.2 | 50.5 | -5.048
889.3 | 50.5 | -5.048
889.4 | 50.5 | -5.048
889.5 | 50.5 | -5.048
889.6 | 50.5 | -5.048
889.7 | 50.5 | -5.048
889.8 | 50.5 | -5.048
889.9 | 50.5 | -5.048
890 | 50.5 | -5.048
890.1 | 50.5 | -5.048
890.2 | 50.5 | -5.049
890.3 | 50.5 | -5.048
890.4 | 50.5 | -5.048
890.5 | 50.5 | -5.048
890.6 | 50.5 | -5.048
890.7 | 50.5 | -5.048
890.8 | 50.5 | -5.048
890.9 | 50.5 | -5.048
891 | 50.5 | -5.048
891.1 | 50.5 | -5.048
891.2 | 50.5 | -5.048
891.3 | 50.5 | -5.048
891.4 | 50.5 | -5.048
891.5 | 50.5 | -5.047
891.6 | 50.5 | -5.047
891.7 | 50.5 | -5.047
891.8 | 50.5 | -5.047
891.9 | 50.5 | -5.047
892 | 50.5 | -5.047
892.1 | 50.5 | -5.047
892.2 | 50.5 | -5.047
892.3 | 50.5 | -5.047
892.4 | 50.5 | -5.047
892.5 | 50.5 | -5.047
892.6 | 50.5 | -5.047
892.7 | 50.5 | -5.047
892.8 | 50.5 | -5.048
892.9 | 50.5 | -5.048
893 | 50.5 | -5.048
893.1 | 50.5 | -5.048
893.2 | 50.5 | -5.048
893.3 | 50.5 | -5.048
893.4 | 50.5 | -5.048
893.5 | 50.5 | -5.048
893.6 | 50.5 | -5.048
893.7 | 50.5 | -5.048
893.8 | 50.5 | -5.048
893.9 | 50.5 | -5.048
894 | 50.5 | -5.048
894.1 | 50.5 | -5.048
894.2 | 50.5 | -5.048
894.3 | 50.5 | -5.048
894.4 | 50.5 | -5.048
894.5 | 50.5 | -5.048
894.6 | 50.5 | -5.048
894.7 | 50.5 | -5.048
894.8 | 50.5 | -5.048
894.9 | 50.5 | -5.048
895 | 50.5 | -5.048
895.1 | 50.5 | -5.048
895.2 | 50.5 | -5.048
895.3 | 50.5 | -5.048
895.4 | 50.5 | -5.048
895.5 | 50.5 | -5.048
895.6 | 50.5 | -5.048
895.7 | 50.5 | -5.048
895.8 | 50.5 | -5.048
895.9 | 50.5 | -5.048
896 | 50.5 | -5.048
896.1 | 50.5 | -5.048
896.2 | 50.5 | -5.047
896.3 | 50.5 | -5.047
896.4 | 50.5 | -5.047
896.5 | 50.5 | -5.047
896.6 | 50.5 | -5.047
896.7 | 50.5 | -5.047
896.8 | 50.5 | -5.047
896.9 | 50.5 | -5.047
897 | 50.5 | -5.047
897.1 | 50.5 | -5.047
897.2 | 50.5 | -5.047
897.3 | 50.5 | -5.047
897.4 | 50.5 | -5.047
897.5 | 50.5 | -5.047
897.6 | 50.5 | -5.047
897.7 | 50.5 | -5.047
897.8 | 50.5 | -5.047
897.9 | 50.5 | -5.047
898 | 50.5 | -5.047
898.1 | 50.5 | -5.047
898.2 | 50.5 | -5.047
898.3 | 50.5 | -5.047
898.4 | 50.5 | -5.047
898.5 | 50.5 | -5.048
898.6 | 50.5 | -5.048
898.7 | 50.5 | -5.048
898.8 | 50.5 | -5.048
898.9 | 50.5 | -5.048
899 | 50.5 | -5.048
899.1 | 50.5 | -5.048
899.2 | 50.5 | -5.048
899.3 | 50.5 | -5.048
899.4 | 50.5 | -5.048
899.5 | 50.5 | -5.048
899.6 | 50.5 | -5.048
899.7 | 50.5 | -5.048
899.8 | 50.5 | -5.048
899.9 | 50.5 | -5.048
900 | 50.5 | -5.048
900.1 | 50.5 | -5.048
900.2 | 50.5 | -5.048
900.3 | 50.5 | -5.048
900.4 | 50.5 | -5.048
900.5 | 50.5 | -5.048
900.6 | 50.5 | -5.048
900.7 | 50.5 | -5.048
900.8 | 50.5 | -5.048
900.9 | 50.5 | -5.048
901 | 50.5 | -5.048
901.1 | 50.5 | -5.048
901.2 | 50.5 | -5.048
901.3 | 50.5 | -5.048
901.4 | 50.5 | -5.048
901.5 | 50.5 | -5.048
901.6 | 50.5 | -5.048
901.7 | 50.5 | -5.048
901.8 | 50.5 | -5.048
901.9 | 50.5 | -5.047
902 | 50.5 | -5.047
902.1 | 50.5 | -5.047
902.2 | 50.5 | -5.047
902.3 | 50.5 | -5.047
902.4 | 50.5 | -5.047
902.5 | 50.5 | -5.047
902.6 | 50.5 | -5.047
902.7 | 50.5 | -5.047
902.8 | 50.5 | -5.047
902.9 | 50.5 | -5.047
903 | 50.5 | -5.047
903.1 | 50.5 | -5.047
903.2 | 50.5 | -5.047
903.3 | 50.5 | -5.047
903.4 | 50.5 | -5.047
903.5 | 50.5 | -5.047
903.6 | 50.5 | -5.047
903.7 | 50.5 | -5.047
903.8 | 50.5 | -5.047
903.9 | 50.5 | -5.047
904 | 50.5 | -5.047
904.1 | 50.5 | -5.047
904.2 | 50.5 | -5.048
904.3 | 50.5 | -5.048
904.4 | 50.5 | -5.048
904.5 | 50.5 | -5.048
904.6 | 50.5 | -5.048
904.7 | 50.5 | -5.048
904.8 | 50.5 | -5.048
904.9 | 50.5 | -5.048
905 | 50.5 | -5.048
905.1 | 50.5 | -5.048
905.2 | 50.5 | -5.048
905.3 | 50.5 | -5.048
905.4 | 50.5 | -5.048
905.5 | 50.5 | -5.048
905.6 | 50.5 | -5.048
905.7 | 50.5 | -5.048
905.8 | 50.5 | -5.048
905.9 | 50.5 | -5.048
906 | 50.5 | -5.048
906.1 | 50.5 | -5.048
906.2 | 50.5 | -5.048
906.3 | 50.5 | -5.048
906.4 | 50.5 | -5.048
906.5 | 50.5 | -5.048
906.6 | 50.5 | -5.048
906.7 | 50.5 | -5.048
906.8 | 50.5 | -5.048
906.9 | 50.5 | -5.048
907 | 50.5 | -5.048
907.1 | 50.5 | -5.048
907.2 | 50.5 | -5.048
907.3 | 50.5 | -5.048
907.4 | 50.5 | -5.048
907.5 | 50.5 | -5.048
907.6 | 50.5 | -5.048
907.7 | 50.5 | -5.048
907.8 | 50.5 | -5.048
907.9 | 50.5 | -5.048
908 | 50.5 | -5.048
908.1 | 50.5 | -5.048
908.2 | 50.5 | -5.048
908.3 | 50.5 | -5.048
908.4 | 50.5 | -5.048
908.5 | 50.5 | -5.048
908.6 | 50.5 | -5.048
908.7 | 50.5 | -5.048
908.8 | 50.5 | -5.048
908.9 | 50.5 | -5.048
909 | 50.5 | -5.048
909.1 | 50.5 | -5.048
909.2 | 50.5 | -5.048
909.3 | 50.5 | -5.048
909.4 | 50.5 | -5.048
909.5 | 50.5 | -5.048
909.6 | 50.5 | -5.048
909.7 | 50.5 | -5.048
909.8 | 50.5 | -5.048
909.9 | 50.5 | -5.048
910 | 50.5 | -5.048
910.1 | 50.5 | -5.047
910.2 | 50.5 | -5.047
910.3 | 50.5 | -5.047
910.4 | 50.5 | -5.047
910.5 | 50.5 | -5.047
910.6 | 50.5 | -5.047
910.7 | 50.5 | -5.047
910.8 | 50.5 | -5.047
910.9 | 50.5 | -5.047
911 | 50.5 | -5.047
911.1 | 50.5 | -5.047
911.2 | 50.5 | -5.047
911.3 | 50.5 | -5.047
911.4 | 50.5 | -5.047
911.5 | 50.5 | -5.047
911.6 | 50.5 | -5.047
911.7 | 50.5 | -5.047
911.8 | 50.5 | -5.047
911.9 | 50.5 | -5.047
912 | 50.5 | -5.047
912.1 | 50.5 | -5.047
912.2 | 50.5 | -5.047
912.3 | 50.5 | -5.048
912.4 | 50.5 | -5.048
912.5 | 50.5 | -5.048
912.6 | 50.5 | -5.048
912.7 | 50.5 | -5.048
912.8 | 50.5 | -5.048
912.9 | 50.5 | -5.048
913 | 50.5 | -5.048
913.1 | 50.5 | -5.048
913.2 | 50.5 | -5.048
913.3 | 50.5 | -5.048
913.4 | 50.5 | -5.048
913.5 | 50.5 | -5.048
913.6 | 50.5 | -5.048
913.7 | 50.5 | -5.048
913.8 | 50.5 | -5.048
913.9 | 50.5 | -5.048
914 | 50.5 | -5.048
914.1 | 50.5 | -5.048
914.2 | 50.5 | -5.048
914.3 | 50.5 | -5.048
914.4 | 50.5 | -5.048
914.5 | 50.5 | -5.048
914.6 | 50.5 | -5.048
914.7 | 50.5 | -5.048
914.8 | 50.5 | -5.048
914.9 | 50.5 | -5.048
915 | 50.5 | -5.048
915.1 | 50.5 | -5.048
915.2 | 50.5 | -5.048
915.3 | 50.5 | -5.048
915.4 | 50.5 | -5.048
915.5 | 50.5 | -5.048
915.6 | 50.5 | -5.048
915.7 | 50.5 | -5.048
915.8 | 50.5 | -5.047
915.9 | 50.5 | -5.047
916 | 50.5 | -5.047
916.1 | 50.5 | -5.047
916.2 | 50.5 | -5.047
916.3 | 50.5 | -5.047
916.4 | 50.5 | -5.047
916.5 | 50.5 | -5.047
916.6 | 50.5 | -5.047
916.7 | 50.5 | -5.047
916.8 | 50.5 | -5.047
916.9 | 50.5 | -5.047
917 | 50.5 | -5.047
917.1 | 50.5 | -5.047
917.2 | 50.5 | -5.047
917.3 | 50.5 | -5.047
917.4 | 50.5 | -5.047
917.5 | 50.5 | -5.047
917.6 | 50.5 | -5.047
917.7 | 50.5 | -5.047
917.8 | 50.5 | -5.047
917.9 | 50.5 | -5.047
918 | 50.5 | -5.047
918.1 | 50.5 | -5.047
918.2 | 50.5 | -5.047
918.3 | 50.5 | -5.047
918.4 | 50.5 | -5.047
918.5 | 50.5 | -5.047
918.6 | 50.5 | -5.047
918.7 | 50.5 | -5.047
918.8 | 50.5 | -5.047
918.9 | 50.5 | -5.047
919 | 50.5 | -5.047
919.1 | 50.5 | -5.047
919.2 | 50.5 | -5.048
919.3 | 50.5 | -5.048
919.4 | 50.5 | -5.048
919.5 | 50.5 | -5.048
919.6 | 50.5 | -5.048
919.7 | 50.5 | -5.048
919.8 | 50.5 | -5.048
919.9 | 50.5 | -5.048
920 | 50.5 | -5.048
920.1 | 50.5 | -5.048
920.2 | 50.5 | -5.048
920.3 | 50.5 | -5.048
920.4 | 50.5 | -5.048
920.5 | 50.5 | -5.048
920.6 | 50.5 | -5.048
920.7 | 50.5 | -5.048
920.8 | 50.5 | -5.048
920.9 | 50.5 | -5.048
921 | 50.5 | -5.048
921.1 | 50.5 | -5.048
921.2 | 50.5 | -5.048
921.3 | 50.5 | -5.048
921.4 | 50.5 | -5.048
921.5 | 50.5 | -5.048
921.6 | 50.5 | -5.048
921.7 | 50.5 | -5.048
921.8 | 50.5 | -5.048
921.9 | 50.5 | -5.048
922 | 50.5 | -5.048
922.1 | 50.5 | -5.048
922.2 | 50.5 | -5.048
922.3 | 50.5 | -5.048
922.4 | 50.5 | -5.048
922.5 | 50.5 | -5.048
922.6 | 50.5 | -5.048
922.7 | 50.5 | -5.048
922.8 | 50.5 | -5.048
922.9 | 50.5 | -5.048
923 | 50.5 | -5.048
923.1 | 50.5 | -5.048
923.2 | 50.5 | -5.048
923.3 | 50.5 | -5.048
923.4 | 50.5 | -5.048
923.5 | 50.5 | -5.048
923.6 | 50.5 | -5.048
923.7 | 50.5 | -5.048
923.8 | 50.5 | -5.048
923.9 | 50.5 | -5.048
924 | 50.5 | -5.048
924.1 | 50.5 | -5.048
924.2 | 50.5 | -5.048
924.3 | 50.5 | -5.048
924.4 | 50.5 | -5.048
924.5 | 50.5 | -5.048
924.6 | 50.5 | -5.048
924.7 | 50.5 | -5.048
924.8 | 50.5 | -5.048
924.9 | 50.5 | -5.048
925 | 50.5 | -5.048
925.1 | 50.5 | -5.048
925.2 | 50.5 | -5.048
925.3 | 50.5 | -5.048
925.4 | 50.5 | -5.048
925.5 | 50.5 | -5.048
925.6 | 50.5 | -5.048
925.7 | 50.5 | -5.048
925.8 | 50.5 | -5.048
925.9 | 50.5 | -5.048
926 | 50.5 | -5.048
926.1 | 50.5 | -5.048
926.2 | 50.5 | -5.047
926.3 | 50.5 | -5.047
926.4 | 50.5 | -5.047
926.5 | 50.5 | -5.047
926.6 | 50.5 | -5.047
926.7 | 50.5 | -5.047
926.8 | 50.5 | -5.047
926.9 | 50.5 | -5.047
927 | 50.5 | -5.047
927.1 | 50.5 | -5.047
927.2 | 50.5 | -5.047
927.3 | 50.5 | -5.047
927.4 | 50.5 | -5.047
927.5 | 50.5 | -5.048
927.6 | 50.5 | -5.048
927.7 | 50.5 | -5.048
927.8 | 50.5 | -5.048
927.9 | 50.5 | -5.048
928 | 50.5 | -5.048
928.1 | 50.5 | -5.048
928.2 | 50.5 | -5.048
928.3 | 50.5 | -5.048
928.4 | 50.5 | -5.048
928.5 | 50.5 | -5.048
928.6 | 50.5 | -5.048
928.7 | 50.5 | -5.048
928.8 | 50.5 | -5.048
928.9 | 50.5 | -5.048
929 | 50.5 | -5.048
929.1 | 50.5 | -5.048
929.2 | 50.5 | -5.048
929.3 | 50.5 | -5.048
929.4 | 50.5 | -5.048
929.5 | 50.5 | -5.048
929.6 | 50.5 | -5.048
929.7 | 50.5 | -5.048
929.8 | 50.5 | -5.048
929.9 | 50.5 | -5.048
930 | 50.5 | -5.048
930.1 | 50.5 | -5.048
930.2 | 50.5 | -5.048
930.3 | 50.5 | -5.048
930.4 | 50.5 | -5.048
930.5 | 50.5 | -5.048
930.6 | 50.5 | -5.048
930.7 | 50.5 | -5.048
930.8 | 50.5 | -5.048
930.9 | 50.5 | -5.048
931 | 50.5 | -5.047
931.1 | 50.5 | -5.048
931.2 | 50.5 | -5.048
931.3 | 50.5 | -5.048
931.4 | 50.5 | -5.048
931.5 | 50.5 | -5.048
931.6 | 50.5 | -5.048
931.7 | 50.5 | -5.048
931.8 | 50.5 | -5.048
931.9 | 50.5 | -5.048
932 | 50.5 | -5.048
932.1 | 50.5 | -5.048
932.2 | 50.5 | -5.048
932.3 | 50.5 | -5.048
932.4 | 50.5 | -5.048
932.5 | 50.5 | -5.048
932.6 | 50.5 | -5.048
932.7 | 50.5 | -5.048
932.8 | 50.5 | -5.048
932.9 | 50.5 | -5.048
933 | 50.5 | -5.048
933.1 | 50.5 | -5.048
933.2 | 50.5 | -5.048
933.3 | 50.5 | -5.048
933.4 | 50.5 | -5.049
933.5 | 50.5 | -5.049
933.6 | 50.5 | -5.049
933.7 | 50.5 | -5.049
933.8 | 50.5 | -5.049
933.9 | 50.5 | -5.049
934 | 50.5 | -5.049
934.1 | 50.5 | -5.049
934.2 | 50.5 | -5.049
934.3 | 50.5 | -5.049
934.4 | 50.5 | -5.049
934.5 | 50.5 | -5.049
934.6 | 50.5 | -5.048
934.7 | 50.5 | -5.048
934.8 | 50.5 | -5.048
934.9 | 50.5 | -5.048
935 | 50.5 | -5.048
935.1 | 50.5 | -5.048
935.2 | 50.5 | -5.048
935.3 | 50.5 | -5.048
935.4 | 50.5 | -5.048
935.5 | 50.5 | -5.048
935.6 | 50.5 | -5.048
935.7 | 50.5 | -5.048
935.8 | 50.5 | -5.048
935.9 | 50.5 | -5.048
936 | 50.5 | -5.048
936.1 | 50.5 | -5.048
936.2 | 50.5 | -5.048
936.3 | 50.5 | -5.048
936.4 | 50.5 | -5.048
936.5 | 50.5 | -5.048
936.6 | 50.5 | -5.048
936.7 | 50.5 | -5.048
936.8 | 50.5 | -5.048
936.9 | 50.5 | -5.047
937 | 50.5 | -5.047
937.1 | 50.5 | -5.047
937.2 | 50.5 | -5.047
937.3 | 50.5 | -5.047
937.4 | 50.5 | -5.047
937.5 | 50.5 | -5.047
937.6 | 50.5 | -5.047
937.7 | 50.5 | -5.047
937.8 | 50.5 | -5.047
937.9 | 50.5 | -5.047
938 | 50.5 | -5.047
938.1 | 50.5 | -5.047
938.2 | 50.5 | -5.047
938.3 | 50.5 | -5.047
938.4 | 50.5 | -5.047
938.5 | 50.5 | -5.047
938.6 | 50.5 | -5.047
938.7 | 50.5 | -5.047
938.8 | 50.5 | -5.047
938.9 | 50.5 | -5.047
939 | 50.5 | -5.047
939.1 | 50.5 | -5.048
939.2 | 50.5 | -5.048
939.3 | 50.5 | -5.048
939.4 | 50.5 | -5.048
939.5 | 50.5 | -5.048
939.6 | 50.5 | -5.048
939.7 | 50.5 | -5.048
939.8 | 50.5 | -5.048
939.9 | 50.5 | -5.048
940 | 50.5 | -5.048
940.1 | 50.5 | -5.048
940.2 | 50.5 | -5.048
940.3 | 50.5 | -5.048
940.4 | 50.5 | -5.048
940.5 | 50.5 | -5.048
940.6 | 50.5 | -5.048
940.7 | 50.5 | -5.048
940.8 | 50.5 | -5.048
940.9 | 50.5 | -5.048
941 | 50.5 | -5.048
941.1 | 50.5 | -5.048
941.2 | 50.5 | -5.048
941.3 | 50.5 | -5.048
941.4 | 50.5 | -5.048
941.5 | 50.5 | -5.048
941.6 | 50.5 | -5.048
941.7 | 50.5 | -5.048
941.8 | 50.5 | -5.048
941.9 | 50.5 | -5.048
942 | 50.5 | -5.048
942.1 | 50.5 | -5.048
942.2 | 50.5 | -5.048
942.3 | 50.5 | -5.048
942.4 | 50.5 | -5.048
942.5 | 50.5 | -5.048
942.6 | 50.5 | -5.048
942.7 | 50.5 | -5.048
942.8 | 50.5 | -5.048
942.9 | 50.5 | -5.048
943 | 50.5 | -5.048
943.1 | 50.5 | -5.048
943.2 | 50.5 | -5.048
943.3 | 50.5 | -5.048
943.4 | 50.5 | -5.048
943.5 | 50.5 | -5.048
943.6 | 50.5 | -5.048
943.7 | 50.5 | -5.048
943.8 | 50.5 | -5.047
943.9 | 50.5 | -5.047
944 | 50.5 | -5.047
944.1 | 50.5 | -5.047
944.2 | 50.5 | -5.047
944.3 | 50.5 | -5.047
944.4 | 50.5 | -5.047
944.5 | 50.5 | -5.047
944.6 | 50.5 | -5.047
944.7 | 50.5 | -5.047
944.8 | 50.5 | -5.047
944.9 | 50.5 | -5.047
945 | 50.5 | -5.047
945.1 | 50.5 | -5.047
945.2 | 50.5 | -5.047
945.3 | 50.5 | -5.047
945.4 | 50.5 | -5.047
945.5 | 50.5 | -5.047
945.6 | 50.5 | -5.047
945.7 | 50.5 | -5.047
945.8 | 50.5 | -5.047
945.9 | 50.5 | -5.047
946 | 50.5 | -5.048
946.1 | 50.5 | -5.048
946.2 | 50.5 | -5.048
946.3 | 50.5 | -5.048
946.4 | 50.5 | -5.048
946.5 | 50.5 | -5.048
946.6 | 50.5 | -5.048
946.7 | 50.5 | -5.048
946.8 | 50.5 | -5.048
946.9 | 50.5 | -5.048
947 | 50.5 | -5.048
947.1 | 50.5 | -5.048
947.2 | 50.5 | -5.048
947.3 | 50.5 | -5.048
947.4 | 50.5 | -5.048
947.5 | 50.5 | -5.048
947.6 | 50.5 | -5.048
947.7 | 50.5 | -5.048
947.8 | 50.5 | -5.048
947.9 | 50.5 | -5.048
948 | 50.5 | -5.048
948.1 | 50.5 | -5.048
948.2 | 50.5 | -5.048
948.3 | 50.5 | -5.048
948.4 | 50.5 | -5.048
948.5 | 50.5 | -5.048
948.6 | 50.5 | -5.048
948.7 | 50.5 | -5.048
948.8 | 50.5 | -5.048
948.9 | 50.5 | -5.048
949 | 50.5 | -5.048
949.1 | 50.5 | -5.048
949.2 | 50.5 | -5.048
949.3 | 50.5 | -5.048
949.4 | 50.5 | -5.048
949.5 | 50.5 | -5.048
949.6 | 50.5 | -5.048
949.7 | 50.5 | -5.048
949.8 | 50.5 | -5.048
949.9 | 50.5 | -5.048
950 | 50.5 | -5.048
950.1 | 50.5 | -5.048
950.2 | 50.5 | -5.048
950.3 | 50.5 | -5.048
950.4 | 50.5 | -5.048
950.5 | 50.5 | -5.048
950.6 | 50.5 | -5.048
950.7 | 50.5 | -5.048
950.8 | 50.5 | -5.048
950.9 | 50.5 | -5.048
951 | 50.5 | -5.048
951.1 | 50.5 | -5.048
951.2 | 50.5 | -5.048
951.3 | 50.5 | -5.048
951.4 | 50.5 | -5.048
951.5 | 50.5 | -5.048
951.6 | 50.5 | -5.048
951.7 | 50.5 | -5.048
951.8 | 50.5 | -5.048
951.9 | 50.5 | -5.048
952 | 50.5 | -5.048
952.1 | 50.5 | -5.048
952.2 | 50.5 | -5.048
952.3 | 50.5 | -5.048
952.4 | 50.5 | -5.048
952.5 | 50.5 | -5.048
952.6 | 50.5 | -5.048
952.7 | 50.5 | -5.048
952.8 | 50.5 | -5.048
952.9 | 50.5 | -5.048
953 | 50.5 | -5.048
953.1 | 50.5 | -5.048
953.2 | 50.5 | -5.048
953.3 | 50.5 | -5.048
953.4 | 50.5 | -5.048
953.5 | 50.5 | -5.048
953.6 | 50.5 | -5.048
953.7 | 50.5 | -5.048
953.8 | 50.5 | -5.048
953.9 | 50.5 | -5.048
954 | 50.5 | -5.048
954.1 | 50.5 | -5.048
954.2 | 50.5 | -5.048
954.3 | 50.5 | -5.048
954.4 | 50.5 | -5.048
954.5 | 50.5 | -5.048
954.6 | 50.5 | -5.048
954.7 | 50.5 | -5.048
954.8 | 50.5 | -5.048
954.9 | 50.5 | -5.048
955 | 50.5 | -5.048
955.1 | 50.5 | -5.048
955.2 | 50.5 | -5.048
955.3 | 50.5 | -5.048
955.4 | 50.5 | -5.048
955.5 | 50.5 | -5.048
955.6 | 50.5 | -5.048
955.7 | 50.5 | -5.048
955.8 | 50.5 | -5.048
955.9 | 50.5 | -5.048
956 | 50.5 | -5.048
956.1 | 50.5 | -5.048
956.2 | 50.5 | -5.048
956.3 | 50.5 | -5.048
956.4 | 50.5 | -5.048
956.5 | 50.5 | -5.048
956.6 | 50.5 | -5.048
956.7 | 50.5 | -5.048
956.8 | 50.5 | -5.048
956.9 | 50.5 | -5.048
957 | 50.5 | -5.048
957.1 | 50.5 | -5.048
957.2 | 50.5 | -5.048
957.3 | 50.5 | -5.048
957.4 | 50.5 | -5.048
957.5 | 50.5 | -5.048
957.6 | 50.5 | -5.048
957.7 | 50.5 | -5.048
957.8 | 50.5 | -5.048
957.9 | 50.5 | -5.048
958 | 50.5 | -5.048
958.1 | 50.5 | -5.048
958.2 | 50.5 | -5.048
958.3 | 50.5 | -5.048
958.4 | 50.5 | -5.048
958.5 | 50.5 | -5.048
958.6 | 50.5 | -5.048
958.7 | 50.5 | -5.048
958.8 | 50.5 | -5.048
958.9 | 50.5 | -5.048
959 | 50.5 | -5.048
959.1 | 50.5 | -5.048
959.2 | 50.5 | -5.048
959.3 | 50.5 | -5.048
959.4 | 50.5 | -5.048
959.5 | 50.5 | -5.048
959.6 | 50.5 | -5.048
959.7 | 50.5 | -5.048
959.8 | 50.5 | -5.048
959.9 | 50.5 | -5.048
960 | 50.5 | -5.048
960.1 | 50.5 | -5.048
960.2 | 50.5 | -5.048
960.3 | 50.5 | -5.048
960.4 | 50.5 | -5.048
960.5 | 50.5 | -5.048
960.6 | 50.5 | -5.048
960.7 | 50.5 | -5.048
960.8 | 50.5 | -5.048
960.9 | 50.5 | -5.048
961 | 50.5 | -5.048
961.1 | 50.5 | -5.048
961.2 | 50.5 | -5.048
961.3 | 50.5 | -5.048
961.4 | 50.5 | -5.048
961.5 | 50.5 | -5.047
961.6 | 50.5 | -5.047
961.7 | 50.5 | -5.047
961.8 | 50.5 | -5.047
961.9 | 50.5 | -5.047
962 | 50.5 | -5.047
962.1 | 50.5 | -5.047
962.2 | 50.5 | -5.047
962.3 | 50.5 | -5.047
962.4 | 50.5 | -5.047
962.5 | 50.5 | -5.047
962.6 | 50.5 | -5.047
962.7 | 50.5 | -5.048
962.8 | 50.5 | -5.048
962.9 | 50.5 | -5.048
963 | 50.5 | -5.048
963.1 | 50.5 | -5.048
963.2 | 50.5 | -5.048
963.3 | 50.5 | -5.048
963.4 | 50.5 | -5.048
963.5 | 50.5 | -5.048
963.6 | 50.5 | -5.048
963.7 | 50.5 | -5.048
963.8 | 50.5 | -5.048
963.9 | 50.5 | -5.048
964 | 50.5 | -5.048
964.1 | 50.5 | -5.048
964.2 | 50.5 | -5.048
964.3 | 50.5 | -5.048
964.4 | 50.5 | -5.048
964.5 | 50.5 | -5.048
964.6 | 50.5 | -5.048
964.7 | 50.5 | -5.048
964.8 | 50.5 | -5.048
964.9 | 50.5 | -5.048
965 | 50.5 | -5.048
965.1 | 50.5 | -5.048
965.2 | 50.5 | -5.048
965.3 | 50.5 | -5.048
965.4 | 50.5 | -5.048
965.5 | 50.5 | -5.048
965.6 | 50.5 | -5.048
965.7 | 50.5 | -5.048
965.8 | 50.5 | -5.048
965.9 | 50.5 | -5.048
966 | 50.5 | -5.048
966.1 | 50.5 | -5.048
966.2 | 50.5 | -5.048
966.3 | 50.5 | -5.048
966.4 | 50.5 | -5.048
966.5 | 50.5 | -5.048
966.6 | 50.5 | -5.048
966.7 | 50.5 | -5.048
966.8 | 50.5 | -5.048
966.9 | 50.5 | -5.048
967 | 50.5 | -5.048
967.1 | 50.5 | -5.048
967.2 | 50.5 | -5.048
967.3 | 50.5 | -5.048
967.4 | 50.5 | -5.048
967.5 | 50.5 | -5.048
967.6 | 50.5 | -5.048
967.7 | 50.5 | -5.048
967.8 | 50.5 | -5.048
967.9 | 50.5 | -5.048
968 | 50.5 | -5.048
968.1 | 50.5 | -5.048
968.2 | 50.5 | -5.048
968.3 | 50.5 | -5.048
968.4 | 50.5 | -5.048
968.5 | 50.5 | -5.048
968.6 | 50.5 | -5.048
968.7 | 50.5 | -5.048
968.8 | 50.5 | -5.048
968.9 | 50.5 | -5.048
969 | 50.5 | -5.048
969.1 | 50.5 | -5.048
969.2 | 50.5 | -5.048
969.3 | 50.5 | -5.048
969.4 | 50.5 | -5.048
969.5 | 50.5 | -5.048
969.6 | 50.5 | -5.048
969.7 | 50.5 | -5.048
969.8 | 50.5 | -5.048
969.9 | 50.5 | -5.048
970 | 50.5 | -5.048
970.1 | 50.5 | -5.048
970.2 | 50.5 | -5.048
970.3 | 50.5 | -5.048
970.4 | 50.5 | -5.048
970.5 | 50.5 | -5.048
970.6 | 50.5 | -5.048
970.7 | 50.5 | -5.048
970.8 | 50.5 | -5.048
970.9 | 50.5 | -5.048
971 | 50.5 | -5.048
971.1 | 50.5 | -5.048
971.2 | 50.5 | -5.048
971.3 | 50.5 | -5.048
971.4 | 50.5 | -5.048
971.5 | 50.5 | -5.048
971.6 | 50.5 | -5.048
971.7 | 50.5 | -5.048
971.8 | 50.5 | -5.047
971.9 | 50.5 | -5.047
972 | 50.5 | -5.047
972.1 | 50.5 | -5.047
972.2 | 50.5 | -5.047
972.3 | 50.5 | -5.047
972.4 | 50.5 | -5.047
972.5 | 50.5 | -5.047
972.6 | 50.5 | -5.047
972.7 | 50.5 | -5.047
972.8 | 50.5 | -5.048
972.9 | 50.5 | -5.048
973 | 50.5 | -5.048
973.1 | 50.5 | -5.048
973.2 | 50.5 | -5.048
973.3 | 50.5 | -5.048
973.4 | 50.5 | -5.048
973.5 | 50.5 | -5.048
973.6 | 50.5 | -5.048
973.7 | 50.5 | -5.048
973.8 | 50.5 | -5.048
973.9 | 50.5 | -5.048
974 | 50.5 | -5.048
974.1 | 50.5 | -5.048
974.2 | 50.5 | -5.048
974.3 | 50.5 | -5.048
974.4 | 50.5 | -5.048
974.5 | 50.5 | -5.047
974.6 | 50.5 | -5.047
974.7 | 50.5 | -5.047
974.8 | 50.5 | -5.047
974.9 | 50.5 | -5.047
975 | 50.5 | -5.047
975.1 | 50.5 | -5.047
975.2 | 50.5 | -5.048
975.3 | 50.5 | -5.048
975.4 | 50.5 | -5.048
975.5 | 50.5 | -5.048
975.6 | 50.5 | -5.048
975.7 | 50.5 | -5.048
975.8 | 50.5 | -5.048
975.9 | 50.5 | -5.048
976 | 50.5 | -5.048
976.1 | 50.5 | -5.048
976.2 | 50.5 | -5.048
976.3 | 50.5 | -5.047
976.4 | 50.5 | -5.047
976.5 | 50.5 | -5.047
976.6 | 50.5 | -5.047
976.7 | 50.5 | -5.047
976.8 | 50.5 | -5.047
976.9 | 50.5 | -5.048
977 | 50.5 | -5.048
977.1 | 50.5 | -5.048
977.2 | 50.5 | -5.048
977.3 | 50.5 | -5.048
977.4 | 50.5 | -5.048
977.5 | 50.5 | -5.047
977.6 | 50.5 | -5.047
977.7 | 50.5 | -5.047
977.8 | 50.5 | -5.047
977.9 | 50.5 | -5.047
978 | 50.5 | -5.047
978.1 | 50.5 | -5.047
978.2 | 50.5 | -5.047
978.3 | 50.5 | -5.047
978.4 | 50.5 | -5.047
978.5 | 50.5 | -5.047
978.6 | 50.5 | -5.047
978.7 | 50.5 | -5.048
978.8 | 50.5 | -5.048
978.9 | 50.5 | -5.048
979 | 50.5 | -5.048
979.1 | 50.5 | -5.048
979.2 | 50.5 | -5.048
979.3 | 50.5 | -5.047
979.4 | 50.5 | -5.047
979.5 | 50.5 | -5.047
979.6 | 50.5 | -5.047
979.7 | 50.5 | -5.047
979.8 | 50.5 | -5.048
979.9 | 50.5 | -5.048
980 | 50.5 | -5.048
980.1 | 50.5 | -5.048
980.2 | 50.5 | -5.048
980.3 | 50.5 | -5.048
980.4 | 50.5 | -5.048
980.5 | 50.5 | -5.048
980.6 | 50.5 | -5.048
980.7 | 50.5 | -5.048
980.8 | 50.5 | -5.048
980.9 | 50.5 | -5.048
981 | 50.5 | -5.047
981.1 | 50.5 | -5.047
981.2 | 50.5 | -5.047
981.3 | 50.5 | -5.047
981.4 | 50.5 | -5.047
981.5 | 50.5 | -5.047
981.6 | 50.5 | -5.047
981.7 | 50.5 | -5.047
981.8 | 50.5 | -5.047
981.9 | 50.5 | -5.047
982 | 50.5 | -5.047
982.1 | 50.5 | -5.047
982.2 | 50.5 | -5.048
982.3 | 50.5 | -5.048
982.4 | 50.5 | -5.048
982.5 | 50.5 | -5.048
982.6 | 50.5 | -5.048
982.7 | 50.5 | -5.048
982.8 | 50.5 | -5.048
982.9 | 50.5 | -5.048
983 | 50.5 | -5.048
983.1 | 50.5 | -5.048
983.2 | 50.5 | -5.048
983.3 | 50.5 | -5.048
983.4 | 50.5 | -5.048
983.5 | 50.5 | -5.048
983.6 | 50.5 | -5.048
983.7 | 50.5 | -5.048
983.8 | 50.5 | -5.048
983.9 | 50.5 | -5.048
984 | 50.5 | -5.048
984.1 | 50.5 | -5.048
984.2 | 50.5 | -5.048
984.3 | 50.5 | -5.048
984.4 | 50.5 | -5.048
984.5 | 50.5 | -5.048
984.6 | 50.5 | -5.048
984.7 | 50.5 | -5.048
984.8 | 50.5 | -5.048
984.9 | 50.5 | -5.048
985 | 50.5 | -5.048
985.1 | 50.5 | -5.048
985.2 | 50.5 | -5.048
985.3 | 50.5 | -5.048
985.4 | 50.5 | -5.048
985.5 | 50.5 | -5.048
985.6 | 50.5 | -5.048
985.7 | 50.5 | -5.048
985.8 | 50.5 | -5.048
985.9 | 50.5 | -5.048
986 | 50.5 | -5.048
986.1 | 50.5 | -5.047
986.2 | 50.5 | -5.047
986.3 | 50.5 | -5.047
986.4 | 50.5 | -5.047
986.5 | 50.5 | -5.047
986.6 | 50.5 | -5.047
986.7 | 50.5 | -5.047
986.8 | 50.5 | -5.048
986.9 | 50.5 | -5.048
987 | 50.5 | -5.048
987.1 | 50.5 | -5.048
987.2 | 50.5 | -5.048
987.3 | 50.5 | -5.048
987.4 | 50.5 | -5.048
987.5 | 50.5 | -5.048
987.6 | 50.5 | -5.048
987.7 | 50.5 | -5.048
987.8 | 50.5 | -5.048
987.9 | 50.5 | -5.048
988 | 50.5 | -5.048
988.1 | 50.5 | -5.048
988.2 | 50.5 | -5.048
988.3 | 50.5 | -5.048
988.4 | 50.5 | -5.048
988.5 | 50.5 | -5.048
988.6 | 50.5 | -5.048
988.7 | 50.5 | -5.048
988.8 | 50.5 | -5.048
988.9 | 50.5 | -5.048
989 | 50.5 | -5.048
989.1 | 50.5 | -5.048
989.2 | 50.5 | -5.048
989.3 | 50.5 | -5.048
989.4 | 50.5 | -5.048
989.5 | 50.5 | -5.048
989.6 | 50.5 | -5.048
989.7 | 50.5 | -5.048
989.8 | 50.5 | -5.048
989.9 | 50.5 | -5.048
990 | 50.5 | -5.048
990.1 | 50.5 | -5.048
990.2 | 50.5 | -5.048
990.3 | 50.5 | -5.048
990.4 | 50.5 | -5.048
990.5 | 50.5 | -5.048
990.6 | 50.5 | -5.048
990.7 | 50.5 | -5.048
990.8 | 50.5 | -5.048
990.9 | 50.5 | -5.048
991 | 50.5 | -5.048
991.1 | 50.5 | -5.048
991.2 | 50.5 | -5.048
991.3 | 50.5 | -5.048
991.4 | 50.5 | -5.048
991.5 | 50.5 | -5.048
991.6 | 50.5 | -5.048
991.7 | 50.5 | -5.048
991.8 | 50.5 | -5.048
991.9 | 50.5 | -5.048
992 | 50.5 | -5.048
992.1 | 50.5 | -5.048
992.2 | 50.5 | -5.048
992.3 | 50.5 | -5.048
992.4 | 50.5 | -5.048
992.5 | 50.5 | -5.048
992.6 | 50.5 | -5.047
992.7 | 50.5 | -5.047
992.8 | 50.5 | -5.047
992.9 | 50.5 | -5.047
993 | 50.5 | -5.047
993.1 | 50.5 | -5.047
993.2 | 50.5 | -5.047
993.3 | 50.5 | -5.047
993.4 | 50.5 | -5.047
993.5 | 50.5 | -5.047
993.6 | 50.5 | -5.047
993.7 | 50.5 | -5.047
993.8 | 50.5 | -5.047
993.9 | 50.5 | -5.047
994 | 50.5 | -5.047
994.1 | 50.5 | -5.047
994.2 | 50.5 | -5.047
994.3 | 50.5 | -5.047
994.4 | 50.5 | -5.047
994.5 | 50.5 | -5.047
994.6 | 50.5 | -5.047
994.7 | 50.5 | -5.047
994.8 | 50.5 | -5.047
994.9 | 50.5 | -5.047
995 | 50.5 | -5.048
995.1 | 50.5 | -5.048
995.2 | 50.5 | -5.048
995.3 | 50.5 | -5.048
995.4 | 50.5 | -5.048
995.5 | 50.5 | -5.048
995.6 | 50.5 | -5.048
995.7 | 50.5 | -5.048
995.8 | 50.5 | -5.048
995.9 | 50.5 | -5.048
996 | 50.5 | -5.048
996.1 | 50.5 | -5.048
996.2 | 50.5 | -5.048
996.3 | 50.5 | -5.048
996.4 | 50.5 | -5.048
996.5 | 50.5 | -5.048
996.6 | 50.5 | -5.048
996.7 | 50.5 | -5.048
996.8 | 50.5 | -5.048
996.9 | 50.5 | -5.048
997 | 50.5 | -5.048
997.1 | 50.5 | -5.048
997.2 | 50.5 | -5.048
997.3 | 50.5 | -5.048
997.4 | 50.5 | -5.048
997.5 | 50.5 | -5.048
997.6 | 50.5 | -5.048
997.7 | 50.5 | -5.048
997.8 | 50.5 | -5.048
997.9 | 50.5 | -5.048
998 | 50.5 | -5.048
998.1 | 50.5 | -5.048
998.2 | 50.5 | -5.048
998.3 | 50.5 | -5.048
998.4 | 50.5 | -5.048
998.5 | 50.5 | -5.048
998.6 | 50.5 | -5.048
998.7 | 50.5 | -5.048
998.8 | 50.5 | -5.048
998.9 | 50.5 | -5.048
999 | 50.5 | -5.048
999.1 | 50.5 | -5.048
999.2 | 50.5 | -5.048
999.3 | 50.5 | -5.048
999.4 | 50.5 | -5.048
999.5 | 50.5 | -5.048
999.6 | 50.5 | -5.048
999.7 | 50.5 | -5.048
999.8 | 50.5 | -5.048
999.9 | 50.5 | -5.048
1000 | 50.5 | -5.048
1000.1 | 50.5 | -5.048
1000.2 | 50.5 | -5.048
1000.3 | 50.5 | -5.048
1000.4 | 50.5 | -5.048
1000.5 | 50.5 | -5.048
1000.6 | 50.5 | -5.048
1000.7 | 50.5 | -5.048
1000.8 | 50.5 | -5.048
1000.9 | 50.5 | -5.047
1001 | 50.5 | -5.047
1001.1 | 50.5 | -5.047
1001.2 | 50.5 | -5.047
1001.3 | 50.5 | -5.047
1001.4 | 50.5 | -5.047
1001.5 | 50.5 | -5.047
1001.6 | 50.5 | -5.047
1001.7 | 50.5 | -5.047
1001.8 | 50.5 | -5.047
1001.9 | 50.5 | -5.048
1002 | 50.5 | -5.048
1002.1 | 50.5 | -5.048
1002.2 | 50.5 | -5.048
1002.3 | 50.5 | -5.048
1002.4 | 50.5 | -5.048
1002.5 | 50.5 | -5.048
1002.6 | 50.5 | -5.048
1002.7 | 50.5 | -5.048
1002.8 | 50.5 | -5.048
1002.9 | 50.5 | -5.048
1003 | 50.5 | -5.048
1003.1 | 50.5 | -5.048
1003.2 | 50.5 | -5.048
1003.3 | 50.5 | -5.048
1003.4 | 50.5 | -5.048
1003.5 | 50.5 | -5.048
1003.6 | 50.5 | -5.048
1003.7 | 50.5 | -5.048
1003.8 | 50.5 | -5.047
1003.9 | 50.5 | -5.047
1004 | 50.5 | -5.047
1004.1 | 50.5 | -5.047
1004.2 | 50.5 | -5.047
1004.3 | 50.5 | -5.048
1004.4 | 50.5 | -5.048
1004.5 | 50.5 | -5.048
1004.6 | 50.5 | -5.048
1004.7 | 50.5 | -5.048
1004.8 | 50.5 | -5.048
1004.9 | 50.5 | -5.048
1005 | 50.5 | -5.048
1005.1 | 50.5 | -5.048
1005.2 | 50.5 | -5.048
1005.3 | 50.5 | -5.048
1005.4 | 50.5 | -5.048
1005.5 | 50.5 | -5.048
1005.6 | 50.5 | -5.048
1005.7 | 50.5 | -5.048
1005.8 | 50.5 | -5.048
1005.9 | 50.5 | -5.048
1006 | 50.5 | -5.048
1006.1 | 50.5 | -5.048
1006.2 | 50.5 | -5.048
1006.3 | 50.5 | -5.048
1006.4 | 50.5 | -5.048
1006.5 | 50.5 | -5.048
1006.6 | 50.5 | -5.048
1006.7 | 50.5 | -5.048
1006.8 | 50.5 | -5.048
1006.9 | 50.5 | -5.048
1007 | 50.5 | -5.048
1007.1 | 50.5 | -5.048
1007.2 | 50.5 | -5.048
1007.3 | 50.5 | -5.048
1007.4 | 50.5 | -5.048
1007.5 | 50.5 | -5.048
1007.6 | 50.5 | -5.048
1007.7 | 50.5 | -5.048
1007.8 | 50.5 | -5.048
1007.9 | 50.5 | -5.047
1008 | 50.5 | -5.047
1008.1 | 50.5 | -5.047
1008.2 | 50.5 | -5.047
1008.3 | 50.5 | -5.047
1008.4 | 50.5 | -5.047
1008.5 | 50.5 | -5.047
1008.6 | 50.5 | -5.047
1008.7 | 50.5 | -5.047
1008.8 | 50.5 | -5.048
1008.9 | 50.5 | -5.048
1009 | 50.5 | -5.048
1009.1 | 50.5 | -5.048
1009.2 | 50.5 | -5.048
1009.3 | 50.5 | -5.048
1009.4 | 50.5 | -5.048
1009.5 | 50.5 | -5.048
1009.6 | 50.5 | -5.048
1009.7 | 50.5 | -5.048
1009.8 | 50.5 | -5.048
1009.9 | 50.5 | -5.048
1010 | 50.5 | -5.048
1010.1 | 50.5 | -5.048
1010.2 | 50.5 | -5.048
1010.3 | 50.5 | -5.048
1010.4 | 50.5 | -5.048
1010.5 | 50.5 | -5.048
1010.6 | 50.5 | -5.048
1010.7 | 50.5 | -5.048
1010.8 | 50.5 | -5.048
1010.9 | 50.5 | -5.048
1011 | 50.5 | -5.048
1011.1 | 50.5 | -5.048
1011.2 | 50.5 | -5.048
1011.3 | 50.5 | -5.048
1011.4 | 50.5 | -5.048
1011.5 | 50.5 | -5.048
1011.6 | 50.5 | -5.048
1011.7 | 50.5 | -5.048
1011.8 | 50.5 | -5.048
1011.9 | 50.5 | -5.048
1012 | 50.5 | -5.048
1012.1 | 50.5 | -5.048
1012.2 | 50.5 | -5.048
1012.3 | 50.5 | -5.048
1012.4 | 50.5 | -5.048
1012.5 | 50.5 | -5.048
1012.6 | 50.5 | -5.048
1012.7 | 50.5 | -5.048
1012.8 | 50.5 | -5.048
1012.9 | 50.5 | -5.048
1013 | 50.5 | -5.048
1013.1 | 50.5 | -5.048
1013.2 | 50.5 | -5.048
1013.3 | 50.5 | -5.048
1013.4 | 50.5 | -5.048
1013.5 | 50.5 | -5.048
1013.6 | 50.5 | -5.048
1013.7 | 50.5 | -5.048
1013.8 | 50.5 | -5.048
1013.9 | 50.5 | -5.048
1014 | 50.5 | -5.048
1014.1 | 50.5 | -5.048
1014.2 | 50.5 | -5.048
1014.3 | 50.5 | -5.048
1014.4 | 50.5 | -5.048
1014.5 | 50.5 | -5.048
1014.6 | 50.5 | -5.048
1014.7 | 50.5 | -5.047
1014.8 | 50.5 | -5.047
1014.9 | 50.5 | -5.047
1015 | 50.5 | -5.047
1015.1 | 50.5 | -5.047
1015.2 | 50.5 | -5.047
1015.3 | 50.5 | -5.047
1015.4 | 50.5 | -5.047
1015.5 | 50.5 | -5.047
1015.6 | 50.5 | -5.047
1015.7 | 50.5 | -5.047
1015.8 | 50.5 | -5.047
1015.9 | 50.5 | -5.047
1016 | 50.5 | -5.047
1016.1 | 50.5 | -5.047
1016.2 | 50.5 | -5.047
1016.3 | 50.5 | -5.047
1016.4 | 50.5 | -5.047
1016.5 | 50.5 | -5.047
1016.6 | 50.5 | -5.047
1016.7 | 50.5 | -5.047
1016.8 | 50.5 | -5.047
1016.9 | 50.5 | -5.047
1017 | 50.5 | -5.047
1017.1 | 50.5 | -5.048
1017.2 | 50.5 | -5.048
1017.3 | 50.5 | -5.048
1017.4 | 50.5 | -5.048
1017.5 | 50.5 | -5.048
1017.6 | 50.5 | -5.048
1017.7 | 50.5 | -5.048
1017.8 | 50.5 | -5.048
1017.9 | 50.5 | -5.048
1018 | 50.5 | -5.048
1018.1 | 50.5 | -5.048
1018.2 | 50.5 | -5.048
1018.3 | 50.5 | -5.048
1018.4 | 50.5 | -5.048
1018.5 | 50.5 | -5.048
1018.6 | 50.5 | -5.048
1018.7 | 50.5 | -5.048
1018.8 | 50.5 | -5.048
1018.9 | 50.5 | -5.048
1019 | 50.5 | -5.048
1019.1 | 50.5 | -5.048
1019.2 | 50.5 | -5.048
1019.3 | 50.5 | -5.048
1019.4 | 50.5 | -5.048
1019.5 | 50.5 | -5.048
1019.6 | 50.5 | -5.048
1019.7 | 50.5 | -5.048
1019.8 | 50.5 | -5.048
1019.9 | 50.5 | -5.048
1020 | 50.5 | -5.048
1020.1 | 50.5 | -5.048
1020.2 | 50.5 | -5.048
1020.3 | 50.5 | -5.048
1020.4 | 50.5 | -5.048
1020.5 | 50.5 | -5.048
1020.6 | 50.5 | -5.048
1020.7 | 50.5 | -5.048
1020.8 | 50.5 | -5.048
1020.9 | 50.5 | -5.048
1021 | 50.5 | -5.048
1021.1 | 50.5 | -5.048
1021.2 | 50.5 | -5.048
1021.3 | 50.5 | -5.048
1021.4 | 50.5 | -5.048
1021.5 | 50.5 | -5.048
1021.6 | 50.5 | -5.048
1021.7 | 50.5 | -5.048
1021.8 | 50.5 | -5.047
1021.9 | 50.5 | -5.047
1022 | 50.5 | -5.047
1022.1 | 50.5 | -5.047
1022.2 | 50.5 | -5.047
1022.3 | 50.5 | -5.047
1022.4 | 50.5 | -5.047
1022.5 | 50.5 | -5.047
1022.6 | 50.5 | -5.047
1022.7 | 50.5 | -5.047
1022.8 | 50.5 | -5.047
1022.9 | 50.5 | -5.047
1023 | 50.5 | -5.047
1023.1 | 50.5 | -5.047
1023.2 | 50.5 | -5.047
1023.3 | 50.5 | -5.047
1023.4 | 50.5 | -5.047
1023.5 | 50.5 | -5.047
1023.6 | 50.5 | -5.047
1023.7 | 50.5 | -5.047
1023.8 | 50.5 | -5.047
1023.9 | 50.5 | -5.047
1024 | 50.5 | -5.047
1024.1 | 50.5 | -5.047
1024.2 | 50.5 | -5.048
1024.3 | 50.5 | -5.048
1024.4 | 50.5 | -5.048
1024.5 | 50.5 | -5.048
1024.6 | 50.5 | -5.048
1024.7 | 50.5 | -5.048
1024.8 | 50.5 | -5.048
1024.9 | 50.5 | -5.048
1025 | 50.5 | -5.048
1025.1 | 50.5 | -5.048
1025.2 | 50.5 | -5.048
1025.3 | 50.5 | -5.048
1025.4 | 50.5 | -5.048
1025.5 | 50.5 | -5.048
1025.6 | 50.5 | -5.048
1025.7 | 50.5 | -5.048
1025.8 | 50.5 | -5.048
1025.9 | 50.5 | -5.048
1026 | 50.5 | -5.048
1026.1 | 50.5 | -5.048
1026.2 | 50.5 | -5.048
1026.3 | 50.5 | -5.048
1026.4 | 50.5 | -5.048
1026.5 | 50.5 | -5.048
1026.6 | 50.5 | -5.048
1026.7 | 50.5 | -5.048
1026.8 | 50.5 | -5.048
1026.9 | 50.5 | -5.048
1027 | 50.5 | -5.048
1027.1 | 50.5 | -5.048
1027.2 | 50.5 | -5.048
1027.3 | 50.5 | -5.048
1027.4 | 50.5 | -5.048
1027.5 | 50.5 | -5.048
1027.6 | 50.5 | -5.048
1027.7 | 50.5 | -5.048
1027.8 | 50.5 | -5.048
1027.9 | 50.5 | -5.048
1028 | 50.5 | -5.048
1028.1 | 50.5 | -5.049
1028.2 | 50.5 | -5.049
1028.3 | 50.5 | -5.049
1028.4 | 50.5 | -5.049
1028.5 | 50.5 | -5.049
1028.6 | 50.5 | -5.049
1028.7 | 50.5 | -5.049
1028.8 | 50.5 | -5.048
1028.9 | 50.5 | -5.048
1029 | 50.5 | -5.048
1029.1 | 50.5 | -5.048
1029.2 | 50.5 | -5.048
1029.3 | 50.5 | -5.047
1029.4 | 50.5 | -5.048
1029.5 | 50.5 | -5.048
1029.6 | 50.5 | -5.048
1029.7 | 50.5 | -5.048
1029.8 | 50.5 | -5.048
1029.9 | 50.5 | -5.048
1030 | 50.5 | -5.048
1030.1 | 50.5 | -5.048
1030.2 | 50.5 | -5.048
1030.3 | 50.5 | -5.048
1030.4 | 50.5 | -5.048
1030.5 | 50.5 | -5.047
1030.6 | 50.5 | -5.047
1030.7 | 50.5 | -5.047
1030.8 | 50.5 | -5.047
1030.9 | 50.5 | -5.047
1031 | 50.5 | -5.047
1031.1 | 50.5 | -5.047
1031.2 | 50.5 | -5.047
1031.3 | 50.5 | -5.047
1031.4 | 50.5 | -5.047
1031.5 | 50.5 | -5.047
1031.6 | 50.5 | -5.047
1031.7 | 50.5 | -5.047
1031.8 | 50.5 | -5.047
1031.9 | 50.5 | -5.047
1032 | 50.5 | -5.047
1032.1 | 50.5 | -5.047
1032.2 | 50.5 | -5.047
1032.3 | 50.5 | -5.047
1032.4 | 50.5 | -5.047
1032.5 | 50.5 | -5.047
1032.6 | 50.5 | -5.047
1032.7 | 50.5 | -5.047
1032.8 | 50.5 | -5.047
1032.9 | 50.5 | -5.047
1033 | 50.5 | -5.047
1033.1 | 50.5 | -5.047
1033.2 | 50.5 | -5.047
1033.3 | 50.5 | -5.047
1033.4 | 50.5 | -5.047
1033.5 | 50.5 | -5.047
1033.6 | 50.5 | -5.047
1033.7 | 50.5 | -5.047
1033.8 | 50.5 | -5.047
1033.9 | 50.5 | -5.047
1034 | 50.5 | -5.047
1034.1 | 50.5 | -5.048
1034.2 | 50.5 | -5.048
1034.3 | 50.5 | -5.048
1034.4 | 50.5 | -5.048
1034.5 | 50.5 | -5.048
1034.6 | 50.5 | -5.048
1034.7 | 50.5 | -5.048
1034.8 | 50.5 | -5.048
1034.9 | 50.5 | -5.048
1035 | 50.5 | -5.048
1035.1 | 50.5 | -5.048
1035.2 | 50.5 | -5.048
1035.3 | 50.5 | -5.048
1035.4 | 50.5 | -5.048
1035.5 | 50.5 | -5.048
1035.6 | 50.5 | -5.048
1035.7 | 50.5 | -5.048
1035.8 | 50.5 | -5.048
1035.9 | 50.5 | -5.048
1036 | 50.5 | -5.048
1036.1 | 50.5 | -5.048
1036.2 | 50.5 | -5.048
1036.3 | 50.5 | -5.048
1036.4 | 50.5 | -5.048
1036.5 | 50.5 | -5.048
1036.6 | 50.5 | -5.048
1036.7 | 50.5 | -5.048
1036.8 | 50.5 | -5.048
1036.9 | 50.5 | -5.048
1037 | 50.5 | -5.048
1037.1 | 50.5 | -5.048
1037.2 | 50.5 | -5.048
1037.3 | 50.5 | -5.048
1037.4 | 50.5 | -5.048
1037.5 | 50.5 | -5.048
1037.6 | 50.5 | -5.047
1037.7 | 50.5 | -5.047
1037.8 | 50.5 | -5.047
1037.9 | 50.5 | -5.047
1038 | 50.5 | -5.047
1038.1 | 50.5 | -5.047
1038.2 | 50.5 | -5.047
1038.3 | 50.5 | -5.047
1038.4 | 50.5 | -5.047
1038.5 | 50.5 | -5.047
1038.6 | 50.5 | -5.047
1038.7 | 50.5 | -5.048
1038.8 | 50.5 | -5.048
1038.9 | 50.5 | -5.048
1039 | 50.5 | -5.048
1039.1 | 50.5 | -5.048
1039.2 | 50.5 | -5.048
1039.3 | 50.5 | -5.048
1039.4 | 50.5 | -5.048
1039.5 | 50.5 | -5.048
1039.6 | 50.5 | -5.048
1039.7 | 50.5 | -5.048
1039.8 | 50.5 | -5.048
1039.9 | 50.5 | -5.048
1040 | 50.5 | -5.048
1040.1 | 50.5 | -5.048
1040.2 | 50.5 | -5.048
1040.3 | 50.5 | -5.048
1040.4 | 50.5 | -5.048
1040.5 | 50.5 | -5.048
1040.6 | 50.5 | -5.048
1040.7 | 50.5 | -5.048
1040.8 | 50.5 | -5.048
1040.9 | 50.5 | -5.048
1041 | 50.5 | -5.048
1041.1 | 50.5 | -5.048
1041.2 | 50.5 | -5.048
1041.3 | 50.5 | -5.048
1041.4 | 50.5 | -5.048
1041.5 | 50.5 | -5.048
1041.6 | 50.5 | -5.048
1041.7 | 50.5 | -5.048
1041.8 | 50.5 | -5.048
1041.9 | 50.5 | -5.048
1042 | 50.5 | -5.048
1042.1 | 50.5 | -5.048
1042.2 | 50.5 | -5.048
1042.3 | 50.5 | -5.048
1042.4 | 50.5 | -5.047
1042.5 | 50.5 | -5.047
1042.6 | 50.5 | -5.047
1042.7 | 50.5 | -5.047
1042.8 | 50.5 | -5.047
1042.9 | 50.5 | -5.047
1043 | 50.5 | -5.047
1043.1 | 50.5 | -5.047
1043.2 | 50.5 | -5.047
1043.3 | 50.5 | -5.047
1043.4 | 50.5 | -5.047
1043.5 | 50.5 | -5.047
1043.6 | 50.5 | -5.047
1043.7 | 50.5 | -5.047
1043.8 | 50.5 | -5.047
1043.9 | 50.5 | -5.047
1044 | 50.5 | -5.047
1044.1 | 50.5 | -5.047
1044.2 | 50.5 | -5.047
1044.3 | 50.5 | -5.047
1044.4 | 50.5 | -5.047
1044.5 | 50.5 | -5.047
1044.6 | 50.5 | -5.048
1044.7 | 50.5 | -5.048
1044.8 | 50.5 | -5.048
1044.9 | 50.5 | -5.048
1045 | 50.5 | -5.048
1045.1 | 50.5 | -5.048
1045.2 | 50.5 | -5.048
1045.3 | 50.5 | -5.048
1045.4 | 50.5 | -5.048
1045.5 | 50.5 | -5.048
1045.6 | 50.5 | -5.048
1045.7 | 50.5 | -5.048
1045.8 | 50.5 | -5.048
1045.9 | 50.5 | -5.048
1046 | 50.5 | -5.048
1046.1 | 50.5 | -5.048
1046.2 | 50.5 | -5.048
1046.3 | 50.5 | -5.048
1046.4 | 50.5 | -5.048
1046.5 | 50.5 | -5.048
1046.6 | 50.5 | -5.048
1046.7 | 50.5 | -5.048
1046.8 | 50.5 | -5.048
1046.9 | 50.5 | -5.048
1047 | 50.5 | -5.048
1047.1 | 50.5 | -5.048
1047.2 | 50.5 | -5.048
1047.3 | 50.5 | -5.048
1047.4 | 50.5 | -5.048
1047.5 | 50.5 | -5.048
1047.6 | 50.5 | -5.048
1047.7 | 50.5 | -5.048
1047.8 | 50.5 | -5.048
1047.9 | 50.5 | -5.048
1048 | 50.5 | -5.048
1048.1 | 50.5 | -5.048
1048.2 | 50.5 | -5.048
1048.3 | 50.5 | -5.048
1048.4 | 50.5 | -5.048
1048.5 | 50.5 | -5.048
1048.6 | 50.5 | -5.048
1048.7 | 50.5 | -5.048
1048.8 | 50.5 | -5.048
1048.9 | 50.5 | -5.048
1049 | 50.5 | -5.048
1049.1 | 50.5 | -5.048
1049.2 | 50.5 | -5.048
1049.3 | 50.5 | -5.048
1049.4 | 50.5 | -5.048
1049.5 | 50.5 | -5.048
1049.6 | 50.5 | -5.048
1049.7 | 50.5 | -5.048
1049.8 | 50.5 | -5.048
1049.9 | 50.5 | -5.048
1050 | 50.5 | -5.048
1050.1 | 50.5 | -5.048
1050.2 | 50.5 | -5.048
1050.3 | 50.5 | -5.048
1050.4 | 50.5 | -5.048
1050.5 | 50.5 | -5.048
1050.6 | 50.5 | -5.048
1050.7 | 50.5 | -5.048
1050.8 | 50.5 | -5.048
1050.9 | 50.5 | -5.048
1051 | 50.5 | -5.048
1051.1 | 50.5 | -5.048
1051.2 | 50.5 | -5.048
1051.3 | 50.5 | -5.048
1051.4 | 50.5 | -5.048
1051.5 | 50.5 | -5.048
1051.6 | 50.5 | -5.048
1051.7 | 50.5 | -5.048
1051.8 | 50.5 | -5.048
1051.9 | 50.5 | -5.048
1052 | 50.5 | -5.048
1052.1 | 50.5 | -5.048
1052.2 | 50.5 | -5.048
1052.3 | 50.5 | -5.048
1052.4 | 50.5 | -5.048
1052.5 | 50.5 | -5.048
1052.6 | 50.5 | -5.048
1052.7 | 50.5 | -5.048
1052.8 | 50.5 | -5.048
1052.9 | 50.5 | -5.048
1053 | 50.5 | -5.048
1053.1 | 50.5 | -5.048
1053.2 | 50.5 | -5.048
1053.3 | 50.5 | -5.048
1053.4 | 50.5 | -5.048
1053.5 | 50.5 | -5.048
1053.6 | 50.5 | -5.048
1053.7 | 50.5 | -5.048
1053.8 | 50.5 | -5.048
1053.9 | 50.5 | -5.048
1054 | 50.5 | -5.048
1054.1 | 50.5 | -5.048
1054.2 | 50.5 | -5.048
1054.3 | 50.5 | -5.048
1054.4 | 50.5 | -5.048
1054.5 | 50.5 | -5.048
1054.6 | 50.5 | -5.048
1054.7 | 50.5 | -5.048
1054.8 | 50.5 | -5.048
1054.9 | 50.5 | -5.048
1055 | 50.5 | -5.048
1055.1 | 50.5 | -5.048
1055.2 | 50.5 | -5.048
1055.3 | 50.5 | -5.048
1055.4 | 50.5 | -5.048
1055.5 | 50.5 | -5.048
1055.6 | 50.5 | -5.048
1055.7 | 50.5 | -5.048
1055.8 | 50.5 | -5.048
1055.9 | 50.5 | -5.048
1056 | 50.5 | -5.048
1056.1 | 50.5 | -5.048
1056.2 | 50.5 | -5.048
1056.3 | 50.5 | -5.048
1056.4 | 50.5 | -5.048
1056.5 | 50.5 | -5.048
1056.6 | 50.5 | -5.048
1056.7 | 50.5 | -5.048
1056.8 | 50.5 | -5.048
1056.9 | 50.5 | -5.048
1057 | 50.5 | -5.048
1057.1 | 50.5 | -5.048
1057.2 | 50.5 | -5.048
1057.3 | 50.5 | -5.048
1057.4 | 50.5 | -5.048
1057.5 | 50.5 | -5.048
1057.6 | 50.5 | -5.048
1057.7 | 50.5 | -5.048
1057.8 | 50.5 | -5.048
1057.9 | 50.5 | -5.048
1058 | 50.5 | -5.048
1058.1 | 50.5 | -5.048
1058.2 | 50.5 | -5.048
1058.3 | 50.5 | -5.048
1058.4 | 50.5 | -5.048
1058.5 | 50.5 | -5.048
1058.6 | 50.5 | -5.048
1058.7 | 50.5 | -5.048
1058.8 | 50.5 | -5.048
1058.9 | 50.5 | -5.048
1059 | 50.5 | -5.048
1059.1 | 50.5 | -5.048
1059.2 | 50.5 | -5.048
1059.3 | 50.5 | -5.048
1059.4 | 50.5 | -5.048
1059.5 | 50.5 | -5.048
1059.6 | 50.5 | -5.048
1059.7 | 50.5 | -5.048
1059.8 | 50.5 | -5.048
1059.9 | 50.5 | -5.048
1060 | 50.5 | -5.048
1060.1 | 50.5 | -5.048
1060.2 | 50.5 | -5.047
1060.3 | 50.5 | -5.047
1060.4 | 50.5 | -5.047
1060.5 | 50.5 | -5.047
1060.6 | 50.5 | -5.047
1060.7 | 50.5 | -5.047
1060.8 | 50.5 | -5.047
1060.9 | 50.5 | -5.047
1061 | 50.5 | -5.047
1061.1 | 50.5 | -5.047
1061.2 | 50.5 | -5.047
1061.3 | 50.5 | -5.047
1061.4 | 50.5 | -5.047
1061.5 | 50.5 | -5.047
1061.6 | 50.5 | -5.047
1061.7 | 50.5 | -5.047
1061.8 | 50.5 | -5.047
1061.9 | 50.5 | -5.047
1062 | 50.5 | -5.047
1062.1 | 50.5 | -5.047
1062.2 | 50.5 | -5.047
1062.3 | 50.5 | -5.047
1062.4 | 50.5 | -5.047
1062.5 | 50.5 | -5.047
1062.6 | 50.5 | -5.048
1062.7 | 50.5 | -5.048
1062.8 | 50.5 | -5.048
1062.9 | 50.5 | -5.048
1063 | 50.5 | -5.048
1063.1 | 50.5 | -5.048
1063.2 | 50.5 | -5.048
1063.3 | 50.5 | -5.048
1063.4 | 50.5 | -5.048
1063.5 | 50.5 | -5.048
1063.6 | 50.5 | -5.048
1063.7 | 50.5 | -5.048
1063.8 | 50.5 | -5.048
1063.9 | 50.5 | -5.048
1064 | 50.5 | -5.048
1064.1 | 50.5 | -5.048
1064.2 | 50.5 | -5.048
1064.3 | 50.5 | -5.048
1064.4 | 50.5 | -5.048
1064.5 | 50.5 | -5.048
1064.6 | 50.5 | -5.048
1064.7 | 50.5 | -5.048
1064.8 | 50.5 | -5.048
1064.9 | 50.5 | -5.048
1065 | 50.5 | -5.048
1065.1 | 50.5 | -5.048
1065.2 | 50.5 | -5.048
1065.3 | 50.5 | -5.048
1065.4 | 50.5 | -5.048
1065.5 | 50.5 | -5.048
1065.6 | 50.5 | -5.048
1065.7 | 50.5 | -5.048
1065.8 | 50.5 | -5.048
1065.9 | 50.5 | -5.048
1066 | 50.5 | -5.048
1066.1 | 50.5 | -5.048
1066.2 | 50.5 | -5.048
1066.3 | 50.5 | -5.048
1066.4 | 50.5 | -5.048
1066.5 | 50.5 | -5.048
1066.6 | 50.5 | -5.048
1066.7 | 50.5 | -5.048
1066.8 | 50.5 | -5.048
1066.9 | 50.5 | -5.048
1067 | 50.5 | -5.048
1067.1 | 50.5 | -5.048
1067.2 | 50.5 | -5.048
1067.3 | 50.5 | -5.048
1067.4 | 50.5 | -5.048
1067.5 | 50.5 | -5.048
1067.6 | 50.5 | -5.048
1067.7 | 50.5 | -5.048
1067.8 | 50.5 | -5.048
1067.9 | 50.5 | -5.048
1068 | 50.5 | -5.048
1068.1 | 50.5 | -5.048
1068.2 | 50.5 | -5.048
1068.3 | 50.5 | -5.048
1068.4 | 50.5 | -5.048
1068.5 | 50.5 | -5.048
1068.6 | 50.5 | -5.048
1068.7 | 50.5 | -5.048
1068.8 | 50.5 | -5.048
1068.9 | 50.5 | -5.048
1069 | 50.5 | -5.048
1069.1 | 50.5 | -5.048
1069.2 | 50.5 | -5.048
1069.3 | 50.5 | -5.048
1069.4 | 50.5 | -5.048
1069.5 | 50.5 | -5.048
1069.6 | 50.5 | -5.048
1069.7 | 50.5 | -5.048
1069.8 | 50.5 | -5.048
1069.9 | 50.5 | -5.048
1070 | 50.5 | -5.048
1070.1 | 50.5 | -5.048
1070.2 | 50.5 | -5.048
1070.3 | 50.5 | -5.048
1070.4 | 50.5 | -5.048
1070.5 | 50.5 | -5.048
1070.6 | 50.5 | -5.048
1070.7 | 50.5 | -5.048
1070.8 | 50.5 | -5.048
1070.9 | 50.5 | -5.048
1071 | 50.5 | -5.048
1071.1 | 50.5 | -5.048
1071.2 | 50.5 | -5.048
1071.3 | 50.5 | -5.048
1071.4 | 50.5 | -5.048
1071.5 | 50.5 | -5.048
1071.6 | 50.5 | -5.048
1071.7 | 50.5 | -5.048
1071.8 | 50.5 | -5.048
1071.9 | 50.5 | -5.048
1072 | 50.5 | -5.048
1072.1 | 50.5 | -5.048
1072.2 | 50.5 | -5.048
1072.3 | 50.5 | -5.048
1072.4 | 50.5 | -5.048
1072.5 | 50.5 | -5.048
1072.6 | 50.5 | -5.048
1072.7 | 50.5 | -5.048
1072.8 | 50.5 | -5.048
1072.9 | 50.5 | -5.048
1073 | 50.5 | -5.048
1073.1 | 50.5 | -5.048
1073.2 | 50.5 | -5.048
1073.3 | 50.5 | -5.048
1073.4 | 50.5 | -5.048
1073.5 | 50.5 | -5.048
1073.6 | 50.5 | -5.048
1073.7 | 50.5 | -5.048
1073.8 | 50.5 | -5.048
1073.9 | 50.5 | -5.048
1074 | 50.5 | -5.048
1074.1 | 50.5 | -5.048
1074.2 | 50.5 | -5.048
1074.3 | 50.5 | -5.048
1074.4 | 50.5 | -5.048
1074.5 | 50.5 | -5.048
1074.6 | 50.5 | -5.048
1074.7 | 50.5 | -5.048
1074.8 | 50.5 | -5.048
1074.9 | 50.5 | -5.048
1075 | 50.5 | -5.048
1075.1 | 50.5 | -5.048
1075.2 | 50.5 | -5.048
1075.3 | 50.5 | -5.048
1075.4 | 50.5 | -5.047
1075.5 | 50.5 | -5.047
1075.6 | 50.5 | -5.047
1075.7 | 50.5 | -5.047
1075.8 | 50.5 | -5.047
1075.9 | 50.5 | -5.047
1076 | 50.5 | -5.047
1076.1 | 50.5 | -5.047
1076.2 | 50.5 | -5.047
1076.3 | 50.5 | -5.047
1076.4 | 50.5 | -5.048
1076.5 | 50.5 | -5.048
1076.6 | 50.5 | -5.048
1076.7 | 50.5 | -5.048
1076.8 | 50.5 | -5.048
1076.9 | 50.5 | -5.048
1077 | 50.5 | -5.048
1077.1 | 50.5 | -5.048
1077.2 | 50.5 | -5.048
1077.3 | 50.5 | -5.048
1077.4 | 50.5 | -5.048
1077.5 | 50.5 | -5.048
1077.6 | 50.5 | -5.048
1077.7 | 50.5 | -5.048
1077.8 | 50.5 | -5.048
1077.9 | 50.5 | -5.048
1078 | 50.5 | -5.048
1078.1 | 50.5 | -5.048
1078.2 | 50.5 | -5.048
1078.3 | 50.5 | -5.048
1078.4 | 50.5 | -5.048
1078.5 | 50.5 | -5.048
1078.6 | 50.5 | -5.048
1078.7 | 50.5 | -5.048
1078.8 | 50.5 | -5.048
1078.9 | 50.5 | -5.048
1079 | 50.5 | -5.048
1079.1 | 50.5 | -5.048
1079.2 | 50.5 | -5.048
1079.3 | 50.5 | -5.048
1079.4 | 50.5 | -5.048
1079.5 | 50.5 | -5.048
1079.6 | 50.5 | -5.048
1079.7 | 50.5 | -5.048
1079.8 | 50.5 | -5.048
1079.9 | 50.5 | -5.048
1080 | 50.5 | -5.048
1080.1 | 50.5 | -5.048
1080.2 | 50.5 | -5.048
1080.3 | 50.5 | -5.048
1080.4 | 50.5 | -5.048
1080.5 | 50.5 | -5.048
1080.6 | 50.5 | -5.048
1080.7 | 50.5 | -5.048
1080.8 | 50.5 | -5.048
1080.9 | 50.5 | -5.048
1081 | 50.5 | -5.048
1081.1 | 50.5 | -5.048
1081.2 | 50.5 | -5.048
1081.3 | 50.5 | -5.048
1081.4 | 50.5 | -5.048
1081.5 | 50.5 | -5.048
1081.6 | 50.5 | -5.048
1081.7 | 50.5 | -5.048
1081.8 | 50.5 | -5.048
1081.9 | 50.5 | -5.048
1082 | 50.5 | -5.048
1082.1 | 50.5 | -5.048
1082.2 | 50.5 | -5.047
1082.3 | 50.5 | -5.047
1082.4 | 50.5 | -5.047
1082.5 | 50.5 | -5.047
1082.6 | 50.5 | -5.047
1082.7 | 50.5 | -5.047
1082.8 | 50.5 | -5.047
1082.9 | 50.5 | -5.047
1083 | 50.5 | -5.047
1083.1 | 50.5 | -5.047
1083.2 | 50.5 | -5.047
1083.3 | 50.5 | -5.047
1083.4 | 50.5 | -5.048
1083.5 | 50.5 | -5.048
1083.6 | 50.5 | -5.048
1083.7 | 50.5 | -5.048
1083.8 | 50.5 | -5.048
1083.9 | 50.5 | -5.048
1084 | 50.5 | -5.048
1084.1 | 50.5 | -5.048
1084.2 | 50.5 | -5.048
1084.3 | 50.5 | -5.048
1084.4 | 50.5 | -5.048
1084.5 | 50.5 | -5.048
1084.6 | 50.5 | -5.048
1084.7 | 50.5 | -5.048
1084.8 | 50.5 | -5.048
1084.9 | 50.5 | -5.048
1085 | 50.5 | -5.048
1085.1 | 50.5 | -5.048
1085.2 | 50.5 | -5.048
1085.3 | 50.5 | -5.048
1085.4 | 50.5 | -5.048
1085.5 | 50.5 | -5.048
1085.6 | 50.5 | -5.048
1085.7 | 50.5 | -5.048
1085.8 | 50.5 | -5.048
1085.9 | 50.5 | -5.048
1086 | 50.5 | -5.048
1086.1 | 50.5 | -5.048
1086.2 | 50.5 | -5.048
1086.3 | 50.5 | -5.048
1086.4 | 50.5 | -5.048
1086.5 | 50.5 | -5.048
1086.6 | 50.5 | -5.048
1086.7 | 50.5 | -5.048
1086.8 | 50.5 | -5.048
1086.9 | 50.5 | -5.048
1087 | 50.5 | -5.048
1087.1 | 50.5 | -5.048
1087.2 | 50.5 | -5.048
1087.3 | 50.5 | -5.048
1087.4 | 50.5 | -5.048
1087.5 | 50.5 | -5.048
1087.6 | 50.5 | -5.048
1087.7 | 50.5 | -5.048
1087.8 | 50.5 | -5.048
1087.9 | 50.5 | -5.048
1088 | 50.5 | -5.048
1088.1 | 50.5 | -5.048
1088.2 | 50.5 | -5.048
1088.3 | 50.5 | -5.048
1088.4 | 50.5 | -5.048
1088.5 | 50.5 | -5.048
1088.6 | 50.5 | -5.048
1088.7 | 50.5 | -5.048
1088.8 | 50.5 | -5.048
1088.9 | 50.5 | -5.048
1089 | 50.5 | -5.048
1089.1 | 50.5 | -5.048
1089.2 | 50.5 | -5.048
1089.3 | 50.5 | -5.048
1089.4 | 50.5 | -5.048
1089.5 | 50.5 | -5.048
1089.6 | 50.5 | -5.048
1089.7 | 50.5 | -5.048
1089.8 | 50.5 | -5.048
1089.9 | 50.5 | -5.048
1090 | 50.5 | -5.048
1090.1 | 50.5 | -5.048
1090.2 | 50.5 | -5.048
1090.3 | 50.5 | -5.048
1090.4 | 50.5 | -5.048
1090.5 | 50.5 | -5.048
1090.6 | 50.5 | -5.048
1090.7 | 50.5 | -5.048
1090.8 | 50.5 | -5.048
1090.9 | 50.5 | -5.048
1091 | 50.5 | -5.048
1091.1 | 50.5 | -5.048
1091.2 | 50.5 | -5.048
1091.3 | 50.5 | -5.048
1091.4 | 50.5 | -5.048
1091.5 | 50.5 | -5.048
1091.6 | 50.5 | -5.048
1091.7 | 50.5 | -5.048
1091.8 | 50.5 | -5.048
1091.9 | 50.5 | -5.048
1092 | 50.5 | -5.048
1092.1 | 50.5 | -5.048
1092.2 | 50.5 | -5.048
1092.3 | 50.5 | -5.048
1092.4 | 50.5 | -5.048
1092.5 | 50.5 | -5.048
1092.6 | 50.5 | -5.048
1092.7 | 50.5 | -5.048
1092.8 | 50.5 | -5.048
1092.9 | 50.5 | -5.048
1093 | 50.5 | -5.048
1093.1 | 50.5 | -5.048
1093.2 | 50.5 | -5.048
1093.3 | 50.5 | -5.048
1093.4 | 50.5 | -5.048
1093.5 | 50.5 | -5.048
1093.6 | 50.5 | -5.048
1093.7 | 50.5 | -5.048
1093.8 | 50.5 | -5.048
1093.9 | 50.5 | -5.048
1094 | 50.5 | -5.048
1094.1 | 50.5 | -5.048
1094.2 | 50.5 | -5.048
1094.3 | 50.5 | -5.048
1094.4 | 50.5 | -5.048
1094.5 | 50.5 | -5.048
1094.6 | 50.5 | -5.048
1094.7 | 50.5 | -5.048
1094.8 | 50.5 | -5.048
1094.9 | 50.5 | -5.048
1095 | 50.5 | -5.048
1095.1 | 50.5 | -5.048
1095.2 | 50.5 | -5.048
1095.3 | 50.5 | -5.048
1095.4 | 50.5 | -5.048
1095.5 | 50.5 | -5.048
1095.6 | 50.5 | -5.048
1095.7 | 50.5 | -5.048
1095.8 | 50.5 | -5.048
1095.9 | 50.5 | -5.048
1096 | 50.5 | -5.048
1096.1 | 50.5 | -5.048
1096.2 | 50.5 | -5.048
1096.3 | 50.5 | -5.048
1096.4 | 50.5 | -5.048
1096.5 | 50.5 | -5.048
1096.6 | 50.5 | -5.048
1096.7 | 50.5 | -5.048
1096.8 | 50.5 | -5.048
1096.9 | 50.5 | -5.048
1097 | 50.5 | -5.048
1097.1 | 50.5 | -5.048
1097.2 | 50.5 | -5.048
1097.3 | 50.5 | -5.048
1097.4 | 50.5 | -5.048
1097.5 | 50.5 | -5.048
1097.6 | 50.5 | -5.048
1097.7 | 50.5 | -5.048
1097.8 | 50.5 | -5.048
1097.9 | 50.5 | -5.048
1098 | 50.5 | -5.048
1098.1 | 50.5 | -5.048
1098.2 | 50.5 | -5.048
1098.3 | 50.5 | -5.048
1098.4 | 50.5 | -5.048
1098.5 | 50.5 | -5.048
1098.6 | 50.5 | -5.048
1098.7 | 50.5 | -5.048
1098.8 | 50.5 | -5.048
1098.9 | 50.5 | -5.048
1099 | 50.5 | -5.048
1099.1 | 50.5 | -5.048
1099.2 | 50.5 | -5.048
1099.3 | 50.5 | -5.048
1099.4 | 50.5 | -5.048
1099.5 | 50.5 | -5.048
1099.6 | 50.5 | -5.048
1099.7 | 50.5 | -5.048
1099.8 | 50.5 | -5.048
1099.9 | 50.5 | -5.048
1100 | 50.5 | -5.048
1100.1 | 50.5 | -5.048
1100.2 | 50.5 | -5.048
1100.3 | 50.5 | -5.048
1100.4 | 50.5 | -5.048
1100.5 | 50.5 | -5.048
1100.6 | 50.5 | -5.048
1100.7 | 50.5 | -5.048
1100.8 | 50.5 | -5.048
1100.9 | 50.5 | -5.048
1101 | 50.5 | -5.048
1101.1 | 50.5 | -5.048
1101.2 | 50.5 | -5.048
1101.3 | 50.5 | -5.048
1101.4 | 50.5 | -5.048
1101.5 | 50.5 | -5.048
1101.6 | 50.5 | -5.048
1101.7 | 50.5 | -5.048
1101.8 | 50.5 | -5.048
1101.9 | 50.5 | -5.048
1102 | 50.5 | -5.048
1102.1 | 50.5 | -5.048
1102.2 | 50.5 | -5.048
1102.3 | 50.5 | -5.048
1102.4 | 50.5 | -5.048
1102.5 | 50.5 | -5.048
1102.6 | 50.5 | -5.048
1102.7 | 50.5 | -5.048
1102.8 | 50.5 | -5.048
1102.9 | 50.5 | -5.048
1103 | 50.5 | -5.048
1103.1 | 50.5 | -5.048
1103.2 | 50.5 | -5.048
1103.3 | 50.5 | -5.048
1103.4 | 50.5 | -5.048
1103.5 | 50.5 | -5.048
1103.6 | 50.5 | -5.048
1103.7 | 50.5 | -5.048
1103.8 | 50.5 | -5.048
1103.9 | 50.5 | -5.048
1104 | 50.5 | -5.048
1104.1 | 50.5 | -5.048
1104.2 | 50.5 | -5.048
1104.3 | 50.5 | -5.048
1104.4 | 50.5 | -5.048
1104.5 | 50.5 | -5.048
1104.6 | 50.5 | -5.048
1104.7 | 50.5 | -5.048
1104.8 | 50.5 | -5.048
1104.9 | 50.5 | -5.048
1105 | 50.5 | -5.048
1105.1 | 50.5 | -5.048
1105.2 | 50.5 | -5.048
1105.3 | 50.5 | -5.048
1105.4 | 50.5 | -5.048
1105.5 | 50.5 | -5.048
1105.6 | 50.5 | -5.048
1105.7 | 50.5 | -5.048
1105.8 | 50.5 | -5.048
1105.9 | 50.5 | -5.048
1106 | 50.5 | -5.048
1106.1 | 50.5 | -5.048
1106.2 | 50.5 | -5.048
1106.3 | 50.5 | -5.048
1106.4 | 50.5 | -5.048
1106.5 | 50.5 | -5.048
1106.6 | 50.5 | -5.048
1106.7 | 50.5 | -5.048
1106.8 | 50.5 | -5.048
1106.9 | 50.5 | -5.048
1107 | 50.5 | -5.048
1107.1 | 50.5 | -5.048
1107.2 | 50.5 | -5.048
1107.3 | 50.5 | -5.048
1107.4 | 50.5 | -5.048
1107.5 | 50.5 | -5.048
1107.6 | 50.5 | -5.048
1107.7 | 50.5 | -5.048
1107.8 | 50.5 | -5.048
1107.9 | 50.5 | -5.048
1108 | 50.5 | -5.048
1108.1 | 50.5 | -5.048
1108.2 | 50.5 | -5.048
1108.3 | 50.5 | -5.048
1108.4 | 50.5 | -5.048
1108.5 | 50.5 | -5.048
1108.6 | 50.5 | -5.048
1108.7 | 50.5 | -5.048
1108.8 | 50.5 | -5.048
1108.9 | 50.5 | -5.048
1109 | 50.5 | -5.048
1109.1 | 50.5 | -5.048
1109.2 | 50.5 | -5.048
1109.3 | 50.5 | -5.048
1109.4 | 50.5 | -5.048
1109.5 | 50.5 | -5.048
1109.6 | 50.5 | -5.048
1109.7 | 50.5 | -5.048
1109.8 | 50.5 | -5.048
1109.9 | 50.5 | -5.048
1110 | 50.5 | -5.048
1110.1 | 50.5 | -5.048
1110.2 | 50.5 | -5.048
1110.3 | 50.5 | -5.048
1110.4 | 50.5 | -5.048
1110.5 | 50.5 | -5.048
1110.6 | 50.5 | -5.048
1110.7 | 50.5 | -5.048
1110.8 | 50.5 | -5.048
1110.9 | 50.5 | -5.048
1111 | 50.5 | -5.048
1111.1 | 50.5 | -5.048
1111.2 | 50.5 | -5.048
1111.3 | 50.5 | -5.048
1111.4 | 50.5 | -5.048
1111.5 | 50.5 | -5.048
1111.6 | 50.5 | -5.048
1111.7 | 50.5 | -5.048
1111.8 | 50.5 | -5.048
1111.9 | 50.5 | -5.048
1112 | 50.5 | -5.048
1112.1 | 50.5 | -5.048
1112.2 | 50.5 | -5.048
1112.3 | 50.5 | -5.048
1112.4 | 50.5 | -5.048
1112.5 | 50.5 | -5.048
1112.6 | 50.5 | -5.048
1112.7 | 50.5 | -5.048
1112.8 | 50.5 | -5.048
1112.9 | 50.5 | -5.048
1113 | 50.5 | -5.048
1113.1 | 50.5 | -5.048
1113.2 | 50.5 | -5.048
1113.3 | 50.5 | -5.048
1113.4 | 50.5 | -5.048
1113.5 | 50.5 | -5.048
1113.6 | 50.5 | -5.048
1113.7 | 50.5 | -5.048
1113.8 | 50.5 | -5.048
1113.9 | 50.5 | -5.048
1114 | 50.5 | -5.048
1114.1 | 50.5 | -5.048
1114.2 | 50.5 | -5.048
1114.3 | 50.5 | -5.048
1114.4 | 50.5 | -5.048
1114.5 | 50.5 | -5.048
1114.6 | 50.5 | -5.048
1114.7 | 50.5 | -5.048
1114.8 | 50.5 | -5.048
1114.9 | 50.5 | -5.048
1115 | 50.5 | -5.048
1115.1 | 50.5 | -5.048
1115.2 | 50.5 | -5.048
1115.3 | 50.5 | -5.048
1115.4 | 50.5 | -5.048
1115.5 | 50.5 | -5.048
1115.6 | 50.5 | -5.048
1115.7 | 50.5 | -5.048
1115.8 | 50.5 | -5.048
1115.9 | 50.5 | -5.048
1116 | 50.5 | -5.048
1116.1 | 50.5 | -5.048
1116.2 | 50.5 | -5.048
1116.3 | 50.5 | -5.048
1116.4 | 50.5 | -5.048
1116.5 | 50.5 | -5.048
1116.6 | 50.5 | -5.048
1116.7 | 50.5 | -5.048
1116.8 | 50.5 | -5.048
1116.9 | 50.5 | -5.048
1117 | 50.5 | -5.048
1117.1 | 50.5 | -5.048
1117.2 | 50.5 | -5.048
1117.3 | 50.5 | -5.048
1117.4 | 50.5 | -5.048
1117.5 | 50.5 | -5.048
1117.6 | 50.5 | -5.048
1117.7 | 50.5 | -5.048
1117.8 | 50.5 | -5.048
1117.9 | 50.5 | -5.048
1118 | 50.5 | -5.048
1118.1 | 50.5 | -5.048
1118.2 | 50.5 | -5.048
1118.3 | 50.5 | -5.048
1118.4 | 50.5 | -5.048
1118.5 | 50.5 | -5.048
1118.6 | 50.5 | -5.048
1118.7 | 50.5 | -5.048
1118.8 | 50.5 | -5.048
1118.9 | 50.5 | -5.048
1119 | 50.5 | -5.048
1119.1 | 50.5 | -5.048
1119.2 | 50.5 | -5.048
1119.3 | 50.5 | -5.048
1119.4 | 50.5 | -5.048
1119.5 | 50.5 | -5.048
1119.6 | 50.5 | -5.048
1119.7 | 50.5 | -5.048
1119.8 | 50.5 | -5.048
1119.9 | 50.5 | -5.048
1120 | 50.5 | -5.048
1120.1 | 50.5 | -5.048
1120.2 | 50.5 | -5.048
1120.3 | 50.5 | -5.048
1120.4 | 50.5 | -5.048
1120.5 | 50.5 | -5.048
1120.6 | 50.5 | -5.048
1120.7 | 50.5 | -5.048
1120.8 | 50.5 | -5.048
1120.9 | 50.5 | -5.048
1121 | 50.5 | -5.048
1121.1 | 50.5 | -5.048
1121.2 | 50.5 | -5.048
1121.3 | 50.5 | -5.048
1121.4 | 50.5 | -5.048
1121.5 | 50.5 | -5.048
1121.6 | 50.5 | -5.048
1121.7 | 50.5 | -5.048
1121.8 | 50.5 | -5.047
1121.9 | 50.5 | -5.047
1122 | 50.5 | -5.047
1122.1 | 50.5 | -5.047
1122.2 | 50.5 | -5.047
1122.3 | 50.5 | -5.047
1122.4 | 50.5 | -5.047
1122.5 | 50.5 | -5.047
1122.6 | 50.5 | -5.047
1122.7 | 50.5 | -5.047
1122.8 | 50.5 | -5.047
1122.9 | 50.5 | -5.047
1123 | 50.5 | -5.048
1123.1 | 50.5 | -5.048
1123.2 | 50.5 | -5.048
1123.3 | 50.5 | -5.048
1123.4 | 50.5 | -5.048
1123.5 | 50.5 | -5.048
1123.6 | 50.5 | -5.048
1123.7 | 50.5 | -5.048
1123.8 | 50.5 | -5.048
1123.9 | 50.5 | -5.048
1124 | 50.5 | -5.048
1124.1 | 50.5 | -5.048
1124.2 | 50.5 | -5.048
1124.3 | 50.5 | -5.048
1124.4 | 50.5 | -5.048
1124.5 | 50.5 | -5.048
1124.6 | 50.5 | -5.048
1124.7 | 50.5 | -5.048
1124.8 | 50.5 | -5.048
1124.9 | 50.5 | -5.048
1125 | 50.5 | -5.048
1125.1 | 50.5 | -5.048
1125.2 | 50.5 | -5.048
1125.3 | 50.5 | -5.048
1125.4 | 50.5 | -5.048
1125.5 | 50.5 | -5.048
1125.6 | 50.5 | -5.048
1125.7 | 50.5 | -5.048
1125.8 | 50.5 | -5.048
1125.9 | 50.5 | -5.048
1126 | 50.5 | -5.048
1126.1 | 50.5 | -5.048
1126.2 | 50.5 | -5.048
1126.3 | 50.5 | -5.048
1126.4 | 50.5 | -5.048
1126.5 | 50.5 | -5.048
1126.6 | 50.5 | -5.048
1126.7 | 50.5 | -5.048
1126.8 | 50.5 | -5.048
1126.9 | 50.5 | -5.048
1127 | 50.5 | -5.048
1127.1 | 50.5 | -5.048
1127.2 | 50.5 | -5.048
1127.3 | 50.5 | -5.048
1127.4 | 50.5 | -5.048
1127.5 | 50.5 | -5.048
1127.6 | 50.5 | -5.047
1127.7 | 50.5 | -5.047
1127.8 | 50.5 | -5.047
1127.9 | 50.5 | -5.047
1128 | 50.5 | -5.047
1128.1 | 50.5 | -5.047
1128.2 | 50.5 | -5.047
1128.3 | 50.5 | -5.047
1128.4 | 50.5 | -5.047
1128.5 | 50.5 | -5.047
1128.6 | 50.5 | -5.047
1128.7 | 50.5 | -5.047
1128.8 | 50.5 | -5.048
1128.9 | 50.5 | -5.048
1129 | 50.5 | -5.048
1129.1 | 50.5 | -5.048
1129.2 | 50.5 | -5.048
1129.3 | 50.5 | -5.048
1129.4 | 50.5 | -5.048
1129.5 | 50.5 | -5.048
1129.6 | 50.5 | -5.048
1129.7 | 50.5 | -5.048
1129.8 | 50.5 | -5.048
1129.9 | 50.5 | -5.048
1130 | 50.5 | -5.048
1130.1 | 50.5 | -5.048
1130.2 | 50.5 | -5.048
1130.3 | 50.5 | -5.048
1130.4 | 50.5 | -5.048
1130.5 | 50.5 | -5.048
1130.6 | 50.5 | -5.048
1130.7 | 50.5 | -5.048
1130.8 | 50.5 | -5.048
1130.9 | 50.5 | -5.048
1131 | 50.5 | -5.048
1131.1 | 50.5 | -5.048
1131.2 | 50.5 | -5.048
1131.3 | 50.5 | -5.048
1131.4 | 50.5 | -5.048
1131.5 | 50.5 | -5.048
1131.6 | 50.5 | -5.048
1131.7 | 50.5 | -5.048
1131.8 | 50.5 | -5.048
1131.9 | 50.5 | -5.048
1132 | 50.5 | -5.048
1132.1 | 50.5 | -5.048
1132.2 | 50.5 | -5.048
1132.3 | 50.5 | -5.048
1132.4 | 50.5 | -5.048
1132.5 | 50.5 | -5.048
1132.6 | 50.5 | -5.048
1132.7 | 50.5 | -5.048
1132.8 | 50.5 | -5.048
1132.9 | 50.5 | -5.048
1133 | 50.5 | -5.048
1133.1 | 50.5 | -5.048
1133.2 | 50.5 | -5.048
1133.3 | 50.5 | -5.048
1133.4 | 50.5 | -5.048
1133.5 | 50.5 | -5.048
1133.6 | 50.5 | -5.047
1133.7 | 50.5 | -5.047
1133.8 | 50.5 | -5.047
1133.9 | 50.5 | -5.047
1134 | 50.5 | -5.047
1134.1 | 50.5 | -5.047
1134.2 | 50.5 | -5.047
1134.3 | 50.5 | -5.047
1134.4 | 50.5 | -5.047
1134.5 | 50.5 | -5.047
1134.6 | 50.5 | -5.048
1134.7 | 50.5 | -5.048
1134.8 | 50.5 | -5.048
1134.9 | 50.5 | -5.048
1135 | 50.5 | -5.048
1135.1 | 50.5 | -5.048
1135.2 | 50.5 | -5.048
1135.3 | 50.5 | -5.048
1135.4 | 50.5 | -5.048
1135.5 | 50.5 | -5.048
1135.6 | 50.5 | -5.048
1135.7 | 50.5 | -5.048
1135.8 | 50.5 | -5.048
1135.9 | 50.5 | -5.048
1136 | 50.5 | -5.048
1136.1 | 50.5 | -5.048
1136.2 | 50.5 | -5.048
1136.3 | 50.5 | -5.048
1136.4 | 50.5 | -5.048
1136.5 | 50.5 | -5.048
1136.6 | 50.5 | -5.048
1136.7 | 50.5 | -5.048
1136.8 | 50.5 | -5.048
1136.9 | 50.5 | -5.048
1137 | 50.5 | -5.048
1137.1 | 50.5 | -5.048
1137.2 | 50.5 | -5.048
1137.3 | 50.5 | -5.049
1137.4 | 50.5 | -5.049
1137.5 | 50.5 | -5.049
1137.6 | 50.5 | -5.049
1137.7 | 50.5 | -5.049
1137.8 | 50.5 | -5.049
1137.9 | 50.5 | -5.049
1138 | 50.5 | -5.049
1138.1 | 50.5 | -5.048
1138.2 | 50.5 | -5.048
1138.3 | 50.5 | -5.048
1138.4 | 50.5 | -5.048
1138.5 | 50.5 | -5.048
1138.6 | 50.5 | -5.048
1138.7 | 50.5 | -5.048
1138.8 | 50.5 | -5.048
1138.9 | 50.5 | -5.048
1139 | 50.5 | -5.048
1139.1 | 50.5 | -5.048
1139.2 | 50.5 | -5.048
1139.3 | 50.5 | -5.047
1139.4 | 50.5 | -5.047
1139.5 | 50.5 | -5.047
1139.6 | 50.5 | -5.047
1139.7 | 50.5 | -5.047
1139.8 | 50.5 | -5.047
1139.9 | 50.5 | -5.047
1140 | 50.5 | -5.047
1140.1 | 50.5 | -5.047
1140.2 | 50.5 | -5.047
1140.3 | 50.5 | -5.047
1140.4 | 50.5 | -5.047
1140.5 | 50.5 | -5.047
1140.6 | 50.5 | -5.047
1140.7 | 50.5 | -5.047
1140.8 | 50.5 | -5.048
1140.9 | 50.5 | -5.048
1141 | 50.5 | -5.048
1141.1 | 50.5 | -5.048
1141.2 | 50.5 | -5.048
1141.3 | 50.5 | -5.048
1141.4 | 50.5 | -5.048
1141.5 | 50.5 | -5.048
1141.6 | 50.5 | -5.048
1141.7 | 50.5 | -5.048
1141.8 | 50.5 | -5.048
1141.9 | 50.5 | -5.048
1142 | 50.5 | -5.048
1142.1 | 50.5 | -5.048
1142.2 | 50.5 | -5.048
1142.3 | 50.5 | -5.048
1142.4 | 50.5 | -5.048
1142.5 | 50.5 | -5.048
1142.6 | 50.5 | -5.048
1142.7 | 50.5 | -5.048
1142.8 | 50.5 | -5.048
1142.9 | 50.5 | -5.048
1143 | 50.5 | -5.048
1143.1 | 50.5 | -5.048
1143.2 | 50.5 | -5.048
1143.3 | 50.5 | -5.048
1143.4 | 50.5 | -5.048
1143.5 | 50.5 | -5.048
1143.6 | 50.5 | -5.048
1143.7 | 50.5 | -5.048
1143.8 | 50.5 | -5.048
1143.9 | 50.5 | -5.048
1144 | 50.5 | -5.048
1144.1 | 50.5 | -5.048
1144.2 | 50.5 | -5.048
1144.3 | 50.5 | -5.048
1144.4 | 50.5 | -5.048
1144.5 | 50.5 | -5.048
1144.6 | 50.5 | -5.048
1144.7 | 50.5 | -5.048
1144.8 | 50.5 | -5.048
1144.9 | 50.5 | -5.048
1145 | 50.5 | -5.048
1145.1 | 50.5 | -5.048
1145.2 | 50.5 | -5.048
1145.3 | 50.5 | -5.048
1145.4 | 50.5 | -5.048
1145.5 | 50.5 | -5.048
1145.6 | 50.5 | -5.048
1145.7 | 50.5 | -5.048
1145.8 | 50.5 | -5.048
1145.9 | 50.5 | -5.048
1146 | 50.5 | -5.048
1146.1 | 50.5 | -5.048
1146.2 | 50.5 | -5.048
1146.3 | 50.5 | -5.048
1146.4 | 50.5 | -5.048
1146.5 | 50.5 | -5.048
1146.6 | 50.5 | -5.047
1146.7 | 50.5 | -5.047
1146.8 | 50.5 | -5.047
1146.9 | 50.5 | -5.047
1147 | 50.5 | -5.047
1147.1 | 50.5 | -5.047
1147.2 | 50.5 | -5.047
1147.3 | 50.5 | -5.047
1147.4 | 50.5 | -5.047
1147.5 | 50.5 | -5.047
1147.6 | 50.5 | -5.047
1147.7 | 50.5 | -5.047
1147.8 | 50.5 | -5.048
1147.9 | 50.5 | -5.048
1148 | 50.5 | -5.048
1148.1 | 50.5 | -5.048
1148.2 | 50.5 | -5.048
1148.3 | 50.5 | -5.048
1148.4 | 50.5 | -5.048
1148.5 | 50.5 | -5.048
1148.6 | 50.5 | -5.048
1148.7 | 50.5 | -5.048
1148.8 | 50.5 | -5.048
1148.9 | 50.5 | -5.048
1149 | 50.5 | -5.048
1149.1 | 50.5 | -5.048
1149.2 | 50.5 | -5.048
1149.3 | 50.5 | -5.048
1149.4 | 50.5 | -5.048
1149.5 | 50.5 | -5.048
1149.6 | 50.5 | -5.048
1149.7 | 50.5 | -5.048
1149.8 | 50.5 | -5.048
1149.9 | 50.5 | -5.048
1150 | 50.5 | -5.048
1150.1 | 50.5 | -5.048
1150.2 | 50.5 | -5.048
1150.3 | 50.5 | -5.048
1150.4 | 50.5 | -5.048
1150.5 | 50.5 | -5.048
1150.6 | 50.5 | -5.048
1150.7 | 50.5 | -5.048
1150.8 | 50.5 | -5.048
1150.9 | 50.5 | -5.048
1151 | 50.5 | -5.048
1151.1 | 50.5 | -5.048
1151.2 | 50.5 | -5.048
1151.3 | 50.5 | -5.048
1151.4 | 50.5 | -5.048
1151.5 | 50.5 | -5.048
1151.6 | 50.5 | -5.048
1151.7 | 50.5 | -5.048
1151.8 | 50.5 | -5.048
1151.9 | 50.5 | -5.048
1152 | 50.5 | -5.048
1152.1 | 50.5 | -5.048
1152.2 | 50.5 | -5.048
1152.3 | 50.5 | -5.048
1152.4 | 50.5 | -5.048
1152.5 | 50.5 | -5.048
1152.6 | 50.5 | -5.047
1152.7 | 50.5 | -5.047
1152.8 | 50.5 | -5.047
1152.9 | 50.5 | -5.047
1153 | 50.5 | -5.047
1153.1 | 50.5 | -5.047
1153.2 | 50.5 | -5.047
1153.3 | 50.5 | -5.047
1153.4 | 50.5 | -5.047
1153.5 | 50.5 | -5.047
1153.6 | 50.5 | -5.047
1153.7 | 50.5 | -5.048
1153.8 | 50.5 | -5.048
1153.9 | 50.5 | -5.048
1154 | 50.5 | -5.048
1154.1 | 50.5 | -5.048
1154.2 | 50.5 | -5.048
1154.3 | 50.5 | -5.048
1154.4 | 50.5 | -5.048
1154.5 | 50.5 | -5.048
1154.6 | 50.5 | -5.048
1154.7 | 50.5 | -5.048
1154.8 | 50.5 | -5.048
1154.9 | 50.5 | -5.048
1155 | 50.5 | -5.048
1155.1 | 50.5 | -5.048
1155.2 | 50.5 | -5.048
1155.3 | 50.5 | -5.048
1155.4 | 50.5 | -5.048
1155.5 | 50.5 | -5.048
1155.6 | 50.5 | -5.048
1155.7 | 50.5 | -5.048
1155.8 | 50.5 | -5.048
1155.9 | 50.5 | -5.048
1156 | 50.5 | -5.048
1156.1 | 50.5 | -5.048
1156.2 | 50.5 | -5.048
1156.3 | 50.5 | -5.048
1156.4 | 50.5 | -5.048
1156.5 | 50.5 | -5.048
1156.6 | 50.5 | -5.048
1156.7 | 50.5 | -5.048
1156.8 | 50.5 | -5.048
1156.9 | 50.5 | -5.048
1157 | 50.5 | -5.048
1157.1 | 50.5 | -5.048
1157.2 | 50.5 | -5.048
1157.3 | 50.5 | -5.048
1157.4 | 50.5 | -5.048
1157.5 | 50.5 | -5.048
1157.6 | 50.5 | -5.048
1157.7 | 50.5 | -5.048
1157.8 | 50.5 | -5.048
1157.9 | 50.5 | -5.048
1158 | 50.5 | -5.048
1158.1 | 50.5 | -5.048
1158.2 | 50.5 | -5.048
1158.3 | 50.5 | -5.048
1158.4 | 50.5 | -5.047
1158.5 | 50.5 | -5.047
1158.6 | 50.5 | -5.047
1158.7 | 50.5 | -5.047
1158.8 | 50.5 | -5.047
1158.9 | 50.5 | -5.047
1159 | 50.5 | -5.047
1159.1 | 50.5 | -5.047
1159.2 | 50.5 | -5.047
1159.3 | 50.5 | -5.047
1159.4 | 50.5 | -5.048
1159.5 | 50.5 | -5.048
1159.6 | 50.5 | -5.048
1159.7 | 50.5 | -5.048
1159.8 | 50.5 | -5.048
1159.9 | 50.5 | -5.048
1160 | 50.5 | -5.048
1160.1 | 50.5 | -5.048
1160.2 | 50.5 | -5.048
1160.3 | 50.5 | -5.048
1160.4 | 50.5 | -5.048
1160.5 | 50.5 | -5.048
1160.6 | 50.5 | -5.048
1160.7 | 50.5 | -5.048
1160.8 | 50.5 | -5.048
1160.9 | 50.5 | -5.048
1161 | 50.5 | -5.048
1161.1 | 50.5 | -5.048
1161.2 | 50.5 | -5.048
1161.3 | 50.5 | -5.048
1161.4 | 50.5 | -5.048
1161.5 | 50.5 | -5.048
1161.6 | 50.5 | -5.048
1161.7 | 50.5 | -5.048
1161.8 | 50.5 | -5.048
1161.9 | 50.5 | -5.048
1162 | 50.5 | -5.048
1162.1 | 50.5 | -5.048
1162.2 | 50.5 | -5.048
1162.3 | 50.5 | -5.048
1162.4 | 50.5 | -5.048
1162.5 | 50.5 | -5.048
1162.6 | 50.5 | -5.048
1162.7 | 50.5 | -5.048
1162.8 | 50.5 | -5.048
1162.9 | 50.5 | -5.048
1163 | 50.5 | -5.048
1163.1 | 50.5 | -5.048
1163.2 | 50.5 | -5.048
1163.3 | 50.5 | -5.048
1163.4 | 50.5 | -5.048
1163.5 | 50.5 | -5.048
1163.6 | 50.5 | -5.048
1163.7 | 50.5 | -5.048
1163.8 | 50.5 | -5.048
1163.9 | 50.5 | -5.048
1164 | 50.5 | -5.048
1164.1 | 50.5 | -5.048
1164.2 | 50.5 | -5.048
1164.3 | 50.5 | -5.048
1164.4 | 50.5 | -5.048
1164.5 | 50.5 | -5.048
1164.6 | 50.5 | -5.048
1164.7 | 50.5 | -5.048
1164.8 | 50.5 | -5.048
1164.9 | 50.5 | -5.048
1165 | 50.5 | -5.048
1165.1 | 50.5 | -5.048
1165.2 | 50.5 | -5.048
1165.3 | 50.5 | -5.048
1165.4 | 50.5 | -5.048
1165.5 | 50.5 | -5.048
1165.6 | 50.5 | -5.048
1165.7 | 50.5 | -5.048
1165.8 | 50.5 | -5.048
1165.9 | 50.5 | -5.048
1166 | 50.5 | -5.048
1166.1 | 50.5 | -5.048
1166.2 | 50.5 | -5.048
1166.3 | 50.5 | -5.048
1166.4 | 50.5 | -5.048
1166.5 | 50.5 | -5.048
1166.6 | 50.5 | -5.048
1166.7 | 50.5 | -5.048
1166.8 | 50.5 | -5.048
1166.9 | 50.5 | -5.048
1167 | 50.5 | -5.048
1167.1 | 50.5 | -5.048
1167.2 | 50.5 | -5.048
1167.3 | 50.5 | -5.048
1167.4 | 50.5 | -5.048
1167.5 | 50.5 | -5.048
1167.6 | 50.5 | -5.048
1167.7 | 50.5 | -5.048
1167.8 | 50.5 | -5.048
1167.9 | 50.5 | -5.048
1168 | 50.5 | -5.048
1168.1 | 50.5 | -5.048
1168.2 | 50.5 | -5.048
1168.3 | 50.5 | -5.048
1168.4 | 50.5 | -5.048
1168.5 | 50.5 | -5.048
1168.6 | 50.5 | -5.048
1168.7 | 50.5 | -5.048
1168.8 | 50.5 | -5.048
1168.9 | 50.5 | -5.048
1169 | 50.5 | -5.048
1169.1 | 50.5 | -5.048
1169.2 | 50.5 | -5.048
1169.3 | 50.5 | -5.048
1169.4 | 50.5 | -5.048
1169.5 | 50.5 | -5.048
1169.6 | 50.5 | -5.048
1169.7 | 50.5 | -5.047
1169.8 | 50.5 | -5.047
1169.9 | 50.5 | -5.047
1170 | 50.5 | -5.047
1170.1 | 50.5 | -5.047
1170.2 | 50.5 | -5.047
1170.3 | 50.5 | -5.047
1170.4 | 50.5 | -5.047
1170.5 | 50.5 | -5.047
1170.6 | 50.5 | -5.047
1170.7 | 50.5 | -5.047
1170.8 | 50.5 | -5.047
1170.9 | 50.5 | -5.047
1171 | 50.5 | -5.048
1171.1 | 50.5 | -5.048
1171.2 | 50.5 | -5.048
1171.3 | 50.5 | -5.048
1171.4 | 50.5 | -5.048
1171.5 | 50.5 | -5.048
1171.6 | 50.5 | -5.048
1171.7 | 50.5 | -5.048
1171.8 | 50.5 | -5.048
1171.9 | 50.5 | -5.048
1172 | 50.5 | -5.048
1172.1 | 50.5 | -5.048
1172.2 | 50.5 | -5.048
1172.3 | 50.5 | -5.048
1172.4 | 50.5 | -5.048
1172.5 | 50.5 | -5.048
1172.6 | 50.5 | -5.048
1172.7 | 50.5 | -5.048
1172.8 | 50.5 | -5.048
1172.9 | 50.5 | -5.048
1173 | 50.5 | -5.048
1173.1 | 50.5 | -5.048
1173.2 | 50.5 | -5.048
1173.3 | 50.5 | -5.047
1173.4 | 50.5 | -5.047
1173.5 | 50.5 | -5.048
1173.6 | 50.5 | -5.048
1173.7 | 50.5 | -5.048
1173.8 | 50.5 | -5.048
1173.9 | 50.5 | -5.048
1174 | 50.5 | -5.048
1174.1 | 50.5 | -5.048
1174.2 | 50.5 | -5.048
1174.3 | 50.5 | -5.048
1174.4 | 50.5 | -5.048
1174.5 | 50.5 | -5.048
1174.6 | 50.5 | -5.048
1174.7 | 50.5 | -5.048
1174.8 | 50.5 | -5.048
1174.9 | 50.5 | -5.048
1175 | 50.5 | -5.048
1175.1 | 50.5 | -5.048
1175.2 | 50.5 | -5.048
1175.3 | 50.5 | -5.048
1175.4 | 50.5 | -5.048
1175.5 | 50.5 | -5.048
1175.6 | 50.5 | -5.047
1175.7 | 50.5 | -5.047
1175.8 | 50.5 | -5.047
1175.9 | 50.5 | -5.047
1176 | 50.5 | -5.047
1176.1 | 50.5 | -5.047
1176.2 | 50.5 | -5.047
1176.3 | 50.5 | -5.047
1176.4 | 50.5 | -5.047
1176.5 | 50.5 | -5.047
1176.6 | 50.5 | -5.047
1176.7 | 50.5 | -5.047
1176.8 | 50.5 | -5.047
1176.9 | 50.5 | -5.047
1177 | 50.5 | -5.047
1177.1 | 50.5 | -5.047
1177.2 | 50.5 | -5.047
1177.3 | 50.5 | -5.047
1177.4 | 50.5 | -5.047
1177.5 | 50.5 | -5.047
1177.6 | 50.5 | -5.047
1177.7 | 50.5 | -5.047
1177.8 | 50.5 | -5.047
1177.9 | 50.5 | -5.047
1178 | 50.5 | -5.047
1178.1 | 50.5 | -5.047
1178.2 | 50.5 | -5.048
1178.3 | 50.5 | -5.048
1178.4 | 50.5 | -5.048
1178.5 | 50.5 | -5.048
1178.6 | 50.5 | -5.048
1178.7 | 50.5 | -5.048
1178.8 | 50.5 | -5.048
1178.9 | 50.5 | -5.048
1179 | 50.5 | -5.048
1179.1 | 50.5 | -5.048
1179.2 | 50.5 | -5.048
1179.3 | 50.5 | -5.048
1179.4 | 50.5 | -5.048
1179.5 | 50.5 | -5.048
1179.6 | 50.5 | -5.048
1179.7 | 50.5 | -5.048
1179.8 | 50.5 | -5.048
1179.9 | 50.5 | -5.048
1180 | 50.5 | -5.048
1180.1 | 50.5 | -5.048
1180.2 | 50.5 | -5.048
1180.3 | 50.5 | -5.048
1180.4 | 50.5 | -5.048
1180.5 | 50.5 | -5.048
1180.6 | 50.5 | -5.048
1180.7 | 50.5 | -5.048
1180.8 | 50.5 | -5.048
1180.9 | 50.5 | -5.048
1181 | 50.5 | -5.048
1181.1 | 50.5 | -5.048
1181.2 | 50.5 | -5.048
1181.3 | 50.5 | -5.048
1181.4 | 50.5 | -5.048
1181.5 | 50.5 | -5.048
1181.6 | 50.5 | -5.047
1181.7 | 50.5 | -5.047
1181.8 | 50.5 | -5.047
1181.9 | 50.5 | -5.047
1182 | 50.5 | -5.047
1182.1 | 50.5 | -5.047
1182.2 | 50.5 | -5.047
1182.3 | 50.5 | -5.047
1182.4 | 50.5 | -5.047
1182.5 | 50.5 | -5.047
1182.6 | 50.5 | -5.048
1182.7 | 50.5 | -5.048
1182.8 | 50.5 | -5.048
1182.9 | 50.5 | -5.048
1183 | 50.5 | -5.048
1183.1 | 50.5 | -5.048
1183.2 | 50.5 | -5.048
1183.3 | 50.5 | -5.048
1183.4 | 50.5 | -5.048
1183.5 | 50.5 | -5.048
1183.6 | 50.5 | -5.048
1183.7 | 50.5 | -5.048
1183.8 | 50.5 | -5.048
1183.9 | 50.5 | -5.048
1184 | 50.5 | -5.048
1184.1 | 50.5 | -5.047
1184.2 | 50.5 | -5.047
1184.3 | 50.5 | -5.047
1184.4 | 50.5 | -5.047
1184.5 | 50.5 | -5.047
1184.6 | 50.5 | -5.047
1184.7 | 50.5 | -5.047
1184.8 | 50.5 | -5.047
1184.9 | 50.5 | -5.048
1185 | 50.5 | -5.048
1185.1 | 50.5 | -5.048
1185.2 | 50.5 | -5.048
1185.3 | 50.5 | -5.048
1185.4 | 50.5 | -5.048
1185.5 | 50.5 | -5.048
1185.6 | 50.5 | -5.048
1185.7 | 50.5 | -5.048
1185.8 | 50.5 | -5.048
1185.9 | 50.5 | -5.048
1186 | 50.5 | -5.048
1186.1 | 50.5 | -5.047
1186.2 | 50.5 | -5.047
1186.3 | 50.5 | -5.047
1186.4 | 50.5 | -5.048
1186.5 | 50.5 | -5.048
1186.6 | 50.5 | -5.048
1186.7 | 50.5 | -5.048
1186.8 | 50.5 | -5.048
1186.9 | 50.5 | -5.048
1187 | 50.5 | -5.048
1187.1 | 50.5 | -5.048
1187.2 | 50.5 | -5.048
1187.3 | 50.5 | -5.047
1187.4 | 50.5 | -5.047
1187.5 | 50.5 | -5.047
1187.6 | 50.5 | -5.047
1187.7 | 50.5 | -5.047
1187.8 | 50.5 | -5.047
1187.9 | 50.5 | -5.047
1188 | 50.5 | -5.047
1188.1 | 50.5 | -5.047
1188.2 | 50.5 | -5.047
1188.3 | 50.5 | -5.047
1188.4 | 50.5 | -5.047
1188.5 | 50.5 | -5.048
1188.6 | 50.5 | -5.048
1188.7 | 50.5 | -5.048
1188.8 | 50.5 | -5.048
1188.9 | 50.5 | -5.048
1189 | 50.5 | -5.048
1189.1 | 50.5 | -5.048
1189.2 | 50.5 | -5.048
1189.3 | 50.5 | -5.048
1189.4 | 50.5 | -5.048
1189.5 | 50.5 | -5.048
1189.6 | 50.5 | -5.048
1189.7 | 50.5 | -5.048
1189.8 | 50.5 | -5.048
1189.9 | 50.5 | -5.048
1190 | 50.5 | -5.048
1190.1 | 50.5 | -5.048
1190.2 | 50.5 | -5.048
1190.3 | 50.5 | -5.048
1190.4 | 50.5 | -5.048
1190.5 | 50.5 | -5.048
1190.6 | 50.5 | -5.048
1190.7 | 50.5 | -5.048
1190.8 | 50.5 | -5.048
1190.9 | 50.5 | -5.048
1191 | 50.5 | -5.048
1191.1 | 50.5 | -5.048
1191.2 | 50.5 | -5.048
1191.3 | 50.5 | -5.048
1191.4 | 50.5 | -5.048
1191.5 | 50.5 | -5.048
1191.6 | 50.5 | -5.048
1191.7 | 50.5 | -5.048
1191.8 | 50.5 | -5.048
1191.9 | 50.5 | -5.048
1192 | 50.5 | -5.048
1192.1 | 50.5 | -5.048
1192.2 | 50.5 | -5.048
1192.3 | 50.5 | -5.048
1192.4 | 50.5 | -5.048
1192.5 | 50.5 | -5.048
1192.6 | 50.5 | -5.048
1192.7 | 50.5 | -5.048
1192.8 | 50.5 | -5.048
1192.9 | 50.5 | -5.048
1193 | 50.5 | -5.048
1193.1 | 50.5 | -5.048
1193.2 | 50.5 | -5.047
1193.3 | 50.5 | -5.047
1193.4 | 50.5 | -5.047
1193.5 | 50.5 | -5.047
1193.6 | 50.5 | -5.047
1193.7 | 50.5 | -5.047
1193.8 | 50.5 | -5.047
1193.9 | 50.5 | -5.047
1194 | 50.5 | -5.048
1194.1 | 50.5 | -5.048
1194.2 | 50.5 | -5.048
1194.3 | 50.5 | -5.048
1194.4 | 50.5 | -5.048
1194.5 | 50.5 | -5.048
1194.6 | 50.5 | -5.048
1194.7 | 50.5 | -5.048
1194.8 | 50.5 | -5.048
1194.9 | 50.5 | -5.048
1195 | 50.5 | -5.048
1195.1 | 50.5 | -5.048
1195.2 | 50.5 | -5.048
1195.3 | 50.5 | -5.048
1195.4 | 50.5 | -5.048
1195.5 | 50.5 | -5.048
1195.6 | 50.5 | -5.048
1195.7 | 50.5 | -5.048
1195.8 | 50.5 | -5.048
1195.9 | 50.5 | -5.048
1196 | 50.5 | -5.048
1196.1 | 50.5 | -5.048
1196.2 | 50.5 | -5.048
1196.3 | 50.5 | -5.048
1196.4 | 50.5 | -5.048
1196.5 | 50.5 | -5.048
1196.6 | 50.5 | -5.048
1196.7 | 50.5 | -5.048
1196.8 | 50.5 | -5.048
1196.9 | 50.5 | -5.048
1197 | 50.5 | -5.048
1197.1 | 50.5 | -5.048
1197.2 | 50.5 | -5.048
1197.3 | 50.5 | -5.048
1197.4 | 50.5 | -5.048
1197.5 | 50.5 | -5.048
1197.6 | 50.5 | -5.048
1197.7 | 50.5 | -5.048
1197.8 | 50.5 | -5.048
1197.9 | 50.5 | -5.047
1198 | 50.5 | -5.047
1198.1 | 50.5 | -5.047
1198.2 | 50.5 | -5.047
1198.3 | 50.5 | -5.047
1198.4 | 50.5 | -5.047
1198.5 | 50.5 | -5.047
1198.6 | 50.5 | -5.047
1198.7 | 50.5 | -5.047
1198.8 | 50.5 | -5.047
1198.9 | 50.5 | -5.047
1199 | 50.5 | -5.047
1199.1 | 50.5 | -5.047
1199.2 | 50.5 | -5.048
1199.3 | 50.5 | -5.048
1199.4 | 50.5 | -5.048
1199.5 | 50.5 | -5.048
1199.6 | 50.5 | -5.048
1199.7 | 50.5 | -5.048
1199.8 | 50.5 | -5.048
1199.9 | 50.5 | -5.048
1200 | 50.5 | -5.048
1200.1 | 50.5 | -5.048
1200.2 | 50.5 | -5.048
1200.3 | 50.5 | -5.048
1200.4 | 50.5 | -5.048
1200.5 | 50.5 | -5.048
1200.6 | 50.5 | -5.048
1200.7 | 50.5 | -5.048
1200.8 | 50.5 | -5.048
1200.9 | 50.5 | -5.048
1201 | 50.5 | -5.048
1201.1 | 50.5 | -5.048
1201.2 | 50.5 | -5.048
1201.3 | 50.5 | -5.048
1201.4 | 50.5 | -5.048
1201.5 | 50.5 | -5.048
1201.6 | 50.5 | -5.048
1201.7 | 50.5 | -5.048
1201.8 | 50.5 | -5.048
1201.9 | 50.5 | -5.048
1202 | 50.5 | -5.049
1202.1 | 50.5 | -5.049
1202.2 | 50.5 | -5.049
1202.3 | 50.5 | -5.049
1202.4 | 50.5 | -5.049
1202.5 | 50.5 | -5.049
1202.6 | 50.5 | -5.049
1202.7 | 50.5 | -5.049
1202.8 | 50.5 | -5.049
1202.9 | 50.5 | -5.049
1203 | 50.5 | -5.049
1203.1 | 50.5 | -5.049
1203.2 | 50.5 | -5.049
1203.3 | 50.5 | -5.049
1203.4 | 50.5 | -5.049
1203.5 | 50.5 | -5.049
1203.6 | 50.5 | -5.049
1203.7 | 50.5 | -5.048
1203.8 | 50.5 | -5.048
1203.9 | 50.5 | -5.048
1204 | 50.5 | -5.048
1204.1 | 50.5 | -5.048
1204.2 | 50.5 | -5.048
1204.3 | 50.5 | -5.048
1204.4 | 50.5 | -5.047
1204.5 | 50.5 | -5.047
1204.6 | 50.5 | -5.047
1204.7 | 50.5 | -5.047
1204.8 | 50.5 | -5.046
1204.9 | 50.5 | -5.046
1205 | 50.5 | -5.046
1205.1 | 50.5 | -5.047
1205.2 | 50.5 | -5.047
1205.3 | 50.5 | -5.047
1205.4 | 50.5 | -5.047
1205.5 | 50.5 | -5.047
1205.6 | 50.5 | -5.047
1205.7 | 50.5 | -5.047
1205.8 | 50.5 | -5.047
1205.9 | 50.5 | -5.047
1206 | 50.5 | -5.047
1206.1 | 50.5 | -5.047
1206.2 | 50.5 | -5.047
1206.3 | 50.5 | -5.047
1206.4 | 50.5 | -5.047
1206.5 | 50.5 | -5.047
1206.6 | 50.5 | -5.047
1206.7 | 50.5 | -5.047
1206.8 | 50.5 | -5.048
1206.9 | 50.5 | -5.048
1207 | 50.5 | -5.048
1207.1 | 50.5 | -5.048
1207.2 | 50.5 | -5.048
1207.3 | 50.5 | -5.048
1207.4 | 50.5 | -5.048
1207.5 | 50.5 | -5.048
1207.6 | 50.5 | -5.048
1207.7 | 50.5 | -5.048
1207.8 | 50.5 | -5.048
1207.9 | 50.5 | -5.048
1208 | 50.5 | -5.048
1208.1 | 50.5 | -5.048
1208.2 | 50.5 | -5.048
1208.3 | 50.5 | -5.048
1208.4 | 50.5 | -5.048
1208.5 | 50.5 | -5.048
1208.6 | 50.5 | -5.048
1208.7 | 50.5 | -5.048
1208.8 | 50.5 | -5.048
1208.9 | 50.5 | -5.048
1209 | 50.5 | -5.048
1209.1 | 50.5 | -5.048
1209.2 | 50.5 | -5.048
1209.3 | 50.5 | -5.048
1209.4 | 50.5 | -5.048
1209.5 | 50.5 | -5.048
1209.6 | 50.5 | -5.048
1209.7 | 50.5 | -5.048
1209.8 | 50.5 | -5.048
1209.9 | 50.5 | -5.048
1210 | 50.5 | -5.048
1210.1 | 50.5 | -5.048
1210.2 | 50.5 | -5.048
1210.3 | 50.5 | -5.048
1210.4 | 50.5 | -5.048
1210.5 | 50.5 | -5.048
1210.6 | 50.5 | -5.048
1210.7 | 50.5 | -5.047
1210.8 | 50.5 | -5.047
1210.9 | 50.5 | -5.047
1211 | 50.5 | -5.047
1211.1 | 50.5 | -5.047
1211.2 | 50.5 | -5.047
1211.3 | 50.5 | -5.047
1211.4 | 50.5 | -5.047
1211.5 | 50.5 | -5.047
1211.6 | 50.5 | -5.047
1211.7 | 50.5 | -5.047
1211.8 | 50.5 | -5.047
1211.9 | 50.5 | -5.047
1212 | 50.5 | -5.047
1212.1 | 50.5 | -5.047
1212.2 | 50.5 | -5.047
1212.3 | 50.5 | -5.047
1212.4 | 50.5 | -5.047
1212.5 | 50.5 | -5.047
1212.6 | 50.5 | -5.047
1212.7 | 50.5 | -5.047
1212.8 | 50.5 | -5.047
1212.9 | 50.5 | -5.047
1213 | 50.5 | -5.048
1213.1 | 50.5 | -5.048
1213.2 | 50.5 | -5.048
1213.3 | 50.5 | -5.048
1213.4 | 50.5 | -5.048
1213.5 | 50.5 | -5.048
1213.6 | 50.5 | -5.048
1213.7 | 50.5 | -5.048
1213.8 | 50.5 | -5.047
1213.9 | 50.5 | -5.047
1214 | 50.5 | -5.047
1214.1 | 50.5 | -5.047
1214.2 | 50.5 | -5.047
1214.3 | 50.5 | -5.047
1214.4 | 50.5 | -5.047
1214.5 | 50.5 | -5.047
1214.6 | 50.5 | -5.047
1214.7 | 50.5 | -5.047
1214.8 | 50.5 | -5.048
1214.9 | 50.5 | -5.048
1215 | 50.5 | -5.048
1215.1 | 50.5 | -5.048
1215.2 | 50.5 | -5.048
1215.3 | 50.5 | -5.048
1215.4 | 50.5 | -5.048
1215.5 | 50.5 | -5.048
1215.6 | 50.5 | -5.048
1215.7 | 50.5 | -5.048
1215.8 | 50.5 | -5.048
1215.9 | 50.5 | -5.048
1216 | 50.5 | -5.048
1216.1 | 50.5 | -5.048
1216.2 | 50.5 | -5.048
1216.3 | 50.5 | -5.048
1216.4 | 50.5 | -5.048
1216.5 | 50.5 | -5.048
1216.6 | 50.5 | -5.048
1216.7 | 50.5 | -5.048
1216.8 | 50.5 | -5.048
1216.9 | 50.5 | -5.048
1217 | 50.5 | -5.048
1217.1 | 50.5 | -5.048
1217.2 | 50.5 | -5.048
1217.3 | 50.5 | -5.048
1217.4 | 50.5 | -5.048
1217.5 | 50.5 | -5.048
1217.6 | 50.5 | -5.048
1217.7 | 50.5 | -5.048
1217.8 | 50.5 | -5.048
1217.9 | 50.5 | -5.048
1218 | 50.5 | -5.048
1218.1 | 50.5 | -5.048
1218.2 | 50.5 | -5.048
1218.3 | 50.5 | -5.048
1218.4 | 50.5 | -5.048
1218.5 | 50.5 | -5.048
1218.6 | 50.5 | -5.048
1218.7 | 50.5 | -5.048
1218.8 | 50.5 | -5.048
1218.9 | 50.5 | -5.048
1219 | 50.5 | -5.048
1219.1 | 50.5 | -5.048
1219.2 | 50.5 | -5.048
1219.3 | 50.5 | -5.048
1219.4 | 50.5 | -5.048
1219.5 | 50.5 | -5.048
1219.6 | 50.5 | -5.048
1219.7 | 50.5 | -5.048
1219.8 | 50.5 | -5.048
1219.9 | 50.5 | -5.048
1220 | 50.5 | -5.048
1220.1 | 50.5 | -5.048
1220.2 | 50.5 | -5.048
1220.3 | 50.5 | -5.048
1220.4 | 50.5 | -5.048
1220.5 | 50.5 | -5.048
1220.6 | 50.5 | -5.048
1220.7 | 50.5 | -5.048
1220.8 | 50.5 | -5.048
1220.9 | 50.5 | -5.048
1221 | 50.5 | -5.048
1221.1 | 50.5 | -5.048
1221.2 | 50.5 | -5.048
1221.3 | 50.5 | -5.048
1221.4 | 50.5 | -5.048
1221.5 | 50.5 | -5.048
1221.6 | 50.5 | -5.048
1221.7 | 50.5 | -5.048
1221.8 | 50.5 | -5.048
1221.9 | 50.5 | -5.048
1222 | 50.5 | -5.048
1222.1 | 50.5 | -5.048
1222.2 | 50.5 | -5.048
1222.3 | 50.5 | -5.048
1222.4 | 50.5 | -5.048
1222.5 | 50.5 | -5.048
1222.6 | 50.5 | -5.048
1222.7 | 50.5 | -5.048
1222.8 | 50.5 | -5.048
1222.9 | 50.5 | -5.048
1223 | 50.5 | -5.048
1223.1 | 50.5 | -5.048
1223.2 | 50.5 | -5.048
1223.3 | 50.5 | -5.048
1223.4 | 50.5 | -5.048
1223.5 | 50.5 | -5.048
1223.6 | 50.5 | -5.048
1223.7 | 50.5 | -5.048
1223.8 | 50.5 | -5.048
1223.9 | 50.5 | -5.048
1224 | 50.5 | -5.048
1224.1 | 50.5 | -5.048
1224.2 | 50.5 | -5.048
1224.3 | 50.5 | -5.048
1224.4 | 50.5 | -5.048
1224.5 | 50.5 | -5.048
1224.6 | 50.5 | -5.048
1224.7 | 50.5 | -5.048
1224.8 | 50.5 | -5.048
1224.9 | 50.5 | -5.048
1225 | 50.5 | -5.048
1225.1 | 50.5 | -5.048
1225.2 | 50.5 | -5.048
1225.3 | 50.5 | -5.048
1225.4 | 50.5 | -5.048
1225.5 | 50.5 | -5.048
1225.6 | 50.5 | -5.048
1225.7 | 50.5 | -5.048
1225.8 | 50.5 | -5.048
1225.9 | 50.5 | -5.047
1226 | 50.5 | -5.047
1226.1 | 50.5 | -5.047
1226.2 | 50.5 | -5.047
1226.3 | 50.5 | -5.047
1226.4 | 50.5 | -5.047
1226.5 | 50.5 | -5.047
1226.6 | 50.5 | -5.047
1226.7 | 50.5 | -5.047
1226.8 | 50.5 | -5.047
1226.9 | 50.5 | -5.047
1227 | 50.5 | -5.047
1227.1 | 50.5 | -5.048
1227.2 | 50.5 | -5.048
1227.3 | 50.5 | -5.048
1227.4 | 50.5 | -5.048
1227.5 | 50.5 | -5.048
1227.6 | 50.5 | -5.048
1227.7 | 50.5 | -5.048
1227.8 | 50.5 | -5.048
1227.9 | 50.5 | -5.048
1228 | 50.5 | -5.048
1228.1 | 50.5 | -5.048
1228.2 | 50.5 | -5.048
1228.3 | 50.5 | -5.048
1228.4 | 50.5 | -5.048
1228.5 | 50.5 | -5.048
1228.6 | 50.5 | -5.048
1228.7 | 50.5 | -5.048
1228.8 | 50.5 | -5.048
1228.9 | 50.5 | -5.048
1229 | 50.5 | -5.048
1229.1 | 50.5 | -5.048
1229.2 | 50.5 | -5.048
1229.3 | 50.5 | -5.048
1229.4 | 50.5 | -5.048
1229.5 | 50.5 | -5.048
1229.6 | 50.5 | -5.048
1229.7 | 50.5 | -5.048
1229.8 | 50.5 | -5.048
1229.9 | 50.5 | -5.048
1230 | 50.5 | -5.048
1230.1 | 50.5 | -5.048
1230.2 | 50.5 | -5.048
1230.3 | 50.5 | -5.048
1230.4 | 50.5 | -5.048
1230.5 | 50.5 | -5.048
1230.6 | 50.5 | -5.048
1230.7 | 50.5 | -5.048
1230.8 | 50.5 | -5.048
1230.9 | 50.5 | -5.048
1231 | 50.5 | -5.048
1231.1 | 50.5 | -5.048
1231.2 | 50.5 | -5.048
1231.3 | 50.5 | -5.048
1231.4 | 50.5 | -5.048
1231.5 | 50.5 | -5.048
1231.6 | 50.5 | -5.048
1231.7 | 50.5 | -5.048
1231.8 | 50.5 | -5.047
1231.9 | 50.5 | -5.047
1232 | 50.5 | -5.047
1232.1 | 50.5 | -5.047
1232.2 | 50.5 | -5.047
1232.3 | 50.5 | -5.047
1232.4 | 50.5 | -5.047
1232.5 | 50.5 | -5.047
1232.6 | 50.5 | -5.047
1232.7 | 50.5 | -5.047
1232.8 | 50.5 | -5.047
1232.9 | 50.5 | -5.047
1233 | 50.5 | -5.047
1233.1 | 50.5 | -5.047
1233.2 | 50.5 | -5.047
1233.3 | 50.5 | -5.047
1233.4 | 50.5 | -5.047
1233.5 | 50.5 | -5.047
1233.6 | 50.5 | -5.047
1233.7 | 50.5 | -5.047
1233.8 | 50.5 | -5.047
1233.9 | 50.5 | -5.047
1234 | 50.5 | -5.047
1234.1 | 50.5 | -5.048
1234.2 | 50.5 | -5.048
1234.3 | 50.5 | -5.048
1234.4 | 50.5 | -5.048
1234.5 | 50.5 | -5.048
1234.6 | 50.5 | -5.048
1234.7 | 50.5 | -5.048
1234.8 | 50.5 | -5.048
1234.9 | 50.5 | -5.048
1235 | 50.5 | -5.048
1235.1 | 50.5 | -5.048
1235.2 | 50.5 | -5.048
1235.3 | 50.5 | -5.048
1235.4 | 50.5 | -5.048
1235.5 | 50.5 | -5.048
1235.6 | 50.5 | -5.048
1235.7 | 50.5 | -5.048
1235.8 | 50.5 | -5.048
1235.9 | 50.5 | -5.048
1236 | 50.5 | -5.048
1236.1 | 50.5 | -5.048
1236.2 | 50.5 | -5.048
1236.3 | 50.5 | -5.048
1236.4 | 50.5 | -5.048
1236.5 | 50.5 | -5.048
1236.6 | 50.5 | -5.048
1236.7 | 50.5 | -5.048
1236.8 | 50.5 | -5.048
1236.9 | 50.5 | -5.048
1237 | 50.5 | -5.048
1237.1 | 50.5 | -5.048
1237.2 | 50.5 | -5.048
1237.3 | 50.5 | -5.048
1237.4 | 50.5 | -5.048
1237.5 | 50.5 | -5.048
1237.6 | 50.5 | -5.048
1237.7 | 50.5 | -5.048
1237.8 | 50.5 | -5.048
1237.9 | 50.5 | -5.048
1238 | 50.5 | -5.048
1238.1 | 50.5 | -5.048
1238.2 | 50.5 | -5.048
1238.3 | 50.5 | -5.048
1238.4 | 50.5 | -5.048
1238.5 | 50.5 | -5.048
1238.6 | 50.5 | -5.048
1238.7 | 50.5 | -5.047
1238.8 | 50.5 | -5.047
1238.9 | 50.5 | -5.047
1239 | 50.5 | -5.047
1239.1 | 50.5 | -5.047
1239.2 | 50.5 | -5.047
1239.3 | 50.5 | -5.047
1239.4 | 50.5 | -5.047
1239.5 | 50.5 | -5.047
1239.6 | 50.5 | -5.047
1239.7 | 50.5 | -5.047
1239.8 | 50.5 | -5.047
1239.9 | 50.5 | -5.047
1240 | 50.5 | -5.047
1240.1 | 50.5 | -5.047
1240.2 | 50.5 | -5.047
1240.3 | 50.5 | -5.047
1240.4 | 50.5 | -5.047
1240.5 | 50.5 | -5.047
1240.6 | 50.5 | -5.047
1240.7 | 50.5 | -5.047
1240.8 | 50.5 | -5.047
1240.9 | 50.5 | -5.047
1241 | 50.5 | -5.047
1241.1 | 50.5 | -5.048
1241.2 | 50.5 | -5.048
1241.3 | 50.5 | -5.048
1241.4 | 50.5 | -5.048
1241.5 | 50.5 | -5.048
1241.6 | 50.5 | -5.048
1241.7 | 50.5 | -5.048
1241.8 | 50.5 | -5.048
1241.9 | 50.5 | -5.048
1242 | 50.5 | -5.048
1242.1 | 50.5 | -5.048
1242.2 | 50.5 | -5.048
1242.3 | 50.5 | -5.048
1242.4 | 50.5 | -5.048
1242.5 | 50.5 | -5.048
1242.6 | 50.5 | -5.048
1242.7 | 50.5 | -5.048
1242.8 | 50.5 | -5.048
1242.9 | 50.5 | -5.048
1243 | 50.5 | -5.048
1243.1 | 50.5 | -5.048
1243.2 | 50.5 | -5.048
1243.3 | 50.5 | -5.048
1243.4 | 50.5 | -5.048
1243.5 | 50.5 | -5.048
1243.6 | 50.5 | -5.048
1243.7 | 50.5 | -5.048
1243.8 | 50.5 | -5.048
1243.9 | 50.5 | -5.048
1244 | 50.5 | -5.048
1244.1 | 50.5 | -5.047
1244.2 | 50.5 | -5.047
1244.3 | 50.5 | -5.047
1244.4 | 50.5 | -5.047
1244.5 | 50.5 | -5.047
1244.6 | 50.5 | -5.047
1244.7 | 50.5 | -5.047
1244.8 | 50.5 | -5.047
1244.9 | 50.5 | -5.046
1245 | 50.5 | -5.046
1245.1 | 50.5 | -5.046
1245.2 | 50.5 | -5.046
1245.3 | 50.5 | -5.046
1245.4 | 50.5 | -5.046
1245.5 | 50.5 | -5.046
1245.6 | 50.5 | -5.046
1245.7 | 50.5 | -5.046
1245.8 | 50.5 | -5.046
1245.9 | 50.5 | -5.046
1246 | 50.5 | -5.046
1246.1 | 50.5 | -5.048
1246.2 | 50.5 | -5.048
1246.3 | 50.5 | -5.048
1246.4 | 50.5 | -5.048
1246.5 | 50.5 | -5.047
1246.6 | 50.5 | -5.047
1246.7 | 50.5 | -5.047
1246.8 | 50.5 | -5.047
1246.9 | 50.5 | -5.048
1247 | 50.5 | -5.048
1247.1 | 50.5 | -5.048
1247.2 | 50.5 | -5.048
1247.3 | 50.5 | -5.048
1247.4 | 50.5 | -5.048
1247.5 | 50.5 | -5.048
1247.6 | 50.5 | -5.048
1247.7 | 50.5 | -5.048
1247.8 | 50.5 | -5.048
1247.9 | 50.5 | -5.048
1248 | 50.5 | -5.048
1248.1 | 50.5 | -5.049
1248.2 | 50.5 | -5.049
1248.3 | 50.5 | -5.049
1248.4 | 50.5 | -5.048
1248.5 | 50.5 | -5.048
1248.6 | 50.5 | -5.048
1248.7 | 50.5 | -5.048
1248.8 | 50.5 | -5.048
1248.9 | 50.5 | -5.048
1249 | 50.5 | -5.048
1249.1 | 50.5 | -5.048
1249.2 | 50.5 | -5.048
1249.3 | 50.5 | -5.047
1249.4 | 50.5 | -5.047
1249.5 | 50.5 | -5.047
1249.6 | 50.5 | -5.047
1249.7 | 50.5 | -5.047
1249.8 | 50.5 | -5.047
1249.9 | 50.5 | -5.047
1250 | 50.5 | -5.047
1250.1 | 50.5 | -5.047
1250.2 | 50.5 | -5.047
1250.3 | 50.5 | -5.047
1250.4 | 50.5 | -5.047
1250.5 | 50.5 | -5.047
1250.6 | 50.5 | -5.047
1250.7 | 50.5 | -5.047
1250.8 | 50.5 | -5.047
1250.9 | 50.5 | -5.047
1251 | 50.5 | -5.047
1251.1 | 50.5 | -5.047
1251.2 | 50.5 | -5.047
1251.3 | 50.5 | -5.047
1251.4 | 50.5 | -5.047
1251.5 | 50.5 | -5.047
1251.6 | 50.5 | -5.047
1251.7 | 50.5 | -5.047
1251.8 | 50.5 | -5.047
1251.9 | 50.5 | -5.047
1252 | 50.5 | -5.047
1252.1 | 50.5 | -5.047
1252.2 | 50.5 | -5.047
1252.3 | 50.5 | -5.047
1252.4 | 50.5 | -5.047
1252.5 | 50.5 | -5.047
1252.6 | 50.5 | -5.047
1252.7 | 50.5 | -5.047
1252.8 | 50.5 | -5.048
1252.9 | 50.5 | -5.048
1253 | 50.5 | -5.048
1253.1 | 50.5 | -5.048
1253.2 | 50.5 | -5.048
1253.3 | 50.5 | -5.048
1253.4 | 50.5 | -5.048
1253.5 | 50.5 | -5.048
1253.6 | 50.5 | -5.048
1253.7 | 50.5 | -5.048
1253.8 | 50.5 | -5.048
1253.9 | 50.5 | -5.048
1254 | 50.5 | -5.049
1254.1 | 50.5 | -5.049
1254.2 | 50.5 | -5.049
1254.3 | 50.5 | -5.049
1254.4 | 50.5 | -5.049
1254.5 | 50.5 | -5.049
1254.6 | 50.5 | -5.049
1254.7 | 50.5 | -5.049
1254.8 | 50.5 | -5.049
1254.9 | 50.5 | -5.049
1255 | 50.5 | -5.049
1255.1 | 50.5 | -5.049
1255.2 | 50.5 | -5.048
1255.3 | 50.5 | -5.048
1255.4 | 50.5 | -5.047
1255.5 | 50.5 | -5.047
1255.6 | 50.5 | -5.047
1255.7 | 50.5 | -5.047
1255.8 | 50.5 | -5.047
1255.9 | 50.5 | -5.047
1256 | 50.5 | -5.047
1256.1 | 50.5 | -5.047
1256.2 | 50.5 | -5.047
1256.3 | 50.5 | -5.047
1256.4 | 50.5 | -5.047
1256.5 | 50.5 | -5.047
1256.6 | 50.5 | -5.047
1256.7 | 50.5 | -5.047
1256.8 | 50.5 | -5.047
1256.9 | 50.5 | -5.047
1257 | 50.5 | -5.047
1257.1 | 50.5 | -5.047
1257.2 | 50.5 | -5.047
1257.3 | 50.5 | -5.047
1257.4 | 50.5 | -5.047
1257.5 | 50.5 | -5.047
1257.6 | 50.5 | -5.047
1257.7 | 50.5 | -5.048
1257.8 | 50.5 | -5.048
1257.9 | 50.5 | -5.048
1258 | 50.5 | -5.048
1258.1 | 50.5 | -5.048
1258.2 | 50.5 | -5.048
1258.3 | 50.5 | -5.048
1258.4 | 50.5 | -5.048
1258.5 | 50.5 | -5.048
1258.6 | 50.5 | -5.048
1258.7 | 50.5 | -5.048
1258.8 | 50.5 | -5.048
1258.9 | 50.5 | -5.048
1259 | 50.5 | -5.048
1259.1 | 50.5 | -5.048
1259.2 | 50.5 | -5.048
1259.3 | 50.5 | -5.048
1259.4 | 50.5 | -5.048
1259.5 | 50.5 | -5.048
1259.6 | 50.5 | -5.048
1259.7 | 50.5 | -5.048
1259.8 | 50.5 | -5.048
1259.9 | 50.5 | -5.048
1260 | 50.5 | -5.048
1260.1 | 50.5 | -5.048
1260.2 | 50.5 | -5.048
1260.3 | 50.5 | -5.048
1260.4 | 50.5 | -5.048
1260.5 | 50.5 | -5.048
1260.6 | 50.5 | -5.048
1260.7 | 50.5 | -5.048
1260.8 | 50.5 | -5.048
1260.9 | 50.5 | -5.048
1261 | 50.5 | -5.048
1261.1 | 50.5 | -5.048
1261.2 | 50.5 | -5.048
1261.3 | 50.5 | -5.048
1261.4 | 50.5 | -5.048
1261.5 | 50.5 | -5.048
1261.6 | 50.5 | -5.048
1261.7 | 50.5 | -5.048
1261.8 | 50.5 | -5.048
1261.9 | 50.5 | -5.048
1262 | 50.5 | -5.048
1262.1 | 50.5 | -5.048
1262.2 | 50.5 | -5.048
1262.3 | 50.5 | -5.048
1262.4 | 50.5 | -5.047
1262.5 | 50.5 | -5.047
1262.6 | 50.5 | -5.047
1262.7 | 50.5 | -5.047
1262.8 | 50.5 | -5.047
1262.9 | 50.5 | -5.047
1263 | 50.5 | -5.047
1263.1 | 50.5 | -5.047
1263.2 | 50.5 | -5.047
1263.3 | 50.5 | -5.047
1263.4 | 50.5 | -5.047
1263.5 | 50.5 | -5.048
1263.6 | 50.5 | -5.048
1263.7 | 50.5 | -5.048
1263.8 | 50.5 | -5.048
1263.9 | 50.5 | -5.048
1264 | 50.5 | -5.048
1264.1 | 50.5 | -5.048
1264.2 | 50.5 | -5.048
1264.3 | 50.5 | -5.048
1264.4 | 50.5 | -5.048
1264.5 | 50.5 | -5.048
1264.6 | 50.5 | -5.048
1264.7 | 50.5 | -5.048
1264.8 | 50.5 | -5.048
1264.9 | 50.5 | -5.048
1265 | 50.5 | -5.048
1265.1 | 50.5 | -5.048
1265.2 | 50.5 | -5.048
1265.3 | 50.5 | -5.048
1265.4 | 50.5 | -5.048
1265.5 | 50.5 | -5.048
1265.6 | 50.5 | -5.048
1265.7 | 50.5 | -5.048
1265.8 | 50.5 | -5.048
1265.9 | 50.5 | -5.048
1266 | 50.5 | -5.048
1266.1 | 50.5 | -5.048
1266.2 | 50.5 | -5.048
1266.3 | 50.5 | -5.048
1266.4 | 50.5 | -5.048
1266.5 | 50.5 | -5.048
1266.6 | 50.5 | -5.048
1266.7 | 50.5 | -5.048
1266.8 | 50.5 | -5.048
1266.9 | 50.5 | -5.048
1267 | 50.5 | -5.048
1267.1 | 50.5 | -5.048
1267.2 | 50.5 | -5.048
1267.3 | 50.5 | -5.048
1267.4 | 50.5 | -5.048
1267.5 | 50.5 | -5.048
1267.6 | 50.5 | -5.048
1267.7 | 50.5 | -5.048
1267.8 | 50.5 | -5.048
1267.9 | 50.5 | -5.048
1268 | 50.5 | -5.048
1268.1 | 50.5 | -5.048
1268.2 | 50.5 | -5.048
1268.3 | 50.5 | -5.048
1268.4 | 50.5 | -5.048
1268.5 | 50.5 | -5.048
1268.6 | 50.5 | -5.048
1268.7 | 50.5 | -5.048
1268.8 | 50.5 | -5.048
1268.9 | 50.5 | -5.048
1269 | 50.5 | -5.048
1269.1 | 50.5 | -5.048
1269.2 | 50.5 | -5.048
1269.3 | 50.5 | -5.048
1269.4 | 50.5 | -5.048
1269.5 | 50.5 | -5.048
1269.6 | 50.5 | -5.048
1269.7 | 50.5 | -5.048
1269.8 | 50.5 | -5.048
1269.9 | 50.5 | -5.048
1270 | 50.5 | -5.048
1270.1 | 50.5 | -5.048
1270.2 | 50.5 | -5.048
1270.3 | 50.5 | -5.048
1270.4 | 50.5 | -5.048
1270.5 | 50.5 | -5.048
1270.6 | 50.5 | -5.048
1270.7 | 50.5 | -5.048
1270.8 | 50.5 | -5.048
1270.9 | 50.5 | -5.048
1271 | 50.5 | -5.048
1271.1 | 50.5 | -5.048
1271.2 | 50.5 | -5.048
1271.3 | 50.5 | -5.048
1271.4 | 50.5 | -5.048
1271.5 | 50.5 | -5.048
1271.6 | 50.5 | -5.048
1271.7 | 50.5 | -5.047
1271.8 | 50.5 | -5.047
1271.9 | 50.5 | -5.047
1272 | 50.5 | -5.047
1272.1 | 50.5 | -5.047
1272.2 | 50.5 | -5.047
1272.3 | 50.5 | -5.047
1272.4 | 50.5 | -5.047
1272.5 | 50.5 | -5.047
1272.6 | 50.5 | -5.047
1272.7 | 50.5 | -5.047
1272.8 | 50.5 | -5.048
1272.9 | 50.5 | -5.048
1273 | 50.5 | -5.048
1273.1 | 50.5 | -5.048
1273.2 | 50.5 | -5.048
1273.3 | 50.5 | -5.048
1273.4 | 50.5 | -5.048
1273.5 | 50.5 | -5.048
1273.6 | 50.5 | -5.048
1273.7 | 50.5 | -5.048
1273.8 | 50.5 | -5.048
1273.9 | 50.5 | -5.048
1274 | 50.5 | -5.048
1274.1 | 50.5 | -5.048
1274.2 | 50.5 | -5.048
1274.3 | 50.5 | -5.048
1274.4 | 50.5 | -5.048
1274.5 | 50.5 | -5.048
1274.6 | 50.5 | -5.048
1274.7 | 50.5 | -5.048
1274.8 | 50.5 | -5.048
1274.9 | 50.5 | -5.048
1275 | 50.5 | -5.048
1275.1 | 50.5 | -5.048
1275.2 | 50.5 | -5.048
1275.3 | 50.5 | -5.048
1275.4 | 50.5 | -5.048
1275.5 | 50.5 | -5.048
1275.6 | 50.5 | -5.048
1275.7 | 50.5 | -5.048
1275.8 | 50.5 | -5.048
1275.9 | 50.5 | -5.048
1276 | 50.5 | -5.048
1276.1 | 50.5 | -5.048
1276.2 | 50.5 | -5.048
1276.3 | 50.5 | -5.048
1276.4 | 50.5 | -5.048
1276.5 | 50.5 | -5.048
1276.6 | 50.5 | -5.048
1276.7 | 50.5 | -5.048
1276.8 | 50.5 | -5.048
1276.9 | 50.5 | -5.048
1277 | 50.5 | -5.048
1277.1 | 50.5 | -5.048
1277.2 | 50.5 | -5.048
1277.3 | 50.5 | -5.048
1277.4 | 50.5 | -5.048
1277.5 | 50.5 | -5.048
1277.6 | 50.5 | -5.048
1277.7 | 50.5 | -5.047
1277.8 | 50.5 | -5.047
1277.9 | 50.5 | -5.047
1278 | 50.5 | -5.047
1278.1 | 50.5 | -5.047
1278.2 | 50.5 | -5.047
1278.3 | 50.5 | -5.047
1278.4 | 50.5 | -5.047
1278.5 | 50.5 | -5.047
1278.6 | 50.5 | -5.047
1278.7 | 50.5 | -5.047
1278.8 | 50.5 | -5.048
1278.9 | 50.5 | -5.048
1279 | 50.5 | -5.048
1279.1 | 50.5 | -5.048
1279.2 | 50.5 | -5.048
1279.3 | 50.5 | -5.048
1279.4 | 50.5 | -5.048
1279.5 | 50.5 | -5.048
1279.6 | 50.5 | -5.048
1279.7 | 50.5 | -5.048
1279.8 | 50.5 | -5.048
1279.9 | 50.5 | -5.048
1280 | 50.5 | -5.048
1280.1 | 50.5 | -5.048
1280.2 | 50.5 | -5.048
1280.3 | 50.5 | -5.048
1280.4 | 50.5 | -5.048
1280.5 | 50.5 | -5.048
1280.6 | 50.5 | -5.048
1280.7 | 50.5 | -5.048
1280.8 | 50.5 | -5.048
1280.9 | 50.5 | -5.047
1281 | 50.5 | -5.047
1281.1 | 50.5 | -5.047
1281.2 | 50.5 | -5.047
1281.3 | 50.5 | -5.047
1281.4 | 50.5 | -5.047
1281.5 | 50.5 | -5.047
1281.6 | 50.5 | -5.047
1281.7 | 50.5 | -5.047
1281.8 | 50.5 | -5.047
1281.9 | 50.5 | -5.047
1282 | 50.5 | -5.047
1282.1 | 50.5 | -5.048
1282.2 | 50.5 | -5.048
1282.3 | 50.5 | -5.047
1282.4 | 50.5 | -5.047
1282.5 | 50.5 | -5.047
1282.6 | 50.5 | -5.047
1282.7 | 50.5 | -5.047
1282.8 | 50.5 | -5.047
1282.9 | 50.5 | -5.047
1283 | 50.5 | -5.047
1283.1 | 50.5 | -5.047
1283.2 | 50.5 | -5.047
1283.3 | 50.5 | -5.048
1283.4 | 50.5 | -5.048
1283.5 | 50.5 | -5.048
1283.6 | 50.5 | -5.048
1283.7 | 50.5 | -5.048
1283.8 | 50.5 | -5.048
1283.9 | 50.5 | -5.048
1284 | 50.5 | -5.048
1284.1 | 50.5 | -5.048
1284.2 | 50.5 | -5.048
1284.3 | 50.5 | -5.048
1284.4 | 50.5 | -5.047
1284.5 | 50.5 | -5.047
1284.6 | 50.5 | -5.047
1284.7 | 50.5 | -5.047
1284.8 | 50.5 | -5.047
1284.9 | 50.5 | -5.047
1285 | 50.5 | -5.047
1285.1 | 50.5 | -5.047
1285.2 | 50.5 | -5.047
1285.3 | 50.5 | -5.047
1285.4 | 50.5 | -5.047
1285.5 | 50.5 | -5.047
1285.6 | 50.5 | -5.047
1285.7 | 50.5 | -5.047
1285.8 | 50.5 | -5.048
1285.9 | 50.5 | -5.048
1286 | 50.5 | -5.048
1286.1 | 50.5 | -5.048
1286.2 | 50.5 | -5.048
1286.3 | 50.5 | -5.048
1286.4 | 50.5 | -5.048
1286.5 | 50.5 | -5.048
1286.6 | 50.5 | -5.048
1286.7 | 50.5 | -5.047
1286.8 | 50.5 | -5.047
1286.9 | 50.5 | -5.047
1287 | 50.5 | -5.047
1287.1 | 50.5 | -5.047
1287.2 | 50.5 | -5.047
1287.3 | 50.5 | -5.047
1287.4 | 50.5 | -5.047
1287.5 | 50.5 | -5.047
1287.6 | 50.5 | -5.047
1287.7 | 50.5 | -5.047
1287.8 | 50.5 | -5.047
1287.9 | 50.5 | -5.048
1288 | 50.5 | -5.048
1288.1 | 50.5 | -5.048
1288.2 | 50.5 | -5.048
1288.3 | 50.5 | -5.048
1288.4 | 50.5 | -5.048
1288.5 | 50.5 | -5.048
1288.6 | 50.5 | -5.048
1288.7 | 50.5 | -5.048
1288.8 | 50.5 | -5.048
1288.9 | 50.5 | -5.048
1289 | 50.5 | -5.048
1289.1 | 50.5 | -5.048
1289.2 | 50.5 | -5.048
1289.3 | 50.5 | -5.048
1289.4 | 50.5 | -5.048
1289.5 | 50.5 | -5.048
1289.6 | 50.5 | -5.048
1289.7 | 50.5 | -5.048
1289.8 | 50.5 | -5.048
1289.9 | 50.5 | -5.048
1290 | 50.5 | -5.048
1290.1 | 50.5 | -5.048
1290.2 | 50.5 | -5.048
1290.3 | 50.5 | -5.048
1290.4 | 50.5 | -5.048
1290.5 | 50.5 | -5.048
1290.6 | 50.5 | -5.048
1290.7 | 50.5 | -5.048
1290.8 | 50.5 | -5.048
1290.9 | 50.5 | -5.048
1291 | 50.5 | -5.048
1291.1 | 50.5 | -5.048
1291.2 | 50.5 | -5.048
1291.3 | 50.5 | -5.048
1291.4 | 50.5 | -5.048
1291.5 | 50.5 | -5.048
1291.6 | 50.5 | -5.048
1291.7 | 50.5 | -5.048
1291.8 | 50.5 | -5.048
1291.9 | 50.5 | -5.048
1292 | 50.5 | -5.048
1292.1 | 50.5 | -5.048
1292.2 | 50.5 | -5.048
1292.3 | 50.5 | -5.048
1292.4 | 50.5 | -5.048
1292.5 | 50.5 | -5.048
1292.6 | 50.5 | -5.047
1292.7 | 50.5 | -5.047
1292.8 | 50.5 | -5.047
1292.9 | 50.5 | -5.047
1293 | 50.5 | -5.047
1293.1 | 50.5 | -5.047
1293.2 | 50.5 | -5.047
1293.3 | 50.5 | -5.047
1293.4 | 50.5 | -5.047
1293.5 | 50.5 | -5.047
1293.6 | 50.5 | -5.047
1293.7 | 50.5 | -5.047
1293.8 | 50.5 | -5.047
1293.9 | 50.5 | -5.048
1294 | 50.5 | -5.048
1294.1 | 50.5 | -5.048
1294.2 | 50.5 | -5.048
1294.3 | 50.5 | -5.048
1294.4 | 50.5 | -5.048
1294.5 | 50.5 | -5.048
1294.6 | 50.5 | -5.048
1294.7 | 50.5 | -5.048
1294.8 | 50.5 | -5.048
1294.9 | 50.5 | -5.048
1295 | 50.5 | -5.048
1295.1 | 50.5 | -5.048
1295.2 | 50.5 | -5.048
1295.3 | 50.5 | -5.048
1295.4 | 50.5 | -5.048
1295.5 | 50.5 | -5.048
1295.6 | 50.5 | -5.048
1295.7 | 50.5 | -5.048
1295.8 | 50.5 | -5.048
1295.9 | 50.5 | -5.048
1296 | 50.5 | -5.048
1296.1 | 50.5 | -5.048
1296.2 | 50.5 | -5.048
1296.3 | 50.5 | -5.048
1296.4 | 50.5 | -5.048
1296.5 | 50.5 | -5.048
1296.6 | 50.5 | -5.048
1296.7 | 50.5 | -5.048
1296.8 | 50.5 | -5.048
1296.9 | 50.5 | -5.048
1297 | 50.5 | -5.048
1297.1 | 50.5 | -5.048
1297.2 | 50.5 | -5.048
1297.3 | 50.5 | -5.048
1297.4 | 50.5 | -5.048
1297.5 | 50.5 | -5.048
1297.6 | 50.5 | -5.048
1297.7 | 50.5 | -5.048
1297.8 | 50.5 | -5.048
1297.9 | 50.5 | -5.048
1298 | 50.5 | -5.048
1298.1 | 50.5 | -5.048
1298.2 | 50.5 | -5.048
1298.3 | 50.5 | -5.048
1298.4 | 50.5 | -5.048
1298.5 | 50.5 | -5.048
1298.6 | 50.5 | -5.048
1298.7 | 50.5 | -5.048
1298.8 | 50.5 | -5.048
1298.9 | 50.5 | -5.048
1299 | 50.5 | -5.048
1299.1 | 50.5 | -5.048
1299.2 | 50.5 | -5.048
1299.3 | 50.5 | -5.048
1299.4 | 50.5 | -5.048
1299.5 | 50.5 | -5.048
1299.6 | 50.5 | -5.048
1299.7 | 50.5 | -5.048
1299.8 | 50.5 | -5.048
1299.9 | 50.5 | -5.048
1300 | 50.5 | -5.048
1300.1 | 50.5 | -5.048
1300.2 | 50.5 | -5.048
1300.3 | 50.5 | -5.048
1300.4 | 50.5 | -5.048
1300.5 | 50.5 | -5.048
1300.6 | 50.5 | -5.048
1300.7 | 50.5 | -5.048
1300.8 | 50.5 | -5.048
1300.9 | 50.5 | -5.048
1301 | 50.5 | -5.048
1301.1 | 50.5 | -5.048
1301.2 | 50.5 | -5.048
1301.3 | 50.5 | -5.048
1301.4 | 50.5 | -5.048
1301.5 | 50.5 | -5.048
1301.6 | 50.5 | -5.048
1301.7 | 50.5 | -5.048
1301.8 | 50.5 | -5.048
1301.9 | 50.5 | -5.048
1302 | 50.5 | -5.048
1302.1 | 50.5 | -5.048
1302.2 | 50.5 | -5.048
1302.3 | 50.5 | -5.048
1302.4 | 50.5 | -5.048
1302.5 | 50.5 | -5.048
1302.6 | 50.5 | -5.048
1302.7 | 50.5 | -5.048
1302.8 | 50.5 | -5.048
1302.9 | 50.5 | -5.048
1303 | 50.5 | -5.048
1303.1 | 50.5 | -5.048
1303.2 | 50.5 | -5.048
1303.3 | 50.5 | -5.047
1303.4 | 50.5 | -5.047
1303.5 | 50.5 | -5.047
1303.6 | 50.5 | -5.047
1303.7 | 50.5 | -5.047
1303.8 | 50.5 | -5.047
1303.9 | 50.5 | -5.047
1304 | 50.5 | -5.047
1304.1 | 50.5 | -5.047
1304.2 | 50.5 | -5.047
1304.3 | 50.5 | -5.047
1304.4 | 50.5 | -5.047
1304.5 | 50.5 | -5.048
1304.6 | 50.5 | -5.048
1304.7 | 50.5 | -5.048
1304.8 | 50.5 | -5.048
1304.9 | 50.5 | -5.048
1305 | 50.5 | -5.048
1305.1 | 50.5 | -5.048
1305.2 | 50.5 | -5.048
1305.3 | 50.5 | -5.048
1305.4 | 50.5 | -5.048
1305.5 | 50.5 | -5.047
1305.6 | 50.5 | -5.047
1305.7 | 50.5 | -5.048
1305.8 | 50.5 | -5.048
1305.9 | 50.5 | -5.048
1306 | 50.5 | -5.048
1306.1 | 50.5 | -5.048
1306.2 | 50.5 | -5.048
1306.3 | 50.5 | -5.048
1306.4 | 50.5 | -5.048
1306.5 | 50.5 | -5.048
1306.6 | 50.5 | -5.048
1306.7 | 50.5 | -5.048
1306.8 | 50.5 | -5.048
1306.9 | 50.5 | -5.048
1307 | 50.5 | -5.048
1307.1 | 50.5 | -5.048
1307.2 | 50.5 | -5.048
1307.3 | 50.5 | -5.048
1307.4 | 50.5 | -5.048
1307.5 | 50.5 | -5.048
1307.6 | 50.5 | -5.048
1307.7 | 50.5 | -5.048
1307.8 | 50.5 | -5.048
1307.9 | 50.5 | -5.048
1308 | 50.5 | -5.048
1308.1 | 50.5 | -5.048
1308.2 | 50.5 | -5.048
1308.3 | 50.5 | -5.048
1308.4 | 50.5 | -5.048
1308.5 | 50.5 | -5.048
1308.6 | 50.5 | -5.048
1308.7 | 50.5 | -5.048
1308.8 | 50.5 | -5.048
1308.9 | 50.5 | -5.048
1309 | 50.5 | -5.048
1309.1 | 50.5 | -5.048
1309.2 | 50.5 | -5.048
1309.3 | 50.5 | -5.048
1309.4 | 50.5 | -5.048
1309.5 | 50.5 | -5.048
1309.6 | 50.5 | -5.048
1309.7 | 50.5 | -5.048
1309.8 | 50.5 | -5.048
1309.9 | 50.5 | -5.048
1310 | 50.5 | -5.048
1310.1 | 50.5 | -5.048
1310.2 | 50.5 | -5.048
1310.3 | 50.5 | -5.048
1310.4 | 50.5 | -5.047
1310.5 | 50.5 | -5.047
1310.6 | 50.5 | -5.047
1310.7 | 50.5 | -5.047
1310.8 | 50.5 | -5.047
1310.9 | 50.5 | -5.047
1311 | 50.5 | -5.047
1311.1 | 50.5 | -5.047
1311.2 | 50.5 | -5.047
1311.3 | 50.5 | -5.047
1311.4 | 50.5 | -5.047
1311.5 | 50.5 | -5.048
1311.6 | 50.5 | -5.048
1311.7 | 50.5 | -5.048
1311.8 | 50.5 | -5.048
1311.9 | 50.5 | -5.048
1312 | 50.5 | -5.048
1312.1 | 50.5 | -5.048
1312.2 | 50.5 | -5.048
1312.3 | 50.5 | -5.048
1312.4 | 50.5 | -5.048
1312.5 | 50.5 | -5.048
1312.6 | 50.5 | -5.048
1312.7 | 50.5 | -5.048
1312.8 | 50.5 | -5.048
1312.9 | 50.5 | -5.048
1313 | 50.5 | -5.048
1313.1 | 50.5 | -5.048
1313.2 | 50.5 | -5.048
1313.3 | 50.5 | -5.048
1313.4 | 50.5 | -5.048
1313.5 | 50.5 | -5.048
1313.6 | 50.5 | -5.048
1313.7 | 50.5 | -5.048
1313.8 | 50.5 | -5.048
1313.9 | 50.5 | -5.048
1314 | 50.5 | -5.048
1314.1 | 50.5 | -5.048
1314.2 | 50.5 | -5.048
1314.3 | 50.5 | -5.048
1314.4 | 50.5 | -5.048
1314.5 | 50.5 | -5.048
1314.6 | 50.5 | -5.048
1314.7 | 50.5 | -5.048
1314.8 | 50.5 | -5.048
1314.9 | 50.5 | -5.048
1315 | 50.5 | -5.048
1315.1 | 50.5 | -5.048
1315.2 | 50.5 | -5.048
1315.3 | 50.5 | -5.048
1315.4 | 50.5 | -5.048
1315.5 | 50.5 | -5.048
1315.6 | 50.5 | -5.048
1315.7 | 50.5 | -5.048
1315.8 | 50.5 | -5.048
1315.9 | 50.5 | -5.048
1316 | 50.5 | -5.048
1316.1 | 50.5 | -5.048
1316.2 | 50.5 | -5.048
1316.3 | 50.5 | -5.048
1316.4 | 50.5 | -5.048
1316.5 | 50.5 | -5.048
1316.6 | 50.5 | -5.048
1316.7 | 50.5 | -5.048
1316.8 | 50.5 | -5.048
1316.9 | 50.5 | -5.048
1317 | 50.5 | -5.048
1317.1 | 50.5 | -5.048
1317.2 | 50.5 | -5.048
1317.3 | 50.5 | -5.048
1317.4 | 50.5 | -5.048
1317.5 | 50.5 | -5.048
1317.6 | 50.5 | -5.048
1317.7 | 50.5 | -5.048
1317.8 | 50.5 | -5.048
1317.9 | 50.5 | -5.048
1318 | 50.5 | -5.048
1318.1 | 50.5 | -5.048
1318.2 | 50.5 | -5.048
1318.3 | 50.5 | -5.048
1318.4 | 50.5 | -5.048
1318.5 | 50.5 | -5.048
1318.6 | 50.5 | -5.048
1318.7 | 50.5 | -5.048
1318.8 | 50.5 | -5.048
1318.9 | 50.5 | -5.048
1319 | 50.5 | -5.048
1319.1 | 50.5 | -5.048
1319.2 | 50.5 | -5.048
1319.3 | 50.5 | -5.048
1319.4 | 50.5 | -5.048
1319.5 | 50.5 | -5.048
1319.6 | 50.5 | -5.048
1319.7 | 50.5 | -5.048
1319.8 | 50.5 | -5.048
1319.9 | 50.5 | -5.048
1320 | 50.5 | -5.048
1320.1 | 50.5 | -5.048
1320.2 | 50.5 | -5.048
1320.3 | 50.5 | -5.048
1320.4 | 50.5 | -5.048
1320.5 | 50.5 | -5.048
1320.6 | 50.5 | -5.048
1320.7 | 50.5 | -5.048
1320.8 | 50.5 | -5.048
1320.9 | 50.5 | -5.048
1321 | 50.5 | -5.048
1321.1 | 50.5 | -5.048
1321.2 | 50.5 | -5.048
1321.3 | 50.5 | -5.048
1321.4 | 50.5 | -5.048
1321.5 | 50.5 | -5.048
1321.6 | 50.5 | -5.048
1321.7 | 50.5 | -5.048
1321.8 | 50.5 | -5.047
1321.9 | 50.5 | -5.047
1322 | 50.5 | -5.047
1322.1 | 50.5 | -5.047
1322.2 | 50.5 | -5.047
1322.3 | 50.5 | -5.047
1322.4 | 50.5 | -5.047
1322.5 | 50.5 | -5.047
1322.6 | 50.5 | -5.047
1322.7 | 50.5 | -5.047
1322.8 | 50.5 | -5.047
1322.9 | 50.5 | -5.048
1323 | 50.5 | -5.048
1323.1 | 50.5 | -5.048
1323.2 | 50.5 | -5.048
1323.3 | 50.5 | -5.048
1323.4 | 50.5 | -5.048
1323.5 | 50.5 | -5.048
1323.6 | 50.5 | -5.048
1323.7 | 50.5 | -5.048
1323.8 | 50.5 | -5.048
1323.9 | 50.5 | -5.048
1324 | 50.5 | -5.048
1324.1 | 50.5 | -5.048
1324.2 | 50.5 | -5.048
1324.3 | 50.5 | -5.048
1324.4 | 50.5 | -5.048
1324.5 | 50.5 | -5.048
1324.6 | 50.5 | -5.048
1324.7 | 50.5 | -5.048
1324.8 | 50.5 | -5.048
1324.9 | 50.5 | -5.048
1325 | 50.5 | -5.048
1325.1 | 50.5 | -5.048
1325.2 | 50.5 | -5.048
1325.3 | 50.5 | -5.048
1325.4 | 50.5 | -5.048
1325.5 | 50.5 | -5.048
1325.6 | 50.5 | -5.048
1325.7 | 50.5 | -5.048
1325.8 | 50.5 | -5.048
1325.9 | 50.5 | -5.048
1326 | 50.5 | -5.048
1326.1 | 50.5 | -5.048
1326.2 | 50.5 | -5.048
1326.3 | 50.5 | -5.048
1326.4 | 50.5 | -5.048
1326.5 | 50.5 | -5.048
1326.6 | 50.5 | -5.048
1326.7 | 50.5 | -5.048
1326.8 | 50.5 | -5.048
1326.9 | 50.5 | -5.048
1327 | 50.5 | -5.048
1327.1 | 50.5 | -5.048
1327.2 | 50.5 | -5.048
1327.3 | 50.5 | -5.048
1327.4 | 50.5 | -5.048
1327.5 | 50.5 | -5.048
1327.6 | 50.5 | -5.048
1327.7 | 50.5 | -5.048
1327.8 | 50.5 | -5.048
1327.9 | 50.5 | -5.048
1328 | 50.5 | -5.048
1328.1 | 50.5 | -5.048
1328.2 | 50.5 | -5.048
1328.3 | 50.5 | -5.048
1328.4 | 50.5 | -5.048
1328.5 | 50.5 | -5.048
1328.6 | 50.5 | -5.048
1328.7 | 50.5 | -5.048
1328.8 | 50.5 | -5.048
1328.9 | 50.5 | -5.048
1329 | 50.5 | -5.048
1329.1 | 50.5 | -5.048
1329.2 | 50.5 | -5.048
1329.3 | 50.5 | -5.048
1329.4 | 50.5 | -5.048
1329.5 | 50.5 | -5.048
1329.6 | 50.5 | -5.048
1329.7 | 50.5 | -5.048
1329.8 | 50.5 | -5.048
1329.9 | 50.5 | -5.048
1330 | 50.5 | -5.048
1330.1 | 50.5 | -5.048
1330.2 | 50.5 | -5.048
1330.3 | 50.5 | -5.048
1330.4 | 50.5 | -5.048
1330.5 | 50.5 | -5.048
1330.6 | 50.5 | -5.048
1330.7 | 50.5 | -5.048
1330.8 | 50.5 | -5.048
1330.9 | 50.5 | -5.048
1331 | 50.5 | -5.048
1331.1 | 50.5 | -5.048
1331.2 | 50.5 | -5.048
1331.3 | 50.5 | -5.048
1331.4 | 50.5 | -5.048
1331.5 | 50.5 | -5.048
1331.6 | 50.5 | -5.048
1331.7 | 50.5 | -5.048
1331.8 | 50.5 | -5.048
1331.9 | 50.5 | -5.048
1332 | 50.5 | -5.048
1332.1 | 50.5 | -5.048
1332.2 | 50.5 | -5.048
1332.3 | 50.5 | -5.048
1332.4 | 50.5 | -5.048
1332.5 | 50.5 | -5.048
1332.6 | 50.5 | -5.048
1332.7 | 50.5 | -5.048
1332.8 | 50.5 | -5.048
1332.9 | 50.5 | -5.048
1333 | 50.5 | -5.048
1333.1 | 50.5 | -5.048
1333.2 | 50.5 | -5.048
1333.3 | 50.5 | -5.048
1333.4 | 50.5 | -5.048
1333.5 | 50.5 | -5.048
1333.6 | 50.5 | -5.048
1333.7 | 50.5 | -5.048
1333.8 | 50.5 | -5.048
1333.9 | 50.5 | -5.048
1334 | 50.5 | -5.048
1334.1 | 50.5 | -5.048
1334.2 | 50.5 | -5.048
1334.3 | 50.5 | -5.048
1334.4 | 50.5 | -5.048
1334.5 | 50.5 | -5.048
1334.6 | 50.5 | -5.048
1334.7 | 50.5 | -5.048
1334.8 | 50.5 | -5.048
1334.9 | 50.5 | -5.048
1335 | 50.5 | -5.048
1335.1 | 50.5 | -5.048
1335.2 | 50.5 | -5.048
1335.3 | 50.5 | -5.048
1335.4 | 50.5 | -5.048
1335.5 | 50.5 | -5.048
1335.6 | 50.5 | -5.048
1335.7 | 50.5 | -5.048
1335.8 | 50.5 | -5.048
1335.9 | 50.5 | -5.048
1336 | 50.5 | -5.048
1336.1 | 50.5 | -5.048
1336.2 | 50.5 | -5.048
1336.3 | 50.5 | -5.048
1336.4 | 50.5 | -5.048
1336.5 | 50.5 | -5.048
1336.6 | 50.5 | -5.048
1336.7 | 50.5 | -5.048
1336.8 | 50.5 | -5.048
1336.9 | 50.5 | -5.048
1337 | 50.5 | -5.048
1337.1 | 50.5 | -5.048
1337.2 | 50.5 | -5.048
1337.3 | 50.5 | -5.048
1337.4 | 50.5 | -5.048
1337.5 | 50.5 | -5.048
1337.6 | 50.5 | -5.048
1337.7 | 50.5 | -5.048
1337.8 | 50.5 | -5.048
1337.9 | 50.5 | -5.048
1338 | 50.5 | -5.048
1338.1 | 50.5 | -5.048
1338.2 | 50.5 | -5.048
1338.3 | 50.5 | -5.048
1338.4 | 50.5 | -5.048
1338.5 | 50.5 | -5.048
1338.6 | 50.5 | -5.048
1338.7 | 50.5 | -5.048
1338.8 | 50.5 | -5.048
1338.9 | 50.5 | -5.048
1339 | 50.5 | -5.048
1339.1 | 50.5 | -5.048
1339.2 | 50.5 | -5.048
1339.3 | 50.5 | -5.048
1339.4 | 50.5 | -5.048
1339.5 | 50.5 | -5.048
1339.6 | 50.5 | -5.048
1339.7 | 50.5 | -5.048
1339.8 | 50.5 | -5.048
1339.9 | 50.5 | -5.048
1340 | 50.5 | -5.048
1340.1 | 50.5 | -5.048
1340.2 | 50.5 | -5.048
1340.3 | 50.5 | -5.048
1340.4 | 50.5 | -5.049
1340.5 | 50.5 | -5.049
1340.6 | 50.5 | -5.048
1340.7 | 50.5 | -5.048
1340.8 | 50.5 | -5.048
1340.9 | 50.5 | -5.048
1341 | 50.5 | -5.048
1341.1 | 50.5 | -5.048
1341.2 | 50.5 | -5.048
1341.3 | 50.5 | -5.048
1341.4 | 50.5 | -5.048
1341.5 | 50.5 | -5.048
1341.6 | 50.5 | -5.048
1341.7 | 50.5 | -5.048
1341.8 | 50.5 | -5.048
1341.9 | 50.5 | -5.048
1342 | 50.5 | -5.048
1342.1 | 50.5 | -5.048
1342.2 | 50.5 | -5.048
1342.3 | 50.5 | -5.048
1342.4 | 50.5 | -5.048
1342.5 | 50.5 | -5.048
1342.6 | 50.5 | -5.048
1342.7 | 50.5 | -5.048
1342.8 | 50.5 | -5.048
1342.9 | 50.5 | -5.047
1343 | 50.5 | -5.047
1343.1 | 50.5 | -5.047
1343.2 | 50.5 | -5.047
1343.3 | 50.5 | -5.047
1343.4 | 50.5 | -5.047
1343.5 | 50.5 | -5.047
1343.6 | 50.5 | -5.047
1343.7 | 50.5 | -5.047
1343.8 | 50.5 | -5.047
1343.9 | 50.5 | -5.047
1344 | 50.5 | -5.047
1344.1 | 50.5 | -5.048
1344.2 | 50.5 | -5.048
1344.3 | 50.5 | -5.048
1344.4 | 50.5 | -5.048
1344.5 | 50.5 | -5.048
1344.6 | 50.5 | -5.048
1344.7 | 50.5 | -5.048
1344.8 | 50.5 | -5.048
1344.9 | 50.5 | -5.048
1345 | 50.5 | -5.048
1345.1 | 50.5 | -5.048
1345.2 | 50.5 | -5.048
1345.3 | 50.5 | -5.048
1345.4 | 50.5 | -5.048
1345.5 | 50.5 | -5.048
1345.6 | 50.5 | -5.048
1345.7 | 50.5 | -5.048
1345.8 | 50.5 | -5.048
1345.9 | 50.5 | -5.048
1346 | 50.5 | -5.048
1346.1 | 50.5 | -5.048
1346.2 | 50.5 | -5.048
1346.3 | 50.5 | -5.048
1346.4 | 50.5 | -5.048
1346.5 | 50.5 | -5.048
1346.6 | 50.5 | -5.048
1346.7 | 50.5 | -5.048
1346.8 | 50.5 | -5.048
1346.9 | 50.5 | -5.048
1347 | 50.5 | -5.048
1347.1 | 50.5 | -5.048
1347.2 | 50.5 | -5.048
1347.3 | 50.5 | -5.048
1347.4 | 50.5 | -5.048
1347.5 | 50.5 | -5.048
1347.6 | 50.5 | -5.048
1347.7 | 50.5 | -5.048
1347.8 | 50.5 | -5.048
1347.9 | 50.5 | -5.048
1348 | 50.5 | -5.048
1348.1 | 50.5 | -5.048
1348.2 | 50.5 | -5.048
1348.3 | 50.5 | -5.048
1348.4 | 50.5 | -5.048
1348.5 | 50.5 | -5.048
1348.6 | 50.5 | -5.048
1348.7 | 50.5 | -5.048
1348.8 | 50.5 | -5.048
1348.9 | 50.5 | -5.048
1349 | 50.5 | -5.048
1349.1 | 50.5 | -5.048
1349.2 | 50.5 | -5.048
1349.3 | 50.5 | -5.048
1349.4 | 50.5 | -5.048
1349.5 | 50.5 | -5.048
1349.6 | 50.5 | -5.048
1349.7 | 50.5 | -5.048
1349.8 | 50.5 | -5.048
1349.9 | 50.5 | -5.048
1350 | 50.5 | -5.048
1350.1 | 50.5 | -5.048
1350.2 | 50.5 | -5.048
1350.3 | 50.5 | -5.048
1350.4 | 50.5 | -5.048
1350.5 | 50.5 | -5.048
1350.6 | 50.5 | -5.048
1350.7 | 50.5 | -5.048
1350.8 | 50.5 | -5.048
1350.9 | 50.5 | -5.048
1351 | 50.5 | -5.048
1351.1 | 50.5 | -5.048
1351.2 | 50.5 | -5.048
1351.3 | 50.5 | -5.048
1351.4 | 50.5 | -5.048
1351.5 | 50.5 | -5.048
1351.6 | 50.5 | -5.048
1351.7 | 50.5 | -5.048
1351.8 | 50.5 | -5.048
1351.9 | 50.5 | -5.048
1352 | 50.5 | -5.048
1352.1 | 50.5 | -5.048
1352.2 | 50.5 | -5.048
1352.3 | 50.5 | -5.048
1352.4 | 50.5 | -5.048
1352.5 | 50.5 | -5.048
1352.6 | 50.5 | -5.048
1352.7 | 50.5 | -5.048
1352.8 | 50.5 | -5.048
1352.9 | 50.5 | -5.048
1353 | 50.5 | -5.048
1353.1 | 50.5 | -5.048
1353.2 | 50.5 | -5.048
1353.3 | 50.5 | -5.048
1353.4 | 50.5 | -5.048
1353.5 | 50.5 | -5.048
1353.6 | 50.5 | -5.048
1353.7 | 50.5 | -5.048
1353.8 | 50.5 | -5.048
1353.9 | 50.5 | -5.048
1354 | 50.5 | -5.048
1354.1 | 50.5 | -5.048
1354.2 | 50.5 | -5.048
1354.3 | 50.5 | -5.048
1354.4 | 50.5 | -5.048
1354.5 | 50.5 | -5.048
1354.6 | 50.5 | -5.048
1354.7 | 50.5 | -5.048
1354.8 | 50.5 | -5.048
1354.9 | 50.5 | -5.048
1355 | 50.5 | -5.048
1355.1 | 50.5 | -5.048
1355.2 | 50.5 | -5.048
1355.3 | 50.5 | -5.048
1355.4 | 50.5 | -5.048
1355.5 | 50.5 | -5.048
1355.6 | 50.5 | -5.048
1355.7 | 50.5 | -5.048
1355.8 | 50.5 | -5.048
1355.9 | 50.5 | -5.048
1356 | 50.5 | -5.048
1356.1 | 50.5 | -5.048
1356.2 | 50.5 | -5.048
1356.3 | 50.5 | -5.048
1356.4 | 50.5 | -5.048
1356.5 | 50.5 | -5.048
1356.6 | 50.5 | -5.048
1356.7 | 50.5 | -5.048
1356.8 | 50.5 | -5.048
1356.9 | 50.5 | -5.048
1357 | 50.5 | -5.048
1357.1 | 50.5 | -5.048
1357.2 | 50.5 | -5.048
1357.3 | 50.5 | -5.048
1357.4 | 50.5 | -5.048
1357.5 | 50.5 | -5.048
1357.6 | 50.5 | -5.048
1357.7 | 50.5 | -5.048
1357.8 | 50.5 | -5.048
1357.9 | 50.5 | -5.048
1358 | 50.5 | -5.048
1358.1 | 50.5 | -5.048
1358.2 | 50.5 | -5.048
1358.3 | 50.5 | -5.048
1358.4 | 50.5 | -5.048
1358.5 | 50.5 | -5.048
1358.6 | 50.5 | -5.048
1358.7 | 50.5 | -5.048
1358.8 | 50.5 | -5.048
1358.9 | 50.5 | -5.048
1359 | 50.5 | -5.048
1359.1 | 50.5 | -5.048
1359.2 | 50.5 | -5.048
1359.3 | 50.5 | -5.048
1359.4 | 50.5 | -5.047
1359.5 | 50.5 | -5.047
1359.6 | 50.5 | -5.047
1359.7 | 50.5 | -5.047
1359.8 | 50.5 | -5.047
1359.9 | 50.5 | -5.047
1360 | 50.5 | -5.047
1360.1 | 50.5 | -5.047
1360.2 | 50.5 | -5.047
1360.3 | 50.5 | -5.047
1360.4 | 50.5 | -5.047
1360.5 | 50.5 | -5.047
1360.6 | 50.5 | -5.047
1360.7 | 50.5 | -5.047
1360.8 | 50.5 | -5.047
1360.9 | 50.5 | -5.047
1361 | 50.5 | -5.047
1361.1 | 50.5 | -5.047
1361.2 | 50.5 | -5.047
1361.3 | 50.5 | -5.047
1361.4 | 50.5 | -5.047
1361.5 | 50.5 | -5.047
1361.6 | 50.5 | -5.048
1361.7 | 50.5 | -5.048
1361.8 | 50.5 | -5.048
1361.9 | 50.5 | -5.048
1362 | 50.5 | -5.048
1362.1 | 50.5 | -5.048
1362.2 | 50.5 | -5.048
1362.3 | 50.5 | -5.048
1362.4 | 50.5 | -5.048
1362.5 | 50.5 | -5.048
1362.6 | 50.5 | -5.048
1362.7 | 50.5 | -5.048
1362.8 | 50.5 | -5.048
1362.9 | 50.5 | -5.048
1363 | 50.5 | -5.048
1363.1 | 50.5 | -5.048
1363.2 | 50.5 | -5.048
1363.3 | 50.5 | -5.048
1363.4 | 50.5 | -5.048
1363.5 | 50.5 | -5.048
1363.6 | 50.5 | -5.048
1363.7 | 50.5 | -5.048
1363.8 | 50.5 | -5.048
1363.9 | 50.5 | -5.048
1364 | 50.5 | -5.048
1364.1 | 50.5 | -5.048
1364.2 | 50.5 | -5.048
1364.3 | 50.5 | -5.048
1364.4 | 50.5 | -5.048
1364.5 | 50.5 | -5.048
1364.6 | 50.5 | -5.048
1364.7 | 50.5 | -5.048
1364.8 | 50.5 | -5.048
1364.9 | 50.5 | -5.048
1365 | 50.5 | -5.048
1365.1 | 50.5 | -5.048
1365.2 | 50.5 | -5.048
1365.3 | 50.5 | -5.048
1365.4 | 50.5 | -5.048
1365.5 | 50.5 | -5.048
1365.6 | 50.5 | -5.048
1365.7 | 50.5 | -5.048
1365.8 | 50.5 | -5.048
1365.9 | 50.5 | -5.048
1366 | 50.5 | -5.048
1366.1 | 50.5 | -5.048
1366.2 | 50.5 | -5.047
1366.3 | 50.5 | -5.047
1366.4 | 50.5 | -5.047
1366.5 | 50.5 | -5.047
1366.6 | 50.5 | -5.047
1366.7 | 50.5 | -5.047
1366.8 | 50.5 | -5.047
1366.9 | 50.5 | -5.047
1367 | 50.5 | -5.047
1367.1 | 50.5 | -5.047
1367.2 | 50.5 | -5.047
1367.3 | 50.5 | -5.047
1367.4 | 50.5 | -5.047
1367.5 | 50.5 | -5.047
1367.6 | 50.5 | -5.047
1367.7 | 50.5 | -5.047
1367.8 | 50.5 | -5.047
1367.9 | 50.5 | -5.047
1368 | 50.5 | -5.047
1368.1 | 50.5 | -5.047
1368.2 | 50.5 | -5.047
1368.3 | 50.5 | -5.047
1368.4 | 50.5 | -5.047
1368.5 | 50.5 | -5.048
1368.6 | 50.5 | -5.048
1368.7 | 50.5 | -5.048
1368.8 | 50.5 | -5.048
1368.9 | 50.5 | -5.047
1369 | 50.5 | -5.047
1369.1 | 50.5 | -5.047
1369.2 | 50.5 | -5.047
1369.3 | 50.5 | -5.047
1369.4 | 50.5 | -5.047
1369.5 | 50.5 | -5.047
1369.6 | 50.5 | -5.047
1369.7 | 50.5 | -5.048
1369.8 | 50.5 | -5.048
1369.9 | 50.5 | -5.048
1370 | 50.5 | -5.048
1370.1 | 50.5 | -5.048
1370.2 | 50.5 | -5.048
1370.3 | 50.5 | -5.048
1370.4 | 50.5 | -5.048
1370.5 | 50.5 | -5.048
1370.6 | 50.5 | -5.048
1370.7 | 50.5 | -5.048
1370.8 | 50.5 | -5.048
1370.9 | 50.5 | -5.048
1371 | 50.5 | -5.048
1371.1 | 50.5 | -5.048
1371.2 | 50.5 | -5.048
1371.3 | 50.5 | -5.048
1371.4 | 50.5 | -5.048
1371.5 | 50.5 | -5.048
1371.6 | 50.5 | -5.048
1371.7 | 50.5 | -5.048
1371.8 | 50.5 | -5.048
1371.9 | 50.5 | -5.048
1372 | 50.5 | -5.048
1372.1 | 50.5 | -5.048
1372.2 | 50.5 | -5.047
1372.3 | 50.5 | -5.047
1372.4 | 50.5 | -5.047
1372.5 | 50.5 | -5.047
1372.6 | 50.5 | -5.047
1372.7 | 50.5 | -5.047
1372.8 | 50.5 | -5.047
1372.9 | 50.5 | -5.047
1373 | 50.5 | -5.047
1373.1 | 50.5 | -5.047
1373.2 | 50.5 | -5.047
1373.3 | 50.5 | -5.047
1373.4 | 50.5 | -5.047
1373.5 | 50.5 | -5.047
1373.6 | 50.5 | -5.047
1373.7 | 50.5 | -5.047
1373.8 | 50.5 | -5.047
1373.9 | 50.5 | -5.047
1374 | 50.5 | -5.047
1374.1 | 50.5 | -5.047
1374.2 | 50.5 | -5.047
1374.3 | 50.5 | -5.047
1374.4 | 50.5 | -5.048
1374.5 | 50.5 | -5.048
1374.6 | 50.5 | -5.048
1374.7 | 50.5 | -5.048
1374.8 | 50.5 | -5.048
1374.9 | 50.5 | -5.048
1375 | 50.5 | -5.048
1375.1 | 50.5 | -5.048
1375.2 | 50.5 | -5.048
1375.3 | 50.5 | -5.048
1375.4 | 50.5 | -5.048
1375.5 | 50.5 | -5.048
1375.6 | 50.5 | -5.048
1375.7 | 50.5 | -5.048
1375.8 | 50.5 | -5.048
1375.9 | 50.5 | -5.048
1376 | 50.5 | -5.048
1376.1 | 50.5 | -5.048
1376.2 | 50.5 | -5.048
1376.3 | 50.5 | -5.048
1376.4 | 50.5 | -5.048
1376.5 | 50.5 | -5.048
1376.6 | 50.5 | -5.048
1376.7 | 50.5 | -5.048
1376.8 | 50.5 | -5.048
1376.9 | 50.5 | -5.048
1377 | 50.5 | -5.048
1377.1 | 50.5 | -5.048
1377.2 | 50.5 | -5.048
1377.3 | 50.5 | -5.048
1377.4 | 50.5 | -5.048
1377.5 | 50.5 | -5.048
1377.6 | 50.5 | -5.048
1377.7 | 50.5 | -5.048
1377.8 | 50.5 | -5.048
1377.9 | 50.5 | -5.048
1378 | 50.5 | -5.048
1378.1 | 50.5 | -5.048
1378.2 | 50.5 | -5.048
1378.3 | 50.5 | -5.048
1378.4 | 50.5 | -5.048
1378.5 | 50.5 | -5.048
1378.6 | 50.5 | -5.048
1378.7 | 50.5 | -5.048
1378.8 | 50.5 | -5.048
1378.9 | 50.5 | -5.048
1379 | 50.5 | -5.048
1379.1 | 50.5 | -5.048
1379.2 | 50.5 | -5.048
1379.3 | 50.5 | -5.048
1379.4 | 50.5 | -5.048
1379.5 | 50.5 | -5.048
1379.6 | 50.5 | -5.048
1379.7 | 50.5 | -5.048
1379.8 | 50.5 | -5.048
1379.9 | 50.5 | -5.048
1380 | 50.5 | -5.048
1380.1 | 50.5 | -5.048
1380.2 | 50.5 | -5.048
1380.3 | 50.5 | -5.048
1380.4 | 50.5 | -5.048
1380.5 | 50.5 | -5.048
1380.6 | 50.5 | -5.048
1380.7 | 50.5 | -5.048
1380.8 | 50.5 | -5.048
1380.9 | 50.5 | -5.048
1381 | 50.5 | -5.048
1381.1 | 50.5 | -5.048
1381.2 | 50.5 | -5.048
1381.3 | 50.5 | -5.048
1381.4 | 50.5 | -5.048
1381.5 | 50.5 | -5.048
1381.6 | 50.5 | -5.048
1381.7 | 50.5 | -5.048
1381.8 | 50.5 | -5.048
1381.9 | 50.5 | -5.048
1382 | 50.5 | -5.048
1382.1 | 50.5 | -5.048
1382.2 | 50.5 | -5.048
1382.3 | 50.5 | -5.048
1382.4 | 50.5 | -5.048
1382.5 | 50.5 | -5.048
1382.6 | 50.5 | -5.048
1382.7 | 50.5 | -5.048
1382.8 | 50.5 | -5.048
1382.9 | 50.5 | -5.048
1383 | 50.5 | -5.048
1383.1 | 50.5 | -5.048
1383.2 | 50.5 | -5.048
1383.3 | 50.5 | -5.048
1383.4 | 50.5 | -5.048
1383.5 | 50.5 | -5.048
1383.6 | 50.5 | -5.048
1383.7 | 50.5 | -5.048
1383.8 | 50.5 | -5.048
1383.9 | 50.5 | -5.047
1384 | 50.5 | -5.047
1384.1 | 50.5 | -5.047
1384.2 | 50.5 | -5.047
1384.3 | 50.5 | -5.047
1384.4 | 50.5 | -5.047
1384.5 | 50.5 | -5.047
1384.6 | 50.5 | -5.047
1384.7 | 50.5 | -5.047
1384.8 | 50.5 | -5.047
1384.9 | 50.5 | -5.047
1385 | 50.5 | -5.047
1385.1 | 50.5 | -5.047
1385.2 | 50.5 | -5.047
1385.3 | 50.5 | -5.047
1385.4 | 50.5 | -5.047
1385.5 | 50.5 | -5.047
1385.6 | 50.5 | -5.047
1385.7 | 50.5 | -5.047
1385.8 | 50.5 | -5.047
1385.9 | 50.5 | -5.047
1386 | 50.5 | -5.047
1386.1 | 50.5 | -5.048
1386.2 | 50.5 | -5.048
1386.3 | 50.5 | -5.048
1386.4 | 50.5 | -5.048
1386.5 | 50.5 | -5.048
1386.6 | 50.5 | -5.048
1386.7 | 50.5 | -5.048
1386.8 | 50.5 | -5.048
1386.9 | 50.5 | -5.048
1387 | 50.5 | -5.048
1387.1 | 50.5 | -5.048
1387.2 | 50.5 | -5.048
1387.3 | 50.5 | -5.048
1387.4 | 50.5 | -5.048
1387.5 | 50.5 | -5.048
1387.6 | 50.5 | -5.048
1387.7 | 50.5 | -5.048
1387.8 | 50.5 | -5.048
1387.9 | 50.5 | -5.048
1388 | 50.5 | -5.048
1388.1 | 50.5 | -5.048
1388.2 | 50.5 | -5.048
1388.3 | 50.5 | -5.048
1388.4 | 50.5 | -5.048
1388.5 | 50.5 | -5.048
1388.6 | 50.5 | -5.048
1388.7 | 50.5 | -5.048
1388.8 | 50.5 | -5.048
1388.9 | 50.5 | -5.048
1389 | 50.5 | -5.048
1389.1 | 50.5 | -5.048
1389.2 | 50.5 | -5.048
1389.3 | 50.5 | -5.048
1389.4 | 50.5 | -5.048
1389.5 | 50.5 | -5.048
1389.6 | 50.5 | -5.048
1389.7 | 50.5 | -5.048
1389.8 | 50.5 | -5.048
1389.9 | 50.5 | -5.048
1390 | 50.5 | -5.048
1390.1 | 50.5 | -5.047
1390.2 | 50.5 | -5.047
1390.3 | 50.5 | -5.047
1390.4 | 50.5 | -5.047
1390.5 | 50.5 | -5.047
1390.6 | 50.5 | -5.047
1390.7 | 50.5 | -5.047
1390.8 | 50.5 | -5.047
1390.9 | 50.5 | -5.047
1391 | 50.5 | -5.047
1391.1 | 50.5 | -5.047
1391.2 | 50.5 | -5.048
1391.3 | 50.5 | -5.048
1391.4 | 50.5 | -5.048
1391.5 | 50.5 | -5.048
1391.6 | 50.5 | -5.048
1391.7 | 50.5 | -5.048
1391.8 | 50.5 | -5.048
1391.9 | 50.5 | -5.048
1392 | 50.5 | -5.048
1392.1 | 50.5 | -5.048
1392.2 | 50.5 | -5.048
1392.3 | 50.5 | -5.048
1392.4 | 50.5 | -5.048
1392.5 | 50.5 | -5.048
1392.6 | 50.5 | -5.048
1392.7 | 50.5 | -5.048
1392.8 | 50.5 | -5.048
1392.9 | 50.5 | -5.048
1393 | 50.5 | -5.048
1393.1 | 50.5 | -5.048
1393.2 | 50.5 | -5.048
1393.3 | 50.5 | -5.048
1393.4 | 50.5 | -5.048
1393.5 | 50.5 | -5.048
1393.6 | 50.5 | -5.048
1393.7 | 50.5 | -5.048
1393.8 | 50.5 | -5.048
1393.9 | 50.5 | -5.048
1394 | 50.5 | -5.048
1394.1 | 50.5 | -5.048
1394.2 | 50.5 | -5.048
1394.3 | 50.5 | -5.048
1394.4 | 50.5 | -5.048
1394.5 | 50.5 | -5.048
1394.6 | 50.5 | -5.048
1394.7 | 50.5 | -5.048
1394.8 | 50.5 | -5.048
1394.9 | 50.5 | -5.048
1395 | 50.5 | -5.048
1395.1 | 50.5 | -5.048
1395.2 | 50.5 | -5.048
1395.3 | 50.5 | -5.048
1395.4 | 50.5 | -5.048
1395.5 | 50.5 | -5.048
1395.6 | 50.5 | -5.048
1395.7 | 50.5 | -5.048
1395.8 | 50.5 | -5.048
1395.9 | 50.5 | -5.048
1396 | 50.5 | -5.048
1396.1 | 50.5 | -5.048
1396.2 | 50.5 | -5.048
1396.3 | 50.5 | -5.048
1396.4 | 50.5 | -5.048
1396.5 | 50.5 | -5.048
1396.6 | 50.5 | -5.048
1396.7 | 50.5 | -5.048
1396.8 | 50.5 | -5.048
1396.9 | 50.5 | -5.048
1397 | 50.5 | -5.048
1397.1 | 50.5 | -5.048
1397.2 | 50.5 | -5.048
1397.3 | 50.5 | -5.048
1397.4 | 50.5 | -5.048
1397.5 | 50.5 | -5.048
1397.6 | 50.5 | -5.048
1397.7 | 50.5 | -5.048
1397.8 | 50.5 | -5.048
1397.9 | 50.5 | -5.048
1398 | 50.5 | -5.048
1398.1 | 50.5 | -5.048
1398.2 | 50.5 | -5.048
1398.3 | 50.5 | -5.048
1398.4 | 50.5 | -5.048
1398.5 | 50.5 | -5.048
1398.6 | 50.5 | -5.048
1398.7 | 50.5 | -5.048
1398.8 | 50.5 | -5.048
1398.9 | 50.5 | -5.048
1399 | 50.5 | -5.048
1399.1 | 50.5 | -5.048
1399.2 | 50.5 | -5.048
1399.3 | 50.5 | -5.048
1399.4 | 50.5 | -5.048
1399.5 | 50.5 | -5.048
1399.6 | 50.5 | -5.048
1399.7 | 50.5 | -5.048
1399.8 | 50.5 | -5.048
1399.9 | 50.5 | -5.048
1400 | 50.5 | -5.048
1400.1 | 50.5 | -5.048
1400.2 | 50.5 | -5.048
1400.3 | 50.5 | -5.048
1400.4 | 50.5 | -5.048
1400.5 | 50.5 | -5.048
1400.6 | 50.5 | -5.048
1400.7 | 50.5 | -5.048
1400.8 | 50.5 | -5.048
1400.9 | 50.5 | -5.048
1401 | 50.5 | -5.048
1401.1 | 50.5 | -5.048
1401.2 | 50.5 | -5.048
1401.3 | 50.5 | -5.048
1401.4 | 50.5 | -5.048
1401.5 | 50.5 | -5.048
1401.6 | 50.5 | -5.048
1401.7 | 50.5 | -5.048
1401.8 | 50.5 | -5.048
1401.9 | 50.5 | -5.048
1402 | 50.5 | -5.048
1402.1 | 50.5 | -5.048
1402.2 | 50.5 | -5.048
1402.3 | 50.5 | -5.048
1402.4 | 50.5 | -5.048
1402.5 | 50.5 | -5.048
1402.6 | 50.5 | -5.048
1402.7 | 50.5 | -5.048
1402.8 | 50.5 | -5.048
1402.9 | 50.5 | -5.047
1403 | 50.5 | -5.047
1403.1 | 50.5 | -5.047
1403.2 | 50.5 | -5.047
1403.3 | 50.5 | -5.047
1403.4 | 50.5 | -5.047
1403.5 | 50.5 | -5.047
1403.6 | 50.5 | -5.047
1403.7 | 50.5 | -5.048
1403.8 | 50.5 | -5.048
1403.9 | 50.5 | -5.048
1404 | 50.5 | -5.048
1404.1 | 50.5 | -5.048
1404.2 | 50.5 | -5.048
1404.3 | 50.5 | -5.048
1404.4 | 50.5 | -5.048
1404.5 | 50.5 | -5.048
1404.6 | 50.5 | -5.048
1404.7 | 50.5 | -5.048
1404.8 | 50.5 | -5.048
1404.9 | 50.5 | -5.048
1405 | 50.5 | -5.048
1405.1 | 50.5 | -5.048
1405.2 | 50.5 | -5.048
1405.3 | 50.5 | -5.048
1405.4 | 50.5 | -5.048
1405.5 | 50.5 | -5.048
1405.6 | 50.5 | -5.048
1405.7 | 50.5 | -5.048
1405.8 | 50.5 | -5.048
1405.9 | 50.5 | -5.048
1406 | 50.5 | -5.048
1406.1 | 50.5 | -5.048
1406.2 | 50.5 | -5.048
1406.3 | 50.5 | -5.048
1406.4 | 50.5 | -5.048
1406.5 | 50.5 | -5.048
1406.6 | 50.5 | -5.048
1406.7 | 50.5 | -5.048
1406.8 | 50.5 | -5.048
1406.9 | 50.5 | -5.048
1407 | 50.5 | -5.048
1407.1 | 50.5 | -5.048
1407.2 | 50.5 | -5.048
1407.3 | 50.5 | -5.048
1407.4 | 50.5 | -5.048
1407.5 | 50.5 | -5.048
1407.6 | 50.5 | -5.048
1407.7 | 50.5 | -5.048
1407.8 | 50.5 | -5.048
1407.9 | 50.5 | -5.048
1408 | 50.5 | -5.048
1408.1 | 50.5 | -5.048
1408.2 | 50.5 | -5.048
1408.3 | 50.5 | -5.048
1408.4 | 50.5 | -5.048
1408.5 | 50.5 | -5.048
1408.6 | 50.5 | -5.048
1408.7 | 50.5 | -5.048
1408.8 | 50.5 | -5.048
1408.9 | 50.5 | -5.048
1409 | 50.5 | -5.048
1409.1 | 50.5 | -5.048
1409.2 | 50.5 | -5.048
1409.3 | 50.5 | -5.048
1409.4 | 50.5 | -5.048
1409.5 | 50.5 | -5.048
1409.6 | 50.5 | -5.048
1409.7 | 50.5 | -5.048
1409.8 | 50.5 | -5.048
1409.9 | 50.5 | -5.048
1410 | 50.5 | -5.048
1410.1 | 50.5 | -5.048
1410.2 | 50.5 | -5.048
1410.3 | 50.5 | -5.048
1410.4 | 50.5 | -5.048
1410.5 | 50.5 | -5.048
1410.6 | 50.5 | -5.048
1410.7 | 50.5 | -5.048
1410.8 | 50.5 | -5.048
1410.9 | 50.5 | -5.048
1411 | 50.5 | -5.048
1411.1 | 50.5 | -5.048
1411.2 | 50.5 | -5.048
1411.3 | 50.5 | -5.048
1411.4 | 50.5 | -5.048
1411.5 | 50.5 | -5.048
1411.6 | 50.5 | -5.048
1411.7 | 50.5 | -5.048
1411.8 | 50.5 | -5.048
1411.9 | 50.5 | -5.048
1412 | 50.5 | -5.048
1412.1 | 50.5 | -5.048
1412.2 | 50.5 | -5.048
1412.3 | 50.5 | -5.048
1412.4 | 50.5 | -5.048
1412.5 | 50.5 | -5.048
1412.6 | 50.5 | -5.048
1412.7 | 50.5 | -5.048
1412.8 | 50.5 | -5.048
1412.9 | 50.5 | -5.048
1413 | 50.5 | -5.048
1413.1 | 50.5 | -5.048
1413.2 | 50.5 | -5.048
1413.3 | 50.5 | -5.048
1413.4 | 50.5 | -5.048
1413.5 | 50.5 | -5.048
1413.6 | 50.5 | -5.048
1413.7 | 50.5 | -5.048
1413.8 | 50.5 | -5.048
1413.9 | 50.5 | -5.048
1414 | 50.5 | -5.048
1414.1 | 50.5 | -5.048
1414.2 | 50.5 | -5.048
1414.3 | 50.5 | -5.048
1414.4 | 50.5 | -5.048
1414.5 | 50.5 | -5.048
1414.6 | 50.5 | -5.048
1414.7 | 50.5 | -5.048
1414.8 | 50.5 | -5.048
1414.9 | 50.5 | -5.048
1415 | 50.5 | -5.048
1415.1 | 50.5 | -5.048
1415.2 | 50.5 | -5.048
1415.3 | 50.5 | -5.048
1415.4 | 50.5 | -5.048
1415.5 | 50.5 | -5.048
1415.6 | 50.5 | -5.048
1415.7 | 50.5 | -5.048
1415.8 | 50.5 | -5.048
1415.9 | 50.5 | -5.048
1416 | 50.5 | -5.048
1416.1 | 50.5 | -5.048
1416.2 | 50.5 | -5.048
1416.3 | 50.5 | -5.048
1416.4 | 50.5 | -5.048
1416.5 | 50.5 | -5.048
1416.6 | 50.5 | -5.048
1416.7 | 50.5 | -5.048
1416.8 | 50.5 | -5.048
1416.9 | 50.5 | -5.048
1417 | 50.5 | -5.048
1417.1 | 50.5 | -5.048
1417.2 | 50.5 | -5.048
1417.3 | 50.5 | -5.048
1417.4 | 50.5 | -5.048
1417.5 | 50.5 | -5.048
1417.6 | 50.5 | -5.048
1417.7 | 50.5 | -5.048
1417.8 | 50.5 | -5.048
1417.9 | 50.5 | -5.048
1418 | 50.5 | -5.048
1418.1 | 50.5 | -5.048
1418.2 | 50.5 | -5.048
1418.3 | 50.5 | -5.048
1418.4 | 50.5 | -5.048
1418.5 | 50.5 | -5.048
1418.6 | 50.5 | -5.048
1418.7 | 50.5 | -5.048
1418.8 | 50.5 | -5.048
1418.9 | 50.5 | -5.048
1419 | 50.5 | -5.048
1419.1 | 50.5 | -5.048
1419.2 | 50.5 | -5.048
1419.3 | 50.5 | -5.048
1419.4 | 50.5 | -5.048
1419.5 | 50.5 | -5.048
1419.6 | 50.5 | -5.048
1419.7 | 50.5 | -5.048
1419.8 | 50.5 | -5.048
1419.9 | 50.5 | -5.048
1420 | 50.5 | -5.048
1420.1 | 50.5 | -5.048
1420.2 | 50.5 | -5.048
1420.3 | 50.5 | -5.048
1420.4 | 50.5 | -5.048
1420.5 | 50.5 | -5.048
1420.6 | 50.5 | -5.048
1420.7 | 50.5 | -5.048
1420.8 | 50.5 | -5.048
1420.9 | 50.5 | -5.048
1421 | 50.5 | -5.048
1421.1 | 50.5 | -5.048
1421.2 | 50.5 | -5.048
1421.3 | 50.5 | -5.048
1421.4 | 50.5 | -5.048
1421.5 | 50.5 | -5.048
1421.6 | 50.5 | -5.048
1421.7 | 50.5 | -5.048
1421.8 | 50.5 | -5.048
1421.9 | 50.5 | -5.048
1422 | 50.5 | -5.048
1422.1 | 50.5 | -5.048
1422.2 | 50.5 | -5.048
1422.3 | 50.5 | -5.048
1422.4 | 50.5 | -5.048
1422.5 | 50.5 | -5.048
1422.6 | 50.5 | -5.048
1422.7 | 50.5 | -5.048
1422.8 | 50.5 | -5.048
1422.9 | 50.5 | -5.048
1423 | 50.5 | -5.048
1423.1 | 50.5 | -5.048
1423.2 | 50.5 | -5.048
1423.3 | 50.5 | -5.048
1423.4 | 50.5 | -5.048
1423.5 | 50.5 | -5.048
1423.6 | 50.5 | -5.048
1423.7 | 50.5 | -5.048
1423.8 | 50.5 | -5.048
1423.9 | 50.5 | -5.048
1424 | 50.5 | -5.048
1424.1 | 50.5 | -5.048
1424.2 | 50.5 | -5.048
1424.3 | 50.5 | -5.048
1424.4 | 50.5 | -5.048
1424.5 | 50.5 | -5.048
1424.6 | 50.5 | -5.048
1424.7 | 50.5 | -5.048
1424.8 | 50.5 | -5.048
1424.9 | 50.5 | -5.047
1425 | 50.5 | -5.047
1425.1 | 50.5 | -5.047
1425.2 | 50.5 | -5.047
1425.3 | 50.5 | -5.047
1425.4 | 50.5 | -5.047
1425.5 | 50.5 | -5.047
1425.6 | 50.5 | -5.047
1425.7 | 50.5 | -5.047
1425.8 | 50.5 | -5.047
1425.9 | 50.5 | -5.047
1426 | 50.5 | -5.047
1426.1 | 50.5 | -5.048
1426.2 | 50.5 | -5.048
1426.3 | 50.5 | -5.048
1426.4 | 50.5 | -5.048
1426.5 | 50.5 | -5.048
1426.6 | 50.5 | -5.048
1426.7 | 50.5 | -5.048
1426.8 | 50.5 | -5.048
1426.9 | 50.5 | -5.048
1427 | 50.5 | -5.048
1427.1 | 50.5 | -5.048
1427.2 | 50.5 | -5.048
1427.3 | 50.5 | -5.048
1427.4 | 50.5 | -5.048
1427.5 | 50.5 | -5.048
1427.6 | 50.5 | -5.048
1427.7 | 50.5 | -5.048
1427.8 | 50.5 | -5.048
1427.9 | 50.5 | -5.048
1428 | 50.5 | -5.048
1428.1 | 50.5 | -5.048
1428.2 | 50.5 | -5.048
1428.3 | 50.5 | -5.048
1428.4 | 50.5 | -5.048
1428.5 | 50.5 | -5.048
1428.6 | 50.5 | -5.048
1428.7 | 50.5 | -5.048
1428.8 | 50.5 | -5.048
1428.9 | 50.5 | -5.048
1429 | 50.5 | -5.048
1429.1 | 50.5 | -5.048
1429.2 | 50.5 | -5.048
1429.3 | 50.5 | -5.048
1429.4 | 50.5 | -5.048
1429.5 | 50.5 | -5.048
1429.6 | 50.5 | -5.048
1429.7 | 50.5 | -5.048
1429.8 | 50.5 | -5.048
1429.9 | 50.5 | -5.048
1430 | 50.5 | -5.048
1430.1 | 50.5 | -5.048
1430.2 | 50.5 | -5.048
1430.3 | 50.5 | -5.048
1430.4 | 50.5 | -5.048
1430.5 | 50.5 | -5.048
1430.6 | 50.5 | -5.049
1430.7 | 50.5 | -5.049
1430.8 | 50.5 | -5.049
1430.9 | 50.5 | -5.049
1431 | 50.5 | -5.049
1431.1 | 50.5 | -5.049
1431.2 | 50.5 | -5.049
1431.3 | 50.5 | -5.049
1431.4 | 50.5 | -5.048
1431.5 | 50.5 | -5.048
1431.6 | 50.5 | -5.048
1431.7 | 50.5 | -5.048
1431.8 | 50.5 | -5.048
1431.9 | 50.5 | -5.048
1432 | 50.5 | -5.048
1432.1 | 50.5 | -5.048
1432.2 | 50.5 | -5.048
1432.3 | 50.5 | -5.048
1432.4 | 50.5 | -5.048
1432.5 | 50.5 | -5.048
1432.6 | 50.5 | -5.048
1432.7 | 50.5 | -5.048
1432.8 | 50.5 | -5.048
1432.9 | 50.5 | -5.048
1433 | 50.5 | -5.048
1433.1 | 50.5 | -5.048
1433.2 | 50.5 | -5.048
1433.3 | 50.5 | -5.048
1433.4 | 50.5 | -5.048
1433.5 | 50.5 | -5.048
1433.6 | 50.5 | -5.048
1433.7 | 50.5 | -5.048
1433.8 | 50.5 | -5.048
1433.9 | 50.5 | -5.048
1434 | 50.5 | -5.048
1434.1 | 50.5 | -5.048
1434.2 | 50.5 | -5.048
1434.3 | 50.5 | -5.048
1434.4 | 50.5 | -5.048
1434.5 | 50.5 | -5.048
1434.6 | 50.5 | -5.048
1434.7 | 50.5 | -5.048
1434.8 | 50.5 | -5.048
1434.9 | 50.5 | -5.048
1435 | 50.5 | -5.048
1435.1 | 50.5 | -5.048
1435.2 | 50.5 | -5.048
1435.3 | 50.5 | -5.048
1435.4 | 50.5 | -5.048
1435.5 | 50.5 | -5.047
1435.6 | 50.5 | -5.047
1435.7 | 50.5 | -5.047
1435.8 | 50.5 | -5.047
1435.9 | 50.5 | -5.047
1436 | 50.5 | -5.047
1436.1 | 50.5 | -5.047
1436.2 | 50.5 | -5.047
1436.3 | 50.5 | -5.047
1436.4 | 50.5 | -5.047
1436.5 | 50.5 | -5.047
1436.6 | 50.5 | -5.048
1436.7 | 50.5 | -5.048
1436.8 | 50.5 | -5.048
1436.9 | 50.5 | -5.048
1437 | 50.5 | -5.048
1437.1 | 50.5 | -5.048
1437.2 | 50.5 | -5.048
1437.3 | 50.5 | -5.048
1437.4 | 50.5 | -5.048
1437.5 | 50.5 | -5.048
1437.6 | 50.5 | -5.048
1437.7 | 50.5 | -5.048
1437.8 | 50.5 | -5.048
1437.9 | 50.5 | -5.048
1438 | 50.5 | -5.048
1438.1 | 50.5 | -5.048
1438.2 | 50.5 | -5.048
1438.3 | 50.5 | -5.048
1438.4 | 50.5 | -5.048
1438.5 | 50.5 | -5.047
1438.6 | 50.5 | -5.047
1438.7 | 50.5 | -5.047
1438.8 | 50.5 | -5.047
1438.9 | 50.5 | -5.047
1439 | 50.5 | -5.047
1439.1 | 50.5 | -5.047
1439.2 | 50.5 | -5.047
1439.3 | 50.5 | -5.047
1439.4 | 50.5 | -5.047
1439.5 | 50.5 | -5.047
1439.6 | 50.5 | -5.048
1439.7 | 50.5 | -5.048
1439.8 | 50.5 | -5.048
1439.9 | 50.5 | -5.048
1440 | 50.5 | -5.048
1440.1 | 50.5 | -5.048
1440.2 | 50.5 | -5.048
1440.3 | 50.5 | -5.048
1440.4 | 50.5 | -5.048
1440.5 | 50.5 | -5.048
1440.6 | 50.5 | -5.048
1440.7 | 50.5 | -5.048
1440.8 | 50.5 | -5.048
1440.9 | 50.5 | -5.048
1441 | 50.5 | -5.048
1441.1 | 50.5 | -5.048
1441.2 | 50.5 | -5.048
1441.3 | 50.5 | -5.048
1441.4 | 50.5 | -5.048
1441.5 | 50.5 | -5.048
1441.6 | 50.5 | -5.048
1441.7 | 50.5 | -5.048
1441.8 | 50.5 | -5.048
1441.9 | 50.5 | -5.048
1442 | 50.5 | -5.048
1442.1 | 50.5 | -5.048
1442.2 | 50.5 | -5.048
1442.3 | 50.5 | -5.048
1442.4 | 50.5 | -5.048
1442.5 | 50.5 | -5.048
1442.6 | 50.5 | -5.048
1442.7 | 50.5 | -5.048
1442.8 | 50.5 | -5.048
1442.9 | 50.5 | -5.048
1443 | 50.5 | -5.048
1443.1 | 50.5 | -5.048
1443.2 | 50.5 | -5.048
1443.3 | 50.5 | -5.048
1443.4 | 50.5 | -5.048
1443.5 | 50.5 | -5.048
1443.6 | 50.5 | -5.048
1443.7 | 50.5 | -5.048
1443.8 | 50.5 | -5.048
1443.9 | 50.5 | -5.048
1444 | 50.5 | -5.048
1444.1 | 50.5 | -5.048
1444.2 | 50.5 | -5.048
1444.3 | 50.5 | -5.048
1444.4 | 50.5 | -5.048
1444.5 | 50.5 | -5.048
1444.6 | 50.5 | -5.048
1444.7 | 50.5 | -5.048
1444.8 | 50.5 | -5.048
1444.9 | 50.5 | -5.048
1445 | 50.5 | -5.048
1445.1 | 50.5 | -5.048
1445.2 | 50.5 | -5.048
1445.3 | 50.5 | -5.047
1445.4 | 50.5 | -5.047
1445.5 | 50.5 | -5.047
1445.6 | 50.5 | -5.047
1445.7 | 50.5 | -5.047
1445.8 | 50.5 | -5.047
1445.9 | 50.5 | -5.047
1446 | 50.5 | -5.047
1446.1 | 50.5 | -5.047
1446.2 | 50.5 | -5.047
1446.3 | 50.5 | -5.047
1446.4 | 50.5 | -5.047
1446.5 | 50.5 | -5.047
1446.6 | 50.5 | -5.047
1446.7 | 50.5 | -5.047
1446.8 | 50.5 | -5.047
1446.9 | 50.5 | -5.047
1447 | 50.5 | -5.047
1447.1 | 50.5 | -5.047
1447.2 | 50.5 | -5.047
1447.3 | 50.5 | -5.047
1447.4 | 50.5 | -5.047
1447.5 | 50.5 | -5.047
1447.6 | 50.5 | -5.048
1447.7 | 50.5 | -5.048
1447.8 | 50.5 | -5.048
1447.9 | 50.5 | -5.048
1448 | 50.5 | -5.048
1448.1 | 50.5 | -5.048
1448.2 | 50.5 | -5.048
1448.3 | 50.5 | -5.048
1448.4 | 50.5 | -5.048
1448.5 | 50.5 | -5.048
1448.6 | 50.5 | -5.048
1448.7 | 50.5 | -5.048
1448.8 | 50.5 | -5.048
1448.9 | 50.5 | -5.048
1449 | 50.5 | -5.048
1449.1 | 50.5 | -5.048
1449.2 | 50.5 | -5.048
1449.3 | 50.5 | -5.048
1449.4 | 50.5 | -5.048
1449.5 | 50.5 | -5.048
1449.6 | 50.5 | -5.048
1449.7 | 50.5 | -5.048
1449.8 | 50.5 | -5.048
1449.9 | 50.5 | -5.048
1450 | 50.5 | -5.048
1450.1 | 50.5 | -5.048
1450.2 | 50.5 | -5.048
1450.3 | 50.5 | -5.048
1450.4 | 50.5 | -5.048
1450.5 | 50.5 | -5.048
1450.6 | 50.5 | -5.048
1450.7 | 50.5 | -5.048
1450.8 | 50.5 | -5.048
1450.9 | 50.5 | -5.048
1451 | 50.5 | -5.048
1451.1 | 50.5 | -5.048
1451.2 | 50.5 | -5.048
1451.3 | 50.5 | -5.047
1451.4 | 50.5 | -5.047
1451.5 | 50.5 | -5.047
1451.6 | 50.5 | -5.048
1451.7 | 50.5 | -5.048
1451.8 | 50.5 | -5.048
1451.9 | 50.5 | -5.048
1452 | 50.5 | -5.048
1452.1 | 50.5 | -5.048
1452.2 | 50.5 | -5.048
1452.3 | 50.5 | -5.048
1452.4 | 50.5 | -5.048
1452.5 | 50.5 | -5.048
1452.6 | 50.5 | -5.048
1452.7 | 50.5 | -5.048
1452.8 | 50.5 | -5.047
1452.9 | 50.5 | -5.047
1453 | 50.5 | -5.047
1453.1 | 50.5 | -5.047
1453.2 | 50.5 | -5.047
1453.3 | 50.5 | -5.047
1453.4 | 50.5 | -5.048
1453.5 | 50.5 | -5.048
1453.6 | 50.5 | -5.048
1453.7 | 50.5 | -5.048
1453.8 | 50.5 | -5.048
1453.9 | 50.5 | -5.048
1454 | 50.5 | -5.048
1454.1 | 50.5 | -5.048
1454.2 | 50.5 | -5.048
1454.3 | 50.5 | -5.048
1454.4 | 50.5 | -5.048
1454.5 | 50.5 | -5.048
1454.6 | 50.5 | -5.048
1454.7 | 50.5 | -5.048
1454.8 | 50.5 | -5.048
1454.9 | 50.5 | -5.048
1455 | 50.5 | -5.048
1455.1 | 50.5 | -5.048
1455.2 | 50.5 | -5.048
1455.3 | 50.5 | -5.048
1455.4 | 50.5 | -5.048
1455.5 | 50.5 | -5.048
1455.6 | 50.5 | -5.048
1455.7 | 50.5 | -5.048
1455.8 | 50.5 | -5.048
1455.9 | 50.5 | -5.048
1456 | 50.5 | -5.048
1456.1 | 50.5 | -5.048
1456.2 | 50.5 | -5.048
1456.3 | 50.5 | -5.048
1456.4 | 50.5 | -5.048
1456.5 | 50.5 | -5.048
1456.6 | 50.5 | -5.048
1456.7 | 50.5 | -5.048
1456.8 | 50.5 | -5.048
1456.9 | 50.5 | -5.048
1457 | 50.5 | -5.048
1457.1 | 50.5 | -5.048
1457.2 | 50.5 | -5.048
1457.3 | 50.5 | -5.048
1457.4 | 50.5 | -5.048
1457.5 | 50.5 | -5.048
1457.6 | 50.5 | -5.048
1457.7 | 50.5 | -5.048
1457.8 | 50.5 | -5.048
1457.9 | 50.5 | -5.048
1458 | 50.5 | -5.048
1458.1 | 50.5 | -5.048
1458.2 | 50.5 | -5.048
1458.3 | 50.5 | -5.048
1458.4 | 50.5 | -5.048
1458.5 | 50.5 | -5.048
1458.6 | 50.5 | -5.048
1458.7 | 50.5 | -5.048
1458.8 | 50.5 | -5.048
1458.9 | 50.5 | -5.048
1459 | 50.5 | -5.048
1459.1 | 50.5 | -5.048
1459.2 | 50.5 | -5.048
1459.3 | 50.5 | -5.048
1459.4 | 50.5 | -5.048
1459.5 | 50.5 | -5.048
1459.6 | 50.5 | -5.048
1459.7 | 50.5 | -5.048
1459.8 | 50.5 | -5.048
1459.9 | 50.5 | -5.048
1460 | 50.5 | -5.048
1460.1 | 50.5 | -5.048
1460.2 | 50.5 | -5.048
1460.3 | 50.5 | -5.048
1460.4 | 50.5 | -5.048
1460.5 | 50.5 | -5.048
1460.6 | 50.5 | -5.048
1460.7 | 50.5 | -5.048
1460.8 | 50.5 | -5.048
1460.9 | 50.5 | -5.048
1461 | 50.5 | -5.047
1461.1 | 50.5 | -5.047
1461.2 | 50.5 | -5.047
1461.3 | 50.5 | -5.047
1461.4 | 50.5 | -5.047
1461.5 | 50.5 | -5.047
1461.6 | 50.5 | -5.047
1461.7 | 50.5 | -5.047
1461.8 | 50.5 | -5.047
1461.9 | 50.5 | -5.047
1462 | 50.5 | -5.047
1462.1 | 50.5 | -5.048
1462.2 | 50.5 | -5.048
1462.3 | 50.5 | -5.048
1462.4 | 50.5 | -5.048
1462.5 | 50.5 | -5.048
1462.6 | 50.5 | -5.048
1462.7 | 50.5 | -5.048
1462.8 | 50.5 | -5.048
1462.9 | 50.5 | -5.048
1463 | 50.5 | -5.048
1463.1 | 50.5 | -5.048
1463.2 | 50.5 | -5.048
1463.3 | 50.5 | -5.048
1463.4 | 50.5 | -5.048
1463.5 | 50.5 | -5.048
1463.6 | 50.5 | -5.048
1463.7 | 50.5 | -5.048
1463.8 | 50.5 | -5.048
1463.9 | 50.5 | -5.048
1464 | 50.5 | -5.048
1464.1 | 50.5 | -5.048
1464.2 | 50.5 | -5.048
1464.3 | 50.5 | -5.048
1464.4 | 50.5 | -5.048
1464.5 | 50.5 | -5.048
1464.6 | 50.5 | -5.048
1464.7 | 50.5 | -5.048
1464.8 | 50.5 | -5.048
1464.9 | 50.5 | -5.048
1465 | 50.5 | -5.048
1465.1 | 50.5 | -5.048
1465.2 | 50.5 | -5.048
1465.3 | 50.5 | -5.048
1465.4 | 50.5 | -5.048
1465.5 | 50.5 | -5.048
1465.6 | 50.5 | -5.048
1465.7 | 50.5 | -5.048
1465.8 | 50.5 | -5.048
1465.9 | 50.5 | -5.048
1466 | 50.5 | -5.048
1466.1 | 50.5 | -5.048
1466.2 | 50.5 | -5.048
1466.3 | 50.5 | -5.048
1466.4 | 50.5 | -5.048
1466.5 | 50.5 | -5.048
1466.6 | 50.5 | -5.048
1466.7 | 50.5 | -5.048
1466.8 | 50.5 | -5.048
1466.9 | 50.5 | -5.048
1467 | 50.5 | -5.048
1467.1 | 50.5 | -5.048
1467.2 | 50.5 | -5.048
1467.3 | 50.5 | -5.048
1467.4 | 50.5 | -5.048
1467.5 | 50.5 | -5.048
1467.6 | 50.5 | -5.048
1467.7 | 50.5 | -5.048
1467.8 | 50.5 | -5.048
1467.9 | 50.5 | -5.048
1468 | 50.5 | -5.048
1468.1 | 50.5 | -5.048
1468.2 | 50.5 | -5.048
1468.3 | 50.5 | -5.048
1468.4 | 50.5 | -5.048
1468.5 | 50.5 | -5.048
1468.6 | 50.5 | -5.048
1468.7 | 50.5 | -5.047
1468.8 | 50.5 | -5.047
1468.9 | 50.5 | -5.047
1469 | 50.5 | -5.047
1469.1 | 50.5 | -5.047
1469.2 | 50.5 | -5.047
1469.3 | 50.5 | -5.047
1469.4 | 50.5 | -5.047
1469.5 | 50.5 | -5.047
1469.6 | 50.5 | -5.047
1469.7 | 50.5 | -5.047
1469.8 | 50.5 | -5.047
1469.9 | 50.5 | -5.047
1470 | 50.5 | -5.047
1470.1 | 50.5 | -5.047
1470.2 | 50.5 | -5.047
1470.3 | 50.5 | -5.047
1470.4 | 50.5 | -5.047
1470.5 | 50.5 | -5.047
1470.6 | 50.5 | -5.047
1470.7 | 50.5 | -5.047
1470.8 | 50.5 | -5.047
1470.9 | 50.5 | -5.047
1471 | 50.5 | -5.047
1471.1 | 50.5 | -5.047
1471.2 | 50.5 | -5.047
1471.3 | 50.5 | -5.047
1471.4 | 50.5 | -5.047
1471.5 | 50.5 | -5.047
1471.6 | 50.5 | -5.047
1471.7 | 50.5 | -5.047
1471.8 | 50.5 | -5.047
1471.9 | 50.5 | -5.047
1472 | 50.5 | -5.048
1472.1 | 50.5 | -5.048
1472.2 | 50.5 | -5.048
1472.3 | 50.5 | -5.048
1472.4 | 50.5 | -5.048
1472.5 | 50.5 | -5.048
1472.6 | 50.5 | -5.048
1472.7 | 50.5 | -5.048
1472.8 | 50.5 | -5.048
1472.9 | 50.5 | -5.048
1473 | 50.5 | -5.048
1473.1 | 50.5 | -5.048
1473.2 | 50.5 | -5.048
1473.3 | 50.5 | -5.048
1473.4 | 50.5 | -5.048
1473.5 | 50.5 | -5.048
1473.6 | 50.5 | -5.048
1473.7 | 50.5 | -5.048
1473.8 | 50.5 | -5.048
1473.9 | 50.5 | -5.048
1474 | 50.5 | -5.048
1474.1 | 50.5 | -5.048
1474.2 | 50.5 | -5.048
1474.3 | 50.5 | -5.048
1474.4 | 50.5 | -5.048
1474.5 | 50.5 | -5.047
1474.6 | 50.5 | -5.047
1474.7 | 50.5 | -5.047
1474.8 | 50.5 | -5.047
1474.9 | 50.5 | -5.047
1475 | 50.5 | -5.047
1475.1 | 50.5 | -5.047
1475.2 | 50.5 | -5.047
1475.3 | 50.5 | -5.047
1475.4 | 50.5 | -5.047
1475.5 | 50.5 | -5.047
1475.6 | 50.5 | -5.047
1475.7 | 50.5 | -5.047
1475.8 | 50.5 | -5.047
1475.9 | 50.5 | -5.047
1476 | 50.5 | -5.047
1476.1 | 50.5 | -5.047
1476.2 | 50.5 | -5.047
1476.3 | 50.5 | -5.047
1476.4 | 50.5 | -5.047
1476.5 | 50.5 | -5.047
1476.6 | 50.5 | -5.047
1476.7 | 50.5 | -5.047
1476.8 | 50.5 | -5.047
1476.9 | 50.5 | -5.047
1477 | 50.5 | -5.047
1477.1 | 50.5 | -5.047
1477.2 | 50.5 | -5.047
1477.3 | 50.5 | -5.047
1477.4 | 50.5 | -5.047
1477.5 | 50.5 | -5.047
1477.6 | 50.5 | -5.047
1477.7 | 50.5 | -5.047
1477.8 | 50.5 | -5.047
1477.9 | 50.5 | -5.047
1478 | 50.5 | -5.048
1478.1 | 50.5 | -5.048
1478.2 | 50.5 | -5.048
1478.3 | 50.5 | -5.048
1478.4 | 50.5 | -5.048
1478.5 | 50.5 | -5.048
1478.6 | 50.5 | -5.048
1478.7 | 50.5 | -5.048
1478.8 | 50.5 | -5.048
1478.9 | 50.5 | -5.048
1479 | 50.5 | -5.048
1479.1 | 50.5 | -5.048
1479.2 | 50.5 | -5.048
1479.3 | 50.5 | -5.048
1479.4 | 50.5 | -5.048
1479.5 | 50.5 | -5.048
1479.6 | 50.5 | -5.048
1479.7 | 50.5 | -5.048
1479.8 | 50.5 | -5.048
1479.9 | 50.5 | -5.048
1480 | 50.5 | -5.048
1480.1 | 50.5 | -5.048
1480.2 | 50.5 | -5.048
1480.3 | 50.5 | -5.048
1480.4 | 50.5 | -5.048
1480.5 | 50.5 | -5.048
1480.6 | 50.5 | -5.048
1480.7 | 50.5 | -5.048
1480.8 | 50.5 | -5.048
1480.9 | 50.5 | -5.048
1481 | 50.5 | -5.048
1481.1 | 50.5 | -5.048
1481.2 | 50.5 | -5.048
1481.3 | 50.5 | -5.048
1481.4 | 50.5 | -5.048
1481.5 | 50.5 | -5.048
1481.6 | 50.5 | -5.048
1481.7 | 50.5 | -5.048
1481.8 | 50.5 | -5.048
1481.9 | 50.5 | -5.048
1482 | 50.5 | -5.048
1482.1 | 50.5 | -5.048
1482.2 | 50.5 | -5.048
1482.3 | 50.5 | -5.048
1482.4 | 50.5 | -5.048
1482.5 | 50.5 | -5.048
1482.6 | 50.5 | -5.048
1482.7 | 50.5 | -5.048
1482.8 | 50.5 | -5.048
1482.9 | 50.5 | -5.048
1483 | 50.5 | -5.048
1483.1 | 50.5 | -5.048
1483.2 | 50.5 | -5.048
1483.3 | 50.5 | -5.048
1483.4 | 50.5 | -5.048
1483.5 | 50.5 | -5.048
1483.6 | 50.5 | -5.048
1483.7 | 50.5 | -5.048
1483.8 | 50.5 | -5.048
1483.9 | 50.5 | -5.048
1484 | 50.5 | -5.048
1484.1 | 50.5 | -5.048
1484.2 | 50.5 | -5.048
1484.3 | 50.5 | -5.048
1484.4 | 50.5 | -5.047
1484.5 | 50.5 | -5.047
1484.6 | 50.5 | -5.047
1484.7 | 50.5 | -5.047
1484.8 | 50.5 | -5.047
1484.9 | 50.5 | -5.047
1485 | 50.5 | -5.047
1485.1 | 50.5 | -5.047
1485.2 | 50.5 | -5.047
1485.3 | 50.5 | -5.047
1485.4 | 50.5 | -5.047
1485.5 | 50.5 | -5.047
1485.6 | 50.5 | -5.047
1485.7 | 50.5 | -5.047
1485.8 | 50.5 | -5.047
1485.9 | 50.5 | -5.047
1486 | 50.5 | -5.047
1486.1 | 50.5 | -5.047
1486.2 | 50.5 | -5.047
1486.3 | 50.5 | -5.047
1486.4 | 50.5 | -5.047
1486.5 | 50.5 | -5.047
1486.6 | 50.5 | -5.047
1486.7 | 50.5 | -5.048
1486.8 | 50.5 | -5.048
1486.9 | 50.5 | -5.048
1487 | 50.5 | -5.048
1487.1 | 50.5 | -5.048
1487.2 | 50.5 | -5.048
1487.3 | 50.5 | -5.048
1487.4 | 50.5 | -5.048
1487.5 | 50.5 | -5.048
1487.6 | 50.5 | -5.048
1487.7 | 50.5 | -5.048
1487.8 | 50.5 | -5.048
1487.9 | 50.5 | -5.048
1488 | 50.5 | -5.048
1488.1 | 50.5 | -5.048
1488.2 | 50.5 | -5.048
1488.3 | 50.5 | -5.047
1488.4 | 50.5 | -5.047
1488.5 | 50.5 | -5.047
1488.6 | 50.5 | -5.047
1488.7 | 50.5 | -5.047
1488.8 | 50.5 | -5.047
1488.9 | 50.5 | -5.047
1489 | 50.5 | -5.047
1489.1 | 50.5 | -5.047
1489.2 | 50.5 | -5.047
1489.3 | 50.5 | -5.047
1489.4 | 50.5 | -5.047
1489.5 | 50.5 | -5.047
1489.6 | 50.5 | -5.047
1489.7 | 50.5 | -5.047
1489.8 | 50.5 | -5.047
1489.9 | 50.5 | -5.047
1490 | 50.5 | -5.047
1490.1 | 50.5 | -5.047
1490.2 | 50.5 | -5.047
1490.3 | 50.5 | -5.047
1490.4 | 50.5 | -5.048
1490.5 | 50.5 | -5.048
1490.6 | 50.5 | -5.048
1490.7 | 50.5 | -5.048
1490.8 | 50.5 | -5.048
1490.9 | 50.5 | -5.048
1491 | 50.5 | -5.048
1491.1 | 50.5 | -5.048
1491.2 | 50.5 | -5.048
1491.3 | 50.5 | -5.048
1491.4 | 50.5 | -5.048
1491.5 | 50.5 | -5.048
1491.6 | 50.5 | -5.048
1491.7 | 50.5 | -5.048
1491.8 | 50.5 | -5.048
1491.9 | 50.5 | -5.048
1492 | 50.5 | -5.048
1492.1 | 50.5 | -5.048
1492.2 | 50.5 | -5.048
1492.3 | 50.5 | -5.048
1492.4 | 50.5 | -5.048
1492.5 | 50.5 | -5.048
1492.6 | 50.5 | -5.048
1492.7 | 50.5 | -5.048
1492.8 | 50.5 | -5.048
1492.9 | 50.5 | -5.048
1493 | 50.5 | -5.048
1493.1 | 50.5 | -5.048
1493.2 | 50.5 | -5.048
1493.3 | 50.5 | -5.048
1493.4 | 50.5 | -5.048
1493.5 | 50.5 | -5.048
1493.6 | 50.5 | -5.048
1493.7 | 50.5 | -5.048
1493.8 | 50.5 | -5.048
1493.9 | 50.5 | -5.048
1494 | 50.5 | -5.048
1494.1 | 50.5 | -5.048
1494.2 | 50.5 | -5.048
1494.3 | 50.5 | -5.048
1494.4 | 50.5 | -5.048
1494.5 | 50.5 | -5.048
1494.6 | 50.5 | -5.048
1494.7 | 50.5 | -5.048
1494.8 | 50.5 | -5.048
1494.9 | 50.5 | -5.048
1495 | 50.5 | -5.047
1495.1 | 50.5 | -5.047
1495.2 | 50.5 | -5.047
1495.3 | 50.5 | -5.047
1495.4 | 50.5 | -5.047
1495.5 | 50.5 | -5.047
1495.6 | 50.5 | -5.047
1495.7 | 50.5 | -5.047
1495.8 | 50.5 | -5.047
1495.9 | 50.5 | -5.047
1496 | 50.5 | -5.047
1496.1 | 50.5 | -5.047
1496.2 | 50.5 | -5.047
1496.3 | 50.5 | -5.047
1496.4 | 50.5 | -5.048
1496.5 | 50.5 | -5.048
1496.6 | 50.5 | -5.048
1496.7 | 50.5 | -5.048
1496.8 | 50.5 | -5.048
1496.9 | 50.5 | -5.048
1497 | 50.5 | -5.048
1497.1 | 50.5 | -5.048
1497.2 | 50.5 | -5.048
1497.3 | 50.5 | -5.048
1497.4 | 50.5 | -5.048
1497.5 | 50.5 | -5.048
1497.6 | 50.5 | -5.048
1497.7 | 50.5 | -5.048
1497.8 | 50.5 | -5.048
1497.9 | 50.5 | -5.048
1498 | 50.5 | -5.048
1498.1 | 50.5 | -5.048
1498.2 | 50.5 | -5.048
1498.3 | 50.5 | -5.048
1498.4 | 50.5 | -5.048
1498.5 | 50.5 | -5.048
1498.6 | 50.5 | -5.048
1498.7 | 50.5 | -5.048
1498.8 | 50.5 | -5.048
1498.9 | 50.5 | -5.048
1499 | 50.5 | -5.048
1499.1 | 50.5 | -5.048
1499.2 | 50.5 | -5.048
1499.3 | 50.5 | -5.048
1499.4 | 50.5 | -5.048
1499.5 | 50.5 | -5.048
1499.6 | 50.5 | -5.048
1499.7 | 50.5 | -5.048
1499.8 | 50.5 | -5.048
1499.9 | 50.5 | -5.048
1500 | 50.5 | -5.048
1500.1 | 50.5 | -5.048
1500.2 | 50.5 | -5.048
1500.3 | 50.5 | -5.048
1500.4 | 50.5 | -5.048
1500.5 | 50.5 | -5.048
1500.6 | 50.5 | -5.048
1500.7 | 50.5 | -5.048
1500.8 | 50.5 | -5.048
1500.9 | 50.5 | -5.048
1501 | 50.5 | -5.048
1501.1 | 50.5 | -5.048
1501.2 | 50.5 | -5.048
1501.3 | 50.5 | -5.048
1501.4 | 50.5 | -5.048
1501.5 | 50.5 | -5.048
1501.6 | 50.5 | -5.048
1501.7 | 50.5 | -5.048
1501.8 | 50.5 | -5.048
1501.9 | 50.5 | -5.048
1502 | 50.5 | -5.048
1502.1 | 50.5 | -5.048
1502.2 | 50.5 | -5.048
1502.3 | 50.5 | -5.048
1502.4 | 50.5 | -5.048
1502.5 | 50.5 | -5.048
1502.6 | 50.5 | -5.048
1502.7 | 50.5 | -5.048
1502.8 | 50.5 | -5.048
1502.9 | 50.5 | -5.048
1503 | 50.5 | -5.048
1503.1 | 50.5 | -5.048
1503.2 | 50.5 | -5.048
1503.3 | 50.5 | -5.048
1503.4 | 50.5 | -5.048
1503.5 | 50.5 | -5.048
1503.6 | 50.5 | -5.048
1503.7 | 50.5 | -5.048
1503.8 | 50.5 | -5.048
1503.9 | 50.5 | -5.048
1504 | 50.5 | -5.048
1504.1 | 50.5 | -5.048
1504.2 | 50.5 | -5.048
1504.3 | 50.5 | -5.048
1504.4 | 50.5 | -5.048
1504.5 | 50.5 | -5.048
1504.6 | 50.5 | -5.048
1504.7 | 50.5 | -5.048
1504.8 | 50.5 | -5.048
1504.9 | 50.5 | -5.048
1505 | 50.5 | -5.048
1505.1 | 50.5 | -5.048
1505.2 | 50.5 | -5.048
1505.3 | 50.5 | -5.048
1505.4 | 50.5 | -5.048
1505.5 | 50.5 | -5.048
1505.6 | 50.5 | -5.048
1505.7 | 50.5 | -5.048
1505.8 | 50.5 | -5.048
1505.9 | 50.5 | -5.048
1506 | 50.5 | -5.048
1506.1 | 50.5 | -5.048
1506.2 | 50.5 | -5.048
1506.3 | 50.5 | -5.048
1506.4 | 50.5 | -5.048
1506.5 | 50.5 | -5.048
1506.6 | 50.5 | -5.048
1506.7 | 50.5 | -5.048
1506.8 | 50.5 | -5.048
1506.9 | 50.5 | -5.048
1507 | 50.5 | -5.048
1507.1 | 50.5 | -5.048
1507.2 | 50.5 | -5.048
1507.3 | 50.5 | -5.048
1507.4 | 50.5 | -5.048
1507.5 | 50.5 | -5.048
1507.6 | 50.5 | -5.048
1507.7 | 50.5 | -5.048
1507.8 | 50.5 | -5.048
1507.9 | 50.5 | -5.048
1508 | 50.5 | -5.048
1508.1 | 50.5 | -5.048
1508.2 | 50.5 | -5.048
1508.3 | 50.5 | -5.048
1508.4 | 50.5 | -5.048
1508.5 | 50.5 | -5.048
1508.6 | 50.5 | -5.048
1508.7 | 50.5 | -5.048
1508.8 | 50.5 | -5.048
1508.9 | 50.5 | -5.048
1509 | 50.5 | -5.048
1509.1 | 50.5 | -5.048
1509.2 | 50.5 | -5.049
1509.3 | 50.5 | -5.048
1509.4 | 50.5 | -5.048
1509.5 | 50.5 | -5.048
1509.6 | 50.5 | -5.048
1509.7 | 50.5 | -5.048
1509.8 | 50.5 | -5.048
1509.9 | 50.5 | -5.048
1510 | 50.5 | -5.048
1510.1 | 50.5 | -5.048
1510.2 | 50.5 | -5.048
1510.3 | 50.5 | -5.048
1510.4 | 50.5 | -5.048
1510.5 | 50.5 | -5.048
1510.6 | 50.5 | -5.048
1510.7 | 50.5 | -5.048
1510.8 | 50.5 | -5.048
1510.9 | 50.5 | -5.048
1511 | 50.5 | -5.048
1511.1 | 50.5 | -5.048
1511.2 | 50.5 | -5.048
1511.3 | 50.5 | -5.048
1511.4 | 50.5 | -5.048
1511.5 | 50.5 | -5.048
1511.6 | 50.5 | -5.048
1511.7 | 50.5 | -5.047
1511.8 | 50.5 | -5.047
1511.9 | 50.5 | -5.047
1512 | 50.5 | -5.047
1512.1 | 50.5 | -5.047
1512.2 | 50.5 | -5.047
1512.3 | 50.5 | -5.047
1512.4 | 50.5 | -5.047
1512.5 | 50.5 | -5.047
1512.6 | 50.5 | -5.047
1512.7 | 50.5 | -5.047
1512.8 | 50.5 | -5.047
1512.9 | 50.5 | -5.047
1513 | 50.5 | -5.047
1513.1 | 50.5 | -5.047
1513.2 | 50.5 | -5.047
1513.3 | 50.5 | -5.047
1513.4 | 50.5 | -5.047
1513.5 | 50.5 | -5.047
1513.6 | 50.5 | -5.047
1513.7 | 50.5 | -5.047
1513.8 | 50.5 | -5.047
1513.9 | 50.5 | -5.047
1514 | 50.5 | -5.048
1514.1 | 50.5 | -5.048
1514.2 | 50.5 | -5.048
1514.3 | 50.5 | -5.048
1514.4 | 50.5 | -5.048
1514.5 | 50.5 | -5.048
1514.6 | 50.5 | -5.048
1514.7 | 50.5 | -5.048
1514.8 | 50.5 | -5.048
1514.9 | 50.5 | -5.048
1515 | 50.5 | -5.048
1515.1 | 50.5 | -5.048
1515.2 | 50.5 | -5.048
1515.3 | 50.5 | -5.048
1515.4 | 50.5 | -5.048
1515.5 | 50.5 | -5.048
1515.6 | 50.5 | -5.048
1515.7 | 50.5 | -5.048
1515.8 | 50.5 | -5.048
1515.9 | 50.5 | -5.048
1516 | 50.5 | -5.048
1516.1 | 50.5 | -5.048
1516.2 | 50.5 | -5.048
1516.3 | 50.5 | -5.048
1516.4 | 50.5 | -5.048
1516.5 | 50.5 | -5.048
1516.6 | 50.5 | -5.048
1516.7 | 50.5 | -5.048
1516.8 | 50.5 | -5.048
1516.9 | 50.5 | -5.048
1517 | 50.5 | -5.048
1517.1 | 50.5 | -5.048
1517.2 | 50.5 | -5.048
1517.3 | 50.5 | -5.048
1517.4 | 50.5 | -5.048
1517.5 | 50.5 | -5.048
1517.6 | 50.5 | -5.048
1517.7 | 50.5 | -5.048
1517.8 | 50.5 | -5.048
1517.9 | 50.5 | -5.048
1518 | 50.5 | -5.048
1518.1 | 50.5 | -5.048
1518.2 | 50.5 | -5.048
1518.3 | 50.5 | -5.048
1518.4 | 50.5 | -5.048
1518.5 | 50.5 | -5.048
1518.6 | 50.5 | -5.047
1518.7 | 50.5 | -5.047
1518.8 | 50.5 | -5.047
1518.9 | 50.5 | -5.047
1519 | 50.5 | -5.047
1519.1 | 50.5 | -5.047
1519.2 | 50.5 | -5.047
1519.3 | 50.5 | -5.047
1519.4 | 50.5 | -5.047
1519.5 | 50.5 | -5.047
1519.6 | 50.5 | -5.047
1519.7 | 50.5 | -5.047
1519.8 | 50.5 | -5.047
1519.9 | 50.5 | -5.047
1520 | 50.5 | -5.047
1520.1 | 50.5 | -5.047
1520.2 | 50.5 | -5.047
1520.3 | 50.5 | -5.047
1520.4 | 50.5 | -5.047
1520.5 | 50.5 | -5.047
1520.6 | 50.5 | -5.047
1520.7 | 50.5 | -5.047
1520.8 | 50.5 | -5.048
1520.9 | 50.5 | -5.048
1521 | 50.5 | -5.048
1521.1 | 50.5 | -5.048
1521.2 | 50.5 | -5.048
1521.3 | 50.5 | -5.048
1521.4 | 50.5 | -5.048
1521.5 | 50.5 | -5.048
1521.6 | 50.5 | -5.048
1521.7 | 50.5 | -5.048
1521.8 | 50.5 | -5.048
1521.9 | 50.5 | -5.048
1522 | 50.5 | -5.048
1522.1 | 50.5 | -5.048
1522.2 | 50.5 | -5.048
1522.3 | 50.5 | -5.048
1522.4 | 50.5 | -5.048
1522.5 | 50.5 | -5.048
1522.6 | 50.5 | -5.048
1522.7 | 50.5 | -5.048
1522.8 | 50.5 | -5.048
1522.9 | 50.5 | -5.048
1523 | 50.5 | -5.048
1523.1 | 50.5 | -5.048
1523.2 | 50.5 | -5.048
1523.3 | 50.5 | -5.048
1523.4 | 50.5 | -5.048
1523.5 | 50.5 | -5.048
1523.6 | 50.5 | -5.048
1523.7 | 50.5 | -5.048
1523.8 | 50.5 | -5.048
1523.9 | 50.5 | -5.048
1524 | 50.5 | -5.048
1524.1 | 50.5 | -5.048
1524.2 | 50.5 | -5.048
1524.3 | 50.5 | -5.048
1524.4 | 50.5 | -5.048
1524.5 | 50.5 | -5.048
1524.6 | 50.5 | -5.048
1524.7 | 50.5 | -5.048
1524.8 | 50.5 | -5.048
1524.9 | 50.5 | -5.048
1525 | 50.5 | -5.048
1525.1 | 50.5 | -5.048
1525.2 | 50.5 | -5.048
1525.3 | 50.5 | -5.048
1525.4 | 50.5 | -5.048
1525.5 | 50.5 | -5.048
1525.6 | 50.5 | -5.048
1525.7 | 50.5 | -5.047
1525.8 | 50.5 | -5.047
1525.9 | 50.5 | -5.047
1526 | 50.5 | -5.047
1526.1 | 50.5 | -5.047
1526.2 | 50.5 | -5.047
1526.3 | 50.5 | -5.047
1526.4 | 50.5 | -5.047
1526.5 | 50.5 | -5.047
1526.6 | 50.5 | -5.047
1526.7 | 50.5 | -5.047
1526.8 | 50.5 | -5.047
1526.9 | 50.5 | -5.047
1527 | 50.5 | -5.047
1527.1 | 50.5 | -5.047
1527.2 | 50.5 | -5.047
1527.3 | 50.5 | -5.047
1527.4 | 50.5 | -5.047
1527.5 | 50.5 | -5.047
1527.6 | 50.5 | -5.047
1527.7 | 50.5 | -5.047
1527.8 | 50.5 | -5.047
1527.9 | 50.5 | -5.047
1528 | 50.5 | -5.048
1528.1 | 50.5 | -5.048
1528.2 | 50.5 | -5.048
1528.3 | 50.5 | -5.048
1528.4 | 50.5 | -5.048
1528.5 | 50.5 | -5.048
1528.6 | 50.5 | -5.048
1528.7 | 50.5 | -5.048
1528.8 | 50.5 | -5.048
1528.9 | 50.5 | -5.048
1529 | 50.5 | -5.048
1529.1 | 50.5 | -5.048
1529.2 | 50.5 | -5.048
1529.3 | 50.5 | -5.048
1529.4 | 50.5 | -5.047
1529.5 | 50.5 | -5.047
1529.6 | 50.5 | -5.047
1529.7 | 50.5 | -5.047
1529.8 | 50.5 | -5.047
1529.9 | 50.5 | -5.047
1530 | 50.5 | -5.047
1530.1 | 50.5 | -5.047
1530.2 | 50.5 | -5.047
1530.3 | 50.5 | -5.047
1530.4 | 50.5 | -5.048
1530.5 | 50.5 | -5.048
1530.6 | 50.5 | -5.048
1530.7 | 50.5 | -5.048
1530.8 | 50.5 | -5.048
1530.9 | 50.5 | -5.048
1531 | 50.5 | -5.048
1531.1 | 50.5 | -5.048
1531.2 | 50.5 | -5.048
1531.3 | 50.5 | -5.048
1531.4 | 50.5 | -5.048
1531.5 | 50.5 | -5.047
1531.6 | 50.5 | -5.047
1531.7 | 50.5 | -5.047
1531.8 | 50.5 | -5.047
1531.9 | 50.5 | -5.047
1532 | 50.5 | -5.047
1532.1 | 50.5 | -5.047
1532.2 | 50.5 | -5.047
1532.3 | 50.5 | -5.047
1532.4 | 50.5 | -5.047
1532.5 | 50.5 | -5.047
1532.6 | 50.5 | -5.048
1532.7 | 50.5 | -5.048
1532.8 | 50.5 | -5.048
1532.9 | 50.5 | -5.048
1533 | 50.5 | -5.048
1533.1 | 50.5 | -5.048
1533.2 | 50.5 | -5.048
1533.3 | 50.5 | -5.048
1533.4 | 50.5 | -5.048
1533.5 | 50.5 | -5.048
1533.6 | 50.5 | -5.048
1533.7 | 50.5 | -5.048
1533.8 | 50.5 | -5.048
1533.9 | 50.5 | -5.048
1534 | 50.5 | -5.048
1534.1 | 50.5 | -5.048
1534.2 | 50.5 | -5.048
1534.3 | 50.5 | -5.048
1534.4 | 50.5 | -5.048
1534.5 | 50.5 | -5.048
1534.6 | 50.5 | -5.048
1534.7 | 50.5 | -5.048
1534.8 | 50.5 | -5.048
1534.9 | 50.5 | -5.048
1535 | 50.5 | -5.047
1535.1 | 50.5 | -5.047
1535.2 | 50.5 | -5.047
1535.3 | 50.5 | -5.047
1535.4 | 50.5 | -5.047
1535.5 | 50.5 | -5.047
1535.6 | 50.5 | -5.047
1535.7 | 50.5 | -5.047
1535.8 | 50.5 | -5.047
1535.9 | 50.5 | -5.047
1536 | 50.5 | -5.047
1536.1 | 50.5 | -5.047
1536.2 | 50.5 | -5.047
1536.3 | 50.5 | -5.047
1536.4 | 50.5 | -5.047
1536.5 | 50.5 | -5.047
1536.6 | 50.5 | -5.047
1536.7 | 50.5 | -5.047
1536.8 | 50.5 | -5.047
1536.9 | 50.5 | -5.047
1537 | 50.5 | -5.047
1537.1 | 50.5 | -5.047
1537.2 | 50.5 | -5.047
1537.3 | 50.5 | -5.047
1537.4 | 50.5 | -5.047
1537.5 | 50.5 | -5.047
1537.6 | 50.5 | -5.047
1537.7 | 50.5 | -5.047
1537.8 | 50.5 | -5.047
1537.9 | 50.5 | -5.047
1538 | 50.5 | -5.047
1538.1 | 50.5 | -5.047
1538.2 | 50.5 | -5.047
1538.3 | 50.5 | -5.047
1538.4 | 50.5 | -5.048
1538.5 | 50.5 | -5.048
1538.6 | 50.5 | -5.048
1538.7 | 50.5 | -5.048
1538.8 | 50.5 | -5.048
1538.9 | 50.5 | -5.048
1539 | 50.5 | -5.048
1539.1 | 50.5 | -5.048
1539.2 | 50.5 | -5.048
1539.3 | 50.5 | -5.048
1539.4 | 50.5 | -5.048
1539.5 | 50.5 | -5.048
1539.6 | 50.5 | -5.048
1539.7 | 50.5 | -5.048
1539.8 | 50.5 | -5.048
1539.9 | 50.5 | -5.048
1540 | 50.5 | -5.048
1540.1 | 50.5 | -5.048
1540.2 | 50.5 | -5.048
1540.3 | 50.5 | -5.048
1540.4 | 50.5 | -5.048
1540.5 | 50.5 | -5.048
1540.6 | 50.5 | -5.048
1540.7 | 50.5 | -5.048
1540.8 | 50.5 | -5.048
1540.9 | 50.5 | -5.048
1541 | 50.5 | -5.048
1541.1 | 50.5 | -5.048
1541.2 | 50.5 | -5.048
1541.3 | 50.5 | -5.048
1541.4 | 50.5 | -5.048
1541.5 | 50.5 | -5.048
1541.6 | 50.5 | -5.048
1541.7 | 50.5 | -5.048
1541.8 | 50.5 | -5.048
1541.9 | 50.5 | -5.048
1542 | 50.5 | -5.048
1542.1 | 50.5 | -5.047
1542.2 | 50.5 | -5.047
1542.3 | 50.5 | -5.047
1542.4 | 50.5 | -5.047
1542.5 | 50.5 | -5.047
1542.6 | 50.5 | -5.047
1542.7 | 50.5 | -5.047
1542.8 | 50.5 | -5.047
1542.9 | 50.5 | -5.047
1543 | 50.5 | -5.047
1543.1 | 50.5 | -5.047
1543.2 | 50.5 | -5.047
1543.3 | 50.5 | -5.047
1543.4 | 50.5 | -5.047
1543.5 | 50.5 | -5.047
1543.6 | 50.5 | -5.047
1543.7 | 50.5 | -5.047
1543.8 | 50.5 | -5.047
1543.9 | 50.5 | -5.047
1544 | 50.5 | -5.047
1544.1 | 50.5 | -5.047
1544.2 | 50.5 | -5.047
1544.3 | 50.5 | -5.048
1544.4 | 50.5 | -5.048
1544.5 | 50.5 | -5.048
1544.6 | 50.5 | -5.048
1544.7 | 50.5 | -5.048
1544.8 | 50.5 | -5.048
1544.9 | 50.5 | -5.048
1545 | 50.5 | -5.048
1545.1 | 50.5 | -5.048
1545.2 | 50.5 | -5.048
1545.3 | 50.5 | -5.048
1545.4 | 50.5 | -5.048
1545.5 | 50.5 | -5.048
1545.6 | 50.5 | -5.048
1545.7 | 50.5 | -5.048
1545.8 | 50.5 | -5.048
1545.9 | 50.5 | -5.048
1546 | 50.5 | -5.048
1546.1 | 50.5 | -5.048
1546.2 | 50.5 | -5.048
1546.3 | 50.5 | -5.048
1546.4 | 50.5 | -5.048
1546.5 | 50.5 | -5.048
1546.6 | 50.5 | -5.048
1546.7 | 50.5 | -5.048
1546.8 | 50.5 | -5.048
1546.9 | 50.5 | -5.048
1547 | 50.5 | -5.048
1547.1 | 50.5 | -5.048
1547.2 | 50.5 | -5.048
1547.3 | 50.5 | -5.048
1547.4 | 50.5 | -5.048
1547.5 | 50.5 | -5.048
1547.6 | 50.5 | -5.048
1547.7 | 50.5 | -5.047
1547.8 | 50.5 | -5.047
1547.9 | 50.5 | -5.047
1548 | 50.5 | -5.047
1548.1 | 50.5 | -5.047
1548.2 | 50.5 | -5.047
1548.3 | 50.5 | -5.047
1548.4 | 50.5 | -5.047
1548.5 | 50.5 | -5.047
1548.6 | 50.5 | -5.047
1548.7 | 50.5 | -5.047
1548.8 | 50.5 | -5.047
1548.9 | 50.5 | -5.047
1549 | 50.5 | -5.047
1549.1 | 50.5 | -5.047
1549.2 | 50.5 | -5.047
1549.3 | 50.5 | -5.047
1549.4 | 50.5 | -5.047
1549.5 | 50.5 | -5.047
1549.6 | 50.5 | -5.047
1549.7 | 50.5 | -5.047
1549.8 | 50.5 | -5.047
1549.9 | 50.5 | -5.047
1550 | 50.5 | -5.048
1550.1 | 50.5 | -5.048
1550.2 | 50.5 | -5.048
1550.3 | 50.5 | -5.048
1550.4 | 50.5 | -5.048
1550.5 | 50.5 | -5.048
1550.6 | 50.5 | -5.048
1550.7 | 50.5 | -5.048
1550.8 | 50.5 | -5.048
1550.9 | 50.5 | -5.048
1551 | 50.5 | -5.048
1551.1 | 50.5 | -5.048
1551.2 | 50.5 | -5.048
1551.3 | 50.5 | -5.048
1551.4 | 50.5 | -5.048
1551.5 | 50.5 | -5.048
1551.6 | 50.5 | -5.048
1551.7 | 50.5 | -5.048
1551.8 | 50.5 | -5.048
1551.9 | 50.5 | -5.048
1552 | 50.5 | -5.048
1552.1 | 50.5 | -5.048
1552.2 | 50.5 | -5.048
1552.3 | 50.5 | -5.048
1552.4 | 50.5 | -5.048
1552.5 | 50.5 | -5.048
1552.6 | 50.5 | -5.048
1552.7 | 50.5 | -5.048
1552.8 | 50.5 | -5.048
1552.9 | 50.5 | -5.048
1553 | 50.5 | -5.048
1553.1 | 50.5 | -5.048
1553.2 | 50.5 | -5.048
1553.3 | 50.5 | -5.048
1553.4 | 50.5 | -5.048
1553.5 | 50.5 | -5.048
1553.6 | 50.5 | -5.048
1553.7 | 50.5 | -5.048
1553.8 | 50.5 | -5.048
1553.9 | 50.5 | -5.048
1554 | 50.5 | -5.048
1554.1 | 50.5 | -5.048
1554.2 | 50.5 | -5.048
1554.3 | 50.5 | -5.048
1554.4 | 50.5 | -5.048
1554.5 | 50.5 | -5.048
1554.6 | 50.5 | -5.048
1554.7 | 50.5 | -5.048
1554.8 | 50.5 | -5.048
1554.9 | 50.5 | -5.047
1555 | 50.5 | -5.047
1555.1 | 50.5 | -5.047
1555.2 | 50.5 | -5.047
1555.3 | 50.5 | -5.047
1555.4 | 50.5 | -5.047
1555.5 | 50.5 | -5.047
1555.6 | 50.5 | -5.047
1555.7 | 50.5 | -5.047
1555.8 | 50.5 | -5.047
1555.9 | 50.5 | -5.047
1556 | 50.5 | -5.048
1556.1 | 50.5 | -5.048
1556.2 | 50.5 | -5.048
1556.3 | 50.5 | -5.048
1556.4 | 50.5 | -5.048
1556.5 | 50.5 | -5.048
1556.6 | 50.5 | -5.048
1556.7 | 50.5 | -5.048
1556.8 | 50.5 | -5.048
1556.9 | 50.5 | -5.048
1557 | 50.5 | -5.048
1557.1 | 50.5 | -5.048
1557.2 | 50.5 | -5.048
1557.3 | 50.5 | -5.048
1557.4 | 50.5 | -5.048
1557.5 | 50.5 | -5.048
1557.6 | 50.5 | -5.048
1557.7 | 50.5 | -5.048
1557.8 | 50.5 | -5.048
1557.9 | 50.5 | -5.048
1558 | 50.5 | -5.048
1558.1 | 50.5 | -5.048
1558.2 | 50.5 | -5.048
1558.3 | 50.5 | -5.048
1558.4 | 50.5 | -5.048
1558.5 | 50.5 | -5.048
1558.6 | 50.5 | -5.048
1558.7 | 50.5 | -5.048
1558.8 | 50.5 | -5.048
1558.9 | 50.5 | -5.048
1559 | 50.5 | -5.048
1559.1 | 50.5 | -5.048
1559.2 | 50.5 | -5.048
1559.3 | 50.5 | -5.048
1559.4 | 50.5 | -5.048
1559.5 | 50.5 | -5.048
1559.6 | 50.5 | -5.048
1559.7 | 50.5 | -5.048
1559.8 | 50.5 | -5.048
1559.9 | 50.5 | -5.048
1560 | 50.5 | -5.048
1560.1 | 50.5 | -5.048
1560.2 | 50.5 | -5.048
1560.3 | 50.5 | -5.048
1560.4 | 50.5 | -5.048
1560.5 | 50.5 | -5.048
1560.6 | 50.5 | -5.048
1560.7 | 50.5 | -5.048
1560.8 | 50.5 | -5.048
1560.9 | 50.5 | -5.048
1561 | 50.5 | -5.048
1561.1 | 50.5 | -5.048
1561.2 | 50.5 | -5.048
1561.3 | 50.5 | -5.048
1561.4 | 50.5 | -5.048
1561.5 | 50.5 | -5.048
1561.6 | 50.5 | -5.048
1561.7 | 50.5 | -5.048
1561.8 | 50.5 | -5.048
1561.9 | 50.5 | -5.048
1562 | 50.5 | -5.048
1562.1 | 50.5 | -5.048
1562.2 | 50.5 | -5.048
1562.3 | 50.5 | -5.048
1562.4 | 50.5 | -5.048
1562.5 | 50.5 | -5.048
1562.6 | 50.5 | -5.048
1562.7 | 50.5 | -5.048
1562.8 | 50.5 | -5.048
1562.9 | 50.5 | -5.048
1563 | 50.5 | -5.048
1563.1 | 50.5 | -5.048
1563.2 | 50.5 | -5.048
1563.3 | 50.5 | -5.048
1563.4 | 50.5 | -5.048
1563.5 | 50.5 | -5.048
1563.6 | 50.5 | -5.048
1563.7 | 50.5 | -5.048
1563.8 | 50.5 | -5.048
1563.9 | 50.5 | -5.048
1564 | 50.5 | -5.048
1564.1 | 50.5 | -5.048
1564.2 | 50.5 | -5.048
1564.3 | 50.5 | -5.048
1564.4 | 50.5 | -5.048
1564.5 | 50.5 | -5.048
1564.6 | 50.5 | -5.048
1564.7 | 50.5 | -5.048
1564.8 | 50.5 | -5.048
1564.9 | 50.5 | -5.048
1565 | 50.5 | -5.048
1565.1 | 50.5 | -5.048
1565.2 | 50.5 | -5.048
1565.3 | 50.5 | -5.048
1565.4 | 50.5 | -5.048
1565.5 | 50.5 | -5.048
1565.6 | 50.5 | -5.048
1565.7 | 50.5 | -5.048
1565.8 | 50.5 | -5.048
1565.9 | 50.5 | -5.048
1566 | 50.5 | -5.048
1566.1 | 50.5 | -5.048
1566.2 | 50.5 | -5.048
1566.3 | 50.5 | -5.048
1566.4 | 50.5 | -5.048
1566.5 | 50.5 | -5.048
1566.6 | 50.5 | -5.048
1566.7 | 50.5 | -5.048
1566.8 | 50.5 | -5.048
1566.9 | 50.5 | -5.048
1567 | 50.5 | -5.048
1567.1 | 50.5 | -5.048
1567.2 | 50.5 | -5.048
1567.3 | 50.5 | -5.048
1567.4 | 50.5 | -5.048
1567.5 | 50.5 | -5.048
1567.6 | 50.5 | -5.048
1567.7 | 50.5 | -5.048
1567.8 | 50.5 | -5.048
1567.9 | 50.5 | -5.048
1568 | 50.5 | -5.048
1568.1 | 50.5 | -5.048
1568.2 | 50.5 | -5.048
1568.3 | 50.5 | -5.048
1568.4 | 50.5 | -5.048
1568.5 | 50.5 | -5.048
1568.6 | 50.5 | -5.048
1568.7 | 50.5 | -5.047
1568.8 | 50.5 | -5.047
1568.9 | 50.5 | -5.047
1569 | 50.5 | -5.047
1569.1 | 50.5 | -5.047
1569.2 | 50.5 | -5.047
1569.3 | 50.5 | -5.047
1569.4 | 50.5 | -5.047
1569.5 | 50.5 | -5.047
1569.6 | 50.5 | -5.047
1569.7 | 50.5 | -5.047
1569.8 | 50.5 | -5.047
1569.9 | 50.5 | -5.047
1570 | 50.5 | -5.047
1570.1 | 50.5 | -5.047
1570.2 | 50.5 | -5.047
1570.3 | 50.5 | -5.047
1570.4 | 50.5 | -5.047
1570.5 | 50.5 | -5.047
1570.6 | 50.5 | -5.047
1570.7 | 50.5 | -5.047
1570.8 | 50.5 | -5.047
1570.9 | 50.5 | -5.047
1571 | 50.5 | -5.047
1571.1 | 50.5 | -5.047
1571.2 | 50.5 | -5.048
1571.3 | 50.5 | -5.048
1571.4 | 50.5 | -5.048
1571.5 | 50.5 | -5.048
1571.6 | 50.5 | -5.048
1571.7 | 50.5 | -5.048
1571.8 | 50.5 | -5.048
1571.9 | 50.5 | -5.048
1572 | 50.5 | -5.048
1572.1 | 50.5 | -5.048
1572.2 | 50.5 | -5.048
1572.3 | 50.5 | -5.048
1572.4 | 50.5 | -5.048
1572.5 | 50.5 | -5.048
1572.6 | 50.5 | -5.048
1572.7 | 50.5 | -5.048
1572.8 | 50.5 | -5.048
1572.9 | 50.5 | -5.048
1573 | 50.5 | -5.048
1573.1 | 50.5 | -5.048
1573.2 | 50.5 | -5.048
1573.3 | 50.5 | -5.048
1573.4 | 50.5 | -5.048
1573.5 | 50.5 | -5.048
1573.6 | 50.5 | -5.048
1573.7 | 50.5 | -5.048
1573.8 | 50.5 | -5.048
1573.9 | 50.5 | -5.048
1574 | 50.5 | -5.048
1574.1 | 50.5 | -5.048
1574.2 | 50.5 | -5.048
1574.3 | 50.5 | -5.048
1574.4 | 50.5 | -5.048
1574.5 | 50.5 | -5.048
1574.6 | 50.5 | -5.048
1574.7 | 50.5 | -5.048
1574.8 | 50.5 | -5.048
1574.9 | 50.5 | -5.048
1575 | 50.5 | -5.048
1575.1 | 50.5 | -5.048
1575.2 | 50.5 | -5.048
1575.3 | 50.5 | -5.048
1575.4 | 50.5 | -5.048
1575.5 | 50.5 | -5.048
1575.6 | 50.5 | -5.048
1575.7 | 50.5 | -5.048
1575.8 | 50.5 | -5.048
1575.9 | 50.5 | -5.048
1576 | 50.5 | -5.048
1576.1 | 50.5 | -5.048
1576.2 | 50.5 | -5.048
1576.3 | 50.5 | -5.048
1576.4 | 50.5 | -5.048
1576.5 | 50.5 | -5.048
1576.6 | 50.5 | -5.048
1576.7 | 50.5 | -5.048
1576.8 | 50.5 | -5.048
1576.9 | 50.5 | -5.048
1577 | 50.5 | -5.048
1577.1 | 50.5 | -5.048
1577.2 | 50.5 | -5.048
1577.3 | 50.5 | -5.048
1577.4 | 50.5 | -5.048
1577.5 | 50.5 | -5.048
1577.6 | 50.5 | -5.048
1577.7 | 50.5 | -5.048
1577.8 | 50.5 | -5.048
1577.9 | 50.5 | -5.048
1578 | 50.5 | -5.048
1578.1 | 50.5 | -5.048
1578.2 | 50.5 | -5.048
1578.3 | 50.5 | -5.048
1578.4 | 50.5 | -5.048
1578.5 | 50.5 | -5.048
1578.6 | 50.5 | -5.048
1578.7 | 50.5 | -5.048
1578.8 | 50.5 | -5.048
1578.9 | 50.5 | -5.048
1579 | 50.5 | -5.048
1579.1 | 50.5 | -5.048
1579.2 | 50.5 | -5.048
1579.3 | 50.5 | -5.048
1579.4 | 50.5 | -5.048
1579.5 | 50.5 | -5.048
1579.6 | 50.5 | -5.048
1579.7 | 50.5 | -5.048
1579.8 | 50.5 | -5.048
1579.9 | 50.5 | -5.048
1580 | 50.5 | -5.048
1580.1 | 50.5 | -5.048
1580.2 | 50.5 | -5.048
1580.3 | 50.5 | -5.048
1580.4 | 50.5 | -5.048
1580.5 | 50.5 | -5.048
1580.6 | 50.5 | -5.048
1580.7 | 50.5 | -5.048
1580.8 | 50.5 | -5.048
1580.9 | 50.5 | -5.048
1581 | 50.5 | -5.048
1581.1 | 50.5 | -5.048
1581.2 | 50.5 | -5.048
1581.3 | 50.5 | -5.048
1581.4 | 50.5 | -5.048
1581.5 | 50.5 | -5.048
1581.6 | 50.5 | -5.048
1581.7 | 50.5 | -5.048
1581.8 | 50.5 | -5.048
1581.9 | 50.5 | -5.047
1582 | 50.5 | -5.047
1582.1 | 50.5 | -5.047
1582.2 | 50.5 | -5.047
1582.3 | 50.5 | -5.047
1582.4 | 50.5 | -5.047
1582.5 | 50.5 | -5.047
1582.6 | 50.5 | -5.047
1582.7 | 50.5 | -5.047
1582.8 | 50.5 | -5.047
1582.9 | 50.5 | -5.047
1583 | 50.5 | -5.047
1583.1 | 50.5 | -5.047
1583.2 | 50.5 | -5.047
1583.3 | 50.5 | -5.047
1583.4 | 50.5 | -5.047
1583.5 | 50.5 | -5.047
1583.6 | 50.5 | -5.047
1583.7 | 50.5 | -5.047
1583.8 | 50.5 | -5.047
1583.9 | 50.5 | -5.047
1584 | 50.5 | -5.048
1584.1 | 50.5 | -5.048
1584.2 | 50.5 | -5.048
1584.3 | 50.5 | -5.048
1584.4 | 50.5 | -5.048
1584.5 | 50.5 | -5.048
1584.6 | 50.5 | -5.048
1584.7 | 50.5 | -5.048
1584.8 | 50.5 | -5.048
1584.9 | 50.5 | -5.048
1585 | 50.5 | -5.048
1585.1 | 50.5 | -5.048
1585.2 | 50.5 | -5.048
1585.3 | 50.5 | -5.048
1585.4 | 50.5 | -5.048
1585.5 | 50.5 | -5.048
1585.6 | 50.5 | -5.048
1585.7 | 50.5 | -5.048
1585.8 | 50.5 | -5.048
1585.9 | 50.5 | -5.048
1586 | 50.5 | -5.048
1586.1 | 50.5 | -5.048
1586.2 | 50.5 | -5.048
1586.3 | 50.5 | -5.048
1586.4 | 50.5 | -5.048
1586.5 | 50.5 | -5.048
1586.6 | 50.5 | -5.048
1586.7 | 50.5 | -5.048
1586.8 | 50.5 | -5.048
1586.9 | 50.5 | -5.048
1587 | 50.5 | -5.048
1587.1 | 50.5 | -5.048
1587.2 | 50.5 | -5.048
1587.3 | 50.5 | -5.048
1587.4 | 50.5 | -5.048
1587.5 | 50.5 | -5.048
1587.6 | 50.5 | -5.048
1587.7 | 50.5 | -5.048
1587.8 | 50.5 | -5.048
1587.9 | 50.5 | -5.048
1588 | 50.5 | -5.048
1588.1 | 50.5 | -5.048
1588.2 | 50.5 | -5.048
1588.3 | 50.5 | -5.048
1588.4 | 50.5 | -5.048
1588.5 | 50.5 | -5.049
1588.6 | 50.5 | -5.049
1588.7 | 50.5 | -5.049
1588.8 | 50.5 | -5.048
1588.9 | 50.5 | -5.048
1589 | 50.5 | -5.048
1589.1 | 50.5 | -5.048
1589.2 | 50.5 | -5.048
1589.3 | 50.5 | -5.048
1589.4 | 50.5 | -5.048
1589.5 | 50.5 | -5.048
1589.6 | 50.5 | -5.048
1589.7 | 50.5 | -5.047
1589.8 | 50.5 | -5.047
1589.9 | 50.5 | -5.047
1590 | 50.5 | -5.048
1590.1 | 50.5 | -5.048
1590.2 | 50.5 | -5.048
1590.3 | 50.5 | -5.048
1590.4 | 50.5 | -5.048
1590.5 | 50.5 | -5.048
1590.6 | 50.5 | -5.048
1590.7 | 50.5 | -5.048
1590.8 | 50.5 | -5.048
1590.9 | 50.5 | -5.048
1591 | 50.5 | -5.048
1591.1 | 50.5 | -5.048
1591.2 | 50.5 | -5.048
1591.3 | 50.5 | -5.048
1591.4 | 50.5 | -5.048
1591.5 | 50.5 | -5.048
1591.6 | 50.5 | -5.048
1591.7 | 50.5 | -5.048
1591.8 | 50.5 | -5.048
1591.9 | 50.5 | -5.048
1592 | 50.5 | -5.048
1592.1 | 50.5 | -5.048
1592.2 | 50.5 | -5.048
1592.3 | 50.5 | -5.048
1592.4 | 50.5 | -5.048
1592.5 | 50.5 | -5.048
1592.6 | 50.5 | -5.048
1592.7 | 50.5 | -5.048
1592.8 | 50.5 | -5.048
1592.9 | 50.5 | -5.048
1593 | 50.5 | -5.048
1593.1 | 50.5 | -5.048
1593.2 | 50.5 | -5.048
1593.3 | 50.5 | -5.048
1593.4 | 50.5 | -5.048
1593.5 | 50.5 | -5.048
1593.6 | 50.5 | -5.048
1593.7 | 50.5 | -5.049
1593.8 | 50.5 | -5.049
1593.9 | 50.5 | -5.049
1594 | 50.5 | -5.049
1594.1 | 50.5 | -5.049
1594.2 | 50.5 | -5.049
1594.3 | 50.5 | -5.049
1594.4 | 50.5 | -5.049
1594.5 | 50.5 | -5.049
1594.6 | 50.5 | -5.049
1594.7 | 50.5 | -5.048
1594.8 | 50.5 | -5.048
1594.9 | 50.5 | -5.048
1595 | 50.5 | -5.048
1595.1 | 50.5 | -5.048
1595.2 | 50.5 | -5.048
1595.3 | 50.5 | -5.048
1595.4 | 50.5 | -5.048
1595.5 | 50.5 | -5.048
1595.6 | 50.5 | -5.048
1595.7 | 50.5 | -5.048
1595.8 | 50.5 | -5.048
1595.9 | 50.5 | -5.048
1596 | 50.5 | -5.048
1596.1 | 50.5 | -5.047
1596.2 | 50.5 | -5.047
1596.3 | 50.5 | -5.047
1596.4 | 50.5 | -5.047
1596.5 | 50.5 | -5.047
1596.6 | 50.5 | -5.047
1596.7 | 50.5 | -5.047
1596.8 | 50.5 | -5.047
1596.9 | 50.5 | -5.047
1597 | 50.5 | -5.047
1597.1 | 50.5 | -5.047
1597.2 | 50.5 | -5.047
1597.3 | 50.5 | -5.047
1597.4 | 50.5 | -5.047
1597.5 | 50.5 | -5.047
1597.6 | 50.5 | -5.047
1597.7 | 50.5 | -5.047
1597.8 | 50.5 | -5.047
1597.9 | 50.5 | -5.047
1598 | 50.5 | -5.047
1598.1 | 50.5 | -5.047
1598.2 | 50.5 | -5.047
1598.3 | 50.5 | -5.047
1598.4 | 50.5 | -5.047
1598.5 | 50.5 | -5.047
1598.6 | 50.5 | -5.047
1598.7 | 50.5 | -5.047
1598.8 | 50.5 | -5.047
1598.9 | 50.5 | -5.047
1599 | 50.5 | -5.047
1599.1 | 50.5 | -5.047
1599.2 | 50.5 | -5.047
1599.3 | 50.5 | -5.047
1599.4 | 50.5 | -5.047
1599.5 | 50.5 | -5.048
1599.6 | 50.5 | -5.048
1599.7 | 50.5 | -5.048
1599.8 | 50.5 | -5.048
1599.9 | 50.5 | -5.048
1600 | 50.5 | -5.048
1600.1 | 50.5 | -5.048
1600.2 | 50.5 | -5.048
1600.3 | 50.5 | -5.048
1600.4 | 50.5 | -5.048
1600.5 | 50.5 | -5.048
1600.6 | 50.5 | -5.048
1600.7 | 50.5 | -5.047
1600.8 | 50.5 | -5.047
1600.9 | 50.5 | -5.047
1601 | 50.5 | -5.047
1601.1 | 50.5 | -5.047
1601.2 | 50.5 | -5.047
1601.3 | 50.5 | -5.047
1601.4 | 50.5 | -5.047
1601.5 | 50.5 | -5.047
1601.6 | 50.5 | -5.048
1601.7 | 50.5 | -5.048
1601.8 | 50.5 | -5.048
1601.9 | 50.5 | -5.048
1602 | 50.5 | -5.048
1602.1 | 50.5 | -5.048
1602.2 | 50.5 | -5.048
1602.3 | 50.5 | -5.048
1602.4 | 50.5 | -5.048
1602.5 | 50.5 | -5.048
1602.6 | 50.5 | -5.048
1602.7 | 50.5 | -5.048
1602.8 | 50.5 | -5.048
1602.9 | 50.5 | -5.048
1603 | 50.5 | -5.048
1603.1 | 50.5 | -5.048
1603.2 | 50.5 | -5.048
1603.3 | 50.5 | -5.048
1603.4 | 50.5 | -5.048
1603.5 | 50.5 | -5.048
1603.6 | 50.5 | -5.048
1603.7 | 50.5 | -5.048
1603.8 | 50.5 | -5.048
1603.9 | 50.5 | -5.048
1604 | 50.5 | -5.048
1604.1 | 50.5 | -5.048
1604.2 | 50.5 | -5.048
1604.3 | 50.5 | -5.048
1604.4 | 50.5 | -5.048
1604.5 | 50.5 | -5.048
1604.6 | 50.5 | -5.048
1604.7 | 50.5 | -5.048
1604.8 | 50.5 | -5.048
1604.9 | 50.5 | -5.048
1605 | 50.5 | -5.048
1605.1 | 50.5 | -5.048
1605.2 | 50.5 | -5.047
1605.3 | 50.5 | -5.048
1605.4 | 50.5 | -5.048
1605.5 | 50.5 | -5.048
1605.6 | 50.5 | -5.048
1605.7 | 50.5 | -5.048
1605.8 | 50.5 | -5.048
1605.9 | 50.5 | -5.048
1606 | 50.5 | -5.048
1606.1 | 50.5 | -5.048
1606.2 | 50.5 | -5.048
1606.3 | 50.5 | -5.048
1606.4 | 50.5 | -5.048
1606.5 | 50.5 | -5.048
1606.6 | 50.5 | -5.048
1606.7 | 50.5 | -5.048
1606.8 | 50.5 | -5.048
1606.9 | 50.5 | -5.048
1607 | 50.5 | -5.048
1607.1 | 50.5 | -5.048
1607.2 | 50.5 | -5.048
1607.3 | 50.5 | -5.048
1607.4 | 50.5 | -5.048
1607.5 | 50.5 | -5.048
1607.6 | 50.5 | -5.048
1607.7 | 50.5 | -5.048
1607.8 | 50.5 | -5.048
1607.9 | 50.5 | -5.048
1608 | 50.5 | -5.048
1608.1 | 50.5 | -5.048
1608.2 | 50.5 | -5.048
1608.3 | 50.5 | -5.048
1608.4 | 50.5 | -5.048
1608.5 | 50.5 | -5.048
1608.6 | 50.5 | -5.048
1608.7 | 50.5 | -5.048
1608.8 | 50.5 | -5.048
1608.9 | 50.5 | -5.047
1609 | 50.5 | -5.047
1609.1 | 50.5 | -5.047
1609.2 | 50.5 | -5.047
1609.3 | 50.5 | -5.047
1609.4 | 50.5 | -5.047
1609.5 | 50.5 | -5.047
1609.6 | 50.5 | -5.047
1609.7 | 50.5 | -5.046
1609.8 | 50.5 | -5.047
1609.9 | 50.5 | -5.047
1610 | 50.5 | -5.047
1610.1 | 50.5 | -5.047
1610.2 | 50.5 | -5.047
1610.3 | 50.5 | -5.047
1610.4 | 50.5 | -5.047
1610.5 | 50.5 | -5.047
1610.6 | 50.5 | -5.047
1610.7 | 50.5 | -5.047
1610.8 | 50.5 | -5.047
1610.9 | 50.5 | -5.048
1611 | 50.5 | -5.048
1611.1 | 50.5 | -5.048
1611.2 | 50.5 | -5.048
1611.3 | 50.5 | -5.048
1611.4 | 50.5 | -5.048
1611.5 | 50.5 | -5.048
1611.6 | 50.5 | -5.048
1611.7 | 50.5 | -5.048
1611.8 | 50.5 | -5.048
1611.9 | 50.5 | -5.048
1612 | 50.5 | -5.048
1612.1 | 50.5 | -5.047
1612.2 | 50.5 | -5.047
1612.3 | 50.5 | -5.047
1612.4 | 50.5 | -5.047
1612.5 | 50.5 | -5.047
1612.6 | 50.5 | -5.047
1612.7 | 50.5 | -5.047
1612.8 | 50.5 | -5.047
1612.9 | 50.5 | -5.047
1613 | 50.5 | -5.047
1613.1 | 50.5 | -5.047
1613.2 | 50.5 | -5.047
1613.3 | 50.5 | -5.048
1613.4 | 50.5 | -5.048
1613.5 | 50.5 | -5.048
1613.6 | 50.5 | -5.048
1613.7 | 50.5 | -5.048
1613.8 | 50.5 | -5.048
1613.9 | 50.5 | -5.048
1614 | 50.5 | -5.048
1614.1 | 50.5 | -5.048
1614.2 | 50.5 | -5.048
1614.3 | 50.5 | -5.048
1614.4 | 50.5 | -5.048
1614.5 | 50.5 | -5.048
1614.6 | 50.5 | -5.048
1614.7 | 50.5 | -5.048
1614.8 | 50.5 | -5.048
1614.9 | 50.5 | -5.048
1615 | 50.5 | -5.048
1615.1 | 50.5 | -5.048
1615.2 | 50.5 | -5.048
1615.3 | 50.5 | -5.048
1615.4 | 50.5 | -5.048
1615.5 | 50.5 | -5.048
1615.6 | 50.5 | -5.048
1615.7 | 50.5 | -5.048
1615.8 | 50.5 | -5.048
1615.9 | 50.5 | -5.048
1616 | 50.5 | -5.048
1616.1 | 50.5 | -5.048
1616.2 | 50.5 | -5.048
1616.3 | 50.5 | -5.048
1616.4 | 50.5 | -5.048
1616.5 | 50.5 | -5.048
1616.6 | 50.5 | -5.048
1616.7 | 50.5 | -5.048
1616.8 | 50.5 | -5.048
1616.9 | 50.5 | -5.048
1617 | 50.5 | -5.048
1617.1 | 50.5 | -5.048
1617.2 | 50.5 | -5.048
1617.3 | 50.5 | -5.048
1617.4 | 50.5 | -5.048
1617.5 | 50.5 | -5.048
1617.6 | 50.5 | -5.048
1617.7 | 50.5 | -5.048
1617.8 | 50.5 | -5.048
1617.9 | 50.5 | -5.048
1618 | 50.5 | -5.048
1618.1 | 50.5 | -5.048
1618.2 | 50.5 | -5.047
1618.3 | 50.5 | -5.047
1618.4 | 50.5 | -5.047
1618.5 | 50.5 | -5.047
1618.6 | 50.5 | -5.047
1618.7 | 50.5 | -5.047
1618.8 | 50.5 | -5.047
1618.9 | 50.5 | -5.047
1619 | 50.5 | -5.047
1619.1 | 50.5 | -5.047
1619.2 | 50.5 | -5.047
1619.3 | 50.5 | -5.048
1619.4 | 50.5 | -5.048
1619.5 | 50.5 | -5.048
1619.6 | 50.5 | -5.048
1619.7 | 50.5 | -5.048
1619.8 | 50.5 | -5.048
1619.9 | 50.5 | -5.048
1620 | 50.5 | -5.048
1620.1 | 50.5 | -5.048
1620.2 | 50.5 | -5.048
1620.3 | 50.5 | -5.048
1620.4 | 50.5 | -5.048
1620.5 | 50.5 | -5.048
1620.6 | 50.5 | -5.048
1620.7 | 50.5 | -5.048
1620.8 | 50.5 | -5.048
1620.9 | 50.5 | -5.048
1621 | 50.5 | -5.048
1621.1 | 50.5 | -5.048
1621.2 | 50.5 | -5.048
1621.3 | 50.5 | -5.048
1621.4 | 50.5 | -5.048
1621.5 | 50.5 | -5.048
1621.6 | 50.5 | -5.048
1621.7 | 50.5 | -5.048
1621.8 | 50.5 | -5.048
1621.9 | 50.5 | -5.048
1622 | 50.5 | -5.048
1622.1 | 50.5 | -5.048
1622.2 | 50.5 | -5.048
1622.3 | 50.5 | -5.048
1622.4 | 50.5 | -5.048
1622.5 | 50.5 | -5.048
1622.6 | 50.5 | -5.048
1622.7 | 50.5 | -5.048
1622.8 | 50.5 | -5.048
1622.9 | 50.5 | -5.048
1623 | 50.5 | -5.048
1623.1 | 50.5 | -5.048
1623.2 | 50.5 | -5.048
1623.3 | 50.5 | -5.048
1623.4 | 50.5 | -5.048
1623.5 | 50.5 | -5.048
1623.6 | 50.5 | -5.048
1623.7 | 50.5 | -5.048
1623.8 | 50.5 | -5.048
1623.9 | 50.5 | -5.048
1624 | 50.5 | -5.048
1624.1 | 50.5 | -5.047
1624.2 | 50.5 | -5.047
1624.3 | 50.5 | -5.047
1624.4 | 50.5 | -5.047
1624.5 | 50.5 | -5.047
1624.6 | 50.5 | -5.047
1624.7 | 50.5 | -5.047
1624.8 | 50.5 | -5.047
1624.9 | 50.5 | -5.047
1625 | 50.5 | -5.047
1625.1 | 50.5 | -5.047
1625.2 | 50.5 | -5.047
1625.3 | 50.5 | -5.048
1625.4 | 50.5 | -5.048
1625.5 | 50.5 | -5.048
1625.6 | 50.5 | -5.048
1625.7 | 50.5 | -5.048
1625.8 | 50.5 | -5.048
1625.9 | 50.5 | -5.048
1626 | 50.5 | -5.048
1626.1 | 50.5 | -5.048
1626.2 | 50.5 | -5.048
1626.3 | 50.5 | -5.048
1626.4 | 50.5 | -5.048
1626.5 | 50.5 | -5.048
1626.6 | 50.5 | -5.048
1626.7 | 50.5 | -5.048
1626.8 | 50.5 | -5.048
1626.9 | 50.5 | -5.048
1627 | 50.5 | -5.048
1627.1 | 50.5 | -5.048
1627.2 | 50.5 | -5.048
1627.3 | 50.5 | -5.048
1627.4 | 50.5 | -5.048
1627.5 | 50.5 | -5.048
1627.6 | 50.5 | -5.048
1627.7 | 50.5 | -5.048
1627.8 | 50.5 | -5.048
1627.9 | 50.5 | -5.048
1628 | 50.5 | -5.048
1628.1 | 50.5 | -5.048
1628.2 | 50.5 | -5.048
1628.3 | 50.5 | -5.048
1628.4 | 50.5 | -5.048
1628.5 | 50.5 | -5.048
1628.6 | 50.5 | -5.048
1628.7 | 50.5 | -5.048
1628.8 | 50.5 | -5.048
1628.9 | 50.5 | -5.048
1629 | 50.5 | -5.048
1629.1 | 50.5 | -5.048
1629.2 | 50.5 | -5.048
1629.3 | 50.5 | -5.048
1629.4 | 50.5 | -5.048
1629.5 | 50.5 | -5.048
1629.6 | 50.5 | -5.048
1629.7 | 50.5 | -5.048
1629.8 | 50.5 | -5.048
1629.9 | 50.5 | -5.048
1630 | 50.5 | -5.048
1630.1 | 50.5 | -5.048
1630.2 | 50.5 | -5.048
1630.3 | 50.5 | -5.048
1630.4 | 50.5 | -5.048
1630.5 | 50.5 | -5.048
1630.6 | 50.5 | -5.048
1630.7 | 50.5 | -5.048
1630.8 | 50.5 | -5.048
1630.9 | 50.5 | -5.048
1631 | 50.5 | -5.048
1631.1 | 50.5 | -5.048
1631.2 | 50.5 | -5.048
1631.3 | 50.5 | -5.048
1631.4 | 50.5 | -5.048
1631.5 | 50.5 | -5.048
1631.6 | 50.5 | -5.048
1631.7 | 50.5 | -5.048
1631.8 | 50.5 | -5.048
1631.9 | 50.5 | -5.048
1632 | 50.5 | -5.048
1632.1 | 50.5 | -5.048
1632.2 | 50.5 | -5.048
1632.3 | 50.5 | -5.048
1632.4 | 50.5 | -5.048
1632.5 | 50.5 | -5.048
1632.6 | 50.5 | -5.048
1632.7 | 50.5 | -5.048
1632.8 | 50.5 | -5.048
1632.9 | 50.5 | -5.048
1633 | 50.5 | -5.048
1633.1 | 50.5 | -5.048
1633.2 | 50.5 | -5.048
1633.3 | 50.5 | -5.048
1633.4 | 50.5 | -5.048
1633.5 | 50.5 | -5.048
1633.6 | 50.5 | -5.048
1633.7 | 50.5 | -5.048
1633.8 | 50.5 | -5.048
1633.9 | 50.5 | -5.048
1634 | 50.5 | -5.048
1634.1 | 50.5 | -5.048
1634.2 | 50.5 | -5.048
1634.3 | 50.5 | -5.048
1634.4 | 50.5 | -5.048
1634.5 | 50.5 | -5.048
1634.6 | 50.5 | -5.048
1634.7 | 50.5 | -5.048
1634.8 | 50.5 | -5.048
1634.9 | 50.5 | -5.048
1635 | 50.5 | -5.048
1635.1 | 50.5 | -5.048
1635.2 | 50.5 | -5.048
1635.3 | 50.5 | -5.048
1635.4 | 50.5 | -5.048
1635.5 | 50.5 | -5.048
1635.6 | 50.5 | -5.048
1635.7 | 50.5 | -5.048
1635.8 | 50.5 | -5.048
1635.9 | 50.5 | -5.048
1636 | 50.5 | -5.048
1636.1 | 50.5 | -5.048
1636.2 | 50.5 | -5.048
1636.3 | 50.5 | -5.048
1636.4 | 50.5 | -5.048
1636.5 | 50.5 | -5.048
1636.6 | 50.5 | -5.048
1636.7 | 50.5 | -5.048
1636.8 | 50.5 | -5.048
1636.9 | 50.5 | -5.048
1637 | 50.5 | -5.048
1637.1 | 50.5 | -5.048
1637.2 | 50.5 | -5.048
1637.3 | 50.5 | -5.048
1637.4 | 50.5 | -5.048
1637.5 | 50.5 | -5.048
1637.6 | 50.5 | -5.048
1637.7 | 50.5 | -5.048
1637.8 | 50.5 | -5.048
1637.9 | 50.5 | -5.048
1638 | 50.5 | -5.048
1638.1 | 50.5 | -5.048
1638.2 | 50.5 | -5.048
1638.3 | 50.5 | -5.048
1638.4 | 50.5 | -5.048
1638.5 | 50.5 | -5.048
1638.6 | 50.5 | -5.048
1638.7 | 50.5 | -5.048
1638.8 | 50.5 | -5.048
1638.9 | 50.5 | -5.048
1639 | 50.5 | -5.048
1639.1 | 50.5 | -5.048
1639.2 | 50.5 | -5.048
1639.3 | 50.5 | -5.048
1639.4 | 50.5 | -5.047
1639.5 | 50.5 | -5.047
1639.6 | 50.5 | -5.047
1639.7 | 50.5 | -5.047
1639.8 | 50.5 | -5.047
1639.9 | 50.5 | -5.047
1640 | 50.5 | -5.047
1640.1 | 50.5 | -5.047
1640.2 | 50.5 | -5.047
1640.3 | 50.5 | -5.047
1640.4 | 50.5 | -5.047
1640.5 | 50.5 | -5.048
1640.6 | 50.5 | -5.048
1640.7 | 50.5 | -5.048
1640.8 | 50.5 | -5.048
1640.9 | 50.5 | -5.048
1641 | 50.5 | -5.048
1641.1 | 50.5 | -5.048
1641.2 | 50.5 | -5.048
1641.3 | 50.5 | -5.048
1641.4 | 50.5 | -5.048
1641.5 | 50.5 | -5.048
1641.6 | 50.5 | -5.048
1641.7 | 50.5 | -5.048
1641.8 | 50.5 | -5.048
1641.9 | 50.5 | -5.048
1642 | 50.5 | -5.048
1642.1 | 50.5 | -5.048
1642.2 | 50.5 | -5.048
1642.3 | 50.5 | -5.048
1642.4 | 50.5 | -5.048
1642.5 | 50.5 | -5.048
1642.6 | 50.5 | -5.048
1642.7 | 50.5 | -5.048
1642.8 | 50.5 | -5.048
1642.9 | 50.5 | -5.048
1643 | 50.5 | -5.048
1643.1 | 50.5 | -5.048
1643.2 | 50.5 | -5.048
1643.3 | 50.5 | -5.048
1643.4 | 50.5 | -5.048
1643.5 | 50.5 | -5.048
1643.6 | 50.5 | -5.048
1643.7 | 50.5 | -5.048
1643.8 | 50.5 | -5.048
1643.9 | 50.5 | -5.048
1644 | 50.5 | -5.048
1644.1 | 50.5 | -5.048
1644.2 | 50.5 | -5.048
1644.3 | 50.5 | -5.048
1644.4 | 50.5 | -5.048
1644.5 | 50.5 | -5.048
1644.6 | 50.5 | -5.048
1644.7 | 50.5 | -5.048
1644.8 | 50.5 | -5.048
1644.9 | 50.5 | -5.048
1645 | 50.5 | -5.048
1645.1 | 50.5 | -5.048
1645.2 | 50.5 | -5.048
1645.3 | 50.5 | -5.048
1645.4 | 50.5 | -5.048
1645.5 | 50.5 | -5.048
1645.6 | 50.5 | -5.048
1645.7 | 50.5 | -5.048
1645.8 | 50.5 | -5.048
1645.9 | 50.5 | -5.048
1646 | 50.5 | -5.048
1646.1 | 50.5 | -5.048
1646.2 | 50.5 | -5.048
1646.3 | 50.5 | -5.048
1646.4 | 50.5 | -5.048
1646.5 | 50.5 | -5.048
1646.6 | 50.5 | -5.048
1646.7 | 50.5 | -5.048
1646.8 | 50.5 | -5.048
1646.9 | 50.5 | -5.048
1647 | 50.5 | -5.048
1647.1 | 50.5 | -5.048
1647.2 | 50.5 | -5.048
1647.3 | 50.5 | -5.048
1647.4 | 50.5 | -5.048
1647.5 | 50.5 | -5.048
1647.6 | 50.5 | -5.048
1647.7 | 50.5 | -5.048
1647.8 | 50.5 | -5.048
1647.9 | 50.5 | -5.048
1648 | 50.5 | -5.048
1648.1 | 50.5 | -5.048
1648.2 | 50.5 | -5.048
1648.3 | 50.5 | -5.048
1648.4 | 50.5 | -5.048
1648.5 | 50.5 | -5.048
1648.6 | 50.5 | -5.048
1648.7 | 50.5 | -5.048
1648.8 | 50.5 | -5.048
1648.9 | 50.5 | -5.048
1649 | 50.5 | -5.048
1649.1 | 50.5 | -5.048
1649.2 | 50.5 | -5.048
1649.3 | 50.5 | -5.048
1649.4 | 50.5 | -5.048
1649.5 | 50.5 | -5.048
1649.6 | 50.5 | -5.048
1649.7 | 50.5 | -5.048
1649.8 | 50.5 | -5.048
1649.9 | 50.5 | -5.048
1650 | 50.5 | -5.048
1650.1 | 50.5 | -5.048
1650.2 | 50.5 | -5.048
1650.3 | 50.5 | -5.048
1650.4 | 50.5 | -5.048
1650.5 | 50.5 | -5.048
1650.6 | 50.5 | -5.048
1650.7 | 50.5 | -5.048
1650.8 | 50.5 | -5.048
1650.9 | 50.5 | -5.048
1651 | 50.5 | -5.048
1651.1 | 50.5 | -5.048
1651.2 | 50.5 | -5.048
1651.3 | 50.5 | -5.048
1651.4 | 50.5 | -5.048
1651.5 | 50.5 | -5.048
1651.6 | 50.5 | -5.048
1651.7 | 50.5 | -5.048
1651.8 | 50.5 | -5.048
1651.9 | 50.5 | -5.048
1652 | 50.5 | -5.048
1652.1 | 50.5 | -5.048
1652.2 | 50.5 | -5.048
1652.3 | 50.5 | -5.048
1652.4 | 50.5 | -5.048
1652.5 | 50.5 | -5.048
1652.6 | 50.5 | -5.048
1652.7 | 50.5 | -5.048
1652.8 | 50.5 | -5.048
1652.9 | 50.5 | -5.048
1653 | 50.5 | -5.048
1653.1 | 50.5 | -5.048
1653.2 | 50.5 | -5.048
1653.3 | 50.5 | -5.048
1653.4 | 50.5 | -5.048
1653.5 | 50.5 | -5.048
1653.6 | 50.5 | -5.048
1653.7 | 50.5 | -5.048
1653.8 | 50.5 | -5.048
1653.9 | 50.5 | -5.048
1654 | 50.5 | -5.048
1654.1 | 50.5 | -5.048
1654.2 | 50.5 | -5.048
1654.3 | 50.5 | -5.048
1654.4 | 50.5 | -5.048
1654.5 | 50.5 | -5.048
1654.6 | 50.5 | -5.048
1654.7 | 50.5 | -5.048
1654.8 | 50.5 | -5.048
1654.9 | 50.5 | -5.048
1655 | 50.5 | -5.048
1655.1 | 50.5 | -5.048
1655.2 | 50.5 | -5.048
1655.3 | 50.5 | -5.048
1655.4 | 50.5 | -5.048
1655.5 | 50.5 | -5.048
1655.6 | 50.5 | -5.048
1655.7 | 50.5 | -5.048
1655.8 | 50.5 | -5.048
1655.9 | 50.5 | -5.048
1656 | 50.5 | -5.048
1656.1 | 50.5 | -5.048
1656.2 | 50.5 | -5.048
1656.3 | 50.5 | -5.048
1656.4 | 50.5 | -5.048
1656.5 | 50.5 | -5.048
1656.6 | 50.5 | -5.048
1656.7 | 50.5 | -5.048
1656.8 | 50.5 | -5.048
1656.9 | 50.5 | -5.048
1657 | 50.5 | -5.048
1657.1 | 50.5 | -5.048
1657.2 | 50.5 | -5.048
1657.3 | 50.5 | -5.048
1657.4 | 50.5 | -5.048
1657.5 | 50.5 | -5.048
1657.6 | 50.5 | -5.048
1657.7 | 50.5 | -5.048
1657.8 | 50.5 | -5.048
1657.9 | 50.5 | -5.048
1658 | 50.5 | -5.048
1658.1 | 50.5 | -5.048
1658.2 | 50.5 | -5.048
1658.3 | 50.5 | -5.048
1658.4 | 50.5 | -5.048
1658.5 | 50.5 | -5.048
1658.6 | 50.5 | -5.048
1658.7 | 50.5 | -5.048
1658.8 | 50.5 | -5.048
1658.9 | 50.5 | -5.048
1659 | 50.5 | -5.048
1659.1 | 50.5 | -5.048
1659.2 | 50.5 | -5.048
1659.3 | 50.5 | -5.048
1659.4 | 50.5 | -5.048
1659.5 | 50.5 | -5.048
1659.6 | 50.5 | -5.048
1659.7 | 50.5 | -5.048
1659.8 | 50.5 | -5.048
1659.9 | 50.5 | -5.048
1660 | 50.5 | -5.048
1660.1 | 50.5 | -5.048
1660.2 | 50.5 | -5.048
1660.3 | 50.5 | -5.048
1660.4 | 50.5 | -5.048
1660.5 | 50.5 | -5.048
1660.6 | 50.5 | -5.048
1660.7 | 50.5 | -5.048
1660.8 | 50.5 | -5.048
1660.9 | 50.5 | -5.048
1661 | 50.5 | -5.048
1661.1 | 50.5 | -5.048
1661.2 | 50.5 | -5.048
1661.3 | 50.5 | -5.048
1661.4 | 50.5 | -5.048
1661.5 | 50.5 | -5.048
1661.6 | 50.5 | -5.048
1661.7 | 50.5 | -5.048
1661.8 | 50.5 | -5.047
1661.9 | 50.5 | -5.047
1662 | 50.5 | -5.047
1662.1 | 50.5 | -5.047
1662.2 | 50.5 | -5.047
1662.3 | 50.5 | -5.047
1662.4 | 50.5 | -5.047
1662.5 | 50.5 | -5.047
1662.6 | 50.5 | -5.047
1662.7 | 50.5 | -5.047
1662.8 | 50.5 | -5.048
1662.9 | 50.5 | -5.048
1663 | 50.5 | -5.048
1663.1 | 50.5 | -5.048
1663.2 | 50.5 | -5.048
1663.3 | 50.5 | -5.048
1663.4 | 50.5 | -5.048
1663.5 | 50.5 | -5.048
1663.6 | 50.5 | -5.048
1663.7 | 50.5 | -5.048
1663.8 | 50.5 | -5.048
1663.9 | 50.5 | -5.048
1664 | 50.5 | -5.048
1664.1 | 50.5 | -5.048
1664.2 | 50.5 | -5.048
1664.3 | 50.5 | -5.048
1664.4 | 50.5 | -5.048
1664.5 | 50.5 | -5.048
1664.6 | 50.5 | -5.048
1664.7 | 50.5 | -5.048
1664.8 | 50.5 | -5.048
1664.9 | 50.5 | -5.048
1665 | 50.5 | -5.048
1665.1 | 50.5 | -5.048
1665.2 | 50.5 | -5.048
1665.3 | 50.5 | -5.048
1665.4 | 50.5 | -5.048
1665.5 | 50.5 | -5.048
1665.6 | 50.5 | -5.048
1665.7 | 50.5 | -5.048
1665.8 | 50.5 | -5.048
1665.9 | 50.5 | -5.048
1666 | 50.5 | -5.048
1666.1 | 50.5 | -5.048
1666.2 | 50.5 | -5.048
1666.3 | 50.5 | -5.048
1666.4 | 50.5 | -5.048
1666.5 | 50.5 | -5.048
1666.6 | 50.5 | -5.048
1666.7 | 50.5 | -5.048
1666.8 | 50.5 | -5.048
1666.9 | 50.5 | -5.048
1667 | 50.5 | -5.048
1667.1 | 50.5 | -5.048
1667.2 | 50.5 | -5.048
1667.3 | 50.5 | -5.048
1667.4 | 50.5 | -5.048
1667.5 | 50.5 | -5.048
1667.6 | 50.5 | -5.048
1667.7 | 50.5 | -5.048
1667.8 | 50.5 | -5.048
1667.9 | 50.5 | -5.048
1668 | 50.5 | -5.048
1668.1 | 50.5 | -5.048
1668.2 | 50.5 | -5.048
1668.3 | 50.5 | -5.048
1668.4 | 50.5 | -5.048
1668.5 | 50.5 | -5.048
1668.6 | 50.5 | -5.048
1668.7 | 50.5 | -5.048
1668.8 | 50.5 | -5.048
1668.9 | 50.5 | -5.048
1669 | 50.5 | -5.048
1669.1 | 50.5 | -5.048
1669.2 | 50.5 | -5.048
1669.3 | 50.5 | -5.048
1669.4 | 50.5 | -5.048
1669.5 | 50.5 | -5.048
1669.6 | 50.5 | -5.048
1669.7 | 50.5 | -5.048
1669.8 | 50.5 | -5.048
1669.9 | 50.5 | -5.048
1670 | 50.5 | -5.048
1670.1 | 50.5 | -5.048
1670.2 | 50.5 | -5.048
1670.3 | 50.5 | -5.048
1670.4 | 50.5 | -5.048
1670.5 | 50.5 | -5.048
1670.6 | 50.5 | -5.048
1670.7 | 50.5 | -5.048
1670.8 | 50.5 | -5.048
1670.9 | 50.5 | -5.048
1671 | 50.5 | -5.048
1671.1 | 50.5 | -5.048
1671.2 | 50.5 | -5.048
1671.3 | 50.5 | -5.048
1671.4 | 50.5 | -5.048
1671.5 | 50.5 | -5.048
1671.6 | 50.5 | -5.048
1671.7 | 50.5 | -5.048
1671.8 | 50.5 | -5.048
1671.9 | 50.5 | -5.048
1672 | 50.5 | -5.048
1672.1 | 50.5 | -5.048
1672.2 | 50.5 | -5.048
1672.3 | 50.5 | -5.048
1672.4 | 50.5 | -5.048
1672.5 | 50.5 | -5.048
1672.6 | 50.5 | -5.048
1672.7 | 50.5 | -5.048
1672.8 | 50.5 | -5.048
1672.9 | 50.5 | -5.048
1673 | 50.5 | -5.048
1673.1 | 50.5 | -5.048
1673.2 | 50.5 | -5.048
1673.3 | 50.5 | -5.048
1673.4 | 50.5 | -5.048
1673.5 | 50.5 | -5.048
1673.6 | 50.5 | -5.048
1673.7 | 50.5 | -5.048
1673.8 | 50.5 | -5.048
1673.9 | 50.5 | -5.048
1674 | 50.5 | -5.048
1674.1 | 50.5 | -5.048
1674.2 | 50.5 | -5.048
1674.3 | 50.5 | -5.048
1674.4 | 50.5 | -5.047
1674.5 | 50.5 | -5.047
1674.6 | 50.5 | -5.047
1674.7 | 50.5 | -5.047
1674.8 | 50.5 | -5.047
1674.9 | 50.5 | -5.047
1675 | 50.5 | -5.047
1675.1 | 50.5 | -5.047
1675.2 | 50.5 | -5.047
1675.3 | 50.5 | -5.047
1675.4 | 50.5 | -5.047
1675.5 | 50.5 | -5.047
1675.6 | 50.5 | -5.047
1675.7 | 50.5 | -5.047
1675.8 | 50.5 | -5.047
1675.9 | 50.5 | -5.047
1676 | 50.5 | -5.047
1676.1 | 50.5 | -5.047
1676.2 | 50.5 | -5.047
1676.3 | 50.5 | -5.047
1676.4 | 50.5 | -5.047
1676.5 | 50.5 | -5.047
1676.6 | 50.5 | -5.047
1676.7 | 50.5 | -5.047
1676.8 | 50.5 | -5.048
1676.9 | 50.5 | -5.048
1677 | 50.5 | -5.048
1677.1 | 50.5 | -5.048
1677.2 | 50.5 | -5.048
1677.3 | 50.5 | -5.048
1677.4 | 50.5 | -5.048
1677.5 | 50.5 | -5.048
1677.6 | 50.5 | -5.048
1677.7 | 50.5 | -5.048
1677.8 | 50.5 | -5.048
1677.9 | 50.5 | -5.048
1678 | 50.5 | -5.048
1678.1 | 50.5 | -5.048
1678.2 | 50.5 | -5.048
1678.3 | 50.5 | -5.048
1678.4 | 50.5 | -5.048
1678.5 | 50.5 | -5.048
1678.6 | 50.5 | -5.048
1678.7 | 50.5 | -5.048
1678.8 | 50.5 | -5.048
1678.9 | 50.5 | -5.048
1679 | 50.5 | -5.048
1679.1 | 50.5 | -5.048
1679.2 | 50.5 | -5.048
1679.3 | 50.5 | -5.048
1679.4 | 50.5 | -5.048
1679.5 | 50.5 | -5.048
1679.6 | 50.5 | -5.048
1679.7 | 50.5 | -5.048
1679.8 | 50.5 | -5.048
1679.9 | 50.5 | -5.048
1680 | 50.5 | -5.048
1680.1 | 50.5 | -5.048
1680.2 | 50.5 | -5.048
1680.3 | 50.5 | -5.048
1680.4 | 50.5 | -5.048
1680.5 | 50.5 | -5.048
1680.6 | 50.5 | -5.048
1680.7 | 50.5 | -5.048
1680.8 | 50.5 | -5.048
1680.9 | 50.5 | -5.048
1681 | 50.5 | -5.048
1681.1 | 50.5 | -5.048
1681.2 | 50.5 | -5.048
1681.3 | 50.5 | -5.048
1681.4 | 50.5 | -5.048
1681.5 | 50.5 | -5.048
1681.6 | 50.5 | -5.047
1681.7 | 50.5 | -5.047
1681.8 | 50.5 | -5.047
1681.9 | 50.5 | -5.047
1682 | 50.5 | -5.047
1682.1 | 50.5 | -5.047
1682.2 | 50.5 | -5.047
1682.3 | 50.5 | -5.047
1682.4 | 50.5 | -5.047
1682.5 | 50.5 | -5.047
1682.6 | 50.5 | -5.048
1682.7 | 50.5 | -5.048
1682.8 | 50.5 | -5.048
1682.9 | 50.5 | -5.048
1683 | 50.5 | -5.048
1683.1 | 50.5 | -5.048
1683.2 | 50.5 | -5.048
1683.3 | 50.5 | -5.048
1683.4 | 50.5 | -5.048
1683.5 | 50.5 | -5.048
1683.6 | 50.5 | -5.048
1683.7 | 50.5 | -5.048
1683.8 | 50.5 | -5.048
1683.9 | 50.5 | -5.048
1684 | 50.5 | -5.048
1684.1 | 50.5 | -5.048
1684.2 | 50.5 | -5.048
1684.3 | 50.5 | -5.048
1684.4 | 50.5 | -5.048
1684.5 | 50.5 | -5.048
1684.6 | 50.5 | -5.048
1684.7 | 50.5 | -5.048
1684.8 | 50.5 | -5.048
1684.9 | 50.5 | -5.048
1685 | 50.5 | -5.048
1685.1 | 50.5 | -5.048
1685.2 | 50.5 | -5.048
1685.3 | 50.5 | -5.048
1685.4 | 50.5 | -5.048
1685.5 | 50.5 | -5.048
1685.6 | 50.5 | -5.048
1685.7 | 50.5 | -5.048
1685.8 | 50.5 | -5.048
1685.9 | 50.5 | -5.048
1686 | 50.5 | -5.048
1686.1 | 50.5 | -5.048
1686.2 | 50.5 | -5.048
1686.3 | 50.5 | -5.048
1686.4 | 50.5 | -5.048
1686.5 | 50.5 | -5.048
1686.6 | 50.5 | -5.048
1686.7 | 50.5 | -5.048
1686.8 | 50.5 | -5.048
1686.9 | 50.5 | -5.048
1687 | 50.5 | -5.048
1687.1 | 50.5 | -5.048
1687.2 | 50.5 | -5.048
1687.3 | 50.5 | -5.048
1687.4 | 50.5 | -5.048
1687.5 | 50.5 | -5.048
1687.6 | 50.5 | -5.048
1687.7 | 50.5 | -5.048
1687.8 | 50.5 | -5.048
1687.9 | 50.5 | -5.048
1688 | 50.5 | -5.048
1688.1 | 50.5 | -5.048
1688.2 | 50.5 | -5.048
1688.3 | 50.5 | -5.048
1688.4 | 50.5 | -5.048
1688.5 | 50.5 | -5.048
1688.6 | 50.5 | -5.048
1688.7 | 50.5 | -5.048
1688.8 | 50.5 | -5.048
1688.9 | 50.5 | -5.048
1689 | 50.5 | -5.048
1689.1 | 50.5 | -5.048
1689.2 | 50.5 | -5.048
1689.3 | 50.5 | -5.048
1689.4 | 50.5 | -5.048
1689.5 | 50.5 | -5.048
1689.6 | 50.5 | -5.048
1689.7 | 50.5 | -5.048
1689.8 | 50.5 | -5.048
1689.9 | 50.5 | -5.048
1690 | 50.5 | -5.048
1690.1 | 50.5 | -5.048
1690.2 | 50.5 | -5.048
1690.3 | 50.5 | -5.048
1690.4 | 50.5 | -5.048
1690.5 | 50.5 | -5.048
1690.6 | 50.5 | -5.048
1690.7 | 50.5 | -5.048
1690.8 | 50.5 | -5.048
1690.9 | 50.5 | -5.048
1691 | 50.5 | -5.048
1691.1 | 50.5 | -5.048
1691.2 | 50.5 | -5.048
1691.3 | 50.5 | -5.048
1691.4 | 50.5 | -5.048
1691.5 | 50.5 | -5.048
1691.6 | 50.5 | -5.048
1691.7 | 50.5 | -5.048
1691.8 | 50.5 | -5.048
1691.9 | 50.5 | -5.048
1692 | 50.5 | -5.048
1692.1 | 50.5 | -5.048
1692.2 | 50.5 | -5.048
1692.3 | 50.5 | -5.048
1692.4 | 50.5 | -5.048
1692.5 | 50.5 | -5.048
1692.6 | 50.5 | -5.048
1692.7 | 50.5 | -5.048
1692.8 | 50.5 | -5.048
1692.9 | 50.5 | -5.048
1693 | 50.5 | -5.048
1693.1 | 50.5 | -5.048
1693.2 | 50.5 | -5.048
1693.3 | 50.5 | -5.048
1693.4 | 50.5 | -5.048
1693.5 | 50.5 | -5.048
1693.6 | 50.5 | -5.048
1693.7 | 50.5 | -5.048
1693.8 | 50.5 | -5.048
1693.9 | 50.5 | -5.048
1694 | 50.5 | -5.048
1694.1 | 50.5 | -5.048
1694.2 | 50.5 | -5.048
1694.3 | 50.5 | -5.048
1694.4 | 50.5 | -5.048
1694.5 | 50.5 | -5.048
1694.6 | 50.5 | -5.048
1694.7 | 50.5 | -5.048
1694.8 | 50.5 | -5.048
1694.9 | 50.5 | -5.048
1695 | 50.5 | -5.048
1695.1 | 50.5 | -5.048
1695.2 | 50.5 | -5.048
1695.3 | 50.5 | -5.048
1695.4 | 50.5 | -5.048
1695.5 | 50.5 | -5.048
1695.6 | 50.5 | -5.048
1695.7 | 50.5 | -5.048
1695.8 | 50.5 | -5.048
1695.9 | 50.5 | -5.048
1696 | 50.5 | -5.048
1696.1 | 50.5 | -5.048
1696.2 | 50.5 | -5.048
1696.3 | 50.5 | -5.048
1696.4 | 50.5 | -5.048
1696.5 | 50.5 | -5.048
1696.6 | 50.5 | -5.048
1696.7 | 50.5 | -5.048
1696.8 | 50.5 | -5.048
1696.9 | 50.5 | -5.048
1697 | 50.5 | -5.048
1697.1 | 50.5 | -5.048
1697.2 | 50.5 | -5.048
1697.3 | 50.5 | -5.048
1697.4 | 50.5 | -5.048
1697.5 | 50.5 | -5.048
1697.6 | 50.5 | -5.048
1697.7 | 50.5 | -5.048
1697.8 | 50.5 | -5.048
1697.9 | 50.5 | -5.048
1698 | 50.5 | -5.048
1698.1 | 50.5 | -5.048
1698.2 | 50.5 | -5.048
1698.3 | 50.5 | -5.048
1698.4 | 50.5 | -5.048
1698.5 | 50.5 | -5.048
1698.6 | 50.5 | -5.048
1698.7 | 50.5 | -5.047
1698.8 | 50.5 | -5.047
1698.9 | 50.5 | -5.047
1699 | 50.5 | -5.048
1699.1 | 50.5 | -5.048
1699.2 | 50.5 | -5.048
1699.3 | 50.5 | -5.048
1699.4 | 50.5 | -5.048
1699.5 | 50.5 | -5.048
1699.6 | 50.5 | -5.048
1699.7 | 50.5 | -5.048
1699.8 | 50.5 | -5.048
1699.9 | 50.5 | -5.048
1700 | 50.5 | -5.047
1700.1 | 50.5 | -5.047
1700.2 | 50.5 | -5.047
1700.3 | 50.5 | -5.047
1700.4 | 50.5 | -5.047
1700.5 | 50.5 | -5.047
1700.6 | 50.5 | -5.047
1700.7 | 50.5 | -5.047
1700.8 | 50.5 | -5.047
1700.9 | 50.5 | -5.047
1701 | 50.5 | -5.047
1701.1 | 50.5 | -5.047
1701.2 | 50.5 | -5.047
1701.3 | 50.5 | -5.047
1701.4 | 50.5 | -5.047
1701.5 | 50.5 | -5.047
1701.6 | 50.5 | -5.047
1701.7 | 50.5 | -5.047
1701.8 | 50.5 | -5.047
1701.9 | 50.5 | -5.047
1702 | 50.5 | -5.047
1702.1 | 50.5 | -5.048
1702.2 | 50.5 | -5.048
1702.3 | 50.5 | -5.048
1702.4 | 50.5 | -5.048
1702.5 | 50.5 | -5.048
1702.6 | 50.5 | -5.048
1702.7 | 50.5 | -5.048
1702.8 | 50.5 | -5.048
1702.9 | 50.5 | -5.048
1703 | 50.5 | -5.048
1703.1 | 50.5 | -5.048
1703.2 | 50.5 | -5.048
1703.3 | 50.5 | -5.048
1703.4 | 50.5 | -5.048
1703.5 | 50.5 | -5.048
1703.6 | 50.5 | -5.048
1703.7 | 50.5 | -5.048
1703.8 | 50.5 | -5.048
1703.9 | 50.5 | -5.048
1704 | 50.5 | -5.048
1704.1 | 50.5 | -5.048
1704.2 | 50.5 | -5.048
1704.3 | 50.5 | -5.048
1704.4 | 50.5 | -5.048
1704.5 | 50.5 | -5.048
1704.6 | 50.5 | -5.048
1704.7 | 50.5 | -5.048
1704.8 | 50.5 | -5.048
1704.9 | 50.5 | -5.048
1705 | 50.5 | -5.048
1705.1 | 50.5 | -5.048
1705.2 | 50.5 | -5.048
1705.3 | 50.5 | -5.048
1705.4 | 50.5 | -5.048
1705.5 | 50.5 | -5.048
1705.6 | 50.5 | -5.048
1705.7 | 50.5 | -5.048
1705.8 | 50.5 | -5.048
1705.9 | 50.5 | -5.048
1706 | 50.5 | -5.048
1706.1 | 50.5 | -5.048
1706.2 | 50.5 | -5.048
1706.3 | 50.5 | -5.048
1706.4 | 50.5 | -5.048
1706.5 | 50.5 | -5.048
1706.6 | 50.5 | -5.048
1706.7 | 50.5 | -5.048
1706.8 | 50.5 | -5.048
1706.9 | 50.5 | -5.048
1707 | 50.5 | -5.048
1707.1 | 50.5 | -5.048
1707.2 | 50.5 | -5.048
1707.3 | 50.5 | -5.048
1707.4 | 50.5 | -5.048
1707.5 | 50.5 | -5.048
1707.6 | 50.5 | -5.048
1707.7 | 50.5 | -5.048
1707.8 | 50.5 | -5.048
1707.9 | 50.5 | -5.048
1708 | 50.5 | -5.048
1708.1 | 50.5 | -5.048
1708.2 | 50.5 | -5.048
1708.3 | 50.5 | -5.048
1708.4 | 50.5 | -5.048
1708.5 | 50.5 | -5.048
1708.6 | 50.5 | -5.048
1708.7 | 50.5 | -5.048
1708.8 | 50.5 | -5.048
1708.9 | 50.5 | -5.048
1709 | 50.5 | -5.048
1709.1 | 50.5 | -5.048
1709.2 | 50.5 | -5.048
1709.3 | 50.5 | -5.048
1709.4 | 50.5 | -5.048
1709.5 | 50.5 | -5.048
1709.6 | 50.5 | -5.048
1709.7 | 50.5 | -5.048
1709.8 | 50.5 | -5.048
1709.9 | 50.5 | -5.048
1710 | 50.5 | -5.048
1710.1 | 50.5 | -5.048
1710.2 | 50.5 | -5.048
1710.3 | 50.5 | -5.048
1710.4 | 50.5 | -5.048
1710.5 | 50.5 | -5.048
1710.6 | 50.5 | -5.048
1710.7 | 50.5 | -5.048
1710.8 | 50.5 | -5.048
1710.9 | 50.5 | -5.048
1711 | 50.5 | -5.048
1711.1 | 50.5 | -5.048
1711.2 | 50.5 | -5.048
1711.3 | 50.5 | -5.048
1711.4 | 50.5 | -5.048
1711.5 | 50.5 | -5.048
1711.6 | 50.5 | -5.048
1711.7 | 50.5 | -5.048
1711.8 | 50.5 | -5.047
1711.9 | 50.5 | -5.047
1712 | 50.5 | -5.047
1712.1 | 50.5 | -5.047
1712.2 | 50.5 | -5.047
1712.3 | 50.5 | -5.047
1712.4 | 50.5 | -5.047
1712.5 | 50.5 | -5.047
1712.6 | 50.5 | -5.047
1712.7 | 50.5 | -5.047
1712.8 | 50.5 | -5.047
1712.9 | 50.5 | -5.047
1713 | 50.5 | -5.048
1713.1 | 50.5 | -5.048
1713.2 | 50.5 | -5.048
1713.3 | 50.5 | -5.048
1713.4 | 50.5 | -5.048
1713.5 | 50.5 | -5.048
1713.6 | 50.5 | -5.048
1713.7 | 50.5 | -5.048
1713.8 | 50.5 | -5.048
1713.9 | 50.5 | -5.048
1714 | 50.5 | -5.048
1714.1 | 50.5 | -5.048
1714.2 | 50.5 | -5.048
1714.3 | 50.5 | -5.048
1714.4 | 50.5 | -5.048
1714.5 | 50.5 | -5.048
1714.6 | 50.5 | -5.048
1714.7 | 50.5 | -5.048
1714.8 | 50.5 | -5.048
1714.9 | 50.5 | -5.048
1715 | 50.5 | -5.048
1715.1 | 50.5 | -5.048
1715.2 | 50.5 | -5.048
1715.3 | 50.5 | -5.048
1715.4 | 50.5 | -5.048
1715.5 | 50.5 | -5.048
1715.6 | 50.5 | -5.048
1715.7 | 50.5 | -5.048
1715.8 | 50.5 | -5.048
1715.9 | 50.5 | -5.048
1716 | 50.5 | -5.048
1716.1 | 50.5 | -5.048
1716.2 | 50.5 | -5.048
1716.3 | 50.5 | -5.048
1716.4 | 50.5 | -5.048
1716.5 | 50.5 | -5.048
1716.6 | 50.5 | -5.048
1716.7 | 50.5 | -5.048
1716.8 | 50.5 | -5.048
1716.9 | 50.5 | -5.048
1717 | 50.5 | -5.048
1717.1 | 50.5 | -5.048
1717.2 | 50.5 | -5.048
1717.3 | 50.5 | -5.048
1717.4 | 50.5 | -5.048
1717.5 | 50.5 | -5.048
1717.6 | 50.5 | -5.048
1717.7 | 50.5 | -5.048
1717.8 | 50.5 | -5.048
1717.9 | 50.5 | -5.048
1718 | 50.5 | -5.048
1718.1 | 50.5 | -5.048
1718.2 | 50.5 | -5.048
1718.3 | 50.5 | -5.048
1718.4 | 50.5 | -5.048
1718.5 | 50.5 | -5.048
1718.6 | 50.5 | -5.048
1718.7 | 50.5 | -5.048
1718.8 | 50.5 | -5.048
1718.9 | 50.5 | -5.048
1719 | 50.5 | -5.048
1719.1 | 50.5 | -5.048
1719.2 | 50.5 | -5.048
1719.3 | 50.5 | -5.048
1719.4 | 50.5 | -5.048
1719.5 | 50.5 | -5.048
1719.6 | 50.5 | -5.048
1719.7 | 50.5 | -5.048
1719.8 | 50.5 | -5.048
1719.9 | 50.5 | -5.048
1720 | 50.5 | -5.048
1720.1 | 50.5 | -5.048
1720.2 | 50.5 | -5.048
1720.3 | 50.5 | -5.048
1720.4 | 50.5 | -5.048
1720.5 | 50.5 | -5.048
1720.6 | 50.5 | -5.048
1720.7 | 50.5 | -5.048
1720.8 | 50.5 | -5.048
1720.9 | 50.5 | -5.048
1721 | 50.5 | -5.048
1721.1 | 50.5 | -5.048
1721.2 | 50.5 | -5.048
1721.3 | 50.5 | -5.048
1721.4 | 50.5 | -5.048
1721.5 | 50.5 | -5.048
1721.6 | 50.5 | -5.048
1721.7 | 50.5 | -5.048
1721.8 | 50.5 | -5.048
1721.9 | 50.5 | -5.048
1722 | 50.5 | -5.048
1722.1 | 50.5 | -5.048
1722.2 | 50.5 | -5.048
1722.3 | 50.5 | -5.048
1722.4 | 50.5 | -5.048
1722.5 | 50.5 | -5.048
1722.6 | 50.5 | -5.048
1722.7 | 50.5 | -5.048
1722.8 | 50.5 | -5.048
1722.9 | 50.5 | -5.048
1723 | 50.5 | -5.048
1723.1 | 50.5 | -5.048
1723.2 | 50.5 | -5.048
1723.3 | 50.5 | -5.048
1723.4 | 50.5 | -5.048
1723.5 | 50.5 | -5.048
1723.6 | 50.5 | -5.048
1723.7 | 50.5 | -5.048
1723.8 | 50.5 | -5.048
1723.9 | 50.5 | -5.048
1724 | 50.5 | -5.048
1724.1 | 50.5 | -5.048
1724.2 | 50.5 | -5.048
1724.3 | 50.5 | -5.048
1724.4 | 50.5 | -5.048
1724.5 | 50.5 | -5.048
1724.6 | 50.5 | -5.048
1724.7 | 50.5 | -5.048
1724.8 | 50.5 | -5.048
1724.9 | 50.5 | -5.048
1725 | 50.5 | -5.048
1725.1 | 50.5 | -5.048
1725.2 | 50.5 | -5.048
1725.3 | 50.5 | -5.048
1725.4 | 50.5 | -5.048
1725.5 | 50.5 | -5.048
1725.6 | 50.5 | -5.048
1725.7 | 50.5 | -5.048
1725.8 | 50.5 | -5.048
1725.9 | 50.5 | -5.048
1726 | 50.5 | -5.048
1726.1 | 50.5 | -5.048
1726.2 | 50.5 | -5.048
1726.3 | 50.5 | -5.048
1726.4 | 50.5 | -5.048
1726.5 | 50.5 | -5.048
1726.6 | 50.5 | -5.048
1726.7 | 50.5 | -5.048
1726.8 | 50.5 | -5.048
1726.9 | 50.5 | -5.048
1727 | 50.5 | -5.048
1727.1 | 50.5 | -5.048
1727.2 | 50.5 | -5.048
1727.3 | 50.5 | -5.048
1727.4 | 50.5 | -5.048
1727.5 | 50.5 | -5.048
1727.6 | 50.5 | -5.048
1727.7 | 50.5 | -5.048
1727.8 | 50.5 | -5.048
1727.9 | 50.5 | -5.048
1728 | 50.5 | -5.048
1728.1 | 50.5 | -5.048
1728.2 | 50.5 | -5.048
1728.3 | 50.5 | -5.048
1728.4 | 50.5 | -5.048
1728.5 | 50.5 | -5.048
1728.6 | 50.5 | -5.048
1728.7 | 50.5 | -5.048
1728.8 | 50.5 | -5.048
1728.9 | 50.5 | -5.048
1729 | 50.5 | -5.048
1729.1 | 50.5 | -5.048
1729.2 | 50.5 | -5.048
1729.3 | 50.5 | -5.048
1729.4 | 50.5 | -5.048
1729.5 | 50.5 | -5.048
1729.6 | 50.5 | -5.048
1729.7 | 50.5 | -5.048
1729.8 | 50.5 | -5.048
1729.9 | 50.5 | -5.048
1730 | 50.5 | -5.048
1730.1 | 50.5 | -5.048
1730.2 | 50.5 | -5.048
1730.3 | 50.5 | -5.048
1730.4 | 50.5 | -5.048
1730.5 | 50.5 | -5.048
1730.6 | 50.5 | -5.048
1730.7 | 50.5 | -5.048
1730.8 | 50.5 | -5.048
1730.9 | 50.5 | -5.048
1731 | 50.5 | -5.048
1731.1 | 50.5 | -5.048
1731.2 | 50.5 | -5.048
1731.3 | 50.5 | -5.048
1731.4 | 50.5 | -5.048
1731.5 | 50.5 | -5.048
1731.6 | 50.5 | -5.048
1731.7 | 50.5 | -5.048
1731.8 | 50.5 | -5.048
1731.9 | 50.5 | -5.048
1732 | 50.5 | -5.048
1732.1 | 50.5 | -5.048
1732.2 | 50.5 | -5.048
1732.3 | 50.5 | -5.048
1732.4 | 50.5 | -5.048
1732.5 | 50.5 | -5.048
1732.6 | 50.5 | -5.048
1732.7 | 50.5 | -5.048
1732.8 | 50.5 | -5.048
1732.9 | 50.5 | -5.048
1733 | 50.5 | -5.048
1733.1 | 50.5 | -5.048
1733.2 | 50.5 | -5.048
1733.3 | 50.5 | -5.048
1733.4 | 50.5 | -5.048
1733.5 | 50.5 | -5.048
1733.6 | 50.5 | -5.048
1733.7 | 50.5 | -5.048
1733.8 | 50.5 | -5.048
1733.9 | 50.5 | -5.048
1734 | 50.5 | -5.048
1734.1 | 50.5 | -5.048
1734.2 | 50.5 | -5.048
1734.3 | 50.5 | -5.048
1734.4 | 50.5 | -5.048
1734.5 | 50.5 | -5.048
1734.6 | 50.5 | -5.048
1734.7 | 50.5 | -5.048
1734.8 | 50.5 | -5.048
1734.9 | 50.5 | -5.048
1735 | 50.5 | -5.048
1735.1 | 50.5 | -5.048
1735.2 | 50.5 | -5.048
1735.3 | 50.5 | -5.048
1735.4 | 50.5 | -5.048
1735.5 | 50.5 | -5.048
1735.6 | 50.5 | -5.048
1735.7 | 50.5 | -5.048
1735.8 | 50.5 | -5.048
1735.9 | 50.5 | -5.048
1736 | 50.5 | -5.048
1736.1 | 50.5 | -5.048
1736.2 | 50.5 | -5.048
1736.3 | 50.5 | -5.048
1736.4 | 50.5 | -5.048
1736.5 | 50.5 | -5.048
1736.6 | 50.5 | -5.048
1736.7 | 50.5 | -5.048
1736.8 | 50.5 | -5.048
1736.9 | 50.5 | -5.048
1737 | 50.5 | -5.048
1737.1 | 50.5 | -5.048
1737.2 | 50.5 | -5.048
1737.3 | 50.5 | -5.048
1737.4 | 50.5 | -5.048
1737.5 | 50.5 | -5.048
1737.6 | 50.5 | -5.048
1737.7 | 50.5 | -5.048
1737.8 | 50.5 | -5.048
1737.9 | 50.5 | -5.048
1738 | 50.5 | -5.048
1738.1 | 50.5 | -5.048
1738.2 | 50.5 | -5.048
1738.3 | 50.5 | -5.048
1738.4 | 50.5 | -5.048
1738.5 | 50.5 | -5.048
1738.6 | 50.5 | -5.048
1738.7 | 50.5 | -5.048
1738.8 | 50.5 | -5.048
1738.9 | 50.5 | -5.048
1739 | 50.5 | -5.048
1739.1 | 50.5 | -5.048
1739.2 | 50.5 | -5.048
1739.3 | 50.5 | -5.048
1739.4 | 50.5 | -5.048
1739.5 | 50.5 | -5.048
1739.6 | 50.5 | -5.048
1739.7 | 50.5 | -5.048
1739.8 | 50.5 | -5.048
1739.9 | 50.5 | -5.048
1740 | 50.5 | -5.048
1740.1 | 50.5 | -5.048
1740.2 | 50.5 | -5.048
1740.3 | 50.5 | -5.048
1740.4 | 50.5 | -5.048
1740.5 | 50.5 | -5.048
1740.6 | 50.5 | -5.048
1740.7 | 50.5 | -5.048
1740.8 | 50.5 | -5.048
1740.9 | 50.5 | -5.048
1741 | 50.5 | -5.048
1741.1 | 50.5 | -5.048
1741.2 | 50.5 | -5.048
1741.3 | 50.5 | -5.048
1741.4 | 50.5 | -5.048
1741.5 | 50.5 | -5.048
1741.6 | 50.5 | -5.048
1741.7 | 50.5 | -5.048
1741.8 | 50.5 | -5.048
1741.9 | 50.5 | -5.048
1742 | 50.5 | -5.048
1742.1 | 50.5 | -5.048
1742.2 | 50.5 | -5.048
1742.3 | 50.5 | -5.048
1742.4 | 50.5 | -5.048
1742.5 | 50.5 | -5.048
1742.6 | 50.5 | -5.048
1742.7 | 50.5 | -5.048
1742.8 | 50.5 | -5.048
1742.9 | 50.5 | -5.048
1743 | 50.5 | -5.048
1743.1 | 50.5 | -5.048
1743.2 | 50.5 | -5.048
1743.3 | 50.5 | -5.048
1743.4 | 50.5 | -5.048
1743.5 | 50.5 | -5.048
1743.6 | 50.5 | -5.048
1743.7 | 50.5 | -5.048
1743.8 | 50.5 | -5.048
1743.9 | 50.5 | -5.048
1744 | 50.5 | -5.048
1744.1 | 50.5 | -5.048
1744.2 | 50.5 | -5.048
1744.3 | 50.5 | -5.048
1744.4 | 50.5 | -5.048
1744.5 | 50.5 | -5.048
1744.6 | 50.5 | -5.048
1744.7 | 50.5 | -5.048
1744.8 | 50.5 | -5.048
1744.9 | 50.5 | -5.048
1745 | 50.5 | -5.048
1745.1 | 50.5 | -5.048
1745.2 | 50.5 | -5.048
1745.3 | 50.5 | -5.048
1745.4 | 50.5 | -5.048
1745.5 | 50.5 | -5.048
1745.6 | 50.5 | -5.048
1745.7 | 50.5 | -5.048
1745.8 | 50.5 | -5.048
1745.9 | 50.5 | -5.048
1746 | 50.5 | -5.048
1746.1 | 50.5 | -5.048
1746.2 | 50.5 | -5.048
1746.3 | 50.5 | -5.048
1746.4 | 50.5 | -5.048
1746.5 | 50.5 | -5.048
1746.6 | 50.5 | -5.048
1746.7 | 50.5 | -5.048
1746.8 | 50.5 | -5.048
1746.9 | 50.5 | -5.048
1747 | 50.5 | -5.048
1747.1 | 50.5 | -5.048
1747.2 | 50.5 | -5.048
1747.3 | 50.5 | -5.048
1747.4 | 50.5 | -5.048
1747.5 | 50.5 | -5.048
1747.6 | 50.5 | -5.048
1747.7 | 50.5 | -5.048
1747.8 | 50.5 | -5.048
1747.9 | 50.5 | -5.048
1748 | 50.5 | -5.048
1748.1 | 50.5 | -5.048
1748.2 | 50.5 | -5.048
1748.3 | 50.5 | -5.048
1748.4 | 50.5 | -5.048
1748.5 | 50.5 | -5.048
1748.6 | 50.5 | -5.048
1748.7 | 50.5 | -5.048
1748.8 | 50.5 | -5.048
1748.9 | 50.5 | -5.048
1749 | 50.5 | -5.048
1749.1 | 50.5 | -5.048
1749.2 | 50.5 | -5.048
1749.3 | 50.5 | -5.048
1749.4 | 50.5 | -5.048
1749.5 | 50.5 | -5.048
1749.6 | 50.5 | -5.048
1749.7 | 50.5 | -5.048
1749.8 | 50.5 | -5.048
1749.9 | 50.5 | -5.048
1750 | 50.5 | -5.048
1750.1 | 50.5 | -5.048
1750.2 | 50.5 | -5.048
1750.3 | 50.5 | -5.048
1750.4 | 50.5 | -5.048
1750.5 | 50.5 | -5.048
1750.6 | 50.5 | -5.048
1750.7 | 50.5 | -5.048
1750.8 | 50.5 | -5.048
1750.9 | 50.5 | -5.048
1751 | 50.5 | -5.048
1751.1 | 50.5 | -5.048
1751.2 | 50.5 | -5.048
1751.3 | 50.5 | -5.048
1751.4 | 50.5 | -5.048
1751.5 | 50.5 | -5.048
1751.6 | 50.5 | -5.048
1751.7 | 50.5 | -5.048
1751.8 | 50.5 | -5.048
1751.9 | 50.5 | -5.048
1752 | 50.5 | -5.048
1752.1 | 50.5 | -5.048
1752.2 | 50.5 | -5.048
1752.3 | 50.5 | -5.048
1752.4 | 50.5 | -5.048
1752.5 | 50.5 | -5.048
1752.6 | 50.5 | -5.048
1752.7 | 50.5 | -5.048
1752.8 | 50.5 | -5.048
1752.9 | 50.5 | -5.048
1753 | 50.5 | -5.048
1753.1 | 50.5 | -5.048
1753.2 | 50.5 | -5.048
1753.3 | 50.5 | -5.048
1753.4 | 50.5 | -5.048
1753.5 | 50.5 | -5.048
1753.6 | 50.5 | -5.048
1753.7 | 50.5 | -5.048
1753.8 | 50.5 | -5.048
1753.9 | 50.5 | -5.048
1754 | 50.5 | -5.048
1754.1 | 50.5 | -5.048
1754.2 | 50.5 | -5.048
1754.3 | 50.5 | -5.048
1754.4 | 50.5 | -5.048
1754.5 | 50.5 | -5.048
1754.6 | 50.5 | -5.048
1754.7 | 50.5 | -5.048
1754.8 | 50.5 | -5.048
1754.9 | 50.5 | -5.048
1755 | 50.5 | -5.048
1755.1 | 50.5 | -5.048
1755.2 | 50.5 | -5.048
1755.3 | 50.5 | -5.048
1755.4 | 50.5 | -5.048
1755.5 | 50.5 | -5.048
1755.6 | 50.5 | -5.048
1755.7 | 50.5 | -5.048
1755.8 | 50.5 | -5.048
1755.9 | 50.5 | -5.048
1756 | 50.5 | -5.048
1756.1 | 50.5 | -5.048
1756.2 | 50.5 | -5.048
1756.3 | 50.5 | -5.048
1756.4 | 50.5 | -5.048
1756.5 | 50.5 | -5.048
1756.6 | 50.5 | -5.048
1756.7 | 50.5 | -5.048
1756.8 | 50.5 | -5.048
1756.9 | 50.5 | -5.048
1757 | 50.5 | -5.048
1757.1 | 50.5 | -5.048
1757.2 | 50.5 | -5.048
1757.3 | 50.5 | -5.048
1757.4 | 50.5 | -5.048
1757.5 | 50.5 | -5.048
1757.6 | 50.5 | -5.048
1757.7 | 50.5 | -5.048
1757.8 | 50.5 | -5.048
1757.9 | 50.5 | -5.048
1758 | 50.5 | -5.048
1758.1 | 50.5 | -5.048
1758.2 | 50.5 | -5.048
1758.3 | 50.5 | -5.048
1758.4 | 50.5 | -5.048
1758.5 | 50.5 | -5.048
1758.6 | 50.5 | -5.048
1758.7 | 50.5 | -5.048
1758.8 | 50.5 | -5.048
1758.9 | 50.5 | -5.048
1759 | 50.5 | -5.048
1759.1 | 50.5 | -5.048
1759.2 | 50.5 | -5.048
1759.3 | 50.5 | -5.048
1759.4 | 50.5 | -5.048
1759.5 | 50.5 | -5.048
1759.6 | 50.5 | -5.048
1759.7 | 50.5 | -5.048
1759.8 | 50.5 | -5.048
1759.9 | 50.5 | -5.048
1760 | 50.5 | -5.048
1760.1 | 50.5 | -5.048
1760.2 | 50.5 | -5.048
1760.3 | 50.5 | -5.048
1760.4 | 50.5 | -5.048
1760.5 | 50.5 | -5.048
1760.6 | 50.5 | -5.048
1760.7 | 50.5 | -5.048
1760.8 | 50.5 | -5.048
1760.9 | 50.5 | -5.048
1761 | 50.5 | -5.048
1761.1 | 50.5 | -5.048
1761.2 | 50.5 | -5.048
1761.3 | 50.5 | -5.048
1761.4 | 50.5 | -5.048
1761.5 | 50.5 | -5.048
1761.6 | 50.5 | -5.048
1761.7 | 50.5 | -5.048
1761.8 | 50.5 | -5.048
1761.9 | 50.5 | -5.048
1762 | 50.5 | -5.047
1762.1 | 50.5 | -5.047
1762.2 | 50.5 | -5.047
1762.3 | 50.5 | -5.047
1762.4 | 50.5 | -5.047
1762.5 | 50.5 | -5.047
1762.6 | 50.5 | -5.047
1762.7 | 50.5 | -5.047
1762.8 | 50.5 | -5.048
1762.9 | 50.5 | -5.048
1763 | 50.5 | -5.048
1763.1 | 50.5 | -5.048
1763.2 | 50.5 | -5.048
1763.3 | 50.5 | -5.048
1763.4 | 50.5 | -5.048
1763.5 | 50.5 | -5.048
1763.6 | 50.5 | -5.048
1763.7 | 50.5 | -5.048
1763.8 | 50.5 | -5.048
1763.9 | 50.5 | -5.048
1764 | 50.5 | -5.048
1764.1 | 50.5 | -5.048
1764.2 | 50.5 | -5.047
1764.3 | 50.5 | -5.047
1764.4 | 50.5 | -5.048
1764.5 | 50.5 | -5.048
1764.6 | 50.5 | -5.048
1764.7 | 50.5 | -5.048
1764.8 | 50.5 | -5.048
1764.9 | 50.5 | -5.048
1765 | 50.5 | -5.048
1765.1 | 50.5 | -5.048
1765.2 | 50.5 | -5.048
1765.3 | 50.5 | -5.048
1765.4 | 50.5 | -5.048
1765.5 | 50.5 | -5.048
1765.6 | 50.5 | -5.048
1765.7 | 50.5 | -5.048
1765.8 | 50.5 | -5.048
1765.9 | 50.5 | -5.048
1766 | 50.5 | -5.048
1766.1 | 50.5 | -5.048
1766.2 | 50.5 | -5.048
1766.3 | 50.5 | -5.048
1766.4 | 50.5 | -5.048
1766.5 | 50.5 | -5.048
1766.6 | 50.5 | -5.048
1766.7 | 50.5 | -5.048
1766.8 | 50.5 | -5.048
1766.9 | 50.5 | -5.048
1767 | 50.5 | -5.048
1767.1 | 50.5 | -5.048
1767.2 | 50.5 | -5.048
1767.3 | 50.5 | -5.048
1767.4 | 50.5 | -5.048
1767.5 | 50.5 | -5.048
1767.6 | 50.5 | -5.048
1767.7 | 50.5 | -5.048
1767.8 | 50.5 | -5.048
1767.9 | 50.5 | -5.047
1768 | 50.5 | -5.047
1768.1 | 50.5 | -5.047
1768.2 | 50.5 | -5.047
1768.3 | 50.5 | -5.047
1768.4 | 50.5 | -5.047
1768.5 | 50.5 | -5.047
1768.6 | 50.5 | -5.047
1768.7 | 50.5 | -5.047
1768.8 | 50.5 | -5.047
1768.9 | 50.5 | -5.047
1769 | 50.5 | -5.047
1769.1 | 50.5 | -5.047
1769.2 | 50.5 | -5.047
1769.3 | 50.5 | -5.047
1769.4 | 50.5 | -5.047
1769.5 | 50.5 | -5.047
1769.6 | 50.5 | -5.047
1769.7 | 50.5 | -5.047
1769.8 | 50.5 | -5.047
1769.9 | 50.5 | -5.047
1770 | 50.5 | -5.047
1770.1 | 50.5 | -5.047
1770.2 | 50.5 | -5.048
1770.3 | 50.5 | -5.048
1770.4 | 50.5 | -5.048
1770.5 | 50.5 | -5.048
1770.6 | 50.5 | -5.048
1770.7 | 50.5 | -5.048
1770.8 | 50.5 | -5.048
1770.9 | 50.5 | -5.048
1771 | 50.5 | -5.048
1771.1 | 50.5 | -5.048
1771.2 | 50.5 | -5.048
1771.3 | 50.5 | -5.048
1771.4 | 50.5 | -5.048
1771.5 | 50.5 | -5.048
1771.6 | 50.5 | -5.048
1771.7 | 50.5 | -5.048
1771.8 | 50.5 | -5.048
1771.9 | 50.5 | -5.048
1772 | 50.5 | -5.048
1772.1 | 50.5 | -5.048
1772.2 | 50.5 | -5.048
1772.3 | 50.5 | -5.048
1772.4 | 50.5 | -5.048
1772.5 | 50.5 | -5.048
1772.6 | 50.5 | -5.048
1772.7 | 50.5 | -5.048
1772.8 | 50.5 | -5.048
1772.9 | 50.5 | -5.048
1773 | 50.5 | -5.048
1773.1 | 50.5 | -5.048
1773.2 | 50.5 | -5.048
1773.3 | 50.5 | -5.048
1773.4 | 50.5 | -5.048
1773.5 | 50.5 | -5.048
1773.6 | 50.5 | -5.048
1773.7 | 50.5 | -5.048
1773.8 | 50.5 | -5.048
1773.9 | 50.5 | -5.048
1774 | 50.5 | -5.048
1774.1 | 50.5 | -5.048
1774.2 | 50.5 | -5.048
1774.3 | 50.5 | -5.048
1774.4 | 50.5 | -5.048
1774.5 | 50.5 | -5.048
1774.6 | 50.5 | -5.048
1774.7 | 50.5 | -5.048
1774.8 | 50.5 | -5.048
1774.9 | 50.5 | -5.048
1775 | 50.5 | -5.048
1775.1 | 50.5 | -5.048
1775.2 | 50.5 | -5.048
1775.3 | 50.5 | -5.048
1775.4 | 50.5 | -5.048
1775.5 | 50.5 | -5.048
1775.6 | 50.5 | -5.048
1775.7 | 50.5 | -5.048
1775.8 | 50.5 | -5.048
1775.9 | 50.5 | -5.048
1776 | 50.5 | -5.048
1776.1 | 50.5 | -5.048
1776.2 | 50.5 | -5.048
1776.3 | 50.5 | -5.048
1776.4 | 50.5 | -5.048
1776.5 | 50.5 | -5.048
1776.6 | 50.5 | -5.048
1776.7 | 50.5 | -5.048
1776.8 | 50.5 | -5.048
1776.9 | 50.5 | -5.048
1777 | 50.5 | -5.048
1777.1 | 50.5 | -5.048
1777.2 | 50.5 | -5.048
1777.3 | 50.5 | -5.048
1777.4 | 50.5 | -5.048
1777.5 | 50.5 | -5.048
1777.6 | 50.5 | -5.048
1777.7 | 50.5 | -5.048
1777.8 | 50.5 | -5.048
1777.9 | 50.5 | -5.048
1778 | 50.5 | -5.048
1778.1 | 50.5 | -5.048
1778.2 | 50.5 | -5.048
1778.3 | 50.5 | -5.048
1778.4 | 50.5 | -5.048
1778.5 | 50.5 | -5.048
1778.6 | 50.5 | -5.048
1778.7 | 50.5 | -5.048
1778.8 | 50.5 | -5.048
1778.9 | 50.5 | -5.048
1779 | 50.5 | -5.048
1779.1 | 50.5 | -5.048
1779.2 | 50.5 | -5.048
1779.3 | 50.5 | -5.048
1779.4 | 50.5 | -5.048
1779.5 | 50.5 | -5.048
1779.6 | 50.5 | -5.048
1779.7 | 50.5 | -5.048
1779.8 | 50.5 | -5.048
1779.9 | 50.5 | -5.048
1780 | 50.5 | -5.048
1780.1 | 50.5 | -5.048
1780.2 | 50.5 | -5.048
1780.3 | 50.5 | -5.048
1780.4 | 50.5 | -5.048
1780.5 | 50.5 | -5.048
1780.6 | 50.5 | -5.048
1780.7 | 50.5 | -5.048
1780.8 | 50.5 | -5.048
1780.9 | 50.5 | -5.048
1781 | 50.5 | -5.048
1781.1 | 50.5 | -5.048
1781.2 | 50.5 | -5.048
1781.3 | 50.5 | -5.048
1781.4 | 50.5 | -5.048
1781.5 | 50.5 | -5.048
1781.6 | 50.5 | -5.048
1781.7 | 50.5 | -5.048
1781.8 | 50.5 | -5.048
1781.9 | 50.5 | -5.048
1782 | 50.5 | -5.048
1782.1 | 50.5 | -5.048
1782.2 | 50.5 | -5.048
1782.3 | 50.5 | -5.048
1782.4 | 50.5 | -5.048
1782.5 | 50.5 | -5.048
1782.6 | 50.5 | -5.048
1782.7 | 50.5 | -5.048
1782.8 | 50.5 | -5.048
1782.9 | 50.5 | -5.048
1783 | 50.5 | -5.048
1783.1 | 50.5 | -5.048
1783.2 | 50.5 | -5.048
1783.3 | 50.5 | -5.048
1783.4 | 50.5 | -5.048
1783.5 | 50.5 | -5.048
1783.6 | 50.5 | -5.048
1783.7 | 50.5 | -5.048
1783.8 | 50.5 | -5.048
1783.9 | 50.5 | -5.048
1784 | 50.5 | -5.048
1784.1 | 50.5 | -5.048
1784.2 | 50.5 | -5.048
1784.3 | 50.5 | -5.048
1784.4 | 50.5 | -5.048
1784.5 | 50.5 | -5.048
1784.6 | 50.5 | -5.048
1784.7 | 50.5 | -5.048
1784.8 | 50.5 | -5.048
1784.9 | 50.5 | -5.048
1785 | 50.5 | -5.048
1785.1 | 50.5 | -5.048
1785.2 | 50.5 | -5.048
1785.3 | 50.5 | -5.048
1785.4 | 50.5 | -5.047
1785.5 | 50.5 | -5.047
1785.6 | 50.5 | -5.047
1785.7 | 50.5 | -5.047
1785.8 | 50.5 | -5.047
1785.9 | 50.5 | -5.047
1786 | 50.5 | -5.047
1786.1 | 50.5 | -5.047
1786.2 | 50.5 | -5.047
1786.3 | 50.5 | -5.047
1786.4 | 50.5 | -5.048
1786.5 | 50.5 | -5.048
1786.6 | 50.5 | -5.048
1786.7 | 50.5 | -5.048
1786.8 | 50.5 | -5.048
1786.9 | 50.5 | -5.048
1787 | 50.5 | -5.048
1787.1 | 50.5 | -5.048
1787.2 | 50.5 | -5.048
1787.3 | 50.5 | -5.048
1787.4 | 50.5 | -5.047
1787.5 | 50.5 | -5.047
1787.6 | 50.5 | -5.047
1787.7 | 50.5 | -5.047
1787.8 | 50.5 | -5.047
1787.9 | 50.5 | -5.047
1788 | 50.5 | -5.047
1788.1 | 50.5 | -5.047
1788.2 | 50.5 | -5.047
1788.3 | 50.5 | -5.047
1788.4 | 50.5 | -5.047
1788.5 | 50.5 | -5.047
1788.6 | 50.5 | -5.047
1788.7 | 50.5 | -5.047
1788.8 | 50.5 | -5.047
1788.9 | 50.5 | -5.047
1789 | 50.5 | -5.047
1789.1 | 50.5 | -5.047
1789.2 | 50.5 | -5.047
1789.3 | 50.5 | -5.047
1789.4 | 50.5 | -5.047
1789.5 | 50.5 | -5.047
1789.6 | 50.5 | -5.047
1789.7 | 50.5 | -5.048
1789.8 | 50.5 | -5.048
1789.9 | 50.5 | -5.048
1790 | 50.5 | -5.048
1790.1 | 50.5 | -5.048
1790.2 | 50.5 | -5.048
1790.3 | 50.5 | -5.048
1790.4 | 50.5 | -5.048
1790.5 | 50.5 | -5.048
1790.6 | 50.5 | -5.048
1790.7 | 50.5 | -5.048
1790.8 | 50.5 | -5.048
1790.9 | 50.5 | -5.048
1791 | 50.5 | -5.048
1791.1 | 50.5 | -5.048
1791.2 | 50.5 | -5.048
1791.3 | 50.5 | -5.048
1791.4 | 50.5 | -5.048
1791.5 | 50.5 | -5.048
1791.6 | 50.5 | -5.048
1791.7 | 50.5 | -5.048
1791.8 | 50.5 | -5.048
1791.9 | 50.5 | -5.048
1792 | 50.5 | -5.048
1792.1 | 50.5 | -5.048
1792.2 | 50.5 | -5.047
1792.3 | 50.5 | -5.047
1792.4 | 50.5 | -5.047
1792.5 | 50.5 | -5.047
1792.6 | 50.5 | -5.047
1792.7 | 50.5 | -5.047
1792.8 | 50.5 | -5.047
1792.9 | 50.5 | -5.047
1793 | 50.5 | -5.047
1793.1 | 50.5 | -5.047
1793.2 | 50.5 | -5.047
1793.3 | 50.5 | -5.047
1793.4 | 50.5 | -5.047
1793.5 | 50.5 | -5.047
1793.6 | 50.5 | -5.047
1793.7 | 50.5 | -5.047
1793.8 | 50.5 | -5.047
1793.9 | 50.5 | -5.047
1794 | 50.5 | -5.047
1794.1 | 50.5 | -5.047
1794.2 | 50.5 | -5.047
1794.3 | 50.5 | -5.047
1794.4 | 50.5 | -5.047
1794.5 | 50.5 | -5.047
1794.6 | 50.5 | -5.047
1794.7 | 50.5 | -5.047
1794.8 | 50.5 | -5.047
1794.9 | 50.5 | -5.047
1795 | 50.5 | -5.047
1795.1 | 50.5 | -5.047
1795.2 | 50.5 | -5.047
1795.3 | 50.5 | -5.047
1795.4 | 50.5 | -5.047
1795.5 | 50.5 | -5.047
1795.6 | 50.5 | -5.048
1795.7 | 50.5 | -5.048
1795.8 | 50.5 | -5.048
1795.9 | 50.5 | -5.048
1796 | 50.5 | -5.048
1796.1 | 50.5 | -5.048
1796.2 | 50.5 | -5.048
1796.3 | 50.5 | -5.048
1796.4 | 50.5 | -5.048
1796.5 | 50.5 | -5.048
1796.6 | 50.5 | -5.048
1796.7 | 50.5 | -5.048
1796.8 | 50.5 | -5.048
1796.9 | 50.5 | -5.048
1797 | 50.5 | -5.048
1797.1 | 50.5 | -5.048
1797.2 | 50.5 | -5.048
1797.3 | 50.5 | -5.048
1797.4 | 50.5 | -5.048
1797.5 | 50.5 | -5.048
1797.6 | 50.5 | -5.048
1797.7 | 50.5 | -5.048
1797.8 | 50.5 | -5.048
1797.9 | 50.5 | -5.048
1798 | 50.5 | -5.048
1798.1 | 50.5 | -5.048
1798.2 | 50.5 | -5.048
1798.3 | 50.5 | -5.048
1798.4 | 50.5 | -5.048
1798.5 | 50.5 | -5.048
1798.6 | 50.5 | -5.048
1798.7 | 50.5 | -5.048
1798.8 | 50.5 | -5.048
1798.9 | 50.5 | -5.048
1799 | 50.5 | -5.048
1799.1 | 50.5 | -5.048
1799.2 | 50.5 | -5.048
1799.3 | 50.5 | -5.048
1799.4 | 50.5 | -5.048
1799.5 | 50.5 | -5.048
1799.6 | 50.5 | -5.048
1799.7 | 50.5 | -5.048
1799.8 | 50.5 | -5.048
1799.9 | 50.5 | -5.048
1800 | 50.5 | -5.048
1800.1 | 50.5 | -5.048
1800.2 | 50.5 | -5.048
1800.3 | 50.5 | -5.048
1800.4 | 50.5 | -5.048
1800.5 | 50.5 | -5.048
1800.6 | 50.5 | -5.048
1800.7 | 50.5 | -5.048
1800.8 | 50.5 | -5.048
1800.9 | 50.5 | -5.048
1801 | 50.5 | -5.048
1801.1 | 50.5 | -5.048
1801.2 | 50.5 | -5.048
1801.3 | 50.5 | -5.048
1801.4 | 50.5 | -5.048
1801.5 | 50.5 | -5.048
1801.6 | 50.5 | -5.048
1801.7 | 50.5 | -5.048
1801.8 | 50.5 | -5.048
1801.9 | 50.5 | -5.048
1802 | 50.5 | -5.048
1802.1 | 50.5 | -5.048
1802.2 | 50.5 | -5.048
1802.3 | 50.5 | -5.048
1802.4 | 50.5 | -5.048
1802.5 | 50.5 | -5.048
1802.6 | 50.5 | -5.048
1802.7 | 50.5 | -5.048
1802.8 | 50.5 | -5.048
1802.9 | 50.5 | -5.048
1803 | 50.5 | -5.048
1803.1 | 50.5 | -5.048
1803.2 | 50.5 | -5.048
1803.3 | 50.5 | -5.048
1803.4 | 50.5 | -5.048
1803.5 | 50.5 | -5.048
1803.6 | 50.5 | -5.048
1803.7 | 50.5 | -5.048
1803.8 | 50.5 | -5.048
1803.9 | 50.5 | -5.048
1804 | 50.5 | -5.048
1804.1 | 50.5 | -5.048
1804.2 | 50.5 | -5.048
1804.3 | 50.5 | -5.048
1804.4 | 50.5 | -5.048
1804.5 | 50.5 | -5.048
1804.6 | 50.5 | -5.048
1804.7 | 50.5 | -5.048
1804.8 | 50.5 | -5.048
1804.9 | 50.5 | -5.048
1805 | 50.5 | -5.048
1805.1 | 50.5 | -5.048
1805.2 | 50.5 | -5.048
1805.3 | 50.5 | -5.048
1805.4 | 50.5 | -5.048
1805.5 | 50.5 | -5.048
1805.6 | 50.5 | -5.048
1805.7 | 50.5 | -5.048
1805.8 | 50.5 | -5.048
1805.9 | 50.5 | -5.048
1806 | 50.5 | -5.048
1806.1 | 50.5 | -5.048
1806.2 | 50.5 | -5.048
1806.3 | 50.5 | -5.048
1806.4 | 50.5 | -5.048
1806.5 | 50.5 | -5.048
1806.6 | 50.5 | -5.048
1806.7 | 50.5 | -5.048
1806.8 | 50.5 | -5.048
1806.9 | 50.5 | -5.048
1807 | 50.5 | -5.048
1807.1 | 50.5 | -5.048
1807.2 | 50.5 | -5.048
1807.3 | 50.5 | -5.048
1807.4 | 50.5 | -5.048
1807.5 | 50.5 | -5.048
1807.6 | 50.5 | -5.048
1807.7 | 50.5 | -5.048
1807.8 | 50.5 | -5.048
1807.9 | 50.5 | -5.048
1808 | 50.5 | -5.048
1808.1 | 50.5 | -5.048
1808.2 | 50.5 | -5.048
1808.3 | 50.5 | -5.048
1808.4 | 50.5 | -5.048
1808.5 | 50.5 | -5.048
1808.6 | 50.5 | -5.048
1808.7 | 50.5 | -5.048
1808.8 | 50.5 | -5.048
1808.9 | 50.5 | -5.048
1809 | 50.5 | -5.048
1809.1 | 50.5 | -5.048
1809.2 | 50.5 | -5.048
1809.3 | 50.5 | -5.048
1809.4 | 50.5 | -5.048
1809.5 | 50.5 | -5.048
1809.6 | 50.5 | -5.048
1809.7 | 50.5 | -5.048
1809.8 | 50.5 | -5.047
1809.9 | 50.5 | -5.047
1810 | 50.5 | -5.047
1810.1 | 50.5 | -5.047
1810.2 | 50.5 | -5.047
1810.3 | 50.5 | -5.047
1810.4 | 50.5 | -5.047
1810.5 | 50.5 | -5.047
1810.6 | 50.5 | -5.047
1810.7 | 50.5 | -5.047
1810.8 | 50.5 | -5.047
1810.9 | 50.5 | -5.047
1811 | 50.5 | -5.047
1811.1 | 50.5 | -5.047
1811.2 | 50.5 | -5.047
1811.3 | 50.5 | -5.047
1811.4 | 50.5 | -5.047
1811.5 | 50.5 | -5.047
1811.6 | 50.5 | -5.047
1811.7 | 50.5 | -5.047
1811.8 | 50.5 | -5.047
1811.9 | 50.5 | -5.047
1812 | 50.5 | -5.048
1812.1 | 50.5 | -5.048
1812.2 | 50.5 | -5.048
1812.3 | 50.5 | -5.048
1812.4 | 50.5 | -5.048
1812.5 | 50.5 | -5.048
1812.6 | 50.5 | -5.048
1812.7 | 50.5 | -5.048
1812.8 | 50.5 | -5.048
1812.9 | 50.5 | -5.048
1813 | 50.5 | -5.048
1813.1 | 50.5 | -5.048
1813.2 | 50.5 | -5.048
1813.3 | 50.5 | -5.048
1813.4 | 50.5 | -5.048
1813.5 | 50.5 | -5.048
1813.6 | 50.5 | -5.048
1813.7 | 50.5 | -5.048
1813.8 | 50.5 | -5.048
1813.9 | 50.5 | -5.048
1814 | 50.5 | -5.048
1814.1 | 50.5 | -5.048
1814.2 | 50.5 | -5.048
1814.3 | 50.5 | -5.048
1814.4 | 50.5 | -5.048
1814.5 | 50.5 | -5.048
1814.6 | 50.5 | -5.048
1814.7 | 50.5 | -5.048
1814.8 | 50.5 | -5.048
1814.9 | 50.5 | -5.048
1815 | 50.5 | -5.048
1815.1 | 50.5 | -5.048
1815.2 | 50.5 | -5.048
1815.3 | 50.5 | -5.048
1815.4 | 50.5 | -5.048
1815.5 | 50.5 | -5.048
1815.6 | 50.5 | -5.048
1815.7 | 50.5 | -5.048
1815.8 | 50.5 | -5.048
1815.9 | 50.5 | -5.048
1816 | 50.5 | -5.048
1816.1 | 50.5 | -5.048
1816.2 | 50.5 | -5.048
1816.3 | 50.5 | -5.048
1816.4 | 50.5 | -5.048
1816.5 | 50.5 | -5.048
1816.6 | 50.5 | -5.047
1816.7 | 50.5 | -5.047
1816.8 | 50.5 | -5.047
1816.9 | 50.5 | -5.047
1817 | 50.5 | -5.047
1817.1 | 50.5 | -5.047
1817.2 | 50.5 | -5.047
1817.3 | 50.5 | -5.047
1817.4 | 50.5 | -5.047
1817.5 | 50.5 | -5.047
1817.6 | 50.5 | -5.047
1817.7 | 50.5 | -5.047
1817.8 | 50.5 | -5.047
1817.9 | 50.5 | -5.047
1818 | 50.5 | -5.047
1818.1 | 50.5 | -5.047
1818.2 | 50.5 | -5.047
1818.3 | 50.5 | -5.047
1818.4 | 50.5 | -5.047
1818.5 | 50.5 | -5.047
1818.6 | 50.5 | -5.047
1818.7 | 50.5 | -5.047
1818.8 | 50.5 | -5.047
1818.9 | 50.5 | -5.048
1819 | 50.5 | -5.048
1819.1 | 50.5 | -5.048
1819.2 | 50.5 | -5.048
1819.3 | 50.5 | -5.048
1819.4 | 50.5 | -5.047
1819.5 | 50.5 | -5.047
1819.6 | 50.5 | -5.047
1819.7 | 50.5 | -5.047
1819.8 | 50.5 | -5.047
1819.9 | 50.5 | -5.047
1820 | 50.5 | -5.047
1820.1 | 50.5 | -5.047
1820.2 | 50.5 | -5.047
1820.3 | 50.5 | -5.048
1820.4 | 50.5 | -5.048
1820.5 | 50.5 | -5.048
1820.6 | 50.5 | -5.048
1820.7 | 50.5 | -5.048
1820.8 | 50.5 | -5.048
1820.9 | 50.5 | -5.048
1821 | 50.5 | -5.048
1821.1 | 50.5 | -5.048
1821.2 | 50.5 | -5.048
1821.3 | 50.5 | -5.048
1821.4 | 50.5 | -5.047
1821.5 | 50.5 | -5.047
1821.6 | 50.5 | -5.048
1821.7 | 50.5 | -5.048
1821.8 | 50.5 | -5.048
1821.9 | 50.5 | -5.048
1822 | 50.5 | -5.048
1822.1 | 50.5 | -5.048
1822.2 | 50.5 | -5.048
1822.3 | 50.5 | -5.048
1822.4 | 50.5 | -5.048
1822.5 | 50.5 | -5.048
1822.6 | 50.5 | -5.048
1822.7 | 50.5 | -5.048
1822.8 | 50.5 | -5.048
1822.9 | 50.5 | -5.048
1823 | 50.5 | -5.048
1823.1 | 50.5 | -5.048
1823.2 | 50.5 | -5.048
1823.3 | 50.5 | -5.048
1823.4 | 50.5 | -5.048
1823.5 | 50.5 | -5.048
1823.6 | 50.5 | -5.048
1823.7 | 50.5 | -5.048
1823.8 | 50.5 | -5.047
1823.9 | 50.5 | -5.047
1824 | 50.5 | -5.047
1824.1 | 50.5 | -5.047
1824.2 | 50.5 | -5.047
1824.3 | 50.5 | -5.047
1824.4 | 50.5 | -5.047
1824.5 | 50.5 | -5.047
1824.6 | 50.5 | -5.047
1824.7 | 50.5 | -5.047
1824.8 | 50.5 | -5.048
1824.9 | 50.5 | -5.048
1825 | 50.5 | -5.048
1825.1 | 50.5 | -5.048
1825.2 | 50.5 | -5.048
1825.3 | 50.5 | -5.048
1825.4 | 50.5 | -5.048
1825.5 | 50.5 | -5.048
1825.6 | 50.5 | -5.048
1825.7 | 50.5 | -5.048
1825.8 | 50.5 | -5.048
1825.9 | 50.5 | -5.048
1826 | 50.5 | -5.048
1826.1 | 50.5 | -5.048
1826.2 | 50.5 | -5.048
1826.3 | 50.5 | -5.048
1826.4 | 50.5 | -5.048
1826.5 | 50.5 | -5.048
1826.6 | 50.5 | -5.048
1826.7 | 50.5 | -5.048
1826.8 | 50.5 | -5.048
1826.9 | 50.5 | -5.048
1827 | 50.5 | -5.048
1827.1 | 50.5 | -5.048
1827.2 | 50.5 | -5.048
1827.3 | 50.5 | -5.047
1827.4 | 50.5 | -5.047
1827.5 | 50.5 | -5.047
1827.6 | 50.5 | -5.047
1827.7 | 50.5 | -5.047
1827.8 | 50.5 | -5.047
1827.9 | 50.5 | -5.047
1828 | 50.5 | -5.047
1828.1 | 50.5 | -5.047
1828.2 | 50.5 | -5.047
1828.3 | 50.5 | -5.047
1828.4 | 50.5 | -5.047
1828.5 | 50.5 | -5.047
1828.6 | 50.5 | -5.047
1828.7 | 50.5 | -5.047
1828.8 | 50.5 | -5.047
1828.9 | 50.5 | -5.047
1829 | 50.5 | -5.047
1829.1 | 50.5 | -5.047
1829.2 | 50.5 | -5.047
1829.3 | 50.5 | -5.047
1829.4 | 50.5 | -5.047
1829.5 | 50.5 | -5.047
1829.6 | 50.5 | -5.047
1829.7 | 50.5 | -5.048
1829.8 | 50.5 | -5.048
1829.9 | 50.5 | -5.048
1830 | 50 | -5.048
1830.1 | 50 | -5.048
1830.2 | 50 | -5.048
1830.3 | 50 | -5.048
1830.4 | 50 | -5.048
1830.5 | 50 | -5.048
1830.6 | 50 | -5.048
1830.7 | 50 | -5.048
1830.8 | 50 | -5.048
1830.9 | 50 | -5.048
1831 | 50 | -5.048
1831.1 | 50 | -5.048
1831.2 | 50 | -4.078
1831.3 | 50 | -1.1
1831.4 | 50 | -0.148
1831.5 | 50 | -0.051
1831.6 | 50 | -0.003
1831.7 | 50 | -0.001
1831.8 | 50 | -0.001
1831.9 | 50 | -0.001
1832 | 50 | -0.001
1832.1 | 50 | -0.001
1832.2 | 50 | -0.001
1832.3 | 50 | -0.001
1832.4 | 50 | -0.001
1832.5 | 50 | -0.001
1832.6 | 50 | -0.001
1832.7 | 50 | -0.001
1832.8 | 50 | -0.001
1832.9 | 50 | -0.001
1833 | 50 | -0.001
1833.1 | 50 | -0.001
1833.2 | 50 | -0.001
1833.3 | 50 | -0.002
1833.4 | 50 | -0.002
1833.5 | 50 | -0.003
1833.6 | 50 | -0.003
1833.7 | 50 | -0.004
1833.8 | 50 | -0.004
1833.9 | 50 | -0.004
1834 | 50 | -0.004
1834.1 | 50 | -0.004
1834.2 | 50 | -0.004
1834.3 | 50 | -0.005
1834.4 | 50 | -0.005
1834.5 | 50 | -0.005
1834.6 | 50 | -0.005
1834.7 | 50 | -0.005
1834.8 | 50 | -0.005
1834.9 | 50 | -0.005
1835 | 50 | -0.004
1835.1 | 50 | -0.004
1835.2 | 50 | -0.004
1835.3 | 50 | -0.004
1835.4 | 50 | -0.004
1835.5 | 50 | -0.004
1835.6 | 50 | -0.004
1835.7 | 50 | -0.004
1835.8 | 50 | -0.004
1835.9 | 50 | -0.004
1836 | 50 | -0.004
1836.1 | 50 | -0.003
1836.2 | 50 | -0.001
1836.3 | 50 | -0.001
1836.4 | 50 | -0.001
1836.5 | 50 | -0.001
1836.6 | 50 | -0.001
1836.7 | 50 | -0.001
1836.8 | 50 | -0.002
1836.9 | 50 | -0.002
1837 | 50 | -0.002
1837.1 | 50 | -0.002
1837.2 | 50 | -0.002
1837.3 | 50 | -0.002
1837.4 | 50 | -0.002
1837.5 | 50 | -0.002
1837.6 | 50 | -0.001
1837.7 | 50 | -0.001
1837.8 | 50 | -0.001
1837.9 | 50 | 0
1838 | 50 | -0.001
1838.1 | 50 | -0.001
1838.2 | 50 | 0
1838.3 | 50 | 0
1838.4 | 50 | 0
1838.5 | 50 | 0
1838.6 | 50 | 0
1838.7 | 50 | 0
1838.8 | 50 | 0
1838.9 | 50 | 0
1839 | 50 | 0
1839.1 | 50 | 0
1839.2 | 50 | 0
1839.3 | 50 | 0
1839.4 | 50 | 0
1839.5 | 50 | 0
1839.6 | 50 | 0
1839.7 | 50 | 0
1839.8 | 50 | 0
1839.9 | 50 | 0
1840 | 50 | 0
1840.1 | 50 | 0
1840.2 | 50 | 0
1840.3 | 50 | 0
1840.4 | 50 | 0
1840.5 | 50 | 0
1840.6 | 50 | 0
1840.7 | 50 | 0
1840.8 | 50 | 0
1840.9 | 50 | 0
1841 | 50 | 0
1841.1 | 50 | 0
1841.2 | 50 | 0
1841.3 | 50 | 0
1841.4 | 50 | 0
1841.5 | 50 | 0
1841.6 | 50 | 0
1841.7 | 50 | 0
1841.8 | 50 | 0
1841.9 | 50 | 0
1842 | 50 | 0
1842.1 | 50 | 0
1842.2 | 50 | 0
1842.3 | 50 | 0
1842.4 | 50 | 0
1842.5 | 50 | 0
1842.6 | 50 | 0
1842.7 | 50 | 0
1842.8 | 50 | 0
1842.9 | 50 | 0
1843 | 50 | 0
1843.1 | 50 | 0
1843.2 | 50 | 0
1843.3 | 50 | 0
1843.4 | 50 | 0
1843.5 | 50 | 0
1843.6 | 50 | 0
1843.7 | 50 | 0
1843.8 | 50 | 0
1843.9 | 50 | 0
1844 | 50 | 0
1844.1 | 50 | 0
1844.2 | 50 | 0
1844.3 | 50 | 0
1844.4 | 50 | 0
1844.5 | 50 | 0
1844.6 | 50 | 0
1844.7 | 50 | 0
1844.8 | 50 | 0
1844.9 | 50 | 0
1845 | 50 | 0
1845.1 | 50 | 0
1845.2 | 50 | 0
1845.3 | 50 | 0
1845.4 | 50 | 0
1845.5 | 50 | 0
1845.6 | 50 | 0
1845.7 | 50 | 0
1845.8 | 50 | 0
1845.9 | 50 | 0
1846 | 50 | 0
1846.1 | 50 | 0
1846.2 | 50 | 0
1846.3 | 50 | 0
1846.4 | 50 | 0
1846.5 | 50 | 0
1846.6 | 50 | 0
1846.7 | 50 | 0
1846.8 | 50 | 0
1846.9 | 50 | 0
1847 | 50 | 0
1847.1 | 50 | 0
1847.2 | 50 | 0
1847.3 | 50 | 0
1847.4 | 50 | 0
1847.5 | 50 | 0
1847.6 | 50 | 0
1847.7 | 50 | 0
1847.8 | 50 | 0
1847.9 | 50 | 0
1848 | 50 | 0
1848.1 | 50 | 0
1848.2 | 50 | 0
1848.3 | 50 | 0
1848.4 | 50 | 0
1848.5 | 50 | 0
1848.6 | 50 | 0
1848.7 | 50 | 0
1848.8 | 50 | 0
1848.9 | 50 | 0
1849 | 50 | 0
1849.1 | 50 | 0
1849.2 | 50 | 0
1849.3 | 50 | 0
1849.4 | 50 | 0
1849.5 | 50 | 0
1849.6 | 50 | 0
1849.7 | 50 | 0
1849.8 | 50 | 0
1849.9 | 50 | 0
1850 | 50 | 0
1850.1 | 50 | 0
1850.2 | 50 | 0
1850.3 | 50 | 0
1850.4 | 50 | 0
1850.5 | 50 | 0
1850.6 | 50 | 0
1850.7 | 50 | 0
1850.8 | 50 | 0
1850.9 | 50 | 0
1851 | 50 | 0
1851.1 | 50 | 0
1851.2 | 50 | 0
1851.3 | 50 | 0
1851.4 | 50 | 0
1851.5 | 50 | 0
1851.6 | 50 | 0
1851.7 | 50 | 0
1851.8 | 50 | 0
1851.9 | 50 | 0
1852 | 50 | 0
1852.1 | 50 | 0
1852.2 | 50 | 0
1852.3 | 50 | 0
1852.4 | 50 | 0
1852.5 | 50 | 0
1852.6 | 50 | 0
1852.7 | 50 | 0
1852.8 | 50 | 0
1852.9 | 50 | 0
1853 | 50 | 0
1853.1 | 50 | 0
1853.2 | 50 | 0
1853.3 | 50 | 0
1853.4 | 50 | 0
1853.5 | 50 | 0
1853.6 | 50 | 0
1853.7 | 50 | 0
1853.8 | 50 | 0
1853.9 | 50 | 0
1854 | 50 | 0
1854.1 | 50 | 0
1854.2 | 50 | 0
1854.3 | 50 | 0
1854.4 | 50 | 0
1854.5 | 50 | 0
1854.6 | 50 | 0
1854.7 | 50 | 0
1854.8 | 50 | 0
1854.9 | 50 | 0
1855 | 50 | 0
1855.1 | 50 | 0
1855.2 | 50 | 0
1855.3 | 50 | 0
1855.4 | 50 | 0
1855.5 | 50 | 0
1855.6 | 50 | 0
1855.7 | 50 | 0
1855.8 | 50 | 0
1855.9 | 50 | 0
1856 | 50 | 0
1856.1 | 50 | 0
1856.2 | 50 | 0
1856.3 | 50 | 0
1856.4 | 50 | 0
1856.5 | 50 | 0
1856.6 | 50 | 0
1856.7 | 50 | 0
1856.8 | 50 | 0
1856.9 | 50 | 0
1857 | 50 | 0
1857.1 | 50 | 0
1857.2 | 50 | 0
1857.3 | 50 | 0
1857.4 | 50 | 0
1857.5 | 50 | 0
1857.6 | 50 | 0
1857.7 | 50 | 0
1857.8 | 50 | 0
1857.9 | 50 | 0
1858 | 50 | 0
1858.1 | 50 | 0
1858.2 | 50 | 0
1858.3 | 50 | 0
1858.4 | 50 | 0
1858.5 | 50 | 0
1858.6 | 50 | 0
1858.7 | 50 | 0
1858.8 | 50 | 0
1858.9 | 50 | 0
1859 | 50 | 0
1859.1 | 50 | 0
1859.2 | 50 | 0
1859.3 | 50 | 0
1859.4 | 50 | 0
1859.5 | 50 | 0
1859.6 | 50 | 0
1859.7 | 50 | 0
1859.8 | 50 | 0
1859.9 | 50 | 0
1860 | 50 | 0

## Test 2.1
Time (s) | Frequency (Hz) | Active Power (MW)
0 | 50 | 0.001 | Test 2.1a | Deadband assessment
1 | 50 | 0.001
2 | 50 | 0.001 | pre-Average | 0.001
3 | 50 | 0.001 | (edit range to average 10s before frequency change)
4 | 50 | 0.001
5 | 50 | 0.001
6 | 50 | 0.001 | Frequency Deviation (Hz) | Primary ()
7 | 50 | 0.001 |  | Contracted | Actual | Test ref
8 | 50 | 0.001 | 0.1Hz | 1 | 0.999 | 2.1b
9 | 50 | 0.001 | 0.2Hz | 2 | 2.001 | 2.1c
10 | 50 | 0.001 | 0.3Hz | 3 | 3.017 | Derived from c and d
11 | 50 | 0.001 | 0.4Hz | 4 | 4.033 | Derived from c and d
12 | 50 | 0.001 | 0.6Hz | 5 | 5.049 | 2.1d | Test 1 result | 5.046
13 | 50 | 0.001 | Maximum response occurs at 0.5Hz so the 0.6Hz response value should be consistent with the contracted 0.5Hz value
14 | 50 | 0.001
15 | 50 | 0.001
16 | 50 | 0.001
17 | 50 | 0.001 | Test 2.1e Tolerance Bands
18 | 50 | 0.001 | Maximum Contracted Response |  | 5 | High max response | 5
19 | 50 | 0.001 | Time | Expected % Response | Contracted expected response value | Left % | Right % | Left Band | Right Band
20 | 50 | 0.001 | 152.5 | 100 | 5 | 0 | 5 | 5 | 5.25
21 | 50 | 0.001 | 154.5 | 84 | 4.2 | -0.8 | 21 | 4.16 | 5.25
22 | 50 | 0.001 | 155 | 80 | 4 | -1 | 21 | 3.95 | 5.05
23 | 50 | 0.001 | 157.5 | 60 | 3 | -2 | 21 | 2.9 | 4.05
24 | 50 | 0.001 | 160 | 40 | 2 | -3 | 21 | 1.85 | 3.05
25 | 50 | 0.001 | 162.5 | 20 | 1 | -4 | 21 | 0.8 | 2.05
26 | 50 | 0.001 | 165 | 0 | 0 | -5 | 21 | -0.25 | 1.05
27 | 50 | 0.001 | 167.5 | -20 | -1 | -5 | 20.2 | -1.25 | 0.01
28 | 50 | 0.001 | 170 | -40 | -2 | -5 | 19.3 | -2.25 | -1.035
29 | 50 | 0.001 | 172.5 | -60 | -3 | -5 | 18.4 | -3.25 | -2.08
30 | 49.98 | 0.003 | 175 | -80 | -4 | -5 | 17.6 | -4.25 | -3.12
31 | 49.98 | 0.194 | 177.5 | -100 | -5 | -5 | 16.7 | -5.25 | -4.165
32 | 49.98 | 0.194 | 179.5 | -100 | -5 | -5 | 0 | -5.25 | -5
33 | 49.98 | 0.196
34 | 49.98 | 0.196
35 | 49.98 | 0.196
36 | 49.98 | 0.198
37 | 49.98 | 0.2
38 | 49.98 | 0.2
39 | 49.98 | 0.2
40 | 49.98 | 0.2
41 | 49.98 | 0.201
42 | 49.98 | 0.201
43 | 49.98 | 0.201
44 | 49.98 | 0.201
45 | 49.98 | 0.201
46 | 49.98 | 0.2
47 | 49.98 | 0.2
48 | 49.98 | 0.2
49 | 49.98 | 0.199
50 | 49.98 | 0.199
51 | 49.98 | 0.199
52 | 49.98 | 0.2
53 | 49.98 | 0.199
54 | 49.98 | 0.199
55 | 49.98 | 0.199
56 | 49.98 | 0.199
57 | 49.98 | 0.199
58 | 49.98 | 0.199
59 | 49.98 | 0.199
60 | 49.9 | 0.199
61 | 49.9 | 1.004
62 | 49.9 | 1.004
63 | 49.9 | 1.003
64 | 49.9 | 1.004
65 | 49.9 | 1.004
66 | 49.9 | 1.005
67 | 49.9 | 1.002
68 | 49.9 | 1.001
69 | 49.9 | 1
70 | 49.9 | 1
71 | 49.9 | 1
72 | 49.9 | 1
73 | 49.9 | 1
74 | 49.9 | 1
75 | 49.9 | 1
76 | 49.9 | 1
77 | 49.9 | 1.002
78 | 49.9 | 1.002
79 | 49.9 | 1.001
80 | 49.9 | 1.001
81 | 49.9 | 1.001
82 | 49.9 | 1.002
83 | 49.9 | 1.001
84 | 49.9 | 1.002
85 | 49.9 | 1.002
86 | 49.9 | 1.001
87 | 49.9 | 1.002
88 | 49.9 | 1.002
89 | 49.9 | 1.001
90 | 49.8 | 2.003
91 | 49.8 | 2.003
92 | 49.8 | 2.003
93 | 49.8 | 2.003
94 | 49.8 | 2.003
95 | 49.8 | 2.003
96 | 49.8 | 2.002
97 | 49.8 | 2.002
98 | 49.8 | 2.002
99 | 49.8 | 2.003
100 | 49.8 | 2.003
101 | 49.8 | 2.002
102 | 49.8 | 2.005
103 | 49.8 | 2.005
104 | 49.8 | 2.005
105 | 49.8 | 2.005
106 | 49.8 | 2.005
107 | 49.8 | 2.005
108 | 49.8 | 2.005
109 | 49.8 | 2.005
110 | 49.8 | 2.005
111 | 49.8 | 2.006
112 | 49.8 | 2.006
113 | 49.8 | 2.005
114 | 49.8 | 2.005
115 | 49.8 | 2.006
116 | 49.8 | 2.005
117 | 49.8 | 2.005
118 | 49.8 | 2.005
119 | 49.8 | 2.005
120 | 49.4 | 5.058
121 | 49.4 | 5.049
122 | 49.4 | 5.052
123 | 49.4 | 5.053
124 | 49.4 | 5.049
125 | 49.4 | 5.049
126 | 49.4 | 5.052
127 | 49.4 | 5.052
128 | 49.4 | 5.058
129 | 49.4 | 5.055
130 | 49.4 | 5.055
131 | 49.4 | 5.056
132 | 49.4 | 5.051
133 | 49.4 | 5.05
134 | 49.4 | 5.065
135 | 49.4 | 5.062
136 | 49.4 | 5.06
137 | 49.4 | 5.06
138 | 49.4 | 5.054
139 | 49.4 | 5.063
140 | 49.4 | 5.057
141 | 49.4 | 5.064
142 | 49.4 | 5.066
143 | 49.4 | 5.066
144 | 49.4 | 5.064
145 | 49.4 | 5.057
146 | 49.4 | 5.057
147 | 49.4 | 5.064
148 | 49.4 | 5.066
149 | 49.4 | 5.067
150 | 49.404 | 5.065
151 | 49.444 | 5.06
152 | 49.484 | 5.055
153 | 49.524 | 5.061
154 | 49.564 | 4.673
155 | 49.604 | 4.135
156 | 49.644 | 3.798
157 | 49.684 | 3.367
158 | 49.724 | 2.926
159 | 49.764 | 2.652
160 | 49.804 | 2.178
161 | 49.84 | 1.709
162 | 49.88 | 1.387
163 | 49.924 | 1.092
164 | 49.964 | 0.614
165 | 50.004 | 0.267
166 | 50.044 | -0.082
167 | 50.084 | -0.464
168 | 50.12 | -0.851
169 | 50.164 | -1.288
170 | 50.204 | -1.612
171 | 50.244 | -2.008
172 | 50.284 | -2.419
173 | 50.324 | -2.769
174 | 50.364 | -3.181
175 | 50.404 | -3.524
176 | 50.444 | -3.983
177 | 50.484 | -4.318
178 | 50.524 | -4.749
179 | 50.564 | -4.899
180 | 50.6 | -5.001
181 | 50.6 | -5.081
182 | 50.6 | -5.086
183 | 50.6 | -5.084
184 | 50.6 | -5.072
185 | 50.6 | -5.08
186 | 50.6 | -5.082
187 | 50.6 | -5.078
188 | 50.6 | -5.07
189 | 50.6 | -5.072
190 | 50.6 | -5.074
191 | 50.6 | -5.074
192 | 50.6 | -5.081
193 | 50.6 | -5.069
194 | 50.6 | -5.073
195 | 50.6 | -5.076
196 | 50.6 | -5.078
197 | 50.6 | -5.078
198 | 50.6 | -5.077
199 | 50.6 | -5.075
200 | 50.6 | -5.071
201 | 50.6 | -5.08
202 | 50.6 | -5.071
203 | 50.6 | -5.082
204 | 50.6 | -5.071
205 | 50.6 | -5.069
206 | 50.6 | -5.073
207 | 50.6 | -5.066
208 | 50.6 | -5.066
209 | 50.6 | -5.069
210 | 50 | -5.065
211 | 50 | -0.1
212 | 50 | -0.104
213 | 50 | -0.103
214 | 50 | -0.098
215 | 50 | -0.091
216 | 50 | -0.094
217 | 50 | -0.093
218 | 50 | -0.089
219 | 50 | -0.092
220 | 50 | -0.09
221 | 50 | -0.088
222 | 50 | -0.087
223 | 50 | -0.089
224 | 50 | -0.074
225 | 50 | -0.092
226 | 50 | -0.088
227 | 50 | -0.087
228 | 50 | -0.093
229 | 50 | -0.091
230 | 50 | -0.1
231 | 50 | -0.093
232 | 50 | -0.095
233 | 50 | -0.096
234 | 50 | -0.089
235 | 50 | -0.087
236 | 50 | -0.088
237 | 50 | -0.094
238 | 50 | -0.095
239 | 50 | -0.086
240 | 50 | -0.091

## Test 2.2
Time (s) | Frequency (Hz) | Active Power (MW)
0 | 50 | 0.001 |  | Test 2.1a | Deadband assessment
1 | 50 | 0.001
2 | 50 | 0.001 |  | pre-Average | 0.001
3 | 50 | 0.001 |  | (edit range to average 10s before frequency change)
4 | 50 | 0.001
5 | 50 | 0.001
6 | 50 | 0.001 |  | Frequency Deviation (Hz) | High
7 | 50 | 0.001 |  |  | Contracted | Actual | Test ref
8 | 50 | 0.001 |  | 0.1Hz | -1 | -1.001 | 2.1b
9 | 50 | 0.001 |  | 0.2Hz | -2 | -2.002 | 2.1c
10 | 50 | 0.001 |  | 0.3Hz | -3 | -3.02 | Derived from c and d
11 | 50 | 0.001 |  | 0.4Hz | -4 | -4.038 | Derived from c and d
12 | 50 | 0.001 |  | 0.5Hz | -5 | -5.056 | 2.1d | Test 1 result | -5.046
13 | 50 | 0.001 |  | Maximum response occurs at 0.5Hz so the 0.6Hz response value should be consistent with the contracted 0.5Hz value
14 | 50 | 0.001
15 | 50 | 0.001
16 | 50 | 0.001
17 | 50 | 0.001 |  | Test 2.1e Tolerance Bands
18 | 50 | 0.001 |  | Maximum Contracted Response |  | 5 | High max response | 5
19 | 50 | 0.001 |  | Time | Expected % Response | Contracted expected response value | Left % | Right % | Left Band | Right Band
20 | 50 | 0.001 |  | 152.5 | -100 | -5 | 0 | 5 | -5 | -5.25
21 | 50 | 0.001 |  | 154.5 | -84 | -4.2 | -0.7 | 21 | -4.165 | -5.25
22 | 50 | 0.001 |  | 155 | -80 | -4 | -1 | 21 | -3.95 | -5.05
23 | 50 | 0.001 |  | 157.5 | -60 | -3 | -2 | 21 | -2.9 | -4.05
24 | 50 | 0.001 |  | 160 | -40 | -2 | -3 | 21 | -1.85 | -3.05
25 | 50 | 0.001 |  | 162.5 | -20 | -1 | -4 | 21 | -0.8 | -2.05
26 | 50 | 0.001 |  | 165 | 0 | 0 | -5 | 21 | 0.25 | -1.05
27 | 50 | 0.001 |  | 167.5 | 20 | 1 | 5 | -20.2 | 1.25 | -0.01
28 | 50 | 0.001 |  | 170 | 40 | 2 | 5 | -19.3 | 2.25 | 1.035
29 | 50 | 0.001 |  | 172.5 | 60 | 3 | 5 | -18.5 | 3.25 | 2.075
30 | 50.02 | -0.01 |  | 175 | 80 | 4 | 5 | -17.6 | 4.25 | 3.12
31 | 50.02 | -0.2 |  | 177.5 | 100 | 5 | 5 | -16.7 | 5.25 | 4.165
32 | 50.02 | -0.2 |  | 179.5 | 100 | 5 | 5 | 0 | 5.25 | 5
33 | 50.02 | -0.2
34 | 50.02 | -0.2
35 | 50.02 | -0.2
36 | 50.02 | -0.2
37 | 50.02 | -0.2
38 | 50.02 | -0.2
39 | 50.02 | -0.199
40 | 50.02 | -0.198
41 | 50.02 | -0.198
42 | 50.02 | -0.198
43 | 50.02 | -0.198
44 | 50.02 | -0.199
45 | 50.02 | -0.199
46 | 50.02 | -0.198
47 | 50.02 | -0.198
48 | 50.02 | -0.2
49 | 50.02 | -0.2
50 | 50.02 | -0.2
51 | 50.02 | -0.2
52 | 50.02 | -0.199
53 | 50.02 | -0.199
54 | 50.02 | -0.199
55 | 50.02 | -0.2
56 | 50.02 | -0.2
57 | 50.02 | -0.199
58 | 50.02 | -0.2
59 | 50.02 | -0.2
60 | 50.1 | -0.2
61 | 50.1 | -1
62 | 50.1 | -1.014
63 | 50.1 | -1.016
64 | 50.1 | -1.013
65 | 50.1 | -1.015
66 | 50.1 | -1.014
67 | 50.1 | -1.01
68 | 50.1 | -1.008
69 | 50.1 | -1.005
70 | 50.1 | -1.001
71 | 50.1 | -1.001
72 | 50.1 | -1
73 | 50.1 | -1
74 | 50.1 | -1
75 | 50.1 | -1
76 | 50.1 | -1
77 | 50.1 | -1
78 | 50.1 | -1
79 | 50.1 | -1
80 | 50.1 | -1
81 | 50.1 | -1
82 | 50.1 | -1
83 | 50.1 | -1
84 | 50.1 | -1
85 | 50.1 | -1
86 | 50.1 | -1
87 | 50.1 | -1
88 | 50.1 | -1.002
89 | 50.1 | -1.002
90 | 50.2 | -1.643
91 | 50.2 | -2.03
92 | 50.2 | -2.032
93 | 50.2 | -2.036
94 | 50.2 | -2.03
95 | 50.2 | -2.024
96 | 50.2 | -2.027
97 | 50.2 | -2.025
98 | 50.2 | -2.022
99 | 50.2 | -2.018
100 | 50.2 | -2.014
101 | 50.2 | -2.011
102 | 50.2 | -2.005
103 | 50.2 | -2.005
104 | 50.2 | -2.003
105 | 50.2 | -2.002
106 | 50.2 | -2.001
107 | 50.2 | -2.007
108 | 50.2 | -2.007
109 | 50.2 | -2.007
110 | 50.2 | -2.007
111 | 50.2 | -2.006
112 | 50.2 | -2.002
113 | 50.2 | -2.008
114 | 50.2 | -2.007
115 | 50.2 | -2.007
116 | 50.2 | -2.006
117 | 50.2 | -2.007
118 | 50.2 | -2.007
119 | 50.2 | -2.007
120 | 50.6 | -5.065
121 | 50.6 | -5.065
122 | 50.6 | -5.065
123 | 50.6 | -5.065
124 | 50.6 | -5.075
125 | 50.6 | -5.065
126 | 50.6 | -5.06
127 | 50.6 | -5.065
128 | 50.6 | -5.06
129 | 50.6 | -5.065
130 | 50.6 | -5.065
131 | 50.6 | -5.07
132 | 50.6 | -5.065
133 | 50.6 | -5.065
134 | 50.6 | -5.055
135 | 50.6 | -5.065
136 | 50.6 | -5.065
137 | 50.6 | -5.065
138 | 50.6 | -5.065
139 | 50.6 | -5.065
140 | 50.6 | -5.07
141 | 50.6 | -5.06
142 | 50.6 | -5.07
143 | 50.6 | -5.065
144 | 50.6 | -5.065
145 | 50.6 | -5.065
146 | 50.6 | -5.065
147 | 50.6 | -5.065
148 | 50.6 | -5.065
149 | 50.6 | -5.07
150 | 50.596 | -5.065
151 | 50.556 | -5.06
152 | 50.516 | -5.065
153 | 50.476 | -5.065
154 | 50.436 | -4.695
155 | 50.396 | -4.26
156 | 50.356 | -3.925
157 | 50.316 | -3.45
158 | 50.276 | -3.065
159 | 50.236 | -2.63
160 | 50.196 | -2.245
161 | 50.156 | -1.985
162 | 50.116 | -1.505
163 | 50.076 | -1.145
164 | 50.036 | -0.775
165 | 49.996 | -0.36
166 | 49.956 | -0.095
167 | 49.916 | 0.35
168 | 49.876 | 0.745
169 | 49.836 | 1.1
170 | 49.796 | 1.525
171 | 49.756 | 1.91
172 | 49.716 | 2.36
173 | 49.676 | 2.61
174 | 49.636 | 2.995
175 | 49.596 | 3.53
176 | 49.556 | 3.875
177 | 49.516 | 4.35
178 | 49.476 | 4.725
179 | 49.436 | 5
180 | 49.4 | 5
181 | 49.4 | 5.08
182 | 49.4 | 5.075
183 | 49.4 | 5.065
184 | 49.4 | 5.05
185 | 49.4 | 5.05
186 | 49.4 | 5.05
187 | 49.4 | 5.045
188 | 49.4 | 5.045
189 | 49.4 | 5.035
190 | 49.4 | 5.045
191 | 49.4 | 5.04
192 | 49.4 | 5.045
193 | 49.4 | 5.04
194 | 49.4 | 5.045
195 | 49.4 | 5.045
196 | 49.4 | 5.04
197 | 49.4 | 5.05
198 | 49.4 | 5.05
199 | 49.4 | 5.055
200 | 49.4 | 5.045
201 | 49.4 | 5.045
202 | 49.4 | 5.05
203 | 49.4 | 5.06
204 | 49.4 | 5.05
205 | 49.4 | 5.05
206 | 49.4 | 5.05
207 | 49.4 | 5.045
208 | 49.4 | 5.06
209 | 49.4 | 5.055
210 | 50 | 5.05
211 | 50 | -0.195
212 | 50 | -0.19
213 | 50 | -0.175
214 | 50 | -0.145
215 | 50 | -0.145
216 | 50 | -0.145
217 | 50 | -0.12
218 | 50 | -0.12
219 | 50 | -0.125
220 | 50 | -0.12
221 | 50 | -0.115
222 | 50 | -0.11
223 | 50 | -0.11
224 | 50 | -0.105
225 | 50 | -0.11
226 | 50 | -0.11
227 | 50 | -0.095
228 | 50 | -0.1
229 | 50 | -0.09
230 | 50 | -0.095
231 | 50 | -0.09
232 | 50 | -0.095
233 | 50 | -0.09
234 | 50 | -0.09
235 | 50 | -0.09
236 | 50 | -0.08
237 | 50 | -0.09
238 | 50 | -0.085
239 | 50 | -0.085
240 | 50 | -0.09
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
|  |  | -1764 | -2178

## Test 3
Time (s) | Frequency (Hz) | Active Power (MW) | expected response | Expected response no delay + deadband
0 | 50.074 | -0.005 | -0.74 | -0.74 | Note: Frequency axis reversed.Frequency Axis Range should mirror corresponding active power in response table.
1 | 50.074 | -0.745 | -0.74 | -0.74
2 | 50.072 | -0.76 | -0.72 | -0.72 | 50.015
3 | 50.074 | -0.75 | -0.74 | -0.74 | 50.015
4 | 50.074 | -0.775 | -0.74 | -0.74
5 | 50.072 | -0.76 | -0.72 | -0.72 | 49.985
6 | 50.07 | -0.735 | -0.7 | -0.7 | 49.985
7 | 50.068 | -0.72 | -0.68 | -0.68
8 | 50.065 | -0.69 | -0.65 | -0.65 | 0
9 | 50.062 | -0.67 | -0.62 | -0.62 | 4000
10 | 50.059 | -0.64 | -0.59 | -0.59 | Deadband
11 | 50.056 | -0.605 | -0.56 | -0.56
12 | 50.053 | -0.58 | -0.53 | -0.53
13 | 50.05 | -0.53 | -0.5 | -0.5
14 | 50.05 | -0.5 | -0.5 | -0.5
15 | 50.047 | -0.495 | -0.47 | -0.47
16 | 50.046 | -0.475 | -0.46 | -0.46
17 | 50.044 | -0.47 | -0.44 | -0.44
18 | 50.044 | -0.445 | -0.44 | -0.44
19 | 50.043 | -0.445 | -0.43 | -0.43
20 | 50.042 | -0.43 | -0.42 | -0.42
21 | 50.043 | -0.435 | -0.43 | -0.43
22 | 50.043 | -0.445 | -0.43 | -0.43
23 | 50.043 | -0.455 | -0.43 | -0.43
24 | 50.042 | -0.445 | -0.42 | -0.42
25 | 50.042 | -0.43 | -0.42 | -0.42
26 | 50.043 | -0.435 | -0.43 | -0.43
27 | 50.045 | -0.465 | -0.45 | -0.45
28 | 50.047 | -0.48 | -0.47 | -0.47
29 | 50.047 | -0.475 | -0.47 | -0.47
30 | 50.048 | -0.48 | -0.48 | -0.48
31 | 50.049 | -0.5 | -0.49 | -0.49
32 | 50.05 | -0.505 | -0.5 | -0.5
33 | 50.051 | -0.495 | -0.51 | -0.51
34 | 50.052 | -0.55 | -0.52 | -0.52
35 | 50.054 | -0.555 | -0.54 | -0.54
36 | 50.057 | -0.555 | -0.57 | -0.57
37 | 50.061 | -0.62 | -0.61 | -0.61
38 | 50.064 | -0.64 | -0.64 | -0.64
39 | 50.067 | -0.665 | -0.67 | -0.67
40 | 50.068 | -0.7 | -0.68 | -0.68
41 | 50.07 | -0.7 | -0.7 | -0.7
42 | 50.07 | -0.73 | -0.7 | -0.7
43 | 50.071 | -0.745 | -0.71 | -0.71
44 | 50.072 | -0.745 | -0.72 | -0.72
45 | 50.072 | -0.745 | -0.72 | -0.72
46 | 50.073 | -0.745 | -0.73 | -0.73
47 | 50.073 | -0.75 | -0.73 | -0.73
48 | 50.075 | -0.76 | -0.75 | -0.75
49 | 50.077 | -0.77 | -0.77 | -0.77
50 | 50.077 | -0.795 | -0.77 | -0.77
51 | 50.077 | -0.815 | -0.77 | -0.77
52 | 50.076 | -0.79 | -0.76 | -0.76
53 | 50.073 | -0.78 | -0.73 | -0.73
54 | 50.074 | -0.755 | -0.74 | -0.74
55 | 50.074 | -0.76 | -0.74 | -0.74
56 | 50.073 | -0.77 | -0.73 | -0.73
57 | 50.073 | -0.75 | -0.73 | -0.73
58 | 50.075 | -0.745 | -0.75 | -0.75
59 | 50.076 | -0.765 | -0.76 | -0.76
60 | 50.075 | -0.79 | -0.75 | -0.75
61 | 50.078 | -0.805 | -0.78 | -0.78
62 | 50.079 | -0.81 | -0.79 | -0.79
63 | 50.079 | -0.82 | -0.79 | -0.79
64 | 50.076 | -0.82 | -0.76 | -0.76
65 | 50.075 | -0.79 | -0.75 | -0.75
66 | 50.075 | -0.805 | -0.75 | -0.75
67 | 50.073 | -0.76 | -0.73 | -0.73
68 | 50.073 | -0.745 | -0.73 | -0.73
69 | 50.07 | -0.755 | -0.7 | -0.7
70 | 50.068 | -0.695 | -0.68 | -0.68
71 | 50.065 | -0.705 | -0.65 | -0.65
72 | 50.061 | -0.66 | -0.61 | -0.61
73 | 50.057 | -0.61 | -0.57 | -0.57
74 | 50.058 | -0.595 | -0.58 | -0.58
75 | 50.055 | -0.58 | -0.55 | -0.55
76 | 50.054 | -0.565 | -0.54 | -0.54
77 | 50.054 | -0.58 | -0.54 | -0.54
78 | 50.052 | -0.55 | -0.52 | -0.52
79 | 50.052 | -0.54 | -0.52 | -0.52
80 | 50.051 | -0.565 | -0.51 | -0.51
81 | 50.051 | -0.52 | -0.51 | -0.51
82 | 50.048 | -0.515 | -0.48 | -0.48
83 | 50.046 | -0.495 | -0.46 | -0.46
84 | 50.042 | -0.47 | -0.42 | -0.42
85 | 50.044 | -0.455 | -0.44 | -0.44
86 | 50.043 | -0.455 | -0.43 | -0.43
87 | 50.043 | -0.445 | -0.43 | -0.43
88 | 50.044 | -0.455 | -0.44 | -0.44
89 | 50.044 | -0.455 | -0.44 | -0.44
90 | 50.044 | -0.46 | -0.44 | -0.44
91 | 50.045 | -0.48 | -0.45 | -0.45
92 | 50.047 | -0.48 | -0.47 | -0.47
93 | 50.046 | -0.48 | -0.46 | -0.46
94 | 50.045 | -0.44 | -0.45 | -0.45
95 | 50.046 | -0.455 | -0.46 | -0.46
96 | 50.046 | -0.465 | -0.46 | -0.46
97 | 50.046 | -0.465 | -0.46 | -0.46
98 | 50.046 | -0.465 | -0.46 | -0.46
99 | 50.046 | -0.475 | -0.46 | -0.46
100 | 50.049 | -0.49 | -0.49 | -0.49
101 | 50.052 | -0.505 | -0.52 | -0.52
102 | 50.053 | -0.545 | -0.53 | -0.53
103 | 50.055 | -0.565 | -0.55 | -0.55
104 | 50.058 | -0.58 | -0.58 | -0.58
105 | 50.058 | -0.61 | -0.58 | -0.58
106 | 50.061 | -0.605 | -0.61 | -0.61
107 | 50.061 | -0.625 | -0.61 | -0.61
108 | 50.059 | -0.64 | -0.59 | -0.59
109 | 50.062 | -0.635 | -0.62 | -0.62
110 | 50.062 | -0.645 | -0.62 | -0.62
111 | 50.063 | -0.64 | -0.63 | -0.63
112 | 50.064 | -0.65 | -0.64 | -0.64
113 | 50.064 | -0.65 | -0.64 | -0.64
114 | 50.065 | -0.655 | -0.65 | -0.65
115 | 50.066 | -0.68 | -0.66 | -0.66
116 | 50.068 | -0.695 | -0.68 | -0.68
117 | 50.069 | -0.7 | -0.69 | -0.69
118 | 50.067 | -0.69 | -0.67 | -0.67
119 | 50.068 | -0.685 | -0.68 | -0.68
120 | 50.068 | -0.685 | -0.68 | -0.68
121 | 50.067 | -0.69 | -0.67 | -0.67
122 | 50.067 | -0.685 | -0.67 | -0.67
123 | 50.067 | -0.695 | -0.67 | -0.67
124 | 50.067 | -0.685 | -0.67 | -0.67
125 | 50.065 | -0.7 | -0.65 | -0.65
126 | 50.068 | -0.71 | -0.68 | -0.68
127 | 50.071 | -0.7 | -0.71 | -0.71
128 | 50.073 | -0.76 | -0.73 | -0.73
129 | 50.076 | -0.77 | -0.76 | -0.76
130 | 50.08 | -0.83 | -0.8 | -0.8
131 | 50.08 | -0.82 | -0.8 | -0.8
132 | 50.081 | -0.835 | -0.81 | -0.81
133 | 50.081 | -0.84 | -0.81 | -0.81
134 | 50.081 | -0.845 | -0.81 | -0.81
135 | 50.081 | -0.84 | -0.81 | -0.81
136 | 50.081 | -0.87 | -0.81 | -0.81
137 | 50.082 | -0.85 | -0.82 | -0.82
138 | 50.082 | -0.855 | -0.82 | -0.82
139 | 50.082 | -0.85 | -0.82 | -0.82
140 | 50.082 | -0.85 | -0.82 | -0.82
141 | 50.082 | -0.84 | -0.82 | -0.82
142 | 50.085 | -0.85 | -0.85 | -0.85
143 | 50.085 | -0.88 | -0.85 | -0.85
144 | 50.088 | -0.91 | -0.88 | -0.88
145 | 50.091 | -0.945 | -0.91 | -0.91
146 | 50.094 | -0.97 | -0.94 | -0.94
147 | 50.095 | -1.005 | -0.95 | -0.95
148 | 50.097 | -1.015 | -0.97 | -0.97
149 | 50.098 | -1.03 | -0.98 | -0.98
150 | 50.098 | -1.015 | -0.98 | -0.98
151 | 50.098 | -1.02 | -0.98 | -0.98
152 | 50.099 | -1.005 | -0.99 | -0.99
153 | 50.099 | -1.02 | -0.99 | -0.99
154 | 50.098 | -1.02 | -0.98 | -0.98
155 | 50.097 | -1.01 | -0.97 | -0.97
156 | 50.096 | -0.995 | -0.96 | -0.96
157 | 50.094 | -0.96 | -0.94 | -0.94
158 | 50.094 | -0.96 | -0.94 | -0.94
159 | 50.091 | -0.945 | -0.91 | -0.91
160 | 50.091 | -0.95 | -0.91 | -0.91
161 | 50.088 | -0.9 | -0.88 | -0.88
162 | 50.087 | -0.91 | -0.87 | -0.87
163 | 50.086 | -0.89 | -0.86 | -0.86
164 | 50.086 | -0.89 | -0.86 | -0.86
165 | 50.088 | -0.865 | -0.88 | -0.88
166 | 50.085 | -0.88 | -0.85 | -0.85
167 | 50.086 | -0.865 | -0.86 | -0.86
168 | 50.085 | -0.875 | -0.85 | -0.85
169 | 50.086 | -0.885 | -0.86 | -0.86
170 | 50.084 | -0.875 | -0.84 | -0.84
171 | 50.084 | -0.875 | -0.84 | -0.84
172 | 50.083 | -0.87 | -0.83 | -0.83
173 | 50.083 | -0.85 | -0.83 | -0.83
174 | 50.083 | -0.855 | -0.83 | -0.83
175 | 50.083 | -0.85 | -0.83 | -0.83
176 | 50.083 | -0.84 | -0.83 | -0.83
177 | 50.081 | -0.825 | -0.81 | -0.81
178 | 50.079 | -0.82 | -0.79 | -0.79
179 | 50.078 | -0.8 | -0.78 | -0.78
180 | 50.076 | -0.78 | -0.76 | -0.76
181 | 50.077 | -0.76 | -0.77 | -0.77
182 | 50.078 | -0.82 | -0.78 | -0.78
183 | 50.078 | -0.8 | -0.78 | -0.78
184 | 50.081 | -0.81 | -0.81 | -0.81
185 | 50.08 | -0.83 | -0.8 | -0.8
186 | 50.081 | -0.835 | -0.81 | -0.81
187 | 50.082 | -0.845 | -0.82 | -0.82
188 | 50.084 | -0.855 | -0.84 | -0.84
189 | 50.084 | -0.855 | -0.84 | -0.84
190 | 50.085 | -0.875 | -0.85 | -0.85
191 | 50.085 | -0.865 | -0.85 | -0.85
192 | 50.086 | -0.89 | -0.86 | -0.86
193 | 50.086 | -0.845 | -0.86 | -0.86
194 | 50.085 | -0.89 | -0.85 | -0.85
195 | 50.085 | -0.88 | -0.85 | -0.85
196 | 50.085 | -0.89 | -0.85 | -0.85
197 | 50.082 | -0.865 | -0.82 | -0.82
198 | 50.083 | -0.865 | -0.83 | -0.83
199 | 50.077 | -0.84 | -0.77 | -0.77
200 | 50.076 | -0.795 | -0.76 | -0.76
201 | 50.076 | -0.765 | -0.76 | -0.76
202 | 50.073 | -0.77 | -0.73 | -0.73
203 | 50.071 | -0.745 | -0.71 | -0.71
204 | 50.071 | -0.735 | -0.71 | -0.71
205 | 50.073 | -0.77 | -0.73 | -0.73
206 | 50.073 | -0.775 | -0.73 | -0.73
207 | 50.072 | -0.75 | -0.72 | -0.72
208 | 50.072 | -0.74 | -0.72 | -0.72
209 | 50.073 | -0.77 | -0.73 | -0.73
210 | 50.072 | -0.74 | -0.72 | -0.72
211 | 50.071 | -0.74 | -0.71 | -0.71
212 | 50.071 | -0.735 | -0.71 | -0.71
213 | 50.071 | -0.735 | -0.71 | -0.71
214 | 50.07 | -0.725 | -0.7 | -0.7
215 | 50.071 | -0.705 | -0.71 | -0.71
216 | 50.072 | -0.745 | -0.72 | -0.72
217 | 50.076 | -0.765 | -0.76 | -0.76
218 | 50.077 | -0.795 | -0.77 | -0.77
219 | 50.081 | -0.82 | -0.81 | -0.81
220 | 50.081 | -0.835 | -0.81 | -0.81
221 | 50.086 | -0.88 | -0.86 | -0.86
222 | 50.087 | -0.89 | -0.87 | -0.87
223 | 50.089 | -0.92 | -0.89 | -0.89
224 | 50.094 | -0.95 | -0.94 | -0.94
225 | 50.094 | -0.97 | -0.94 | -0.94
226 | 50.095 | -0.99 | -0.95 | -0.95
227 | 50.098 | -1.01 | -0.98 | -0.98
228 | 50.097 | -0.995 | -0.97 | -0.97
229 | 50.098 | -0.99 | -0.98 | -0.98
230 | 50.098 | -1 | -0.98 | -0.98
231 | 50.099 | -1.01 | -0.99 | -0.99
232 | 50.097 | -1.02 | -0.97 | -0.97
233 | 50.097 | -1 | -0.97 | -0.97
234 | 50.097 | -1 | -0.97 | -0.97
235 | 50.096 | -0.99 | -0.96 | -0.96
236 | 50.095 | -0.995 | -0.95 | -0.95
237 | 50.095 | -0.98 | -0.95 | -0.95
238 | 50.095 | -0.97 | -0.95 | -0.95
239 | 50.094 | -0.92 | -0.94 | -0.94
240 | 50.093 | -0.955 | -0.93 | -0.93
241 | 50.092 | -0.95 | -0.92 | -0.92
242 | 50.092 | -0.95 | -0.92 | -0.92
243 | 50.091 | -0.95 | -0.91 | -0.91
244 | 50.089 | -0.925 | -0.89 | -0.89
245 | 50.086 | -0.915 | -0.86 | -0.86
246 | 50.085 | -0.905 | -0.85 | -0.85
247 | 50.085 | -0.88 | -0.85 | -0.85
248 | 50.083 | -0.875 | -0.83 | -0.83
249 | 50.078 | -0.815 | -0.78 | -0.78
250 | 50.078 | -0.79 | -0.78 | -0.78
251 | 50.077 | -0.795 | -0.77 | -0.77
252 | 50.075 | -0.755 | -0.75 | -0.75
253 | 50.073 | -0.745 | -0.73 | -0.73
254 | 50.07 | -0.755 | -0.7 | -0.7
255 | 50.067 | -0.73 | -0.67 | -0.67
256 | 50.066 | -0.69 | -0.66 | -0.66
257 | 50.063 | -0.66 | -0.63 | -0.63
258 | 50.061 | -0.665 | -0.61 | -0.61
259 | 50.062 | -0.64 | -0.62 | -0.62
260 | 50.062 | -0.63 | -0.62 | -0.62
261 | 50.062 | -0.62 | -0.62 | -0.62
262 | 50.059 | -0.615 | -0.59 | -0.59
263 | 50.059 | -0.61 | -0.59 | -0.59
264 | 50.059 | -0.605 | -0.59 | -0.59
265 | 50.059 | -0.585 | -0.59 | -0.59
266 | 50.059 | -0.62 | -0.59 | -0.59
267 | 50.059 | -0.61 | -0.59 | -0.59
268 | 50.057 | -0.6 | -0.57 | -0.57
269 | 50.059 | -0.59 | -0.59 | -0.59
270 | 50.059 | -0.615 | -0.59 | -0.59
271 | 50.061 | -0.61 | -0.61 | -0.61
272 | 50.063 | -0.615 | -0.63 | -0.63
273 | 50.063 | -0.655 | -0.63 | -0.63
274 | 50.066 | -0.65 | -0.66 | -0.66
275 | 50.065 | -0.675 | -0.65 | -0.65
276 | 50.064 | -0.66 | -0.64 | -0.64
277 | 50.063 | -0.63 | -0.63 | -0.63
278 | 50.061 | -0.65 | -0.61 | -0.61
279 | 50.062 | -0.625 | -0.62 | -0.62
280 | 50.061 | -0.615 | -0.61 | -0.61
281 | 50.062 | -0.625 | -0.62 | -0.62
282 | 50.064 | -0.66 | -0.64 | -0.64
283 | 50.065 | -0.66 | -0.65 | -0.65
284 | 50.069 | -0.705 | -0.69 | -0.69
285 | 50.076 | -0.73 | -0.76 | -0.76
286 | 50.076 | -0.755 | -0.76 | -0.76
287 | 50.081 | -0.815 | -0.81 | -0.81
288 | 50.086 | -0.86 | -0.86 | -0.86
289 | 50.089 | -0.89 | -0.89 | -0.89
290 | 50.091 | -0.915 | -0.91 | -0.91
291 | 50.092 | -0.93 | -0.92 | -0.92
292 | 50.095 | -0.98 | -0.95 | -0.95
293 | 50.096 | -0.98 | -0.96 | -0.96
294 | 50.096 | -1 | -0.96 | -0.96
295 | 50.1 | -1 | -1 | -1
296 | 50.099 | -1.02 | -0.99 | -0.99
297 | 50.099 | -1.03 | -0.99 | -0.99
298 | 50.099 | -1.03 | -0.99 | -0.99
299 | 50.097 | -1.03 | -0.97 | -0.97
300 | 50.097 | -0.995 | -0.97 | -0.97
301 | 50.096 | -0.985 | -0.96 | -0.96
302 | 50.095 | -0.97 | -0.95 | -0.95
303 | 50.096 | -0.995 | -0.96 | -0.96
304 | 50.095 | -0.985 | -0.95 | -0.95
305 | 50.093 | -0.995 | -0.93 | -0.93
306 | 50.094 | -0.97 | -0.94 | -0.94
307 | 50.095 | -0.99 | -0.95 | -0.95
308 | 50.095 | -0.975 | -0.95 | -0.95
309 | 50.096 | -0.99 | -0.96 | -0.96
310 | 50.096 | -0.995 | -0.96 | -0.96
311 | 50.097 | -0.985 | -0.97 | -0.97
312 | 50.099 | -1.015 | -0.99 | -0.99
313 | 50.1 | -1.015 | -1 | -1
314 | 50.101 | -1.055 | -1.01 | -1.01
315 | 50.102 | -1.055 | -1.02 | -1.02
316 | 50.102 | -1.055 | -1.02 | -1.02
317 | 50.101 | -1.045 | -1.01 | -1.01
318 | 50.099 | -1.015 | -0.99 | -0.99
319 | 50.098 | -1.02 | -0.98 | -0.98
320 | 50.097 | -1.03 | -0.97 | -0.97
321 | 50.097 | -1.01 | -0.97 | -0.97
322 | 50.098 | -1.01 | -0.98 | -0.98
323 | 50.098 | -1.03 | -0.98 | -0.98
324 | 50.101 | -1.045 | -1.01 | -1.01
325 | 50.101 | -1.05 | -1.01 | -1.01
326 | 50.105 | -1.055 | -1.05 | -1.05
327 | 50.108 | -1.09 | -1.08 | -1.08
328 | 50.108 | -1.11 | -1.08 | -1.08
329 | 50.108 | -1.12 | -1.08 | -1.08
330 | 50.106 | -1.11 | -1.06 | -1.06
331 | 50.107 | -1.09 | -1.07 | -1.07
332 | 50.105 | -1.07 | -1.05 | -1.05
333 | 50.102 | -1.05 | -1.02 | -1.02
334 | 50.101 | -1.06 | -1.01 | -1.01
335 | 50.098 | -1.055 | -0.98 | -0.98
336 | 50.099 | -1.02 | -0.99 | -0.99
337 | 50.099 | -1.015 | -0.99 | -0.99
338 | 50.099 | -1.02 | -0.99 | -0.99
339 | 50.102 | -1.03 | -1.02 | -1.02
340 | 50.101 | -1.045 | -1.01 | -1.01
341 | 50.102 | -1.02 | -1.02 | -1.02
342 | 50.102 | -1.055 | -1.02 | -1.02
343 | 50.102 | -1.08 | -1.02 | -1.02
344 | 50.103 | -1.06 | -1.03 | -1.03
345 | 50.103 | -1.06 | -1.03 | -1.03
346 | 50.103 | -1.07 | -1.03 | -1.03
347 | 50.103 | -1.055 | -1.03 | -1.03
348 | 50.102 | -1.06 | -1.02 | -1.02
349 | 50.102 | -1.05 | -1.02 | -1.02
350 | 50.103 | -1.065 | -1.03 | -1.03
351 | 50.102 | -1.065 | -1.02 | -1.02
352 | 50.101 | -1.045 | -1.01 | -1.01
353 | 50.1 | -1.055 | -1 | -1
354 | 50.1 | -1.015 | -1 | -1
355 | 50.099 | -1.035 | -0.99 | -0.99
356 | 50.098 | -1.03 | -0.98 | -0.98
357 | 50.095 | -1.01 | -0.95 | -0.95
358 | 50.098 | -1.015 | -0.98 | -0.98
359 | 50.1 | -1.035 | -1 | -1
360 | 50.103 | -1.045 | -1.03 | -1.03
361 | 50.103 | -1.06 | -1.03 | -1.03
362 | 50.106 | -1.06 | -1.06 | -1.06
363 | 50.107 | -1.09 | -1.07 | -1.07
364 | 50.11 | -1.135 | -1.1 | -1.1
365 | 50.112 | -1.15 | -1.12 | -1.12
366 | 50.119 | -1.2 | -1.19 | -1.19
367 | 50.12 | -1.24 | -1.2 | -1.2
368 | 50.124 | -1.25 | -1.24 | -1.24
369 | 50.127 | -1.3 | -1.27 | -1.27
370 | 50.13 | -1.345 | -1.3 | -1.3
371 | 50.131 | -1.345 | -1.31 | -1.31
372 | 50.132 | -1.36 | -1.32 | -1.32
373 | 50.134 | -1.38 | -1.34 | -1.34
374 | 50.136 | -1.395 | -1.36 | -1.36
375 | 50.136 | -1.415 | -1.36 | -1.36
376 | 50.136 | -1.405 | -1.36 | -1.36
377 | 50.137 | -1.415 | -1.37 | -1.37
378 | 50.137 | -1.405 | -1.37 | -1.37
379 | 50.137 | -1.405 | -1.37 | -1.37
380 | 50.14 | -1.46 | -1.4 | -1.4
381 | 50.141 | -1.47 | -1.41 | -1.41
382 | 50.14 | -1.46 | -1.4 | -1.4
383 | 50.139 | -1.42 | -1.39 | -1.39
384 | 50.139 | -1.435 | -1.39 | -1.39
385 | 50.138 | -1.42 | -1.38 | -1.38
386 | 50.136 | -1.39 | -1.36 | -1.36
387 | 50.136 | -1.405 | -1.36 | -1.36
388 | 50.136 | -1.415 | -1.36 | -1.36
389 | 50.133 | -1.395 | -1.33 | -1.33
390 | 50.135 | -1.405 | -1.35 | -1.35
391 | 50.134 | -1.41 | -1.34 | -1.34
392 | 50.131 | -1.34 | -1.31 | -1.31
393 | 50.131 | -1.345 | -1.31 | -1.31
394 | 50.131 | -1.355 | -1.31 | -1.31
395 | 50.132 | -1.36 | -1.32 | -1.32
396 | 50.132 | -1.37 | -1.32 | -1.32
397 | 50.134 | -1.37 | -1.34 | -1.34
398 | 50.132 | -1.36 | -1.32 | -1.32
399 | 50.133 | -1.38 | -1.33 | -1.33
400 | 50.133 | -1.365 | -1.33 | -1.33
401 | 50.136 | -1.395 | -1.36 | -1.36
402 | 50.137 | -1.41 | -1.37 | -1.37
403 | 50.135 | -1.4 | -1.35 | -1.35
404 | 50.136 | -1.4 | -1.36 | -1.36
405 | 50.136 | -1.395 | -1.36 | -1.36
406 | 50.136 | -1.405 | -1.36 | -1.36
407 | 50.137 | -1.405 | -1.37 | -1.37
408 | 50.135 | -1.4 | -1.35 | -1.35
409 | 50.135 | -1.4 | -1.35 | -1.35
410 | 50.134 | -1.385 | -1.34 | -1.34
411 | 50.135 | -1.395 | -1.35 | -1.35
412 | 50.137 | -1.405 | -1.37 | -1.37
413 | 50.136 | -1.415 | -1.36 | -1.36
414 | 50.136 | -1.4 | -1.36 | -1.36
415 | 50.136 | -1.405 | -1.36 | -1.36
416 | 50.134 | -1.4 | -1.34 | -1.34
417 | 50.131 | -1.405 | -1.31 | -1.31
418 | 50.129 | -1.36 | -1.29 | -1.29
419 | 50.128 | -1.36 | -1.28 | -1.28
420 | 50.129 | -1.325 | -1.29 | -1.29
421 | 50.128 | -1.355 | -1.28 | -1.28
422 | 50.125 | -1.305 | -1.25 | -1.25
423 | 50.12 | -1.255 | -1.2 | -1.2
424 | 50.113 | -1.165 | -1.13 | -1.13
425 | 50.107 | -1.135 | -1.07 | -1.07
426 | 50.102 | -1.09 | -1.02 | -1.02
427 | 50.094 | -1.055 | -0.94 | -0.94
428 | 50.091 | -0.985 | -0.91 | -0.91
429 | 50.085 | -0.9 | -0.85 | -0.85
430 | 50.078 | -0.835 | -0.78 | -0.78
431 | 50.074 | -0.79 | -0.74 | -0.74
432 | 50.07 | -0.755 | -0.7 | -0.7
433 | 50.068 | -0.705 | -0.68 | -0.68
434 | 50.067 | -0.7 | -0.67 | -0.67
435 | 50.067 | -0.71 | -0.67 | -0.67
436 | 50.067 | -0.68 | -0.67 | -0.67
437 | 50.071 | -0.7 | -0.71 | -0.71
438 | 50.071 | -0.735 | -0.71 | -0.71
439 | 50.079 | -0.76 | -0.79 | -0.79
440 | 50.078 | -0.795 | -0.78 | -0.78
441 | 50.078 | -0.805 | -0.78 | -0.78
442 | 50.08 | -0.815 | -0.8 | -0.8
443 | 50.081 | -0.82 | -0.81 | -0.81
444 | 50.081 | -0.85 | -0.81 | -0.81
445 | 50.083 | -0.845 | -0.83 | -0.83
446 | 50.08 | -0.83 | -0.8 | -0.8
447 | 50.08 | -0.83 | -0.8 | -0.8
448 | 50.078 | -0.795 | -0.78 | -0.78
449 | 50.076 | -0.795 | -0.76 | -0.76
450 | 50.072 | -0.78 | -0.72 | -0.72
451 | 50.072 | -0.77 | -0.72 | -0.72
452 | 50.07 | -0.735 | -0.7 | -0.7
453 | 50.07 | -0.73 | -0.7 | -0.7
454 | 50.068 | -0.7 | -0.68 | -0.68
455 | 50.064 | -0.66 | -0.64 | -0.64
456 | 50.061 | -0.64 | -0.61 | -0.61
457 | 50.057 | -0.62 | -0.57 | -0.57
458 | 50.055 | -0.565 | -0.55 | -0.55
459 | 50.052 | -0.525 | -0.52 | -0.52
460 | 50.049 | -0.525 | -0.49 | -0.49
461 | 50.049 | -0.515 | -0.49 | -0.49
462 | 50.048 | -0.505 | -0.48 | -0.48
463 | 50.048 | -0.505 | -0.48 | -0.48
464 | 50.047 | -0.505 | -0.47 | -0.47
465 | 50.047 | -0.495 | -0.47 | -0.47
466 | 50.047 | -0.475 | -0.47 | -0.47
467 | 50.046 | -0.47 | -0.46 | -0.46
468 | 50.046 | -0.47 | -0.46 | -0.46
469 | 50.046 | -0.46 | -0.46 | -0.46
470 | 50.046 | -0.48 | -0.46 | -0.46
471 | 50.047 | -0.53 | -0.47 | -0.47
472 | 50.049 | -0.515 | -0.49 | -0.49
473 | 50.048 | -0.505 | -0.48 | -0.48
474 | 50.047 | -0.49 | -0.47 | -0.47
475 | 50.047 | -0.5 | -0.47 | -0.47
476 | 50.047 | -0.47 | -0.47 | -0.47
477 | 50.047 | -0.475 | -0.47 | -0.47
478 | 50.047 | -0.5 | -0.47 | -0.47
479 | 50.046 | -0.485 | -0.46 | -0.46
480 | 50.046 | -0.47 | -0.46 | -0.46
481 | 50.045 | -0.46 | -0.45 | -0.45
482 | 50.045 | -0.5 | -0.45 | -0.45
483 | 50.046 | -0.48 | -0.46 | -0.46
484 | 50.051 | -0.515 | -0.51 | -0.51
485 | 50.058 | -0.575 | -0.58 | -0.58
486 | 50.059 | -0.61 | -0.59 | -0.59
487 | 50.063 | -0.64 | -0.63 | -0.63
488 | 50.063 | -0.645 | -0.63 | -0.63
489 | 50.067 | -0.695 | -0.67 | -0.67
490 | 50.068 | -0.735 | -0.68 | -0.68
491 | 50.071 | -0.735 | -0.71 | -0.71
492 | 50.072 | -0.745 | -0.72 | -0.72
493 | 50.07 | -0.745 | -0.7 | -0.7
494 | 50.07 | -0.72 | -0.7 | -0.7
495 | 50.07 | -0.725 | -0.7 | -0.7
496 | 50.069 | -0.705 | -0.69 | -0.69
497 | 50.068 | -0.69 | -0.68 | -0.68
498 | 50.066 | -0.695 | -0.66 | -0.66
499 | 50.068 | -0.685 | -0.68 | -0.68
500 | 50.071 | -0.725 | -0.71 | -0.71
501 | 50.074 | -0.75 | -0.74 | -0.74
502 | 50.073 | -0.755 | -0.73 | -0.73
503 | 50.074 | -0.765 | -0.74 | -0.74
504 | 50.073 | -0.745 | -0.73 | -0.73
505 | 50.074 | -0.77 | -0.74 | -0.74
506 | 50.074 | -0.745 | -0.74 | -0.74
507 | 50.073 | -0.76 | -0.73 | -0.73
508 | 50.072 | -0.75 | -0.72 | -0.72
509 | 50.071 | -0.73 | -0.71 | -0.71
510 | 50.073 | -0.73 | -0.73 | -0.73
511 | 50.071 | -0.725 | -0.71 | -0.71
512 | 50.07 | -0.725 | -0.7 | -0.7
513 | 50.069 | -0.71 | -0.69 | -0.69
514 | 50.066 | -0.69 | -0.66 | -0.66
515 | 50.065 | -0.68 | -0.65 | -0.65
516 | 50.062 | -0.66 | -0.62 | -0.62
517 | 50.062 | -0.66 | -0.62 | -0.62
518 | 50.062 | -0.64 | -0.62 | -0.62
519 | 50.062 | -0.645 | -0.62 | -0.62
520 | 50.062 | -0.64 | -0.62 | -0.62
521 | 50.063 | -0.635 | -0.63 | -0.63
522 | 50.063 | -0.67 | -0.63 | -0.63
523 | 50.065 | -0.675 | -0.65 | -0.65
524 | 50.068 | -0.69 | -0.68 | -0.68
525 | 50.067 | -0.67 | -0.67 | -0.67
526 | 50.069 | -0.7 | -0.69 | -0.69
527 | 50.068 | -0.705 | -0.68 | -0.68
528 | 50.066 | -0.655 | -0.66 | -0.66
529 | 50.065 | -0.675 | -0.65 | -0.65
530 | 50.065 | -0.69 | -0.65 | -0.65
531 | 50.065 | -0.67 | -0.65 | -0.65
532 | 50.065 | -0.685 | -0.65 | -0.65
533 | 50.064 | -0.675 | -0.64 | -0.64
534 | 50.062 | -0.67 | -0.62 | -0.62
535 | 50.062 | -0.635 | -0.62 | -0.62
536 | 50.062 | -0.635 | -0.62 | -0.62
537 | 50.062 | -0.64 | -0.62 | -0.62
538 | 50.063 | -0.645 | -0.63 | -0.63
539 | 50.06 | -0.65 | -0.6 | -0.6
540 | 50.061 | -0.625 | -0.61 | -0.61
541 | 50.061 | -0.63 | -0.61 | -0.61
542 | 50.062 | -0.625 | -0.62 | -0.62
543 | 50.064 | -0.645 | -0.64 | -0.64
544 | 50.067 | -0.66 | -0.67 | -0.67
545 | 50.067 | -0.69 | -0.67 | -0.67
546 | 50.068 | -0.7 | -0.68 | -0.68
547 | 50.071 | -0.72 | -0.71 | -0.71
548 | 50.071 | -0.73 | -0.71 | -0.71
549 | 50.074 | -0.73 | -0.74 | -0.74
550 | 50.075 | -0.78 | -0.75 | -0.75
551 | 50.077 | -0.77 | -0.77 | -0.77
552 | 50.078 | -0.805 | -0.78 | -0.78
553 | 50.077 | -0.82 | -0.77 | -0.77
554 | 50.077 | -0.825 | -0.77 | -0.77
555 | 50.077 | -0.8 | -0.77 | -0.77
556 | 50.076 | -0.795 | -0.76 | -0.76
557 | 50.075 | -0.78 | -0.75 | -0.75
558 | 50.074 | -0.755 | -0.74 | -0.74
559 | 50.075 | -0.735 | -0.75 | -0.75
560 | 50.076 | -0.735 | -0.76 | -0.76
561 | 50.077 | -0.75 | -0.77 | -0.77
562 | 50.076 | -0.79 | -0.76 | -0.76
563 | 50.079 | -0.82 | -0.79 | -0.79
564 | 50.079 | -0.82 | -0.79 | -0.79
565 | 50.082 | -0.83 | -0.82 | -0.82
566 | 50.082 | -0.84 | -0.82 | -0.82
567 | 50.086 | -0.85 | -0.86 | -0.86
568 | 50.085 | -0.885 | -0.85 | -0.85
569 | 50.078 | -0.855 | -0.78 | -0.78
570 | 50.08 | -0.845 | -0.8 | -0.8
571 | 50.08 | -0.82 | -0.8 | -0.8
572 | 50.078 | -0.8 | -0.78 | -0.78
573 | 50.075 | -0.795 | -0.75 | -0.75
574 | 50.074 | -0.77 | -0.74 | -0.74
575 | 50.072 | -0.74 | -0.72 | -0.72
576 | 50.068 | -0.75 | -0.68 | -0.68
577 | 50.068 | -0.7 | -0.68 | -0.68
578 | 50.065 | -0.67 | -0.65 | -0.65
579 | 50.067 | -0.695 | -0.67 | -0.67
580 | 50.07 | -0.695 | -0.7 | -0.7
581 | 50.07 | -0.725 | -0.7 | -0.7
582 | 50.072 | -0.745 | -0.72 | -0.72
583 | 50.073 | -0.75 | -0.73 | -0.73
584 | 50.074 | -0.75 | -0.74 | -0.74
585 | 50.076 | -0.765 | -0.76 | -0.76
586 | 50.077 | -0.78 | -0.77 | -0.77
587 | 50.078 | -0.85 | -0.78 | -0.78
588 | 50.078 | -0.805 | -0.78 | -0.78
589 | 50.079 | -0.815 | -0.79 | -0.79
590 | 50.079 | -0.83 | -0.79 | -0.79
591 | 50.08 | -0.83 | -0.8 | -0.8
592 | 50.078 | -0.82 | -0.78 | -0.78
593 | 50.082 | -0.855 | -0.82 | -0.82
594 | 50.081 | -0.82 | -0.81 | -0.81
595 | 50.083 | -0.86 | -0.83 | -0.83
596 | 50.083 | -0.865 | -0.83 | -0.83
597 | 50.082 | -0.83 | -0.82 | -0.82
598 | 50.079 | -0.83 | -0.79 | -0.79
599 | 50.077 | -0.805 | -0.77 | -0.77
600 | 50.075 | -0.8 | -0.75 | -0.75
601 | 50.074 | -0.775 | -0.74 | -0.74
602 | 50.07 | -0.745 | -0.7 | -0.7
603 | 50.068 | -0.72 | -0.68 | -0.68
604 | 50.066 | -0.695 | -0.66 | -0.66
605 | 50.066 | -0.655 | -0.66 | -0.66
606 | 50.063 | -0.64 | -0.63 | -0.63
607 | 50.063 | -0.66 | -0.63 | -0.63
608 | 50.061 | -0.645 | -0.61 | -0.61
609 | 50.06 | -0.635 | -0.6 | -0.6
610 | 50.057 | -0.6 | -0.57 | -0.57
611 | 50.057 | -0.58 | -0.57 | -0.57
612 | 50.057 | -0.585 | -0.57 | -0.57
613 | 50.055 | -0.585 | -0.55 | -0.55
614 | 50.053 | -0.56 | -0.53 | -0.53
615 | 50.05 | -0.53 | -0.5 | -0.5
616 | 50.047 | -0.52 | -0.47 | -0.47
617 | 50.047 | -0.485 | -0.47 | -0.47
618 | 50.045 | -0.455 | -0.45 | -0.45
619 | 50.045 | -0.465 | -0.45 | -0.45
620 | 50.045 | -0.485 | -0.45 | -0.45
621 | 50.048 | -0.495 | -0.48 | -0.48
622 | 50.049 | -0.49 | -0.49 | -0.49
623 | 50.049 | -0.5 | -0.49 | -0.49
624 | 50.051 | -0.53 | -0.51 | -0.51
625 | 50.052 | -0.515 | -0.52 | -0.52
626 | 50.056 | -0.58 | -0.56 | -0.56
627 | 50.057 | -0.575 | -0.57 | -0.57
628 | 50.059 | -0.59 | -0.59 | -0.59
629 | 50.06 | -0.605 | -0.6 | -0.6
630 | 50.064 | -0.63 | -0.64 | -0.64
631 | 50.062 | -0.64 | -0.62 | -0.62
632 | 50.063 | -0.66 | -0.63 | -0.63
633 | 50.063 | -0.65 | -0.63 | -0.63
634 | 50.062 | -0.655 | -0.62 | -0.62
635 | 50.061 | -0.635 | -0.61 | -0.61
636 | 50.059 | -0.615 | -0.59 | -0.59
637 | 50.057 | -0.59 | -0.57 | -0.57
638 | 50.055 | -0.59 | -0.55 | -0.55
639 | 50.052 | -0.54 | -0.52 | -0.52
640 | 50.051 | -0.54 | -0.51 | -0.51
641 | 50.048 | -0.505 | -0.48 | -0.48
642 | 50.048 | -0.495 | -0.48 | -0.48
643 | 50.047 | -0.475 | -0.47 | -0.47
644 | 50.047 | -0.48 | -0.47 | -0.47
645 | 50.048 | -0.485 | -0.48 | -0.48
646 | 50.048 | -0.485 | -0.48 | -0.48
647 | 50.049 | -0.505 | -0.49 | -0.49
648 | 50.046 | -0.505 | -0.46 | -0.46
649 | 50.047 | -0.485 | -0.47 | -0.47
650 | 50.045 | -0.47 | -0.45 | -0.45
651 | 50.044 | -0.48 | -0.44 | -0.44
652 | 50.041 | -0.46 | -0.41 | -0.41
653 | 50.041 | -0.415 | -0.41 | -0.41
654 | 50.04 | -0.41 | -0.4 | -0.4
655 | 50.038 | -0.41 | -0.38 | -0.38
656 | 50.041 | -0.395 | -0.41 | -0.41
657 | 50.037 | -0.385 | -0.37 | -0.37
658 | 50.037 | -0.37 | -0.37 | -0.37
659 | 50.034 | -0.35 | -0.34 | -0.34
660 | 50.033 | -0.325 | -0.33 | -0.33
661 | 50.034 | -0.37 | -0.34 | -0.34
662 | 50.037 | -0.35 | -0.37 | -0.37
663 | 50.034 | -0.35 | -0.34 | -0.34
664 | 50.032 | -0.35 | -0.32 | -0.32
665 | 50.033 | -0.305 | -0.33 | -0.33
666 | 50.029 | -0.305 | -0.29 | -0.29
667 | 50.028 | -0.265 | -0.28 | -0.28
668 | 50.028 | -0.275 | -0.28 | -0.28
669 | 50.027 | -0.265 | -0.27 | -0.27
670 | 50.029 | -0.295 | -0.29 | -0.29
671 | 50.03 | -0.31 | -0.3 | -0.3
672 | 50.03 | -0.315 | -0.3 | -0.3
673 | 50.031 | -0.32 | -0.31 | -0.31
674 | 50.032 | -0.32 | -0.32 | -0.32
675 | 50.034 | -0.365 | -0.34 | -0.34
676 | 50.034 | -0.36 | -0.34 | -0.34
677 | 50.036 | -0.37 | -0.36 | -0.36
678 | 50.041 | -0.4 | -0.41 | -0.41
679 | 50.04 | -0.42 | -0.4 | -0.4
680 | 50.044 | -0.43 | -0.44 | -0.44
681 | 50.045 | -0.46 | -0.45 | -0.45
682 | 50.049 | -0.48 | -0.49 | -0.49
683 | 50.048 | -0.53 | -0.48 | -0.48
684 | 50.05 | -0.53 | -0.5 | -0.5
685 | 50.052 | -0.525 | -0.52 | -0.52
686 | 50.052 | -0.545 | -0.52 | -0.52
687 | 50.051 | -0.53 | -0.51 | -0.51
688 | 50.052 | -0.525 | -0.52 | -0.52
689 | 50.055 | -0.525 | -0.55 | -0.55
690 | 50.053 | -0.54 | -0.53 | -0.53
691 | 50.053 | -0.55 | -0.53 | -0.53
692 | 50.053 | -0.55 | -0.53 | -0.53
693 | 50.054 | -0.56 | -0.54 | -0.54
694 | 50.057 | -0.55 | -0.57 | -0.57
695 | 50.058 | -0.575 | -0.58 | -0.58
696 | 50.058 | -0.59 | -0.58 | -0.58
697 | 50.058 | -0.6 | -0.58 | -0.58
698 | 50.059 | -0.59 | -0.59 | -0.59
699 | 50.055 | -0.61 | -0.55 | -0.55
700 | 50.055 | -0.59 | -0.55 | -0.55
701 | 50.055 | -0.59 | -0.55 | -0.55
702 | 50.056 | -0.59 | -0.56 | -0.56
703 | 50.056 | -0.59 | -0.56 | -0.56
704 | 50.056 | -0.58 | -0.56 | -0.56
705 | 50.054 | -0.53 | -0.54 | -0.54
706 | 50.052 | -0.58 | -0.52 | -0.52
707 | 50.053 | -0.545 | -0.53 | -0.53
708 | 50.052 | -0.55 | -0.52 | -0.52
709 | 50.052 | -0.525 | -0.52 | -0.52
710 | 50.05 | -0.505 | -0.5 | -0.5
711 | 50.047 | -0.51 | -0.47 | -0.47
712 | 50.048 | -0.48 | -0.48 | -0.48
713 | 50.048 | -0.49 | -0.48 | -0.48
714 | 50.048 | -0.48 | -0.48 | -0.48
715 | 50.054 | -0.495 | -0.54 | -0.54
716 | 50.051 | -0.515 | -0.51 | -0.51
717 | 50.054 | -0.54 | -0.54 | -0.54
718 | 50.059 | -0.565 | -0.59 | -0.59
719 | 50.061 | -0.605 | -0.61 | -0.61
720 | 50.065 | -0.665 | -0.65 | -0.65
721 | 50.075 | -0.705 | -0.75 | -0.75
722 | 50.079 | -0.775 | -0.79 | -0.79
723 | 50.084 | -0.865 | -0.84 | -0.84
724 | 50.093 | -0.9 | -0.93 | -0.93
725 | 50.094 | -0.925 | -0.94 | -0.94
726 | 50.096 | -1 | -0.96 | -0.96
727 | 50.098 | -1.005 | -0.98 | -0.98
728 | 50.098 | -0.98 | -0.98 | -0.98
729 | 50.095 | -1 | -0.95 | -0.95
730 | 50.093 | -0.985 | -0.93 | -0.93
731 | 50.093 | -0.97 | -0.93 | -0.93
732 | 50.093 | -0.96 | -0.93 | -0.93
733 | 50.093 | -0.96 | -0.93 | -0.93
734 | 50.092 | -0.95 | -0.92 | -0.92
735 | 50.095 | -0.965 | -0.95 | -0.95
736 | 50.097 | -0.985 | -0.97 | -0.97
737 | 50.096 | -1.015 | -0.96 | -0.96
738 | 50.1 | -1.02 | -1 | -1
739 | 50.1 | -1.035 | -1 | -1
740 | 50.101 | -1.06 | -1.01 | -1.01
741 | 50.103 | -1.06 | -1.03 | -1.03
742 | 50.108 | -1.08 | -1.08 | -1.08
743 | 50.11 | -1.11 | -1.1 | -1.1
744 | 50.111 | -1.15 | -1.11 | -1.11
745 | 50.112 | -1.165 | -1.12 | -1.12
746 | 50.112 | -1.16 | -1.12 | -1.12
747 | 50.114 | -1.14 | -1.14 | -1.14
748 | 50.11 | -1.13 | -1.1 | -1.1
749 | 50.105 | -1.095 | -1.05 | -1.05
750 | 50.103 | -1.06 | -1.03 | -1.03
751 | 50.1 | -1.05 | -1 | -1
752 | 50.099 | -1.03 | -0.99 | -0.99
753 | 50.095 | -1.015 | -0.95 | -0.95
754 | 50.093 | -0.97 | -0.93 | -0.93
755 | 50.087 | -0.925 | -0.87 | -0.87
756 | 50.082 | -0.89 | -0.82 | -0.82
757 | 50.08 | -0.825 | -0.8 | -0.8
758 | 50.076 | -0.79 | -0.76 | -0.76
759 | 50.07 | -0.76 | -0.7 | -0.7
760 | 50.066 | -0.695 | -0.66 | -0.66
761 | 50.062 | -0.64 | -0.62 | -0.62
762 | 50.057 | -0.62 | -0.57 | -0.57
763 | 50.056 | -0.58 | -0.56 | -0.56
764 | 50.051 | -0.545 | -0.51 | -0.51
765 | 50.05 | -0.52 | -0.5 | -0.5
766 | 50.047 | -0.43 | -0.47 | -0.47
767 | 50.045 | -0.46 | -0.45 | -0.45
768 | 50.044 | -0.48 | -0.44 | -0.44
769 | 50.043 | -0.445 | -0.43 | -0.43
770 | 50.04 | -0.445 | -0.4 | -0.4
771 | 50.038 | -0.415 | -0.38 | -0.38
772 | 50.038 | -0.405 | -0.38 | -0.38
773 | 50.035 | -0.38 | -0.35 | -0.35
774 | 50.035 | -0.355 | -0.35 | -0.35
775 | 50.034 | -0.355 | -0.34 | -0.34
776 | 50.034 | -0.35 | -0.34 | -0.34
777 | 50.033 | -0.36 | -0.33 | -0.33
778 | 50.03 | -0.345 | -0.3 | -0.3
779 | 50.034 | -0.33 | -0.34 | -0.34
780 | 50.035 | -0.335 | -0.35 | -0.35
781 | 50.033 | -0.335 | -0.33 | -0.33
782 | 50.032 | -0.335 | -0.32 | -0.32
783 | 50.031 | -0.295 | -0.31 | -0.31
784 | 50.031 | -0.31 | -0.31 | -0.31
785 | 50.031 | -0.33 | -0.31 | -0.31
786 | 50.032 | -0.33 | -0.32 | -0.32
787 | 50.032 | -0.335 | -0.32 | -0.32
788 | 50.033 | -0.33 | -0.33 | -0.33
789 | 50.034 | -0.36 | -0.34 | -0.34
790 | 50.034 | -0.345 | -0.34 | -0.34
791 | 50.034 | -0.335 | -0.34 | -0.34
792 | 50.035 | -0.4 | -0.35 | -0.35
793 | 50.036 | -0.37 | -0.36 | -0.36
794 | 50.038 | -0.405 | -0.38 | -0.38
795 | 50.043 | -0.415 | -0.43 | -0.43
796 | 50.043 | -0.455 | -0.43 | -0.43
797 | 50.047 | -0.46 | -0.47 | -0.47
798 | 50.047 | -0.475 | -0.47 | -0.47
799 | 50.048 | -0.495 | -0.48 | -0.48
800 | 50.049 | -0.505 | -0.49 | -0.49
801 | 50.053 | -0.505 | -0.53 | -0.53
802 | 50.052 | -0.55 | -0.52 | -0.52
803 | 50.055 | -0.59 | -0.55 | -0.55
804 | 50.056 | -0.565 | -0.56 | -0.56
805 | 50.056 | -0.575 | -0.56 | -0.56
806 | 50.058 | -0.59 | -0.58 | -0.58
807 | 50.057 | -0.575 | -0.57 | -0.57
808 | 50.057 | -0.59 | -0.57 | -0.57
809 | 50.057 | -0.575 | -0.57 | -0.57
810 | 50.057 | -0.59 | -0.57 | -0.57
811 | 50.059 | -0.61 | -0.59 | -0.59
812 | 50.058 | -0.605 | -0.58 | -0.58
813 | 50.058 | -0.565 | -0.58 | -0.58
814 | 50.057 | -0.575 | -0.57 | -0.57
815 | 50.057 | -0.59 | -0.57 | -0.57
816 | 50.057 | -0.625 | -0.57 | -0.57
817 | 50.06 | -0.635 | -0.6 | -0.6
818 | 50.058 | -0.6 | -0.58 | -0.58
819 | 50.059 | -0.6 | -0.59 | -0.59
820 | 50.062 | -0.61 | -0.62 | -0.62
821 | 50.063 | -0.64 | -0.63 | -0.63
822 | 50.067 | -0.655 | -0.67 | -0.67
823 | 50.068 | -0.7 | -0.68 | -0.68
824 | 50.068 | -0.725 | -0.68 | -0.68
825 | 50.07 | -0.73 | -0.7 | -0.7
826 | 50.07 | -0.71 | -0.7 | -0.7
827 | 50.075 | -0.735 | -0.75 | -0.75
828 | 50.073 | -0.745 | -0.73 | -0.73
829 | 50.076 | -0.755 | -0.76 | -0.76
830 | 50.077 | -0.79 | -0.77 | -0.77
831 | 50.078 | -0.805 | -0.78 | -0.78
832 | 50.079 | -0.83 | -0.79 | -0.79
833 | 50.08 | -0.82 | -0.8 | -0.8
834 | 50.083 | -0.835 | -0.83 | -0.83
835 | 50.082 | -0.85 | -0.82 | -0.82
836 | 50.083 | -0.855 | -0.83 | -0.83
837 | 50.085 | -0.86 | -0.85 | -0.85
838 | 50.084 | -0.88 | -0.84 | -0.84
839 | 50.084 | -0.865 | -0.84 | -0.84
840 | 50.086 | -0.89 | -0.86 | -0.86
841 | 50.089 | -0.88 | -0.89 | -0.89
842 | 50.091 | -0.925 | -0.91 | -0.91
843 | 50.093 | -0.94 | -0.93 | -0.93
844 | 50.095 | -0.96 | -0.95 | -0.95
845 | 50.097 | -0.99 | -0.97 | -0.97
846 | 50.101 | -1 | -1.01 | -1.01
847 | 50.1 | -1.035 | -1 | -1
848 | 50.101 | -1.045 | -1.01 | -1.01
849 | 50.099 | -1.055 | -0.99 | -0.99
850 | 50.099 | -1.005 | -0.99 | -0.99
851 | 50.101 | -1.01 | -1.01 | -1.01
852 | 50.098 | -1.015 | -0.98 | -0.98
853 | 50.097 | -1.01 | -0.97 | -0.97
854 | 50.096 | -1.005 | -0.96 | -0.96
855 | 50.096 | -0.985 | -0.96 | -0.96
856 | 50.094 | -0.985 | -0.94 | -0.94
857 | 50.091 | -0.98 | -0.91 | -0.91
858 | 50.091 | -0.95 | -0.91 | -0.91
859 | 50.09 | -0.95 | -0.9 | -0.9
860 | 50.089 | -0.915 | -0.89 | -0.89
861 | 50.087 | -0.9 | -0.87 | -0.87
862 | 50.084 | -0.88 | -0.84 | -0.84
863 | 50.082 | -0.865 | -0.82 | -0.82
864 | 50.081 | -0.85 | -0.81 | -0.81
865 | 50.081 | -0.85 | -0.81 | -0.81
866 | 50.08 | -0.83 | -0.8 | -0.8
867 | 50.079 | -0.82 | -0.79 | -0.79
868 | 50.079 | -0.805 | -0.79 | -0.79
869 | 50.082 | -0.82 | -0.82 | -0.82
870 | 50.082 | -0.805 | -0.82 | -0.82
871 | 50.081 | -0.84 | -0.81 | -0.81
872 | 50.081 | -0.83 | -0.81 | -0.81
873 | 50.08 | -0.825 | -0.8 | -0.8
874 | 50.08 | -0.815 | -0.8 | -0.8
875 | 50.079 | -0.815 | -0.79 | -0.79
876 | 50.079 | -0.83 | -0.79 | -0.79
877 | 50.079 | -0.83 | -0.79 | -0.79
878 | 50.08 | -0.84 | -0.8 | -0.8
879 | 50.079 | -0.815 | -0.79 | -0.79
880 | 50.078 | -0.815 | -0.78 | -0.78
881 | 50.075 | -0.805 | -0.75 | -0.75
882 | 50.076 | -0.78 | -0.76 | -0.76
883 | 50.076 | -0.77 | -0.76 | -0.76
884 | 50.075 | -0.795 | -0.75 | -0.75
885 | 50.074 | -0.775 | -0.74 | -0.74
886 | 50.073 | -0.77 | -0.73 | -0.73
887 | 50.072 | -0.755 | -0.72 | -0.72
888 | 50.071 | -0.735 | -0.71 | -0.71
889 | 50.071 | -0.74 | -0.71 | -0.71
890 | 50.07 | -0.73 | -0.7 | -0.7
891 | 50.069 | -0.73 | -0.69 | -0.69
892 | 50.069 | -0.72 | -0.69 | -0.69
893 | 50.068 | -0.735 | -0.68 | -0.68
894 | 50.069 | -0.72 | -0.69 | -0.69
895 | 50.068 | -0.7 | -0.68 | -0.68
896 | 50.068 | -0.695 | -0.68 | -0.68
897 | 50.07 | -0.685 | -0.7 | -0.7
898 | 50.068 | -0.695 | -0.68 | -0.68
899 | 50.068 | -0.7 | -0.68 | -0.68
900 | 50.068 | -0.71 | -0.68 | -0.68
901 | 50.069 | -0.71 | -0.69 | -0.69
902 | 50.072 | -0.715 | -0.72 | -0.72
903 | 50.074 | -0.77 | -0.74 | -0.74
904 | 50.073 | -0.735 | -0.73 | -0.73
905 | 50.075 | -0.76 | -0.75 | -0.75
906 | 50.074 | -0.78 | -0.74 | -0.74
907 | 50.073 | -0.76 | -0.73 | -0.73
908 | 50.073 | -0.76 | -0.73 | -0.73
909 | 50.071 | -0.715 | -0.71 | -0.71
910 | 50.069 | -0.73 | -0.69 | -0.69
911 | 50.07 | -0.72 | -0.7 | -0.7
912 | 50.073 | -0.735 | -0.73 | -0.73
913 | 50.072 | -0.75 | -0.72 | -0.72
914 | 50.07 | -0.73 | -0.7 | -0.7
915 | 50.068 | -0.735 | -0.68 | -0.68
916 | 50.069 | -0.7 | -0.69 | -0.69
917 | 50.069 | -0.72 | -0.69 | -0.69
918 | 50.069 | -0.685 | -0.69 | -0.69
919 | 50.065 | -0.69 | -0.65 | -0.65
920 | 50.062 | -0.685 | -0.62 | -0.62
921 | 50.06 | -0.64 | -0.6 | -0.6
922 | 50.057 | -0.615 | -0.57 | -0.57
923 | 50.056 | -0.545 | -0.56 | -0.56
924 | 50.054 | -0.53 | -0.54 | -0.54
925 | 50.054 | -0.545 | -0.54 | -0.54
926 | 50.056 | -0.545 | -0.56 | -0.56
927 | 50.056 | -0.575 | -0.56 | -0.56
928 | 50.057 | -0.605 | -0.57 | -0.57
929 | 50.059 | -0.6 | -0.59 | -0.59
930 | 50.063 | -0.63 | -0.63 | -0.63
931 | 50.065 | -0.66 | -0.65 | -0.65
932 | 50.067 | -0.675 | -0.67 | -0.67
933 | 50.067 | -0.685 | -0.67 | -0.67
934 | 50.072 | -0.695 | -0.72 | -0.72
935 | 50.073 | -0.73 | -0.73 | -0.73
936 | 50.073 | -0.755 | -0.73 | -0.73
937 | 50.075 | -0.76 | -0.75 | -0.75
938 | 50.076 | -0.78 | -0.76 | -0.76
939 | 50.079 | -0.785 | -0.79 | -0.79
940 | 50.079 | -0.8 | -0.79 | -0.79
941 | 50.079 | -0.805 | -0.79 | -0.79
942 | 50.079 | -0.81 | -0.79 | -0.79
943 | 50.079 | -0.82 | -0.79 | -0.79
944 | 50.079 | -0.805 | -0.79 | -0.79
945 | 50.08 | -0.82 | -0.8 | -0.8
946 | 50.08 | -0.825 | -0.8 | -0.8
947 | 50.081 | -0.855 | -0.81 | -0.81
948 | 50.085 | -0.83 | -0.85 | -0.85
949 | 50.086 | -0.89 | -0.86 | -0.86
950 | 50.086 | -0.88 | -0.86 | -0.86
951 | 50.086 | -0.875 | -0.86 | -0.86
952 | 50.083 | -0.905 | -0.83 | -0.83
953 | 50.085 | -0.875 | -0.85 | -0.85
954 | 50.083 | -0.865 | -0.83 | -0.83
955 | 50.08 | -0.82 | -0.8 | -0.8
956 | 50.079 | -0.83 | -0.79 | -0.79
957 | 50.077 | -0.785 | -0.77 | -0.77
958 | 50.077 | -0.795 | -0.77 | -0.77
959 | 50.075 | -0.795 | -0.75 | -0.75
960 | 50.075 | -0.765 | -0.75 | -0.75
961 | 50.077 | -0.79 | -0.77 | -0.77
962 | 50.079 | -0.795 | -0.79 | -0.79
963 | 50.079 | -0.83 | -0.79 | -0.79
964 | 50.082 | -0.82 | -0.82 | -0.82
965 | 50.081 | -0.82 | -0.81 | -0.81
966 | 50.084 | -0.85 | -0.84 | -0.84
967 | 50.084 | -0.85 | -0.84 | -0.84
968 | 50.082 | -0.835 | -0.82 | -0.82
969 | 50.081 | -0.84 | -0.81 | -0.81
970 | 50.08 | -0.835 | -0.8 | -0.8
971 | 50.077 | -0.815 | -0.77 | -0.77
972 | 50.076 | -0.775 | -0.76 | -0.76
973 | 50.072 | -0.735 | -0.72 | -0.72
974 | 50.071 | -0.735 | -0.71 | -0.71
975 | 50.071 | -0.725 | -0.71 | -0.71
976 | 50.073 | -0.755 | -0.73 | -0.73
977 | 50.073 | -0.75 | -0.73 | -0.73
978 | 50.073 | -0.75 | -0.73 | -0.73
979 | 50.075 | -0.735 | -0.75 | -0.75
980 | 50.075 | -0.765 | -0.75 | -0.75
981 | 50.076 | -0.77 | -0.76 | -0.76
982 | 50.076 | -0.79 | -0.76 | -0.76
983 | 50.079 | -0.785 | -0.79 | -0.79
984 | 50.081 | -0.815 | -0.81 | -0.81
985 | 50.083 | -0.835 | -0.83 | -0.83
986 | 50.083 | -0.86 | -0.83 | -0.83
987 | 50.085 | -0.89 | -0.85 | -0.85
988 | 50.085 | -0.885 | -0.85 | -0.85
989 | 50.087 | -0.895 | -0.87 | -0.87
990 | 50.088 | -0.91 | -0.88 | -0.88
991 | 50.089 | -0.925 | -0.89 | -0.89
992 | 50.091 | -0.94 | -0.91 | -0.91
993 | 50.092 | -0.925 | -0.92 | -0.92
994 | 50.093 | -0.955 | -0.93 | -0.93
995 | 50.094 | -0.97 | -0.94 | -0.94
996 | 50.098 | -1.01 | -0.98 | -0.98
997 | 50.103 | -1.035 | -1.03 | -1.03
998 | 50.105 | -1.08 | -1.05 | -1.05
999 | 50.107 | -1.12 | -1.07 | -1.07
1000 | 50.11 | -1.115 | -1.1 | -1.1
1001 | 50.111 | -1.12 | -1.11 | -1.11
1002 | 50.114 | -1.135 | -1.14 | -1.14
1003 | 50.114 | -1.165 | -1.14 | -1.14
1004 | 50.117 | -1.17 | -1.17 | -1.17
1005 | 50.114 | -1.19 | -1.14 | -1.14
1006 | 50.114 | -1.17 | -1.14 | -1.14
1007 | 50.111 | -1.155 | -1.11 | -1.11
1008 | 50.11 | -1.15 | -1.1 | -1.1
1009 | 50.108 | -1.11 | -1.08 | -1.08
1010 | 50.104 | -1.095 | -1.04 | -1.04
1011 | 50.101 | -1.065 | -1.01 | -1.01
1012 | 50.099 | -1.03 | -0.99 | -0.99
1013 | 50.093 | -1.01 | -0.93 | -0.93
1014 | 50.093 | -0.995 | -0.93 | -0.93
1015 | 50.09 | -0.965 | -0.9 | -0.9
1016 | 50.085 | -0.915 | -0.85 | -0.85
1017 | 50.084 | -0.88 | -0.84 | -0.84
1018 | 50.084 | -0.865 | -0.84 | -0.84
1019 | 50.081 | -0.865 | -0.81 | -0.81
1020 | 50.079 | -0.825 | -0.79 | -0.79
1021 | 50.078 | -0.825 | -0.78 | -0.78
1022 | 50.076 | -0.795 | -0.76 | -0.76
1023 | 50.076 | -0.775 | -0.76 | -0.76
1024 | 50.073 | -0.78 | -0.73 | -0.73
1025 | 50.073 | -0.745 | -0.73 | -0.73
1026 | 50.072 | -0.71 | -0.72 | -0.72
1027 | 50.069 | -0.735 | -0.69 | -0.69
1028 | 50.069 | -0.725 | -0.69 | -0.69
1029 | 50.069 | -0.72 | -0.69 | -0.69
1030 | 50.069 | -0.73 | -0.69 | -0.69
1031 | 50.069 | -0.7 | -0.69 | -0.69
1032 | 50.068 | -0.705 | -0.68 | -0.68
1033 | 50.068 | -0.685 | -0.68 | -0.68
1034 | 50.07 | -0.695 | -0.7 | -0.7
1035 | 50.068 | -0.695 | -0.68 | -0.68
1036 | 50.07 | -0.7 | -0.7 | -0.7
1037 | 50.073 | -0.73 | -0.73 | -0.73
1038 | 50.074 | -0.74 | -0.74 | -0.74
1039 | 50.079 | -0.785 | -0.79 | -0.79
1040 | 50.08 | -0.8 | -0.8 | -0.8
1041 | 50.083 | -0.865 | -0.83 | -0.83
1042 | 50.087 | -0.86 | -0.87 | -0.87
1043 | 50.087 | -0.905 | -0.87 | -0.87
1044 | 50.088 | -0.895 | -0.88 | -0.88
1045 | 50.091 | -0.915 | -0.91 | -0.91
1046 | 50.089 | -0.9 | -0.89 | -0.89
1047 | 50.09 | -0.94 | -0.9 | -0.9
1048 | 50.088 | -0.925 | -0.88 | -0.88
1049 | 50.088 | -0.92 | -0.88 | -0.88
1050 | 50.087 | -0.905 | -0.87 | -0.87
1051 | 50.09 | -0.89 | -0.9 | -0.9
1052 | 50.088 | -0.89 | -0.88 | -0.88
1053 | 50.088 | -0.91 | -0.88 | -0.88
1054 | 50.088 | -0.94 | -0.88 | -0.88
1055 | 50.088 | -0.915 | -0.88 | -0.88
1056 | 50.087 | -0.915 | -0.87 | -0.87
1057 | 50.085 | -0.86 | -0.85 | -0.85
1058 | 50.084 | -0.88 | -0.84 | -0.84
1059 | 50.083 | -0.875 | -0.83 | -0.83
1060 | 50.083 | -0.86 | -0.83 | -0.83
1061 | 50.084 | -0.84 | -0.84 | -0.84
1062 | 50.083 | -0.845 | -0.83 | -0.83
1063 | 50.083 | -0.855 | -0.83 | -0.83
1064 | 50.083 | -0.855 | -0.83 | -0.83
1065 | 50.086 | -0.91 | -0.86 | -0.86
1066 | 50.086 | -0.9 | -0.86 | -0.86
1067 | 50.086 | -0.89 | -0.86 | -0.86
1068 | 50.087 | -0.91 | -0.87 | -0.87
1069 | 50.088 | -0.9 | -0.88 | -0.88
1070 | 50.09 | -0.905 | -0.9 | -0.9
1071 | 50.089 | -0.915 | -0.89 | -0.89
1072 | 50.088 | -0.92 | -0.88 | -0.88
1073 | 50.091 | -0.91 | -0.91 | -0.91
1074 | 50.09 | -0.925 | -0.9 | -0.9
1075 | 50.091 | -0.94 | -0.91 | -0.91
1076 | 50.091 | -0.94 | -0.91 | -0.91
1077 | 50.091 | -0.94 | -0.91 | -0.91
1078 | 50.089 | -0.94 | -0.89 | -0.89
1079 | 50.09 | -0.925 | -0.9 | -0.9
1080 | 50.085 | -0.9 | -0.85 | -0.85
1081 | 50.087 | -0.9 | -0.87 | -0.87
1082 | 50.085 | -0.88 | -0.85 | -0.85
1083 | 50.082 | -0.865 | -0.82 | -0.82
1084 | 50.079 | -0.85 | -0.79 | -0.79
1085 | 50.077 | -0.79 | -0.77 | -0.77
1086 | 50.074 | -0.79 | -0.74 | -0.74
1087 | 50.073 | -0.765 | -0.73 | -0.73
1088 | 50.076 | -0.75 | -0.76 | -0.76
1089 | 50.073 | -0.76 | -0.73 | -0.73
1090 | 50.074 | -0.77 | -0.74 | -0.74
1091 | 50.073 | -0.76 | -0.73 | -0.73
1092 | 50.071 | -0.74 | -0.71 | -0.71
1093 | 50.072 | -0.75 | -0.72 | -0.72
1094 | 50.074 | -0.735 | -0.74 | -0.74
1095 | 50.074 | -0.765 | -0.74 | -0.74
1096 | 50.075 | -0.765 | -0.75 | -0.75
1097 | 50.077 | -0.78 | -0.77 | -0.77
1098 | 50.078 | -0.78 | -0.78 | -0.78
1099 | 50.084 | -0.84 | -0.84 | -0.84
1100 | 50.088 | -0.86 | -0.88 | -0.88
1101 | 50.088 | -0.9 | -0.88 | -0.88
1102 | 50.093 | -0.925 | -0.93 | -0.93
1103 | 50.097 | -0.985 | -0.97 | -0.97
1104 | 50.1 | -1.015 | -1 | -1
1105 | 50.1 | -1.045 | -1 | -1
1106 | 50.104 | -1.045 | -1.04 | -1.04
1107 | 50.104 | -1.065 | -1.04 | -1.04
1108 | 50.108 | -1.09 | -1.08 | -1.08
1109 | 50.106 | -1.09 | -1.06 | -1.06
1110 | 50.107 | -1.075 | -1.07 | -1.07
1111 | 50.106 | -1.09 | -1.06 | -1.06
1112 | 50.107 | -1.1 | -1.07 | -1.07
1113 | 50.106 | -1.105 | -1.06 | -1.06
1114 | 50.106 | -1.1 | -1.06 | -1.06
1115 | 50.106 | -1.095 | -1.06 | -1.06
1116 | 50.106 | -1.095 | -1.06 | -1.06
1117 | 50.105 | -1.095 | -1.05 | -1.05
1118 | 50.105 | -1.1 | -1.05 | -1.05
1119 | 50.106 | -1.08 | -1.06 | -1.06
1120 | 50.106 | -1.09 | -1.06 | -1.06
1121 | 50.106 | -1.09 | -1.06 | -1.06
1122 | 50.105 | -1.095 | -1.05 | -1.05
1123 | 50.104 | -1.095 | -1.04 | -1.04
1124 | 50.104 | -1.08 | -1.04 | -1.04
1125 | 50.101 | -1.06 | -1.01 | -1.01
1126 | 50.104 | -1.065 | -1.04 | -1.04
1127 | 50.104 | -1.085 | -1.04 | -1.04
1128 | 50.104 | -1.07 | -1.04 | -1.04
1129 | 50.104 | -1.06 | -1.04 | -1.04
1130 | 50.103 | -1.065 | -1.03 | -1.03
1131 | 50.101 | -1.06 | -1.01 | -1.01
1132 | 50.1 | -1.035 | -1 | -1
1133 | 50.097 | -1.045 | -0.97 | -0.97
1134 | 50.094 | -1 | -0.94 | -0.94
1135 | 50.095 | -0.975 | -0.95 | -0.95
1136 | 50.092 | -0.96 | -0.92 | -0.92
1137 | 50.092 | -0.96 | -0.92 | -0.92
1138 | 50.092 | -0.965 | -0.92 | -0.92
1139 | 50.092 | -0.935 | -0.92 | -0.92
1140 | 50.091 | -0.925 | -0.91 | -0.91
1141 | 50.092 | -0.94 | -0.92 | -0.92
1142 | 50.092 | -0.94 | -0.92 | -0.92
1143 | 50.092 | -0.96 | -0.92 | -0.92
1144 | 50.093 | -0.95 | -0.93 | -0.93
1145 | 50.092 | -0.94 | -0.92 | -0.92
1146 | 50.092 | -0.965 | -0.92 | -0.92
1147 | 50.092 | -0.955 | -0.92 | -0.92
1148 | 50.092 | -0.945 | -0.92 | -0.92
1149 | 50.092 | -0.955 | -0.92 | -0.92
1150 | 50.091 | -0.95 | -0.91 | -0.91
1151 | 50.088 | -0.945 | -0.88 | -0.88
1152 | 50.091 | -0.925 | -0.91 | -0.91
1153 | 50.091 | -0.925 | -0.91 | -0.91
1154 | 50.091 | -0.935 | -0.91 | -0.91
1155 | 50.09 | -0.925 | -0.9 | -0.9
1156 | 50.088 | -0.93 | -0.88 | -0.88
1157 | 50.086 | -0.915 | -0.86 | -0.86
1158 | 50.087 | -0.9 | -0.87 | -0.87
1159 | 50.086 | -0.895 | -0.86 | -0.86
1160 | 50.085 | -0.89 | -0.85 | -0.85
1161 | 50.085 | -0.88 | -0.85 | -0.85
1162 | 50.085 | -0.88 | -0.85 | -0.85
1163 | 50.084 | -0.855 | -0.84 | -0.84
1164 | 50.084 | -0.85 | -0.84 | -0.84
1165 | 50.084 | -0.86 | -0.84 | -0.84
1166 | 50.084 | -0.86 | -0.84 | -0.84
1167 | 50.086 | -0.855 | -0.86 | -0.86
1168 | 50.083 | -0.885 | -0.83 | -0.83
1169 | 50.086 | -0.88 | -0.86 | -0.86
1170 | 50.087 | -0.89 | -0.87 | -0.87
1171 | 50.087 | -0.9 | -0.87 | -0.87
1172 | 50.088 | -0.91 | -0.88 | -0.88
1173 | 50.089 | -0.925 | -0.89 | -0.89
1174 | 50.089 | -0.92 | -0.89 | -0.89
1175 | 50.087 | -0.91 | -0.87 | -0.87
1176 | 50.091 | -0.925 | -0.91 | -0.91
1177 | 50.093 | -0.92 | -0.93 | -0.93
1178 | 50.091 | -0.935 | -0.91 | -0.91
1179 | 50.091 | -0.95 | -0.91 | -0.91
1180 | 50.091 | -0.955 | -0.91 | -0.91
1181 | 50.092 | -0.945 | -0.92 | -0.92
1182 | 50.092 | -0.935 | -0.92 | -0.92
1183 | 50.091 | -0.95 | -0.91 | -0.91
1184 | 50.091 | -0.94 | -0.91 | -0.91
1185 | 50.092 | -0.945 | -0.92 | -0.92
1186 | 50.092 | -0.935 | -0.92 | -0.92
1187 | 50.092 | -0.95 | -0.92 | -0.92
1188 | 50.091 | -0.93 | -0.91 | -0.91
1189 | 50.091 | -0.915 | -0.91 | -0.91
1190 | 50.091 | -0.94 | -0.91 | -0.91
1191 | 50.09 | -0.925 | -0.9 | -0.9
1192 | 50.089 | -0.96 | -0.89 | -0.89
1193 | 50.089 | -0.91 | -0.89 | -0.89
1194 | 50.089 | -0.91 | -0.89 | -0.89
1195 | 50.091 | -0.935 | -0.91 | -0.91
1196 | 50.092 | -0.97 | -0.92 | -0.92
1197 | 50.095 | -0.93 | -0.95 | -0.95
1198 | 50.095 | -0.96 | -0.95 | -0.95
1199 | 50.095 | -0.965 | -0.95 | -0.95
1200 | 50.097 | -0.985 | -0.97 | -0.97
1201 | 50.096 | -1 | -0.96 | -0.96
1202 | 50.097 | -0.985 | -0.97 | -0.97
1203 | 50.097 | -1 | -0.97 | -0.97
1204 | 50.098 | -1 | -0.98 | -0.98
1205 | 50.098 | -1.02 | -0.98 | -0.98
1206 | 50.098 | -1 | -0.98 | -0.98
1207 | 50.098 | -1.02 | -0.98 | -0.98
1208 | 50.102 | -1.035 | -1.02 | -1.02
1209 | 50.101 | -1.01 | -1.01 | -1.01
1210 | 50.101 | -1.045 | -1.01 | -1.01
1211 | 50.101 | -1.035 | -1.01 | -1.01
1212 | 50.101 | -1.045 | -1.01 | -1.01
1213 | 50.101 | -1.04 | -1.01 | -1.01
1214 | 50.099 | -1.02 | -0.99 | -0.99
1215 | 50.101 | -1.045 | -1.01 | -1.01
1216 | 50.1 | -1.035 | -1 | -1
1217 | 50.101 | -1.05 | -1.01 | -1.01
1218 | 50.1 | -1.055 | -1 | -1
1219 | 50.099 | -1.03 | -0.99 | -0.99
1220 | 50.098 | -1.03 | -0.98 | -0.98
1221 | 50.096 | -0.98 | -0.96 | -0.96
1222 | 50.096 | -0.985 | -0.96 | -0.96
1223 | 50.094 | -0.965 | -0.94 | -0.94
1224 | 50.095 | -0.97 | -0.95 | -0.95
1225 | 50.094 | -0.985 | -0.94 | -0.94
1226 | 50.094 | -0.96 | -0.94 | -0.94
1227 | 50.091 | -0.955 | -0.91 | -0.91
1228 | 50.091 | -0.95 | -0.91 | -0.91
1229 | 50.09 | -0.945 | -0.9 | -0.9
1230 | 50.09 | -0.93 | -0.9 | -0.9
1231 | 50.09 | -0.925 | -0.9 | -0.9
1232 | 50.091 | -0.96 | -0.91 | -0.91
1233 | 50.092 | -0.95 | -0.92 | -0.92
1234 | 50.093 | -0.96 | -0.93 | -0.93
1235 | 50.094 | -0.96 | -0.94 | -0.94
1236 | 50.097 | -0.995 | -0.97 | -0.97
1237 | 50.099 | -1 | -0.99 | -0.99
1238 | 50.102 | -1.03 | -1.02 | -1.02
1239 | 50.102 | -1.06 | -1.02 | -1.02
1240 | 50.103 | -1.06 | -1.03 | -1.03
1241 | 50.103 | -1.065 | -1.03 | -1.03
1242 | 50.104 | -1.07 | -1.04 | -1.04
1243 | 50.104 | -1.085 | -1.04 | -1.04
1244 | 50.103 | -1.08 | -1.03 | -1.03
1245 | 50.099 | -1.035 | -0.99 | -0.99
1246 | 50.098 | -1.015 | -0.98 | -0.98
1247 | 50.095 | -0.975 | -0.95 | -0.95
1248 | 50.095 | -0.975 | -0.95 | -0.95
1249 | 50.092 | -0.96 | -0.92 | -0.92
1250 | 50.09 | -0.92 | -0.9 | -0.9
1251 | 50.09 | -0.935 | -0.9 | -0.9
1252 | 50.091 | -0.9 | -0.91 | -0.91
1253 | 50.091 | -0.95 | -0.91 | -0.91
1254 | 50.094 | -0.94 | -0.94 | -0.94
1255 | 50.095 | -0.97 | -0.95 | -0.95
1256 | 50.096 | -0.965 | -0.96 | -0.96
1257 | 50.099 | -0.995 | -0.99 | -0.99
1258 | 50.1 | -1.03 | -1 | -1
1259 | 50.104 | -1.055 | -1.04 | -1.04
1260 | 50.105 | -1.08 | -1.05 | -1.05
1261 | 50.109 | -1.1 | -1.09 | -1.09
1262 | 50.107 | -1.135 | -1.07 | -1.07
1263 | 50.109 | -1.13 | -1.09 | -1.09
1264 | 50.111 | -1.135 | -1.11 | -1.11
1265 | 50.111 | -1.14 | -1.11 | -1.11
1266 | 50.11 | -1.135 | -1.1 | -1.1
1267 | 50.108 | -1.14 | -1.08 | -1.08
1268 | 50.107 | -1.12 | -1.07 | -1.07
1269 | 50.106 | -1.115 | -1.06 | -1.06
1270 | 50.105 | -1.09 | -1.05 | -1.05
1271 | 50.102 | -1.075 | -1.02 | -1.02
1272 | 50.104 | -1.075 | -1.04 | -1.04
1273 | 50.105 | -1.08 | -1.05 | -1.05
1274 | 50.109 | -1.1 | -1.09 | -1.09
1275 | 50.109 | -1.14 | -1.09 | -1.09
1276 | 50.111 | -1.14 | -1.11 | -1.11
1277 | 50.113 | -1.15 | -1.13 | -1.13
1278 | 50.116 | -1.165 | -1.16 | -1.16
1279 | 50.116 | -1.2 | -1.16 | -1.16
1280 | 50.119 | -1.24 | -1.19 | -1.19
1281 | 50.122 | -1.26 | -1.22 | -1.22
1282 | 50.123 | -1.26 | -1.23 | -1.23
1283 | 50.124 | -1.275 | -1.24 | -1.24
1284 | 50.124 | -1.3 | -1.24 | -1.24
1285 | 50.125 | -1.275 | -1.25 | -1.25
1286 | 50.125 | -1.275 | -1.25 | -1.25
1287 | 50.125 | -1.295 | -1.25 | -1.25
1288 | 50.123 | -1.275 | -1.23 | -1.23
1289 | 50.123 | -1.305 | -1.23 | -1.23
1290 | 50.123 | -1.27 | -1.23 | -1.23
1291 | 50.123 | -1.275 | -1.23 | -1.23
1292 | 50.122 | -1.265 | -1.22 | -1.22
1293 | 50.118 | -1.205 | -1.18 | -1.18
1294 | 50.114 | -1.16 | -1.14 | -1.14
1295 | 50.11 | -1.155 | -1.1 | -1.1
1296 | 50.108 | -1.12 | -1.08 | -1.08
1297 | 50.106 | -1.1 | -1.06 | -1.06
1298 | 50.103 | -1.055 | -1.03 | -1.03
1299 | 50.1 | -1.035 | -1 | -1
1300 | 50.099 | -1.02 | -0.99 | -0.99
1301 | 50.096 | -1.02 | -0.96 | -0.96
1302 | 50.095 | -0.97 | -0.95 | -0.95
1303 | 50.094 | -0.975 | -0.94 | -0.94
1304 | 50.095 | -0.96 | -0.95 | -0.95
1305 | 50.094 | -0.96 | -0.94 | -0.94
1306 | 50.094 | -0.975 | -0.94 | -0.94
1307 | 50.094 | -0.975 | -0.94 | -0.94
1308 | 50.095 | -0.975 | -0.95 | -0.95
1309 | 50.094 | -0.975 | -0.94 | -0.94
1310 | 50.094 | -0.975 | -0.94 | -0.94
1311 | 50.094 | -0.975 | -0.94 | -0.94
1312 | 50.091 | -0.96 | -0.91 | -0.91
1313 | 50.091 | -0.925 | -0.91 | -0.91
1314 | 50.09 | -0.93 | -0.9 | -0.9
1315 | 50.088 | -0.925 | -0.88 | -0.88
1316 | 50.088 | -0.925 | -0.88 | -0.88
1317 | 50.088 | -0.93 | -0.88 | -0.88
1318 | 50.088 | -0.91 | -0.88 | -0.88
1319 | 50.086 | -0.915 | -0.86 | -0.86
1320 | 50.09 | -0.915 | -0.9 | -0.9
1321 | 50.09 | -0.925 | -0.9 | -0.9
1322 | 50.093 | -0.94 | -0.93 | -0.93
1323 | 50.095 | -0.96 | -0.95 | -0.95
1324 | 50.096 | -0.975 | -0.96 | -0.96
1325 | 50.098 | -0.985 | -0.98 | -0.98
1326 | 50.1 | -1.03 | -1 | -1
1327 | 50.1 | -1.055 | -1 | -1
1328 | 50.101 | -1.06 | -1.01 | -1.01
1329 | 50.1 | -1.04 | -1 | -1
1330 | 50.1 | -1.03 | -1 | -1
1331 | 50.099 | -1.035 | -0.99 | -0.99
1332 | 50.099 | -1.02 | -0.99 | -0.99
1333 | 50.1 | -1.03 | -1 | -1
1334 | 50.102 | -1.03 | -1.02 | -1.02
1335 | 50.104 | -1.07 | -1.04 | -1.04
1336 | 50.104 | -1.075 | -1.04 | -1.04
1337 | 50.105 | -1.08 | -1.05 | -1.05
1338 | 50.105 | -1.08 | -1.05 | -1.05
1339 | 50.106 | -1.075 | -1.06 | -1.06
1340 | 50.104 | -1.07 | -1.04 | -1.04
1341 | 50.104 | -1.075 | -1.04 | -1.04
1342 | 50.104 | -1.06 | -1.04 | -1.04
1343 | 50.104 | -1.08 | -1.04 | -1.04
1344 | 50.104 | -1.07 | -1.04 | -1.04
1345 | 50.102 | -1.095 | -1.02 | -1.02
1346 | 50.1 | -1.05 | -1 | -1
1347 | 50.101 | -1.035 | -1.01 | -1.01
1348 | 50.101 | -1.04 | -1.01 | -1.01
1349 | 50.1 | -1.045 | -1 | -1
1350 | 50.099 | -1.02 | -0.99 | -0.99
1351 | 50.099 | -1.01 | -0.99 | -0.99
1352 | 50.098 | -1 | -0.98 | -0.98
1353 | 50.096 | -0.99 | -0.96 | -0.96
1354 | 50.095 | -0.985 | -0.95 | -0.95
1355 | 50.095 | -0.985 | -0.95 | -0.95
1356 | 50.094 | -0.97 | -0.94 | -0.94
1357 | 50.091 | -0.94 | -0.91 | -0.91
1358 | 50.091 | -0.94 | -0.91 | -0.91
1359 | 50.085 | -0.905 | -0.85 | -0.85
1360 | 50.086 | -0.89 | -0.86 | -0.86
1361 | 50.083 | -0.875 | -0.83 | -0.83
1362 | 50.082 | -0.855 | -0.82 | -0.82
1363 | 50.082 | -0.835 | -0.82 | -0.82
1364 | 50.078 | -0.835 | -0.78 | -0.78
1365 | 50.08 | -0.805 | -0.8 | -0.8
1366 | 50.079 | -0.82 | -0.79 | -0.79
1367 | 50.08 | -0.81 | -0.8 | -0.8
1368 | 50.083 | -0.82 | -0.83 | -0.83
1369 | 50.083 | -0.85 | -0.83 | -0.83
1370 | 50.086 | -0.88 | -0.86 | -0.86
1371 | 50.089 | -0.925 | -0.89 | -0.89
1372 | 50.093 | -0.945 | -0.93 | -0.93
1373 | 50.094 | -0.955 | -0.94 | -0.94
1374 | 50.097 | -0.99 | -0.97 | -0.97
1375 | 50.098 | -0.995 | -0.98 | -0.98
1376 | 50.098 | -1.015 | -0.98 | -0.98
1377 | 50.098 | -0.995 | -0.98 | -0.98
1378 | 50.098 | -0.99 | -0.98 | -0.98
1379 | 50.098 | -1 | -0.98 | -0.98
1380 | 50.098 | -1 | -0.98 | -0.98
1381 | 50.095 | -1 | -0.95 | -0.95
1382 | 50.092 | -0.955 | -0.92 | -0.92
1383 | 50.091 | -0.93 | -0.91 | -0.91
1384 | 50.087 | -0.9 | -0.87 | -0.87
1385 | 50.085 | -0.9 | -0.85 | -0.85
1386 | 50.085 | -0.88 | -0.85 | -0.85
1387 | 50.086 | -0.88 | -0.86 | -0.86
1388 | 50.086 | -0.885 | -0.86 | -0.86
1389 | 50.086 | -0.89 | -0.86 | -0.86
1390 | 50.087 | -0.91 | -0.87 | -0.87
1391 | 50.087 | -0.885 | -0.87 | -0.87
1392 | 50.087 | -0.895 | -0.87 | -0.87
1393 | 50.09 | -0.9 | -0.9 | -0.9
1394 | 50.089 | -0.915 | -0.89 | -0.89
1395 | 50.09 | -0.905 | -0.9 | -0.9
1396 | 50.09 | -0.91 | -0.9 | -0.9
1397 | 50.093 | -0.935 | -0.93 | -0.93
1398 | 50.093 | -0.96 | -0.93 | -0.93
1399 | 50.095 | -0.975 | -0.95 | -0.95
1400 | 50.097 | -0.975 | -0.97 | -0.97
1401 | 50.097 | -1 | -0.97 | -0.97
1402 | 50.097 | -1 | -0.97 | -0.97
1403 | 50.097 | -0.995 | -0.97 | -0.97
1404 | 50.1 | -1 | -1 | -1
1405 | 50.099 | -1.02 | -0.99 | -0.99
1406 | 50.096 | -1.01 | -0.96 | -0.96
1407 | 50.094 | -0.99 | -0.94 | -0.94
1408 | 50.093 | -0.95 | -0.93 | -0.93
1409 | 50.09 | -0.945 | -0.9 | -0.9
1410 | 50.09 | -0.945 | -0.9 | -0.9
1411 | 50.087 | -0.935 | -0.87 | -0.87
1412 | 50.088 | -0.915 | -0.88 | -0.88
1413 | 50.087 | -0.895 | -0.87 | -0.87
1414 | 50.085 | -0.9 | -0.85 | -0.85
1415 | 50.086 | -0.87 | -0.86 | -0.86
1416 | 50.087 | -0.91 | -0.87 | -0.87
1417 | 50.087 | -0.895 | -0.87 | -0.87
1418 | 50.09 | -0.905 | -0.9 | -0.9
1419 | 50.09 | -0.91 | -0.9 | -0.9
1420 | 50.092 | -0.96 | -0.92 | -0.92
1421 | 50.095 | -0.985 | -0.95 | -0.95
1422 | 50.096 | -0.99 | -0.96 | -0.96
1423 | 50.096 | -1 | -0.96 | -0.96
1424 | 50.096 | -0.99 | -0.96 | -0.96
1425 | 50.095 | -0.985 | -0.95 | -0.95
1426 | 50.095 | -0.985 | -0.95 | -0.95
1427 | 50.095 | -1.01 | -0.95 | -0.95
1428 | 50.096 | -0.985 | -0.96 | -0.96
1429 | 50.094 | -0.97 | -0.94 | -0.94
1430 | 50.094 | -0.97 | -0.94 | -0.94
1431 | 50.093 | -0.955 | -0.93 | -0.93
1432 | 50.092 | -0.96 | -0.92 | -0.92
1433 | 50.091 | -0.96 | -0.91 | -0.91
1434 | 50.094 | -1.03 | -0.94 | -0.94
1435 | 50.093 | -0.965 | -0.93 | -0.93
1436 | 50.094 | -0.97 | -0.94 | -0.94
1437 | 50.092 | -0.975 | -0.92 | -0.92
1438 | 50.093 | -0.96 | -0.93 | -0.93
1439 | 50.092 | -0.96 | -0.92 | -0.92
1440 | 50.091 | -0.91 | -0.91 | -0.91
1441 | 50.09 | -0.93 | -0.9 | -0.9
1442 | 50.09 | -0.925 | -0.9 | -0.9
1443 | 50.087 | -0.915 | -0.87 | -0.87
1444 | 50.088 | -0.91 | -0.88 | -0.88
1445 | 50.088 | -0.9 | -0.88 | -0.88
1446 | 50.088 | -0.91 | -0.88 | -0.88
1447 | 50.088 | -0.9 | -0.88 | -0.88
1448 | 50.088 | -0.915 | -0.88 | -0.88
1449 | 50.086 | -0.885 | -0.86 | -0.86
1450 | 50.086 | -0.895 | -0.86 | -0.86
1451 | 50.083 | -0.88 | -0.83 | -0.83
1452 | 50.081 | -0.83 | -0.81 | -0.81
1453 | 50.078 | -0.825 | -0.78 | -0.78
1454 | 50.076 | -0.795 | -0.76 | -0.76
1455 | 50.073 | -0.775 | -0.73 | -0.73
1456 | 50.072 | -0.755 | -0.72 | -0.72
1457 | 50.07 | -0.71 | -0.7 | -0.7
1458 | 50.069 | -0.7 | -0.69 | -0.69
1459 | 50.069 | -0.705 | -0.69 | -0.69
1460 | 50.068 | -0.7 | -0.68 | -0.68
1461 | 50.068 | -0.7 | -0.68 | -0.68
1462 | 50.068 | -0.685 | -0.68 | -0.68
1463 | 50.067 | -0.7 | -0.67 | -0.67
1464 | 50.067 | -0.73 | -0.67 | -0.67
1465 | 50.067 | -0.68 | -0.67 | -0.67
1466 | 50.066 | -0.675 | -0.66 | -0.66
1467 | 50.065 | -0.655 | -0.65 | -0.65
1468 | 50.065 | -0.66 | -0.65 | -0.65
1469 | 50.066 | -0.665 | -0.66 | -0.66
1470 | 50.068 | -0.705 | -0.68 | -0.68
1471 | 50.069 | -0.695 | -0.69 | -0.69
1472 | 50.072 | -0.745 | -0.72 | -0.72
1473 | 50.073 | -0.755 | -0.73 | -0.73
1474 | 50.075 | -0.79 | -0.75 | -0.75
1475 | 50.079 | -0.78 | -0.79 | -0.79
1476 | 50.079 | -0.82 | -0.79 | -0.79
1477 | 50.08 | -0.85 | -0.8 | -0.8
1478 | 50.083 | -0.855 | -0.83 | -0.83
1479 | 50.084 | -0.855 | -0.84 | -0.84
1480 | 50.085 | -0.885 | -0.85 | -0.85
1481 | 50.084 | -0.85 | -0.84 | -0.84
1482 | 50.087 | -0.855 | -0.87 | -0.87
1483 | 50.086 | -0.87 | -0.86 | -0.86
1484 | 50.087 | -0.905 | -0.87 | -0.87
1485 | 50.088 | -0.91 | -0.88 | -0.88
1486 | 50.091 | -0.93 | -0.91 | -0.91
1487 | 50.094 | -0.95 | -0.94 | -0.94
1488 | 50.097 | -0.985 | -0.97 | -0.97
1489 | 50.1 | -1.01 | -1 | -1
1490 | 50.1 | -1.02 | -1 | -1
1491 | 50.101 | -1.02 | -1.01 | -1.01
1492 | 50.102 | -1.03 | -1.02 | -1.02
1493 | 50.103 | -1.08 | -1.03 | -1.03
1494 | 50.104 | -1.065 | -1.04 | -1.04
1495 | 50.104 | -1.02 | -1.04 | -1.04
1496 | 50.104 | -1.08 | -1.04 | -1.04
1497 | 50.107 | -1.1 | -1.07 | -1.07
1498 | 50.105 | -1.07 | -1.05 | -1.05
1499 | 50.105 | -1.105 | -1.05 | -1.05
1500 | 50.105 | -1.11 | -1.05 | -1.05
1501 | 50.105 | -1.08 | -1.05 | -1.05
1502 | 50.105 | -1.08 | -1.05 | -1.05
1503 | 50.105 | -1.07 | -1.05 | -1.05
1504 | 50.103 | -1.06 | -1.03 | -1.03
1505 | 50.1 | -1.055 | -1 | -1
1506 | 50.099 | -1.05 | -0.99 | -0.99
1507 | 50.101 | -1.055 | -1.01 | -1.01
1508 | 50.096 | -0.995 | -0.96 | -0.96
1509 | 50.098 | -1.02 | -0.98 | -0.98
1510 | 50.098 | -1.01 | -0.98 | -0.98
1511 | 50.099 | -0.995 | -0.99 | -0.99
1512 | 50.104 | -1.045 | -1.04 | -1.04
1513 | 50.107 | -1.06 | -1.07 | -1.07
1514 | 50.107 | -1.105 | -1.07 | -1.07
1515 | 50.108 | -1.12 | -1.08 | -1.08
1516 | 50.111 | -1.13 | -1.11 | -1.11
1517 | 50.112 | -1.145 | -1.12 | -1.12
1518 | 50.113 | -1.165 | -1.13 | -1.13
1519 | 50.115 | -1.18 | -1.15 | -1.15
1520 | 50.118 | -1.185 | -1.18 | -1.18
1521 | 50.119 | -1.215 | -1.19 | -1.19
1522 | 50.122 | -1.225 | -1.22 | -1.22
1523 | 50.124 | -1.275 | -1.24 | -1.24
1524 | 50.122 | -1.285 | -1.22 | -1.22
1525 | 50.124 | -1.29 | -1.24 | -1.24
1526 | 50.124 | -1.285 | -1.24 | -1.24
1527 | 50.124 | -1.295 | -1.24 | -1.24
1528 | 50.125 | -1.275 | -1.25 | -1.25
1529 | 50.128 | -1.295 | -1.28 | -1.28
1530 | 50.127 | -1.285 | -1.27 | -1.27
1531 | 50.128 | -1.325 | -1.28 | -1.28
1532 | 50.128 | -1.335 | -1.28 | -1.28
1533 | 50.131 | -1.35 | -1.31 | -1.31
1534 | 50.13 | -1.35 | -1.3 | -1.3
1535 | 50.13 | -1.355 | -1.3 | -1.3
1536 | 50.13 | -1.355 | -1.3 | -1.3
1537 | 50.131 | -1.335 | -1.31 | -1.31
1538 | 50.131 | -1.345 | -1.31 | -1.31
1539 | 50.131 | -1.345 | -1.31 | -1.31
1540 | 50.13 | -1.35 | -1.3 | -1.3
1541 | 50.13 | -1.355 | -1.3 | -1.3
1542 | 50.129 | -1.33 | -1.29 | -1.29
1543 | 50.128 | -1.32 | -1.28 | -1.28
1544 | 50.127 | -1.315 | -1.27 | -1.27
1545 | 50.127 | -1.3 | -1.27 | -1.27
1546 | 50.124 | -1.275 | -1.24 | -1.24
1547 | 50.124 | -1.275 | -1.24 | -1.24
1548 | 50.123 | -1.28 | -1.23 | -1.23
1549 | 50.124 | -1.275 | -1.24 | -1.24
1550 | 50.124 | -1.275 | -1.24 | -1.24
1551 | 50.124 | -1.285 | -1.24 | -1.24
1552 | 50.124 | -1.275 | -1.24 | -1.24
1553 | 50.121 | -1.24 | -1.21 | -1.21
1554 | 50.121 | -1.245 | -1.21 | -1.21
1555 | 50.119 | -1.21 | -1.19 | -1.19
1556 | 50.118 | -1.225 | -1.18 | -1.18
1557 | 50.115 | -1.23 | -1.15 | -1.15
1558 | 50.115 | -1.215 | -1.15 | -1.15
1559 | 50.115 | -1.18 | -1.15 | -1.15
1560 | 50.115 | -1.195 | -1.15 | -1.15
1561 | 50.113 | -1.16 | -1.13 | -1.13
1562 | 50.113 | -1.135 | -1.13 | -1.13
1563 | 50.108 | -1.14 | -1.08 | -1.08
1564 | 50.107 | -1.12 | -1.07 | -1.07
1565 | 50.105 | -1.09 | -1.05 | -1.05
1566 | 50.105 | -1.09 | -1.05 | -1.05
1567 | 50.102 | -1.075 | -1.02 | -1.02
1568 | 50.102 | -1.055 | -1.02 | -1.02
1569 | 50.101 | -1.06 | -1.01 | -1.01
1570 | 50.099 | -1.02 | -0.99 | -0.99
1571 | 50.1 | -1.01 | -1 | -1
1572 | 50.101 | -1.035 | -1.01 | -1.01
1573 | 50.1 | -1.03 | -1 | -1
1574 | 50.101 | -1.035 | -1.01 | -1.01
1575 | 50.098 | -1.01 | -0.98 | -0.98
1576 | 50.095 | -1.01 | -0.95 | -0.95
1577 | 50.095 | -0.995 | -0.95 | -0.95
1578 | 50.092 | -0.965 | -0.92 | -0.92
1579 | 50.091 | -0.96 | -0.91 | -0.91
1580 | 50.091 | -0.965 | -0.91 | -0.91
1581 | 50.092 | -0.97 | -0.92 | -0.92
1582 | 50.092 | -0.935 | -0.92 | -0.92
1583 | 50.092 | -0.965 | -0.92 | -0.92
1584 | 50.091 | -0.945 | -0.91 | -0.91
1585 | 50.089 | -0.94 | -0.89 | -0.89
1586 | 50.091 | -0.95 | -0.91 | -0.91
1587 | 50.09 | -0.935 | -0.9 | -0.9
1588 | 50.09 | -0.93 | -0.9 | -0.9
1589 | 50.092 | -0.92 | -0.92 | -0.92
1590 | 50.091 | -0.94 | -0.91 | -0.91
1591 | 50.094 | -0.95 | -0.94 | -0.94
1592 | 50.096 | -0.995 | -0.96 | -0.96
1593 | 50.096 | -0.985 | -0.96 | -0.96
1594 | 50.097 | -0.985 | -0.97 | -0.97
1595 | 50.099 | -1.01 | -0.99 | -0.99
1596 | 50.098 | -1.02 | -0.98 | -0.98
1597 | 50.097 | -1.02 | -0.97 | -0.97
1598 | 50.095 | -0.97 | -0.95 | -0.95
1599 | 50.094 | -0.975 | -0.94 | -0.94
1600 | 50.09 | -0.945 | -0.9 | -0.9
1601 | 50.09 | -0.935 | -0.9 | -0.9
1602 | 50.088 | -0.9 | -0.88 | -0.88
1603 | 50.087 | -0.9 | -0.87 | -0.87
1604 | 50.085 | -0.89 | -0.85 | -0.85
1605 | 50.084 | -0.875 | -0.84 | -0.84
1606 | 50.084 | -0.855 | -0.84 | -0.84
1607 | 50.085 | -0.88 | -0.85 | -0.85
1608 | 50.087 | -0.895 | -0.87 | -0.87
1609 | 50.089 | -0.925 | -0.89 | -0.89
1610 | 50.09 | -0.925 | -0.9 | -0.9
1611 | 50.093 | -0.92 | -0.93 | -0.93
1612 | 50.095 | -0.975 | -0.95 | -0.95
1613 | 50.096 | -1.01 | -0.96 | -0.96
1614 | 50.097 | -1 | -0.97 | -0.97
1615 | 50.1 | -1.02 | -1 | -1
1616 | 50.101 | -1.03 | -1.01 | -1.01
1617 | 50.101 | -1.035 | -1.01 | -1.01
1618 | 50.102 | -1.04 | -1.02 | -1.02
1619 | 50.105 | -1.09 | -1.05 | -1.05
1620 | 50.106 | -1.09 | -1.06 | -1.06
1621 | 50.107 | -1.095 | -1.07 | -1.07
1622 | 50.108 | -1.11 | -1.08 | -1.08
1623 | 50.111 | -1.14 | -1.11 | -1.11
1624 | 50.111 | -1.15 | -1.11 | -1.11
1625 | 50.113 | -1.165 | -1.13 | -1.13
1626 | 50.114 | -1.16 | -1.14 | -1.14
1627 | 50.116 | -1.17 | -1.16 | -1.16
1628 | 50.116 | -1.195 | -1.16 | -1.16
1629 | 50.116 | -1.165 | -1.16 | -1.16
1630 | 50.112 | -1.17 | -1.12 | -1.12
1631 | 50.11 | -1.155 | -1.1 | -1.1
1632 | 50.11 | -1.14 | -1.1 | -1.1
1633 | 50.107 | -1.105 | -1.07 | -1.07
1634 | 50.104 | -1.075 | -1.04 | -1.04
1635 | 50.103 | -1.06 | -1.03 | -1.03
1636 | 50.1 | -1.02 | -1 | -1
1637 | 50.097 | -1.02 | -0.97 | -0.97
1638 | 50.094 | -0.97 | -0.94 | -0.94
1639 | 50.094 | -0.975 | -0.94 | -0.94
1640 | 50.093 | -0.96 | -0.93 | -0.93
1641 | 50.091 | -0.93 | -0.91 | -0.91
1642 | 50.09 | -0.905 | -0.9 | -0.9
1643 | 50.089 | -0.93 | -0.89 | -0.89
1644 | 50.088 | -0.915 | -0.88 | -0.88
1645 | 50.087 | -0.895 | -0.87 | -0.87
1646 | 50.087 | -0.88 | -0.87 | -0.87
1647 | 50.086 | -0.88 | -0.86 | -0.86
1648 | 50.086 | -0.895 | -0.86 | -0.86
1649 | 50.087 | -0.905 | -0.87 | -0.87
1650 | 50.086 | -0.905 | -0.86 | -0.86
1651 | 50.089 | -0.895 | -0.89 | -0.89
1652 | 50.092 | -0.935 | -0.92 | -0.92
1653 | 50.095 | -0.945 | -0.95 | -0.95
1654 | 50.101 | -1.02 | -1.01 | -1.01
1655 | 50.105 | -1.05 | -1.05 | -1.05
1656 | 50.106 | -1.08 | -1.06 | -1.06
1657 | 50.11 | -1.105 | -1.1 | -1.1
1658 | 50.113 | -1.125 | -1.13 | -1.13
1659 | 50.113 | -1.16 | -1.13 | -1.13
1660 | 50.114 | -1.15 | -1.14 | -1.14
1661 | 50.115 | -1.18 | -1.15 | -1.15
1662 | 50.118 | -1.18 | -1.18 | -1.18
1663 | 50.122 | -1.24 | -1.22 | -1.22
1664 | 50.12 | -1.245 | -1.2 | -1.2
1665 | 50.122 | -1.24 | -1.22 | -1.22
1666 | 50.122 | -1.265 | -1.22 | -1.22
1667 | 50.126 | -1.265 | -1.26 | -1.26
1668 | 50.122 | -1.26 | -1.22 | -1.22
1669 | 50.122 | -1.28 | -1.22 | -1.22
1670 | 50.122 | -1.25 | -1.22 | -1.22
1671 | 50.121 | -1.24 | -1.21 | -1.21
1672 | 50.118 | -1.205 | -1.18 | -1.18
1673 | 50.116 | -1.195 | -1.16 | -1.16
1674 | 50.115 | -1.21 | -1.15 | -1.15
1675 | 50.109 | -1.14 | -1.09 | -1.09
1676 | 50.11 | -1.165 | -1.1 | -1.1
1677 | 50.109 | -1.135 | -1.09 | -1.09
1678 | 50.108 | -1.12 | -1.08 | -1.08
1679 | 50.108 | -1.105 | -1.08 | -1.08
1680 | 50.108 | -1.115 | -1.08 | -1.08
1681 | 50.108 | -1.115 | -1.08 | -1.08
1682 | 50.108 | -1.12 | -1.08 | -1.08
1683 | 50.109 | -1.13 | -1.09 | -1.09
1684 | 50.11 | -1.12 | -1.1 | -1.1
1685 | 50.111 | -1.135 | -1.11 | -1.11
1686 | 50.116 | -1.17 | -1.16 | -1.16
1687 | 50.12 | -1.21 | -1.2 | -1.2
1688 | 50.121 | -1.225 | -1.21 | -1.21
1689 | 50.122 | -1.245 | -1.22 | -1.22
1690 | 50.125 | -1.285 | -1.25 | -1.25
1691 | 50.125 | -1.295 | -1.25 | -1.25
1692 | 50.126 | -1.3 | -1.26 | -1.26
1693 | 50.128 | -1.315 | -1.28 | -1.28
1694 | 50.128 | -1.31 | -1.28 | -1.28
1695 | 50.128 | -1.32 | -1.28 | -1.28
1696 | 50.127 | -1.31 | -1.27 | -1.27
1697 | 50.129 | -1.31 | -1.29 | -1.29
1698 | 50.127 | -1.305 | -1.27 | -1.27
1699 | 50.127 | -1.315 | -1.27 | -1.27
1700 | 50.126 | -1.31 | -1.26 | -1.26
1701 | 50.127 | -1.28 | -1.27 | -1.27
1702 | 50.126 | -1.305 | -1.26 | -1.26
1703 | 50.125 | -1.285 | -1.25 | -1.25
1704 | 50.124 | -1.275 | -1.24 | -1.24
1705 | 50.123 | -1.255 | -1.23 | -1.23
1706 | 50.122 | -1.25 | -1.22 | -1.22
1707 | 50.121 | -1.25 | -1.21 | -1.21
1708 | 50.119 | -1.24 | -1.19 | -1.19
1709 | 50.12 | -1.24 | -1.2 | -1.2
1710 | 50.12 | -1.235 | -1.2 | -1.2
1711 | 50.121 | -1.255 | -1.21 | -1.21
1712 | 50.12 | -1.255 | -1.2 | -1.2
1713 | 50.123 | -1.26 | -1.23 | -1.23
1714 | 50.126 | -1.255 | -1.26 | -1.26
1715 | 50.126 | -1.3 | -1.26 | -1.26
1716 | 50.127 | -1.325 | -1.27 | -1.27
1717 | 50.128 | -1.315 | -1.28 | -1.28
1718 | 50.129 | -1.32 | -1.29 | -1.29
1719 | 50.132 | -1.345 | -1.32 | -1.32
1720 | 50.133 | -1.35 | -1.33 | -1.33
1721 | 50.138 | -1.395 | -1.38 | -1.38
1722 | 50.141 | -1.435 | -1.41 | -1.41
1723 | 50.144 | -1.46 | -1.44 | -1.44
1724 | 50.144 | -1.465 | -1.44 | -1.44
1725 | 50.144 | -1.475 | -1.44 | -1.44
1726 | 50.147 | -1.515 | -1.47 | -1.47
1727 | 50.147 | -1.5 | -1.47 | -1.47
1728 | 50.15 | -1.54 | -1.5 | -1.5
1729 | 50.15 | -1.55 | -1.5 | -1.5
1730 | 50.151 | -1.555 | -1.51 | -1.51
1731 | 50.153 | -1.6 | -1.53 | -1.53
1732 | 50.153 | -1.575 | -1.53 | -1.53
1733 | 50.153 | -1.58 | -1.53 | -1.53
1734 | 50.157 | -1.61 | -1.57 | -1.57
1735 | 50.156 | -1.59 | -1.56 | -1.56
1736 | 50.153 | -1.595 | -1.53 | -1.53
1737 | 50.152 | -1.575 | -1.52 | -1.52
1738 | 50.151 | -1.565 | -1.51 | -1.51
1739 | 50.148 | -1.535 | -1.48 | -1.48
1740 | 50.147 | -1.53 | -1.47 | -1.47
1741 | 50.143 | -1.505 | -1.43 | -1.43
1742 | 50.143 | -1.465 | -1.43 | -1.43
1743 | 50.139 | -1.425 | -1.39 | -1.39
1744 | 50.136 | -1.4 | -1.36 | -1.36
1745 | 50.133 | -1.37 | -1.33 | -1.33
1746 | 50.131 | -1.345 | -1.31 | -1.31
1747 | 50.131 | -1.355 | -1.31 | -1.31
1748 | 50.127 | -1.35 | -1.27 | -1.27
1749 | 50.126 | -1.32 | -1.26 | -1.26
1750 | 50.124 | -1.265 | -1.24 | -1.24
1751 | 50.12 | -1.25 | -1.2 | -1.2
1752 | 50.12 | -1.235 | -1.2 | -1.2
1753 | 50.119 | -1.235 | -1.19 | -1.19
1754 | 50.119 | -1.24 | -1.19 | -1.19
1755 | 50.12 | -1.235 | -1.2 | -1.2
1756 | 50.121 | -1.25 | -1.21 | -1.21
1757 | 50.12 | -1.235 | -1.2 | -1.2
1758 | 50.12 | -1.23 | -1.2 | -1.2
1759 | 50.12 | -1.23 | -1.2 | -1.2
1760 | 50.124 | -1.245 | -1.24 | -1.24
1761 | 50.122 | -1.265 | -1.22 | -1.22
1762 | 50.123 | -1.275 | -1.23 | -1.23
1763 | 50.123 | -1.265 | -1.23 | -1.23
1764 | 50.123 | -1.27 | -1.23 | -1.23
1765 | 50.12 | -1.25 | -1.2 | -1.2
1766 | 50.122 | -1.26 | -1.22 | -1.22
1767 | 50.123 | -1.265 | -1.23 | -1.23
1768 | 50.123 | -1.265 | -1.23 | -1.23
1769 | 50.123 | -1.275 | -1.23 | -1.23
1770 | 50.124 | -1.24 | -1.24 | -1.24
1771 | 50.123 | -1.29 | -1.23 | -1.23
1772 | 50.121 | -1.25 | -1.21 | -1.21
1773 | 50.12 | -1.24 | -1.2 | -1.2
1774 | 50.117 | -1.19 | -1.17 | -1.17
1775 | 50.117 | -1.195 | -1.17 | -1.17
1776 | 50.115 | -1.205 | -1.15 | -1.15
1777 | 50.112 | -1.165 | -1.12 | -1.12
1778 | 50.112 | -1.155 | -1.12 | -1.12
1779 | 50.111 | -1.155 | -1.11 | -1.11
1780 | 50.108 | -1.145 | -1.08 | -1.08
1781 | 50.108 | -1.12 | -1.08 | -1.08
1782 | 50.107 | -1.11 | -1.07 | -1.07
1783 | 50.107 | -1.105 | -1.07 | -1.07
1784 | 50.107 | -1.095 | -1.07 | -1.07
1785 | 50.107 | -1.115 | -1.07 | -1.07
1786 | 50.108 | -1.115 | -1.08 | -1.08
1787 | 50.109 | -1.105 | -1.09 | -1.09
1788 | 50.112 | -1.155 | -1.12 | -1.12
1789 | 50.112 | -1.15 | -1.12 | -1.12
1790 | 50.112 | -1.155 | -1.12 | -1.12
1791 | 50.114 | -1.195 | -1.14 | -1.14
1792 | 50.113 | -1.175 | -1.13 | -1.13
1793 | 50.114 | -1.165 | -1.14 | -1.14
1794 | 50.113 | -1.175 | -1.13 | -1.13
1795 | 50.114 | -1.165 | -1.14 | -1.14
1796 | 50.115 | -1.2 | -1.15 | -1.15
1797 | 50.116 | -1.2 | -1.16 | -1.16
1798 | 50.118 | -1.19 | -1.18 | -1.18
1799 | 50.118 | -1.215 | -1.18 | -1.18
1800 | 50.121 | -1.23 | -1.21 | -1.21
1801 | 50.117 | -1.2 | -1.17 | -1.17
1802 | 50.114 | -1.195 | -1.14 | -1.14
1803 | 50.107 | -1.145 | -1.07 | -1.07
1804 | 50.101 | -1.07 | -1.01 | -1.01
1805 | 50.093 | -0.98 | -0.93 | -0.93
1806 | 50.086 | -0.925 | -0.86 | -0.86
1807 | 50.078 | -0.82 | -0.78 | -0.78
1808 | 50.067 | -0.725 | -0.67 | -0.67
1809 | 50.058 | -0.625 | -0.58 | -0.58
1810 | 50.049 | -0.525 | -0.49 | -0.49
1811 | 50.046 | -0.47 | -0.46 | -0.46
1812 | 50.043 | -0.445 | -0.43 | -0.43
1813 | 50.042 | -0.44 | -0.42 | -0.42
1814 | 50.042 | -0.43 | -0.42 | -0.42
1815 | 50.043 | -0.44 | -0.43 | -0.43
1816 | 50.046 | -0.455 | -0.46 | -0.46
1817 | 50.049 | -0.465 | -0.49 | -0.49
1818 | 50.05 | -0.495 | -0.5 | -0.5
1819 | 50.055 | -0.565 | -0.55 | -0.55
1820 | 50.059 | -0.565 | -0.59 | -0.59
1821 | 50.06 | -0.63 | -0.6 | -0.6
1822 | 50.063 | -0.67 | -0.63 | -0.63
1823 | 50.067 | -0.69 | -0.67 | -0.67
1824 | 50.071 | -0.75 | -0.71 | -0.71
1825 | 50.075 | -0.765 | -0.75 | -0.75
1826 | 50.078 | -0.82 | -0.78 | -0.78
1827 | 50.081 | -0.83 | -0.81 | -0.81
1828 | 50.084 | -0.875 | -0.84 | -0.84
1829 | 50.086 | -0.88 | -0.86 | -0.86
1830 | 50.087 | -0.9 | -0.87 | -0.87
1831 | 50.089 | -0.905 | -0.89 | -0.89
1832 | 50.091 | -0.91 | -0.91 | -0.91
1833 | 50.091 | -0.93 | -0.91 | -0.91
1834 | 50.09 | -0.94 | -0.9 | -0.9
1835 | 50.09 | -0.94 | -0.9 | -0.9
1836 | 50.089 | -0.94 | -0.89 | -0.89
1837 | 50.087 | -0.9 | -0.87 | -0.87
1838 | 50.087 | -0.895 | -0.87 | -0.87
1839 | 50.085 | -0.91 | -0.85 | -0.85
1840 | 50.087 | -0.895 | -0.87 | -0.87
1841 | 50.087 | -0.895 | -0.87 | -0.87
1842 | 50.085 | -0.89 | -0.85 | -0.85
1843 | 50.085 | -0.865 | -0.85 | -0.85
1844 | 50.085 | -0.875 | -0.85 | -0.85
1845 | 50.085 | -0.875 | -0.85 | -0.85
1846 | 50.082 | -0.865 | -0.82 | -0.82
1847 | 50.081 | -0.85 | -0.81 | -0.81
1848 | 50.079 | -0.8 | -0.79 | -0.79
1849 | 50.077 | -0.795 | -0.77 | -0.77
1850 | 50.074 | -0.77 | -0.74 | -0.74
1851 | 50.074 | -0.76 | -0.74 | -0.74
1852 | 50.073 | -0.765 | -0.73 | -0.73
1853 | 50.073 | -0.745 | -0.73 | -0.73
1854 | 50.072 | -0.74 | -0.72 | -0.72
1855 | 50.074 | -0.735 | -0.74 | -0.74
1856 | 50.072 | -0.765 | -0.72 | -0.72
1857 | 50.073 | -0.745 | -0.73 | -0.73
1858 | 50.075 | -0.77 | -0.75 | -0.75
1859 | 50.074 | -0.77 | -0.74 | -0.74
1860 | 50.073 | -0.765 | -0.73 | -0.73
1861 | 50.073 | -0.765 | -0.73 | -0.73
1862 | 50.073 | -0.755 | -0.73 | -0.73
1863 | 50.07 | -0.76 | -0.7 | -0.7
1864 | 50.069 | -0.735 | -0.69 | -0.69
1865 | 50.066 | -0.69 | -0.66 | -0.66
1866 | 50.064 | -0.675 | -0.64 | -0.64
1867 | 50.064 | -0.655 | -0.64 | -0.64
1868 | 50.061 | -0.66 | -0.61 | -0.61
1869 | 50.061 | -0.64 | -0.61 | -0.61
1870 | 50.061 | -0.635 | -0.61 | -0.61
1871 | 50.063 | -0.64 | -0.63 | -0.63
1872 | 50.06 | -0.66 | -0.6 | -0.6
1873 | 50.06 | -0.61 | -0.6 | -0.6
1874 | 50.059 | -0.615 | -0.59 | -0.59
1875 | 50.056 | -0.59 | -0.56 | -0.56
1876 | 50.053 | -0.575 | -0.53 | -0.53
1877 | 50.054 | -0.555 | -0.54 | -0.54
1878 | 50.053 | -0.55 | -0.53 | -0.53
1879 | 50.052 | -0.545 | -0.52 | -0.52
1880 | 50.049 | -0.515 | -0.49 | -0.49
1881 | 50.049 | -0.505 | -0.49 | -0.49
1882 | 50.047 | -0.47 | -0.47 | -0.47
1883 | 50.045 | -0.47 | -0.45 | -0.45
1884 | 50.042 | -0.46 | -0.42 | -0.42
1885 | 50.042 | -0.435 | -0.42 | -0.42
1886 | 50.04 | -0.405 | -0.4 | -0.4
1887 | 50.036 | -0.41 | -0.36 | -0.36
1888 | 50.039 | -0.4 | -0.39 | -0.39
1889 | 50.039 | -0.405 | -0.39 | -0.39
1890 | 50.042 | -0.435 | -0.42 | -0.42
1891 | 50.042 | -0.43 | -0.42 | -0.42
1892 | 50.045 | -0.465 | -0.45 | -0.45
1893 | 50.045 | -0.45 | -0.45 | -0.45
1894 | 50.045 | -0.44 | -0.45 | -0.45
1895 | 50.045 | -0.455 | -0.45 | -0.45
1896 | 50.045 | -0.47 | -0.45 | -0.45
1897 | 50.044 | -0.455 | -0.44 | -0.44
1898 | 50.042 | -0.42 | -0.42 | -0.42
1899 | 50.042 | -0.435 | -0.42 | -0.42
1900 | 50.041 | -0.43 | -0.41 | -0.41
1901 | 50.041 | -0.43 | -0.41 | -0.41
1902 | 50.042 | -0.435 | -0.42 | -0.42
1903 | 50.044 | -0.435 | -0.44 | -0.44
1904 | 50.043 | -0.45 | -0.43 | -0.43
1905 | 50.043 | -0.44 | -0.43 | -0.43
1906 | 50.042 | -0.44 | -0.42 | -0.42
1907 | 50.041 | -0.42 | -0.41 | -0.41
1908 | 50.041 | -0.44 | -0.41 | -0.41
1909 | 50.041 | -0.42 | -0.41 | -0.41
1910 | 50.044 | -0.43 | -0.44 | -0.44
1911 | 50.043 | -0.465 | -0.43 | -0.43
1912 | 50.044 | -0.46 | -0.44 | -0.44
1913 | 50.044 | -0.46 | -0.44 | -0.44
1914 | 50.045 | -0.455 | -0.45 | -0.45
1915 | 50.045 | -0.47 | -0.45 | -0.45
1916 | 50.044 | -0.46 | -0.44 | -0.44
1917 | 50.045 | -0.42 | -0.45 | -0.45
1918 | 50.043 | -0.455 | -0.43 | -0.43
1919 | 50.044 | -0.455 | -0.44 | -0.44
1920 | 50.045 | -0.455 | -0.45 | -0.45
1921 | 50.045 | -0.45 | -0.45 | -0.45
1922 | 50.044 | -0.455 | -0.44 | -0.44
1923 | 50.039 | -0.45 | -0.39 | -0.39
1924 | 50.04 | -0.41 | -0.4 | -0.4
1925 | 50.039 | -0.42 | -0.39 | -0.39
1926 | 50.037 | -0.45 | -0.37 | -0.37
1927 | 50.037 | -0.395 | -0.37 | -0.37
1928 | 50.037 | -0.375 | -0.37 | -0.37
1929 | 50.036 | -0.37 | -0.36 | -0.36
1930 | 50.031 | -0.345 | -0.31 | -0.31
1931 | 50.031 | -0.325 | -0.31 | -0.31
1932 | 50.031 | -0.335 | -0.31 | -0.31
1933 | 50.028 | -0.32 | -0.28 | -0.28
1934 | 50.029 | -0.295 | -0.29 | -0.29
1935 | 50.027 | -0.28 | -0.27 | -0.27
1936 | 50.026 | -0.27 | -0.26 | -0.26
1937 | 50.022 | -0.25 | -0.22 | -0.22
1938 | 50.023 | -0.23 | -0.23 | -0.23
1939 | 50.023 | -0.25 | -0.23 | -0.23
1940 | 50.024 | -0.24 | -0.24 | -0.24
1941 | 50.024 | -0.25 | -0.24 | -0.24
1942 | 50.023 | -0.23 | -0.23 | -0.23
1943 | 50.021 | -0.215 | -0.21 | -0.21
1944 | 50.018 | -0.195 | -0.18 | -0.18
1945 | 50.016 | -0.19 | -0.16 | -0.16
1946 | 50.015 | -0.19 | -0.15 | -0.15
1947 | 50.014 | -0.01 | -0.14 | 0
1948 | 50.013 | -0.015 | -0.13 | 0
1949 | 50.013 | -0.015 | -0.13 | 0
1950 | 50.013 | 0 | -0.13 | 0
1951 | 50.012 | -0.005 | -0.12 | 0
1952 | 50.01 | 0 | -0.1 | 0
1953 | 50.01 | 0 | -0.1 | 0
1954 | 50.01 | 0.005 | -0.1 | 0
1955 | 50.011 | 0 | -0.11 | 0
1956 | 50.011 | 0 | -0.11 | 0
1957 | 50.012 | 0 | -0.12 | 0
1958 | 50.014 | -0.01 | -0.14 | 0
1959 | 50.016 | -0.165 | -0.16 | -0.16
1960 | 50.016 | -0.055 | -0.16 | -0.16
1961 | 50.019 | -0.185 | -0.19 | -0.19
1962 | 50.019 | -0.195 | -0.19 | -0.19
1963 | 50.02 | -0.195 | -0.2 | -0.2
1964 | 50.019 | -0.195 | -0.19 | -0.19
1965 | 50.019 | -0.19 | -0.19 | -0.19
1966 | 50.02 | -0.185 | -0.2 | -0.2
1967 | 50.02 | -0.205 | -0.2 | -0.2
1968 | 50.02 | -0.21 | -0.2 | -0.2
1969 | 50.019 | -0.19 | -0.19 | -0.19
1970 | 50.021 | -0.215 | -0.21 | -0.21
1971 | 50.024 | -0.215 | -0.24 | -0.24
1972 | 50.025 | -0.245 | -0.25 | -0.25
1973 | 50.026 | -0.26 | -0.26 | -0.26
1974 | 50.027 | -0.275 | -0.27 | -0.27
1975 | 50.025 | -0.26 | -0.25 | -0.25
1976 | 50.023 | -0.26 | -0.23 | -0.23
1977 | 50.022 | -0.235 | -0.22 | -0.22
1978 | 50.019 | -0.22 | -0.19 | -0.19
1979 | 50.016 | -0.2 | -0.16 | -0.16
1980 | 50.014 | -0.145 | -0.14 | 0
1981 | 50.01 | 0.01 | -0.1 | 0
1982 | 50.008 | 0.005 | -0.08 | 0
1983 | 50.007 | -0.01 | -0.07 | 0
1984 | 50.006 | 0 | -0.06 | 0
1985 | 50.005 | -0.005 | -0.05 | 0
1986 | 50.004 | 0 | -0.04 | 0
1987 | 50.003 | 0 | -0.03 | 0
1988 | 50.003 | -0.015 | -0.03 | 0
1989 | 50.003 | -0.01 | -0.03 | 0
1990 | 50.003 | -0.015 | -0.03 | 0
1991 | 50.004 | -0.02 | -0.04 | 0
1992 | 50.007 | -0.015 | -0.07 | 0
1993 | 50.008 | -0.01 | -0.08 | 0
1994 | 50.011 | 0 | -0.11 | 0
1995 | 50.011 | -0.005 | -0.11 | 0
1996 | 50.012 | -0.01 | -0.12 | 0
1997 | 50.012 | -0.015 | -0.12 | 0
1998 | 50.011 | -0.01 | -0.11 | 0
1999 | 50.011 | -0.01 | -0.11 | 0
2000 | 50.011 | 0 | -0.11 | 0
2001 | 50.011 | 0 | -0.11 | 0
2002 | 50.012 | 0.005 | -0.12 | 0
2003 | 50.013 | 0.005 | -0.13 | 0
2004 | 50.013 | 0.01 | -0.13 | 0
2005 | 50.013 | 0.01 | -0.13 | 0
2006 | 50.014 | 0.005 | -0.14 | 0
2007 | 50.014 | 0.01 | -0.14 | 0
2008 | 50.015 | 0 | -0.15 | -0.15
2009 | 50.015 | -0.035 | -0.15 | -0.15
2010 | 50.016 | -0.07 | -0.16 | -0.16
2011 | 50.016 | -0.1 | -0.16 | -0.16
2012 | 50.016 | -0.16 | -0.16 | -0.16
2013 | 50.016 | -0.16 | -0.16 | -0.16
2014 | 50.017 | -0.165 | -0.17 | -0.17
2015 | 50.018 | -0.165 | -0.18 | -0.18
2016 | 50.018 | -0.17 | -0.18 | -0.18
2017 | 50.018 | -0.18 | -0.18 | -0.18
2018 | 50.017 | -0.18 | -0.17 | -0.17
2019 | 50.014 | -0.17 | -0.14 | 0
2020 | 50.017 | 0 | -0.17 | -0.17
2021 | 50.014 | 0 | -0.14 | 0
2022 | 50.013 | -0.025 | -0.13 | 0
2023 | 50.016 | -0.12 | -0.16 | -0.16
2024 | 50.017 | -0.165 | -0.17 | -0.17
2025 | 50.017 | -0.175 | -0.17 | -0.17
2026 | 50.018 | -0.175 | -0.18 | -0.18
2027 | 50.018 | -0.185 | -0.18 | -0.18
2028 | 50.022 | -0.2 | -0.22 | -0.22
2029 | 50.019 | -0.2 | -0.19 | -0.19
2030 | 50.019 | -0.19 | -0.19 | -0.19
2031 | 50.017 | -0.18 | -0.17 | -0.17
2032 | 50.018 | -0.185 | -0.18 | -0.18
2033 | 50.018 | -0.2 | -0.18 | -0.18
2034 | 50.016 | -0.175 | -0.16 | -0.16
2035 | 50.016 | -0.13 | -0.16 | -0.16
2036 | 50.013 | -0.015 | -0.13 | 0
2037 | 50.011 | -0.01 | -0.11 | 0
2038 | 50.01 | -0.01 | -0.1 | 0
2039 | 50.01 | -0.015 | -0.1 | 0
2040 | 50.011 | -0.01 | -0.11 | 0
2041 | 50.012 | -0.01 | -0.12 | 0
2042 | 50.01 | 0 | -0.1 | 0
2043 | 50.01 | 0 | -0.1 | 0
2044 | 50.01 | -0.005 | -0.1 | 0
2045 | 50.011 | 0 | -0.11 | 0
2046 | 50.011 | 0.005 | -0.11 | 0
2047 | 50.01 | 0.01 | -0.1 | 0
2048 | 50.01 | 0.01 | -0.1 | 0
2049 | 50.01 | -0.01 | -0.1 | 0
2050 | 50.01 | 0.01 | -0.1 | 0
2051 | 50.011 | -0.005 | -0.11 | 0
2052 | 50.012 | -0.01 | -0.12 | 0
2053 | 50.015 | -0.01 | -0.15 | -0.15
2054 | 50.013 | 0.005 | -0.13 | 0
2055 | 50.013 | 0 | -0.13 | 0
2056 | 50.016 | 0.01 | -0.16 | -0.16
2057 | 50.016 | -0.085 | -0.16 | -0.16
2058 | 50.017 | -0.185 | -0.17 | -0.17
2059 | 50.018 | -0.175 | -0.18 | -0.18
2060 | 50.018 | -0.19 | -0.18 | -0.18
2061 | 50.017 | -0.185 | -0.17 | -0.17
2062 | 50.017 | -0.185 | -0.17 | -0.17
2063 | 50.019 | -0.2 | -0.19 | -0.19
2064 | 50.016 | -0.2 | -0.16 | -0.16
2065 | 50.018 | -0.19 | -0.18 | -0.18
2066 | 50.018 | -0.195 | -0.18 | -0.18
2067 | 50.018 | -0.195 | -0.18 | -0.18
2068 | 50.019 | -0.2 | -0.19 | -0.19
2069 | 50.02 | -0.195 | -0.2 | -0.2
2070 | 50.021 | -0.215 | -0.21 | -0.21
2071 | 50.019 | -0.225 | -0.19 | -0.19
2072 | 50.025 | -0.24 | -0.25 | -0.25
2073 | 50.024 | -0.265 | -0.24 | -0.24
2074 | 50.024 | -0.255 | -0.24 | -0.24
2075 | 50.024 | -0.25 | -0.24 | -0.24
2076 | 50.025 | -0.255 | -0.25 | -0.25
2077 | 50.029 | -0.245 | -0.29 | -0.29
2078 | 50.026 | -0.275 | -0.26 | -0.26
2079 | 50.027 | -0.275 | -0.27 | -0.27
2080 | 50.027 | -0.275 | -0.27 | -0.27
2081 | 50.027 | -0.275 | -0.27 | -0.27
2082 | 50.027 | -0.265 | -0.27 | -0.27
2083 | 50.026 | -0.275 | -0.26 | -0.26
2084 | 50.025 | -0.265 | -0.25 | -0.25
2085 | 50.022 | -0.24 | -0.22 | -0.22
2086 | 50.02 | -0.23 | -0.2 | -0.2
2087 | 50.019 | -0.195 | -0.19 | -0.19
2088 | 50.016 | -0.19 | -0.16 | -0.16
2089 | 50.017 | -0.17 | -0.17 | -0.17
2090 | 50.018 | -0.18 | -0.18 | -0.18
2091 | 50.019 | -0.195 | -0.19 | -0.19
2092 | 50.019 | -0.21 | -0.19 | -0.19
2093 | 50.023 | -0.22 | -0.23 | -0.23
2094 | 50.024 | -0.25 | -0.24 | -0.24
2095 | 50.031 | -0.29 | -0.31 | -0.31
2096 | 50.036 | -0.335 | -0.36 | -0.36
2097 | 50.039 | -0.39 | -0.39 | -0.39
2098 | 50.043 | -0.46 | -0.43 | -0.43
2099 | 50.048 | -0.505 | -0.48 | -0.48
2100 | 50.055 | -0.53 | -0.55 | -0.55
2101 | 50.059 | -0.62 | -0.59 | -0.59
2102 | 50.065 | -0.64 | -0.65 | -0.65
2103 | 50.069 | -0.685 | -0.69 | -0.69
2104 | 50.075 | -0.755 | -0.75 | -0.75
2105 | 50.08 | -0.805 | -0.8 | -0.8
2106 | 50.083 | -0.83 | -0.83 | -0.83
2107 | 50.084 | -0.855 | -0.84 | -0.84
2108 | 50.087 | -0.865 | -0.87 | -0.87
2109 | 50.089 | -0.91 | -0.89 | -0.89
2110 | 50.095 | -0.955 | -0.95 | -0.95
2111 | 50.098 | -0.995 | -0.98 | -0.98
2112 | 50.097 | -1.01 | -0.97 | -0.97
2113 | 50.097 | -1.01 | -0.97 | -0.97
2114 | 50.094 | -0.99 | -0.94 | -0.94
2115 | 50.093 | -0.96 | -0.93 | -0.93
2116 | 50.093 | -0.96 | -0.93 | -0.93
2117 | 50.093 | -0.96 | -0.93 | -0.93
2118 | 50.093 | -0.96 | -0.93 | -0.93
2119 | 50.093 | -0.955 | -0.93 | -0.93
2120 | 50.093 | -0.97 | -0.93 | -0.93
2121 | 50.094 | -0.965 | -0.94 | -0.94
2122 | 50.094 | -0.97 | -0.94 | -0.94
2123 | 50.097 | -0.98 | -0.97 | -0.97
2124 | 50.099 | -1.03 | -0.99 | -0.99
2125 | 50.1 | -1.035 | -1 | -1
2126 | 50.101 | -1.035 | -1.01 | -1.01
2127 | 50.101 | -1.04 | -1.01 | -1.01
2128 | 50.102 | -1.05 | -1.02 | -1.02
2129 | 50.103 | -1.045 | -1.03 | -1.03
2130 | 50.104 | -1.06 | -1.04 | -1.04
2131 | 50.105 | -1.07 | -1.05 | -1.05
2132 | 50.105 | -1.085 | -1.05 | -1.05
2133 | 50.105 | -1.09 | -1.05 | -1.05
2134 | 50.105 | -1.08 | -1.05 | -1.05
2135 | 50.105 | -1.09 | -1.05 | -1.05
2136 | 50.109 | -1.09 | -1.09 | -1.09
2137 | 50.108 | -1.11 | -1.08 | -1.08
2138 | 50.108 | -1.115 | -1.08 | -1.08
2139 | 50.111 | -1.105 | -1.11 | -1.11
2140 | 50.111 | -1.14 | -1.11 | -1.11
2141 | 50.109 | -1.15 | -1.09 | -1.09
2142 | 50.109 | -1.13 | -1.09 | -1.09
2143 | 50.105 | -1.09 | -1.05 | -1.05
2144 | 50.104 | -1.08 | -1.04 | -1.04
2145 | 50.103 | -1.055 | -1.03 | -1.03
2146 | 50.101 | -1.055 | -1.01 | -1.01
2147 | 50.099 | -1.015 | -0.99 | -0.99
2148 | 50.097 | -0.975 | -0.97 | -0.97
2149 | 50.096 | -0.985 | -0.96 | -0.96
2150 | 50.095 | -0.97 | -0.95 | -0.95
2151 | 50.093 | -0.945 | -0.93 | -0.93
2152 | 50.094 | -0.97 | -0.94 | -0.94
2153 | 50.094 | -0.995 | -0.94 | -0.94
2154 | 50.095 | -0.97 | -0.95 | -0.95
2155 | 50.096 | -0.975 | -0.96 | -0.96
2156 | 50.098 | -1.02 | -0.98 | -0.98
2157 | 50.1 | -1 | -1 | -1
2158 | 50.101 | -1.035 | -1.01 | -1.01
2159 | 50.101 | -1.035 | -1.01 | -1.01
2160 | 50.101 | -1.035 | -1.01 | -1.01
2161 | 50.102 | -1.055 | -1.02 | -1.02
2162 | 50.105 | -1.085 | -1.05 | -1.05
2163 | 50.104 | -1.085 | -1.04 | -1.04
2164 | 50.104 | -1.07 | -1.04 | -1.04
2165 | 50.103 | -1.065 | -1.03 | -1.03
2166 | 50.101 | -1.055 | -1.01 | -1.01
2167 | 50.098 | -0.995 | -0.98 | -0.98
2168 | 50.098 | -1.01 | -0.98 | -0.98
2169 | 50.098 | -1 | -0.98 | -0.98
2170 | 50.095 | -0.97 | -0.95 | -0.95
2171 | 50.093 | -0.96 | -0.93 | -0.93
2172 | 50.09 | -0.95 | -0.9 | -0.9
2173 | 50.088 | -0.91 | -0.88 | -0.88
2174 | 50.089 | -0.92 | -0.89 | -0.89
2175 | 50.09 | -0.925 | -0.9 | -0.9
2176 | 50.089 | -0.915 | -0.89 | -0.89
2177 | 50.088 | -0.91 | -0.88 | -0.88
2178 | 50.085 | -0.875 | -0.85 | -0.85
2179 | 50.083 | -0.865 | -0.83 | -0.83
2180 | 50.084 | -0.85 | -0.84 | -0.84
2181 | 50.083 | -0.84 | -0.83 | -0.83
2182 | 50.081 | -0.84 | -0.81 | -0.81
2183 | 50.078 | -0.81 | -0.78 | -0.78
2184 | 50.076 | -0.76 | -0.76 | -0.76
2185 | 50.073 | -0.765 | -0.73 | -0.73
2186 | 50.07 | -0.735 | -0.7 | -0.7
2187 | 50.07 | -0.72 | -0.7 | -0.7
2188 | 50.069 | -0.715 | -0.69 | -0.69
2189 | 50.069 | -0.7 | -0.69 | -0.69
2190 | 50.063 | -0.67 | -0.63 | -0.63
2191 | 50.063 | -0.63 | -0.63 | -0.63
2192 | 50.062 | -0.635 | -0.62 | -0.62
2193 | 50.062 | -0.65 | -0.62 | -0.62
2194 | 50.062 | -0.64 | -0.62 | -0.62
2195 | 50.058 | -0.6 | -0.58 | -0.58
2196 | 50.058 | -0.6 | -0.58 | -0.58
2197 | 50.055 | -0.58 | -0.55 | -0.55
2198 | 50.058 | -0.585 | -0.58 | -0.58
2199 | 50.058 | -0.595 | -0.58 | -0.58
2200 | 50.057 | -0.6 | -0.57 | -0.57
2201 | 50.059 | -0.61 | -0.59 | -0.59
2202 | 50.06 | -0.595 | -0.6 | -0.6
2203 | 50.06 | -0.61 | -0.6 | -0.6
2204 | 50.06 | -0.625 | -0.6 | -0.6
2205 | 50.06 | -0.61 | -0.6 | -0.6
2206 | 50.06 | -0.61 | -0.6 | -0.6
2207 | 50.06 | -0.625 | -0.6 | -0.6
2208 | 50.061 | -0.62 | -0.61 | -0.61
2209 | 50.06 | -0.625 | -0.6 | -0.6
2210 | 50.057 | -0.61 | -0.57 | -0.57
2211 | 50.056 | -0.57 | -0.56 | -0.56
2212 | 50.055 | -0.49 | -0.55 | -0.55
2213 | 50.052 | -0.53 | -0.52 | -0.52
2214 | 50.052 | -0.535 | -0.52 | -0.52
2215 | 50.05 | -0.52 | -0.5 | -0.5
2216 | 50.047 | -0.49 | -0.47 | -0.47
2217 | 50.042 | -0.435 | -0.42 | -0.42
2218 | 50.039 | -0.425 | -0.39 | -0.39
2219 | 50.038 | -0.385 | -0.38 | -0.38
2220 | 50.036 | -0.38 | -0.36 | -0.36
2221 | 50.034 | -0.36 | -0.34 | -0.34
2222 | 50.031 | -0.35 | -0.31 | -0.31
2223 | 50.032 | -0.325 | -0.32 | -0.32
2224 | 50.035 | -0.345 | -0.35 | -0.35
2225 | 50.035 | -0.375 | -0.35 | -0.35
2226 | 50.035 | -0.36 | -0.35 | -0.35
2227 | 50.036 | -0.36 | -0.36 | -0.36
2228 | 50.036 | -0.37 | -0.36 | -0.36
2229 | 50.038 | -0.375 | -0.38 | -0.38
2230 | 50.04 | -0.4 | -0.4 | -0.4
2231 | 50.038 | -0.38 | -0.38 | -0.38
2232 | 50.039 | -0.4 | -0.39 | -0.39
2233 | 50.039 | -0.4 | -0.39 | -0.39
2234 | 50.039 | -0.415 | -0.39 | -0.39
2235 | 50.039 | -0.41 | -0.39 | -0.39
2236 | 50.04 | -0.4 | -0.4 | -0.4
2237 | 50.041 | -0.42 | -0.41 | -0.41
2238 | 50.041 | -0.43 | -0.41 | -0.41
2239 | 50.041 | -0.42 | -0.41 | -0.41
2240 | 50.043 | -0.42 | -0.43 | -0.43
2241 | 50.043 | -0.445 | -0.43 | -0.43
2242 | 50.045 | -0.455 | -0.45 | -0.45
2243 | 50.046 | -0.455 | -0.46 | -0.46
2244 | 50.05 | -0.505 | -0.5 | -0.5
2245 | 50.05 | -0.505 | -0.5 | -0.5
2246 | 50.05 | -0.52 | -0.5 | -0.5
2247 | 50.052 | -0.525 | -0.52 | -0.52
2248 | 50.053 | -0.54 | -0.53 | -0.53
2249 | 50.055 | -0.555 | -0.55 | -0.55
2250 | 50.058 | -0.6 | -0.58 | -0.58
2251 | 50.058 | -0.61 | -0.58 | -0.58
2252 | 50.062 | -0.615 | -0.62 | -0.62
2253 | 50.062 | -0.65 | -0.62 | -0.62
2254 | 50.063 | -0.66 | -0.63 | -0.63
2255 | 50.065 | -0.65 | -0.65 | -0.65
2256 | 50.065 | -0.66 | -0.65 | -0.65
2257 | 50.064 | -0.67 | -0.64 | -0.64
2258 | 50.064 | -0.665 | -0.64 | -0.64
2259 | 50.064 | -0.675 | -0.64 | -0.64
2260 | 50.065 | -0.66 | -0.65 | -0.65
2261 | 50.064 | -0.67 | -0.64 | -0.64
2262 | 50.064 | -0.665 | -0.64 | -0.64
2263 | 50.064 | -0.65 | -0.64 | -0.64
2264 | 50.063 | -0.645 | -0.63 | -0.63
2265 | 50.063 | -0.67 | -0.63 | -0.63
2266 | 50.063 | -0.66 | -0.63 | -0.63
2267 | 50.063 | -0.66 | -0.63 | -0.63
2268 | 50.067 | -0.695 | -0.67 | -0.67
2269 | 50.066 | -0.655 | -0.66 | -0.66
2270 | 50.065 | -0.665 | -0.65 | -0.65
2271 | 50.065 | -0.665 | -0.65 | -0.65
2272 | 50.064 | -0.675 | -0.64 | -0.64
2273 | 50.062 | -0.66 | -0.62 | -0.62
2274 | 50.063 | -0.675 | -0.63 | -0.63
2275 | 50.063 | -0.66 | -0.63 | -0.63
2276 | 50.064 | -0.645 | -0.64 | -0.64
2277 | 50.066 | -0.695 | -0.66 | -0.66
2278 | 50.068 | -0.725 | -0.68 | -0.68
2279 | 50.068 | -0.7 | -0.68 | -0.68
2280 | 50.067 | -0.71 | -0.67 | -0.67
2281 | 50.068 | -0.7 | -0.68 | -0.68
2282 | 50.067 | -0.7 | -0.67 | -0.67
2283 | 50.068 | -0.685 | -0.68 | -0.68
2284 | 50.069 | -0.685 | -0.69 | -0.69
2285 | 50.072 | -0.73 | -0.72 | -0.72
2286 | 50.074 | -0.75 | -0.74 | -0.74
2287 | 50.078 | -0.805 | -0.78 | -0.78
2288 | 50.078 | -0.81 | -0.78 | -0.78
2289 | 50.08 | -0.825 | -0.8 | -0.8
2290 | 50.083 | -0.83 | -0.83 | -0.83
2291 | 50.082 | -0.855 | -0.82 | -0.82
2292 | 50.085 | -0.85 | -0.85 | -0.85
2293 | 50.086 | -0.885 | -0.86 | -0.86
2294 | 50.089 | -0.92 | -0.89 | -0.89
2295 | 50.089 | -0.905 | -0.89 | -0.89
2296 | 50.09 | -0.9 | -0.9 | -0.9
2297 | 50.091 | -0.94 | -0.91 | -0.91
2298 | 50.091 | -0.935 | -0.91 | -0.91
2299 | 50.093 | -0.97 | -0.93 | -0.93
2300 | 50.094 | -0.975 | -0.94 | -0.94
2301 | 50.094 | -0.96 | -0.94 | -0.94
2302 | 50.092 | -0.955 | -0.92 | -0.92
2303 | 50.089 | -0.935 | -0.89 | -0.89
2304 | 50.087 | -0.91 | -0.87 | -0.87
2305 | 50.086 | -0.9 | -0.86 | -0.86
2306 | 50.086 | -0.89 | -0.86 | -0.86
2307 | 50.084 | -0.855 | -0.84 | -0.84
2308 | 50.084 | -0.865 | -0.84 | -0.84
2309 | 50.084 | -0.87 | -0.84 | -0.84
2310 | 50.085 | -0.88 | -0.85 | -0.85
2311 | 50.084 | -0.885 | -0.84 | -0.84
2312 | 50.084 | -0.885 | -0.84 | -0.84
2313 | 50.084 | -0.865 | -0.84 | -0.84
2314 | 50.084 | -0.875 | -0.84 | -0.84
2315 | 50.084 | -0.86 | -0.84 | -0.84
2316 | 50.085 | -0.875 | -0.85 | -0.85
2317 | 50.088 | -0.89 | -0.88 | -0.88
2318 | 50.087 | -0.915 | -0.87 | -0.87
2319 | 50.088 | -0.905 | -0.88 | -0.88
2320 | 50.088 | -0.905 | -0.88 | -0.88
2321 | 50.091 | -0.905 | -0.91 | -0.91
2322 | 50.091 | -0.925 | -0.91 | -0.91
2323 | 50.09 | -0.92 | -0.9 | -0.9
2324 | 50.086 | -0.925 | -0.86 | -0.86
2325 | 50.086 | -0.905 | -0.86 | -0.86
2326 | 50.085 | -0.875 | -0.85 | -0.85
2327 | 50.083 | -0.855 | -0.83 | -0.83
2328 | 50.08 | -0.855 | -0.8 | -0.8
2329 | 50.079 | -0.815 | -0.79 | -0.79
2330 | 50.074 | -0.8 | -0.74 | -0.74
2331 | 50.074 | -0.76 | -0.74 | -0.74
2332 | 50.073 | -0.76 | -0.73 | -0.73
2333 | 50.07 | -0.71 | -0.7 | -0.7
2334 | 50.069 | -0.745 | -0.69 | -0.69
2335 | 50.069 | -0.705 | -0.69 | -0.69
2336 | 50.068 | -0.695 | -0.68 | -0.68
2337 | 50.068 | -0.71 | -0.68 | -0.68
2338 | 50.067 | -0.71 | -0.67 | -0.67
2339 | 50.066 | -0.7 | -0.66 | -0.66
2340 | 50.065 | -0.66 | -0.65 | -0.65
2341 | 50.064 | -0.665 | -0.64 | -0.64
2342 | 50.064 | -0.67 | -0.64 | -0.64
2343 | 50.06 | -0.645 | -0.6 | -0.6
2344 | 50.059 | -0.615 | -0.59 | -0.59
2345 | 50.058 | -0.61 | -0.58 | -0.58
2346 | 50.055 | -0.57 | -0.55 | -0.55
2347 | 50.053 | -0.56 | -0.53 | -0.53
2348 | 50.05 | -0.525 | -0.5 | -0.5
2349 | 50.046 | -0.49 | -0.46 | -0.46
2350 | 50.042 | -0.45 | -0.42 | -0.42
2351 | 50.041 | -0.425 | -0.41 | -0.41
2352 | 50.039 | -0.39 | -0.39 | -0.39
2353 | 50.039 | -0.39 | -0.39 | -0.39
2354 | 50.036 | -0.395 | -0.36 | -0.36
2355 | 50.036 | -0.375 | -0.36 | -0.36
2356 | 50.036 | -0.375 | -0.36 | -0.36
2357 | 50.033 | -0.32 | -0.33 | -0.33
2358 | 50.029 | -0.3 | -0.29 | -0.29
2359 | 50.029 | -0.295 | -0.29 | -0.29
2360 | 50.028 | -0.31 | -0.28 | -0.28
2361 | 50.028 | -0.295 | -0.28 | -0.28
2362 | 50.028 | -0.285 | -0.28 | -0.28
2363 | 50.028 | -0.29 | -0.28 | -0.28
2364 | 50.027 | -0.275 | -0.27 | -0.27
2365 | 50.025 | -0.275 | -0.25 | -0.25
2366 | 50.026 | -0.26 | -0.26 | -0.26
2367 | 50.022 | -0.24 | -0.22 | -0.22
2368 | 50.02 | -0.195 | -0.2 | -0.2
2369 | 50.016 | -0.205 | -0.16 | -0.16
2370 | 50.016 | -0.165 | -0.16 | -0.16
2371 | 50.014 | 0 | -0.14 | 0
2372 | 50.013 | 0.01 | -0.13 | 0
2373 | 50.013 | 0.005 | -0.13 | 0
2374 | 50.013 | 0.015 | -0.13 | 0
2375 | 50.012 | 0.01 | -0.12 | 0
2376 | 50.01 | 0.01 | -0.1 | 0
2377 | 50.012 | 0 | -0.12 | 0
2378 | 50.011 | 0 | -0.11 | 0
2379 | 50.01 | -0.005 | -0.1 | 0
2380 | 50.011 | -0.015 | -0.11 | 0
2381 | 50.013 | -0.01 | -0.13 | 0
2382 | 50.013 | 0 | -0.13 | 0
2383 | 50.016 | 0 | -0.16 | -0.16
2384 | 50.015 | -0.015 | -0.15 | -0.15
2385 | 50.016 | -0.095 | -0.16 | -0.16
2386 | 50.017 | -0.165 | -0.17 | -0.17
2387 | 50.017 | -0.19 | -0.17 | -0.17
2388 | 50.014 | -0.15 | -0.14 | 0
2389 | 50.012 | -0.01 | -0.12 | 0
2390 | 50.012 | 0.01 | -0.12 | 0
2391 | 50.011 | 0.005 | -0.11 | 0
2392 | 50.011 | 0 | -0.11 | 0
2393 | 50.009 | -0.01 | -0.09 | 0
2394 | 50.009 | 0 | -0.09 | 0
2395 | 50.008 | -0.01 | -0.08 | 0
2396 | 50.01 | -0.01 | -0.1 | 0
2397 | 50.01 | -0.01 | -0.1 | 0
2398 | 50.008 | 0.005 | -0.08 | 0
2399 | 50.007 | 0.005 | -0.07 | 0
2400 | 50.002 | 0.005 | -0.02 | 0
2401 | 50 | 0.005 | 0 | 0
2402 | 49.999 | 0 | 0.01 | 0
2403 | 49.996 | -0.01 | 0.04 | 0
2404 | 49.993 | 0 | 0.07 | 0
2405 | 49.99 | 0.005 | 0.1 | 0
2406 | 49.988 | -0.005 | 0.12 | 0
2407 | 49.984 | -0.01 | 0.16 | 0.16
2408 | 49.985 | 0.045 | 0.15 | 0.15
2409 | 49.984 | 0.035 | 0.16 | 0.16
2410 | 49.984 | 0.165 | 0.16 | 0.16
2411 | 49.981 | 0.19 | 0.19 | 0.19
2412 | 49.98 | 0.21 | 0.2 | 0.2
2413 | 49.98 | 0.215 | 0.2 | 0.2
2414 | 49.979 | 0.225 | 0.21 | 0.21
2415 | 49.979 | 0.23 | 0.21 | 0.21
2416 | 49.979 | 0.22 | 0.21 | 0.21
2417 | 49.98 | 0.205 | 0.2 | 0.2
2418 | 49.98 | 0.22 | 0.2 | 0.2
2419 | 49.981 | 0.19 | 0.19 | 0.19
2420 | 49.98 | 0.205 | 0.2 | 0.2
2421 | 49.98 | 0.21 | 0.2 | 0.2
2422 | 49.979 | 0.22 | 0.21 | 0.21
2423 | 49.977 | 0.245 | 0.23 | 0.23
2424 | 49.977 | 0.24 | 0.23 | 0.23
2425 | 49.978 | 0.2 | 0.22 | 0.22
2426 | 49.981 | 0.225 | 0.19 | 0.19
2427 | 49.982 | 0.19 | 0.18 | 0.18
2428 | 49.983 | 0.19 | 0.17 | 0.17
2429 | 49.984 | 0.175 | 0.16 | 0.16
2430 | 49.986 | 0.01 | 0.14 | 0
2431 | 49.988 | 0.01 | 0.12 | 0
2432 | 49.988 | 0.005 | 0.12 | 0
2433 | 49.988 | -0.005 | 0.12 | 0
2434 | 49.987 | 0.01 | 0.13 | 0
2435 | 49.987 | -0.01 | 0.13 | 0
2436 | 49.986 | -0.01 | 0.14 | 0
2437 | 49.985 | 0 | 0.15 | 0.15
2438 | 49.985 | 0.035 | 0.15 | 0.15
2439 | 49.98 | 0.18 | 0.2 | 0.2
2440 | 49.982 | 0.19 | 0.18 | 0.18
2441 | 49.979 | 0.22 | 0.21 | 0.21
2442 | 49.978 | 0.225 | 0.22 | 0.22
2443 | 49.979 | 0.23 | 0.21 | 0.21
2444 | 49.98 | 0.21 | 0.2 | 0.2
2445 | 49.984 | 0.205 | 0.16 | 0.16
2446 | 49.985 | 0.165 | 0.15 | 0.15
2447 | 49.987 | 0 | 0.13 | 0
2448 | 49.99 | 0.005 | 0.1 | 0
2449 | 49.99 | 0 | 0.1 | 0
2450 | 49.993 | 0.01 | 0.07 | 0
2451 | 49.991 | 0.015 | 0.09 | 0
2452 | 49.991 | 0.005 | 0.09 | 0
2453 | 49.991 | 0.005 | 0.09 | 0
2454 | 49.992 | 0 | 0.08 | 0
2455 | 49.991 | 0 | 0.09 | 0
2456 | 49.989 | 0.005 | 0.11 | 0
2457 | 49.985 | 0 | 0.15 | 0.15
2458 | 49.981 | 0.1 | 0.19 | 0.19
2459 | 49.981 | 0.19 | 0.19 | 0.19
2460 | 49.978 | 0.22 | 0.22 | 0.22
2461 | 49.979 | 0.25 | 0.21 | 0.21
2462 | 49.975 | 0.23 | 0.25 | 0.25
2463 | 49.975 | 0.275 | 0.25 | 0.25
2464 | 49.974 | 0.275 | 0.26 | 0.26
2465 | 49.971 | 0.28 | 0.29 | 0.29
2466 | 49.973 | 0.28 | 0.27 | 0.27
2467 | 49.974 | 0.285 | 0.26 | 0.26
2468 | 49.974 | 0.28 | 0.26 | 0.26
2469 | 49.975 | 0.27 | 0.25 | 0.25
2470 | 49.976 | 0.295 | 0.24 | 0.24
2471 | 49.975 | 0.265 | 0.25 | 0.25
2472 | 49.975 | 0.265 | 0.25 | 0.25
2473 | 49.974 | 0.265 | 0.26 | 0.26
2474 | 49.974 | 0.265 | 0.26 | 0.26
2475 | 49.975 | 0.265 | 0.25 | 0.25
2476 | 49.976 | 0.25 | 0.24 | 0.24
2477 | 49.977 | 0.24 | 0.23 | 0.23
2478 | 49.979 | 0.225 | 0.21 | 0.21
2479 | 49.977 | 0.215 | 0.23 | 0.23
2480 | 49.979 | 0.21 | 0.21 | 0.21
2481 | 49.977 | 0.21 | 0.23 | 0.23
2482 | 49.975 | 0.235 | 0.25 | 0.25
2483 | 49.975 | 0.265 | 0.25 | 0.25
2484 | 49.973 | 0.285 | 0.27 | 0.27
2485 | 49.97 | 0.28 | 0.3 | 0.3
2486 | 49.97 | 0.3 | 0.3 | 0.3
2487 | 49.968 | 0.33 | 0.32 | 0.32
2488 | 49.965 | 0.345 | 0.35 | 0.35
2489 | 49.963 | 0.36 | 0.37 | 0.37
2490 | 49.963 | 0.36 | 0.37 | 0.37
2491 | 49.962 | 0.38 | 0.38 | 0.38
2492 | 49.961 | 0.39 | 0.39 | 0.39
2493 | 49.959 | 0.42 | 0.41 | 0.41
2494 | 49.959 | 0.415 | 0.41 | 0.41
2495 | 49.958 | 0.425 | 0.42 | 0.42
2496 | 49.958 | 0.44 | 0.42 | 0.42
2497 | 49.956 | 0.45 | 0.44 | 0.44
2498 | 49.954 | 0.46 | 0.46 | 0.46
2499 | 49.954 | 0.48 | 0.46 | 0.46
2500 | 49.954 | 0.49 | 0.46 | 0.46
2501 | 49.954 | 0.48 | 0.46 | 0.46
2502 | 49.955 | 0.485 | 0.45 | 0.45
2503 | 49.956 | 0.45 | 0.44 | 0.44
2504 | 49.957 | 0.455 | 0.43 | 0.43
2505 | 49.957 | 0.43 | 0.43 | 0.43
2506 | 49.957 | 0.445 | 0.43 | 0.43
2507 | 49.958 | 0.445 | 0.42 | 0.42
2508 | 49.964 | 0.435 | 0.36 | 0.36
2509 | 49.958 | 0.445 | 0.42 | 0.42
2510 | 49.958 | 0.435 | 0.42 | 0.42
2511 | 49.958 | 0.43 | 0.42 | 0.42
2512 | 49.958 | 0.455 | 0.42 | 0.42
2513 | 49.956 | 0.455 | 0.44 | 0.44
2514 | 49.956 | 0.46 | 0.44 | 0.44
2515 | 49.954 | 0.485 | 0.46 | 0.46
2516 | 49.95 | 0.52 | 0.5 | 0.5
2517 | 49.947 | 0.52 | 0.53 | 0.53
2518 | 49.946 | 0.555 | 0.54 | 0.54
2519 | 49.942 | 0.59 | 0.58 | 0.58
2520 | 49.941 | 0.605 | 0.59 | 0.59
2521 | 49.939 | 0.59 | 0.61 | 0.61
2522 | 49.939 | 0.605 | 0.61 | 0.61
2523 | 49.938 | 0.635 | 0.62 | 0.62
2524 | 49.937 | 0.64 | 0.63 | 0.63
2525 | 49.937 | 0.66 | 0.63 | 0.63
2526 | 49.936 | 0.65 | 0.64 | 0.64
2527 | 49.934 | 0.685 | 0.66 | 0.66
2528 | 49.931 | 0.7 | 0.69 | 0.69
2529 | 49.93 | 0.72 | 0.7 | 0.7
2530 | 49.929 | 0.725 | 0.71 | 0.71
2531 | 49.928 | 0.75 | 0.72 | 0.72
2532 | 49.925 | 0.775 | 0.75 | 0.75
2533 | 49.926 | 0.795 | 0.74 | 0.74
2534 | 49.926 | 0.805 | 0.74 | 0.74
2535 | 49.923 | 0.775 | 0.77 | 0.77
2536 | 49.923 | 0.795 | 0.77 | 0.77
2537 | 49.92 | 0.805 | 0.8 | 0.8
2538 | 49.921 | 0.82 | 0.79 | 0.79
2539 | 49.921 | 0.815 | 0.79 | 0.79
2540 | 49.922 | 0.815 | 0.78 | 0.78
2541 | 49.922 | 0.815 | 0.78 | 0.78
2542 | 49.922 | 0.78 | 0.78 | 0.78
2543 | 49.923 | 0.795 | 0.77 | 0.77
2544 | 49.923 | 0.795 | 0.77 | 0.77
2545 | 49.923 | 0.795 | 0.77 | 0.77
2546 | 49.923 | 0.8 | 0.77 | 0.77
2547 | 49.923 | 0.81 | 0.77 | 0.77
2548 | 49.92 | 0.8 | 0.8 | 0.8
2549 | 49.92 | 0.815 | 0.8 | 0.8
2550 | 49.917 | 0.81 | 0.83 | 0.83
2551 | 49.914 | 0.85 | 0.86 | 0.86
2552 | 49.913 | 0.89 | 0.87 | 0.87
2553 | 49.91 | 0.93 | 0.9 | 0.9
2554 | 49.91 | 0.915 | 0.9 | 0.9
2555 | 49.907 | 0.925 | 0.93 | 0.93
2556 | 49.907 | 0.95 | 0.93 | 0.93
2557 | 49.907 | 0.96 | 0.93 | 0.93
2558 | 49.909 | 0.96 | 0.91 | 0.91
2559 | 49.907 | 0.935 | 0.93 | 0.93
2560 | 49.907 | 0.905 | 0.93 | 0.93
2561 | 49.907 | 0.95 | 0.93 | 0.93
2562 | 49.908 | 0.965 | 0.92 | 0.92
2563 | 49.906 | 0.985 | 0.94 | 0.94
2564 | 49.905 | 1 | 0.95 | 0.95
2565 | 49.905 | 0.985 | 0.95 | 0.95
2566 | 49.902 | 0.995 | 0.98 | 0.98
2567 | 49.905 | 0.975 | 0.95 | 0.95
2568 | 49.904 | 1 | 0.96 | 0.96
2569 | 49.902 | 1 | 0.98 | 0.98
2570 | 49.903 | 1.005 | 0.97 | 0.97
2571 | 49.906 | 0.995 | 0.94 | 0.94
2572 | 49.905 | 0.975 | 0.95 | 0.95
2573 | 49.908 | 0.985 | 0.92 | 0.92
2574 | 49.908 | 0.945 | 0.92 | 0.92
2575 | 49.912 | 0.925 | 0.88 | 0.88
2576 | 49.915 | 0.885 | 0.85 | 0.85
2577 | 49.917 | 0.85 | 0.83 | 0.83
2578 | 49.92 | 0.85 | 0.8 | 0.8
2579 | 49.92 | 0.815 | 0.8 | 0.8
2580 | 49.921 | 0.815 | 0.79 | 0.79
2581 | 49.918 | 0.84 | 0.82 | 0.82
2582 | 49.917 | 0.83 | 0.83 | 0.83
2583 | 49.917 | 0.855 | 0.83 | 0.83
2584 | 49.917 | 0.87 | 0.83 | 0.83
2585 | 49.921 | 0.825 | 0.79 | 0.79
2586 | 49.925 | 0.805 | 0.75 | 0.75
2587 | 49.927 | 0.755 | 0.73 | 0.73
2588 | 49.928 | 0.755 | 0.72 | 0.72
2589 | 49.932 | 0.74 | 0.68 | 0.68
2590 | 49.932 | 0.705 | 0.68 | 0.68
2591 | 49.934 | 0.7 | 0.66 | 0.66
2592 | 49.935 | 0.67 | 0.65 | 0.65
2593 | 49.935 | 0.665 | 0.65 | 0.65
2594 | 49.936 | 0.665 | 0.64 | 0.64
2595 | 49.935 | 0.655 | 0.65 | 0.65
2596 | 49.933 | 0.695 | 0.67 | 0.67
2597 | 49.929 | 0.695 | 0.71 | 0.71
2598 | 49.928 | 0.735 | 0.72 | 0.72
2599 | 49.922 | 0.79 | 0.78 | 0.78
2600 | 49.921 | 0.795 | 0.79 | 0.79
2601 | 49.918 | 0.805 | 0.82 | 0.82
2602 | 49.915 | 0.875 | 0.85 | 0.85
2603 | 49.912 | 0.895 | 0.88 | 0.88
2604 | 49.91 | 0.905 | 0.9 | 0.9
2605 | 49.909 | 0.935 | 0.91 | 0.91
2606 | 49.909 | 0.94 | 0.91 | 0.91
2607 | 49.913 | 0.925 | 0.87 | 0.87
2608 | 49.913 | 0.91 | 0.87 | 0.87
2609 | 49.916 | 0.88 | 0.84 | 0.84
2610 | 49.919 | 0.85 | 0.81 | 0.81
2611 | 49.921 | 0.83 | 0.79 | 0.79
2612 | 49.924 | 0.815 | 0.76 | 0.76
2613 | 49.925 | 0.775 | 0.75 | 0.75
2614 | 49.928 | 0.765 | 0.72 | 0.72
2615 | 49.929 | 0.745 | 0.71 | 0.71
2616 | 49.93 | 0.725 | 0.7 | 0.7
2617 | 49.931 | 0.715 | 0.69 | 0.69
2618 | 49.936 | 0.675 | 0.64 | 0.64
2619 | 49.94 | 0.655 | 0.6 | 0.6
2620 | 49.94 | 0.62 | 0.6 | 0.6
2621 | 49.944 | 0.6 | 0.56 | 0.56
2622 | 49.947 | 0.55 | 0.53 | 0.53
2623 | 49.952 | 0.53 | 0.48 | 0.48
2624 | 49.953 | 0.5 | 0.47 | 0.47
2625 | 49.954 | 0.48 | 0.46 | 0.46
2626 | 49.957 | 0.47 | 0.43 | 0.43
2627 | 49.959 | 0.45 | 0.41 | 0.41
2628 | 49.96 | 0.435 | 0.4 | 0.4
2629 | 49.962 | 0.4 | 0.38 | 0.38
2630 | 49.962 | 0.385 | 0.38 | 0.38
2631 | 49.962 | 0.335 | 0.38 | 0.38
2632 | 49.964 | 0.38 | 0.36 | 0.36
2633 | 49.962 | 0.375 | 0.38 | 0.38
2634 | 49.961 | 0.39 | 0.39 | 0.39
2635 | 49.961 | 0.4 | 0.39 | 0.39
2636 | 49.96 | 0.405 | 0.4 | 0.4
2637 | 49.956 | 0.415 | 0.44 | 0.44
2638 | 49.954 | 0.445 | 0.46 | 0.46
2639 | 49.953 | 0.505 | 0.47 | 0.47
2640 | 49.952 | 0.475 | 0.48 | 0.48
2641 | 49.951 | 0.495 | 0.49 | 0.49
2642 | 49.951 | 0.5 | 0.49 | 0.49
2643 | 49.954 | 0.495 | 0.46 | 0.46
2644 | 49.956 | 0.47 | 0.44 | 0.44
2645 | 49.959 | 0.425 | 0.41 | 0.41
2646 | 49.965 | 0.4 | 0.35 | 0.35
2647 | 49.969 | 0.36 | 0.31 | 0.31
2648 | 49.972 | 0.32 | 0.28 | 0.28
2649 | 49.977 | 0.255 | 0.23 | 0.23
2650 | 49.982 | 0.195 | 0.18 | 0.18
2651 | 49.985 | 0.085 | 0.15 | 0.15
2652 | 49.989 | 0.01 | 0.11 | 0
2653 | 49.994 | 0 | 0.06 | 0
2654 | 49.999 | -0.005 | 0.01 | 0
2655 | 50 | 0 | 0 | 0
2656 | 50.002 | 0.005 | -0.02 | 0
2657 | 50.005 | 0 | -0.05 | 0
2658 | 50.009 | 0 | -0.09 | 0
2659 | 50.009 | 0 | -0.09 | 0
2660 | 50.01 | 0.005 | -0.1 | 0
2661 | 50.01 | 0.005 | -0.1 | 0
2662 | 50.011 | 0.005 | -0.11 | 0
2663 | 50.012 | 0.005 | -0.12 | 0
2664 | 50.013 | 0.01 | -0.13 | 0
2665 | 50.014 | 0.01 | -0.14 | 0
2666 | 50.016 | -0.145 | -0.16 | -0.16
2667 | 50.019 | -0.19 | -0.19 | -0.19
2668 | 50.022 | -0.21 | -0.22 | -0.22
2669 | 50.025 | -0.255 | -0.25 | -0.25
2670 | 50.028 | -0.275 | -0.28 | -0.28
2671 | 50.031 | -0.31 | -0.31 | -0.31
2672 | 50.031 | -0.315 | -0.31 | -0.31
2673 | 50.032 | -0.325 | -0.32 | -0.32
2674 | 50.032 | -0.25 | -0.32 | -0.32
2675 | 50.034 | -0.355 | -0.34 | -0.34
2676 | 50.035 | -0.375 | -0.35 | -0.35
2677 | 50.037 | -0.37 | -0.37 | -0.37
2678 | 50.039 | -0.41 | -0.39 | -0.39
2679 | 50.041 | -0.42 | -0.41 | -0.41
2680 | 50.041 | -0.44 | -0.41 | -0.41
2681 | 50.045 | -0.43 | -0.45 | -0.45
2682 | 50.045 | -0.455 | -0.45 | -0.45
2683 | 50.045 | -0.46 | -0.45 | -0.45
2684 | 50.046 | -0.47 | -0.46 | -0.46
2685 | 50.047 | -0.47 | -0.47 | -0.47
2686 | 50.048 | -0.48 | -0.48 | -0.48
2687 | 50.048 | -0.515 | -0.48 | -0.48
2688 | 50.05 | -0.525 | -0.5 | -0.5
2689 | 50.051 | -0.53 | -0.51 | -0.51
2690 | 50.052 | -0.54 | -0.52 | -0.52
2691 | 50.054 | -0.55 | -0.54 | -0.54
2692 | 50.055 | -0.54 | -0.55 | -0.55
2693 | 50.055 | -0.565 | -0.55 | -0.55
2694 | 50.051 | -0.555 | -0.51 | -0.51
2695 | 50.053 | -0.54 | -0.53 | -0.53
2696 | 50.053 | -0.565 | -0.53 | -0.53
2697 | 50.053 | -0.545 | -0.53 | -0.53
2698 | 50.053 | -0.565 | -0.53 | -0.53
2699 | 50.052 | -0.555 | -0.52 | -0.52
2700 | 50.051 | -0.545 | -0.51 | -0.51
2701 | 50.05 | -0.52 | -0.5 | -0.5
2702 | 50.049 | -0.52 | -0.49 | -0.49
2703 | 50.052 | -0.535 | -0.52 | -0.52
2704 | 50.051 | -0.52 | -0.51 | -0.51
2705 | 50.051 | -0.49 | -0.51 | -0.51
2706 | 50.05 | -0.535 | -0.5 | -0.5
2707 | 50.05 | -0.52 | -0.5 | -0.5
2708 | 50.05 | -0.515 | -0.5 | -0.5
2709 | 50.051 | -0.53 | -0.51 | -0.51
2710 | 50.052 | -0.535 | -0.52 | -0.52
2711 | 50.052 | -0.535 | -0.52 | -0.52
2712 | 50.052 | -0.54 | -0.52 | -0.52
2713 | 50.051 | -0.52 | -0.51 | -0.51
2714 | 50.051 | -0.525 | -0.51 | -0.51
2715 | 50.051 | -0.525 | -0.51 | -0.51
2716 | 50.051 | -0.53 | -0.51 | -0.51
2717 | 50.052 | -0.53 | -0.52 | -0.52
2718 | 50.053 | -0.535 | -0.53 | -0.53
2719 | 50.053 | -0.55 | -0.53 | -0.53
2720 | 50.054 | -0.565 | -0.54 | -0.54
2721 | 50.057 | -0.57 | -0.57 | -0.57
2722 | 50.057 | -0.6 | -0.57 | -0.57
2723 | 50.057 | -0.59 | -0.57 | -0.57
2724 | 50.057 | -0.59 | -0.57 | -0.57
2725 | 50.058 | -0.6 | -0.58 | -0.58
2726 | 50.057 | -0.6 | -0.57 | -0.57
2727 | 50.06 | -0.595 | -0.6 | -0.6
2728 | 50.055 | -0.58 | -0.55 | -0.55
2729 | 50.053 | -0.55 | -0.53 | -0.53
2730 | 50.053 | -0.555 | -0.53 | -0.53
2731 | 50.053 | -0.555 | -0.53 | -0.53
2732 | 50.05 | -0.52 | -0.5 | -0.5
2733 | 50.052 | -0.53 | -0.52 | -0.52
2734 | 50.054 | -0.56 | -0.54 | -0.54
2735 | 50.055 | -0.555 | -0.55 | -0.55
2736 | 50.055 | -0.55 | -0.55 | -0.55
2737 | 50.056 | -0.58 | -0.56 | -0.56
2738 | 50.058 | -0.59 | -0.58 | -0.58
2739 | 50.056 | -0.585 | -0.56 | -0.56
2740 | 50.057 | -0.6 | -0.57 | -0.57
2741 | 50.058 | -0.59 | -0.58 | -0.58
2742 | 50.057 | -0.6 | -0.57 | -0.57
2743 | 50.057 | -0.59 | -0.57 | -0.57
2744 | 50.056 | -0.565 | -0.56 | -0.56
2745 | 50.056 | -0.58 | -0.56 | -0.56
2746 | 50.057 | -0.595 | -0.57 | -0.57
2747 | 50.057 | -0.6 | -0.57 | -0.57
2748 | 50.057 | -0.585 | -0.57 | -0.57
2749 | 50.058 | -0.595 | -0.58 | -0.58
2750 | 50.058 | -0.59 | -0.58 | -0.58
2751 | 50.058 | -0.6 | -0.58 | -0.58
2752 | 50.058 | -0.65 | -0.58 | -0.58
2753 | 50.058 | -0.595 | -0.58 | -0.58
2754 | 50.058 | -0.605 | -0.58 | -0.58
2755 | 50.061 | -0.64 | -0.61 | -0.61
2756 | 50.061 | -0.64 | -0.61 | -0.61
2757 | 50.059 | -0.635 | -0.59 | -0.59
2758 | 50.057 | -0.6 | -0.57 | -0.57
2759 | 50.054 | -0.56 | -0.54 | -0.54
2760 | 50.051 | -0.565 | -0.51 | -0.51
2761 | 50.05 | -0.51 | -0.5 | -0.5
2762 | 50.046 | -0.505 | -0.46 | -0.46
2763 | 50.047 | -0.485 | -0.47 | -0.47
2764 | 50.046 | -0.49 | -0.46 | -0.46
2765 | 50.046 | -0.47 | -0.46 | -0.46
2766 | 50.046 | -0.475 | -0.46 | -0.46
2767 | 50.044 | -0.445 | -0.44 | -0.44
2768 | 50.046 | -0.475 | -0.46 | -0.46
2769 | 50.049 | -0.465 | -0.49 | -0.49
2770 | 50.048 | -0.48 | -0.48 | -0.48
2771 | 50.05 | -0.51 | -0.5 | -0.5
2772 | 50.051 | -0.515 | -0.51 | -0.51
2773 | 50.053 | -0.53 | -0.53 | -0.53
2774 | 50.055 | -0.58 | -0.55 | -0.55
2775 | 50.059 | -0.575 | -0.59 | -0.59
2776 | 50.058 | -0.59 | -0.58 | -0.58
2777 | 50.058 | -0.59 | -0.58 | -0.58
2778 | 50.058 | -0.585 | -0.58 | -0.58
2779 | 50.058 | -0.605 | -0.58 | -0.58
2780 | 50.053 | -0.61 | -0.53 | -0.53
2781 | 50.063 | -0.67 | -0.63 | -0.63
2782 | 50.06 | -0.625 | -0.6 | -0.6
2783 | 50.061 | -0.625 | -0.61 | -0.61
2784 | 50.06 | -0.615 | -0.6 | -0.6
2785 | 50.063 | -0.64 | -0.63 | -0.63
2786 | 50.064 | -0.655 | -0.64 | -0.64
2787 | 50.064 | -0.67 | -0.64 | -0.64
2788 | 50.064 | -0.675 | -0.64 | -0.64
2789 | 50.065 | -0.66 | -0.65 | -0.65
2790 | 50.065 | -0.67 | -0.65 | -0.65
2791 | 50.064 | -0.665 | -0.64 | -0.64
2792 | 50.063 | -0.645 | -0.63 | -0.63
2793 | 50.062 | -0.66 | -0.62 | -0.62
2794 | 50.062 | -0.645 | -0.62 | -0.62
2795 | 50.062 | -0.65 | -0.62 | -0.62
2796 | 50.061 | -0.655 | -0.61 | -0.61
2797 | 50.061 | -0.625 | -0.61 | -0.61
2798 | 50.061 | -0.63 | -0.61 | -0.61
2799 | 50.059 | -0.615 | -0.59 | -0.59
2800 | 50.059 | -0.595 | -0.59 | -0.59
2801 | 50.059 | -0.62 | -0.59 | -0.59
2802 | 50.059 | -0.61 | -0.59 | -0.59
2803 | 50.059 | -0.615 | -0.59 | -0.59
2804 | 50.059 | -0.635 | -0.59 | -0.59
2805 | 50.06 | -0.615 | -0.6 | -0.6
2806 | 50.059 | -0.615 | -0.59 | -0.59
2807 | 50.06 | -0.62 | -0.6 | -0.6
2808 | 50.059 | -0.61 | -0.59 | -0.59
2809 | 50.059 | -0.615 | -0.59 | -0.59
2810 | 50.059 | -0.615 | -0.59 | -0.59
2811 | 50.059 | -0.61 | -0.59 | -0.59
2812 | 50.06 | -0.63 | -0.6 | -0.6
2813 | 50.06 | -0.61 | -0.6 | -0.6
2814 | 50.06 | -0.61 | -0.6 | -0.6
2815 | 50.06 | -0.61 | -0.6 | -0.6
2816 | 50.056 | -0.6 | -0.56 | -0.56
2817 | 50.053 | -0.54 | -0.53 | -0.53
2818 | 50.048 | -0.52 | -0.48 | -0.48
2819 | 50.044 | -0.495 | -0.44 | -0.44
2820 | 50.04 | -0.44 | -0.4 | -0.4
2821 | 50.037 | -0.39 | -0.37 | -0.37
2822 | 50.033 | -0.355 | -0.33 | -0.33
2823 | 50.03 | -0.325 | -0.3 | -0.3
2824 | 50.027 | -0.305 | -0.27 | -0.27
2825 | 50.026 | -0.265 | -0.26 | -0.26
2826 | 50.024 | -0.25 | -0.24 | -0.24
2827 | 50.022 | -0.225 | -0.22 | -0.22
2828 | 50.021 | -0.22 | -0.21 | -0.21
2829 | 50.017 | -0.205 | -0.17 | -0.17
2830 | 50.016 | -0.185 | -0.16 | -0.16
2831 | 50.016 | -0.105 | -0.16 | -0.16
2832 | 50.016 | -0.165 | -0.16 | -0.16
2833 | 50.016 | -0.155 | -0.16 | -0.16
2834 | 50.015 | 0.01 | -0.15 | -0.15
2835 | 50.015 | 0.01 | -0.15 | -0.15
2836 | 50.014 | 0.01 | -0.14 | 0
2837 | 50.013 | 0 | -0.13 | 0
2838 | 50.013 | 0.01 | -0.13 | 0
2839 | 50.012 | 0 | -0.12 | 0
2840 | 50.012 | 0.01 | -0.12 | 0
2841 | 50.016 | 0 | -0.16 | -0.16
2842 | 50.017 | -0.015 | -0.17 | -0.17
2843 | 50.017 | -0.19 | -0.17 | -0.17
2844 | 50.018 | -0.225 | -0.18 | -0.18
2845 | 50.02 | -0.215 | -0.2 | -0.2
2846 | 50.021 | -0.205 | -0.21 | -0.21
2847 | 50.021 | -0.215 | -0.21 | -0.21
2848 | 50.021 | -0.205 | -0.21 | -0.21
2849 | 50.025 | -0.26 | -0.25 | -0.25
2850 | 50.029 | -0.275 | -0.29 | -0.29
2851 | 50.026 | -0.3 | -0.26 | -0.26
2852 | 50.03 | -0.3 | -0.3 | -0.3
2853 | 50.03 | -0.325 | -0.3 | -0.3
2854 | 50.03 | -0.25 | -0.3 | -0.3
2855 | 50.03 | -0.31 | -0.3 | -0.3
2856 | 50.03 | -0.325 | -0.3 | -0.3
2857 | 50.03 | -0.3 | -0.3 | -0.3
2858 | 50.029 | -0.295 | -0.29 | -0.29
2859 | 50.03 | -0.29 | -0.3 | -0.3
2860 | 50.029 | -0.29 | -0.29 | -0.29
2861 | 50.029 | -0.3 | -0.29 | -0.29
2862 | 50.029 | -0.31 | -0.29 | -0.29
2863 | 50.03 | -0.3 | -0.3 | -0.3
2864 | 50.033 | -0.3 | -0.33 | -0.33
2865 | 50.034 | -0.345 | -0.34 | -0.34
2866 | 50.034 | -0.35 | -0.34 | -0.34
2867 | 50.035 | -0.355 | -0.35 | -0.35
2868 | 50.035 | -0.365 | -0.35 | -0.35
2869 | 50.034 | -0.345 | -0.34 | -0.34
2870 | 50.035 | -0.355 | -0.35 | -0.35
2871 | 50.034 | -0.375 | -0.34 | -0.34
2872 | 50.035 | -0.375 | -0.35 | -0.35
2873 | 50.035 | -0.36 | -0.35 | -0.35
2874 | 50.035 | -0.36 | -0.35 | -0.35
2875 | 50.038 | -0.39 | -0.38 | -0.38
2876 | 50.039 | -0.4 | -0.39 | -0.39
2877 | 50.043 | -0.42 | -0.43 | -0.43
2878 | 50.042 | -0.43 | -0.42 | -0.42
2879 | 50.041 | -0.435 | -0.41 | -0.41
2880 | 50.04 | -0.43 | -0.4 | -0.4
2881 | 50.041 | -0.45 | -0.41 | -0.41
2882 | 50.04 | -0.42 | -0.4 | -0.4
2883 | 50.041 | -0.43 | -0.41 | -0.41
2884 | 50.041 | -0.43 | -0.41 | -0.41
2885 | 50.04 | -0.42 | -0.4 | -0.4
2886 | 50.04 | -0.4 | -0.4 | -0.4
2887 | 50.039 | -0.395 | -0.39 | -0.39
2888 | 50.039 | -0.405 | -0.39 | -0.39
2889 | 50.039 | -0.41 | -0.39 | -0.39
2890 | 50.039 | -0.395 | -0.39 | -0.39
2891 | 50.037 | -0.395 | -0.37 | -0.37
2892 | 50.036 | -0.37 | -0.36 | -0.36
2893 | 50.033 | -0.38 | -0.33 | -0.33
2894 | 50.035 | -0.355 | -0.35 | -0.35
2895 | 50.033 | -0.365 | -0.33 | -0.33
2896 | 50.03 | -0.35 | -0.3 | -0.3
2897 | 50.03 | -0.325 | -0.3 | -0.3
2898 | 50.03 | -0.325 | -0.3 | -0.3
2899 | 50.026 | -0.305 | -0.26 | -0.26
2900 | 50.027 | -0.285 | -0.27 | -0.27
2901 | 50.024 | -0.265 | -0.24 | -0.24
2902 | 50.023 | -0.245 | -0.23 | -0.23
2903 | 50.023 | -0.24 | -0.23 | -0.23
2904 | 50.022 | -0.245 | -0.22 | -0.22
2905 | 50.02 | -0.225 | -0.2 | -0.2
2906 | 50.017 | -0.195 | -0.17 | -0.17
2907 | 50.015 | -0.165 | -0.15 | -0.15
2908 | 50.014 | -0.005 | -0.14 | 0
2909 | 50.015 | 0.01 | -0.15 | -0.15
2910 | 50.016 | -0.015 | -0.16 | -0.16
2911 | 50.016 | -0.185 | -0.16 | -0.16
2912 | 50.019 | -0.19 | -0.19 | -0.19
2913 | 50.022 | -0.215 | -0.22 | -0.22
2914 | 50.022 | -0.225 | -0.22 | -0.22
2915 | 50.023 | -0.265 | -0.23 | -0.23
2916 | 50.028 | -0.285 | -0.28 | -0.28
2917 | 50.025 | -0.255 | -0.25 | -0.25
2918 | 50.027 | -0.265 | -0.27 | -0.27
2919 | 50.024 | -0.265 | -0.24 | -0.24
2920 | 50.024 | -0.26 | -0.24 | -0.24
2921 | 50.022 | -0.255 | -0.22 | -0.22
2922 | 50.026 | -0.25 | -0.26 | -0.26
2923 | 50.023 | -0.28 | -0.23 | -0.23
2924 | 50.024 | -0.245 | -0.24 | -0.24
2925 | 50.024 | -0.25 | -0.24 | -0.24
2926 | 50.023 | -0.25 | -0.23 | -0.23
2927 | 50.024 | -0.25 | -0.24 | -0.24
2928 | 50.025 | -0.27 | -0.25 | -0.25
2929 | 50.025 | -0.265 | -0.25 | -0.25
2930 | 50.025 | -0.25 | -0.25 | -0.25
2931 | 50.023 | -0.17 | -0.23 | -0.23
2932 | 50.023 | -0.23 | -0.23 | -0.23
2933 | 50.022 | -0.225 | -0.22 | -0.22
2934 | 50.022 | -0.22 | -0.22 | -0.22
2935 | 50.02 | -0.195 | -0.2 | -0.2
2936 | 50.019 | -0.2 | -0.19 | -0.19
2937 | 50.02 | -0.2 | -0.2 | -0.2
2938 | 50.019 | -0.195 | -0.19 | -0.19
2939 | 50.02 | -0.205 | -0.2 | -0.2
2940 | 50.02 | -0.2 | -0.2 | -0.2
2941 | 50.021 | -0.205 | -0.21 | -0.21
2942 | 50.021 | -0.225 | -0.21 | -0.21
2943 | 50.024 | -0.26 | -0.24 | -0.24
2944 | 50.025 | -0.26 | -0.25 | -0.25
2945 | 50.028 | -0.28 | -0.28 | -0.28
2946 | 50.027 | -0.29 | -0.27 | -0.27
2947 | 50.027 | -0.265 | -0.27 | -0.27
2948 | 50.028 | -0.305 | -0.28 | -0.28
2949 | 50.025 | -0.28 | -0.25 | -0.25
2950 | 50.023 | -0.255 | -0.23 | -0.23
2951 | 50.023 | -0.26 | -0.23 | -0.23
2952 | 50.024 | -0.24 | -0.24 | -0.24
2953 | 50.024 | -0.255 | -0.24 | -0.24
2954 | 50.024 | -0.255 | -0.24 | -0.24
2955 | 50.024 | -0.25 | -0.24 | -0.24
2956 | 50.024 | -0.265 | -0.24 | -0.24
2957 | 50.021 | -0.27 | -0.21 | -0.21
2958 | 50.023 | -0.195 | -0.23 | -0.23
2959 | 50.023 | -0.225 | -0.23 | -0.23
2960 | 50.02 | -0.22 | -0.2 | -0.2
2961 | 50.021 | -0.215 | -0.21 | -0.21
2962 | 50.021 | -0.215 | -0.21 | -0.21
2963 | 50.019 | -0.195 | -0.19 | -0.19
2964 | 50.017 | -0.205 | -0.17 | -0.17
2965 | 50.017 | -0.185 | -0.17 | -0.17
2966 | 50.014 | -0.18 | -0.14 | 0
2967 | 50.015 | -0.07 | -0.15 | -0.15
2968 | 50.016 | -0.165 | -0.16 | -0.16
2969 | 50.016 | -0.17 | -0.16 | -0.16
2970 | 50.016 | -0.16 | -0.16 | -0.16
2971 | 50.014 | 0.005 | -0.14 | 0
2972 | 50.013 | -0.005 | -0.13 | 0
2973 | 50.011 | 0 | -0.11 | 0
2974 | 50.012 | -0.01 | -0.12 | 0
2975 | 50.013 | 0 | -0.13 | 0
2976 | 50.014 | 0.005 | -0.14 | 0
2977 | 50.016 | -0.17 | -0.16 | -0.16
2978 | 50.018 | -0.195 | -0.18 | -0.18
2979 | 50.022 | -0.24 | -0.22 | -0.22
2980 | 50.022 | -0.22 | -0.22 | -0.22
2981 | 50.025 | -0.23 | -0.25 | -0.25
2982 | 50.024 | -0.25 | -0.24 | -0.24
2983 | 50.021 | -0.255 | -0.21 | -0.21
2984 | 50.021 | -0.24 | -0.21 | -0.21
2985 | 50.021 | -0.225 | -0.21 | -0.21
2986 | 50.019 | -0.2 | -0.19 | -0.19
2987 | 50.016 | -0.195 | -0.16 | -0.16
2988 | 50.017 | -0.17 | -0.17 | -0.17
2989 | 50.016 | -0.17 | -0.16 | -0.16
2990 | 50.015 | -0.05 | -0.15 | -0.15
2991 | 50.012 | 0 | -0.12 | 0
2992 | 50.011 | 0 | -0.11 | 0
2993 | 50.01 | 0 | -0.1 | 0
2994 | 50.009 | -0.005 | -0.09 | 0
2995 | 50.005 | 0.01 | -0.05 | 0
2996 | 50.005 | -0.01 | -0.05 | 0
2997 | 50.005 | -0.005 | -0.05 | 0
2998 | 50.004 | -0.01 | -0.04 | 0
2999 | 50.003 | -0.01 | -0.03 | 0
3000 | 50.003 | -0.01 | -0.03 | 0
3001 | 50.004 | -0.01 | -0.04 | 0
3002 | 50.004 | 0 | -0.04 | 0
3003 | 50.003 | -0.01 | -0.03 | 0
3004 | 50.004 | 0 | -0.04 | 0
3005 | 50.005 | -0.005 | -0.05 | 0
3006 | 50.006 | 0 | -0.06 | 0
3007 | 50.009 | 0 | -0.09 | 0
3008 | 50.009 | 0.01 | -0.09 | 0
3009 | 50.012 | 0.005 | -0.12 | 0
3010 | 50.012 | 0 | -0.12 | 0
3011 | 50.013 | 0.005 | -0.13 | 0
3012 | 50.016 | -0.085 | -0.16 | -0.16
3013 | 50.015 | -0.19 | -0.15 | -0.15
3014 | 50.016 | -0.145 | -0.16 | -0.16
3015 | 50.017 | -0.195 | -0.17 | -0.17
3016 | 50.016 | -0.19 | -0.16 | -0.16
3017 | 50.016 | -0.185 | -0.16 | -0.16
3018 | 50.013 | -0.045 | -0.13 | 0
3019 | 50.012 | -0.01 | -0.12 | 0
3020 | 50.011 | -0.01 | -0.11 | 0
3021 | 50.01 | -0.005 | -0.1 | 0
3022 | 50.01 | -0.01 | -0.1 | 0
3023 | 50.009 | -0.01 | -0.09 | 0
3024 | 50.01 | -0.005 | -0.1 | 0
3025 | 50.01 | -0.01 | -0.1 | 0
3026 | 50.01 | 0 | -0.1 | 0
3027 | 50.011 | 0 | -0.11 | 0
3028 | 50.01 | -0.01 | -0.1 | 0
3029 | 50.011 | -0.015 | -0.11 | 0
3030 | 50.012 | -0.015 | -0.12 | 0
3031 | 50.012 | -0.015 | -0.12 | 0
3032 | 50.014 | -0.01 | -0.14 | 0
3033 | 50.014 | 0 | -0.14 | 0
3034 | 50.016 | -0.105 | -0.16 | -0.16
3035 | 50.017 | -0.175 | -0.17 | -0.17
3036 | 50.018 | -0.175 | -0.18 | -0.18
3037 | 50.019 | -0.18 | -0.19 | -0.19
3038 | 50.019 | -0.19 | -0.19 | -0.19
3039 | 50.018 | -0.185 | -0.18 | -0.18
3040 | 50.018 | -0.195 | -0.18 | -0.18
3041 | 50.018 | -0.19 | -0.18 | -0.18
3042 | 50.023 | -0.215 | -0.23 | -0.23
3043 | 50.02 | -0.215 | -0.2 | -0.2
3044 | 50.021 | -0.205 | -0.21 | -0.21
3045 | 50.022 | -0.225 | -0.22 | -0.22
3046 | 50.021 | -0.205 | -0.21 | -0.21
3047 | 50.024 | -0.24 | -0.24 | -0.24
3048 | 50.022 | -0.225 | -0.22 | -0.22
3049 | 50.022 | -0.215 | -0.22 | -0.22
3050 | 50.02 | -0.225 | -0.2 | -0.2
3051 | 50.02 | -0.205 | -0.2 | -0.2
3052 | 50.022 | -0.205 | -0.22 | -0.22
3053 | 50.022 | -0.21 | -0.22 | -0.22
3054 | 50.022 | -0.215 | -0.22 | -0.22
3055 | 50.023 | -0.225 | -0.23 | -0.23
3056 | 50.023 | -0.245 | -0.23 | -0.23
3057 | 50.021 | -0.22 | -0.21 | -0.21
3058 | 50.021 | -0.23 | -0.21 | -0.21
3059 | 50.02 | -0.22 | -0.2 | -0.2
3060 | 50.02 | -0.205 | -0.2 | -0.2
3061 | 50.019 | -0.205 | -0.19 | -0.19
3062 | 50.019 | -0.205 | -0.19 | -0.19
3063 | 50.019 | -0.205 | -0.19 | -0.19
3064 | 50.019 | -0.215 | -0.19 | -0.19
3065 | 50.019 | -0.21 | -0.19 | -0.19
3066 | 50.02 | -0.22 | -0.2 | -0.2
3067 | 50.021 | -0.215 | -0.21 | -0.21
3068 | 50.022 | -0.22 | -0.22 | -0.22
3069 | 50.022 | -0.21 | -0.22 | -0.22
3070 | 50.022 | -0.22 | -0.22 | -0.22
3071 | 50.025 | -0.22 | -0.25 | -0.25
3072 | 50.024 | -0.23 | -0.24 | -0.24
3073 | 50.025 | -0.255 | -0.25 | -0.25
3074 | 50.027 | -0.255 | -0.27 | -0.27
3075 | 50.028 | -0.255 | -0.28 | -0.28
3076 | 50.03 | -0.29 | -0.3 | -0.3
3077 | 50.033 | -0.31 | -0.33 | -0.33
3078 | 50.031 | -0.345 | -0.31 | -0.31
3079 | 50.033 | -0.35 | -0.33 | -0.33
3080 | 50.033 | -0.345 | -0.33 | -0.33
3081 | 50.032 | -0.345 | -0.32 | -0.32
3082 | 50.033 | -0.335 | -0.33 | -0.33
3083 | 50.032 | -0.345 | -0.32 | -0.32
3084 | 50.029 | -0.33 | -0.29 | -0.29
3085 | 50.029 | -0.31 | -0.29 | -0.29
3086 | 50.028 | -0.315 | -0.28 | -0.28
3087 | 50.028 | -0.255 | -0.28 | -0.28
3088 | 50.028 | -0.29 | -0.28 | -0.28
3089 | 50.029 | -0.3 | -0.29 | -0.29
3090 | 50.03 | -0.305 | -0.3 | -0.3
3091 | 50.032 | -0.325 | -0.32 | -0.32
3092 | 50.033 | -0.32 | -0.33 | -0.33
3093 | 50.037 | -0.36 | -0.37 | -0.37
3094 | 50.038 | -0.4 | -0.38 | -0.38
3095 | 50.039 | -0.41 | -0.39 | -0.39
3096 | 50.043 | -0.425 | -0.43 | -0.43
3097 | 50.043 | -0.45 | -0.43 | -0.43
3098 | 50.044 | -0.46 | -0.44 | -0.44
3099 | 50.044 | -0.495 | -0.44 | -0.44
3100 | 50.047 | -0.46 | -0.47 | -0.47
3101 | 50.045 | -0.47 | -0.45 | -0.45
3102 | 50.043 | -0.485 | -0.43 | -0.43
3103 | 50.046 | -0.455 | -0.46 | -0.46
3104 | 50.047 | -0.465 | -0.47 | -0.47
3105 | 50.047 | -0.48 | -0.47 | -0.47
3106 | 50.047 | -0.495 | -0.47 | -0.47
3107 | 50.048 | -0.49 | -0.48 | -0.48
3108 | 50.048 | -0.495 | -0.48 | -0.48
3109 | 50.045 | -0.51 | -0.45 | -0.45
3110 | 50.045 | -0.48 | -0.45 | -0.45
3111 | 50.044 | -0.455 | -0.44 | -0.44
3112 | 50.043 | -0.445 | -0.43 | -0.43
3113 | 50.043 | -0.42 | -0.43 | -0.43
3114 | 50.04 | -0.41 | -0.4 | -0.4
3115 | 50.038 | -0.38 | -0.38 | -0.38
3116 | 50.039 | -0.39 | -0.39 | -0.39
3117 | 50.039 | -0.385 | -0.39 | -0.39
3118 | 50.038 | -0.385 | -0.38 | -0.38
3119 | 50.036 | -0.38 | -0.36 | -0.36
3120 | 50.036 | -0.36 | -0.36 | -0.36
3121 | 50.035 | -0.355 | -0.35 | -0.35
3122 | 50.034 | -0.37 | -0.34 | -0.34
3123 | 50.034 | -0.36 | -0.34 | -0.34
3124 | 50.034 | -0.35 | -0.34 | -0.34
3125 | 50.033 | -0.35 | -0.33 | -0.33
3126 | 50.033 | -0.35 | -0.33 | -0.33
3127 | 50.033 | -0.365 | -0.33 | -0.33
3128 | 50.034 | -0.355 | -0.34 | -0.34
3129 | 50.035 | -0.375 | -0.35 | -0.35
3130 | 50.039 | -0.36 | -0.39 | -0.39
3131 | 50.038 | -0.4 | -0.38 | -0.38
3132 | 50.038 | -0.4 | -0.38 | -0.38
3133 | 50.038 | -0.41 | -0.38 | -0.38
3134 | 50.037 | -0.385 | -0.37 | -0.37
3135 | 50.037 | -0.395 | -0.37 | -0.37
3136 | 50.036 | -0.385 | -0.36 | -0.36
3137 | 50.035 | -0.375 | -0.35 | -0.35
3138 | 50.034 | -0.35 | -0.34 | -0.34
3139 | 50.033 | -0.35 | -0.33 | -0.33
3140 | 50.034 | -0.335 | -0.34 | -0.34
3141 | 50.029 | -0.35 | -0.29 | -0.29
3142 | 50.03 | -0.305 | -0.3 | -0.3
3143 | 50.029 | -0.295 | -0.29 | -0.29
3144 | 50.026 | -0.285 | -0.26 | -0.26
3145 | 50.029 | -0.24 | -0.29 | -0.29
3146 | 50.026 | -0.275 | -0.26 | -0.26
3147 | 50.025 | -0.295 | -0.25 | -0.25
3148 | 50.027 | -0.265 | -0.27 | -0.27
3149 | 50.028 | -0.275 | -0.28 | -0.28
3150 | 50.03 | -0.31 | -0.3 | -0.3
3151 | 50.031 | -0.315 | -0.31 | -0.31
3152 | 50.031 | -0.325 | -0.31 | -0.31
3153 | 50.028 | -0.345 | -0.28 | -0.28
3154 | 50.031 | -0.305 | -0.31 | -0.31
3155 | 50.031 | -0.335 | -0.31 | -0.31
3156 | 50.031 | -0.36 | -0.31 | -0.31
3157 | 50.032 | -0.345 | -0.32 | -0.32
3158 | 50.033 | -0.345 | -0.33 | -0.33
3159 | 50.033 | -0.35 | -0.33 | -0.33
3160 | 50.034 | -0.345 | -0.34 | -0.34
3161 | 50.036 | -0.35 | -0.36 | -0.36
3162 | 50.036 | -0.375 | -0.36 | -0.36
3163 | 50.037 | -0.385 | -0.37 | -0.37
3164 | 50.035 | -0.37 | -0.35 | -0.35
3165 | 50.036 | -0.36 | -0.36 | -0.36
3166 | 50.035 | -0.375 | -0.35 | -0.35
3167 | 50.036 | -0.37 | -0.36 | -0.36
3168 | 50.036 | -0.38 | -0.36 | -0.36
3169 | 50.039 | -0.375 | -0.39 | -0.39
3170 | 50.039 | -0.405 | -0.39 | -0.39
3171 | 50.041 | -0.41 | -0.41 | -0.41
3172 | 50.042 | -0.425 | -0.42 | -0.42
3173 | 50.043 | -0.445 | -0.43 | -0.43
3174 | 50.044 | -0.45 | -0.44 | -0.44
3175 | 50.044 | -0.46 | -0.44 | -0.44
3176 | 50.044 | -0.45 | -0.44 | -0.44
3177 | 50.043 | -0.445 | -0.43 | -0.43
3178 | 50.042 | -0.43 | -0.42 | -0.42
3179 | 50.042 | -0.44 | -0.42 | -0.42
3180 | 50.042 | -0.435 | -0.42 | -0.42
3181 | 50.038 | -0.41 | -0.38 | -0.38
3182 | 50.04 | -0.42 | -0.4 | -0.4
3183 | 50.04 | -0.405 | -0.4 | -0.4
3184 | 50.04 | -0.425 | -0.4 | -0.4
3185 | 50.042 | -0.415 | -0.42 | -0.42
3186 | 50.042 | -0.44 | -0.42 | -0.42
3187 | 50.043 | -0.46 | -0.43 | -0.43
3188 | 50.044 | -0.445 | -0.44 | -0.44
3189 | 50.044 | -0.455 | -0.44 | -0.44
3190 | 50.046 | -0.48 | -0.46 | -0.46
3191 | 50.048 | -0.49 | -0.48 | -0.48
3192 | 50.048 | -0.495 | -0.48 | -0.48
3193 | 50.049 | -0.49 | -0.49 | -0.49
3194 | 50.049 | -0.51 | -0.49 | -0.49
3195 | 50.049 | -0.515 | -0.49 | -0.49
3196 | 50.049 | -0.5 | -0.49 | -0.49
3197 | 50.048 | -0.5 | -0.48 | -0.48
3198 | 50.049 | -0.495 | -0.49 | -0.49
3199 | 50.049 | -0.495 | -0.49 | -0.49
3200 | 50.05 | -0.5 | -0.5 | -0.5
3201 | 50.043 | -0.505 | -0.43 | -0.43
3202 | 50.05 | -0.51 | -0.5 | -0.5
3203 | 50.049 | -0.5 | -0.49 | -0.49
3204 | 50.049 | -0.51 | -0.49 | -0.49
3205 | 50.047 | -0.485 | -0.47 | -0.47
3206 | 50.046 | -0.465 | -0.46 | -0.46
3207 | 50.046 | -0.485 | -0.46 | -0.46
3208 | 50.047 | -0.5 | -0.47 | -0.47
3209 | 50.046 | -0.505 | -0.46 | -0.46
3210 | 50.045 | -0.47 | -0.45 | -0.45
3211 | 50.046 | -0.47 | -0.46 | -0.46
3212 | 50.045 | -0.47 | -0.45 | -0.45
3213 | 50.046 | -0.46 | -0.46 | -0.46
3214 | 50.047 | -0.465 | -0.47 | -0.47
3215 | 50.048 | -0.505 | -0.48 | -0.48
3216 | 50.051 | -0.505 | -0.51 | -0.51
3217 | 50.052 | -0.53 | -0.52 | -0.52
3218 | 50.052 | -0.535 | -0.52 | -0.52
3219 | 50.054 | -0.53 | -0.54 | -0.54
3220 | 50.054 | -0.535 | -0.54 | -0.54
3221 | 50.057 | -0.56 | -0.57 | -0.57
3222 | 50.056 | -0.575 | -0.56 | -0.56
3223 | 50.055 | -0.575 | -0.55 | -0.55
3224 | 50.052 | -0.535 | -0.52 | -0.52
3225 | 50.05 | -0.55 | -0.5 | -0.5
3226 | 50.049 | -0.535 | -0.49 | -0.49
3227 | 50.049 | -0.52 | -0.49 | -0.49
3228 | 50.049 | -0.515 | -0.49 | -0.49
3229 | 50.048 | -0.505 | -0.48 | -0.48
3230 | 50.048 | -0.495 | -0.48 | -0.48
3231 | 50.048 | -0.505 | -0.48 | -0.48
3232 | 50.048 | -0.49 | -0.48 | -0.48
3233 | 50.048 | -0.485 | -0.48 | -0.48
3234 | 50.049 | -0.505 | -0.49 | -0.49
3235 | 50.05 | -0.515 | -0.5 | -0.5
3236 | 50.05 | -0.515 | -0.5 | -0.5
3237 | 50.05 | -0.515 | -0.5 | -0.5
3238 | 50.049 | -0.505 | -0.49 | -0.49
3239 | 50.049 | -0.515 | -0.49 | -0.49
3240 | 50.049 | -0.505 | -0.49 | -0.49
3241 | 50.049 | -0.5 | -0.49 | -0.49
3242 | 50.049 | -0.505 | -0.49 | -0.49
3243 | 50.052 | -0.495 | -0.52 | -0.52
3244 | 50.051 | -0.52 | -0.51 | -0.51
3245 | 50.051 | -0.515 | -0.51 | -0.51
3246 | 50.049 | -0.5 | -0.49 | -0.49
3247 | 50.048 | -0.49 | -0.48 | -0.48
3248 | 50.049 | -0.49 | -0.49 | -0.49
3249 | 50.051 | -0.535 | -0.51 | -0.51
3250 | 50.053 | -0.555 | -0.53 | -0.53
3251 | 50.057 | -0.54 | -0.57 | -0.57
3252 | 50.054 | -0.565 | -0.54 | -0.54
3253 | 50.052 | -0.525 | -0.52 | -0.52
3254 | 50.052 | -0.54 | -0.52 | -0.52
3255 | 50.052 | -0.54 | -0.52 | -0.52
3256 | 50.049 | -0.535 | -0.49 | -0.49
3257 | 50.05 | -0.51 | -0.5 | -0.5
3258 | 50.05 | -0.52 | -0.5 | -0.5
3259 | 50.049 | -0.535 | -0.49 | -0.49
3260 | 50.049 | -0.51 | -0.49 | -0.49
3261 | 50.048 | -0.505 | -0.48 | -0.48
3262 | 50.048 | -0.515 | -0.48 | -0.48
3263 | 50.049 | -0.485 | -0.49 | -0.49
3264 | 50.05 | -0.495 | -0.5 | -0.5
3265 | 50.05 | -0.505 | -0.5 | -0.5
3266 | 50.05 | -0.51 | -0.5 | -0.5
3267 | 50.051 | -0.515 | -0.51 | -0.51
3268 | 50.052 | -0.535 | -0.52 | -0.52
3269 | 50.055 | -0.575 | -0.55 | -0.55
3270 | 50.057 | -0.59 | -0.57 | -0.57
3271 | 50.058 | -0.6 | -0.58 | -0.58
3272 | 50.06 | -0.6 | -0.6 | -0.6
3273 | 50.061 | -0.615 | -0.61 | -0.61
3274 | 50.061 | -0.625 | -0.61 | -0.61
3275 | 50.061 | -0.615 | -0.61 | -0.61
3276 | 50.06 | -0.6 | -0.6 | -0.6
3277 | 50.062 | -0.615 | -0.62 | -0.62
3278 | 50.065 | -0.635 | -0.65 | -0.65
3279 | 50.066 | -0.655 | -0.66 | -0.66
3280 | 50.067 | -0.68 | -0.67 | -0.67
3281 | 50.07 | -0.71 | -0.7 | -0.7
3282 | 50.07 | -0.73 | -0.7 | -0.7
3283 | 50.07 | -0.71 | -0.7 | -0.7
3284 | 50.069 | -0.795 | -0.69 | -0.69
3285 | 50.07 | -0.71 | -0.7 | -0.7
3286 | 50.069 | -0.73 | -0.69 | -0.69
3287 | 50.068 | -0.72 | -0.68 | -0.68
3288 | 50.065 | -0.695 | -0.65 | -0.65
3289 | 50.062 | -0.675 | -0.62 | -0.62
3290 | 50.059 | -0.635 | -0.59 | -0.59
3291 | 50.059 | -0.615 | -0.59 | -0.59
3292 | 50.06 | -0.62 | -0.6 | -0.6
3293 | 50.064 | -0.665 | -0.64 | -0.64
3294 | 50.065 | -0.695 | -0.65 | -0.65
3295 | 50.068 | -0.675 | -0.68 | -0.68
3296 | 50.068 | -0.695 | -0.68 | -0.68
3297 | 50.068 | -0.695 | -0.68 | -0.68
3298 | 50.068 | -0.69 | -0.68 | -0.68
3299 | 50.072 | -0.715 | -0.72 | -0.72
3300 | 50.072 | -0.74 | -0.72 | -0.72
3301 | 50.072 | -0.74 | -0.72 | -0.72
3302 | 50.073 | -0.74 | -0.73 | -0.73
3303 | 50.073 | -0.735 | -0.73 | -0.73
3304 | 50.073 | -0.75 | -0.73 | -0.73
3305 | 50.074 | -0.745 | -0.74 | -0.74
3306 | 50.077 | -0.77 | -0.77 | -0.77
3307 | 50.078 | -0.78 | -0.78 | -0.78
3308 | 50.088 | -0.8 | -0.88 | -0.88
3309 | 50.081 | -0.84 | -0.81 | -0.81
3310 | 50.081 | -0.84 | -0.81 | -0.81
3311 | 50.081 | -0.83 | -0.81 | -0.81
3312 | 50.081 | -0.83 | -0.81 | -0.81
3313 | 50.081 | -0.83 | -0.81 | -0.81
3314 | 50.081 | -0.83 | -0.81 | -0.81
3315 | 50.081 | -0.84 | -0.81 | -0.81
3316 | 50.08 | -0.835 | -0.8 | -0.8
3317 | 50.077 | -0.82 | -0.77 | -0.77
3318 | 50.077 | -0.785 | -0.77 | -0.77
3319 | 50.076 | -0.785 | -0.76 | -0.76
3320 | 50.074 | -0.755 | -0.74 | -0.74
3321 | 50.073 | -0.77 | -0.73 | -0.73
3322 | 50.073 | -0.76 | -0.73 | -0.73
3323 | 50.069 | -0.755 | -0.69 | -0.69
3324 | 50.067 | -0.72 | -0.67 | -0.67
3325 | 50.066 | -0.685 | -0.66 | -0.66
3326 | 50.065 | -0.675 | -0.65 | -0.65
3327 | 50.062 | -0.635 | -0.62 | -0.62
3328 | 50.062 | -0.61 | -0.62 | -0.62
3329 | 50.064 | -0.645 | -0.64 | -0.64
3330 | 50.06 | -0.61 | -0.6 | -0.6
3331 | 50.059 | -0.615 | -0.59 | -0.59
3332 | 50.057 | -0.595 | -0.57 | -0.57
3333 | 50.056 | -0.565 | -0.56 | -0.56
3334 | 50.056 | -0.57 | -0.56 | -0.56
3335 | 50.056 | -0.57 | -0.56 | -0.56
3336 | 50.059 | -0.575 | -0.59 | -0.59
3337 | 50.06 | -0.61 | -0.6 | -0.6
3338 | 50.06 | -0.635 | -0.6 | -0.6
3339 | 50.061 | -0.63 | -0.61 | -0.61
3340 | 50.063 | -0.665 | -0.63 | -0.63
3341 | 50.063 | -0.65 | -0.63 | -0.63
3342 | 50.062 | -0.635 | -0.62 | -0.62
3343 | 50.062 | -0.615 | -0.62 | -0.62
3344 | 50.057 | -0.61 | -0.57 | -0.57
3345 | 50.057 | -0.6 | -0.57 | -0.57
3346 | 50.057 | -0.6 | -0.57 | -0.57
3347 | 50.055 | -0.575 | -0.55 | -0.55
3348 | 50.055 | -0.585 | -0.55 | -0.55
3349 | 50.056 | -0.56 | -0.56 | -0.56
3350 | 50.057 | -0.565 | -0.57 | -0.57
3351 | 50.057 | -0.58 | -0.57 | -0.57
3352 | 50.057 | -0.58 | -0.57 | -0.57
3353 | 50.057 | -0.575 | -0.57 | -0.57
3354 | 50.057 | -0.595 | -0.57 | -0.57
3355 | 50.056 | -0.58 | -0.56 | -0.56
3356 | 50.055 | -0.58 | -0.55 | -0.55
3357 | 50.051 | -0.59 | -0.51 | -0.51
3358 | 50.051 | -0.575 | -0.51 | -0.51
3359 | 50.05 | -0.52 | -0.5 | -0.5
3360 | 50.048 | -0.515 | -0.48 | -0.48
3361 | 50.045 | -0.475 | -0.45 | -0.45
3362 | 50.043 | -0.435 | -0.43 | -0.43
3363 | 50.042 | -0.425 | -0.42 | -0.42
3364 | 50.041 | -0.435 | -0.41 | -0.41
3365 | 50.041 | -0.43 | -0.41 | -0.41
3366 | 50.04 | -0.43 | -0.4 | -0.4
3367 | 50.04 | -0.42 | -0.4 | -0.4
3368 | 50.04 | -0.42 | -0.4 | -0.4
3369 | 50.041 | -0.435 | -0.41 | -0.41
3370 | 50.043 | -0.435 | -0.43 | -0.43
3371 | 50.044 | -0.445 | -0.44 | -0.44
3372 | 50.047 | -0.49 | -0.47 | -0.47
3373 | 50.048 | -0.495 | -0.48 | -0.48
3374 | 50.048 | -0.485 | -0.48 | -0.48
3375 | 50.05 | -0.49 | -0.5 | -0.5
3376 | 50.053 | -0.505 | -0.53 | -0.53
3377 | 50.053 | -0.54 | -0.53 | -0.53
3378 | 50.057 | -0.54 | -0.57 | -0.57
3379 | 50.057 | -0.595 | -0.57 | -0.57
3380 | 50.059 | -0.605 | -0.59 | -0.59
3381 | 50.062 | -0.65 | -0.62 | -0.62
3382 | 50.067 | -0.695 | -0.67 | -0.67
3383 | 50.067 | -0.655 | -0.67 | -0.67
3384 | 50.067 | -0.7 | -0.67 | -0.67
3385 | 50.068 | -0.7 | -0.68 | -0.68
3386 | 50.069 | -0.695 | -0.69 | -0.69
3387 | 50.071 | -0.72 | -0.71 | -0.71
3388 | 50.071 | -0.7 | -0.71 | -0.71
3389 | 50.072 | -0.735 | -0.72 | -0.72
3390 | 50.074 | -0.76 | -0.74 | -0.74
3391 | 50.074 | -0.755 | -0.74 | -0.74
3392 | 50.073 | -0.745 | -0.73 | -0.73
3393 | 50.075 | -0.745 | -0.75 | -0.75
3394 | 50.072 | -0.76 | -0.72 | -0.72
3395 | 50.073 | -0.745 | -0.73 | -0.73
3396 | 50.073 | -0.775 | -0.73 | -0.73
3397 | 50.075 | -0.76 | -0.75 | -0.75
3398 | 50.077 | -0.815 | -0.77 | -0.77
3399 | 50.077 | -0.795 | -0.77 | -0.77
3400 | 50.078 | -0.815 | -0.78 | -0.78
3401 | 50.081 | -0.81 | -0.81 | -0.81
3402 | 50.08 | -0.825 | -0.8 | -0.8
3403 | 50.081 | -0.825 | -0.81 | -0.81
3404 | 50.083 | -0.855 | -0.83 | -0.83
3405 | 50.087 | -0.875 | -0.87 | -0.87
3406 | 50.092 | -0.91 | -0.92 | -0.92
3407 | 50.092 | -0.955 | -0.92 | -0.92
3408 | 50.093 | -0.97 | -0.93 | -0.93
3409 | 50.096 | -0.97 | -0.96 | -0.96
3410 | 50.096 | -0.985 | -0.96 | -0.96
3411 | 50.096 | -0.995 | -0.96 | -0.96
3412 | 50.097 | -0.995 | -0.97 | -0.97
3413 | 50.096 | -0.995 | -0.96 | -0.96
3414 | 50.097 | -0.985 | -0.97 | -0.97
3415 | 50.093 | -0.985 | -0.93 | -0.93
3416 | 50.094 | -0.955 | -0.94 | -0.94
3417 | 50.092 | -0.965 | -0.92 | -0.92
3418 | 50.09 | -0.935 | -0.9 | -0.9
3419 | 50.085 | -0.9 | -0.85 | -0.85
3420 | 50.085 | -0.89 | -0.85 | -0.85
3421 | 50.08 | -0.85 | -0.8 | -0.8
3422 | 50.077 | -0.785 | -0.77 | -0.77
3423 | 50.075 | -0.78 | -0.75 | -0.75
3424 | 50.074 | -0.77 | -0.74 | -0.74
3425 | 50.073 | -0.755 | -0.73 | -0.73
3426 | 50.072 | -0.74 | -0.72 | -0.72
3427 | 50.069 | -0.745 | -0.69 | -0.69
3428 | 50.069 | -0.7 | -0.69 | -0.69
3429 | 50.066 | -0.68 | -0.66 | -0.66
3430 | 50.061 | -0.66 | -0.61 | -0.61
3431 | 50.059 | -0.615 | -0.59 | -0.59
3432 | 50.057 | -0.6 | -0.57 | -0.57
3433 | 50.053 | -0.59 | -0.53 | -0.53
3434 | 50.052 | -0.55 | -0.52 | -0.52
3435 | 50.051 | -0.52 | -0.51 | -0.51
3436 | 50.049 | -0.52 | -0.49 | -0.49
3437 | 50.048 | -0.515 | -0.48 | -0.48
3438 | 50.048 | -0.495 | -0.48 | -0.48
3439 | 50.048 | -0.505 | -0.48 | -0.48
3440 | 50.048 | -0.51 | -0.48 | -0.48
3441 | 50.048 | -0.495 | -0.48 | -0.48
3442 | 50.048 | -0.505 | -0.48 | -0.48
3443 | 50.048 | -0.51 | -0.48 | -0.48
3444 | 50.048 | -0.495 | -0.48 | -0.48
3445 | 50.048 | -0.49 | -0.48 | -0.48
3446 | 50.048 | -0.495 | -0.48 | -0.48
3447 | 50.048 | -0.49 | -0.48 | -0.48
3448 | 50.051 | -0.48 | -0.51 | -0.51
3449 | 50.051 | -0.52 | -0.51 | -0.51
3450 | 50.05 | -0.52 | -0.5 | -0.5
3451 | 50.048 | -0.5 | -0.48 | -0.48
3452 | 50.045 | -0.47 | -0.45 | -0.45
3453 | 50.044 | -0.46 | -0.44 | -0.44
3454 | 50.043 | -0.46 | -0.43 | -0.43
3455 | 50.043 | -0.445 | -0.43 | -0.43
3456 | 50.042 | -0.425 | -0.42 | -0.42
3457 | 50.042 | -0.445 | -0.42 | -0.42
3458 | 50.041 | -0.445 | -0.41 | -0.41
3459 | 50.041 | -0.425 | -0.41 | -0.41
3460 | 50.044 | -0.42 | -0.44 | -0.44
3461 | 50.043 | -0.455 | -0.43 | -0.43
3462 | 50.043 | -0.435 | -0.43 | -0.43
3463 | 50.043 | -0.445 | -0.43 | -0.43
3464 | 50.044 | -0.45 | -0.44 | -0.44
3465 | 50.043 | -0.455 | -0.43 | -0.43
3466 | 50.043 | -0.46 | -0.43 | -0.43
3467 | 50.041 | -0.44 | -0.41 | -0.41
3468 | 50.04 | -0.42 | -0.4 | -0.4
3469 | 50.035 | -0.4 | -0.35 | -0.35
3470 | 50.034 | -0.37 | -0.34 | -0.34
3471 | 50.032 | -0.345 | -0.32 | -0.32
3472 | 50.032 | -0.315 | -0.32 | -0.32
3473 | 50.032 | -0.335 | -0.32 | -0.32
3474 | 50.033 | -0.35 | -0.33 | -0.33
3475 | 50.032 | -0.335 | -0.32 | -0.32
3476 | 50.032 | -0.325 | -0.32 | -0.32
3477 | 50.03 | -0.325 | -0.3 | -0.3
3478 | 50.031 | -0.315 | -0.31 | -0.31
3479 | 50.03 | -0.325 | -0.3 | -0.3
3480 | 50.03 | -0.315 | -0.3 | -0.3
3481 | 50.03 | -0.325 | -0.3 | -0.3
3482 | 50.031 | -0.325 | -0.31 | -0.31
3483 | 50.031 | -0.33 | -0.31 | -0.31
3484 | 50.031 | -0.34 | -0.31 | -0.31
3485 | 50.031 | -0.345 | -0.31 | -0.31
3486 | 50.032 | -0.345 | -0.32 | -0.32
3487 | 50.03 | -0.315 | -0.3 | -0.3
3488 | 50.027 | -0.275 | -0.27 | -0.27
3489 | 50.026 | -0.29 | -0.26 | -0.26
3490 | 50.025 | -0.28 | -0.25 | -0.25
3491 | 50.024 | -0.26 | -0.24 | -0.24
3492 | 50.023 | -0.265 | -0.23 | -0.23
3493 | 50.022 | -0.23 | -0.22 | -0.22
3494 | 50.022 | -0.23 | -0.22 | -0.22
3495 | 50.022 | -0.225 | -0.22 | -0.22
3496 | 50.021 | -0.22 | -0.21 | -0.21
3497 | 50.021 | -0.22 | -0.21 | -0.21
3498 | 50.023 | -0.225 | -0.23 | -0.23
3499 | 50.023 | -0.25 | -0.23 | -0.23
3500 | 50.025 | -0.255 | -0.25 | -0.25
3501 | 50.029 | -0.29 | -0.29 | -0.29
3502 | 50.031 | -0.29 | -0.31 | -0.31
3503 | 50.034 | -0.31 | -0.34 | -0.34
3504 | 50.035 | -0.365 | -0.35 | -0.35
3505 | 50.039 | -0.38 | -0.39 | -0.39
3506 | 50.039 | -0.415 | -0.39 | -0.39
3507 | 50.042 | -0.4 | -0.42 | -0.42
3508 | 50.043 | -0.43 | -0.43 | -0.43
3509 | 50.045 | -0.445 | -0.45 | -0.45
3510 | 50.049 | -0.465 | -0.49 | -0.49
3511 | 50.049 | -0.5 | -0.49 | -0.49
3512 | 50.053 | -0.54 | -0.53 | -0.53
3513 | 50.054 | -0.545 | -0.54 | -0.54
3514 | 50.054 | -0.555 | -0.54 | -0.54
3515 | 50.058 | -0.575 | -0.58 | -0.58
3516 | 50.059 | -0.615 | -0.59 | -0.59
3517 | 50.059 | -0.61 | -0.59 | -0.59
3518 | 50.06 | -0.64 | -0.6 | -0.6
3519 | 50.061 | -0.625 | -0.61 | -0.61
3520 | 50.062 | -0.635 | -0.62 | -0.62
3521 | 50.064 | -0.67 | -0.64 | -0.64
3522 | 50.064 | -0.675 | -0.64 | -0.64
3523 | 50.062 | -0.635 | -0.62 | -0.62
3524 | 50.059 | -0.615 | -0.59 | -0.59
3525 | 50.059 | -0.615 | -0.59 | -0.59
3526 | 50.058 | -0.6 | -0.58 | -0.58
3527 | 50.056 | -0.56 | -0.56 | -0.56
3528 | 50.055 | -0.56 | -0.55 | -0.55
3529 | 50.052 | -0.54 | -0.52 | -0.52
3530 | 50.049 | -0.495 | -0.49 | -0.49
3531 | 50.046 | -0.475 | -0.46 | -0.46
3532 | 50.041 | -0.445 | -0.41 | -0.41
3533 | 50.039 | -0.42 | -0.39 | -0.39
3534 | 50.036 | -0.375 | -0.36 | -0.36
3535 | 50.033 | -0.36 | -0.33 | -0.33
3536 | 50.033 | -0.365 | -0.33 | -0.33
3537 | 50.029 | -0.325 | -0.29 | -0.29
3538 | 50.028 | -0.325 | -0.28 | -0.28
3539 | 50.025 | -0.3 | -0.25 | -0.25
3540 | 50.027 | -0.285 | -0.27 | -0.27
3541 | 50.027 | -0.29 | -0.27 | -0.27
3542 | 50.028 | -0.285 | -0.28 | -0.28
3543 | 50.029 | -0.3 | -0.29 | -0.29
3544 | 50.031 | -0.34 | -0.31 | -0.31
3545 | 50.031 | -0.325 | -0.31 | -0.31
3546 | 50.032 | -0.325 | -0.32 | -0.32
3547 | 50.033 | -0.345 | -0.33 | -0.33
3548 | 50.033 | -0.355 | -0.33 | -0.33
3549 | 50.032 | -0.35 | -0.32 | -0.32
3550 | 50.032 | -0.335 | -0.32 | -0.32
3551 | 50.031 | -0.325 | -0.31 | -0.31
3552 | 50.031 | -0.315 | -0.31 | -0.31
3553 | 50.031 | -0.315 | -0.31 | -0.31
3554 | 50.03 | -0.325 | -0.3 | -0.3
3555 | 50.029 | -0.305 | -0.29 | -0.29
3556 | 50.028 | -0.275 | -0.28 | -0.28
3557 | 50.027 | -0.28 | -0.27 | -0.27
3558 | 50.029 | -0.31 | -0.29 | -0.29
3559 | 50.03 | -0.315 | -0.3 | -0.3
3560 | 50.03 | -0.315 | -0.3 | -0.3
3561 | 50.031 | -0.3 | -0.31 | -0.31
3562 | 50.032 | -0.325 | -0.32 | -0.32
3563 | 50.031 | -0.315 | -0.31 | -0.31
3564 | 50.028 | -0.32 | -0.28 | -0.28
3565 | 50.029 | -0.285 | -0.29 | -0.29
3566 | 50.026 | -0.275 | -0.26 | -0.26
3567 | 50.023 | -0.265 | -0.23 | -0.23
3568 | 50.021 | -0.205 | -0.21 | -0.21
3569 | 50.02 | -0.195 | -0.2 | -0.2
3570 | 50.014 | -0.19 | -0.14 | 0
3571 | 50.014 | -0.01 | -0.14 | 0
3572 | 50.014 | 0 | -0.14 | 0
3573 | 50.011 | -0.01 | -0.11 | 0
3574 | 50.011 | 0.005 | -0.11 | 0
3575 | 50.01 | 0 | -0.1 | 0
3576 | 50.009 | -0.01 | -0.09 | 0
3577 | 50.006 | -0.005 | -0.06 | 0
3578 | 50.006 | -0.01 | -0.06 | 0
3579 | 50.005 | -0.01 | -0.05 | 0
3580 | 50.005 | 0 | -0.05 | 0
3581 | 50.004 | 0 | -0.04 | 0
3582 | 50.004 | -0.01 | -0.04 | 0
3583 | 50.005 | 0 | -0.05 | 0
3584 | 50.004 | -0.005 | -0.04 | 0
3585 | 50.005 | -0.005 | -0.05 | 0
3586 | 50.008 | 0 | -0.08 | 0
3587 | 50.007 | -0.005 | -0.07 | 0
3588 | 50.006 | 0.01 | -0.06 | 0
3589 | 50.007 | 0.01 | -0.07 | 0
3590 | 50.005 | 0.01 | -0.05 | 0
3591 | 50.004 | 0 | -0.04 | 0
3592 | 50.003 | 0.005 | -0.03 | 0
3593 | 50.002 | 0 | -0.02 | 0
3594 | 50.002 | 0.005 | -0.02 | 0
3595 | 50.002 | 0.005 | -0.02 | 0
3596 | 50.002 | 0 | -0.02 | 0
3597 | 50.004 | 0 | -0.04 | 0
3598 | 50.003 | 0.005 | -0.03 | 0
3599 | 50.003 | 0 | -0.03 | 0
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
|  |  | 500 | 500
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | -0.005
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | -0.01
| 50 | 0.005
| 50 | -0.005
| 50 | 0.01
| 50 | -0.005
| 50 | 0
| 50 | -0.015
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0.015
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | -0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | 0.01
| 50 | -0.01
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | -0.015
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.015
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | -0.005
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0.005
| 50 | -0.01
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | 0.005
| 50 | -0.015
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0.015
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | -0.01
| 50 | 0.005
| 50 | -0.005
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0
| 50 | -0.005
| 50 | -0.005
| 50 | -0.01
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.02
| 50 | 0.015
| 50 | 0.015
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | -0.01
| 50 | 0.01
| 50 | 0.01
| 50 | -0.005
| 50 | 0.015
| 50 | 0.01
| 50 | 0.02
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | 0
| 50 | 0.02
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | 0
| 50 | 0.015
| 50 | 0
| 50 | 0.015
| 50 | 0.01
| 50 | 0.015
| 50 | 0.005
| 50 | 0.015
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | -0.005
| 50 | 0.005
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | -0.01
| 50 | -0.01
| 50 | -0.01
| 50 | -0.01
| 50 | 0
| 50 | -0.01
| 50 | -0.005
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | 0.01
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | 0.015
| 50 | 0.01
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.02
| 50 | 0.015
| 50 | 0.01
| 50 | 0.015
| 50 | 0.015
| 50 | 0
| 50 | -0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | -0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0.005
| 50 | -0.01
| 50 | -0.01
| 50 | 0
| 50 | 0.01
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | -0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.015
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | 0.015
| 50 | -0.01
| 50 | 0.01
| 50 | 0.01
| 50 | -0.01
| 50 | -0.01
| 50 | 0.01
| 50 | -0.01
| 50 | 0
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | -0.015
| 50 | -0.015
| 50 | -0.01
| 50 | -0.015
| 50 | -0.015
| 50 | -0.015
| 50 | -0.01
| 50 | -0.015
| 50 | -0.015
| 50 | -0.01
| 50 | -0.015
| 50 | -0.01
| 50 | -0.015
| 50 | -0.01
| 50 | -0.01
| 50 | -0.015
| 50 | -0.015
| 50 | -0.005
| 50 | -0.01
| 50 | -0.01
| 50 | -0.01
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | -0.01
| 50 | -0.01
| 50 | -0.005
| 50 | 0
| 50 | -0.01
| 50 | -0.005
| 50 | -0.01
| 50 | -0.005
| 50 | -0.01
| 50 | -0.01
| 50 | -0.01
| 50 | -0.01
| 50 | -0.02
| 50 | -0.01
| 50 | -0.01
| 50 | -0.015
| 50 | -0.02
| 50 | -0.015
| 50 | -0.02
| 50 | -0.01
| 50 | -0.01
| 50 | -0.015
| 50 | -0.015
| 50 | -0.015
| 50 | -0.015
| 50 | 0
| 50 | -0.02
| 50 | -0.015
| 50 | -0.025
| 50 | -0.015
| 50 | -0.02
| 50 | -0.02
| 50 | -0.01
| 50 | -0.015
| 50 | -0.01
| 50 | -0.01
| 50 | -0.02
| 50 | -0.015
| 50 | -0.015
| 50 | -0.01
| 50 | -0.01
| 50 | -0.015
| 50 | -0.005
| 50 | 0
| 50 | -0.01
| 50 | 0
| 50 | 0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | -0.005
| 50 | 0.005
| 50 | 0
| 50 | 0.015
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0.015
| 50 | 0.015
| 50 | 0.015
| 50 | -0.01
| 50 | -0.01
| 50 | 0.015
| 50 | 0.01
| 50 | 0.015
| 50 | 0
| 50 | 0.005
| 50 | 0
| 50 | -0.005
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | -0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | -0.005
| 50 | -0.01
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | -0.01
| 50 | 0
| 50 | 0
| 50 | 0.01
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0.015
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0.01
| 50 | 0.01
| 50 | 0.015
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.01
| 50 | 0.005
| 50 | 0
| 50 | 0.01
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | -0.005
| 50 | -0.01
| 50 | 0
| 50 | -0.01
| 50 | -0.005
| 50 | -0.005
| 50 | -0.015
| 50 | -0.01
| 50 | -0.005
| 50 | -0.01
| 50 | -0.015
| 50 | 0.01
| 50 | -0.01
| 50 | 0.01
| 50 | -0.005
| 50 | 0.01
| 50 | 0.01
| 50 | -0.01
| 50 | 0.005
| 50 | 0.005
| 50 | 0.005
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | 0
| 50 | -0.01
| 50 | 0.005
| 50 | -0.005
| 50 | -0.005
| 50 | -0.005