## Slide 1: GSR016: Embedded Generation Assumptions
Bieshoy Awad

## Slide 2: Contents
2
Background
Scope of the Workgroup
Assumptions
Modelling EG for Investment Planning Studies
  Current practice
  Example
  How to Achieve Consistency
System Operability Implications
Data exchange between different parties

## Slide 3: Background
3
Workgroup to address issues arising from
The size and connection level
Contractual arrangement
These issues are
The inclusion of Small and Medium Embedded Power Stations in the Security and Economy background is subject to interpretation.
Lack of BM participants make certain boundaries inoperable.

## Slide 4: Scope
4
Question 1: How to ensure that Small and Medium Embedded Power Stations are appropriately accounted for in the investment planning studies?
Question 2: How to ensure that system is operable with an increased capacity of generation that is not a part of the Balancing Mechanism?

## Slide 5: Scope
5
Workgroup to agree the following:
  Should we include Small and Medium Embedded Generation in Section 4 Economy Planned Transfer conditions?
  Should we include Small and Medium Embedded Generation in Section 4 Security Planned Transfer conditions?
  Should we have a criteria to ensure the system is operable with high output of non-BM generation and combinations of outages?
  What data is required to ensure the change is effective?
  What process change is necessary to ensure data is communicated to Scottish TOs
Expected change to the NETS SQSS
  Change of the ACS Peak Demand definition
  Removal of exclusions of Small and Medium Embedded Power Stations
  Operability criteria
Yes
Yes
Maybe
Certain
Certain
Maybe
CPA/FES
TBC

## Slide 6: Assumptions
6
The current methodology and background assumptions
  produce the most economic transmission solution for transmission connected generation; and
  do not result in a erroneous or infeasible assumptions on generation output.
There is no evidence that the operational regime will differ between
  a large power station or a small power station of the same technology; or between
  a directly connected power station and an embedded power station of the same technology and capacity.
Where any of these assumptions are inaccurate, the inaccuracy will be rectified by the proposals of the GSR022 workgroup.

## Slide 7: Modelling EG for Investment Planning Studies
7
How to ensure that Small and Medium Embedded Power Stations are appropriately accounted for in the investment planning studies?

## Slide 8: Current Practice
8
Section 2:
No distinction between power plants based on connection level or size
Limits to Loss of Power Infeed Risks
2.5.1: the sum of the registered capacities of the generating units disconnected from the system by a secured event,
Generation Connection Capacity Requirements
2.8.1 the active power output of the power station shall be set equal to its “registered capacity”;
2.8.5 conditions on the national electricity transmission system shall be set to those which “ought reasonably to be expected to arise in the course of a year of operation”. Such conditions shall include forecast demand cycles, typical power station operating regimes and typical planned outage patterns modified where appropriate by the provisions of paragraph 2.11.

## Slide 9: Current Practice
9
Section 4:
Some distinction between power plants based on connection level or size
At ACS peak demand with an intact system
ACS Peak Demand = ACS Peak Underlying Demand minus contribution from Embedded Small and Medium Power Stations.
The method used to calculate these contribution is not defined
There could be some discrepancies between method applied various DNOs when calculating the contribution for W24 submissions and that applied by NGET for FES

## Slide 10: Current Practice
10
Appendix C: Modelling of Security Planned Transfer
Appendix D: Application of the Interconnection Allowance
Appendix E: Modelling of Economy Planned Transfer
Embedded Small and Medium Power Stations are
implicitly accounted for in the ACS Peak Demand;
have the same contribution to both security and economy planned transfer conditions
treated differently from Transmission connected Power Stations and Embedded Large Power Stations

## Slide 11: Example
11
For simplicity, only a small group is considered. However the issue is more relevant to wider boundaries – The group is assumed to be in E&W
Assumed contribution from each of the Medium Embedded Windfarms: 15MW (For illustrative purposes only)
ACS Peak Demand at the GSP = 70MW
Under the economy background conditions, the group will be exporting 56MW
Under the security background conditions, the group will be importing 70MW

## Slide 12: Example
12
Example: Same group but the two medium windfarms are connected to the transmission system
ACS Peak Demand at the GSP = 100MW
Under the economy background conditions, the group will be exporting 152MW
Under the security background conditions, the group will be importing 100MW

## Slide 13: Issues Highlighted by the Example
13
The same power station could be treated in two different way based on whether it is connected directly to the transmission system or embedded within the distributions system.
This could result in boundaries being reinforced to a requirement that is either a lot higher or a lot lower than the optimal capacity.
This could result in
  Over investment on certain boundaries,
  Excessive constraints costs on other boundaries, or
  Demand not being met because of restrictions on the transmission system
Notes
For a small group, similar to the example provided, application of Section 2 and Section 3 criteria should mitigate the risks
For wider system boundaries the risk is higher.
We are currently working on study cases to show the impact on ETYS boundaries

## Slide 14: How to Achieve Consistency
14
Change some definitions
  ACS Peak Demand
  Plant Margin
  Economy Planned Transfer Conditions
  Planned Transfer Conditions
  Security Planned Transfer Conditions
Remove exclusions of Embedded Small Power Stations, and Embedded Medium Power Stations from
  Appendix C
  Appendix D
  Appendix E

## Slide 15: Changes Proposed to the Legal Text
15
11. Terms and Definitions
ACS Peak Demand
The estimated unrestricted winter peak demand (MW and MVar) on the national electricity transmission system for the average cold spell (ACS) condition. This represents the demand to be met by large power stations (directly connected or embedded), medium power stations (directly connected or embedded) and small power stations (directly connected or embedded) which are directly connected to the national electricity transmission system and by electricity imported into the onshore transmission system from external systems across external interconnections (and which is not adjusted to take into account demand management or other techniques that could modify demand).
Plant Margin
The amount by which the total installed capacity of directly connected power stations and embedded large power stations exceeds the net amount of the ACS peak demand minus the total imports from external systems. This is often expressed as a percentage (e.g. 20%) or as a decimal fraction (e.g. 0.2) of the net amount of the ACS peak demand minus the total imports from external systems.

## Slide 16: Changes Proposed to the Legal Text
16
Economy Planned Transfer Conditions
The condition arising from scaling the registered capacity of each directly connected power station and embedded large power station according to the type of generation such that the total of the scaled capacities is equal to the ACS peak demand. This scaling shall follow the techniques described in Appendix E.
Planned Transfer Conditions
The condition arising from scaling the registered capacities of each directly connected power station and embedded large power station such that the total of the scaled capacities is equal to the ACS peak demand minus imports from external systems. This scaling shall follow the techniques described in Appendix C.

## Slide 17: Changes Proposed to the Legal Text
17
Security Planned Transfer Conditions
The condition arising from scaling the registered capacity of each directly connected power station and embedded large power station that is considered able to reliably contribute to peak demand security such that the total of the scaled capacities is equal to the ACS peak demand. Generation powered by intermittent sources (e.g. wind, wave, solar) and imports from external systems are not included in this condition. This scaling shall follow the techniques described in Appendix C.

## Slide 18: Changes Proposed to the Legal Text
18
Appendix C
C.3 In some circumstances apparent future plant margins may exceed 20%. This may arise where NGET has been notified of increases in future generation capacity but has not yet been formally notified of future reductions in generation capacity due to plant closures. The ranking order technique maintains the output of directly connected power stations and embedded large power stations considered more likely to operate at times of ACS peak demand at more realistic levels and treats those less likely to operate as non- contributory.
C.4 This is achieved by ranking all directly connected power stations and embedded large power stations in order of likelihood of operation at times of ACS peak demand. Those power stations considered least likely to operate at peak are progressively removed and treated as non-contributory until a plant margin of 20% or just below is achieved. The output of the remainder is then calculated using the same scaling method as used in the straight scaling technique described in paragraphs C.5 and C.6 below.

## Slide 19: Changes Proposed to the Legal Text
19
C.5 In this technique, all directly connected power stations and embedded large power stations on the system at the time of the ACS peak demand are considered contributory and their output is calculated by applying a scaling factor to their registered capacity proportional to an availability representative of the generating plant type at the time of ACS peak demand such that their aggregate output is equal to the forecast ACS peak demand minus total imports from external systems.
C.6 PTi = the output of the ith directly connected or embedded large power station of generating plant type T
AT = an availability representative of generating plant type T at the time of ACS peak demand
RTi = the registered capacity of the ith directly connected or embedded large power station of generating plant type T
Ploss= total national electricity transmission system active power losses at time of ACS peak demand
Lj = the active power demand at the jth national electricity transmission system demand site at the time of ACS peak demand

## Slide 20: Changes Proposed to the Legal Text
20
Appendix D
Figure D.1 – Notes
2. 'Generation' shall comprise (a) the output from large power stations, medium power stations, and small power stations whether these are embedded or directly connected to the national electricity transmission system
(b) the output from directly connected small and medium power stations
(bc) imports into the national electricity transmission system from external systems

## Slide 21: Changes Proposed to the Legal Text
21
Appendix E
E.5 All remaining directly connected power stations and embedded large power stations on the system at the time of the ACS peak demand are considered contributory and their output is calculated by applying a scaling factor to their registered capacity such that their aggregate output is equal to the forecast ACS peak demand minus the total output of directly scaled plant.

## Slide 22: Changes Proposed to the Legal Text
22
E.6 PTi = the output of the ith directly connected or embedded large power station of generating plant type T
DT = the direct scaling factor for directly scaled generation of plant type T
RDTk = the registered capacity of the kth directly connected or embedded large power station of generation plant type DT in the directly scaled category
RVTn = the registered capacity of the nth directly connected or embedded large power station of generation plant type VT in the variably scaled category
Ploss= total national electricity transmission system active power losses at time of ACS peak demand
Lj = the active power demand at the jth national electricity transmission system demand site at the time of ACS peak demand

## Slide 23: System Operability Implications
23
How to ensure that system is operable with an increased capacity of generation that is not a part of the Balancing Mechanism?

## Slide 24: Why it is necessary to be able to constrain generation
Balancing generation and demand
Facilitating the provision of ancillary services
  Frequency response
  System inertia
  Voltage control
Ensuring that the system is secured for the next fault
  Thermal constraints
  Voltage constraints
  Stability constraints
Issues that are relevant to this workgroup
Issues that may not be relevant to this workgroup

## Slide 25: Why it is necessary to be able to constrain generation
Local boundary issues
Wider boundary issues

## Slide 26: How to Address This
Local boundaries that are at risk. Are we aware of any?
Wider boundaries that are at risk. We are currently looking at this.
What options do we have (investment/intertipping/requiring developers to be a part of the BM)?
How to decide what the right option is?
Does the current SQSS clauses 2.12, 2.13, and 4.7 to 4.10 provide enough justification to this decision?
How would we fund any additional works?

## Slide 27: Data Exchange between Different Parties
27
Do all parties have access to the data necessary to make the modification effective?

## Slide 28: Data Exchange
NGET
DNO
TOs
W24
Connection Application
Connection Application
W24
Construction Planning Assumptions
FES Scenarios

## Slide 29: W24 DNO Submissions
DNO1 (owns Substation A) submits:
Point A:
Demand (MW and MVAr)
Deduction made from Demand for Small, Medium or Customer Stations
Point B:
Demand (MW and MVAr)
Deduction made from Demand at Small, Medium or Customer Stations
At Peak Demand time of Point A
At Peak/Min Demand time of GB Transmission System
At Peak Demand time of Access Period
At Peak Demand time of Point A
Total value of Access Period
A
400 kV
132 kV
B
DNO1
DNO2

## Slide 30: W24 DNO Submissions
For all GSPs with embedded generation, DNOs submit the following data
No. of Small, Medium or Customer Power Stations
Number of Generating Units within these stations
Summated Capacity of all these Generating Units
PC.A.3.1.4: From 2015 onwards (GC0042), for Power Stations with capacity of at least 1MW, DNOs submit the following data
A unique reference
Fuel type
Registered Capacity
DNO node as indicated on the Single Line Diagrams
Geographical location of wind/solar generation
Control mode
Loss of mains protection

## Slide 31: Future Energy Scenarios
Scenarios are created by NGET FES Team and shared in full with other Transmission Licensees
Date contains
  Underlying peak demand
  Aggregated capacity of different generation technologies small and medium embedded generation (1 MW and above) at each GSP
  Aggregated capacity of different generation technologies of small embedded generation (below 1 MW) at each GSP
  No information on contractual arrangements
Prosperity
Green Ambition
No Progression
Consumer Power
Gone Green
Slow Progression
Green Ambition
Prosperity

## Slide 32: Construction Planning Assumptions
  Based on contracted background (TEC Register and Embedded Generation Register)
  Includes
    Transmission Connected Generation (subject to a BCA)
    Embedded Generation that is subject to a BEGA
    Embedded Generation that is subject to a BELLA
  Excludes
    Embedded Generation that is not subject to a BELLA/BEGA
  Provides visibility of what is a BM participant (BCAs and BEGAs)

## Slide 33: Discussion

## Slide 34: GSR022: Review of Security and Economy Planned Transfer Conditions
34
Scope and Terms of Reference

## Slide 35: GSR022: Review of Security and Economy Planned Transfer Conditions
35
Two separate work streams
Security Planned Transfer
  Decision mainly political
  Some analysis is required
Economy Planned Transfer
  Decision mainly economic
  Required understanding of the operating regimes for different types of plants
  Comprehensive statistical analysis and Cost Benefit Analysis studies are necessary
  The introduction of an additional background should not be ruled out at this stage
It is proposed that the Workgroup reports on each work stream separately.

## Slide 36: GSR022- WS1: Security Planned Transfer Conditions
36
What is it that we are trying to achieve, and what are the expectations of our stakeholders?
Providing transmission capacity to ensure that the peak demand can be supplied by generation that might be available in a different part of the network
vs.
Providing transmission capacity to ensure that the peak demand can be supplied by generation that we are 100% certain is available
Potentially a criteria that applies differently for different areas could be used (large vs small area or importing vs exporting area)

## Slide 37: GSR022- WS1: Security Planned Transfer Conditions
37
Review of the Straight Scaling Technique (Could be an interim position)
Review of assumptions on Interconnectors
Review of assumptions on other generation types
A view on Demand Side Management

## Slide 38: GSR022- WS2: Economy Planned Transfer Conditions
38
  Is a need to change existing scaling factors?
  What is the most suitable way to model new technologies (solar, storage, …etc.)?
  What is the level to which all types of generation should be dispatched at?
  How to address scenarios with generation being in excess of demand?
Has there been any change to assumptions that were used to specify the current scaling factors?
To what extent did the CPA conducted by the GSR009 workgroup consider different boundaries.
Is there any discrepancy between the methodology used by GSR009 workgroup and that used by different TOs to support the need case for their investment?
Is there any discrepancy between the methodology used by GSR009 workgroup and NOA?
Do we need a new set of Planned Transfer Conditions or is it sufficient to modify the Economy Planned Transfer Conditions?
What methodology should we use for CPA?
What scenarios should be covered by the CPA?
What are the “new” scaling factors?
What data do we have regarding all different types of generation
What are the advantages/disadvantages of a locational criteria (large vs small area or importing vs exporting area)

## Slide 39: Discussion