## Sheet1
Parameter | Baseline Assumption |  | Notes | Worst Case Assumption (where different from Baseline) |  | Notes
Probability of an offshore transformer fault | 0.002 | events/transformer/year | Transformer Supplier Figure | 0.02 | events/transformer/year | Higher estimate taken from CIGRE TB537 - Transformer Fire Safety Practices Section 3.11 Table 1 - 1983 survey
Mean Time To Repair Offshore Transformer | 4 | months | Service Organisation Estimate
Probability of Failure of HV GIS Bay (disconnector) | 0.0011 | events/bay/year | Supplier HV Switchgear Group Figure
Mean Time To Repair HV GIS Bay | 10 | days | Service Organisation Estimate
Probability of Failure of MV GIS Bay | 0.0011 | events/bay/year | MV Switchgear Supplier Group Figure
Mean Time To Repair MV GIS Bay | 10 | days | Service Organisation Estimate
Failure Rate of MV Cable Interlink | 0.0008 | failures/km/year | Carbon Trust 33/66kV Array Cable Comparison "Best Case"
Length of MV Interlink Cable | 3 | km | Typical Layout | 16 | km | Based on an actual layout believed to be an extreme case
Mean Time To Repair MV Cable Link | 2 | months | Estimate from cable supplier/installer | 3 | months | Based on practical experience
Failure Rate of HV Cable Interlink | 0.0008 | failures/km/year | Use same rate as MV cable - Cable supplier estimate actually 0.0002
Length of HV Interlink Cable | 1.5 | km | Typical Layout | 8 | km | Based on an actual layout believed to be an extreme case
Mean Time To Repair HV Cable Link | 2 | months | Estimate from cable supplier/installer | 3 | months | Based on practical experience
Failure Rate of HV Export Cables | 0.0008 | failures/km/year | Use same rate as MV cable - Cable supplier estimate actually 0.0002
Length of HV Export Cables | 200 | km | Total export cable length for a typical layout | 240 | km | Increased to cover projects expected to use AC connection solution
Mean Time To Repair HV Export Cable | 2 | months | Estimate from cable supplier/installer | 3 | months | Based on practical experience
Capacity of HV Interlink | 25 | % | Assuming even generation across the windfarm and that each export circuit is rated to 50% of the windfarm capacity this is the maximum amount of power that can be transferred from one circuit to other before the remaining circuit reaches its capacity
Capacity of MV Interlink | 25 | % | Assuming even generation across the windfarm and that each export circuit is rated to 50% of the windfarm capacity this is the maximum amount of power that can be transferred from one circuit to other before the remaining circuit reaches its capacity
Average service duration for offshore transformer & HV GIS | 2.6667 | hours/year | Based on 8 hour shift once every 3 years - visual inspection when in service in-between | 4 | hours/year | Increased outage time to 12 hours to include time for De-energisation & Re-energisation safety process
Value of energy during contracted period | 115 | £/MWh | Latest CFD winning bid value | 140 | £/MWh | Highest value from current project under development
Value of energy after contracted period | 75 | £/MWh | Future estimate from Developer
Capital Cost Difference between single transformer module based system & multiple transformer based system (HV Interlink) | 23.5 | £M | Supplier Estimate
Capital Cost Difference between single transformer module based system & multiple transformer based system (MV Interlink) | 23.5 | £M | Supplier Estimate
Capital Cost Difference between single transformer module based system & multiple transformer based system (No Interlink) | 25 | £M | Supplier Estimate
Wind Farm Owner Cost of Finance | 6.25 | % | As per GSR014 Review | 7.9 | % | Upper value advised by OFTO
OFTO Cost of Finance | 6.25 | % | Same rate of finance as Wind Farm Owner | 7.9 | % | Upper value advised by OFTO
Social Time Preference Rate (STPR) | 3.5 | %
Lifetime of OFTO Assets | 25 | years |  | 20 | years | Potential shortened lifetime