## Revision_History
Revision | Date | Summary of Changes
1 | 2015-06-19 | First Release
2 | 2015-06-19 | 2nd Release after comments
3 | 2015-06-25 | 3rd Release after comments - generic generation profile inserted
4 | 2015-07-29 | Correction of OFTO Loan Repayment - payment changed to ensure capital is paid back at end of loan period
5 | 2015-07-31 | Additional Case added - two single transformer modules without any interlinks
6 | 2015-08-04 | Cell E154 Corrected - outage time due to loss of export cable added
7 | 2015-08-14 | Diagrams updated, default energy price updated, default capex cost differences updated
8 | 2015-08-19 | Tidy up of text and equations

## Comparison
Cost Benefit Analysis of Single Transformer Offshore Modules vs Multiple Transformer Offshore Modules
Purpose
This spreadsheet compares four solutions for offshore windfarm connections to the grid.
1) A system using a traditional Offshore Substation Platform (OSP) with two cables to shore and two transformers on the platform.
2) A system using two Single Transformer Modules each with a dedicated cable to shore and a single transformer on each module plus a HV interlink between the modules.
3) A system using two Single Transformer Modules each with a dedicated cable to shore and a single transformer on each module plus a MV interlink between the modules.
4) A system using two Single Transformer Modules each with a dedicated cable to shore and a single transformer on each module but with no interlink between the offshore modules
Capital cost savings are achieved when using the single transformer modules through the simplification of the equipment onboard which leads to a significantly lower size & weight.
In addition the lifting vessel used to install the wind turbine foundations can be used to install the single transformer modules - leading to significant cost savings
However the fact that the two transformers are installed on separated platforms can lead to a reduction in the system redundancy.
In the event that an export cable or the transformer or HV switchgear on one single tranformer module fails, the power from half of the windfarm cannot be exported unless interlinks are provided between the faulty module and the remaining module.
This allows the affected turbines to export their power via the other module.
Assumptions |  |  |  | Analysis Inputs - vary to recalculate |  | Analysis Assumptions (don't change)
The following assumptions are made in this analysis:
System Capacity |  |  |  | 500 | MW
Probability of an offshore transformer fault |  |  |  | 0.002 | events/transformer/year
Mean Time To Repair Offshore Transformer |  |  |  | 4 | months
Probability of Failure of HV GIS Bay |  |  |  | 0.0011 | events/bay/year
Mean Time To Repair HV GIS Bay |  |  |  | 10 | days
Probability of Failure of MV GIS Bay |  |  |  | 0.0011 | events/bay/year
Mean Time To Repair MV GIS Bay |  |  |  | 10 | days
Failure Rate of MV Cable Interlink |  |  |  | 0.0008 | failures/km/year
Length of MV Interlink Cable |  |  |  | 3 | km |  | Total Cable Length - may be multiple circuits (used to calculate probability of failure) - initially set as 2 x HV link length i.e. 2 MV cables in parallel
Mean Time To Repair MV Cable Link |  |  |  | 2 | months
Failure Rate of HV Cable Interlink |  |  |  | 0.0008 | failures/km/year
Length of HV Interlink Cable |  |  |  | 1.5 | km |  | Total Cable Length - (used to calculate probability of failure)
Mean Time To Repair HV Cable Link |  |  |  | 2 | months
Failure Rate of HV Export Cables |  |  |  | 0.0008 | failures/km/year
Length of HV Export Cables |  |  |  | 200 | km |  | Total length of two circuits
Mean Time To Repair HV Export Cable |  |  |  | 2 | months
Capacity of HV Interlink |  |  |  | 25 | % |  | Expressed as a proportion of the windfarm output - set to 25% as this is max that alternative export path can support assuming even generation, less than this and additional losses are caused if one export cable fails.
Capacity of MV Interlink |  |  |  | 25 | % |  | Expressed as a proportion of the windfarm output - set to 25% as this is max that alternative export path can support assuming even generation, less than this and additional losses are caused if one export cable fails.
Average service duration for offshore transformer & HV GIS |  |  |  | 2.6667 | hours/year |  | Based on 8 hour shift once every 3 years - visual inspection when in service in-between
Value of energy during contracted period |  |  |  | 115 | £/MWh |  | Assumes 15 year contracted period
Value of energy after contracted period |  |  |  | 75 | £/MWh |  | Assumes 10 year post contract period
Capital Cost Difference between single transformer module based system & multiple transformer based system (HV Interlink) |  |  |  | 23.5 | £M |  | Capex price includes cost of switchgear needed for HV interlink and HV interlink cable
Capital Cost Difference between single transformer module based system & multiple transformer based system (MV Interlink) |  |  |  | 23.5 | £M |  | Capex price includes cost of switchgear needed for MV interlink and MV interlink cable(s)
Capital Cost Difference between single transformer module based system & multiple transformer based system (No Interlink) |  |  |  | 25 | £M
Wind Farm Owner Cost of Finance |  |  |  | 6.25 | % |  | As per GSR 014 Review - If this is changed Loan Repayments need to be recalculated manually in OFTO Loan Repayment Calculator Sheet (cells AF20 and AG20 need to be changed)
OFTO Cost of Finance |  |  |  | 6.25 | % |  | As per GSR 014 Review - If this is changed Loan Repayments need to be recalculated manually in OFTO Loan Repayment Calculator Sheet (cells AF20 and AG20 need to be changed)
Social Time Preference Rate (STPR) |  |  |  | 3.5 | %
Typical SLD for a system using a two transformer module (platform) | [5 empty] | Typical SLD for a system using two single transformer modules (platforms) - HV Interlink | [5 empty] | Typical SLD for a system using two single transformer modules (platforms) - MV interlink | [5 empty] | Typical SLD for a system using two single transformer modules (platforms) - No interlink
Calculation of the effect of limitations of system capacity on the energy exported from the power transmission systems.
Input Data |  |  | Graph1 Data |  |  |  | Graph 2 Data
Graph 1 - Windfarm Output vs Windspeed
Hub height wind speed (m/s) | No. of hours per year | Wind Turbine Power output (%) | Hub height wind speed (m/s) | Windfarm Power Output w/o Fault (MW) | Curtailed Power Output if system limited to a maximum of 50% of rating (MW) | Curtailed Power Output if half of system export capacity is lost (MW) | Hub height wind speed (m/s) | Uncurtailed Energy Generation (MWh/yr) | Curtailed Energy Output if system limited to a maximum of 50% of rating (MWh/yr) | Curtailed Energy Output if half of system export capacity is lost (MWh/yr)
0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 112 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2 | 221 | 0.0034844 | 2 | 0.017422 | 0.017422 | 0.008711 | 2 | 3.8503 | 3.8503 | 1.9251
3 | 350 | 0.72423 | 3 | 3.6211 | 3.6211 | 1.8106 | 3 | 1267.3975 | 1267.3975 | 633.6987
4 | 463 | 2.4466 | 4 | 12.2329 | 12.2329 | 6.1165 | 4 | 5663.8366 | 5663.8366 | 2831.9183
5 | 559 | 5.8571 | 5 | 29.2856 | 29.2856 | 14.6428 | 5 | 16370.6702 | 16370.6702 | 8185.3351
6 | 620 | 11.2043 | 6 | 56.0213 | 56.0213 | 28.0106 | 6 | 34733.1915 | 34733.1915 | 17366.5958
7 | 706 | 18.5606 | 7 | 92.8029 | 92.8029 | 46.4015 | 7 | 65518.8613 | 65518.8613 | 32759.4307
8 | 757 | 28.3722 | 8 | 141.8608 | 141.8608 | 70.9304 | 8 | 107388.6286 | 107388.6286 | 53694.3143
9 | 740 | 40.6224 | 9 | 203.1121 | 203.1121 | 101.5561 | 9 | 150302.9766 | 150302.9766 | 75151.4883
10 | 727 | 55.1003 | 10 | 275.5013 | 250 | 137.7506 | 10 | 200289.4132 | 181750 | 100144.7066
11 | 691 | 70.698 | 11 | 353.49 | 250 | 176.745 | 11 | 244261.5567 | 172750 | 122130.7783
12 | 629 | 84.1377 | 12 | 420.6886 | 250 | 210.3443 | 12 | 264613.146 | 157250 | 132306.573
13 | 530 | 93.1975 | 13 | 465.9876 | 250 | 232.9938 | 13 | 246973.4374 | 132500 | 123486.7187 |  |  | Graph 2 -Annual MWh Generated at each windspeed vs windspeed
14 | 427 | 97.8463 | 14 | 489.2317 | 250 | 244.6158 | 14 | 208901.9309 | 106750 | 104450.9655
15 | 346 | 99.4414 | 15 | 497.2068 | 250 | 248.6034 | 15 | 172033.544 | 86500 | 86016.772
16 | 269 | 99.8724 | 16 | 499.3622 | 250 | 249.6811 | 16 | 134328.4383 | 67250 | 67164.2191
17 | 209 | 99.9735 | 17 | 499.8677 | 250 | 249.9338 | 17 | 104472.3425 | 52250 | 52236.1712
18 | 162 | 99.9953 | 18 | 499.9765 | 250 | 249.9882 | 18 | 80996.1851 | 40500 | 40498.0926
19 | 102 | 100 | 19 | 500 | 250 | 250 | 19 | 51000 | 25500 | 25500
20 | 62 | 100.0007 | 20 | 500.0033 | 250 | 250.0016 | 20 | 31000.2044 | 15500 | 15500.1022
21 | 36 | 100.0007 | 21 | 500.0033 | 250 | 250.0017 | 21 | 18000.1196 | 9000 | 9000.0598
22 | 21 | 100.0007 | 22 | 500.0033 | 250 | 250.0017 | 22 | 10500.0698 | 5250 | 5250.0349
23 | 11 | 100.0007 | 23 | 500.0033 | 250 | 250.0017 | 23 | 5500.0366 | 2750 | 2750.0183
24 | 8 | 100.0007 | 24 | 500.0033 | 250 | 250.0017 | 24 | 4000.0266 | 2000 | 2000.0133
25 | 4 | 97.3136 | 25 | 486.5681 | 250 | 243.284 | 25 | 1946.2723 | 1000 | 973.1361
26 | 1 | 40.66 | 26 | 203.3001 | 203.3001 | 101.65 | 26 | 203.3001 | 203.3001 | 101.65
27 | 1 | 32.9062 | 27 | 164.531 | 164.531 | 82.2655 | 27 | 164.531 | 164.531 | 82.2655
28 | 1 | 27.6725 | 28 | 138.3623 | 138.3623 | 69.1811 | 28 | 138.3623 | 138.3623 | 69.1811
29 | 1 | 0 | 29 | 0 | 0 | 0 | 29 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0
[7 empty] | Totals (MWh/yr) | 2160572.3293 | 1440255.606 | 1080286.1647
[7 empty] | Capacity Factor | 0.49289 | 0.32856 | 0.24644
[7 empty] | Difference (MWh/yr) |  | 720316.7233 | 1080286.1647
[7 empty] | Equivalent Power Lost (MW) |  | 82.1623 | 123.2219
Calculation of Outage durations and energy lost due to Transformer, Switchgear or Cable Failure
|  |  |  | Two Transformer OSP |  | Single Transformer Module inc HV Interlink |  | Single Transformer Module inc MV Interlink |  | Single Transformer Module no Interlink |  | Units
Probability of a transformer fault |  |  |  | 0.002 |  | 0.002 |  | 0.002 |  | 0.002
Mean Outage Time Due to Transformer Fault |  |  |  | 5.84 |  | 5.84 |  | 5.84 |  | 5.84 |  | hrs/year
Probability of a fault in a bay of HV GIS |  |  |  | 0.0011 |  | 0.0011 |  | 0.0011 |  | 0.0011
Mean Outage Time Due to HV GIS Bay Fault |  |  |  | 0.264 |  | 0.264 |  | 0.264 |  | 0.264 |  | hrs/year
Probability of HV Cable Cross Link fault |  |  |  | n/a |  | 0.0012 |  | n/a |  | n/a
Mean Outage Time Due to HV Cross Link Cable Fault |  |  |  | n/a |  | 1.752 |  | n/a |  | n/a |  | hrs/year
Probability of a fault in a bay of MV GIS |  |  |  | 0.0011 |  | 0.0011 |  | 0.0011 |  | 0.0011
Mean Outage Time Due to MV GIS Bay Fault |  |  |  | 0.264 |  | 0.264 |  | 0.264 |  | 0.264 |  | hrs/year
Probability of MV Cable Cross Link fault |  |  |  | n/a |  | n/a |  | 0.0024 |  | n/a
Mean Outage Time Due to MV Cross Link Cable Fault |  |  |  | n/a |  | n/a |  | 3.504 |  | n/a |  | hrs/year
Probability of a HV Export Cable Failure |  |  |  | 0.08 |  | 0.08 |  | 0.08 |  | 0.08
Mean Outage Time Due to HV Export Cable Failure |  |  |  | 116.8 |  | 116.8 |  | 116.8 |  | 116.8 |  | hrs/year
Mean Time when MV Cable Cross Link and Tx or HV GIS out of service |  |  |  | n/a |  | n/a |  | 0.029299 |  | n/a
Outage Time for OSP based system where either an export cable or a transformer or HV GIS is out of service and MV cross link between switchboards is in service(output of system limited to maximum of 50% of rating) - Case 1 |  |  |  | 245.2672 |  |  |  | n/a |  |  |  | Hours/year
Outage Time for OSP based system where either an export cable or a transformer or HV GIS is out of service AND MV cross link between switchboards is Out of Service (loss of production from one half of windfarm) - Case 2 |  |  |  | 0.54078 | [7 empty] | Hours/year
Outage Time on single transformer module based system with HV interlink where transformer or HV disconnector adjacent to transformer is out of service (loss of production from one half of windfarm) - Case 3 | [5 empty] | 12.208 | [5 empty] | Hours/year
Outage Time on single transformer module based system with HV interlink where HV export cable or disconnector in series with HV export cable is out of service - HV cross link in service (output of system limited to 50% of rating) - Case 4 | [5 empty] | 233.332 | [5 empty] | Hours/year
Outage Time on system with single transformer module based system with HV interlink where primary HV export cable or disconnector in series with primary export cable is faulty AND HV cross link or associated disconnectors are faulty (loss of production from one half of windfarm) - Case 5 | [5 empty] | 0.79604 | [5 empty] | Hours/year
Outage Time on system with single transformer module based system with MV interlink where primary HV export cable, transformer or HV disconnector is faulty and MV interlink is in service (output of system limited to 50% of rating) - Case 6 | [7 empty] | 244.6773 |  |  |  | Hours/year
Outage Time on system with single transformer module based system with MV interlink where primary HV export cable, transformer or HV disconnector is faulty and MV interlink out of service (loss of production from one half of windfarm) - Case 7 | [7 empty] | 1.1307 |  |  |  | Hours/year
Outage Time on single transformer module based system without interlink where transformer or HV disconnector adjacent to transformer is out of service (loss of production from one half of windfarm) - Case 8 | [9 empty] | 12.208 |  | Hours/year
Outage Time on single transformer module based system without interlink where HV export cable is out of service (loss of production from one half of windfarm) - Case 9 | [9 empty] | 233.6 |  | Hours/year
Maintenance Outage Duration per system (during which system limited to 50% of rating) |  |  |  | 5.3333 |  |  |  | 5.3333 |  |  |  | Hours/year
Maintenance Outage Duration per system (during which production from one half of windfarm is lost) | [5 empty] | 5.3333 |  |  |  | 5.3333
Total outage duration where system limited to 50% of rating |  |  |  | 250.6006 |  | 233.332 |  | 250.0106 |  | 0 |  | Hours/year
Total outage duration where there is loss of production from one half of windfarm |  |  |  | 0.54078 |  | 18.3374 |  | 1.1307 |  | 251.1413 |  | Hours/year
Average energy loss during outage |  |  |  | 20656.5491 |  | 21430.6515 |  | 20680.7717 |  | 30946.1056 |  | MWh/year
Value of energy loss due to outage (contract) |  |  |  | 2.3755 |  | 2.4645 |  | 2.3783 |  | 3.5588 |  | £M/year
Value of energy loss due to outage (outside contract) |  |  |  | 1.5492 |  | 1.6073 |  | 1.5511 |  | 2.321 |  | £M/year
Calculation of Commercial Impact - Single Transformer Platform based System with HV interlink | [12 empty] | Calculation of Commercial Impact - Single Transformer Platform based System with MV interlink | [11 empty] | Calculation of Commercial Impact - Single Transformer Platform based System with no interlink
Year | Annual Financing cost reduction WFO (£M) | Annual Financing cost reduction OFTO (£M) | Cost of Energy Lost (Contracted Period) (£M) | Cost of Energy Lost (After Contracted Period) (£M) | Difference in cost before contracted period (£M) | Difference in cost during contracted period (£M) | Difference in cost after contracted period (£M) | Discount factor (using STPR) | Total Difference in Cost (£M) | Ownership | Notes |  | Year | Annual Financing cost reduction WFO (£M) | Annual Financing cost reduction OFTO (£M) | Cost of Energy Lost (Contracted Period) (£M) | Cost of Energy Lost (After Contracted Period) (£M) | Difference in cost before contracted period (£M) | Difference in cost during contracted period (£M) | Difference in cost after contracted period (£M) | Discount factor (using STPR) | Total Difference in Cost (£M) | Ownership | Notes | Year | Annual Financing cost reduction WFO (£M) | Annual Financing cost reduction OFTO (£M) | Cost of Energy Lost (Contracted Period) (£M) | Cost of Energy Lost (After Contracted Period) (£M) | Difference in cost before contracted period (£M) | Difference in cost during contracted period (£M) | Difference in cost after contracted period (£M) | Discount factor (using STPR) | Total Difference in Cost (£M) | Ownership | Notes
1 | -0.48958 |  |  |  | -0.48958 |  |  | 1 | -0.48958 | WFO |  |  | 1 | -0.48958 |  |  |  | -0.48958 |  |  | 1 | -0.48958 | WFO |  | 1 | -0.52083 |  |  |  | -0.52083 |  |  | 1 | -0.52083 | WFO
2 | -0.97917 |  |  |  | -0.97917 |  |  | 0.96618 | -0.94605 | WFO |  |  | 2 | -0.97917 |  |  |  | -0.97917 |  |  | 0.96618 | -0.94605 | WFO |  | 2 | -1.0417 |  |  |  | -1.0417 |  |  | 0.96618 | -1.0064 | WFO
3 | -1.4688 |  | 0.044511 |  | -0.73438 | -0.68986 |  | 0.93351 | -1.3295 | WFO | Full generation for 6 months of year 3 |  | 3 | -1.4688 |  | 0.0013928 |  | -0.73438 | -0.73298 |  | 0.93351 | -1.3698 | WFO | Full generation for 6 months of year 3 | 3 | -1.5625 |  | 0.59165 |  | -0.78125 | -0.1896 |  | 0.93351 | -0.9063 | WFO | Full generation for 6 months of year 3
4 | -1.4688 |  | 0.089022 |  |  | -1.3797 |  | 0.90194 | -1.2444 | WFO |  |  | 4 | -1.4688 |  | 0.0027856 |  |  | -1.466 |  | 0.90194 | -1.3222 | WFO |  | 4 | -1.5625 |  | 1.1833 |  |  | -0.3792 |  | 0.90194 | -0.34202 | WFO
5 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.87144 | -1.5471 | OFTO | Transfer to OFTO at start of year 5 |  | 5 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.87144 | -1.6222 | OFTO | Transfer to OFTO at start of year 5 | 5 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.87144 | -0.69715 | OFTO | Transfer to OFTO at start of year 5
6 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.84197 | -1.4947 | OFTO |  |  | 6 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.84197 | -1.5673 | OFTO |  | 6 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.84197 | -0.67358 | OFTO
7 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.8135 | -1.4442 | OFTO |  |  | 7 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.8135 | -1.5143 | OFTO |  | 7 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.8135 | -0.6508 | OFTO
8 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.78599 | -1.3954 | OFTO |  |  | 8 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.78599 | -1.4631 | OFTO |  | 8 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.78599 | -0.62879 | OFTO
9 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.75941 | -1.3482 | OFTO |  |  | 9 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.75941 | -1.4137 | OFTO |  | 9 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.75941 | -0.60753 | OFTO
10 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.73373 | -1.3026 | OFTO |  |  | 10 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.73373 | -1.3659 | OFTO |  | 10 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.73373 | -0.58699 | OFTO
11 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.70892 | -1.2585 | OFTO |  |  | 11 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.70892 | -1.3197 | OFTO |  | 11 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.70892 | -0.56714 | OFTO
12 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.68495 | -1.216 | OFTO |  |  | 12 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.68495 | -1.275 | OFTO |  | 12 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.68495 | -0.54796 | OFTO
13 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.66178 | -1.1749 | OFTO |  |  | 13 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.66178 | -1.2319 | OFTO |  | 13 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.66178 | -0.52943 | OFTO
14 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.6394 | -1.1351 | OFTO |  |  | 14 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.6394 | -1.1903 | OFTO |  | 14 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.6394 | -0.51152 | OFTO
15 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.61778 | -1.0967 | OFTO |  |  | 15 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.61778 | -1.15 | OFTO |  | 15 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.61778 | -0.49423 | OFTO
16 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.59689 | -1.0596 | OFTO |  |  | 16 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.59689 | -1.1111 | OFTO |  | 16 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.59689 | -0.47751 | OFTO
17 |  | -1.8643 | 0.089022 |  |  | -1.7753 |  | 0.57671 | -1.0238 | OFTO |  |  | 17 |  | -1.8643 | 0.0027856 |  |  | -1.8615 |  | 0.57671 | -1.0735 | OFTO |  | 17 |  | -1.9833 | 1.1833 |  |  | -0.8 |  | 0.57671 | -0.46137 | OFTO
18 |  | -1.8643 | 0.044511 | 0.029029 |  | -0.88764 | -0.90312 | 0.5572 | -0.99782 | OFTO | 15 year contract expires mid way through year 18 |  | 18 |  | -1.8643 | 0.0013928 | 0.00090835 |  | -0.93076 | -0.93124 | 0.5572 | -1.0375 | OFTO | 15 year contract expires mid way through year 18 | 18 |  | -1.9833 | 0.59165 | 0.38586 |  | -0.4 | -0.60579 | 0.5572 | -0.56043 | OFTO | 15 year contract expires mid way through year 18
19 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.53836 | -0.97241 | OFTO |  |  | 19 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.53836 | -1.0027 | OFTO |  | 19 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.53836 | -0.65227 | OFTO
20 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.52016 | -0.93953 | OFTO |  |  | 20 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.52016 | -0.96878 | OFTO |  | 20 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.52016 | -0.63021 | OFTO
21 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.50257 | -0.90776 | OFTO |  |  | 21 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.50257 | -0.93602 | OFTO |  | 21 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.50257 | -0.6089 | OFTO
22 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.48557 | -0.87706 | OFTO |  |  | 22 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.48557 | -0.90437 | OFTO |  | 22 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.48557 | -0.58831 | OFTO
23 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.46915 | -0.8474 | OFTO |  |  | 23 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.46915 | -0.87379 | OFTO |  | 23 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.46915 | -0.56842 | OFTO
24 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.45329 | -0.81874 | OFTO | 20 years of OFTO Ownership |  | 24 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.45329 | -0.84424 | OFTO | 20 years of OFTO Ownership | 24 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.45329 | -0.54919 | OFTO | 20 years of OFTO Ownership
25 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.43796 | -0.79106 | OFTO |  |  | 25 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.43796 | -0.81569 | OFTO |  | 25 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.43796 | -0.53062 | OFTO
26 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.42315 | -0.76431 | OFTO |  |  | 26 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.42315 | -0.78811 | OFTO |  | 26 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.42315 | -0.51268 | OFTO
27 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.40884 | -0.73846 | OFTO |  |  | 27 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.40884 | -0.76145 | OFTO |  | 27 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.40884 | -0.49534 | OFTO
28 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.39501 | -0.71349 | OFTO |  |  | 28 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.39501 | -0.7357 | OFTO |  | 28 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.39501 | -0.47859 | OFTO
29 |  | -1.8643 |  | 0.058058 |  |  | -1.8062 | 0.38165 | -0.68936 | OFTO | 25 years of OFTO Ownership |  | 29 |  | -1.8643 |  | 0.0018167 |  |  | -1.8625 | 0.38165 | -0.71083 | OFTO | 25 years of OFTO Ownership | 29 |  | -1.9833 |  | 0.77172 |  |  | -1.2116 | 0.38165 | -0.46241 | OFTO | 25 years of OFTO Ownership
[8 empty] | Total Cost Difference | -30.5638 | £M | [10 empty] | Total Cost Difference | -31.8049 | £M | [9 empty] | Total Cost Difference | -16.847 | £M
[8 empty] | Negative Indicates Saving Overall | [12 empty] | Negative Indicates Saving Overall | [11 empty] | Negative Indicates Saving Overall
Note on C93: nigel.platt: Mean characteristic created from 6 examples of different WTGs and capacities
Note on I127: nigel.platt: Total predicted energy output from system per year if no faults
Note on H129: nigel.platt: Energy lost if fault present all year
Note on H131: nigel.platt: Equals the power lost if the fault was present all year divided by the number of hours per year
Note on I158: nigel.platt: Assumes all MV cross link cables are connected by one bay of MV GIS at each end of interlink
Note on E163: nigel.platt: Assume that the two circuits on a multitransformer OSP are turned off in sequence.
Note on I163: nigel.platt: Assume that the single transformer modules are turned off in sequence
Note on G164: nigel.platt: Assume that the single transformer modules are turned off in sequence
Note on K164: nigel.platt: Assume that the single transformer modules are turned off in sequence
Note on D183: nigel.platt: Assume windfarm starts to generate 50% in year 3
Note on C185: nigel.platt: Change multiplier to G10 for 20 year OFTO Loan Term Value = quarterly repayment difference per £M saving x £M saving x 4 (as there are four quarterly repayments per year)
Note on D198: nigel.platt: Half of generation in this year is in the 15 year contract period

## OFTO_Loan_Repayment_Calculator
OFTO Loan Repayment Calculator
Assume Quarterly Repayments
OFTO Loan Duration |  | 20 or 25 | years
Interest Rate |  | 6.25 | %
Interest Only Repayment - per £M Loan | [5 empty] | 15625
Calculated Quarterly Repayment - per £M loan - 20 years Loan | [5 empty] | 21985
Calculated Quarterly Repayment - per £M loan - 25 years Loan | [5 empty] | 19833
Quarterly Loan Repayment (per £M) - Interest only |  |  |  | 15625
Increment for Calculation |  |  |  | 250
[30 empty] | Manual | Manual
[30 empty] | Test 20 yr | Test 25 yr
|  | Repayment | 15625 | 15875 | 16125 | 16375 | 16625 | 16875 | 17125 | 17375 | 17625 | 17875 | 18125 | 18375 | 18625 | 18875 | 19125 | 19375 | 19625 | 19875 | 20125 | 20375 | 20625 | 20875 | 21125 | 21375 | 21625 | 21875 | 22125 | 21985 | 19833 | Manually Insert Values
Outstanding Loan @ 20 years |  |  | 1000000 | 960691.6636 | 921383.3273 | 882074.9909 | 842766.6546 | 803458.3182 | 764149.9818 | 724841.6455 | 685533.3091 | 646224.9727 | 606916.6364 | 567608.3 | 528299.9637 | 488991.6273 | 449683.2909 | 410374.9546 | 371066.6182 | 331758.2819 | 292449.9455 | 253141.6091 | 213833.2728 | 174524.9364 | 135216.6 | 95908.2637 | 56599.9273 | 17291.591 | -22016.7454 | -4.077 |  | Remaining Balance After 20 Years
Outstanding Loan @ 25 years |  |  | 1000000 | 940584.9109 | 881169.8218 | 821754.7327 | 762339.6436 | 702924.5544 | 643509.4653 | 584094.3762 | 524679.2871 | 465264.198 | 405849.1089 | 346434.0198 | 287018.9307 | 227603.8415 | 168188.7524 | 108773.6633 | 49358.5742 | -10056.5149 | -69471.604 | -128886.6931 | -188301.7822 | -247716.8713 | -307131.9605 | -366547.0496 | -425962.1387 | -485377.2278 | -544792.3169 |  | -74.7799 | Remaining Balance After 25 Years
Year | Quarter | Month | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan | Outstanding Loan
1 | 1 | 3 | 1000000 | 999750 | 999500 | 999250 | 999000 | 998750 | 998500 | 998250 | 998000 | 997750 | 997500 | 997250 | 997000 | 996750 | 996500 | 996250 | 996000 | 995750 | 995500 | 995250 | 995000 | 994750 | 994500 | 994250 | 994000 | 993750 | 993500 | 993640 | 995792
1 | 2 | 6 | 1000000 | 999496.0938 | 998992.1875 | 998488.2812 | 997984.375 | 997480.4688 | 996976.5625 | 996472.6562 | 995968.75 | 995464.8438 | 994960.9375 | 994457.0312 | 993953.125 | 993449.2188 | 992945.3125 | 992441.4062 | 991937.5 | 991433.5938 | 990929.6875 | 990425.7812 | 989921.875 | 989417.9688 | 988914.0625 | 988410.1562 | 987906.25 | 987402.3438 | 986898.4375 | 987180.625 | 991518.25
1 | 3 | 9 | 1000000 | 999238.2202 | 998476.4404 | 997714.6606 | 996952.8809 | 996191.1011 | 995429.3213 | 994667.5415 | 993905.7617 | 993143.9819 | 992382.2021 | 991620.4224 | 990858.6426 | 990096.8628 | 989335.083 | 988573.3032 | 987811.5234 | 987049.7437 | 986287.9639 | 985526.1841 | 984764.4043 | 984002.6245 | 983240.8447 | 982479.0649 | 981717.2852 | 980955.5054 | 980193.7256 | 980620.3223 | 987177.7227
1 | 4 | 12 | 1000000 | 998976.3174 | 997952.6348 | 996928.9522 | 995905.2696 | 994881.587 | 993857.9044 | 992834.2218 | 991810.5392 | 990786.8567 | 989763.1741 | 988739.4915 | 987715.8089 | 986692.1263 | 985668.4437 | 984644.7611 | 983621.0785 | 982597.3959 | 981573.7133 | 980550.0307 | 979526.3481 | 978502.6655 | 977478.9829 | 976455.3003 | 975431.6177 | 974407.9351 | 973384.2525 | 973957.5148 | 982769.3746
2 | 1 | 15 | 1000000 | 998710.3224 | 997420.6447 | 996130.9671 | 994841.2895 | 993551.6118 | 992261.9342 | 990972.2566 | 989682.5789 | 988392.9013 | 987103.2237 | 985813.546 | 984523.8684 | 983234.1907 | 981944.5131 | 980654.8355 | 979365.1578 | 978075.4802 | 976785.8026 | 975496.1249 | 974206.4473 | 972916.7697 | 971627.092 | 970337.4144 | 969047.7368 | 967758.0591 | 966468.3815 | 967190.601 | 978292.1461
2 | 2 | 18 | 1000000 | 998440.1712 | 996880.3423 | 995320.5135 | 993760.6846 | 992200.8558 | 990641.0269 | 989081.1981 | 987521.3692 | 985961.5404 | 984401.7115 | 982841.8827 | 981282.0538 | 979722.225 | 978162.3961 | 976602.5673 | 975042.7384 | 973482.9096 | 971923.0807 | 970363.2519 | 968803.423 | 967243.5942 | 965683.7653 | 964123.9365 | 962564.1077 | 961004.2788 | 959444.45 | 960317.9541 | 973744.9608
2 | 3 | 21 | 1000000 | 998165.7988 | 996331.5977 | 994497.3965 | 992663.1953 | 990828.9941 | 988994.793 | 987160.5918 | 985326.3906 | 983492.1894 | 981657.9883 | 979823.7871 | 977989.5859 | 976155.3847 | 974321.1836 | 972486.9824 | 970652.7812 | 968818.58 | 966984.3789 | 965150.1777 | 963315.9765 | 961481.7754 | 959647.5742 | 957813.373 | 955979.1718 | 954144.9707 | 952310.7695 | 953337.9221 | 969126.7258
2 | 4 | 24 | 1000000 | 997887.1394 | 995774.2789 | 993661.4183 | 991548.5577 | 989435.6972 | 987322.8366 | 985209.976 | 983097.1155 | 980984.2549 | 978871.3943 | 976758.5338 | 974645.6732 | 972532.8126 | 970419.9521 | 968307.0915 | 966194.2309 | 964081.3704 | 961968.5098 | 959855.6492 | 957742.7887 | 955629.9281 | 953517.0675 | 951404.207 | 949291.3464 | 947178.4858 | 945065.6253 | 946248.8272 | 964436.3309
3 | 1 | 27 | 1000000 | 997604.126 | 995208.252 | 992812.378 | 990416.5039 | 988020.6299 | 985624.7559 | 983228.8819 | 980833.0079 | 978437.1339 | 976041.2599 | 973645.3859 | 971249.5118 | 968853.6378 | 966457.7638 | 964061.8898 | 961666.0158 | 959270.1418 | 956874.2678 | 954478.3937 | 952082.5197 | 949686.6457 | 947290.7717 | 944894.8977 | 942499.0237 | 940103.1497 | 937707.2757 | 939048.9651 | 959672.6486
3 | 2 | 30 | 1000000 | 997316.6905 | 994633.3809 | 991950.0714 | 989266.7618 | 986583.4523 | 983900.1427 | 981216.8332 | 978533.5236 | 975850.2141 | 973166.9046 | 970483.595 | 967800.2855 | 965116.9759 | 962433.6664 | 959750.3568 | 957067.0473 | 954383.7377 | 951700.4282 | 949017.1186 | 946333.8091 | 943650.4996 | 940967.19 | 938283.8805 | 935600.5709 | 932917.2614 | 930233.9518 | 931736.6052 | 954834.5337
3 | 3 | 33 | 1000000 | 997024.7637 | 994049.5275 | 991074.2912 | 988099.055 | 985123.8187 | 982148.5825 | 979173.3462 | 976198.1099 | 973222.8737 | 970247.6374 | 967272.4012 | 964297.1649 | 961321.9287 | 958346.6924 | 955371.4562 | 952396.2199 | 949420.9836 | 946445.7474 | 943470.5111 | 940495.2749 | 937520.0386 | 934544.8024 | 931569.5661 | 928594.3298 | 925619.0936 | 922643.8573 | 924309.9896 | 949920.8233
3 | 4 | 36 | 1000000 | 996728.2757 | 993456.5514 | 990184.827 | 986913.1027 | 983641.3784 | 980369.6541 | 977097.9297 | 973826.2054 | 970554.4811 | 967282.7568 | 964011.0324 | 960739.3081 | 957467.5838 | 954195.8595 | 950924.1352 | 947652.4108 | 944380.6865 | 941108.9622 | 937837.2379 | 934565.5135 | 931293.7892 | 928022.0649 | 924750.3406 | 921478.6162 | 918206.8919 | 914935.1676 | 916767.3332 | 944930.3362
4 | 1 | 39 | 1000000 | 996427.155 | 992854.31 | 989281.465 | 985708.6199 | 982135.7749 | 978562.9299 | 974990.0849 | 971417.2399 | 967844.3949 | 964271.5498 | 960698.7048 | 957125.8598 | 953553.0148 | 949980.1698 | 946407.3248 | 942834.4798 | 939261.6347 | 935688.7897 | 932115.9447 | 928543.0997 | 924970.2547 | 921397.4097 | 917824.5646 | 914251.7196 | 910678.8746 | 907106.0296 | 909106.8228 | 939861.8727
4 | 2 | 42 | 1000000 | 996121.3293 | 992242.6586 | 988363.9878 | 984485.3171 | 980606.6464 | 976727.9757 | 972849.305 | 968970.6342 | 965091.9635 | 961213.2928 | 957334.6221 | 953455.9514 | 949577.2807 | 945698.6099 | 941819.9392 | 937941.2685 | 934062.5978 | 930183.9271 | 926305.2563 | 922426.5856 | 918547.9149 | 914669.2442 | 910790.5735 | 906911.9027 | 903033.232 | 899154.5613 | 901326.6169 | 934714.2145
4 | 3 | 45 | 1000000 | 995810.7251 | 991621.4501 | 987432.1752 | 983242.9002 | 979053.6253 | 974864.3503 | 970675.0754 | 966485.8004 | 962296.5255 | 958107.2505 | 953917.9756 | 949728.7006 | 945539.4257 | 941350.1507 | 937160.8758 | 932971.6008 | 928782.3259 | 924593.0509 | 920403.776 | 916214.501 | 912025.2261 | 907835.9511 | 903646.6762 | 899457.4012 | 895268.1263 | 891078.8513 | 893424.8453 | 929486.1241
4 | 4 | 48 | 1000000 | 995495.2676 | 990990.5353 | 986485.8029 | 981981.0705 | 977476.3382 | 972971.6058 | 968466.8734 | 963962.141 | 959457.4087 | 954952.6763 | 950447.9439 | 945943.2116 | 941438.4792 | 936933.7468 | 932429.0145 | 927924.2821 | 923419.5497 | 918914.8173 | 914410.085 | 909905.3526 | 905400.6202 | 900895.8879 | 896391.1555 | 891886.4231 | 887381.6908 | 882876.9584 | 885399.6085 | 924176.3447
5 | 1 | 51 | 1000000 | 995174.8812 | 990349.7624 | 985524.6436 | 980699.5247 | 975874.4059 | 971049.2871 | 966224.1683 | 961399.0495 | 956573.9307 | 951748.8119 | 946923.6931 | 942098.5742 | 937273.4554 | 932448.3366 | 927623.2178 | 922798.099 | 917972.9802 | 913147.8614 | 908322.7425 | 903497.6237 | 898672.5049 | 893847.3861 | 889022.2673 | 884197.1485 | 879372.0297 | 874546.9109 | 877248.9774 | 918783.6001
5 | 2 | 54 | 1000000 | 994849.4887 | 989698.9774 | 984548.4661 | 979397.9548 | 974247.4435 | 969096.9322 | 963946.4209 | 958795.9096 | 953645.3983 | 948494.8871 | 943344.3758 | 938193.8645 | 933043.3532 | 927892.8419 | 922742.3306 | 917591.8193 | 912441.308 | 907290.7967 | 902140.2854 | 896989.7741 | 891839.2628 | 886688.7515 | 881538.2402 | 876387.7289 | 871237.2176 | 866086.7063 | 868970.9927 | 913306.5939
5 | 3 | 57 | 1000000 | 994519.012 | 989038.0239 | 983557.0359 | 978076.0479 | 972595.0598 | 967114.0718 | 961633.0838 | 956152.0957 | 950671.1077 | 945190.1197 | 939709.1316 | 934228.1436 | 928747.1556 | 923266.1675 | 917785.1795 | 912304.1915 | 906823.2034 | 901342.2154 | 895861.2274 | 890380.2393 | 884899.2513 | 879418.2633 | 873937.2752 | 868456.2872 | 862975.2992 | 857494.3111 | 860563.6644 | 907744.0094
5 | 4 | 60 | 1000000 | 994183.3715 | 988366.7431 | 982550.1146 | 976733.4861 | 970916.8576 | 965100.2292 | 959283.6007 | 953466.9722 | 947650.3438 | 941833.7153 | 936017.0868 | 930200.4583 | 924383.8299 | 918567.2014 | 912750.5729 | 906933.9445 | 901117.316 | 895300.6875 | 889484.059 | 883667.4306 | 877850.8021 | 872034.1736 | 866217.5452 | 860400.9167 | 854584.2882 | 848767.6597 | 852024.9717 | 902094.5096
6 | 1 | 63 | 1000000 | 993842.4867 | 987684.9734 | 981527.4601 | 975369.9468 | 969212.4335 | 963054.9203 | 956897.407 | 950739.8937 | 944582.3804 | 938424.8671 | 932267.3538 | 926109.8405 | 919952.3272 | 913794.8139 | 907637.3006 | 901479.7873 | 895322.274 | 889164.7608 | 883007.2475 | 876849.7342 | 870692.2209 | 864534.7076 | 858377.1943 | 852219.681 | 846062.1677 | 839904.6544 | 843352.8619 | 896356.7363
6 | 2 | 66 | 1000000 | 993496.2756 | 986992.5511 | 980488.8267 | 973985.1023 | 967481.3778 | 960977.6534 | 954473.9289 | 947970.2045 | 941466.4801 | 934962.7556 | 928459.0312 | 921955.3068 | 915451.5823 | 908947.8579 | 902444.1334 | 895940.409 | 889436.6846 | 882932.9601 | 876429.2357 | 869925.5113 | 863421.7868 | 856918.0624 | 850414.338 | 843910.6135 | 837406.8891 | 830903.1646 | 834545.2503 | 890529.3103
6 | 3 | 69 | 1000000 | 993144.6549 | 986289.3097 | 979433.9646 | 972578.6195 | 965723.2743 | 958867.9292 | 952012.5841 | 945157.239 | 938301.8938 | 931446.5487 | 924591.2036 | 917735.8584 | 910880.5133 | 904025.1682 | 897169.823 | 890314.4779 | 883459.1328 | 876603.7876 | 869748.4425 | 862893.0974 | 856037.7522 | 849182.4071 | 842327.062 | 835471.7169 | 828616.3717 | 821761.0266 | 825600.0199 | 884610.8308
6 | 4 | 72 | 1000000 | 992787.5401 | 985575.0802 | 978362.6203 | 971150.1604 | 963937.7005 | 956725.2406 | 949512.7807 | 942300.3208 | 935087.8609 | 927875.401 | 920662.9411 | 913450.4812 | 906238.0213 | 899025.5614 | 891813.1015 | 884600.6416 | 877388.1817 | 870175.7218 | 862963.2619 | 855750.802 | 848538.3421 | 841325.8822 | 834113.4223 | 826900.9624 | 819688.5025 | 812476.0426 | 816515.0202 | 878599.875
7 | 1 | 75 | 1000000 | 992424.8454 | 984849.6908 | 977274.5362 | 969699.3817 | 962124.2271 | 954549.0725 | 946973.9179 | 939398.7633 | 931823.6087 | 924248.4542 | 916673.2996 | 909098.145 | 901522.9904 | 893947.8358 | 886372.6812 | 878797.5266 | 871222.3721 | 863647.2175 | 856072.0629 | 848496.9083 | 840921.7537 | 833346.5991 | 825771.4446 | 818196.29 | 810621.1354 | 803045.9808 | 807288.0674 | 872494.998
7 | 2 | 78 | 1000000 | 992056.4836 | 984112.9673 | 976169.4509 | 968225.9345 | 960282.4181 | 952338.9018 | 944395.3854 | 936451.869 | 928508.3526 | 920564.8363 | 912621.3199 | 904677.8035 | 896734.2871 | 888790.7708 | 880847.2544 | 872903.738 | 864960.2216 | 857016.7053 | 849073.1889 | 841129.6725 | 833186.1561 | 825242.6398 | 817299.1234 | 809355.607 | 801412.0906 | 793468.5743 | 797916.9434 | 866294.7324
7 | 3 | 81 | 1000000 | 991682.3662 | 983364.7324 | 975047.0985 | 966729.4647 | 958411.8309 | 950094.1971 | 941776.5633 | 933458.9295 | 925141.2956 | 916823.6618 | 908506.028 | 900188.3942 | 891870.7604 | 883553.1265 | 875235.4927 | 866917.8589 | 858600.2251 | 850282.5913 | 841964.9575 | 833647.3236 | 825329.6898 | 817012.056 | 808694.4222 | 800376.7884 | 792059.1545 | 783741.5207 | 788399.3957 | 859997.5876
7 | 4 | 84 | 1000000 | 991302.4032 | 982604.8063 | 973907.2095 | 965209.6126 | 956512.0158 | 947814.4189 | 939116.8221 | 930419.2252 | 921721.6284 | 913024.0315 | 904326.4347 | 895628.8378 | 886931.241 | 878233.6441 | 869536.0473 | 860838.4505 | 852140.8536 | 843443.2568 | 834745.6599 | 826048.0631 | 817350.4662 | 808652.8694 | 799955.2725 | 791257.6757 | 782560.0788 | 773862.482 | 778733.1362 | 853602.0499
8 | 1 | 87 | 1000000 | 990916.5032 | 981833.0064 | 972749.5096 | 963666.0128 | 954582.516 | 945499.0192 | 936415.5224 | 927332.0256 | 918248.5288 | 909165.032 | 900081.5352 | 890998.0384 | 881914.5416 | 872831.0448 | 863747.548 | 854664.0512 | 845580.5544 | 836497.0576 | 827413.5608 | 818330.0641 | 809246.5673 | 800163.0705 | 791079.5737 | 781996.0769 | 772912.5801 | 763829.0833 | 768915.8415 | 847106.5819
8 | 2 | 90 | 1000000 | 990524.5736 | 981049.1471 | 971573.7207 | 962098.2943 | 952622.8678 | 943147.4414 | 933672.015 | 924196.5885 | 914721.1621 | 905245.7357 | 895770.3092 | 886294.8828 | 876819.4563 | 867344.0299 | 857868.6035 | 848393.177 | 838917.7506 | 829442.3242 | 819966.8977 | 810491.4713 | 801016.0449 | 791540.6184 | 782065.192 | 772589.7656 | 763114.3391 | 753638.9127 | 758945.1515 | 840509.6222
8 | 3 | 93 | 1000000 | 990126.52 | 980253.0401 | 970379.5601 | 960506.0801 | 950632.6001 | 940759.1202 | 930885.6402 | 921012.1602 | 911138.6802 | 901265.2003 | 891391.7203 | 881518.2403 | 871644.7604 | 861771.2804 | 851897.8004 | 842024.3204 | 832150.8405 | 822277.3605 | 812403.8805 | 802530.4005 | 792656.9206 | 782783.4406 | 772909.9606 | 763036.4806 | 753163.0007 | 743289.5207 | 748818.6695 | 833809.5851
8 | 4 | 96 | 1000000 | 989722.2469 | 979444.4938 | 969166.7407 | 958888.9876 | 948611.2345 | 938333.4814 | 928055.7283 | 917777.9752 | 907500.2221 | 897222.469 | 886944.7159 | 876666.9628 | 866389.2097 | 856111.4566 | 845833.7035 | 835555.9504 | 825278.1973 | 815000.4442 | 804722.6911 | 794444.938 | 784167.185 | 773889.4319 | 763611.6788 | 753333.9257 | 743056.1726 | 732778.4195 | 738533.9612 | 827004.8599
9 | 1 | 99 | 1000000 | 989311.657 | 978623.314 | 967934.971 | 957246.628 | 946558.2851 | 935869.9421 | 925181.5991 | 914493.2561 | 903804.9131 | 893116.5701 | 882428.2271 | 871739.8841 | 861051.5411 | 850363.1981 | 839674.8552 | 828986.5122 | 818298.1692 | 807609.8262 | 796921.4832 | 786233.1402 | 775544.7972 | 764856.4542 | 754168.1112 | 743479.7682 | 732791.4253 | 722103.0823 | 728088.5543 | 820093.8108
9 | 2 | 102 | 1000000 | 988894.6517 | 977789.3033 | 966683.955 | 955578.6066 | 944473.2583 | 933367.9099 | 922262.5616 | 911157.2132 | 900051.8649 | 888946.5165 | 877841.1682 | 866735.8198 | 855630.4715 | 844525.1231 | 833419.7748 | 822314.4264 | 811209.0781 | 800103.7297 | 788998.3814 | 777893.033 | 766787.6847 | 755682.3363 | 744576.988 | 733471.6396 | 722366.2913 | 711260.9429 | 717479.938 | 813074.7766
9 | 3 | 105 | 1000000 | 988471.1306 | 976942.2612 | 965413.3917 | 953884.5223 | 942355.6529 | 930826.7835 | 919297.9141 | 907769.0447 | 896240.1752 | 884711.3058 | 873182.4364 | 861653.567 | 850124.6976 | 838595.8282 | 827066.9587 | 815538.0893 | 804009.2199 | 792480.3505 | 780951.4811 | 769422.6117 | 757893.7422 | 746364.8728 | 734836.0034 | 723307.134 | 711778.2646 | 700249.3952 | 706705.562 | 805946.07
9 | 4 | 108 | 1000000 | 988040.992 | 976081.984 | 964122.976 | 952163.968 | 940204.96 | 928245.952 | 916286.944 | 904327.936 | 892368.928 | 880409.92 | 868450.912 | 856491.904 | 844532.896 | 832573.888 | 820614.88 | 808655.872 | 796696.864 | 784737.856 | 772778.848 | 760819.84 | 748860.832 | 736901.824 | 724942.816 | 712983.808 | 701024.8 | 689065.792 | 695762.8364 | 798705.9773
10 | 1 | 111 | 1000000 | 987604.1325 | 975208.265 | 962812.3975 | 950416.53 | 938020.6625 | 925624.795 | 913228.9275 | 900833.06 | 888437.1925 | 876041.325 | 863645.4575 | 851249.59 | 838853.7225 | 826457.855 | 814061.9875 | 801666.12 | 789270.2525 | 776874.385 | 764478.5175 | 752082.65 | 739686.7825 | 727290.915 | 714895.0475 | 702499.18 | 690103.3125 | 677707.445 | 684649.1308 | 791352.7582
10 | 2 | 114 | 1000000 | 987160.4471 | 974320.8941 | 961481.3412 | 948641.7883 | 935802.2353 | 922962.6824 | 910123.1295 | 897283.5765 | 884444.0236 | 871604.4707 | 858764.9178 | 845925.3648 | 833085.8119 | 820246.259 | 807406.706 | 794567.1531 | 781727.6002 | 768888.0472 | 756048.4943 | 743208.9414 | 730369.3884 | 717529.8355 | 704690.2826 | 691850.7296 | 679011.1767 | 666171.6238 | 673361.7734 | 783884.6451
10 | 3 | 117 | 1000000 | 986709.8291 | 973419.6581 | 960129.4872 | 946839.3162 | 933549.1453 | 920258.9743 | 906968.8034 | 893678.6324 | 880388.4615 | 867098.2905 | 853808.1196 | 840517.9487 | 827227.7777 | 813937.6068 | 800647.4358 | 787357.2649 | 774067.0939 | 760776.923 | 747486.752 | 734196.5811 | 720906.4101 | 707616.2392 | 694326.0682 | 681035.8973 | 667745.7264 | 654455.5554 | 661898.0511 | 776299.8426
10 | 4 | 120 | 1000000 | 986252.1701 | 972504.3403 | 958756.5104 | 945008.6805 | 931260.8507 | 917513.0208 | 903765.1909 | 890017.3611 | 876269.5312 | 862521.7013 | 848773.8715 | 835026.0416 | 821278.2117 | 807530.3819 | 793782.552 | 780034.7221 | 766286.8923 | 752539.0624 | 738791.2325 | 725043.4027 | 711295.5728 | 697547.7429 | 683799.9131 | 670052.0832 | 656304.2533 | 642556.4235 | 650255.2082 | 768596.5277
11 | 1 | 123 | 1000000 | 985787.3603 | 971574.7206 | 957362.0809 | 943149.4412 | 928936.8015 | 914724.1617 | 900511.522 | 886298.8823 | 872086.2426 | 857873.6029 | 843660.9632 | 829448.3235 | 815235.6838 | 801023.0441 | 786810.4044 | 772597.7647 | 758385.125 | 744172.4852 | 729959.8455 | 715747.2058 | 701534.5661 | 687321.9264 | 673109.2867 | 658896.647 | 644684.0073 | 630471.3676 | 638430.4458 | 760772.8484
11 | 2 | 126 | 1000000 | 985315.2878 | 970630.5756 | 955945.8634 | 941261.1512 | 926576.439 | 911891.7268 | 897207.0146 | 882522.3024 | 867837.5902 | 853152.878 | 838468.1658 | 823783.4536 | 809098.7413 | 794414.0291 | 779729.3169 | 765044.6047 | 750359.8925 | 735675.1803 | 720990.4681 | 706305.7559 | 691621.0437 | 676936.3315 | 662251.6193 | 647566.9071 | 632882.1949 | 618197.4827 | 626420.9215 | 752826.9242
11 | 3 | 129 | 1000000 | 984835.8392 | 969671.6783 | 954507.5175 | 939343.3567 | 924179.1958 | 909015.035 | 893850.8742 | 878686.7133 | 863522.5525 | 848358.3917 | 833194.2308 | 818030.07 | 802865.9092 | 787701.7484 | 772537.5875 | 757373.4267 | 742209.2659 | 727045.105 | 711880.9442 | 696716.7834 | 681552.6225 | 666388.4617 | 651224.3009 | 636060.14 | 620895.9792 | 605731.8184 | 614223.7484 | 744756.8449
11 | 4 | 132 | 1000000 | 984348.8992 | 968697.7983 | 953046.6975 | 937395.5966 | 921744.4958 | 906093.3949 | 890442.2941 | 874791.1932 | 859140.0924 | 843488.9915 | 827837.8907 | 812186.7899 | 796535.689 | 780884.5882 | 765233.4873 | 749582.3865 | 733931.2856 | 718280.1848 | 702629.0839 | 686977.9831 | 671326.8823 | 655675.7814 | 640024.6806 | 624373.5797 | 608722.4789 | 593071.378 | 601835.9945 | 736560.6706
12 | 1 | 135 | 1000000 | 983854.3507 | 967708.7014 | 951563.0521 | 935417.4028 | 919271.7535 | 903126.1042 | 886980.4549 | 870834.8056 | 854689.1563 | 838543.507 | 822397.8577 | 806252.2084 | 790106.5592 | 773960.9099 | 757815.2606 | 741669.6113 | 725523.962 | 709378.3127 | 693232.6634 | 677087.0141 | 660941.3648 | 644795.7155 | 628650.0662 | 612504.4169 | 596358.7676 | 580213.1183 | 589254.6819 | 728236.4311
12 | 2 | 138 | 1000000 | 983352.0749 | 966704.1499 | 950056.2248 | 933408.2997 | 916760.3747 | 900112.4496 | 883464.5245 | 866816.5995 | 850168.6744 | 833520.7493 | 816872.8243 | 800224.8992 | 783576.9741 | 766929.0491 | 750281.124 | 733633.1989 | 716985.2739 | 700337.3488 | 683689.4237 | 667041.4987 | 650393.5736 | 633745.6485 | 617097.7235 | 600449.7984 | 583801.8733 | 567153.9483 | 576476.7863 | 719782.1253
12 | 3 | 141 | 1000000 | 982841.9511 | 965683.9022 | 948525.8533 | 931367.8044 | 914209.7555 | 897051.7066 | 879893.6577 | 862735.6088 | 845577.5599 | 828419.511 | 811261.4622 | 794103.4133 | 776945.3644 | 759787.3155 | 742629.2666 | 725471.2177 | 708313.1688 | 691155.1199 | 673997.071 | 656839.0221 | 639680.9732 | 622522.9243 | 605364.8754 | 588206.8265 | 571048.7776 | 553890.7287 | 563499.2361 | 711195.721
12 | 4 | 144 | 1000000 | 982323.8566 | 964647.7132 | 946971.5698 | 929295.4264 | 911619.283 | 893943.1395 | 876266.9961 | 858590.8527 | 840914.7093 | 823238.5659 | 805562.4225 | 787886.2791 | 770210.1357 | 752533.9923 | 734857.8489 | 717181.7055 | 699505.562 | 681829.4186 | 664153.2752 | 646477.1318 | 628800.9884 | 611124.845 | 593448.7016 | 575772.5582 | 558096.4148 | 540420.2714 | 550318.9117 | 702475.1541
13 | 1 | 147 | 1000000 | 981797.6668 | 963595.3337 | 945393.0005 | 927190.6674 | 908988.3342 | 890786.0011 | 872583.6679 | 854381.3348 | 836179.0016 | 817976.6685 | 799774.3353 | 781572.0022 | 763369.669 | 745167.3359 | 726965.0027 | 708762.6696 | 690560.3364 | 672358.0033 | 654155.6701 | 635953.337 | 617751.0038 | 599548.6707 | 581346.3375 | 563144.0044 | 544941.6712 | 526739.3381 | 536932.6447 | 693618.3284
13 | 2 | 150 | 1000000 | 981263.2554 | 962526.5108 | 943789.7662 | 925053.0216 | 906316.277 | 887579.5324 | 868842.7878 | 850106.0432 | 831369.2986 | 812632.5539 | 793895.8093 | 775159.0647 | 756422.3201 | 737685.5755 | 718948.8309 | 700212.0863 | 681475.3417 | 662738.5971 | 644001.8525 | 625265.1079 | 606528.3633 | 587791.6187 | 569054.8741 | 550318.1295 | 531581.3849 | 512844.6403 | 523337.2172 | 684623.1148
13 | 3 | 153 | 1000000 | 980720.4938 | 961440.9875 | 942161.4813 | 922881.975 | 903602.4688 | 884322.9626 | 865043.4563 | 845763.9501 | 826484.4438 | 807204.9376 | 787925.4314 | 768645.9251 | 749366.4189 | 730086.9126 | 710807.4064 | 691527.9002 | 672248.3939 | 652968.8877 | 633689.3814 | 614409.8752 | 595130.369 | 575850.8627 | 556571.3565 | 537291.8502 | 518012.344 | 498732.8378 | 509529.3613 | 675487.351
13 | 4 | 156 | 1000000 | 980169.2515 | 960338.503 | 940507.7544 | 920677.0059 | 900846.2574 | 881015.5089 | 861184.7603 | 841354.0118 | 821523.2633 | 801692.5148 | 781861.7662 | 762031.0177 | 742200.2692 | 722369.5207 | 702538.7721 | 682708.0236 | 662877.2751 | 643046.5266 | 623215.778 | 603385.0295 | 583554.281 | 563723.5325 | 543892.7839 | 524062.0354 | 504231.2869 | 484400.5384 | 495505.7575 | 666208.8408
14 | 1 | 159 | 1000000 | 979609.396 | 959218.7921 | 938828.1881 | 918437.5841 | 898046.9801 | 877656.3762 | 857265.7722 | 836875.1682 | 816484.5643 | 796093.9603 | 775703.3563 | 755312.7524 | 734922.1484 | 714531.5444 | 694140.9404 | 673750.3365 | 653359.7325 | 632969.1285 | 612578.5246 | 592187.9206 | 571797.3166 | 551406.7126 | 531016.1087 | 510625.5047 | 490234.9007 | 469844.2968 | 481263.035 | 656785.354
14 | 2 | 162 | 1000000 | 979040.7928 | 958081.5857 | 937122.3785 | 916163.1714 | 895203.9642 | 874244.7571 | 853285.5499 | 832326.3427 | 811367.1356 | 790407.9284 | 769448.7213 | 748489.5141 | 727530.307 | 706571.0998 | 685611.8926 | 664652.6855 | 643693.4783 | 622734.2712 | 601775.064 | 580815.8568 | 559856.6497 | 538897.4425 | 517938.2354 | 496979.0282 | 476019.8211 | 455060.6139 | 466797.7699 | 647214.6251
14 | 3 | 165 | 1000000 | 978463.3052 | 956926.6105 | 935389.9157 | 913853.2209 | 892316.5262 | 870779.8314 | 849243.1366 | 827706.4418 | 806169.7471 | 784633.0523 | 763096.3575 | 741559.6628 | 720022.968 | 698486.2732 | 676949.5785 | 655412.8837 | 633876.1889 | 612339.4941 | 590802.7994 | 569266.1046 | 547729.4098 | 526192.7151 | 504656.0203 | 483119.3255 | 461582.6308 | 440045.936 | 452106.4851 | 637494.3536
14 | 4 | 168 | 1000000 | 977876.7944 | 955753.5887 | 933630.3831 | 911507.1775 | 889383.9719 | 867260.7662 | 845137.5606 | 823014.355 | 800891.1494 | 778767.9437 | 756644.7381 | 734521.5325 | 712398.3269 | 690275.1212 | 668151.9156 | 646028.71 | 623905.5044 | 601782.2987 | 579659.0931 | 557535.8875 | 535412.6819 | 513289.4762 | 491166.2706 | 469043.065 | 446919.8594 | 424796.6537 | 437185.6489 | 627622.2029
15 | 1 | 171 | 1000000 | 977281.1193 | 954562.2386 | 931843.3579 | 909124.4771 | 886405.5964 | 863686.7157 | 840967.835 | 818248.9543 | 795530.0736 | 772811.1929 | 750092.3122 | 727373.4314 | 704654.5507 | 681935.67 | 659216.7893 | 636497.9086 | 613779.0279 | 591060.1472 | 568341.2664 | 545622.3857 | 522903.505 | 500184.6243 | 477465.7436 | 454746.8629 | 432027.9822 | 409309.1015 | 422031.6747 | 617595.7998
15 | 2 | 174 | 1000000 | 976676.1368 | 953352.2736 | 930028.4103 | 906704.5471 | 883380.6839 | 860056.8207 | 836732.9574 | 813409.0942 | 790085.231 | 766761.3678 | 743437.5045 | 720113.6413 | 696789.7781 | 673465.9149 | 650142.0516 | 626818.1884 | 603494.3252 | 580170.462 | 556846.5987 | 533522.7355 | 510198.8723 | 486875.0091 | 463551.1458 | 440227.2826 | 416903.4194 | 393579.5562 | 406640.9196 | 607412.7342
15 | 3 | 177 | 1000000 | 976061.7014 | 952123.4028 | 928185.1042 | 904246.8057 | 880308.5071 | 856370.2085 | 832431.9099 | 808493.6113 | 784555.3127 | 760617.0141 | 736678.7155 | 712740.417 | 688802.1184 | 664863.8198 | 640925.5212 | 616987.2226 | 593048.924 | 569110.6254 | 545172.3268 | 521234.0283 | 497295.7297 | 473357.4311 | 449419.1325 | 425480.8339 | 401542.5353 | 377604.2367 | 391009.6839 | 597070.5582
15 | 4 | 180 | 1000000 | 975437.6655 | 950875.331 | 926312.9965 | 901750.662 | 877188.3275 | 852625.993 | 828063.6585 | 803501.324 | 778938.9895 | 754376.655 | 729814.3205 | 705251.986 | 680689.6515 | 656127.317 | 631564.9825 | 607002.648 | 582440.3135 | 557877.979 | 533315.6444 | 508753.3099 | 484190.9754 | 459628.6409 | 435066.3064 | 410503.9719 | 385941.6374 | 361379.3029 | 375134.2103 | 586566.7857
16 | 1 | 183 | 1000000 | 974803.879 | 949607.758 | 924411.6371 | 899215.5161 | 874019.3951 | 848823.2741 | 823627.1531 | 798431.0322 | 773234.9112 | 748038.7902 | 722842.6692 | 697646.5482 | 672450.4273 | 647254.3063 | 622058.1853 | 596862.0643 | 571665.9434 | 546469.8224 | 521273.7014 | 496077.5804 | 470881.4594 | 445685.3385 | 420489.2175 | 395293.0965 | 370096.9755 | 344900.8545 | 359010.6823 | 575898.8917
16 | 2 | 186 | 1000000 | 974160.1896 | 948320.3793 | 922480.5689 | 896640.7585 | 870800.9482 | 844961.1378 | 819121.3274 | 793281.517 | 767441.7067 | 741601.8963 | 715762.0859 | 689922.2756 | 664082.4652 | 638242.6548 | 612402.8445 | 586563.0341 | 560723.2237 | 534883.4133 | 509043.603 | 483203.7926 | 457363.9822 | 431524.1719 | 405684.3615 | 379844.5511 | 354004.7408 | 328164.9304 | 342635.2242 | 565064.3119
16 | 3 | 189 | 1000000 | 973506.4426 | 947012.8852 | 920519.3278 | 894025.7704 | 867532.213 | 841038.6556 | 814545.0982 | 788051.5407 | 761557.9833 | 735064.4259 | 708570.8685 | 682077.3111 | 655583.7537 | 629090.1963 | 602596.6389 | 576103.0815 | 549609.5241 | 523115.9667 | 496622.4093 | 470128.8519 | 443635.2945 | 417141.7371 | 390648.1796 | 364154.6222 | 337661.0648 | 311167.5074 | 326003.8996 | 554060.4417
16 | 4 | 192 | 1000000 | 972842.4808 | 945684.9615 | 918527.4423 | 891369.923 | 864212.4038 | 837054.8846 | 809897.3653 | 782739.8461 | 755582.3268 | 728424.8076 | 701267.2883 | 674109.7691 | 646952.2499 | 619794.7306 | 592637.2114 | 565479.6921 | 538322.1729 | 511164.6537 | 484007.1344 | 456849.6152 | 429692.0959 | 402534.5767 | 375377.0575 | 348219.5382 | 321062.019 | 293904.4997 | 309112.7105 | 542884.6361
17 | 1 | 195 | 1000000 | 972168.1445 | 944336.289 | 916504.4336 | 888672.5781 | 860840.7226 | 833008.8671 | 805177.0116 | 777345.1562 | 749513.3007 | 721681.4452 | 693849.5897 | 666017.7342 | 638185.8788 | 610354.0233 | 582522.1678 | 554690.3123 | 526858.4569 | 499026.6014 | 471194.7459 | 443362.8904 | 415531.0349 | 387699.1795 | 359867.324 | 332035.4685 | 304203.613 | 276371.7575 | 291957.5966 | 531534.2086
17 | 2 | 198 | 1000000 | 971483.2718 | 942966.5436 | 914449.8153 | 885933.0871 | 857416.3589 | 828899.6307 | 800382.9025 | 771866.1742 | 743349.446 | 714832.7178 | 686315.9896 | 657799.2613 | 629282.5331 | 600765.8049 | 572249.0767 | 543732.3485 | 515215.6202 | 486698.892 | 458182.1638 | 429665.4356 | 401148.7074 | 372631.9791 | 344115.2509 | 315598.5227 | 287081.7945 | 258565.0663 | 274534.4341 | 520006.4306
17 | 3 | 201 | 1000000 | 970787.6979 | 941575.3958 | 912363.0937 | 883150.7916 | 853938.4895 | 824726.1874 | 795513.8853 | 766301.5832 | 737089.2811 | 707876.979 | 678664.6769 | 649452.3748 | 620240.0727 | 591027.7706 | 561815.4685 | 532603.1664 | 503390.8643 | 474178.5622 | 444966.2601 | 415753.958 | 386541.6559 | 357329.3538 | 328117.0517 | 298904.7496 | 269692.4475 | 240480.1454 | 256839.0346 | 508298.5311
17 | 4 | 204 | 1000000 | 970081.2557 | 940162.5114 | 910243.767 | 880325.0227 | 850406.2784 | 820487.5341 | 790568.7898 | 760650.0454 | 730731.3011 | 700812.5568 | 670893.8125 | 640975.0682 | 611056.3238 | 581137.5795 | 551218.8352 | 521300.0909 | 491381.3466 | 461462.6022 | 431543.8579 | 401625.1136 | 371706.3693 | 341787.625 | 311868.8806 | 281950.1363 | 252031.392 | 222112.6477 | 238867.1445 | 496407.6956
18 | 1 | 207 | 1000000 | 969363.7753 | 938727.5506 | 908091.3259 | 877455.1012 | 846818.8765 | 816182.6518 | 785546.4271 | 754910.2024 | 724273.9777 | 693637.753 | 663001.5283 | 632365.3036 | 601729.0789 | 571092.8542 | 540456.6295 | 509820.4048 | 479184.1801 | 448547.9554 | 417911.7307 | 387275.506 | 356639.2813 | 326003.0566 | 295366.8319 | 264730.6072 | 234094.3825 | 203458.1578 | 220614.4436 | 484331.0659
18 | 2 | 210 | 1000000 | 968635.0843 | 937270.1686 | 905905.2529 | 874540.3372 | 843175.4214 | 811810.5057 | 780445.59 | 749080.6743 | 717715.7586 | 686350.8429 | 654985.9272 | 623621.0115 | 592256.0958 | 560891.18 | 529526.2643 | 498161.3486 | 466796.4329 | 435431.5172 | 404066.6015 | 372701.6858 | 341336.7701 | 309971.8544 | 278606.9387 | 247242.0229 | 215877.1072 | 184512.1915 | 202076.5443 | 472065.7388
18 | 3 | 213 | 1000000 | 967895.0075 | 935790.015 | 903685.0224 | 871580.0299 | 839475.0374 | 807370.0449 | 775265.0524 | 743160.0599 | 711055.0673 | 678950.0748 | 646845.0823 | 614740.0898 | 582635.0973 | 550530.1047 | 518425.1122 | 486320.1197 | 454215.1272 | 422110.1347 | 390005.1421 | 357900.1496 | 325795.1571 | 293690.1646 | 261585.1721 | 229480.1796 | 197375.187 | 165270.1945 | 183248.9903 | 459608.7659
18 | 4 | 216 | 1000000 | 967143.367 | 934286.7339 | 901430.1009 | 868573.4679 | 835716.8349 | 802860.2018 | 770003.5688 | 737146.9358 | 704290.3028 | 671433.6697 | 638577.0367 | 605720.4037 | 572863.7707 | 540007.1376 | 507150.5046 | 474293.8716 | 441437.2385 | 408580.6055 | 375723.9725 | 342867.3395 | 310010.7064 | 277154.0734 | 244297.4404 | 211440.8074 | 178584.1743 | 145727.5413 | 164127.2558 | 446957.1529
19 | 1 | 219 | 1000000 | 966379.9821 | 932759.9642 | 899139.9462 | 865519.9283 | 831899.9104 | 798279.8925 | 764659.8746 | 731039.8567 | 697419.8387 | 663799.8208 | 630179.8029 | 596559.785 | 562939.7671 | 529319.7491 | 495699.7312 | 462079.7133 | 428459.6954 | 394839.6775 | 361219.6596 | 327599.6416 | 293979.6237 | 260359.6058 | 226739.5879 | 193119.57 | 159499.5521 | 125879.5341 | 144706.7442 | 434107.8584
19 | 2 | 222 | 1000000 | 965604.6693 | 931209.3386 | 896814.0079 | 862418.6772 | 828023.3465 | 793628.0158 | 759232.6851 | 724837.3544 | 690442.0237 | 656046.693 | 621651.3623 | 587256.0316 | 552860.7009 | 518465.3702 | 484070.0395 | 449674.7088 | 415279.3781 | 380884.0474 | 346488.7167 | 312093.386 | 277698.0553 | 243302.7246 | 208907.3939 | 174512.0633 | 140116.7326 | 105721.4019 | 124982.787 | 421057.7937
19 | 3 | 225 | 1000000 | 964817.2423 | 929634.4845 | 894451.7268 | 859268.969 | 824086.2113 | 788903.4536 | 753720.6958 | 718537.9381 | 683355.1803 | 648172.4226 | 612989.6649 | 577806.9071 | 542624.1494 | 507441.3916 | 472258.6339 | 437075.8762 | 401893.1184 | 366710.3607 | 331527.6029 | 296344.8452 | 261162.0875 | 225979.3297 | 190796.572 | 155613.8142 | 120431.0565 | 85248.2988 | 104950.6431 | 407803.8217
19 | 4 | 228 | 1000000 | 964017.5117 | 928035.0233 | 892052.535 | 856070.0467 | 820087.5584 | 784105.07 | 748122.5817 | 712140.0934 | 676157.605 | 640175.1167 | 604192.6284 | 568210.14 | 532227.6517 | 496245.1634 | 460262.6751 | 424280.1867 | 388297.6984 | 352315.2101 | 316332.7217 | 280350.2334 | 244367.7451 | 208385.2567 | 172402.7684 | 136420.2801 | 100437.7918 | 64455.3034 | 84605.4969 | 394342.7564
20 | 1 | 231 | 1000000 | 963205.2853 | 926410.5706 | 889615.8559 | 852821.1412 | 816026.4265 | 779231.7117 | 742436.997 | 705642.2823 | 668847.5676 | 632052.8529 | 595258.1382 | 558463.4235 | 521668.7088 | 484873.9941 | 448079.2794 | 411284.5646 | 374489.8499 | 337695.1352 | 300900.4205 | 264105.7058 | 227310.9911 | 190516.2764 | 153721.5617 | 116926.847 | 80132.1323 | 43337.4175 | 63942.4578 | 380671.362
20 | 2 | 234 | 1000000 | 962380.3679 | 924760.7357 | 887141.1036 | 849521.4715 | 811901.8394 | 774282.2072 | 736662.5751 | 699042.943 | 661423.3109 | 623803.6787 | 586184.0466 | 548564.4145 | 510944.7823 | 473325.1502 | 435705.5181 | 398085.886 | 360466.2538 | 322846.6217 | 285226.9896 | 247607.3575 | 209987.7253 | 172368.0932 | 134748.4611 | 97128.8289 | 59509.1968 | 21889.5647 | 42956.5587 | 366786.352
20 | 3 | 237 | 1000000 | 961542.5611 | 923085.1222 | 884627.6834 | 846170.2445 | 807712.8056 | 769255.3667 | 730797.9278 | 692340.489 | 653883.0501 | 615425.6112 | 576968.1723 | 538510.7335 | 500053.2946 | 461595.8557 | 423138.4168 | 384680.9779 | 346223.5391 | 307766.1002 | 269308.6613 | 230851.2224 | 192393.7835 | 153936.3447 | 115478.9058 | 77021.4669 | 38564.028 | 106.5891 | 21642.7549 | 352684.3888
20 | 4 | 240 | 1000000 | 960691.6636 | 921383.3273 | 882074.9909 | 842766.6546 | 803458.3182 | 764149.9818 | 724841.6455 | 685533.3091 | 646224.9727 | 606916.6364 | 567608.3 | 528299.9637 | 488991.6273 | 449683.2909 | 410374.9546 | 371066.6182 | 331758.2819 | 292449.9455 | 253141.6091 | 213833.2728 | 174524.9364 | 135216.6 | 95908.2637 | 56599.9273 | 17291.591 | -22016.7454 | -4.077 | 338362.0824
21 | 1 | 243 | 1000000 | 959827.4709 | 919654.9418 | 879482.4126 | 839309.8835 | 799137.3544 | 758964.8253 | 718792.2962 | 678619.7671 | 638447.2379 | 598274.7088 | 558102.1797 | 517929.6506 | 477757.1215 | 437584.5924 | 397412.0632 | 357239.5341 | 317067.005 | 276894.4759 | 236721.9468 | 196549.4177 | 156376.8885 | 116204.3594 | 76031.8303 | 35859.3012 | -4313.2279 | -44485.757 | -21989.1407 | 323815.9899
21 | 2 | 246 | 1000000 | 958949.7751 | 917899.5502 | 876849.3253 | 835799.1005 | 794748.8756 | 753698.6507 | 712648.4258 | 671598.2009 | 630547.976 | 589497.7512 | 548447.5263 | 507397.3014 | 466347.0765 | 425296.8516 | 384246.6267 | 343196.4018 | 302146.177 | 261095.9521 | 220045.7272 | 178995.5023 | 137945.2774 | 96895.0525 | 55844.8277 | 14794.6028 | -26255.6221 | -67305.847 | -44317.7211 | 309042.6147
21 | 3 | 249 | 1000000 | 958058.3654 | 916116.7307 | 874175.0961 | 832233.4614 | 790291.8268 | 748350.1921 | 706408.5575 | 664466.9228 | 622525.2882 | 580583.6535 | 538642.0189 | 496700.3842 | 454758.7496 | 412817.1149 | 370875.4803 | 328933.8456 | 286992.211 | 245050.5763 | 203108.9417 | 161167.307 | 119225.6724 | 77284.0377 | 35342.4031 | -6599.2316 | -48540.8662 | -90482.5009 | -66995.1855 | 294038.4056
21 | 4 | 252 | 1000000 | 957153.0273 | 914306.0546 | 871459.0819 | 828612.1092 | 785765.1366 | 742918.1639 | 700071.1912 | 657224.2185 | 614377.2458 | 571530.2731 | 528683.3004 | 485836.3277 | 442989.355 | 400142.3823 | 357295.4097 | 314448.437 | 271601.4643 | 228754.4916 | 185907.5189 | 143060.5462 | 100213.5735 | 57366.6008 | 14519.6281 | -28327.3446 | -71174.3172 | -114021.2899 | -90026.9852 | 278799.7557
22 | 1 | 255 | 1000000 | 956233.5434 | 912467.0867 | 868700.6301 | 824934.1734 | 781167.7168 | 737401.2602 | 693634.8035 | 649868.3469 | 606101.8903 | 562335.4336 | 518568.977 | 474802.5203 | 431036.0637 | 387269.6071 | 343503.1504 | 299736.6938 | 255970.2372 | 212203.7805 | 168437.3239 | 124670.8672 | 80904.4106 | 37137.954 | -6628.5027 | -50394.9593 | -94161.416 | -137927.8726 | -113418.6569 | 263323.0019
22 | 2 | 258 | 1000000 | 955299.6925 | 910599.385 | 865899.0774 | 821198.7699 | 776498.4624 | 731798.1549 | 687097.8473 | 642397.5398 | 597697.2323 | 552996.9248 | 508296.6172 | 463596.3097 | 418896.0022 | 374195.6947 | 329495.3872 | 284795.0796 | 240094.7721 | 195394.4646 | 150694.1571 | 105993.8495 | 61293.542 | 16593.2345 | -28107.073 | -72807.3806 | -117507.6881 | -162207.9956 | -137175.8234 | 247604.4238
22 | 3 | 261 | 1000000 | 954351.2502 | 908702.5003 | 863053.7505 | 817405.0007 | 771756.2509 | 726107.501 | 680458.7512 | 634810.0014 | 589161.2515 | 543512.5017 | 497863.7519 | 452215.0021 | 406566.2522 | 360917.5024 | 315268.7526 | 269620.0027 | 223971.2529 | 178322.5031 | 132673.7533 | 87025.0034 | 41376.2536 | -4272.4962 | -49921.246 | -95569.9959 | -141218.7457 | -186867.4955 | -161304.1956 | 231640.2429
22 | 4 | 264 | 1000000 | 953387.9885 | 906775.9769 | 860163.9654 | 813551.9538 | 766939.9423 | 720327.9307 | 673715.9192 | 627103.9076 | 580491.8961 | 533879.8846 | 487267.873 | 440655.8615 | 394043.8499 | 347431.8384 | 300819.8268 | 254207.8153 | 207595.8037 | 160983.7922 | 114371.7807 | 67759.7691 | 21147.7576 | -25464.254 | -72076.2655 | -118688.2771 | -165300.2886 | -211912.3002 | -185809.5737 | 215426.6217
23 | 1 | 267 | 1000000 | 952409.6758 | 904819.3516 | 857229.0273 | 809638.7031 | 762048.3789 | 714458.0547 | 666867.7304 | 619277.4062 | 571687.082 | 524096.7578 | 476506.4335 | 428916.1093 | 381325.7851 | 333735.4609 | 286145.1366 | 238554.8124 | 190964.4882 | 143374.164 | 95783.8397 | 48193.5155 | 603.1913 | -46987.1329 | -94577.4572 | -142167.7814 | -189758.1056 | -237348.4298 | -210697.8483 | 198959.6626
23 | 2 | 270 | 1000000 | 951416.077 | 902832.1539 | 854248.2309 | 805664.3078 | 757080.3848 | 708496.4618 | 659912.5387 | 611328.6157 | 562744.6926 | 514160.7696 | 465576.8466 | 416992.9235 | 368409.0005 | 319825.0774 | 271241.1544 | 222657.2313 | 174073.3083 | 125489.3853 | 76905.4622 | 28321.5392 | -20262.3839 | -68846.3069 | -117430.2299 | -166014.153 | -214598.076 | -263181.9991 | -235975.0022 | 182235.4074
23 | 3 | 273 | 1000000 | 950406.9532 | 900813.9063 | 851220.8595 | 801627.8126 | 752034.7658 | 702441.719 | 652848.6721 | 603255.6253 | 553662.5785 | 504069.5316 | 454476.4848 | 404883.4379 | 355290.3911 | 305697.3443 | 256104.2974 | 206511.2506 | 156918.2038 | 107325.1569 | 57732.1101 | 8139.0632 | -41453.9836 | -91047.0304 | -140640.0773 | -190233.1241 | -239826.171 | -289419.2178 | -261647.1116 | 165249.8356
23 | 4 | 276 | 1000000 | 949382.0618 | 898764.1236 | 848146.1854 | 797528.2472 | 746910.309 | 696292.3708 | 645674.4326 | 595056.4944 | 544438.5562 | 493820.618 | 443202.6799 | 392584.7417 | 341966.8035 | 291348.8653 | 240730.9271 | 190112.9889 | 139495.0507 | 88877.1125 | 38259.1743 | -12358.7639 | -62976.7021 | -113594.6403 | -164212.5785 | -214830.5167 | -265448.4549 | -316066.3931 | -287720.3477 | 147998.8643
24 | 1 | 279 | 1000000 | 948341.1565 | 896682.313 | 845023.4696 | 793364.6261 | 741705.7826 | 690046.9391 | 638388.0956 | 586729.2522 | 535070.4087 | 483411.5652 | 431752.7217 | 380093.8782 | 328435.0348 | 276776.1913 | 225117.3478 | 173458.5043 | 121799.6609 | 70140.8174 | 18481.9739 | -33176.8696 | -84835.7131 | -136494.5565 | -188153.4 | -239812.2435 | -291471.087 | -343129.9305 | -314200.9781 | 130478.3466
24 | 2 | 282 | 1000000 | 947283.9871 | 894567.9742 | 841851.9613 | 789135.9484 | 736419.9355 | 683703.9225 | 630987.9096 | 578271.8967 | 525555.8838 | 472839.8709 | 420123.858 | 367407.8451 | 314691.8322 | 261975.8193 | 209259.8064 | 156543.7935 | 103827.7806 | 51111.7676 | -1604.2453 | -54320.2582 | -107036.2711 | -159752.284 | -212468.2969 | -265184.3098 | -317900.3227 | -370616.3356 | -341095.3684 | 112684.0707
24 | 3 | 285 | 1000000 | 946210.2994 | 892420.5988 | 838630.8982 | 784841.1976 | 731051.4969 | 677261.7963 | 623472.0957 | 569682.3951 | 515892.6945 | 462102.9939 | 408313.2933 | 354523.5927 | 300733.8921 | 246944.1915 | 193154.4908 | 139364.7902 | 85575.0896 | 31785.389 | -22004.3116 | -75794.0122 | -129583.7128 | -183373.4134 | -237163.114 | -290952.8147 | -344742.5153 | -398532.2159 | -368409.9835 | 94611.7593
24 | 4 | 288 | 1000000 | 945119.8353 | 890239.6706 | 835359.506 | 780479.3413 | 725599.1766 | 670719.0119 | 615838.8472 | 560958.6825 | 506078.5179 | 451198.3532 | 396318.1885 | 341438.0238 | 286557.8591 | 231677.6944 | 176797.5298 | 121917.3651 | 67037.2004 | 12157.0357 | -42723.129 | -97603.2936 | -152483.4583 | -207363.623 | -262243.7877 | -317123.9524 | -372004.1171 | -426884.2817 | -396151.3895 | 76257.0681
25 | 1 | 291 | 1000000 | 944012.3327 | 888024.6655 | 832036.9982 | 776049.331 | 720061.6637 | 664073.9965 | 608086.3292 | 552098.662 | 496110.9947 | 440123.3274 | 384135.6602 | 328147.9929 | 272160.3257 | 216172.6584 | 160184.9912 | 104197.3239 | 48209.6567 | -7778.0106 | -63765.6779 | -119753.3451 | -175741.0124 | -231728.6796 | -287716.3469 | -343704.0141 | -399691.6814 | -455679.3486 | -424326.255 | 57615.5848
25 | 2 | 294 | 1000000 | 942887.5254 | 885775.0509 | 828662.5763 | 771550.1018 | 714437.6272 | 657325.1527 | 600212.6781 | 543100.2035 | 485987.729 | 428875.2544 | 371762.7799 | 314650.3053 | 257537.8308 | 200425.3562 | 143312.8817 | 86200.4071 | 29087.9325 | -28024.542 | -85137.0166 | -142249.4911 | -199361.9657 | -256474.4402 | -313586.9148 | -370699.3894 | -427811.8639 | -484924.3385 | -452941.3527 | 38682.8283
25 | 3 | 297 | 1000000 | 941745.143 | 883490.2861 | 825235.4291 | 766980.5721 | 708725.7151 | 650470.8582 | 592216.0012 | 533961.1442 | 475706.2873 | 417451.4303 | 359196.5733 | 300941.7163 | 242686.8594 | 184432.0024 | 126177.1454 | 67922.2885 | 9667.4315 | -48587.4255 | -106842.2825 | -165097.1394 | -223351.9964 | -281606.8534 | -339861.7103 | -398116.5673 | -456371.4243 | -514626.2813 | -482003.5614 | 19454.2475
25 | 4 | 300 | 1000000 | 940584.9109 | 881169.8218 | 821754.7327 | 762339.6436 | 702924.5544 | 643509.4653 | 584094.3762 | 524679.2871 | 465264.198 | 405849.1089 | 346434.0198 | 287018.9307 | 227603.8415 | 168188.7524 | 108773.6633 | 49358.5742 | -10056.5149 | -69471.604 | -128886.6931 | -188301.7822 | -247716.8713 | -307131.9605 | -366547.0496 | -425962.1387 | -485377.2278 | -544792.3169 | -511519.867 | -74.7799