## Note
Note to 2019 ETYS Appendix B
Where overhead line circuits are strung on the same transmission towers, their proximity to each other can lead to current and voltage in one circuit inducing current and voltage in the other. This mutual coupling between circuits can affect the Positive Phase Sequence parameters of overhead line circuits. The Positive Phase Sequence values in these tables are taken from PowerFactory models used by National Grid ESO for 2019 ETYS analysis which include these mutual coupling effects.
When using power analysis applications that are not capable of modelling mutual coupling, it may be necessary to adjust overhead line parameters in line with accepted industry assumptions. These adjustments are likely to only have minor impact on power flow but can have material impact on voltages over larger networks. ETYS data users are advised to contact National Grid ESO for advice if intending to use this data in this way.

## Menu
Electricity Ten Year Statement (ETYS) 2019
Appendix B - Supplementary Technical Data
Table | Title
B.1.1a | SHE Transmission Index of Substation Codes
B.1.1b | SPT Index of Substation Codes
B.1.1c | NGET Index of Substation Codes
B.1.1d | OFTO Index of Substation Codes
B.2.1a | SHE Transmission Circuits 2019/20
B.2.1b | SPT Circuits 2019/20
B.2.1c | NGET Circuits 2019/20
B.2.1d | OFTO Circuits 2019/20
B.2.2a | SHE Transmission Circuit Changes 2020/21 to 2028/29
B.2.2b | SPT Transmission Circuit Changes 2020/21 to 2028/29
B.2.2c | NGET Transmission Circuit Changes 2020/21 to 2028/29
B.2.2d | OFTO Circuit Changes 2020/21 to 2028/29
B.3.1a | SHE Transmission Transformers Winter 2019/20
B.3.1b | SPT Transformers Winter 2019/20
B.3.1c | NGET Transformers Winter 2019/20
B.3.1d | OFTO Transformers 2019/20
B.3.2a | SHE Transmission Transformer Changes 2020/21 to 2028/29
B.3.2b | SPT Transformer Changes 2020/21 to 2028/29
B.3.2c | NGET Transformer Changes 2020/21 to 2028/29
B.3.2d | OFTO Transformer Changes 2020/21 to 2028/29
B.4.1a | SHE Transmission Reactive Compensation Equipment Winter 2019/20
B.4.1b | SPT Reactive Compensation Equipment Winter 2019/20
B.4.1c | NGET Reactive Compensation Equipment Winter 2019/20
B.4.1d | OFTO Reactive Compensation Equipment Winter 2019/20
B.4.2a | SHE Transmission Reactive Compensation Equipment Changes 2020/21 to 2028/29
B.4.2b | SPT Reactive Compensation Equipment Changes 2020/21 to 2028/29
B.4.2c | NGET Reactive Compensation Equipment Changes 2020/21 to 2028/29
B.4.2d | OFTO Reactive Compensation Equipment Changes 2020/21 to 2028/29

## B-1-1a
Table B.1.1a - SHE Transmission Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABBA | ABERDEEN BAY | 132
ABED | ABERARDER | 132
ABED | ABERARDER | 33
ABED | ABERARDER | 0.7
ABNE | ABERNETHY | 132
ABNE | ABERNETHY | 33
ACHL | ACHLACHAN | 33
ACHL | ACHLACHAN | 0.7
ACHR | A-CHRUACH | 132
ACHR | A-CHRUACH | 33
ACHR | A-CHRUACH | 0.7
AIGA | AIGAS | 132
AIGA | AIGAS | 11
ALNE | ALNESS | 132
ALNE | ALNESS | 33
ALYT | ALYTH | 400
ALYT | ALYTH | 275
ALYT | ALYTH | 33
AMUL | AMULREE | 132
ANSU | AN SUIDHE | 132
ANSU | AN SUIDHE | 33
ANSU | AN SUIDHE | 0.7
ARBR | ARBROATH | 132
ARBR | ARBROATH | 33
ARBS | ARBROATH | 33
ARBS | ARBROATH | 0.4
ARDK | ARDKINGLAS | 132
ARDK | ARDKINGLAS | 33
ARDK | ARDKINGLAS | 0.7
ARDR | ARDROSS | 275
ARMO | ARDMORE | 132
ARMO | ARDMORE | 33
ARNI | ARNISH | 132
ARNI | ARNISH | 33
BADA | BAD A CHEO FARM | 33
BADA | BAD A CHEO FARM | 0.7
BAIW | BAILLIE | 0.7
BEAT | BEATRICE | 400
BEAU | BEAULY | 400
BEAU | BEAULY | 275
BEAU | BEAULY | 132
BEAU | BEAULY | 33
BEIN | BEINNEUN | 132
BEIN | BEINNEUN | 33
BEIN | BEINNEUN | 0.7
BENA | BEN AKETIL | 33
BENA | BEN AKETIL | 0.7
BERB | BERRY BURN | 275
BERB | BERRY BURN | 33
BERB | BERRY BURN | 0.7
BETH | BEINN THARSUINN | 33
BETH | BEINN THARSUINN | 0.7
BEWF | BEAW FIELD | 132
BEWF | BEAW FIELD | 33
BEWF | BEAW FIELD | 0.7
BHLA | BHLARAIDH | 132
BHLA | BHLARAIDH | 33
BHLA | BHLARAIDH | 0.7
BIHI | BIRKHILL | 132
BILB | BILBO SOLAR FARM | 33
BILB | BILBO SOLAR FARM | 0.4
BLHI | BLACKHILLOCK | 400
BLHI | BLACKHILLOCK | 275
BLHI | BLACKHILLOCK | 132
BLHI | BLACKHILLOCK | 33
BLRH | BLARY HILL FARM | 33
BLRH | BLARY HILL FARM | 0.7
BOAG | BOAT OF GARTEN | 132
BOAG | BOAT OF GARTEN | 33
BOYN | BOYNDIE | 33
BOYN | BOYNDIE | 0.7
BRCW | BRACO WEST | 275
BRCW | BRACO WEST | 33
BRDU | BRAES OF DOUNE | 33
BRDU | BRAES OF DOUNE | 0.7
BREC | BRECHIN | 132
BRID | BRIDGE OF DUN | 132
BRID | BRIDGE OF DUN | 33
BRLG | BRAELANGWELL | 33
BRLG | BRAELANGWELL | 0.7
BROA | BROADFORD | 132
BROA | BROADFORD | 33
BROR | BRORA | 132
BROR | BRORA | 33
BTUI | BEINN AN TUIRC | 33
BTUI | BEINN AN TUIRC | 0.7
BUMU | BURGHMUIR | 132
BUMU | BURGHMUIR | 33
BUWH | BURN OF WHILK | 33
BUWH | BURN OF WHILK | 0.7
CAAD | CARRADALE | 132
CAAD | CARRADALE | 33
CAID | CAIRN DUHIE | 275
CAID | CAIRN DUHIE | 33
CAID | CAIRN DUHIE | 0.7
CAIH | CAIRNMORE HILL | 33
CAIH | CAIRNMORE HILL | 0.7
CAIN | CAPENHURST-INCE | 275
CAIN | CAPENHURST-INCE | 33
CAIR | CAIRN UISH | 33
CAIR | CAIRN UISH | 0.7
CAMW | CAMSTER FARM | 33
CAMW | CAMSTER FARM | 0.7
CASH | CASHLIE | 33
CASH | CASHLIE | 11
CASS | CASSLEY | 132
CASS | CASSLEY | 33
CAUS | CAUSEYMIRE | 33
CAUS | CAUSEYMIRE | 0.7
CEAN | CEANNACROC | 132
CEAN | CEANNACROC | 33
CEAN | CEANNACROC | 11
CHAR | CHARLESTON | 132
CHAR | CHARLESTON | 33
CLAC | CLACHAN | 132
CLAC | CLACHAN | 33
CLAC | CLACHAN | 11
CLAG | CLACHAIG GLEN | 33
CLAG | CLACHAIG GLEN | 0.7
CLAS | CLASHINDARROCH | 33
CLAS | CLASHINDARROCH | 0.7
CLAY | CLAYHILLS | 132
CLAY | CLAYHILLS | 33
CLGO | CLASH GOUR | 275
CLGO | CLASH GOUR | 132
CLGO | CLASH GOUR | 33
CLGO | CLASH GOUR | 0.7
CLOI | CLOICHE | 132
CLOI | CLOICHE | 33
CLOI | CLOICHE | 0.7
CLSO | CLASHINDARROCH | 132
CLSO | CLASHINDARROCH | 33
CLSO | CLASHINDARROCH | 0.7
CLUN | CLUNIE | 132
CLUN | CLUNIE | 11
COGA | CORRIEGARTH | 132
COGA | CORRIEGARTH | 33
COGL | COIRE GLAS | 400
COGL | COIRE GLAS | 15
COIN | COIRE NA CLOICHE | 33
COIN | COIRE NA CLOICHE | 0.7
CONN | CONNAGILL | 275
CONN | CONNAGILL | 132
CONN | CONNAGILL | 33
CORI | CORRIEMOILLIE | 132
CORI | CORRIEMOILLIE | 33
CORI | CORRIEMOILLIE | 0.7
COST | COSTA HEAD | 33
COST | COSTA HEAD | 0.7
COUA | COUPAR ANGUS | 132
COUA | COUPAR ANGUS | 33
COUA | COUPAR ANGUS | 0.7
COUB | COUPAR | 33
COUB | COUPAR | 11
COUW | COUR | 33
COUW | COUR | 0.7
CRAI | CRAIGIEBUCKLER | 132
CRAI | CRAIGIEBUCKLER | 33
CRDH | CREAG DHUBH | 275
CRDH | CREAG DHUBH | 132
CRDH | CREAG DHUBH | 33
CREA | CREAG RIABHACH FARM | 132
CREA | CREAG RIABHACH FARM | 33
CREA | CREAG RIABHACH FARM | 0.7
CRMY | CORRIMONY | 33
CRMY | CORRIMONY | 0.7
CRSS | CROSSAIG | 220
CRSS | CROSSAIG | 132
CRSS | CROSSAIG | 33
CULL | CULLIGRAN | 132
CULL | CULLIGRAN | 11
DAAS | DALLAS | 275
DAAS | DALLAS | 33
DEAN | DEANIE | 132
DEAN | DEANIE | 11
DENS | DENSIDE | 132
DEUC | DEUCHERAN HILL | 33
DEUC | DEUCHERAN HILL | 0.7
DORE | DORENELL | 132
DORE | DORENELL | 33
DORE | DORENELL | 0.7
DOUN | DOUNREAY | 275
DOUN | DOUNREAY | 220
DOUN | DOUNREAY | 132
DOUN | DOUNREAY | 33
DRUL | DRUIM LETHANN | 132
DRUL | DRUIM LETHANN | 33
DRUL | DRUIM LETHANN | 0.7
DUBE | DUNBEATH | 132
DUBE | DUNBEATH | 33
DUBE | DUNBEATH | 0.7
DUCC | DUNMOREE COMPOUND | 132
DUDH | DUDHOPE | 132
DUDH | DUDHOPE | 33
DUGR | DUNVEGAN GRID | 132
DUGR | DUNVEGAN GRID | 33
DUNM | DUNMAGLASS | 132
DUNM | DUNMAGLASS | 33
DUNO | DUNOON | 33
DYCE | DYCE | 132
DYCE | DYCE | 33
EDIN | EDINBANE | 132
EDIN | EDINBANE | 33
EDIN | EDINBANE | 0.7
EDNT | EDINTORE FARM | 33
EDNT | EDINTORE FARM | 0.7
ELCH | ELCHIES | 132
ELCH | ELCHIES | 33
ELCH | ELCHIES | 0.7
ELGI | ELGIN | 132
ELGI | ELGIN | 33
ENEI | ENERGY ISLES | 132
ENEI | ENERGY ISLES | 33
ENEI | ENERGY ISLES | 0.7
ERRL | ERROL PV | 33
ERRL | ERROL PV | 0.4
ERRO | ERROCHTY | 132
ERRO | ERROCHTY | 11
FAAR | FARR FARM | 132
FAAR | FARR FARM | 33
FAAR | FARR FARM | 0.7
FARI | FARIGAIG | 275
FARI | FARIGAIG | 132
FARI | FARIGAIG | 33
FASN | FASNAKYLE | 275
FASN | FASNAKYLE | 33
FASN | FASNAKYLE | 11
FAUG | FORT AUGUSTUS | 400
FAUG | FORT AUGUSTUS | 275
FAUG | FORT AUGUSTUS | 132
FAUG | FORT AUGUSTUS | 33
FAWI | FAIRBURN FARM | 33
FAWI | FAIRBURN FARM | 0.7
FERO | FERNOCH | 132
FERO | FERNOCH | 33
FERO | FERNOCH | 0.7
FETT | FETTERESSO | 400
FETT | FETTERESSO | 275
FETT | FETTERESSO | 132
FETT | FETTERESSO | 33
FEWI | FETTERESSO | 33
FEWI | FETTERESSO | 0.7
FIDD | FIDDES | 275
FIDD | FIDDES | 132
FIDD | FIDDES | 33
FINL | FINLARIG | 132
FINL | FINLARIG | 11
FINS | ORKNEY FINSTOWN | 220
FINS | ORKNEY FINSTOWN | 132
FINS | ORKNEY FINSTOWN | 33
FINS | ORKNEY FINSTOWN | 0.7
FOFF |  | 275
FOGG | FOGGIETON | 132
FOYE | FOYERS | 275
FOYE | FOYERS | 18
FRAS | FRASERBURGH | 132
FRAS | FRASERBURGH | 33
FRSD | FREASDAIL | 33
FRSD | FREASDAIL | 0.7
FWIL | FORT WILLIAM | 132
FWIL | FORT WILLIAM | 33
FYRI | FYRISH | 275
FYRI | FYRISH | 132
FYRI | FYRISH | 33
GILB | GILLS BAY | 132
GLAG | GLENAGNES | 132
GLCA | GLENCASSLEY | 33
GLCA | GLENCASSLEY | 0.7
GLDO | GLENDOE | 132
GLDO | GLENDOE | 18
GLEN | GLENMORISTON | 132
GLEN | GLENMORISTON | 11
GLFA | GLENFARCLAS | 132
GLFA | GLENFARCLAS | 33
GLKO | GLEN KYLLACHY | 132
GLKO | GLEN KYLLACHY | 33
GLKO | GLEN KYLLACHY | 0.7
GLNE | GLEAN EOGHAINN | 33
GLNE | GLEAN EOGHAINN | 0.7
GLNU | GLEN ULLINISH FARM | 33
GLNU | GLEN ULLINISH FARM | 0.7
GLOF | GLENS OF FOUNDLAND | 33
GLOF | GLENS OF FOUNDLAND | 0.7
GLSH | GELNSHERO FARM | 132
GLSH | GELNSHERO FARM | 33
GLSH | GELNSHERO FARM | 0.7
GOHI | GORDONSTOWN HILL | 33
GOHI | GORDONSTOWN HILL | 0.7
GOLT | GOLTICLAY | 33
GOLT | GOLTICLAY | 0.8
GORW | GORDONBUSH FARM | 275
GORW | GORDONBUSH FARM | 33
GORW | GORDONBUSH FARM | 0.7
GRIF | GRIFFIN FARM | 132
GRIF | GRIFFIN FARM | 33
GRIF | GRIFFIN FARM | 0.7
GRUB | GRUDIE BRIDGE | 132
GRUB | GRUDIE BRIDGE | 33
GRUB | GRUDIE BRIDGE | 11
HALY | HALSARY FARM | 33
HALY | HALSARY FARM | 0.7
HEST | HESTA HEAD | 33
HEST | HESTA HEAD | 0.7
HIGL | HILL OF GLASCHYLE | 33
HIGL | HILL OF GLASCHYLE | 0.7
HITO | HILL OF TOWIE | 33
HITO | HILL OF TOWIE | 0.7
HYWD | HYWIND | 33
HYWD | HYWIND | 0.7
INAW | INVERAWE | 33
INAW | INVERAWE | 11
INGA | INVERGARRY | 400
INGA | INVERGARRY | 132
INGA | INVERGARRY | 33
INGA | INVERGARRY | 11
INNE | INVERNESS | 132
INNE | INVERNESS | 33
INRU | INVERUGIE | 132
INSW | INSCH | 0.7
INVE | INVERARAY | 132
INVR | INVERARNAN | 132
INVR | INVERARNAN | 33
JAMB | JAMESFIELD | 33
JAMB | JAMESFIELD | 0.4
KEIT | KEITH | 275
KEIT | KEITH | 132
KEIT | KEITH | 33
KIIN | KILLIN | 132
KIIN | KILLIN | 33
KILC | KILLIN | 132
KILO | KINLOCHLEVEN | 132
KILO | KINLOCHLEVEN | 33
KILO | KINLOCHLEVEN | 6.6
KINT | KINTORE | 400
KINT | KINTORE | 275
KINT | KINTORE | 132
KINT | KINTORE | 33
KINW | KINCARDINE | 33
KINW | KINCARDINE | 0.7
KIOR | KILMORACK | 132
KIOR | KILMORACK | 11
KISO | KILBRAUR SOUTH | 33
KISO | KILBRAUR SOUTH | 0.9
KNOC | KNOCKNAGAEL | 275
KNOC | KNOCKNAGAEL | 132
KNOC | KNOCKNAGAEL | 33
KRTO | KIRKTON | 33
KRTO | KIRKTON | 0.4
LAGG | LAGGAN | 132
LAIR | LAIRG | 132
LAIR | LAIRG | 33
LAIR | LAIRG | 0.7
LHBR | LOCHABER | 33
LIMK | LIMEKILNS FARM | 132
LIMK | LIMEKILNS FARM | 33
LIMK | LIMEKILNS FARM | 0.7
LIVI | LIVISHIE | 11
LLUC | LOCH LUICHART FARM | 33
LLUC | LOCH LUICHART FARM | 0.7
LOCB | LOCH BUIDHE | 275
LOCB | LOCH BUIDHE | 132
LOCB | LOCH BUIDHE | 33
LOCH | LOCHAY | 132
LOCH | LOCHAY | 33
LOCH | LOCHAY | 11
LOCL | LOCH LUNDIE | 132
LUBR | LUBREOCH | 33
LUIC | LUICHART | 132
LUIC | LUICHART | 11
LUMB | LUMBS | 132
LUNA | LUNANHEAD | 132
LUNA | LUNANHEAD | 33
LUND | LUNDAVRA | 132
LYND | LYNDHURST | 132
LYND | LYNDHURST | 33
MACD | MACDUFF | 132
MACD | MACDUFF | 33
MEIK | MEIKLETON FARM | 33
MEIK | MEIKLETON FARM | 0.7
MELG | MELGARVE | 400
MELG | MELGARVE | 132
MELG | MELGARVE | 33
MIHW | MID HILL FARM | 33
MIHW | MID HILL FARM | 0.7
MILC | MILTON OF CRAIGIE | 132
MILC | MILTON OF CRAIGIE | 33
MILS | MILLENNIUM SOUTH FARM | 132
MILS | MILLENNIUM SOUTH FARM | 33
MILS | MILLENNIUM SOUTH FARM | 0.7
MILW | MILLENIUM | 132
MILW | MILLENIUM | 33
MILW | MILLENIUM | 0.7
MITA | MILLTOWN AIRFIELD | 33
MITA | MILLTOWN AIRFIELD | 0.4
MORF | MORAY FIRTH | 400
MORF | MORAY FIRTH | 275
MOSS | MOSSFORD | 132
MOSS | MOSSFORD | 11
MOTA | MOULTAIVE | 132
MOYW | MOY | 33
MOYW | MOY | 0.7
MUAI | MUAITHEBHEAL | 132
MUAI | MUAITHEBHEAL | 33
MUAI | MUAITHEBHEAL | 0.7
MYBS | MYBSTER | 132
MYBS | MYBSTER | 33
NAIR | NAIRN | 132
NAIR | NAIRN | 33
NANT | NANT | 132
NANT | NANT | 11
NEDE | NEW DEER | 400
NEDE | NEW DEER | 275
NESQ | NESS OF QUOYS | 33
NESQ | NESS OF QUOYS | 0.7
NOVA | NOVAR | 33
NOVA | NOVAR | 0.7
NOVW | NOVAR | 33
NOVW | NOVAR | 0.7
NWGL | NORTH CONNECT | 400
ORRI | ORRIN | 132
ORRI | ORRIN | 33
ORRI | ORRIN | 11
PAUL | PAUL'S HILL | 33
PAUL | PAUL'S HILL | 0.7
PEHE | PETERHEAD | 400
PEHE | PETERHEAD | 275
PEHE | PETERHEAD | 132
PEHE | PETERHEAD | 33
PEHE | PETERHEAD | 23.5
PEHE | PETERHEAD | 15.8
PEHG | PETERHEAD GRANGE | 132
PEHG | PETERHEAD GRANGE | 33
PEHS | PETERHEAD SHELL | 11
PENF | PENTLAND FIRTH | 132
PENF | PENTLAND FIRTH | 33
PENF | PENTLAND FIRTH | 6.6
PERS | PERSLEY | 275
PERS | PERSLEY | 132
PERS | PERSLEY | 33
PITL | PITLOCHRY | 11
PORA | PORT ANN | 132
PORA | PORT ANN | 33
QUOI | QUOICH | 132
QUOI | QUOICH | 11
RANN | RANNOCH | 132
RANN | RANNOCH | 33
RANN | RANNOCH | 11
REDM | REDMOSS | 132
REDM | REDMOSS | 33
ROSE | ROSEHALL | 33
ROSE | ROSEHALL | 0.7
ROTI | ROTHIENORMAN | 400
ROTI | ROTHIENORMAN | 275
ROTI | ROTHIENORMAN | 132
ROTI | ROTHIENORMAN | 33
RTHE | ROTHES III | 33
RTHE | ROTHES III | 0.7
SALA | SALLACHY | 132
SALA | SALLACHY | 33
SALA | SALLACHY | 0.8
SFEG | ST FERGUS | 132
SFEG | ST FERGUS | 11
SFEM | ST FERGUS | 132
SFEM | ST FERGUS | 11
SFER | ST FERGUS | 132
SFIL | ST FILLANS | 132
SFIL | ST FILLANS | 33
SFIL | ST FILLANS | 11
SHET | SHETLAND | 132
SHIN | SHIN | 132
SHIN | SHIN | 33
SHIN | SHIN | 11
SLKB | SLACKBUIE | 132
SLOY | SLOY | 132
SLOY | SLOY | 11
SOUI | SOUND OF ISLAY | 33
SOUI | SOUND OF ISLAY | 0.7
SPCH | SPEYSIDE CHP | 33
SPCH | SPEYSIDE CHP | 11
SPIT | SPITTAL | 275
SPIT | SPITTAL | 132
SPIT | SPITTAL | 33
SPYW | SPEYSLAW | 33
SPYW | SPEYSLAW | 0.4
STOM | STONEYWOOD MILLS | 33
STOM | STONEYWOOD MILLS | 11
STRB | STRATH BRORA | 275
STRB | STRATH BRORA | 33
STRB | STRATH BRORA | 0.7
STRI | STRICHEN | 132
STRI | STRICHEN | 33
STRL | STRONELAIRG | 132
STRL | STRONELAIRG | 33
STRL | STRONELAIRG | 0.7
STRS | STROUPSTER | 33
STRS | STROUPSTER | 0.7
STRW | STRATHY | 132
STRW | STRATHY | 33
STRW | STRATHY | 0.7
STWN | STORNOWAY | 132
STWN | STORNOWAY | 33
STWN | STORNOWAY | 0.7
TABS | TARLAND | 33
TABS | TARLAND | 0.4
TANG | TANGY | 33
TANG | TANGY | 0.7
TARL | TARLAND | 132
TARL | TARLAND | 33
TAYN | TAYNUILT | 132
TAYN | TAYNUILT | 33
TEAL | TEALING | 275
TEAL | TEALING | 132
TEAL | TEALING | 33
THUS | THURSO SOUTH | 275
THUS | THURSO SOUTH | 132
THUS | THURSO SOUTH | 33
TLYM | TULLYMURDOCH | 33
TLYM | TULLYMURDOCH | 0.7
TOMN | TOM NAN CLACH | 33
TOMN | TOM NAN CLACH | 0.7
TOMT | TOMATIN | 275
TOMT | TOMATIN | 132
TOMT | TOMATIN | 33
TORA | TORR ACHILTY | 33
TORA | TORR ACHILTY | 11
TULW | TULLO | 33
TULW | TULLO | 0.7
TUMB | TUMMEL BRIDGE | 132
TUMB | TUMMEL BRIDGE | 33
TUMB | TUMMEL BRIDGE | 11
TUMM | TUMMEL | 400
TUMM | TUMMEL | 275
TUMM | TUMMEL | 132
TUMM | TUMMEL | 33
WATH | WATHEGAR FARM | 33
WATH | WATHEGAR FARM | 0.7
WESR | WESTRAY | 33
WESR | WESTRAY | 0.7
WHIB | WHITE BRIDGE | 132
WILW | WILLOW | 132
WILW | WILLOW | 33
WILW | WILLOW | 0.7
WIOW | WILLOWDALE | 132
WIOW | WILLOWDALE | 33
WISL | WEST ISLAY | 33
WISL | WEST ISLAY | 0.7
WOHI | WOODHILL | 132
WOHI | WOODHILL | 33

## B-1-1b
Table B.1.1b - SPT Index of Substation Codes
Site Code | Site Name | Voltage (kV)
AIKE | AIKENGALL | 33
AIRI | AIRIES | 33
ANDE | ANDERSHAW | 33
AREC | ARECLEOCH | 132
AREC | ARECLEOCH | 33
ASVA | ASSEL VALLEY | 33
AUCH | AUCHENCROSH | 275
AUCW | AUCHENWYND | 132
AURO | AUCHROBERT | 33
AYR- | AYR | 275
AYR- | AYR | 33
BAGA | BATHGATE RAIL | 25
BAGA | BATHGATE | 33
BAIN | BAINSFORD | 33
BENB | BENBRACK WIND FARM | 33
BERW | BERWICK | 132
BERW | BERWICK | 33
BLAH | BLACKHILL | 132
BLAH | BLACKHILL | 33
BLCW | BLACKCRAIG | 33
BLKL | BLACKLAW | 132
BLKL | BLACKLAW | 33
BLLX | BLACKLAW EXTENSION | 132
BLLX | BLACKLAW EXTENSION | 33
BONB | BONNYBRIDGE BORDER NODE | 275
BONB | BONNYBRIDGE BORDER NODE | 400
BONN | BONNYBRIDGE | 25
BONN | BONNYBRIDGE | 132
BONN | BONNYBRIDGE | 33
BONN | BONNYBRIDGE | 400
BPGR | BP GRANGEMOUTH | 11
BRAP | BRAEHEAD PARK | 132
BRAP | BRAEHEAD PARK | 33
BRNX | BRANXTON | 400
BROC | BROKEN CROSS | 132
BROX | BROXBURN | 33
BUSB | BUSBY | 275
CAFA | CARSFAD | 132
CAFA | CARSFAD | 11
CALD | CALDER WATER | 33
CATY | CARNTYNE | 25
CATY | CARNTYNE | 33
CHAP | CHAPELCROSS | 132
CHAP | CHAPELCROSS | 33
CHAS | CHARLOTTE STREET | 275
CHMO | CHIRMORIE | 132
CLYM | CLYDE'S MILL | 275
CLYM | CLYDE'S MILL | 33
CLYN | CLYDE NORTH | 275
CLYN | CLYDE NORTH | 33
CLYS | CLYDE SOUTH | 275
CLYS | CLYDE SOUTH | 33
COAL | COALBURN | 400
COAT | COATBRIDGE | 275
COAT | COATBRIDGE | 33
COCK | COCKENZIE | 275
COCK | COCKENZIE | 33
COYL | COYLTON | 132
COYL | COYLTON | 275
COYL | COYLTON | 33
COYT | COYLTON TEE | 132
CRDY | CROSSDYKES | 33
CROE | CROOKEDSTANE | 33
CROO | CROOKSTON | 132
CRYR | CRYSTAL RIG | 132
CRYR | CRYSTAL RIG | 400
CUMB | CUMBERNAULD | 132
CUMB | CUMBERNAULD | 33
CUMH | CUMBERHEAD | 132
CUMH | CUMBERHEAD | 33
CUPA | CUPAR | 33
CURR | CURRIE | 25
CURR | CURRIE | 275
CURR | CURRIE | 33
CURR | CURRIE | 11
DALB | DALMALLY BORDER NODE | 275
DALL | DALMALLY | 275
DALM | DALMARNOCK | 132
DALM | DALMARNOCK | 275
DALQ | DALQUHANDY | 33
DALS | DALSWINTON | 33
DENN | DENNY NORTH | 132
DENN | DENNY NORTH | 275
DENN | DENNY NORTH | 33
DENN | DENNY NORTH | 400
DESA | DERSALLOCH | 33
DEVM | DEVOL MOOR | 25
DEVM | DEVOL MOOR | 132
DEVM | DEVOL MOOR | 33
DEVM | DEVOL MOOR | 400
DEVO | DEVONSIDE | 132
DEVO | DEVONSIDE | 33
DEWP | DEWAR PLACE | 275
DEWP | DEWAR PLACE | 33
DONO | DOUGLAS NORTH | 132
DOWE | DOUGLAS WEST | 33
DRCR | DRUMCROSS | 132
DRCR | DRUMCROSS | 33
DRUM | DRUMCHAPEL | 275
DRUM | DRUMCHAPEL | 33
DUMF | DUMFRIES | 132
DUMF | DUMFRIES | 33
DUNE | DUNLAW EXTENSION | 132
DUNE | DUNLAW EXTENSION | 33
DUNF | DUNFERMLINE | 132
DUNF | DUNFERMLINE | 33
DUNH | DUNHILL | 33
EARB | EARLSBURN | 33
EAST | EARLSTOUN | 132
EAST | EARLSTOUN | 11
ECCF | ECCLEFECHAN | 25
ECCL | ECCLES | 132
ECCL | ECCLES | 33
EERH | EASTERHOUSE | 275
EERH | EASTERHOUSE | 33
EKIL | EAST KILBRIDE | 275
EKIL | EAST KILBRIDE | 33
EKIS | EAST KILBRIDE SOUTH | 275
EKIS | EAST KILBRIDE SOUTH | 33
ELDE | ELDERSLIE | 132
ELDE | ELDERSLIE | 33
ELVA | ELVANFOOT | 25
ELVA | ELVANFOOT | 132
ELVA | ELVANFOOT | 275
ELVA | ELVANFOOT | 400
ELVN | ELVANFOOT NORTH 132KV | 132
ELVN | ELVANFOOT NORTH 400KV | 400
ENHI | ENOCH HILL WIND FARM | 33
ERSK | ERSKINE | 132
ERSK | ERSKINE | 33
ESST | ESSENSIDE | 132
EWEH | EWE HILL | 132
EWEH | EWE HILL | 33
EXON | EXXON MOBIL | 33
EXON | EXXON MOBIL | 11
FALL | FALLAGO | 400
FASI | FAW SIDE | 132
FINN | FINNIESTON | 132
FINN | FINNIESTON | 33
GALA | GALASHIELS | 132
GALA | GALASHIELS | 33
GARB | GARELOCH BOUNDARY | 132
GAWH | GALAWHISTLE | 132
GAWH | GALAWHISTLE | 33
GIFF | GIFFNOCK | 275
GLAP | GLEN APP | 33
GLGL | GLENGLASS | 132
GLGL | GLENGLASS | 33
GLLE | GLENLEE | 132
GLLE | GLENLEE | 11
GLLU | GLENLUCE | 132
GLLU | GLENLUCE | 33
GLMU | GLENMUCKLOCH | 33
GLNI | GLENNISTON | 132
GLNI | GLENNISTON | 33
GLRB | GLENROTHES BOUNDARY | 275
GLRO | GLENROTHES | 275
GLRO | GLENROTHES | 33
GORG | GORGIE | 33
GOVA | GOVAN | 132
GOVA | GOVAN | 33
GRMO | GRANGEMOUTH | 275
GRMO | GRANGEMOUTH | 33
GRNA | GRETNA | 132
GRNA | GRETNA | 33
GRNA | GRETNA | 400
HABU | HARRY BURN WIND FARM | 33
HADH | HADYARD HILL | 132
HADH | HADYARD HILL | 33
HAGR | HAGGS ROAD | 132
HAGR | HAGGS ROAD | 33
HAKB | HARKER BORDER NODE | 132
HAKB | HARKER BORDER NODE | 400
HARE | HARESTANES | 132
HARE | HARESTANES | 33
HARH | HARBURN HEAD | 33
HAWI | HAWICK | 132
HAWI | HAWICK | 33
HELE | HELENSBURGH | 132
HELE | HELENSBURGH | 33
HOPR | HOPSRIG WIND FARM | 33
HUCS | HUNTERSTON CONVERTER STATION | 400
HUER | HUNTERSTON | 132
HUER | HUNTERSTON | 33
HUER | HUNTERSTON | 400
HUNE | HUNTERSTON EAST | 400
HUNF | HUNTERSTON FARM | 132
HUNF | HUNTERSTON FARM | 33
HUNN | HUNTERSTON NORTH | 220
INKE | INVERKEITHING | 33
INVB | INVERARNAN BORDER NODE | 275
INVR | INVERARNAN | 275
INWI | INNERWICK | 25
JOHN | JOHNSTONE | 33
JUNA | JUNCTION A | 132
JUNV | JUNCTION V | 132
KAIM | KAIMES | 275
KAIM | KAIMES | 33
KEIH | KEITHSHILL | 33
KENE | KENNOXHEAD WINDFARM EXTENSION | 33
KENN | KENNOXHEAD | 132
KEOO | KENDOON | 132
KEOO | KENDOON | 11
KIER | KILLERMONT | 132
KIER | KILLERMONT | 33
KILB | KILBOWIE | 132
KILB | KILBOWIE | 33
KILB | KILBOWIE | 11
KILG | KILGALLIOCH | 275
KILG | KILGALLIOCH | 33
KILS | KILMARNOCK SOUTH | 132
KILS | KILMARNOCK SOUTH | 275
KILS | KILMARNOCK SOUTH | 33
KILT | KILMARNOCK TOWN | 33
KILW | KILWINNING | 132
KILW | KILWINNING | 33
KINC | KINCARDINE | 275
KINC | KINCARDINE | 33
KYPE | KYPE MUIR | 132
KYPE | KYPE MUIR | 33
LAMB | LAMBHILL | 275
LEVE | LEVEN | 33
LING | LIVINGSTON | 132
LING | LIVINGSTON | 33
LINM | LINNMILL | 132
LINM | LINNMILL | 33
LOAN | LONGANNET | 275
LONB | LONGBURN | 132
LOPA | LONGPARK | 33
LORG | LORG WIND FARM | 33
MAHI | MARK HILL | 132
MAHI | MARK HILL | 275
MAHI | MARK HILL | 33
MARG | MARGREE | 132
MARM | MARSHALL MEADOWS | 25
MAYB | MAYBOLE | 132
MAYB | MAYBOLE | 33
MAYT | MAYBOLE TEE | 132
MEAD | MEADOWHEAD | 132
MEAD | MEADOWHEAD | 11
MIDM | MIDDLE MUIR | 33
MINN | MINNYGAP | 33
MINS | MINSCA | 33
MOFF | MOFFAT | 132
MOFF | MOFFAT | 33
MOFF | MOFFAT | 400
MONQ | MONQUHILL | 33
MOSH | MOSSMORRAN SHELL | 132
NEAR | NEWARTHILL | 33
NECU | NEW CUMNOCK | 132
NECU | NEW CUMNOCK | 275
NECU | NEW CUMNOCK | 33
NEIL | NEILSTON | 400
NETS | NEWTON STEWART | 132
NETS | NEWTON STEWART | 33
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 132
NLEI | NORTH LOWTHER | 33
NNGA | NEART NA GAOITHE | 33
NNGB | NEART NA GAOITHE | 33
PAIS | PAISLEY | 132
PAIS | PAISLEY | 33
PART | PARTICK | 132
PART | PARTICK | 33
PENC | PENCLOE | 33
POGB | POGBIE | 33
POLK | POLKEMMET | 33
POOB | PORTOBELLO | 25
POOB | PORTOBELLO | 33
PORD | PORT DUNDAS | 275
PORD | PORT DUNDAS | 33
RAVE | RAVENSCRAIG | 33
REDH | REDHOUSE | 132
REDH | REDHOUSE | 33
ROBP | ROTHES BIOPOWER | 33
ROBP | ROTHES BIOPOWER | 11
SACO | SALTCOATS | 25
SAKN | SANDY KNOWE | 132
SANQ | SANQUHAR WIND FARM | 132
SANX | ST ANDREWS CROSS | 25
SANX | ST ANDREWS CROSS | 33
SCOP | SCOOP HILL WIND FARM | 132
SHRU | SHRUBHILL | 275
SHRU | SHRUBHILL | 33
SIGH | SIGHTHILL | 275
SMEA | SMEATON | 132
SMEA | SMEATON | 275
SMEA | SMEATON | 33
SMEA | SMEATON | 400
SNED | SNEDDON LAW | 33
SNQR | SANQUHAR | 33
SOKY | SOUTH KYLE | 132
SOKY | SOUTH KYLE | 33
SOLW | SOLWAY BANK | 33
SPAV | SPANGO VALLEY | 132
SPAV | SPANGO VALLEY | 33
STCR | STEVEN'S CROFT | 33
STCR | STEVEN'S CROFT | 11
STHA | STRATHAVEN | 275
STIR | STIRLING | 33
STLE | STRATHLEVEN | 25
STLE | STRATHLEVEN | 132
STLE | STRATHLEVEN | 33
STNO | STRANOCH WIND FARM | 33
STWB | STELLA WEST BORDER NODE | 400
TELR | TELFORD ROAD | 33
TODD | TODDLEBURN | 33
TONG | TONGLAND | 132
TONG | TONGLAND | 33
TONG | TONGLAND | 11
TORH | TORR HILL | 33
TORM | TORMYWHEEL | 33
TORN | TORNESS | 132
TORN | TORNESS | 33
TORN | TORNESS | 400
TRAL | TRALORG | 33
VIRD | VIRIDOR | 11
VIRD | VIRIDOR | 33
WESE | WESTERDOD | 132
WFIB | WESTFIELD BOUNDARY | 275
WFIE | WESTFIELD | 132
WFIE | WESTFIELD | 275
WFIE | WESTFIELD | 33
WGEO | WEST GEORGE STREET | 33
WHBR | WHITELAW BRAE | 33
WHHO | WHITEHOUSE | 33
WHLL | WHITESIDE HILL | 33
WHTB | WHISTLEFIELD BOUNDARY | 132
WHTL | WHISTLEFIELD | 33
WISH | WISHAW (GOWKTHRAPPLE) | 25
WISH | WISHAW (GOWKTHRAPPLE) | 132
WISH | WISHAW (GOWKTHRAPPLE) | 275
WISH | WISHAW (GOWKTHRAPPLE) | 33
WISH | WISHAW (GOWKTHRAPPLE) | 400
WIYH | WINDYHILL | 132
WIYH | WINDYHILL | 275
WIYH | WINDYHILL | 400
WLEE | WHITELEE | 275
WLEE | WHITELEE | 33
WLEX | WHITELEE EXTENSION | 275
WLEX | WHITELEE EXTENSION | 33

## B-1-1c
Table B.1.1c - NGET Transmission Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABHA | ABHAM | 132
ABHA | ABHAM | 400
ABTH | ABERTHAW | 132
ABTH | ABERTHAW | 275
ALDW | ALDWARKE | 275
ALDW | ALDWARKE | 33
ALST | ALPHA STEEL | 33
ALVE | ALVERDISCOTT | 132
ALVE | ALVERDISCOTT | 400
AMEM | AMERSHAM | 132
AMEM | AMERSHAM | 400
AUST | AUST | 400
AXMI | AXMINSTER | 400
BAGB | BAGLAN BAY | 275
BARK | BARKING | 132
BARK | BARKING | 275
BARK | BARKING | 56.6
BARP | BARKING PS | 275
BARW | BARKING WEST (LE) | 33
BEDD | BEDDINGTON | 132
BEDD | BEDDINGTON | 275
BEDD | BEDDINGTON | 33
BEDD | BEDDINGTON | 400
BEDT | BEDDINGTON TEE | 132
BESW | BERKSWELL | 132
BESW | BERKSWELL | 275
BICF | BICKER FEN | 132
BICF | BICKER FEN | 400
BIRK | BIRKENHEAD | 132
BIRK | BIRKENHEAD | 275
BISW | BISHOPS WOOD | 132
BISW | BISHOPS WOOD | 275
BLYT | BLYTH | 132
BLYT | BLYTH | 275
BLYT | BLYTH | 400
BLYT | BLYTH | 66
BODE | BODELWYDDAN SUBSTATION | 132
BODE | BODELWYDDAN SUBSTATION | 275
BODE | BODELWYDDAN SUBSTATION | 400
BOLN | BOLNEY | 132
BOLN | BOLNEY | 400
BOTW | BOTLEY WOOD | 132
BOTW | BOTLEY WOOD | 400
BRAI | BRAINTREE | 132
BRAI | BRAINTREE | 400
BRAW | BRADFORD WEST | 132
BRAW | BRADFORD WEST | 275
BRAW | BRADFORD WEST | 400
BRED | BREDBURY | 132
BRED | BREDBURY | 275
BRFO | BRAMFORD | 132
BRFO | BRAMFORD | 400
BRIM | BRIMSDOWN | 132
BRIM | BRIMSDOWN | 275
BRIN | BRINSWORTH | 275
BRIN | BRINSWORTH | 400
BRIT | BRITNED | 400
BRLE | BRAMLEY | 132
BRLE | BRAMLEY | 400
BRWA | BRIDGEWATER | 275
BRWA | BRIDGEWATER | 400
BULL | BULLS LODGE | 400
BURW | BURWELL MAIN | 132
BURW | BURWELL MAIN | 400
BUSH | BUSHBURY | 132
BUSH | BUSHBURY | 275
BUSH | BUSHBURY | 33
BUST | BUSTLEHOLME | 132
BUST | BUSTLEHOLME | 275
BUST | BUSTLEHOLME | 400
CAMA | CAMBRIDGE ARMS | 132
CAML | CAMBLESFORTH | 66
CANT | CANTERBURY | 132
CANT | CANTERBURY | 400
CAPE | CAPENHURST | 132
CAPE | CAPENHURST | 275
CAPE | CAPENHURST | 400
CARE | CARDIFF EAST | 132
CARE | CARDIFF EAST | 275
CARR | CARRINGTON | 132
CARR | CARRINGTON | 275
CARR | CARRINGTON | 400
CELL | CELLARHEAD | 132
CELL | CELLARHEAD | 400
CHIC | CHICKERELL | 132
CHIC | CHICKERELL | 400
CHIL | CHILLING | 400
CHSI | CHESSINGTON | 132
CHSI | CHESSINGTON | 275
CHTE | CHESTERFIELD | 132
CHTE | CHESTERFIELD | 275
CHUE | CHAFFORD HUNDRED | 400
CILF | CILFYNNYD | 275
CILF | CILFYNNYD | 400
CITR | CITY ROAD | 132
CITR | CITY ROAD | 400
CLEH | CLEVE HILL | 400
CONQ | CONNAHS QUAY | 132
CONQ | CONNAHS QUAY | 400
COSO | CORYTON SOUTH | 400
COTT | COTTAM | 400
COVE | COVENTRY | 132
COVE | COVENTRY | 275
COWL | COWLEY | 132
COWL | COWLEY | 400
COWT | COWBRIDGE TEE | 275
CREB | CREYKE BECK | 132
CREB | CREYKE BECK | 275
CREB | CREYKE BECK | 400
CULJ | CULHAM JET | 33
CULJ | CULHAM JET | 400
DAIN | DAINES | 275
DAIN | DAINES | 400
DAMC | DAMHEAD CREEK | 400
DEES | DEESIDE | 400
DIDC | DIDCOT | 400
DINO | DINORWIG | 400
DRAK | DRAKELOW | 132
DRAK | DRAKELOW | 275
DRAK | DRAKELOW | 400
DRAX | DRAX | 132
DRAX | DRAX | 400
DUNG | DUNGENESS | 275
DUNG | DUNGENESS | 400
EALI | EALING | 275
EALI | EALING | 66
EASO | EATON SOCON | 132
EASO | EATON SOCON | 400
ECLA | EAST CLAYDON | 132
ECLA | EAST CLAYDON | 400
EGGB | EGGBOROUGH | 400
ELLA | ELLAND | 132
ELLA | ELLAND | 275
ELST | ELSTREE | 132
ELST | ELSTREE | 275
ELST | ELSTREE | 400
ENDE | ENDERBY | 132
ENDE | ENDERBY | 400
EXET | EXETER | 132
EXET | EXETER | 400
FAWL | FAWLEY | 132
FAWL | FAWLEY | 400
FECK | FECKENHAM | 275
FECK | FECKENHAM | 400
FECK | FECKENHAM | 66
FENW | FENWICK TEE | 400
FERR | FERRYBRIDGE | 132
FERR | FERRYBRIDGE | 275
FERR | FERRYBRIDGE | 400
FERR | FERRYBRIDGE | 66
FFES | FFESTINIOG | 275
FIDF | FIDDLERS FERRY | 132
FIDF | FIDDLERS FERRY | 275
FLEE | FLEET | 132
FLEE | FLEET | 400
FLIB | FLINTSHIRE BRIDGE CONVERTER STATION | 275
FLIB | FLINTSHIRE BRIDGE CONVERTER STATION | 400
FOUR | FOURSTONES | 275
FOUR | FOURSTONES | 33
FROD | FRODSHAM | 132
FROD | FRODSHAM | 275
FROD | FRODSHAM | 400
GART | GARTH CABLE COMPOUND | 400
GRAI | GRAIN | 132
GRAI | GRAIN | 400
GRAN | GRANGE | 66
GREN | GRENDON | 132
GREN | GRENDON | 400
GRIW | GRIMSBY WEST | 132
GRIW | GRIMSBY WEST | 400
GRSA | GREYSTONES A | 275
GRSB | GREYSTONES B | 275
GRST | GREYSTONES | 275
GRST | GREYSTONES | 66
GRTO | GRANGETOWN | 275
GRTO | GRANGETOWN | 66
GWYN | GWYNEDD | 132
GWYN | GWYNEDD | 33
GWYN | GWYNEDD | 400
HACK | HACKNEY | 132
HACK | HACKNEY | 275
HACK | HACKNEY | 400
HACK | HACKNEY | 66
HAMB | HAMBLETON TEE | 400
HAMH | HAMS HALL | 132
HAMH | HAMS HALL | 275
HAMH | HAMS HALL | 400
HARK | HARKER | 132
HARK | HARKER | 275
HARK | HARKER | 400
HARM | HARTMOOR | 275
HARM | HARTMOOR | 66
HATL | HARTLEPOOL | 275
HAWP | HAWTHORN PIT | 275
HAWP | HAWTHORN PIT | 400
HAWP | HAWTHORN PIT | 66
HEDD | HEDDON TEE (CODE NOW MEDB) | 400
HEDN | HEDON | 132
HEDN | HEDON | 275
HEDN | HEDON | 400
HEDO | HEDON (GIS) | 132
HEDO | HEDON (GIS) | 275
HEND | HENDON | 132
HEYS | HEYSHAM | 132
HEYS | HEYSHAM | 400
HIBU | HIGHBURY | 132
HIBU | HIGHBURY | 400
HIGM | HIGH MARNHAM | 275
HIGM | HIGH MARNHAM | 400
HINP | HINKLEY POINT | 275
HINP | HINKLEY POINT | 400
HUMR | HUMBER REFINERY | 33
HUMR | HUMBER REFINERY | 400
HURS | HURST | 132
HURS | HURST | 275
HUTT | HUTTON | 132
HUTT | HUTTON | 400
IMPP | IMPERIAL PARK | 33
IMPP | IMPERIAL PARK | 400
INCE | INCE | 132
INDQ | INDIAN QUEENS | 132
INDQ | INDIAN QUEENS | 400
IROA | IRON ACTON | 132
IROA | IRON ACTON | 275
IRON | IRONBRIDGE | 132
IRON | IRONBRIDGE | 400
ISLI | ISLINGTON | 132
IVER | IVER | 132
IVER | IVER | 275
IVER | IVER | 400
IVER | IVER | 66
JORD | JORDANTHORPE | 275
JORD | JORDANTHORPE | 33
KEAD | KEADBY | 132
KEAD | KEADBY | 400
KEAP | KEADBY POWER (COMPANY) | 400
KEAR | KEARSLEY | 132
KEAR | KEARSLEY | 275
KEAR | KEARSLEY | 33
KEAR | KEARSLEY | 400
KEMS | KEMSLEY | 132
KEMS | KEMSLEY | 400
KENG | KENSAL GREEN | 400
KIBY | KIRKBY | 132
KIBY | KIRKBY | 275
KILL | KILLINGHOLME | 400
KINO | KINGSNORTH | 132
KINO | KINGSNORTH | 400
KIRK | KIRKSTALL | 132
KIRK | KIRKSTALL | 275
KITW | KITWELL | 132
KITW | KITWELL | 275
KNAR | KNARESBOROUGH | 132
KNAR | KNARESBOROUGH | 275
LACK | LACKENBY | 275
LACK | LACKENBY | 400
LACK | LACKENBY | 66
LAGA | LANGAGE | 400
LAKE | LAKESIDE CABLE COOLING STATION | 400
LALE | LALEHAM | 132
LALE | LALEHAM | 275
LAND | LANDULPH | 132
LAND | LANDULPH | 400
LEGA | LEGACY | 132
LEGA | LEGACY | 400
LEIB | LEIGHTON BUZZARD | 275
LEIB | LEIGHTON BUZZARD | 400
LEIS | LEISTON | 132
LEIS | LEISTON | 400
LEMR | LEA MARSTON | 132
LISD | LISTER DRIVE | 132
LISD | LISTER DRIVE | 275
LITB | LITTLE BARFORD | 400
LITT | LITTLEBROOK | 132
LITT | LITTLEBROOK | 275
LITT | LITTLEBROOK | 33
LITT | LITTLEBROOK | 400
LODR | LODGE ROAD | 66
LOFI | LONGFIELD | 400
LOVE | LOVEDEAN | 132
LOVE | LOVEDEAN | 400
MACC | MACCLESFIELD | 275
MACC | MACCLESFIELD | 33
MACC | MACCLESFIELD | 400
MAGA | MARGAM | 275
MANN | MANNINGTON | 132
MANN | MANNINGTON | 400
MAWO | MARCHWOOD | 400
MEDW | MEDWAY | 400
MELK | MELKSHAM | 132
MELK | MELKSHAM | 275
MELK | MELKSHAM | 400
MIDL | MIDDLETON | 400
MILH | MILL HILL | 132
MILH | MILL HILL | 275
MITY | MINETY | 132
MITY | MINETY | 400
MONF | MONK FRYSTON | 275
MONF | MONK FRYSTON | 400
NECH | NECHELLS | 132
NECH | NECHELLS | 275
NECT | NECTON | 132
NECT | NECTON | 400
NEEP | NEEPSEND | 275
NEEP | NEEPSEND | 33
NEEP | NEEPSEND | 400
NEWX | NEW CROSS | 132
NEWX | NEW CROSS | 275
NEWX | NEW CROSS | 66
NFLE | NORTHFLEET EAST | 132
NFLE | NORTHFLEET EAST | 400
NHYD | NORTH HYDE | 275
NHYD | NORTH HYDE | 66
NINF | NINFIELD | 132
NINF | NINFIELD | 400
NORL | NORTON LEES | 275
NORL | NORTON LEES | 33
NORM | NORWICH MAIN | 400
NORT | NORTON | 132
NORT | NORTON | 275
NORT | NORTON | 400
NORW | NORWICH | 132
NORW | NORWICH | 400
NOTR | NORWICH TROWSE | 132
NURS | NURSLING | 132
NURS | NURSLING | 33
NURS | NURSLING BATTERY STORAGE COMPOUND | 33
NURS | NURSLING | 400
OCKH | OCKER HILL | 132
OCKH | OCKER HILL | 275
OFFE | OFFERTON | 275
OFFE | OFFERTON | 33
OLDB | OLDBURY | 132
OLDB | OLDBURY | 275
OLDB | OLDBURY | 400
OLDS | OLDSBURY ON SEVERN | 132
OSBA | OSBALDWICK | 132
OSBA | OSBALDWICK | 400
PADI | PADIHAM | 132
PADI | PADIHAM | 400
PAFB | PATFORD BRIDGE | 400
PELH | PELHAM | 132
PELH | PELHAM | 400
PEMB | PEMBROKE | 132
PEMB | PEMBROKE | 400
PENE | PENWORTHAM EAST | 132
PENN | PENN | 132
PENN | PENN | 275
PENN | PENN | 400
PENT | PENTIR | 132
PENT | PENTIR | 400
PENW | PENWORTHAM WEST | 132
PERH | PENRHOS | 132
PEWO | PENWORTHAM | 275
PEWO | PENWORTHAM | 400
PITS | PITSMOOR | 275
PITS | PITSMOOR | 33
POPP | POPPLETON | 275
POPP | POPPLETON | 33
PORH | PORT HAM | 132
PUDM | PUDDING MILL LANE | 400
PYLE | PYLE | 132
PYLE | PYLE | 275
QUER | QUERNMOOR | 400
RAIN | RAINHILL | 132
RAIN | RAINHILL | 275
RASS | RASSAU | 132
RASS | RASSAU | 400
RATS | RATCLIFFE-ON-SOAR | 132
RATS | RATCLIFFE-ON-SOAR | 275
RATS | RATCLIFFE-ON-SOAR | 400
RAYL | RAYLEIGH | 400
RAYM | RAYLEIGH MAIN | 132
REBR | REDBRIDGE | 275
REBR | REDBRIDGE | 33
RHIG | RHIGOS | 400
RICH | RICHBOROUGH | 400
ROCH | ROCHDALE | 132
ROCH | ROCHDALE | 275
ROCH | ROCHDALE | 400
ROCK | ROCKSAVAGE | 132
ROCK | ROCKSAVAGE | 400
ROWD | ROWDOWN | 275
ROWD | ROWDOWN | 400
RUGE | RUGELEY | 132
RUGE | RUGELEY | 400
RYEH | RYEHOUSE | 132
RYEH | RYEHOUSE | 400
RYHA | RYHALL (NETWORK RAIL) | 400
SAEN | SALTEND NORTH S/STN | 132
SAEN | SALTEND NORTH S/STN | 275
SAES | SALT END SOUTH | 275
SAES | SALT END SOUTH | 33
SAFO | SANDFORD | 400
SALH | SALTHOLME | 132
SALH | SALTHOLME | 275
SASA | ST ASAPH | 132
SEAB | SEABANK | 132
SEAB | SEABANK | 400
SELL | SELLINDGE | 132
SELL | SELLINDGE | 275
SELL | SELLINDGE | 400
SELL4A | SELLINDGE COMPOUND A | 400
SELL4B | SELLINDGE COMPOUND B | 400
SHBA | SOUTH HUMBER BANK | 400
SHEC | SHEFFIELD CITY | 275
SHEC | SHEFFIELD CITY | 33
SHEE | SHEERNESS | 132
SHRE | SHREWSBURY | 132
SHRE | SHREWSBURY | 400
SING | SINGLEWELL | 275
SING | SINGLEWELL | 400
SIZE | SIZEWELL | 132
SIZE | SIZEWELL | 400
SJOW | ST JOHNS WOOD | 132
SJOW | ST JOHNS WOOD | 275
SJOW | ST JOHNS WOOD | 400
SJOW | ST JOHNS WOOD | 66
SKLG | SKELTON GRANGE | 132
SKLG | SKELTON GRANGE | 275
SMAN | SOUTH MANCHESTER | 132
SMAN | SOUTH MANCHESTER | 275
SPEN | SPENNYMOOR | 132
SPEN | SPENNYMOOR | 275
SPEN | SPENNYMOOR | 400
SPLN | SPALDING | 400
SSHI | SOUTH SHIELDS | 275
SSHI | SOUTH SHIELDS | 33
STAH | STANAH | 132
STAH | STANAH | 400
STAL | STALYBRIDGE | 132
STAL | STALYBRIDGE | 275
STAL | STALYBRIDGE | 400
STAY | STAYTHORPE | 400
STEN | STELLA NORTH | 132
STES | STELLA SOUTH | 132
STEW | STELLA WEST | 275
STEW | STELLA WEST | 400
STOB | STOKE BARDOLPH | 132
STOB | STOKE BARDOLPH | 400
STSB | STOCKSBRIDGE | 400
STSB | STOCKSBRIDGE | 66
STYC | STAYTHORPE C (FOR USE IN OLTA) | 132
SUND | SUNDON | 132
SUND | SUNDON | 33
SUND | SUNDON | 400
SUTB | SUTTON BRIDGE | 400
SWAN | SWANSEA NORTH | 132
SWAN | SWANSEA NORTH | 275
SWAN | SWANSEA NORTH | 400
TAUN | TAUNTON | 132
TAUN | TAUNTON | 400
TEMP | TEMPLEBOROUGH | 275
TEMP | TEMPLEBOROUGH | 33
THOM | THORPE MARSH | 275
THOM | THORPE MARSH | 400
THOM | THORPE MARSH | 66
THTO | THORNTON | 400
THUR | THURCROFT | 275
THUR | THURCROFT | 66
TILB | TILBURY | 132
TILB | TILBURY | 275
TILB | TILBURY | 400
TINP | TINSLEY PARK | 275
TINP | TINSLEY PARK | 33
TODP | TOD POINT | 275
TODP | TOD POINT | 400
TODP | TOD POINT | 66
TOTE | TOTTENHAM EAST | 275
TOTT | TOTTENHAM | 132
TOTT | TOTTENHAM | 275
TOTW | TOTTENHAM WEST | 275
TRAW | TRAWSFYNYDD | 132
TRAW | TRAWSFYNYDD | 275
TRAW | TRAWSFYNYDD | 400
TREM | TREMORFA | 275
TREM | TREMORFA | 33
TREU | TREUDDYN (PRON. TRITHIN) | 400
TYNE | TYNEMOUTH | 132
TYNE | TYNEMOUTH | 275
UPPB | UPPER BOAT | 132
UPPB | UPPER BOAT | 275
UPPB | UPPER BOAT | 33
USKM | USKMOUTH | 132
USKM | USKMOUTH | 275
WALH | WALHAM | 400
WALP | WALPOLE | 132
WALP | WALPOLE | 400
WALX | WALTHAM CROSS | 275
WALX | WALTHAM CROSS | 400
WARL | WARLEY | 132
WARL | WARLEY | 275
WASF | WASHWAY FARM | 132
WASF | WASHWAY FARM | 275
WATS | WATFORD SOUTH | 132
WATS | WATFORD SOUTH | 275
WBOL | WEST BOLDON | 275
WBOL | WEST BOLDON | 66
WBUR | WEST BURTON | 132
WBUR | WEST BURTON | 400
WEAV | WEAVERHAM - PROSPECTIVE CONNECTION | 400
WHAM | WEST HAM | 132
WHAM | WEST HAM | 275
WHAM | WEST HAM | 400
WHGA | WHITEGATE | 132
WHGA | WHITEGATE | 275
WHSO | WHITSON | 275
WHSO | WHITSON | 33
WHSO | WHITSON | 400
WIBA | WINCOBANK | 275
WIBA | WINCOBANK | 33
WIEN | WILLENHALL | 275
WIEN | WILLENHALL | 132
WIEN | WILLENHALL | 33
WILE | WILLINGTON EAST | 132
WILE | WILLINGTON EAST | 400
WILL | WILLINGTON | 132
WILL | WILLINGTON | 275
WILL | WILLINGTON | 400
WILT | WILTON | 275
WIMB | WIMBLEDON | 132
WIMB | WIMBLEDON | 275
WIMB | WIMBLEDON | 33
WIMB | WIMBLEDON | 400
WISD | WILLESDEN | 132
WISD | WILLESDEN | 275
WISD | WILLESDEN | 400
WISD | WILLESDEN | 66
WMEL | WEST MELTON | 132
WMEL | WEST MELTON | 275
WTHU | WEST THURROCK | 275
WTHU | WEST THURROCK | 33
WTHU | WEST THURROCK | 400
WWEY | WEST WEYBRIDGE | 132
WWEY | WEST WEYBRIDGE | 275
WWEY | WEST WEYBRIDGE | 400
WYLF | WYLFA | 132
WYLF | WYLFA | 400
WYMO | WYMONDLEY | 400

## B-1-1d
Table B.1.1c - OFTO Transmission Index of Substation Codes
Site Code | Site Name
ABBA | ABERDEEN OFFSHORE WIND FARM
BEAT | BEATRICE ONSHORE
BEIW | BEATRICE OFFSHORE
BOSO | BARROW ONSHORE SITE
BOSW | BARROW OFFSHORE WIND FARM
BBWO | BURBO BANK EXTENSION ONSHORE SUBSTATION
BBWW | BURBO BANK EXTENSION OFFSHORE WIND FARM
CLTO | CLACTON
DOGB | DOGGER BANK
DUDW | DUDGEON OFFSHORE WIND FARM
DUDO | DUDGEON ONSHORE SUBSTATION
EANO | EAST ANGLIA ONSHORE
EAAW | EAST ANGLIA OFFSHORE
GANW | GALLOPER NORTH OFFSHORE
GALO | GALLOPER ONSHORE
GGON | GREATER GABBARD ONSHORE SUBSTATION
GREG | GREATER GABBARD OFFSHORE WIND FARM
GUNS | GUNFLEET SANDS
GWAW | GWYNT-Y-MOR OFFSHORE WIND FARM A
GWBW | GWYNT-Y-MOR OFFSHORE WIND FARM B
GWYO | GWYNT-Y-MOR ONSHORE SITE
HONW | HORNSEA
HOWA | HORNSEA P1 220KV ONSHORE SUBSTATION
HOWW | HORNSEA OFFSHORE WIND FARM
HOWR | HORNSEA P1 220KV REACTOR SUBSTATION
HUMO | HUMBER GATEWAY ONSHORE SITE
HUMW | HUMBER GATEWAY OFFSHORE WIND FARM
LINO | LINCS ONSHORE CONNECTION
LINS | LINCS OFFSHORE WIND FARM
LONO | LONDON ARRAY ONSHORE SITE
LONW | LONDON ARRAY OFFSHORE WIND FARM
MOWE | MORAY EAST OFFSHORE SUBSTATION 220KV AND 66KV
MORF | MORAY EAST ONSHORE SUBSTATION 275KV
ORMO | ORMONDE ONSHORE CONNECTION
ORMW | ORMONDE OFFSHORE WIND FARM
RACO | RACE BANK ONSHORE CONNECTION
RACW | RACE BANK OFFSHORE WINDFARM
RAMW | RAMPION
RORE | ROBIN RIGG EAST ONSHORE
RORW | ROBIN RIGG WEST ONSHORE
RREW | ROBIN RIGG EAST OFFSHORE
RRWW | ROBIN RIGG WEST OFFSHORE
SALL | SALL
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2
THAW | THANET WIND ONSHORE SUBSTATION
THOW | THANET WIND OFFSHORE SUBSTATION
TKON | TRITON KNOLL ONSHORE WIND FARM
TKNE | TRITON KNOLL EAST OFFSHORE WIND FARM
TKNW | TRITON KNOLL WEST OFFSHORE WIND FARM
TRIM | TRIMPELL
TWIN | TWINEHAM
WAAO | WALNEY 1 ONSHORE SITE
WAAW | WALNEY 1 OFFSHORE SUBSTATION
WABO | WALNEY 2 ONSHORE SITE
WABW | WALNEY 2 OFFSHORE SUBSTATION
WACW | WALNEY 3 OFFSHORE SUBSTATION
WADW | WALNEY 4 OFFSHORE SUBSTATION
WOWE | WALNEY EXTENSION
WDSO | WEST OF DUDDON SANDS ONSHORE SITE
WDSW | WEST OF DUDDON SANDS OFFSHORE WIND FARM
WERO | WESTERMOST ROUGH ONSHORE
WERW | WESTERMOST ROUGH OFFSHORE

## B-2-1a
Table B.2.1a - SHE Transmission Circuits for 2019/20
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 132 | 123 | 106 | 123
ABNE1R | AMUL1G | 28.0986 | 0.0014 | Composite | 2.87 | 6.58 | 1.4 | 132 | 123 | 106 | 123
AIGA1Q | KIOR1Q | 2.7974 | 0.1226 | Composite | 0.26 | 0.59 | 0.66 | 111 | 103 | 89 | 103
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.2 | 2.55 | 156 | 142 | 142 | 142
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.2 | 2.55 | 156 | 142 | 142 | 142
ALNE3J | COIN3- | 0 | 17.5 | Cable | 12.95 | 16.8 | 1.79 | 38.3 | 34.8 | 34.8 | 34.8
ALNE3J | NOVW32 | 13 | 0 | OHL | 5.93 | 13.25 | 1.42 | 47.9 | 46.9 | 43.4 | 46.9
ALNE3J | NOVW32 | 13 | 0 | OHL | 5.93 | 13.25 | 1.42 | 47.9 | 46.9 | 43.4 | 46.9
ALNE3J | NOVA3- | 8.45 | 0 | OHL | 13.36 | 25.4 | 0.09 | 22.3 | 21.1 | 18 | 21.1
ALNE3J | BETH3- | 13.3 | 0 | OHL | 6.07 | 13.56 | 1.46 | 47.9 | 46.9 | 43.4 | 46.9
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.25 | 0.8 | 10.22 | 153 | 129 | 129 | 129
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7 | 1.61 | 0.34 | 132 | 123 | 106 | 123
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.25 | 0.8 | 10.22 | 153 | 129 | 129 | 129
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7 | 1.61 | 0.34 | 132 | 123 | 106 | 123
ANSU3- | ANSU3W | 0 | 11 | Cable | 2.81 | 5.78 | 0.61 | 39 | 39 | 39 | 39
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.32 | 3.36 | 0.72 | 132 | 123 | 106 | 123
ARBR1R | DENS1R | 14.5 | 0 | OHL | 1.32 | 3.36 | 0.72 | 132 | 123 | 106 | 123
ARDK1- | INVE1J | 9 | 0 | OHL | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123
ARDK1- | SLOY1T | 10 | 0 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123
ARDK3K | ARDK3- | 0.03 | 0 | OHL | 0.05 | 0.1 | 0 | 22.5 | 21 | 18 | 21
ARDR2Q | FYRI2J | 1.8 | 0 | OHL | 0.01 | 0.1 | 0.38 | 702 | 665 | 599 | 665
ARDR2Q | LOCB2K | 34.13 | 0 | OHL | 0.2 | 1.88 | 7.24 | 702 | 665 | 599 | 665
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 83 | 77 | 67 | 77
BEAU1J | BEAU1R | 0 | 2.42 | Cable | 0.09 | 0.22 | 2.87 | 152 | 140 | 140 | 140
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.01 | 0.27 | 141 | 136 | 136 | 136
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 111 | 103 | 89 | 103
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.02 | 0.12 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | BEAU1S | 0 | 2.42 | Cable | 0.09 | 0.22 | 2.87 | 152 | 140 | 140 | 140
BEAU1K | KIOR1Q | 1.2402 | 0.0598 | Composite | 0.13 | 0.29 | 0.06 | 111 | 103 | 89 | 103
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.02 | 0.12 | 10.47 | 444 | 403 | 403 | 403
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.01 | 6.9 | 1.47 | 126 | 117 | 101 | 117
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.01 | 6.9 | 1.47 | 126 | 117 | 101 | 117
BEAU1N | BEAU1K | 0 | 0.25 | Cable | 0.01 | 0.02 | 0.3 | 141 | 136 | 136 | 136
BEAU1N | KNOC1J | 17.1 | 0 | OHL | 1.56 | 3.98 | 0.86 | 132 | 123 | 106 | 123
BEAU1P | BEAU1L | 0 | 1.74 | Cable | 0.06 | 0.16 | 2.06 | 152 | 140 | 140 | 140
BEAU1Q | BEAU1M | 0 | 1.74 | Cable | 0.06 | 0.16 | 2.06 | 152 | 140 | 140 | 140
BEAU1R | INNE1Q | 13.44 | 0 | OHL | 1.37 | 3.13 | 0.66 | 126 | 117 | 101 | 117
BEAU1S | INNE1R | 13.44 | 0 | OHL | 1.37 | 3.13 | 0.66 | 126 | 117 | 101 | 117
BEAU1T | KNOC1J | 17.1 | 0 | OHL | 1.56 | 3.98 | 0.86 | 132 | 123 | 106 | 123
BEAU2J | FASN2- | 24.288 | 1.012 | Composite | 0.07 | 1.03 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.1 | 0.69 | 4.67 | 935 | 880 | 790 | 880
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.18 | 1.68 | 6.46 | 702 | 665 | 599 | 665
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.1 | 0.69 | 4.67 | 935 | 880 | 790 | 880
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.18 | 1.68 | 6.46 | 702 | 665 | 599 | 665
BEAU4- | FAUG4- | 48.6 | 0 | OHL | 0.06 | 0.93 | 29.39 | 2780 | 2670 | 2480 | 2670
BERB3- | BERB3W | 0 | 3 | Cable | 1.37 | 3.06 | 0.33 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | BERB3W | 0 | 3 | Cable | 1.37 | 3.06 | 0.33 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | BERB3W | 0 | 3 | Cable | 1.37 | 3.06 | 0.33 | 47.9 | 43.4 | 43.4 | 43.4
BERB3- | HIGL31 | 1.2 | 0 | OHL | 0.55 | 1.22 | 0.13 | 47.9 | 46.9 | 43.4 | 46.9
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.17 | 5.29 | 1.29 | 203 | 193 | 176 | 193
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.17 | 5.3 | 1.32 | 203 | 193 | 176 | 193
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.04 | 13.79 | 580 | 546 | 546 | 546
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.3 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2J | BERB2Q | 46.26 | 0 | OHL | 0.26 | 1.9 | 12.61 | 935 | 880 | 790 | 880
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.05 | 14.29 | 580 | 546 | 546 | 546
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.19 | 1.36 | 9 | 935 | 880 | 790 | 880
BLHI2L | KINT2J | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2M | PEHERSV1 | 82.72 | 0 | OHL | 0.42 | 3.58 | 21.6 | 1090 | 1030 | 920 | 1030
BOAG1Q | GLFA1- | 33 | 0 | OHL | 3.35 | 7.68 | 1.63 | 126 | 117 | 101 | 117
BOAG1Q | TOMT1K | 23.42 | 0 | OHL | 1.19 | 5.25 | 1.22 | 241 | 230 | 210 | 230
BOAG1R | TOMT1J | 23.42 | 0 | OHL | 1.19 | 5.25 | 1.22 | 241 | 230 | 210 | 230
BOAG3- | TOMN3J | 0 | 22 | Cable | 8.5 | 20.62 | 2.46 | 48.6 | 48.6 | 48.6 | 48.6
BRCW2J | TUMM2K | 62.8 | 0 | OHL | 0.17 | 2.54 | 17.95 | 1910 | 1830 | 1710 | 1830
BRCW2K | BONB2J | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BRCW3- | BRDU3J | 0 | 11 | Cable | 3.65 | 10.47 | 1.24 | 49 | 49 | 49 | 49
BRCW3- | BRDU3K | 0 | 11 | Cable | 3.65 | 10.47 | 1.24 | 49 | 49 | 49 | 49
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BRID3- | TULW39 | 10 | 0 | OHL | 17 | 35 | 0 | 22.5 | 21 | 18 | 21
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 83 | 77 | 67 | 77
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.01 | 9.96 | 2.33 | 83 | 77 | 67 | 77
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.12 | 0.27 | 0.06 | 111 | 103 | 89 | 103
BROR1Q | DUBE1Q | 38.8 | 0 | OHL | 3.94 | 9.01 | 1.91 | 126 | 117 | 101 | 117
BROR1Q | LOCB1K | 22.12 | 0 | OHL | 2.25 | 5.15 | 1.1 | 126 | 117 | 101 | 117
BUMU1Q | CHAR1- | 42.2 | 0 | OHL | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
BUMU1R | AMUL1E | 17.8 | 0 | OHL | 1.82 | 4.17 | 0.88 | 132 | 123 | 106 | 123
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.31 | 2.77 | 0.72 | 448 | 430 | 398 | 430
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.31 | 2.77 | 0.72 | 448 | 430 | 398 | 430
CAAD3J | BTUI3K | 0 | 9 | Cable | 4.21 | 8.68 | 0.92 | 47.9 | 43.4 | 43.4 | 43.4
CAAD3J | BTUI3L | 12 | 0 | OHL | 1.7 | 2.82 | 0.58 | 99 | 92 | 79 | 92
CAIN2- | BLHI2K | 9.77 | 0 | OHL | 0.06 | 0.4 | 2.72 | 935 | 880 | 790 | 880
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.24 | 1.68 | 11.42 | 935 | 880 | 790 | 880
CAIN3J | CLAS3K | 0 | 8 | Cable | 1.47 | 3.93 | 1.92 | 107.4 | 97.6 | 97.6 | 97.6
CASS1Q | LAIR1Q | 28 | 0 | OHL | 2.84 | 6.75 | 1.33 | 111 | 103 | 89 | 103
CEAN1Q | BEIN11 | 0.87 | 0 | OHL | 0.1 | 0.21 | 0.04 | 221 | 216 | 208 | 216
CHAR1- | BIHI1R | 3.9 | 0 | OHL | 0.17 | 0.85 | 0.21 | 229 | 211 | 183 | 211
CHAR1R | BIHI1Q | 3.9 | 0 | OHL | 0.17 | 0.85 | 0.21 | 229 | 211 | 183 | 211
CHAR1S | GLAG1Q | 1.4 | 0.91 | Composite | 0.17 | 0.38 | 1.71 | 126 | 117 | 101 | 117
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 1.4 | 0.91 | Composite | 0.17 | 0.38 | 1.71 | 126 | 117 | 101 | 117
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117
CLAC1Q | SLOY1K | 14.2 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.05 | 0.13 | 2.9 | 155 | 129 | 129 | 129
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.05 | 0.13 | 2.9 | 155 | 129 | 129 | 129
CLAY1S | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1T | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.93 | 8.55 | 1.97 | 241 | 230 | 210 | 230
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.41 | 3.58 | 0.76 | 126 | 117 | 101 | 117
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.93 | 8.55 | 1.97 | 241 | 230 | 210 | 230
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.41 | 3.58 | 0.76 | 126 | 117 | 101 | 117
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7 | 2.88 | 0.78 | 203 | 193 | 176 | 193
CONN1C | STRW1C | 12 | 0 | OHL | 0.6 | 2.48 | 0.67 | 203 | 193 | 176 | 193
CONN1J | CONN1C | 0 | 0.76 | Cable | 0.02 | 0.06 | 1.04 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 76.0713 | 0.2687 | Composite | 0.46 | 4.2 | 16.18 | 702 | 665 | 599 | 665
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.02 | 0.07 | 0.84 | 126 | 116 | 116 | 116
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.24 | 2.27 | 0.55 | 464 | 446 | 414 | 446
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.02 | 0.06 | 0.74 | 126 | 116 | 116 | 116
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.24 | 2.26 | 0.55 | 464 | 446 | 414 | 446
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.07 | 0.32 | 0.08 | 224 | 211 | 189 | 211
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.07 | 0.32 | 0.08 | 224 | 211 | 189 | 211
CORI3- | LLUC3- | 0 | 2.6 | Cable | 0.48 | 1.28 | 0.62 | 107 | 98 | 98 | 98
CORI3K | CORI3J | 0 | 1 | Cable | 0.47 | 0.5 | 0.19 | 67.2 | 65.8 | 61 | 65.8
COUA1Q | BIHI1Q | 14.6 | 0 | OHL | 0.74 | 3.27 | 0.75 | 241 | 230 | 210 | 230
COUA1R | BIHI1R | 14.6 | 0 | OHL | 0.74 | 3.27 | 0.75 | 241 | 230 | 210 | 230
COUA3- | COUA38 | 24.3 | 0 | OHL | 35.99 | 76.71 | 0 | 22.3 | 21.1 | 18 | 21.1
COUA3- | COUA39 | 17.39 | 0 | OHL | 23.92 | 52.79 | 0.01 | 22.3 | 21.1 | 18 | 21.1
COUA3- | TLYM3- | 0 | 19 | Cable | 17.48 | 16.34 | 3.04 | 28.3 | 28.3 | 28.3 | 28.3
COUW31 | COUW32 | 0 | 4 | Cable | 4.78 | 4.15 | 0.34 | 29.4 | 26.7 | 26.7 | 26.7
COUW31 | FRSD3- | 9 | 0 | OHL | 4.1 | 9.17 | 0.99 | 47.9 | 46.9 | 43.4 | 46.9
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.03 | 0.1 | 1.46 | 149 | 137 | 137 | 137
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.03 | 0.1 | 1.46 | 149 | 137 | 137 | 137
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.48 | 1.06 | 0.22 | 132 | 123 | 106 | 123
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.48 | 1.06 | 0.22 | 132 | 123 | 106 | 123
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.89 | 3.92 | 0.9 | 241 | 230 | 210 | 230
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.89 | 3.92 | 0.9 | 241 | 230 | 210 | 230
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.02 | 0.05 | 4.45 | 240 | 240 | 240 | 240
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.02 | 0.06 | 4.57 | 240 | 240 | 240 | 240
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.34 | 1.91 | 0.46 | 183 | 160 | 149 | 160
DENS1R | TEAL1- | 8.7 | 0 | OHL | 0.34 | 1.91 | 0.46 | 183 | 160 | 149 | 160
DOUN2- | THUS2J | 15.4 | 0 | OHL | 0.08 | 0.85 | 3.28 | 965 | 925 | 865 | 925
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.08 | 0.85 | 3.28 | 965 | 925 | 865 | 925
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.46 | 3.17 | 12.27 | 535 | 490 | 430 | 490
DOUN2- | CONN2J | 10.34 | 0 | OHL | 0.06 | 0.57 | 2.19 | 702 | 665 | 599 | 665
DUBE1Q | MYBS1R | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 117 | 101 | 117
DUDH1Q | GLAG1Q | 0 | 1.95 | Cable | 0.06 | 0.12 | 2.91 | 160 | 145 | 145 | 145
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.26 | 0.44 | 5.3 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 0 | 1.95 | Cable | 0.06 | 0.12 | 2.91 | 160 | 145 | 145 | 145
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.26 | 0.44 | 5.3 | 131 | 113 | 113 | 113
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.21 | 2 | 0.47 | 83 | 77 | 67 | 77
DUGR3- | BENA3- | 5 | 0 | OHL | 5.3 | 14.55 | 0 | 34.3 | 32.3 | 29.2 | 32.3
DUNM1- | DUNM1C | 6 | 0 | OHL | 0.3 | 1.24 | 0.34 | 203 | 193 | 176 | 193
DYCE1J | ABBA1- | 0 | 7.8 | Cable | 0.11 | 1.23 | 10.14 | 173 | 158 | 158 | 158
DYCE1Q | DYCE1J | 1.93 | 0 | OHL | 0.1 | 0.43 | 0.33 | 241 | 230 | 210 | 230
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.05 | 0.05 | 2.43 | 150 | 143 | 143 | 143
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.05 | 0.05 | 2.43 | 150 | 143 | 143 | 143
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.52 | 2.28 | 0.52 | 241 | 230 | 210 | 230
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.63 | 2.3 | 0.52 | 145 | 131 | 116 | 131
ELGI1L | NAIR1Q | 32.9 | 0 | OHL | 3.35 | 7.64 | 1.63 | 126 | 117 | 101 | 117
ELGI1M | NAIR1R | 32.9 | 0 | OHL | 3.35 | 7.64 | 1.63 | 126 | 117 | 101 | 117
ELGI1Q | ELGI1L | 0 | 1.89 | Cable | 0.04 | 0.05 | 1.48 | 150 | 130 | 130 | 130
ELGI1Q | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1R | ELGI1M | 0 | 1.89 | Cable | 0.04 | 0.05 | 1.48 | 150 | 130 | 130 | 130
ELGI1R | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.01 | 0.1 | 2.57 | 300 | 280 | 280 | 280
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.01 | 0.09 | 2.51 | 300 | 280 | 280 | 280
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123
FAAR1Q | TOMT1K | 7.2 | 0 | OHL | 0.65 | 1.66 | 0.36 | 132 | 123 | 106 | 123
FAAR1R | TOMT1J | 7.2 | 0 | OHL | 0.65 | 1.66 | 0.36 | 132 | 123 | 106 | 123
FARI1J | COGA1C | 0 | 4.11 | Cable | 0.07 | 0.33 | 6.24 | 176 | 176 | 176 | 176
FARI1K | DUNM1C | 0 | 4.07 | Cable | 0.06 | 0.28 | 6.17 | 210 | 196 | 196 | 196
FASN2- | FAUG2J | 24.384 | 1.016 | Composite | 0.07 | 1.03 | 7.26 | 1910 | 1830 | 1710 | 1830
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127
FAUG1- | FAUG1M | 0 | 0.29 | Cable | 0.01 | 0.02 | 0.49 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 0 | 0.2 | Cable | 0.01 | 0.02 | 0.34 | 220 | 209 | 209 | 209
FAUG1- | FAUG1P | 0 | 0.59 | Cable | 0.01 | 0.06 | 0.87 | 202 | 202 | 202 | 202
FAUG1- | LAGG1Q | 6.49 | 0 | OHL | 0.74 | 1.48 | 0.33 | 221 | 216 | 208 | 216
FAUG1- | LAGG1R | 6.49 | 0 | OHL | 0.74 | 1.48 | 0.33 | 221 | 216 | 208 | 216
FAUG1M | LOCL1Q | 8.5 | 0 | OHL | 0.97 | 1.93 | 0.43 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 8.5 | 0 | OHL | 0.97 | 1.93 | 0.43 | 255 | 247 | 237 | 247
FAUG1P | LOCL1S | 8.66 | 0 | OHL | 0.44 | 1.79 | 0.49 | 203 | 193 | 176 | 193
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.21 | 3.13 | 22.06 | 1910 | 1830 | 1710 | 1830
FAUG4- | MELG4J | 24.01 | 0 | OHL | 0.03 | 0.46 | 14.52 | 2780 | 2670 | 2480 | 2670
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.71 | 1.07 | 0.26 | 83 | 77 | 67 | 77
FETT2Q | KINB2J | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT3S | MIHW3- | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 48.6 | 48.6 | 48.6 | 48.6
FETT3S | MIHW3- | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 48.6 | 48.6 | 48.6 | 48.6
FIDD1Q | FOGG1R | 25.4 | 0 | OHL | 3 | 6.16 | 1.24 | 112 | 104 | 90 | 104
FIDD3- | TULW3- | 15 | 0 | OHL | 11.1 | 14.4 | 1.53 | 38.3 | 38.1 | 34.8 | 38.1
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 111 | 103 | 89 | 103
FOYE2- | FARI2J | 8.4 | 0 | OHL | 0.05 | 0.34 | 2.36 | 935 | 880 | 790 | 880
FOYE2- | FARI2K | 8.4 | 0 | OHL | 0.05 | 0.34 | 2.36 | 935 | 880 | 790 | 880
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.5 | 133 | 124 | 107 | 124
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.5 | 126 | 117 | 101 | 117
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.98 | 7.92 | 1.74 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.98 | 7.92 | 1.74 | 255 | 247 | 237 | 247
FWIL3- | LHBR3- | 0 | 1.3 | Cable | 0.51 | 1.25 | 0.15 | 53.7 | 48.6 | 48.6 | 48.6
FWIL3- | LHBR3- | 0 | 1.3 | Cable | 0.51 | 1.25 | 0.15 | 53.7 | 48.6 | 48.6 | 48.6
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.22 | 1.98 | 7.62 | 702 | 665 | 599 | 665
GLDO8- | GLDO8J | 0 | 1.2 | Cable | 0.39 | 1.02 | 0.01 | 131 | 131 | 131 | 131
GLEN1Q | BHLA11 | 0 | 7.8 | Cable | 0.14 | 0.61 | 28.36 | 208 | 187 | 187 | 187
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.55 | 1.13 | 0.23 | 221 | 216 | 208 | 216
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.08 | 0.56 | 2.17 | 535 | 490 | 430 | 490
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.14 | 0.61 | 0.14 | 224 | 211 | 189 | 211
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.14 | 0.61 | 0.14 | 224 | 211 | 189 | 211
HYWD30 | HYWD31 | 0 | 1.5 | Cable | 0.58 | 1.41 | 0.17 | 40.6 | 40.6 | 40.6 | 40.6
HYWD31 | HYWD32 | 0 | 26 | Cable | 19.11 | 26.26 | 2.31 | 32.6 | 32.6 | 32.6 | 32.6
INGA1Q | LOCL1Q | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.11 | 0.38 | 6.33 | 171 | 165 | 165 | 165
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1 | 0.38 | 6.27 | 171 | 165 | 165 | 165
INNE1Q | NAIR1Q | 29.3 | 0 | OHL | 2.86 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1T | NAIR1R | 29.3 | 0 | OHL | 2.86 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE3- | MOYW3- | 17.5 | 0 | OHL | 3.99 | 8.9 | 3.83 | 95.8 | 93.8 | 86.8 | 93.8
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 142 | 128 | 142
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.09 | 0.4 | 0.09 | 241 | 230 | 210 | 230
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.31 | 1.37 | 0.32 | 241 | 230 | 210 | 230
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 117 | 101 | 117
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.09 | 0.4 | 0.09 | 241 | 230 | 210 | 230
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.31 | 1.37 | 0.32 | 241 | 230 | 210 | 230
INRU1S | PEHE1- | 0 | 3 | Cable | 0.07 | 0.25 | 4.1 | 186 | 186 | 186 | 186
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.38 | 0.62 | 195 | 181 | 157 | 181
INVE1J | ACHR1R | 21.17 | 0 | OHL | 3 | 4.98 | 1.04 | 99 | 92 | 79 | 92
INVE1J | FERO1S | 15.21 | 0 | OHL | 2.16 | 3.57 | 0.74 | 99 | 92 | 79 | 92
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
INVE1K | SLOY1J | 22.6 | 0 | OHL | 2.29 | 5.25 | 1.11 | 126 | 117 | 101 | 117
INVE1K | ANSU1- | 11.13 | 0 | OHL | 1.58 | 2.61 | 0.54 | 99 | 92 | 79 | 92
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.36 | 0.29 | 132 | 126 | 106 | 126
KEIT1- | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | GLFA1- | 29.6 | 0 | OHL | 3.01 | 6.9 | 1.47 | 126 | 117 | 101 | 117
KEIT3- | KEIT39 | 18.6 | 0 | OHL | 47.61 | 52.76 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
KEIT3- | GLOF3J | 25.5 | 0 | OHL | 62.75 | 83.85 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KEIT3- | EDNT3- | 0 | 4.55 | Cable | 5.43 | 4.72 | 0.39 | 29.4 | 26.7 | 26.7 | 26.7
KEIT3A | HITO3- | 9 | 0 | OHL | 0.73 | 0.97 | 0.11 | 38.3 | 37.5 | 34.8 | 37.5
KEIT3A | HITO3- | 9 | 0 | OHL | 0.73 | 0.97 | 0.11 | 38.3 | 37.5 | 34.8 | 37.5
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 111 | 103 | 89 | 103
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
KIIN1- | INVR1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 83 | 77 | 67 | 77
KILC1Q | TAYN1Q | 7.52 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILO3- | KILO3Q | 0 | 1 | Cable | 0.8 | 3.24 | 0.01 | 43 | 41 | 38 | 41
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.02 | 0.35 | 148 | 140 | 140 | 140
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.01 | 0.34 | 148 | 140 | 140 | 140
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.01 | 0.03 | 0.79 | 165 | 141 | 141 | 141
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.01 | 0.03 | 0.79 | 165 | 141 | 141 | 141
KINT1- | FOGG1Q | 15.6 | 0 | OHL | 1.83 | 3.74 | 0.75 | 112 | 104 | 90 | 104
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030
KINT2J | TEAL2J | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
KINB2K | TEAL2J | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
KINT2K | PEHE2Q | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KINT2K | TEAL2K | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
KINT2K | FETT2P | 32.15 | 0 | OHL | 0.16 | 1.4 | 8.45 | 955 | 880 | 760 | 880
KINT2K | FETT2Q | 32.15 | 0 | OHL | 0.16 | 1.4 | 8.45 | 955 | 885 | 760 | 885
KINT3- | GOHI3- | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
KINT3- | GLOF3K | 33.7 | 0 | OHL | 82.93 | 115.3 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.04 | 8.36 | 930 | 900 | 900 | 900
KNOC2J | BERB2Q | 46.98 | 0 | OHL | 0.27 | 1.93 | 12.81 | 935 | 880 | 790 | 880
KNOC2J | FARI2J | 14.9 | 0 | OHL | 0.09 | 0.6 | 4.18 | 935 | 880 | 790 | 880
KNOC2J | TOMT2K | 18.46 | 0 | OHL | 0.09 | 1.02 | 3.93 | 810 | 765 | 685 | 765
KNOC2K | DAAS2- | 60.22 | 0 | OHL | 0.34 | 2.48 | 16.42 | 935 | 880 | 790 | 880
KNOC2K | FARI2K | 14.9 | 0 | OHL | 0.09 | 0.6 | 4.18 | 935 | 880 | 790 | 880
KNOC2K | TOMT2J | 18.46 | 0 | OHL | 0.09 | 1.02 | 3.93 | 810 | 765 | 685 | 765
KNOC2M | KNOC2K | 0 | 1.29 | Cable | 0.01 | 0.04 | 7.34 | 930 | 900 | 900 | 900
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.65 | 1.34 | 0.28 | 221 | 216 | 208 | 216
LAIR1Q | SHIN1- | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 111 | 103 | 89 | 103
LAIR3- | LAIR3W | 0 | 10 | Cable | 4.56 | 10.19 | 1.1 | 40 | 40 | 40 | 40
LAIR3- | LAIR3W | 0 | 10 | Cable | 4.56 | 10.19 | 1.1 | 40 | 40 | 40 | 40
LOCL1S | QUOI1Q | 18.3 | 0 | OHL | 1.91 | 4.54 | 0.9 | 111 | 103 | 89 | 103
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.13 | 1.18 | 0.29 | 464 | 446 | 414 | 446
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.13 | 1.21 | 0.29 | 464 | 446 | 414 | 446
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.39 | 133 | 124 | 107 | 124
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.39 | 133 | 124 | 107 | 124
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUND1- | FWIL1R | 9.3 | 0 | OHL | 0.85 | 2.16 | 0.46 | 136 | 129 | 118 | 129
LUND1- | KILO1- | 15.2 | 0 | OHL | 1.05 | 3.44 | 0.77 | 111 | 103 | 89 | 103
MACD3- | BOYN3Q | 8 | 0 | OHL | 5.95 | 7.71 | 0.82 | 38.3 | 37.5 | 34.8 | 37.5
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILW1S | BEIN11 | 2.8 | 0 | OHL | 0.32 | 0.66 | 0.14 | 221 | 216 | 208 | 216
MILW1S | MILW1Q | 1.3 | 0 | OHL | 0.07 | 0.27 | 0.07 | 203 | 193 | 176 | 193
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.02 | 0.05 | 0.01 | 132 | 123 | 106 | 123
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.02 | 0.05 | 0.01 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MYBS1Q | LOCB1J | 81.61 | 0 | OHL | 8.3 | 19 | 4.03 | 126 | 117 | 101 | 117
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.36 | 0.93 | 0.2 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.36 | 0.93 | 0.2 | 126 | 117 | 101 | 117
MYBS1S | SPIT1M | 4.5 | 0 | OHL | 0.1 | 1 | 0.24 | 463 | 444 | 415 | 444
MYBS1T | SPIT1K | 4.5 | 0 | OHL | 0.1 | 1 | 0.24 | 463 | 444 | 415 | 444
MYBS3J | BUWH3- | 20 | 0 | OHL | 2.39 | 20.7 | 1.7 | 32.6 | 28.8 | 26.7 | 28.8
MYBS3J | WATH3- | 0 | 5 | Cable | 5.88 | 5.6 | 0.4 | 26.3 | 26.3 | 26.3 | 26.3
MYBS3J | ACHL3- | 0 | 2 | Cable | 2.39 | 2.07 | 0.17 | 29.4 | 26.7 | 26.7 | 26.7
MYBS3K | CAMW3W | 12 | 0 | OHL | 3.24 | 5.52 | 2.64 | 75.7 | 66.9 | 62.1 | 66.9
MYBS3N | BADA3- | 0 | 5 | Cable | 2.28 | 5.09 | 0.55 | 47.9 | 43.4 | 43.4 | 43.4
ORRI1S | DUCC1J | 10.76 | 0 | OHL | 0.25 | 2.35 | 0.57 | 464 | 446 | 414 | 446
ORRI1T | DUCC1K | 10.76 | 0 | OHL | 0.25 | 2.35 | 0.57 | 464 | 446 | 414 | 446
ORRI3- | FAWI3W | 3.5 | 0 | OHL | 1.28 | 3.44 | 0.69 | 59.5 | 52.7 | 48.8 | 52.7
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE2U | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.02 | 5.25 | 313 | 313 | 313 | 313
PEHE2V | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.02 | 5.25 | 313 | 313 | 313 | 313
PEHE2W | PEHEMEC1 | 0 | 1 | Cable | 0.01 | 0.02 | 5.25 | 313 | 313 | 313 | 313
PEHG3- | HYWD30 | 0 | 0.5 | Cable | 0.19 | 0.47 | 0.06 | 40.6 | 40.6 | 40.6 | 40.6
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.08 | 0.22 | 5.1 | 155 | 129 | 129 | 129
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.08 | 0.22 | 5.1 | 155 | 129 | 129 | 129
PORA1Q | ANSU1- | 24.27 | 0 | OHL | 3.44 | 5.71 | 1.19 | 99 | 92 | 79 | 92
PORA1Q | CRSS1Q | 48.3 | 0 | OHL | 6.84 | 11.36 | 2.35 | 99 | 92 | 79 | 92
PORA1R | ACHR1R | 14.23 | 0 | OHL | 2.02 | 3.34 | 0.69 | 99 | 92 | 79 | 92
PORA1R | CRSS1R | 48.3 | 0 | OHL | 6.84 | 11.36 | 2.35 | 99 | 92 | 79 | 92
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 126 | 119 | 108 | 119
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
REDM3- | KINW3 | 24 | 0 | OHL | 17.52 | 23.28 | 4.8 | 38.4 | 37.5 | 34.6 | 37.5
REDM3- | KINW3 | 24 | 0 | OHL | 17.52 | 23.28 | 4.8 | 38.4 | 37.5 | 34.6 | 37.5
SFEG1Q | SFEG1S | 0 | 0.4 | Cable | 0.01 | 0.03 | 0.46 | 160 | 135 | 135 | 135
SFEG1R | SFEG1T | 0 | 0.4 | Cable | 0.01 | 0.03 | 0.46 | 160 | 135 | 135 | 135
SFER1L | SFEM1Q | 1.9 | 1.1 | Composite | 0.38 | 0.56 | 1.87 | 132 | 122 | 106 | 122
SFER1L | SFEG1Q | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 117 | 101 | 117
SFER1M | SFEM1R | 1.9 | 1.1 | Composite | 0.38 | 0.56 | 1.87 | 132 | 122 | 106 | 122
SFER1M | SFEG1R | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 126 | 117 | 101 | 117
SHIN1- | LOCB1J | 12.19 | 0 | OHL | 1.24 | 2.84 | 0.6 | 126 | 117 | 101 | 117
SHIN1- | LOCB1K | 12.18 | 0 | OHL | 1.24 | 2.84 | 0.6 | 126 | 117 | 101 | 117
SHIN3- | ROSE3- | 9.5 | 0 | OHL | 8.93 | 9.5 | 0.86 | 33.6 | 32 | 30.5 | 32
SLOY1J | SLOY1N | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 111 | 103 | 89 | 103
SLOY1J | SLOY1P | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 111 | 103 | 89 | 103
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.55 | 1.25 | 0.27 | 132 | 123 | 106 | 123
SLOY1K | SLOY1L | 1.2896 | 0.0104 | Composite | 0.13 | 0.3 | 0.06 | 111 | 103 | 89 | 103
SLOY1K | SLOY1M | 1.2896 | 0.0104 | Composite | 0.13 | 0.3 | 0.06 | 111 | 103 | 89 | 103
SLOY1K | INVR1- | 11.22 | 0 | OHL | 1.14 | 2.61 | 0.55 | 132 | 126 | 106 | 126
SLOY1J | GARB1R | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
SLOY1J | GARB1S | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
SLOY1K | GARB1Q | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
SLOY1K | GARB1T | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
STRB2- | LOCB2K | 18.9 | 0 | OHL | 0.15 | 1.03 | 3.99 | 535 | 490 | 430 | 490
STRL1- | MELG1J | 0 | 10 | Cable | 0.06 | 0.8 | 18.01 | 317 | 281 | 281 | 281
STRW12 | STRW1C | 0 | 0.35 | Cable | 0.01 | 0.06 | 0.48 | 200 | 178 | 178 | 178
TARL1Q | FOGG1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
TARL1R | FOGG1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
TARL3- | TARL3J | 9.8 | 0 | OHL | 15.17 | 32.24 | 0 | 26.5 | 24.7 | 21.3 | 24.7
TARL3J | TARL3K | 15.3 | 0 | OHL | 25.25 | 50.8 | 0 | 25.2 | 23.9 | 21.6 | 23.9
TAYN1R | FERO1S | 7.49 | 0 | OHL | 1.06 | 1.76 | 0.37 | 99 | 92 | 79 | 92
TEAL1- | BIHI1Q | 5.6 | 0 | OHL | 0.24 | 1.2 | 0.29 | 229 | 211 | 183 | 211
TEAL1- | BIHI1R | 5.6 | 0 | OHL | 0.24 | 1.2 | 0.29 | 229 | 211 | 183 | 211
TEAL2J | WFIB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2K | FETT2P | 83.55 | 0 | OHL | 0.42 | 3.65 | 21.99 | 955 | 880 | 760 | 880
TEAL2K | GLRB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
THUS2J | SPIT2J | 12.1 | 0 | OHL | 0.06 | 0.67 | 2.58 | 965 | 925 | 865 | 925
THUS2K | SPIT2K | 12.1 | 0 | OHL | 0.06 | 0.67 | 2.58 | 965 | 925 | 865 | 925
THUS3- | STRS30 | 0 | 27 | Cable | 12.32 | 27.52 | 2.96 | 47.9 | 43.4 | 43.4 | 43.4
TUMM4- | BONB4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670
TUMM4- | MELG4J | 53.19 | 0 | OHL | 0.07 | 1.02 | 32.16 | 2780 | 2670 | 2480 | 2670
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.09 | 0.28 | 3.44 | 153 | 140 | 140 | 140
WHIB1A | ERRO1J | 4.87 | 0 | OHL | 0.5 | 1.14 | 0.24 | 132 | 123 | 106 | 123
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.09 | 0.28 | 3.44 | 153 | 140 | 140 | 140
WHIB1B | ERRO1K | 4.87 | 0 | OHL | 0.5 | 1.14 | 0.24 | 132 | 123 | 106 | 123
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.36 | 0.84 | 0.18 | 132 | 123 | 106 | 123
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.36 | 0.84 | 0.18 | 132 | 123 | 106 | 123
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.01 | 0.04 | 0.52 | 153 | 140 | 140 | 140
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.01 | 0.04 | 0.52 | 153 | 140 | 140 | 140
WHIB1G | GRIF1T | 14.17 | 0 | OHL | 1.45 | 3.32 | 0.7 | 132 | 123 | 106 | 123
WHIB1H | GRIF1S | 14.17 | 0 | OHL | 1.45 | 3.32 | 0.7 | 132 | 123 | 106 | 123
WHTB1S | DUNO1Q | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
WHTB1T | DUNO1R | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.08 | 0.29 | 3.91 | 174 | 147 | 147 | 147
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.08 | 0.29 | 3.91 | 174 | 147 | 147 | 147

## B-2-1b
Table B.2.1b - SPT Transmission Circuits ETYS Yr1 - 2019/20
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0422 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0422 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.716 | 3.8726 | 0.9882 | 171 | 152 | 152 | 152
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.72 | 3.8943 | 0.9935 | 171 | 152 | 152 | 152
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.9576 | 4.8683 | 1.5223 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.9569 | 4.8645 | 1.4665 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430
BLAH1- | GLGL1Q | 12.6 | 0.44 | Composite | 0.4848 | 2.7278 | 1.2134 | 134 | 123 | 123 | 123
BLAH1- | GLGL1R | 12.6 | 0.435 | Composite | 0.485 | 2.7281 | 1.2195 | 134 | 123 | 123 | 123
BLCW1- | MARG1- | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 166 | 159 | 147 | 159
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2976 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4261 | 2.3082 | 0.5872 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4261 | 2.3082 | 0.5872 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 8.08 | 0.3 | parallel Composite | 0.1876 | 0.4239 | 1.241 | 240 | 234 | 202 | 234
BONN1- | STIR1S | 3.3 | 12.2 | Composite | 0.2518 | 1.5349 | 21.8297 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 3.3 | 12.2 | Composite | 0.2518 | 1.5349 | 21.8297 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BPGR3- | BPGR3R | 0 | 0 | Series Reactor | 0 | 25 | 0 | 96 | 96 | 96 | 96
BPGR3- | BPGR3R | 0 | 0 | Series Reactor | 0 | 25 | 0 | 96 | 96 | 96 | 96
BRAE1G | BRAP1- | 0 | 2.1 | Cable | 0.0418 | 0.1748 | 3.0232 | 250 | 250 | 250 | 250
BRAE1G | GOVA1R | 0 | 4.03 | Cable | 0.175 | 0.2752 | 7.984 | 125 | 113 | 110 | 113
BRAE1P | GOVA1Q | 0 | 4.03 | Cable | 0.175 | 0.2752 | 7.984 | 125 | 113 | 110 | 113
BRAE1P | PAIS1Q | 4.52 | 0 | OHL | 0.0885 | 0.8142 | 0.2833 | 268 | 268 | 268 | 268
BRAP1- | ERSK1Q | 3.17 | 6.23 | Composite | 0.4457 | 1.0567 | 12.451 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4932 | 1.1319 | 12.97 | 102 | 79 | 79 | 79
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.7936 | 2.3392 | 0.5257 | 132 | 123 | 106 | 123
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.7936 | 2.3392 | 0.5257 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 750 | 690 | 630 | 690
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.2337 | 0.5239 | 0.1455 | 132 | 123 | 106 | 123
CAFA5- | CAFA5R | 0 | 0 | Series Reactor | 0.33333 | 21.1544 | 0 | 30 | 30 | 30 | 30
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CHAP1- | DUMF1- | 26.9 | 0.17 | Composite | 1.0626 | 6.0703 | 1.3831 | 171 | 155 | 155 | 155
CHAP1- | DUMF1- | 26.9 | 0 | OHL | 1.0663 | 6.0851 | 1.9201 | 171 | 155 | 155 | 155
CHAP1- | ECCF1J | 6.569 | 0.181 | Composite | 0.5993 | 1.4912 | 0.9041 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.126 | Composite | 0.5981 | 1.4864 | 0.7304 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.1721 | 2.9186 | 1.0133 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 1.1707 | 2.9133 | 0.9613 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.018976 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 9.17 | 0 | OHL | 0.0207 | 0.3232 | 2.9288 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.22 | 0 | OHL | 0.1223 | 1.9018 | 17.3649 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.058 | 0.079 | 24.356 | 291 | 245 | 245 | 245
COAL1- | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180
COAL1- | LINM1R | 5.774 | 3.2 | Composite | 0.244 | 1.516 | 3.055 | 134 | 123 | 123 | 123
COAL1- | MIDM1- | 0 | 14.47 | Cable | 0.4086 | 0.9392 | 17.8217 | 158 | 146 | 146 | 146
COAL1A | GAWH1Q | 0 | 10.5 | Cable | 0.1651 | 0.9039 | 17.3003 | 241 | 241 | 241 | 241
COAL1A | LINM1Q | 5.774 | 3.14 | Composite | 0.246 | 1.521 | 3.108 | 134 | 123 | 123 | 123
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0824 | 0.7441 | 5.0794 | 1090 | 1030 | 925 | 1030
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0429 | 0.3869 | 2.6411 | 1090 | 1030 | 925 | 1030
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.1404 | 1.3254 | 37.0306 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.1404 | 1.3252 | 37.0251 | 1090 | 1030 | 925 | 1030
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.402 | 0.9996 | 0.5105 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8416 | 2.1448 | 1.0636 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.285 | 0.08 | Composite | 0.0057 | 0.0513 | 0.463 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.36 | 0 | OHL | 0.006 | 0.0538 | 0.389 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.607 | 3.9558 | 1.2029 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 14.135 | 0 | OHL | 0.0622 | 0.5572 | 4.0537 | 1200 | 1120 | 1020 | 1120
COYW2T | KILS2- | 14.135 | 0 | OHL | 0.0622 | 0.5572 | 4.0537 | 1200 | 1120 | 1020 | 1120
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4941 | 2.6834 | 0.984 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.4943 | 2.6844 | 0.9979 | 229 | 211 | 183 | 211
CRUA2Q | CRUA2S | 0 | 0.4 | Cable | 0.0001 | 0.0103 | 2.0513 | 283 | 283 | 283 | 283
CRUA2R | CRUA2T | 0 | 0.4 | Cable | 0.0001 | 0.0103 | 2.0513 | 283 | 283 | 283 | 283
CRUA2S | DALL2- | 8.16 | 0 | OHL | 0.0345 | 0.3333 | 2.2691 | 570 | 570 | 570 | 570
CRUA2T | DALL2- | 8.16 | 0 | OHL | 0.0345 | 0.3333 | 2.2691 | 570 | 570 | 570 | 570
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0178 | 0.2543 | 8.5869 | 2473 | 2349 | 2148 | 2349
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.014 | 0.2043 | 44.411 | 935 | 785 | 785 | 785
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.2628 | 0.9459 | 5.1157 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2621 | 0.9437 | 5.0983 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.18 | 0 | OHL | 0.1901 | 1.716 | 11.714 | 1090 | 1030 | 920 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0421 | 0.3804 | 2.5966 | 1090 | 1030 | 925 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0421 | 0.3804 | 2.5966 | 1090 | 1030 | 925 | 1030
CURR2- | KINC2- | 55.82 | 0 | OHL | 0.2516 | 2.2709 | 15.502 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0172 | 0.0996 | 6.0533 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0171 | 0.099 | 5.954 | 120 | 120 | 120 | 120
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 957 | 881 | 762 | 881
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 123 | 106 | 123
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.6915 | 1.7146 | 0.386 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.6806 | 1.6869 | 0.38 | 107 | 107 | 101 | 107
DEVM4- | HUNE4- | 50.471 | 0.167 | Composite | 0.0893 | 0.9392 | 34.236 | 1316 | 1067 | 1067 | 1067
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.0464 | 0.5238 | 18.2287 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1T | 5.8 | 5.4 | Composite | 0.3125 | 1.7559 | 7.112 | 162 | 154 | 141 | 154
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8813 | 7.1564 | 1.6058 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUMF3A | DUMF3B | 0 | 0 | Series Reactor | 0.6855 | 36.7936 | 0 | 45 | 45 | 45 | 45
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8266 | 1.944 | 7.8096 | 102 | 91 | 91 | 91
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8266 | 1.944 | 7.8096 | 102 | 91 | 91 | 91
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 152 | 122 | 122 | 122
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.6909 | 1.7093 | 0.5595 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.6909 | 1.7093 | 0.5595 | 132 | 122 | 106 | 122
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.1531 | 0.3432 | 0.0953 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.8465 | 7.3431 | 1.534 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8128 | 7.1065 | 1.5419 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.0444 | 0.6414 | 67.8893 | 2330 | 1840 | 1840 | 1840
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.0444 | 0.6414 | 67.8893 | 2330 | 1840 | 1840 | 1840
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 46.23 | 0 | OHL | 0.1043 | 1.6221 | 14.8036 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 2.55 | 0.24 | Composite | 0.12 | 0.559 | 0.684 | 229 | 211 | 183 | 211
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1517 | 0.8271 | 0.4569 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 2.55 | 0.24 | Composite | 0.121 | 0.561 | 0.73 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1523 | 0.8319 | 0.5267 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1147 | 1.2422 | 39.2362 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0411 | 0.4453 | 14.0699 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
ESST1R | KIER1R | 0 | 4.56 | Cable | 0.133 | 0.19 | 8.531 | 100 | 80 | 60 | 80
ESST1R | WIYH1- | 2.089 | 1.376 | Composite | 0.2353 | 0.6228 | 2.5767 | 233 | 200 | 200 | 200
EWEH1Q | GRNA1- | 15.7 | 0.12 | Composite | 1.1828 | 3.4623 | 0.9844 | 131 | 131 | 131 | 131
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0399 | 0.5705 | 19.2679 | 2473 | 2349 | 2148 | 2349
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1- | 15.3129 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123
GARB1R | STLE1- | 26.9091 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.0304 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.0609 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.0819 | 0.3304 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.7398 | 0.1623 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105
GIFF3A | GIFF3B | 0 | 0 | Series Reactor | 0.6855 | 108.4978 | 0 | 30 | 30 | 30 | 30
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.6963 | 1.6715 | 0.4063 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7223 | 6.7475 | 1.5202 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7223 | 6.7475 | 1.5202 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 1.9937 | 4.9416 | 1.1133 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 1.9937 | 4.9416 | 1.1133 | 49 | 49 | 49 | 49
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 171 | 171 | 171 | 171
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 130 | 125 | 110 | 125
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 156 | 145 | 156
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.359 | 0.7999 | 0.7252 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0662 | 0.6092 | 3.9929 | 875 | 875 | 760 | 875
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0545 | 0.5013 | 3.2857 | 955 | 885 | 760 | 885
GLRO3A | GLRO3B | 0 | 0 | Series Reactor | 0.6855 | 108.4978 | 0 | 30 | 30 | 30 | 30
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.0675 | 0.6108 | 4.1461 | 1050 | 965 | 880 | 965
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 5.0163 | 12.4825 | 2.7907 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.4295 | 1.0647 | 0.2399 | 132 | 123 | 106 | 123
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0034 | 0.0373 | 1.1795 | 2210 | 2130 | 1980 | 2130
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0766 | 0.8299 | 26.2179 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.304 | 1.375 | 21.563 | 184 | 184 | 184 | 184
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 4.5622 | 11.3553 | 2.5375 | 132 | 123 | 106 | 123
HELE1- | WIYH1- | 24.7994 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1448 | 1448 | 1448 | 1448
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1448 | 1448 | 1448 | 1448
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | KILS4- | 59.125 | 0 | OHL | 0.0834 | 1.043 | 37.9987 | 2030 | 1930 | 1770 | 1930
HUER4- | KILS4T | 59.125 | 0 | OHL | 0.0834 | 1.043 | 37.9987 | 2037 | 1940 | 1760 | 1940
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | NEIL4Q | 35.617 | 0.167 | Composite | 0.0703 | 0.6873 | 24.2829 | 1320 | 1070 | 1070 | 1070
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.5999 | 3.0327 | 6.8904 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4319 | 2.1239 | 6.6193 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.0181 | 0.099 | 1.8948 | 165 | 165 | 165 | 165
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.0176 | 0.0964 | 1.8454 | 165 | 165 | 165 | 165
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4859 | 2.6321 | 0.6696 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3185 | 1.7253 | 0.4389 | 151 | 151 | 151 | 151
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0396 | 0.3572 | 2.4383 | 1090 | 1030 | 925 | 1030
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1822 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240
KAIM3- | KAIM3A | 0 | 0 | Series Reactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120
KAIM3- | KAIM3B | 0 | 0 | Series Reactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120
KEOO1- | NECU1R | 26.51 | 0 | OHL | 0.8244 | 4.8402 | 1.6558 | 133 | 123 | 106 | 123
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6165 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0175 | 0.154 | 2.0858 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0178 | 0.1548 | 2.24 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0699 | 0.6763 | 20.5081 | 2000 | 1920 | 1790 | 1920
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0699 | 0.6763 | 20.5081 | 1995 | 1926 | 1787 | 1926
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 760 | 620 | 620 | 620
KINB2K | KINC2- | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 910 | 885 | 760 | 885
KINC2- | LOAN2Q | 4.28 | 0.31 | Composite | 0.0187 | 0.1831 | 4.4844 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 4.28 | 0.17 | Composite | 0.0185 | 0.1792 | 2.8954 | 765 | 620 | 620 | 620
LAMB2- | LAMB2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0178 | 0.1603 | 1.0942 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0188 | 0.1623 | 2.1962 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1050 | 965 | 880 | 965
LAMB2T | LOAN2- | 53.67 | 0.225 | Composite | 0.1948 | 2.0808 | 18.1931 | 795 | 620 | 620 | 620
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1120 | 1060 | 990 | 1060
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | MOSM2L | 26.196 | 0.194 | Composite | 0.1186 | 1.0915 | 8.8674 | 760 | 620 | 620 | 620
LOAN2- | WFIE2- | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 760 | 620 | 620 | 620
MARG1- | NECU1Q | 34.35 | 0.9 | Composite | 1.1386 | 6.5312 | 3.5807 | 241 | 230 | 210 | 230
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1478 | 2.8481 | 0.9694 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | MOSM2L | 5.3 | 0 | OHL | 0.0239 | 0.22 | 1.4416 | 955 | 885 | 760 | 885
MOSM2- | MOSM2T | 5.3 | 0 | OHL | 0.0239 | 0.22 | 1.4416 | 955 | 885 | 760 | 885
MOSM2T | WFIE2- | 2.943 | 0 | OHL | 0.0133 | 0.1221 | 0.8005 | 955 | 885 | 760 | 885
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1092 | 1.0391 | 7.0792 | 957 | 881 | 764 | 881
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
RAVE3- | WISH3S | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3S | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3T | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
RAVE3- | WISH3T | 0 | 4.1 | Cable | 1.9201 | 3.9532 | 0.005 | 45 | 45 | 45 | 45
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 75.76 | 0 | OHL | 0.1605 | 1.4592 | 44.5196 | 1390 | 1280 | 1110 | 1280
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.0716 | 1.0286 | 71.6778 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1316 | 1.1878 | 36.3204 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0239 | 0.2235 | 6.8252 | 2000 | 1920 | 1790 | 1920
STIR1S | WFIE1A | 37.6 | 5.4 | Composite | 3.1938 | 8.9123 | 8.7178 | 162 | 154 | 141 | 154
STLE1- | WIYH1- | 12.8916 | 0.2908 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 950 | 885 | 760 | 885
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
Table B.2.1c - NGET Transmission Circuits ETYS Yr1 - 2019/20
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 1389 | 1284 | 1108 | 1284
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 1389 | 1284 | 1108 | 1284
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629
ABTH21 | UPPB22 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882
ABTH22 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879
ABTH22 | UPPB21 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 772
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911
AMEM4A | IVER4A | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2009 | 1911 | 1746 | 1911
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933
AMEM4B | IVER4B | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933
AXMI41 | CHIC42 | 39.5 | 0 | OHL | 0.0429 | 0.687 | 26.0389 | 2779 | 2568 | 2217 | 2568
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2779 | 2568 | 2217 | 2568
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115
BAGB21 | SWAN21 | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1548
BARK21 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK21 | REBR21 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081
BARK22 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK22 | REBR22 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0155 | 0.191 | 5.6429 | 2009 | 1911 | 1746 | 1911
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0156 | 0.1915 | 10.4541 | 2009 | 1909 | 1710 | 1909
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.0692 | 0.7576 | 7.8243 | 944 | 882 | 762 | 882
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 827
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0689 | 0.7539 | 6.2735 | 762 | 762 | 662 | 762
BEDD23 | WIMB21 | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 930
BEDD4A | ROWD42 | 0 | 11.676 | Cable | 0.0079 | 0.138 | 127.4459 | 1309 | 1309 | 1309 | 1309
BEDD4B | ROWD41 | 0 | 11.676 | Cable | 0.0105 | 0.0957 | 210.168 | 1415 | 1415 | 1223 | 1415
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 56.939 | 0.631 | Composite | 0.2314 | 2.4189 | 22.4142 | 819 | 819 | 638 | 819
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 817
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 1031
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1236 | 1176 | 1074 | 1176
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1236 | 1176 | 1074 | 1176
BLYT41 | HEDD4A | 26.636 | 0.121 | Composite | 0.0426 | 0.514 | 18.0175 | 2199 | 2092 | 1911 | 2092
BLYT41 | HEDD4B | 26.636 | 0.49 | Composite | 0.0429 | 0.5194 | 24.1171 | 2199 | 2092 | 1911 | 2092
BODE41 | GWYN4A | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 1056
BODE41 | GWYN4B | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
BODE4A | BODE4B | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 500 | 500 | 500
BODE4C | BODE4D | 0 | 0.25 | Cable | 0.0002 | 0.003 | 2.7288 | 500 | 500 | 500 | 500
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOTW41 | FAWL41 | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 1109 | 901 | 1109
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0134 | 0.2147 | 8.1357 | 2779 | 2568 | 2217 | 2568
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0451 | 0.8316 | 32.2964 | 2779 | 2568 | 2217 | 2568
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.065 | 1.1398 | 43.92 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0358 | 0.5745 | 21.7727 | 2779 | 2568 | 2217 | 2568
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 762
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 762
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1204 | 1115 | 1018 | 1115
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 2470 | 2350 | 2146 | 2350
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0768 | 0.8127 | 5.4608 | 948 | 882 | 753 | 882
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.762 | 850 | 850 | 675 | 850
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2780 | 2570 | 2220 | 2570
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | LEIS4A | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2780 | 2780 | 2780 | 2780
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1093 | 1031 | 925 | 1031
BRIM2B | TOTT24 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1085 | 1031 | 925 | 1031
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1093 | 1031 | 925 | 1031
BRIM2C | TOTT22 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT23 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 934
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 557
BRIN21 | NORL22 | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 419
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 686 | 686 | 686 | 686
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395
BRIT41 | BRIT41 | 0 | 0 | Series Reactor | 0 | 0.125 | 0 | 67 | 67 | 67 | 67
BRIT41 | BRIT41 | 0 | 0 | Series Reactor | 0 | 0.125 | 0 | 67 | 67 | 67 | 67
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2568
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2277
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2568 | 2217 | 2568
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRWA2A | HINP22 | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 767 | 620 | 767
BRWA2B | HINP21 | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 762 | 762 | 619 | 762
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0224 | 0.3591 | 13.6101 | 2779 | 2568 | 2217 | 2568
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2910 | 2238 | 2910
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3102 | 2935 | 2765 | 2935
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3102 | 2935 | 2765 | 2935
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3102 | 2935 | 2765 | 2935
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 1038
BUSH21 | WIEN21 | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 762
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 713
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 713
BUST41 | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1203
BUST41 | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 2568 | 2217 | 2568
CAMA11 | IROA13 | 0 | 1 | Cable | 0.793 | 5.917 | 1.66 | 455 | 455 | 455 | 455
CAMA12 | IROA12 | 0 | 1 | Cable | 0.814 | 5.749 | 3.3761 | 455 | 455 | 455 | 455
CANT41 | CLEH41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 2038
CANT41 | SELL4C | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048
CANT41 | KEMS41 | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 2038
CANT41 | SELL4D | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048
CAPE1A | INCE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 3.2486 | 258 | 258 | 240 | 258
CAPE1B | INCE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 3.2416 | 240 | 240 | 240 | 240
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2890 | 2750 | 2420 | 2750
CAPE4A | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2780 | 2570 | 2220 | 2570
CAPE4B | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 835
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 835
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9776 | 3102 | 3048 | 2958 | 3048
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO41 | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR41 | DAIN41 | 2.545 | 0 | OHL | 0.0043 | 0.0496 | 1.5076 | 2169 | 2084 | 1940 | 2084
CARR4A | DAIN41 | 2.063 | 0 | OHL | 0.0035 | 0.0404 | 1.2165 | 1507 | 1507 | 1507 | 1507
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1524 | 1524 | 1524 | 1524
CELL41 | DAIN41 | 53.412 | 2.31 | parallel Composite | 0.0847 | 1.031 | 76.931 | 2508 | 2508 | 2300 | 2508
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2175 | 2069 | 1890 | 2069
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2175 | 2069 | 1890 | 2069
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0495 | 0.6067 | 18.9879 | 3102 | 3048 | 2958 | 3048
CHIC41 | EXET41 | 75.92 | 0 | OHL | 0.0824 | 1.3205 | 50.0469 | 2779 | 2568 | 2217 | 2568
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829
CHIC42 | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHUE4A | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2827
CHUE4A | WTHU4D | 2.4188 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048
CHUE4B | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2924
CHUE4B | WTHU4C | 2.5806 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048
CILF2A | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF2B | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136
CLEH41 | KEMS41 | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1438
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 1710 | 1710 | 1710 | 1710
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302
CONQ41 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1438
CONQ41 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 3075 | 2876 | 2663 | 2876
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 2423 | 2327 | 2167 | 2327
COTT41 | GREN41 | 129.478 | 0 | OHL | 0.2293 | 2.5548 | 75.7188 | 2009 | 1911 | 1746 | 1911
COTT41 | KEAD41 | 34.628 | 0 | OHL | 0.0595 | 0.6858 | 20.1792 | 2212 | 2125 | 1979 | 2125
COTT41 | KEAD41 | 34.479 | 0 | OHL | 0.0592 | 0.6828 | 20.0931 | 2212 | 2125 | 1979 | 2125
COTT41 | RYHA41 | 76.891 | 0 | OHL | 0.0834 | 1.3374 | 50.6872 | 2780 | 2780 | 2780 | 2780
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0506 | 0.5544 | 21.5604 | 2212 | 2125 | 1979 | 2125
COTT42 | RYHA4B | 76.816 | 0 | OHL | 0.0834 | 1.3361 | 50.638 | 2780 | 2780 | 2780 | 2780
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0105 | 0.1321 | 3.9942 | 3326 | 3160 | 2971 | 3160
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0619 | 1.1211 | 9.699 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.007 | 0.113 | 4.2822 | 2771 | 2568 | 2217 | 2568
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0125 | 0.2001 | 7.5827 | 2779 | 2568 | 2217 | 2568
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0394 | 0.6314 | 23.9301 | 2779 | 2568 | 2217 | 2568
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0537 | 0.9095 | 34.8191 | 2779 | 2568 | 2217 | 2568
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 1132
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 1132
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879
CREB2A | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB2B | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 2771 | 2771 | 2663 | 2771
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO41 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO42 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CULJ41 | DIDC41 | 4.898 | 0 | OHL | 0.0053 | 0.0852 | 3.2288 | 2771 | 2568 | 2217 | 2568
DAIN41 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0541 | 0.6511 | 66.8001 | 2397 | 2302 | 2144 | 2302
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1604 | 1604 | 1557 | 1604
DINO41 | PENT41 | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9578 | 1623 | 1623 | 1571 | 1623
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1169
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2009 | 1911 | 1746 | 1911
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1769 | 1769 | 1320 | 1769
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2089 | 2089 | 1878 | 2089
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2771 | 2568 | 2217 | 2568
DRAX41 | FENW4A | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2867
DRAX42 | THTO42 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2779 | 2568 | 2217 | 2568
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3065 | 2829 | 2418 | 2829
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830
DUNG41 | SELL4F | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 525
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 524 | 518 | 401 | 518
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 750
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO4A | RYHA4B | 58.769 | 0 | OHL | 0.0638 | 1.0222 | 38.7404 | 2780 | 2780 | 2780 | 2780
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO4B | RYHA42 | 58.95 | 0 | OHL | 0.064 | 1.0253 | 38.8593 | 2780 | 2780 | 2780 | 2780
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 2779 | 2568 | 2217 | 2568
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1389 | 1284 | 1108 | 1284
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1239
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2217 | 2217 | 1801 | 2217
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2779 | 2568 | 2217 | 2568
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 762
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST12 | HEND11 | 0 | 1 | Cable | 0.081 | 0.634 | 16.01 | 299 | 275 | 218 | 275
ELST21 | MILH2A | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 524
ELST21 | MILH2B | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 524
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 762
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 762
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 762
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 762
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST4A | ELST41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0749 | 0.6969 | 20.0233 | 1590 | 1500 | 1346 | 1500
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0747 | 0.6944 | 19.9464 | 1590 | 1500 | 1346 | 1500
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911
FAWL41 | LOVE41 | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 1109 | 901 | 1109
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4527 | 1967 | 1874 | 1712 | 1874
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1967 | 1875 | 1712 | 1875
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FENW4A | KEAD42 | 42.52 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876
FERR21 | FERR21 | 0 | 0.8161 | Cable | 0.0027 | 0.0204 | 6.0881 | 600 | 600 | 600 | 600
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823
FERR23 | FERR23 | 0 | 0.72603 | Cable | 0.0024 | 0.0182 | 5.4162 | 600 | 600 | 600 | 600
FERR2A | FERR23 | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115
FERR2B | FERR22 | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 1031
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 480 | 480 | 330 | 480
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512
FIDF21 | FIDF23 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF22 | FIDF24 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF22 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF23 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF24 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2212 | 2125 | 1979 | 2125
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.0748 | 0.8176 | 23.8163 | 2212 | 2125 | 1979 | 2125
FOUR21 | HARK21 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032
GART4A | KEAD43 | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3180 | 3000 | 2692 | 3000
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032
GART4B | KEAD41 | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3180 | 3000 | 2692 | 3000
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3102 | 2935 | 2633 | 2935
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390
GRAI41 | TILB41 | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2003 | 2003 | 1939 | 2003
GREN41 | STAY41 | 101.832 | 0 | OHL | 0.1852 | 2.0259 | 59.0223 | 2514 | 2439 | 2314 | 2439
GREN41 | SUND41 | 39.75 | 0 | OHL | 0.0723 | 0.7909 | 23.0368 | 2009 | 1911 | 1746 | 1911
GREN41 | SUND42 | 39.955 | 0 | OHL | 0.0727 | 0.795 | 23.1553 | 2009 | 1911 | 1746 | 1911
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GRSA21 | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119
GRSA21 | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1119
GRSA21 | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GRSA21 | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GRSB21 | LACK2C | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1119
GRSB21 | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1119
GRSB21 | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GRSB21 | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 180 | 180 | 180
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HACK2A | TOTT2B | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK2B | TOTT2A | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HAKB1- | HARK13 | 8.487 | 0 | OHL | 0.917 | 2.075 | 0.451 | 132 | 123 | 106 | 123
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3111 | 3326
HAMB4A | PEWO41 | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2473
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
HAMB4B | PEWO41 | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2473
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1362 | 1285 | 1202 | 1285
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1206 | 1.5777 | 77.2944 | 2009 | 1912 | 1746 | 1912
HARK13 | JUNV1- | 16.243 | 0 | OHL | 1.194 | 2.729 | 0.743 | 132 | 123 | 106 | 123
HARK22 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 774
HARK41 | HAKB4- | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2169 | 2084 | 1940 | 2084
HARK41 | HAKB4B | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2170 | 2084 | 1941 | 2084
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1110 | 1038 | 962 | 1038
HATL21 | HARM21 | 13.983 | 0 | OHL | 0.0531 | 0.5772 | 3.9082 | 1093 | 1031 | 925 | 1031
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0332 | 0.335 | 2.0887 | 1382 | 1279 | 1157 | 1279
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1148 | 1086 | 1021 | 1086
HATL21 | WBOL21 | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1093 | 1031 | 926 | 1031
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 874
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1093 | 1031 | 925 | 1031
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2545 | 2421 | 2211 | 2421
HEDD4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
HEDD4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
HEDD4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
HEDD4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664
HEYS41 | HEYS41 | 1.692 | 0 | OHL | 0.0036 | 0.0347 | 0.9467 | 1390 | 1390 | 1390 | 1390
HEYS41 | HEYS41 | 1.416 | 0 | OHL | 0.0031 | 0.0291 | 0.7923 | 1390 | 1390 | 1390 | 1390
HEYS41 | HEYS41 | 1.416 | 0 | OHL | 0.0031 | 0.0291 | 0.7923 | 1390 | 1390 | 1390 | 1390
HEYS41 | HEYS41 | 1.692 | 0 | OHL | 0.0036 | 0.0347 | 0.9467 | 1390 | 1390 | 1390 | 1390
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3330 | 3160 | 2970 | 3160
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0254 | 0.2958 | 13.2571 | 2212 | 2125 | 1979 | 2125
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056
HINP41 | MELK41 | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | MELK41 | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | TAUN41 | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1979 | 2125
HINP41 | TAUN42 | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1979 | 2125
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771
HURS21 | LITT2A | 5.164 | 2.613 | Composite | 0.0288 | 0.2786 | 27.8693 | 864 | 864 | 824 | 864
HURS21 | LITT2B | 5.14 | 2.659 | Composite | 0.0288 | 0.2786 | 28.329 | 864 | 864 | 824 | 864
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 882 | 704 | 882
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 882 | 704 | 882
HUTT41 | HUTT41 | 0 | 0 | Thyristor Controlled Series Capacitor | 0 | 0.0702 | 0 | 2750 | 2750 | 2750 | 2750
HUTT41 | HUTT41 | 0 | 0 | Thyristor Controlled Series Capacitor | 0 | 0.0702 | 0 | 2750 | 2750 | 2750 | 2750
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284
IROA11 | OLDS12 | 12.577 | 0 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 423
IROA12 | OLDS12 | 12.572 | 0 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 424
IROA21 | MELK21 | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 581
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 581
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750
IRON41 | LEGA4A | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.2909 | 9.0977 | 2397 | 2302 | 2144 | 2302
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 419
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 419
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 960
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 776
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 776
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 1360 | 1280 | 1200 | 1280
JORD21 | NORL21 | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 419
KEAD41 | KEAP41 | 0.321 | 0 | OHL | 0.0007 | 0.0066 | 0.179 | 3000 | 3000 | 3000 | 3000
KEAD42 | KEAP42 | 0.433 | 0.42 | Composite | 0.0013 | 0.0151 | 7.1841 | 3000 | 3000 | 3000 | 3000
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0308 | 0.4944 | 18.7376 | 2779 | 2568 | 2217 | 2568
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0307 | 0.4916 | 18.6331 | 3326 | 3160 | 2971 | 3160
KEAR21 | WGHA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 830 | 830 | 665 | 830
KEAR21 | WGHA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 835
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0721 | 0.7367 | 22.6825 | 1926 | 1832 | 1674 | 1832
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0717 | 0.7289 | 22.3721 | 1926 | 1832 | 1674 | 1832
KENG41 | SJOW41 | 0 | 4.63 | Cable | 0.0021 | 0.0583 | 56.3205 | 1770 | 1730 | 1600 | 1730
KENG41 | SJOW41 | 0 | 4.5 | Cable | 0.002 | 0.0567 | 54.7391 | 2000 | 2000 | 2000 | 2000
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 1327 | 1298 | 1200 | 1298
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 1327 | 1298 | 1200 | 1298
KENG41 | WLSD41 | 0 | 2.892 | Cable | 0.0013 | 0.0372 | 35.179 | 1770 | 1730 | 1600 | 1730
KENG41 | WLSD42 | 0 | 2.892 | Cable | 0.0013 | 0.0372 | 35.179 | 1770 | 1730 | 1600 | 1730
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 762
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 762
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY22 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1381 | 1339 | 1258 | 1339
KIBY21 | WASF2B | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KIBY22 | WASF2A | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KILL41 | KILL41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2750 | 2750 | 2750 | 2750
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720
KINO41 | KINO41 | 0 | 0 | Series Reactor | 0.0027 | 2 | 0 | 2002 | 2002 | 2002 | 2002
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
KINO41 | TILB41 | 15.4784 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2003 | 2003 | 1948 | 2003
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 762
KITW21 | OCKH21 | 13.738 | 0.222 | Composite | 0.0525 | 0.5743 | 6.2479 | 772 | 772 | 619 | 772
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 667
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 551 | 512 | 442 | 512
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 551 | 512 | 442 | 512
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1148 | 1086 | 1021 | 1086
LACK41 | NORT41 | 22.443 | 0.25 | Composite | 0.0404 | 0.4515 | 17.428 | 1831 | 1739 | 1588 | 1739
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2418
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2418
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213
LAND41 | LAGA41 | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7628 | 2423 | 2327 | 2168 | 2327
LAND42 | LAGA41 | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8376 | 1389 | 1284 | 1108 | 1284
LEGA41 | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 2002 | 2002 | 2002
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIS11 | SIZE11 | 0 | 2.149 | Cable | 0.0196 | 0.2155 | 4.8028 | 301 | 301 | 243 | 301
LEIS11 | SIZE11 | 0 | 2.148 | Cable | 0.0195 | 0.2154 | 4.8006 | 301 | 301 | 243 | 301
LEIS11 | SIZE1A | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 301
LEIS11 | SIZE1B | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 301
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2780 | 2780 | 2780 | 2780
LISD21 | LISD21 | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 750 | 740 | 750
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6835 | 1389 | 1284 | 1108 | 1284
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0176 | 0.1632 | 4.6835 | 1389 | 1284 | 1108 | 1284
LITT41 | WTHU4E | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1883
LITT41 | WTHU4F | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1883
LOFI4A | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOFI4B | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568
MACC41 | STAL42 | 31.196 | 0 | OHL | 0.062 | 0.617 | 18.1761 | 1710 | 1627 | 1488 | 1627
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3160 | 2971 | 3160
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 682 | 629 | 538 | 629
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2518 | 2395 | 2188 | 2395
NECT4A | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3299 | 3078 | 3299
NECT4B | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3330 | 3160 | 2970 | 3160
NECT4B | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3330 | 3260 | 3060 | 3260
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 419
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 419
NEEP4A | STSB4B | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 819
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 827 | 779 | 827
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | SING41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 419
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 419
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1372 | 1293 | 1197 | 1293
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORW11 | NOTR11 | 0 | 1 | Cable | 0.2362 | 0.778 | 0.3149 | 350 | 350 | 350 | 350
NORW14 | NOTR12 | 0 | 1 | Cable | 0.236 | 0.778 | 0.315 | 324 | 299 | 299 | 299
OCKH21 | WIEN21 | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 672
OCKH2A | WIEN21 | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0375 | 0.3474 | 2.2265 | 1093 | 1031 | 925 | 1031
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2771 | 2568 | 2217 | 2568
PADI41 | PEWO41 | 37.608 | 0 | OHL | 0.0556 | 0.7049 | 23.1779 | 2169 | 2084 | 1940 | 2084
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2779 | 2568 | 2217 | 2568
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2779 | 2569 | 2217 | 2569
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2771 | 2771 | 2692 | 2771
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 217.727 | 5.468 | parallel Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2568 | 2217 | 2568
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0633 | 0.9555 | 131.5497 | 1135 | 1135 | 992 | 1135
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PERH11 | WYLF11 | 19.94 | 0 | OHL | 0.475 | 4.232 | 1.0947 | 333 | 331 | 304 | 331
PERH11 | WYLF11 | 19.94 | 0 | OHL | 0.475 | 4.232 | 1.0947 | 330 | 330 | 300 | 330
PEWO21 | WASF2B | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO22 | WASF2A | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 419
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 439 | 439 | 381 | 439
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136
PYLE21 | PYLE2A | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1204 | 1115 | 1018 | 1115
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2757 | 2147 | 2056 | 1904 | 2056
RATS41 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2147 | 2056 | 1904 | 2056
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1309
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 2212 | 2125 | 1979 | 2125
REBR21 | TOTT22 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127
REBR22 | TOTT21 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
ROCH21 | WGHA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 905 | 882 | 762 | 882
ROCH21 | WGHA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 841
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2780 | 2780 | 2780 | 2780
RYEH41 | WALX4A | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2779 | 2568 | 2217 | 2568
RYEH41 | RYEH4A | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569
RYEH41 | RYEH4B | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569
RYEH4A | WALX4B | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2779 | 2568 | 2217 | 2568
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1517 | 1517 | 1517 | 1517
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424
SELL41 | SELL41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860
SELL41 | SELL4C | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4C | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 2369
SELL41 | SELL4D | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3100 | 3100 | 3100 | 3100
SELL41 | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3326 | 3326 | 3326
SELL4C | SELL41 | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 2369
SELL4D | SELL41 | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 2369
SELL4F | SELL41 | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 2369
SHRE4B | SHRE4A | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 2170 | 2007.25 | 1732.745 | 2007.25
SJOW21 | TOTT23 | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 868 | 835 | 682 | 835
SJOW21 | TOTT24 | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 868 | 835 | 682 | 835
SJOW41 | SJOW41 | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 240 | 240 | 240 | 240
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2350 | 2146 | 2350
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2350 | 2146 | 2350
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SSHI21 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1236 | 1176 | 1074 | 1176
SSHI21 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1093 | 1031 | 925 | 1031
STAL42 | STSB4A | 28.555 | 5.057 | Composite | 0.0343 | 0.5535 | 95.384 | 1649 | 1528 | 1399 | 1528
STAL4A | THOM41 | 71.245 | 4.978 | Composite | 0.0791 | 1.2942 | 122.4093 | 1330 | 1171 | 1001 | 1171
STEN11 | STES11 | 0 | 1 | Cable | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 198
STEW21 | STEW21 | 0 | 0.435 | Cable | 0.0007 | 0.0116 | 2.5837 | 854 | 795 | 700 | 795
STEW21 | STEW21 | 0 | 0.068 | Cable | 0.0002 | 0.0014 | 0.5787 | 274 | 274 | 250 | 274
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3048 | 2935 | 2692 | 2935
SUTB4A | WALP41 | 3.85 | 0 | OHL | 0.008 | 0.0773 | 2.2055 | 1450 | 1340 | 1150 | 1340
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 421 | 421 | 381 | 421
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 764
THOM22 | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882
THUR2A | THUR21 | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1120 | 1060 | 990 | 1060
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119
TILB41 | TILB4B | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
TILB4A | TILB41 | 0.05808 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1093 | 1031 | 925 | 1031
USKM12 | USKM11 | 0 | 0 | Series Reactor | 0.25 | 20 | 0 | 90 | 90 | 90 | 90
USKM21 | USKM2A | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956
USKM2A | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641
USKM2B | USKM21 | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629
WBUR42 | WBUR41 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1500 | 1500 | 1500
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 2780 | 2571.5 | 2219.83 | 2571.5
WTHU41 | WTHU41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WTHU42 | WTHU42 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
FLIB41 | HUCS4 | 0 | 389 | HVDC link |  | N/A | N/A | 2200 | 2200 | 2200 | 2200
SPIT2K | BLHI4R | 0 | 113 | HVDC link |  | N/A | N/A | 1200 | 1200 | 1200 | 1200

## B-2-1d
Table B.2.1d - OFTO Transmission Circuits ETYS Yr1 - 2019/20
OFTO | Station | Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
Aberdeen Offshore Wind Farm Limited | Aberdeen Offshore Wind Farm | ABBA6- | ABBA6J | 0 | 4.35 | Cable | 0.8279 | 1.1577 | 1.595 | 60 | 66
" | " | ABBA6- | ABBA6K | 0 | 3.98 | Cable | 0.7612 | 1.0645 | 1.467 | 60 | 66
" | " | ABBA6- | ABBA61 | 0 | 1 | Cable | 0.0314 | 0.0052 | 0.0109 | 160 | 66
" | " | ABBA1A | ABBA11 | 0 | 3 | Cable | 0.0476 | 0.0665 | 1.467 | 300 | 132
Beatrice Offshore Windfarm Ltd | Beatrice Wind Farm | BEAT21 | BEAT21 | 0 | 19.2 | Cable | 0.1031 | 0.528 | 72.4016 | 321 | 220
" | " | BEAT22 | BEAT22 | 0 | 19.2 | Cable | 0.1031 | 0.528 | 72.4016 | 321 | 220
" | " | BEIW21 | BEAT2A | 0 | 70 | Cable | 0.7231 | 1.7355 | 216.1738 | 321 | 220
" | " | BEIW21 | BEAT2C | 0 | 70 | Cable | 0.7231 | 1.7355 | 216.1738 | 321 | 220
|  | BEAT21 | BEAT22 | 0 | 1.315 | Cable | 0.0108 | 0.0046 | 1.3537 | 321 | 220
Barrow Offshore Wind Ltd | Barrow Offshore Wind Farm | BOSO1A | BOSW10 | 0 | 26.9 | Cable | 0.0154 | 0.0216 | 0.2209 | 106 | 132
" | " | BOSO10 | BOSO1A | 0 | 2.633 | Cable | 0.0009 | 0.0029 | 0.0311 | 126 | 132
DONG Energy Burbo Extension (UK) Ltd | Burbo Bank Extension Offshore Wind Farm | BODE41 | BBWO41 | 0 | 0.83 | Cable | 0.0012 | 0.009 | 0.07 | 277 | 400
" | " | BBWO11 | BBWW11 | 0 | 34.622 | Cable | 0.3875 | 0.9335 | 103.7527 | 277 | 220
Dudgeon Offshore Wind Ltd | Dudgeon Offshore Wind Farm | DUDW11 | DUDO11 | 0 | 91.31 | Cable | 1.8163 | 6.8193 | 110.6215 | 204 | 132
" | " | DUDW12 | DUDO11 | 0 | 91.31 | Cable | 1.8163 | 6.8193 | 110.6215 | 204 | 132
Galloper Wind Farm Limited | Galloper | GALO11 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 890 | 132
" | " | GALO11 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 890 | 132
" | " | GALO11 | GANW11 | 0 | 45.8 | Cable | 1.23 | 2.8301 | 58.38 | 780 | 132
" | " | GALO11 | GANW11 | 0 | 45.8 | Cable | 1.23 | 2.8301 | 58.38 | 780 | 132
Greater Gabbard Offshore Winds Ltd | Greater Gabbard Offshore Wind Farm | GGON11 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
" | " | GGON12 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
" | " | GGON13 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
" | " | GALO11 | GGON11 | 0 | 17 | Cable | 0.36 | 1.07 | 20.5 | 150 | 132
Gunfleet Sands Ltd | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS11 | 0 | 12.789 | Cable | 0.3254 | 0.8061 | 15.5518 | 158 | 132
Gwynt Y Mor Offshore Wind Farm Ltd | GWYNT Y MOR PS | GWYO11 | GWBW11 | 0 | 33.3 | Cable | 0.00973 | 0.1625 | 0.3768 | 150 | 132
" | " | GWYO11 | GWBW11 | 0 | 33.3 | Cable | 0.00973 | 0.1625 | 0.3768 | 150 | 132
" | " | GWYO11 | GWAW12 | 0 | 30.3 | Cable | 0.008763 | 0.0233 | 0.3463 | 150 | 132
" | " | GWYO11 | GWAW12 | 0 | 30.3 | Cable | 0.008763 | 0.0233 | 0.3463 | 150 | 132
E.ON Climate & Renewables UK Humber Wind Ltd | Humber Gateway Offshore Wind Farm | HUMO11 | HUMW11 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 122 | 132
" | " | HUMO12 | HUMW12 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 122 | 132
Lincs Wind Farm Ltd | Lincolnshire Offshore Windfarm | LINS10 | LINO1A | 0 | 12.5 | Cable | 0.2163 | 1.0055 | 15.8962 | 153 | 132
" | " | LINS10 | LINO1B | 0 | 12.5 | Cable | 0.2163 | 1.0055 | 15.8962 | 153 | 132
" | " | LINO1A | LINO10 | 0 | 47.5 | Cable | 1.8279 | 3.459 | 53.6443 | 153 | 132
" | " | LINO1B | LINO10 | 0 | 47.5 | Cable | 1.8279 | 3.459 | 53.6443 | 153 | 132
London Array Ltd | London Array Offshore Wind Farm | CLEH40 | LONO41 | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
" | " | CLEH40 | LONO42 | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
" | " | LONO1A | LOAW11 | 0 | 53.743 | Cable | 1.5817 | 2.9724 | 73.0267 | 167 | 150
" | " | LONO1B | LOAW11 | 0 | 53.743 | Cable | 1.5817 | 2.9724 | 73.0267 | 167 | 150
" | " | LONO1C | LOAW12 | 0 | 52.567 | Cable | 1.5467 | 2.9071 | 71.4473 | 167 | 150
" | " | LONO1D | LOAW12 | 0 | 52.567 | Cable | 1.5467 | 2.9071 | 71.4473 | 167 | 150
Ormonde Energy Ltd | Ormonde Offshore Windfarm | ORMO11 | ORMW11 | 0 | 44.267 | Cable | 0.7323 | 3.104 | 46.68 | 158 | 132
DONG Energy RB (UK) Limited | Race Bank Offshore | RACO21 | RACO2A | 0 | 82.5 | Cable | 0.487 | 2.1112 | 247.8447 | 484 | 220
" | " | RACO22 | RACO2B | 0 | 83.5 | Cable | 0.4934 | 2.136 | 250.7489 | 484 | 220
" | " | RACO4A | RACO4C | 0 | 0.3 | Cable | 0.0004 | 0.0032 | 2.4278 | 484 | 400
" | " | RACO4B | RACO4D | 0 | 0.3 | Cable | 0.0004 | 0.0032 | 2.4278 | 484 | 400
" | " | RACW21 | RACW22 | 0 | 6.7 | Cable | 0.0433 | 0.1661 | 19.4582 | 484 | 220
" | " | WALP41 | RACO4A | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
| " | WALP41 | RACO4B | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
E.ON UK Renewables UK Robin Rigg East Ltd | Robin Rigg East Offshore Wind Farm | RORE11 | RREW1A | 0 | 1.8 | Cable | 0.05 | 0.15 | 1.6 | 114 | 132
" | " | RREW1A | RREW11 | 0 | 12.6 | Cable | 0.73 | 1.02 | 10.46 | 103 | 132
E.ON UK Renewables UK Robin Rigg East Ltd | Robin Rigg West Offshore Wind Farm | RORW11 | RRWW1B | 0 | 1.8 | Cable | 0.05 | 0.15 | 1.6 | 114 | 132
" | " | RRWW1B | RRWW11 | 0 | 12.6 | Cable | 0.73 | 1.02 | 10.46 | 103 | 132
Scira Offshore Energy Ltd | Sheringham Shoal Offshore Wind Farm | SSAW11 | SSAW1A | 0 | 22.4 | Cable | 0.006171 | 0.017998 | 0.24522 | 178 | 132
" | " | SSAW1A | SSAW12 | 0 | 0.4 | Cable | 8.3e-05 | 0.000275 | 0.005255 | 178 | 132
" | " | SSBW11 | SSBW1B | 0 | 20.5 | Cable | 0.005647 | 0.016472 | 0.22442 | 178 | 132
" | " | SSBW1B | SSBW12 | 0 | 0.4 | Cable | 8.3e-05 | 0.000275 | 0.005255 | 178 | 132
" | " | SSAW12 | SALL11 | 0 | 22 | Cable | 0.003965 | 0.017929 | 0.30224 | 190 | 132
" | " | SSBW12 | SALL12 | 0 | 22 | Cable | 0.003965 | 0.017929 | 0.30224 | 190 | 132
Thanet Offshore Wind Ltd | Thanet Offshore Wind Farm | THAW11 | THOW11 | 0 | 28.89 | cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
" | " | THAW12 | THOW12 | 0 | 28.89 | cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
Westermost Rough Ltd | Westermost Rough Offshore Wind Farm | WERW12 | WERO1C | 0 | 9.6525 | Cable | 0.13835 | 0.50506 | 15.2902 | 214.3413 | 150
" | " | WERO1C | WERO1B | 0 | 1.482 | Cable | 0.016282 | 0.073145 | 2.6692 | 231.7484 | 150
" | " | WERO1B | WERO1A | 0 | 13.9185 | Cable | 0.13374 | 0.85744 | 26.2286 | 229.4101 | 150
" | " | WERO1A | WERO11 | 0 | 0.78055 | Cable | 0.0065636 | 0.046673 | 1.5245 | 140.0623 | 150
" | " | WERO22 | WERO2A | 0 | 0.039 | Cable | 0.00031845 | 0.0012888 | 0.13463 | 256.7809 | 275
" | " | WERO2A | HEDO21 | 0 | 0.29 | Cable | 0.0023679 | 0.0095833 | 1.0011 | 256.7809 | 275
" | " | WERO21 | WERO2B | 0 | 0.103 | Cable | 0.00084102 | 0.0034037 | 0.35556 | 256.7809 | 275
" | " | WERO2B | HEDO21 | 0 | 0.265 | Cable | 0.0021638 | 0.0087572 | 0.9148 | 394.1498 | 275
Morecambe Wind Ltd | West of Duddon Sands Offshore Wind Farm | WDSO1A | WDSW11 | 0 | 39.4 | Cable | 0.6396 | 1.8368 | 64.2338 | 209 | 155
" | " | WDSO1B | WDSW12 | 0 | 39.4 | Cable | 0.6396 | 1.8368 | 64.2338 | 209 | 155
" | " | WDSO11 | WDSO1A | 0 | 2.675 | Cable | 0.0234 | 0.161 | 5.1485 | 209 | 155
" | " | WDSO12 | WDSO1B | 0 | 2.675 | Cable | 0.0234 | 0.161 | 5.1485 | 209 | 155
" | " | HEYS40 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
" | " | HEYS40 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
RAMPION OFFSHORE WIND LIMITED | Rampion Offshore Wind Farm | BOLN41 | TWIN4A | 0 | 2.602 | Cable | 0.0028 | 0.0042 | 4.4179 | 411.1 | 400
" | " | BOLN41 | TWIN4B | 0 | 2.764 | Cable | 0.0036 | 0.0053 | 5.6068 | 411.1 | 400
" | " | TWIN1A | RAMW1A | 0 | 42.346 | Cable | 0.6872 | 1.9295 | 78.5805 | 209.9 | 150
" | " | TWIN1B | RAMW1B | 0 | 42.286 | Cable | 0.6864 | 1.9267 | 78.4554 | 209.9 | 150
DONG Walney UK Ltd | Walney 1 Offshore Wind Farm | WAAO11 | WAAO1A | 2.9 | 0 | Cable | 0.076045 | 0.13688 | 3.5539 | 192 | 132
" | " | WAAO1A | WAAW11 | 43.7 | 0 | Cable | 1.2943 | 2.3298 | 55.0577 | 164 | 132
Walney (UK) Offshore Windfarms Ltd | Walney 2 Offshore Wind Farm | WABO11 | WABO1A | 0 | 5.23 | Cable | 0.15 | 0.27 | 6.384 | 192 | 132
" | " | WABO1A | WABW11 | 0 | 44.13 | Cable | 1.266 | 2.279 | 53.869 | 164 | 132
DONG Energy Walney Extension (UK) Ltd | Walney Extension | MIDL41 | WOWE41 | 0 | 2.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
" | " | MIDL41 | WOWE41 | 0 | 2.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
" | Walney 3 Offshore Wind Farm | WOWE21 | WACW21 | 0 | 82.1 | Cable | 0.9432 | 1.99 | 251.59 | 347 | 220
" | " | WADW21 | WACW21 | 0 | 24.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 220
" | Walney 4 Offshore Wind Farm | WOWE21 | WADW21 | 0 | 68.7 | Cable | 0.7775 | 1.6599 | 209.9395 | 347 | 220
East Anglia One Limited | East Anglia One | BRFO41 | BRST41 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
" | " | BRFO41 | BRST42 | 0 | 0.47 | Cable | 0.0012052 | 0.0060172 | 3.8508 | 369 | 400
" | " | BRST21 | EANO21 | 0 | 36.9 | Cable | 0.13748 | 1.2511 | 138.0246 | 370 | 220
" | " | BRST22 | EANO21 | 0 | 36.9 | Cable | 0.13748 | 1.2511 | 138.0246 | 370 | 220
" | " | EANO21 | EAAW21 | 0 | 62.55 | Cable | 0.4782 | 1.4862 | 196.88 | 384 | 220
" | " | EANO21 | EAAW21 | 0 | 62.55 | Cable | 0.4782 | 1.4862 | 196.88 | 384 | 220
" | " | EAAW21 | EAAW21 | 0 | 21.41 | Cable | 0.146 | 0.5 | 70.9723 | 410 | 220
" | " | EAAW22 | EAAW22 | 0 | 21.41 | Cable | 0.146 | 0.5 | 70.9723 | 410 | 220
Hornsea 1 Limited | Hornsea Power Station 1A | HOWR2A | HOWW2A | 0 | 66.2 | Cable | 0.4924 | 1.6413 | 175.1469 | - | 220
" | " | HOWW2B | HOWW2A | 0 | 12.3 | Cable | 0.15756 | 0.30496 | 34.5997 | - | 220
" | " | HOWR2A | HOWA21 | 0 | 105.103 | Cable | 0.68384 | 3.2701 | 292.1283 | - | 220
" | Hornsea Power Station 1B | HOWR2B | HOWW2B | 0 | 72.2 | Cable | 0.47736 | 1.7155 | 203.0972 | - | 220
" | " | HOWR2B | HOWA21 | 0 | 104.903 | Cable | 0.69628 | 3.1955 | 303.8973 | - | 220
" | " | HOWW2C | HOWW2B | 0 | 13.9 | Cable | 0.17806 | 0.34463 | 39.1004 | - | 220
" | Hornsea Power Station 1C | HOWR2C | HOWW2C | 0 | 85 | Cable | 0.63223 | 2.1074 | 224.8866 | - | 220
" | " | HOWR2C | HOWA21 | 0 | 104.703 | Cable | 0.68087 | 3.2601 | 291.07 | - | 220

## B-2-2a
B.2.2a - SHE Transmission Circuit Changes 2020/21 to 2028/29
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
ABED1T | ABED1- | 2020 | Addition | 5 | 0 | OHL | 0.25 | 1.04 | 0.28 | 163 | 152 | 131 | 152
BLHI1J | KEIT1K | 2020 | Addition | 0 | 4 | Cable | 0.08 | 0.34 | 5.48 | 200 | 178 | 178 | 178
BLHI1K | KEIT1J | 2020 | Addition | 0 | 4 | Cable | 0.08 | 0.34 | 5.48 | 200 | 178 | 178 | 178
CAAD3- | BLRH3- | 2020 | Addition | 8.5 | 0 | OHL | 3.98 | 8.2 | 0.87 | 47.9 | 46.9 | 43.4 | 46.9
CAAD3- | WISL3- | 2020 | Addition | 0 | 85 | Cable | 38.71 | 88.28 | 7.56 | 30 | 30 | 30 | 30
DOUN2- | GORW2- | 2020 | Changed | 58.1 | 0 | OHL | 0.35 | 3.2 | 12.32 | 702 | 665 | 599 | 665
DUNM1- | ABED1T | 2020 | Addition | 2.76 | 0 | OHL | 0.14 | 0.57 | 0.16 | 203 | 193 | 176 | 193
DUNM1- | DUNM1C | 2020 | Removal | 6 | 0 | OHL | 0.3 | 1.24 | 0.34 | 203 | 193 | 176 | 193
DUNM1C | ABED1T | 2020 | Addition | 3.24 | 0 | OHL | 0.16 | 0.67 | 0.18 | 203 | 193 | 176 | 193
ELGI3- | MEIK3- | 2020 | Addition | 0 | 18 | Cable | 16.87 | 18.02 | 1.67 | 33.6 | 30.5 | 30.5 | 30.5
GORW2- | STRB2- | 2020 | Changed | 10.3 | 0 | OHL | 0.06 | 0.57 | 2.18 | 702 | 665 | 599 | 665
KEIT1- | MACD1Q | 2020 | Removal | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1- | MACD1R | 2020 | Removal | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1J | MACD1Q | 2020 | Addition | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT1K | MACD1R | 2020 | Addition | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 111 | 103 | 89 | 103
KEIT3- | SPCH3- | 2020 | Addition | 1 | 0 | OHL | 0.72 | 1.04 | 0.09 | 29.4 | 28.8 | 26.7 | 28.8
LOCL1S | QUOI1Q | 2020 | Changed | 18.3 | 0 | OHL | 0.92 | 3.79 | 1.03 | 203 | 193 | 176 | 193
STRB2- | LOCB2K | 2020 | Changed | 18.9 | 0 | OHL | 0.11 | 1.04 | 4.01 | 702 | 665 | 599 | 665
ABED1T | ABED1- | 2021 | Removal | 5 | 0 | OHL | 0.25 | 1.04 | 0.28 | 163 | 152 | 131 | 152
ABNE3- | ERRL3- | 2021 | Addition | 7 | 0 | OHL | 7.42 | 20.37 | 0 | 29.3 | 27.2 | 23.5 | 27.2
BEAU4- | FAUG4- | 2021 | Removal | 48.6 | 0 | OHL | 0.06 | 0.93 | 29.39 | 2780 | 2670 | 2480 | 2670
BEAU4- | FAUG4J | 2021 | Addition | 48.6 | 0 | OHL | 0.06 | 0.93 | 29.39 | 2780 | 2670 | 2480 | 2670
BLHI2L | KINT2J | 2021 | Removal | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2L | ROTI2J | 2021 | Addition | 35.36 | 0 | OHL | 0.18 | 1.56 | 9.34 | 1090 | 1030 | 925 | 1030
BLHI2M | PEHERSV1 | 2021 | Removal | 82.72 | 0 | OHL | 0.42 | 3.58 | 21.6 | 1090 | 1030 | 920 | 1030
BLHI2M | ROTI2K | 2021 | Addition | 35.36 | 0 | OHL | 0.18 | 1.56 | 9.34 | 1090 | 1030 | 925 | 1030
DUNM1- | ABED1T | 2021 | Removal | 2.76 | 0 | OHL | 0.14 | 0.57 | 0.16 | 203 | 193 | 176 | 193
DUNM1- | DUNM1T | 2021 | Addition | 2.76 | 0 | OHL | 0.14 | 0.57 | 0.16 | 203 | 193 | 176 | 193
DUNM1C | ABED1T | 2021 | Removal | 3.24 | 0 | OHL | 0.16 | 0.67 | 0.18 | 203 | 193 | 176 | 193
DUNM1T | ABED1- | 2021 | Addition | 5 | 0 | OHL | 0.25 | 1.04 | 0.28 | 163 | 152 | 131 | 152
DUNM1T | DUNM1C | 2021 | Addition | 3.24 | 0 | OHL | 0.16 | 0.67 | 0.18 | 203 | 193 | 176 | 193
FAUG1- | LAGG1Q | 2021 | Removal | 6.49 | 0 | OHL | 0.74 | 1.48 | 0.33 | 221 | 216 | 208 | 216
FAUG1- | LAGG1R | 2021 | Removal | 6.49 | 0 | OHL | 0.74 | 1.48 | 0.33 | 221 | 216 | 208 | 216
FAUG1J | LAGG1Q | 2021 | Addition | 6.49 | 0 | OHL | 0.74 | 1.48 | 0.33 | 221 | 216 | 208 | 216
FAUG1K | LAGG1R | 2021 | Addition | 6.49 | 0 | OHL | 0.74 | 1.48 | 0.33 | 221 | 216 | 208 | 216
FAUG1P | LOCL1S | 2021 | Removal | 8.66 | 0 | OHL | 0.44 | 1.79 | 0.49 | 203 | 193 | 176 | 193
FAUG1P | MILS1Q | 2021 | Addition | 5.41 | 0 | OHL | 0.27 | 1.12 | 0.3 | 203 | 193 | 176 | 193
FAUG4- | MELG4J | 2021 | Removal | 24.01 | 0 | OHL | 0.03 | 0.46 | 14.52 | 2780 | 2670 | 2480 | 2670
FAUG4J | MELG4J | 2021 | Addition | 24.01 | 0 | OHL | 0.03 | 0.46 | 14.52 | 2780 | 2670 | 2480 | 2670
INVE1J | ACHR1R | 2021 | Changed | 21.17 | 0 | OHL | 0.34 | 3.96 | 1.29 | 739 | 710 | 662 | 710
INVE1K | ANSU1- | 2021 | Changed | 11.13 | 0 | OHL | 0.18 | 2.08 | 0.68 | 739 | 710 | 662 | 710
KEIT3- | GLOF3J | 2021 | Removal | 25.5 | 0 | OHL | 62.75 | 83.85 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KEIT3- | KEIT39 | 2021 | Removal | 18.6 | 0 | OHL | 47.61 | 52.76 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
KINT2K | PEHE2Q | 2021 | Removal | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
KINT3- | GLOF3K | 2021 | Removal | 33.7 | 0 | OHL | 82.93 | 115.3 | 0 | 17.1 | 16.3 | 13.7 | 16.3
KINT3- | GOHI3- | 2021 | Removal | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
LOCL1S | MILS1Q | 2021 | Addition | 3.25 | 0 | OHL | 0.16 | 0.67 | 0.18 | 203 | 193 | 176 | 193
PEHE2Q | NEDE2K | 2021 | Addition | 22.39 | 0 | OHL | 0.11 | 0.99 | 5.91 | 1090 | 1030 | 925 | 1030
PEHERSV1 | NEDE2J | 2021 | Addition | 22.39 | 0 | OHL | 0.11 | 0.99 | 5.91 | 1090 | 1030 | 925 | 1030
PORA1Q | ANSU1- | 2021 | Changed | 24.27 | 0 | OHL | 0.39 | 4.54 | 1.48 | 739 | 710 | 662 | 710
PORA1R | ACHR1R | 2021 | Removal | 14.23 | 0 | OHL | 2.02 | 3.34 | 0.69 | 99 | 92 | 79 | 92
PORA1R | PORA1T | 2021 | Addition | 5.6 | 0 | OHL | 0.78 | 1.25 | 0.27 | 99 | 92 | 79 | 92
PORA1S | ACHR1R | 2021 | Addition | 14.23 | 0 | OHL | 0.23 | 2.66 | 0.87 | 739 | 710 | 662 | 710
PORA1S | PORA1U | 2021 | Addition | 5.6 | 0 | OHL | 0.78 | 1.25 | 0.27 | 99 | 92 | 79 | 92
ROTI2J | KINT2J | 2021 | Addition | 23.24 | 0 | OHL | 0.09 | 1.02 | 6.13 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2021 | Addition | 24.97 | 0 | OHL | 0.12 | 1.1 | 6.59 | 1090 | 1030 | 925 | 1030
ROTI2K | KINT2K | 2021 | Addition | 23.24 | 0 | OHL | 0.09 | 1.02 | 6.13 | 1380 | 1320 | 1230 | 1320
ROTI2K | NEDE2K | 2021 | Addition | 24.97 | 0 | OHL | 0.12 | 1.1 | 6.59 | 1090 | 1030 | 925 | 1030
ROTI3- | GLOF3J | 2021 | Addition | 25.5 | 0 | OHL | 62.75 | 83.85 | 0 | 17.1 | 16.3 | 13.7 | 16.3
ROTI3- | GLOF3K | 2021 | Addition | 33.7 | 0 | OHL | 82.93 | 115.3 | 0 | 17.1 | 16.3 | 13.7 | 16.3
ROTI3- | GOHI3- | 2021 | Addition | 0 | 11 | Cable | 38.98 | 58.78 | 1.67 | 29.4 | 26.7 | 26.7 | 26.7
ROTI3- | KEIT39 | 2021 | Addition | 18.6 | 0 | OHL | 47.61 | 52.76 | 0.23 | 17.1 | 16.3 | 13.7 | 16.3
TOMT1K | GLKO1- | 2021 | Addition | 3 | 0 | OHL | 0.4 | 0.67 | 0.16 | 83 | 77 | 67 | 77
CAAD3- | WISL3- | 2023 | Changed | 0 | 85 | Cable | 38.71 | 88.28 | 7.56 | 36 | 36 | 36 | 36
DOUN1- | LIMK1- | 2023 | Addition | 4 | 0 | OHL | 0.36 | 0.86 | 0.22 | 111 | 103 | 89 | 103
GILB1J | GILB1L | 2023 | Addition | 0 | 7.06 | Cable | 0.04 | 0.54 | 12.66 | 348 | 348 | 348 | 348
GILB1K | GILB1M | 2023 | Addition | 0 | 7.06 | Cable | 0.04 | 0.54 | 12.66 | 348 | 348 | 348 | 348
MILS3J | MILS3K | 2023 | Addition | 0 | 5 | Cable | 2.89 | 4.91 | 0.48 | 38 | 38 | 38 | 38
PORA3- | SOUI3- | 2023 | Addition | 50 | 0 | OHL | 129 | 156.2 | 0.73 | 16.9 | 15.7 | 13.5 | 15.7
THUS1J | THUS1L | 2023 | Addition | 0 | 3.03 | Cable | 0.02 | 0.23 | 5.43 | 348 | 348 | 348 | 348
THUS1K | THUS1M | 2023 | Addition | 0 | 3.03 | Cable | 0.02 | 0.23 | 5.43 | 348 | 348 | 348 | 348
THUS1L | GILB1L | 2023 | Addition | 13.1 | 0 | OHL | 0.3 | 2.78 | 0.72 | 463 | 444 | 415 | 444
THUS1M | GILB1M | 2023 | Addition | 13.1 | 0 | OHL | 0.3 | 2.78 | 0.72 | 463 | 444 | 415 | 444
ABNE1S | CHAR1- | 2023 | Addition | 24.5 | 0 | OHL | 2.49 | 5.67 | 1.22 | 132 | 123 | 106 | 123
ABNE1T | BUMU1Q | 2023 | Addition | 17.7 | 0 | OHL | 1.8 | 4.09 | 0.88 | 132 | 123 | 106 | 123
ABNE3- | JAMB3- | 2023 | Addition | 2 | 0 | OHL | 2.12 | 5.82 | 0 | 35.4 | 33.9 | 31.2 | 33.9
ALYT2A | FETT2P | 2023 | Addition | 67.35 | 0 | OHL | 0.3 | 2.8 | 18.32 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2023 | Addition | 16.2 | 0 | OHL | 0.07 | 0.67 | 4.41 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2023 | Addition | 67.35 | 0 | OHL | 0.3 | 2.8 | 18.32 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2023 | Addition | 16.2 | 0 | OHL | 0.07 | 0.67 | 4.41 | 1090 | 1030 | 925 | 1030
BEAU1J | BEAU1R | 2023 | Changed | 0 | 2.4 | Cable | 0.03 | 0.2 | 3.94 | 265 | 263 | 263 | 263
BEAU1K | BEAU1S | 2023 | Changed | 0 | 2.4 | Cable | 0.03 | 0.2 | 3.94 | 265 | 263 | 263 | 263
BEAU1R | INNE1Q | 2023 | Changed | 13.4 | 0 | OHL | 0.68 | 3 | 0.7 | 241 | 230 | 210 | 230
BEAU1S | INNE1R | 2023 | Changed | 13.4 | 0 | OHL | 0.68 | 3 | 0.7 | 241 | 230 | 210 | 230
BROA1Q | EDIN1- | 2023 | Removal | 44.9 | 0 | OHL | 6.01 | 9.96 | 2.33 | 83 | 77 | 67 | 77
BROA1R | EDIN1- | 2023 | Addition | 46.06 | 0 | OHL | 2.3 | 9.53 | 2.58 | 203 | 193 | 176 | 193
BROA1R | FAUG1- | 2023 | Addition | 90.94 | 0 | OHL | 4.55 | 18.83 | 5.09 | 203 | 193 | 176 | 193
BROR3- | KISO3- | 2023 | Addition | 21 | 0 | OHL | 18.9 | 22.68 | 1.72 | 35.4 | 33.9 | 31.2 | 33.9
BUMU1Q | CHAR1- | 2023 | Removal | 38.4999 | 3.7001 | Composite | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
CAAD3J | TANG30 | 2023 | Addition | 17 | 0 | OHL | 6.24 | 16.7 | 2.04 | 53.7 | 48.8 | 47.1 | 48.8
DAAS3- | RTHE3- | 2023 | Addition | 0 | 3.5 | Cable | 3.28 | 3.5 | 0.33 | 37.2 | 30.5 | 30.5 | 30.5
DOUN2A | DOUN2B | 2023 | Addition | 0 | 2 | Cable | 0.01 | 0.05 | 5.31 | 240 | 240 | 240 | 240
DOUN2B | DOUN2C | 2023 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.67 | 240 | 240 | 240 | 240
DOUN2C | FINS2C | 2023 | Addition | 0 | 60 | Cable | 0.82 | 1.61 | 142.3 | 240 | 240 | 240 | 240
DUGR1Q | EDIN1- | 2023 | Changed | 8.99 | 0 | OHL | 0.45 | 1.86 | 0.5 | 203 | 193 | 176 | 193
ELGI1L | NAIR1Q | 2023 | Changed | 33.9 | 0 | OHL | 1.73 | 7.59 | 1.76 | 241 | 230 | 210 | 230
ELGI1M | NAIR1R | 2023 | Changed | 33.9 | 0 | OHL | 1.73 | 7.59 | 1.76 | 241 | 230 | 210 | 230
ELGI1Q | ELGI1L | 2023 | Changed | 0 | 1.8 | Cable | 0.04 | 0.05 | 1.41 | 251 | 252 | 252 | 252
ELGI1Q | KEIT1- | 2023 | Changed | 27.4 | 0 | OHL | 1.4 | 6.14 | 1.43 | 241 | 230 | 210 | 230
ELGI1R | ELGI1M | 2023 | Changed | 0 | 1.8 | Cable | 0.04 | 0.05 | 1.41 | 251 | 252 | 252 | 252
ELGI1R | KEIT1- | 2023 | Changed | 27.4 | 0 | OHL | 1.4 | 6.14 | 1.43 | 241 | 230 | 210 | 230
ELGI3- | MITA3- | 2023 | Addition | 0 | 7 | Cable | 5.21 | 6.75 | 0.71 | 42.4 | 34.8 | 34.8 | 34.8
ELGI3- | MITA3- | 2023 | Addition | 0 | 7 | Cable | 5.21 | 6.75 | 0.71 | 42.4 | 34.8 | 34.8 | 34.8
ELGI3- | SPYW3- | 2023 | Addition | 0 | 8.8 | Cable | 8.25 | 8.81 | 0.82 | 37.2 | 30.5 | 30.5 | 30.5
FERO1S | CRDH1K | 2023 | Addition | 5.02 | 0 | OHL | 0.71 | 1.18 | 0.25 | 99 | 92 | 79 | 92
FETT3S | FEWI3- | 2023 | Addition | 6 | 0 | OHL | 2.74 | 6.11 | 0.66 | 47.9 | 46.9 | 43.4 | 46.9
FINS2A | FINS2B | 2023 | Addition | 0 | 12 | Cable | 0.07 | 0.3 | 31.89 | 240 | 240 | 240 | 240
FINS2B | FINS2C | 2023 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.67 | 240 | 240 | 240 | 240
GLFA3- | PAUL30 | 2023 | Addition | 0 | 12.5 | Cable | 14.93 | 12.98 | 1.06 | 32.6 | 26.7 | 26.7 | 26.7
INNE1Q | NAIR1Q | 2023 | Removal | 29.3 | 0 | OHL | 2.86 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1Q | SLKB1J | 2023 | Addition | 1.97 | 0 | OHL | 0.1 | 0.44 | 0.1 | 241 | 230 | 210 | 230
INNE1T | NAIR1R | 2023 | Removal | 29.3 | 0 | OHL | 2.86 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1T | SLKB1K | 2023 | Addition | 1.97 | 0 | OHL | 0.1 | 0.44 | 0.1 | 241 | 230 | 210 | 230
INVE1J | CRDH1K | 2023 | Addition | 10.19 | 0 | OHL | 1.45 | 2.39 | 0.5 | 99 | 92 | 79 | 92
INVE1J | FERO1S | 2023 | Removal | 15.21 | 0 | OHL | 2.16 | 3.57 | 0.74 | 99 | 92 | 79 | 92
INVE1K | CRDH1J | 2023 | Addition | 10.12 | 0 | OHL | 1.44 | 2.38 | 0.5 | 99 | 92 | 79 | 92
INVE1K | KILC1Q | 2023 | Removal | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
KILC1Q | CRDH1J | 2023 | Addition | 4.98 | 0 | OHL | 0.71 | 1.17 | 0.24 | 99 | 92 | 79 | 92
KINT2J | TEAL2A | 2023 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
KINT2J | TEAL2J | 2023 | Removal | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
KINT2K | FETT2P | 2023 | Changed | 32.15 | 0 | OHL | 0.16 | 1.4 | 8.45 | 1090 | 1030 | 925 | 1030
KINT2K | FETT2Q | 2023 | Changed | 32.15 | 0 | OHL | 0.16 | 1.4 | 8.45 | 1090 | 1030 | 925 | 1030
KINT2K | TEAL2B | 2023 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
KINT2K | TEAL2K | 2023 | Removal | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
LAIR1Q | LOCB1J | 2023 | Addition | 17 | 0 | OHL | 0.4 | 3.71 | 0.9 | 464 | 446 | 414 | 446
LAIR1Q | SHIN1- | 2023 | Removal | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 111 | 103 | 89 | 103
LAIR1R | CREA1- | 2023 | Addition | 22 | 0 | OHL | 2.23 | 5.13 | 1.08 | 132 | 123 | 106 | 123
LAIR1R | LOCB1K | 2023 | Addition | 17 | 0 | OHL | 0.4 | 3.71 | 0.9 | 464 | 446 | 414 | 446
NAIR1Q | SLKB1L | 2023 | Addition | 26.33 | 0 | OHL | 1.34 | 5.9 | 1.37 | 241 | 230 | 210 | 230
NAIR1R | SLKB1M | 2023 | Addition | 26.33 | 0 | OHL | 1.34 | 5.9 | 1.37 | 241 | 230 | 210 | 230
SLKB1J | SLKB1L | 2023 | Addition | 0 | 1.5 | Cable | 0.02 | 0.1 | 2.32 | 306 | 253 | 253 | 253
SLKB1K | SLKB1M | 2023 | Addition | 0 | 1.5 | Cable | 0.02 | 0.1 | 2.32 | 306 | 253 | 253 | 253
TEAL2K | FETT2P | 2023 | Removal | 83.55 | 0 | OHL | 0.42 | 3.65 | 21.99 | 955 | 880 | 760 | 880
ABNE3- | JAMB3- | 2025 | Addition | 2 | 0 | OHL | 2.12 | 5.82 | 0 | 35.4 | 33.9 | 31.2 | 33.9
ARBR3- | ARBS31 | 2025 | Addition | 0 | 3 | Cable | 2.81 | 3 | 0.28 | 31.7 | 28.5 | 28.5 | 28.5
ARBR3- | ARBS31 | 2025 | Addition | 0 | 3 | Cable | 2.81 | 3 | 0.28 | 31.7 | 28.5 | 28.5 | 28.5
BLHI2L | ROTI2J | 2025 | Removal | 35.36 | 0 | OHL | 0.18 | 1.56 | 9.34 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2K | 2025 | Removal | 35.36 | 0 | OHL | 0.18 | 1.56 | 9.34 | 1090 | 1030 | 925 | 1030
BLHI4- | ROTI4J | 2025 | Addition | 35.4 | 0 | OHL | 0.07 | 0.68 | 20.83 | 1980 | 1900 | 1770 | 1900
BLHI4- | ROTI4K | 2025 | Addition | 35.4 | 0 | OHL | 0.07 | 0.68 | 20.83 | 1980 | 1900 | 1770 | 1900
BREC1Q | DENS1Q | 2025 | Addition | 26.1 | 0 | OHL | 2.98 | 5.92 | 1.31 | 255 | 247 | 237 | 247
BREC1Q | FIDD1B | 2025 | Removal | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 2025 | Removal | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BREC1R | DENS1R | 2025 | Addition | 26.1 | 0 | OHL | 2.98 | 5.92 | 1.31 | 255 | 247 | 237 | 247
CAAD3J | CLAG3- | 2025 | Addition | 12 | 0 | OHL | 12.72 | 34.92 | 0 | 33.1 | 31.4 | 28.4 | 31.4
CAAD3J | CLAG3- | 2025 | Addition | 12 | 0 | OHL | 12.72 | 34.92 | 0 | 33.1 | 31.4 | 28.4 | 31.4
CASS1Q | SALA1- | 2025 | Addition | 6 | 0 | OHL | 0.63 | 1.31 | 0.32 | 112 | 104 | 90 | 104
CONN1K | CONN1D | 2025 | Addition | 0.66 | 0.66 | Cable | 0.01 | 0.06 | 0.91 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 2025 | Removal | 76.0713 | 0.2687 | Composite | 0.46 | 4.2 | 16.18 | 702 | 665 | 599 | 665
CORI3J | LLUC31 | 2025 | Addition | 0 | 10 | Cable | 4.68 | 9.64 | 1.02 | 55.8 | 50.6 | 50.6 | 50.6
DENS1Q | TEAL1- | 2025 | Changed | 8.7 | 0 | OHL | 0.99 | 1.97 | 0.44 | 255 | 247 | 237 | 247
DENS1R | TEAL1- | 2025 | Removal | 8.7 | 0 | OHL | 0.34 | 1.91 | 0.46 | 183 | 160 | 149 | 160
DENS1R | TEAL1- | 2025 | Addition | 8.7 | 0 | OHL | 0.99 | 1.97 | 0.44 | 255 | 247 | 237 | 247
DOUN2- | CONN2K | 2025 | Addition | 10.33 | 0 | OHL | 0.06 | 0.57 | 2.19 | 702 | 665 | 599 | 665
DOUN2- | GORW2- | 2025 | Removal | 58.1 | 0 | OHL | 0.35 | 3.2 | 12.32 | 702 | 665 | 599 | 665
DOUN2D | DOUN2E | 2025 | Addition | 0 | 2 | Cable | 0.01 | 0.05 | 5.31 | 240 | 240 | 240 | 240
DOUN2E | DOUN2F | 2025 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.67 | 240 | 240 | 240 | 240
DOUN2F | FINS2F | 2025 | Addition | 0 | 60 | Cable | 0.82 | 1.61 | 142.3 | 240 | 240 | 240 | 240
FIDD1Q | FOGG1R | 2025 | Removal | 25.4 | 0 | OHL | 3 | 6.16 | 1.24 | 112 | 104 | 90 | 104
FIDD2Q | KINT2J | 2025 | Addition | 35.6 | 0 | OHL | 0.22 | 1.9 | 7.84 | 695 | 640 | 550 | 640
FIDD2Q | TEAL2A | 2025 | Addition | 65 | 0 | OHL | 0.39 | 3.46 | 14.31 | 695 | 640 | 550 | 640
FIDD2R | KINT2K | 2025 | Addition | 35.6 | 0 | OHL | 0.22 | 1.9 | 7.84 | 695 | 640 | 550 | 640
FIDD2R | TEAL2B | 2025 | Addition | 65 | 0 | OHL | 0.39 | 3.46 | 14.31 | 695 | 640 | 550 | 640
FINS2D | FINS2E | 2025 | Addition | 0 | 12 | Cable | 0.07 | 0.3 | 31.89 | 240 | 240 | 240 | 240
FINS2E | FINS2F | 2025 | Addition | 0 | 0.5 | Cable | 0.01 | 0.01 | 1.67 | 240 | 240 | 240 | 240
GORW2- | STRB2- | 2025 | Removal | 10.3 | 0 | OHL | 0.06 | 0.57 | 2.18 | 702 | 665 | 599 | 665
GORW2A | CONN2J | 2025 | Addition | 46.57 | 0 | OHL | 0.28 | 2.56 | 9.87 | 702 | 665 | 599 | 665
GORW2A | LOCB2J | 2025 | Addition | 18.7893 | 10.9807 | Composite | 0.18 | 1.64 | 6.31 | 702 | 665 | 599 | 665
KINT2J | TEAL2A | 2025 | Removal | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
KINT2K | TEAL2B | 2025 | Removal | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.14 | 695 | 640 | 550 | 640
MELG1J | GLSH1J | 2025 | Addition | 0 | 0.2 | Cable | 0.01 | 0.02 | 0.27 | 220 | 211 | 211 | 211
MYBS3J | GOLT3- | 2025 | Addition | 14 | 0 | OHL | 14.84 | 40.74 | 0 | 33.2 | 31.4 | 28.4 | 31.4
MYBS3J | GOLT3- | 2025 | Addition | 14 | 0 | OHL | 14.84 | 40.74 | 0 | 33.2 | 31.4 | 28.4 | 31.4
MYBS3M | HALY3- | 2025 | Addition | 5 | 0 | OHL | 2.28 | 5.09 | 0.55 | 47.9 | 43.4 | 43.1 | 43.4
PEHE2Q | NEDE2K | 2025 | Removal | 22.39 | 0 | OHL | 0.11 | 0.99 | 5.91 | 1090 | 1030 | 925 | 1030
PEHE4J | NEDE4J | 2025 | Addition | 22.39 | 0 | OHL | 0.04 | 0.43 | 13.17 | 1980 | 1900 | 1770 | 1900
PEHE4K | NEDE4K | 2025 | Addition | 22.39 | 0 | OHL | 0.04 | 0.43 | 13.17 | 1980 | 1900 | 1770 | 1900
PEHERSV1 | NEDE2J | 2025 | Removal | 22.39 | 0 | OHL | 0.11 | 0.99 | 5.91 | 1090 | 1030 | 925 | 1030
PORA1Q | CRSS1Q | 2025 | Changed | 48.3 | 0 | OHL | 0.77 | 9.03 | 2.95 | 739 | 710 | 662 | 710
PORA1Q | PORA1U | 2025 | Addition | 5.6 | 0 | OHL | 0.78 | 1.25 | 0.27 | 99 | 92 | 79 | 92
PORA1R | ACHR1R | 2025 | Addition | 14.23 | 0 | OHL | 0.23 | 2.66 | 0.87 | 739 | 710 | 662 | 710
PORA1R | CRSS1R | 2025 | Changed | 48.3 | 0 | OHL | 0.77 | 9.03 | 2.95 | 739 | 710 | 662 | 710
PORA1S | ACHR1R | 2025 | Removal | 14.23 | 0 | OHL | 0.23 | 2.66 | 0.87 | 739 | 710 | 662 | 710
PORA1S | PORA1U | 2025 | Removal | 5.6 | 0 | OHL | 0.78 | 1.25 | 0.27 | 99 | 92 | 79 | 92
ROTI2J | KINT2J | 2025 | Removal | 23.24 | 0 | OHL | 0.09 | 1.02 | 6.13 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2025 | Removal | 24.97 | 0 | OHL | 0.12 | 1.1 | 6.59 | 1090 | 1030 | 925 | 1030
ROTI2K | KINT2K | 2025 | Removal | 23.24 | 0 | OHL | 0.09 | 1.02 | 6.13 | 1380 | 1320 | 1230 | 1320
ROTI2K | NEDE2K | 2025 | Removal | 24.97 | 0 | OHL | 0.12 | 1.1 | 6.59 | 1090 | 1030 | 925 | 1030
ROTI4J | KINT4J | 2025 | Addition | 23.2 | 0 | OHL | 0.05 | 0.45 | 13.65 | 1980 | 1900 | 1770 | 1900
ROTI4J | NEDE4J | 2025 | Addition | 24.97 | 0 | OHL | 0.05 | 0.48 | 14.69 | 1980 | 1900 | 1770 | 1900
ROTI4K | KINT4K | 2025 | Addition | 23.2 | 0 | OHL | 0.05 | 0.45 | 13.65 | 1980 | 1900 | 1770 | 1900
ROTI4K | NEDE4K | 2025 | Addition | 24.97 | 0 | OHL | 0.05 | 0.48 | 14.69 | 1980 | 1900 | 1770 | 1900
SHIN1- | LOCB1J | 2025 | Changed | 12.19 | 0 | OHL | 1.39 | 2.77 | 0.61 | 255 | 247 | 237 | 247
SHIN1- | LOCB1K | 2025 | Changed | 12.19 | 0 | OHL | 1.39 | 2.77 | 0.61 | 255 | 247 | 237 | 247
SHIN3- | BRLG3- | 2025 | Addition | 0 | 9.8 | Cable | 3.78 | 9.18 | 1.1 | 53.7 | 48.8 | 48.8 | 48.8
SHIN3- | BRLG3- | 2025 | Addition | 0 | 9.8 | Cable | 3.78 | 9.18 | 1.1 | 53.7 | 48.8 | 48.8 | 48.8
SHIN3- | GLCA3- | 2025 | Addition | 0 | 9.8 | Cable | 3.78 | 9.18 | 1.1 | 53.7 | 48.8 | 48.8 | 48.8
SHIN3- | GLCA3- | 2025 | Addition | 0 | 9.8 | Cable | 3.78 | 9.18 | 1.1 | 53.7 | 48.8 | 48.8 | 48.8
STRB2- | CONN2K | 2025 | Addition | 58.07 | 0 | OHL | 0.35 | 3.19 | 12.31 | 702 | 665 | 599 | 665
STRI3- | BILB3- | 2025 | Addition | 10 | 0 | OHL | 10.6 | 29.1 | 0 | 29.3 | 27.2 | 23.5 | 27.2
STRW13 | STRW17 | 2025 | Addition | 0 | 0.27 | Cable | 0.01 | 0.02 | 0.37 | 200 | 178 | 178 | 178
STRW17 | CONN1D | 2025 | Addition | 12.12 | 0 | OHL | 0.61 | 2.51 | 0.68 | 203 | 193 | 176 | 193
TARL3- | TABS3L | 2025 | Addition | 5 | 0 | OHL | 5.3 | 14.55 | 0 | 35.4 | 33.9 | 31.2 | 33.9
ALYT2A | FETT2P | 2028 | Removal | 67.35 | 0 | OHL | 0.3 | 2.8 | 18.32 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2028 | Removal | 16.2 | 0 | OHL | 0.07 | 0.67 | 4.41 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2K | 2028 | Addition | 16.2 | 0 | OHL | 0.07 | 0.66 | 4.5 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2028 | Removal | 67.35 | 0 | OHL | 0.3 | 2.8 | 18.32 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2J | 2028 | Addition | 16.2 | 0 | OHL | 0.07 | 0.66 | 4.5 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2028 | Removal | 16.2 | 0 | OHL | 0.07 | 0.67 | 4.41 | 1090 | 1030 | 925 | 1030
ALYT4J | FETT4Q | 2028 | Addition | 67.35 | 0 | OHL | 0.13 | 1.3 | 39.62 | 1980 | 1900 | 1770 | 1900
ALYT4K | FETT4R | 2028 | Addition | 67.35 | 0 | OHL | 0.13 | 1.3 | 39.62 | 1980 | 1900 | 1770 | 1900
BERB2Q | CAID2- | 2028 | Addition | 7.99 | 0 | OHL | 0.05 | 0.33 | 2.18 | 935 | 880 | 790 | 880
BERB2Q | CLGO2A | 2028 | Addition | 0.46 | 0 | OHL | 0.01 | 0.02 | 0.13 | 935 | 880 | 790 | 880
BEWF1- | ENEI1- | 2028 | Addition | 34 | 0 | OHL | 1.72 | 7.04 | 1.9 | 162 | 154 | 141 | 154
BLHI1J | ELCH1- | 2028 | Addition | 20 | 0 | OHL | 1 | 4.14 | 1.12 | 203 | 193 | 176 | 193
BLHI2A | CLGO2A | 2028 | Addition | 45.8 | 0 | OHL | 0.26 | 1.89 | 12.49 | 935 | 880 | 790 | 880
BLHI2B | DAAS2- | 2028 | Addition | 33.02 | 0 | OHL | 0.19 | 1.36 | 9 | 935 | 880 | 790 | 880
BLHI2J | BERB2Q | 2028 | Removal | 46.26 | 0 | OHL | 0.26 | 1.9 | 12.61 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 2028 | Removal | 33.02 | 0 | OHL | 0.19 | 1.36 | 9 | 935 | 880 | 790 | 880
CAMW3X | MYBS3K | 2028 | Addition | 0 | 10 | Cable | 4.63 | 11.24 | 1.34 | 53.7 | 48.8 | 48.8 | 48.8
CLOI1- | CLOI11 | 2028 | Addition | 8 | 0 | OHL | 0.26 | 1.74 | 0.42 | 280 | 270 | 245 | 270
COGL4- | COGL4J | 2028 | Addition | 0 | 1.95 | Cable | 0.01 | 0.03 | 9.17 | 930 | 900 | 900 | 900
COGL4- | COGL4K | 2028 | Addition | 0 | 1.95 | Cable | 0.01 | 0.03 | 9.17 | 930 | 900 | 900 | 900
CRSS1J | WILW1- | 2028 | Addition | 10 | 0 | OHL | 0.91 | 2.16 | 0.54 | 132 | 123 | 106 | 123
DAAS2- | CLGO2- | 2028 | Addition | 12.77 | 0 | OHL | 0.07 | 0.53 | 3.48 | 935 | 880 | 790 | 880
FAUG1- | FAUG1M | 2028 | Removal | 0 | 0.29 | Cable | 0.01 | 0.02 | 0.49 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 2028 | Removal | 0 | 0.2 | Cable | 0.01 | 0.02 | 0.34 | 220 | 209 | 209 | 209
FAUG1M | LOCL1Q | 2028 | Removal | 8.5 | 0 | OHL | 0.97 | 1.93 | 0.43 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 2028 | Removal | 8.5 | 0 | OHL | 0.97 | 1.93 | 0.43 | 255 | 247 | 237 | 247
FAUG4J | INGA4K | 2028 | Addition | 8.5 | 0 | OHL | 0.02 | 0.16 | 4.88 | 1940 | 1860 | 1720 | 1860
FAUG4K | INGA4J | 2028 | Addition | 8.5 | 0 | OHL | 0.02 | 0.16 | 4.88 | 1940 | 1860 | 1720 | 1860
FWIL1Q | INGA1J | 2028 | Addition | 34.9 | 0 | OHL | 3.98 | 7.92 | 1.74 | 255 | 247 | 237 | 247
FWIL1Q | LOCL1Q | 2028 | Removal | 34.9 | 0 | OHL | 3.98 | 7.92 | 1.74 | 255 | 247 | 237 | 247
FWIL1R | INGA1K | 2028 | Addition | 34.9 | 0 | OHL | 3.98 | 7.92 | 1.74 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 2028 | Removal | 34.9 | 0 | OHL | 3.98 | 7.92 | 1.74 | 255 | 247 | 237 | 247
INGA1Q | INGA1K | 2028 | Addition | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
INGA1Q | LOCL1Q | 2028 | Removal | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 111 | 103 | 89 | 103
INGA4J | COGL4J | 2028 | Addition | 10 | 0 | OHL | 0.02 | 0.2 | 5.79 | 1470 | 1350 | 1170 | 1350
INGA4K | COGL4K | 2028 | Addition | 10 | 0 | OHL | 0.02 | 0.2 | 5.79 | 1470 | 1350 | 1170 | 1350
KINT2J | PERS2R | 2028 | Changed | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1180 | 1120 | 1020 | 1120
KINT2K | FETT2P | 2028 | Removal | 32.15 | 0 | OHL | 0.16 | 1.4 | 8.45 | 1090 | 1030 | 925 | 1030
KINT2K | FETT2Q | 2028 | Removal | 32.15 | 0 | OHL | 0.16 | 1.4 | 8.45 | 1090 | 1030 | 925 | 1030
KINT2K | PEHE2R | 2028 | Changed | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1180 | 1120 | 1020 | 1120
KINT4J | FETT4Q | 2028 | Addition | 32.15 | 0 | OHL | 0.06 | 0.62 | 18.91 | 1980 | 1900 | 1770 | 1900
KINT4K | FETT4R | 2028 | Addition | 32.15 | 0 | OHL | 0.06 | 0.62 | 18.91 | 1980 | 1900 | 1770 | 1900
KNOC2J | BERB2Q | 2028 | Removal | 46.98 | 0 | OHL | 0.27 | 1.93 | 12.81 | 935 | 880 | 790 | 880
KNOC2J | CAID2- | 2028 | Addition | 38.99 | 0 | OHL | 0.22 | 1.61 | 10.63 | 935 | 880 | 790 | 880
KNOC2K | CLGO2- | 2028 | Addition | 47.45 | 0 | OHL | 0.27 | 1.95 | 12.94 | 935 | 880 | 790 | 880
KNOC2K | DAAS2- | 2028 | Removal | 60.22 | 0 | OHL | 0.34 | 2.48 | 16.42 | 935 | 880 | 790 | 880
MELG1K | CLOI1- | 2028 | Addition | 0 | 0.2 | Cable | 0.01 | 0.03 | 0.54 | 220 | 211 | 211 | 211
PEHE2- | PERS2Q | 2028 | Changed | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1180 | 1120 | 1020 | 1120
PEHG3- | KRTO3- | 2028 | Addition | 0 | 6 | Cable | 2.32 | 5.62 | 0.67 | 53.7 | 48.8 | 48.8 | 48.8
THUS3- | CAIH3- | 2028 | Addition | 0 | 10 | Cable | 4.68 | 9.64 | 1.02 | 55.8 | 50.6 | 50.6 | 50.6

## B-2-2b
Table B.2.2b - SPT Transmission Circuit Changes 2020/21 to 2028/29
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (pu on 100MVA) | X (pu on 100MVA) | B (pu on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
COAL1- | LINM1R | 2020 | Addition | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 130 | 130 | 130 | 130
COAL1A | LINM1Q | 2020 | Addition | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
COCK2- | KAIM2- | 2020 | Change | 18.29 | 0 | OHL | 0.07735 | 0.74704 | 5.0861 | 1120 | 1060 | 990 | 1060
COCK2- | SMEA2- | 2020 | Change | 9.51 | 0 | OHL | 0.040219 | 0.38843 | 2.6445 | 1120 | 1060 | 990 | 1060
COYL2- | COYW2S | 2020 | Change | 1.29 | 0.08 | Composite | 0.0058 | 0.0536 | 0.4557 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 2020 | Change | 1.32 | 0 | OHL | 0.0059 | 0.0543 | 0.3691 | 1500 | 1500 | 1500 | 1500
COYW2S | KILS2- | 2020 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 2020 | Change | 13.37 | 0 | OHL | 0.0597 | 0.5489 | 3.744 | 1500 | 1500 | 1500 | 1500
DUNB1Q | DUNB1S | 2020 | Addition | 0 | 0.15 | Cable | 0.005 | 0.0152 | 0.3194 | 90 | 90 | 90 | 90
DUNB1R | DUNB1T | 2020 | Addition | 0 | 0.15 | Cable | 0.005 | 0.0165 | 0.1478 | 90 | 90 | 90 | 90
KAIM2- | SMEA2- | 2020 | Change | 8.78 | 0 | OHL | 0.0377 | 0.3731 | 2.385 | 1120 | 1060 | 990 | 1060
COAL1A | LINM1Q | 2020 | Removed | 5.774 | 3.14 | OHL | 0.246 | 1.521 | 3.108 | 293 | 293 | 293 | 293
COAL1- | LINM1R | 2020 | Removed | 5.774 | 3.2 | OHL | 0.244 | 1.516 | 3.055 | 130 | 130 | 130 | 130
COAL1- | DONO1- | 2021 | Addition | 0 | 4.5 | Cable | 0.12707 | 0.29209 | 5.5423 | 165 | 165 | 165 | 165
COAL1A | CUMH1A | 2021 | Addition | 0 | 7.5 | Cable | 0.11794 | 0.64566 | 12.3574 | 241 | 241 | 241 | 241
COCK2- | SMEA2- | 2021 | Change | 9.51 | 0 | OHL | 0.040219 | 0.38843 | 2.6445 | 1120 | 1060 | 990 | 1060
CRYR4- | TORN4- | 2021 | Change | 9.36 | 2.1 | Composite | 0.012534 | 0.18573 | 52.4997 | 1400 | 1400 | 1400 | 1400
CUMH1A | CUMH1- | 2021 | Addition | 0 | 0.2 | Cable | 0.003145 | 0.017218 | 0.32953 | 242 | 242 | 242 | 242
CUMH1B | CUMH1- | 2021 | Addition | 0 | 0.2 | Cable | 0.003145 | 0.017218 | 0.32953 | 242 | 242 | 242 | 242
CUMH1B | GAWH1Q | 2021 | Addition | 0 | 3 | Cable | 0.047176 | 0.25826 | 4.9429 | 241 | 241 | 241 | 241
DENN2- | LAMB2T | 2021 | Addition | 32.18 | 0 | OHL | 0.14506 | 1.3095 | 8.9356 | 953 | 882 | 762 | 882
DENN2- | LOAN2- | 2021 | Addition | 21.59 | 0 | OHL | 0.049814 | 0.76944 | 6.8256 | 1500 | 1500 | 1500 | 1500
ELDE1Q | JOHN1Q | 2021 | Change | 0 | 2.79 | Cable | 0.078781 | 0.1811 | 3.4362 | 229 | 211 | 183 | 211
GLGL1Q | SAKN1- | 2021 | Addition | 6.5 | 0 | OHL | 0.48761 | 1.4314 | 0.34188 | 166 | 159 | 147 | 159
GLNI1- | MOSM1B | 2021 | Change | 1.41 | 0.11 | Composite | 0.065378 | 0.23617 | 0.44211 | 171 | 171 | 171 | 171
KAIM2- | SMEA2- | 2021 | Change | 8.78 | 0 | OHL | 0.037131 | 0.35861 | 2.4415 | 1120 | 1060 | 990 | 1060
MIDM1- | DONO1- | 2021 | Addition | 0 | 10.57 | Cable | 0.29846 | 0.68608 | 13.0183 | 158 | 146 | 146 | 146
NECU1- | SOKY1- | 2021 | Addition | 0 | 4.5 | Cable | 0.029184 | 0.26775 | 7.8824 | 242 | 223 | 192 | 223
NNGA2- | NNGA2T | 2021 | Addition | 0 | 12.3 | Cable | 0.093 | 0.447 | 31.794 | 381 | 381 | 381 | 381
NNGA2G | NNGA2T | 2021 | Addition | 0 | 34 | Cable | 0.225 | 0.882 | 87.8859 | 381 | 381 | 381 | 381
NNGB2- | NNGB2T | 2021 | Addition | 0 | 12.3 | Cable | 0.093 | 0.447 | 31.794 | 381 | 381 | 381 | 381
NNGB2G | NNGB2T | 2021 | Addition | 0 | 34 | Cable | 0.225 | 0.882 | 87.8859 | 381 | 381 | 381 | 381
COAL1A | GAWH1Q | 2021 | Removed | 0 | 10.5 | Cable | 0.16512 | 0.90393 | 17.3003 | 241 | 241 | 241 | 241
COAL1- | MIDM1- | 2021 | Removed | 0 | 14.47 | Cable | 0.40859 | 0.93923 | 17.8217 | 158 | 146 | 146 | 146
FIFE1A | WFIE1A | 2021 | Removed | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 100 | 100 | 100
FIFE1B | WFIE1B | 2021 | Removed | 0 | 0.69 | Cable | 0.031 | 0.498 | 1.935 | 130 | 100 | 100 | 100
LAMB2T | LOAN2- | 2021 | Removed | 53.67 | 0.225 | Composite | 0.1948 | 2.0808 | 18.1931 | 795 | 620 | 620 | 620
BENB1- | BENB1B | 2023 | Addition | 3 | 0 | OHL | 0.22505 | 0.66065 | 0.15779 | 167 | 160 | 149 | 160
BENB1B | KEOO1Q | 2023 | Addition | 4 | 0 | OHL | 0.10215 | 0.71045 | 0.25502 | 482 | 445 | 385 | 445
BENB1B | NECU1B | 2023 | Addition | 20.25 | 0 | OHL | 0.51715 | 3.5966 | 1.2911 | 482 | 445 | 385 | 445
BLAH1- | GLGL1- | 2023 | Change | 13.6 | 0.375 | Composite | 0.51536 | 2.926 | 1.6551 | 268 | 246 | 246 | 246
BLAH1- | GLGL1- | 2023 | Change | 13.6 | 0.375 | Composite | 0.51536 | 2.926 | 1.6551 | 268 | 246 | 246 | 246
BROC1- | BROC1T | 2023 | Addition | 3.2 | 0 | OHL | 0.24005 | 0.70469 | 0.16831 | 167 | 160 | 149 | 160
BROC1T | COAL1A | 2023 | Addition | 0 | 3.2 | Cable | 0.026108 | 0.26144 | 5.959 | 293 | 293 | 293 | 123
BROC1T | LINM1Q | 2023 | Addition | 5.774 | 0 | OHL | 0.13731 | 1.3023 | 0.29716 | 416 | 399 | 368 | 399
CHMO1- | MAHI1R | 2023 | Addition | 1.01 | 0 | OHL | 0.075876 | 0.22223 | 0.05319 | 167 | 160 | 149 | 160
DALB2A | DALL2- | 2023 | Addition | 0 | 0.0001 | Cable | 0 | 1e-06 | 0 | 1000 | 1000 | 1000 | 1000
DALB2B | DALL2- | 2023 | Addition | 0 | 0.0001 | Cable | 0 | 1e-06 | 0 | 1000 | 1000 | 1000 | 1000
ECCL1- | GALA1- | 2023 | Addition | 30.58 | 0 | OHL | 2.2946 | 6.9615 | 1.5439 | 166 | 159 | 147 | 159
ECCL1- | GALA1- | 2023 | Addition | 30.14 | 0 | OHL | 2.2615 | 6.8582 | 1.5222 | 166 | 159 | 147 | 159
ENHI1- | NECU1C | 2023 | Addition | 0 | 5 | Cable | 0.14119 | 0.32454 | 6.5687 | 122 | 107 | 107 | 107
GARE1S | WHTL1S | 2023 | Change | 1.68 | 0 | OHL | 0.12606 | 0.37719 | 0.086008 | 167 | 160 | 149 | 160
GARE1T | WHTL1T | 2023 | Change | 1.67 | 0 | OHL | 0.1253 | 0.37486 | 0.085509 | 167 | 160 | 149 | 160
GHPS1- | GLGL1- | 2023 | Addition | 10 | 0 | OHL | 0.37505 | 2.1425 | 0.53778 | 327 | 313 | 293 | 313
GHPS1- | GLGL1- | 2023 | Addition | 10 | 0 | OHL | 0.37505 | 2.1425 | 0.53778 | 327 | 313 | 293 | 313
GLGL1- | SANQ1- | 2023 | Addition | 4 | 0.3 | Composite | 0.30864 | 0.89236 | 0.70569 | 286 | 278 | 272 | 278
GLLE1- | NETS1- | 2023 | Change | 30.04 | 0 | OHL | 2.28 | 6.6936 | 1.5326 | 286 | 278 | 272 | 278
GLLE1- | NETS1- | 2023 | Change | 30.04 | 0 | OHL | 2.28 | 6.6936 | 1.5326 | 286 | 278 | 272 | 278
KEOO1- | KEOO1R | 2023 | Addition | 2.5 | 0 | OHL | 0.2269 | 0.58976 | 0.12138 | 133 | 128 | 119 | 128
KEOO1Q | MARG1Q | 2023 | Addition | 0 | 0.9 | Cable | 0.014153 | 0.077479 | 1.4829 | 241 | 241 | 241 | 241
KEOO1R | LONB1T | 2023 | Addition | 10 | 0 | OHL | 0.53116 | 2.1273 | 0.54561 | 242 | 234 | 217 | 234
KEOO1R | NECU1B | 2023 | Addition | 24.25 | 0 | OHL | 0.6193 | 4.3071 | 1.5461 | 482 | 445 | 385 | 445
KINB2J | KINC2- | 2023 | Change | 10.325 | 0.385 | Composite | 0.046692 | 0.42371 | 7.0632 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2023 | Change | 10.71 | 0 | OHL | 0.0483 | 0.43635 | 2.9716 | 1090 | 1030 | 925 | 1030
LONB1- | LONB1T | 2023 | Addition | 2 | 0 | OHL | 0.15003 | 0.44043 | 0.10519 | 166 | 159 | 147 | 159
LONB1T | LORG1- | 2023 | Addition | 8 | 0 | OHL | 0.60013 | 1.7617 | 0.42078 | 166 | 159 | 147 | 159
MAHI1R | STNO1- | 2023 | Addition | 4.5 | 0 | OHL | 0.33758 | 0.99097 | 0.23669 | 167 | 160 | 146 | 160
MARG1- | MARG1Q | 2023 | Addition | 10.1 | 0 | OHL | 0.50518 | 2.1466 | 0.55178 | 241 | 230 | 210 | 230
MOFF1- | SCOP1- | 2023 | Addition | 0 | 10 | Cable | 0.072257 | 0.82323 | 40.4522 | 280 | 280 | 280 | 280
MOFF1- | SCOP1- | 2023 | Addition | 0 | 10 | Cable | 0.072257 | 0.82323 | 40.4522 | 280 | 280 | 280 | 280
WHTB1S | WHTL1S | 2023 | Change | 2.05 | 0 | OHL | 0.15381 | 0.46016 | 0.10497 | 167 | 160 | 149 | 160
WHTB1T | WHTL1T | 2023 | Change | 2.05 | 0 | OHL | 0.15381 | 0.46016 | 0.10497 | 167 | 160 | 149 | 160
COAL1A | LINM1Q | 2023 | Removed | 5.774 | 3.2 | Composite | 0.16342 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
ECCL1- | GALA1- | 2023 | Removed | 31.37 | 0 | OHL | 2.8465 | 7.3431 | 1.534 | 132 | 123 | 106 | 123
MARG1- | NECU1B | 2023 | Removed | 34.35 | 0.9 | Composite | 1.1434 | 6.7098 | 3.5381 | 241 | 230 | 210 | 230
KEOO1- | NECU1B | 2023 | Removed | 26.51 | 0 | OHL | 0.8292 | 5.0188 | 1.6132 | 133 | 123 | 106 | 123
ECCL1- | GALA1- | 2023 | Removed | 30.94 | 0 | OHL | 2.8128 | 7.1065 | 1.5419 | 132 | 123 | 106 | 123
BENB3- | TORH3- | 2025 | Addition | 12 | 0 | OHL | 9.6107 | 35.1006 | 0.048055 | 48 | 48 | 48 | 48
BRNX4- | CRYR4- | 2025 | Addition | 13.86 | 0 | OHL | 0.017779 | 0.25427 | 8.5869 | 2522 | 2397 | 2189 | 2397
BRNX4- | ECCL4A | 2025 | Addition | 34.2 | 0 | OHL | 0.044184 | 0.64033 | 20.975 | 2771 | 2674 | 2480 | 2674
BRNX4- | ECCL4B | 2025 | Addition | 34.2 | 0 | OHL | 0.044184 | 0.64033 | 20.975 | 2771 | 2674 | 2480 | 2674
BRNX4- | SMEA4Q | 2025 | Addition | 58.82 | 0 | OHL | 0.076946 | 1.1404 | 35.1287 | 2473 | 2349 | 2148 | 2349
BRNX4- | TORN4- | 2025 | Addition | 0 | 2.1 | Cable | 0.000528 | 0.014019 | 46.7008 | 1040 | 900 | 900 | 900
BRNX4- | TORN4- | 2025 | Addition | 0 | 1.94 | Cable | 0.000487 | 0.012951 | 43.1426 | 945 | 800 | 800 | 800
CAFA1Q | KEOO1- | 2025 | Change | 2.58 | 0 | OHL | 0.19796 | 0.56816 | 0.1357 | 135 | 130 | 121 | 130
CHAP1- | HAKB1- | 2025 | Change | 14.72 | 0 | OHL | 1.1184 | 3.1888 | 0.77795 | 284 | 263 | 227 | 263
ELVA1- | NLEI1- | 2025 | Addition | 14 | 0 | OHL | 0.74363 | 2.9782 | 0.76385 | 226 | 209 | 181 | 209
FASI1- | FASI1T | 2025 | Addition | 2.6 | 0 | OHL | 0.19755 | 0.56324 | 0.13741 | 284 | 262 | 227 | 262
FASI1T | HAWI1- | 2025 | Addition | 19.11 | 0 | OHL | 1.7313 | 4.1776 | 1.0002 | 161 | 155 | 144 | 155
GLLE1- | TONG1- | 2025 | Change | 33.1 | 0 | OHL | 2.0121 | 7.3466 | 1.7169 | 163 | 150 | 127 | 150
GLLE1- | TONG1- | 2025 | Addition | 33.1 | 0 | OHL | 2.0121 | 7.3466 | 1.7169 | 163 | 150 | 127 | 150
GRNA1- | FASI1T | 2025 | Addition | 36.24 | 0 | OHL | 2.7565 | 7.9411 | 1.897 | 284 | 278 | 270 | 278
GRNA1- | JUNV1- | 2025 | Change | 4.74 | 0 | OHL | 0.35903 | 1.1333 | 0.2315 | 167 | 164 | 159 | 164
KENN1- | COAL1A | 2025 | Addition | 15.4 | 2 | Composite | 1.2117 | 3.5211 | 3.2733 | 167 | 161 | 150 | 161
KEOO1- | GLLE1- | 2025 | Addition | 7.68 | 0 | OHL | 0.19932 | 1.4827 | 0.45961 | 482 | 445 | 385 | 445
KEOO1- | KEOO1R | 2025 | Change | 6.2 | 0 | OHL | 0.16091 | 1.197 | 0.37104 | 482 | 445 | 385 | 445
KEOO1Q | GLLE1- | 2025 | Addition | 13.88 | 0 | OHL | 0.36023 | 2.6797 | 0.83065 | 482 | 445 | 385 | 445
SMEA4Q | WISH4- | 2025 | Addition | 61.77 | 0 | OHL | 0.12654 | 1.2657 | 34.9519 | 1995 | 1926 | 1787 | 1926
SMEA4R | WISH4- | 2025 | Change | 61.77 | 0 | OHL | 0.12654 | 1.2657 | 34.9519 | 1995 | 1926 | 1787 | 1926
STHA4A | WISH4- | 2025 | Change | 11.6 | 0 | OHL | 0.023652 | 0.23742 | 6.6044 | 1995 | 1926 | 1787 | 1926
STHA4B | WISH4- | 2025 | Addition | 13.99 | 0 | OHL | 0.028501 | 0.28543 | 7.9774 | 1995 | 1926 | 1787 | 1926
SMEA4Q | STHA4B | 2025 | Removed | 75.76 | 0 | OHL | 0.16054 | 1.4592 | 44.5196 | 1390 | 1280 | 1110 | 1280
ECCL4B | TORN4- | 2025 | Removed | 34.2 | 2.1 | Composite | 0.044397 | 0.64143 | 67.8893 | 2330 | 1840 | 1840 | 1840
ELVA4- | STHA4A | 2025 | Removed | 48.56 | 0 | OHL | 0.084978 | 0.92036 | 29.0717 | 2210 | 2130 | 1980 | 2130
CRYR4- | TORN4- | 2025 | Removed | 9.36 | 2.1 | Composite | 0.012534 | 0.18573 | 52.4997 | 1400 | 1400 | 1400 | 1400
SMEA4Q | TORN4- | 2025 | Removed | 54.32 | 1.94 | Composite | 0.071618 | 1.0286 | 71.6778 | 900 | 760 | 760 | 760
DUMF1- | TONG1Q | 2025 | Removed | 0 | 43.58 | Cable | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
GLLE1- | KEOO1- | 2025 | Removed | 7.68 | 0 | OHL | 0.69633 | 1.6715 | 0.4063 | 132 | 123 | 106 | 123
ECCL4A | TORN4- | 2025 | Removed | 34.2 | 2.1 | Composite | 0.044397 | 0.64143 | 67.8893 | 2330 | 1840 | 1840 | 1840
GRNA1- | HAWI1- | 2025 | Removed | 55.35 | 0 | OHL | 4.9794 | 12.4863 | 2.7913 | 132 | 123 | 106 | 123
BONN2- | DENN2- | 2028 | Addition | 3.25 | 1 | Composite | 0.015199 | 0.17709 | 6.0833 | 1372 | 1324 | 1228 | 1324
BONN2- | NEAR2T | 2028 | Addition | 17 | 0 | OHL | 0.073942 | 0.77855 | 4.3296 | 1372 | 1324 | 1228 | 1324
BONN4- | DENN4- | 2028 | Addition | 3.25 | 0.75 | Composite | 0.00687 | 0.075358 | 18.43 | 1995 | 1926 | 1786 | 1926
BONN4- | WISH4- | 2028 | Addition | 40.36 | 0 | OHL | 0.082973 | 0.87365 | 21.7471 | 1995 | 1926 | 1786 | 1926
BRNX4A | BRNX4- | 2028 | Addition | 0 | 0.25 | Cable | 0 | 2e-06 | 0 | 6928 | 6928 | 6928 | 6928
COAL4A | ELVN4- | 2028 | Addition | 26.77 | 0 | OHL | 0.046846 | 0.50737 | 16.0266 | 2210 | 2130 | 1980 | 2130
COAL4A | STHA4A | 2028 | Addition | 21.79 | 0 | OHL | 0.038132 | 0.41299 | 13.045 | 2210 | 2130 | 1980 | 2130
GHPS1- | ELVN1- | 2028 | Addition | 25 | 0 | OHL | 0.64884 | 4.8265 | 1.4961 | 482 | 445 | 385 | 445
GHPS1- | ELVN1- | 2028 | Addition | 25 | 0 | OHL | 0.64884 | 4.8265 | 1.4961 | 482 | 445 | 385 | 445
KINB4J | KINC4A | 2028 | Addition | 10.5 | 0 | OHL | 0.022944 | 0.22135 | 5.8026 | 1590 | 1500 | 1350 | 1500
KINB4K | KINC4S | 2028 | Addition | 10.15 | 0 | OHL | 0.022189 | 0.21434 | 5.6016 | 1590 | 1500 | 1350 | 1500
KINC4B | KINC4S | 2028 | Addition | 0 | 0.35 | Cable | 0.000176 | 0.004673 | 3.8917 | 1590 | 1500 | 1350 | 1500
NEAR2T | EERH2- | 2028 | Addition | 7.74 | 0 | OHL | 0.033247 | 0.32887 | 2.0967 | 1372 | 1306 | 1192 | 1306
NEAR2T | NEAR2Q | 2028 | Addition | 7.6 | 0 | OHL | 0.033056 | 0.34806 | 1.9356 | 1372 | 1324 | 1228 | 1324
BONN2B | DENN2- | 2028 | Removed | 3.812 | 0.46 | Composite | 0.018312 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
KINB2K | KINC2- | 2028 | Removed | 10.71 | 0 | OHL | 0.0483 | 0.43635 | 2.9716 | 1090 | 1030 | 925 | 1030
BONN2A | DENN2- | 2028 | Removed | 3.812 | 0.55 | Composite | 0.018312 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
KINB2J | KINC2- | 2028 | Removed | 10.325 | 0.385 | Composite | 0.046692 | 0.42371 | 7.0632 | 1090 | 1030 | 925 | 1030
NEAR2Q | WISH2- | 2028 | Removed | 16.1 | 0 | OHL | 0.07257 | 0.65499 | 4.4712 | 955 | 885 | 760 | 885
EERH2- | NEAR2Q | 2028 | Removed | 0 | 15.34 | Cable | 0.077 | 0.632 | 4.283 | 1500 | 1500 | 1500 | 1500

## B-2-2c
B.2.2c - NGET Transmission Circuit Changes 2020/21 to 2028/2029
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BEDD21 | WIMB21 | 2020 | Change | 8.5 | 0.968 | Composite | 0.0412 | 0.3922 | 10.7954 | 1100 | 1100 | 1100 | 1100
BEDD23 | WIMB21 | 2020 | Change | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 1100 | 1100 | 1100 | 1100
BOTW41 | CHIL41 | 2020 | Addition | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 1109 | 1109 | 901 | 1109
BOTW41 | FAWL41 | 2020 | Removed | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 1109 | 901 | 1109
BRLE41 | FLEE41 | 2020 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3820 | 3820 | 2217 | 3820
BRLE41 | FLEE41 | 2020 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3820 | 3820 | 2217 | 3820
CHIL41 | FAWL41 | 2020 | Addition | 0 | 3.57 | Cable | 0.0018 | 0.0112 | 109.0992 | 1109 | 901 | 901 | 901
CHIL41 | FAWL41 | 2020 | Addition | 0 | 3.57 | Cable | 0.0036 | 0.0225 | 54.5496 | 1109 | 901 | 901 | 901
CHIL41 | LOVE41 | 2020 | Addition | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 1109 | 901 | 901 | 901
CILF41 | RASS41 | 2020 | Change | 26.901 | 0 | OHL | 0.0295 | 0.491 | 17.0223 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 2020 | Change | 25.011 | 0 | OHL | 0.0273 | 0.4458 | 16.1543 | 2779 | 2568 | 2217 | 2568
FAWL41 | LOVE41 | 2020 | Removed | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 1109 | 901 | 1109
FLEE41 | LOVE41 | 2020 | Change | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3100 | 3100 | 1979 | 3100
FLEE41 | LOVE41 | 2020 | Change | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3100 | 3100 | 1979 | 3100
HARK41 | HAKB4B | 2020 | Removed | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2170 | 2170 | 2170 | 2170
KEMS41 | LOFI4A | 2020 | Change | 38.035 | 0 | OHL | 0.0594 | 0.733 | 22.7097 | 3070 | 1832 | 1674 | 1832
KEMS41 | LOFI4B | 2020 | Change | 37.572 | 0 | OHL | 0.0587 | 0.7235 | 22.4507 | 3070 | 1832 | 1674 | 1832
KINO41 | NFLE41 | 2020 | Change | 23.626 | 0 | OHL | 0.0249 | 0.4177 | 15.452 | 3102 | 2935 | 2692 | 2935
LITT41 | LOFI4A | 2020 | Change | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3070 | 1284 | 1108 | 1284
LITT41 | LOFI4B | 2020 | Change | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3070 | 1284 | 1108 | 1284
PEMB41 | WALH41 | 2020 | Change | 217.727 | 5.468 | parallel Composite | 0.2373 | 3.8184 | 207.0444 | 2779 | 2568 | 2217 | 2568
RASS41 | WALH41 | 2020 | Change | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2848 | 109.657 | 2779 | 2568 | 2217 | 2568
SING41 | KINO41 | 2020 | Change | 17.685 | 0 | OHL | 0.0157 | 0.3038 | 11.8869 | 3820 | 3820 | 2510 | 3820
STEW21 | STEW21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 854 | 854 | 854 | 854
STEW21 | STEW21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 854 | 854 | 854 | 854
STEW21 | STEW21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 854 | 854 | 854 | 854
STEW21 | STEW21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 854 | 854 | 854 | 854
WASF2A | WASF21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 1521 | 1521 | 1521 | 1521
WASF2A | WASF21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 1521 | 1521 | 1521 | 1521
WASF2B | WASF21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 1521 | 1521 | 1521 | 1521
WASF2B | WASF21 | 2020 | Addition | 0 | 0 | Series Reactor (Power Control Device) | 0 | 0.8402 | 0 | 1521 | 1521 | 1521 | 1521
BEDD21 | WIMB21 | 2021 | Change | 8.5 | 0.968 | Composite | 0.000409 | 0.003915 | 0.117 | 859 | 830 | 715 | 830
BEDD23 | WIMB21 | 2021 | Change | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 930
CILF41 | RASS41 | 2021 | Change | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 2021 | Change | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568
KINO41 | NFLE41 | 2021 | Change | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
PEMB41 | WALH41 | 2021 | Change | 217.727 | 5.468 | parallel Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568
RASS41 | WALH41 | 2021 | Change | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568
SING41 | KINO41 | 2021 | Change | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748
CELL41 | DRAK41 | 2023 | Change | 45.704 | 0 | OHL | 0.0714 | 0.8801 | 27.3086 | 2175 | 2069 | 1890 | 2069
CELL41 | DRAK41 | 2023 | Change | 45.012 | 0 | OHL | 0.0703 | 0.8668 | 26.8964 | 2175 | 2069 | 1890 | 2069
HATL21 | HARM21 | 2023 | Change | 13.983 | 0 | OHL | 0.000472 | 0.005702 | 0.039648 | 1093 | 1010 | 910 | 1010
HAWP21 | NORT21 | 2023 | Removed | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 874
HAWP41 | NORT41 | 2023 | Change | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 2550 | 2421 | 2211 | 2421
HAWP21 | HATL21 | 2023 | Addition | 31.443 | 0 | OHL | 0.001066 | 0.012811 | 0.089228 | 1090 | 1010 | 910 | 1010
HAWP21 | OFFE21 | 2023 | Change | 9.514 | 0 | OHL | 0.000379 | 0.003948 | 0.026412 | 1093 | 1010 | 910 | 1010
KENG41 | SJOW41 | 2023 | Change | 0 | 6 | Cable | 0.0027 | 0.0473 | 43.6608 | 2000 | 1730 | 1600 | 1730
KENG41 | SJOW41 | 2023 | Change | 0 | 6 | Cable | 0.0027 | 0.0473 | 43.6608 | 2000 | 2000 | 2000 | 2000
KENG41 | WLSD41 | 2023 | Change | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1730 | 1600 | 1730
KENG41 | WLSD42 | 2023 | Change | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1730 | 1600 | 1730
LACK41 | NORT41 | 2023 | Change | 22.443 | 0.25 | Composite | 0.000387 | 0.00448 | 0.16178 | 3100 | 3050 | 2790 | 3050
NORT21 | SALH21 | 2023 | Change | 12.178 | 0 | OHL | 0.000431 | 0.005178 | 0.032966 | 1372 | 1330 | 1240 | 1330
NORT41 | HAWP41 | 2023 | Addition | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 2780 | 2730 | 2500 | 2730
OFFE21 | WBOL21 | 2023 | Change | 8.207 | 0 | OHL | 0.000327 | 0.003406 | 0.022784 | 1093 | 1010 | 910 | 1010
RAYL41 | TILB4A | 2023 | Change | 20.499 | 0 | OHL | 0.000319 | 0.003933 | 0.12301 | 3100 | 3050 | 2790 | 3050
THTO41 | THTO42 | 2023 | Addition | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 2470 | 2470 | 2470 | 2470
THTO41 | THTO43 | 2023 | Addition | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 2470 | 2470 | 2470 | 2470
WBOL21 | HAWP21 | 2023 | Addition | 17.721 | 0 | OHL | 0.000705 | 0.007355 | 0.049196 | 1090 | 1010 | 910 | 1010
WIMB12 | WIMB11 | 2023 | Addition | 0 | 0 | Series Reactor | 0.2468 | 19.8333 | 0 | 90 | 90 | 90 | 90
WIMB12 | WIMB11 | 2023 | Addition | 0 | 0 | Series Reactor | 0.2468 | 19.8333 | 0 | 90 | 90 | 90 | 90
SJOW21 | TOTT24 | 2023 | Removed | 0 | 16.508 | Cable | 0.000297 | 0.003632 | 1.7944 | 868 | 830 | 715 | 830
SJOW21 | TOTT23 | 2023 | Removed | 0 | 16.368 | Cable | 0.000295 | 0.003601 | 1.7792 | 868 | 830 | 715 | 830
HATL21 | WBOL21 | 2023 | Removed | 49.164 | 0 | OHL | 0.001929 | 0.020384 | 0.13673 | 1093 | 1010 | 910 | 1010
BRFO41 | NORM41 | 2025 | Change | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 3820 | 1500 | 1346 | 1500
BRFO41 | NORM41 | 2025 | Change | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 3820 | 1500 | 1346 | 1500
BRAI4A | BRFO41 | 2028 | Change | 49.699 | 0 | OHL | 0.0443 | 0.8539 | 33.3859 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 2028 | Change | 53.678 | 0 | OHL | 0.0582 | 0.9335 | 35.3912 | 2779 | 2568 | 2217 | 2568
BRAI4B | PELH41 | 2028 | Removed | 65.942 | 0 | OHL | 0.065 | 1.1398 | 43.92 | 2779 | 2568 | 2217 | 2568
BRFO41 | BRAI4B | 2028 | Addition | 48.267 | 0 | OHL | 0.0428 | 0.829 | 32.4419 | 2779 | 2568 | 2217 | 2568
BRFO41 | FRIN41 | 2028 | Change | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568
BRFO41 | FRIN41 | 2028 | Change | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2780 | 2570 | 2220 | 2570
BRFO41 | PELH41 | 2028 | Addition | 69.301 | 0 | OHL | 0.0701 | 1.1997 | 46.0176 | 2780 | 2935 | 2765 | 2935
BRFO41 | PELH41 | 2028 | Change | 69.301 | 0 | OHL | 0.0701 | 1.1997 | 46.0176 | 2780 | 2935 | 2765 | 2935
FRIN41 | BRFO41 | 2028 | Addition | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2780 | 2569 | 2217 | 2569
FRIN41 | BRFO41 | 2028 | Addition | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2569
FRIN41 | SIZE41 | 2028 | Addition | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568
FRIN41 | SIZE41 | 2028 | Addition | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2780 | 2568 | 2217 | 2568
HIKP41 | HIKP42 | 2028 | Addition | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2000 | 2000 | 2000 | 2000
HIKP41 | PURI4B | 2028 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 3050 | 2790 | 3050
HIKP41 | TAUN41 | 2028 | Addition | 27.644 | 0 | OHL | 0.0503 | 0.55 | 16.0209 | 2210 | 2160 | 1860 | 2160
HIKP41 | TAUN42 | 2028 | Addition | 27.657 | 0 | OHL | 0.0503 | 0.5503 | 16.0284 | 2210 | 2160 | 1860 | 2160
HIKP42 | PURI4A | 2028 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 3050 | 2790 | 3050
HINP21 | BRWA2B | 2028 | Removed | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 762 | 762 | 619 | 762
HINP22 | BRWA2A | 2028 | Removed | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 767 | 620 | 767
HINP41 | HIKP41 | 2028 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 2210 | 2160 | 1860 | 2160
HINP41 | HIKP41 | 2028 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 2210 | 2160 | 1860 | 2160
HINP41 | SAFO41 | 2028 | Addition | 24.54 | 8.15 | Composite | 0.0376 | 0.5627 | 203.1782 | 3070 | 3050 | 2790 | 3050
HINP41 | SEAB41 | 2028 | Addition | 53.385 | 8.15 | Composite | 0.0697 | 1.1063 | 220.9169 | 3100 | 3050 | 2790 | 3050
HINP41 | TAUN41 | 2028 | Removed | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1979 | 2125
HINP41 | MELK41 | 2028 | Removed | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | MELK41 | 2028 | Removed | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | TAUN42 | 2028 | Removed | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1979 | 2125
LEIS1A | FRIN41 | 2028 | Change | 6.8 | 0 | OHL | 0.0074 | 0.1183 | 4.4826 | 2780 | 2780 | 2780 | 2780
LOFI4A | SELL41 | 2028 | Addition | 66 | 4 | Composite | 0.0608 | 1.1838 | 94.7095 | 3300 | 3050 | 2790 | 3050
LOFI4B | SELL41 | 2028 | Addition | 66 | 4 | Composite | 0.0608 | 1.1838 | 94.7095 | 3300 | 3050 | 2790 | 3050
MELK41 | PURI4A | 2028 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 3100 | 3050 | 2790 | 3050
MELK41 | PURI4B | 2028 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 3100 | 3050 | 2790 | 3050
OSBA41 | EGGB42 | 2028 | Addition | 33 | 0 | OHL | 0.0431 | 0.6343 | 19.8755 | 2780 | 2730 | 2500 | 2730
OSBA42 | EGGB41 | 2028 | Addition | 33 | 0 | OHL | 0.0431 | 0.6343 | 19.8755 | 2780 | 2730 | 2500 | 2730
PURI4A | BRIW41 | 2028 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 3100 | 3050 | 2790 | 3050
PURI4B | BRIW41 | 2028 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 3100 | 3050 | 2790 | 3050
SAFO41 | SEAB41 | 2028 | Addition | 28.845 | 0 | OHL | 0.0322 | 0.5436 | 17.7387 | 3070 | 3050 | 2790 | 3050
SIZE41 | FRIN41 | 2028 | Change | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568

## B-2-2d
B.2.2d - OFTO Transmission Circuit Changes 2020/21 to 2028/2029
OFTO | Site | Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage (kV)
Triton Knoll Offshore Wind Farm Ltd | Triton Knoll | TKNO21 | TKNW21 | 2020 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | TBC | 220
" | Triton Knoll | TKNO21 | TKNE21 | 2020 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | TBC | 400
" | Triton Knoll | BICF41 | TKNO41 | 2020 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | TBC | 400
" | Triton Knoll | BICF41 | TKNO41 | 2020 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | TBC | 220
Breesea Limited | Hornsea 2A | HOWB2 | HOWR2B | 2021 | Addition | 0 | 103.4 | Cable | 0.6 | 2.457 | 348.037 | TBC | 220
" | Hornsea 2A | HOWR2B | HOWW2D | 2021 | Addition | 0 | 62.2 | Cable | 0.434 | 1.544 | 170.92 | TBC | 220
Soundmark Wind Limited | Hornsea 2B | HOWB2 | HOWR2B | 2021 | Addition | 0 | 103.55 | Cable | 0.601 | 2.461 | 348.479 | TBC | 220
" | Hornsea 2B | HOWR2B | HOWW2D | 2021 | Addition | 0 | 61.6 | Cable | 0.42992 | 1.5294 | 169.2655 | TBC | 220
Moray Offshore Windfarm (East) Ltd | Moray Firth (MORL) | NEDE21 | MORF21 | 2021 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 275
" | Moray Firth (MORL) | NEDE21 | MORF21 | 2021 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 275
" | Moray Firth (MORL) | NEDE21 | MORF21 | 2021 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 275
" | Moray Firth (MORL) | MORF21 | MOWE21 | 2021 | Addition | 0 | 101 | Cable | TBC |  |  | TBC | 220
" | Moray Firth (MORL) | MORF21 | MOWE21 | 2021 | Addition | 0 | 94 | Cable | TBC |  |  | TBC | 220
" | Moray Firth (MORL) | MORF21 | MOWW21 | 2021 | Addition | 0 | 94.5 | Cable | TBC |  |  | TBC | 220
Sonningmay Wind Limited | Hornsea 2C | HOWB2 | HOWR2B | 2023 | Addition | 0 | 103.7 | Cable | 0.602 | 2.465 | 348.922 | TBC | 220
" | Hornsea 2C | HOWR2B | HOWW2D | 2023 | Addition | 0 | 60.2 | Cable | 0.42 | 1.495 | 165.428 | TBC | 220
Seagreen Wind Energy Ltd | Firth of Forth I | PHASE 1 Onshore 275kV | TEAL21 | 2023 | Addition | 0 | 0.5 | Cable | TBC |  |  | TBC | 275
" | Firth of Forth I | PHASE 1 Onshore 275kV | TEAL21 | 2023 | Addition | 0 | 0.5 | Cable | TBC |  |  | TBC | 275
" | Firth of Forth I | PHASE 1 Onshore 275kV | TEAL21 | 2023 | Addition | 0 | 0.5 | Cable | TBC |  |  | TBC | 275
" | Firth of Forth I | Offshore PLATFORM 1 | PHASE 1 Onshore 275kV | 2023 | Addition | 0 | 77.12 | Cable | TBC |  |  | TBC | 275
" | Firth of Forth I | Offshore PLATFORM 2 | PHASE 1 Onshore 275kV | 2023 | Addition | 0 | 82.96 | Cable | TBC |  |  | TBC | 275
" | Firth of Forth I | Offshore PLATFORM 3 | PHASE 1 Onshore 275kV | 2023 | Addition | 0 | 88.74 | Cable | TBC |  |  | TBC | 275
East Anglia THREE Limited | East Anglia 3A | BRFO41 | Onshore HVDC Converter station | 2023 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 400
" | East Anglia 3A | Onshore HVDC Converter station | Offshore HVDC Converter station | 2023 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 320
" | East Anglia 3A | Offshore HVDC Converter station | Offshore platform A | 2023 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 220
" | East Anglia 3B | Offshore HVDC Converter station | Offshore platform B | 2025 | Addition | 0 | TBC | Cable | TBC |  |  | TBC | 220
Moray Offshore Windfarm (West) Limited | Moray Offshore (WDA) | BLHI4 | Moray Onshore 400kV | 2025 | Addition | 0 | 0.5 | Cable | TBC |  |  | TBC | 400
" | Moray Offshore (WDA) | BLHI4 | Moray Onshore 400kV | 2025 | Addition | 0 | 0.5 | Cable | TBC |  |  | TBC | 400
" | Moray Offshore (WDA) | Moray Onshore 220kV | Moray Offshore 220kV | 2025 | Addition | 0 | 72 | Cable | TBC |  |  | TBC | 220
" | Moray Offshore (WDA) | Moray Onshore 220kV | Moray Offshore 220kV | 2025 | Addition | 0 | 72 | Cable | TBC |  |  | TBC | 220
Seagreen Wind Energy Ltd | Firth of Forth 2 | PHASE 2 Onshore 400kV | BRXT4 | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 400
" | Firth of Forth 2 | PHASE 2 Onshore 400kV | BRXT4 | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 400
" | Firth of Forth 2 | PHASE 2 Onshore 400kV | BRXT4 | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 400
" | Firth of Forth 2 | PHASE 2 Onshore 400kV | BRXT4 | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 400
" | Firth of Forth 2 | PHASE 2 Onshore 400kV | BRXT4 | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 400
" | Firth of Forth 2 | PHASE 2 Onshore 400kV | BRXT4 | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 400
" | Firth of Forth 2 | PHASE 2 Onshore 275kV | Offshore platform 275kV | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 275
" | Firth of Forth 2 | PHASE 2 Onshore 275kV | Offshore platform 275kV | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 275
" | Firth of Forth 2 | PHASE 2 Onshore 275kV | Offshore platform 275kV | 2025 | Addition | TBC |  |  | TBC |  |  | TBC | 275
" | Firth of Forth 2 | PHASE 2 Onshore 275kV | Offshore platform 275kV | 2028 | Addition | TBC |  |  | TBC |  |  | TBC | 275
" | Firth of Forth 2 | PHASE 2 Onshore 275kV | Offshore platform 275kV | 2028 | Addition | TBC |  |  | TBC |  |  | TBC | 275
" | Firth of Forth 2 | PHASE 2 Onshore 275kV | Offshore platform 275kV | 2028 | Addition | TBC |  |  | TBC |  |  | TBC | 275
Orsted Hornsea Project Three Uk Ltd | Hornsea 3A | HVDC Onshore 400kV | HVDC Offshore 400kV | 2025 | Addition | 0 | 220 | Cable | 0.0202 | TBC |  | TBC | 400
" | Hornsea 3A | HVDC Onshore 400kV | HVDC Offshore 400kV | 2025 | Addition | 0 | 220 | Cable | 0.0202 | TBC |  | TBC | 400
" | Hornsea 3A | HVDC Onshore 400kV | HVDC Offshore 400kV | 2025 | Addition | 0 | 220 | Cable | 0.0202 | TBC |  | TBC | 400
" | Hornsea 3A | NORM4 | HVDC Onshore 400kV | 2025 | Addition | 0 | 1.8 | Cable | 0.0102 | 0.3404 | 71.94 | TBC | 400
" | Hornsea 3B | HVDC Onshore 400kV | HVDC Offshore 400kV | 2025 | Addition | 0 | 220 | Cable | 0.0202 | TBC |  | TBC | 400
" | Hornsea 3B | HVDC Onshore 400kV | HVDC Offshore 400kV | 2025 | Addition | 0 | 220 | Cable | 0.0202 | TBC |  | TBC | 400
" | Hornsea 3B | HVDC Onshore 400kV | HVDC Offshore 400kV | 2025 | Addition | 0 | 220 | Cable | 0.0202 | TBC |  | TBC | 400
" | Hornsea 3B | NORM4 | HVDC Onshore 400kV | 2025 | Addition | 0 | 1.8 | Cable | 0.0102 | 0.3404 | 71.94 | TBC | 400
Orsted Hornsea Project Four Limited | Hornsea 4 | Onshore 275kV | Reactivs Comp S/S 275kV | 2028 | Addition | 0 | 59 | Cable | 0.04866 | 0.2257 | 139.1726 | TBC | 275
" | Hornsea 4 | Onshore 275kV | Reactivs Comp S/S 275kV | 2028 | Addition | 0 | 59 | Cable | 0.04866 | 0.2257 | 139.1726 | TBC | 275
" | Hornsea 4 | Onshore 275kV | Reactivs Comp S/S 275kV | 2028 | Addition | 0 | 59 | Cable | 0.04866 | 0.2257 | 139.1726 | TBC | 275
" | Hornsea 4 | Onshore 275kV | Reactivs Comp S/S 275kV | 2028 | Addition | 0 | 59 | Cable | 0.04866 | 0.2257 | 139.1726 | TBC | 275
" | Hornsea 4 | Onshore 275kV | Reactivs Comp S/S 275kV | 2028 | Addition | 0 | 59 | Cable | 0.04866 | 0.2257 | 139.1726 | TBC | 275
" | Hornsea 4 | Reactivs Comp S/S 275kV | Offshore platform 275kV | 2028 | Addition | 0 | 60 | Cable | 0.0299 | 0.1155 | 60.6327 | TBC | 275
" | Hornsea 4 | Reactivs Comp S/S 275kV | Offshore platform 275kV | 2028 | Addition | 0 | 60 | Cable | 0.0299 | 0.1155 | 60.6327 | TBC | 275
" | Hornsea 4 | Reactivs Comp S/S 275kV | Offshore platform 275kV | 2028 | Addition | 0 | 60 | Cable | 0.0299 | 0.1155 | 60.6327 | TBC | 275
" | Hornsea 4 | Reactivs Comp S/S 275kV | Offshore platform 275kV | 2028 | Addition | 0 | 60 | Cable | 0.0299 | 0.1155 | 60.6327 | TBC | 275
" | Hornsea 4 | Reactivs Comp S/S 275kV | Offshore platform 275kV | 2028 | Addition | 0 | 60 | Cable | 0.0299 | 0.1155 | 60.6327 | TBC | 275
" | Hornsea 4 | CREB4/NORM4 | Onshore 400kV | 2028 | Addition | 0 | 0.5 | Cable | 0.0102 | 0.3404 | 71.94 | TBC | 400
" | Hornsea 4 | CREB4/NORM4 | Onshore 400kV | 2028 | Addition | 0 | 0.5 | Cable | 0.0102 | 0.3404 | 71.94 | TBC | 400

## B-3-1a
Table B.3.1a - SHETL Transformer Parameters for 2019/20
Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
ACHR1R | ACHR3- | 0.36 | 18 | 0 | 90
AIGA1Q | AIGA5- | 1.76 | 44.89 | 0 | 22.5
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.615 | 17.82 | -0.026 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU2J | BEAU1J | 0.6786 | 12.2312 | 0 | 120
BEAU2J | BEAU1J | 0.6786 | 12.1644 | 0 | 120
BEAU2K | BEAU1K | 0.6786 | 12.1895 | 0 | 120
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.0009 | 1200
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.0009 | 1200
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 0.1486 | 5.3035 | -0.0025 | 360
BLHI2K | BLHI1K | 0.1506 | 5.3034 | -0.0017 | 360
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.0007 | 1200
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.0006 | 1200
BLHI4- | BLHI2L | 0.0252 | 1.1997 | -0.0007 | 1200
BLHI4- | BLHI2M | 0.0253 | 1.2081 | -0.0007 | 1200
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRCW2J | BRCW3- | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 0.42 | 20 | 0 | 120
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 39 | 0 | 30
BROR1- | BROR3- | 0.763 | 25.144 | 0 | 45
BUMU1Q | BUMU3- | 0.366 | 25.37 | -0.034 | 90
BUMU1R | BUMU3- | 0.376 | 25.42 | -0.035 | 90
CAAD1Q | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1Q | CAAD3J | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3- | 1.04 | 27.65 | 0 | 60
CAAD1R | CAAD3J | 0.5 | 25 | 0 | 90
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120
CASS1Q | CASS3- | 1.518 | 39.871 | 0 | 30
CEAN1Q | CEAN5- | 1.182 | 36.714 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAC1Q | CLAC5J | 0.75 | 25 | 0 | 60
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
CLUN1Q | CLUN5J | 0.71 | 19.53 | 0 | 60
CLUN1R | CLUN5K | 0.71 | 19.55 | 0 | 60
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90
CONN2J | CONN1J | 0.143 | 5.3036 | -0.0019 | 360
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
CORI1J | CORI3J | 8.3 | 27.5 | 0 | 60
COUA1Q | COUA3- | 0.2143 | 25.0741 | -0.0067 | 120
COUA1R | COUA3- | 0.2151 | 25.1241 | -0.0092 | 120
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
CRSS1J | COUW31 | 0.3629 | 18.0297 | -0.0123 | 90
CRSS1J | CRSS1Q | 0.0582 | 2.145 | 0 | 240
CRSS1K | CRSS1R | 0.0582 | 2.1492 | 0 | 240
CRSS2A | CRSS1J | 0.2466 | 9.0008 | -0.0029 | 240
CRSS2B | CRSS1K | 0.2459 | 9.0175 | -0.0042 | 240
CULL1Q | CULL5- | 1.46 | 37.6 | 0 | 25
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DEAN1Q | DEAN5- | 1.01 | 25.1 | 0 | 40
DORE11 | DORE31 | 0.21 | 9.89 | 0 | 120
DORE12 | DORE32 | 0.21 | 9.89 | 0 | 120
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DOUN2- | DOUN1- | 0.2112 | 7.7054 | -0.0041 | 240
DOUN2- | DOUN1- | 0.2237 | 7.9135 | -0.0043 | 240
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.617 | 17.65 | -0.029 | 60
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120
DYCE1Q | DYCE3- | 0.9463 | 26.6499 | -0.4258 | 60
DYCE1R | DYCE3- | 0.9517 | 26.7164 | -0.4078 | 60
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1J | ERRO1A | 0.04 | 1.942 | 0 | 240
ERRO1J | ERRO1T | 0.068 | 3.73 | 0 | 150
ERRO1J | ERRO5L | 0.72 | 26.6 | 0 | 60
ERRO1K | ERRO1B | 0.04 | 1.942 | 0 | 240
ERRO1K | ERRO5J | 0.72 | 26.6 | 0 | 60
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FARI2J | FARI1J | 0.4989 | 8.2933 | -0.038 | 120
FARI2K | FARI1K | 0.4955 | 8.3186 | -0.038 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1Q | FAUG3- | 2.23 | 64.33 | 0 | 15
FAUG2J | FAUG1- | 0.2606 | 7.7039 | -0.0035 | 240
FAUG2K | FAUG1- | 0.2629 | 7.7039 | -0.0043 | 240
FAUG4- | FAUG1- | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 0.3185 | 8.4523 | -0.013 | 240
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FETT2R | FETT1- | 0.217 | 4.2737 | -0.0057 | 240
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FINL1Q | FINL5- | 0.96 | 27.11 | 0 | 45
FOYE2J | FOYE0J | 0.17 | 8.17 | 0 | 165
FOYE2J | FOYE0K | 0.18 | 7.99 | 0 | 165
FRAS1Q | FRAS3- | 0.642 | 26.904 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.904 | 0 | 45
FWIL1Q | FWIL3- | 0.499 | 24.995 | 0 | 120
FWIL1R | FWIL3- | 0.499 | 24.995 | 0 | 120
FYRI2J | FYRI1J | 0.0967 | 3.8863 | -0.0026 | 480
FYRI2K | FYRI1K | 0.0971 | 3.8738 | -0.0021 | 480
GLDO1G | GLDO8- | 0.206 | 10.681 | 0 | 120
GLEN1Q | GLEN5- | 0.55 | 21.94 | 0 | 70
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90
INGA1Q | INGA5- | 1.162 | 25.006 | 0 | 25
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
INVB2A | INVR1- | 0.2217 | 4.3026 | -0.007 | 240
INVB2B | INVR1- | 0.2164 | 4.257 | -0.007 | 240
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEIT3A | 0.499 | 24.995 | 0 | 90
KEIT2Q | KEIT1- | 0.2735 | 8.6123 | -0.005 | 240
KEIT2R | KEIT1- | 0.3328 | 8.9104 | -0.0389 | 240
KIIN1- | KIIN3- | 0.772 | 24.877 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.521 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.78 | 0 | 45
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT1- | 0.3771 | 10.1929 | -0.018 | 240
KINT2K | KINT1- | 0.3751 | 10.2314 | -0.0147 | 240
KINT2K | KINT1- | 0.6786 | 12.1477 | 0 | 120
KIOR1Q | KIOR5- | 1.78 | 45.42 | 0 | 22.5
KNOC2J | KNOC1J | 0.2216 | 4.311 | -0.0076 | 240
KNOC2K | KNOC1J | 0.2205 | 4.3319 | -0.0062 | 240
LAIR1Q | LAIR3- | 0.425 | 24.674 | 0 | 90
LOCB2J | LOCB1J | 0.2181 | 8.1262 | -0.0043 | 240
LOCB2K | LOCB1K | 0.22 | 8.197 | -0.0046 | 240
LOCH1- | LOCH5J | 1.93 | 38.52 | 0 | 25
LOCH1- | LOCH5K | 1.93 | 38.2 | 0 | 25
LUIC1Q | LUIC5J | 0.763 | 37.548 | 0 | 45
LUIC1R | LUIC5K | 0.7668 | 37.548 | 0 | 45
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.429 | 25.741 | 0 | 90
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MELG4J | MELG1J | 0.108 | 3.957 | -0.0034 | 480
MELG4K | MELG1K | 0.106 | 3.957 | -0.0033 | 480
MILC1R | MILC3- | 0.78 | 24.83 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.13 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MOSS1Q | MOSS5- | 1.192 | 36.847 | 0 | 30
MOSS1R | MOSS5- | 1.2267 | 36.913 | 0 | 30
MYBS1S | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1S | MYBS3M | 0.2645 | 24.6069 | -0.024 | 120
MYBS1T | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3N | 0.2578 | 24.757 | -0.024 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6 | 0 | 60
NANT1Q | NANT5- | 1.47 | 56.67 | 0 | 30
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
ORRI1R | ORRI5- | 2.17 | 48.75 | 0 | 20
PEHE1- | PEHS5- | 2.58 | 42.33 | 0 | 15
PEHE2Q | PEHE1- | 0.4842 | 9.9549 | -0.0178 | 240
PEHE2R | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240
PEHE2S | PEHE0J | 0.02 | 1.93 | 0 | 776
PEHE2T | PEHE0K | 0.02 | 1.94 | 0 | 776
PEHE2U | PEHE0L | 0.097 | 4.8 | 0 | 313
PEHE2V | PEHE0M | 0.097 | 4.8 | 0 | 313
PEHE2W | PEHE0N | 0.097 | 4.8 | 0 | 313
PEHERSV1 | PEHE1- | 0.2649 | 9.2254 | -0.0049 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.4 | 0 | 45
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PERS2Q | PERS1Q | 0.3363 | 8.9061 | -0.0412 | 240
PERS2R | PERS1R | 0.3341 | 8.8645 | -0.0419 | 240
PORA1Q | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 1.803 | 29.812 | 0 | 30
QUOI1- | QUOI5- | 1.34 | 33.13 | 0 | 30
RANN1Q | RANN3Q | 0.43 | 24.66 | 0 | 90
RANN1R | RANN3Q | 0.43 | 24.66 | 0 | 90
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
SFEG1Q | SFEG5- | 2.28 | 93.87 | 0 | 30
SFEG1R | SFEG5- | 2.28 | 92.8 | 0 | 30
SFEM1Q | SFEM5J | 1.8 | 41.19 | 0 | 27
SFEM1R | SFEM5K | 1.8 | 41.19 | 0 | 27
SFIL1Q | SFIL5- | 1.99 | 39.48 | 0 | 25
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
SHIN1- | SHIN5- | 1.4823 | 80.16 | 0 | 40
SLOY1L | SLOY5L | 0.79 | 23.08 | 0 | 50
SLOY1M | SLOY5M | 0.79 | 22.9 | 0 | 50
SLOY1N | SLOY5N | 0.79 | 22.98 | 0 | 50
SLOY1P | SLOY5P | 0.8 | 23.2 | 0 | 50
SPIT2J | SPIT1J | 0.218 | 8.185 | -0.0037 | 240
SPIT2J | SPIT1J | 0.218 | 8.23 | -0.004 | 240
SPIT2K | SPIT1K | 0.131 | 4.99 | -0.0031 | 360
SPIT2K | SPIT1M | 0.129 | 4.99 | -0.0029 | 360
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
STRL1- | STRL3P | 0.2 | 17.74 | -0.01 | 120
STRL1- | STRL3Q | 0.2 | 17.65 | -0.01 | 120
STRL1- | STRL3R | 0.2 | 17.67 | -0.01 | 120
STRW12 | STRW31 | 0.05 | 18 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.53 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.787 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.787 | 0 | 90
TEAL2J | TEAL1- | 0.3619 | 10.1602 | -0.0118 | 180
TEAL2K | TEAL1- | 0.2564 | 11.7305 | -0.0131 | 180
TEAL2K | TEAL1- | 0.5506 | 11.8761 | 0 | 180
THUS1J | THUS3- | 0.2621 | 24.6736 | -0.022 | 120
THUS1K | THUS3- | 0.2614 | 24.7403 | -0.02 | 120
THUS2J | THUS1J | 0.0985 | 3.9363 | -0.003 | 480
THUS2K | THUS1K | 0.1 | 3.9362 | -0.002 | 480
TOMT2J | TOMT1J | 0.0985 | 3.9363 | -0.003 | 480
TOMT2K | TOMT1K | 0.0985 | 3.9363 | -0.003 | 480
TUMB1Q | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMB1R | TUMB5- | 0.499 | 24.995 | 0 | 21
TUMM2J | TUMM1J | 0.259 | 7.7457 | -0.0041 | 240
TUMM2K | TUMM1K | 0.2595 | 7.829 | -0.004 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.24 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
Table B.3.1b - SPT Transmission Transformers 2019/20
Node1 | Node2 | R (pu on 100MVA) | X (pu on 100MVA) | B (pu on 100MVA) | Rating (MVA)
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
BAGA1Q | BAGA0J | 0.5559 | 33.3287 | 0 | 18
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA0K | 0.5559 | 33.3287 | 0 | 18
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1Q | MARM0J | 0.933 | 56.0122 | 0 | 10
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BERW1R | MARM0K | 0.933 | 56.0122 | 0 | 10
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN0J | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN0K | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN0L | 0.558 | 33.4787 | 0 | 24
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY0J | 2.24 | 57.9567 | -0.0633 | 10
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY0K | 2.2 | 57.9583 | -0.0625 | 10
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3- | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3- | 0.4868 | 20.6609 | -0.2478 | 120
CLYM2- | CLYM3- | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3- | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1- | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1A | 0.1216 | 9.6242 | -0.0793 | 240
COAL4- | COAL1A | 0.0914 | 6.4382 | -0.0751 | 360
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1718 | 8.665 | -0.0204 | 120
COYL2- | COYL1- | 0.3396 | 12.8288 | -0.2375 | 120
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR1- | CRYR31 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR1- | CRYR32 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR1B | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1A | 0.1079 | 8.5702 | -0.0341 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM0J | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM0K | 1.232 | 73.8097 | 0 | 5
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 160
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 160
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3A | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3B | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3- | 0.8069 | 21.4849 | -0.3294 | 60
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCF1J | ECCF0J | 1.4773 | 33.3006 | -0.0896 | 15
ECCF1K | ECCF0K | 0.4481 | 26.8629 | 0 | 18
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EKIL2S | EKIL3- | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3- | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3- | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3- | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA4- | ELVA0J | 0.1612 | 34.0696 | -0.0029 | 80
ELVA4- | ELVA0K | 0.1613 | 34.0696 | -0.0101 | 80
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 0.5259 | 26.8282 | -0.0075 | 60
ERSK1R | ERSK3- | 0.5296 | 27.1115 | -0.0073 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 0.4311 | 25.9297 | -0.0244 | 90
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3A | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3B | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60
GORG1R | GORG3- | 0.8167 | 26.9876 | -0.0071 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.3876 | 19.4628 | -0.0275 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.5381 | 25.2943 | -0.0108 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1- | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1- | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
INWI1Q | INWI0J | 0.917 | 55.0024 | 0 | 10
INWI1R | INWI0K | 0.917 | 55.0024 | 0 | 10
JOHN1Q | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60
JOHN1R | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60
KAIM2- | KAIM3A | 0.4944 | 20.244 | -0.245 | 120
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILT2Q | KILT3- | 0.4927 | 18.4934 | -0.1756 | 120
KILT2R | KILT3- | 0.4976 | 18.4933 | -0.1775 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KYPE1- | KYPE3- | 0.1922 | 14.207 | -0.0113 | 120
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MIDM1- | MIDM3- | 0.4664 | 13.6087 | -0.0075 | 60
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37.5
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37.5
MOSM1A | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1B | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1A | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1B | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1173 | 8.6992 | -0.0311 | 240
NECU2- | NECU1- | 0.1173 | 8.5659 | -0.0322 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0297 | 240
NECU2- | NECU1Q | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 0.1164 | 8.5534 | -0.0287 | 240
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB0J | 0.5559 | 33.3287 | 0 | 18
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB0K | 0.5559 | 33.3287 | 0 | 18
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 90
REDH1- | REDH3- | 0.94 | 20.7787 | 0 | 60
SACO1Q | SACO0J | 0.933 | 56.0022 | 0 | 10
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO0K | 0.933 | 56.0022 | 0 | 10
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SANX1Q | SANX0J | 0.558 | 33.4787 | 0 | 18
SANX1Q | SANX3- | 0.8844 | 21.5485 | -0.309 | 60
SANX1R | SANX0K | 0.558 | 33.4787 | 0 | 18
SANX1R | SANX3- | 0.8767 | 21.2319 | -0.3087 | 60
SHRU2Q | SHRU3- | 0.4926 | 19.9939 | -0.2739 | 120
SHRU2R | SHRU3- | 0.4656 | 19.9946 | -0.3204 | 120
SIGH2Q | SIGH3A | 0.2282 | 13.7759 | -0.032 | 180
SIGH2R | SIGH3A | 0.2141 | 13.765 | -0.0372 | 180
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4722 | 18.7441 | -0.1542 | 120
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 120
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1- | STLE0J | 0.958 | 57.502 | 0 | 10
STLE1- | STLE0K | 0.958 | 57.502 | 0 | 10
STLE1- | STLE3S | 0.4217 | 25.741 | -0.028 | 90
STLE1- | STLE3S | 0.4235 | 25.6743 | -0.0254 | 90
TELR1Q | TELR3- | 0.9688 | 26.4656 | -0.0572 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG1R | 0.0267 | 1.3331 | 0 | 90
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30
TONG1Q | TONG1R | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WESE1- | AIKE3A | 0.5667 | 13.2333 | 0 | 90
WESE1- | AIKE3B | 0.5667 | 13.2333 | 0 | 90
WFIE1A | WFIE3- | 0.9889 | 20.4928 | 0 | 60
WFIE1B | WFIE3- | 0.9528 | 20.5613 | 0 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH0J | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH0K | 0.4979 | 29.8997 | 0 | 26
WISH2- | WISH3- | 0.4821 | 24.1785 | -0.226 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.1517 | 8.707 | -0.1161 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.2306 | 12.2562 | -0.0292 | 120
WLEX2- | WLEX3B | 0.2306 | 12.2728 | -0.0271 | 120
WLEX2- | WLEX3C | 0.2306 | 12.2728 | -0.0275 | 120

## B-3-1c
Table B.3.1c - NGET Transformer Parameters for 2019/20
Node1 | Node2 | R (pu on 100MVA) | X (pu on 100MVA) | B (pu on 100MVA) | Rating (MVA)
ABHA41 | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264
ABHA42 | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 279
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211
ABTH21 | ABTH13 | 0.0977 | 8.1994 | -1.7127 | 212
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135
ALDW21 | ALDW31 | 0.656 | 25.925 | -0.297 | 98
ALDW21 | ALDW31 | 0.656 | 25.925 | -0.297 | 98
ALVE4A | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275
AMEM41 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255
AMEM42 | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 275
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARK11 | 0.1646 | 8.0383 | -0.1808 | 211
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 258
BEDD21 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 240
BEDD21 | BEDT1A | 0.2264 | 12.2479 | -0.6062 | 126
BEDD22 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 240
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD23 | BEDT1B | 0.2264 | 12.2479 | -0.6062 | 126
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 867
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 273
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT4A | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT4B | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BODE41 | GWYN12 | 0.0547 | 3.513 | -0.8921 | 320
BODE41 | GWYN11 | 0.0547 | 3.513 | -0.8921 | 320
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 276
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 277
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 278
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 278
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 312
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 271
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 272
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO12 | 0.1307 | 7.9515 | -0.1098 | 240
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1096
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270
BRLE41 | BRLE1A | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE1B | 0.1303 | 7.8698 | -0.4285 | 263
BRWA2A | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BURW41 | BURW11 | 0.1372 | 8.0197 | -0.1238 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 265
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 278
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST4A | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST4B | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT12 | 0.1509 | 8.2849 | -0.3279 | 264
CANT41 | CANT11 | 0.1658 | 8.426 | -0.2939 | 264
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 279
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 180
CAPE4A | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845
CAPE4B | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272
CARR4A | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CARR4B | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 273
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 280
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 278
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 255
CHSI21 | CHSI11 | 0.2264 | 12.2479 | -0.6062 | 126
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 249
CHSI21 | CHSI11 | 0.2264 | 12.2479 | -0.6062 | 126
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 251
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 278
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 251
CILF41 | CILF2A | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF2B | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269
CITR41 | CITR12 | 0.0997 | 8.0088 | -0.093 | 266
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277
CONQ41 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259
CONQ41 | CONQ12 | 0.1045 | 7.8806 | -0.0998 | 240
CONQ41 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 279
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 266
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB2A | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB2A | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB2B | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB2B | 0.0176 | 1.5826 | -0.1148 | 750
CULJ41 | CULJ31 | 0.069 | 25 | 0 | 90
CULJ41 | CULJ32 | 0.069 | 25 | 0 | 90
CULJ41 | CULJ33 | 0.069 | 25 | 0 | 90
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 849
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EASO4A | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
EASO41 | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 272
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279
ELST21 | ELST12 | 0.1954 | 8.0796 | -0.2295 | 189
ELST21 | ELST12 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST13 | 0.1985 | 8.1167 | -0.4624 | 189
ELST21 | ELST14 | 0.3567 | 11.136 | -0.7303 | 126
ELST22 | ELST11 | 0.1923 | 8.081 | -1.4418 | 189
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 212
ELST22 | ELST15 | 0.3567 | 11.136 | -0.7303 | 127
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1100
ELST4B | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 278
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139
FECK41 | FECK21 | 0.0211 | 1.6463 | -14.2471 | 1114
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FERR21 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR21 | FERR61 | 0.237 | 10.8633 | -0.263 | 204
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278
FERR4A | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR4A | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113
FIDF21 | FIDF12 | 0.2847 | 12.2467 | -1.4346 | 120
FIDF21 | FIDF13 | 0.1594 | 8.6081 | -0.2215 | 261
FIDF22 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271
FIDF23 | FIDF11 | 0.2847 | 12.2467 | -1.4346 | 120
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 240
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 240
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 300
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLIB41 | FLIB41 | 0.0007 | 0.08 | 0 | 3000
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 146
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD11 | 0.054 | 4.8906 | -0.1253 | 499
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063
FROD41 | WEAV 71 | 0.3209 | 20.5475 | -0.1224 | 80
FROD41 | WEAV 71 | 0.3209 | 20.5475 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278
GREN41 | GREN12 | 0.1035 | 7.8472 | -0.0758 | 240
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268
HACK21 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK22 | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK21 | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK22 | 0.0182 | 1.5763 | -0.0904 | 1210
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 137
HARK22 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK21 | 0.0321 | 2.4344 | -0.0528 | 555
HARK41 | HARK22 | 0.0292 | 2.402 | -0.2732 | 573
HARK41 | HARK22 | 0.0376 | 2.3797 | -3.9009 | 547
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 191
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1063
HEDO21 | HEDN11 | 0.133 | 8.0758 | -0.2287 | 218
HEDO21 | HEDN11 | 0.133 | 8.0758 | -0.2287 | 218
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2150
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 539
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 507
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 279
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 279
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 217
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 250
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 278
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 265
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 279
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 125
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER22 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER41 | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1135
IVER41 | IVER22 | 0.0326 | 2.3798 | -3.9003 | 500
IVER42 | IVER21 | 0.0326 | 2.3798 | -3.9003 | 500
IVER42 | IVER23 | 0.0132 | 1.4627 | -2.0624 | 841
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 276
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 256
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278
KEAD4D | KEAD41 | 0.0002 | 0.4178 | 0 | 2210
KEAD4C | KEAD41 | 0.0002 | 0.2873 | 0 | 2210
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 257
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 236
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 240
KIBY22 | KIBY11 | 0.1681 | 8.3396 | -1.4878 | 211
KIBY22 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 269
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 278
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 279
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264
KIRK21 | KIRK11 | 0.1575 | 8.0988 | -0.027 | 266
KIRK2A | KIRK21 | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
LACK41 | LACK2C | 0.0174 | 1.598 | -0.1503 | 1154
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 240
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA4A | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEGA4B | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEIS4A | LEIS11 | 0.103 | 7.9231 | -0.0638 | 240
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 253
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 240
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 267
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 240
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 274
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 884
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 279
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 240
MELK41 | MELK11 | 0.1041 | 7.8535 | -0.0851 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK21 | 0 | 1.692 | 0 | 886
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MILH21 | MILH11 | 0.179 | 8.3648 | -4.7616 | 211
MILH21 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH21 | MILH12 | 0.1266 | 8.6449 | -1.9406 | 264
MILH21 | MILH12 | 0.179 | 8.3648 | -4.7616 | 199
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 240
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 263
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 263
MITY41 | MITY12 | 0.137 | 7.9818 | -0.1471 | 240
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1138
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 270
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 269
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 272
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 886
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2C | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 187
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278
NINF41 | NINF12 | 0.1509 | 7.9378 | -0.9251 | 253
NORL2A | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORL2B | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORM41 | NORW11 | 0.1264 | 8.4534 | -0.357 | 277
NORM41 | NORW11 | 0.1509 | 7.9378 | -0.9251 | 253
NORM41 | NORW12 | 0.1118 | 8.3874 | -0.0906 | 278
NORM41 | NORW12 | 0.1509 | 7.9378 | -0.9251 | 267
NORM41 | NORW11 | 0.1307 | 7.9515 | -0.1098 | 240
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 280
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 252
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 253
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 262
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.179 | 8.3648 | -4.7616 | 202
OCKH2A | OCKH21 | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 100
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 115
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB4A | OLDB21 | 0.0146 | 1.609 | -1.8746 | 1115
OSBA41 | OSBA1* | 0.103 | 7.9231 | -0.0638 | 269
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 240
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 274
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN4A | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138
PENN4B | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 257
PEWO2A | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO2B | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278
PEWO41 | PEWO21 | 0.021 | 1.669 | -12.6082 | 876
PEWO41 | PEWO21 | 0.0175 | 1.5879 | -4.0069 | 1139
PEWO41 | PEWO22 | 0.0178 | 1.5995 | -1.2431 | 845
PEWO41 | PEWO22 | 0.0189 | 1.6132 | -0.7226 | 1129
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 110
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 120
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 279
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273
RATS41 | RATS11 | 0.103 | 7.9231 | -0.0638 | 262
RATS41 | RATS11 | 0.1046 | 7.8493 | -0.0881 | 240
RATS41 | RATS12 | 0.1278 | 8.0061 | -0.2276 | 277
RATS41 | RATS12 | 0.1373 | 8.1976 | -0.1719 | 278
RATS41 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125
RAYL41 | RAYM11 | 0.1309 | 7.8656 | -0.4549 | 262
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240
RAYL41 | RAYM11 | 0.1759 | 7.9134 | -0.267 | 240
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 278
REBR21 | REBR31 | 0.665 | 28.1922 | -0.151 | 112
REBR22 | REBR32 | 0.665 | 28.1922 | -0.151 | 111
REBR21 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH12 | 0.2847 | 12.2467 | -1.4346 | 140
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RYEH41 | RYEH12 | 0.1326 | 8.774 | -0.7141 | 260
RYEH41 | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260
RYEH41 | RYEH13 | 0.1372 | 8.0197 | -0.1238 | 253
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1307 | 7.9515 | -0.1098 | 276
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273
SELL41 | SELL12 | 0.103 | 7.9231 | -0.0638 | 270
SELL41 | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 269
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 240
SJOW21 | SJOW13 | 0.1441 | 8.6238 | -0.2707 | 251
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273
SJOW41 | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 270
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 800
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 804
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 279
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN42 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 240
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198
STAL21 | STAL11 | 0.2188 | 8.097 | -1.9861 | 280
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 279
STAL41 | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271
STAY4A | STAY41 | 0.0002 | 0.4178 | -13.831 | 2750
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STEN11 | 0.3392 | 11.9012 | -0.7294 | 141
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 274
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1172
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STSB4A | STSB41 | 0.0003 | 0.1825 | 0 | 2000
SUND41 | SUND11 | 0.1303 | 7.8698 | -0.4285 | 278
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254
SWAN21 | SWAN11 | 0.1646 | 8.0383 | -0.1808 | 211
SWAN21 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 240
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN4A | SWAN21 | 0.0178 | 1.5995 | -1.2431 | 851
TAUN42 | TAUN11 | 0.1759 | 7.9134 | -0.267 | 279
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
THOM41 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 879
THOM41 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879
THOM42 | THOM21 | 0.0152 | 1.6463 | -0.1118 | 1100
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 180
TILB21 | TILB11 | 0.3792 | 12.0524 | -0.3982 | 131
TILB21 | TILB12 | 0.3792 | 12.0524 | -0.3982 | 134
TILB41 | TILB13 | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 1153
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP21 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 135
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP22 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 172
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 139
TOTT21 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265
TOTT22 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198
TOTT23 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT24 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 279
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 222
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 262
UPPB22 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 105
UPPB22 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 105
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 312
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 253
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 240
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 240
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 266
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 274
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278
WALX4A | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4B | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1137
WALX4B | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1137
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264
WASF21 | WASF11 | 0.197 | 7.9698 | -0.2553 | 207
WASF22 | WASF12 | 0.197 | 7.9698 | -0.2553 | 207
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 279
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 139
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 264
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 263
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 271
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263
WHAM4A | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHAM4B | WHAM41 | 0.001 | 0.35 | 0 | 1410
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO32 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.5913 | 19.0842 | -0.4269 | 100
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIEN21 | WIEN11 | 0.1594 | 8.6081 | -0.2215 | 288
WIEN21 | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 296
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278
WILE41 | WILL21 | 0.0268 | 2.7989 | -0.3188 | 686
WILL21 | WILL11 | 0.2847 | 12.2467 | -1.4346 | 140
WILL21 | WILL12 | 0.2847 | 12.2467 | -1.4346 | 140
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206
WIMB21 | WIMB11 | 0.1923 | 8.081 | -1.4418 | 189
WIMB21 | WIMB12 | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB12 | 0.1845 | 7.8956 | -0.1938 | 249
WIMB21 | WIMB13 | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB13 | 0.1845 | 7.8956 | -0.1938 | 249
WIMB21 | WIMB14 | 0.179 | 8.3648 | -4.7616 | 202
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 249
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WLSD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949
WLSD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 1000
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4B | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.2188 | 8.097 | -1.9861 | 280
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250
WWEY22 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 202
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY41 | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY41 | WWEY22 | 0.0185 | 1.614 | -0.5638 | 886
WWEY42 | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845
WWEY42 | WWEY23 | 0.0178 | 1.5995 | -1.2431 | 845
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273

## B-3-1d
Table B.3.1d- OFTO Transformer Parameters for 2019/20
OFTO | Site | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
Aberdeen Offshore Wind Farm Limited | Aberdeen Offshore Wind Farm | ABBA1- | ABBA6- | 0.795 | 15.9 | 0 | 120 | 132/66
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW10 | BOSW30 | 0.316 | 15.0833 | 0 | 120 | 132/33
Beatrice Offshore Windfarm Ltd | Beatrice Wind Farm | BEAT41 | BEAT21 | 0.15 | 16.03 | 0 | 320 | 400/220
|  | BEAT41 | BEAT22 | 0.15 | 16.03 | 0 | 320 | 400/220
|  | BEAT21 | BEIW31 | 0.89 | 15.25 | 0 | 310 | 220/33
|  | BEAT22 | BEIW32 | 0.89 | 15.25 | 0 | 310 | 220/33
East Anglia One Limited | East Anglia One | BRST41 | BRST21 | 0.0296 | 3.375 | 0 | 400 | 400/220
" |  | BRST41 | BRST21 | 0.0296 | 3.375 | 0 | 400 | 400/220
" |  | EANO21 | EAAW61/62 | 0.0296 | 7.035 | 0 | 400/200/200 | 220/66
" |  | EANO22 | EAAW63/64 | 0.0296 | 7.035 | 0 | 400/200/200 | 220/66
DONG Energy Burbo Extension (UK) Ltd | Burbo Bank Extension Wind Farm | BURB41 | BURB21 | 0.08 | 5.8995 | -0.3558 | 200 | 400/220/15.5
" | " | BURB41 | BURB21 | 0.08 | 5.8995 | -0.3558 | 200 | 400/220/15.5
" | " | BUBW20 | BUBW30 | 0.1 | 6.0492 | -0.8147 | 200 | 220/34
" | " | BUBW20 | BUBW30 | 0.1 | 6.0992 | -0.8147 | 200 | 220/34
Dudgeon Offshore Wind Ltd | Dudgeon Offshore Wind Farm | DUDW1 | DUDW3 | 0.1275 | 6.117 | 0 | 200 | 132/33
" | " | DUDW1 | DUDW3 | 0.1275 | 6.117 | 0 | 200 | 132/33
" | " | NECT41 | DUDO1 | 0.1264 | 8.4534 | -0.357 | 200 | 400/132/33
" | " | NECT41 | DUDO1 | 0.1264 | 8.4534 | -0.357 | 200 | 400/132/33
Galloper Wind Farm Limited | Galloper | GALO1 | GANW32/GANW34 | 0.6 | 50.3964 | 0 | 180 | 132/33/33
" | " | GALO1 | GANW31/GANW33 | 0.6 | 50.3964 | 0 | 180 | 132/33/33
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON11 | GGON51 | 0.0241 | 11 | 0 | 90 | 132/13.9
" | " | GGON12 | GGON52 | 0.0241 | 11 | 0 | 90 | 132/13.9
" | " | GGON13 | GGON53 | 0.0241 | 11 | 0 | 90 | 132/13.9
" | " | GREG11 | GREG31 | 0.3667 | 23.3305 | 0 | 180 | 132/33
" | " | GREG12 | GREG32 | 0.3667 | 23.3305 | 0 | 180 | 132/33
" | " | GREG1A | GREG3A | 0.4111 | 23.3297 | 0 | 90 | 132/33
" | " | GREG1B | GREG3B | 0.4111 | 23.3297 | 0 | 90 | 132/33
" | " | GREG13 | GREG33 | 0.3667 | 23.3305 | 0 | 180 | 132/33
TC Gunfleet OFTO Limited | Gunfleet Sands Offshore Wind Farm | GUNS11 | GUNS31 | 0.2372 | 8.5717 | 0 | 120 | 132/33
" | " | GUNS11 | GUNS31 | 0.2372 | 8.5717 | 0 | 120 | 132/33
E.ON Climate & Renewables UK Humber Wind Ltd | Humber Gateway Offshore Wind Farm | HEDO21 | HUMO11 | 0.1441 | 8.6238 | -0.2707 | 240 | 275/132/33
" | " | HEDO21 | HUMO12 | 0.1441 | 8.6238 | -0.2707 | 240 | 275/132/33
" | " | HUMW11 | HUMW31 | 0.23 | 8.57 | 0 | 140 | 132/33
" | " | HUMW12 | HUMW32 | 0.23 | 8.57 | 0 | 140 | 132/33
TC Lincs OFTO Limited | Lincs Wind Farm | LINO41 | LINO10 | 0.041667 | 4.6665 | 0 | 300 | 400/132/13
" | " | LINO41 | LINO10 | 0.041667 | 4.6665 | 0 | 300 | 400/132/13
" | " | LINS11 | LINS30 | 0.045833 | 5.8328 | -0.351 | 240 | 132/33
" | " | LINS11 | LINS30 | 0.045833 | 5.8328 | -0.351 | 240 | 132/33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | LONO11 | 0.33 | 6.4556 | 0 | 180/180/90 | 400/150/13.9
" | " | LONO42 | LONO12 | 0.33 | 6.4111 | 0 | 180/180/90 | 400/150/13.9
" | " | LONO41 | LONO13 | 0.33 | 6.4611 | 0 | 180/180/90 | 400/150/13.9
" | " | LONO42 | LONO14 | 0.33 | 6.4389 | 0 | 180/180/90 | 400/150/13.9
" | " | LOAW11 | LOAW31 | 0.402 | 6.56 | 0 | 180 | 150/33
" | " | LOAW12 | LOAW32 | 0.407 | 6.58 | 0 | 180 | 150/33
" | " | LOAW13 | LOAW33 | 0.4045 | 6.57 | 0 | 180 | 150/33
" | " | LOAW14 | LOAW34 | 0.4045 | 6.57 | 0 | 180 | 150/33
Gwynt y Môr OFTO Plc | Gwynt y Môr Offshore Wind Farm | BODE4C | GWYO10 | 0.054688 | 3.5313 | 0 | 320 | 400/132/13.9
" | " | BODE4D | GWYO10 | 0.054688 | 3.5313 | 0 | 320 | 400/132/13.9
" | " | GWYW10 | GWBW30 | 0.15625 | 11.3438 | 0 | 160 | 132/33
" | " | GWYW10 | GWAW30 | 0.15625 | 11.3625 | 0 | 160 | 132/33
" | " | GWYW10 | GWBW30 | 0.15625 | 11.375 | 0 | 160 | 132/33
" | " | GWYW10 | GWAW30 | 0.15625 | 11.3313 | 0 | 160 | 132/33
TC Ormonde OFTO Limited | Ormonde Offshore Windfarm | ORMW11 | ORMW31 | 0.464 | 14.421 | 0 | 85 | 132/33
" | " | ORMW11 | ORMW31 | 0.465 | 14.479 | 0 | 85 | 132/33
" | " | ORMW12 | ORMW32 | 0.348 | 13.465 | 0 | 110 | 132/33
DONG Energy RB (UK) Limited | Race Bank Offshore Wind Farm | RACO21 | RACW31 | 0.11449 | 6.0389 | 0 | 200 | 220/34
" | " | RACO21 | RACW32 | 0.11465 | 6.0789 | 0 | 200 | 220/34
" | " | RACO22 | RACW33 | 0.11476 | 6.0989 | 0 | 200 | 220/34
" | " | RACO22 | RACW34 | 0.11435 | 6.0689 | 0 | 200 | 220/34
" | " | RACO41 | RACO21 | 0.03165 | 3.1526 | -0.8396 | 360 | 400/220
" | " | RACO42 | RACO22 | 0.031779 | 3.1582 | -0.8396 | 360 | 400/220
RAMPION OFFSHORE WIND LIMITED | Rampion Offshore Wind Farm | RAMW1C | RAMW31 | 0.33 | 12.23 | -0.144 | 240 | 150/33
" | " | RAMW1D | RAMW32 | 0.33 | 12.76 | -0.144 | 240 | 150/33
" | " | TWNE41 | TWNE11 | 0.17 | 12.24 | -1.9406 | 240 | 400/150/33
" | " | TWNE42 | TWNE12 | 0.17 | 12.74 | -1.9406 | 240 | 400/150/33
E.ON UK Renewables UK Robin Rigg East Ltd | Robin Rigg East Offshore Wind Farm | RREW11 | RREW32 | 0.3 | 11.36 | 0 | 100 | 132/33
E.ON UK Renewables UK Robin Rigg West Ltd | Robin Rigg West Offshore Wind Farm | RRWW11 | RRWW32 | 0.3 | 11.36 | 0 | 100 | 132/33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SSAW31 | 0.23 | 12.07 | 0 | 90 | 132/33
" | " | SSAW11 | SSAW31 | 0.23 | 12.07 | 0 | 90 | 132/33
" | " | SSBW12 | SSBW32 | 0.23 | 12.07 | 0 | 90 | 132/33
" | " | SSBW12 | SSBW32 | 0.23 | 12.07 | 0 | 90 | 132/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW10 | THOW30 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
" | " | THOW10 | THOW30 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
Blue Transmission Walney 1 Limited | Walney 1 Offshore Wind Farm | WAAW11 | WAAW31 | 0.41667 | 8.75 | 0 | 120 | 132/33
" | " | WAAW11 | WAAW31 | 0.41667 | 8.75 | 0 | 120 | 132/33
Blue Transmission Walney 2 Limited | Walney 2 Offshore Wind Farm | WABW11 | WABW31 | 0.2395 | 8.2882 | 0 | 120 | 132/33
" | " | WABW11 | WABW31 | 0.2432 | 8.3214 | 0 | 120 | 132/33
DONG Energy Walney Extension (UK) Ltd | Walney 3 Offshore Wind Farm | WACW21 | WACW31 | 0.23 | 12.0378 | -0.6518 | 280 | 220/34
" | " | WACW21 | WACW32 | 0.23 | 12.0378 | -0.6518 | 280 | 220/34
" | Walney 4 Offshore Wind Farm | WADW21 | WADW31 | 0.23 | 12.0378 | -0.6518 | 280 | 220/34
" | " | WADW21 | WADW32 | 0.23 | 12.0378 | -0.6518 | 280 | 220/34
- | Walney Extension | WOWE41 | WOWE21 | 0.0255 | 2.6169 | -1.0975 | 470 | 400/220
- | " | WOWE42 | WOWE22 | 0.0255 | 2.6169 | -1.0975 | 470 | 400/220
- | " | WOWE21 | WOWE51 | 0.1286 | 8.5705 | -0.3212 | 140 | 220/22
- | " | WOWE22 | WOWE52 | 0.1286 | 8.5705 | -0.3212 | 140 | 220/22
WoDS Transmission Plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | WDSO11 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
" | " | WDSO42 | WDSO12 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
" | " | WDSW11 | WDSW31 | 0.20833 | 5 | 0 | 240 | 155/34
" | " | WDSW12 | WDSW31 | 0.20833 | 5 | 0 | 240 | 155/34
Westermost Rough Ltd | Westernost Rough Offshore Wind Farm | WERW21 | WERW11 | 0.09 | 6.62 | 0 | 225/225/137.5 | 275/150/33
" | " | WERW22 | WERW11 | 0.09 | 6.58 | 0 | 225/225/137.5 | 275/150/33
" | " | WERW12 | WERW31 | 0.12 | 7.14 | 0 | 140 | 150/33
" | " | WERW12 | WERW31 | 0.12 | 7.14 | 0 | 140 | 150/33
Hornsea 1 Limited | Hornsea Onshore wind farm | HOWA41 | HOWA21 | 0.01 | 2.68 | -0.25778 | 430 | 400/220
" | " | HOWA41 | HOWA21 | 0.01 | 2.68 | -0.25778 | 430 | 400/220
" | " | HOWA41 | HOWA21 | 0.01 | 2.68 | -0.25778 | 430 | 400/220
" | Hornsea Power Station 1A | HOWW1A | HOWW32/34 | 0.016667 | 2.4125 | -0.97904 | 240 | 220/34
" | " | HOWW1A | HOWW31/33 | 0.016667 | 2.4125 | -0.97904 | 240 | 220/34
" | Hornsea Power Station 1B | HOWW1B | HOWW32/34 | 0.016667 | 2.4125 | -0.97904 | 240 | 220/34
" | " | HOWW1B | HOWW31/33 | 0.016667 | 2.4125 | -0.97904 | 240 | 220/34
" | Hornsea Power Station 1C | HOWW1C | HOWW32/34 | 0.016667 | 2.4125 | -0.97904 | 240 | 220/34
" | " | HOWW1C | HOWW31/33 | 0.016667 | 2.4125 | -0.97904 | 240 | 220/34

## B-3-2a
B.3.2a - SHE TransmissionTransformer Changes 2020/21 to 2028/29
Node1 | Node2 | Year | Status | R (pu on 100MVA) | X (pu on 100MVA) | B (pu on 100MVA) | Rating (MVA)
ABED1- | ABED3- | 2020 | Addition | 0.33 | 21.7 | 0 | 60
DYCE1Q | DYCE3- | 2020 | Changed | 0.5828 | 24.9932 | 0 | 90
DYCE1R | DYCE3- | 2020 | Changed | 0.5828 | 24.9932 | 0 | 90
FARI2K | FARI1K | 2020 | Changed | 0.2184 | 8.2304 | -0.004 | 240
ABNE1Q | ABNE3- | 2021 | Changed | 0.2621 | 24.6736 | -0.0222 | 120
ABNE1R | ABNE3- | 2021 | Changed | 0.2614 | 24.7403 | -0.0197 | 120
CAAD1Q | CAAD3- | 2021 | Changed | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1R | CAAD3- | 2021 | Changed | 0.2621 | 24.6736 | -0.0222 | 120
FAUG1Q | FAUG3- | 2021 | Changed | 1.1951 | 25.0827 | 0 | 45
FAUG4- | FAUG1- | 2021 | Removal | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 2021 | Removal | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1J | 2021 | Addition | 0.108 | 3.957 | -0.0034 | 480
FAUG4K | FAUG1K | 2021 | Addition | 0.108 | 3.957 | -0.0034 | 480
GLKO1- | GLKO3J | 2021 | Addition | 0.36 | 18 | 0 | 60
PORA1Q | PORA3- | 2021 | Removal | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 2021 | Removal | 1.803 | 29.812 | 0 | 30
PORA1T | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
ROTI2J | ROTI3- | 2021 | Addition | 0.39 | 18 | 0 | 120
ROTI2J | ROTI3- | 2021 | Addition | 0.39 | 18 | 0 | 120
LIMK1- | LIMK3- | 2022 | Addition | 0.36 | 18 | 0 | 120
MILS1Q | MILS3J | 2022 | Addition | 0.36 | 18 | 0 | 60
PENF1- | PENF3A | 2022 | Addition | 0.36 | 18 | 0 | 42
ARNI1K | ARNI3- | 2023 | Addition | 0.36 | 18 | 0 | 60
BROA1Q | BROA3- | 2023 | Changed | 0.5 | 25 | 0 | 45
BROA1R | BROA3J | 2023 | Addition | 1.19 | 39 | 0 | 30
CAAD1Q | CAAD3J | 2023 | Changed | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1R | CAAD3J | 2023 | Changed | 0.2621 | 24.6736 | -0.0222 | 120
CRDH2J | CRDH1J | 2023 | Addition | 0.098 | 3.936 | -0.0025 | 480
CRDH2K | CRDH1K | 2023 | Addition | 0.098 | 3.936 | -0.0025 | 480
CREA1- | CREA3- | 2023 | Addition | 0.4 | 20 | 0 | 90
DOUN2- | DOUN2A | 2023 | Addition | 0.066 | 5.333 | 0 | 360
DRUL1- | DRUL3- | 2023 | Addition | 0.36 | 18 | 0 | 60
EDIN1- | GLNU3- | 2023 | Addition | 0.36 | 18 | 0 | 60
FINS1- | COST3- | 2023 | Addition | 0.54 | 18 | 0 | 45
FINS1- | FINS3- | 2023 | Addition | 0.451 | 25 | 0 | 120
FINS1- | FINS3- | 2023 | Addition | 0.451 | 25 | 0 | 120
FINS1- | HEST3- | 2023 | Addition | 0.54 | 18 | 0 | 45
FINS2A | FINS1- | 2023 | Addition | 0.044 | 5.833 | 0 | 360
PENF1- | PENF3A | 2023 | Changed | 0.36 | 18 | 0 | 84
STWN1- | STWN3J | 2023 | Addition | 0.36 | 18 | 0 | 90
STWN1- | STWN3K | 2023 | Addition | 0.36 | 18 | 0 | 90
TEAL2B | TEAL2K | 2023 | Addition | 0.005 | 0.4 | 0 | 700
TEAL2J | TEAL2A | 2023 | Addition | 0.005 | 0.4 | 0 | 700
ARBR1Q | ARBR3- | 2025 | Changed | 0.36 | 18 | 0 | 120
ARBR1R | ARBR3- | 2025 | Changed | 0.36 | 18 | 0 | 120
BEAU2J | BEAU1J | 2025 | Changed | 0.1486 | 5.3035 | -0.002 | 360
BEAU2J | BEAU1J | 2025 | Changed | 0.1486 | 5.3035 | -0.002 | 360
BEAU2K | BEAU1K | 2025 | Changed | 0.1486 | 5.3035 | -0.002 | 360
BEWF1- | BEWF3- | 2025 | Addition | 0.36 | 18 | 0 | 90
BLHI4- | BLHI2L | 2025 | Removal | 0.0252 | 1.1997 | -0.0007 | 1200
BLHI4- | BLHI2M | 2025 | Removal | 0.0253 | 1.2081 | -0.0007 | 1200
CLSO1- | CLSO3- | 2025 | Addition | 0.9 | 18 | 0 | 60
CONN2K | CONN1K | 2025 | Addition | 0.143 | 5.3036 | -0.002 | 360
CORI1J | CORI3J | 2025 | Changed | 1 | 20 | 0 | 90
DOUN2- | DOUN2D | 2025 | Addition | 0.066 | 5.333 | 0 | 360
FIDD1Q | FIDD3- | 2025 | Removal | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 2025 | Removal | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 2025 | Removal | 0.4562 | 26.084 | 0 | 90
FIDD2Q | FIDD3- | 2025 | Addition | 0.36 | 18 | 0 | 120
FIDD2R | FIDD3- | 2025 | Addition | 0.36 | 18 | 0 | 120
FINS2D | FINS1- | 2025 | Addition | 0.044 | 5.833 | 0 | 360
GLSH1J | GLSH31 | 2025 | Addition | 0.6 | 17.4 | 0 | 120
GLSH1J | GLSH32 | 2025 | Addition | 0.6 | 17.4 | 0 | 120
GORW2- | GORW3- | 2025 | Removal | 0.258 | 20.06 | 0 | 120
GORW2A | GORW3- | 2025 | Addition | 0.258 | 20.06 | 0 | 120
KINT4J | KINT2K | 2025 | Addition | 0.0252 | 1.1997 | -0.001 | 1200
KINT4K | KINT2J | 2025 | Addition | 0.0253 | 1.2081 | -0.001 | 1200
PEHE4J | PEHE2Q | 2025 | Addition | 0.026 | 1.533 | -0.0007 | 1200
PEHE4K | PEHERSV1 | 2025 | Addition | 0.026 | 1.533 | -0.0007 | 1200
PENF1B | PENF3B | 2025 | Addition | 3.6 | 18 | 0 | 96
ROTI1J | ROTI3- | 2025 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI1K | ROTI3- | 2025 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI2J | ROTI3- | 2025 | Removal | 0.39 | 18 | 0 | 120
ROTI2J | ROTI3- | 2025 | Removal | 0.39 | 18 | 0 | 120
ROTI4J | ROTI1J | 2025 | Addition | 0.2149 | 8.0138 | -0.013 | 240
ROTI4K | ROTI1K | 2025 | Addition | 0.2149 | 8.0138 | -0.013 | 240
SALA1- | SALA3- | 2025 | Addition | 0.36 | 17.99 | 0 | 90
STRW13 | STRW33 | 2025 | Addition | 0.5 | 25 | 0 | 90
STRW13 | STRW34 | 2025 | Addition | 0.5 | 25 | 0 | 90
TARL1Q | TARL3- | 2025 | Changed | 0.36 | 18 | 0 | 90
TARL1R | TARL3- | 2025 | Changed | 0.36 | 18 | 0 | 90
WESR3- | FINS1- | 2025 | Addition | 0.36 | 18 | 0 | 90
ALYT4J | ALYT2A | 2028 | Addition | 0.017 | 1.59 | -0.001 | 1000
ALYT4K | ALYT2B | 2028 | Addition | 0.017 | 1.59 | -0.001 | 1000
BLHI2B | BLHI2K | 2028 | Addition | 0.005 | 0.4 | 0 | 865
BLHI2J | BLHI1J | 2028 | Addition | 0.1486 | 5.3035 | -0.0025 | 360
BLHI2J | BLHI2A | 2028 | Addition | 0.005 | 0.4 | 0 | 865
BLHI2K | BLHI1K | 2028 | Addition | 0.1486 | 5.3035 | -0.0025 | 360
CAID2- | CAID3- | 2028 | Addition | 0.36 | 18 | 0 | 120
CLGO1- | CLGO3- | 2028 | Addition | 0.36 | 18 | 0 | 270
CLGO2- | CLGO1- | 2028 | Addition | 0.1486 | 5.3035 | -0.0025 | 360
CLGO2A | CLGO1- | 2028 | Addition | 0.1486 | 5.3035 | -0.0025 | 360
CLOI11 | CLOI3- | 2028 | Addition | 0.36 | 18 | 0 | 120
CLOI11 | CLOI3- | 2028 | Addition | 0.36 | 18 | 0 | 120
ELCH1- | ELCH3- | 2028 | Addition | 0.75 | 15 | 0 | 120
ENEI1- | ENEI3- | 2028 | Addition | 0.08 | 4 | 0 | 150
FETT2R | FETT1- | 2028 | Removal | 0.217 | 4.2737 | -0.0057 | 240
FETT4J | FETT1- | 2028 | Addition | 0.2149 | 8.0138 | -0.013 | 240
INGA4J | INGA1K | 2028 | Addition | 0.131 | 7.952 | -0.11 | 240
INGA4K | INGA1J | 2028 | Addition | 0.131 | 7.952 | -0.11 | 240
MUAI1- | MUAI3A | 2028 | Addition | 0.36 | 18 | 0 | 90
MUAI1- | MUAI3B | 2028 | Addition | 0.36 | 18 | 0 | 90
PEHG1Q | PEHG3- | 2028 | Changed | 0.5 | 25 | 0 | 90
PEHG1R | PEHG3- | 2028 | Changed | 0.5 | 25 | 0 | 90
PENF1C | PENF3C | 2028 | Addition | 3.6 | 18 | 0 | 96
STRW1C | STRW35 | 2028 | Addition | 0.36 | 18 | 0 | 120
WESR3- | FINS1- | 2028 | Addition | 0.36 | 18 | 0 | 90
WILW1- | WILW3- | 2028 | Addition | 0.36 | 18 | 0 | 60

## B-3-2b
Table B.3.2b - SPT Transmission Transformer Changes 2020/21 to 2028/29
Node1 | Node2 | Year | Status | R (pu on 100MVA) | X (pu on 100MVA) | B (pu on 100MVA) | Rating (MVA)
CHAS2R | CHAS3A | 2020 | Addition | 0.2836 | 14.325 | -0.0055 | 120
DUNB1S | DUNB3B | 2020 | Addition | 0.3635 | 25.4418 | 0 | 90
DUNB1T | DUNB3B | 2020 | Addition | 0.3635 | 25.4418 | 0 | 90
KILS4T | KILS2- | 2020 | Addition | 0.0148 | 1.6509 | -0.1193 | 1000
TONG1- | TONG3- | 2020 | Addition | 0.533 | 26.9114 | -0.0078 | 60
TONG1- | TONG3- | 2020 | Addition | 0.5309 | 27.0615 | -0.008 | 60
CHAS2R | CHAS3- | 2020 | Removed | 0.4868 | 20.6609 | -0.2478 | 120
CHAS2Q | CHAS3A | 2021 | Addition | 0.2836 | 14.325 | -0.0055 | 120
CHAS2Q | CHAS3A | 2021 | Removed | 0.4875 | 18.1601 | -0.1331 | 120
CRYR4- | NNGA2- | 2021 | Addition | 0.1071 | 5.8919 | -0.0108 | 280
CRYR4- | NNGB2- | 2021 | Addition | 0.1071 | 5.8919 | -0.0108 | 280
CUMH1- | CUMH3- | 2021 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DONO1- | DONO3- | 2021 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
FALL4- | FALL3C | 2021 | Addition | 0.2564 | 16.6647 | 0 | 120
MIDM1- | KENE3- | 2021 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
SHRU2R | SHRU3- | 2021 | Change | 0.2373 | 19.9986 | -0.0132 | 120
BENB1- | BENB3- | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
COYL2- | COYL1- | 2023 | Change | 0.1476 | 8.7488 | -0.1299 | 240
COYL2- | COYL1- | 2023 | Change | 0.1476 | 8.7488 | -0.1299 | 240
ELVA1- | HABU3- | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
ELVA2R | ELVA1- | 2023 | Addition | 0.0984 | 5.8325 | -0.2121 | 360
ENHI1- | ENHI3- | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
EWEH1Q | EWEH3A | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
GHPS1- | GHPS3A | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
GHPS1- | GHPS3B | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
GHPS1- | GHPS3C | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
KYPE1- | HARG3- | 2023 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
LORG1- | LORG3- | 2023 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
MAHI2- | MAHI1B | 2023 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
MOFF4- | MOFF1- | 2023 | Addition | 0.1483 | 10.0614 | -0.3432 | 240
NECU2- | NECU1Q | 2023 | Removed | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 2023 | Removed | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 2023 | Addition | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 2023 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1B | 2023 | Addition | 0.1164 | 8.5534 | -0.0287 | 240
NECU2- | NECU1C | 2023 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
NECU2- | NECU1C | 2023 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
NEIL4R | NEIL2- | 2023 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
NETS1- | NETS3- | 2023 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
STNO1- | STNO3- | 2023 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DENN4- | DENN2- | 2025 | Addition | 0.0164 | 1.6449 | -0.1161 | 1000
KENN1- | KENN3- | 2025 | Addition | 0.1922 | 14.207 | -0.0113 | 120
NLEI1- | NLEI3A | 2025 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NLEI1- | NLEI3B | 2025 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
TONG1- | TONG1R | 2025 | Removed | 0.0267 | 1.3331 | 0 | 90
TONG1Q | TONG1R | 2025 | Removed | 0.0125 | 2.5 | 0 | 90
BONN2A | BONN1- | 2028 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 2028 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
BONN4- | BONN1- | 2028 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
BONN4- | BONN1- | 2028 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
ELVN4- | ELVN1- | 2028 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
ELVN4- | ELVN1- | 2028 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
ELVN4- | ELVN1- | 2028 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
KINC4A | KINC2- | 2028 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4A | KINC2- | 2028 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4B | KINC2- | 2028 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
KINC4B | KINC2- | 2028 | Addition | 0.015 | 1.6499 | -0.2252 | 1000

## B-3-2c
B.3.2c - NGET TransmissionTransformer Changes 2020/21 to 2028/2029
Node1 | Node2 | Year | Status | R (pu on 100MVA) | X (pu on 100MVA) | B (pu on 100MVA) | Rating (MVA)
Eleclink HVDC Connections | Eleclink HVDC Connections | 2020 | Addition | 0 | 1 | 0 | 1200
IVER41 | IVER21 | 2020 | Addition | 0.0152 | 1.6463 | -0.1118 | 775
NINF41 | NINF91 | 2020 | Addition | 0 | 3.8867 | 0 | 150
SELL41 | SELL91 | 2020 | Addition | 0 | 3.8867 | 0 | 150
SELL41 | SELL91 | 2020 | Addition | 0 | 3.8867 | 0 | 150
TILB41 | TILB11 | 2020 | Addition | 0.1307 | 7.9515 | -0.1098 | 131
IVER41 | IVER21 | 2020 | Removed | 0.0326 | 2.3798 | -3.9003 | 500
TILB21 | TILB11 | 2020 | Removed | 0.3792 | 12.0524 | -0.3982 | 131
ELST21 | ELST14 | 2021 | Removed | 0.3567 | 11.136 | -0.7303 | 126
ELST22 | ELST15 | 2021 | Removed | 0.3567 | 11.136 | -0.7303 | 127
HARK41 | HARK21 | 2021 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK41 | HARK21 | 2021 | Removed | 0.0321 | 2.4344 | -0.0528 | 555
NINF41 | NINF91 | 2021 | Removed | 0 | 3.8867 | 0 | 150
SELL41 | SELL91 | 2021 | Removed | 0 | 3.8867 | 0 | 150
SELL41 | SELL91 | 2021 | Removed | 0 | 3.8867 | 0 | 150
TILB21 | TILB11 | 2021 | Addition | 0.3792 | 12.0524 | -0.3982 | 131
TILB41 | TILB11 | 2021 | Removed | 0.1307 | 7.9515 | -0.1098 | 131
HAWP41 | HAWP21 | 2023 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
HARK41 | HARK22 | 2023 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK41 | HARK22 | 2023 | Removed | 0.0376 | 2.3797 | -3.9009 | 547
SJOW41 | SJOW13 | 2023 | Addition | 0.1229 | 8.3873 | -0.1147 | 240
SJOW21 | SJOW13 | 2023 | Removed | 0.1441 | 8.6238 | -0.2707 | 251
SJOW41 | LODR62 | 2023 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
SJOW21 | LODR62 | 2023 | Removed | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | LODR61 | 2023 | Removed | 0.3062 | 11.0235 | -0.4552 | 198
WIMB21 | WIMB13 | 2023 | Removed | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB14 | 2023 | Removed | 0.179 | 8.3648 | -4.7616 | 202
WIMB21 | WIMB12 | 2023 | Removed | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB13 | 2023 | Removed | 0.1845 | 7.8956 | -0.1938 | 249
WIMB21 | WIMB11 | 2023 | Removed | 0.1923 | 8.081 | -1.4418 | 189
WIMB21 | WIMB12 | 2023 | Removed | 0.1845 | 7.8956 | -0.1938 | 249
WIMB41 | WIMB11 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2023 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB21 | 2023 | Addition | 0.014 | 2.6567 | -0.1528 | 950
EXET41 | EXET41 | 2025 | Addition | 0.001 | 0.1019 | 0 | 1500
BRIW41 | BRWA11 | 2028 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
BRIW41 | BRWA11 | 2028 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
BRWA2A | BRWA11 | 2028 | Removed | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 2028 | Removed | 0.167 | 7.9774 | -0.2092 | 255
SAFO41 | SAFO11 | 2028 | Addition | 0.1307 | 7.9515 | -0.1098 | 200
SAFO41 | SAFO12 | 2028 | Addition | 0.1307 | 7.9515 | -0.1098 | 180
SEAB41 | SEAB11 | 2028 | Removed | 0.1307 | 7.9515 | -0.1098 | 276

## B-3-2d
B.3.2d - OFTO TransmissionTransformer Changes 2020/21 to 2028/2029
OFTO | Site | Node 1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage Ratio (kV)
Triton Knoll Offshore Wind Farm Ltd | Triton Knoll | TKNO41 | TKNO21 | 2020 | Addition | TBC |  |  | 450/450/200 | 400/220
" | Triton Knoll | TKNO41 | TKNO21 | 2020 | Addition | TBC |  |  | 450/450/200 | 400/220
" | Triton Knoll | TKNW21 | String 66kV GIS | 2020 | Addition | TBC |  |  | 420 | 220/66
" | Triton Knoll | TKNE21 | String 66kV GIS | 2020 | Addition | TBC |  |  | 420 | 220/66
Moray Offshore Windfarm (East) Ltd | Moray Firth (MORL) | MORF2 | MORO21 | 2021 | Addition | TBC |  |  | 340 | 275/220
" | Moray Firth (MORL) | MORF2 | MORO21 | 2021 | Addition | TBC |  |  | 340 | 275/220
" | Moray Firth (MORL) | MORF2 | MORO21 | 2021 | Addition | TBC |  |  | 340 | 275/220
" | Moray Firth (MORL) | MOWE21 | MOWE6 | 2021 | Addition | TBC |  |  | 315 | 220/66
" | Moray Firth (MORL) | MOWE21 | MOWE6 | 2021 | Addition | TBC |  |  | 315 | 220/66
" | Moray Firth (MORL) | MOWW21 | MOWW21 | 2021 | Addition | TBC |  |  | 315 | 220/66
Breesea Limited | Hornsea2A | HOWB4 | HOWB2 | 2021 | Addition | TBC |  |  | 475 | 400/220
" | Hornsea2B | HOWB4 | HOWB2 | 2021 | Addition | TBC |  |  | 475 | 400/220
" | Hornsea2B | HOWB4 | HOWB2 | 2021 | Addition | TBC |  |  | 475 | 400/220
" | Hornsea2A | HOWW2D | HOWW6 | 2021 | Addition | TBC |  |  | 270 | 220/66
" | Hornsea2A | HOWW2D | HOWW6 | 2021 | Addition | TBC |  |  | 270 | 220/66
Soundmark Wind Limited | Hornsea2B | HOWW2D | HOWW6 | 2021 | Addition | TBC |  |  | 270 | 220/66
" | Hornsea2B | HOWW2D | HOWW6 | 2021 | Addition | TBC |  |  | 270 | 220/66
Sonningmay Wind Limited | Hornsea2C | HOWW2D | HOWW6 | 2023 | Addition | TBC |  |  | 270 | 220/66
" | Hornsea2C | HOWW2D | HOWW6 | 2023 | Addition | TBC |  |  | 270 | 220/66
Seagreen Wind Energy Ltd | Firth of Forth I | Offshore PLATFORM 1 275kV | Seagreen 66kV | 2023 | Addition | TBC |  |  | 400 | 275/66
" | Firth of Forth I | Offshore PLATFORM 2 275kV | Seagreen 66kV | 2023 | Addition | TBC |  |  | 400 | 275/66
" | Firth of Forth I | Offshore PLATFORM 3 275kV | Seagreen 66kV | 2023 | Addition | TBC |  |  | 400 | 275/66
East Anglia THREE Limited | East Anglia 3A | BRFO41 | Onshore HVDC Converter station | 2023 | Addition | TBC |  |  | TBC | 400/320
" | East Anglia 3A | Onshore HVDC Converter station | Offshore HVDC Converter station | 2023 | Addition | TBC |  |  | TBC | 320/220
" | East Anglia 3A | Offshore platform A | EAAW31 | 2023 | Addition | TBC |  |  | TBC | 220/33
" | East Anglia 3B | Offshore platform B | EAAW31 | 2025 | Addition | TBC |  |  | TBC | 220/33
Orsted Hornsea Project Three Uk Ltd | Hornsea 3A | HVDC Onshore 400kV | HVDC Onshore 500kV | 2025 | Addition | TBC |  |  | 850 | 500/400
" | Hornsea 3A | HVDC Onshore 400kV | HVDC Onshore 500kV | 2025 | Addition | TBC |  |  | 850 | 500/400
" | Hornsea 3B | HVDC Offshore 500kV | HVDC Offshore 66kV | 2025 | Addition | TBC |  |  | 850 | 500/66
" | Hornsea 3B | HVDC Offshore 500kV | HVDC Offshore 66kV | 2025 | Addition | TBC |  |  | 850 | 500/66
Moray Offshore Windfarm (West) Limited | Moray Offshore (WDA) | Moray Onshore 400kV | Moray Onshore 220kV | 2025 | Addition | TBC |  |  | TBC | 400/220
" | Moray Offshore (WDA) | Moray Onshore 400kV | Moray Onshore 220kV | 2025 | Addition | TBC |  |  | TBC | 400/220
" | Moray Offshore (WDA) | Moray Offshore 220kV | Moray Offshore 66 kV | 2025 | Addition | TBC |  |  | TBC | 220/66
" | Moray Offshore (WDA) | Moray Offshore 220kV | Moray Offshore 66 kV | 2025 | Addition | TBC |  |  | TBC | 220/66
Seagreen Wind Energy Ltd | Firth of Forth 2 | Offshore 275kV | Seagreen 66kV | 2025 | Addition | TBC |  |  | 430 | 275/66
" | Firth of Forth 2 | Offshore 275kV | Seagreen 66kV | 2025 | Addition | TBC |  |  | 430 | 275/66
" | Firth of Forth 2 | Offshore 275kV | Seagreen 66kV | 2025 | Addition | TBC |  |  | 430 | 275/66
" | Firth of Forth 2 | Offshore 275kV | Seagreen 66kV | 2028 | Addition | TBC |  |  | 430 | 275/66
" | Firth of Forth 2 | Offshore 275kV | Seagreen 66kV | 2028 | Addition | TBC |  |  | 430 | 275/66
" | Firth of Forth 2 | Offshore 275kV | Seagreen 66kV | 2028 | Addition | TBC |  |  | 430 | 275/66
Orsted Hornsea Project Four Limited | Hornsea 4 | Onshore 400 kV | Onshore 275kV | 2028 | Addition | TBC |  |  | 594 | 400/275
" | Hornsea 4 | Onshore 400 kV | Onshore 275kV | 2028 | Addition | TBC |  |  | 594 | 400/275
" | Hornsea 4 | Onshore 400 kV | Onshore 275kV | 2028 | Addition | TBC |  |  | 594 | 400/275
" | Hornsea 4 | Onshore 400 kV | Onshore 275kV | 2028 | Addition | TBC |  |  | 594 | 400/275
" | Hornsea 4 | Onshore 400 kV | Onshore 275kV | 2028 | Addition | TBC |  |  | 594 | 400/275
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66
" | Hornsea 4 | Offshore platform 275kV | Offshore platform 66kV | 2028 | Addition | TBC |  |  | 338 | 275/66

## B-4-1a
Table B.4.1a - SHE Transmission Reactive Compensation Equipment, Winter 2019/20
Site Name | Node | Unit Number | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ABERDEEN BAY | ABBA1- | 1 | 13.38 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1J | 1 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1K | 2 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
BEAULY | BEAU3U | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU3V | 2 |  | 90 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Z | 4 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT1- | 1 |  | 100 | Shunt Reactor | 132
KINTORE | KINT1B | 2 |  | 100 | Shunt Reactor | 132
KINTORE | KINT3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
MACDUFF | MACD3- | 1 | 10 |  | Mechanically Switched Capacitor | 33
MELGARVE | MELG4J | 1 | 100 | 100 | STATCOM | 400
MELGARVE | MELG4K | 1 | 100 | 100 | STATCOM | 400
TEALING | TEAL1- | 1 |  | 100 | Shunt Reactor | 132
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275
TEALING | TEAL3W | 1 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 2 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL10 | 1 | 45 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL10 | 2 | 45 |  | Mechanically Switched Capacitor | 132

## B-4-1b
Table B.4.1b - SPT Reactive Compensation Equipment, Winter 2019/20
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Auchencrosh | AUCH2- | 1 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 2 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 3 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 4 | 59 |  | FILTER BANK | 275
Auchencrosh | AUCH2- | 5 | 59 |  | FILTER BANK | 275
Bonnybridge | BONN3U | 1 |  | 60 | REACTOR | 33
Bonnybridge | BONN3V | 2 |  | 60 | REACTOR | 33
COALBURN | COAL3U | 1 |  | 60 | REACTOR | 33
COCKENZIE | COCK2- | 1 | 230 |  | MSCDN | 275
CRYSTAL RIG | CRYR3V | 1 |  | 60 | REACTOR | 33
Currie | CURR3W | 3 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 1 |  | 60 | REACTOR | 33
DEWAR PLACE | DEWP3- | 2 |  | 60 | REACTOR | 33
ECCLES | ECCL3V | 1 |  | 60 | REACTOR | 33
ELVANFOOT | ELVA4- | 1 | 225 |  | MSCDN | 400
ELVANFOOT | ELVA3V | 1 |  | 60 | REACTOR | 33
GIFFNOCK | GIFF3A | 1 |  | 60 | REACTOR | 33
Hunterston Converter Station | HUCS4- | 1 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 2 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 3 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 4 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 5 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 6 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 7 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 8 | 240 |  | FILTER BANK | 400
Hunterston Converter Station | HUCS4- | 1 |  | 200 | REACTOR | 400
Hunterston Converter Station | HUCS4- | 1 | 382 | -248 | STATCOM | 400
HUNTERSTON NORTH | HUNN3W | 1 |  | 60 | REACTOR | 33
HUNTERSTON NORTH | HUNN3X | 2 |  | 60 | REACTOR | 33
KILLGALLIOCH WIND FARM | KILG2- | 1 |  | 60 | REACTOR | 275
KILMARNOCK SOUTH | KILS3U | 4 |  | 60 | REACTOR | 33
LONGANNET | LOAN2- | 1 | 230 |  | MSCDN | 275
LONGANNET | LOAN2- | 2 | 230 |  | MSCDN | 275
MARK'S HILL | MAHI3U | 2 |  | 60 | REACTOR | 33
MOFFAT | MOFF4- | 1 | 230 |  | MSCDN | 400
MOFFAT | MOFF3U | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3U | 1 |  | 60 | REACTOR | 33
NEILSTON | NEIL3V | 2 |  | 60 | REACTOR | 33
Shrubhill | SHRU3- | 1 |  | 60 | REACTOR | 33
Shrubhill | SHRU3- | 2 |  | 60 | REACTOR | 33
TORNESS | TORN4- | 1 | 9 |  | FILTER BANK | 400
TORNESS | TORN4- | 1 |  | 150 | REACTOR | 400
TORNESS | TORN4- | 2 |  | 150 | REACTOR | 400
WINDYHILL | WIYH3W | 3 |  | 60 | REACTOR | 33
WINDYHILL | WIYH2- | 1 | 150 |  | MSCDN | 275
WISHAW | WISH3W | 1 |  | 60 | REACTOR | 33
Phoenix Hybrid Reactive Compensation | NEIL2- | 1 | 70 | 33 | Synch Comp | 275
Phoenix Hybrid Reactive Compensation | NEIL2- | 1 | 70 | 70 | STATCOM | 275

## B-4-1c
Table B.4.1c - NGET Reactive Compensation Equipment, Winter 2019/20
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
Aberthaw | ABTH11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Aberthaw | ABTH11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Abham | ABHA11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Abham | ABHA11 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Alverdiscott | ALVE11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Barking | BARK21 | 2B WDG 1 |  | 30 | Reactor | 275
Barking | BARK21 | 2B WDG 2 |  | 30 | Reactor | 275
Barking | BARK21 | 4B WDG 1 |  | 30 | Reactor | 275
Barking | BARK21 | 4B WDG 2 |  | 30 | Reactor | 275
Beddington | BEDD21 | 3B | 155 |  | Mechanically Switched Capacitor | 275
Beddington | BEDD21 | 4B | 155 |  | Mechanically Switched Capacitor | 275
Beddington | BEDD21 | 1B |  | 60 | Reactor | 275
Beddington | BEDD21 | 2B |  | 60 | Reactor | 275
Beddington | BEDD21 | 3B |  | 60 | Reactor | 275
Beddington | BEDD21 | 4B |  | 60 | Reactor | 275
Beddington | BEDD21 | 5B |  | 100 | Reactor | 275
Beddington | BEDD21 | 6A |  | 100 | Reactor | 275
Berkswell | BESW21 | 4 | 150 |  | Mechanically Switched Capacitor | 275
Berkswell | BESW11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Berkswell | BESW11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Berkswell | BESW11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Birkenhead | BIRK11 | 4 WDG A |  | 30 | Reactor | 132
Birkenhead | BIRK11 | 4 WDG B |  | 30 | Reactor | 132
Bridgewater | BRWA21 | G | 60 | 60 | SVC | 275
Bishops Wood | BISW11 | A | 60 |  | Mechanically Switched Capacitor | 132
Bishops Wood | BISW11 | B | 60 |  | Mechanically Switched Capacitor | 132
Bishops Wood | BISW11 | C | 60 |  | Mechanically Switched Capacitor | 132
Blyth | BLYT21 | 1 | 155 |  | Mechanically Switched Capacitor | 275
Blyth | BLYT21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
Bolney | BOLN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Bolney | BOLN41 | 1 |  | 55 | Reactor | 400
Bolney | BOLN41 | 2 |  | 55 | Reactor | 400
Bolney | BOLN41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | BOLN41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | BOLN41 | 6 | 100 | -225 | SVC | 400
Bradford West | BRAW11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Bradford West | BRAW21 | 3 |  | 60 | Reactor | 275
Bradford West | BRAW21 | 4 WDG A |  | 30 | Reactor | 275
Bradford West | BRAW21 | 4 WDG B |  | 30 | Reactor | 275
Bramford | BRFO11 | A | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO11 | B | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO11 | C | 60 |  | Mechanically Switched Capacitor | 132
Bramford | BRFO41 | 1 |  | 200 | Reactor | 400
Bredbury | BRED21 | 1 WDG 1 |  | 30 | Reactor | 275
Bredbury | BRED21 | 1 WDG 2 |  | 30 | Reactor | 275
Bredbury | BRED21 | 3 WDG 1 |  | 30 | Reactor | 275
Bredbury | BRED21 | 3 WDG 2 |  | 30 | Reactor | 275
Bridgewater | BRWA11 | 1A | 40 |  | Mechanically Switched Capacitor | 132
Bridgewater | BRWA11 | 1B | 40 |  | Mechanically Switched Capacitor | 132
Bridgewater | BRWA2A | G | 60 | -60 | SVC | 275
Bushbury | BUSH21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
Bushbury | BUSH11 | A | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH11 | B | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH11 | C | 60 |  | Mechanically Switched Capacitor | 132
Bushbury | BUSH21 | 3 |  | 60 | Reactor | 275
Bustleholm | BUST21 | 4 | 20 |  | Mechanically Switched Capacitor | 275
Bustleholm | BUST21 | 4 |  | 60 | Reactor | 275
Bustleholm | BUST21 | 1 WDG A |  | 30 | Reactor | 275
Bustleholm | BUST21 | 1 WDG B |  | 30 | Reactor | 275
Canterbury | CANT41 | 4 |  | 200 | Reactor | 400
Capenhurst | CAPE21 | 1 | 155 |  | Mechanically Switched Capacitor | 275
Cellarhead | CELL12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | CELL41 | 8 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | CELL11 | 2A | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2B | 60 |  | Mechanically Switched Capacitor | 132
Cellarhead | CELL41 | 2 WDG A |  | 30 | Reactor | 400
Cellarhead | CELL41 | 2 WDG B |  | 30 | Reactor | 400
Cellarhead | CELL41 | 3 WDG A |  | 30 | Reactor | 400
Cellarhead | CELL41 | 3 WDG B |  | 30 | Reactor | 400
Cellarhead | CELL41 | 5 | 95 | -150 | SVC | 400
Cellarhead | CELL41 | 6 | 95 | -150 | SVC | 400
Chesterfield | CHTE21 | 4 |  | 60 | Reactor | 275
Chickerell | CHIC42 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Chickerell | CHIC41 | 2 |  | 60 | Reactor | 400
Cilfynydd | CILF41 | 1 |  | 60 | Reactor | 400
Cilfynydd | CILF41 | 2 |  | 60 | Reactor | 400
Cilfynydd | CILF41 | 4 |  | 200 | Reactor | 400
Cilfynydd | CILF41 | 6 |  | 200 | Reactor | 400
City Road | CITR41 | 4 | 55 |  | Mechanically Switched Capacitor | 400
City Road | CITR41 | 2 | 55 |  | Mechanically Switched Capacitor | 400
City Road | CITR41 | 1 |  | 200 | Reactor | 400
Connah's Quay | CONQ41 | 1 WDG 1 |  | 30 | Reactor | 400
Connah's Quay | CONQ41 | 1 WDG 2 |  | 30 | Reactor | 400
Coventry | COVE11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Coventry | COVE21 | 3 |  | 60 | Reactor | 275
Coventry | COVE21 | A | 60 | -60 | SVC | 275
Cowley | COWL11 | A | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL11 | B | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL11 | C | 60 |  | Mechanically Switched Capacitor | 132
Cowley | COWL41 | 2 |  | 200 | Reactor | 400
Cowley | COWL41 | 3 |  | 200 | Reactor | 400
Didcot | DIDC41 | A |  | 2640 | Series Reactor (bypassed) | 400
Drakelow | DRAK41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Drakelow | DRAK41 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Drakelow | DRAK41 | 4 |  | 200 | Reactor | 400
Drakelow | DRAK41 | 6 |  | 200 | Reactor | 400
Drax | DRAX41 | 1 |  | 60 | Reactor | 400
Drax | DRAX41 | 2 |  | 60 | Reactor | 400
Drax | DRAX41 |  |  | 1320 | Series Reactor (bypassed) | 400
East Claydon | ECLA41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
East Claydon | ECLA41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
East Claydon | ECLA12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
East Claydon | ECLA41 | 1 WDG A |  | 30 | Reactor | 400
East Claydon | ECLA41 | 1 WDG B |  | 30 | Reactor | 400
East Claydon | ECLA41 | 2 WDG A |  | 30 | Reactor | 400
East Claydon | ECLA41 | 2 WDG B |  | 30 | Reactor | 400
East Claydon | ECLA40 | 6 | 202 | -225 | SVC | 400
Elland | ELLA21 | 2 |  | 60 | Reactor | 275
Elstree | ELST41 | 1 |  | 200 | Reactor | 400
Elstree | ELST21 | M | 60 | -60 | SVC | 275
Elstree | ELST22 | L | 60 | -60 | SVC | 275
Elstree | ELST41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Enderby | ENDE41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Enderby | ENDE41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Exeter | EXET41 | 1 | 25 |  | Mechanically Switched Capacitor | 400
Exeter | EXET41 | 2 | 25 |  | Mechanically Switched Capacitor | 400
Exeter | EXET11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Exeter | EXET41 | 3 | 95 | -150 | SVC | 400
Exeter | EXET41 | 5 | 95 | -150 | SVC | 400
Feckenham | FECK41 | 4 WDG A |  | 30 | Reactor | 400
Feckenham | FECK41 | 4 WDG B |  | 30 | Reactor | 400
Feckenham | FECK21 | 6 | 125 | -145 | SVC | 275
Fiddlers Ferry | FIDF21 |  |  | 750 | Series Reactor (bypassed) | 275
Fiddlers Ferry | FIDF21 |  |  | 750 | Series Reactor (bypassed) | 275
Fleet | FLEE41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Fleet | FLEE11 | 2A | 50 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2B | 50 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2C | 50 |  | Mechanically Switched Capacitor | 132
Fleet | FLEE41 | 3A WDG 1 |  | 30 | Reactor | 400
Fleet | FLEE41 | 3A WDG 2 |  | 30 | Reactor | 400
Fleet | FLEE41 | 4A WDG 1 |  | 30 | Reactor | 400
Fleet | FLEE41 | 4A WDG 2 |  | 30 | Reactor | 400
Flintshire Bridge | FLIB41 | 1 |  | 0.01 | Reactor | 400
Flintshire Bridge | FLIB41 | 2 |  | 0.01 | Reactor | 400
Flintshire Bridge | FLIB41 | 3 |  | 0.01 | Reactor | 400
Grain | GRAI41 | 1 |  | 200 | Reactor | 400
Grain | GRAI41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Britned | BRIT41 | 1 |  | 67 | Series Reactor (bypassed) | 400
Britned | BRIT41 | 2 |  | 67 | Series Reactor (bypassed) | 400
Grendon | GREN41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 6 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 4 | 225 |  | Mechanically Switched Capacitor | 400
Grendon | GREN11 | 1A | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN11 | 1B | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN11 | 1C | 60 |  | Mechanically Switched Capacitor | 132
Grendon | GREN41 | 1 |  | 60 | Reactor | 400
Greystones | GRSB21 | 3 |  | 100 | Reactor | 275
Greystones | GRSB21 | 1 |  | 100 | Reactor | 275
Hams Hall | HAMH40 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Hams Hall | HAMH40 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 4 |  | 200 | Reactor | 400
Harker | HARK41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3A | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3B | 225 |  | Mechanically Switched Capacitor | 400
Harker | HARK21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
Harker | HARK21 | 7 | 125 | -145 | SVC | 275
Harker | HARK22 | 8 | 125 | -145 | SVC | 275
Hurst | HURS21 | 2B | 155 |  | Mechanically Switched Capacitor | 275
Hurst | HURS21 | 2 |  | 60 | Reactor | 275
Hurst | HURS21 | 3 |  | 60 | Reactor | 275
Hurst | HURS21 | 4 |  | 100 | Reactor | 275
Hurst | HURS21 | 7 |  | 100 | Reactor | 275
Hurst | HURS21 | 1 |  | 100 | Reactor | 275
Hurst | HURS21 | 2A |  | 100 | Reactor | 275
Hutton | HUTT41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Hutton | HUTT41 | 1 |  | 2750 | Series Reactor (bypassed) | 400 (in parallel with series capacitor)
Hutton | HUTT41 | 2 |  | 2750 | Series Reactor (bypassed) | 400 (in parallel with series capacitor)
Hutton | HUTT41 | 1 |  | 2770 | Thyristor Controlled Series Capacitor (bypassed) | 400
Hutton | HUTT41 | 2 |  | 2770 | Thyristor Controlled Series Capacitor (bypassed) | 400
Hedon | HEDN11 | 1 |  | 15 | Reactor | 150
Hedon | HEDN11 | 2 |  | 15 | Reactor | 150
Indian Queens | INDQ41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Indian Queens | INDQ11 |  | 55 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ11 | 4 | 55 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ11 | 3 | 55 |  | Mechanically Switched Capacitor | 132
Indian Queens | INDQ41 | 2 |  | 200 | Reactor | 400
Indian Queens | INDQ41 | 1 |  | 60 | Reactor | 400
Iron Acton | IROA21 | 6 | 45 |  | Mechanically Switched Capacitor | 132
Iron Acton | IROA21 | E | 60 | -60 | SVC | 275
Iron Acton | IROA21 | F | 60 | -60 | SVC | 275
Ironbridge | IRON41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
Ironbridge | IRON11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Iver | IVER21 | 1A |  | 60 | Reactor | 275
Iver | IVER4B | 5A |  | 55 | Reactor | 400
Iver | IVER4A | 6B |  | 55 | Reactor | 400
Jordanthorpe | JORD21 | 1 |  | 60 | Reactor | 275
Kearsley | KEAR11 | A | 50 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | B | 50 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | C | 50 |  | Mechanically Switched Capacitor | 132
Kearsley | KEAR41 | 3A |  | 60 | Reactor | 400
Killingholme | KILL41 |  |  | 2750 | Series Reactor (bypassed) | 400
Kingsnorth | KINO41 | 3 |  | 200 | Reactor | 400
Kingsnorth | KINO41 | 4 |  | 200 | Reactor | 400
Kingsnorth | KINO41 | 1 WDG 1 |  | 25 | Reactor | 400
Kingsnorth | KINO41 | 1 WDG 2 |  | 25 | Reactor | 400
Kingsnorth | KINO41 | 2 WDG 1 |  | 25 | Reactor | 400
Kingsnorth | KINO41 | 2 WDG 2 |  | 25 | Reactor | 400
Kingsnorth | KINO41 | 1 |  | 2000 | Series Reactor (bypassed) | 400
Kirkby | KIBY41 | 1A | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY42 | 2A | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY42 | 3B | 45 |  | Mechanically Switched Capacitor | 132
Kirkby | KIBY41 | 4A | 45 |  | Mechanically Switched Capacitor | 132
Kirkstall | KIRK21 | 3 | 150 |  | Mechanically Switched Capacitor | 275
Kirkstall | KIRK21 | 2 |  | 60 | Reactor | 275
Kirkstall | KIRK21 | 4 |  | 60 | Reactor | 275
Lackenby | LACK21 | A | 20 |  | Mechanically Switched Capacitor | 275
Lackenby | LACK21 | B | 20 |  | Mechanically Switched Capacitor | 275
Lackenby | LACK21 | C | 20 |  | Mechanically Switched Capacitor | 275
Laleham | LALE21 | 3 |  | 100 | Reactor | 275
Laleham | LALE21 | 1 |  | 100 | Reactor | 275
Laleham | LALE21 | 2 |  | 100 | Reactor | 275
Landulph | LAND11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Landulph | LAND42 | 1 |  | 200 | Reactor | 400
Landulph | LAND41 | 2 WDG A |  | 30 | Reactor | 400
Landulph | LAND41 | 2 WDG B |  | 30 | Reactor | 400
Landulph | LAND42 | H | 60 | -60 | SVC | 400
Legacy | LEGA41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Legacy | LEGA41 | 1 |  | 60 | Reactor | 400
Legacy | LEGA41 | 2 |  | 60 | Reactor | 400
Lister Drive | LISD21 | 1 |  | 100 | Reactor | 275
Lister Drive | LISD21 |  |  | 750 | Series Reactor (bypassed) | 275 (Birkenhead circuit)
Lovedean | LOVE41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Lovedean | LOVE41 | 3 |  | 60 | Reactor | 400
Lovedean | LOVE41 | 7 |  | 200 | Reactor | 400
Lovedean | LOVE41 | 1 |  | 200 | Reactor | 400
Lovedean | LOVE41 | 4A |  | 60 | Reactor | 400
Lovedean | LOVE41 | 5 | 95 | -150 | SVC | 400
Mannington | MANN11 | A | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN11 | B | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN11 | C | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN11 | A | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN11 | B | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN11 | C | 60 |  | Mechanically Switched Capacitor | 132
Mannington | MANN41 | 1 | 95 | -150 | SVC | 400
Mannington | MANN41 | 2 | 95 | -150 | SVC | 400
Melksham | MELK11 | A | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK11 | B | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK11 | C | 60 |  | Mechanically Switched Capacitor | 132
Melksham | MELK41 | 5 |  | 60 | Reactor | 400
Melksham | MELK41 | 6 |  | 60 | Reactor | 400
Melksham | MELK41 | 1 |  | 200 | Reactor | 400
Mill Hill | MILH21 | 1B WDNG 1 |  | 25 | Reactor | 275
Mill Hill | MILH21 | 1B WDNG 2 |  | 25 | Reactor | 275
Mill Hill | MILH21 | 2A WDNG 1 |  | 25 | Reactor | 275
Mill Hill | MILH21 | 2A WDNG 2 |  | 25 | Reactor | 275
Monk Fryston | MONF22 | 1 | 155 |  | Mechanically Switched Capacitor | 275
Nechells | NECH21 | A |  | 60 | Reactor | 275
Nechells | NECH21 | WDG 1 |  | 30 | Reactor | 275
Nechells | NECH21 | WDG 2 |  | 30 | Reactor | 275
Newcross | NEWX21 | 5 |  | 100 | Reactor | 275
Newcross | NEWX21 | 6 |  | 100 | Reactor | 275
Ninfield | NINF41 | 5 | 100 | -225 | SVC | 400
Ninfield | NINF41 | 6 | 150 | -200 | SVC | 400
Ninfield | NINF41 | 1 |  | 200 | Reactor | 400
Ninfield | NINF41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Norwich Trowse | NORW11 | A | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW11 | B | 60 |  | Mechanically Switched Capacitor | 132
Norwich Trowse | NORW11 | C | 60 |  | Mechanically Switched Capacitor | 132
Nursling | NURS41 | 2 |  | 60 | Shunt Reactor | 400
Ocker Hill | OCKH21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
Oldbury | OLDB21 | WDG A |  | 30 | Reactor | 275
Oldbury | OLDB21 | WDG B |  | 30 | Reactor | 275
Pelham | PELH41 | 3 |  | 200 | Reactor | 400
Pelham | PELH41 | 1 WDG A |  | 25 | Reactor | 400
Pelham | PELH41 | 1 WDG B |  | 25 | Reactor | 400
Pelham | PELH41 | 2 WDG A |  | 25 | Reactor | 400
Pelham | PELH41 | 2 WDG B |  | 25 | Reactor | 400
Pelham | PELH41 | 5 | 120 | -150 | SVC | 400
Pelham | PELH41 | 6 | 120 | -150 | SVC | 400
Pembroke | PEMB41 | 1 |  | 60 | Reactor | 400
Pembroke | PEMB41 | 2 |  | 60 | Reactor | 400
Penn | PENN21 | B | 60 | -60 | SVC | 275
Penrhos | PERH11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
Pentir | PENT41 | 1 |  | 200 | Reactor | 400
Pentir | PENT41 | 2 |  | 200 | Reactor | 400
Pentir | PENT41 | 5 |  | 200 | Reactor | 400
Penwortham | PEWO41 | 6 |  | 60 | Reactor | 400
Pitsmoor | PITS21 | 3 |  | 60 | Reactor | 275
Pitsmoor | PITS21 | 4 |  | 60 | Reactor | 275
Pyle | PYLE21 | J | 60 | -60 | SVC | 275
Pyle | PYLE21 | K | 60 | -60 | SVC | 275
Port Ham | PORH11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Port Ham | PORH11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 2 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 4 | 45 |  | Mechanically Switched Capacitor | 132
Ratcliffe-On-Soar | RATS41 | 3 |  | 60 | Reactor | 400
Ratcliffe-On-Soar | RATS41 | 2 |  | 200 | Reactor | 400
Rayleigh | RAYL41 | 5 |  | 60 | Reactor | 400
Richborough | RICH41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Richborough | RICH41 | 1 | 75 | -225 | SVC | 400
Rochdale | ROCH11 | A | 60 |  | Mechanically Switched Capacitor | 132
Rochdale | ROCH11 | B | 60 |  | Mechanically Switched Capacitor | 132
Rochdale | ROCH11 | C | 60 |  | Mechanically Switched Capacitor | 132
Sellindge | SELL41 | 1 | 155 | -200 | SVC | 400
Sellindge | SELL41 | 2 | 155 | -200 | SVC | 400
Sellindge | SELL41 |  |  | 1860 | Series Reactor (bypassed) | 400
Skelton Grange | SKLG11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG21 | 6 | 150 |  | Mechanically Switched Capacitor | 275
Skelton Grange | SKLG21 | 3 |  | 100 | Reactor | 275
Spennymoor | SPEN41 | 1 |  | 60 | Reactor | 400
St Johns Wood | SJOW12 | A | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW12 | B | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW12 | C | 60 |  | Mechanically Switched Capacitor | 132
St Johns Wood | SJOW41 | 2 |  | 200 | Reactor | 400
St Johns Wood | SJOW41 | 4 |  | 200 | Reactor | 400
St Johns Wood | SJOW21 | 2B |  | 55 | Reactor | 275
St Johns Wood | SJOW41 | 1 |  | 200 | Reactor | 400
St Johns Wood | SJOW21 | 1 | 144 | -150 | SVC | 275
St Johns Wood | SJOW21 | 3 | 144 | -150 | SVC | 275
Staythorpe | STAY41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Stella West | STEW21 | 2 | 100 |  | Reactor | 275
Sundon | SUND41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Sundon | SUND42 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Sundon | SUND41 | 5 WDG 1 |  | 30 | Reactor | 400
Sundon | SUND41 | 5 WDG 2 |  | 30 | Reactor | 400
Sundon | SUND42 | 8 WDG 1 |  | 30 | Reactor | 400
Sundon | SUND42 | 8 WDG 2 |  | 30 | Reactor | 400
Swansea | SWAN11 | A | 60 |  | Mechanically Switched Capacitor | 132
Swansea | SWAN11 | B | 60 |  | Mechanically Switched Capacitor | 132
Swansea | SWAN11 | C | 60 |  | Mechanically Switched Capacitor | 132
Thorpe Marsh | THOM41 | 2 |  | 200 | Reactor | 400
Thorpe Marsh | THOM42 | 6 |  | 200 | Reactor | 400
Tottenham | TOTT24 | 3 |  | 100 | Reactor | 275
Tottenham | TOTT21 | 5 |  | 100 | Reactor | 275
Tottenham | TOTT23 | 1 |  | 100 | Reactor | 275
Tynemouth | TYNE21 | 2A |  | 60 | Reactor | 275
Uskmouth | USKM11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
Uskmouth | USKM11 | 1 |  | 90 | Series Reactor | 132
Walham | WALH41 | 2 |  | 60 | Reactor | 400
Walham | WALH41 | 3 |  | 60 | Reactor | 400
Walham | WALH41 | 4 |  | 200 | Reactor | 400
Walham | WALH41 | 1 | 60 |  | Mechanically Switched Capacitor | 400
Walpole | WALP11 | 4A | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 4B | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 4C | 60 |  | Mechanically Switched Capacitor | 132
Walpole | WALP41 | 1 |  | 55 | Reactor | 400
Walpole | WALP41 | 2 |  | 55 | Reactor | 400
Walpole | WALP41 | 3 |  | 55 | Reactor | 400
Warley | WARL11 | A | 50 |  | Mechanically Switched Capacitor | 132
Warley | WARL11 | B | 50 |  | Mechanically Switched Capacitor | 132
Warley | WARL11 | C | 50 |  | Mechanically Switched Capacitor | 132
West Burton | WBUR42 | 1 |  | 200 | Reactor | 400
West Burton | WBUR41 |  |  | 1500 | Series Reactor (bypassed) | 400
West Ham | WHAM41 | 4 | 225 |  | Mechanically Switched Capacitor | 400
West Ham | WHAM41 | 1 |  | 200 | Reactor | 400
West Melton | WMEL12 | 3A | 45 |  | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3B | 45 |  | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3C | 45 |  | Mechanically Switched Capacitor | 132
West Thurrock | WTHU41 | 1 |  | 2400 | Series Reactor (bypassed) | 400 (Littlebrook-Tilbury circuit)
West Thurrock | WTHU41 | 2 |  | 2400 | Series Reactor (bypassed) | 400 (Littlebrook-Tilbury circuit)
West Weybridge | WWEY41 | 1 |  | 100 | Reactor | 400
West of Duddon Sands Onshore | WDSO12 | 1A |  | 30 | Reactor | 155
West of Duddon Sands Onshore | WDSO11 | 2A |  | 30 | Reactor | 155
West of Duddon Sands Onshore | WDSO11 | 4 |  | 60 | Reactor | 155
Whitegate | WHGA21 | 2 | 150 |  | Mechanically Switched Capacitor | 275
Whitegate | WHGA20 | 4A |  | 60 | Reactor | 275
Whitegate | WHGA20 | 4B |  | 60 | Reactor | 275
Willesden | WISD21 | 2B |  | 55 | Reactor | 275
Willesden | WISD21 | 3B WDG 1 |  | 25 | Reactor | 275
Willesden | WISD21 | 3B WDG 2 |  | 25 | Reactor | 275
Willington | WILE41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Willington | WILE41 | 8 | 95 | -150 | SVC | 400
Wimbledon | WIMB21 | 2 |  | 100 | Reactor | 275
Wimbledon | WIMB21 | 4 |  | 100 | Reactor | 275
Wimbledon | WIMB41 | 6 |  | 225 | Reactor | 400
Wymondley | WYMO41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Wymondley | WYMO41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Wymondley | WYMO41 | 3 |  | 200 | Reactor | 400

## B-4-2a
Table B.4.2a - SHE Transmission Reactive Compensation Equipment, 20121/22 to 2028/29
Site Name | Node | Unit Number | Year | Status | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
MEIKLETON FARM | MEIK3- | 1 | 2020 | Addition |  | 2 | Shunt Reactor | 33
DOUNREAY | DOUN3Y | 1 | 2023 | Addition |  | 90 | Shunt Reactor - SGT tertiary | 33
ORKNEY FINSTOWN | FINS3Y | 1 | 2023 | Addition |  | 90 | Shunt Reactor - SGT tertiary | 33
ALYTH | ALYT2A | 1 | 2023 | Addition | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | ALYT2A | 1 | 2023 | Addition | 225 | 75 | SVC | 275
ORKNEY FINSTOWN | FINS1- | 1 | 2023 | Addition | 70 | 35 | Synchronous Condenser | 132
ORKNEY FINSTOWN | FINS1- | 2 | 2023 | Addition | 70 | 35 | Synchronous Condenser | 132
DOUNREAY | DOUN3Z | 1 | 2025 | Addition |  | 90 | Shunt Reactor - SGT tertiary | 33
ORKNEY FINSTOWN | FINS3Z | 1 | 2025 | Addition |  | 90 | Shunt Reactor - SGT tertiary | 33
TUMMEL | TUMM2J | 1 | 2025 | Addition | 100 |  | Mechanically Switched Capacitor | 275
TUMMEL | TUMM2J | 1 | 2025 | Addition | 225 | 75 | SVC | 275
ALYTH | ALYT2A | 1 | 2028 | Removal | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | ALYT4J | 1 | 2028 | Addition | 100 |  | Mechanically Switched Capacitor | 400
ALYTH | ALYT2A | 1 | 2028 | Removal | 225 | 75 | SVC | 275
ALYTH | ALYT4J | 1 | 2028 | Addition | 225 | 75 | SVC | 400

## B-4-2b
Table B.4.2b - SPT Reactive Compensation Equipment, 2021/22 to 2028/29
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
SMEATON | Addition | 2020 | SMEA3U | 1 |  | 60 | REACTOR | 33
SMEATON | Addition | 2020 | SMEA3V | 1 |  | 60 | REACTOR | 33
Shrubhill | Remove | 2021 | SHRU3- | 2 |  | 60 | REACTOR | 33
Hunterston Synch Comp | Addition | 2025 | HUER4- | 1 | 300 | 140 | Synch Comp | 400
Kincardine Synch Comp | Addition | 2025 | KINC2- | 1 | 300 | 140 | Synch Comp | 275
Strathaven Synch Comp | Addition | 2025 | STHA4A | 1 | 150 | 70 | Synch Comp | 400
Strathaven Synch Comp | Addition | 2025 | STHA4B | 1 | 150 | 70 | Synch Comp | 400
Eccles Hybrid Reactive Compensation | Addition | 2025 | ECCL4A | 1 | 150 | 70 | Synch Comp | 275
Eccles Hybrid Reactive Compensation | Addition | 2025 | ECCL4A | 1 | 150 | 150 | STATCOM | 275
Eccles Hybrid Reactive Compensation | Addition | 2025 | ECCL4B | 1 | 150 | 70 | Synch Comp | 275
Eccles Hybrid Reactive Compensation | Addition | 2025 | ECCL4B | 1 | 150 | 150 | STATCOM | 275

## B-4-2c
Table B.4.2c - NGET Reactive Compensation Equipment, 2019/20 to 2027/28
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Iver | Addition | 2020 | IVER21 | 3A |  | 60 | Reactor | 275
Ninfield | Removed | 2020 | NINF41 | 6 | 150 | -198.3 | SVC | 400
Sellindge | Removed | 2020 | SELL41 | 1 | 155 | -200 | SVC | 400
Sellindge | Removed | 2020 | SELL41 | 2 | 155 | -200 | SVC | 400
Washway Farm | Addition | 2020 | WASF22 | 1 | 0 | 0 | Power Control Device(bypassed) | 275
Washway Farm | Addition | 2020 | WASF21 | 2 | 0 | 0 | Power Control Device(bypassed) | 275
Washway Farm | Addition | 2020 | WASF21 | 3 | 0 | 0 | Power Control Device(bypassed) | 275
Washway Farm | Addition | 2020 | WASF22 | 4 | 0 | 0 | Power Control Device(bypassed) | 275
Stella West | Addition | 2020 | STEW41 | 1 | 0 | 0 | Power Control Device(bypassed) | 400
Stella West | Addition | 2020 | STEW41 | 2 | 0 | 0 | Power Control Device(bypassed) | 400
Stella West | Addition | 2020 | STEW41 | 3 | 0 | 0 | Power Control Device(bypassed) | 400
Stella West | Addition | 2020 | STEW41 | 4 | 0 | 0 | Power Control Device(bypassed) | 400
Pentir | Removed | 2021 | PENT41 | 1 |  | 200 | Reactor | 400
Ninfield | Addition | 2021 | NINF41 | 9 | 75 | -160 | SVC | 400
Bolney | Addition | 2023 | BOLN41 | 8 | 225 |  | Mechanically Switched Capacitor | 400
Bolney | Addition | 2023 | BOLN41 | 10 | 65 |  | Mechanically Switched Capacitor | 400
Burwell | Addition | 2023 | BURW41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Burwell | Addition | 2023 | BURW41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Burwell | Addition | 2023 | BURW41 | 3 | 225 |  | Mechanically Switched Capacitor | 400
Ninfield | Addition | 2023 | NINF41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Ninfield | Addition | 2023 | NINF41 | 7 | 65 |  | Mechanically Switched Capacitor | 400
Ninfield | Addition | 2023 | NINF41 | 9 | 75 | -160 | SVC | 400
Norton | Addition | 2023 | NORT41 | 1 | 200 |  | Mechanically Switched Capacitor | 400
Wimbledon | Addition | 2023 | WIMB41 | 5 |  | 200 | Reactor | 400
Wimbledon | Removed | 2023 | WIMB21 | 2 |  | 100 | Reactor | 275
Wimbledon | Removed | 2023 | WIMB21 | 4 |  | 100 | Reactor | 275
Bolney | Addition | 2023 | BOLN41 | 9 | 75 | -160 | SVC | 400
Osbaldwick | Addition | 2023 | OSBA41 | 1 | 200 |  | Mechanically Switched Capacitor | 400
Stella West | Addition | 2023 | STEW41 | 3 | 200 |  | Mechanically Switched Capacitor | 400
Thornton | Addition | 2023 | THTO43 | 1 |  | 2470 | Series Reactor | 400
Thornton | Addition | 2023 | THTO43 | 2 |  | 2470 | Series Reactor | 400
Wimbledon | Addition | 2023 | WIMB11 | 1 |  | 90 | Series Reactor | 132
Wimbledon | Addition | 2023 | WIMB11 | 2 |  | 90 | Series Reactor | 132
Eaton Socon | Addition | 2028 | EASO41 | 10 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Stella West | Addition | 2028 | STEW41 | 11 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Stoke Bardolph | Addition | 2028 | STOB41 | 12 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Sundon | Addition | 2028 | SUND41 | 13 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Penwortham | Addition | 2028 | PEWO41 | 3 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Penwortham | Addition | 2028 | PEWO41 | 4 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Hutton | Addition | 2028 | HUTT41 | 5 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Hutton | Addition | 2028 | HUTT41 | 6 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Padiham | Addition | 2028 | PADI41 | 8 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Eaton Socon | Addition | 2028 | EASO41 | 9 | 225 |  | Dummy Mechanically Switched Capacitor | 400
Cellarhead | Addition | 2028 | CELL41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Cellarhead | Addition | 2028 | CELL41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Daines | Addition | 2028 | DAIN41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Ironbridge | Addition | 2028 | IRON41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Ironbridge | Addition | 2028 | IRON41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Legacy | Addition | 2028 | LEGA41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Legacy | Addition | 2028 | LEGA41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Padiham | Addition | 2028 | PADI41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Penwortham | Addition | 2028 | PEWO41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
Penwortham | Addition | 2028 | PEWO41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
Hinkley Point C | Addition | 2028 | HIKP41 |  |  | 2000 | Series Reactor | 400
Stella West | Addition | 2028 | STEW41 | 3 | 200 |  | Mechanically Switched Capacitor | 400

## B-4-2d
Table B.4.2d - Indicative Offshore Reactive Compensation Equipment Changes, 2019/20 to 2027/28
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Hornsea Power Station 2A | Addition | 2020 | HOWB41 | SH3 |  | 85 | Reactor | 400
" | Addition | 2020 | HOWB41 | SH4 |  | 85 | Reactor | 400
" | Addition | 2020 | HOWB21 | SH1 |  | 300 | Reactor | 220
" | Addition | 2021 | HOWR2B1 | SH2 |  | 170 | Reactor | 220
" | Addition | 2021 | HOWW2D1 | SH3 |  | 90 | Reactor | 220
" | Addition | 2021 | HOWB41 | SVC1 | -160 | 145 | SVC | 400
Hornsea Power Station 2B | Addition | 2021 | HOWB21 | SH1 |  | 300 | Reactor | 220
" | Addition | 2021 | HOWR2B1 | SH2 |  | 170 | Reactor | 220
" | Addition | 2021 | HOWW2D1 | SH3 |  | 90 | Reactor | 220
" | Addition | 2021 | HOWB41 | SVC2 | -160 | 145 | SVC | 400
Hornsea Power Station 2C | Addition | 2021 | HOWB21 | SH1 |  | 300 | Reactor | 220
" | Addition | 2021 | HOWR2B1 | SH2 |  | 170 | Reactor | 220
" | Addition | 2021 | HOWW2D1 | SH3 |  | 90 | Reactor | 220
" | Addition | 2021 | HOWB41 | SVC3 | -160 | 145 | SVC | 400
Triton Knoll | Addition | 2021 | TKNW21 | 1 |  | 43 | Shunt Reactor | 220
Triton Knoll | Addition | 2021 | TKNE21 | 2 |  | 43 | Shunt Reactor | 220
Triton Knoll | Addition | 2021 | TKNW21 | 1 |  | 172 | Shunt Reactor | 220
Triton Knoll | Addition | 2021 | TKNE21 | 2 |  | 172 | Shunt Reactor | 220
Triton Knoll | Addition | 2021 | TKNW21 | 1 | -143 | 143 | SVC 1 | 220
Triton Knoll | Addition | 2021 | TKNE21 | 2 | -143 | 143 | SVC 2 | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 1 |  | 30 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 2 |  | 30 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 3 |  | 30 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 1 |  | 80 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 2 |  | 80 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 3 |  | 80 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 1 |  | 140-120 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 2 |  | 140-120 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 3 |  | 140-120 | Shunt Reactor | 220
Moray Firth (MORL) | Addition | 2021 | MORF21 | 1 | -125 | 144 | SVC | 33
Moray Firth (MORL) | Addition | 2021 | MORF21 | 2 | -125 | 144 | SVC | 33
Moray Firth (MORL) | Addition | 2021 | MORF21 | 3 | -125 | 144 | SVC | 33
Moray Firth (MORL) | Addition | 2021 | MORF21 | 1 |  | 40 | Shunt Reactor | 275
Moray Firth (MORL) | Addition | 2021 | MORF21 | 2 |  | 40 | Shunt Reactor | 275
Moray Firth (MORL) | Addition | 2021 | MORF21 | 3 |  | 40 | Shunt Reactor | 275
Firth of Forth 1 | Addition | 2023 | Phase1 Onshore | TBC |  | 150 | Reactor | 275
Firth of Forth 1 | Addition | 2023 | Phase1 Onshore | TBC |  | 150 | Reactor | 275
Firth of Forth 1 | Addition | 2023 | Phase1 Onshore | TBC |  | 150 | Reactor | 275
Firth of Forth 1 | Addition | 2023 | Phase1 Onshore | TBC |  | 150 | Reactor | 275
Firth of Forth 1 | Addition | 2023 | Phase1 Onshore | TBC |  | 150 | Reactor | 275
Firth of Forth 1 | Addition | 2023 | Phase1 Onshore | TBC |  | 150 | Reactor | 275
Hornsea 3A | Addition | 2025 | Onshore 400kV | 1 |  | 50 | Shunt Reactor | 400
Hornsea 3B | Addition | 2025 | Onshore 400kV | 1 |  | 50 | Shunt Reactor | 400
Firth of Forth 2 | Addition | 2025 | Onshore 275kV | 1 | 0 | 160 | SVC | 275
Firth of Forth 2 | Addition | 2025 | Onshore 275kV | 1 |  | TBC | Shunt Reactor | 275
Firth of Forth 2 | Addition | 2028 | Onshore 275kV | 4 |  | TBC | Shunt Reactor | 275
Firth of Forth 2 | Addition | 2028 | Onshore 275kV | 5 |  | TBC | Shunt Reactor | 275
Firth of Forth 2 | Addition | 2028 | Onshore 275kV | 6 |  | TBC | Shunt Reactor | 275
Firth of Forth 2 | Addition | 2028 | Onshore 275kV | 1 | 0 | 160 | SVC | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 1 | 0 | 300 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 2 | 0 | 300 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 3 | 0 | 300 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 4 | 0 | 300 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 5 | 0 | 300 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 1 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 2 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 3 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 4 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 275kV | 5 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Reactive Comp S/S 275kV | 1 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Reactive Comp S/S 275kV | 2 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Reactive Comp S/S 275kV | 3 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Reactive Comp S/S 275kV | 4 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Reactive Comp S/S 275kV | 5 | 0 | 150 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Offshore 275kV | 1 | 0 | 100 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Offshore 275kV | 2 | 0 | 100 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Offshore 275kV | 3 | 0 | 100 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Offshore 275kV | 4 | 0 | 100 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Offshore 275kV | 5 | 0 | 100 | Shunt Reactor | 275
Hornsea 4 | Addition | 2028 | Onshore 400kV | 1 | 0 | 75 | Shunt Reactor | 400
Hornsea 4 | Addition | 2028 | Onshore 400kV | 2 | 0 | 75 | Shunt Reactor | 400
Hornsea 4 | Addition | 2028 | Onshore 400kV | 1 | -200 | 200 | SVC | 400
Hornsea 4 | Addition | 2028 | Onshore 400kV | 2 | -200 | 200 | SVC | 400
Hornsea 4 | Addition | 2028 | Onshore 400kV | 3 | -200 | 200 | SVC | 400
Hornsea 4 | Addition | 2028 | Onshore 400kV | 4 | -200 | 200 | SVC | 400
Hornsea 4 | Addition | 2028 | Onshore 400kV | 5 | -200 | 200 | SVC | 400