## Menu
Electricity Ten Year Statement 2019
Appendix D - Fault Levels at Minimum
Table | Title
D1.0 | SHE Transmission Fault Levels (kA) at Minimum, Summer 2019/20
D2.0 | SPT Fault Levels (kA) at Minimum, Summer 2019/20
D3.0 | NGET Fault Levels (kA) at Minimum, Summer 2019/20

## D1.0
ETYS 19 Yr 1 - SHE Transmission Fault Levels (kA) at Minimum, Summer 2019/20
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 17.64 | 6.77 | 4.51 | 14.08 | 19.93 | 7.68 | 5 | 15.86 | Back To Menu
BLACKHILLOCK | 400 | 22.01 | 8.46 | 6.01 | 17.97 | 25.42 | 9.78 | 6.75 | 20.58
FORT AUGUSTUS | 400 | 16.1 | 6.17 | 4.04 | 12.77 | 18.18 | 7 | 4.52 | 14.41
MELGARVE | 400 | 15.12 | 5.79 | 3.74 | 11.94 | 16.87 | 6.5 | 4.05 | 13.25
BEAULY | 275 | 31.02 | 12.09 | 7.33 | 24.43 | 36.5 | 14.33 | 8.12 | 28.39
BERRY BURN | 275 | 23.24 | 9.33 | 3.76 | 16.94 | 21.13 | 8.64 | 3.13 | 15.36
BLACKHILLOCK I | 275 | 34.15 | 13.41 | 8.04 | 27 | 40.5 | 15.96 | 9.24 | 31.8
BLACKHILLOCK II | 275 | 24.74 | 9.56 | 6.64 | 20.16 | 28.88 | 11.25 | 6.99 | 22.9
BRACO WEST | 275 | 26.12 | 10.21 | 5.21 | 19.66 | 24.52 | 9.73 | 4.67 | 18.42
CAIRNFORD | 275 | 30.28 | 12.04 | 6.02 | 23.04 | 31.9 | 12.89 | 5.38 | 23.61
CONNAGILL | 275 | 13.23 | 5.25 | 2.96 | 10.38 | 15.26 | 6.09 | 3.17 | 11.78
DALLAS | 275 | 24.05 | 9.64 | 3.99 | 17.62 | 22.19 | 9.07 | 3.33 | 16.15
DOUNREAY | 275 | 13.86 | 5.49 | 3.3 | 11.07 | 16.94 | 6.7 | 4 | 13.47
FARIGAIG I | 275 | 27.03 | 10.63 | 5.83 | 20.86 | 25.35 | 10.24 | 4.5 | 18.99
FARIGAIG II | 275 | 27.03 | 10.63 | 5.83 | 20.86 | 25.37 | 10.25 | 4.53 | 19.02
FASNAKYLE | 275 | 24.09 | 9.36 | 5.42 | 18.66 | 24.82 | 9.78 | 5.11 | 18.94
FETTERESSO | 275 | 30.62 | 12.23 | 5.42 | 22.71 | 28.37 | 11.54 | 4.5 | 20.83
FORT AUGUSTUS | 275 | 22.26 | 8.64 | 5.03 | 17.24 | 23.2 | 9.06 | 5.23 | 18.04
FOYERS | 275 | 27.37 | 10.72 | 6.27 | 21.43 | 22.93 | 9.38 | 3.56 | 16.82
FYRISH | 275 | 19.97 | 7.88 | 4.02 | 15.16 | 20.86 | 8.32 | 4.15 | 15.92
GORDONBUSH | 275 | 13.81 | 5.56 | 2.37 | 10.23 | 14.6 | 5.91 | 2.57 | 10.93
KEITH | 275 | 33.12 | 13.07 | 7.37 | 25.86 | 39.17 | 15.55 | 8.27 | 30.26
KINTORE | 275 | 37.19 | 14.66 | 8.26 | 28.99 | 40.08 | 16.02 | 7.9 | 30.56
KNOCKNAGAEL | 275 | 31.57 | 12.32 | 7.39 | 24.81 | 34.91 | 13.81 | 7.51 | 27.05
LOCH BUIDHE | 275 | 18.84 | 7.46 | 3.84 | 14.39 | 20.21 | 8.08 | 4.06 | 15.49
PERSLEY | 275 | 26.18 | 10.44 | 4.97 | 19.74 | 25.97 | 10.44 | 4.89 | 19.65
PETERHEAD | 275 | 31.95 | 12.46 | 8.29 | 25.92 | 30.82 | 12.25 | 6.76 | 24.09
SPITTAL | 275 | 13.39 | 5.29 | 3.46 | 10.94 | 16.66 | 6.55 | 4.34 | 13.6
STRATHBRORA | 275 | 14.91 | 5.98 | 2.61 | 11.07 | 15.85 | 6.4 | 2.88 | 11.93
TEALING | 275 | 34.4 | 13.75 | 5.73 | 25.18 | 33.98 | 13.83 | 5.22 | 24.77
THURSO SOUTH | 275 | 13 | 5.15 | 3.19 | 10.47 | 15.71 | 6.21 | 3.8 | 12.58
TOMATIN | 275 | 20.72 | 8.13 | 4.27 | 15.77 | 20.42 | 8.14 | 3.92 | 15.43
TUMMEL | 275 | 20.93 | 8.21 | 4.26 | 15.87 | 19.96 | 7.95 | 3.96 | 15.2
ABERDEEN BAY | 132 | 14.5 | 6.16 | 0.65 | 9.36 | 14.62 | 6.23 | 0.75 | 9.55
ABERNETHY | 132 | 12.41 | 6.17 | 0.02 | 8.75 | 13.52 | 6.46 | 0.13 | 9.27
A-CHRUACH | 132 | 11.31 | 6.02 | 0.01 | 8.52 | 12.39 | 6.15 | 0.08 | 8.78
AIGAS | 132 | 24.75 | 11.16 | 0.59 | 16.37 | 25.2 | 11.64 | 0.53 | 16.99
ALNESS | 132 | 26.28 | 10.19 | 4.05 | 18.46 | 31.13 | 12.19 | 4.3 | 21.54
AN SUIDHE | 132 | 14.08 | 7.4 | 0.01 | 10.47 | 14.35 | 7.09 | 0.09 | 10.12
ARBROATH | 132 | 12.25 | 5.69 | 0.31 | 8.35 | 11.88 | 5.38 | 0.61 | 8.22
ARDKINGLAS | 132 | 22.22 | 10.7 | 0.11 | 15.24 | 21.2 | 10.04 | 0.35 | 14.54
ARDMORE | 132 | 1.83 | 1.05 | 0 | 1.48 | 2.55 | 1.42 | 0 | 2.01
BEAULY | 132 | 35.32 | 14.64 | 3.92 | 24.63 | 43.8 | 18.08 | 5.12 | 30.69
BEINNEUN | 132 | 12.82 | 6.22 | 0.03 | 8.82 | 14.99 | 7.04 | 0.15 | 10.1
BHLARAIDH | 132 | 13.76 | 6.49 | 0.06 | 9.23 | 15.71 | 7.3 | 0.26 | 10.58
BLACKHILLOCK | 132 | 29.68 | 11.2 | 6.69 | 22.54 | 35.26 | 13.39 | 7.36 | 26.29
BOAT OF GARTEN | 132 | 11.82 | 5 | 0.59 | 7.67 | 12.51 | 5.26 | 0.85 | 8.29
BRECHIN | 132 | 10.8 | 5.45 | 0.01 | 7.72 | 11.6 | 5.55 | 0.05 | 7.9
BRIDGE OF DUN | 132 | 9.16 | 4.7 | 0.01 | 6.66 | 10.17 | 4.91 | 0.07 | 7.01
BROADFORD | 132 | 3.08 | 1.72 | 0 | 2.43 | 3.78 | 1.99 | 0 | 2.82
BRORA | 132 | 10.98 | 5.28 | 0.05 | 7.52 | 11.15 | 5.23 | 0.24 | 7.64
BURGHMUIR | 132 | 10.37 | 5.25 | 0.01 | 7.43 | 12 | 5.78 | 0.09 | 8.26
CARRADALE | 132 | 12.87 | 5.42 | 1.15 | 8.82 | 14.9 | 6.19 | 1.55 | 10.31
CASSLEY | 132 | 6.4 | 3.17 | 0.13 | 4.62 | 6.23 | 2.99 | 0.15 | 4.37
CEANNACROC | 132 | 12.36 | 6.03 | 0.02 | 8.55 | 14.26 | 6.74 | 0.12 | 9.66
CHARLESTON | 132 | 30.67 | 12.77 | 2.85 | 20.91 | 36.05 | 15.17 | 3.43 | 24.88
CLACHAN | 132 | 20.91 | 10.16 | 0.09 | 14.46 | 20.49 | 9.79 | 0.3 | 14.15
CLAYHILLS | 132 | 29.71 | 12.26 | 2.77 | 20.11 | 36.76 | 15.55 | 2.72 | 24.72
CLUNIE | 132 | 16.65 | 7.63 | 0.24 | 11.03 | 17.02 | 7.7 | 0.53 | 11.41
CONNAGILL | 132 | 12.72 | 4.84 | 2.71 | 9.55 | 15.57 | 5.95 | 3.06 | 11.47
CORRIEGARTH | 132 | 8.28 | 3.38 | 0.49 | 5.27 | 9.46 | 3.82 | 0.8 | 6.21
CORRIEMOILLIE | 132 | 17.93 | 7.39 | 1.41 | 11.86 | 21.38 | 8.79 | 1.87 | 14.3
COUPAR ANGUS | 132 | 18.53 | 8.04 | 0.81 | 12.18 | 18.87 | 8.02 | 1.44 | 12.78
CRAIGIEBUCKLER | 132 | 31.79 | 12.94 | 3.37 | 21.67 | 40.14 | 16.56 | 3.57 | 27
CROSSAIG | 132 | 18.21 | 7.77 | 1.83 | 12.82 | 22.95 | 9.7 | 2.32 | 16.04
CULLIGRAN | 132 | 13.75 | 6.76 | 0.04 | 9.61 | 13.92 | 6.67 | 0.15 | 9.58
DEANIE | 132 | 9.85 | 5.01 | 0.01 | 7.09 | 10.09 | 4.9 | 0.06 | 7
DORENELL | 132 | 11.21 | 4.8 | 0.31 | 7.09 | 13.04 | 5.44 | 0.65 | 8.34
DOUNREAY | 132 | 15.02 | 5.75 | 3.18 | 11.31 | 19.9 | 7.63 | 4.05 | 14.85
DUDHOPE | 132 | 28.58 | 12.15 | 1.92 | 19.1 | 32.56 | 14.28 | 1.76 | 21.95
DUNBEATH | 132 | 10.22 | 4.84 | 0.08 | 6.92 | 10.05 | 4.72 | 0.22 | 6.89
DUNMAGLASS | 132 | 9.74 | 3.88 | 0.87 | 6.36 | 11.27 | 4.46 | 1.26 | 7.57
DUNOON | 132 | 8.77 | 4.58 | 0.02 | 6.5 | 8.8 | 4.34 | 0.07 | 6.2
DUNVEGAN | 132 | 2.03 | 1.16 | 0 | 1.64 | 2.88 | 1.61 | 0 | 2.27
DYCE | 132 | 18.66 | 7.97 | 0.88 | 12.15 | 18.85 | 8.07 | 1.03 | 12.45
EDINBANE | 132 | 2.15 | 1.22 | 0 | 1.73 | 3.02 | 1.68 | 0 | 2.38
ELGIN | 132 | 12.08 | 5.76 | 0.25 | 8.39 | 12.1 | 5.64 | 0.55 | 8.53
ERROCHTY | 132 | 30.61 | 12.65 | 4.52 | 22.41 | 34.73 | 14.53 | 4.33 | 24.88
FARIGAIG I | 132 | 11.62 | 4.49 | 1.69 | 8.04 | 13.5 | 5.21 | 2.05 | 9.41
FARIGAIG II | 132 | 11.6 | 4.48 | 1.7 | 8.04 | 13.68 | 5.27 | 2.11 | 9.56
FARR | 132 | 17.77 | 7.63 | 0.48 | 11.27 | 18.12 | 7.88 | 0.76 | 11.9
FERNOCH | 132 | 9.11 | 4.98 | 0.01 | 7.05 | 11.02 | 5.66 | 0.04 | 8.04
FETTERESSO | 132 | 21.03 | 8.11 | 3.2 | 14.67 | 24.4 | 9.41 | 3.75 | 17.05
FIDDES | 132 | 11.07 | 5.64 | 0.01 | 7.99 | 12.47 | 5.95 | 0.09 | 8.5
FINLARIG | 132 | 15.76 | 7.8 | 0.03 | 11.06 | 17.61 | 8.42 | 0.12 | 12.03
FORT AUGUSTUS | 132 | 34.42 | 13.05 | 7.19 | 25.64 | 43.88 | 16.77 | 8.47 | 32.19
FORT WILLIAM | 132 | 7.14 | 3.54 | 0.09 | 5.09 | 8.16 | 3.88 | 0.22 | 5.71
FRASERBURGH | 132 | 10.9 | 4.98 | 0.26 | 7.3 | 11.49 | 5.18 | 0.52 | 7.84
FYRISH | 132 | 27.99 | 10.69 | 5.41 | 20.53 | 33.37 | 12.76 | 6.42 | 24.47
GLENDOE | 132 | 29.75 | 11.81 | 3.37 | 20.07 | 35.67 | 14.58 | 3.37 | 24
GLENFARCLAS | 132 | 5.4 | 2.63 | 0.01 | 3.74 | 5.85 | 2.73 | 0.07 | 3.93
GLENMORISTON | 132 | 15.14 | 7.14 | 0.06 | 10.16 | 17.12 | 7.92 | 0.26 | 11.46
GRIFFIN | 132 | 12.15 | 6.02 | 0.03 | 8.54 | 13.47 | 6.42 | 0.19 | 9.27
GRUDIE BRIDGE | 132 | 15.07 | 6.33 | 0.85 | 9.81 | 17.34 | 7.26 | 1.22 | 11.49
INVERARAY | 132 | 23.77 | 11.4 | 0.13 | 16.25 | 24.68 | 11.67 | 0.21 | 16.71
INVERARNAN | 132 | 41.6 | 17.23 | 4.95 | 29.32 | 46.99 | 19.47 | 5.14 | 32.68
INVERGARRY | 132 | 15.81 | 7.35 | 0.11 | 10.51 | 16.26 | 7.55 | 0.24 | 10.92
INVERNESS | 132 | 34.73 | 14.1 | 4.06 | 24 | 41.47 | 16.9 | 4.68 | 28.58
KEITH | 132 | 24.9 | 9.94 | 5 | 19.06 | 33.2 | 13.52 | 6.21 | 25.33
KILLIN | 132 | 17.6 | 8.61 | 0.05 | 12.23 | 20.65 | 9.71 | 0.18 | 13.92
KILMORACK | 132 | 30.96 | 13.28 | 1.9 | 20.69 | 35.33 | 15.3 | 1.89 | 23.52
KINLOCHLEVEN | 132 | 4.81 | 2.41 | 0.03 | 3.44 | 5.45 | 2.6 | 0.08 | 3.76
KINTORE | 132 | 34.09 | 13.52 | 5.47 | 24.58 | 42.86 | 17.06 | 6.43 | 30.56
KNOCKNAGAEL | 132 | 37.68 | 15.05 | 5.78 | 27.06 | 45.09 | 17.97 | 6.98 | 32.39
LAIRG | 132 | 12.51 | 5.89 | 0.19 | 8.53 | 13.07 | 6.04 | 0.41 | 8.95
LOCH BUIDHE | 132 | 24.05 | 9.79 | 4.22 | 18.07 | 29.52 | 12 | 4.87 | 21.85
LOCHAY | 132 | 15.48 | 7.68 | 0.03 | 10.89 | 17.45 | 8.35 | 0.11 | 11.92
LUICHART | 132 | 19.34 | 7.97 | 1.57 | 12.85 | 21.7 | 8.94 | 1.87 | 14.51
LUNANHEAD | 132 | 15.2 | 6.51 | 0.81 | 10.02 | 14.82 | 6.3 | 1.3 | 10.2
LYNDHURST | 132 | 25.81 | 11.22 | 1.17 | 17.04 | 28.33 | 12.46 | 1.4 | 19.02
MACDUFF | 132 | 7.66 | 3.65 | 0.12 | 5.29 | 8.41 | 3.88 | 0.27 | 5.76
MELGARVE | 132 | 26.28 | 9.9 | 5.69 | 19.69 | 33.35 | 12.64 | 6.6 | 24.48
MILLENNIUM | 132 | 14.55 | 6.92 | 0.05 | 9.83 | 16.78 | 7.81 | 0.18 | 11.23
MILTON OF CRAIGIE | 132 | 30.23 | 12.59 | 2.97 | 20.77 | 34.92 | 14.87 | 2.99 | 24.02
MOSSFORD | 132 | 16.49 | 6.88 | 1.06 | 10.79 | 19.43 | 8.08 | 1.46 | 12.88
MYBSTER I | 132 | 14.99 | 6.33 | 1.52 | 10.47 | 16.82 | 7.22 | 1.1 | 11.31
MYBSTER II | 132 | 13.28 | 5.08 | 2.86 | 10.05 | 16.38 | 6.25 | 3.57 | 12.41
NAIRN | 132 | 11.19 | 5.48 | 0.14 | 7.89 | 10.85 | 5.14 | 0.35 | 7.63
NANT | 132 | 9.28 | 5.03 | 0.01 | 7.13 | 9.28 | 4.71 | 0.07 | 6.73
ORRIN | 132 | 21.44 | 8.87 | 1.75 | 14.29 | 24.11 | 9.96 | 2.08 | 16.16
PERSLEY | 132 | 31.55 | 12.8 | 4.06 | 22.16 | 40.68 | 16.58 | 4.94 | 28.39
PETERHEAD | 132 | 26.78 | 10.23 | 5.62 | 20.08 | 33.82 | 13.03 | 6.25 | 24.68
PETERHEAD GRANGE | 132 | 18.79 | 7.78 | 1.21 | 12.21 | 20.83 | 8.73 | 1.45 | 13.79
PORT ANN | 132 | 10.07 | 5.25 | 0.04 | 7.47 | 10.15 | 5.01 | 0.12 | 7.21
QUOICH | 132 | 8.99 | 4.33 | 0.02 | 6.15 | 8.95 | 4.21 | 0.13 | 6.08
RANNOCH | 132 | 10.04 | 4.88 | 0.24 | 7.14 | 10.31 | 4.8 | 0.55 | 7.33
REDMOSS | 132 | 27.66 | 11.69 | 1.77 | 18.3 | 32.94 | 14.38 | 1.68 | 22.01
SHIN | 132 | 20.34 | 8.85 | 1.06 | 13.58 | 22.12 | 9.62 | 1.63 | 15.24
SLOY | 132 | 36.79 | 16.05 | 1.77 | 24.47 | 40.75 | 17.86 | 2 | 27.25
SPITTAL | 132 | 17.13 | 6.94 | 3.51 | 13.33 | 21.95 | 8.83 | 4.46 | 16.95
ST FERGUS GAS TERMINAL | 132 | 18.34 | 7.74 | 0.8 | 11.75 | 19.87 | 8.59 | 0.69 | 12.84
ST FERGUS MOBIL | 132 | 17.65 | 7.63 | 0.5 | 11.29 | 18.89 | 8.46 | 0.48 | 12.45
ST FILLIANS | 132 | 7.94 | 4.13 | 0 | 5.84 | 7.88 | 3.92 | 0.04 | 5.58
STRATHY NORTH | 132 | 9.37 | 3.77 | 0.85 | 6.18 | 10.67 | 4.26 | 1.27 | 7.3
STRICHEN | 132 | 11.57 | 5.25 | 0.3 | 7.73 | 12.22 | 5.49 | 0.62 | 8.38
STRONELAIRG | 132 | 22.22 | 8.43 | 4.31 | 16.23 | 28.16 | 10.87 | 5.12 | 20.49
TARLAND | 132 | 7.94 | 3.88 | 0.06 | 5.55 | 7.83 | 3.65 | 0.16 | 5.32
TAYNUILT | 132 | 8.78 | 4.71 | 0.06 | 6.73 | 9.19 | 4.61 | 0.23 | 6.75
TEALING | 132 | 34.47 | 13.99 | 5.15 | 24.93 | 40.91 | 16.79 | 5.08 | 28.82
THURSO SOUTH | 132 | 19.88 | 7.69 | 4.11 | 14.98 | 25.42 | 9.81 | 5.25 | 19.12
TOMATIN | 132 | 28.21 | 10.74 | 5.57 | 20.76 | 32.86 | 12.67 | 5.51 | 23.43
TUMMEL | 132 | 25.58 | 10.16 | 4.32 | 18.68 | 27.83 | 11.45 | 3.93 | 20.13
TUMMEL BRIDGE | 132 | 28.03 | 11.86 | 2.85 | 19.62 | 30.44 | 13.1 | 2.43 | 20.96
WILLOWDALE | 132 | 30.76 | 12.59 | 3.29 | 21.09 | 39.03 | 16.18 | 3.63 | 26.52
WOODHILL | 132 | 30.46 | 12.55 | 2.92 | 20.66 | 38.38 | 16.04 | 3.17 | 25.85
ABERNETHY | 33 | 20.6 | 8.63 | 0.41 | 12.6 | 3.06 | 2.12 | 0 | 3
ALNESS | 33 | 28.59 | 10.53 | 7.51 | 22.4 | 2.25 | 1.56 | 0 | 2.21
ARBROATH | 33 | 23.41 | 9.25 | 1.79 | 14.87 | 1.57 | 1.09 | 0 | 1.54
ARDMORE | 33 | 5.81 | 3.07 | 0 | 4.34 | 1.04 | 0.72 | 0 | 1.02
BEAULY | 33 | 27.75 | 10.61 | 4.13 | 19.13 | 1.47 | 1.02 | 0 | 1.44
BERRY BURN | 33 | 22.16 | 8.16 | 5.34 | 16.88 | 1.12 | 0.78 | 0 | 1.1
BOAT OF GARTEN | 33 | 24.85 | 9.57 | 2.75 | 16.28 | 2.23 | 1.54 | 0 | 2.18
BRACO WEST | 33 | 41.33 | 15.31 | 9.65 | 31.3 | 2.25 | 1.56 | 0 | 2.21
BRIDGE OF DUN | 33 | 18.63 | 7.91 | 0.26 | 11.44 | 2.18 | 1.51 | 0 | 2.14
BROADFORD | 33 | 6.31 | 2.87 | 0.01 | 4.08 | 0.77 | 0.53 | 0 | 0.75
BRORA | 33 | 13.52 | 5.41 | 0.73 | 8.37 | 1.1 | 0.76 | 0 | 1.08
BURGHMUIR | 33 | 20.64 | 8.77 | 0.3 | 12.7 | 2.19 | 1.52 | 0 | 2.14
CAIRNFORD | 33 | 25.41 | 9.32 | 6.59 | 19.77 | 1.14 | 0.79 | 0 | 1.12
CARRADALE I | 33 | 22.3 | 8.78 | 2.5 | 14.92 | 2.18 | 1.51 | 0 | 2.14
CARRADALE II | 33 | 23.79 | 9.2 | 3.47 | 16.48 | 2.18 | 1.51 | 0 | 2.14
CASSLEY | 33 | 11.47 | 4.55 | 1.17 | 7.6 | 1.09 | 0.76 | 0 | 1.07
CEANNACROC | 33 | 2.51 | 1 | 0.12 | 1.54 | 2.73 | 1.09 | 0.12 | 1.67
CHARLESTON | 33 | 28.82 | 10.8 | 6.26 | 21.53 | 1.61 | 1.11 | 0 | 1.57
CLACHAN | 33 | 3.74 | 1.44 | 0.37 | 2.41 | 4.11 | 1.58 | 0.41 | 2.65
CLAYHILLS | 33 | 30.49 | 11.63 | 4.59 | 21.03 | 3.15 | 2.18 | 0 | 3.09
COUPAR ANGUS | 33 | 28.66 | 10.8 | 5.32 | 20.59 | 2.19 | 1.52 | 0 | 2.15
CRAIGIEBUCKLER | 33 | 25.73 | 10.03 | 2.39 | 16.58 | 1.59 | 1.1 | 0 | 1.56
DALLAS | 33 | 22.33 | 8.22 | 5.44 | 17.06 | 1.13 | 0.78 | 0 | 1.11
DOUNREAY | 33 | 23.14 | 8.59 | 5.49 | 17.64 | 2.18 | 1.51 | 0 | 2.14
DUDHOPE | 33 | 30.45 | 11.68 | 4.38 | 20.89 | 2.96 | 2.05 | 0 | 2.9
DUNBEATH | 33 | 9.43 | 3.72 | 0.67 | 5.93 | 0.41 | 0.28 | 0 | 0.4
DUNOON | 33 | 21.59 | 9.6 | 0.1 | 13.68 | 2.17 | 1.51 | 0 | 2.13
DUNVEGAN | 33 | 6.2 | 3.23 | 0 | 4.56 | 1.06 | 0.73 | 0 | 1.04
DYCE | 33 | 26.72 | 10.33 | 3.07 | 17.67 | 3.06 | 2.12 | 0 | 3
ELGIN | 33 | 23.86 | 9.51 | 1.5 | 14.95 | 1.9 | 1.31 | 0 | 1.86
FASNAKYLE | 33 | 39.88 | 14.72 | 9.44 | 30.25 | 2.23 | 1.55 | 0 | 2.19
FETTERESSO | 33 | 19.02 | 7.09 | 3.6 | 13.62 | 1.12 | 0.78 | 0 | 1.1
FIDDES | 33 | 20.94 | 8.83 | 0.33 | 12.82 | 2.19 | 1.52 | 0 | 2.15
FORT AUGUSTUS | 33 | 7.21 | 2.69 | 1.4 | 5.2 | 0.74 | 0.52 | 0 | 0.73
FORT WILLIAM | 33 | 20.2 | 8.62 | 0.23 | 12.42 | 0.89 | 0.62 | 0 | 0.88
FRASERBURGH | 33 | 22.41 | 8.87 | 1.43 | 13.98 | 2.22 | 1.54 | 0 | 2.18
GLENFARCLAS | 33 | 9.69 | 4.05 | 0.19 | 5.91 | 1.11 | 0.77 | 0 | 1.09
GRUDIE BRIDGE | 33 | 24.67 | 9.45 | 3.26 | 16.62 | 2.21 | 1.53 | 0 | 2.16
INVERNESS | 33 | 39.1 | 14.85 | 6.88 | 27.88 | 3.32 | 2.3 | 0 | 3.26
KEITH I | 33 | 26.7 | 10.02 | 6.46 | 20.63 | 2.23 | 1.55 | 0 | 2.19
KEITH II | 33 | 28.29 | 10.55 | 6.95 | 21.88 | 2.25 | 1.56 | 0 | 2.21
KILLIN | 33 | 25.47 | 10.37 | 0.9 | 15.57 | 2.2 | 1.52 | 0 | 2.15
KINLOCHLEVEN | 33 | 9.18 | 3.89 | 0.22 | 5.73 | 0.71 | 0.49 | 0 | 0.69
KINTORE | 33 | 40.62 | 15.38 | 7.55 | 29.3 | 3.37 | 2.32 | 0 | 3.28
LAIRG | 33 | 14.4 | 5.62 | 1.43 | 9.38 | 1.11 | 0.77 | 0 | 1.08
LUNANHEAD | 33 | 27.5 | 10.62 | 3.92 | 18.94 | 2.21 | 1.53 | 0 | 2.16
LYNDHURST | 33 | 29.64 | 11.4 | 3.82 | 19.95 | 2.98 | 2.07 | 0 | 2.92
MACDUFF | 33 | 22.95 | 9.92 | 0.28 | 14.31 | 2.23 | 1.55 | 0 | 2.19
MILTON OF CRAIGIE | 33 | 28.75 | 10.99 | 4.49 | 20.04 | 3.34 | 2.31 | 0 | 3.27
MYBSTER I | 33 | 24.61 | 9.17 | 5.56 | 18.52 | 2.2 | 1.53 | 0 | 2.16
MYBSTER II | 33 | 24.66 | 9.14 | 6.01 | 18.94 | 2.19 | 1.52 | 0 | 2.15
MYBSTER III | 33 | 24.97 | 9.22 | 6.54 | 19.57 | 2.19 | 1.52 | 0 | 2.15
NAIRN | 33 | 22.75 | 9.28 | 0.79 | 13.92 | 3.08 | 2.14 | 0 | 3.02
PERSLEY | 33 | 29.39 | 10.96 | 7.1 | 22.6 | 2.25 | 1.56 | 0 | 2.21
PETERHEAD GRANGE | 33 | 24.7 | 9.46 | 3.07 | 16.46 | 0.61 | 0.42 | 0 | 0.6
PORT ANN | 33 | 20.81 | 8.87 | 0.28 | 12.82 | 1.85 | 1.28 | 0 | 1.81
RANNOCH | 33 | 23.43 | 9.52 | 1.03 | 14.5 | 2.2 | 1.52 | 0 | 2.16
REDMOSS | 33 | 28.04 | 10.71 | 4.17 | 19.31 | 3.12 | 2.16 | 0 | 3.06
SHIN | 33 | 25.69 | 9.84 | 3.72 | 17.64 | 2.17 | 1.5 | 0 | 2.13
ST FILLIANS | 33 | 4.09 | 1.55 | 0.58 | 2.77 | 4.8 | 1.79 | 0.91 | 3.44
STRICHEN | 33 | 22.89 | 8.95 | 1.84 | 14.5 | 2.26 | 1.57 | 0 | 2.22
TARLAND | 33 | 16.18 | 6.71 | 0.38 | 9.86 | 1.57 | 1.09 | 0 | 1.54
TAYNUILT | 33 | 21.09 | 8.86 | 0.43 | 12.96 | 2.17 | 1.51 | 0 | 2.13
THURSO SOUTH | 33 | 27.11 | 10.06 | 7.32 | 21.55 | 2.21 | 1.53 | 0 | 2.16
TUMMEL BRIDGE | 33 | 5.63 | 2.07 | 1.98 | 4.9 | 1.1 | 0.76 | 0 | 1.07
WILLOWDALE | 33 | 30.79 | 11.75 | 4.66 | 21.28 | 3.11 | 2.15 | 0 | 3.04
WOODHILL | 33 | 29.08 | 10.94 | 5.76 | 21.24 | 4.65 | 3.22 | 0 | 4.55

## D2.0
ETYS 19 Yr 1 - SPT Fault Levels (kA) at Minimum, Summer 2019/20
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
COAL4- | 400 | 37.79 | 14.07 | 6.29 | 26.19 | 37.42 | 14.86 | 5.96 | 26.97 | Back To Menu
CRYR4- | 400 | 40.3 | 14.75 | 8.37 | 29.23 | 43.02 | 16.55 | 8.62 | 32.03
DENN4- | 400 | 16.94 | 6.07 | 4.54 | 13.12 | 17.23 | 6.48 | 4.43 | 13.59
DEVM4- | 400 | 25.29 | 9.3 | 5.15 | 18.3 | 24.66 | 9.66 | 4.65 | 18.31
ECCL4A | 400 | 36.18 | 13.29 | 7.5 | 26.29 | 33.92 | 13.19 | 6.29 | 24.94
ECCL4B | 400 | 36.21 | 13.3 | 7.5 | 26.3 | 34.05 | 13.24 | 6.32 | 25.05
ELVA4- | 400 | 41.67 | 15.45 | 6.64 | 28.5 | 38.63 | 15.47 | 5.46 | 27.33
FALL4- | 400 | 36.29 | 13.38 | 7.25 | 26.17 | 36.79 | 14.27 | 7.03 | 27.21
GRNA4- | 400 | 41.04 | 15.51 | 5.86 | 27.8 | 36.97 | 14.66 | 6.31 | 27.05
HUCS4- | 400 | 37.71 | 13.42 | 8.81 | 27.79 | 50.23 | 18.79 | 11.91 | 38.48
HUER4- | 400 | 37.88 | 13.48 | 8.85 | 27.91 | 50.38 | 18.85 | 11.91 | 38.57
HUNE4- | 400 | 37.88 | 13.48 | 8.84 | 27.9 | 50.39 | 18.85 | 11.92 | 38.58
KILS4- | 400 | 31.97 | 11.84 | 5.56 | 22.3 | 34.23 | 13.42 | 6.1 | 25.08
MOFF4- | 400 | 34.83 | 13.21 | 5.01 | 23.68 | 31.94 | 12.83 | 4.76 | 22.91
STHA4A | 400 | 41.34 | 15.05 | 7.74 | 29.02 | 44.18 | 17.12 | 8.21 | 32.42
STHA4B | 400 | 38.87 | 14.27 | 7.43 | 27.6 | 40.49 | 15.74 | 7.64 | 29.91
TORN4- | 400 | 46.18 | 16.71 | 10.12 | 33.76 | 52.38 | 19.77 | 12.64 | 40.59
WISH4- | 400 | 38.04 | 13.99 | 6.58 | 26.36 | 40.16 | 15.64 | 7.39 | 29.51
AUCH2- | 275 | 8.84 | 3.64 | 0.76 | 5.91 | 9.99 | 4.19 | 0.87 | 6.79
BUSB2- | 275 | 39.74 | 14.67 | 7.12 | 27.87 | 40.68 | 16.1 | 6.01 | 28.78
CLYM2- | 275 | 54.1 | 19.27 | 11.2 | 38.46 | 58.35 | 22.41 | 11.17 | 42.86
CLYN2Q | 275 | 13.54 | 4.95 | 4.22 | 11.23 | 16.27 | 6.04 | 5.13 | 13.67
CLYS2R | 275 | 13.8 | 5.11 | 3.83 | 11.05 | 14.84 | 5.63 | 4.12 | 12.09
COCK2- | 275 | 44.64 | 16.39 | 9.08 | 32.26 | 47.55 | 18.48 | 9.12 | 35.25
COYL2- | 275 | 26.27 | 9.85 | 5.31 | 19.24 | 31.28 | 12.23 | 5.86 | 23.16
CURR2- | 275 | 41.84 | 15.43 | 7.45 | 29.26 | 44.78 | 17.5 | 8.03 | 32.77
DALL2- | 275 | 29.98 | 10.52 | 6.51 | 21.39 | 28.1 | 10.82 | 5.36 | 20.66
DENN2- | 275 | 43.49 | 15.54 | 8.39 | 30.37 | 45.68 | 17.56 | 8.79 | 33.62
EERH2- | 275 | 49.57 | 17.83 | 9.8 | 35.02 | 50.24 | 19.49 | 8.78 | 36.35
EKIS2- | 275 | 43.53 | 15.91 | 8.4 | 30.9 | 48.9 | 19.18 | 8.07 | 35.19
ELVA2Q | 275 | 14.28 | 5.16 | 4.99 | 12.29 | 16.48 | 6.2 | 4.87 | 13.63
ELVA2R | 275 | 14.41 | 5.21 | 5.04 | 12.41 | 15.36 | 5.73 | 4.74 | 12.84
GLRO2- | 275 | 31.3 | 11.8 | 4.2 | 20.88 | 29.26 | 11.74 | 4.1 | 20.71
GRMO2- | 275 | 34.44 | 12.83 | 5.7 | 23.85 | 33.31 | 13.16 | 5.89 | 24.5
INVR2- | 275 | 28.58 | 10.47 | 4.99 | 19.8 | 27.38 | 10.81 | 4.43 | 19.73
KAIM2- | 275 | 43.75 | 16.06 | 8.35 | 31.06 | 48.68 | 18.92 | 8.49 | 35.25
KILG2- | 275 | 9.71 | 4.02 | 0.8 | 6.48 | 12.22 | 5.08 | 1.23 | 8.41
KILS2- | 275 | 30.42 | 11.17 | 7.27 | 23.06 | 37.03 | 14.14 | 8.61 | 28.61
KINC2- | 275 | 43.46 | 15.68 | 9.4 | 31.57 | 40.4 | 15.81 | 6.96 | 29.32
LAMB2- | 275 | 44.58 | 15.97 | 8.2 | 30.78 | 42.69 | 16.75 | 6.97 | 30.66
LOAN2- | 275 | 54.45 | 19.16 | 11.02 | 38.12 | 51.62 | 20.1 | 7.97 | 36.4
MAHI2- | 275 | 10.45 | 4.27 | 0.99 | 7.02 | 13.01 | 5.35 | 1.44 | 9
MOSM2- | 275 | 36 | 13.37 | 5.16 | 24.07 | 34.52 | 13.7 | 5.42 | 24.8
NEAR2Q | 275 | 40.19 | 14.93 | 6.71 | 27.83 | 40.36 | 15.95 | 6.33 | 28.88
NECU2- | 275 | 23.13 | 8.78 | 4.31 | 16.72 | 26.44 | 10.42 | 4.93 | 19.68
NEIL2- | 275 | 45.44 | 16.42 | 9.42 | 32.64 | 48.1 | 18.61 | 9.4 | 35.71
SMEA2- | 275 | 44.93 | 16.43 | 9.5 | 32.74 | 51.61 | 19.84 | 10.43 | 38.49
STHA2A | 275 | 48.41 | 17.45 | 10.32 | 35 | 55.03 | 21.02 | 11.53 | 41.27
STHA2B | 275 | 48.82 | 17.59 | 10.46 | 35.33 | 56.14 | 21.53 | 11.64 | 42.08
WFIE2- | 275 | 38.74 | 14.28 | 5.73 | 25.92 | 37.99 | 15 | 6.04 | 27.26
WISH2- | 275 | 41.04 | 15.06 | 8.65 | 29.94 | 47.41 | 18.14 | 10.41 | 36.06
WIYH2- | 275 | 46.62 | 16.47 | 9.61 | 32.9 | 50.39 | 19.22 | 10.48 | 37.66
WLEE2- | 275 | 38.9 | 14.74 | 5.34 | 26.19 | 38.98 | 16.96 | 7.2 | 31.18
WLEX2- | 275 | 31.79 | 12.55 | 3.01 | 20.76 | 30.4 | 13.4 | 5.71 | 24.66
AREC1- | 132 | 7.38 | 2.91 | 0.69 | 4.8 | 9.68 | 3.81 | 1.02 | 6.41
BLAH1- | 132 | 17.38 | 6.67 | 2.18 | 11.61 | 21.75 | 8.46 | 2.94 | 14.91
BLCW1- | 132 | 5.97 | 2.42 | 0.35 | 3.78 | 7.09 | 2.87 | 0.58 | 4.64
BONN1- | 132 | 35.18 | 13.06 | 6.75 | 25.22 | 44.72 | 17.36 | 8.03 | 32.58
BRAP1- | 132 | 24.92 | 9.92 | 2.54 | 16.56 | 29.32 | 12.09 | 2.86 | 19.96
CHAP1- | 132 | 24.08 | 9.92 | 0.75 | 14.78 | 26.42 | 11.36 | 1.1 | 17.16
COAL1- | 132 | 13.53 | 4.88 | 4.29 | 11.19 | 17.95 | 6.57 | 5.21 | 14.51
COAL1A | 132 | 26.35 | 9.54 | 7.26 | 20.76 | 33.75 | 12.18 | 9.16 | 26.38
COYL1- | 132 | 22.19 | 8.7 | 4.36 | 16.66 | 28 | 11.2 | 5.26 | 21.1
CRYR1- | 132 | 11.06 | 4 | 3.71 | 9.36 | 14.69 | 5.34 | 4.76 | 12.31
CRYR1A | 132 | 11.36 | 4.09 | 4.01 | 9.79 | 15.02 | 5.46 | 5 | 12.71
CURR1A | 132 | 24.99 | 8.99 | 6.33 | 19.04 | 31.07 | 11.46 | 7.68 | 23.89
CURR1B | 132 | 17.09 | 6.18 | 4.36 | 13.1 | 21.09 | 7.79 | 5.35 | 16.37
DALM1- | 132 | 22.5 | 8.02 | 6.14 | 17.48 | 28.03 | 10.27 | 7.73 | 22.25
DEVM1- | 132 | 27.8 | 10.6 | 6.47 | 21.46 | 34.72 | 13.56 | 7.67 | 26.84
DEVO1- | 132 | 20.83 | 8.71 | 0.75 | 13.06 | 22.4 | 9.83 | 1.46 | 15.37
DUMF1- | 132 | 15.58 | 6.68 | 0.25 | 9.69 | 19.02 | 8.24 | 0.45 | 12.09
DUNE1- | 132 | 13.14 | 5.77 | 0.37 | 8.53 | 15.28 | 6.67 | 0.69 | 10.13
ECCL1- | 132 | 24.82 | 9.22 | 7.7 | 20.74 | 32.02 | 12.12 | 9.37 | 26.51
GALA1- | 132 | 14.91 | 6.63 | 0.13 | 9.5 | 16.51 | 7.41 | 0.43 | 10.91
GAWH1Q | 132 | 20.97 | 7.95 | 3.02 | 14.27 | 25.97 | 10.17 | 3.08 | 17.46
GLLE1- | 132 | 9.25 | 4.02 | 0.29 | 5.97 | 10.8 | 4.81 | 0.35 | 7.15
GLNI1- | 132 | 34.11 | 12.94 | 4.64 | 22.95 | 42.04 | 16.76 | 5.24 | 28.94
GRNA1- | 132 | 31.15 | 11.72 | 6.61 | 23.18 | 39.83 | 15.37 | 8.05 | 29.79
HAWI1- | 132 | 8.47 | 4.23 | 0.01 | 5.99 | 9.61 | 4.59 | 0.05 | 6.54
HELE1- | 132 | 15.31 | 7.51 | 0.02 | 10.63 | 16.46 | 7.93 | 0.14 | 11.35
HUER1- | 132 | 28.78 | 10.58 | 7.78 | 22.75 | 35.86 | 13.58 | 9.79 | 29
KEOO1- | 132 | 9.96 | 4.17 | 0.74 | 6.63 | 11.63 | 4.96 | 0.89 | 7.9
KILS1- | 132 | 24.83 | 9.85 | 3.64 | 17.57 | 26.19 | 10.69 | 4.77 | 19.89
KILW1Q | 132 | 20.8 | 8.26 | 1.74 | 13.42 | 21.49 | 8.93 | 1.66 | 14.28
KILW1R | 132 | 20.6 | 8.23 | 1.57 | 13.21 | 21.07 | 8.8 | 1.52 | 13.97
MAHI1- | 132 | 8.65 | 3.28 | 1.43 | 6.06 | 10.96 | 4.17 | 1.95 | 7.85
MARG1- | 132 | 6.17 | 2.48 | 0.42 | 3.92 | 7.23 | 2.92 | 0.57 | 4.71
MAYB1- | 132 | 13.14 | 5.97 | 0.16 | 8.6 | 14.5 | 6.61 | 0.31 | 9.65
MEAD1- | 132 | 23.84 | 9.4 | 1.83 | 15.12 | 24.16 | 9.99 | 1.79 | 15.92
MOFF1- | 132 | 20.53 | 7.47 | 5.81 | 16.37 | 26.79 | 9.87 | 7.6 | 21.57
MOSM1A | 132 | 32.6 | 12.46 | 4.36 | 21.98 | 40.66 | 16.21 | 5.46 | 28.39
MOSM1B | 132 | 32.52 | 12.43 | 4.31 | 21.9 | 40.64 | 16.22 | 5.39 | 28.32
NECU1- | 132 | 22.72 | 8.36 | 5.02 | 16.85 | 29.81 | 11.19 | 6.31 | 22.13
NEIL1- | 132 | 35.54 | 13.06 | 8.52 | 27 | 45.49 | 17.29 | 10.73 | 35.19
NETS1- | 132 | 6.4 | 2.98 | 0.04 | 4.25 | 7.59 | 3.53 | 0.1 | 5.09
REDH1- | 132 | 24.1 | 10.18 | 0.67 | 15.06 | 26.86 | 11.71 | 1 | 17.56
SMEA1- | 132 | 16.07 | 6.33 | 4.46 | 13.42 | 17.98 | 7.08 | 5.33 | 15.34
STLE1- | 132 | 18.6 | 8.65 | 0.07 | 12.29 | 19.43 | 9.1 | 0.33 | 13.2
TONG1- | 132 | 8.7 | 4.01 | 0.26 | 5.93 | 12.23 | 5.68 | 0.35 | 8.38
TORN1- | 132 | 26.05 | 9.39 | 7.15 | 20.43 | 32.09 | 11.74 | 9.25 | 25.85
WESE1- | 132 | 10.92 | 3.96 | 3.45 | 9.06 | 14.45 | 5.3 | 4.21 | 11.71
WFIE1A | 132 | 25.18 | 10.17 | 4.02 | 18.41 | 28.09 | 11.63 | 4.97 | 21.42
WFIE1B | 132 | 31.87 | 12.37 | 3.94 | 21.44 | 36.89 | 15.07 | 4.81 | 26.13
WISH1- | 132 | 11.89 | 4.3 | 3.83 | 9.91 | 15.22 | 5.55 | 4.87 | 12.72
WIYH1- | 132 | 38.86 | 14.54 | 8.9 | 29.45 | 49.8 | 19.41 | 11.31 | 38.77
AYR-3- | 33 | 36.31 | 13.1 | 8.7 | 27.22 | 5.93 | 4.11 | 0 | 5.81
BAGA3- | 33 | 24.99 | 9.31 | 3.09 | 16.25 | 4.39 | 3.04 | 0 | 4.29
BAIN3- | 33 | 27.92 | 10.21 | 5.43 | 19.86 | 2.98 | 2.07 | 0 | 2.92
BERW3- | 33 | 24.11 | 9.68 | 1.14 | 14.84 | 4.49 | 3.07 | 0 | 4.34
BLCW3- | 33 | 13.02 | 5.01 | 1.22 | 8.3 | 2.21 | 1.53 | 0 | 2.17
BONN3- | 33 | 28.91 | 10.33 | 7.73 | 22.34 | 4.46 | 3.09 | 0 | 4.37
BPGR3- | 33 | 48.45 | 16.73 | 10.22 | 33.88 | 5.86 | 4.06 | 0 | 5.74
BRAP3- | 33 | 26.9 | 9.97 | 4.33 | 18.43 | 4.44 | 3.07 | 0 | 4.35
BROX3- | 33 | 24.62 | 9.06 | 3.12 | 15.94 | 4.38 | 3.03 | 0 | 4.29
CATY3- | 33 | 26.14 | 9.59 | 4.36 | 17.92 | 3 | 2.08 | 0 | 2.94
CHAP3- | 33 | 32.55 | 11.81 | 3.61 | 20.31 | 4.59 | 3.18 | 0 | 4.49
CHAS3- | 33 | 44.96 | 16.23 | 9.29 | 32.25 | 5.97 | 4.13 | 0 | 5.85
CLYM3- | 33 | 44.3 | 15.85 | 10.39 | 32.8 | 5.97 | 4.14 | 0 | 5.85
CLYN3A | 33 | 28.03 | 10.27 | 6.68 | 21.2 | 3.02 | 2.1 | 0 | 2.96
CLYN3B | 33 | 28.13 | 10.3 | 6.7 | 21.27 | 3.02 | 2.1 | 0 | 2.96
CLYN3C | 33 | 28.01 | 10.26 | 6.7 | 21.21 | 3.02 | 2.1 | 0 | 2.96
CLYN3D | 33 | 28.04 | 10.27 | 6.64 | 21.17 | 3.02 | 2.1 | 0 | 2.96
CLYS3A | 33 | 27.93 | 10.26 | 6.24 | 20.76 | 3 | 2.08 | 0 | 2.94
CLYS3B | 33 | 27.88 | 10.25 | 6.17 | 20.66 | 3 | 2.08 | 0 | 2.94
COAT3- | 33 | 36.04 | 12.79 | 10.64 | 28.73 | 5.91 | 4.09 | 0 | 5.79
COCK3- | 33 | 39.47 | 14.18 | 10.27 | 30.31 | 5.95 | 4.13 | 0 | 5.83
COYL3- | 33 | 30.29 | 11.38 | 4.38 | 20.48 | 3.03 | 2.1 | 0 | 2.96
CROO3J | 33 | 31.56 | 11.98 | 3.09 | 20.03 | 3.03 | 2.1 | 0 | 2.97
CROO3K | 33 | 26.07 | 9.82 | 3.28 | 17.16 | 3.03 | 2.1 | 0 | 2.97
CUMB3- | 33 | 25.64 | 9.42 | 4 | 17.32 | 4.38 | 3.03 | 0 | 4.29
CUPA3- | 33 | 22.85 | 8.98 | 0.73 | 13.43 | 4.33 | 3 | 0 | 4.24
DALM3- | 33 | 26.06 | 9.26 | 7.47 | 20.56 | 4.45 | 3.08 | 0 | 4.36
DESA3- | 33 | 19.4 | 7.33 | 2.54 | 12.91 | 2.23 | 1.55 | 0 | 2.19
DEVM3- | 33 | 32.72 | 12.37 | 4.36 | 21.86 | 2.98 | 2.07 | 0 | 2.92
DEVO3- | 33 | 25.61 | 9.44 | 3 | 16.34 | 4.38 | 3.03 | 0 | 4.29
DEWP3- | 33 | 45.88 | 16.52 | 11.05 | 34.42 | 7.85 | 5.44 | 0 | 7.69
DRCR3- | 33 | 23.89 | 9.02 | 2.21 | 14.96 | 4.33 | 2.99 | 0 | 4.24
DRUM3- | 33 | 36.14 | 12.81 | 10.31 | 28.42 | 5.88 | 4.07 | 0 | 5.76
DUMF3I | 33 | 17.42 | 6.63 | 1.3 | 10.68 | 1.51 | 1.05 | 0 | 1.48
DUNB3- | 33 | 32.03 | 11.84 | 2.85 | 19.59 | 3.11 | 2.16 | 0 | 3.05
DUNE3- | 33 | 25.64 | 10.22 | 1.6 | 16.05 | 4.46 | 3.09 | 0 | 4.37
DUNF3- | 33 | 27.57 | 10.33 | 3.23 | 17.84 | 4.37 | 3.03 | 0 | 4.28
DUNH3- | 33 | 23.16 | 8.5 | 5.24 | 17.26 | 4.38 | 3.03 | 0 | 4.29
ECCL3- | 33 | 28.73 | 11.06 | 5.52 | 21.16 | 5.13 | 3.51 | 0 | 4.97
EERH3- | 33 | 41.84 | 14.85 | 12.45 | 33.44 | 5.94 | 4.12 | 0 | 5.82
EKIL3- | 33 | 48.44 | 17.28 | 13.33 | 37.77 | 6.01 | 4.16 | 0 | 5.88
EKIS3- | 33 | 37.05 | 13.16 | 9.39 | 28.01 | 5.94 | 4.11 | 0 | 5.82
ELDE3- | 33 | 34.29 | 12.84 | 4.61 | 22.77 | 3.03 | 2.1 | 0 | 2.97
ERSK3- | 33 | 26.22 | 9.77 | 3.73 | 17.55 | 2.98 | 2.07 | 0 | 2.92
EWEH3- | 33 | 18.65 | 7.35 | 1.14 | 11.53 | 2.26 | 1.56 | 0 | 2.21
FINN3- | 33 | 29.09 | 10.59 | 5.64 | 20.62 | 4.4 | 3.05 | 0 | 4.31
GALA3- | 33 | 24.16 | 9.5 | 1.47 | 14.9 | 4.79 | 3.31 | 0 | 4.68
GAWH3- | 33 | 21.33 | 7.81 | 5.07 | 16.12 | 2.25 | 1.56 | 0 | 2.21
GIFF3A | 33 | 35.5 | 12.94 | 7.4 | 25.69 | 5.37 | 3.72 | 0 | 5.26
GIFF3B | 33 | 33.76 | 12.29 | 7.16 | 24.54 | 5.36 | 3.7 | 0 | 5.24
GLGL3- | 33 | 21.44 | 8 | 3.51 | 14.83 | 4.36 | 3.02 | 0 | 4.27
GLLU3- | 33 | 14.53 | 6.31 | 0.07 | 9 | 3.74 | 2.58 | 0 | 3.65
GLNI3- | 33 | 27.85 | 10.2 | 5.61 | 20.04 | 4.43 | 3.07 | 0 | 4.34
GLRO3A | 33 | 30.31 | 10.78 | 7.26 | 22.51 | 5.34 | 3.69 | 0 | 5.22
GLRO3B | 33 | 30.38 | 10.81 | 7.28 | 22.56 | 5.34 | 3.69 | 0 | 5.22
GORG3- | 33 | 26.68 | 9.7 | 4.62 | 18.34 | 2.98 | 2.07 | 0 | 2.92
GOVA3- | 33 | 28.3 | 10.37 | 4.94 | 19.61 | 4.47 | 3.09 | 0 | 4.37
GRMO3A | 33 | 34.9 | 12.4 | 8.32 | 25.85 | 5.84 | 4.04 | 0 | 5.72
GRMO3C | 33 | 34.98 | 12.41 | 8.46 | 26.02 | 5.84 | 4.05 | 0 | 5.72
HAGR3- | 33 | 28.11 | 10.46 | 3.97 | 18.76 | 3.03 | 2.1 | 0 | 2.97
HAWI3- | 33 | 18.06 | 7.71 | 0.12 | 11.02 | 2.94 | 2.03 | 0 | 2.88
HELE3- | 33 | 24.25 | 9.91 | 0.49 | 14.5 | 2.95 | 2.05 | 0 | 2.89
HUNF3- | 33 | 37.98 | 14.2 | 6.17 | 26.25 | 3.02 | 2.09 | 0 | 2.96
INKE3- | 33 | 26.8 | 10.19 | 1.8 | 16.2 | 4.38 | 3.03 | 0 | 4.29
JOHN3- | 33 | 27.16 | 9.94 | 5.05 | 19.1 | 3.02 | 2.09 | 0 | 2.96
KAIM3- | 33 | 27.99 | 9.86 | 7.87 | 21.82 | 5.72 | 3.96 | 0 | 5.6
KIER3- | 33 | 29.07 | 10.61 | 5.04 | 20.04 | 4.41 | 3.05 | 0 | 4.32
KILB3- | 33 | 31.56 | 11.75 | 5.03 | 21.64 | 3.03 | 2.1 | 0 | 2.96
KILS3- | 33 | 35.53 | 12.73 | 8.98 | 26.98 | 5.92 | 4.1 | 0 | 5.8
KILT3- | 33 | 43.68 | 15.8 | 9.12 | 31.47 | 5.97 | 4.13 | 0 | 5.85
KILW3- | 33 | 26.21 | 9.59 | 4.67 | 18.24 | 4.4 | 3.05 | 0 | 4.31
LEVE3- | 33 | 28.76 | 11.37 | 0.84 | 16.92 | 2.98 | 2.06 | 0 | 2.92
LING3- | 33 | 23.97 | 8.78 | 3.06 | 15.49 | 4.41 | 3.05 | 0 | 4.32
LINM3- | 33 | 26.91 | 9.6 | 6.47 | 20.04 | 4.43 | 3.07 | 0 | 4.34
MAHI3- | 33 | 27.12 | 10.25 | 3.43 | 17.93 | 2.99 | 2.07 | 0 | 2.93
MAYB3- | 33 | 18.22 | 7.3 | 0.69 | 11.02 | 1.55 | 1.07 | 0 | 1.52
NEAR3- | 33 | 46.31 | 16.72 | 9.44 | 33.08 | 5.94 | 4.11 | 0 | 5.82
NETS3- | 33 | 11.32 | 4.76 | 0.41 | 7.14 | 2.91 | 1.99 | 0 | 2.81
PAIS3- | 33 | 31.39 | 11.55 | 5.56 | 21.89 | 3.04 | 2.11 | 0 | 2.98
PART3- | 33 | 32.9 | 12.34 | 4.09 | 21.53 | 2.98 | 2.07 | 0 | 2.92
POOB3- | 33 | 42.6 | 15.13 | 11.42 | 32.82 | 5.97 | 4.13 | 0 | 5.85
PORD3- | 33 | 46.27 | 16.63 | 11.1 | 34.62 | 5.98 | 4.14 | 0 | 5.86
RAVE3- | 33 | 39.16 | 15.1 | 2.42 | 23.77 | 5.9 | 4.08 | 0 | 5.78
REDH3- | 33 | 28.81 | 10.98 | 2.45 | 17.98 | 3.72 | 2.58 | 0 | 3.64
SACO3J | 33 | 27.33 | 10.14 | 3.72 | 18.06 | 2.99 | 2.07 | 0 | 2.93
SACO3K | 33 | 29.79 | 11.21 | 3.55 | 19.4 | 3.03 | 2.1 | 0 | 2.97
SANX3- | 33 | 29.71 | 10.88 | 4.65 | 20.03 | 3.02 | 2.09 | 0 | 2.96
SHRU3- | 33 | 46.75 | 16.83 | 9.49 | 33.29 | 5.95 | 4.12 | 0 | 5.83
SIGH3A | 33 | 39.02 | 13.96 | 9.78 | 29.52 | 4.52 | 3.13 | 0 | 4.43
SIGH3B | 33 | 38.92 | 13.93 | 9.65 | 29.35 | 4.52 | 3.13 | 0 | 4.43
SPAV3- | 33 | 25.69 | 9.65 | 3.15 | 16.8 | 4.42 | 3.06 | 0 | 4.33
STHA3- | 33 | 45.48 | 16.44 | 10.68 | 33.93 | 5.96 | 4.13 | 0 | 5.83
STIR3- | 33 | 28.32 | 10.2 | 5.72 | 20.14 | 4.41 | 3.06 | 0 | 4.32
STLE3S | 33 | 25.91 | 9.89 | 1.44 | 15.43 | 2.97 | 2.06 | 0 | 2.91
TELR3- | 33 | 25.46 | 9.44 | 3.17 | 16.52 | 3 | 2.08 | 0 | 2.93
WFIE3- | 33 | 35.1 | 13.13 | 4.46 | 23.03 | 3.01 | 2.09 | 0 | 2.95
WGEO3- | 33 | 46.08 | 16.66 | 9.23 | 32.79 | 5.96 | 4.13 | 0 | 5.84
WHHO3- | 33 | 39 | 14.06 | 8.95 | 28.83 | 5.94 | 4.12 | 0 | 5.82
WHTL3- | 33 | 24.69 | 9.97 | 0.54 | 14.64 | 2.22 | 1.54 | 0 | 2.18
WISH3- | 33 | 36.26 | 12.98 | 9.38 | 27.74 | 5.91 | 4.09 | 0 | 5.79
WLEE3A | 33 | 35.03 | 12.79 | 8.22 | 26.32 | 3.03 | 2.1 | 0 | 2.97
WLEE3B | 33 | 35.21 | 12.86 | 8.22 | 26.41 | 3.03 | 2.1 | 0 | 2.97
WLEE3C | 33 | 34.93 | 12.76 | 8.19 | 26.23 | 3.03 | 2.1 | 0 | 2.97
WLEX3A | 33 | 34.61 | 12.68 | 7.72 | 25.64 | 3.03 | 2.1 | 0 | 2.97
WLEX3B | 33 | 34.58 | 12.66 | 7.72 | 25.62 | 3.03 | 2.1 | 0 | 2.97
WLEX3C | 33 | 34.58 | 12.66 | 7.72 | 25.62 | 3.03 | 2.1 | 0 | 2.97
BAGA0J | 25 | 15.61 | 5.77 | 3.12 | 11.27 | 0 | 0 | 0 | 0
BAGA0K | 25 | 15.6 | 5.76 | 3.11 | 11.26 | 0 | 0 | 0 | 0
BONN0J | 25 | 17.32 | 6.29 | 5.07 | 13.97 | 0 | 0 | 0 | 0
BONN0K | 25 | 17.32 | 6.29 | 5.07 | 13.97 | 0 | 0 | 0 | 0
BONN0L | 25 | 17.32 | 6.29 | 5.07 | 13.97 | 0 | 0 | 0 | 0
CATY0J | 25 | 9.94 | 3.68 | 1.68 | 6.88 | 0 | 0 | 0 | 0
CATY0K | 25 | 9.95 | 3.68 | 1.71 | 6.92 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.2 | 2.97 | 2.52 | 6.72 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.2 | 2.97 | 2.52 | 6.72 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.4 | 5.98 | 1.11 | 9.56 | 0 | 0 | 0 | 0
ECCF0K | 25 | 18.87 | 7.16 | 2.16 | 12.28 | 0 | 0 | 0 | 0
ELVA0J | 25 | 19.07 | 6.75 | 7.92 | 17.46 | 0 | 0 | 0 | 0
ELVA0K | 25 | 19.07 | 6.75 | 7.92 | 17.46 | 0 | 0 | 0 | 0
INWI0J | 25 | 10.88 | 3.92 | 3.34 | 8.88 | 0 | 0 | 0 | 0
INWI0K | 25 | 10.88 | 3.92 | 3.34 | 8.88 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.54 | 3.58 | 1.61 | 6.67 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.54 | 3.58 | 1.61 | 6.67 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.48 | 6.67 | 5.47 | 14.9 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.48 | 6.67 | 5.47 | 14.9 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.38 | 3.76 | 2.77 | 8.09 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.34 | 3.75 | 2.7 | 8.01 | 0 | 0 | 0 | 0
SANX0J | 25 | 16.68 | 5.99 | 4.49 | 12.96 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.66 | 5.99 | 4.42 | 12.89 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.12 | 3.71 | 1.96 | 7.22 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.12 | 3.71 | 1.96 | 7.22 | 0 | 0 | 0 | 0
WISH0J | 25 | 20.93 | 7.52 | 6.29 | 16.92 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.93 | 7.52 | 6.29 | 16.92 | 0 | 0 | 0 | 0
CAFA5- | 11 | 21.4 | 8.09 | 3.41 | 14.84 | 2.22 | 1.54 | 0 | 2.17
CURR5- | 11 | 32.71 | 12.07 | 5.52 | 22.59 | 4.47 | 3.1 | 0 | 4.38
EAST5- | 11 | 15.74 | 6.14 | 1.24 | 9.93 | 1.13 | 0.79 | 0 | 1.11
GLLE5- | 11 | 16.68 | 6.32 | 2.32 | 11.27 | 2.24 | 1.55 | 0 | 2.2
KEOO5- | 11 | 16.82 | 6.4 | 2.31 | 11.35 | 2.22 | 1.54 | 0 | 2.17
KILB5- | 11 | 27.04 | 10.12 | 3.95 | 18.27 | 2.98 | 2.06 | 0 | 2.92
TONG5- | 11 | 64.14 | 25.67 | 4.14 | 40.45 | 4.56 | 3.16 | 0 | 4.47

## D3.0
ETYS 19 Yr 1 - NGET Fault Levels (kA) at Minimum, Summer 2019/20
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 29.2093 | 10.6661 | 2.0035 | 17.0876 | 29.1594 | 11.3659 | 1.7908 | 17.8647 | Back To Menu
ABHA4B | 400 | 29.1887 | 10.6585 | 2.0016 | 17.075 | 29.1466 | 11.3601 | 1.7865 | 17.8521
ABTH1 M1 | 132 | 26.2158 | 9.7258 | 5.6483 | 19.4027 | 25.7978 | 10.1121 | 5.795 | 20.0957
ABTH1 M2 | 132 | 24.113 | 9.3142 | 7.1437 | 20.3159 | 21.8976 | 8.7448 | 6.4044 | 18.7715
ABTH1 R1 | 132 | 26.1505 | 9.9937 | 7.1202 | 21.2535 | 29.3195 | 11.5129 | 8.3013 | 24.583
ABTH1 R2 | 132 | 26.1505 | 9.9937 | 7.1202 | 21.2535 | 29.3195 | 11.5129 | 8.3013 | 24.583
ABTH2 M1 | 275 | 39.5248 | 14.4048 | 7.0221 | 27.3936 | 38.5481 | 15.0975 | 6.4155 | 27.7666
ABTH2 M2 | 275 | 39.5248 | 14.4048 | 7.0221 | 27.3936 | 38.5481 | 15.0975 | 6.4155 | 27.7666
ABTH2 M4 | 275 | 39.5248 | 14.4048 | 7.0221 | 27.3936 | 38.5481 | 15.0975 | 6.4155 | 27.7666
ABTH2 R | 275 | 33.6653 | 12.4326 | 3.6657 | 21.2481 | 30.8505 | 12.2306 | 2.6404 | 19.9371
ALDW2 MC1 | 275 | 56.344 | 20.7966 | 9.7035 | 39.1143 | 57.6959 | 22.6707 | 9.6408 | 41.7021
ALDW2 MC2 | 275 | 56.344 | 20.7966 | 9.7035 | 39.1143 | 57.6959 | 22.6707 | 9.6408 | 41.7021
ALDW2 MC3 | 275 | 56.344 | 20.7966 | 9.7035 | 39.1143 | 57.6959 | 22.6707 | 9.6408 | 41.7021
ALDW2 MC4 | 275 | 56.344 | 20.7966 | 9.7035 | 39.1143 | 57.6959 | 22.6707 | 9.6408 | 41.7021
AMEM1 M1 | 132 | 27.1879 | 9.8028 | 9.6446 | 23.5078 | 33.278 | 12.2425 | 10.9554 | 28.2689
AMEM1 M2 | 132 | 27.1879 | 9.8028 | 9.6446 | 23.5078 | 33.278 | 12.2425 | 10.9554 | 28.2689
AMEM1 R1 | 132 | 27.1879 | 9.8028 | 9.6446 | 23.5078 | 33.278 | 12.2425 | 10.9554 | 28.2689
AMEM1 R2 | 132 | 27.1879 | 9.8028 | 9.6446 | 23.5078 | 33.278 | 12.2425 | 10.9554 | 28.2689
AMEM4 M | 400 | 45.7603 | 16.5758 | 4.1285 | 27.5702 | 40.1054 | 15.7462 | 2.9275 | 25.196
AMEM4 R | 400 | 46.5458 | 16.8315 | 4.22 | 28.0232 | 40.0034 | 15.6445 | 2.9035 | 25.0282
AXMI4 MC1 | 400 | 32.9477 | 12.1056 | 6.6532 | 23.7731 | 29.9407 | 11.6393 | 5.6173 | 22.0778
AXMI4 MC2 | 400 | 32.9477 | 12.1056 | 6.6532 | 23.7731 | 29.9407 | 11.6393 | 5.6173 | 22.0778
BAGB2 M1 | 275 | 35.6522 | 13.0771 | 7.4394 | 25.9332 | 38.6709 | 14.8084 | 8.8595 | 29.8017
BAGB2 M2 | 275 | 35.6522 | 13.0771 | 7.4394 | 25.9332 | 38.6709 | 14.8084 | 8.8595 | 29.8017
BAGB2 R1 | 275 | 35.6522 | 13.0771 | 7.4394 | 25.9332 | 38.6709 | 14.8084 | 8.8595 | 29.8017
BAGB2 R2 | 275 | 35.6522 | 13.0771 | 7.4394 | 25.9332 | 38.6709 | 14.8084 | 8.8595 | 29.8017
BARK2 M1 | 275 | 49.9087 | 17.9971 | 12.676 | 38.1278 | 50.9316 | 19.2952 | 12.9934 | 40.2809
BARK2 M2 | 275 | 47.5916 | 17.2114 | 12.3592 | 36.6997 | 50.5934 | 19.1404 | 13.3852 | 40.4538
BARK2 R1 | 275 | 49.9087 | 17.9971 | 12.676 | 38.1278 | 50.9316 | 19.2952 | 12.9934 | 40.2809
BARK2 R2 | 275 | 47.5916 | 17.2114 | 12.3592 | 36.6997 | 50.5934 | 19.1404 | 13.3852 | 40.4538
BARK4 M1 | 400 | 93.3993 | 32.9271 | 28.1521 | 74.7181 | 96.4582 | 37.0633 | 25.973 | 78.3885
BARK4 M2 | 400 | 93.3993 | 32.9271 | 28.1521 | 74.7181 | 96.4582 | 37.0633 | 25.973 | 78.3885
BARK4 R1 | 400 | 93.3993 | 32.9271 | 28.1521 | 74.7181 | 96.4582 | 37.0633 | 25.973 | 78.3885
BARK4 R2 | 400 | 93.3993 | 32.9271 | 28.1521 | 74.7181 | 96.4582 | 37.0633 | 25.973 | 78.3885
BEDD2 M1/4 | 275 | 53.343 | 19.2389 | 12.1986 | 39.4064 | 57.6191 | 22.0336 | 12.4899 | 43.6502
BEDD2 M2/3 | 275 | 67.5974 | 24.0801 | 15.2352 | 49.2897 | 72.2268 | 27.5399 | 15.5013 | 54.4486
BEDD2 R1 | 275 | 47.0281 | 17.2934 | 10.3598 | 34.8164 | 48.2773 | 18.5397 | 10.461 | 36.68
BEDD2 R2 | 275 | 67.5974 | 24.0801 | 15.2352 | 49.2897 | 72.2268 | 27.5399 | 15.5013 | 54.4486
BEDD2 R3 | 275 | 67.5974 | 24.0801 | 15.2352 | 49.2897 | 72.2268 | 27.5399 | 15.5013 | 54.4486
BEDD2 R4 | 275 | 47.0281 | 17.2934 | 10.3598 | 34.8164 | 48.2773 | 18.5397 | 10.461 | 36.68
BEDD4B | 400 | 37.5185 | 13.7264 | 2.8115 | 22.2236 | 34.4025 | 13.6352 | 3.3908 | 22.6739
BESW2 MC1 | 275 | 52.6348 | 19.3413 | 10.2152 | 37.5679 | 48.2869 | 19.1102 | 8.2619 | 35.2878
BESW2 MC2 | 275 | 52.6348 | 19.3413 | 10.2152 | 37.5679 | 48.2869 | 19.1102 | 8.2619 | 35.2878
BESW2 MC3 | 275 | 52.6348 | 19.3413 | 10.2152 | 37.5679 | 48.2869 | 19.1102 | 8.2619 | 35.2878
BESW2 MC4 | 275 | 52.6348 | 19.3413 | 10.2152 | 37.5679 | 48.2869 | 19.1102 | 8.2619 | 35.2878
BICF4A | 400 | 74.7507 | 27.1313 | 24.0401 | 62.4095 | 54.6181 | 21.671 | 14.1255 | 44.7728
BICF4B | 400 | 74.7507 | 27.1313 | 24.0401 | 62.4095 | 54.6181 | 21.671 | 14.1255 | 44.7728
BIRK2 MC1 | 275 | 52.5103 | 18.5466 | 13.4967 | 39.7256 | 55.0619 | 20.7528 | 12.3145 | 41.6634
BIRK2 MC2 | 275 | 52.5103 | 18.5466 | 13.4967 | 39.7256 | 55.0619 | 20.7528 | 12.3145 | 41.6634
BIRK2 MC3 | 275 | 52.5103 | 18.5466 | 13.4967 | 39.7256 | 55.0619 | 20.7528 | 12.3145 | 41.6634
BIRK2 MC4 | 275 | 52.5103 | 18.5466 | 13.4967 | 39.7256 | 55.0619 | 20.7528 | 12.3145 | 41.6634
BISW2 MC1 | 275 | 56.571 | 20.7544 | 11.1298 | 40.4809 | 55.0057 | 21.5439 | 9.4118 | 39.8794
BISW2 MC2 | 275 | 56.571 | 20.7544 | 11.1298 | 40.4809 | 55.0057 | 21.5439 | 9.4118 | 39.8794
BISW2 MC3 | 275 | 56.571 | 20.7544 | 11.1298 | 40.4809 | 55.0057 | 21.5439 | 9.4118 | 39.8794
BISW2 MC4 | 275 | 56.571 | 20.7544 | 11.1298 | 40.4809 | 55.0057 | 21.5439 | 9.4118 | 39.8794
BLYT1A | 132 | 32.3707 | 11.4938 | 4.7366 | 20.9914 | 34.0541 | 12.833 | 5.3573 | 23.506
BLYT1B | 132 | 32.1255 | 11.4354 | 4.6912 | 20.8633 | 33.8714 | 12.7776 | 5.3185 | 23.3888
BLYT2 M1 | 275 | 74.8102 | 27.3092 | 23.0152 | 61.6362 | 74.2653 | 28.6469 | 21.5131 | 62.026
BLYT2 M2 | 275 | 74.8102 | 27.3092 | 23.0152 | 61.6362 | 74.2653 | 28.6469 | 21.5131 | 62.026
BLYT2 R1 | 275 | 74.8102 | 27.3092 | 23.0152 | 61.6362 | 74.2653 | 28.6469 | 21.5131 | 62.026
BLYT2 R2 | 275 | 74.8102 | 27.3092 | 23.0152 | 61.6362 | 74.2653 | 28.6469 | 21.5131 | 62.026
BODE4 M1 | 400 | 54.8185 | 19.5404 | 11.9761 | 39.6105 | 48.7495 | 19.0186 | 8.0018 | 34.8982
BODE4 R1 | 400 | 54.8185 | 19.5404 | 11.9761 | 39.6105 | 48.7495 | 19.0186 | 8.0018 | 34.8982
BOLN4 M1 | 400 | 53.9146 | 19.9117 | 15.9267 | 44.0861 | 48.4 | 18.6755 | 14.4748 | 40.8859
BOLN4 M2 | 400 | 53.9146 | 19.9117 | 15.9267 | 44.0861 | 48.4 | 18.6755 | 14.4748 | 40.8859
BOLN4 R1 | 400 | 53.9146 | 19.9117 | 15.9267 | 44.0861 | 48.4 | 18.6755 | 14.4748 | 40.8859
BOLN4 R2 | 400 | 53.9146 | 19.9117 | 15.9267 | 44.0861 | 48.4 | 18.6755 | 14.4748 | 40.8859
BOTW4 MC1 | 400 | 48.6828 | 17.5736 | 10.2577 | 35.1106 | 39.2269 | 15.3775 | 6.8043 | 28.5514
BOTW4 MC2 | 400 | 48.6828 | 17.5736 | 10.2577 | 35.1106 | 39.2269 | 15.3775 | 6.8043 | 28.5514
BRAI4A | 400 | 54.3349 | 19.5199 | 12.3798 | 39.9851 | 44.1862 | 17.141 | 8.5994 | 32.8405
BRAI4A BRFO | 400 | 54.3349 | 19.5199 | 12.3798 | 39.9851 | 44.1862 | 17.141 | 8.5994 | 32.8405
BRAI4A RAYL | 400 | 54.3349 | 19.5199 | 12.3798 | 39.9851 | 44.1862 | 17.141 | 8.5994 | 32.8405
BRAI4B | 400 | 52.3542 | 18.8692 | 11.4918 | 38.1768 | 42.0415 | 16.2762 | 8.0987 | 31.1167
BRAI4B PELH | 400 | 52.3542 | 18.8692 | 11.4918 | 38.1768 | 42.0415 | 16.2762 | 8.0987 | 31.1167
BRAI4B RAYL | 400 | 52.3542 | 18.8692 | 11.4918 | 38.1768 | 42.0415 | 16.2762 | 8.0987 | 31.1167
BRAW2 MC1 | 275 | 56.8466 | 20.6187 | 13.6544 | 42.8137 | 60.7691 | 23.2396 | 13.4588 | 46.3246
BRAW2 MC2 | 275 | 56.8466 | 20.6187 | 13.6544 | 42.8137 | 60.7691 | 23.2396 | 13.4588 | 46.3246
BRAW2 MC3 | 275 | 56.8466 | 20.6187 | 13.6544 | 42.8137 | 60.7691 | 23.2396 | 13.4588 | 46.3246
BRAW2 MC4 | 275 | 56.8466 | 20.6187 | 13.6544 | 42.8137 | 60.7691 | 23.2396 | 13.4588 | 46.3246
BRAW4A | 400 | 33.2043 | 11.987 | 4.3025 | 21.2546 | 30.4767 | 11.5342 | 4.2464 | 20.5583
BRED2 MC1 | 275 | 69.744 | 25.3324 | 14.5666 | 50.3921 | 70.4154 | 27.3762 | 12.5962 | 51.3119
BRED2 MC2 | 275 | 69.744 | 25.3324 | 14.5666 | 50.3921 | 70.4154 | 27.3762 | 12.5962 | 51.3119
BRED2 MC3 | 275 | 69.744 | 25.3324 | 14.5666 | 50.3921 | 70.4154 | 27.3762 | 12.5962 | 51.3119
BRED2 MC4 | 275 | 69.744 | 25.3324 | 14.5666 | 50.3921 | 70.4154 | 27.3762 | 12.5962 | 51.3119
BRFO4 M3 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 M5 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 M6 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 M7 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 MC1 | 400 | 70.1619 | 24.5866 | 18.1088 | 52.8795 | 68.8959 | 26.0732 | 15.292 | 52.1651
BRFO4 MC2 | 400 | 70.1619 | 24.5866 | 18.1088 | 52.8795 | 68.8959 | 26.0732 | 15.292 | 52.1651
BRFO4 MC3 | 400 | 70.1619 | 24.5866 | 18.1088 | 52.8795 | 68.8959 | 26.0732 | 15.292 | 52.1651
BRFO4 MC4 | 400 | 70.1619 | 24.5866 | 18.1088 | 52.8795 | 68.8959 | 26.0732 | 15.292 | 52.1651
BRFO4 R3 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 R5 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 R6 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRFO4 R7 | 400 | 70.1619 | 25.2512 | 23.1142 | 58.8248 | 68.8959 | 26.318 | 20.741 | 57.9604
BRIM1 M1 | 132 | 36.2863 | 12.8156 | 12.8688 | 30.9928 | 48.1856 | 17.5536 | 16.4515 | 41.276
BRIM1 M2 | 132 | 36.2863 | 12.8156 | 12.8688 | 30.9928 | 48.1856 | 17.5536 | 16.4515 | 41.276
BRIM1 R1 | 132 | 36.2863 | 12.8156 | 12.8688 | 30.9928 | 48.1856 | 17.5536 | 16.4515 | 41.276
BRIM1 R2 | 132 | 36.2863 | 12.8156 | 12.8688 | 30.9928 | 48.1856 | 17.5536 | 16.4515 | 41.276
BRIN2 M1 | 275 | 57.3683 | 20.9245 | 12.9226 | 42.5143 | 62.9994 | 24.4377 | 12.5378 | 47.0979
BRIN2 M2 | 275 | 60.4785 | 22.0311 | 15.408 | 46.5647 | 65.9966 | 25.2783 | 15.5795 | 51.3284
BRIN2 R1 | 275 | 57.3683 | 20.9245 | 12.9226 | 42.5143 | 62.9994 | 24.4377 | 12.5378 | 47.0979
BRIN2 R2 | 275 | 60.4785 | 22.0311 | 15.408 | 46.5647 | 65.9966 | 25.2783 | 15.5795 | 51.3284
BRIN4 MC1 | 400 | 60.6328 | 21.7446 | 14.0446 | 44.7962 | 51.2791 | 19.8537 | 10.6692 | 38.7466
BRIN4 MC4 | 400 | 60.6328 | 21.7446 | 14.0446 | 44.7962 | 51.2791 | 19.8537 | 10.6692 | 38.7466
BRLE4 M1 | 400 | 94.8301 | 32.9848 | 20.2024 | 66.85 | 88.7203 | 33.9362 | 18.6926 | 66.6856
BRLE4 M2 | 400 | 94.8301 | 32.9848 | 20.2024 | 66.85 | 88.7203 | 33.9362 | 18.6926 | 66.6856
BRLE4 R1 | 400 | 94.8301 | 32.9848 | 20.2024 | 66.85 | 88.7203 | 33.9362 | 18.6926 | 66.6856
BRLE4 R2 | 400 | 94.8301 | 32.9848 | 20.2024 | 66.85 | 88.7203 | 33.9362 | 18.6926 | 66.6856
BULL4 MC1 | 400 | 57.8026 | 20.6954 | 12.7664 | 42.0342 | 46.4783 | 18.1029 | 8.297 | 33.8983
BULL4 MC2 | 400 | 57.8026 | 20.6954 | 12.7664 | 42.0342 | 46.4783 | 18.1029 | 8.297 | 33.8983
BURW4 MC1 | 400 | 73.4912 | 25.9801 | 17.4254 | 54.1668 | 55.1621 | 21.6871 | 10.2862 | 40.9564
BURW4 MC2 | 400 | 73.4912 | 25.9801 | 17.4254 | 54.1668 | 55.1621 | 21.6871 | 10.2862 | 40.9564
BURW4 MC3 | 400 | 73.4912 | 25.9801 | 17.4254 | 54.1668 | 55.1621 | 21.6871 | 10.2862 | 40.9564
BURW4 MC4 | 400 | 73.4912 | 25.9801 | 17.4254 | 54.1668 | 55.1621 | 21.6871 | 10.2862 | 40.9564
BUSH2 MC1 | 275 | 50.2514 | 18.4223 | 10.607 | 36.6601 | 51.9032 | 20.1585 | 10.0694 | 38.5778
BUSH2 MC2 | 275 | 50.2514 | 18.4223 | 10.607 | 36.6601 | 51.9032 | 20.1585 | 10.0694 | 38.5778
BUSH2 MC3 | 275 | 50.2514 | 18.4223 | 10.607 | 36.6601 | 51.9032 | 20.1585 | 10.0694 | 38.5778
BUSH2 MC4 | 275 | 50.2514 | 18.4223 | 10.607 | 36.6601 | 51.9032 | 20.1585 | 10.0694 | 38.5778
BUST2 M1 | 275 | 64.3448 | 23.0162 | 16.675 | 49.2248 | 68.9467 | 26.1823 | 16.3287 | 53.3561
BUST2 M2 | 275 | 64.3448 | 23.0162 | 16.675 | 49.2248 | 68.9467 | 26.1823 | 16.3287 | 53.3561
BUST2 R1 | 275 | 64.3448 | 23.0162 | 16.675 | 49.2248 | 68.9467 | 26.1823 | 16.3287 | 53.3561
BUST2 R2 | 275 | 64.3448 | 23.0162 | 16.675 | 49.2248 | 68.9467 | 26.1823 | 16.3287 | 53.3561
CANT4 MC1 | 400 | 70.4088 | 25.3063 | 14.5307 | 50.3192 | 54.3187 | 21.3436 | 9.3191 | 39.5035
CANT4 MC2 | 400 | 70.4088 | 25.3063 | 14.5307 | 50.3192 | 54.3187 | 21.3436 | 9.3191 | 39.5035
CANT4 MC3 | 400 | 70.4088 | 25.3063 | 14.5307 | 50.3192 | 54.3187 | 21.3436 | 9.3191 | 39.5035
CANT4 MC4 | 400 | 70.4088 | 25.3063 | 14.5307 | 50.3192 | 54.3187 | 21.3436 | 9.3191 | 39.5035
CANT4 R5 | 400 | 70.4107 | 25.3079 | 14.5311 | 50.3219 | 54.3167 | 21.3438 | 9.3122 | 39.4968
CANT4 R5 | 400 | 70.4107 | 25.3079 | 14.5311 | 50.3219 | 54.3167 | 21.3438 | 9.3122 | 39.4968
CANT4 R5 | 400 | 70.4107 | 25.3079 | 14.5311 | 50.3219 | 54.3167 | 21.3438 | 9.3122 | 39.4968
CAPE2 M1 | 275 | 59.4096 | 20.6612 | 17.2469 | 46.4662 | 69.9716 | 25.6286 | 19.7552 | 55.9996
CAPE2 M2 | 275 | 59.4096 | 20.6612 | 17.2469 | 46.4662 | 69.9716 | 25.6286 | 19.7552 | 55.9996
CAPE2 R1 | 275 | 59.4096 | 20.6612 | 17.2469 | 46.4662 | 69.9716 | 25.6286 | 19.7552 | 55.9996
CAPE2 R2 | 275 | 59.4096 | 20.6612 | 17.2469 | 46.4662 | 69.9716 | 25.6286 | 19.7552 | 55.9996
CAPE4A | 400 | 65.5903 | 22.917 | 15.4729 | 47.8824 | 68.9256 | 25.9299 | 15.1316 | 51.802
CAPE4B | 400 | 65.5933 | 22.9181 | 15.4733 | 47.8843 | 69.3903 | 26.0998 | 15.2001 | 52.1108
CARE2 MC1 | 275 | 37.3553 | 13.7586 | 6.1026 | 25.5602 | 34.4432 | 13.564 | 5.9047 | 25.0871
CARE2 MC2 | 275 | 37.3553 | 13.7586 | 6.1026 | 25.5602 | 34.4432 | 13.564 | 5.9047 | 25.0871
CARR1 M1 | 132 | 31.3449 | 11.6064 | 9.3299 | 25.7438 | 37.7506 | 14.3447 | 11.2327 | 31.5191
CARR1 M2 | 132 | 31.3449 | 11.6064 | 9.3299 | 25.7438 | 37.7506 | 14.3447 | 11.2327 | 31.5191
CARR1 M3 | 132 | 31.3449 | 11.6064 | 9.3299 | 25.7438 | 37.7506 | 14.3447 | 11.2327 | 31.5191
CARR1 M4 | 132 | 41.6471 | 14.7798 | 13.6462 | 34.548 | 53.8628 | 19.8015 | 17.1256 | 45.1292
CARR1 R1 | 132 | 31.3449 | 11.6064 | 9.3299 | 25.7438 | 37.7506 | 14.3447 | 11.2327 | 31.5191
CARR1 R2 | 132 | 31.3449 | 11.6064 | 9.3299 | 25.7438 | 37.7506 | 14.3447 | 11.2327 | 31.5191
CARR1 R3 | 132 | 41.6471 | 14.7798 | 13.6462 | 34.548 | 53.8628 | 19.8015 | 17.1256 | 45.1292
CARR1 R4 | 132 | 41.6471 | 14.7798 | 13.6462 | 34.548 | 53.8628 | 19.8015 | 17.1256 | 45.1292
CARR1B | 132 | 40.8941 | 14.4055 | 7.5601 | 27.9326 | 51.019 | 19.3165 | 6.7431 | 34.0607
CARR1C | 132 | 40.7083 | 14.3866 | 7.1622 | 27.5079 | 50.5427 | 19.265 | 5.2604 | 32.5053
CARR1D | 132 | 40.9992 | 14.424 | 7.7776 | 28.1763 | 51.3918 | 19.3651 | 7.0746 | 34.4611
CARR2 M1 | 275 | 71.8473 | 25.6733 | 18.6864 | 54.994 | 80.0516 | 30.0772 | 20.63 | 63.1656
CARR2 M2 | 275 | 71.8473 | 25.6733 | 18.6864 | 54.994 | 80.0516 | 30.0772 | 20.63 | 63.1656
CARR2 R1 | 275 | 71.8473 | 25.6733 | 18.6864 | 54.994 | 80.0516 | 30.0772 | 20.63 | 63.1656
CARR2 R2 | 275 | 71.8473 | 25.6733 | 18.6864 | 54.994 | 80.0516 | 30.0772 | 20.63 | 63.1656
CARR4 M1 | 400 | 89.5985 | 32.3745 | 26.262 | 72.0464 | 82.8207 | 32.2199 | 22.3767 | 67.9424
CARR4 M2/4 | 400 | 89.5985 | 32.3745 | 26.262 | 72.0464 | 82.8207 | 32.2199 | 22.3767 | 67.9424
CARR4 R1 | 400 | 89.5985 | 32.3745 | 26.262 | 72.0464 | 82.8207 | 32.2199 | 22.3767 | 67.9424
CARR4 R1/2 | 400 | 89.5985 | 32.3745 | 26.262 | 72.0464 | 82.8207 | 32.2199 | 22.3767 | 67.9424
CARR4 R2 | 400 | 89.5985 | 32.3745 | 26.262 | 72.0464 | 82.8207 | 32.2199 | 22.3767 | 67.9424
CARR4 R4 | 400 | 89.5985 | 32.3745 | 26.262 | 72.0464 | 82.8207 | 32.2199 | 22.3767 | 67.9424
CARR4A | 400 | 83.9181 | 28.5436 | 7.7308 | 48.0975 | 77.6797 | 29.5919 | 7.0483 | 48.8976
CARR4B | 400 | 83.9895 | 28.5739 | 7.6846 | 48.0942 | 76.3449 | 29.2088 | 6.6381 | 47.9456
CASK1 M1 | 132 | 49.1731 | 16.3188 | 12.4832 | 35.5615 | 55.2189 | 19.4137 | 15.3163 | 42.7714
CELL1 M1 | 132 | 44.8975 | 16.6925 | 14.4363 | 38.0431 | 55.9279 | 21.9442 | 17.0466 | 48.0804
CELL1 M2 | 132 | 43.2638 | 16.0132 | 12.04 | 34.686 | 48.4884 | 18.6754 | 13.0901 | 39.5012
CELL1 R1 | 132 | 44.8975 | 16.6925 | 14.4363 | 38.0431 | 55.9279 | 21.9442 | 17.0466 | 48.0804
CELL1 R2 | 132 | 43.2638 | 16.0132 | 12.04 | 34.686 | 48.4884 | 18.6754 | 13.0901 | 39.5012
CELL1A | 132 | 37.1759 | 13.4219 | 7.0215 | 26.0029 | 46.0401 | 18.4308 | 8.4398 | 34.5049
CELL4 M1 | 400 | 78.0334 | 27.9118 | 14.7605 | 54.2337 | 69.2687 | 26.9908 | 13.355 | 51.5258
CELL4 M2 | 400 | 78.0334 | 27.9118 | 14.7605 | 54.2337 | 69.2687 | 26.9908 | 13.355 | 51.5258
CELL4 R1 | 400 | 78.0334 | 27.9118 | 14.7605 | 54.2337 | 69.2687 | 26.9908 | 13.355 | 51.5258
CELL4 R2 | 400 | 78.0334 | 27.9118 | 14.7605 | 54.2337 | 69.2687 | 26.9908 | 13.355 | 51.5258
CHIC4 MB1 | 400 | 31.0304 | 11.4378 | 6.282 | 22.4575 | 27.4205 | 10.6451 | 5.2836 | 20.338
CHIC4 MB2 | 400 | 31.0304 | 11.4378 | 6.282 | 22.4575 | 27.4205 | 10.6451 | 5.2836 | 20.338
CHIC4 R1/2 | 400 | 30.9002 | 11.5705 | 9.0547 | 25.4179 | 26.2326 | 10.2747 | 7.1128 | 21.6434
CHSI2 MC1 | 275 | 74.0099 | 26.4572 | 16.2476 | 53.6638 | 67.7699 | 26.5532 | 11.4705 | 49.0224
CHSI2 MC2 | 275 | 74.0099 | 26.4572 | 16.2476 | 53.6638 | 67.7699 | 26.5532 | 11.4705 | 49.0224
CHSI2 MC3 | 275 | 74.0099 | 26.4572 | 16.2476 | 53.6638 | 67.7699 | 26.5532 | 11.4705 | 49.0224
CHSI2 MC4 | 275 | 74.0099 | 26.4572 | 16.2476 | 53.6638 | 67.7699 | 26.5532 | 11.4705 | 49.0224
CHTE2 MC1 | 275 | 60.6045 | 21.782 | 15.122 | 45.9264 | 55.236 | 21.7005 | 10.8003 | 41.4894
CHTE2 MC2 | 275 | 60.6045 | 21.782 | 15.122 | 45.9264 | 55.236 | 21.7005 | 10.8003 | 41.4894
CHTE2 MC3 | 275 | 60.6045 | 21.782 | 15.122 | 45.9264 | 55.236 | 21.7005 | 10.8003 | 41.4894
CHTE2 MC4 | 275 | 60.6045 | 21.782 | 15.122 | 45.9264 | 55.236 | 21.7005 | 10.8003 | 41.4894
CILF4 M1 | 400 | 56.5679 | 20.0268 | 11.579 | 39.9011 | 56.1829 | 21.4817 | 10.698 | 41.0777
CILF4 M2 | 400 | 56.5679 | 20.0268 | 11.579 | 39.9011 | 56.1829 | 21.4817 | 10.698 | 41.0777
CILF4 R1 | 400 | 56.5679 | 20.0268 | 11.579 | 39.9011 | 56.1829 | 21.4817 | 10.698 | 41.0777
CILF4 R2 | 400 | 56.5679 | 20.0268 | 11.579 | 39.9011 | 56.1829 | 21.4817 | 10.698 | 41.0777
CITR4 M5 | 400 | 84.3308 | 28.6724 | 19.4246 | 59.9736 | 98.1345 | 36.9892 | 19.7802 | 72.0908
CITR4 M6 | 400 | 84.3308 | 28.6724 | 19.4246 | 59.9736 | 98.1345 | 36.9892 | 19.7802 | 72.0908
CITR4 MC1 | 400 | 84.3335 | 28.6732 | 19.4255 | 59.9755 | 98.1456 | 36.9908 | 19.8085 | 72.1214
CITR4 MC2 | 400 | 84.3335 | 28.6732 | 19.4255 | 59.9755 | 98.1456 | 36.9908 | 19.8085 | 72.1214
CITR4 MC3 | 400 | 84.3335 | 28.6732 | 19.4255 | 59.9755 | 98.1456 | 36.9908 | 19.8085 | 72.1214
CITR4 MC4 | 400 | 84.3335 | 28.6732 | 19.4255 | 59.9755 | 98.1456 | 36.9908 | 19.8085 | 72.1214
CITR4 R5 | 400 | 84.3308 | 28.6724 | 19.4246 | 59.9736 | 98.1345 | 36.9892 | 19.7802 | 72.0908
CITR4 R6 | 400 | 84.3308 | 28.6724 | 19.4246 | 59.9736 | 98.1345 | 36.9892 | 19.7802 | 72.0908
CLEH4 M1 | 400 | 61.5858 | 22.1507 | 12.944 | 44.2698 | 49.7853 | 19.5003 | 8.1175 | 35.6951
CLEH4 R1 | 400 | 61.5858 | 22.1507 | 12.944 | 44.2698 | 49.7853 | 19.5003 | 8.1175 | 35.6951
CONQ4 M1 | 400 | 76.4677 | 26.5612 | 17.3091 | 54.8724 | 88.6647 | 33.0041 | 21.2329 | 67.9077
CONQ4 M2 | 400 | 76.4677 | 26.5612 | 17.3091 | 54.8724 | 88.6647 | 33.0041 | 21.2329 | 67.9077
CONQ4 M3 | 400 | 76.4677 | 26.5612 | 17.3091 | 54.8724 | 88.6647 | 33.0041 | 21.2329 | 67.9077
CONQ4 M4 | 400 | 76.4677 | 26.5612 | 17.3091 | 54.8724 | 88.6647 | 33.0041 | 21.2329 | 67.9077
CONQ4 R1/3 | 400 | 76.4677 | 26.5612 | 17.3091 | 54.8724 | 88.6647 | 33.0041 | 21.2329 | 67.9077
CONQ4 R2/4 | 400 | 76.4677 | 26.5612 | 17.3091 | 54.8724 | 88.6647 | 33.0041 | 21.2329 | 67.9077
COSO4 M | 400 | 72.778 | 25.5602 | 14.9512 | 51.0988 | 69.7529 | 26.5803 | 14.9255 | 52.5158
COSO4 R | 400 | 72.778 | 25.5602 | 14.9512 | 51.0988 | 69.7529 | 26.5803 | 14.9255 | 52.5158
COTT4 M1 | 400 | 80.4272 | 28.7004 | 18.2545 | 58.843 | 67.7162 | 26.1314 | 13.8937 | 50.8491
COTT4 M2 | 400 | 80.4272 | 28.7004 | 18.2545 | 58.843 | 67.7162 | 26.1314 | 13.8937 | 50.8491
COTT4 M3 | 400 | 74.6293 | 27.4271 | 22.5128 | 61.3006 | 67.1265 | 26.0068 | 19.5066 | 56.2859
COTT4 M4 | 400 | 74.6293 | 27.4271 | 22.5128 | 61.3006 | 67.1265 | 26.0068 | 19.5066 | 56.2859
COTT4 R1/2 | 400 | 74.6293 | 27.4271 | 22.5128 | 61.3006 | 67.1265 | 26.0068 | 19.5066 | 56.2859
COTT4 R3/4 | 400 | 74.6293 | 27.4271 | 22.5128 | 61.3006 | 67.1265 | 26.0068 | 19.5066 | 56.2859
COVE2 MC1 | 275 | 54.8786 | 19.9795 | 11.6647 | 39.92 | 54.0565 | 20.8946 | 11.3299 | 40.8794
COVE2 MC2 | 275 | 54.8786 | 19.9795 | 11.6647 | 39.92 | 54.0565 | 20.8946 | 11.3299 | 40.8794
COVE2 MC3 | 275 | 54.8786 | 19.9795 | 11.6647 | 39.92 | 54.0565 | 20.8946 | 11.3299 | 40.8794
COVE2 MC4 | 275 | 54.8786 | 19.9795 | 11.6647 | 39.92 | 54.0565 | 20.8946 | 11.3299 | 40.8794
COWL4 M1 | 400 | 99.8655 | 35.8565 | 30.3858 | 81.0946 | 91.6932 | 35.2565 | 26.3455 | 76.2058
COWL4 M2 | 400 | 99.8655 | 35.8565 | 30.3858 | 81.0946 | 91.6932 | 35.2565 | 26.3455 | 76.2058
COWL4 R1 | 400 | 99.8655 | 35.8565 | 30.3858 | 81.0946 | 91.6932 | 35.2565 | 26.3455 | 76.2058
COWL4 R2 | 400 | 99.8655 | 35.8565 | 30.3858 | 81.0946 | 91.6932 | 35.2565 | 26.3455 | 76.2058
CREB2A | 275 | 57.6964 | 20.3767 | 12.0493 | 40.8663 | 60.5711 | 22.4104 | 10.9741 | 42.6672
CREB2B | 275 | 57.6933 | 20.3746 | 12.0474 | 40.8614 | 61.0726 | 22.5919 | 11.0614 | 43.0113
CREB4 MB1 | 400 | 89.2977 | 31.3063 | 22.2408 | 66.5145 | 83.0119 | 31.5268 | 18.8792 | 63.4648
CREB4 MB2 | 400 | 89.2977 | 31.3063 | 22.2408 | 66.5145 | 83.0119 | 31.5268 | 18.8792 | 63.4648
CREB4 RB1 | 400 | 89.2977 | 31.3063 | 22.2408 | 66.5145 | 83.0119 | 31.5268 | 18.8792 | 63.4648
CREB4 RB2 | 400 | 89.2977 | 31.3063 | 22.2408 | 66.5145 | 83.0119 | 31.5268 | 18.8792 | 63.4648
DAIN4 M1 | 400 | 91.2646 | 31.8526 | 19.2382 | 64.2845 | 84.9723 | 32.6591 | 16.405 | 62.592
DAIN4 M2 | 400 | 91.2646 | 31.8526 | 19.2382 | 64.2845 | 84.9723 | 32.6591 | 16.405 | 62.592
DAIN4 R1 | 400 | 91.2646 | 31.8526 | 19.2382 | 64.2845 | 84.9723 | 32.6591 | 16.405 | 62.592
DAIN4 R2 | 400 | 91.2646 | 31.8526 | 19.2382 | 64.2845 | 84.9723 | 32.6591 | 16.405 | 62.592
DIDC4 M1 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 M2 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 M3 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 M4 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 M5 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 M6 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 R1/2 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 R3/4 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 R5 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DIDC4 R6 | 400 | 95.9261 | 33.3311 | 22.1403 | 69.2775 | 95.2252 | 35.6377 | 23.7517 | 74.1509
DINO4 1 | 400 | 38.7148 | 14.0855 | 8.052 | 27.9719 | 46.8821 | 17.6733 | 10.7728 | 35.7666
DINO4 2 | 400 | 38.7148 | 14.0855 | 8.052 | 27.9719 | 46.8821 | 17.6733 | 10.7728 | 35.7666
DINO4 3 | 400 | 38.7148 | 14.0855 | 8.052 | 27.9719 | 46.8821 | 17.6733 | 10.7728 | 35.7666
DRAK1 M1 | 132 | 31.4651 | 11.274 | 12.8543 | 28.7981 | 38.9476 | 14.3361 | 15.9636 | 36.238
DRAK1 M2 | 132 | 31.4651 | 11.274 | 12.8543 | 28.7981 | 38.9476 | 14.3361 | 15.9636 | 36.238
DRAK1 R1 | 132 | 31.4651 | 11.274 | 12.8543 | 28.7981 | 38.9476 | 14.3361 | 15.9636 | 36.238
DRAK1 R2 | 132 | 31.4651 | 11.274 | 12.8543 | 28.7981 | 38.9476 | 14.3361 | 15.9636 | 36.238
DRAK4 M1 | 400 | 98.2718 | 34.3889 | 19.4675 | 68.1007 | 94.9169 | 36.6521 | 17.0177 | 68.8516
DRAK4 M2 | 400 | 98.2718 | 34.3889 | 19.4675 | 68.1007 | 94.9169 | 36.6521 | 17.0177 | 68.8516
DRAK4 M3 | 400 | 98.2718 | 34.3889 | 19.4675 | 68.1007 | 94.9169 | 36.6521 | 17.0177 | 68.8516
DRAK4 R1/3 | 400 | 98.2718 | 34.3889 | 19.4675 | 68.1007 | 94.9169 | 36.6521 | 17.0177 | 68.8516
DRAK4 R2 | 400 | 98.2718 | 34.3889 | 19.4675 | 68.1007 | 94.9169 | 36.6521 | 17.0177 | 68.8516
DRAX1 M1 | 132 | 38.0202 | 11.3701 | 11.1443 | 27.224 | 47.8373 | 16.1661 | 14.1551 | 37.0174
DRAX1 M2 | 132 | 38.0202 | 11.3701 | 11.1443 | 27.224 | 47.8373 | 16.1661 | 14.1551 | 37.0174
DRAX1 R1 | 132 | 38.0202 | 11.3701 | 11.1443 | 27.224 | 47.8373 | 16.1661 | 14.1551 | 37.0174
DRAX1 R2 | 132 | 38.0202 | 11.3701 | 11.1443 | 27.224 | 47.8373 | 16.1661 | 14.1551 | 37.0174
DRAX4 M1 | 400 | 92.3758 | 31.661 | 24.1135 | 68.8889 | 94.7779 | 35.0364 | 24.6878 | 74.2367
DRAX4 M2 | 400 | 92.3758 | 31.661 | 24.1135 | 68.8889 | 94.7779 | 35.0364 | 24.6878 | 74.2367
DRAX4 M3 | 400 | 92.3758 | 31.661 | 24.1135 | 68.8889 | 94.7779 | 35.0364 | 24.6878 | 74.2367
DRAX4 M4 | 400 | 83.6953 | 29.0057 | 22.8265 | 63.8467 | 85.8178 | 31.7852 | 23.2296 | 68.1807
DRAX4 M5 | 400 | 83.6953 | 29.0057 | 22.8265 | 63.8467 | 85.8178 | 31.7852 | 23.2296 | 68.1807
DRAX4 M6 | 400 | 83.6953 | 29.0057 | 22.8265 | 63.8467 | 85.8178 | 31.7852 | 23.2296 | 68.1807
DRAX4 R1/2/3 | 400 | 92.3758 | 31.661 | 24.1135 | 68.8889 | 94.7779 | 35.0364 | 24.6878 | 74.2367
DRAX4 R4/5/6 | 400 | 83.6953 | 29.0057 | 22.8265 | 63.8467 | 85.8178 | 31.7852 | 23.2296 | 68.1807
DUNG2 M1 | 275 | 40.7346 | 14.5467 | 12.73 | 33.3022 | 40.6641 | 15.1188 | 11.9831 | 33.3642
DUNG2 M2 | 275 | 40.7346 | 14.5467 | 12.73 | 33.3022 | 40.6641 | 15.1188 | 11.9831 | 33.3642
DUNG2 R1 | 275 | 40.7346 | 14.5467 | 12.73 | 33.3022 | 40.6641 | 15.1188 | 11.9831 | 33.3642
DUNG2 R2 | 275 | 40.7346 | 14.5467 | 12.73 | 33.3022 | 40.6641 | 15.1188 | 11.9831 | 33.3642
DUNG4 M1 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
DUNG4 M2 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
DUNG4 M3 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
DUNG4 M4 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
DUNG4 M5 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
DUNG4 R1/2 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
DUNG4 R4/5 | 400 | 61.5357 | 21.8357 | 9.1928 | 40.0732 | 53.8299 | 20.5693 | 8.3287 | 37.418
EALI2 MC1 | 275 | 53.8965 | 18.9382 | 11.9885 | 38.7711 | 60.3317 | 23.3012 | 7.9072 | 40.8602
EALI2 MC2 | 275 | 53.8965 | 18.9382 | 11.9885 | 38.7711 | 60.3317 | 23.3012 | 7.9072 | 40.8602
EALI2 MC3 | 275 | 53.8965 | 18.9382 | 11.9885 | 38.7711 | 60.3317 | 23.3012 | 7.9072 | 40.8602
EALI2 MC4 | 275 | 53.8965 | 18.9382 | 11.9885 | 38.7711 | 60.3317 | 23.3012 | 7.9072 | 40.8602
EASO4 M1 | 400 | 68.2347 | 24.3545 | 15.4553 | 49.8977 | 65.3242 | 24.5972 | 16.9326 | 51.7183
EASO4 M2 | 400 | 68.2347 | 24.3545 | 15.4553 | 49.8977 | 65.3242 | 24.5972 | 16.9326 | 51.7183
EASO4 R1 | 400 | 68.2347 | 24.3545 | 15.4553 | 49.8977 | 65.3242 | 24.5972 | 16.9326 | 51.7183
EASO4 R2 | 400 | 68.2347 | 24.3545 | 15.4553 | 49.8977 | 65.3242 | 24.5972 | 16.9326 | 51.7183
EASO4A | 400 | 68.2347 | 24.3545 | 15.4553 | 49.8977 | 65.3242 | 24.5972 | 16.9326 | 51.7183
EASO4B | 400 | 68.2347 | 24.3545 | 15.4553 | 49.8977 | 65.3242 | 24.5972 | 16.9326 | 51.7183
ECLA1 M1 | 132 | 42.6991 | 15.9196 | 12.9444 | 35.4582 | 46.3916 | 17.8591 | 14.3752 | 39.6317
ECLA1 M2 | 132 | 42.6991 | 15.9196 | 12.9444 | 35.4582 | 46.3916 | 17.8591 | 14.3752 | 39.6317
ECLA1 R1 | 132 | 41.5394 | 15.5909 | 12.1481 | 34.1969 | 50.5045 | 19.409 | 14.9071 | 42.3556
ECLA1 R2 | 132 | 41.5394 | 15.5909 | 12.1481 | 34.1969 | 50.5045 | 19.409 | 14.9071 | 42.3556
ECLA4 M1 | 400 | 92.0614 | 32.377 | 19.9876 | 65.7757 | 81.0579 | 31.2883 | 16.0412 | 60.2895
ECLA4 M2 | 400 | 92.0614 | 32.377 | 19.9876 | 65.7757 | 81.0579 | 31.2883 | 16.0412 | 60.2895
ECLA4 R1 | 400 | 92.0614 | 32.377 | 19.9876 | 65.7757 | 81.0579 | 31.2883 | 16.0412 | 60.2895
ECLA4 R2 | 400 | 92.0614 | 32.377 | 19.9876 | 65.7757 | 81.0579 | 31.2883 | 16.0412 | 60.2895
EGGB4 M1 | 400 | 81.3693 | 28.3978 | 19.9964 | 60.1569 | 79.4186 | 29.8921 | 17.7491 | 60.0229
EGGB4 M2 | 400 | 81.3693 | 28.3978 | 19.9964 | 60.1569 | 79.4186 | 29.8921 | 17.7491 | 60.0229
EGGB4 R1 | 400 | 73.4704 | 25.7837 | 19.1255 | 55.5891 | 71.2979 | 26.8151 | 16.6547 | 54.5769
EGGB4 R2 | 400 | 73.4704 | 25.7837 | 19.1255 | 55.5891 | 71.2979 | 26.8151 | 16.6547 | 54.5769
ELLA2 MC1 | 275 | 56.1835 | 20.3881 | 8.0274 | 36.8605 | 59.6742 | 22.9063 | 7.9457 | 40.34
ELLA2 MC2 | 275 | 56.1835 | 20.3881 | 8.0274 | 36.8605 | 59.6742 | 22.9063 | 7.9457 | 40.34
ELLA2 MC3 | 275 | 56.1835 | 20.3881 | 8.0274 | 36.8605 | 59.6742 | 22.9063 | 7.9457 | 40.34
ELLA2 MC4 | 275 | 56.1835 | 20.3881 | 8.0274 | 36.8605 | 59.6742 | 22.9063 | 7.9457 | 40.34
ELST1 M1 | 132 | 30.037 | 11.0774 | 9.5833 | 25.2491 | 37.068 | 13.9061 | 11.6508 | 31.3171
ELST1 M2 | 132 | 41.3886 | 15.0112 | 12.5357 | 33.7648 | 50.9171 | 19.541 | 14.8414 | 42.4765
ELST1 M3 | 132 | 27.3287 | 10.3936 | 6.1585 | 20.8573 | 31.0639 | 12.0761 | 7.3276 | 24.4058
ELST1 R1 | 132 | 30.037 | 11.0774 | 9.5833 | 25.2491 | 37.068 | 13.9061 | 11.6508 | 31.3171
ELST1 R2 | 132 | 41.3886 | 15.0112 | 12.5357 | 33.7648 | 50.9171 | 19.541 | 14.8414 | 42.4765
ELST1 R3 | 132 | 27.3287 | 10.3936 | 6.1585 | 20.8573 | 31.0639 | 12.0761 | 7.3276 | 24.4058
ELST2 M1 | 275 | 57.7975 | 20.7611 | 14.7358 | 44.0964 | 65.2266 | 24.4812 | 16.8862 | 51.5078
ELST2 M2 | 275 | 58.5154 | 21.186 | 13.3101 | 43.2717 | 66.5493 | 25.4259 | 14.6005 | 50.5581
ELST2 R1 | 275 | 57.7975 | 20.7611 | 14.7358 | 44.0964 | 65.2266 | 24.4812 | 16.8862 | 51.5078
ELST2 R2 | 275 | 58.5154 | 21.186 | 13.3101 | 43.2717 | 66.5493 | 25.4259 | 14.6005 | 50.5581
ELST4 M1 | 400 | 73.1341 | 26.2018 | 22.453 | 59.508 | 88.8702 | 33.5401 | 26.9715 | 74.4044
ELST4 R1 | 400 | 73.1341 | 26.2018 | 22.453 | 59.508 | 88.8702 | 33.5401 | 26.9715 | 74.4044
ELST4A | 400 | 50.7669 | 18.1093 | 6.4536 | 32.0641 | 50.1636 | 18.8926 | 7.6122 | 34.3304
ENDE4 MC1 | 400 | 77.3652 | 27.7571 | 15.6209 | 54.8754 | 57.1777 | 22.5046 | 10.2458 | 42.0722
ENDE4 MC2 | 400 | 77.3652 | 27.7571 | 15.6209 | 54.8754 | 57.1777 | 22.5046 | 10.2458 | 42.0722
ENDE4 MC3 | 400 | 77.3652 | 27.7571 | 15.6209 | 54.8754 | 57.1777 | 22.5046 | 10.2458 | 42.0722
ENDE4 MC4 | 400 | 77.3652 | 27.7571 | 15.6209 | 54.8754 | 57.1777 | 22.5046 | 10.2458 | 42.0722
EXET4 M1 | 400 | 44.9583 | 16.2583 | 8.9709 | 31.9636 | 46.1874 | 17.8009 | 9.3209 | 34.4952
EXET4 M2 | 400 | 44.9583 | 16.2583 | 8.9709 | 31.9636 | 46.1874 | 17.8009 | 9.3209 | 34.4952
EXET4 R1 | 400 | 44.9583 | 16.2583 | 8.9709 | 31.9636 | 46.1874 | 17.8009 | 9.3209 | 34.4952
EXET4 R2 | 400 | 44.9583 | 16.2583 | 8.9709 | 31.9636 | 46.1874 | 17.8009 | 9.3209 | 34.4952
FAWL1 M1 | 132 | 34.7431 | 12.3129 | 13.04 | 30.453 | 45.6697 | 17.1013 | 16.114 | 40.2989
FAWL1 M2 | 132 | 34.7431 | 12.3129 | 13.04 | 30.453 | 45.6697 | 17.1013 | 16.114 | 40.2989
FAWL1 R1 | 132 | 34.7431 | 12.3129 | 13.04 | 30.453 | 45.6697 | 17.1013 | 16.114 | 40.2989
FAWL1 R2 | 132 | 34.7431 | 12.3129 | 13.04 | 30.453 | 45.6697 | 17.1013 | 16.114 | 40.2989
FAWL4 M1/3 | 400 | 36.9547 | 13.2943 | 4.9201 | 23.721 | 31.5256 | 12.1373 | 4.2118 | 21.3766
FAWL4 M1/3(1) | 400 | 36.9547 | 13.2943 | 4.9201 | 23.721 | 31.5256 | 12.1373 | 4.2118 | 21.3766
FAWL4 M2/4(2) | 400 | 36.9547 | 13.2943 | 4.9201 | 23.721 | 31.5256 | 12.1373 | 4.2118 | 21.3766
FAWL4 M2/4(3) | 400 | 36.9547 | 13.2943 | 4.9201 | 23.721 | 31.5256 | 12.1373 | 4.2118 | 21.3766
FAWL4 R1/3 | 400 | 36.9547 | 13.2943 | 4.9201 | 23.721 | 31.5256 | 12.1373 | 4.2118 | 21.3766
FAWL4 R2/4 | 400 | 36.9547 | 13.2943 | 4.9201 | 23.721 | 31.5256 | 12.1373 | 4.2118 | 21.3766
FECK2 M1 | 275 | 56.8476 | 20.7542 | 13.1881 | 42.539 | 58.2 | 22.3194 | 13.2926 | 44.8571
FECK2 M2 | 275 | 56.8476 | 20.7542 | 13.1881 | 42.539 | 58.2 | 22.3194 | 13.2926 | 44.8571
FECK2 R | 275 | 56.8476 | 20.7542 | 13.1881 | 42.539 | 58.2 | 22.3194 | 13.2926 | 44.8571
FECK4 M1 | 400 | 68.0321 | 24.7925 | 12.1927 | 47.2546 | 60.9874 | 23.8423 | 11.7245 | 45.4426
FECK4 M2 | 400 | 68.0321 | 24.7925 | 12.1927 | 47.2546 | 60.9874 | 23.8423 | 11.7245 | 45.4426
FECK4 R1 | 400 | 68.0321 | 24.7925 | 12.1927 | 47.2546 | 60.9874 | 23.8423 | 11.7245 | 45.4426
FECK4 R2 | 400 | 68.0321 | 24.7925 | 12.1927 | 47.2546 | 60.9874 | 23.8423 | 11.7245 | 45.4426
FENW4A | 400 | 86.1678 | 29.177 | 11.1966 | 52.459 | 79.6163 | 29.9521 | 7.266 | 49.6247
FERR2 M1 | 275 | 52.1239 | 18.7483 | 10.5392 | 37.0533 | 55.2869 | 20.7986 | 11.0045 | 40.4182
FERR2 M2 | 275 | 51.9869 | 18.4997 | 13.3673 | 39.5298 | 57.3305 | 21.3641 | 13.2176 | 43.4309
FERR2 R1 | 275 | 55.0676 | 19.7693 | 10.9394 | 38.8974 | 57.4679 | 21.776 | 9.851 | 40.6469
FERR2 R2 | 275 | 55.0676 | 19.7693 | 10.9394 | 38.8974 | 57.4679 | 21.776 | 9.851 | 40.6469
FERR2A | 275 | 52.0116 | 18.3927 | 11.0399 | 37.0511 | 57.2028 | 21.2677 | 10.7843 | 40.8614
FERR2B | 275 | 51.6806 | 18.4685 | 8.415 | 34.5333 | 54.5964 | 20.5397 | 8.5254 | 37.5729
FERR4A | 400 | 63.14 | 21.8997 | 8.1212 | 39.092 | 59.0259 | 22.1611 | 7.5185 | 38.859
FFES2 Term205 | 275 | 27.6872 | 10.4344 | 1.7167 | 16.4732 | 29.4967 | 11.581 | 1.775 | 18.153
FFES2 Term210 | 275 | 27.6923 | 10.4373 | 1.7132 | 16.4738 | 29.8714 | 11.7207 | 1.7933 | 18.3688
FIDF2 M1 | 275 | 46.8783 | 16.6769 | 13.7931 | 37.3777 | 49.0708 | 18.2582 | 13.3168 | 39.1379
FIDF2 M2 | 275 | 46.1973 | 16.4075 | 13.6235 | 36.8272 | 47.4265 | 17.6494 | 12.6711 | 37.631
FIDF2 M3 | 275 | 55.9328 | 19.9259 | 14.151 | 42.3305 | 55.7137 | 21.0328 | 12.9087 | 42.6536
FIDF2 M4 | 275 | 56.388 | 20.0842 | 14.2733 | 42.6767 | 57.3835 | 21.6331 | 13.4718 | 44.0656
FIDF2 R1 | 275 | 46.8783 | 16.6769 | 13.7931 | 37.3777 | 49.0708 | 18.2582 | 13.3168 | 39.1379
FIDF2 R2 | 275 | 56.388 | 20.0842 | 14.2733 | 42.6767 | 57.3835 | 21.6331 | 13.4718 | 44.0656
FLEE4 MC1 | 400 | 82.2641 | 28.847 | 17.4801 | 58.2759 | 71.7972 | 27.7874 | 14.1229 | 53.4202
FLEE4 MC2 | 400 | 82.2641 | 28.847 | 17.4801 | 58.2759 | 71.7972 | 27.7874 | 14.1229 | 53.4202
FLEE4 MC3 | 400 | 82.2641 | 28.847 | 17.4801 | 58.2759 | 71.7972 | 27.7874 | 14.1229 | 53.4202
FLEE4 MC4 | 400 | 82.2641 | 28.847 | 17.4801 | 58.2759 | 71.7972 | 27.7874 | 14.1229 | 53.4202
FLIB4 M1 | 400 | 73.0815 | 25.4673 | 16.6502 | 52.6664 | 84.5817 | 31.7136 | 19.017 | 63.8669
FLIB4 M2 | 400 | 73.0815 | 25.4673 | 16.6502 | 52.6664 | 84.5817 | 31.7136 | 19.017 | 63.8669
FOUR2 MC1 | 275 | 37.0792 | 14.3259 | 5.2759 | 25.5358 | 32.1135 | 13.0926 | 4.0783 | 22.594
FOUR2 MC2 | 275 | 37.0792 | 14.3259 | 5.2759 | 25.5358 | 32.1135 | 13.0926 | 4.0783 | 22.594
FROD2 MC1 | 275 | 46.7518 | 16.5821 | 14.3231 | 37.7738 | 51.7042 | 18.9806 | 16.1451 | 42.9877
FROD2 MC3 | 275 | 46.6803 | 16.2585 | 9.0885 | 32.0815 | 51.086 | 18.6743 | 9.6798 | 36.0893
FROD4 M1 | 400 | 65.6603 | 23.478 | 21.113 | 54.3159 | 69.7049 | 26.1557 | 22.5748 | 59.5646
FROD4 R1 | 400 | 65.6603 | 23.478 | 21.113 | 54.3159 | 69.7049 | 26.1557 | 22.5748 | 59.5646
GART4A | 400 | 77.9923 | 26.8304 | 10.8828 | 48.8267 | 69.8238 | 26.4189 | 6.5041 | 43.8661
GART4B | 400 | 79.7878 | 27.4729 | 10.6788 | 49.5313 | 75.4515 | 28.508 | 7.2979 | 47.6143
GRAI4 M1 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 M2 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 M3 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 M4 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 M5 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 M6 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 M7 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 R1/2 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 R3 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 R4 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 R5 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 R6 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GRAI4 R7 | 400 | 93.3078 | 32.8697 | 27.9715 | 74.4563 | 90.0321 | 34.064 | 27.0999 | 75.2738
GREN1 M1 | 132 | 35.3011 | 13.0719 | 10.4427 | 28.9292 | 41.6525 | 16.2805 | 10.9507 | 33.9749
GREN1 M2 | 132 | 35.7993 | 13.3108 | 10.8246 | 29.6488 | 38.0942 | 14.8447 | 10.2708 | 31.2643
GREN1 R1 | 132 | 35.3011 | 13.0719 | 10.4427 | 28.9292 | 41.6525 | 16.2805 | 10.9507 | 33.9749
GREN1 R2 | 132 | 35.7993 | 13.3108 | 10.8246 | 29.6488 | 38.0942 | 14.8447 | 10.2708 | 31.2643
GREN4 M1 | 400 | 67.7849 | 24.7458 | 12.0039 | 46.9997 | 50.2287 | 20.1183 | 8.7058 | 37.1574
GREN4 M2 | 400 | 67.7849 | 24.7458 | 12.0039 | 46.9997 | 50.2287 | 20.1183 | 8.7058 | 37.1574
GREN4 R1 | 400 | 67.7849 | 24.7458 | 12.0039 | 46.9997 | 50.2287 | 20.1183 | 8.7058 | 37.1574
GREN4 R2 | 400 | 67.7849 | 24.7458 | 12.0039 | 46.9997 | 50.2287 | 20.1183 | 8.7058 | 37.1574
GRIW4 MC1 | 400 | 57.3535 | 20.4154 | 15.0169 | 43.8887 | 53.2974 | 20.36 | 11.0701 | 39.8635
GRIW4 MC2 | 400 | 57.3535 | 20.4154 | 15.0169 | 43.8887 | 53.2974 | 20.36 | 11.0701 | 39.8635
GRSA2 M1 | 275 | 52.8586 | 18.8245 | 15.891 | 42.5128 | 56.3866 | 20.9373 | 15.7104 | 45.3202
GRSA2 M2 | 275 | 52.8586 | 18.8245 | 15.891 | 42.5128 | 56.3866 | 20.9373 | 15.7104 | 45.3202
GRSA2 R1 | 275 | 52.8586 | 18.8245 | 15.891 | 42.5128 | 56.3866 | 20.9373 | 15.7104 | 45.3202
GRSA2 R2 | 275 | 52.8586 | 18.8245 | 15.891 | 42.5128 | 56.3866 | 20.9373 | 15.7104 | 45.3202
GRSB2 M3 | 275 | 53.1683 | 18.9209 | 16.0633 | 42.8215 | 57.2818 | 21.2114 | 16.3911 | 46.3886
GRSB2 M4 | 275 | 53.1683 | 18.9209 | 16.0633 | 42.8215 | 57.2818 | 21.2114 | 16.3911 | 46.3886
GRSB2 R3 | 275 | 53.1683 | 18.9209 | 16.0633 | 42.8215 | 57.2818 | 21.2114 | 16.3911 | 46.3886
GRSB2 R4 | 275 | 53.1683 | 18.9209 | 16.0633 | 42.8215 | 57.2818 | 21.2114 | 16.3911 | 46.3886
HACK2A | 275 | 60.7359 | 21.2257 | 9.5054 | 39.5231 | 63.9842 | 23.8481 | 10.415 | 44.1413
HACK2B | 275 | 59.6656 | 20.8658 | 9.5228 | 39.0316 | 64.1119 | 23.9249 | 10.4603 | 44.2953
HACK4 M1 | 400 | 87.6442 | 29.7091 | 20.1045 | 62.1195 | 104.1606 | 38.5947 | 22.7634 | 77.3444
HACK4 M2 | 400 | 87.6442 | 29.7091 | 20.1045 | 62.1195 | 104.1606 | 38.5947 | 22.7634 | 77.3444
HACK4 R1 | 400 | 87.6442 | 29.7091 | 20.1045 | 62.1195 | 104.1606 | 38.5947 | 22.7634 | 77.3444
HACK4 R2 | 400 | 87.6442 | 29.7091 | 20.1045 | 62.1195 | 104.1606 | 38.5947 | 22.7634 | 77.3444
HAMB4A | 400 | 58.5774 | 20.2799 | 7.7738 | 36.4539 | 53.7233 | 20.5199 | 4.6477 | 33.6673
HAMB4A_HEYS | 400 | 58.5774 | 20.2799 | 7.7738 | 36.4539 | 53.7233 | 20.5199 | 4.6477 | 33.6673
HAMB4A_PEWO | 400 | 58.5774 | 20.2799 | 7.7738 | 36.4539 | 53.7233 | 20.5199 | 4.6477 | 33.6673
HAMB4B | 400 | 58.556 | 20.2742 | 7.7661 | 36.4381 | 53.3968 | 20.3969 | 4.6477 | 33.4933
HAMB4B_HEYS | 400 | 58.556 | 20.2742 | 7.7661 | 36.4381 | 53.3968 | 20.3969 | 4.6477 | 33.4933
HAMB4B_PEWO | 400 | 58.556 | 20.2742 | 7.7661 | 36.4381 | 53.3968 | 20.3969 | 4.6477 | 33.4933
HAMH1B | 132 | 46.082 | 16.2847 | 9.3682 | 32.3983 | 55.6174 | 21.0762 | 5.9861 | 35.7924
HAMH1C | 132 | 45.1551 | 16.0622 | 8.17 | 30.8854 | 53.9054 | 20.115 | 7.6607 | 36.1076
HAMH4 M1 | 400 | 66.3894 | 24.1044 | 12.3028 | 46.3915 | 65.561 | 25.3278 | 12.8887 | 48.7077
HAMH4 M2 | 400 | 66.3894 | 24.1044 | 12.3028 | 46.3915 | 65.561 | 25.3278 | 12.8887 | 48.7077
HAMH4 R1 | 400 | 66.3894 | 24.1044 | 12.3028 | 46.3915 | 65.561 | 25.3278 | 12.8887 | 48.7077
HAMH4 R2 | 400 | 66.3894 | 24.1044 | 12.3028 | 46.3915 | 65.561 | 25.3278 | 12.8887 | 48.7077
HARK1 M1 | 132 | 26.8283 | 10.3067 | 6.9914 | 21.5673 | 31.4555 | 12.3545 | 7.6413 | 25.1133
HARK1 M2 | 132 | 26.8283 | 10.3067 | 6.9914 | 21.5673 | 31.4555 | 12.3545 | 7.6413 | 25.1133
HARK1 R1 | 132 | 26.4786 | 10.6241 | 7.3274 | 22.3522 | 31.1464 | 12.7295 | 8.7125 | 26.7147
HARK1 R2 | 132 | 28.9014 | 11.2382 | 7.6484 | 23.5416 | 34.6075 | 13.7505 | 9.1061 | 28.5522
HARK1 R3 | 132 | 28.9014 | 11.2382 | 7.6484 | 23.5416 | 34.6075 | 13.7505 | 9.1061 | 28.5522
HARK2 MC1 | 275 | 34.2554 | 12.8044 | 8.6157 | 26.7238 | 37.9415 | 14.5046 | 9.7999 | 30.3125
HARK2 MC11 | 275 | 36.5155 | 13.8146 | 11.2437 | 30.7805 | 41.599 | 16.0633 | 12.874 | 35.591
HARK2 MC12 | 275 | 36.5155 | 13.8146 | 11.2437 | 30.7805 | 41.599 | 16.0633 | 12.874 | 35.591
HARK2 MC13 | 275 | 36.5155 | 13.8146 | 11.2437 | 30.7805 | 41.599 | 16.0633 | 12.874 | 35.591
HARK2 MC2 | 275 | 34.2554 | 12.8044 | 8.6157 | 26.7238 | 37.9415 | 14.5046 | 9.7999 | 30.3125
HARK2 MC3 | 275 | 34.2554 | 12.8044 | 8.6157 | 26.7238 | 37.9415 | 14.5046 | 9.7999 | 30.3125
HARK2 MC4 | 275 | 34.2554 | 12.8044 | 8.6157 | 26.7238 | 37.9415 | 14.5046 | 9.7999 | 30.3125
HARK2 MC6 | 275 | 34.2554 | 12.8044 | 8.6157 | 26.7238 | 37.9415 | 14.5046 | 9.7999 | 30.3125
HARK2 MC8 | 275 | 36.5155 | 13.8146 | 11.2437 | 30.7805 | 41.599 | 16.0633 | 12.874 | 35.591
HARK2 MC9 | 275 | 36.5155 | 13.8146 | 11.2437 | 30.7805 | 41.599 | 16.0633 | 12.874 | 35.591
HARK4 M1 | 400 | 55.6277 | 20.0527 | 10.7135 | 39.0722 | 50.98 | 19.5852 | 11.1539 | 38.8515
HARK4 M2 | 400 | 55.6277 | 20.0527 | 10.7135 | 39.0722 | 50.98 | 19.5852 | 11.1539 | 38.8515
HARK4 R1 | 400 | 55.6277 | 20.0527 | 10.7135 | 39.0722 | 50.98 | 19.5852 | 11.1539 | 38.8515
HARK4 R2 | 400 | 55.6277 | 20.0527 | 10.7135 | 39.0722 | 50.98 | 19.5852 | 11.1539 | 38.8515
HARM2 MC1 | 275 | 62.6663 | 22.4414 | 14.2337 | 45.9707 | 55.3515 | 21.5461 | 9.4093 | 39.8801
HARM2 MC2 | 275 | 62.6663 | 22.4414 | 14.2337 | 45.9707 | 55.3515 | 21.5461 | 9.4093 | 39.8801
HARM2 MC3 | 275 | 62.6663 | 22.4414 | 14.2337 | 45.9707 | 55.3515 | 21.5461 | 9.4093 | 39.8801
HARM2 MC4 | 275 | 62.6663 | 22.4414 | 14.2337 | 45.9707 | 55.3515 | 21.5461 | 9.4093 | 39.8801
HATL2 M1 | 275 | 86.2354 | 29.5884 | 24.233 | 66.0773 | 91.5782 | 33.7024 | 26.0247 | 73.6871
HATL2 M2 | 275 | 86.2354 | 29.5884 | 24.233 | 66.0773 | 91.5782 | 33.7024 | 26.0247 | 73.6871
HATL2 R1 | 275 | 86.2354 | 29.5884 | 24.233 | 66.0773 | 91.5782 | 33.7024 | 26.0247 | 73.6871
HATL2 R2 | 275 | 86.2354 | 29.5884 | 24.233 | 66.0773 | 91.5782 | 33.7024 | 26.0247 | 73.6871
HAWP2 MC1 | 275 | 72.9457 | 25.8276 | 17.8355 | 54.3612 | 68.0217 | 26.2057 | 12.9539 | 50.0143
HAWP2 MC2 | 275 | 72.9457 | 25.8276 | 17.8355 | 54.3612 | 68.0217 | 26.2057 | 12.9539 | 50.0143
HAWP2 MC3 | 275 | 72.9457 | 25.8276 | 17.8355 | 54.3612 | 68.0217 | 26.2057 | 12.9539 | 50.0143
HAWP2 MC4 | 275 | 72.9457 | 25.8276 | 17.8355 | 54.3612 | 68.0217 | 26.2057 | 12.9539 | 50.0143
HEDO2 M1 | 275 | 49.4266 | 18.0307 | 12.9211 | 38.4203 | 54.8123 | 20.5881 | 14.8461 | 43.9621
HEDO2 M2 | 275 | 49.4266 | 18.0307 | 12.9211 | 38.4203 | 54.8123 | 20.5881 | 14.8461 | 43.9621
HEDO2 R1 | 275 | 49.4266 | 18.0307 | 12.9211 | 38.4203 | 54.8123 | 20.5881 | 14.8461 | 43.9621
HEDO2 R2 | 275 | 49.4266 | 18.0307 | 12.9211 | 38.4203 | 54.8123 | 20.5881 | 14.8461 | 43.9621
HEYS1 M1 | 132 | 34.066 | 11.2946 | 11.6152 | 27.5881 | 38.8875 | 13.8766 | 12.7406 | 32.3651
HEYS1 M2 | 132 | 34.066 | 11.2946 | 11.6152 | 27.5881 | 38.8875 | 13.8766 | 12.7406 | 32.3651
HEYS1 R1 | 132 | 34.066 | 11.2946 | 11.6152 | 27.5881 | 38.8875 | 13.8766 | 12.7406 | 32.3651
HEYS1 R2 | 132 | 34.066 | 11.2946 | 11.6152 | 27.5881 | 38.8875 | 13.8766 | 12.7406 | 32.3651
HEYS4 M1 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 M2 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 M3 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 M4 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 M5 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 R1/2 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 R3/4 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HEYS4 R5 | 400 | 74.1773 | 26.4318 | 24.6123 | 61.9926 | 83.8635 | 31.2168 | 28.4769 | 72.6242
HIBU4 M1 | 400 | 86.6318 | 29.3685 | 20.0691 | 61.6024 | 103.7691 | 38.3329 | 23.3523 | 77.5631
HIBU4 M2 | 400 | 86.6318 | 29.3685 | 20.0691 | 61.6024 | 103.7691 | 38.3329 | 23.3523 | 77.5631
HIBU4 R1 | 400 | 86.6318 | 29.3685 | 20.0691 | 61.6024 | 103.7691 | 38.3329 | 23.3523 | 77.5631
HIBU4 R2 | 400 | 86.6318 | 29.3685 | 20.0691 | 61.6024 | 103.7691 | 38.3329 | 23.3523 | 77.5631
HIGM2 M1 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM2 M2 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM2 M3 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM2 R1 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM2 R4 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM2 R5 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM2 R6 | 275 | 56.4498 | 20.6574 | 15.265 | 44.479 | 54.0064 | 21.1573 | 11.6041 | 41.5251
HIGM4 MC1 | 400 | 67.1382 | 24.1936 | 15.5852 | 49.8001 | 57.0526 | 22.1896 | 10.4633 | 41.8442
HIGM4 MC2 | 400 | 67.1382 | 24.1936 | 15.5852 | 49.8001 | 57.0526 | 22.1896 | 10.4633 | 41.8442
HIGM4A | 400 | 56.7467 | 20.1736 | 8.0937 | 36.6236 | 49.1101 | 18.8584 | 4.7429 | 31.4127
HINP2 M1 | 275 | 22.1444 | 7.8601 | 7.4993 | 18.6152 | 24.243 | 8.8796 | 8.0678 | 20.6255
HINP2 M2 | 275 | 22.5117 | 7.9988 | 7.5465 | 18.8584 | 26.7941 | 9.8571 | 8.474 | 22.4141
HINP4 M1 | 400 | 57.9229 | 20.3958 | 14.1494 | 42.9934 | 61.1327 | 22.8764 | 16.5174 | 48.8695
HINP4 M2 | 400 | 57.9229 | 20.3958 | 14.1494 | 42.9934 | 61.1327 | 22.8764 | 16.5174 | 48.8695
HINP4 M3 | 400 | 57.9229 | 20.3958 | 14.1494 | 42.9934 | 61.1327 | 22.8764 | 16.5174 | 48.8695
HINP4 M4 | 400 | 57.9229 | 20.3958 | 14.1494 | 42.9934 | 61.1327 | 22.8764 | 16.5174 | 48.8695
HINP4 R1/2 | 400 | 57.9229 | 20.3958 | 14.1494 | 42.9934 | 61.1327 | 22.8764 | 16.5174 | 48.8695
HINP4 R3/4 | 400 | 57.9229 | 20.3958 | 14.1494 | 42.9934 | 61.1327 | 22.8764 | 16.5174 | 48.8695
HUMR4 M1 | 400 | 73.6987 | 25.7772 | 19.545 | 55.9994 | 77.8092 | 28.9131 | 20.4228 | 61.3121
HUMR4 M2 | 400 | 73.6987 | 25.7772 | 19.545 | 55.9994 | 77.8092 | 28.9131 | 20.4228 | 61.3121
HUMR4 R1 | 400 | 73.6987 | 25.7772 | 19.545 | 55.9994 | 77.8092 | 28.9131 | 20.4228 | 61.3121
HUMR4 R2 | 400 | 73.6987 | 25.7772 | 19.545 | 55.9994 | 77.8092 | 28.9131 | 20.4228 | 61.3121
HURS2 MC1 | 275 | 61.0142 | 21.5633 | 16.0125 | 46.5076 | 66.4928 | 26.2392 | 14.7734 | 51.8812
HURS2 MC2 | 275 | 61.0142 | 21.5633 | 16.0125 | 46.5076 | 66.4928 | 26.2392 | 14.7734 | 51.8812
HURS2 MC3 | 275 | 61.0142 | 21.5633 | 16.0125 | 46.5076 | 66.4928 | 26.2392 | 14.7734 | 51.8812
HURS2 MC4 | 275 | 61.0142 | 21.5633 | 16.0125 | 46.5076 | 66.4928 | 26.2392 | 14.7734 | 51.8812
HUTT4 MC1 | 400 | 60.5331 | 22.2173 | 18.0999 | 49.5199 | 46.3755 | 18.5157 | 11.2482 | 37.4333
HUTT4 MC2 | 400 | 60.5331 | 22.2173 | 18.0999 | 49.5199 | 46.3755 | 18.5157 | 11.2482 | 37.4333
HUTT4 MC3 | 400 | 60.5331 | 22.2173 | 18.0999 | 49.5199 | 46.3755 | 18.5157 | 11.2482 | 37.4333
HUTT4 MC4 | 400 | 60.5331 | 22.2173 | 18.0999 | 49.5199 | 46.3755 | 18.5157 | 11.2482 | 37.4333
IMPP4 MC1 | 400 | 44.046 | 15.9579 | 8.9877 | 31.5555 | 40.6222 | 15.6191 | 8.0352 | 30.1239
IMPP4 MC2 | 400 | 44.046 | 15.9579 | 8.9877 | 31.5555 | 40.6222 | 15.6191 | 8.0352 | 30.1239
INDQ4 MC1 | 400 | 28.2627 | 10.5973 | 4.5916 | 19.5785 | 31.6251 | 12.2833 | 5.857 | 23.2282
INDQ4 MC2 | 400 | 28.2627 | 10.5973 | 4.5916 | 19.5785 | 31.6251 | 12.2833 | 5.857 | 23.2282
INDQ4 MC3 | 400 | 28.2627 | 10.5973 | 4.5916 | 19.5785 | 31.6251 | 12.2833 | 5.857 | 23.2282
INDQ4 MC4 | 400 | 28.2627 | 10.5973 | 4.5916 | 19.5785 | 31.6251 | 12.2833 | 5.857 | 23.2282
IROA1 M1 | 132 | 37.0797 | 13.4374 | 9.5499 | 28.5533 | 46.3125 | 17.4174 | 11.7013 | 36.3333
IROA1 M2 | 132 | 37.0797 | 13.4374 | 9.5499 | 28.5533 | 46.3125 | 17.4174 | 11.7013 | 36.3333
IROA1 R1 | 132 | 39.7346 | 14.3228 | 10.0083 | 30.2639 | 48.8581 | 18.4126 | 11.7536 | 37.793
IROA1 R2 | 132 | 27.0575 | 9.803 | 8.0989 | 21.9624 | 33.0801 | 12.3618 | 9.2375 | 26.7197
IROA2 MC1 | 275 | 50.262 | 18.1875 | 9.514 | 35.2351 | 50.5983 | 19.5116 | 10.0404 | 37.6339
IROA2 MC2 | 275 | 50.262 | 18.1875 | 9.514 | 35.2351 | 50.5983 | 19.5116 | 10.0404 | 37.6339
IROA2 MC3 | 275 | 50.262 | 18.1875 | 9.514 | 35.2351 | 50.5983 | 19.5116 | 10.0404 | 37.6339
IROA2 MC4 | 275 | 50.262 | 18.1875 | 9.514 | 35.2351 | 50.5983 | 19.5116 | 10.0404 | 37.6339
IROA2 MC5 | 275 | 50.262 | 18.1875 | 9.514 | 35.2351 | 50.5983 | 19.5116 | 10.0404 | 37.6339
IRON1 M1 | 132 | 27.2283 | 10.559 | 8.8649 | 23.7976 | 30.6503 | 12.0158 | 9.9797 | 26.9726
IRON1 M2 | 132 | 27.1013 | 10.515 | 8.7721 | 23.6425 | 30.3362 | 11.9076 | 9.8021 | 26.642
IRON1 R1 | 132 | 18.1926 | 6.613 | 6.3725 | 15.7247 | 20.7972 | 7.6034 | 7.4041 | 18.157
IRON1 R2 | 132 | 18.1926 | 6.613 | 6.3725 | 15.7247 | 20.7972 | 7.6034 | 7.4041 | 18.157
IRON4 M1 | 400 | 61.402 | 22.2732 | 11.5953 | 43.0944 | 56.0821 | 21.9205 | 10.2776 | 41.2778
IRON4 M2 | 400 | 61.402 | 22.2732 | 11.5953 | 43.0944 | 56.0821 | 21.9205 | 10.2776 | 41.2778
IRON4 R1 | 400 | 61.402 | 22.2732 | 11.5953 | 43.0944 | 56.0821 | 21.9205 | 10.2776 | 41.2778
IRON4 R2 | 400 | 61.402 | 22.2732 | 11.5953 | 43.0944 | 56.0821 | 21.9205 | 10.2776 | 41.2778
IVER2 M1 | 275 | 59.1219 | 21.354 | 14.8595 | 45.0586 | 65.236 | 24.72 | 15.7813 | 50.7406
IVER2 M2 | 275 | 59.1219 | 21.354 | 14.8595 | 45.0586 | 65.236 | 24.72 | 15.7813 | 50.7406
IVER2 R1 | 275 | 59.1219 | 21.354 | 14.8595 | 45.0586 | 65.236 | 24.72 | 15.7813 | 50.7406
IVER2 R2 | 275 | 60.0824 | 21.6998 | 13.9793 | 44.6674 | 62.4746 | 23.9901 | 13.3597 | 47.2868
IVER4A | 400 | 42.4552 | 15.2602 | 5.3063 | 26.8875 | 41.5675 | 15.8052 | 5.6609 | 28.0129
IVER4B | 400 | 41.0761 | 14.8194 | 4.9921 | 25.9498 | 39.6763 | 15.2898 | 4.9095 | 26.5326
JORD2 MC1 | 275 | 46.0255 | 17.2489 | 8.6432 | 33.0367 | 47.296 | 19.3469 | 7.394 | 34.7546
JORD2 MC2 | 275 | 46.0255 | 17.2489 | 8.6432 | 33.0367 | 47.296 | 19.3469 | 7.394 | 34.7546
KEAD4 M2 | 400 | 78.9877 | 27.9591 | 19.525 | 59.0652 | 78.167 | 29.5345 | 18.2466 | 60.0147
KEAD4 M3 | 400 | 78.4593 | 27.6578 | 20.159 | 59.273 | 71.9858 | 27.2668 | 16.2646 | 54.8256
KEAD4 R2 | 400 | 78.9877 | 27.9591 | 19.525 | 59.0652 | 78.167 | 29.5345 | 18.2466 | 60.0147
KEAD4 R3 | 400 | 76.9932 | 27.3967 | 17.6699 | 56.4148 | 65.9729 | 25.3492 | 14.314 | 50.1632
KEAR2 M1 | 275 | 65.1461 | 23.3988 | 16.8245 | 49.9154 | 73.1125 | 27.5604 | 18.1273 | 57.1037
KEAR2 M2 | 275 | 65.1461 | 23.3988 | 16.8245 | 49.9154 | 73.1125 | 27.5604 | 18.1273 | 57.1037
KEAR2 R1 | 275 | 65.1461 | 23.3988 | 16.8245 | 49.9154 | 73.1125 | 27.5604 | 18.1273 | 57.1037
KEAR2 R2 | 275 | 65.1461 | 23.3988 | 16.8245 | 49.9154 | 73.1125 | 27.5604 | 18.1273 | 57.1037
KEMS4 M1 | 400 | 91.1956 | 31.1011 | 19.5272 | 63.5108 | 82.1737 | 31.2681 | 15.8544 | 60.0742
KEMS4 M2 | 400 | 91.1956 | 31.1011 | 19.5272 | 63.5108 | 82.1737 | 31.2681 | 15.8544 | 60.0742
KEMS4 R1 | 400 | 91.1956 | 31.1011 | 19.5272 | 63.5108 | 82.1737 | 31.2681 | 15.8544 | 60.0742
KEMS4 R2 | 400 | 91.1956 | 31.1011 | 19.5272 | 63.5108 | 82.1737 | 31.2681 | 15.8544 | 60.0742
KENG4 M1 | 400 | 83.8578 | 28.4512 | 19.9417 | 60.1778 | 100.6416 | 37.2067 | 23.0731 | 75.6912
KENG4 M2 | 400 | 83.8578 | 28.4512 | 19.9417 | 60.1778 | 100.6416 | 37.2067 | 23.0731 | 75.6912
KENG4 R1 | 400 | 83.8578 | 28.4512 | 19.9417 | 60.1778 | 100.6416 | 37.2067 | 23.0731 | 75.6912
KENG4 R2 | 400 | 83.8578 | 28.4512 | 19.9417 | 60.1778 | 100.6416 | 37.2067 | 23.0731 | 75.6912
KIBY2 M1 | 275 | 62.9162 | 22.2336 | 15.5288 | 46.9718 | 69.973 | 26.3416 | 15.7789 | 53.0316
KIBY2 M2 | 275 | 62.9162 | 22.2336 | 15.5288 | 46.9718 | 69.973 | 26.3416 | 15.7789 | 53.0316
KIBY2 R1 | 275 | 55.9622 | 20.0318 | 13.4774 | 41.8066 | 57.7124 | 21.8369 | 13.0552 | 43.9372
KIBY2 R2 | 275 | 55.9622 | 20.0318 | 13.4774 | 41.8066 | 57.7124 | 21.8369 | 13.0552 | 43.9372
KILL4 M1 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 M2 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 M3 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 M4 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 M5 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 M9 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 R1/2 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 R3/4 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 R5 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KILL4 R9 | 400 | 78.0058 | 27.7884 | 26.7308 | 66.0295 | 84.3543 | 31.4949 | 28.2675 | 72.808
KINO1 M1 | 132 | 28.591 | 10.1399 | 10.1145 | 24.4544 | 34.8916 | 12.9196 | 12.2301 | 30.5012
KINO1 M2 | 132 | 28.591 | 10.1399 | 10.1145 | 24.4544 | 34.8916 | 12.9196 | 12.2301 | 30.5012
KINO1 R1 | 132 | 28.591 | 10.1399 | 10.1145 | 24.4544 | 34.8916 | 12.9196 | 12.2301 | 30.5012
KINO1 R2 | 132 | 28.591 | 10.1399 | 10.1145 | 24.4544 | 34.8916 | 12.9196 | 12.2301 | 30.5012
KINO1A | 132 | 28.2623 | 9.9643 | 6.0831 | 20.1747 | 34.4036 | 12.7797 | 7.2416 | 25.3149
KINO1B | 132 | 23.691 | 8.8879 | 1.5373 | 14.1068 | 25.4558 | 10.2802 | 0.88202 | 15.4205
KINO4 M1 | 400 | 86.5348 | 30.7001 | 25.9929 | 69.4094 | 87.54 | 33.2201 | 25.9705 | 72.9508
KINO4 M2 | 400 | 86.5348 | 30.7001 | 25.9929 | 69.4094 | 87.54 | 33.2201 | 25.9705 | 72.9508
KINO4 M3 | 400 | 86.5348 | 30.7001 | 25.9929 | 69.4094 | 87.54 | 33.2201 | 25.9705 | 72.9508
KINO4 M4 | 400 | 86.5348 | 30.7001 | 25.9929 | 69.4094 | 87.54 | 33.2201 | 25.9705 | 72.9508
KINO4 R1/2 | 400 | 86.5348 | 30.7001 | 25.9929 | 69.4094 | 87.54 | 33.2201 | 25.9705 | 72.9508
KINO4 R3/4 | 400 | 86.5348 | 30.7001 | 25.9929 | 69.4094 | 87.54 | 33.2201 | 25.9705 | 72.9508
KIRK2 MC1 | 275 | 48.0378 | 17.6095 | 11.2893 | 36.1929 | 51.2568 | 19.6839 | 12.4517 | 40.289
KIRK2 MC2 | 275 | 48.0378 | 17.6095 | 11.2893 | 36.1929 | 51.2568 | 19.6839 | 12.4517 | 40.289
KIRK2 MC3 | 275 | 48.0378 | 17.6095 | 11.2893 | 36.1929 | 51.2568 | 19.6839 | 12.4517 | 40.289
KIRK2 MC4 | 275 | 48.0378 | 17.6095 | 11.2893 | 36.1929 | 51.2568 | 19.6839 | 12.4517 | 40.289
KIRK2A | 275 | 47.4374 | 17.0147 | 6.0513 | 30.1138 | 47.9155 | 18.6781 | 7.6038 | 34.0186
KITW2 MC1 | 275 | 54.3858 | 19.9119 | 11.1053 | 39.2649 | 55.8153 | 21.7209 | 10.1477 | 40.8656
KITW2 MC2 | 275 | 54.3858 | 19.9119 | 11.1053 | 39.2649 | 55.8153 | 21.7209 | 10.1477 | 40.8656
KITW2 MC3 | 275 | 54.3858 | 19.9119 | 11.1053 | 39.2649 | 55.8153 | 21.7209 | 10.1477 | 40.8656
KITW2 MC4 | 275 | 54.3858 | 19.9119 | 11.1053 | 39.2649 | 55.8153 | 21.7209 | 10.1477 | 40.8656
KNAR2 MC1 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
KNAR2 MC1 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
KNAR2 MC1 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
KNAR2 MC1 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
KNAR2 MC2 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
KNAR2 MC2 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
KNAR2 MC2 | 275 | 27.644 | 11.1648 | 2.4141 | 18.2035 | 26.3901 | 10.893 | 3.4597 | 18.8647
LACK2 M1 | 275 | 62.9797 | 21.5839 | 17.9958 | 48.5201 | 68.919 | 25.2084 | 20.1705 | 55.8205
LACK2 M2 | 275 | 62.9797 | 21.5839 | 17.9958 | 48.5201 | 68.919 | 25.2084 | 20.1705 | 55.8205
LACK2 R1 | 275 | 62.9797 | 21.5839 | 17.9958 | 48.5201 | 68.919 | 25.2084 | 20.1705 | 55.8205
LACK2 R2 | 275 | 62.9797 | 21.5839 | 17.9958 | 48.5201 | 68.919 | 25.2084 | 20.1705 | 55.8205
LACK4 M1 | 400 | 66.584 | 24.1016 | 21.2934 | 55.3782 | 64.2651 | 24.3585 | 20.5507 | 54.9988
LACK4 M2 | 400 | 66.584 | 24.1016 | 21.2934 | 55.3782 | 64.2651 | 24.3585 | 20.5507 | 54.9988
LACK4 R1 | 400 | 66.584 | 24.1016 | 21.2934 | 55.3782 | 64.2651 | 24.3585 | 20.5507 | 54.9988
LACK4 R2 | 400 | 66.584 | 24.1016 | 21.2934 | 55.3782 | 64.2651 | 24.3585 | 20.5507 | 54.9988
LAGA4 M1 | 400 | 30.9105 | 11.4789 | 5.4287 | 21.6623 | 34.8254 | 13.4417 | 6.9483 | 25.9577
LAGA4 M2 | 400 | 30.9105 | 11.4789 | 5.4287 | 21.6623 | 34.8254 | 13.4417 | 6.9483 | 25.9577
LAGA4 R1 | 400 | 30.9105 | 11.4789 | 5.4287 | 21.6623 | 34.8254 | 13.4417 | 6.9483 | 25.9577
LAGA4 R2 | 400 | 30.9105 | 11.4789 | 5.4287 | 21.6623 | 34.8254 | 13.4417 | 6.9483 | 25.9577
LALE2 MC1 | 275 | 55.2425 | 19.628 | 15.5137 | 43.2719 | 61.8724 | 23.7624 | 15.3242 | 48.9292
LALE2 MC2 | 275 | 55.2425 | 19.628 | 15.5137 | 43.2719 | 61.8724 | 23.7624 | 15.3242 | 48.9292
LALE2 MC3 | 275 | 55.2425 | 19.628 | 15.5137 | 43.2719 | 61.8724 | 23.7624 | 15.3242 | 48.9292
LALE2 MC4 | 275 | 55.2425 | 19.628 | 15.5137 | 43.2719 | 61.8724 | 23.7624 | 15.3242 | 48.9292
LAND4 MC1 | 400 | 26.5609 | 9.9615 | 4.4988 | 18.5865 | 28.2711 | 11.0658 | 4.7923 | 20.4417
LAND4 MC2 | 400 | 26.5609 | 9.9615 | 4.4988 | 18.5865 | 28.2711 | 11.0658 | 4.7923 | 20.4417
LEGA4 M1 | 400 | 63.9164 | 22.7301 | 13.4164 | 45.5616 | 58.4287 | 22.7644 | 10.6691 | 42.8628
LEGA4 M2 | 400 | 63.9164 | 22.7301 | 13.4164 | 45.5616 | 58.4287 | 22.7644 | 10.6691 | 42.8628
LEGA4 R1 | 400 | 63.9164 | 22.7301 | 13.4164 | 45.5616 | 58.4287 | 22.7644 | 10.6691 | 42.8628
LEGA4 R2 | 400 | 63.9164 | 22.7301 | 13.4164 | 45.5616 | 58.4287 | 22.7644 | 10.6691 | 42.8628
LEIS1 M1 | 132 | 53.7942 | 19.2428 | 19.3504 | 46.5638 | 64.4633 | 23.422 | 23.112 | 56.2357
LEIS1 M2 | 132 | 53.7942 | 19.2428 | 19.3504 | 46.5638 | 64.4633 | 23.422 | 23.112 | 56.2357
LEIS1 R1 | 132 | 53.7942 | 19.2428 | 19.3504 | 46.5638 | 64.4633 | 23.422 | 23.112 | 56.2357
LEIS1 R2 | 132 | 53.7942 | 19.2428 | 19.3504 | 46.5638 | 64.4633 | 23.422 | 23.112 | 56.2357
LISD2 M1 | 275 | 58.8962 | 20.9228 | 14.2766 | 43.8658 | 65.8707 | 24.9647 | 14.6064 | 49.9119
LISD2 M2 | 275 | 58.8962 | 20.9228 | 14.2766 | 43.8658 | 65.8707 | 24.9647 | 14.6064 | 49.9119
LISD2 R1 | 275 | 58.8962 | 20.9228 | 14.2766 | 43.8658 | 65.8707 | 24.9647 | 14.6064 | 49.9119
LISD2 R2 | 275 | 58.8962 | 20.9228 | 14.2766 | 43.8658 | 65.8707 | 24.9647 | 14.6064 | 49.9119
LITB4 Term500 | 400 | 64.7255 | 22.6199 | 6.9989 | 38.9884 | 62.8566 | 23.542 | 9.7971 | 43.0905
LITT4 M1 | 400 | 90.2312 | 30.7724 | 19.294 | 62.8127 | 90.0805 | 34.141 | 18.4155 | 66.6982
LITT4 M2 | 400 | 90.2312 | 30.7724 | 19.294 | 62.8127 | 90.0805 | 34.141 | 18.4155 | 66.6982
LITT4 M3 | 400 | 90.2312 | 30.7724 | 19.294 | 62.8127 | 90.0805 | 34.141 | 18.4155 | 66.6982
LITT4 R1 | 400 | 90.2312 | 30.7724 | 19.294 | 62.8127 | 90.0805 | 34.141 | 18.4155 | 66.6982
LITT4 R2 | 400 | 90.2312 | 30.7724 | 19.294 | 62.8127 | 90.0805 | 34.141 | 18.4155 | 66.6982
LITT4 R3 | 400 | 90.2312 | 30.7724 | 19.294 | 62.8127 | 90.0805 | 34.141 | 18.4155 | 66.6982
LOFI4A | 400 | 73.8969 | 24.9708 | 6.0441 | 41.3581 | 67.1116 | 25.7731 | 3.7777 | 40.2264
LOFI4A_KEMS | 400 | 73.8969 | 24.9708 | 6.0441 | 41.3581 | 67.1116 | 25.7731 | 3.7777 | 40.2264
LOFI4A_LITT | 400 | 73.8969 | 24.9708 | 6.0441 | 41.3581 | 67.1116 | 25.7731 | 3.7777 | 40.2264
LOFI4A_ROWD | 400 | 73.8969 | 24.9708 | 6.0441 | 41.3581 | 67.1116 | 25.7731 | 3.7777 | 40.2264
LOFI4B | 400 | 73.2324 | 24.8031 | 5.8894 | 40.9662 | 67.5866 | 25.9718 | 3.727 | 40.4567
LOFI4B_KEMS | 400 | 73.2324 | 24.8031 | 5.8894 | 40.9662 | 67.5866 | 25.9718 | 3.727 | 40.4567
LOFI4B_LITT | 400 | 73.2324 | 24.8031 | 5.8894 | 40.9662 | 67.5866 | 25.9718 | 3.727 | 40.4567
LOFI4B_ROWD | 400 | 73.2324 | 24.8031 | 5.8894 | 40.9662 | 67.5866 | 25.9718 | 3.727 | 40.4567
LOVE4 M1 | 400 | 71.61 | 25.3265 | 14.294 | 50.1111 | 64.3921 | 24.743 | 13.0253 | 48.0172
LOVE4 M2 | 400 | 71.61 | 25.3265 | 14.294 | 50.1111 | 64.3921 | 24.743 | 13.0253 | 48.0172
LOVE4 R1 | 400 | 71.61 | 25.3265 | 14.294 | 50.1111 | 64.3921 | 24.743 | 13.0253 | 48.0172
LOVE4 R2 | 400 | 71.61 | 25.3265 | 14.294 | 50.1111 | 64.3921 | 24.743 | 13.0253 | 48.0172
MACC2 MC1 | 275 | 52.5066 | 19.1868 | 12.9117 | 40.0459 | 51.1182 | 19.6355 | 11.5155 | 39.2843
MACC2 MC2 | 275 | 52.5066 | 19.1868 | 12.9117 | 40.0459 | 51.1182 | 19.6355 | 11.5155 | 39.2843
MACC4 MC1 | 400 | 69.9819 | 25.8063 | 20.0123 | 56.5078 | 57.4566 | 22.7655 | 14.3827 | 46.5781
MACC4 MC2 | 400 | 69.9819 | 25.8063 | 20.0123 | 56.5078 | 57.4566 | 22.7655 | 14.3827 | 46.5781
MACC4 MC3 | 400 | 69.9819 | 25.8063 | 20.0123 | 56.5078 | 57.4566 | 22.7655 | 14.3827 | 46.5781
MACC4 MC4 | 400 | 69.9819 | 25.8063 | 20.0123 | 56.5078 | 57.4566 | 22.7655 | 14.3827 | 46.5781
MAGA2 MC1 | 275 | 39.4126 | 14.4121 | 7.4836 | 27.8654 | 38.4224 | 15.1018 | 6.6523 | 28.0095
MAGA2 MC2 | 275 | 39.4126 | 14.4121 | 7.4836 | 27.8654 | 38.4224 | 15.1018 | 6.6523 | 28.0095
MANN4 M5 | 400 | 43.2315 | 15.658 | 8.6636 | 30.8074 | 43.5366 | 16.5879 | 9.5608 | 33.0196
MANN4 MC1 | 400 | 43.2315 | 15.658 | 8.6636 | 30.8074 | 43.5366 | 16.5879 | 9.5608 | 33.0196
MANN4 MC2 | 400 | 43.2315 | 15.658 | 8.6636 | 30.8074 | 43.5366 | 16.5879 | 9.5608 | 33.0196
MANN4 MC3 | 400 | 43.2315 | 15.658 | 8.6636 | 30.8074 | 43.5366 | 16.5879 | 9.5608 | 33.0196
MANN4 MC4 | 400 | 43.2315 | 15.658 | 8.6636 | 30.8074 | 43.5366 | 16.5879 | 9.5608 | 33.0196
MANN4 R5 | 400 | 43.2315 | 15.658 | 8.6636 | 30.8074 | 43.5366 | 16.5879 | 9.5608 | 33.0196
MAWO4 M | 400 | 39.4841 | 14.3631 | 7.9851 | 28.2977 | 34.5888 | 13.3517 | 6.7958 | 25.678
MAWO4 R | 400 | 39.4841 | 14.3631 | 7.9851 | 28.2977 | 34.5888 | 13.3517 | 6.7958 | 25.678
MEDW4 Term500 | 400 | 82.3101 | 28.3407 | 16.8166 | 56.8964 | 79.0359 | 29.7703 | 17.1128 | 59.2143
MELK1 M1 | 132 | 40.6161 | 14.4196 | 14.4195 | 34.8119 | 50.6158 | 18.5571 | 16.9867 | 43.2305
MELK1 M2 | 132 | 40.6161 | 14.4196 | 14.4195 | 34.8119 | 50.6158 | 18.5571 | 16.9867 | 43.2305
MELK1 R1 | 132 | 40.6161 | 14.4196 | 14.4195 | 34.8119 | 50.6158 | 18.5571 | 16.9867 | 43.2305
MELK1 R2 | 132 | 40.6161 | 14.4196 | 14.4195 | 34.8119 | 50.6158 | 18.5571 | 16.9867 | 43.2305
MELK4 M1 | 400 | 81.3089 | 28.7623 | 15.4623 | 56.1383 | 75.2257 | 29.22 | 12.9389 | 54.2623
MELK4 M2 | 400 | 81.3089 | 28.7623 | 15.4623 | 56.1383 | 75.2257 | 29.22 | 12.9389 | 54.2623
MELK4 M3 | 400 | 81.3089 | 28.7623 | 15.4623 | 56.1383 | 75.2257 | 29.22 | 12.9389 | 54.2623
MELK4 R1 | 400 | 81.3089 | 28.7623 | 15.4623 | 56.1383 | 75.2257 | 29.22 | 12.9389 | 54.2623
MELK4 R2 | 400 | 81.3089 | 28.7623 | 15.4623 | 56.1383 | 75.2257 | 29.22 | 12.9389 | 54.2623
MELK4 R3 | 400 | 81.3089 | 28.7623 | 15.4623 | 56.1383 | 75.2257 | 29.22 | 12.9389 | 54.2623
MILH1 M1 | 132 | 37.1693 | 13.8998 | 8.7996 | 28.4568 | 43.609 | 17.6176 | 9.0259 | 33.9409
MILH1 M2 | 132 | 37.1693 | 13.8998 | 8.7996 | 28.4568 | 43.609 | 17.6176 | 9.0259 | 33.9409
MILH1 R1 | 132 | 37.1634 | 13.8976 | 8.7991 | 28.4533 | 43.6017 | 17.6145 | 9.0402 | 33.9508
MILH1 R2 | 132 | 37.1634 | 13.8976 | 8.7991 | 28.4533 | 43.6017 | 17.6145 | 9.0402 | 33.9508
MITY4 MC1 | 400 | 67.4533 | 25.1185 | 18.0075 | 53.5304 | 55.6625 | 22.2643 | 13.2041 | 44.6907
MITY4 MC2 | 400 | 67.4533 | 25.1185 | 18.0075 | 53.5304 | 55.6625 | 22.2643 | 13.2041 | 44.6907
MITY4 MC3 | 400 | 67.4533 | 25.1185 | 18.0075 | 53.5304 | 55.6625 | 22.2643 | 13.2041 | 44.6907
MITY4 MC4 | 400 | 67.4533 | 25.1185 | 18.0075 | 53.5304 | 55.6625 | 22.2643 | 13.2041 | 44.6907
MONF2 M1 | 275 | 58.0366 | 20.9675 | 15.7799 | 45.4325 | 61.5368 | 23.305 | 15.2939 | 48.2522
MONF2 M2 | 275 | 58.0366 | 20.9675 | 15.7799 | 45.4325 | 61.5368 | 23.305 | 15.2939 | 48.2522
MONF2 R1 | 275 | 51.954 | 18.6778 | 16.2475 | 42.662 | 56.469 | 21.1307 | 16.383 | 46.2664
MONF2 R2 | 275 | 51.954 | 18.6778 | 16.2475 | 42.662 | 56.469 | 21.1307 | 16.383 | 46.2664
MONF4 MC2 | 400 | 67.2113 | 23.8733 | 15.9872 | 49.7491 | 63.2192 | 23.9636 | 14.3851 | 48.2747
MONF4 MC3 | 400 | 67.2113 | 23.8733 | 15.9872 | 49.7491 | 63.2192 | 23.9636 | 14.3851 | 48.2747
NECH2 MC1 | 275 | 64.824 | 23.1815 | 16.4747 | 49.2583 | 68.0718 | 26.0656 | 15.0386 | 51.9009
NECH2 MC2 | 275 | 64.824 | 23.1815 | 16.4747 | 49.2583 | 68.0718 | 26.0656 | 15.0386 | 51.9009
NECH2 MC3 | 275 | 64.824 | 23.1815 | 16.4747 | 49.2583 | 68.0718 | 26.0656 | 15.0386 | 51.9009
NECH2 MC4 | 275 | 64.824 | 23.1815 | 16.4747 | 49.2583 | 68.0718 | 26.0656 | 15.0386 | 51.9009
NECT4 M1 | 400 | 58.9692 | 21.207 | 13.7338 | 43.7251 | 42.0747 | 16.8733 | 5.7648 | 29.6273
NECT4 R1 | 400 | 58.9692 | 21.207 | 13.7338 | 43.7251 | 42.0747 | 16.8733 | 5.7648 | 29.6273
NEEP2 M1 | 275 | 53.375 | 19.6017 | 12.0097 | 39.7307 | 58.2133 | 22.9549 | 11.6987 | 44.1618
NEEP2 M2 | 275 | 53.375 | 19.6017 | 12.0097 | 39.7307 | 58.2133 | 22.9549 | 11.6987 | 44.1618
NEEP2 R1/R2 | 275 | 53.375 | 19.6017 | 12.0097 | 39.7307 | 58.2133 | 22.9549 | 11.6987 | 44.1618
NEWX2 M5 | 275 | 65.141 | 22.9546 | 16.3703 | 48.833 | 74.1407 | 28.9026 | 15.416 | 56.2905
NEWX2 M5 | 275 | 65.141 | 22.9546 | 16.3703 | 48.833 | 74.1407 | 28.9026 | 15.416 | 56.2905
NEWX2 M6 | 275 | 65.141 | 22.9546 | 16.3703 | 48.833 | 74.1407 | 28.9026 | 15.416 | 56.2905
NEWX2 R6 | 275 | 65.141 | 22.9546 | 16.3703 | 48.833 | 74.1407 | 28.9026 | 15.416 | 56.2905
NEWX2 R5 | 275 | 65.141 | 22.9546 | 16.3703 | 48.833 | 74.1407 | 28.9026 | 15.416 | 56.2905
NFLE4 M1 | 400 | 78.4934 | 27.1411 | 16.4061 | 54.7894 | 70.4391 | 27.1946 | 12.675 | 51.1339
NFLE4 M2 | 400 | 78.4934 | 27.1411 | 16.4061 | 54.7894 | 70.4391 | 27.1946 | 12.675 | 51.1339
NFLE4 R1 | 400 | 78.4934 | 27.1411 | 16.4061 | 54.7894 | 70.4391 | 27.1946 | 12.675 | 51.1339
NFLE4 R2 | 400 | 78.4934 | 27.1411 | 16.4061 | 54.7894 | 70.4391 | 27.1946 | 12.675 | 51.1339
NHYD2A | 275 | 42.5834 | 15.9475 | 2.6401 | 25.1933 | 37.8108 | 17.6262 | 0.45859 | 25.3858
NHYD2B | 275 | 43.0194 | 16.0819 | 2.3654 | 25.1086 | 38.1639 | 17.3397 | 1.0112 | 25.5333
NHYD2C | 275 | 43.0194 | 16.0819 | 2.3654 | 25.1086 | 38.1639 | 17.3397 | 1.0112 | 25.5333
NINF4 M1 | 400 | 53.7521 | 19.4717 | 11.5431 | 39.0802 | 47.9605 | 18.4223 | 10.6697 | 36.7227
NINF4 M2 | 400 | 53.7521 | 19.4717 | 11.5431 | 39.0802 | 47.9605 | 18.4223 | 10.6697 | 36.7227
NINF4 R1 | 400 | 53.7521 | 19.4717 | 11.5431 | 39.0802 | 47.9605 | 18.4223 | 10.6697 | 36.7227
NINF4 R2 | 400 | 53.7521 | 19.4717 | 11.5431 | 39.0802 | 47.9605 | 18.4223 | 10.6697 | 36.7227
NORL2A | 275 | 47.436 | 17.3653 | 4.0172 | 28.5754 | 48.7219 | 19.8305 | 2.4236 | 30.4682
NORL2B | 275 | 46.6857 | 17.1644 | 3.5414 | 27.8155 | 47.9157 | 19.7581 | 2.1257 | 30.0679
NORM4 M1 | 400 | 55.5242 | 20.0458 | 12.625 | 40.974 | 46.2099 | 18.0032 | 9.9599 | 35.4203
NORM4 M2 | 400 | 55.5242 | 20.0458 | 12.625 | 40.974 | 46.2099 | 18.0032 | 9.9599 | 35.4203
NORM4 R1 | 400 | 55.5242 | 20.0458 | 12.625 | 40.974 | 46.2099 | 18.0032 | 9.9599 | 35.4203
NORM4 R2 | 400 | 55.5242 | 20.0458 | 12.625 | 40.974 | 46.2099 | 18.0032 | 9.9599 | 35.4203
NORT2 M1 | 275 | 78.5069 | 27.375 | 21.7185 | 60.4326 | 82.1763 | 30.8776 | 19.3414 | 63.0089
NORT2 M2 | 275 | 78.5069 | 27.375 | 21.7185 | 60.4326 | 82.1763 | 30.8776 | 19.3414 | 63.0089
NORT2 R1 | 275 | 78.5069 | 27.375 | 21.7185 | 60.4326 | 82.1763 | 30.8776 | 19.3414 | 63.0089
NORT2 R2 | 275 | 78.5069 | 27.375 | 21.7185 | 60.4326 | 82.1763 | 30.8776 | 19.3414 | 63.0089
NORT4 M1 | 400 | 78.6769 | 28.1309 | 25.5456 | 65.3287 | 72.3042 | 27.6822 | 21.2021 | 60.3506
NORT4 M2 | 400 | 78.6769 | 28.1309 | 25.5456 | 65.3287 | 72.3042 | 27.6822 | 21.2021 | 60.3506
NORT4 R1 | 400 | 78.6769 | 28.1309 | 25.5456 | 65.3287 | 72.3042 | 27.6822 | 21.2021 | 60.3506
NORT4 R2 | 400 | 78.6769 | 28.1309 | 25.5456 | 65.3287 | 72.3042 | 27.6822 | 21.2021 | 60.3506
NURS4 MC1 | 400 | 41.5799 | 14.8874 | 5.713 | 26.767 | 38.423 | 14.6223 | 5.7353 | 26.4144
NURS4 MC2 | 400 | 41.5799 | 14.8874 | 5.713 | 26.767 | 38.423 | 14.6223 | 5.7353 | 26.4144
NURS4A | 400 | 43.9855 | 15.9693 | 9.0134 | 31.5974 | 41.5516 | 15.877 | 9.0935 | 31.547
OCKH1 M1 | 132 | 24.1449 | 8.7254 | 8.2863 | 20.6258 | 32.6386 | 11.9644 | 10.9928 | 27.9131
OCKH1 M2 | 132 | 24.1449 | 8.7254 | 8.2863 | 20.6258 | 32.6386 | 11.9644 | 10.9928 | 27.9131
OCKH1 R1 | 132 | 24.1449 | 8.7254 | 8.2863 | 20.6258 | 32.6386 | 11.9644 | 10.9928 | 27.9131
OCKH1 R2 | 132 | 24.1449 | 8.7254 | 8.2863 | 20.6258 | 32.6386 | 11.9644 | 10.9928 | 27.9131
OCKH2 MC1 | 275 | 49.6184 | 18.2545 | 10.0043 | 35.82 | 53.3163 | 20.7487 | 10.3911 | 39.7341
OCKH2 MC2 | 275 | 49.6184 | 18.2545 | 10.0043 | 35.82 | 53.3163 | 20.7487 | 10.3911 | 39.7341
OCKH2 MC3 | 275 | 49.6184 | 18.2545 | 10.0043 | 35.82 | 53.3163 | 20.7487 | 10.3911 | 39.7341
OCKH2 MC4 | 275 | 49.6184 | 18.2545 | 10.0043 | 35.82 | 53.3163 | 20.7487 | 10.3911 | 39.7341
OCKH2A | 275 | 44.5823 | 16.117 | 4.2023 | 26.9952 | 46.2792 | 17.8363 | 4.6231 | 29.8475
OFFE2 MC1 | 275 | 65.1961 | 23.5472 | 13.2849 | 46.5856 | 58.1545 | 23.0174 | 8.6057 | 41.1572
OFFE2 MC2 | 275 | 65.1961 | 23.5472 | 13.2849 | 46.5856 | 58.1545 | 23.0174 | 8.6057 | 41.1572
OLDB2 MC1 | 275 | 47.952 | 17.6817 | 10.0014 | 35.0071 | 51.1212 | 19.7325 | 10.4373 | 38.3432
OLDB2 MC2 | 275 | 47.952 | 17.6817 | 10.0014 | 35.0071 | 51.1212 | 19.7325 | 10.4373 | 38.3432
OSBA4 MC1 | 400 | 51.2434 | 18.556 | 11.7535 | 37.9957 | 48.2258 | 18.291 | 11.7173 | 37.5846
OSBA4 MC2 | 400 | 51.2434 | 18.556 | 11.7535 | 37.9957 | 48.2258 | 18.291 | 11.7173 | 37.5846
OSBA4 MC3/4 | 400 | 50.7218 | 18.3972 | 11.941 | 37.9586 | 42.8964 | 16.4937 | 9.3032 | 32.6289
PADI1 M1 | 132 | 31.6318 | 11.3507 | 11.179 | 27.2313 | 39.4362 | 14.4579 | 13.5462 | 33.9927
PADI1 M2 | 132 | 31.6318 | 11.3507 | 11.179 | 27.2313 | 39.4362 | 14.4579 | 13.5462 | 33.9927
PADI1 R1 | 132 | 31.6318 | 11.3507 | 11.179 | 27.2313 | 39.4362 | 14.4579 | 13.5462 | 33.9927
PADI1 R2 | 132 | 31.6318 | 11.3507 | 11.179 | 27.2313 | 39.4362 | 14.4579 | 13.5462 | 33.9927
PADI4 MC1 | 400 | 64.665 | 23.1425 | 14.2829 | 47.0113 | 53.3533 | 20.855 | 9.4343 | 38.9277
PADI4 MC2 | 400 | 64.665 | 23.1425 | 14.2829 | 47.0113 | 53.3533 | 20.855 | 9.4343 | 38.9277
PADI4 MC3 | 400 | 64.665 | 23.1425 | 14.2829 | 47.0113 | 53.3533 | 20.855 | 9.4343 | 38.9277
PADI4 MC4 | 400 | 64.665 | 23.1425 | 14.2829 | 47.0113 | 53.3533 | 20.855 | 9.4343 | 38.9277
PELH4 M1 | 400 | 101.625 | 35.0079 | 23.8563 | 73.3649 | 93.633 | 35.6661 | 18.8054 | 69.2449
PELH4 M2 | 400 | 101.625 | 35.0079 | 23.8563 | 73.3649 | 93.633 | 35.6661 | 18.8054 | 69.2449
PELH4 R1 | 400 | 101.625 | 35.0079 | 23.8563 | 73.3649 | 93.633 | 35.6661 | 18.8054 | 69.2449
PELH4 R2 | 400 | 101.625 | 35.0079 | 23.8563 | 73.3649 | 93.633 | 35.6661 | 18.8054 | 69.2449
PEMB4 M1 | 400 | 37.8225 | 13.5991 | 8.5915 | 27.8235 | 36.0744 | 13.6883 | 8.8502 | 28.2084
PEMB4 M2 | 400 | 37.8225 | 13.5991 | 8.5915 | 27.8235 | 36.0744 | 13.6883 | 8.8502 | 28.2084
PEMB4 M3 | 400 | 37.8225 | 13.5991 | 8.5915 | 27.8235 | 36.0744 | 13.6883 | 8.8502 | 28.2084
PEMB4 M4 | 400 | 37.8225 | 13.5991 | 8.5915 | 27.8235 | 36.0744 | 13.6883 | 8.8502 | 28.2084
PEMB4 R1/2 | 400 | 37.8225 | 13.5991 | 8.5915 | 27.8235 | 36.0744 | 13.6883 | 8.8502 | 28.2084
PEMB4 R3/4 | 400 | 37.8225 | 13.5991 | 8.5915 | 27.8235 | 36.0744 | 13.6883 | 8.8502 | 28.2084
PENN2 MC1 | 275 | 59.0447 | 21.4525 | 12.777 | 43.1154 | 64.3257 | 24.5834 | 13.8947 | 48.6609
PENN2 MC2 | 275 | 59.0447 | 21.4525 | 12.777 | 43.1154 | 64.3257 | 24.5834 | 13.8947 | 48.6609
PENN2 MC3 | 275 | 59.0447 | 21.4525 | 12.777 | 43.1154 | 64.3257 | 24.5834 | 13.8947 | 48.6609
PENN2 MC4 | 275 | 59.0447 | 21.4525 | 12.777 | 43.1154 | 64.3257 | 24.5834 | 13.8947 | 48.6609
PENT4 M1 | 400 | 41.4024 | 15.0052 | 8.6332 | 29.8537 | 48.8652 | 18.4988 | 10.6146 | 36.7758
PENT4 M2 | 400 | 41.4024 | 15.0052 | 8.6332 | 29.8537 | 48.8652 | 18.4988 | 10.6146 | 36.7758
PENT4 R1 | 400 | 41.4024 | 15.0052 | 8.6332 | 29.8537 | 48.8652 | 18.4988 | 10.6146 | 36.7758
PENT4 R2 | 400 | 41.4024 | 15.0052 | 8.6332 | 29.8537 | 48.8652 | 18.4988 | 10.6146 | 36.7758
PEWO2A | 275 | 60.3645 | 21.4075 | 17.9529 | 48.2277 | 65.1594 | 24.2018 | 18.393 | 52.6195
PEWO2B | 275 | 61.3762 | 22.1586 | 21.9691 | 53.3061 | 66.072 | 24.6995 | 23.1067 | 58.0372
PEWO4 M1 | 400 | 78.5968 | 28.1436 | 25.1776 | 64.9786 | 79.4609 | 30.3353 | 23.8167 | 66.7172
PEWO4 M2 | 400 | 78.5968 | 28.1436 | 25.1776 | 64.9786 | 79.4609 | 30.3353 | 23.8167 | 66.7172
PEWO4 M3 | 400 | 78.5968 | 28.1436 | 25.1776 | 64.9786 | 79.4609 | 30.3353 | 23.8167 | 66.7172
PEWO4 M4 | 400 | 78.5968 | 28.1436 | 25.1776 | 64.9786 | 79.4609 | 30.3353 | 23.8167 | 66.7172
PEWO4 R1/2 | 400 | 78.5968 | 28.1436 | 25.1776 | 64.9786 | 79.4609 | 30.3353 | 23.8167 | 66.7172
PEWO4 R3/4 | 400 | 78.5968 | 28.1436 | 25.1776 | 64.9786 | 79.4609 | 30.3353 | 23.8167 | 66.7172
PITS2 MC1 | 275 | 54.4733 | 19.7498 | 8.2327 | 36.1631 | 60.83 | 23.6841 | 7.589 | 41.0834
PITS2 MC2 | 275 | 54.4733 | 19.7498 | 8.2327 | 36.1631 | 60.83 | 23.6841 | 7.589 | 41.0834
PITS2 MC3 | 275 | 54.4733 | 19.7498 | 8.2327 | 36.1631 | 60.83 | 23.6841 | 7.589 | 41.0834
PITS2 MC4 | 275 | 54.4733 | 19.7498 | 8.2327 | 36.1631 | 60.83 | 23.6841 | 7.589 | 41.0834
POPP2 MC1 | 275 | 26.3249 | 10.4871 | 2.8741 | 17.7052 | 22.9957 | 9.4554 | 3.1179 | 16.4898
POPP2 MC2 | 275 | 26.3249 | 10.4871 | 2.8741 | 17.7052 | 22.9957 | 9.4554 | 3.1179 | 16.4898
PUDM4 MC1 | 400 | 77.6494 | 26.6915 | 17.6642 | 55.4117 | 85.224 | 33.181 | 16.5477 | 63.4727
PUDM4 MC2 | 400 | 77.6494 | 26.6915 | 17.6642 | 55.4117 | 85.224 | 33.181 | 16.5477 | 63.4727
PYLE2 MC1 | 275 | 41.7479 | 15.2734 | 7.5721 | 29.1719 | 40.7817 | 16.011 | 7.2137 | 29.8567
PYLE2 MC2 | 275 | 41.7749 | 15.2827 | 7.5775 | 29.1905 | 40.8109 | 16.0212 | 7.2238 | 29.8812
QUER4A | 400 | 66.9988 | 22.8561 | 9.6028 | 41.9261 | 64.3633 | 24.3368 | 5.4682 | 39.8857
QUER4A_HEYS | 400 | 66.9988 | 22.8561 | 9.6028 | 41.9261 | 64.3633 | 24.3368 | 5.4682 | 39.8857
QUER4A_HUTT | 400 | 66.9988 | 22.8561 | 9.6028 | 41.9261 | 64.3633 | 24.3368 | 5.4682 | 39.8857
QUER4A_PEWO | 400 | 66.9988 | 22.8561 | 9.6028 | 41.9261 | 64.3633 | 24.3368 | 5.4682 | 39.8857
QUER4B | 400 | 67.4758 | 22.9907 | 9.7586 | 42.2724 | 65.9187 | 24.8349 | 5.9857 | 41.1075
QUER4B_HEYS | 400 | 67.4758 | 22.9907 | 9.7586 | 42.2724 | 65.9187 | 24.8349 | 5.9857 | 41.1075
QUER4B_HUTT | 400 | 67.4758 | 22.9907 | 9.7586 | 42.2724 | 65.9187 | 24.8349 | 5.9857 | 41.1075
QUER4B_PEWO | 400 | 67.4758 | 22.9907 | 9.7586 | 42.2724 | 65.9187 | 24.8349 | 5.9857 | 41.1075
RAIN2 MC1 | 275 | 65.8329 | 23.1695 | 16.6632 | 49.4298 | 69.0973 | 26.0529 | 15.2303 | 52.0746
RAIN2 MC2 | 275 | 65.8329 | 23.1695 | 16.6632 | 49.4298 | 69.0973 | 26.0529 | 15.2303 | 52.0746
RAIN2 MC3 | 275 | 65.8329 | 23.1695 | 16.6632 | 49.4298 | 69.0973 | 26.0529 | 15.2303 | 52.0746
RAIN2 MC4 | 275 | 65.8329 | 23.1695 | 16.6632 | 49.4298 | 69.0973 | 26.0529 | 15.2303 | 52.0746
RASS4 M1 | 400 | 43.2343 | 16.0044 | 12.5937 | 35.2274 | 38.2583 | 14.9425 | 10.2278 | 31.3597
RASS4 M2 | 400 | 43.2343 | 16.0044 | 12.5937 | 35.2274 | 38.2583 | 14.9425 | 10.2278 | 31.3597
RATS1 M1 | 132 | 42.0918 | 14.9539 | 13.9794 | 35.1274 | 48.2385 | 17.8776 | 16.296 | 41.5787
RATS1 M2 | 132 | 42.0918 | 14.9539 | 13.9794 | 35.1274 | 48.2385 | 17.8776 | 16.296 | 41.5787
RATS1 R1 | 132 | 37.9674 | 13.6078 | 12.6188 | 31.8631 | 43.3818 | 16.1958 | 13.7271 | 36.6314
RATS1 R2 | 132 | 37.9674 | 13.6078 | 12.6188 | 31.8631 | 43.3818 | 16.1958 | 13.7271 | 36.6314
RATS2A | 275 | 41.4625 | 14.7976 | 9.532 | 30.4589 | 44.3868 | 16.0365 | 18.2198 | 40.8988
RATS4 M1 | 400 | 106.3753 | 36.8355 | 23.6732 | 75.7664 | 106.5571 | 40.2574 | 25.5439 | 82.4764
RATS4 M2 | 400 | 106.3753 | 36.8355 | 23.6732 | 75.7664 | 106.5571 | 40.2574 | 25.5439 | 82.4764
RATS4 M3 | 400 | 106.3753 | 36.8355 | 23.6732 | 75.7664 | 106.5571 | 40.2574 | 25.5439 | 82.4764
RATS4 M4 | 400 | 106.3753 | 36.8355 | 23.6732 | 75.7664 | 106.5571 | 40.2574 | 25.5439 | 82.4764
RATS4 R1/2 | 400 | 106.3753 | 36.8355 | 23.6732 | 75.7664 | 106.5571 | 40.2574 | 25.5439 | 82.4764
RATS4 R3/4 | 400 | 106.3753 | 36.8355 | 23.6732 | 75.7664 | 106.5571 | 40.2574 | 25.5439 | 82.4764
RAYL4 M1 | 400 | 77.6456 | 28.0324 | 22.9818 | 62.6255 | 67.3556 | 26.238 | 18.2292 | 55.3354
RAYL4 M2 | 400 | 77.6456 | 28.0324 | 22.9818 | 62.6255 | 67.3556 | 26.238 | 18.2292 | 55.3354
RAYL4 R1 | 400 | 77.6456 | 28.0324 | 22.9818 | 62.6255 | 67.3556 | 26.238 | 18.2292 | 55.3354
RAYL4 R2 | 400 | 77.6456 | 28.0324 | 22.9818 | 62.6255 | 67.3556 | 26.238 | 18.2292 | 55.3354
REBR2 MC1 | 275 | 58.503 | 21.3973 | 18.8821 | 49.1424 | 57.9325 | 22.5827 | 16.0526 | 47.9894
REBR2 MC2 | 275 | 56.3952 | 20.6404 | 18.4202 | 47.6101 | 57.4198 | 22.4811 | 15.7452 | 47.5383
REBR2 MC3 | 275 | 56.3952 | 20.6404 | 18.4202 | 47.6101 | 57.4198 | 22.4811 | 15.7452 | 47.5383
REBR2 MC4 | 275 | 58.503 | 21.3973 | 18.8821 | 49.1424 | 57.9325 | 22.5827 | 16.0526 | 47.9894
RHIG4 M1 | 400 | 41.5683 | 14.9877 | 8.6342 | 29.8299 | 40.3392 | 15.4925 | 7.7914 | 29.7011
RHIG4 R1 | 400 | 41.5683 | 14.9877 | 8.6342 | 29.8299 | 40.3392 | 15.4925 | 7.7914 | 29.7011
ROCH2 MC1 | 275 | 63.1179 | 22.7648 | 9.2634 | 41.4576 | 63.5583 | 24.4657 | 9.1864 | 43.7861
ROCH2 MC2 | 275 | 63.1179 | 22.7648 | 9.2634 | 41.4576 | 63.5583 | 24.4657 | 9.1864 | 43.7861
ROCH2 MC3 | 275 | 63.1179 | 22.7648 | 9.2634 | 41.4576 | 63.5583 | 24.4657 | 9.1864 | 43.7861
ROCH2 MC4 | 275 | 63.1179 | 22.7648 | 9.2634 | 41.4576 | 63.5583 | 24.4657 | 9.1864 | 43.7861
ROCK1A | 132 | 47.3954 | 16.3142 | 16.3849 | 39.4567 | 50.239 | 18.1558 | 16.4242 | 42.1004
ROCK4 Term900 | 400 | 63.834 | 22.23 | 15.6314 | 47.0693 | 67.7383 | 25.1614 | 17.287 | 52.8707
RUGE4 M1 | 400 | 57.9426 | 21.3119 | 9.7179 | 39.8575 | 48.1024 | 19.2179 | 6.9609 | 34.1391
RUGE4 M2 | 400 | 57.9426 | 21.3119 | 9.7179 | 39.8575 | 48.1024 | 19.2179 | 6.9609 | 34.1391
RUGE4 R1 | 400 | 57.9426 | 21.3119 | 9.7179 | 39.8575 | 48.1024 | 19.2179 | 6.9609 | 34.1391
RUGE4 R2 | 400 | 57.9426 | 21.3119 | 9.7179 | 39.8575 | 48.1024 | 19.2179 | 6.9609 | 34.1391
RYEH4 M1 | 400 | 61.5408 | 21.8506 | 14.8905 | 45.792 | 66.4486 | 24.8275 | 17.0553 | 52.1668
RYEH4 R1 | 400 | 61.5408 | 21.8506 | 14.8905 | 45.792 | 66.4486 | 24.8275 | 17.0553 | 52.1668
RYHA4 MC1 | 400 | 40.0367 | 14.7971 | 8.6621 | 29.5883 | 27.6041 | 10.9501 | 4.0624 | 19.5482
RYHA4B_LOAD2 | 400 | 40.5097 | 14.9636 | 8.8017 | 29.9634 | 29.0401 | 11.5184 | 4.2431 | 20.5326
SAEN2 MC1 | 275 | 49.4437 | 18.0355 | 12.9233 | 38.4293 | 55.1986 | 20.7195 | 15.0549 | 44.3567
SAEN2 MC2 | 275 | 49.4437 | 18.0355 | 12.9233 | 38.4293 | 55.1986 | 20.7195 | 15.0549 | 44.3567
SAES2 M | 275 | 49.4734 | 18.0463 | 12.9301 | 38.4515 | 55.581 | 20.8288 | 15.4769 | 44.9333
SAES2 R | 275 | 49.4734 | 18.0463 | 12.9301 | 38.4515 | 55.581 | 20.8288 | 15.4769 | 44.9333
SALH2 MC1 | 275 | 73.7215 | 25.9207 | 18.3998 | 55.0572 | 74.6188 | 28.2007 | 15.9963 | 55.8782
SALH2 MC2 | 275 | 73.7215 | 25.9207 | 18.3998 | 55.0572 | 74.6188 | 28.2007 | 15.9963 | 55.8782
SEAB4 M1 | 400 | 42.6931 | 15.8178 | 12.4124 | 34.7822 | 49.1662 | 18.7186 | 15.1022 | 41.5742
SEAB4 M2 | 400 | 42.6931 | 15.8178 | 12.4124 | 34.7822 | 49.1662 | 18.7186 | 15.1022 | 41.5742
SEAB4 R1 | 400 | 42.6931 | 15.8178 | 12.4124 | 34.7822 | 49.1662 | 18.7186 | 15.1022 | 41.5742
SEAB4 R2 | 400 | 42.6931 | 15.8178 | 12.4124 | 34.7822 | 49.1662 | 18.7186 | 15.1022 | 41.5742
SELL4 M1 | 400 | 67.5582 | 24.3925 | 13.8544 | 48.3506 | 59.0652 | 22.5612 | 13.881 | 45.7874
SELL4 M2 | 400 | 67.5582 | 24.3925 | 13.8544 | 48.3506 | 59.0652 | 22.5612 | 13.881 | 45.7874
SELL4 R1 | 400 | 67.5582 | 24.3925 | 13.8544 | 48.3506 | 59.0652 | 22.5612 | 13.881 | 45.7874
SELL4 R2 | 400 | 67.5582 | 24.3925 | 13.8544 | 48.3506 | 59.0652 | 22.5612 | 13.881 | 45.7874
SELL4A | 400 | 67.5034 | 23.7067 | 6.3894 | 39.9158 | 59.0181 | 22.372 | 7.683 | 39.3218
SELL4B | 400 | 67.5033 | 23.7067 | 6.3894 | 39.9157 | 59.018 | 22.372 | 7.6829 | 39.3217
SELW4 M3 | 400 | 67.4392 | 24.3529 | 13.8236 | 48.2637 | 58.7875 | 22.4689 | 13.7263 | 45.5021
SELW4 M4 | 400 | 67.4392 | 24.3529 | 13.8236 | 48.2637 | 58.7875 | 22.4689 | 13.7263 | 45.5021
SELW4 R3 | 400 | 67.4392 | 24.3529 | 13.8236 | 48.2637 | 58.7875 | 22.4689 | 13.7263 | 45.5021
SELW4 R4 | 400 | 67.4392 | 24.3529 | 13.8236 | 48.2637 | 58.7875 | 22.4689 | 13.7263 | 45.5021
SETW4A | 400 | 67.4295 | 23.6835 | 6.3802 | 39.8738 | 58.9704 | 22.3567 | 7.6607 | 39.2779
SETW4B | 400 | 67.4294 | 23.6835 | 6.3802 | 39.8737 | 58.9703 | 22.3567 | 7.6607 | 39.2778
SHBA4 M1 | 400 | 64.6911 | 23.2026 | 22.4394 | 55.2529 | 68.3922 | 25.5749 | 23.398 | 59.5664
SHBA4 M2 | 400 | 64.6911 | 23.2026 | 22.4394 | 55.2529 | 68.3922 | 25.5749 | 23.398 | 59.5664
SHBA4 R1 | 400 | 64.6911 | 23.2026 | 22.4394 | 55.2529 | 68.3922 | 25.5749 | 23.398 | 59.5664
SHBA4 R2 | 400 | 64.6911 | 23.2026 | 22.4394 | 55.2529 | 68.3922 | 25.5749 | 23.398 | 59.5664
SHEC2 MC1 | 275 | 49.0563 | 18.2233 | 9.9991 | 35.7707 | 51.5967 | 21.0333 | 7.5024 | 37.248
SHEC2 MC2 | 275 | 49.0563 | 18.2233 | 9.9991 | 35.7707 | 51.5967 | 21.0333 | 7.5024 | 37.248
SHRE4B | 400 | 49.2466 | 18.0887 | 9.3022 | 34.8834 | 41.7339 | 16.4977 | 6.8386 | 30.1699
SING4 MC1 | 400 | 72.1553 | 25.1559 | 15.0656 | 50.6415 | 64.3717 | 24.8706 | 11.1381 | 46.3105
SING4 MC2 | 400 | 72.1553 | 25.1559 | 15.0656 | 50.6415 | 64.3717 | 24.8706 | 11.1381 | 46.3105
SIZE4 M1 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 M2 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 M3 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 M4 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 R1 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 R2 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 R3 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SIZE4 R4 | 400 | 60.2298 | 21.1109 | 16.4755 | 46.3309 | 68.317 | 25.0804 | 20.2895 | 55.7585
SJOW2 MC1 | 275 | 72.6746 | 25.6861 | 18.6604 | 54.986 | 83.1617 | 31.6789 | 22.0654 | 66.8661
SJOW2 MC2 | 275 | 72.6746 | 25.6861 | 18.6604 | 54.986 | 83.1617 | 31.6789 | 22.0654 | 66.8661
SJOW2 MC3 | 275 | 72.6746 | 25.6861 | 18.6604 | 54.986 | 83.1617 | 31.6789 | 22.0654 | 66.8661
SJOW2 MC4 | 275 | 72.6746 | 25.6861 | 18.6604 | 54.986 | 83.1617 | 31.6789 | 22.0654 | 66.8661
SJOW4 M1 | 400 | 87.576 | 29.6216 | 20.5133 | 62.4045 | 105.3762 | 38.7419 | 24.9552 | 79.7445
SJOW4 M2 | 400 | 87.576 | 29.6216 | 20.5133 | 62.4045 | 105.3762 | 38.7419 | 24.9552 | 79.7445
SJOW4 M3 | 400 | 87.576 | 29.6216 | 20.5133 | 62.4045 | 105.3762 | 38.7419 | 24.9552 | 79.7445
SJOW4 M4 | 400 | 87.576 | 29.6216 | 20.5133 | 62.4045 | 105.3762 | 38.7419 | 24.9552 | 79.7445
SJOW4 R1/2 | 400 | 87.576 | 29.6216 | 20.5133 | 62.4045 | 105.3762 | 38.7419 | 24.9552 | 79.7445
SJOW4 R3/4 | 400 | 87.576 | 29.6216 | 20.5133 | 62.4045 | 105.3762 | 38.7419 | 24.9552 | 79.7445
SKLG2 MC1 | 275 | 51.3132 | 19.0312 | 16.182 | 43.0962 | 52.2701 | 20.2707 | 15.3123 | 43.9794
SKLG2 MC2 | 275 | 51.3132 | 19.0312 | 16.182 | 43.0962 | 52.2701 | 20.2707 | 15.3123 | 43.9794
SKLG2 MC3 | 275 | 51.3132 | 19.0312 | 16.182 | 43.0962 | 52.2701 | 20.2707 | 15.3123 | 43.9794
SKLG2 MC4 | 275 | 51.3132 | 19.0312 | 16.182 | 43.0962 | 52.2701 | 20.2707 | 15.3123 | 43.9794
SMAN2 MC1 | 275 | 67.6477 | 24.9902 | 20.7129 | 56.0543 | 69.7754 | 27.0996 | 19.7276 | 58.0523
SMAN2 MC2 | 275 | 67.6477 | 24.9902 | 20.7129 | 56.0543 | 69.7754 | 27.0996 | 19.7276 | 58.0523
SMAN2 MC3 | 275 | 67.6477 | 24.9902 | 20.7129 | 56.0543 | 69.7754 | 27.0996 | 19.7276 | 58.0523
SMAN2 MC4 | 275 | 67.6477 | 24.9902 | 20.7129 | 56.0543 | 69.7754 | 27.0996 | 19.7276 | 58.0523
SPEN4 MC3 | 400 | 56.3162 | 20.1438 | 12.8774 | 41.3651 | 48.3218 | 18.6222 | 9.4355 | 35.7712
SPEN4 MC4 | 400 | 56.3162 | 20.1438 | 12.8774 | 41.3651 | 48.3218 | 18.6222 | 9.4355 | 35.7712
SPEN4 MC1 | 400 | 56.3502 | 20.1571 | 12.8853 | 41.3918 | 48.9496 | 18.841 | 9.6883 | 36.3335
SPEN4 MC2 | 400 | 56.3502 | 20.1571 | 12.8853 | 41.3918 | 48.9496 | 18.841 | 9.6883 | 36.3335
SPLN4 M1 | 400 | 59.2871 | 21.3171 | 14.1532 | 44.3002 | 50.9452 | 19.6112 | 11.8866 | 39.621
SPLN4 R1 | 400 | 59.2871 | 21.3171 | 14.1532 | 44.3002 | 50.9452 | 19.6112 | 11.8866 | 39.621
SSHI2 MC1 | 275 | 62.2057 | 22.6423 | 11.88 | 43.901 | 57.6419 | 22.6759 | 9.7022 | 41.7708
SSHI2 MC2 | 275 | 62.2057 | 22.6423 | 11.88 | 43.901 | 57.6419 | 22.6759 | 9.7022 | 41.7708
STAL2 M1 | 275 | 72.056 | 26.2018 | 14.9006 | 51.9555 | 71.1026 | 27.5161 | 14.1348 | 53.0485
STAL2 M2 | 275 | 72.056 | 26.2018 | 14.9006 | 51.9555 | 71.1026 | 27.5161 | 14.1348 | 53.0485
STAL2 R1 | 275 | 72.056 | 26.2018 | 14.9006 | 51.9555 | 71.1026 | 27.5161 | 14.1348 | 53.0485
STAL2 R2 | 275 | 72.056 | 26.2018 | 14.9006 | 51.9555 | 71.1026 | 27.5161 | 14.1348 | 53.0485
STAL4 MC1 | 400 | 34.2461 | 12.4677 | 8.8808 | 26.5128 | 31.7862 | 12.2237 | 7.9047 | 25.1917
STAL4 MC2 | 400 | 47.721 | 17.6269 | 9.4541 | 34.3822 | 38.5523 | 15.2033 | 6.4652 | 27.9658
STAY4 M1 | 400 | 80.3853 | 28.8783 | 16.5877 | 57.4278 | 68.8726 | 26.849 | 13.1142 | 51.0844
STAY4 M2 | 400 | 80.3853 | 28.8783 | 16.5877 | 57.4278 | 68.8726 | 26.849 | 13.1142 | 51.0844
STAY4 R1 | 400 | 80.3853 | 28.8783 | 16.5877 | 57.4278 | 68.8726 | 26.849 | 13.1142 | 51.0844
STAY4 R2 | 400 | 80.3853 | 28.8783 | 16.5877 | 57.4278 | 68.8726 | 26.849 | 13.1142 | 51.0844
STAY4A | 400 | 63.2881 | 22.8351 | 15.3279 | 47.6215 | 54.3575 | 20.9791 | 11.9081 | 41.577
STEN1 M1 | 132 | 49.6231 | 17.9192 | 17.956 | 43.2976 | 61.864 | 22.9431 | 21.8441 | 54.2905
STEN1 M2 | 132 | 49.6231 | 17.9192 | 17.956 | 43.2976 | 61.864 | 22.9431 | 21.8441 | 54.2905
STEN1 R1 | 132 | 49.6231 | 17.9192 | 17.956 | 43.2976 | 61.864 | 22.9431 | 21.8441 | 54.2905
STEN1 R2 | 132 | 49.6231 | 17.9192 | 17.956 | 43.2976 | 61.864 | 22.9431 | 21.8441 | 54.2905
STES1 M1 | 132 | 49.8459 | 17.7246 | 14.5432 | 39.6096 | 61.8882 | 22.809 | 17.1618 | 49.4186
STES1 M2 | 132 | 49.8459 | 17.7246 | 14.5432 | 39.6096 | 61.8882 | 22.809 | 17.1618 | 49.4186
STES1 R1 | 132 | 49.8459 | 17.7246 | 14.5432 | 39.6096 | 61.8882 | 22.809 | 17.1618 | 49.4186
STES1 R2 | 132 | 49.8459 | 17.7246 | 14.5432 | 39.6096 | 61.8882 | 22.809 | 17.1618 | 49.4186
STEW2 M1 | 275 | 72.0734 | 26.3648 | 22.6441 | 59.9295 | 74.9627 | 28.652 | 23.0852 | 63.6053
STEW2 M2 | 275 | 72.0734 | 26.3648 | 22.6441 | 59.9295 | 74.9627 | 28.652 | 23.0852 | 63.6053
STEW2 R1 | 275 | 72.0734 | 26.3648 | 22.6441 | 59.9295 | 74.9627 | 28.652 | 23.0852 | 63.6053
STEW2 R2 | 275 | 72.0734 | 26.3648 | 22.6441 | 59.9295 | 74.9627 | 28.652 | 23.0852 | 63.6053
STEW4 M1 | 400 | 65.7149 | 23.6936 | 20.9212 | 54.4289 | 58.9363 | 22.6823 | 17.4421 | 49.5197
STEW4 M2 | 400 | 65.7149 | 23.6936 | 20.9212 | 54.4289 | 58.9363 | 22.6823 | 17.4421 | 49.5197
STEW4 R1 | 400 | 65.7149 | 23.6936 | 20.9212 | 54.4289 | 58.9363 | 22.6823 | 17.4421 | 49.5197
STEW4 R2a | 400 | 65.7149 | 23.6936 | 20.9212 | 54.4289 | 58.9363 | 22.6823 | 17.4421 | 49.5197
STOB4 M1 | 400 | 58.0692 | 21.3703 | 11.0664 | 41.2885 | 48.9754 | 19.4739 | 7.8032 | 35.3434
STOB4 R1 | 400 | 58.0692 | 21.3703 | 11.0664 | 41.2885 | 48.9754 | 19.4739 | 7.8032 | 35.3434
STSB4 MC1 | 400 | 51.7999 | 18.7908 | 11.4987 | 38.0728 | 43.8278 | 17.091 | 7.7028 | 31.8731
STSB4 MC2 | 400 | 51.7999 | 18.7908 | 11.4987 | 38.0728 | 43.8278 | 17.091 | 7.7028 | 31.8731
STSB4A | 400 | 48.6812 | 17.3691 | 5.4703 | 30.034 | 40.2218 | 15.5525 | 3.1836 | 25.1782
SUND4 M1 | 400 | 90.2011 | 31.6687 | 19.9917 | 64.7781 | 82.0978 | 31.4024 | 16.5748 | 60.9845
SUND4 M2 | 400 | 74.4426 | 26.5572 | 16.1811 | 53.7386 | 67.5167 | 25.8631 | 13.8647 | 50.4406
SUND4 R1 | 400 | 90.2011 | 31.6687 | 19.9917 | 64.7781 | 82.0978 | 31.4024 | 16.5748 | 60.9845
SUND4 R2 | 400 | 74.4426 | 26.5572 | 16.1811 | 53.7386 | 67.5167 | 25.8631 | 13.8647 | 50.4406
SUTB4A | 400 | 65.213 | 23.4767 | 14.1223 | 47.3233 | 60.8816 | 23.378 | 13.8476 | 46.9091
SWAN2 MC3 | 275 | 23.4732 | 8.481 | 7.0838 | 19.0778 | 26.2747 | 9.7375 | 7.7671 | 21.5379
SWAN2 MC4 | 275 | 23.4732 | 8.481 | 7.0838 | 19.0778 | 26.2747 | 9.7375 | 7.7671 | 21.5379
SWAN4 M1 | 400 | 30.8803 | 11.2882 | 6.6058 | 22.5698 | 29.2966 | 11.1512 | 6.6226 | 22.3928
SWAN4 M2 | 400 | 30.8803 | 11.2882 | 6.6058 | 22.5698 | 29.2966 | 11.1512 | 6.6226 | 22.3928
SWAN4 M3 | 400 | 43.4704 | 15.5529 | 9.2844 | 31.2796 | 46.4559 | 17.5682 | 10.1915 | 35.0367
SWAN4 M4 | 400 | 43.4704 | 15.5529 | 9.2844 | 31.2796 | 46.4559 | 17.5682 | 10.1915 | 35.0367
SWAN4 R3 | 400 | 43.4704 | 15.5529 | 9.2844 | 31.2796 | 46.4559 | 17.5682 | 10.1915 | 35.0367
SWAN4 R4 | 400 | 43.4704 | 15.5529 | 9.2844 | 31.2796 | 46.4559 | 17.5682 | 10.1915 | 35.0367
TAUN4 M1 | 400 | 41.8034 | 15.2348 | 8.433 | 29.9782 | 39.1017 | 15.3216 | 6.4247 | 28.0927
TAUN4 M2 | 400 | 42.2506 | 15.3713 | 8.5458 | 30.284 | 40.256 | 15.7283 | 6.869 | 29.1122
TEMP2 MC1 | 275 | 53.6696 | 19.7254 | 11.5519 | 39.4478 | 58.0291 | 22.8042 | 10.7932 | 43.0431
TEMP2 MC2 | 275 | 53.6696 | 19.7254 | 11.5519 | 39.4478 | 58.0291 | 22.8042 | 10.7932 | 43.0431
TEMP2 MC3 | 275 | 53.8601 | 19.7806 | 11.6593 | 39.6334 | 58.7395 | 23.0655 | 10.9901 | 43.6096
THOM2 M1 | 275 | 60.7684 | 21.9379 | 16.9524 | 47.9773 | 64.9354 | 24.427 | 17.5667 | 52.1118
THOM2 R1 | 275 | 60.7684 | 21.9379 | 16.9524 | 47.9773 | 64.9354 | 24.427 | 17.5667 | 52.1118
THOM4 MC1 | 400 | 74.2004 | 26.1348 | 18.2521 | 55.2123 | 71.7513 | 27.1701 | 16.0684 | 54.4927
THOM4 MC2 | 400 | 74.2004 | 26.1348 | 18.2521 | 55.2123 | 71.7513 | 27.1701 | 16.0684 | 54.4927
THOM4 MC3 | 400 | 74.2004 | 26.1348 | 18.2521 | 55.2123 | 71.7513 | 27.1701 | 16.0684 | 54.4927
THOM4 MC4 | 400 | 74.2004 | 26.1348 | 18.2521 | 55.2123 | 71.7513 | 27.1701 | 16.0684 | 54.4927
THOM4 M5 | 400 | 73.1587 | 26.0686 | 16.0704 | 52.937 | 68.839 | 26.2678 | 14.3968 | 51.5451
THTO4 M1 | 400 | 77.0757 | 27.2068 | 19.4596 | 57.9359 | 66.7198 | 25.5754 | 13.2326 | 49.4017
THTO4 M2 | 400 | 60.5067 | 21.7169 | 14.7375 | 45.4498 | 52.2736 | 20.0587 | 10.5963 | 38.9635
THTO4 M3 | 400 | 60.5067 | 21.7169 | 14.7375 | 45.4498 | 52.2736 | 20.0587 | 10.5963 | 38.9635
THTO4 M4 | 400 | 77.0757 | 27.2068 | 19.4596 | 57.9359 | 66.7198 | 25.5754 | 13.2326 | 49.4017
THTO4 R1/2 | 400 | 59.2984 | 21.234 | 13.9944 | 44.0238 | 53.1785 | 20.2654 | 11.2224 | 39.8819
THTO4 R3/4 | 400 | 59.2984 | 21.234 | 13.9944 | 44.0238 | 53.1785 | 20.2654 | 11.2224 | 39.8819
THUR2 MC1 | 275 | 57.4638 | 21.4514 | 10.1679 | 40.5047 | 60.8211 | 23.9073 | 10.6455 | 44.4555
THUR2 MC2 | 275 | 57.4638 | 21.4514 | 10.1679 | 40.5047 | 60.8211 | 23.9073 | 10.6455 | 44.4555
THUR2 MC3 | 275 | 57.4638 | 21.4514 | 10.1679 | 40.5047 | 60.8211 | 23.9073 | 10.6455 | 44.4555
THUR2 MC4 | 275 | 57.4638 | 21.4514 | 10.1679 | 40.5047 | 60.8211 | 23.9073 | 10.6455 | 44.4555
TILB2 M1 | 275 | 63.5179 | 22.4349 | 17.7072 | 49.4348 | 68.4889 | 25.4872 | 18.6323 | 54.6767
TILB2 M2 | 275 | 63.5179 | 22.4349 | 17.7072 | 49.4348 | 68.4889 | 25.4872 | 18.6323 | 54.6767
TILB2 R1 | 275 | 63.5179 | 22.4349 | 17.7072 | 49.4348 | 68.4889 | 25.4872 | 18.6323 | 54.6767
TILB2 R2 | 275 | 63.5179 | 22.4349 | 17.7072 | 49.4348 | 68.4889 | 25.4872 | 18.6323 | 54.6767
TILB4 M2 | 400 | 95.8667 | 33.8453 | 28.7581 | 76.6226 | 95.0047 | 36.3006 | 26.7703 | 78.1071
TILB4 M3 | 400 | 95.8667 | 33.8453 | 28.7581 | 76.6226 | 95.0047 | 36.3006 | 26.7703 | 78.1071
TILB4 R2 | 400 | 95.8667 | 33.8453 | 28.7581 | 76.6226 | 95.0047 | 36.3006 | 26.7703 | 78.1071
TILB4 R3 | 400 | 95.8667 | 33.8453 | 28.7581 | 76.6226 | 95.0047 | 36.3006 | 26.7703 | 78.1071
TINP2 M1 | 275 | 52.6048 | 19.0674 | 6.5274 | 33.4928 | 53.3276 | 20.6126 | 5.4106 | 34.5611
TINP2 M2 | 275 | 52.6562 | 19.0701 | 6.5365 | 33.5057 | 54.0274 | 20.871 | 5.4759 | 34.992
TODP2 MC1 | 275 | 63.122 | 21.8485 | 16.3554 | 47.2539 | 59.5275 | 22.6163 | 12.2821 | 44.2663
TODP2 MC2 | 275 | 63.122 | 21.8485 | 16.3554 | 47.2539 | 59.5275 | 22.6163 | 12.2821 | 44.2663
TOTE2A | 275 | 64.762 | 23.0565 | 16.522 | 49.1288 | 69.8523 | 26.5527 | 15.5386 | 53.0898
TOTE2B | 275 | 66.396 | 23.6178 | 16.6527 | 50.0533 | 68.7247 | 26.0988 | 15.1923 | 52.1016
TOTT2 MC1 | 275 | 64.9516 | 23.8482 | 20.1106 | 53.837 | 68.0715 | 27.7319 | 18.0127 | 57.2316
TOTT2 MC2A | 275 | 65.5763 | 24.0669 | 20.277 | 54.3127 | 65.9699 | 27.3241 | 16.3396 | 54.9818
TOTT2 MC2B | 275 | 66.396 | 23.6178 | 16.6527 | 50.0533 | 68.7247 | 26.0988 | 15.1923 | 52.1016
TOTT2 MC3 | 275 | 65.5763 | 24.0669 | 20.277 | 54.3127 | 65.9699 | 27.3241 | 16.3396 | 54.9818
TOTT2 MC4A | 275 | 64.9516 | 23.8482 | 20.1106 | 53.837 | 68.0715 | 27.7319 | 18.0127 | 57.2316
TOTT2 MC4B | 275 | 64.762 | 23.0565 | 16.522 | 49.1288 | 69.8523 | 26.5527 | 15.5386 | 53.0898
TOTT2 MC5 | 275 | 66.396 | 23.6178 | 16.6527 | 50.0533 | 68.7247 | 26.0988 | 15.1923 | 52.1016
TOTT2 MC6 | 275 | 66.396 | 23.6178 | 16.6527 | 50.0533 | 68.7247 | 26.0988 | 15.1923 | 52.1016
TOTT2 MC7 | 275 | 64.762 | 23.0565 | 16.522 | 49.1288 | 69.8523 | 26.5527 | 15.5386 | 53.0898
TOTT2 MC8 | 275 | 64.762 | 23.0565 | 16.522 | 49.1288 | 69.8523 | 26.5527 | 15.5386 | 53.0898
TRAW2 M1 | 275 | 34.0185 | 12.3645 | 9.3659 | 26.8519 | 38.8455 | 14.603 | 9.9076 | 30.5594
TRAW2 M2 | 275 | 34.0185 | 12.3645 | 9.3659 | 26.8519 | 38.8455 | 14.603 | 9.9076 | 30.5594
TRAW2 R1 | 275 | 34.0185 | 12.3645 | 9.3659 | 26.8519 | 38.8455 | 14.603 | 9.9076 | 30.5594
TRAW2 R2 | 275 | 34.0185 | 12.3645 | 9.3659 | 26.8519 | 38.8455 | 14.603 | 9.9076 | 30.5594
TRAW4 MC1 | 400 | 41.1349 | 15.3616 | 11.723 | 33.4475 | 38.9184 | 15.3394 | 10.1128 | 31.8059
TRAW4 MC2 | 400 | 41.1349 | 15.3616 | 11.723 | 33.4475 | 38.9184 | 15.3394 | 10.1128 | 31.8059
TRAW4 MC3 | 400 | 41.1349 | 15.3616 | 11.723 | 33.4475 | 38.9184 | 15.3394 | 10.1128 | 31.8059
TRAW4 MC4 | 400 | 41.1349 | 15.3616 | 11.723 | 33.4475 | 38.9184 | 15.3394 | 10.1128 | 31.8059
TREM2 MC1 | 275 | 37.4604 | 13.3268 | 1.8427 | 20.6896 | 35.3483 | 13.8487 | 1.9099 | 21.4949
TREM2 MC2 | 275 | 37.4604 | 13.3268 | 1.8427 | 20.6896 | 35.3483 | 13.8487 | 1.9099 | 21.4949
TREU4A | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 59.961 | 23.0149 | 3.9859 | 36.5339
TREU4A_DEES1 | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 59.961 | 23.0149 | 3.9859 | 36.5339
TREU4A_LEGA1 | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 59.961 | 23.0149 | 3.9859 | 36.5339
TREU4A_TRAW1 | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 59.961 | 23.0149 | 3.9859 | 36.5339
TREU4B | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 60.0514 | 23.0479 | 3.9919 | 36.5866
TREU4B_DEES2 | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 60.0514 | 23.0479 | 3.9919 | 36.5866
TREU4B_LEGA2 | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 60.0514 | 23.0479 | 3.9919 | 36.5866
TREU4B_TRAW2 | 400 | 62.0145 | 21.4316 | 5.9531 | 36.262 | 60.0514 | 23.0479 | 3.9919 | 36.5866
TYNE2 MC1 | 275 | 58.3863 | 21.3871 | 10.8996 | 41.1455 | 54.0955 | 21.218 | 9.5086 | 39.5154
TYNE2 MC2 | 275 | 58.3863 | 21.3871 | 10.8996 | 41.1455 | 54.0955 | 21.218 | 9.5086 | 39.5154
TYNE2A | 275 | 58.0656 | 20.8736 | 4.1247 | 33.6445 | 51.2541 | 20.1669 | 2.9761 | 31.4964
UPPB2 MC1 | 275 | 33.7463 | 12.3983 | 7.9552 | 25.489 | 34.7655 | 13.3495 | 7.9459 | 26.8249
UPPB2 MC2 | 275 | 35.7443 | 13.066 | 8.2214 | 26.6995 | 36.1966 | 13.9061 | 7.916 | 27.5822
UPPB2 MC3 | 275 | 35.7443 | 13.066 | 8.2214 | 26.6995 | 36.1966 | 13.9061 | 7.916 | 27.5822
UPPB2 MC4 | 275 | 33.7463 | 12.3983 | 7.9552 | 25.489 | 34.7655 | 13.3495 | 7.9459 | 26.8249
USKM2 M1 | 275 | 52.3867 | 18.5544 | 10.2688 | 36.5087 | 58.7447 | 22.3009 | 11.7649 | 43.303
USKM2 M2 | 275 | 52.3867 | 18.5544 | 10.2688 | 36.5087 | 58.7447 | 22.3009 | 11.7649 | 43.303
USKM2 R1 | 275 | 52.3867 | 18.5544 | 10.2688 | 36.5087 | 58.7447 | 22.3009 | 11.7649 | 43.303
USKM2 R2 | 275 | 52.3867 | 18.5544 | 10.2688 | 36.5087 | 58.7447 | 22.3009 | 11.7649 | 43.303
USKM2A | 275 | 51.4822 | 17.6138 | 4.4408 | 29.3505 | 56.985 | 21.4096 | 4.9192 | 35.1969
WALH4 MC1 | 400 | 52.1188 | 18.9972 | 9.9503 | 36.8163 | 47.1586 | 18.3146 | 9.5987 | 35.4995
WALH4 MC2 | 400 | 52.1188 | 18.9972 | 9.9503 | 36.8163 | 47.1586 | 18.3146 | 9.5987 | 35.4995
WALH4 MC3 | 400 | 52.1188 | 18.9972 | 9.9503 | 36.8163 | 47.1586 | 18.3146 | 9.5987 | 35.4995
WALH4 MC4 | 400 | 52.1188 | 18.9972 | 9.9503 | 36.8163 | 47.1586 | 18.3146 | 9.5987 | 35.4995
WALP R4 | 132 | 49.4185 | 17.2392 | 15.5568 | 39.9368 | 61.7927 | 23.2234 | 18.0817 | 50.9245
WALP1 M4 | 132 | 49.4185 | 17.2392 | 15.5568 | 39.9368 | 61.7927 | 23.2234 | 18.0817 | 50.9245
WALP4 M1 | 400 | 75.8734 | 26.8272 | 17.993 | 55.9323 | 71.1287 | 27.0635 | 17.1143 | 55.3879
WALP4 M2 | 400 | 75.8734 | 26.8272 | 17.993 | 55.9323 | 71.1287 | 27.0635 | 17.1143 | 55.3879
WALP4 R1 | 400 | 75.8734 | 26.8272 | 17.993 | 55.9323 | 71.1287 | 27.0635 | 17.1143 | 55.3879
WALP4 R2 | 400 | 75.8734 | 26.8272 | 17.993 | 55.9323 | 71.1287 | 27.0635 | 17.1143 | 55.3879
WALPM3 | 132 | 49.4185 | 17.2392 | 15.5568 | 39.9368 | 61.7927 | 23.2234 | 18.0817 | 50.9245
WALPR3 | 132 | 49.4185 | 17.2392 | 15.5568 | 39.9368 | 61.7927 | 23.2234 | 18.0817 | 50.9245
WALX2 M1 | 275 | 76.0043 | 26.4645 | 14.7777 | 52.2042 | 79.5392 | 29.8042 | 14.8384 | 56.9878
WALX2 M2 | 275 | 76.5021 | 26.6168 | 14.7733 | 52.4151 | 83.3092 | 31.1579 | 15.5198 | 59.5838
WALX2 R1 | 275 | 76.0043 | 26.4645 | 14.7777 | 52.2042 | 79.5392 | 29.8042 | 14.8384 | 56.9878
WALX2 R2 | 275 | 76.5021 | 26.6168 | 14.7733 | 52.4151 | 83.3092 | 31.1579 | 15.5198 | 59.5838
WALX4A | 400 | 58.5199 | 20.2692 | 7.9053 | 36.5702 | 61.8047 | 22.9412 | 8.7145 | 41.1582
WALX4B | 400 | 58.7004 | 20.3364 | 7.928 | 36.688 | 57.487 | 21.4271 | 8.1653 | 38.4678
WARL2 MC1 | 275 | 58.4874 | 20.9809 | 13.5846 | 43.2561 | 56.2752 | 21.7243 | 10.6917 | 41.4145
WARL2 MC2 | 275 | 58.4874 | 20.9809 | 13.5846 | 43.2561 | 56.2752 | 21.7243 | 10.6917 | 41.4145
WARL2 MC3 | 275 | 58.4874 | 20.9809 | 13.5846 | 43.2561 | 56.2752 | 21.7243 | 10.6917 | 41.4145
WARL2 MC4 | 275 | 58.4874 | 20.9809 | 13.5846 | 43.2561 | 56.2752 | 21.7243 | 10.6917 | 41.4145
WASF2A | 275 | 51.0336 | 18.1639 | 5.5433 | 31.231 | 46.9708 | 18.1408 | 3.3461 | 29.0011
WASF2B | 275 | 54.51 | 19.2661 | 5.8882 | 33.1346 | 52.4304 | 20.2474 | 3.5224 | 32.1566
WBOL2 MC1 | 275 | 69.0922 | 24.8351 | 13.9943 | 49.1164 | 62.8298 | 24.6338 | 10.7615 | 45.5989
WBOL2 MC2 | 275 | 69.0922 | 24.8351 | 13.9943 | 49.1164 | 62.8298 | 24.6338 | 10.7615 | 45.5989
WBOL2 MC3 | 275 | 69.0922 | 24.8351 | 13.9943 | 49.1164 | 62.8298 | 24.6338 | 10.7615 | 45.5989
WBOL2 MC4 | 275 | 69.0922 | 24.8351 | 13.9943 | 49.1164 | 62.8298 | 24.6338 | 10.7615 | 45.5989
WBUR1 M1 | 132 | 20.5173 | 7.2953 | 6.4664 | 16.7835 | 24.1701 | 8.9184 | 7.7902 | 20.4027
WBUR1 M2 | 132 | 20.5173 | 7.2953 | 6.4664 | 16.7835 | 24.1701 | 8.9184 | 7.7902 | 20.4027
WBUR1 R1 | 132 | 20.5173 | 7.2953 | 6.4664 | 16.7835 | 24.1701 | 8.9184 | 7.7902 | 20.4027
WBUR1 R2 | 132 | 20.3128 | 7.2457 | 6.3178 | 16.5647 | 24.0464 | 8.8813 | 7.6637 | 20.2238
WBUR4 M1 | 400 | 82.3594 | 28.9329 | 22.1562 | 63.0735 | 73.8935 | 27.9211 | 18.6298 | 58.1163
WBUR4 M2 | 400 | 82.3594 | 28.9329 | 22.1562 | 63.0735 | 73.8935 | 27.9211 | 18.6298 | 58.1163
WBUR4 M3 | 400 | 82.3594 | 28.9329 | 22.1562 | 63.0735 | 73.8935 | 27.9211 | 18.6298 | 58.1163
WBUR4 M4 | 400 | 82.3594 | 28.9329 | 22.1562 | 63.0735 | 73.8935 | 27.9211 | 18.6298 | 58.1163
WBUR4 R1/2 | 400 | 85.1463 | 30.0973 | 20.5743 | 63.1384 | 72.9754 | 27.919 | 16.7405 | 56.2239
WBUR4 R3/4 | 400 | 85.1463 | 30.0973 | 20.5743 | 63.1384 | 72.9754 | 27.919 | 16.7405 | 56.2239
WHAM4 M1 | 400 | 89.5064 | 31.56 | 27.3248 | 71.9574 | 104.4123 | 39.6159 | 30.0403 | 86.0657
WHAM4 M2 | 400 | 89.5064 | 31.56 | 27.3248 | 71.9574 | 104.4123 | 39.6159 | 30.0403 | 86.0657
WHAM4 R1 | 400 | 89.5064 | 31.56 | 27.3248 | 71.9574 | 104.4123 | 39.6159 | 30.0403 | 86.0657
WHAM4 R2 | 400 | 89.5064 | 31.56 | 27.3248 | 71.9574 | 104.4123 | 39.6159 | 30.0403 | 86.0657
WHAM4A | 400 | 76.3353 | 25.2498 | 9.4778 | 45.1864 | 83.3986 | 31.7619 | 11.9269 | 56.8451
WHAM4B | 400 | 76.3791 | 25.2622 | 9.4786 | 45.2047 | 83.464 | 31.7869 | 11.9272 | 56.8807
WHGA2 MC1 | 275 | 62.1552 | 22.6193 | 13.8561 | 45.8446 | 61.947 | 24.0535 | 11.7661 | 45.7829
WHGA2 MC2 | 275 | 62.1552 | 22.6193 | 13.8561 | 45.8446 | 61.947 | 24.0535 | 11.7661 | 45.7829
WHGA2 MC3 | 275 | 62.1552 | 22.6193 | 13.8561 | 45.8446 | 61.947 | 24.0535 | 11.7661 | 45.7829
WHGA2 MC4 | 275 | 62.1552 | 22.6193 | 13.8561 | 45.8446 | 61.947 | 24.0535 | 11.7661 | 45.7829
WHSO2 M1 | 275 | 48.5039 | 17.3501 | 8.9192 | 33.456 | 54.0159 | 20.6121 | 10.3116 | 39.4615
WHSO2 M2 | 275 | 48.5039 | 17.3501 | 8.9192 | 33.456 | 54.0159 | 20.6121 | 10.3116 | 39.4615
WHSO2 R1 | 275 | 52.3239 | 18.5447 | 10.9874 | 37.2135 | 59.2552 | 22.3823 | 12.8983 | 44.5516
WHSO2 R2 | 275 | 52.3239 | 18.5447 | 10.9874 | 37.2135 | 59.2552 | 22.3823 | 12.8983 | 44.5516
WIBA2 MC1 | 275 | 53.5757 | 19.7 | 11.5157 | 39.3757 | 58.8987 | 23.3448 | 10.1483 | 43.1628
WIBA2 MC1 | 275 | 53.5757 | 19.7 | 11.5157 | 39.3757 | 58.8987 | 23.3448 | 10.1483 | 43.1628
WIBA2 MC2 | 275 | 53.5757 | 19.7 | 11.5157 | 39.3757 | 58.8987 | 23.3448 | 10.1483 | 43.1628
WIBA2 MC2 | 275 | 53.5757 | 19.7 | 11.5157 | 39.3757 | 58.8987 | 23.3448 | 10.1483 | 43.1628
WILE4 M1 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 M1 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 M2 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 M2 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 R1 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 R1 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 R2 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILE4 R2 | 400 | 88.7711 | 32.4212 | 24.8873 | 70.7377 | 81.5296 | 31.9917 | 21.5929 | 66.8361
WILL1 M2 | 132 | 48.1278 | 16.9683 | 15.2786 | 39.2754 | 55.9529 | 21.1296 | 17.8574 | 47.7391
WILL1 R1 | 132 | 34.6833 | 12.8544 | 10.6785 | 28.8573 | 38.9857 | 14.9759 | 12.3539 | 33.533
WILL1 R2 | 132 | 48.1278 | 16.9683 | 15.2786 | 39.2754 | 55.9529 | 21.1296 | 17.8574 | 47.7391
WILL2 M2 | 275 | 23.3275 | 8.3107 | 8.5697 | 20.3228 | 25.1933 | 9.1825 | 9.0514 | 22.0374
WILL2 M2 | 275 | 23.3275 | 8.3107 | 8.5697 | 20.3228 | 25.1933 | 9.1825 | 9.0514 | 22.0374
WILT2A | 275 | 52.3858 | 18.3823 | 9.795 | 35.7915 | 55.8577 | 20.6184 | 9.248 | 38.4069
WILT2A | 275 | 52.3858 | 18.3823 | 9.795 | 35.7915 | 55.8577 | 20.6184 | 9.248 | 38.4069
WILT2B | 275 | 52.3868 | 18.3826 | 9.795 | 35.7919 | 55.8591 | 20.619 | 9.2479 | 38.4075
WILT2B | 275 | 52.3868 | 18.3826 | 9.795 | 35.7919 | 55.8591 | 20.619 | 9.2479 | 38.4075
WILT2C | 275 | 52.6917 | 18.4747 | 9.9475 | 36.0747 | 56.7458 | 20.8878 | 9.9101 | 39.4499
WILT2C | 275 | 52.6917 | 18.4747 | 9.9475 | 36.0747 | 56.7458 | 20.8878 | 9.9101 | 39.4499
WILT2D | 275 | 52.6911 | 18.4745 | 9.9474 | 36.0744 | 56.7434 | 20.8871 | 9.9086 | 39.4474
WILT2D | 275 | 52.6911 | 18.4745 | 9.9474 | 36.0744 | 56.7434 | 20.8871 | 9.9086 | 39.4474
WIMB2 MC1 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC1 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC2 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC2 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC3 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC3 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC4 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2 MC4 | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2A | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB2A | 275 | 70.089 | 24.5726 | 17.7378 | 52.4887 | 81.1891 | 30.7987 | 20.1514 | 63.7073
WIMB4 MB2 | 400 | 74.8664 | 25.6824 | 17.8216 | 54.142 | 88.8192 | 33.5271 | 17.659 | 65.0736
WIMB4 MB2 | 400 | 74.8664 | 25.6824 | 17.8216 | 54.142 | 88.8192 | 33.5271 | 17.659 | 65.0736
WIMB4 RB2 | 400 | 74.8664 | 25.6824 | 17.8216 | 54.142 | 88.8192 | 33.5271 | 17.659 | 65.0736
WIMB4 RB2 | 400 | 74.8664 | 25.6824 | 17.8216 | 54.142 | 88.8192 | 33.5271 | 17.659 | 65.0736
WISD2 M1 | 275 | 61.4522 | 21.3992 | 19.0996 | 49.3626 | 72.8367 | 26.8566 | 22.1005 | 60.0815
WISD2 M2 | 275 | 61.4522 | 21.3992 | 19.0996 | 49.3626 | 72.8367 | 26.8566 | 22.1005 | 60.0815
WISD2 R1 | 275 | 61.4522 | 21.3992 | 19.0996 | 49.3626 | 72.8367 | 26.8566 | 22.1005 | 60.0815
WISD2 R2 | 275 | 61.4522 | 21.3992 | 19.0996 | 49.3626 | 72.8367 | 26.8566 | 22.1005 | 60.0815
WISD2A | 275 | 53.8271 | 18.688 | 10.5993 | 37.0282 | 60.1309 | 22.8619 | 12.3154 | 44.647
WISD6 M1 | 66 | 42.719 | 15.0196 | 15.2665 | 36.5075 | 30.5396 | 11.4707 | 10.1175 | 26.3396
WISD6 M2 | 66 | 42.719 | 15.0196 | 15.2665 | 36.5075 | 30.5396 | 11.4707 | 10.1175 | 26.3396
WISD6 R1 | 66 | 42.719 | 15.0196 | 15.2665 | 36.5075 | 30.5396 | 11.4707 | 10.1175 | 26.3396
WISD6 R2 | 66 | 42.719 | 15.0196 | 15.2665 | 36.5075 | 30.5396 | 11.4707 | 10.1175 | 26.3396
WMEL2 MC1 | 275 | 67.5284 | 24.5895 | 13.3029 | 48.0776 | 68.2859 | 26.6848 | 11.7109 | 49.4489
WMEL2 MC2 | 275 | 67.5284 | 24.5895 | 13.3029 | 48.0776 | 68.2859 | 26.6848 | 11.7109 | 49.4489
WMEL2 MC3 | 275 | 67.5284 | 24.5895 | 13.3029 | 48.0776 | 68.2859 | 26.6848 | 11.7109 | 49.4489
WMEL2 MC4 | 275 | 67.5284 | 24.5895 | 13.3029 | 48.0776 | 68.2859 | 26.6848 | 11.7109 | 49.4489
WTHU4A | 400 | 71.8133 | 24.2105 | 6.2238 | 40.4626 | 63.4988 | 24.4394 | 4.2222 | 38.7846
WTHU4B | 400 | 71.8133 | 24.2105 | 6.2238 | 40.4626 | 64.6819 | 24.8719 | 4.3008 | 39.4749
WWEY2 M1 | 275 | 64.3982 | 23.1262 | 15.936 | 48.6414 | 65.4667 | 24.8665 | 15.5003 | 50.6669
WWEY2 M2 | 275 | 64.3982 | 23.1262 | 15.936 | 48.6414 | 65.4667 | 24.8665 | 15.5003 | 50.6669
WWEY2 R1 | 275 | 65.2145 | 23.5433 | 14.7934 | 48.0887 | 67.3797 | 25.6887 | 15.3579 | 51.6872
WWEY2 R2 | 275 | 65.2145 | 23.5433 | 14.7934 | 48.0887 | 67.3797 | 25.6887 | 15.3579 | 51.6872
WWEY4A | 400 | 45.3151 | 16.1351 | 5.7177 | 28.5362 | 42.0959 | 16.0098 | 5.7733 | 28.4146
WWEY4B | 400 | 45.8449 | 16.3001 | 5.9229 | 28.9747 | 42.1249 | 16.0717 | 5.9816 | 28.7105
WYLF1 M1 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 M1 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 M2 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 M2 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 R1 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 R1 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 R2 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF1 R2 | 132 | 19.2392 | 6.0178 | 6.6678 | 15.1783 | 21.5415 | 7.4873 | 6.9775 | 17.5661
WYLF4 M1 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 M1 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 M2 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 M2 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 R1 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 R1 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 R2 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYLF4 R2 | 400 | 32.2952 | 11.7872 | 6.7345 | 23.4041 | 29.1955 | 11.3671 | 5.3253 | 21.4008
WYMO4 M1 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 M1 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 M2 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 M2 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 R1 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 R1 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 R2 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024
WYMO4 R2 | 400 | 87.4882 | 30.73 | 19.7621 | 63.2209 | 81.6102 | 31.0804 | 16.8481 | 60.8024