## Menu
Electricity Ten Year Statement 2019
Appendix D - Fault Levels at Peak
Table | Title
D1.1 | SHE Transmission Fault Levels (kA), Winter 2019/20
D1.2 | SHE Transmission Fault Levels (kA), Winter 2020/21
D1.3 | SHE Transmission Fault Levels (kA), Winter 2021/22
D1.4 | SHE Transmission Fault Levels (kA), Winter 2022/23
D1.5 | SHE Transmission Fault Levels (kA), Winter 2023/24
D1.6 | SHE Transmission Fault Levels (kA), Winter 2025/26
D1.7 | SHE Transmission Fault Levels (kA), Winter 2028/29
D2.1 | SPT Fault Levels (kA), Winter 2019/20
D2.2 | SPT Fault Levels (kA), Winter 2020/21
D2.3 | SPT Fault Levels (kA), Winter 2021/22
D2.4 | SPT Fault Levels (kA), Winter 2022/23
D2.5 | SPT Fault Levels (kA), Winter 2023/24
D2.6 | SPT Fault Levels (kA), Winter 2025/26
D2.7 | SPT Fault Levels (kA), Winter 2028/29
D3.1 | NGET Fault Levels (kA), Winter 2019/20
D3.2 | NGET Fault Levels (kA), Winter 2020/21
D3.3 | NGET Fault Levels (kA), Winter 2021/22
D3.4 | NGET Fault Levels (kA), Winter 2022/23
D3.5 | NGET Fault Levels (kA), Winter 2023/24
D3.6 | NGET Fault Levels (kA), Winter 2025/26
D3.7 | NGET Fault Levels (kA), Winter 2028/29

## D1.1
ETYS 19 Yr 1 - SHE Transmission Fault Levels (kA), Winter 2019/20
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 27.64 | 10.63 | 6.57 | 21.61 | 27.25 | 10.53 | 6.48 | 21.38 | Back To Menu
BLACKHILLOCK | 400 | 34.37 | 13.15 | 9.21 | 27.81 | 34.48 | 13.24 | 8.92 | 27.64
FORT AUGUSTUS | 400 | 24.6 | 9.45 | 5.8 | 19.17 | 24.39 | 9.41 | 5.8 | 19.11
MELGARVE | 400 | 22.61 | 8.67 | 5.31 | 17.58 | 22.23 | 8.59 | 5.11 | 17.26
BEAULY | 275 | 55.93 | 22.12 | 11.05 | 42.33 | 55.99 | 22.29 | 10.71 | 42.23
BERRY BURN | 275 | 32.57 | 13.32 | 4.09 | 22.93 | 25.12 | 10.42 | 3.26 | 18
BLACKHILLOCK I | 275 | 58.56 | 23.22 | 12.21 | 45.05 | 59.51 | 23.66 | 12.27 | 45.72
BLACKHILLOCK II | 275 | 33.28 | 12.85 | 8.73 | 26.9 | 35.4 | 13.81 | 8.17 | 27.71
BRACO WEST | 275 | 33.65 | 13.24 | 6.08 | 24.81 | 27.77 | 11.05 | 5.11 | 20.75
CAIRNFORD | 275 | 47.16 | 19.03 | 7.58 | 34.49 | 41.67 | 17.09 | 5.84 | 30.01
CONNAGILL | 275 | 20.96 | 8.28 | 4.61 | 16.32 | 21.36 | 8.51 | 4.24 | 16.27
DALLAS | 275 | 33.95 | 13.86 | 4.41 | 24.01 | 26.65 | 11.03 | 3.55 | 19.15
DOUNREAY | 275 | 22.95 | 9.04 | 5.55 | 18.33 | 25.1 | 9.87 | 5.95 | 19.91
FARIGAIG I | 275 | 41.73 | 16.77 | 7.11 | 30.82 | 32.29 | 13.29 | 4.83 | 23.63
FARIGAIG II | 275 | 41.8 | 16.79 | 7.16 | 30.91 | 32.35 | 13.31 | 4.88 | 23.71
FASNAKYLE | 275 | 36.18 | 14.15 | 7.31 | 27.33 | 31.81 | 12.63 | 6 | 23.86
FETTERESSO | 275 | 44.05 | 17.84 | 6.14 | 31.38 | 33.63 | 13.84 | 4.64 | 24.21
FORT AUGUSTUS | 275 | 31.37 | 12.22 | 6.52 | 23.81 | 28.6 | 11.22 | 6.14 | 22
FOYERS | 275 | 41.48 | 16.61 | 7.56 | 31.05 | 28.08 | 11.72 | 3.56 | 20.13
FYRISH | 275 | 29.59 | 11.81 | 5 | 21.7 | 26.79 | 10.8 | 4.82 | 20.09
GORDONBUSH | 275 | 20.8 | 8.41 | 3.26 | 15.16 | 19.09 | 7.77 | 3.22 | 14.21
KEITH | 275 | 55.54 | 22.2 | 10.63 | 42.03 | 56.62 | 22.74 | 10.47 | 42.63
KINTORE | 275 | 66.16 | 26.35 | 12.38 | 49.64 | 56.87 | 23.01 | 9.61 | 42.16
KNOCKNAGAEL | 275 | 55.8 | 22.22 | 10.44 | 41.86 | 51.21 | 20.64 | 9.27 | 38.45
LOCH BUIDHE | 275 | 29.91 | 11.96 | 5.15 | 22.06 | 27.45 | 11.08 | 4.97 | 20.64
PERSLEY | 275 | 39.34 | 15.82 | 6.28 | 28.65 | 32.38 | 13.11 | 5.58 | 24.11
PETERHEAD | 275 | 65.24 | 25.15 | 18.47 | 54.04 | 44.43 | 17.72 | 9.28 | 34.35
SPITTAL | 275 | 22.04 | 8.66 | 5.76 | 18 | 24.8 | 9.68 | 6.54 | 20.23
STRATHBRORA | 275 | 22.72 | 9.17 | 3.6 | 16.57 | 20.91 | 8.49 | 3.63 | 15.63
TEALING | 275 | 48.95 | 19.87 | 6.67 | 34.76 | 40.95 | 16.85 | 5.59 | 29.43
THURSO SOUTH | 275 | 21.1 | 8.29 | 5.27 | 17 | 22.83 | 8.96 | 5.54 | 18.21
TOMATIN | 275 | 29.35 | 11.66 | 5.18 | 21.67 | 25.08 | 10.09 | 4.34 | 18.62
TUMMEL | 275 | 26.35 | 10.33 | 5.15 | 19.76 | 22.38 | 8.93 | 4.33 | 16.95
ABERDEEN BAY | 132 | 19.39 | 8.11 | 1.72 | 13.18 | 17.4 | 7.33 | 1.37 | 11.74
ABERNETHY | 132 | 15.33 | 7.6 | 0.21 | 10.96 | 15.58 | 7.39 | 0.5 | 10.95
A-CHRUACH | 132 | 15.24 | 7.84 | 0.35 | 11.44 | 15.12 | 7.24 | 0.73 | 10.96
AIGAS | 132 | 34.27 | 16.07 | 0.41 | 23.15 | 30.98 | 14.71 | 0.47 | 21.27
ALNESS | 132 | 34.26 | 13.32 | 4.77 | 23.61 | 37.61 | 14.78 | 4.78 | 25.68
AN SUIDHE | 132 | 17.89 | 9.37 | 0.09 | 13.34 | 16.61 | 8.11 | 0.33 | 11.8
ARBROATH | 132 | 13.43 | 6.31 | 0.38 | 9.3 | 12.47 | 5.68 | 0.69 | 8.72
ARDKINGLAS | 132 | 28.57 | 13.82 | 0.25 | 19.8 | 24.46 | 11.56 | 0.6 | 16.95
ARDMORE | 132 | 5.78 | 2.56 | 0.91 | 4.53 | 6.73 | 2.93 | 1.08 | 5.23
BEAULY | 132 | 57.09 | 24.06 | 5.79 | 39.81 | 63.69 | 26.54 | 7.15 | 44.69
BEINNEUN | 132 | 19.62 | 9.28 | 0.86 | 13.99 | 20.3 | 9.28 | 1.43 | 14.55
BHLARAIDH | 132 | 20.44 | 9.45 | 1.15 | 14.52 | 20.76 | 9.48 | 1.77 | 15.18
BLACKHILLOCK | 132 | 38.31 | 14.41 | 8.47 | 28.85 | 41.92 | 15.9 | 8.42 | 30.91
BOAT OF GARTEN | 132 | 14.88 | 6.33 | 0.72 | 9.68 | 14.52 | 6.12 | 1.02 | 9.68
BRECHIN | 132 | 12.85 | 6.4 | 0.16 | 9.21 | 12.96 | 6.11 | 0.26 | 8.91
BRIDGE OF DUN | 132 | 10.7 | 5.42 | 0.12 | 7.79 | 11.28 | 5.37 | 0.29 | 7.88
BROADFORD | 132 | 6.05 | 3.07 | 0.07 | 4.41 | 6.17 | 2.95 | 0.25 | 4.42
BRORA | 132 | 12.58 | 6.21 | 0.04 | 8.82 | 12.19 | 5.8 | 0.23 | 8.44
BURGHMUIR | 132 | 12.35 | 6.28 | 0.05 | 8.92 | 13.62 | 6.53 | 0.23 | 9.46
CARRADALE | 132 | 17.53 | 7.25 | 1.82 | 12.07 | 18.68 | 7.62 | 2.24 | 13.02
CASSLEY | 132 | 7.28 | 3.61 | 0.21 | 5.32 | 6.84 | 3.27 | 0.26 | 4.88
CEANNACROC | 132 | 18.67 | 8.9 | 0.71 | 13.3 | 19.05 | 8.79 | 1.15 | 13.57
CHARLESTON | 132 | 39.95 | 16.92 | 3.75 | 27.68 | 43.72 | 18.63 | 4.23 | 30.58
CLACHAN | 132 | 27.81 | 13.4 | 0.51 | 19.46 | 24.24 | 11.48 | 0.8 | 17.04
CLAYHILLS | 132 | 39.83 | 16.76 | 3.11 | 26.81 | 46.16 | 19.94 | 2.86 | 31.06
CLUNIE | 132 | 20.82 | 9.63 | 0.41 | 14.03 | 19.56 | 8.88 | 0.77 | 13.33
CONNAGILL | 132 | 17.05 | 6.4 | 4.05 | 13.11 | 19.59 | 7.41 | 4.1 | 14.58
CORRIEGARTH | 132 | 11.43 | 4.53 | 1.54 | 7.94 | 11.88 | 4.68 | 1.83 | 8.45
CORRIEMOILLIE | 132 | 29.45 | 12.01 | 3.13 | 20.11 | 30.88 | 12.59 | 3.41 | 21.22
COUPAR ANGUS | 132 | 22.34 | 9.79 | 1.03 | 14.87 | 21.17 | 9.02 | 1.72 | 14.49
CRAIGIEBUCKLER | 132 | 44 | 18.17 | 4.14 | 29.83 | 51.98 | 21.77 | 4.02 | 34.8
CROSSAIG | 132 | 26.03 | 10.93 | 2.92 | 18.38 | 30.38 | 12.64 | 3.38 | 21.25
CULLIGRAN | 132 | 18.01 | 8.91 | 0.2 | 12.8 | 16.39 | 7.86 | 0.35 | 11.47
DEANIE | 132 | 12.55 | 6.34 | 0.1 | 9.06 | 11.69 | 5.63 | 0.21 | 8.17
DORENELL | 132 | 15.34 | 6.38 | 1.35 | 10.38 | 16.22 | 6.59 | 1.91 | 11.23
DOUNREAY | 132 | 21.08 | 7.98 | 4.72 | 16 | 26.88 | 10.22 | 5.64 | 20.09
DUDHOPE | 132 | 36.26 | 15.75 | 2.32 | 24.59 | 38.48 | 17.21 | 1.98 | 26.32
DUNBEATH | 132 | 12.2 | 5.84 | 0.12 | 8.38 | 11.25 | 5.31 | 0.28 | 7.8
DUNMAGLASS | 132 | 13.5 | 5.24 | 2.19 | 9.61 | 14.21 | 5.51 | 2.48 | 10.28
DUNOON | 132 | 9.67 | 5.03 | 0.09 | 7.2 | 9.31 | 4.55 | 0.16 | 6.6
DUNVEGAN | 132 | 6.52 | 2.88 | 0.73 | 4.8 | 7.95 | 3.46 | 0.96 | 5.86
DYCE | 132 | 24.83 | 10.54 | 1.92 | 16.83 | 22.34 | 9.52 | 1.7 | 15.17
EDINBANE | 132 | 6.67 | 2.98 | 0.66 | 4.87 | 8.03 | 3.52 | 0.89 | 5.87
ELGIN | 132 | 13.66 | 6.68 | 0.23 | 9.68 | 12.96 | 6.13 | 0.56 | 9.22
ERROCHTY | 132 | 44.49 | 18.39 | 6.41 | 32.42 | 45.17 | 18.94 | 5.34 | 32.13
FARIGAIG I | 132 | 14.5 | 5.56 | 2.36 | 10.23 | 15.71 | 6.02 | 2.62 | 11.13
FARIGAIG II | 132 | 15.17 | 5.79 | 2.75 | 10.93 | 16.54 | 6.3 | 3.01 | 11.93
FARR | 132 | 22.29 | 9.74 | 0.65 | 14.42 | 20.96 | 9.22 | 0.97 | 14.01
FERNOCH | 132 | 13.07 | 6.6 | 1.37 | 10.71 | 14.56 | 6.95 | 1.67 | 11.5
FETTERESSO | 132 | 22.52 | 8.67 | 3.42 | 15.68 | 24.92 | 9.59 | 3.84 | 17.4
FIDDES | 132 | 14.57 | 7.15 | 0.7 | 10.81 | 14.99 | 6.89 | 1.12 | 10.87
FINLARIG | 132 | 21.42 | 10.26 | 0.66 | 15.17 | 21.74 | 10.09 | 0.88 | 15.16
FORT AUGUSTUS | 132 | 54.32 | 20.99 | 9.78 | 39.46 | 63.02 | 24.55 | 10.44 | 45.15
FORT WILLIAM | 132 | 10 | 4.71 | 1.32 | 7.98 | 10.42 | 4.74 | 1.5 | 8.2
FRASERBURGH | 132 | 12.38 | 5.69 | 0.38 | 8.42 | 12.36 | 5.58 | 0.68 | 8.57
FYRISH | 132 | 36.89 | 14.09 | 6.7 | 26.63 | 40.66 | 15.55 | 7.52 | 29.5
GLENDOE | 132 | 42.28 | 17.55 | 2.9 | 27.73 | 46.29 | 19.76 | 2.97 | 30.91
GLENFARCLAS | 132 | 7.23 | 3.4 | 0.21 | 5.02 | 7.12 | 3.22 | 0.38 | 4.93
GLENMORISTON | 132 | 22.61 | 10.53 | 1.2 | 16.09 | 22.63 | 10.32 | 1.74 | 16.33
GRIFFIN | 132 | 16.63 | 8.03 | 0.5 | 11.86 | 16.64 | 7.74 | 1.05 | 11.99
GRUDIE BRIDGE | 132 | 22.98 | 9.62 | 1.67 | 15.27 | 23.45 | 9.79 | 2.03 | 15.87
INVERARAY | 132 | 34.65 | 16.27 | 0.99 | 24 | 31.3 | 14.53 | 0.8 | 21.36
INVERARNAN | 132 | 52.39 | 22.26 | 5.04 | 36.52 | 54.61 | 23 | 5.11 | 37.64
INVERGARRY | 132 | 20.22 | 9.72 | 0.22 | 13.97 | 18.88 | 8.95 | 0.36 | 13.02
INVERNESS | 132 | 47.95 | 20.07 | 4.25 | 32.64 | 52.6 | 21.95 | 4.84 | 35.87
KEITH | 132 | 34.11 | 13.65 | 6.85 | 26.15 | 43.04 | 17.69 | 7.91 | 32.93
KILLIN | 132 | 24.52 | 11.58 | 0.99 | 17.37 | 26.23 | 11.91 | 1.46 | 18.31
KILMORACK | 132 | 46.91 | 20.74 | 2 | 31.33 | 47.52 | 21.03 | 1.94 | 31.68
KINLOCHLEVEN | 132 | 6.67 | 3.15 | 0.64 | 5.09 | 6.94 | 3.14 | 0.77 | 5.21
KINTORE | 132 | 47.76 | 19.04 | 7.81 | 34.73 | 55.27 | 22.12 | 8.26 | 39.54
KNOCKNAGAEL | 132 | 53.12 | 21.87 | 6.47 | 37.4 | 58.03 | 23.63 | 7.61 | 41.02
LAIRG | 132 | 15.91 | 7.49 | 0.47 | 11.07 | 15.47 | 7.12 | 0.82 | 10.89
LOCH BUIDHE | 132 | 30.98 | 12.88 | 4.81 | 23.03 | 35.82 | 14.81 | 5.29 | 26.22
LOCHAY | 132 | 21.08 | 10.11 | 0.63 | 14.93 | 21.59 | 10.02 | 0.85 | 15.02
LUICHART | 132 | 29.42 | 12.08 | 2.68 | 19.77 | 29.1 | 11.95 | 2.73 | 19.63
LUNANHEAD | 132 | 17 | 7.36 | 0.92 | 11.33 | 15.95 | 6.8 | 1.44 | 11.06
LYNDHURST | 132 | 32.07 | 14.27 | 1.32 | 21.5 | 32.8 | 14.66 | 1.55 | 22.29
MACDUFF | 132 | 9.53 | 4.44 | 0.69 | 6.98 | 9.65 | 4.37 | 0.87 | 7.04
MELGARVE | 132 | 37.37 | 14.06 | 7.95 | 27.83 | 44.25 | 16.78 | 8.36 | 32.1
MILLENNIUM | 132 | 22.1 | 10.37 | 0.72 | 15.39 | 22.53 | 10.33 | 1.1 | 15.71
MILTON OF CRAIGIE | 132 | 38.64 | 16.41 | 3.78 | 26.98 | 41.57 | 18 | 3.53 | 28.98
MOSSFORD | 132 | 26.14 | 10.83 | 2.2 | 17.52 | 27.23 | 11.25 | 2.54 | 18.45
MYBSTER I | 132 | 18.9 | 8.03 | 1.69 | 13.05 | 19.97 | 8.64 | 1.07 | 13.28
MYBSTER II | 132 | 19.76 | 7.49 | 4.45 | 15.04 | 22.45 | 8.5 | 5.07 | 17.1
NAIRN | 132 | 12.53 | 6.29 | 0.14 | 9.03 | 11.59 | 5.56 | 0.38 | 8.24
NANT | 132 | 11.67 | 6.14 | 0.26 | 8.95 | 10.73 | 5.29 | 0.39 | 7.88
ORRIN | 132 | 32.24 | 13.33 | 2.78 | 21.64 | 32.14 | 13.26 | 2.9 | 21.66
PERSLEY | 132 | 42.8 | 17.67 | 4.88 | 29.87 | 52.03 | 21.55 | 5.62 | 36.1
PETERHEAD | 132 | 33.67 | 12.76 | 7.94 | 25.98 | 40.04 | 15.37 | 7.81 | 29.54
PETERHEAD GRANGE | 132 | 22.68 | 9.39 | 1.54 | 14.82 | 23.54 | 9.88 | 1.71 | 15.68
PORT ANN | 132 | 12.15 | 6.29 | 0.3 | 9.2 | 11.35 | 5.54 | 0.39 | 8.23
QUOICH | 132 | 12.08 | 5.89 | 0.16 | 8.48 | 10.57 | 4.99 | 0.34 | 7.39
RANNOCH | 132 | 12.07 | 5.83 | 0.7 | 8.95 | 11.49 | 5.31 | 1.05 | 8.56
REDMOSS | 132 | 36.4 | 15.74 | 1.83 | 24.09 | 40.37 | 18.03 | 1.7 | 27.2
SHIN | 132 | 26.59 | 11.76 | 1.26 | 17.89 | 26.9 | 11.8 | 2.06 | 18.74
SLOY | 132 | 48.15 | 21.38 | 2.12 | 32.35 | 48.91 | 21.64 | 2.36 | 32.96
SPITTAL | 132 | 22.34 | 9.02 | 4.85 | 17.61 | 27.51 | 11.01 | 5.85 | 21.41
ST FERGUS GAS TERMINAL | 132 | 22.65 | 9.53 | 1.24 | 14.72 | 22.73 | 9.84 | 0.9 | 14.82
ST FERGUS MOBIL | 132 | 21.4 | 9.31 | 0.62 | 13.78 | 21.32 | 9.63 | 0.55 | 14.17
ST FILLIANS | 132 | 10.12 | 5.05 | 0.26 | 7.41 | 9.08 | 4.39 | 0.31 | 6.52
STRATHY NORTH | 132 | 12.94 | 5.1 | 1.77 | 8.98 | 13.42 | 5.28 | 2.18 | 9.65
STRICHEN | 132 | 13.6 | 6.16 | 0.64 | 9.35 | 13.41 | 6.01 | 0.97 | 9.47
STRONELAIRG | 132 | 32.59 | 12.32 | 6.41 | 23.83 | 38.36 | 14.86 | 6.92 | 27.93
TARLAND | 132 | 8.57 | 4.23 | 0.09 | 6.08 | 8.17 | 3.82 | 0.2 | 5.6
TAYNUILT | 132 | 11.1 | 5.73 | 0.85 | 8.96 | 10.86 | 5.27 | 1.14 | 8.59
TEALING | 132 | 44.22 | 18.27 | 6.47 | 32.31 | 48.39 | 20.2 | 5.59 | 34.16
THURSO SOUTH | 132 | 30.62 | 11.67 | 7.12 | 23.63 | 36.36 | 13.84 | 8.24 | 27.82
TOMATIN | 132 | 38.92 | 14.88 | 7.1 | 28.15 | 41.58 | 16.14 | 6.27 | 29.09
TUMMEL | 132 | 32.09 | 12.62 | 5.63 | 23.49 | 32.26 | 13.28 | 4.5 | 23.29
TUMMEL BRIDGE | 132 | 39.63 | 16.86 | 3.67 | 27.52 | 38.37 | 16.63 | 2.74 | 26.26
WILLOWDALE | 132 | 41.69 | 17.37 | 3.86 | 28.42 | 49.78 | 21 | 4.01 | 33.7
WOODHILL | 132 | 41.29 | 17.34 | 3.33 | 27.86 | 48.85 | 20.79 | 3.42 | 32.82
ABERNETHY | 33 | 27.2 | 11.15 | 1.72 | 17.48 | 3.02 | 2.1 | 0 | 2.96
ALNESS | 33 | 53.36 | 20.69 | 9.15 | 38.4 | 2.16 | 1.5 | 0 | 2.12
ARBROATH | 33 | 26.72 | 10.54 | 2.52 | 17.42 | 1.53 | 1.06 | 0 | 1.5
ARDMORE | 33 | 22.51 | 9.09 | 4.13 | 16.98 | 1.08 | 0.75 | 0 | 1.06
BEAULY | 33 | 34.07 | 13.07 | 5.37 | 23.86 | 1.48 | 1.02 | 0 | 1.45
BERRY BURN | 33 | 41.03 | 15.33 | 7.59 | 29.27 | 1.08 | 0.75 | 0 | 1.06
BOAT OF GARTEN | 33 | 33.37 | 13.08 | 3.46 | 21.96 | 2.15 | 1.49 | 0 | 2.11
BRACO WEST | 33 | 58.08 | 22.27 | 10.03 | 41.53 | 2.2 | 1.52 | 0 | 2.16
BRIDGE OF DUN | 33 | 23.15 | 9.62 | 1.01 | 14.62 | 2.13 | 1.47 | 0 | 2.09
BROADFORD | 33 | 9.83 | 4.02 | 0.62 | 6.31 | 0.75 | 0.52 | 0 | 0.73
BRORA | 33 | 14.25 | 5.7 | 0.8 | 8.85 | 1.09 | 0.75 | 0 | 1.07
BURGHMUIR | 33 | 23.47 | 9.9 | 0.64 | 14.64 | 2.14 | 1.48 | 0 | 2.1
CAIRNFORD | 33 | 32.9 | 12.28 | 6.75 | 24.12 | 1.09 | 0.76 | 0 | 1.07
CARRADALE I | 33 | 27.6 | 10.85 | 3.47 | 18.82 | 2.14 | 1.48 | 0 | 2.1
CARRADALE II | 33 | 51 | 19.94 | 5.53 | 33.73 | 2.16 | 1.5 | 0 | 2.12
CASSLEY | 33 | 12.99 | 5.1 | 1.71 | 8.92 | 1.09 | 0.75 | 0 | 1.06
CEANNACROC | 33 | 3.41 | 1.33 | 0.35 | 2.24 | 3.32 | 1.31 | 0.26 | 2.11
CHARLESTON | 33 | 31.12 | 11.65 | 7.24 | 23.72 | 1.57 | 1.09 | 0 | 1.54
CLACHAN | 33 | 7.35 | 2.74 | 1.65 | 5.53 | 6.32 | 2.39 | 1.03 | 4.41
CLAYHILLS | 33 | 32.62 | 12.47 | 5.03 | 22.66 | 3.02 | 2.1 | 0 | 2.97
COUPAR ANGUS | 33 | 41.22 | 15.83 | 8.01 | 30.39 | 2.14 | 1.48 | 0 | 2.09
CRAIGIEBUCKLER | 33 | 27.12 | 10.61 | 2.53 | 17.53 | 1.53 | 1.06 | 0 | 1.5
DALLAS | 33 | 40.83 | 15.31 | 7.32 | 28.97 | 1.1 | 0.76 | 0 | 1.08
DOUNREAY | 33 | 39.78 | 14.9 | 8.08 | 29.15 | 2.19 | 1.52 | 0 | 2.15
DUDHOPE | 33 | 34.1 | 13.11 | 5.34 | 23.88 | 2.89 | 2 | 0 | 2.83
DUNBEATH | 33 | 12.33 | 4.81 | 1.09 | 7.89 | 0.4 | 0.27 | 0 | 0.39
DUNOON | 33 | 28.66 | 12.56 | 0.56 | 18.32 | 2.14 | 1.48 | 0 | 2.09
DUNVEGAN | 33 | 17.11 | 7.04 | 1.49 | 11.44 | 1.08 | 0.75 | 0 | 1.06
DYCE | 33 | 36.42 | 13.86 | 6.11 | 25.72 | 2.96 | 2.05 | 0 | 2.9
ELGIN | 33 | 26.16 | 10.47 | 1.72 | 16.53 | 1.8 | 1.25 | 0 | 1.77
FASNAKYLE | 33 | 54.99 | 20.28 | 12.91 | 41.59 | 2.17 | 1.5 | 0 | 2.12
FETTERESSO | 33 | 30.32 | 11.37 | 6.21 | 22.29 | 1.08 | 0.75 | 0 | 1.06
FIDDES | 33 | 36.79 | 14.83 | 3.73 | 24.7 | 2.15 | 1.49 | 0 | 2.11
FORT AUGUSTUS | 33 | 9.99 | 3.69 | 2.47 | 7.7 | 0.72 | 0.5 | 0 | 0.7
FORT WILLIAM | 33 | 39.89 | 15.87 | 6.03 | 28.47 | 0.88 | 0.61 | 0 | 0.86
FRASERBURGH | 33 | 24.23 | 9.52 | 2.07 | 15.54 | 2.12 | 1.47 | 0 | 2.08
GLENFARCLAS | 33 | 19.8 | 8.02 | 0.86 | 12.2 | 1.09 | 0.76 | 0 | 1.07
GRUDIE BRIDGE | 33 | 38.82 | 14.48 | 8.42 | 28.91 | 2.19 | 1.52 | 0 | 2.14
INVERNESS | 33 | 54.5 | 21.33 | 7.63 | 37.79 | 3.21 | 2.23 | 0 | 3.15
KEITH I | 33 | 49.41 | 18.78 | 12.73 | 39.29 | 2.17 | 1.51 | 0 | 2.13
KEITH II | 33 | 39.69 | 14.91 | 8.09 | 29.18 | 2.17 | 1.51 | 0 | 2.13
KILLIN | 33 | 34.85 | 13.66 | 4.17 | 23.49 | 2.15 | 1.49 | 0 | 2.11
KINLOCHLEVEN | 33 | 16.01 | 6.4 | 2.21 | 11.26 | 0.72 | 0.5 | 0 | 0.7
KINTORE | 33 | 56.8 | 21.68 | 12.31 | 42.97 | 3.24 | 2.24 | 0 | 3.17
LAIRG | 33 | 24.76 | 9.68 | 2.51 | 16.2 | 1.09 | 0.76 | 0 | 1.07
LUNANHEAD | 33 | 32.17 | 12.54 | 4.82 | 22.55 | 2.17 | 1.5 | 0 | 2.13
LYNDHURST | 33 | 32.33 | 12.45 | 4.47 | 22.08 | 2.92 | 2.02 | 0 | 2.86
MACDUFF | 33 | 40.46 | 16.47 | 4.16 | 27.46 | 2.18 | 1.51 | 0 | 2.14
MILTON OF CRAIGIE | 33 | 34.76 | 13.29 | 6.32 | 25.11 | 3.26 | 2.26 | 0 | 3.2
MYBSTER I | 33 | 46.6 | 17.56 | 9.52 | 34.36 | 2.19 | 1.52 | 0 | 2.15
MYBSTER II | 33 | 48.9 | 18.47 | 9.81 | 35.93 | 2.19 | 1.52 | 0 | 2.15
MYBSTER III | 33 | 34.7 | 12.86 | 8.5 | 26.69 | 2.2 | 1.52 | 0 | 2.15
NAIRN | 33 | 25.25 | 10.33 | 0.97 | 15.58 | 3.01 | 2.09 | 0 | 2.95
PERSLEY | 33 | 32.64 | 12.21 | 8.22 | 25.49 | 2.16 | 1.5 | 0 | 2.12
PETERHEAD GRANGE | 33 | 28.49 | 11.16 | 3.47 | 19.26 | 0.58 | 0.4 | 0 | 0.57
PORT ANN | 33 | 33.43 | 13.43 | 3.88 | 22.87 | 1.84 | 1.27 | 0 | 1.8
RANNOCH | 33 | 38.74 | 15.19 | 4.14 | 25.62 | 2.16 | 1.5 | 0 | 2.12
REDMOSS | 33 | 38.92 | 15.42 | 5.07 | 26.88 | 3.03 | 2.1 | 0 | 2.97
SHIN | 33 | 32.14 | 12.43 | 4.33 | 21.92 | 2.17 | 1.5 | 0 | 2.12
ST FILLIANS | 33 | 6.64 | 2.41 | 2.33 | 5.74 | 6.77 | 2.44 | 2.57 | 6.03
STRICHEN | 33 | 32.74 | 12.47 | 5.26 | 22.89 | 2.15 | 1.49 | 0 | 2.11
TARLAND | 33 | 20.1 | 8.46 | 0.64 | 12.6 | 1.51 | 1.05 | 0 | 1.48
TAYNUILT | 33 | 34.9 | 13.82 | 5.1 | 24.64 | 2.18 | 1.51 | 0 | 2.14
THURSO SOUTH | 33 | 63.8 | 23.74 | 19.34 | 52.91 | 2.2 | 1.53 | 0 | 2.16
TUMMEL BRIDGE | 33 | 10.33 | 3.74 | 4.5 | 9.78 | 1.12 | 0.78 | 0 | 1.1
WILLOWDALE | 33 | 32.96 | 12.65 | 4.97 | 22.86 | 3.01 | 2.09 | 0 | 2.95
WOODHILL | 33 | 31.92 | 12.04 | 6.68 | 23.7 | 4.47 | 3.1 | 0 | 4.38

## D1.2
ETYS 19 Yr 2 - SHE Transmission Fault Levels (kA), Winter 2020/21
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 27.9 | 10.73 | 6.66 | 21.83 | 27.58 | 10.66 | 6.57 | 21.64 | Back To Menu
BLACKHILLOCK | 400 | 35.24 | 13.49 | 9.44 | 28.52 | 35.35 | 13.57 | 9.15 | 28.34
FORT AUGUSTUS | 400 | 24.69 | 9.48 | 5.84 | 19.24 | 24.51 | 9.46 | 5.84 | 19.21
MELGARVE | 400 | 22.62 | 8.68 | 5.33 | 17.6 | 22.27 | 8.6 | 5.12 | 17.29
BEAULY | 275 | 56.42 | 22.31 | 11.19 | 42.74 | 56.87 | 22.64 | 10.88 | 42.9
BERRY BURN | 275 | 33.15 | 13.56 | 4.15 | 23.33 | 25.61 | 10.62 | 3.32 | 18.34
BLACKHILLOCK I | 275 | 59.86 | 23.76 | 12.45 | 46.05 | 60.82 | 24.18 | 12.51 | 46.71
BLACKHILLOCK II | 275 | 33.96 | 13.11 | 8.91 | 27.45 | 36.11 | 14.09 | 8.34 | 28.26
BRACO WEST | 275 | 33.57 | 13.2 | 6.12 | 24.78 | 27.81 | 11.07 | 5.14 | 20.79
CAIRNFORD | 275 | 48.05 | 19.4 | 7.7 | 35.14 | 42.41 | 17.4 | 5.93 | 30.54
CONNAGILL | 275 | 21.14 | 8.33 | 4.68 | 16.46 | 21.54 | 8.56 | 4.29 | 16.4
DALLAS | 275 | 34.55 | 14.11 | 4.47 | 24.43 | 27.14 | 11.23 | 3.61 | 19.49
DOUNREAY | 275 | 23.18 | 9.08 | 5.7 | 18.54 | 25.34 | 9.93 | 6.08 | 20.12
FARIGAIG I | 275 | 42.44 | 17.04 | 7.23 | 31.33 | 33.87 | 13.88 | 5.38 | 25.01
FARIGAIG II | 275 | 42.67 | 17.13 | 7.36 | 31.57 | 34.29 | 14.03 | 5.61 | 25.46
FASNAKYLE | 275 | 36.61 | 14.32 | 7.42 | 27.66 | 32.31 | 12.82 | 6.1 | 24.23
FETTERESSO | 275 | 44.5 | 18.02 | 6.2 | 31.69 | 33.89 | 13.95 | 4.68 | 24.41
FORT AUGUSTUS | 275 | 31.69 | 12.35 | 6.61 | 24.06 | 28.98 | 11.36 | 6.24 | 22.31
FOYERS | 275 | 42.23 | 16.9 | 7.7 | 31.61 | 29.46 | 12.25 | 3.95 | 21.28
FYRISH | 275 | 29.99 | 11.96 | 5.12 | 22.03 | 27.23 | 10.97 | 4.92 | 20.43
GORDONBUSH | 275 | 21.29 | 8.47 | 3.88 | 15.86 | 19.82 | 7.97 | 3.64 | 14.91
KEITH | 275 | 56.73 | 22.7 | 10.81 | 42.91 | 57.82 | 23.23 | 10.65 | 43.5
KINTORE | 275 | 66.94 | 26.66 | 12.52 | 50.23 | 57.44 | 23.25 | 9.72 | 42.6
KNOCKNAGAEL | 275 | 56.58 | 22.52 | 10.61 | 42.45 | 52.65 | 21.2 | 9.55 | 39.52
LOCH BUIDHE | 275 | 30.26 | 12.08 | 5.34 | 22.42 | 27.86 | 11.23 | 5.14 | 21.03
PERSLEY | 275 | 39.67 | 15.96 | 6.33 | 28.89 | 32.64 | 13.21 | 5.62 | 24.31
PETERHEAD | 275 | 65.57 | 25.28 | 18.53 | 54.29 | 44.68 | 17.83 | 9.33 | 34.54
SPITTAL | 275 | 22.2 | 8.69 | 5.85 | 18.13 | 24.97 | 9.72 | 6.63 | 20.37
STRATHBRORA | 275 | 23.21 | 9.24 | 4.18 | 17.25 | 21.62 | 8.69 | 4.04 | 16.33
TEALING | 275 | 49.36 | 20.02 | 6.76 | 35.08 | 40.48 | 16.69 | 5.48 | 29.09
THURSO SOUTH | 275 | 21.27 | 8.33 | 5.37 | 17.14 | 23 | 9 | 5.62 | 18.35
TOMATIN | 275 | 29.85 | 11.85 | 5.27 | 22.04 | 25.62 | 10.31 | 4.42 | 19
TUMMEL | 275 | 26.53 | 10.4 | 5.2 | 19.9 | 22.56 | 9 | 4.37 | 17.09
ABERARDER | 132 | 14.47 | 5.59 | 2.11 | 10.03 | 15.16 | 5.92 | 2.22 | 10.6
ABERDEEN BAY | 132 | 19.21 | 8.03 | 1.76 | 13.11 | 17.4 | 7.31 | 1.53 | 11.87
ABERNETHY | 132 | 15.39 | 7.63 | 0.21 | 11 | 15.56 | 7.38 | 0.49 | 10.93
A-CHRUACH | 132 | 15.28 | 7.88 | 0.35 | 11.49 | 15.15 | 7.26 | 0.73 | 10.99
AIGAS | 132 | 34.72 | 16.28 | 0.42 | 23.45 | 31.41 | 14.91 | 0.47 | 21.56
ALNESS | 132 | 35.24 | 13.7 | 4.91 | 24.29 | 38.71 | 15.22 | 4.89 | 26.41
AN SUIDHE | 132 | 17.94 | 9.41 | 0.09 | 13.4 | 16.64 | 8.13 | 0.33 | 11.83
ARBROATH | 132 | 13.52 | 6.35 | 0.38 | 9.36 | 12.54 | 5.71 | 0.7 | 8.77
ARDKINGLAS | 132 | 28.67 | 13.88 | 0.25 | 19.88 | 24.52 | 11.6 | 0.6 | 17
ARDMORE | 132 | 5.83 | 2.58 | 0.91 | 4.57 | 6.77 | 2.96 | 1.09 | 5.27
BEAULY | 132 | 57.71 | 24.32 | 5.83 | 40.23 | 64.39 | 26.83 | 7.21 | 45.16
BEINNEUN | 132 | 19.74 | 9.33 | 0.89 | 14.09 | 20.5 | 9.36 | 1.47 | 14.72
BHLARAIDH | 132 | 20.45 | 9.47 | 1.15 | 14.54 | 20.83 | 9.51 | 1.78 | 15.23
BLACKHILLOCK | 132 | 41.35 | 15.61 | 8.89 | 30.97 | 45.19 | 17.25 | 8.77 | 33.16
BOAT OF GARTEN | 132 | 15.09 | 6.42 | 0.73 | 9.81 | 14.72 | 6.21 | 1.03 | 9.82
BRECHIN | 132 | 12.9 | 6.42 | 0.17 | 9.25 | 13.01 | 6.13 | 0.27 | 8.94
BRIDGE OF DUN | 132 | 10.74 | 5.44 | 0.12 | 7.82 | 11.31 | 5.38 | 0.29 | 7.91
BROADFORD | 132 | 6.24 | 3.16 | 0.06 | 4.53 | 6.32 | 3.01 | 0.25 | 4.51
BRORA | 132 | 12.71 | 6.27 | 0.04 | 8.91 | 12.33 | 5.86 | 0.24 | 8.53
BURGHMUIR | 132 | 12.42 | 6.31 | 0.05 | 8.97 | 13.69 | 6.56 | 0.23 | 9.51
CARRADALE | 132 | 18.55 | 7.65 | 1.87 | 12.69 | 19.52 | 7.95 | 2.32 | 13.56
CASSLEY | 132 | 7.35 | 3.65 | 0.22 | 5.38 | 6.91 | 3.3 | 0.27 | 4.93
CEANNACROC | 132 | 18.78 | 8.95 | 0.74 | 13.39 | 19.24 | 8.87 | 1.18 | 13.72
CHARLESTON | 132 | 40.31 | 17.05 | 3.83 | 27.95 | 43.93 | 18.72 | 4.27 | 30.74
CLACHAN | 132 | 27.9 | 13.45 | 0.51 | 19.54 | 24.3 | 11.52 | 0.8 | 17.09
CLAYHILLS | 132 | 39.95 | 16.81 | 3.12 | 26.89 | 46.29 | 19.99 | 2.86 | 31.14
CLUNIE | 132 | 20.91 | 9.68 | 0.41 | 14.09 | 19.56 | 8.89 | 0.76 | 13.33
CONNAGILL | 132 | 17.15 | 6.43 | 4.09 | 13.19 | 19.69 | 7.44 | 4.14 | 14.67
CORRIEGARTH | 132 | 11.6 | 4.6 | 1.55 | 8.05 | 12.04 | 4.75 | 1.84 | 8.55
CORRIEMOILLIE | 132 | 29.79 | 12.14 | 3.17 | 20.34 | 31.25 | 12.74 | 3.46 | 21.47
COUPAR ANGUS | 132 | 22.6 | 9.89 | 1.09 | 15.08 | 21.36 | 9.1 | 1.78 | 14.65
CRAIGIEBUCKLER | 132 | 44.13 | 18.22 | 4.16 | 29.92 | 52.12 | 21.83 | 4.03 | 34.89
CROSSAIG | 132 | 27.41 | 11.48 | 2.96 | 19.2 | 31.61 | 13.13 | 3.4 | 21.96
CULLIGRAN | 132 | 18.23 | 9.02 | 0.19 | 12.95 | 16.55 | 7.94 | 0.35 | 11.57
DEANIE | 132 | 12.7 | 6.42 | 0.09 | 9.17 | 11.78 | 5.67 | 0.21 | 8.23
DORENELL | 132 | 15.79 | 6.6 | 1.35 | 10.68 | 16.63 | 6.77 | 1.92 | 11.5
DOUNREAY | 132 | 21.2 | 8.01 | 4.81 | 16.13 | 27.03 | 10.26 | 5.73 | 20.24
DUDHOPE | 132 | 36.58 | 15.87 | 2.37 | 24.81 | 38.73 | 17.31 | 2.01 | 26.49
DUNBEATH | 132 | 12.31 | 5.89 | 0.12 | 8.45 | 11.34 | 5.36 | 0.29 | 7.87
DUNMAGLASS | 132 | 15.67 | 5.96 | 3.04 | 11.46 | 17.16 | 6.6 | 3.17 | 12.51
DUNOON | 132 | 9.71 | 5.05 | 0.09 | 7.23 | 9.38 | 4.59 | 0.16 | 6.65
DUNVEGAN | 132 | 6.59 | 2.91 | 0.73 | 4.85 | 8.03 | 3.5 | 0.96 | 5.91
DYCE | 132 | 24.77 | 10.5 | 2.02 | 16.87 | 22.57 | 9.58 | 1.99 | 15.54
EDINBANE | 132 | 6.76 | 3.02 | 0.65 | 4.92 | 8.12 | 3.56 | 0.89 | 5.93
ELGIN | 132 | 13.96 | 6.78 | 0.27 | 9.86 | 13.26 | 6.24 | 0.61 | 9.43
ERROCHTY | 132 | 44.7 | 18.48 | 6.44 | 32.57 | 45.36 | 19.02 | 5.37 | 32.27
FARIGAIG I | 132 | 14.82 | 5.69 | 2.41 | 10.45 | 16.11 | 6.17 | 2.72 | 11.44
FARIGAIG II | 132 | 17.65 | 6.56 | 4.47 | 13.75 | 21.06 | 7.88 | 4.82 | 15.97
FARR | 132 | 22.64 | 9.9 | 0.65 | 14.65 | 21.3 | 9.37 | 0.99 | 14.24
FERNOCH | 132 | 13.09 | 6.62 | 1.37 | 10.73 | 14.58 | 6.96 | 1.67 | 11.52
FETTERESSO | 132 | 22.74 | 8.75 | 3.46 | 15.83 | 25.15 | 9.68 | 3.87 | 17.56
FIDDES | 132 | 14.62 | 7.17 | 0.71 | 10.86 | 15.04 | 6.91 | 1.14 | 10.91
FINLARIG | 132 | 21.24 | 10.19 | 0.69 | 15.1 | 21.28 | 9.86 | 0.94 | 14.88
FORT AUGUSTUS | 132 | 54.03 | 20.87 | 9.75 | 39.26 | 63.02 | 24.53 | 10.47 | 45.16
FORT WILLIAM | 132 | 10.04 | 4.73 | 1.33 | 8.02 | 10.48 | 4.77 | 1.5 | 8.25
FRASERBURGH | 132 | 12.4 | 5.7 | 0.38 | 8.45 | 12.38 | 5.6 | 0.68 | 8.6
FYRISH | 132 | 38.03 | 14.52 | 6.96 | 27.5 | 41.95 | 16.04 | 7.79 | 30.47
GLENDOE | 132 | 42.2 | 17.51 | 2.92 | 27.69 | 46.46 | 19.82 | 3.02 | 31.05
GLENFARCLAS | 132 | 7.32 | 3.44 | 0.21 | 5.08 | 7.21 | 3.26 | 0.39 | 4.99
GLENMORISTON | 132 | 22.62 | 10.54 | 1.19 | 16.1 | 22.71 | 10.36 | 1.74 | 16.39
GRIFFIN | 132 | 16.71 | 8.07 | 0.5 | 11.91 | 16.71 | 7.77 | 1.05 | 12.04
GRUDIE BRIDGE | 132 | 23.26 | 9.73 | 1.69 | 15.46 | 23.74 | 9.91 | 2.06 | 16.07
INVERARAY | 132 | 34.79 | 16.35 | 0.99 | 24.11 | 31.38 | 14.59 | 0.8 | 21.43
INVERARNAN | 132 | 52.72 | 22.4 | 5.12 | 36.8 | 54.88 | 23.1 | 5.18 | 37.85
INVERGARRY | 132 | 20.32 | 9.77 | 0.22 | 14.05 | 19.04 | 9.03 | 0.36 | 13.14
INVERNESS | 132 | 48.68 | 20.37 | 4.33 | 33.14 | 53.56 | 22.33 | 4.93 | 36.52
KEITH | 132 | 32.54 | 13.04 | 6.64 | 25.09 | 41.21 | 16.96 | 7.77 | 31.76
KILLIN | 132 | 24.29 | 11.49 | 1.02 | 17.27 | 25.46 | 11.55 | 1.55 | 17.89
KILMORACK | 132 | 47.47 | 20.98 | 2.02 | 31.69 | 48.11 | 21.29 | 1.97 | 32.07
KINLOCHLEVEN | 132 | 6.7 | 3.16 | 0.64 | 5.12 | 6.98 | 3.15 | 0.78 | 5.24
KINTORE | 132 | 47.88 | 19.08 | 7.86 | 34.84 | 55.46 | 22.19 | 8.32 | 39.71
KNOCKNAGAEL | 132 | 53.92 | 22.18 | 6.59 | 37.97 | 59.1 | 24.04 | 7.78 | 41.79
LAIRG | 132 | 16.08 | 7.57 | 0.48 | 11.19 | 15.63 | 7.19 | 0.84 | 11
LOCH BUIDHE | 132 | 31.31 | 13.02 | 4.93 | 23.34 | 36.23 | 14.97 | 5.41 | 26.58
LOCHAY | 132 | 20.81 | 10.01 | 0.64 | 14.8 | 20.5 | 9.55 | 0.85 | 14.36
LUICHART | 132 | 29.76 | 12.22 | 2.71 | 20 | 29.46 | 12.09 | 2.77 | 19.87
LUNANHEAD | 132 | 17.11 | 7.4 | 0.94 | 11.41 | 16 | 6.82 | 1.47 | 11.11
LYNDHURST | 132 | 32.33 | 14.38 | 1.34 | 21.67 | 32.92 | 14.72 | 1.55 | 22.37
MACDUFF | 132 | 9.73 | 4.53 | 0.65 | 7.07 | 9.72 | 4.38 | 0.83 | 7.03
MELGARVE | 132 | 37.22 | 14 | 7.93 | 27.72 | 44.08 | 16.72 | 8.34 | 31.98
MILLENNIUM | 132 | 22.21 | 10.41 | 0.74 | 15.47 | 22.72 | 10.42 | 1.12 | 15.85
MILTON OF CRAIGIE | 132 | 38.99 | 16.54 | 3.85 | 27.24 | 41.86 | 18.11 | 3.6 | 29.2
MOSSFORD | 132 | 26.45 | 10.96 | 2.23 | 17.72 | 27.56 | 11.39 | 2.57 | 18.67
MYBSTER I | 132 | 19.04 | 8.08 | 1.71 | 13.14 | 20.12 | 8.7 | 1.08 | 13.38
MYBSTER II | 132 | 19.8 | 7.49 | 4.48 | 15.08 | 22.49 | 8.51 | 5.1 | 17.14
NAIRN | 132 | 12.74 | 6.38 | 0.15 | 9.17 | 11.78 | 5.64 | 0.39 | 8.37
NANT | 132 | 11.68 | 6.15 | 0.27 | 8.96 | 10.74 | 5.3 | 0.39 | 7.89
ORRIN | 132 | 32.62 | 13.49 | 2.81 | 21.88 | 32.54 | 13.42 | 2.94 | 21.92
PERSLEY | 132 | 42.93 | 17.72 | 4.9 | 29.96 | 52.18 | 21.61 | 5.64 | 36.21
PETERHEAD | 132 | 34.38 | 13.03 | 8.09 | 26.51 | 40.87 | 15.69 | 7.95 | 30.13
PETERHEAD GRANGE | 132 | 22.92 | 9.5 | 1.52 | 14.96 | 23.78 | 9.99 | 1.73 | 15.85
PORT ANN | 132 | 12.2 | 6.33 | 0.3 | 9.25 | 11.37 | 5.56 | 0.39 | 8.25
QUOICH | 132 | 14.24 | 6.47 | 0.3 | 9.45 | 11.92 | 5.26 | 0.5 | 7.94
RANNOCH | 132 | 12.12 | 5.86 | 0.7 | 8.99 | 11.54 | 5.33 | 1.05 | 8.6
REDMOSS | 132 | 36.5 | 15.78 | 1.84 | 24.15 | 40.47 | 18.08 | 1.7 | 27.27
SHIN | 132 | 26.88 | 11.89 | 1.28 | 18.09 | 27.1 | 11.9 | 2.07 | 18.9
SLOY | 132 | 48.41 | 21.51 | 2.12 | 32.53 | 49.12 | 21.74 | 2.37 | 33.11
SPITTAL | 132 | 22.51 | 9.08 | 4.93 | 17.77 | 27.72 | 11.08 | 5.93 | 21.6
ST FERGUS GAS TERMINAL | 132 | 22.87 | 9.65 | 1.21 | 14.86 | 22.88 | 9.93 | 0.89 | 14.93
ST FERGUS MOBIL | 132 | 21.58 | 9.42 | 0.59 | 13.91 | 21.44 | 9.71 | 0.54 | 14.27
ST FILLIANS | 132 | 10.1 | 5.04 | 0.27 | 7.4 | 9.04 | 4.37 | 0.32 | 6.49
STRATHY NORTH | 132 | 13 | 5.12 | 1.77 | 9.01 | 13.48 | 5.3 | 2.19 | 9.68
STRICHEN | 132 | 13.64 | 6.19 | 0.65 | 9.39 | 13.45 | 6.03 | 0.98 | 9.51
STRONELAIRG | 132 | 32.38 | 12.24 | 6.38 | 23.69 | 38.12 | 14.76 | 6.88 | 27.76
TARLAND | 132 | 8.59 | 4.24 | 0.09 | 6.09 | 8.19 | 3.82 | 0.2 | 5.6
TAYNUILT | 132 | 11.11 | 5.74 | 0.86 | 8.98 | 10.87 | 5.27 | 1.15 | 8.61
TEALING | 132 | 44.62 | 18.42 | 6.59 | 32.64 | 48.63 | 20.29 | 5.62 | 34.32
THURSO SOUTH | 132 | 30.78 | 11.7 | 7.25 | 23.79 | 36.54 | 13.88 | 8.36 | 27.99
TOMATIN | 132 | 39.53 | 15.11 | 7.23 | 28.6 | 42.3 | 16.41 | 6.38 | 29.59
TUMMEL | 132 | 32.27 | 12.7 | 5.67 | 23.62 | 32.44 | 13.35 | 4.53 | 23.42
TUMMEL BRIDGE | 132 | 39.81 | 16.94 | 3.69 | 27.65 | 38.54 | 16.71 | 2.75 | 26.38
WILLOWDALE | 132 | 41.81 | 17.42 | 3.87 | 28.5 | 49.92 | 21.05 | 4.02 | 33.8
WOODHILL | 132 | 41.41 | 17.39 | 3.34 | 27.94 | 48.98 | 20.85 | 3.43 | 32.91
ABERNETHY | 33 | 27.2 | 11.12 | 1.75 | 17.48 | 2.99 | 2.07 | 0 | 2.93
ALNESS | 33 | 53.44 | 20.72 | 9.17 | 38.47 | 2.17 | 1.5 | 0 | 2.12
ARBROATH | 33 | 26.93 | 10.62 | 2.57 | 17.58 | 1.54 | 1.07 | 0 | 1.51
ARDMORE | 33 | 22.61 | 9.13 | 4.15 | 17.06 | 1.08 | 0.75 | 0 | 1.06
BEAULY | 33 | 34.22 | 13.13 | 5.41 | 23.98 | 1.48 | 1.02 | 0 | 1.45
BERRY BURN | 33 | 41.24 | 15.4 | 7.63 | 29.42 | 1.09 | 0.76 | 0 | 1.07
BOAT OF GARTEN | 33 | 33.56 | 13.16 | 3.48 | 22.09 | 2.17 | 1.5 | 0 | 2.12
BRACO WEST | 33 | 58.11 | 22.29 | 10.05 | 41.56 | 2.2 | 1.53 | 0 | 2.16
BRIDGE OF DUN | 33 | 23.16 | 9.63 | 1.02 | 14.63 | 2.13 | 1.47 | 0 | 2.08
BROADFORD | 33 | 9.97 | 4.06 | 0.64 | 6.38 | 0.75 | 0.52 | 0 | 0.74
BRORA | 33 | 14.41 | 5.76 | 0.81 | 8.95 | 1.1 | 0.76 | 0 | 1.08
BURGHMUIR | 33 | 23.58 | 9.94 | 0.65 | 14.71 | 2.15 | 1.49 | 0 | 2.11
CAIRNFORD | 33 | 32.91 | 12.28 | 6.76 | 24.13 | 1.09 | 0.76 | 0 | 1.07
CARRADALE I | 33 | 36.1 | 14.56 | 3.32 | 23.9 | 2.15 | 1.49 | 0 | 2.11
CARRADALE II | 33 | 51.37 | 20.04 | 5.67 | 34.01 | 2.15 | 1.49 | 0 | 2.11
CASSLEY | 33 | 13.03 | 5.11 | 1.72 | 8.95 | 1.09 | 0.75 | 0 | 1.07
CEANNACROC | 33 | 3.44 | 1.35 | 0.35 | 2.26 | 3.35 | 1.32 | 0.26 | 2.13
CHARLESTON | 33 | 30.97 | 11.58 | 7.31 | 23.68 | 1.55 | 1.08 | 0 | 1.52
CLACHAN | 33 | 7.38 | 2.75 | 1.66 | 5.56 | 6.33 | 2.39 | 1.04 | 4.42
CLAYHILLS | 33 | 32.69 | 12.49 | 5.05 | 22.72 | 3.03 | 2.1 | 0 | 2.97
COUPAR ANGUS | 33 | 43.65 | 16.7 | 8.81 | 32.43 | 2.14 | 1.48 | 0 | 2.1
CRAIGIEBUCKLER | 33 | 27.16 | 10.62 | 2.54 | 17.56 | 1.53 | 1.06 | 0 | 1.5
DALLAS | 33 | 40.66 | 15.24 | 7.3 | 28.85 | 1.09 | 0.76 | 0 | 1.07
DOUNREAY | 33 | 39.71 | 14.86 | 8.12 | 29.14 | 2.18 | 1.51 | 0 | 2.14
DUDHOPE | 33 | 34.31 | 13.18 | 5.4 | 24.04 | 2.91 | 2.01 | 0 | 2.85
DUNBEATH | 33 | 12.43 | 4.85 | 1.1 | 7.95 | 0.4 | 0.28 | 0 | 0.39
DUNOON | 33 | 28.77 | 12.6 | 0.56 | 18.39 | 2.15 | 1.49 | 0 | 2.1
DUNVEGAN | 33 | 17.2 | 7.08 | 1.49 | 11.49 | 1.08 | 0.75 | 0 | 1.06
DYCE | 33 | 38.51 | 14.54 | 7.44 | 28.01 | 2.17 | 1.5 | 0 | 2.13
ELGIN | 33 | 29.59 | 12.05 | 1.65 | 18.69 | 1.84 | 1.27 | 0 | 1.8
FASNAKYLE | 33 | 55.51 | 20.47 | 13.05 | 42 | 2.19 | 1.52 | 0 | 2.15
FETTERESSO | 33 | 30.61 | 11.48 | 6.26 | 22.5 | 1.09 | 0.75 | 0 | 1.07
FIDDES | 33 | 36.97 | 14.89 | 3.78 | 24.84 | 2.16 | 1.5 | 0 | 2.12
FORT AUGUSTUS | 33 | 10.16 | 3.76 | 2.52 | 7.83 | 0.73 | 0.51 | 0 | 0.72
FORT WILLIAM | 33 | 39.46 | 15.7 | 5.98 | 28.18 | 0.87 | 0.6 | 0 | 0.85
FRASERBURGH | 33 | 24.17 | 9.51 | 2.01 | 15.47 | 2.13 | 1.48 | 0 | 2.09
GLENFARCLAS | 33 | 19.92 | 8.07 | 0.86 | 12.27 | 1.1 | 0.76 | 0 | 1.08
GRUDIE BRIDGE | 33 | 39.34 | 14.68 | 8.54 | 29.29 | 2.21 | 1.54 | 0 | 2.17
INVERNESS | 33 | 55.16 | 21.58 | 7.74 | 38.26 | 3.26 | 2.26 | 0 | 3.19
KEITH I | 33 | 51.9 | 19.75 | 12.79 | 40.72 | 2.17 | 1.51 | 0 | 2.13
KEITH II | 33 | 39.56 | 14.88 | 8.02 | 29.07 | 2.19 | 1.52 | 0 | 2.15
KILLIN | 33 | 35.04 | 13.74 | 4.23 | 23.67 | 2.16 | 1.5 | 0 | 2.12
KINLOCHLEVEN | 33 | 16.07 | 6.42 | 2.22 | 11.3 | 0.72 | 0.5 | 0 | 0.71
KINTORE | 33 | 56.81 | 21.68 | 12.34 | 43.01 | 3.24 | 2.24 | 0 | 3.16
LAIRG | 33 | 24.88 | 9.73 | 2.52 | 16.28 | 1.09 | 0.76 | 0 | 1.07
LUNANHEAD | 33 | 32.11 | 12.49 | 4.9 | 22.57 | 2.14 | 1.49 | 0 | 2.1
LYNDHURST | 33 | 32.2 | 12.39 | 4.52 | 22.05 | 2.89 | 2 | 0 | 2.83
MACDUFF | 33 | 41.22 | 16.73 | 4.02 | 27.68 | 2.19 | 1.52 | 0 | 2.15
MILTON OF CRAIGIE | 33 | 35.25 | 13.47 | 6.42 | 25.47 | 3.31 | 2.3 | 0 | 3.25
MYBSTER I | 33 | 46.35 | 17.46 | 9.52 | 34.21 | 2.18 | 1.51 | 0 | 2.13
MYBSTER II | 33 | 48.94 | 18.48 | 9.85 | 35.99 | 2.2 | 1.52 | 0 | 2.15
MYBSTER III | 33 | 34.5 | 12.78 | 8.49 | 26.57 | 2.18 | 1.51 | 0 | 2.14
NAIRN | 33 | 25.64 | 10.47 | 1.01 | 15.83 | 3.05 | 2.12 | 0 | 2.99
PERSLEY | 33 | 32.69 | 12.23 | 8.23 | 25.53 | 2.17 | 1.5 | 0 | 2.13
PETERHEAD GRANGE | 33 | 28.62 | 11.23 | 3.42 | 19.3 | 0.58 | 0.41 | 0 | 0.57
PORT ANN | 33 | 33.67 | 13.52 | 3.96 | 23.08 | 1.84 | 1.27 | 0 | 1.8
RANNOCH | 33 | 38.89 | 15.25 | 4.16 | 25.72 | 2.17 | 1.5 | 0 | 2.12
REDMOSS | 33 | 38.88 | 15.4 | 5.08 | 26.86 | 3.02 | 2.1 | 0 | 2.96
SHIN | 33 | 32.39 | 12.51 | 4.46 | 22.15 | 2.17 | 1.5 | 0 | 2.13
ST FILLIANS | 33 | 6.66 | 2.42 | 2.33 | 5.75 | 6.79 | 2.45 | 2.58 | 6.04
STRICHEN | 33 | 32.74 | 12.48 | 5.19 | 22.84 | 2.15 | 1.49 | 0 | 2.11
TARLAND | 33 | 20.12 | 8.46 | 0.64 | 12.61 | 1.51 | 1.05 | 0 | 1.48
TAYNUILT | 33 | 34.97 | 13.84 | 5.13 | 24.7 | 2.18 | 1.51 | 0 | 2.14
THURSO SOUTH | 33 | 63.44 | 23.6 | 19.31 | 52.67 | 2.18 | 1.51 | 0 | 2.14
TUMMEL BRIDGE | 33 | 10.38 | 3.76 | 4.53 | 9.84 | 1.12 | 0.78 | 0 | 1.1
WILLOWDALE | 33 | 33.02 | 12.67 | 4.98 | 22.9 | 3.02 | 2.09 | 0 | 2.96
WOODHILL | 33 | 31.97 | 12.05 | 6.69 | 23.74 | 4.48 | 3.1 | 0 | 4.39

## D1.3
ETYS 19 Yr 3 - SHE Transmission Fault Levels (kA), Winter 2021/22
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 28.6 | 11.01 | 6.83 | 22.39 | 28.4 | 10.99 | 6.71 | 22.25 | Back To Menu
BLACKHILLOCK | 400 | 33.07 | 12.69 | 9.19 | 27.14 | 34.13 | 13.12 | 9.1 | 27.66
FORT AUGUSTUS | 400 | 26.36 | 10.14 | 6.18 | 20.53 | 27.66 | 10.66 | 6.7 | 21.78
MELGARVE | 400 | 23.8 | 9.14 | 5.57 | 18.51 | 23.73 | 9.19 | 5.35 | 18.36
BEAULY | 275 | 56.34 | 22.22 | 11.4 | 42.82 | 57.08 | 22.7 | 10.99 | 43.09
BERRY BURN | 275 | 32.54 | 13.28 | 4.28 | 23.06 | 25.47 | 10.55 | 3.37 | 18.3
BLACKHILLOCK I | 275 | 54.44 | 21.61 | 12.03 | 42.59 | 57.27 | 22.77 | 12.33 | 44.53
BLACKHILLOCK II | 275 | 34.06 | 13.2 | 9.05 | 27.71 | 37.08 | 14.49 | 8.72 | 29.21
BRACO WEST | 275 | 35.65 | 14 | 6.55 | 26.36 | 28.75 | 11.46 | 5.32 | 21.52
CAIRNFORD | 275 | 44.06 | 17.78 | 7.62 | 32.77 | 40.58 | 16.63 | 5.99 | 29.51
CONNAGILL | 275 | 21.21 | 8.36 | 4.7 | 16.51 | 21.63 | 8.6 | 4.31 | 16.46
DALLAS | 275 | 33.64 | 13.71 | 4.61 | 24 | 26.85 | 11.1 | 3.65 | 19.35
DOUNREAY | 275 | 23.26 | 9.11 | 5.71 | 18.59 | 25.44 | 9.96 | 6.1 | 20.19
FARIGAIG I | 275 | 42.39 | 16.98 | 7.42 | 31.43 | 33.89 | 13.87 | 5.45 | 25.06
FARIGAIG II | 275 | 42.61 | 17.06 | 7.54 | 31.67 | 34.31 | 14.02 | 5.68 | 25.5
FASNAKYLE | 275 | 36.27 | 14.16 | 7.46 | 27.49 | 32.33 | 12.81 | 6.15 | 24.26
FETTERESSO | 275 | 40.51 | 16.41 | 6.15 | 29.36 | 32.63 | 13.42 | 4.71 | 23.7
FORT AUGUSTUS | 275 | 31.11 | 12.1 | 6.58 | 23.7 | 29.02 | 11.33 | 6.44 | 22.47
FOYERS | 275 | 42.19 | 16.84 | 7.92 | 31.74 | 29.43 | 12.22 | 3.99 | 21.27
FYRISH | 275 | 30.01 | 11.96 | 5.15 | 22.06 | 27.27 | 10.98 | 4.94 | 20.46
GORDONBUSH | 275 | 21.35 | 8.49 | 3.9 | 15.9 | 19.89 | 8 | 3.66 | 14.97
KEITH | 275 | 51.89 | 20.75 | 10.6 | 39.95 | 54.65 | 21.94 | 10.63 | 41.66
KINTORE | 275 | 55.09 | 22.04 | 10.97 | 42.15 | 52.29 | 21.18 | 9.44 | 39.38
KNOCKNAGAEL | 275 | 56.46 | 22.4 | 10.96 | 42.63 | 52.93 | 21.26 | 9.83 | 39.9
LOCH BUIDHE | 275 | 30.28 | 12.08 | 5.36 | 22.44 | 27.91 | 11.25 | 5.16 | 21.07
NEW DEER | 275 | 41.08 | 16.35 | 8.47 | 31.59 | 31.89 | 13.12 | 4.51 | 23.07
PERSLEY | 275 | 32.7 | 13.25 | 5.22 | 23.96 | 29.51 | 11.99 | 5.03 | 21.99
PETERHEAD | 275 | 37.6 | 15.14 | 6.78 | 28.19 | 33.42 | 13.57 | 5.8 | 24.99
ROTHIENORMAN | 275 | 48.42 | 19.15 | 10.66 | 37.74 | 43.44 | 17.56 | 8 | 32.83
SPITTAL | 275 | 22.29 | 8.72 | 5.86 | 18.19 | 25.08 | 9.76 | 6.65 | 20.45
STRATHBRORA | 275 | 23.27 | 9.26 | 4.2 | 17.29 | 21.69 | 8.72 | 4.06 | 16.39
TEALING | 275 | 47.6 | 19.28 | 6.9 | 34.17 | 39.82 | 16.4 | 5.57 | 28.77
THURSO SOUTH | 275 | 21.35 | 8.36 | 5.38 | 17.2 | 23.09 | 9.04 | 5.63 | 18.41
TOMATIN | 275 | 30.11 | 11.93 | 5.45 | 22.32 | 26.3 | 10.53 | 4.85 | 19.75
TUMMEL | 275 | 26.96 | 10.56 | 5.34 | 20.26 | 22.86 | 9.11 | 4.45 | 17.34
ABERARDER | 132 | 14.5 | 5.6 | 2.13 | 10.05 | 15.18 | 5.93 | 2.23 | 10.62
ABERDEEN BAY | 132 | 19.14 | 7.99 | 1.83 | 13.12 | 17.51 | 7.35 | 1.58 | 11.97
ABERNETHY | 132 | 15.5 | 7.67 | 0.23 | 11.08 | 16.46 | 7.73 | 0.67 | 11.61
A-CHRUACH | 132 | 21.23 | 9.15 | 1.48 | 14.42 | 20.48 | 8.63 | 1.91 | 14.12
AIGAS | 132 | 34.83 | 16.32 | 0.42 | 23.5 | 31.56 | 14.98 | 0.46 | 21.65
ALNESS | 132 | 35.31 | 13.72 | 4.94 | 24.34 | 38.77 | 15.24 | 4.9 | 26.45
AN SUIDHE | 132 | 24.17 | 10.67 | 1.18 | 16.26 | 22.05 | 9.51 | 1.5 | 14.95
ARBROATH | 132 | 13.59 | 6.38 | 0.39 | 9.41 | 12.6 | 5.73 | 0.71 | 8.82
ARDKINGLAS | 132 | 29.22 | 14.01 | 0.29 | 20.1 | 25.04 | 11.78 | 0.63 | 17.3
ARDMORE | 132 | 5.84 | 2.59 | 0.92 | 4.58 | 6.79 | 2.96 | 1.09 | 5.28
BEAULY | 132 | 58.04 | 24.37 | 6.04 | 40.5 | 65.23 | 27.1 | 7.48 | 45.8
BEINNEUN | 132 | 18.55 | 8.54 | 0.9 | 12.97 | 19.57 | 8.78 | 1.46 | 13.87
BHLARAIDH | 132 | 19.03 | 8.57 | 1.17 | 13.29 | 19.72 | 8.83 | 1.76 | 14.25
BLACKHILLOCK | 132 | 40.62 | 15.35 | 8.81 | 30.52 | 44.8 | 17.11 | 8.78 | 32.97
BOAT OF GARTEN | 132 | 15.44 | 6.58 | 0.74 | 10.03 | 14.98 | 6.33 | 1.04 | 9.99
BRECHIN | 132 | 13 | 6.46 | 0.17 | 9.31 | 13.11 | 6.17 | 0.28 | 9.01
BRIDGE OF DUN | 132 | 10.82 | 5.48 | 0.13 | 7.87 | 11.41 | 5.42 | 0.3 | 7.97
BROADFORD | 132 | 6.24 | 3.15 | 0.06 | 4.52 | 6.32 | 3 | 0.25 | 4.5
BRORA | 132 | 12.74 | 6.29 | 0.04 | 8.93 | 12.34 | 5.87 | 0.24 | 8.54
BURGHMUIR | 132 | 12.48 | 6.34 | 0.05 | 9.01 | 13.77 | 6.6 | 0.24 | 9.56
CARRADALE | 132 | 18.88 | 7.77 | 1.9 | 12.88 | 20.07 | 8.13 | 2.56 | 14.06
CASSLEY | 132 | 7.36 | 3.65 | 0.21 | 5.38 | 6.91 | 3.3 | 0.27 | 4.93
CEANNACROC | 132 | 17.72 | 8.22 | 0.75 | 12.38 | 18.43 | 8.34 | 1.18 | 12.98
CHARLESTON | 132 | 40.55 | 17.14 | 3.92 | 28.16 | 44.32 | 18.87 | 4.38 | 31.06
CLACHAN | 132 | 28.46 | 13.59 | 0.56 | 19.78 | 24.83 | 11.7 | 0.84 | 17.39
CLAYHILLS | 132 | 37.87 | 15.93 | 3.02 | 25.55 | 44.46 | 19.18 | 2.83 | 29.95
CLUNIE | 132 | 21.06 | 9.73 | 0.43 | 14.19 | 19.8 | 8.98 | 0.79 | 13.49
CONNAGILL | 132 | 17.23 | 6.46 | 4.11 | 13.25 | 19.79 | 7.48 | 4.16 | 14.74
CORRIEGARTH | 132 | 11.66 | 4.62 | 1.56 | 8.09 | 12.11 | 4.77 | 1.85 | 8.6
CORRIEMOILLIE | 132 | 29.8 | 12.14 | 3.15 | 20.32 | 31.16 | 12.69 | 3.45 | 21.41
COUPAR ANGUS | 132 | 22.75 | 9.95 | 1.11 | 15.18 | 21.49 | 9.15 | 1.8 | 14.74
CRAIGIEBUCKLER | 132 | 41.54 | 17.17 | 3.98 | 28.27 | 49.73 | 20.83 | 3.96 | 33.41
CROSSAIG | 132 | 28 | 11.7 | 2.89 | 19.43 | 32.24 | 13.36 | 3.35 | 22.24
CULLIGRAN | 132 | 18.28 | 9.05 | 0.19 | 12.99 | 16.61 | 7.97 | 0.35 | 11.61
DEANIE | 132 | 12.73 | 6.44 | 0.09 | 9.2 | 11.82 | 5.69 | 0.21 | 8.26
DORENELL | 132 | 15.87 | 6.62 | 1.38 | 10.75 | 16.75 | 6.82 | 1.96 | 11.61
DOUNREAY | 132 | 21.33 | 8.06 | 4.84 | 16.23 | 27.2 | 10.32 | 5.77 | 20.37
DUDHOPE | 132 | 36.8 | 15.95 | 2.43 | 24.99 | 39 | 17.42 | 2.05 | 26.68
DUNBEATH | 132 | 12.35 | 5.91 | 0.12 | 8.48 | 11.37 | 5.37 | 0.29 | 7.89
DUNMAGLASS | 132 | 15.66 | 5.96 | 3.02 | 11.44 | 17.12 | 6.59 | 3.13 | 12.46
DUNOON | 132 | 9.72 | 5.05 | 0.09 | 7.23 | 9.38 | 4.59 | 0.16 | 6.65
DUNVEGAN | 132 | 6.6 | 2.91 | 0.73 | 4.85 | 8.04 | 3.5 | 0.96 | 5.91
DYCE | 132 | 24.31 | 10.28 | 2.09 | 16.62 | 22.45 | 9.52 | 2.03 | 15.49
EDINBANE | 132 | 6.76 | 3.02 | 0.65 | 4.92 | 8.13 | 3.56 | 0.89 | 5.93
ELGIN | 132 | 14 | 6.8 | 0.27 | 9.88 | 13.28 | 6.25 | 0.61 | 9.45
ERROCHTY | 132 | 44.69 | 18.47 | 6.45 | 32.58 | 45.34 | 19.01 | 5.4 | 32.28
FARIGAIG I | 132 | 14.87 | 5.7 | 2.43 | 10.49 | 16.17 | 6.19 | 2.73 | 11.49
FARIGAIG II | 132 | 17.66 | 6.56 | 4.49 | 13.77 | 21.07 | 7.88 | 4.85 | 16
FARR | 132 | 23.21 | 10.19 | 0.63 | 15.04 | 21.86 | 9.66 | 0.97 | 14.63
FERNOCH | 132 | 13.22 | 6.66 | 1.36 | 10.78 | 14.69 | 6.99 | 1.66 | 11.56
FETTERESSO | 132 | 22.6 | 8.71 | 3.46 | 15.78 | 25.16 | 9.69 | 3.9 | 17.61
FIDDES | 132 | 14.69 | 7.18 | 0.74 | 10.9 | 15.16 | 6.95 | 1.17 | 11.01
FINLARIG | 132 | 21.33 | 10.23 | 0.7 | 15.16 | 21.35 | 9.89 | 0.96 | 14.94
FORT AUGUSTUS I | 132 | 47.79 | 18.28 | 9.59 | 35.45 | 57.2 | 21.97 | 10.77 | 41.84
FORT AUGUSTUS II | 132 | 41.57 | 15.83 | 8.13 | 30.52 | 48.03 | 18.52 | 8.22 | 34.41
FORT WILLIAM | 132 | 9.89 | 4.65 | 1.27 | 7.84 | 10.31 | 4.69 | 1.43 | 8.06
FRASERBURGH | 132 | 12.08 | 5.53 | 0.4 | 8.23 | 12.25 | 5.53 | 0.7 | 8.51
FYRISH | 132 | 38.09 | 14.54 | 7.01 | 27.58 | 42 | 16.05 | 7.83 | 30.53
GLEN KYLLACHY | 132 | 30.1 | 12.92 | 1 | 19.28 | 35.6 | 15.04 | 1.58 | 22.86
GLENDOE | 132 | 38.59 | 15.75 | 3.23 | 25.5 | 43.54 | 18.23 | 3.27 | 29.05
GLENFARCLAS | 132 | 7.53 | 3.53 | 0.26 | 5.25 | 7.35 | 3.31 | 0.44 | 5.12
GLENMORISTON | 132 | 20.82 | 9.4 | 1.23 | 14.53 | 21.33 | 9.52 | 1.75 | 15.22
GRIFFIN | 132 | 16.79 | 8.1 | 0.51 | 11.96 | 16.8 | 7.81 | 1.06 | 12.1
GRUDIE BRIDGE | 132 | 23.26 | 9.73 | 1.67 | 15.43 | 23.66 | 9.87 | 2.04 | 16
INVERARAY | 132 | 36.15 | 16.6 | 1.5 | 24.97 | 33.34 | 15.19 | 1.27 | 22.75
INVERARNAN | 132 | 52.93 | 22.46 | 5.01 | 36.77 | 55.02 | 23.14 | 5.11 | 37.84
INVERGARRY | 132 | 19.54 | 9.26 | 0.25 | 13.35 | 18.6 | 8.74 | 0.38 | 12.74
INVERNESS | 132 | 48.67 | 20.36 | 4.38 | 33.17 | 53.65 | 22.36 | 4.99 | 36.61
KEITH | 132 | 32.15 | 12.89 | 6.61 | 24.84 | 40.86 | 16.82 | 7.76 | 31.54
KILLIN | 132 | 24.4 | 11.53 | 1.05 | 17.36 | 25.56 | 11.59 | 1.57 | 17.96
KILMORACK | 132 | 47.67 | 21.02 | 2.05 | 31.78 | 48.52 | 21.44 | 1.96 | 32.29
KINLOCHLEVEN | 132 | 6.68 | 3.15 | 0.64 | 5.1 | 6.98 | 3.15 | 0.78 | 5.23
KINTORE | 132 | 44.35 | 17.74 | 7.11 | 32.2 | 52.45 | 21.05 | 7.81 | 37.57
KNOCKNAGAEL | 132 | 53.9 | 22.16 | 6.69 | 38.03 | 59.2 | 24.07 | 7.9 | 41.95
LAIRG | 132 | 16.13 | 7.6 | 0.47 | 11.22 | 15.66 | 7.21 | 0.83 | 11.02
LOCH BUIDHE | 132 | 31.75 | 13.17 | 5.05 | 23.67 | 36.8 | 15.18 | 5.55 | 27.01
LOCHAY | 132 | 20.9 | 10.05 | 0.65 | 14.86 | 20.58 | 9.58 | 0.86 | 14.41
LUICHART | 132 | 29.82 | 12.23 | 2.72 | 20.01 | 29.4 | 12.06 | 2.75 | 19.81
LUNANHEAD | 132 | 17.19 | 7.44 | 0.94 | 11.46 | 16.11 | 6.87 | 1.47 | 11.18
LYNDHURST | 132 | 32.53 | 14.45 | 1.38 | 21.82 | 33.22 | 14.84 | 1.6 | 22.58
MACDUFF | 132 | 9.64 | 4.51 | 0.58 | 6.95 | 9.65 | 4.36 | 0.76 | 6.93
MELGARVE | 132 | 38.84 | 14.61 | 8.3 | 28.96 | 46.03 | 17.46 | 8.72 | 33.41
MILLENNIUM | 132 | 20.59 | 9.37 | 0.78 | 14.03 | 21.49 | 9.64 | 1.15 | 14.79
MILTON OF CRAIGIE | 132 | 39.22 | 16.62 | 3.93 | 27.44 | 42.13 | 18.22 | 3.65 | 29.42
MOSSFORD | 132 | 26.45 | 10.95 | 2.21 | 17.69 | 27.47 | 11.35 | 2.55 | 18.6
MYBSTER I | 132 | 19.11 | 8.11 | 1.71 | 13.19 | 20.19 | 8.73 | 1.08 | 13.42
MYBSTER II | 132 | 19.94 | 7.55 | 4.51 | 15.19 | 22.66 | 8.57 | 5.14 | 17.27
NAIRN | 132 | 12.77 | 6.39 | 0.15 | 9.19 | 11.77 | 5.64 | 0.39 | 8.37
NANT | 132 | 11.83 | 6.2 | 0.27 | 9.04 | 10.84 | 5.34 | 0.39 | 7.94
ORRIN | 132 | 32.7 | 13.5 | 2.82 | 21.92 | 32.44 | 13.38 | 2.89 | 21.82
PERSLEY | 132 | 40.45 | 16.73 | 4.54 | 28.19 | 49.76 | 20.63 | 5.34 | 34.51
PETERHEAD | 132 | 30.46 | 11.74 | 5.79 | 22.39 | 37.15 | 14.44 | 6.19 | 26.61
PETERHEAD GRANGE | 132 | 21.36 | 8.88 | 1.43 | 13.99 | 22.7 | 9.55 | 1.64 | 15.14
PORT ANN | 132 | 15.26 | 6.76 | 0.77 | 10.34 | 12.38 | 5.4 | 0.67 | 8.3
QUOICH | 132 | 13.94 | 6.29 | 0.32 | 9.21 | 11.79 | 5.18 | 0.51 | 7.84
RANNOCH | 132 | 12.19 | 5.89 | 0.71 | 9.04 | 11.61 | 5.37 | 1.06 | 8.65
REDMOSS | 132 | 34.83 | 15.03 | 1.85 | 23.11 | 39.16 | 17.44 | 1.71 | 26.38
SHIN | 132 | 27.08 | 11.97 | 1.26 | 18.2 | 27.33 | 11.99 | 2.08 | 19.04
SLOY | 132 | 49.02 | 21.65 | 2.13 | 32.75 | 49.64 | 21.89 | 2.38 | 33.33
SPITTAL | 132 | 22.59 | 9.11 | 4.94 | 17.83 | 27.81 | 11.12 | 5.94 | 21.67
ST FERGUS GAS TERMINAL | 132 | 21.4 | 9.03 | 1.21 | 13.99 | 22 | 9.53 | 0.92 | 14.39
ST FERGUS MOBIL | 132 | 20.27 | 8.82 | 0.63 | 13.11 | 20.68 | 9.33 | 0.57 | 13.76
ST FILLIANS | 132 | 10.13 | 5.06 | 0.27 | 7.42 | 9.07 | 4.38 | 0.32 | 6.51
STRATHY NORTH | 132 | 13.06 | 5.14 | 1.78 | 9.05 | 13.54 | 5.32 | 2.2 | 9.73
STRICHEN | 132 | 13.25 | 5.98 | 0.68 | 9.14 | 13.28 | 5.94 | 1.01 | 9.41
STRONELAIRG | 132 | 33.52 | 12.68 | 6.57 | 24.5 | 39.39 | 15.3 | 6.94 | 28.58
TARLAND | 132 | 8.63 | 4.25 | 0.1 | 6.1 | 8.23 | 3.84 | 0.2 | 5.64
TAYNUILT | 132 | 11.24 | 5.78 | 0.86 | 9.04 | 10.97 | 5.31 | 1.16 | 8.66
TEALING | 132 | 44.87 | 18.51 | 6.69 | 32.87 | 48.9 | 20.4 | 5.7 | 34.55
THURSO SOUTH | 132 | 30.89 | 11.74 | 7.26 | 23.86 | 36.66 | 13.93 | 8.36 | 28.06
TOMATIN | 132 | 41.4 | 15.82 | 7.59 | 29.97 | 45.4 | 17.55 | 7.37 | 32.18
TUMMEL | 132 | 32.25 | 12.69 | 5.68 | 23.63 | 32.36 | 13.34 | 4.5 | 23.36
TUMMEL BRIDGE | 132 | 39.84 | 16.95 | 3.72 | 27.69 | 38.58 | 16.72 | 2.79 | 26.43
WILLOWDALE | 132 | 39.5 | 16.47 | 3.68 | 26.97 | 47.73 | 20.13 | 3.9 | 32.37
WOODHILL | 132 | 39.16 | 16.45 | 3.23 | 26.5 | 46.91 | 19.95 | 3.37 | 31.59
ABERNETHY | 33 | 29.74 | 12.05 | 2.07 | 19.12 | 2.16 | 1.5 | 0 | 2.11
ALNESS | 33 | 53.78 | 20.84 | 9.3 | 38.77 | 2.18 | 1.51 | 0 | 2.13
ARBROATH | 33 | 27.06 | 10.67 | 2.59 | 17.67 | 1.54 | 1.07 | 0 | 1.51
ARDMORE | 33 | 22.68 | 9.16 | 4.18 | 17.13 | 1.08 | 0.75 | 0 | 1.06
BEAULY | 33 | 33.92 | 13 | 5.43 | 23.82 | 1.46 | 1.01 | 0 | 1.43
BERRY BURN | 33 | 41.48 | 15.49 | 7.68 | 29.59 | 1.1 | 0.76 | 0 | 1.08
BOAT OF GARTEN | 33 | 34.05 | 13.34 | 3.55 | 22.42 | 2.18 | 1.51 | 0 | 2.14
BRACO WEST | 33 | 58.77 | 22.51 | 10.36 | 42.2 | 2.21 | 1.53 | 0 | 2.16
BRIDGE OF DUN | 33 | 23.45 | 9.74 | 1.05 | 14.83 | 2.15 | 1.49 | 0 | 2.11
BROADFORD | 33 | 9.99 | 4.07 | 0.64 | 6.39 | 0.75 | 0.52 | 0 | 0.74
BRORA | 33 | 14.39 | 5.75 | 0.81 | 8.94 | 1.1 | 0.76 | 0 | 1.08
BURGHMUIR | 33 | 23.7 | 9.99 | 0.66 | 14.79 | 2.16 | 1.5 | 0 | 2.12
CAIRNFORD | 33 | 33.37 | 12.46 | 6.83 | 24.45 | 1.11 | 0.77 | 0 | 1.09
CARRADALE I | 33 | 39.35 | 15.55 | 5.75 | 27.74 | 2.15 | 1.49 | 0 | 2.1
CARRADALE II | 33 | 52.02 | 20.26 | 5.76 | 34.42 | 2.17 | 1.5 | 0 | 2.13
CASSLEY | 33 | 13.09 | 5.14 | 1.73 | 8.99 | 1.09 | 0.76 | 0 | 1.07
CEANNACROC | 33 | 3.46 | 1.35 | 0.36 | 2.27 | 3.37 | 1.33 | 0.26 | 2.15
CHARLESTON | 33 | 31.43 | 11.76 | 7.36 | 23.99 | 1.59 | 1.1 | 0 | 1.56
CLACHAN | 33 | 7.42 | 2.77 | 1.68 | 5.59 | 6.36 | 2.4 | 1.04 | 4.44
CLAYHILLS | 33 | 32.65 | 12.49 | 4.99 | 22.66 | 3.05 | 2.11 | 0 | 2.99
COUPAR ANGUS | 33 | 44.28 | 16.94 | 8.96 | 32.92 | 2.17 | 1.5 | 0 | 2.13
CRAIGIEBUCKLER | 33 | 27.15 | 10.62 | 2.54 | 17.56 | 1.54 | 1.07 | 0 | 1.51
DALLAS | 33 | 41.07 | 15.39 | 7.4 | 29.17 | 1.1 | 0.77 | 0 | 1.08
DOUNREAY | 33 | 40.12 | 15.02 | 8.2 | 29.45 | 2.21 | 1.53 | 0 | 2.16
DUDHOPE | 33 | 34.45 | 13.24 | 5.44 | 24.16 | 2.92 | 2.02 | 0 | 2.86
DUNBEATH | 33 | 12.54 | 4.89 | 1.1 | 8.02 | 0.4 | 0.28 | 0 | 0.39
DUNOON | 33 | 28.7 | 12.58 | 0.55 | 18.34 | 2.14 | 1.48 | 0 | 2.1
DUNVEGAN | 33 | 17.22 | 7.08 | 1.49 | 11.51 | 1.09 | 0.75 | 0 | 1.07
DYCE | 33 | 38.69 | 14.61 | 7.55 | 28.22 | 2.19 | 1.52 | 0 | 2.14
ELGIN | 33 | 29.84 | 12.13 | 1.74 | 18.89 | 1.84 | 1.28 | 0 | 1.81
FASNAKYLE | 33 | 55.78 | 20.57 | 13.14 | 42.22 | 2.2 | 1.53 | 0 | 2.16
FETTERESSO | 33 | 30.89 | 11.59 | 6.31 | 22.7 | 1.1 | 0.76 | 0 | 1.08
FIDDES | 33 | 37.32 | 15.02 | 3.88 | 25.13 | 2.18 | 1.51 | 0 | 2.14
FORT AUGUSTUS | 33 | 20.03 | 7.54 | 3.37 | 14.04 | 1.1 | 0.76 | 0 | 1.08
FORT WILLIAM | 33 | 40.49 | 16.03 | 6.14 | 28.81 | 0.88 | 0.61 | 0 | 0.86
FRASERBURGH | 33 | 24.15 | 9.52 | 2.02 | 15.48 | 2.17 | 1.51 | 0 | 2.13
GLENFARCLAS | 33 | 21.81 | 8.8 | 1.05 | 13.49 | 1.09 | 0.76 | 0 | 1.07
GRUDIE BRIDGE | 33 | 39.15 | 14.59 | 8.57 | 29.21 | 2.19 | 1.52 | 0 | 2.14
INVERNESS | 33 | 55.29 | 21.63 | 7.8 | 38.39 | 3.26 | 2.26 | 0 | 3.2
KEITH I | 33 | 49.72 | 18.66 | 12.75 | 39.15 | 2.21 | 1.53 | 0 | 2.17
KEITH II | 33 | 39.7 | 14.95 | 8.02 | 29.15 | 2.21 | 1.53 | 0 | 2.17
KILLIN | 33 | 35.42 | 13.88 | 4.34 | 23.97 | 2.16 | 1.5 | 0 | 2.12
KINLOCHLEVEN | 33 | 16.12 | 6.44 | 2.22 | 11.34 | 0.73 | 0.5 | 0 | 0.71
KINTORE | 33 | 47.55 | 18.02 | 9.67 | 35.15 | 3.27 | 2.26 | 0 | 3.2
LAIRG | 33 | 24.97 | 9.76 | 2.54 | 16.34 | 1.1 | 0.76 | 0 | 1.08
LUNANHEAD | 33 | 32.46 | 12.65 | 4.88 | 22.77 | 2.19 | 1.52 | 0 | 2.15
LYNDHURST | 33 | 32.66 | 12.58 | 4.55 | 22.34 | 2.95 | 2.04 | 0 | 2.89
MACDUFF | 33 | 39.42 | 16.08 | 3.29 | 26.04 | 2.21 | 1.53 | 0 | 2.17
MILTON OF CRAIGIE | 33 | 35.43 | 13.54 | 6.48 | 25.63 | 3.32 | 2.3 | 0 | 3.26
MYBSTER I | 33 | 47.01 | 17.71 | 9.66 | 34.7 | 2.2 | 1.53 | 0 | 2.16
MYBSTER II | 33 | 49.09 | 18.54 | 9.88 | 36.1 | 2.2 | 1.53 | 0 | 2.16
MYBSTER III | 33 | 34.98 | 12.96 | 8.6 | 26.93 | 2.21 | 1.53 | 0 | 2.17
NAIRN | 33 | 25.68 | 10.47 | 1.06 | 15.87 | 3.03 | 2.1 | 0 | 2.97
PERSLEY | 33 | 32.75 | 12.27 | 8.09 | 25.44 | 2.19 | 1.52 | 0 | 2.15
PETERHEAD GRANGE | 33 | 28.41 | 11.18 | 3.29 | 19.1 | 0.59 | 0.41 | 0 | 0.58
PORT ANN | 33 | 32.22 | 12.73 | 4.49 | 22.49 | 1.85 | 1.29 | 0 | 1.82
RANNOCH | 33 | 39.08 | 15.32 | 4.19 | 25.87 | 2.18 | 1.51 | 0 | 2.13
REDMOSS | 33 | 38.86 | 15.4 | 5.08 | 26.86 | 3.02 | 2.09 | 0 | 2.96
ROTHIENORMAN | 33 | 62.51 | 23.55 | 15.77 | 49.08 | 2.2 | 1.52 | 0 | 2.15
SHIN | 33 | 32.48 | 12.56 | 4.4 | 22.16 | 2.19 | 1.52 | 0 | 2.14
ST FILLIANS | 33 | 6.69 | 2.43 | 2.34 | 5.78 | 6.81 | 2.46 | 2.59 | 6.06
STRICHEN | 33 | 32.79 | 12.52 | 5.21 | 22.91 | 2.19 | 1.52 | 0 | 2.15
TARLAND | 33 | 20.32 | 8.53 | 0.68 | 12.74 | 1.52 | 1.06 | 0 | 1.49
TAYNUILT | 33 | 35.19 | 13.89 | 5.22 | 24.86 | 2.19 | 1.52 | 0 | 2.14
THURSO SOUTH | 33 | 64.19 | 23.86 | 19.63 | 53.37 | 2.19 | 1.52 | 0 | 2.15
TUMMEL BRIDGE | 33 | 10.46 | 3.78 | 4.56 | 9.91 | 1.13 | 0.79 | 0 | 1.11
WILLOWDALE | 33 | 32.95 | 12.66 | 4.92 | 22.82 | 3.04 | 2.11 | 0 | 2.98
WOODHILL | 33 | 31.92 | 12.05 | 6.61 | 23.65 | 4.5 | 3.12 | 0 | 4.41

## D1.4
ETYS 19 Yr 4 - SHE Transmission Fault Levels (kA), Winter 2022/23
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 28.61 | 11.01 | 6.81 | 22.38 | 28.33 | 10.97 | 6.67 | 22.18 | Back To Menu
BLACKHILLOCK | 400 | 31.74 | 12.18 | 8.82 | 26.04 | 32.67 | 12.56 | 8.71 | 26.48
FORT AUGUSTUS | 400 | 26.47 | 10.19 | 6.19 | 20.6 | 27.76 | 10.7 | 6.72 | 21.85
MELGARVE | 400 | 23.94 | 9.2 | 5.6 | 18.6 | 23.83 | 9.23 | 5.36 | 18.42
BEAULY | 275 | 56.36 | 22.24 | 11.31 | 42.77 | 56.91 | 22.64 | 10.89 | 42.91
BERRY BURN | 275 | 31.86 | 13.01 | 4.16 | 22.56 | 24.88 | 10.31 | 3.29 | 17.87
BLACKHILLOCK I | 275 | 53 | 21.05 | 11.68 | 41.44 | 55.61 | 22.12 | 11.94 | 43.22
BLACKHILLOCK II | 275 | 32.72 | 12.68 | 8.69 | 26.62 | 35.55 | 13.9 | 8.35 | 28
BRACO WEST | 275 | 35.38 | 13.9 | 6.49 | 26.15 | 28.4 | 11.32 | 5.25 | 21.26
CAIRNFORD | 275 | 42.83 | 17.29 | 7.38 | 31.83 | 39.35 | 16.13 | 5.81 | 28.62
CONNAGILL | 275 | 21.91 | 8.62 | 4.83 | 17.02 | 22.17 | 8.81 | 4.38 | 16.84
DALLAS | 275 | 32.85 | 13.39 | 4.48 | 23.42 | 26.2 | 10.83 | 3.57 | 18.89
DOUNREAY | 275 | 24.27 | 9.49 | 5.99 | 19.41 | 26.44 | 10.34 | 6.37 | 20.99
FARIGAIG I | 275 | 42.05 | 16.86 | 7.3 | 31.14 | 33.51 | 13.72 | 5.36 | 24.77
FARIGAIG II | 275 | 42.28 | 16.94 | 7.43 | 31.38 | 33.93 | 13.87 | 5.59 | 25.21
FASNAKYLE | 275 | 36.11 | 14.11 | 7.39 | 27.34 | 32.11 | 12.73 | 6.08 | 24.08
FETTERESSO | 275 | 39.84 | 16.14 | 6.09 | 28.91 | 31.85 | 13.1 | 4.6 | 23.13
FORT AUGUSTUS | 275 | 30.97 | 12.05 | 6.53 | 23.57 | 28.89 | 11.28 | 6.41 | 22.36
FOYERS | 275 | 41.86 | 16.72 | 7.8 | 31.44 | 29.09 | 12.09 | 3.92 | 21.02
FYRISH | 275 | 29.98 | 11.95 | 5.1 | 22 | 27.15 | 10.93 | 4.9 | 20.36
GORDONBUSH | 275 | 21.59 | 8.59 | 3.89 | 16.03 | 19.98 | 8.04 | 3.64 | 15.01
KEITH | 275 | 50.5 | 20.2 | 10.28 | 38.85 | 53.05 | 21.3 | 10.28 | 40.41
KINTORE | 275 | 54.02 | 21.61 | 10.82 | 41.38 | 51.01 | 20.65 | 9.22 | 38.43
KNOCKNAGAEL | 275 | 56.19 | 22.3 | 10.81 | 42.36 | 52.5 | 21.1 | 9.69 | 39.53
LOCH BUIDHE | 275 | 30.53 | 12.18 | 5.33 | 22.56 | 27.96 | 11.27 | 5.12 | 21.07
NEW DEER | 275 | 39.6 | 15.76 | 8.15 | 30.44 | 30.6 | 12.59 | 4.32 | 22.13
PERSLEY | 275 | 31.75 | 12.87 | 5.06 | 23.25 | 28.56 | 11.61 | 4.87 | 21.28
PETERHEAD | 275 | 36.37 | 14.64 | 6.55 | 27.26 | 32.21 | 13.08 | 5.58 | 24.08
ROTHIENORMAN | 275 | 46.99 | 18.58 | 10.37 | 36.64 | 42.03 | 16.98 | 7.78 | 31.8
SPITTAL | 275 | 22.99 | 8.98 | 6.03 | 18.73 | 25.77 | 10.02 | 6.79 | 20.97
STRATHBRORA | 275 | 23.48 | 9.35 | 4.18 | 17.4 | 21.76 | 8.75 | 4.04 | 16.41
TEALING | 275 | 50.03 | 20.16 | 8.05 | 36.56 | 41.31 | 16.94 | 6.21 | 30.17
THURSO SOUTH | 275 | 22.09 | 8.63 | 5.56 | 17.77 | 23.83 | 9.32 | 5.79 | 18.97
TOMATIN | 275 | 29.8 | 11.81 | 5.37 | 22.07 | 26 | 10.42 | 4.79 | 19.52
TUMMEL | 275 | 26.67 | 10.44 | 5.26 | 20.03 | 22.57 | 9 | 4.39 | 17.11
ABERARDER | 132 | 14.35 | 5.55 | 2.1 | 9.95 | 15.03 | 5.87 | 2.21 | 10.51
ABERDEEN BAY | 132 | 18.7 | 7.8 | 1.78 | 12.81 | 17.12 | 7.19 | 1.54 | 11.71
ABERNETHY | 132 | 15.41 | 7.63 | 0.23 | 11.02 | 16.28 | 7.64 | 0.68 | 11.48
A-CHRUACH | 132 | 21.2 | 9.15 | 1.47 | 14.4 | 20.42 | 8.61 | 1.9 | 14.08
AIGAS | 132 | 34.51 | 16.18 | 0.4 | 23.29 | 31.25 | 14.84 | 0.46 | 21.45
ALNESS | 132 | 35.12 | 13.65 | 4.89 | 24.19 | 38.54 | 15.15 | 4.86 | 26.28
AN SUIDHE | 132 | 24.07 | 10.63 | 1.17 | 16.2 | 21.94 | 9.47 | 1.49 | 14.88
ARBROATH | 132 | 13.45 | 6.32 | 0.38 | 9.32 | 12.43 | 5.66 | 0.69 | 8.7
ARDKINGLAS | 132 | 29.11 | 13.97 | 0.28 | 20.04 | 24.92 | 11.73 | 0.63 | 17.22
ARDMORE | 132 | 5.8 | 2.57 | 0.91 | 4.55 | 6.74 | 2.94 | 1.09 | 5.25
BEAULY | 132 | 57.77 | 24.26 | 6.01 | 40.31 | 64.91 | 26.96 | 7.44 | 45.58
BEINNEUN | 132 | 18.42 | 8.48 | 0.89 | 12.88 | 19.43 | 8.71 | 1.45 | 13.78
BHLARAIDH | 132 | 18.97 | 8.55 | 1.16 | 13.25 | 19.65 | 8.8 | 1.75 | 14.2
BLACKHILLOCK | 132 | 39.48 | 14.92 | 8.55 | 29.66 | 43.49 | 16.61 | 8.51 | 32.01
BOAT OF GARTEN | 132 | 15.21 | 6.47 | 0.73 | 9.89 | 14.8 | 6.24 | 1.04 | 9.87
BRECHIN | 132 | 12.86 | 6.39 | 0.18 | 9.21 | 12.97 | 6.11 | 0.28 | 8.91
BRIDGE OF DUN | 132 | 10.71 | 5.42 | 0.13 | 7.79 | 11.29 | 5.36 | 0.3 | 7.89
BROADFORD | 132 | 6.19 | 3.13 | 0.06 | 4.49 | 6.27 | 2.98 | 0.25 | 4.47
BRORA | 132 | 12.67 | 6.26 | 0.04 | 8.89 | 12.26 | 5.84 | 0.23 | 8.49
BURGHMUIR | 132 | 12.39 | 6.29 | 0.05 | 8.94 | 13.56 | 6.49 | 0.24 | 9.42
CARRADALE | 132 | 18.83 | 7.74 | 1.92 | 12.86 | 20.04 | 8.11 | 2.58 | 14.06
CASSLEY | 132 | 7.28 | 3.62 | 0.21 | 5.33 | 6.84 | 3.26 | 0.26 | 4.88
CEANNACROC | 132 | 17.59 | 8.17 | 0.74 | 12.29 | 18.3 | 8.29 | 1.17 | 12.89
CHARLESTON | 132 | 40.23 | 16.98 | 4.01 | 28.02 | 44.13 | 18.78 | 4.41 | 30.96
CLACHAN | 132 | 28.37 | 13.55 | 0.56 | 19.72 | 24.75 | 11.67 | 0.84 | 17.34
CLAYHILLS | 132 | 36.9 | 15.53 | 2.94 | 24.9 | 43.38 | 18.71 | 2.77 | 29.23
CLUNIE | 132 | 20.85 | 9.64 | 0.41 | 14.05 | 19.52 | 8.86 | 0.77 | 13.3
CONNAGILL | 132 | 17.35 | 6.5 | 4.16 | 13.35 | 19.89 | 7.51 | 4.19 | 14.81
CORRIEGARTH | 132 | 11.54 | 4.58 | 1.54 | 8.01 | 11.98 | 4.72 | 1.83 | 8.51
CORRIEMOILLIE | 132 | 29.62 | 12.06 | 3.15 | 20.21 | 31.03 | 12.64 | 3.44 | 21.3
COUPAR ANGUS | 132 | 22.56 | 9.86 | 1.11 | 15.06 | 21.33 | 9.08 | 1.8 | 14.64
CRAIGIEBUCKLER | 132 | 40.48 | 16.73 | 3.88 | 27.54 | 48.51 | 20.32 | 3.85 | 32.59
CROSSAIG | 132 | 28 | 11.69 | 2.91 | 19.44 | 32.17 | 13.32 | 3.36 | 22.2
CULLIGRAN | 132 | 18.09 | 8.96 | 0.19 | 12.86 | 16.48 | 7.9 | 0.35 | 11.52
DEANIE | 132 | 12.6 | 6.37 | 0.09 | 9.1 | 11.74 | 5.65 | 0.21 | 8.2
DORENELL | 132 | 15.45 | 6.45 | 1.34 | 10.47 | 16.31 | 6.64 | 1.91 | 11.3
DOUNREAY | 132 | 23.95 | 9.05 | 5.3 | 18.1 | 30.4 | 11.53 | 6.32 | 22.63
DUDHOPE | 132 | 36.5 | 15.81 | 2.48 | 24.83 | 38.7 | 17.29 | 2.05 | 26.51
DUNBEATH | 132 | 12.34 | 5.91 | 0.12 | 8.47 | 11.34 | 5.36 | 0.28 | 7.86
DUNMAGLASS | 132 | 15.52 | 5.9 | 2.99 | 11.34 | 16.97 | 6.53 | 3.1 | 12.34
DUNOON | 132 | 9.7 | 5.04 | 0.09 | 7.22 | 9.34 | 4.56 | 0.16 | 6.62
DUNVEGAN | 132 | 6.55 | 2.89 | 0.72 | 4.81 | 7.98 | 3.47 | 0.95 | 5.86
DYCE | 132 | 23.7 | 10.03 | 2.03 | 16.21 | 21.93 | 9.3 | 1.98 | 15.13
EDINBANE | 132 | 6.7 | 2.99 | 0.65 | 4.88 | 8.06 | 3.53 | 0.88 | 5.87
ELGIN | 132 | 13.7 | 6.65 | 0.27 | 9.67 | 13.04 | 6.13 | 0.61 | 9.28
ERROCHTY | 132 | 44.25 | 18.3 | 6.37 | 32.24 | 44.87 | 18.81 | 5.33 | 31.93
FARIGAIG I | 132 | 14.71 | 5.64 | 2.4 | 10.37 | 15.98 | 6.12 | 2.7 | 11.36
FARIGAIG II | 132 | 17.48 | 6.49 | 4.44 | 13.63 | 20.86 | 7.8 | 4.79 | 15.83
FARR | 132 | 22.83 | 10 | 0.64 | 14.78 | 21.57 | 9.51 | 0.97 | 14.42
FERNOCH | 132 | 13.14 | 6.63 | 1.31 | 10.69 | 14.54 | 6.93 | 1.61 | 11.41
FETTERESSO | 132 | 21.59 | 8.31 | 3.32 | 15.08 | 23.99 | 9.24 | 3.73 | 16.79
FIDDES | 132 | 14.45 | 7.06 | 0.74 | 10.73 | 14.92 | 6.84 | 1.16 | 10.83
FINLARIG | 132 | 21.24 | 10.19 | 0.7 | 15.11 | 21.24 | 9.83 | 0.96 | 14.87
FORT AUGUSTUS I | 132 | 48.38 | 18.52 | 9.57 | 35.77 | 58.16 | 22.35 | 10.86 | 42.47
FORT AUGUSTUS II | 132 | 41.48 | 15.8 | 8.11 | 30.45 | 47.91 | 18.47 | 8.2 | 34.33
FORT WILLIAM | 132 | 9.84 | 4.62 | 1.29 | 7.82 | 10.28 | 4.67 | 1.46 | 8.06
FRASERBURGH | 132 | 11.68 | 5.34 | 0.4 | 7.95 | 11.87 | 5.35 | 0.68 | 8.24
FYRISH | 132 | 37.91 | 14.47 | 6.96 | 27.41 | 41.77 | 15.96 | 7.77 | 30.35
GILLS BAY | 132 | 21.24 | 8.24 | 3.37 | 15.02 | 20.46 | 8.17 | 2.93 | 14.48
GLEN KYLLACHY | 132 | 29.47 | 12.62 | 1.02 | 18.86 | 34.81 | 14.68 | 1.59 | 22.36
GLENDOE | 132 | 38.85 | 15.9 | 3.12 | 25.6 | 43.86 | 18.43 | 3.13 | 29.19
GLENFARCLAS | 132 | 7.42 | 3.48 | 0.25 | 5.17 | 7.21 | 3.25 | 0.42 | 5.02
GLENMORISTON | 132 | 20.75 | 9.38 | 1.22 | 14.48 | 21.25 | 9.49 | 1.74 | 15.16
GRIFFIN | 132 | 16.66 | 8.04 | 0.5 | 11.87 | 16.64 | 7.73 | 1.06 | 11.99
GRUDIE BRIDGE | 132 | 23.09 | 9.66 | 1.67 | 15.33 | 23.54 | 9.82 | 2.04 | 15.92
INVERARAY | 132 | 36.06 | 16.57 | 1.49 | 24.92 | 33.23 | 15.15 | 1.26 | 22.68
INVERARNAN | 132 | 52.95 | 22.45 | 5.05 | 36.8 | 54.34 | 22.87 | 5.1 | 37.44
INVERGARRY | 132 | 19.51 | 9.26 | 0.24 | 13.34 | 18.54 | 8.72 | 0.37 | 12.71
INVERNESS | 132 | 48.16 | 20.16 | 4.31 | 32.82 | 53.01 | 22.11 | 4.9 | 36.18
KEITH | 132 | 31.37 | 12.58 | 6.47 | 24.26 | 39.85 | 16.4 | 7.58 | 30.77
KILLIN | 132 | 24.31 | 11.49 | 1.06 | 17.31 | 25.43 | 11.53 | 1.58 | 17.88
KILMORACK | 132 | 47.35 | 20.89 | 2.01 | 31.56 | 48.16 | 21.29 | 1.93 | 32.05
KINLOCHLEVEN | 132 | 6.63 | 3.12 | 0.64 | 5.05 | 6.91 | 3.12 | 0.77 | 5.18
KINTORE | 132 | 43.05 | 17.22 | 6.92 | 31.27 | 51.01 | 20.47 | 7.61 | 36.55
KNOCKNAGAEL | 132 | 53.37 | 21.96 | 6.58 | 37.64 | 58.53 | 23.81 | 7.78 | 41.46
LAIRG | 132 | 16 | 7.54 | 0.47 | 11.13 | 15.52 | 7.15 | 0.82 | 10.93
LIMEKILNS | 132 | 19.98 | 7.98 | 2.05 | 13.34 | 21.8 | 8.8 | 2.22 | 14.66
LOCH BUIDHE | 132 | 31.68 | 13.15 | 5.02 | 23.61 | 36.66 | 15.12 | 5.51 | 26.9
LOCHAY | 132 | 20.81 | 10.01 | 0.66 | 14.81 | 20.46 | 9.53 | 0.86 | 14.34
LUICHART | 132 | 29.58 | 12.13 | 2.7 | 19.86 | 29.24 | 11.99 | 2.75 | 19.71
LUNANHEAD | 132 | 17.05 | 7.37 | 0.94 | 11.36 | 15.9 | 6.78 | 1.45 | 11.04
LYNDHURST | 132 | 32.27 | 14.32 | 1.41 | 21.66 | 32.99 | 14.74 | 1.59 | 22.44
MACDUFF | 132 | 9.42 | 4.4 | 0.58 | 6.8 | 9.47 | 4.27 | 0.77 | 6.81
MELGARVE | 132 | 38.93 | 14.64 | 8.32 | 29.02 | 46.13 | 17.5 | 8.72 | 33.47
MILLENNIUM | 132 | 20.46 | 9.32 | 0.77 | 13.95 | 21.35 | 9.58 | 1.14 | 14.69
MILLENNIUM SOUTH | 132 | 31.86 | 13.14 | 1.98 | 20.57 | 30.66 | 12.68 | 2.23 | 20.17
MILTON OF CRAIGIE | 132 | 38.91 | 16.47 | 4.03 | 27.32 | 41.78 | 18.08 | 3.68 | 29.25
MOSSFORD | 132 | 26.27 | 10.87 | 2.21 | 17.58 | 27.34 | 11.29 | 2.55 | 18.51
MYBSTER I | 132 | 19.22 | 8.16 | 1.7 | 13.24 | 20.25 | 8.76 | 1.07 | 13.45
MYBSTER II | 132 | 20 | 7.57 | 4.54 | 15.24 | 22.67 | 8.57 | 5.14 | 17.26
NAIRN | 132 | 12.52 | 6.27 | 0.14 | 9.01 | 11.53 | 5.53 | 0.38 | 8.2
NANT | 132 | 11.77 | 6.18 | 0.26 | 9 | 10.79 | 5.31 | 0.39 | 7.9
ORRIN | 132 | 32.43 | 13.39 | 2.81 | 21.74 | 32.32 | 13.32 | 2.92 | 21.76
PERSLEY | 132 | 39.41 | 16.3 | 4.42 | 27.47 | 48.53 | 20.12 | 5.2 | 33.66
PETERHEAD | 132 | 28.97 | 11.17 | 5.52 | 21.31 | 35.34 | 13.74 | 5.89 | 25.33
PETERHEAD GRANGE | 132 | 20.49 | 8.5 | 1.41 | 13.44 | 21.87 | 9.18 | 1.61 | 14.6
PORT ANN | 132 | 15.18 | 6.73 | 0.77 | 10.28 | 12.3 | 5.36 | 0.66 | 8.25
QUOICH | 132 | 13.98 | 6.31 | 0.31 | 9.23 | 11.92 | 5.24 | 0.51 | 7.93
RANNOCH | 132 | 12.09 | 5.84 | 0.71 | 8.97 | 11.51 | 5.32 | 1.05 | 8.58
REDMOSS | 132 | 33.94 | 14.65 | 1.8 | 22.52 | 38.22 | 17.02 | 1.68 | 25.76
SHIN | 132 | 26.93 | 11.92 | 1.24 | 18.1 | 27.14 | 11.91 | 2.05 | 18.9
SLOY | 132 | 48.96 | 21.63 | 2.11 | 32.7 | 49.82 | 21.98 | 2.36 | 33.45
SPITTAL | 132 | 22.79 | 9.19 | 5 | 17.99 | 28.02 | 11.19 | 6 | 21.83
ST FERGUS GAS TERMINAL | 132 | 20.57 | 8.66 | 1.21 | 13.47 | 21.42 | 9.24 | 1.02 | 14.08
ST FERGUS MOBIL | 132 | 19.49 | 8.46 | 0.63 | 12.6 | 20.02 | 9.01 | 0.57 | 13.31
ST FILLIANS | 132 | 10.07 | 5.03 | 0.27 | 7.38 | 9.01 | 4.35 | 0.32 | 6.47
STRATHY NORTH | 132 | 13.1 | 5.16 | 1.77 | 9.06 | 13.55 | 5.33 | 2.19 | 9.73
STRICHEN | 132 | 12.81 | 5.77 | 0.67 | 8.84 | 12.87 | 5.75 | 0.99 | 9.12
STRONELAIRG | 132 | 33.6 | 12.7 | 6.59 | 24.56 | 39.51 | 15.34 | 7.02 | 28.71
TARLAND | 132 | 8.42 | 4.15 | 0.09 | 5.96 | 8.04 | 3.75 | 0.2 | 5.51
TAYNUILT | 132 | 11.19 | 5.76 | 0.86 | 9.01 | 10.92 | 5.28 | 1.15 | 8.62
TEALING | 132 | 44.52 | 18.33 | 6.92 | 32.85 | 48.63 | 20.25 | 5.91 | 34.55
THURSO SOUTH | 132 | 31.77 | 12.06 | 7.51 | 24.56 | 38.1 | 14.47 | 8.67 | 29.13
TOMATIN | 132 | 40.24 | 15.38 | 7.37 | 29.12 | 44.17 | 17.07 | 7.17 | 31.31
TUMMEL | 132 | 31.93 | 12.56 | 5.61 | 23.38 | 32.02 | 13.2 | 4.45 | 23.11
TUMMEL BRIDGE | 132 | 39.45 | 16.79 | 3.66 | 27.41 | 38.18 | 16.55 | 2.74 | 26.14
WILLOWDALE | 132 | 38.48 | 16.04 | 3.58 | 26.27 | 46.56 | 19.64 | 3.8 | 31.58
WOODHILL | 132 | 38.16 | 16.03 | 3.15 | 25.81 | 45.76 | 19.46 | 3.29 | 30.81
ABERNETHY | 33 | 29.65 | 12.01 | 2.08 | 19.07 | 2.15 | 1.49 | 0 | 2.11
ALNESS | 33 | 53.25 | 20.64 | 9.16 | 38.34 | 2.16 | 1.5 | 0 | 2.12
ARBROATH | 33 | 26.75 | 10.52 | 2.64 | 17.52 | 1.51 | 1.05 | 0 | 1.48
ARDMORE | 33 | 22.72 | 9.17 | 4.2 | 17.17 | 1.08 | 0.75 | 0 | 1.06
BEAULY | 33 | 33.88 | 12.98 | 5.41 | 23.78 | 1.46 | 1.01 | 0 | 1.43
BERRY BURN | 33 | 40.91 | 15.28 | 7.58 | 29.18 | 1.08 | 0.75 | 0 | 1.06
BOAT OF GARTEN | 33 | 33.62 | 13.17 | 3.51 | 22.14 | 2.16 | 1.5 | 0 | 2.12
BRACO WEST | 33 | 57.94 | 22.19 | 10.24 | 41.62 | 2.17 | 1.51 | 0 | 2.13
BRIDGE OF DUN | 33 | 23.19 | 9.63 | 1.05 | 14.67 | 2.12 | 1.47 | 0 | 2.08
BROADFORD | 33 | 9.91 | 4.03 | 0.64 | 6.34 | 0.75 | 0.52 | 0 | 0.73
BRORA | 33 | 14.28 | 5.71 | 0.8 | 8.87 | 1.09 | 0.75 | 0 | 1.07
BURGHMUIR | 33 | 23.51 | 9.88 | 0.68 | 14.66 | 2.12 | 1.47 | 0 | 2.08
CAIRNFORD | 33 | 32.28 | 12.05 | 6.59 | 23.63 | 1.08 | 0.75 | 0 | 1.06
CARRADALE I | 33 | 38.77 | 15.31 | 5.74 | 27.39 | 2.11 | 1.46 | 0 | 2.07
CARRADALE II | 33 | 51.4 | 20.05 | 5.58 | 33.93 | 2.16 | 1.5 | 0 | 2.12
CASSLEY | 33 | 12.89 | 5.06 | 1.7 | 8.85 | 1.07 | 0.74 | 0 | 1.05
CEANNACROC | 33 | 3.45 | 1.35 | 0.36 | 2.27 | 3.36 | 1.33 | 0.26 | 2.14
CHARLESTON | 33 | 30.94 | 11.56 | 7.37 | 23.72 | 1.55 | 1.08 | 0 | 1.52
CLACHAN | 33 | 7.41 | 2.76 | 1.68 | 5.59 | 6.34 | 2.39 | 1.04 | 4.43
CLAYHILLS | 33 | 32.21 | 12.33 | 4.9 | 22.34 | 3.03 | 2.1 | 0 | 2.97
COUPAR ANGUS | 33 | 43.63 | 16.69 | 8.87 | 32.48 | 2.14 | 1.48 | 0 | 2.1
CRAIGIEBUCKLER | 33 | 26.52 | 10.37 | 2.48 | 17.15 | 1.5 | 1.04 | 0 | 1.47
DALLAS | 33 | 40.18 | 15.07 | 7.21 | 28.52 | 1.08 | 0.75 | 0 | 1.06
DOUNREAY | 33 | 40.84 | 15.27 | 8.47 | 30.07 | 2.18 | 1.51 | 0 | 2.14
DUDHOPE | 33 | 33.95 | 13.03 | 5.45 | 23.88 | 2.86 | 1.98 | 0 | 2.8
DUNBEATH | 33 | 12.49 | 4.87 | 1.09 | 7.98 | 0.4 | 0.28 | 0 | 0.39
DUNOON | 33 | 28.9 | 12.64 | 0.61 | 18.48 | 2.14 | 1.48 | 0 | 2.1
DUNVEGAN | 33 | 17.15 | 7.05 | 1.49 | 11.46 | 1.08 | 0.75 | 0 | 1.06
DYCE | 33 | 38.11 | 14.39 | 7.46 | 27.81 | 2.15 | 1.49 | 0 | 2.11
ELGIN | 33 | 29.22 | 11.9 | 1.64 | 18.47 | 1.82 | 1.26 | 0 | 1.78
FASNAKYLE | 33 | 55.16 | 20.34 | 12.99 | 41.75 | 2.18 | 1.51 | 0 | 2.13
FETTERESSO | 33 | 30.22 | 11.33 | 6.2 | 22.23 | 1.07 | 0.74 | 0 | 1.05
FIDDES | 33 | 37 | 14.89 | 3.88 | 24.93 | 2.15 | 1.49 | 0 | 2.11
FORT AUGUSTUS | 33 | 19.92 | 7.5 | 3.35 | 13.96 | 1.09 | 0.76 | 0 | 1.07
FORT WILLIAM | 33 | 39.35 | 15.6 | 6 | 28.07 | 0.86 | 0.6 | 0 | 0.84
FRASERBURGH | 33 | 23.44 | 9.24 | 1.98 | 15.04 | 2.11 | 1.47 | 0 | 2.07
GLENFARCLAS | 33 | 21.43 | 8.64 | 1.03 | 13.25 | 1.07 | 0.74 | 0 | 1.05
GRUDIE BRIDGE | 33 | 39.09 | 14.57 | 8.53 | 29.14 | 2.19 | 1.52 | 0 | 2.15
INVERNESS | 33 | 54.71 | 21.39 | 7.73 | 37.98 | 3.22 | 2.24 | 0 | 3.16
KEITH I | 33 | 49.36 | 18.51 | 12.81 | 38.99 | 2.15 | 1.49 | 0 | 2.11
KEITH II | 33 | 38.99 | 14.68 | 7.89 | 28.64 | 2.17 | 1.5 | 0 | 2.12
KILLIN | 33 | 35.47 | 13.89 | 4.41 | 24.05 | 2.15 | 1.49 | 0 | 2.11
KINLOCHLEVEN | 33 | 16.03 | 6.41 | 2.22 | 11.28 | 0.72 | 0.5 | 0 | 0.7
KINTORE | 33 | 46.61 | 17.66 | 9.5 | 34.47 | 3.21 | 2.22 | 0 | 3.13
LAIRG | 33 | 24.86 | 9.72 | 2.53 | 16.27 | 1.09 | 0.76 | 0 | 1.07
LUNANHEAD | 33 | 32.1 | 12.48 | 4.96 | 22.62 | 2.14 | 1.48 | 0 | 2.1
LYNDHURST | 33 | 32.19 | 12.38 | 4.58 | 22.09 | 2.89 | 2 | 0 | 2.83
MACDUFF | 33 | 38.48 | 15.71 | 3.28 | 25.49 | 2.17 | 1.51 | 0 | 2.13
MILTON OF CRAIGIE | 33 | 34.9 | 13.32 | 6.48 | 25.32 | 3.25 | 2.25 | 0 | 3.19
MYBSTER I | 33 | 46.79 | 17.61 | 9.68 | 34.59 | 2.18 | 1.51 | 0 | 2.14
MYBSTER II | 33 | 49.22 | 18.57 | 10 | 36.27 | 2.19 | 1.52 | 0 | 2.15
MYBSTER III | 33 | 34.69 | 12.85 | 8.57 | 26.74 | 2.19 | 1.52 | 0 | 2.15
NAIRN | 33 | 25.18 | 10.26 | 1.05 | 15.56 | 2.97 | 2.06 | 0 | 2.91
PERSLEY | 33 | 31.98 | 11.98 | 7.92 | 24.85 | 2.14 | 1.49 | 0 | 2.1
PETERHEAD GRANGE | 33 | 27.48 | 10.81 | 3.19 | 18.49 | 0.57 | 0.4 | 0 | 0.56
PORT ANN | 33 | 32.97 | 13.12 | 4.56 | 23.12 | 1.83 | 1.27 | 0 | 1.8
RANNOCH | 33 | 38.9 | 15.25 | 4.18 | 25.75 | 2.16 | 1.5 | 0 | 2.12
REDMOSS | 33 | 38.16 | 15.14 | 4.95 | 26.36 | 2.98 | 2.06 | 0 | 2.92
ROTHIENORMAN | 33 | 61.05 | 23 | 15.4 | 47.92 | 2.14 | 1.49 | 0 | 2.1
SHIN | 33 | 32.25 | 12.46 | 4.36 | 21.99 | 2.17 | 1.5 | 0 | 2.13
ST FILLIANS | 33 | 6.66 | 2.42 | 2.34 | 5.76 | 6.78 | 2.44 | 2.58 | 6.04
STRICHEN | 33 | 32.07 | 12.24 | 5.14 | 22.45 | 2.14 | 1.49 | 0 | 2.1
TARLAND | 33 | 19.92 | 8.36 | 0.67 | 12.49 | 1.49 | 1.04 | 0 | 1.47
TAYNUILT | 33 | 35.13 | 13.87 | 5.2 | 24.82 | 2.18 | 1.51 | 0 | 2.14
THURSO SOUTH | 33 | 62.91 | 23.27 | 20.92 | 53.83 | 2.18 | 1.51 | 0 | 2.14
TUMMEL BRIDGE | 33 | 10.27 | 3.71 | 4.48 | 9.73 | 1.11 | 0.77 | 0 | 1.09
WILLOWDALE | 33 | 32.16 | 12.35 | 4.81 | 22.27 | 2.97 | 2.06 | 0 | 2.91
WOODHILL | 33 | 31.2 | 11.77 | 6.47 | 23.12 | 4.4 | 3.05 | 0 | 4.31

## D1.5
ETYS 19 Yr 5 - SHE Transmission Fault Levels (kA), Winter 2023/24
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 28.87 | 11.1 | 6.83 | 22.53 | 28.45 | 11.01 | 6.68 | 22.25 | Back To Menu
BLACKHILLOCK | 400 | 31.89 | 12.22 | 8.85 | 26.13 | 32.65 | 12.54 | 8.69 | 26.42
FORT AUGUSTUS | 400 | 26.56 | 10.21 | 6.18 | 20.62 | 27.76 | 10.7 | 6.69 | 21.82
MELGARVE | 400 | 23.93 | 9.19 | 5.56 | 18.56 | 23.74 | 9.19 | 5.32 | 18.33
ALYTH | 275 | 54.49 | 21.82 | 9.26 | 40.11 | 37.4 | 15.61 | 4.22 | 26.3
BEAULY | 275 | 57.48 | 22.68 | 11.35 | 43.43 | 57.61 | 22.92 | 10.92 | 43.34
BERRY BURN | 275 | 31.95 | 13.06 | 4.12 | 22.59 | 24.86 | 10.3 | 3.27 | 17.84
BLACKHILLOCK I | 275 | 53.6 | 21.24 | 11.74 | 41.78 | 55.87 | 22.18 | 11.94 | 43.31
BLACKHILLOCK II | 275 | 32.85 | 12.71 | 8.71 | 26.68 | 35.55 | 13.88 | 8.32 | 27.96
BRACO WEST | 275 | 34.76 | 13.65 | 6.36 | 25.67 | 27.92 | 11.13 | 5.18 | 20.91
CAIRNFORD | 275 | 43.22 | 17.43 | 7.37 | 32.02 | 39.42 | 16.15 | 5.78 | 28.62
CONNAGILL | 275 | 24.19 | 9.51 | 5.17 | 18.62 | 24.14 | 9.61 | 4.6 | 18.18
CREAGH DUBH | 275 | 29.9 | 11.85 | 5.73 | 22.5 | 27.79 | 11.15 | 4.8 | 20.56
DALLAS | 275 | 33.08 | 13.49 | 4.49 | 23.56 | 26.23 | 10.84 | 3.57 | 18.9
DOUNREAY | 275 | 27.46 | 10.72 | 6.65 | 21.81 | 29.82 | 11.65 | 7.12 | 23.59
FARIGAIG I | 275 | 42.4 | 17.01 | 7.26 | 31.32 | 33.59 | 13.77 | 5.33 | 24.8
FARIGAIG II | 275 | 42.63 | 17.09 | 7.38 | 31.55 | 34.01 | 13.92 | 5.56 | 25.24
FASNAKYLE | 275 | 36.35 | 14.19 | 7.37 | 27.44 | 32.15 | 12.74 | 6.05 | 24.07
FETTERESSO | 275 | 42.65 | 17.21 | 6.74 | 31.07 | 31.01 | 12.84 | 4.46 | 22.62
FORT AUGUSTUS | 275 | 31.01 | 12.06 | 6.49 | 23.54 | 28.83 | 11.25 | 6.37 | 22.28
FOYERS | 275 | 42.18 | 16.86 | 7.76 | 31.61 | 29.13 | 12.11 | 3.9 | 21.03
FYRISH | 275 | 30.73 | 12.25 | 5.15 | 22.47 | 27.56 | 11.1 | 4.92 | 20.62
GORDONBUSH | 275 | 22.8 | 9.07 | 3.98 | 16.81 | 20.78 | 8.36 | 3.7 | 15.53
KEITH | 275 | 51.03 | 20.38 | 10.31 | 39.13 | 53.27 | 21.36 | 10.26 | 40.47
KINTORE | 275 | 55.35 | 22.08 | 11.15 | 42.38 | 51.31 | 20.74 | 9.35 | 38.69
KNOCKNAGAEL | 275 | 56.94 | 22.62 | 10.77 | 42.77 | 52.79 | 21.24 | 9.58 | 39.62
LOCH BUIDHE | 275 | 32.4 | 12.91 | 5.58 | 23.84 | 29.29 | 11.79 | 5.37 | 22.04
NEW DEER | 275 | 40.08 | 15.93 | 8.22 | 30.75 | 30.71 | 12.63 | 4.31 | 22.18
PERSLEY | 275 | 32.07 | 12.98 | 5.08 | 23.45 | 28.68 | 11.65 | 4.87 | 21.35
PETERHEAD | 275 | 36.78 | 14.79 | 6.59 | 27.5 | 32.5 | 13.2 | 5.58 | 24.25
ROTHIENORMAN | 275 | 47.74 | 18.83 | 10.54 | 37.17 | 42.33 | 17.08 | 7.88 | 32.03
SPITTAL | 275 | 25.38 | 9.92 | 6.47 | 20.5 | 28 | 10.9 | 7.18 | 22.6
STRATHBRORA | 275 | 24.76 | 9.85 | 4.29 | 18.23 | 22.6 | 9.09 | 4.12 | 16.97
TEALING | 275 | 57.36 | 22.92 | 10.31 | 42.72 | 43.87 | 18.02 | 6.63 | 32.12
THURSO SOUTH | 275 | 24.53 | 9.58 | 6.03 | 19.58 | 26.05 | 10.19 | 6.16 | 20.57
TOMATIN | 275 | 29.97 | 11.88 | 5.34 | 22.15 | 25.94 | 10.41 | 4.56 | 19.29
TUMMEL | 275 | 26.33 | 10.31 | 5.18 | 19.76 | 22.23 | 8.86 | 4.32 | 16.85
ABERARDER | 132 | 14.33 | 5.54 | 2.1 | 9.93 | 15 | 5.86 | 2.2 | 10.49
ABERDEEN BAY | 132 | 18.8 | 7.84 | 1.78 | 12.87 | 17.16 | 7.2 | 1.54 | 11.72
ABERNETHY | 132 | 24.32 | 11.57 | 0.4 | 16.77 | 23.48 | 10.74 | 1.26 | 16.44
A-CHRUACH | 132 | 20.04 | 8.75 | 1.15 | 13.53 | 19.49 | 8.29 | 1.62 | 13.34
AIGAS | 132 | 34.75 | 16.25 | 0.38 | 23.37 | 31.4 | 14.89 | 0.44 | 21.51
ALNESS | 132 | 35.4 | 13.75 | 4.91 | 24.35 | 38.71 | 15.21 | 4.86 | 26.36
AN SUIDHE | 132 | 22.15 | 9.94 | 0.8 | 14.86 | 20.34 | 8.87 | 1.19 | 13.74
ARBROATH | 132 | 13.46 | 6.32 | 0.39 | 9.32 | 12.43 | 5.65 | 0.71 | 8.7
ARDKINGLAS | 132 | 27.21 | 13.1 | 0.27 | 18.79 | 23.43 | 11 | 0.62 | 16.18
ARDMORE | 132 | 6.53 | 2.88 | 0.71 | 4.78 | 7.62 | 3.29 | 0.89 | 5.55
ARNISH | 132 | 8.12 | 3.04 | 1.84 | 6.13 | 10.26 | 3.82 | 2.46 | 7.86
BEAULY | 132 | 58.39 | 24.37 | 5.85 | 40.32 | 65.32 | 27.01 | 7.25 | 45.45
BEINNEUN | 132 | 18.46 | 8.5 | 0.89 | 12.91 | 19.46 | 8.73 | 1.45 | 13.8
BHLARAIDH | 132 | 18.98 | 8.55 | 1.16 | 13.26 | 19.66 | 8.81 | 1.75 | 14.21
BLACKHILLOCK | 132 | 39.44 | 14.89 | 8.56 | 29.63 | 43.39 | 16.56 | 8.51 | 31.93
BOAT OF GARTEN | 132 | 15.33 | 6.54 | 0.72 | 9.96 | 14.81 | 6.26 | 1.02 | 9.88
BRECHIN | 132 | 12.82 | 6.37 | 0.18 | 9.19 | 12.96 | 6.1 | 0.28 | 8.91
BRIDGE OF DUN | 132 | 10.66 | 5.4 | 0.13 | 7.76 | 11.28 | 5.36 | 0.31 | 7.89
BROADFORD I | 132 | 3.42 | 1.87 | 0.01 | 2.66 | 4.93 | 2.68 | 0.02 | 3.8
BROADFORD II | 132 | 8.16 | 3.59 | 0.23 | 5.31 | 7.63 | 3.22 | 0.57 | 5.13
BRORA | 132 | 13.81 | 6.82 | 0.04 | 9.68 | 13.04 | 6.19 | 0.26 | 9.01
BURGHMUIR | 132 | 15.31 | 7.67 | 0.08 | 10.93 | 16.33 | 7.74 | 0.36 | 11.31
CARRADALE | 132 | 18.85 | 7.74 | 1.96 | 12.9 | 20.14 | 8.13 | 2.69 | 14.2
CASSLEY | 132 | 8.46 | 4.09 | 0.18 | 5.97 | 7.65 | 3.59 | 0.28 | 5.36
CEANNACROC | 132 | 17.63 | 8.19 | 0.74 | 12.32 | 18.33 | 8.3 | 1.17 | 12.91
CHARLESTON | 132 | 41.23 | 17.33 | 4.3 | 28.81 | 44.66 | 18.94 | 4.66 | 31.45
CLACHAN | 132 | 26.4 | 12.65 | 0.54 | 18.43 | 23.16 | 10.9 | 0.82 | 16.24
CLAYHILLS | 132 | 37.06 | 15.59 | 2.94 | 24.99 | 43.43 | 18.73 | 2.75 | 29.25
CLUNIE | 132 | 20.79 | 9.61 | 0.41 | 14.01 | 19.51 | 8.85 | 0.77 | 13.29
CONNAGILL | 132 | 18 | 6.73 | 4.32 | 13.85 | 20.55 | 7.75 | 4.32 | 15.29
CORRIEGARTH | 132 | 11.53 | 4.57 | 1.53 | 8 | 11.96 | 4.71 | 1.83 | 8.5
CORRIEMOILLIE | 132 | 29.75 | 12.09 | 3.12 | 20.22 | 31.13 | 12.66 | 3.41 | 21.32
COUPAR ANGUS | 132 | 22.63 | 9.88 | 1.11 | 15.09 | 21.27 | 9.05 | 1.8 | 14.59
CRAIGIEBUCKLER | 132 | 40.72 | 16.82 | 3.89 | 27.68 | 48.61 | 20.35 | 3.85 | 32.63
CREAG DHUBH | 132 | 34.76 | 13.27 | 6.51 | 25.29 | 38.1 | 14.74 | 5.88 | 26.73
CREAG RIABHACH | 132 | 11.37 | 5.27 | 0.52 | 7.98 | 11.29 | 5.04 | 0.92 | 8.05
CROSSAIG | 132 | 27.78 | 11.58 | 2.88 | 19.26 | 31.8 | 13.15 | 3.31 | 21.91
CULLIGRAN | 132 | 18.17 | 8.99 | 0.19 | 12.9 | 16.53 | 7.92 | 0.35 | 11.55
DEANIE | 132 | 12.65 | 6.39 | 0.09 | 9.13 | 11.77 | 5.67 | 0.21 | 8.22
DORENELL | 132 | 15.4 | 6.43 | 1.34 | 10.43 | 16.25 | 6.62 | 1.9 | 11.26
DOUNREAY | 132 | 25.03 | 9.44 | 5.59 | 18.94 | 31.69 | 12 | 6.65 | 23.62
DRUIM LETHANN | 132 | 8.11 | 3.04 | 1.82 | 6.12 | 10.25 | 3.82 | 2.43 | 7.83
DUDHOPE | 132 | 37.29 | 16.1 | 2.6 | 25.37 | 39.17 | 17.47 | 2.12 | 26.83
DUNBEATH | 132 | 12.81 | 6.17 | 0.11 | 8.83 | 11.63 | 5.52 | 0.28 | 8.08
DUNMAGLASS | 132 | 15.5 | 5.89 | 2.98 | 11.32 | 16.94 | 6.52 | 3.09 | 12.32
DUNOON | 132 | 9.72 | 5 | 0.09 | 7.16 | 9.39 | 4.55 | 0.16 | 6.6
DUNVEGAN | 132 | 8.33 | 3.45 | 0.94 | 5.82 | 10.12 | 4.16 | 1.17 | 7.05
DYCE | 132 | 23.81 | 10.07 | 2.03 | 16.27 | 21.92 | 9.3 | 1.97 | 15.12
EDINBANE | 132 | 8.91 | 3.68 | 1.08 | 6.28 | 11.12 | 4.53 | 1.48 | 7.89
ELGIN | 132 | 16.17 | 7.04 | 0.65 | 10.61 | 15.19 | 6.53 | 0.99 | 10.22
ERROCHTY | 132 | 44.09 | 18.25 | 6.3 | 32.11 | 44.65 | 18.74 | 5.28 | 31.77
FARIGAIG I | 132 | 14.69 | 5.63 | 2.39 | 10.36 | 15.95 | 6.11 | 2.69 | 11.34
FARIGAIG II | 132 | 17.46 | 6.49 | 4.43 | 13.6 | 20.83 | 7.79 | 4.78 | 15.8
FARR | 132 | 22.9 | 10.06 | 0.61 | 14.84 | 21.49 | 9.51 | 0.94 | 14.39
FERNOCH | 132 | 17.92 | 8.39 | 0.77 | 12.64 | 19.03 | 8.58 | 1.16 | 13.3
FETTERESSO | 132 | 22.79 | 8.77 | 3.51 | 15.91 | 24.82 | 9.57 | 3.79 | 17.32
FIDDES | 132 | 14.39 | 7.03 | 0.75 | 10.69 | 14.83 | 6.8 | 1.17 | 10.78
FINLARIG | 132 | 21.18 | 10.13 | 0.72 | 15.05 | 21.18 | 9.79 | 0.97 | 14.82
FINSTOWN | 132 | 20.13 | 7.68 | 3.73 | 14.59 | 24.22 | 9.3 | 4.64 | 17.8
FORT AUGUSTUS I | 132 | 49.18 | 18.78 | 9.54 | 36.1 | 58.98 | 22.62 | 10.81 | 42.81
FORT AUGUSTUS II | 132 | 41.53 | 15.81 | 8.11 | 30.47 | 47.91 | 18.47 | 8.19 | 34.31
FORT WILLIAM | 132 | 9.86 | 4.63 | 1.29 | 7.84 | 10.28 | 4.67 | 1.46 | 8.06
FRASERBURGH | 132 | 11.63 | 5.33 | 0.4 | 7.93 | 11.83 | 5.33 | 0.68 | 8.22
FYRISH | 132 | 38.24 | 14.58 | 7.01 | 27.64 | 41.97 | 16.03 | 7.8 | 30.47
GILLS BAY | 132 | 23.58 | 9.12 | 3.82 | 16.71 | 22.02 | 8.78 | 3.17 | 15.6
GLEN KYLLACHY | 132 | 29.73 | 12.78 | 0.97 | 19.05 | 28.26 | 12.56 | 1.51 | 19.27
GLENDOE | 132 | 39.27 | 16.07 | 3.01 | 25.73 | 44.18 | 18.59 | 3 | 29.29
GLENFARCLAS | 132 | 7.64 | 3.57 | 0.27 | 5.32 | 7.38 | 3.31 | 0.45 | 5.14
GLENMORISTON | 132 | 20.77 | 9.39 | 1.22 | 14.5 | 21.27 | 9.5 | 1.74 | 15.17
GRIFFIN | 132 | 17.37 | 8.37 | 0.5 | 12.34 | 17.15 | 7.96 | 1.08 | 12.34
GRUDIE BRIDGE | 132 | 23.18 | 9.68 | 1.65 | 15.34 | 23.61 | 9.84 | 2.03 | 15.94
INVERARAY | 132 | 31.44 | 14.74 | 0.88 | 21.72 | 28.21 | 13.02 | 0.88 | 19.3
INVERARNAN | 132 | 51.51 | 21.74 | 5.13 | 35.88 | 53.81 | 22.54 | 5.19 | 37.06
INVERGARRY | 132 | 19.6 | 9.32 | 0.24 | 13.41 | 18.58 | 8.75 | 0.37 | 12.74
INVERNESS | 132 | 48.43 | 20.27 | 4.27 | 32.93 | 53.2 | 22.19 | 4.86 | 36.24
KEITH | 132 | 33.45 | 13.15 | 6.45 | 25.05 | 42.29 | 17.14 | 7.56 | 31.8
KILLIN | 132 | 24.23 | 11.42 | 1.08 | 17.23 | 25.35 | 11.47 | 1.6 | 17.82
KILMORACK | 132 | 47.78 | 20.99 | 1.93 | 31.62 | 48.45 | 21.36 | 1.87 | 32.08
KINLOCHLEVEN | 132 | 6.63 | 3.12 | 0.64 | 5.06 | 6.91 | 3.12 | 0.77 | 5.19
KINTORE | 132 | 43.51 | 17.39 | 7.03 | 31.62 | 51.29 | 20.56 | 7.68 | 36.76
KNOCKNAGAEL | 132 | 53.7 | 22.09 | 6.54 | 37.78 | 58.76 | 23.9 | 7.72 | 41.52
LAIRG | 132 | 24.77 | 10.13 | 3.07 | 17.4 | 23.43 | 9.67 | 2.57 | 16.24
LIMEKILNS | 132 | 20.7 | 8.27 | 2.04 | 13.73 | 22.4 | 9.05 | 2.19 | 14.99
LOCH BUIDHE | 132 | 35.17 | 14.53 | 5.5 | 26.05 | 40.51 | 16.65 | 5.95 | 29.5
LOCHAY | 132 | 20.75 | 9.96 | 0.67 | 14.75 | 20.41 | 9.49 | 0.87 | 14.29
LUICHART | 132 | 29.72 | 12.16 | 2.67 | 19.86 | 29.34 | 12.01 | 2.73 | 19.72
LUNANHEAD | 132 | 17.09 | 7.38 | 0.96 | 11.4 | 15.93 | 6.78 | 1.48 | 11.07
LYNDHURST | 132 | 32.82 | 14.54 | 1.45 | 22.01 | 33.23 | 14.82 | 1.64 | 22.6
MACDUFF | 132 | 9.34 | 4.37 | 0.57 | 6.74 | 9.34 | 4.22 | 0.75 | 6.71
MELGARVE | 132 | 38.73 | 14.56 | 8.26 | 28.86 | 45.82 | 17.37 | 8.66 | 33.23
MILLENNIUM | 132 | 20.49 | 9.33 | 0.77 | 13.97 | 21.37 | 9.6 | 1.14 | 14.71
MILLENNIUM SOUTH | 132 | 31.39 | 12.89 | 1.97 | 20.2 | 30.4 | 12.55 | 2.22 | 19.97
MILTON OF CRAIGIE | 132 | 39.87 | 16.8 | 4.33 | 28.09 | 42.48 | 18.32 | 3.87 | 29.77
MOSSFORD | 132 | 26.38 | 10.9 | 2.18 | 17.6 | 27.43 | 11.31 | 2.53 | 18.53
MYBSTER I | 132 | 20.1 | 8.57 | 1.68 | 13.8 | 20.94 | 9.09 | 1.04 | 13.89
MYBSTER II | 132 | 20.7 | 7.82 | 4.66 | 15.72 | 23.32 | 8.81 | 5.27 | 17.73
NAIRN | 132 | 15 | 6.66 | 0.43 | 9.85 | 13.69 | 5.95 | 0.68 | 9.09
NANT | 132 | 16.98 | 8.06 | 0.17 | 11.56 | 15.22 | 7.05 | 0.29 | 10.27
ORRIN | 132 | 32.6 | 13.42 | 2.76 | 21.74 | 32.44 | 13.34 | 2.89 | 21.77
PERSLEY | 132 | 39.62 | 16.37 | 4.45 | 27.61 | 48.7 | 20.18 | 5.22 | 33.76
PETERHEAD | 132 | 29.46 | 11.35 | 5.61 | 21.66 | 35.87 | 13.94 | 5.98 | 25.69
PETERHEAD GRANGE | 132 | 20.61 | 8.57 | 1.38 | 13.49 | 21.91 | 9.21 | 1.59 | 14.62
PORT ANN | 132 | 14.55 | 6.52 | 0.6 | 9.82 | 11.94 | 5.23 | 0.58 | 7.98
QUOICH | 132 | 12.78 | 5.68 | 0.35 | 8.38 | 11.48 | 5.04 | 0.52 | 7.66
RANNOCH | 132 | 12.01 | 5.81 | 0.7 | 8.91 | 11.43 | 5.29 | 1.05 | 8.52
REDMOSS | 132 | 34.05 | 14.69 | 1.79 | 22.57 | 38.25 | 17.06 | 1.66 | 25.79
SHIN | 132 | 27.02 | 12.2 | 0.76 | 18.02 | 25.77 | 11.46 | 1.79 | 17.99
SLOY | 132 | 46.41 | 20.49 | 2.16 | 31.14 | 47.27 | 20.79 | 2.39 | 31.79
SPITTAL | 132 | 23.97 | 9.68 | 5.2 | 18.89 | 29.26 | 11.71 | 6.19 | 22.75
ST FERGUS GAS TERMINAL | 132 | 20.69 | 8.73 | 1.18 | 13.53 | 21.45 | 9.27 | 0.99 | 14.1
ST FERGUS MOBIL | 132 | 19.57 | 8.53 | 0.6 | 12.66 | 20.02 | 9.04 | 0.55 | 13.33
ST FILLIANS | 132 | 10.06 | 5.02 | 0.27 | 7.37 | 9 | 4.34 | 0.32 | 6.46
STORNOWAY | 132 | 8.12 | 3.04 | 1.84 | 6.14 | 10.26 | 3.82 | 2.46 | 7.87
STRATHY NORTH | 132 | 13.47 | 5.3 | 1.79 | 9.29 | 13.91 | 5.47 | 2.24 | 9.98
STRICHEN | 132 | 12.79 | 5.77 | 0.68 | 8.84 | 12.84 | 5.74 | 1 | 9.12
STRONELAIRG | 132 | 33.38 | 12.62 | 6.53 | 24.38 | 39.17 | 15.22 | 6.89 | 28.4
TARLAND | 132 | 8.36 | 4.12 | 0.09 | 5.92 | 7.97 | 3.72 | 0.19 | 5.45
TAYNUILT | 132 | 15.05 | 7.23 | 0.63 | 10.84 | 14.31 | 6.64 | 0.98 | 10.37
TEALING | 132 | 45.97 | 18.81 | 7.7 | 34.3 | 49.76 | 20.64 | 6.31 | 35.5
THURSO SOUTH | 132 | 34.46 | 13.05 | 8.03 | 26.49 | 40.72 | 15.44 | 9.11 | 30.95
TOMATIN | 132 | 41.01 | 15.69 | 7.46 | 29.64 | 44.58 | 17.29 | 6.74 | 31.19
TUMMEL | 132 | 31.65 | 12.46 | 5.54 | 23.16 | 31.69 | 13.07 | 4.38 | 22.86
TUMMEL BRIDGE | 132 | 39.29 | 16.74 | 3.62 | 27.3 | 37.99 | 16.48 | 2.72 | 26.02
WILLOWDALE | 132 | 38.68 | 16.12 | 3.6 | 26.39 | 46.65 | 19.67 | 3.8 | 31.62
WOODHILL | 132 | 38.35 | 16.1 | 3.15 | 25.92 | 45.83 | 19.49 | 3.27 | 30.83
ABERNETHY | 33 | 35.14 | 13.63 | 4.43 | 23.71 | 2.13 | 1.48 | 0 | 2.09
ALNESS | 33 | 53.22 | 20.62 | 9.23 | 38.38 | 2.15 | 1.49 | 0 | 2.11
ARBROATH | 33 | 26.73 | 10.52 | 2.62 | 17.5 | 1.52 | 1.05 | 0 | 1.49
ARDMORE | 33 | 20.68 | 8.29 | 3.26 | 14.98 | 1.08 | 0.75 | 0 | 1.06
BEAULY | 33 | 34 | 13.02 | 5.43 | 23.84 | 1.46 | 1.01 | 0 | 1.43
BERRY BURN | 33 | 40.8 | 15.24 | 7.56 | 29.11 | 1.08 | 0.75 | 0 | 1.06
BOAT OF GARTEN | 33 | 33.46 | 13.11 | 3.49 | 22.03 | 2.14 | 1.48 | 0 | 2.1
BRACO WEST | 33 | 57.8 | 22.15 | 10.15 | 41.47 | 2.18 | 1.51 | 0 | 2.13
BRIDGE OF DUN | 33 | 23.11 | 9.61 | 1.05 | 14.64 | 2.13 | 1.48 | 0 | 2.09
BROADFORD I | 33 | 8.71 | 4 | 0.08 | 5.73 | 1.05 | 0.73 | 0 | 1.03
BROADFORD II | 33 | 9.77 | 3.78 | 1.1 | 6.45 | 0.75 | 0.52 | 0 | 0.74
BRORA | 33 | 17.78 | 7.36 | 0.72 | 11.13 | 1.09 | 0.75 | 0 | 1.07
BURGHMUIR | 33 | 25.52 | 10.51 | 1.09 | 15.96 | 2.14 | 1.48 | 0 | 2.1
CAIRNFORD | 33 | 32.15 | 12 | 6.58 | 23.55 | 1.07 | 0.74 | 0 | 1.05
CARRADALE I | 33 | 38.78 | 15.32 | 5.71 | 27.37 | 2.12 | 1.47 | 0 | 2.08
CARRADALE II | 33 | 57.66 | 22.58 | 6.29 | 38.22 | 2.14 | 1.49 | 0 | 2.1
CASSLEY | 33 | 13.28 | 5.14 | 1.82 | 9.1 | 1.07 | 0.74 | 0 | 1.05
CEANNACROC | 33 | 3.46 | 1.35 | 0.36 | 2.27 | 3.37 | 1.33 | 0.26 | 2.14
CHARLESTON | 33 | 31.06 | 11.59 | 7.5 | 23.9 | 1.56 | 1.08 | 0 | 1.53
CLACHAN | 33 | 7.42 | 2.77 | 1.68 | 5.59 | 6.34 | 2.39 | 1.04 | 4.42
CLAYHILLS | 33 | 31.95 | 12.22 | 4.87 | 22.16 | 2.99 | 2.07 | 0 | 2.93
COUPAR ANGUS | 33 | 43.65 | 16.68 | 8.99 | 32.58 | 2.13 | 1.47 | 0 | 2.08
CRAIGIEBUCKLER | 33 | 26.28 | 10.28 | 2.46 | 17 | 1.49 | 1.03 | 0 | 1.46
DALLAS | 33 | 44.35 | 16.74 | 7.25 | 30.93 | 1.07 | 0.74 | 0 | 1.05
DOUNREAY | 33 | 41.4 | 15.46 | 8.68 | 30.55 | 2.19 | 1.52 | 0 | 2.15
DUDHOPE | 33 | 34.09 | 13.07 | 5.55 | 24.04 | 2.86 | 1.99 | 0 | 2.81
DUNBEATH | 33 | 12.6 | 4.91 | 1.1 | 8.05 | 0.4 | 0.28 | 0 | 0.39
DUNOON | 33 | 28.62 | 12.48 | 0.58 | 18.22 | 2.14 | 1.48 | 0 | 2.1
DUNVEGAN | 33 | 19.03 | 7.52 | 1.89 | 12.53 | 1.08 | 0.75 | 0 | 1.06
DYCE | 33 | 38.02 | 14.35 | 7.47 | 27.76 | 2.13 | 1.48 | 0 | 2.09
ELGIN | 33 | 30.07 | 11.87 | 3.4 | 20.18 | 1.8 | 1.25 | 0 | 1.77
FASNAKYLE | 33 | 55.19 | 20.35 | 13 | 41.77 | 2.17 | 1.51 | 0 | 2.13
FETTERESSO | 33 | 36.67 | 13.95 | 5.91 | 25.64 | 1.07 | 0.74 | 0 | 1.05
FIDDES | 33 | 37.04 | 14.89 | 3.94 | 25 | 2.14 | 1.48 | 0 | 2.1
FINSTOWN | 33 | 35.65 | 13.32 | 6.74 | 25.58 | 2.16 | 1.5 | 0 | 2.12
FORT AUGUSTUS | 33 | 19.93 | 7.5 | 3.35 | 13.96 | 1.09 | 0.75 | 0 | 1.07
FORT WILLIAM | 33 | 39.42 | 15.63 | 6.02 | 28.12 | 0.86 | 0.6 | 0 | 0.84
FRASERBURGH | 33 | 23.23 | 9.17 | 1.91 | 14.87 | 2.1 | 1.46 | 0 | 2.06
GLENFARCLAS | 33 | 24.33 | 9.89 | 1.04 | 15.02 | 1.09 | 0.75 | 0 | 1.07
GRUDIE BRIDGE | 33 | 39.23 | 14.62 | 8.55 | 29.22 | 2.2 | 1.52 | 0 | 2.15
INVERNESS | 33 | 54.74 | 21.4 | 7.73 | 37.99 | 3.22 | 2.23 | 0 | 3.16
KEITH I | 33 | 49.82 | 18.61 | 12.91 | 39.23 | 2.15 | 1.49 | 0 | 2.11
KEITH II | 33 | 39.47 | 14.78 | 8 | 28.9 | 2.16 | 1.5 | 0 | 2.12
KILLIN | 33 | 35.75 | 13.99 | 4.52 | 24.3 | 2.15 | 1.49 | 0 | 2.11
KINLOCHLEVEN | 33 | 16.04 | 6.41 | 2.22 | 11.29 | 0.72 | 0.5 | 0 | 0.7
KINTORE | 33 | 46.3 | 17.53 | 9.48 | 34.27 | 3.17 | 2.19 | 0 | 3.09
LAIRG | 33 | 26.44 | 10.04 | 4.88 | 19.08 | 1.09 | 0.76 | 0 | 1.07
LUNANHEAD | 33 | 31.71 | 12.27 | 4.97 | 22.33 | 2.15 | 1.49 | 0 | 2.1
LYNDHURST | 33 | 32.31 | 12.42 | 4.64 | 22.2 | 2.9 | 2.01 | 0 | 2.84
MACDUFF | 33 | 38.63 | 15.74 | 3.33 | 25.59 | 2.14 | 1.48 | 0 | 2.1
MILTON OF CRAIGIE | 33 | 35.09 | 13.38 | 6.61 | 25.53 | 3.26 | 2.26 | 0 | 3.2
MYBSTER I | 33 | 47.39 | 17.82 | 9.86 | 35.07 | 2.19 | 1.52 | 0 | 2.14
MYBSTER II | 33 | 49.63 | 18.72 | 10.09 | 36.56 | 2.21 | 1.53 | 0 | 2.16
MYBSTER III | 33 | 35.16 | 13.01 | 8.74 | 27.14 | 2.2 | 1.52 | 0 | 2.15
NAIRN | 33 | 26.26 | 10.3 | 2.34 | 16.9 | 2.96 | 2.05 | 0 | 2.91
PERSLEY | 33 | 31.7 | 11.87 | 7.88 | 24.66 | 2.12 | 1.47 | 0 | 2.08
PETERHEAD GRANGE | 33 | 27.34 | 10.77 | 3.15 | 18.37 | 0.57 | 0.39 | 0 | 0.56
PORT ANN | 33 | 33.03 | 13.15 | 4.63 | 23.23 | 1.83 | 1.27 | 0 | 1.79
RANNOCH | 33 | 38.75 | 15.19 | 4.17 | 25.66 | 2.15 | 1.49 | 0 | 2.11
REDMOSS | 33 | 37.9 | 15.03 | 4.94 | 26.19 | 2.95 | 2.04 | 0 | 2.89
ROTHIENORMAN | 33 | 61.69 | 23.24 | 15.58 | 48.44 | 2.16 | 1.5 | 0 | 2.12
SHIN | 33 | 32.28 | 12.52 | 3.83 | 21.54 | 2.17 | 1.5 | 0 | 2.13
ST FILLIANS | 33 | 6.68 | 2.43 | 2.35 | 5.78 | 6.79 | 2.45 | 2.59 | 6.05
STRICHEN | 33 | 32.03 | 12.23 | 5.1 | 22.4 | 2.14 | 1.48 | 0 | 2.1
TARLAND | 33 | 19.78 | 8.3 | 0.66 | 12.41 | 1.48 | 1.03 | 0 | 1.45
TAYNUILT | 33 | 36.88 | 14 | 6.42 | 26.22 | 2.18 | 1.51 | 0 | 2.14
THURSO SOUTH | 33 | 64.35 | 23.77 | 21.6 | 55.22 | 2.19 | 1.52 | 0 | 2.15
TUMMEL BRIDGE | 33 | 10.37 | 3.75 | 4.52 | 9.83 | 1.12 | 0.78 | 0 | 1.1
WILLOWDALE | 33 | 31.89 | 12.24 | 4.78 | 22.09 | 2.93 | 2.03 | 0 | 2.87
WOODHILL | 33 | 30.93 | 11.66 | 6.43 | 22.93 | 4.35 | 3.02 | 0 | 4.27

## D1.6
ETYS 19 Yr 7 - SHE Transmission Fault Levels (kA), Winter 2025/26
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BEAULY | 400 | 30.57 | 11.7 | 7.56 | 24.12 | 29.02 | 11.2 | 7.04 | 22.89 | Back To Menu
BLACKHILLOCK | 400 | 41.24 | 15.74 | 11.85 | 34.11 | 36.69 | 14.29 | 9.11 | 29.32
FORT AUGUSTUS | 400 | 27.63 | 10.61 | 6.49 | 21.5 | 27.96 | 10.77 | 6.78 | 22.01
KINTORE | 400 | 32.49 | 12.57 | 8.08 | 25.86 | 31.44 | 12.25 | 7.35 | 24.68
MELGARVE | 400 | 24.93 | 9.56 | 5.81 | 19.34 | 24.12 | 9.33 | 5.51 | 18.7
NEW DEER | 400 | 38 | 14.66 | 9.97 | 30.71 | 32.02 | 12.76 | 5.89 | 23.93
PETERHEAD | 400 | 35.5 | 13.71 | 9.28 | 28.68 | 31.17 | 12.27 | 6.99 | 24.33
ROTHIENORMAN | 400 | 41.34 | 15.9 | 11.16 | 33.64 | 38.85 | 15.21 | 8.71 | 30.21
ALYTH | 275 | 52.88 | 21.15 | 8.95 | 38.86 | 36.32 | 15.17 | 3.94 | 25.4
BEAULY | 275 | 61.31 | 24.15 | 12.47 | 46.62 | 60.21 | 23.94 | 11.66 | 45.51
BERRY BURN | 275 | 32.34 | 13.24 | 4.03 | 22.75 | 24.61 | 10.22 | 3.21 | 17.66
BLACKHILLOCK | 275 | 59.77 | 23.55 | 13.84 | 47.14 | 58.61 | 23.37 | 12.16 | 45.2
BRACO WEST | 275 | 32.04 | 12.58 | 5.88 | 23.67 | 26.38 | 10.47 | 5.05 | 19.86
CAIRNFORD | 275 | 46.5 | 18.7 | 8.03 | 34.47 | 40.78 | 16.74 | 5.92 | 29.59
CONNAGILL I | 275 | 26.58 | 10.46 | 5.5 | 20.29 | 26.15 | 10.43 | 4.77 | 19.52
CONNAGILL II | 275 | 26.75 | 10.52 | 5.55 | 20.43 | 26.21 | 10.45 | 4.75 | 19.53
CREAGH DUBH | 275 | 29.07 | 11.52 | 5.5 | 21.79 | 24.96 | 10.03 | 4.49 | 18.67
DALLAS | 275 | 33.85 | 13.82 | 4.47 | 24 | 26.19 | 10.84 | 3.57 | 18.9
DOUNREAY | 275 | 31.13 | 12.14 | 7.41 | 24.58 | 34.26 | 13.37 | 8.11 | 27.01
FARIGAIG I | 275 | 42.85 | 17.25 | 7.02 | 31.42 | 33.21 | 13.65 | 5.13 | 24.43
FARIGAIG II | 275 | 43.08 | 17.33 | 7.14 | 31.65 | 33.63 | 13.8 | 5.36 | 24.87
FASNAKYLE | 275 | 35.91 | 13.99 | 7.41 | 27.2 | 31.39 | 12.42 | 6.04 | 23.61
FETTERESSO | 275 | 42.83 | 17.23 | 6.88 | 31.24 | 31.13 | 12.93 | 4.18 | 22.47
FIDDES | 275 | 26.02 | 10.47 | 4.05 | 18.85 | 21.05 | 8.61 | 3.21 | 15.39
FORT AUGUSTUS | 275 | 29.78 | 11.56 | 6.33 | 22.67 | 27.38 | 10.67 | 6.11 | 21.2
FOYERS | 275 | 42.57 | 17.09 | 7.47 | 31.63 | 28.73 | 11.98 | 3.72 | 20.67
FYRISH | 275 | 30.86 | 12.31 | 5.09 | 22.49 | 27.11 | 10.94 | 4.8 | 20.26
GORDONBUSH | 275 | 23.27 | 9.27 | 3.85 | 16.97 | 20.66 | 8.35 | 3.39 | 15.2
KEITH | 275 | 56.5 | 22.45 | 11.9 | 43.65 | 55.69 | 22.43 | 10.37 | 42.09
KINTORE | 275 | 61.14 | 24.14 | 13.67 | 47.8 | 65.03 | 25.91 | 12.92 | 49.56
KNOCKNAGAEL | 275 | 59.13 | 23.54 | 10.88 | 44.18 | 53.44 | 21.54 | 9.58 | 40.04
LOCH BUIDHE | 275 | 33.84 | 13.48 | 5.66 | 24.72 | 30.17 | 12.16 | 5.34 | 22.53
PERSLEY | 275 | 33.72 | 13.54 | 5.69 | 24.85 | 30.35 | 12.31 | 5.1 | 22.51
PETERHEAD | 275 | 41.55 | 16.28 | 10.07 | 33.1 | 41.93 | 16.64 | 8.69 | 32.23
SPITTAL | 275 | 28.11 | 11 | 6.91 | 22.46 | 30.41 | 11.88 | 7.49 | 24.29
STRATHBRORA | 275 | 24.99 | 9.97 | 4.04 | 18.14 | 22.6 | 9.12 | 3.72 | 16.62
TEALING | 275 | 56.17 | 22.41 | 10.11 | 41.8 | 44.04 | 18.04 | 6.75 | 32.26
THURSO SOUTH | 275 | 27.22 | 10.64 | 6.48 | 21.52 | 28.44 | 11.16 | 6.44 | 22.22
TOMATIN | 275 | 29.74 | 11.8 | 5.22 | 21.92 | 25.5 | 10.23 | 4.65 | 19.11
TUMMEL | 275 | 24.83 | 9.7 | 4.93 | 18.65 | 21.07 | 8.39 | 4.1 | 15.96
ABERARDER | 132 | 13.79 | 5.32 | 2.05 | 9.57 | 14.55 | 5.67 | 2.19 | 10.21
ABERDEEN BAY | 132 | 18.49 | 7.67 | 1.78 | 12.62 | 17.04 | 7.12 | 1.55 | 11.63
ABERNETHY | 132 | 23.76 | 11.16 | 0.48 | 16.27 | 23.16 | 10.51 | 1.35 | 16.22
A-CHRUACH | 132 | 23.31 | 9.85 | 1.87 | 15.8 | 21.74 | 9.06 | 2.26 | 15.07
AIGAS | 132 | 38.28 | 17.85 | 0.41 | 25.66 | 33.14 | 15.75 | 0.44 | 22.72
ALNESS | 132 | 33.25 | 12.88 | 4.73 | 22.95 | 36.2 | 14.18 | 4.7 | 24.76
AN SUIDHE | 132 | 24.81 | 10.64 | 1.72 | 16.77 | 22.6 | 9.59 | 1.88 | 15.44
ARBROATH | 132 | 12.59 | 6.02 | 0.51 | 9.03 | 13.03 | 6 | 0.9 | 9.38
ARDKINGLAS | 132 | 27.55 | 12.99 | 0.33 | 18.7 | 23.57 | 10.94 | 0.69 | 16.17
ARDMORE | 132 | 6.59 | 2.9 | 0.73 | 4.83 | 7.69 | 3.31 | 0.93 | 5.61
ARNISH | 132 | 13.09 | 4.81 | 3.98 | 10.78 | 15.71 | 5.76 | 4.89 | 13.03
BEAULY | 132 | 70.82 | 28.62 | 11.07 | 51.55 | 76.82 | 31.03 | 11.26 | 55.14
BEAW FIELD | 132 | 40.49 | 15.44 | 7.28 | 29.11 | 16.17 | 5.96 | 4.55 | 12.97
BEINNEUN | 132 | 17.7 | 8.06 | 0.92 | 12.32 | 18.81 | 8.37 | 1.47 | 13.3
BHLARAIDH | 132 | 18.03 | 8.06 | 1.14 | 12.53 | 18.76 | 8.35 | 1.69 | 13.51
BLACKHILLOCK | 132 | 40.85 | 15.42 | 8.95 | 30.76 | 44.21 | 16.91 | 8.46 | 32.37
BOAT OF GARTEN | 132 | 14.97 | 6.37 | 0.72 | 9.73 | 14.57 | 6.14 | 1.03 | 9.71
BRECHIN | 132 | 13.24 | 6.66 | 0.12 | 9.54 | 13.02 | 6.22 | 0.22 | 9.01
BRIDGE OF DUN | 132 | 10.95 | 5.6 | 0.1 | 8.02 | 11.38 | 5.45 | 0.28 | 7.99
BROADFORD I | 132 | 3.4 | 1.85 | 0.01 | 2.63 | 4.89 | 2.65 | 0.02 | 3.77
BROADFORD II | 132 | 8.12 | 3.57 | 0.24 | 5.28 | 7.62 | 3.21 | 0.57 | 5.12
BRORA | 132 | 13.78 | 6.86 | 0.03 | 9.73 | 12.82 | 6.12 | 0.24 | 8.89
BURGHMUIR | 132 | 15.15 | 7.54 | 0.09 | 10.76 | 16.23 | 7.66 | 0.38 | 11.21
CARRADALE | 132 | 20.28 | 8.09 | 2.23 | 13.67 | 21.47 | 8.48 | 3.05 | 15.05
CASSLEY | 132 | 10.42 | 4.82 | 0.61 | 7.44 | 10.73 | 4.84 | 0.71 | 7.55
CEANNACROC | 132 | 16.92 | 7.77 | 0.77 | 11.76 | 17.74 | 7.97 | 1.19 | 12.45
CHARLESTON | 132 | 37.96 | 15.75 | 4.3 | 26.58 | 42.07 | 17.67 | 4.65 | 29.63
CLACHAN | 132 | 26.91 | 12.61 | 0.64 | 18.47 | 23.47 | 10.9 | 0.93 | 16.35
CLASHINDARROCH EXTENSION | 132 | 16.78 | 6.97 | 1.55 | 11.4 | 18.79 | 7.64 | 2.14 | 12.94
CLAYHILLS | 132 | 34.5 | 14.26 | 2.98 | 23.15 | 40.99 | 17.42 | 2.8 | 27.44
CLUNIE | 132 | 20.38 | 9.38 | 0.43 | 13.69 | 19.24 | 8.7 | 0.78 | 13.09
CONNAGILL | 132 | 18.07 | 6.75 | 4.37 | 13.92 | 20.56 | 7.75 | 4.35 | 15.31
CORRIEGARTH | 132 | 11.11 | 4.41 | 1.45 | 7.68 | 11.49 | 4.53 | 1.72 | 8.13
CORRIEMOILLIE | 132 | 32.08 | 12.85 | 3.74 | 21.91 | 33.46 | 13.36 | 4.11 | 23
COUPAR ANGUS | 132 | 21.91 | 9.5 | 1.16 | 14.59 | 20.95 | 8.87 | 1.85 | 14.39
CRAIGIEBUCKLER | 132 | 37.44 | 15.2 | 3.86 | 25.36 | 45.39 | 18.73 | 3.83 | 30.32
CREAG DHUBH | 132 | 33.65 | 12.84 | 6.27 | 24.43 | 35.9 | 13.93 | 5.48 | 25.18
CREAG RIABHACH | 132 | 11.47 | 5.37 | 0.49 | 8.08 | 11.31 | 5.08 | 0.89 | 8.07
CROSSAIG | 132 | 30.74 | 12.21 | 3.54 | 20.81 | 34.37 | 13.7 | 3.88 | 23.25
CULLIGRAN | 132 | 18.68 | 9.29 | 0.16 | 13.3 | 16.62 | 7.99 | 0.33 | 11.63
DEANIE | 132 | 12.76 | 6.48 | 0.08 | 9.24 | 11.69 | 5.64 | 0.2 | 8.18
DORENELL | 132 | 15.41 | 6.45 | 1.3 | 10.43 | 16.21 | 6.61 | 1.86 | 11.21
DOUNREAY | 132 | 25.64 | 9.64 | 5.8 | 19.44 | 32.39 | 12.24 | 6.91 | 24.21
DRUIM LETHANN | 132 | 13.06 | 4.8 | 3.92 | 10.71 | 15.68 | 5.75 | 4.8 | 12.94
DUDHOPE | 132 | 34.5 | 14.7 | 2.67 | 23.45 | 37.08 | 16.35 | 2.18 | 25.31
DUNBEATH | 132 | 12.77 | 6.19 | 0.09 | 8.85 | 11.47 | 5.46 | 0.26 | 7.98
DUNMAGLASS | 132 | 14.84 | 5.64 | 2.83 | 10.81 | 16.21 | 6.25 | 2.92 | 11.75
DUNOON | 132 | 10.61 | 5.12 | 0.34 | 7.58 | 10.08 | 4.59 | 0.66 | 7.15
DUNVEGAN | 132 | 8.35 | 3.46 | 0.94 | 5.83 | 10.12 | 4.16 | 1.17 | 7.05
DYCE | 132 | 23.34 | 9.78 | 2.05 | 15.88 | 21.75 | 9.17 | 2.01 | 14.98
EDINBANE | 132 | 8.92 | 3.68 | 1.08 | 6.28 | 11.12 | 4.53 | 1.48 | 7.89
ELGIN | 132 | 16.07 | 7 | 0.64 | 10.54 | 15 | 6.45 | 0.97 | 10.09
ERROCHTY | 132 | 41.94 | 17.36 | 5.83 | 30.38 | 42.59 | 17.84 | 5.06 | 30.29
FARIGAIG I | 132 | 14.05 | 5.39 | 2.28 | 9.9 | 15.26 | 5.84 | 2.57 | 10.84
FARIGAIG II | 132 | 16.66 | 6.19 | 4.21 | 12.97 | 19.87 | 7.43 | 4.54 | 15.06
FARR | 132 | 22.06 | 9.64 | 0.63 | 14.27 | 20.88 | 9.19 | 0.95 | 13.95
FERNOCH | 132 | 17.36 | 8.12 | 0.8 | 12.29 | 18.54 | 8.35 | 1.18 | 12.99
FETTERESSO | 132 | 19.93 | 7.66 | 3.1 | 13.93 | 21.71 | 8.36 | 3.3 | 15.13
FINLARIG | 132 | 20.99 | 10.02 | 0.74 | 14.91 | 21 | 9.69 | 0.99 | 14.69
FINSTOWN | 132 | 30.24 | 11.59 | 5.29 | 21.67 | 36.65 | 14.16 | 6.58 | 26.61
FORT AUGUSTUS I | 132 | 43.39 | 16.56 | 8.54 | 31.96 | 51.83 | 19.88 | 9.59 | 37.71
FORT AUGUSTUS II | 132 | 36.9 | 14.05 | 7.28 | 27.15 | 42.07 | 16.23 | 7.17 | 30.13
FORT WILLIAM | 132 | 9.74 | 4.55 | 1.3 | 7.73 | 10.21 | 4.61 | 1.47 | 8
FRASERBURGH | 132 | 11.71 | 5.34 | 0.42 | 7.97 | 11.86 | 5.33 | 0.7 | 8.24
FYRISH | 132 | 35.78 | 13.62 | 6.65 | 25.91 | 39.07 | 14.9 | 7.34 | 28.42
GILLS BAY | 132 | 26.39 | 10.27 | 3.89 | 18.41 | 25.71 | 10.35 | 3.15 | 17.78
GLEN KYLLACHY | 132 | 28.39 | 12.13 | 1.02 | 18.18 | 33.4 | 14.06 | 1.59 | 21.48
GLENDOE | 132 | 35.66 | 14.47 | 3.11 | 23.58 | 40.34 | 16.79 | 3.14 | 26.88
GLENFARCLAS | 132 | 7.52 | 3.51 | 0.27 | 5.23 | 7.28 | 3.27 | 0.45 | 5.07
GLENMORISTON | 132 | 19.65 | 8.8 | 1.21 | 13.64 | 20.24 | 8.97 | 1.7 | 14.39
GLENSHERO | 132 | 37.4 | 14.09 | 7.63 | 27.56 | 44.67 | 16.94 | 8.38 | 32.34
GRIFFIN | 132 | 17.17 | 8.24 | 0.5 | 12.16 | 17.03 | 7.89 | 1.08 | 12.24
GRUDIE BRIDGE | 132 | 24.43 | 10.11 | 1.78 | 16.09 | 24.61 | 10.17 | 2.08 | 16.46
INVERARAY | 132 | 32.97 | 14.78 | 1.84 | 22.75 | 29.1 | 13.08 | 1.37 | 19.87
INVERARNAN | 132 | 49.41 | 20.84 | 4.52 | 33.99 | 50.93 | 21.34 | 4.59 | 34.77
INVERGARRY | 132 | 18.73 | 8.79 | 0.27 | 12.7 | 17.97 | 8.38 | 0.39 | 12.25
INVERNESS | 132 | 47.3 | 20.02 | 3.99 | 32.3 | 51.26 | 21.53 | 4.63 | 35.08
KEITH | 132 | 32.9 | 12.94 | 6.44 | 24.74 | 41.33 | 16.76 | 7.49 | 31.19
KILLIN | 132 | 24 | 11.28 | 1.12 | 17.07 | 25.11 | 11.34 | 1.64 | 17.67
KILMORACK | 132 | 55.41 | 23.96 | 2.78 | 36.66 | 53.82 | 23.56 | 2.19 | 35.51
KINLOCHLEVEN | 132 | 6.59 | 3.09 | 0.64 | 5.01 | 6.88 | 3.1 | 0.78 | 5.15
KINTORE | 132 | 41.97 | 16.49 | 7.29 | 30.61 | 50.4 | 19.9 | 8.18 | 36.33
KNOCKNAGAEL | 132 | 52.4 | 21.83 | 6.01 | 36.88 | 56.44 | 23.16 | 7.15 | 39.9
LAIRG | 132 | 26.45 | 10.87 | 2.88 | 18.25 | 24.59 | 10.23 | 2.41 | 16.88
LIMEKILNS | 132 | 20.98 | 8.39 | 1.99 | 13.86 | 22.55 | 9.12 | 2.16 | 15.05
LOCH BUIDHE | 132 | 37.38 | 15.54 | 5.24 | 27.21 | 42.15 | 17.39 | 5.65 | 30.24
LOCHAY | 132 | 20.57 | 9.85 | 0.69 | 14.61 | 20.24 | 9.39 | 0.89 | 14.17
LUICHART | 132 | 31.87 | 12.86 | 3.19 | 21.39 | 30.64 | 12.43 | 3.01 | 20.58
LUNANHEAD | 132 | 16.46 | 7.05 | 0.99 | 10.96 | 15.58 | 6.6 | 1.49 | 10.83
LYNDHURST | 132 | 30.72 | 13.43 | 1.53 | 20.51 | 31.79 | 14.04 | 1.7 | 21.56
MACDUFF | 132 | 9.32 | 4.37 | 0.59 | 6.76 | 9.28 | 4.19 | 0.76 | 6.69
MELGARVE | 132 | 37.63 | 14.14 | 8.02 | 28.02 | 44.98 | 17 | 8.84 | 32.89
MILLENNIUM | 132 | 19.52 | 8.79 | 0.8 | 13.23 | 20.51 | 9.13 | 1.15 | 14.06
MILLENNIUM SOUTH | 132 | 29.03 | 11.84 | 2.04 | 18.78 | 28.63 | 11.76 | 2.26 | 18.89
MILTON OF CRAIGIE | 132 | 36.59 | 15.23 | 4.28 | 25.82 | 39.91 | 17.03 | 3.89 | 27.97
MOSSFORD | 132 | 28.11 | 11.49 | 2.45 | 18.7 | 29 | 11.81 | 2.72 | 19.43
MYBSTER I | 132 | 20.39 | 8.72 | 1.61 | 13.94 | 21.01 | 9.15 | 0.97 | 13.91
MYBSTER II | 132 | 21.49 | 8.11 | 4.78 | 16.25 | 23.95 | 9.04 | 5.38 | 18.17
NAIRN | 132 | 15.13 | 6.71 | 0.44 | 9.94 | 13.78 | 5.98 | 0.7 | 9.15
NANT | 132 | 16.31 | 7.75 | 0.16 | 11.13 | 14.55 | 6.75 | 0.28 | 9.82
ORRIN | 132 | 35.3 | 14.32 | 3.41 | 23.67 | 33.94 | 13.84 | 3.21 | 22.79
PERSLEY | 132 | 36.87 | 14.97 | 4.48 | 25.65 | 45.84 | 18.72 | 5.24 | 31.71
PETERHEAD | 132 | 29.36 | 11.21 | 6.44 | 22.3 | 36.31 | 13.97 | 7.11 | 26.87
PETERHEAD GRANGE | 132 | 20.65 | 8.52 | 1.54 | 13.6 | 22.03 | 9.22 | 1.71 | 14.74
PORT ANN | 132 | 22.95 | 9.87 | 1.76 | 15.72 | 19.78 | 8.52 | 1.27 | 13.32
QUOICH | 132 | 12.39 | 5.48 | 0.36 | 8.1 | 11.2 | 4.91 | 0.52 | 7.46
RANNOCH | 132 | 11.9 | 5.74 | 0.71 | 8.83 | 11.37 | 5.25 | 1.05 | 8.47
REDMOSS | 132 | 31.8 | 13.49 | 1.84 | 20.92 | 36.21 | 15.91 | 1.71 | 24.21
ROTHIENORMAN | 132 | 15.51 | 5.74 | 4.44 | 12.55 | 19.38 | 7.2 | 5.16 | 15.35
SALLACHY | 132 | 9.35 | 4.36 | 0.63 | 6.8 | 10.04 | 4.49 | 0.88 | 7.23
SHETLAND | 132 | 40.78 | 15.49 | 7.76 | 29.66 | 16.18 | 5.96 | 4.58 | 13.01
SHIN | 132 | 29.78 | 13.42 | 1.1 | 20.08 | 28.36 | 12.49 | 2.11 | 19.77
SLOY | 132 | 46.22 | 20.09 | 2.16 | 30.58 | 47.21 | 20.54 | 2.39 | 31.45
SPITTAL | 132 | 24.55 | 9.92 | 5.3 | 19.33 | 29.76 | 11.92 | 6.26 | 23.11
ST FERGUS GAS TERMINAL | 132 | 20.76 | 8.7 | 1.31 | 13.61 | 21.55 | 9.27 | 1.06 | 14.17
ST FERGUS MOBIL | 132 | 19.65 | 8.49 | 0.68 | 12.69 | 20.11 | 9.03 | 0.58 | 13.36
ST FILLIANS | 132 | 10 | 4.98 | 0.27 | 7.32 | 8.95 | 4.31 | 0.32 | 6.42
STORNOWAY | 132 | 13.08 | 4.8 | 3.95 | 10.75 | 15.7 | 5.76 | 4.86 | 13
STRATHY NORTH | 132 | 13.36 | 5.27 | 1.69 | 9.14 | 13.63 | 5.37 | 2.11 | 9.7
STRATHY SOUTH | 132 | 15.31 | 5.99 | 2.31 | 10.77 | 15.66 | 6.13 | 2.57 | 11.24
STRICHEN | 132 | 12.88 | 5.79 | 0.71 | 8.89 | 12.89 | 5.75 | 1.02 | 9.15
STRONELAIRG | 132 | 32.59 | 12.31 | 6.38 | 23.79 | 38.52 | 14.94 | 6.72 | 27.84
TARLAND | 132 | 9.08 | 4.32 | 0.27 | 6.37 | 9.96 | 4.5 | 0.52 | 6.88
TAYNUILT | 132 | 14.55 | 6.97 | 0.68 | 10.54 | 13.93 | 6.45 | 1.04 | 10.16
TEALING | 132 | 41.21 | 16.65 | 7.21 | 30.76 | 45.79 | 18.82 | 6.01 | 32.62
THURSO SOUTH | 132 | 38.49 | 14.62 | 8.63 | 29.31 | 44.93 | 17.13 | 9.64 | 33.86
TOMATIN | 132 | 38.49 | 14.72 | 7 | 27.81 | 42.1 | 16.28 | 6.81 | 29.83
TUMMEL | 132 | 29.85 | 11.76 | 5.14 | 21.78 | 29.75 | 12.32 | 3.94 | 21.36
TUMMEL BRIDGE | 132 | 37.59 | 16 | 3.46 | 26.08 | 36.54 | 15.8 | 2.69 | 25.04
WILLOWDALE | 132 | 35.93 | 14.71 | 3.63 | 24.43 | 43.93 | 18.25 | 3.85 | 29.65
WOODHILL | 132 | 35.52 | 14.65 | 3.18 | 23.89 | 43.07 | 18.04 | 3.32 | 28.82
ABERNETHY | 33 | 36.04 | 13.93 | 4.8 | 24.51 | 2.14 | 1.48 | 0 | 2.1
ALNESS | 33 | 52.66 | 20.4 | 9.1 | 37.95 | 2.14 | 1.48 | 0 | 2.09
ARBROATH | 33 | 35.13 | 14.28 | 2.2 | 22.38 | 2.15 | 1.49 | 0 | 2.1
ARDMORE | 33 | 21.15 | 8.46 | 3.45 | 15.41 | 1.09 | 0.75 | 0 | 1.06
BEAULY | 33 | 33.92 | 12.92 | 5.89 | 24.17 | 1.42 | 0.99 | 0 | 1.4
BERRY BURN | 33 | 40.68 | 15.2 | 7.53 | 29.02 | 1.07 | 0.75 | 0 | 1.05
BOAT OF GARTEN | 33 | 33.08 | 12.96 | 3.43 | 21.77 | 2.14 | 1.48 | 0 | 2.09
BRACO WEST | 33 | 56.26 | 21.59 | 9.58 | 40.12 | 2.16 | 1.5 | 0 | 2.12
BRIDGE OF DUN | 33 | 23.66 | 9.84 | 0.99 | 14.91 | 2.12 | 1.47 | 0 | 2.08
BROADFORD I | 33 | 8.68 | 3.98 | 0.09 | 5.71 | 1.05 | 0.73 | 0 | 1.03
BROADFORD II | 33 | 9.79 | 3.79 | 1.11 | 6.47 | 0.75 | 0.52 | 0 | 0.74
BRORA | 33 | 17.42 | 7.2 | 0.72 | 10.9 | 1.05 | 0.73 | 0 | 1.03
BURGHMUIR | 33 | 25.53 | 10.5 | 1.13 | 15.97 | 2.15 | 1.49 | 0 | 2.1
CAIRNFORD | 33 | 40.1 | 15.34 | 6.23 | 27.93 | 1.07 | 0.74 | 0 | 1.05
CARRADALE I | 33 | 39.68 | 15.53 | 6.25 | 28.21 | 2.16 | 1.5 | 0 | 2.12
CARRADALE II | 33 | 64.74 | 25.45 | 6.62 | 42.61 | 2.17 | 1.5 | 0 | 2.12
CASSLEY | 33 | 13.85 | 5.3 | 2.46 | 9.96 | 1.08 | 0.75 | 0 | 1.06
CEANNACROC | 33 | 3.41 | 1.33 | 0.36 | 2.25 | 3.32 | 1.31 | 0.26 | 2.11
CHARLESTON | 33 | 30.64 | 11.43 | 7.46 | 23.63 | 1.56 | 1.08 | 0 | 1.53
CLACHAN | 33 | 7.54 | 2.81 | 1.72 | 5.7 | 6.43 | 2.43 | 1.06 | 4.49
CLAYHILLS | 33 | 31.11 | 11.87 | 4.82 | 21.61 | 2.95 | 2.04 | 0 | 2.89
COUPAR ANGUS | 33 | 43.44 | 16.6 | 8.92 | 32.4 | 2.14 | 1.48 | 0 | 2.1
CRAIGIEBUCKLER | 33 | 26 | 10.15 | 2.47 | 16.82 | 1.49 | 1.04 | 0 | 1.46
DALLAS | 33 | 44.19 | 16.68 | 7.2 | 30.8 | 1.07 | 0.74 | 0 | 1.05
DOUNREAY | 33 | 41.19 | 15.37 | 8.73 | 30.47 | 2.17 | 1.5 | 0 | 2.12
DUDHOPE | 33 | 33.73 | 12.91 | 5.59 | 23.85 | 2.87 | 1.99 | 0 | 2.81
DUNBEATH | 33 | 12.46 | 4.85 | 1.09 | 7.96 | 0.39 | 0.27 | 0 | 0.38
DUNOON | 33 | 33.76 | 13.97 | 1.41 | 21.16 | 2.12 | 1.47 | 0 | 2.08
DUNVEGAN | 33 | 19.18 | 7.57 | 1.93 | 12.64 | 1.08 | 0.75 | 0 | 1.05
DYCE | 33 | 38.42 | 14.48 | 7.6 | 28.08 | 2.16 | 1.5 | 0 | 2.12
ELGIN | 33 | 29.79 | 11.74 | 3.47 | 20.07 | 1.76 | 1.22 | 0 | 1.73
FASNAKYLE | 33 | 54.01 | 19.91 | 12.67 | 40.83 | 2.14 | 1.49 | 0 | 2.1
FETTERESSO | 33 | 34.11 | 12.96 | 5.62 | 23.95 | 0.98 | 0.68 | 0 | 0.96
FIDDES | 33 | 61.65 | 22.89 | 15.23 | 47.6 | 2.15 | 1.49 | 0 | 2.11
FINSTOWN | 33 | 51.19 | 19.2 | 8.89 | 36.05 | 2.14 | 1.48 | 0 | 2.1
FORT AUGUSTUS | 33 | 19.74 | 7.43 | 3.34 | 13.85 | 1.09 | 0.75 | 0 | 1.06
FORT WILLIAM | 33 | 39.14 | 15.48 | 6.09 | 27.99 | 0.86 | 0.6 | 0 | 0.84
FRASERBURGH | 33 | 23.4 | 9.2 | 2.04 | 15.05 | 2.09 | 1.45 | 0 | 2.05
GLENFARCLAS | 33 | 24.04 | 9.76 | 1.03 | 14.84 | 1.07 | 0.75 | 0 | 1.05
GRUDIE BRIDGE | 33 | 39.36 | 14.61 | 8.96 | 29.63 | 2.16 | 1.5 | 0 | 2.12
INVERNESS | 33 | 54.14 | 21.2 | 7.49 | 37.48 | 3.18 | 2.21 | 0 | 3.12
KEITH I | 33 | 50.34 | 18.79 | 13.2 | 39.78 | 2.14 | 1.48 | 0 | 2.1
KEITH II | 33 | 39.06 | 14.63 | 7.89 | 28.59 | 2.16 | 1.49 | 0 | 2.11
KILLIN | 33 | 36.08 | 14.09 | 4.72 | 24.65 | 2.14 | 1.48 | 0 | 2.09
KINLOCHLEVEN | 33 | 16.02 | 6.39 | 2.24 | 11.28 | 0.72 | 0.5 | 0 | 0.7
KINTORE | 33 | 46.12 | 17.41 | 9.66 | 34.29 | 3.2 | 2.21 | 0 | 3.12
LAIRG | 33 | 26.53 | 10.06 | 4.93 | 19.16 | 1.08 | 0.75 | 0 | 1.06
LUNANHEAD | 33 | 31.51 | 12.18 | 5.03 | 22.25 | 2.15 | 1.49 | 0 | 2.11
LYNDHURST | 33 | 32.09 | 12.31 | 4.69 | 22.11 | 2.91 | 2.02 | 0 | 2.86
MACDUFF | 33 | 39.42 | 16.03 | 3.61 | 26.29 | 2.12 | 1.47 | 0 | 2.08
MILTON OF CRAIGIE | 33 | 35.02 | 13.34 | 6.67 | 25.54 | 3.3 | 2.29 | 0 | 3.23
MYBSTER I | 33 | 53.52 | 20.5 | 9.63 | 38.62 | 2.17 | 1.5 | 0 | 2.13
MYBSTER II | 33 | 49.19 | 18.55 | 10.01 | 36.25 | 2.18 | 1.51 | 0 | 2.14
MYBSTER III | 33 | 40.43 | 15.11 | 8.64 | 30.01 | 2.17 | 1.5 | 0 | 2.12
NAIRN | 33 | 26.48 | 10.38 | 2.36 | 17.04 | 2.99 | 2.07 | 0 | 2.93
PERSLEY | 33 | 31.21 | 11.66 | 7.79 | 24.29 | 2.12 | 1.47 | 0 | 2.08
PETERHEAD GRANGE | 33 | 27.38 | 10.76 | 3.3 | 18.52 | 0.57 | 0.39 | 0 | 0.56
PORT ANN | 33 | 36.33 | 14.18 | 5.43 | 25.48 | 1.81 | 1.25 | 0 | 1.77
RANNOCH | 33 | 38.68 | 15.16 | 4.19 | 25.64 | 2.16 | 1.5 | 0 | 2.11
REDMOSS | 33 | 37.49 | 14.85 | 4.91 | 25.91 | 2.96 | 2.05 | 0 | 2.9
ROTHIENORMAN | 33 | 41.7 | 15.76 | 12.12 | 34.4 | 2.1 | 1.45 | 0 | 2.05
SHIN | 33 | 54.3 | 21.56 | 3.76 | 34.24 | 2.15 | 1.49 | 0 | 2.11
ST FILLIANS | 33 | 6.71 | 2.44 | 2.36 | 5.8 | 6.81 | 2.46 | 2.6 | 6.07
STRICHEN | 33 | 32.79 | 12.47 | 5.54 | 23.18 | 2.13 | 1.48 | 0 | 2.09
TARLAND | 33 | 29.51 | 12.55 | 0.73 | 18.48 | 2.11 | 1.47 | 0 | 2.07
TAYNUILT | 33 | 36.24 | 13.79 | 6.13 | 25.63 | 2.17 | 1.51 | 0 | 2.13
THURSO SOUTH | 33 | 67.86 | 25.02 | 23.09 | 58.47 | 2.18 | 1.51 | 0 | 2.14
TUMMEL BRIDGE | 33 | 10.43 | 3.77 | 4.54 | 9.88 | 1.12 | 0.78 | 0 | 1.1
WILLOWDALE | 33 | 31.46 | 12.06 | 4.75 | 21.8 | 2.95 | 2.05 | 0 | 2.9
WOODHILL | 33 | 30.6 | 11.53 | 6.37 | 22.67 | 4.39 | 3.05 | 0 | 4.31

## D1.7
ETYS 19 Yr 10 - SHE Transmission Fault Levels (kA), Winter 2028/29
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ALYTH | 400 | 46.21 | 18.1 | 9.35 | 34.94 | 36.82 | 14.75 | 6.9 | 27.77 | Back To Menu
BEAULY | 400 | 41.71 | 16.04 | 9.61 | 32.3 | 37.23 | 14.5 | 8.44 | 28.94
BLACKHILLOCK | 400 | 48.2 | 18.45 | 13.44 | 39.53 | 41.62 | 16.24 | 10.28 | 33.24
CORRIE GLAS | 400 | 52.21 | 20.34 | 10.08 | 38.85 | 50.58 | 19.96 | 9.36 | 37.59
FETTEROSSO | 400 | 43.66 | 17.25 | 8.24 | 32.63 | 34.12 | 13.93 | 5.07 | 24.76
FORT AUGUSTUS | 400 | 54.54 | 21.11 | 11.52 | 41.37 | 57.16 | 22.38 | 11.51 | 43.15
INVERGARRY | 400 | 50.47 | 19.6 | 10.14 | 37.86 | 55.71 | 21.81 | 10.6 | 41.44
KINTORE | 400 | 49.79 | 19.36 | 11.73 | 39.1 | 46.79 | 18.39 | 10.3 | 36.3
MELGARVE | 400 | 41.54 | 16.07 | 8.68 | 31.41 | 39.43 | 15.42 | 8.25 | 30.06
NEW DEER | 400 | 43.59 | 16.91 | 10.69 | 34.61 | 35.33 | 14.19 | 6.02 | 26.08
PETERHEAD | 400 | 39.61 | 15.38 | 9.75 | 31.49 | 33.97 | 13.44 | 7.26 | 26.27
ROTHIENORMAN | 400 | 50.26 | 19.44 | 12.71 | 40.2 | 45.27 | 17.88 | 9.41 | 34.69
ALYTH | 275 | 45.78 | 17.85 | 10.53 | 35.77 | 41.55 | 16.44 | 8.57 | 31.81
BEAULY | 275 | 72.94 | 28.68 | 14.65 | 55.21 | 69.48 | 27.66 | 13.12 | 52.24
BERRY BURN | 275 | 36.75 | 14.84 | 5.62 | 26.61 | 31.04 | 12.55 | 5.59 | 23.34
BLACKHILLOCK | 275 | 67.11 | 26.31 | 15.53 | 52.74 | 66.13 | 26.26 | 13.91 | 51.05
BRACO WEST | 275 | 39.03 | 15.33 | 7.02 | 28.7 | 30.41 | 12.14 | 5.54 | 22.7
CAIRN DUHIE | 275 | 36.86 | 14.94 | 5.26 | 26.39 | 30.28 | 12.34 | 4.83 | 22.28
CAIRNFORD | 275 | 50.96 | 20.44 | 8.62 | 37.53 | 44.33 | 18.19 | 6.27 | 32
CLASH GOUR | 275 | 35.72 | 14.43 | 5.39 | 25.8 | 29.22 | 11.87 | 4.96 | 21.74
CONNAGILL I | 275 | 28.55 | 11.25 | 5.72 | 21.63 | 27.71 | 11.07 | 4.9 | 20.56
CONNAGILL II | 275 | 28.43 | 11.2 | 5.7 | 21.54 | 27.46 | 10.98 | 4.83 | 20.36
CREAGH DUBH | 275 | 30.75 | 12.2 | 5.76 | 23.01 | 26.31 | 10.57 | 4.74 | 19.69
DALLAS | 275 | 35.55 | 14.33 | 5.42 | 25.69 | 28.9 | 11.77 | 4.54 | 21.19
DOUNREAY | 275 | 33.52 | 13.09 | 7.73 | 26.25 | 36.42 | 14.24 | 8.4 | 28.53
FARIGAIG I | 275 | 47.09 | 18.99 | 7.4 | 34.25 | 35.82 | 14.75 | 5.37 | 26.23
FARIGAIG II | 275 | 47.33 | 19.08 | 7.52 | 34.5 | 36.27 | 14.91 | 5.61 | 26.7
FASNAKYLE | 275 | 40.56 | 15.78 | 8.33 | 30.65 | 34.77 | 13.77 | 6.5 | 25.97
FIDDES | 275 | 28.65 | 11.51 | 4.42 | 20.7 | 22.9 | 9.39 | 3.34 | 16.61
FORT AUGUSTUS | 275 | 33.41 | 12.95 | 7.11 | 25.42 | 31 | 12.04 | 6.92 | 23.94
FOYERS | 275 | 46.56 | 18.72 | 7.83 | 34.31 | 30.76 | 12.86 | 3.85 | 22.03
FYRISH | 275 | 33.59 | 13.41 | 5.4 | 24.36 | 29.04 | 11.73 | 5.08 | 21.66
GORDONBUSH | 275 | 24.52 | 9.79 | 3.94 | 17.78 | 21.52 | 8.71 | 3.46 | 15.79
KEITH | 275 | 63.09 | 24.98 | 13.14 | 48.46 | 62.48 | 25.1 | 11.64 | 47.14
KINTORE | 275 | 66.2 | 25.95 | 15.4 | 52.1 | 70.48 | 27.96 | 14.32 | 53.86
KNOCKNAGAEL | 275 | 67.21 | 26.77 | 11.94 | 49.8 | 59.59 | 24.05 | 10.37 | 44.39
LOCH BUIDHE | 275 | 36.24 | 14.46 | 5.86 | 26.31 | 31.82 | 12.84 | 5.54 | 23.7
PERSLEY | 275 | 36.33 | 14.56 | 6.1 | 26.69 | 32.43 | 13.15 | 5.42 | 24.01
PETERHEAD | 275 | 45.57 | 17.85 | 10.76 | 36 | 45.38 | 18.03 | 9.15 | 34.65
SPITTAL | 275 | 29.97 | 11.75 | 7.14 | 23.75 | 31.99 | 12.52 | 7.71 | 25.41
STRATHBRORA | 275 | 26.36 | 10.54 | 4.13 | 19.03 | 23.58 | 9.53 | 3.82 | 17.29
TEALING | 275 | 61.53 | 24.21 | 12.94 | 47.17 | 52.4 | 21.17 | 8.92 | 38.85
THURSO SOUTH | 275 | 29.13 | 11.4 | 6.73 | 22.85 | 30.01 | 11.8 | 6.63 | 23.33
TOMATIN | 275 | 32.22 | 12.79 | 5.54 | 23.63 | 27.21 | 10.92 | 4.87 | 20.32
TUMMEL | 275 | 27.93 | 10.93 | 5.45 | 20.91 | 23.34 | 9.3 | 4.5 | 17.66
ABERARDER | 132 | 14.25 | 5.5 | 2.1 | 9.89 | 15.02 | 5.86 | 2.25 | 10.54
ABERDEEN BAY | 132 | 19 | 7.88 | 1.82 | 12.96 | 17.4 | 7.28 | 1.57 | 11.86
ABERNETHY | 132 | 24.78 | 11.69 | 0.47 | 17 | 23.77 | 10.82 | 1.37 | 16.66
A-CHRUACH | 132 | 24.18 | 10.24 | 1.91 | 16.39 | 22.32 | 9.32 | 2.29 | 15.47
AIGAS | 132 | 40.6 | 19.01 | 0.4 | 27.28 | 34.74 | 16.58 | 0.44 | 23.88
ALNESS | 132 | 35.73 | 13.85 | 5 | 24.59 | 38.74 | 15.19 | 4.94 | 26.43
AN SUIDHE | 132 | 25.82 | 11.11 | 1.76 | 17.46 | 23.26 | 9.9 | 1.91 | 15.9
ARBROATH | 132 | 13.08 | 6.27 | 0.54 | 9.4 | 13.43 | 6.19 | 0.94 | 9.68
ARDKINGLAS | 132 | 28.73 | 13.63 | 0.31 | 19.6 | 24.28 | 11.32 | 0.68 | 16.69
ARDMORE | 132 | 7.01 | 3.09 | 0.73 | 5.1 | 8.05 | 3.47 | 0.92 | 5.83
ARNISH | 132 | 18.26 | 6.75 | 5.01 | 14.55 | 22.33 | 8.23 | 6.34 | 17.98
BEAULY | 132 | 77.38 | 31.25 | 12.32 | 56.51 | 83.22 | 33.59 | 12.33 | 59.83
BEAW FIELD | 132 | 44.57 | 17.08 | 7.57 | 31.72 | 22.23 | 8.73 | 4.79 | 17.13
BEINNEUN | 132 | 19.41 | 9.1 | 0.85 | 13.72 | 20.18 | 9.16 | 1.43 | 14.38
BHLARAIDH | 132 | 20.06 | 9.2 | 1.08 | 14.1 | 20.4 | 9.26 | 1.7 | 14.8
BLACKHILLOCK | 132 | 64.76 | 24.59 | 13.34 | 48.12 | 70.79 | 27.19 | 12.72 | 51.18
BOAT OF GARTEN | 132 | 15.49 | 6.6 | 0.73 | 10.06 | 15.01 | 6.34 | 1.05 | 10.01
BRECHIN | 132 | 13.87 | 6.98 | 0.15 | 10.03 | 13.48 | 6.43 | 0.26 | 9.36
BRIDGE OF DUN | 132 | 11.42 | 5.84 | 0.13 | 8.39 | 11.76 | 5.63 | 0.33 | 8.29
BROADFORD I | 132 | 3.49 | 1.9 | 0.02 | 2.71 | 5.02 | 2.72 | 0.02 | 3.87
BROADFORD II | 132 | 8.44 | 3.71 | 0.22 | 5.48 | 7.8 | 3.29 | 0.57 | 5.23
BRORA | 132 | 14.1 | 7.03 | 0.03 | 9.97 | 13.16 | 6.28 | 0.25 | 9.12
BURGHMUIR | 132 | 15.65 | 7.81 | 0.09 | 11.14 | 16.57 | 7.83 | 0.41 | 11.47
CARRADALE | 132 | 21.23 | 8.46 | 2.33 | 14.3 | 22.34 | 8.83 | 3.18 | 15.66
CASSLEY | 132 | 10.55 | 4.89 | 0.61 | 7.53 | 10.85 | 4.89 | 0.71 | 7.63
CEANNACROC | 132 | 18.49 | 8.73 | 0.71 | 13.06 | 18.96 | 8.68 | 1.15 | 13.43
CHARLESTON | 132 | 41.17 | 17.06 | 4.73 | 28.86 | 44.9 | 18.86 | 5 | 31.67
CLACHAN | 132 | 27.94 | 13.19 | 0.61 | 19.26 | 24.09 | 11.24 | 0.9 | 16.8
CLASH GOUR | 132 | 34.62 | 13.04 | 7.23 | 25.67 | 36.64 | 13.93 | 7.15 | 26.84
CLASHINDARROCH EXTENSION | 132 | 18.51 | 7.85 | 1.47 | 12.57 | 20.28 | 8.37 | 2.08 | 13.91
CLAYHILLS | 132 | 36.33 | 15 | 3.15 | 24.36 | 42.93 | 18.24 | 2.92 | 28.71
CLOICHE | 132 | 36.58 | 14.68 | 3.08 | 23.84 | 33.99 | 13.89 | 3.77 | 23.41
CLUNIE | 132 | 21.12 | 9.75 | 0.41 | 14.2 | 19.73 | 8.95 | 0.77 | 13.43
CONNAGILL | 132 | 20.21 | 7.58 | 4.53 | 15.26 | 22.78 | 8.64 | 4.42 | 16.63
CORRIEGARTH | 132 | 11.48 | 4.55 | 1.54 | 7.97 | 11.93 | 4.7 | 1.83 | 8.48
CORRIEMOILLIE | 132 | 33.23 | 13.31 | 3.81 | 22.64 | 34.46 | 13.76 | 4.2 | 23.65
COUPAR ANGUS | 132 | 22.86 | 9.92 | 1.16 | 15.2 | 21.56 | 9.14 | 1.86 | 14.78
CRAIGIEBUCKLER | 132 | 39.48 | 16.01 | 4.1 | 26.73 | 47.61 | 19.63 | 4.03 | 31.79
CREAG DHUBH | 132 | 35.26 | 13.46 | 6.54 | 25.58 | 37.62 | 14.59 | 5.76 | 26.39
CREAG RIABHACH | 132 | 11.65 | 5.46 | 0.5 | 8.21 | 11.48 | 5.16 | 0.9 | 8.2
CROSSAIG | 132 | 33.09 | 13.13 | 3.85 | 22.43 | 37.34 | 14.87 | 4.24 | 25.26
CULLIGRAN | 132 | 19.4 | 9.68 | 0.16 | 13.85 | 17.18 | 8.28 | 0.33 | 12.03
DEANIE | 132 | 13.19 | 6.71 | 0.08 | 9.57 | 12.05 | 5.82 | 0.2 | 8.43
DORENELL | 132 | 17.12 | 7.31 | 1.22 | 11.56 | 17.52 | 7.24 | 1.81 | 12.05
DOUNREAY | 132 | 26.42 | 9.93 | 5.95 | 20 | 33.3 | 12.58 | 7.06 | 24.85
DRUIM LETHANN | 132 | 18.2 | 6.74 | 4.88 | 14.41 | 22.25 | 8.22 | 6.15 | 17.77
DUDHOPE | 132 | 37.27 | 15.87 | 2.87 | 25.31 | 39.44 | 17.42 | 2.28 | 26.92
DUNBEATH | 132 | 13.08 | 6.35 | 0.09 | 9.07 | 11.72 | 5.58 | 0.26 | 8.16
DUNMAGLASS | 132 | 15.34 | 5.84 | 2.92 | 11.17 | 16.75 | 6.45 | 3 | 12.13
DUNOON | 132 | 10.82 | 5.23 | 0.34 | 7.74 | 10.29 | 4.69 | 0.66 | 7.29
DUNVEGAN | 132 | 9.19 | 3.78 | 1.12 | 6.46 | 10.95 | 4.46 | 1.36 | 7.67
DYCE | 132 | 24.21 | 10.15 | 2.11 | 16.46 | 22.38 | 9.44 | 2.05 | 15.39
EDINBANE | 132 | 9.67 | 3.97 | 1.18 | 6.8 | 11.88 | 4.82 | 1.61 | 8.42
ELCHIES | 132 | 19.13 | 8.33 | 0.67 | 12.44 | 17.1 | 7.19 | 1 | 11.17
ELGIN | 132 | 16.35 | 7.12 | 0.67 | 10.74 | 15.33 | 6.58 | 1.01 | 10.32
ENERGY ISLES | 132 | 15.09 | 6.41 | 1.04 | 10.11 | 18.62 | 7.71 | 1.67 | 12.58
ERROCHTY | 132 | 44.74 | 18.5 | 6.29 | 32.46 | 45.07 | 18.91 | 5.21 | 31.95
FARIGAIG I | 132 | 14.58 | 5.59 | 2.36 | 10.26 | 15.8 | 6.05 | 2.65 | 11.21
FARIGAIG II | 132 | 17.28 | 6.42 | 4.37 | 13.45 | 20.59 | 7.71 | 4.71 | 15.6
FARR | 132 | 23.05 | 10.11 | 0.61 | 14.91 | 21.55 | 9.53 | 0.92 | 14.39
FERNOCH | 132 | 18.05 | 8.47 | 0.77 | 12.74 | 19.13 | 8.63 | 1.16 | 13.36
FETTERESSO | 132 | 15.82 | 5.88 | 4.04 | 12.36 | 19.74 | 7.38 | 4.68 | 15.11
FINLARIG | 132 | 21.69 | 10.38 | 0.77 | 15.45 | 21.53 | 9.96 | 1.01 | 15.09
FINSTOWN | 132 | 33.45 | 12.8 | 5.93 | 24.03 | 40.63 | 15.65 | 7.48 | 29.62
FORT AUGUSTUS I | 132 | 48.85 | 18.49 | 10.28 | 36.43 | 58.64 | 22.29 | 11.59 | 43.11
FORT AUGUSTUS II | 132 | 50.8 | 19.2 | 10.69 | 37.85 | 57.73 | 22.15 | 10.13 | 41.46
FORT WILLIAM | 132 | 10.2 | 4.62 | 1.29 | 7.83 | 10.77 | 4.77 | 1.49 | 8.24
FRASERBURGH | 132 | 12.25 | 5.59 | 0.42 | 8.34 | 12.32 | 5.55 | 0.72 | 8.56
FYRISH | 132 | 38.61 | 14.69 | 7.16 | 27.94 | 41.98 | 16.01 | 7.88 | 30.51
GILLS BAY | 132 | 29.59 | 11.58 | 4.03 | 20.41 | 29.95 | 12.11 | 3.26 | 20.38
GLEN KYLLACHY | 132 | 29.91 | 12.83 | 1 | 19.14 | 35.1 | 14.82 | 1.58 | 22.53
GLENDOE | 132 | 39.39 | 15.94 | 3.42 | 25.96 | 44.6 | 18.52 | 3.51 | 29.7
GLENFARCLAS | 132 | 7.7 | 3.59 | 0.28 | 5.37 | 7.48 | 3.35 | 0.47 | 5.22
GLENMORISTON | 132 | 22.14 | 10.21 | 1.13 | 15.56 | 22.19 | 10.05 | 1.67 | 15.88
GLENSHERO | 132 | 72.86 | 27.79 | 12.39 | 51.69 | 85.19 | 32.8 | 12.91 | 59.3
GRIFFIN | 132 | 17.67 | 8.5 | 0.51 | 12.54 | 17.44 | 8.09 | 1.1 | 12.54
GRUDIE BRIDGE | 132 | 25.19 | 10.44 | 1.79 | 16.55 | 25.22 | 10.43 | 2.09 | 16.84
INVERARAY | 132 | 34.55 | 15.58 | 1.87 | 23.91 | 30.13 | 13.61 | 1.39 | 20.63
INVERARNAN | 132 | 53.62 | 22.61 | 4.98 | 36.96 | 55.23 | 23.12 | 5.08 | 37.78
INVERGARRY | 132 | 24.13 | 9.53 | 2.64 | 16.13 | 25.29 | 10.29 | 1.99 | 16.54
INVERNESS | 132 | 51.11 | 21.64 | 4.22 | 34.83 | 55.24 | 23.21 | 4.91 | 37.73
KEITH | 132 | 33.77 | 13.27 | 6.68 | 25.44 | 42.41 | 17.2 | 7.76 | 32.08
KILLIN | 132 | 24.86 | 11.73 | 1.18 | 17.76 | 25.85 | 11.69 | 1.71 | 18.24
KILMORACK | 132 | 59.67 | 25.87 | 2.86 | 39.45 | 57.28 | 25.14 | 2.22 | 37.78
KINLOCHLEVEN | 132 | 6.71 | 3.1 | 0.57 | 4.96 | 6.94 | 3.1 | 0.71 | 5.09
KINTORE | 132 | 44.42 | 17.43 | 7.78 | 32.43 | 53.06 | 20.94 | 8.66 | 38.27
KNOCKNAGAEL | 132 | 56.96 | 23.72 | 6.5 | 40.05 | 61.13 | 25.07 | 7.72 | 43.17
LAIRG | 132 | 27.09 | 11.14 | 2.94 | 18.69 | 25.11 | 10.45 | 2.46 | 17.24
LIMEKILNS | 132 | 21.52 | 8.62 | 1.99 | 14.18 | 23.05 | 9.33 | 2.17 | 15.37
LOCH BUIDHE | 132 | 38.62 | 16.07 | 5.38 | 28.11 | 43.41 | 17.93 | 5.79 | 31.14
LOCHAY | 132 | 21.25 | 10.2 | 0.72 | 15.15 | 20.79 | 9.66 | 0.93 | 14.59
LUICHART | 132 | 33.18 | 13.4 | 3.28 | 22.22 | 31.68 | 12.85 | 3.08 | 21.26
LUNANHEAD | 132 | 17.25 | 7.39 | 1.04 | 11.49 | 16.15 | 6.84 | 1.55 | 11.23
LYNDHURST | 132 | 32.92 | 14.4 | 1.6 | 21.96 | 33.47 | 14.81 | 1.75 | 22.69
MACDUFF | 132 | 10.2 | 4.86 | 0.65 | 7.52 | 9.98 | 4.55 | 0.83 | 7.27
MELGARVE | 132 | 74.02 | 28.03 | 13.99 | 53.63 | 86.65 | 33.1 | 14.75 | 61.57
MILLENNIUM | 132 | 21.78 | 10.1 | 0.72 | 15.01 | 22.32 | 10.15 | 1.1 | 15.45
MILLENNIUM SOUTH | 132 | 31.4 | 12.81 | 2.09 | 20.2 | 30.45 | 12.51 | 2.28 | 19.98
MILTON OF CRAIGIE | 132 | 39.73 | 16.51 | 4.75 | 28.09 | 42.67 | 18.21 | 4.16 | 29.9
MOSSFORD | 132 | 29.05 | 11.88 | 2.48 | 19.28 | 29.8 | 12.15 | 2.77 | 19.94
MUAITHEBEHEAL | 132 | 18.23 | 6.74 | 4.93 | 14.47 | 22.29 | 8.22 | 6.24 | 17.87
MYBSTER I | 132 | 21.02 | 9 | 1.62 | 14.35 | 21.58 | 9.4 | 0.98 | 14.27
MYBSTER II | 132 | 22.37 | 8.45 | 4.91 | 16.86 | 24.66 | 9.32 | 5.46 | 18.64
NAIRN | 132 | 15.44 | 6.85 | 0.45 | 10.14 | 14 | 6.08 | 0.71 | 9.3
NANT | 132 | 17.11 | 8.13 | 0.17 | 11.67 | 15.26 | 7.07 | 0.3 | 10.29
ORRIN | 132 | 36.94 | 14.99 | 3.52 | 24.72 | 35.21 | 14.37 | 3.29 | 23.61
PERSLEY | 132 | 38.88 | 15.76 | 4.77 | 27.05 | 48.12 | 19.62 | 5.54 | 33.28
PETERHEAD | 132 | 31.16 | 11.89 | 6.8 | 23.62 | 38.44 | 14.78 | 7.48 | 28.38
PETERHEAD GRANGE | 132 | 21.78 | 8.99 | 1.63 | 14.34 | 23.41 | 9.76 | 2.06 | 15.87
PORT ANN | 132 | 23.91 | 10.31 | 1.82 | 16.4 | 20.45 | 8.82 | 1.3 | 13.77
QUOICH | 132 | 12.87 | 5.71 | 0.35 | 8.41 | 11.49 | 5.05 | 0.52 | 7.65
RANNOCH | 132 | 12.22 | 5.92 | 0.69 | 9.06 | 11.59 | 5.36 | 1.04 | 8.63
REDMOSS | 132 | 33.43 | 14.17 | 1.93 | 21.97 | 37.86 | 16.63 | 1.77 | 25.29
ROTHIENORMAN | 132 | 16.22 | 6 | 4.63 | 13.11 | 20.22 | 7.51 | 5.36 | 15.98
SALLACHY | 132 | 9.46 | 4.42 | 0.63 | 6.88 | 10.16 | 4.55 | 0.89 | 7.32
SHETLAND | 132 | 44.85 | 17.13 | 8.04 | 32.26 | 22.24 | 8.73 | 4.82 | 17.16
SHIN | 132 | 30.61 | 13.83 | 1.11 | 20.66 | 29.05 | 12.81 | 2.14 | 20.26
SLOY | 132 | 49.02 | 21.49 | 2.03 | 32.42 | 49.37 | 21.63 | 2.29 | 32.88
SPITTAL | 132 | 25.39 | 10.26 | 5.43 | 19.95 | 30.7 | 12.29 | 6.4 | 23.78
ST FERGUS GAS TERMINAL | 132 | 21.89 | 9.17 | 1.35 | 14.33 | 22.63 | 9.73 | 1.1 | 14.87
ST FERGUS MOBIL | 132 | 20.68 | 8.95 | 0.69 | 13.35 | 21.07 | 9.48 | 0.59 | 14
ST FILLIANS | 132 | 10.2 | 5.1 | 0.26 | 7.47 | 9.04 | 4.37 | 0.3 | 6.49
STORNOWAY | 132 | 18.23 | 6.74 | 4.93 | 14.46 | 22.29 | 8.22 | 6.23 | 17.86
STRATHY NORTH | 132 | 15.72 | 6.17 | 2.14 | 10.86 | 17.28 | 6.74 | 2.86 | 12.39
STRATHY SOUTH | 132 | 15.62 | 6.11 | 2.33 | 10.97 | 15.95 | 6.25 | 2.6 | 11.43
STRICHEN | 132 | 13.5 | 6.07 | 0.73 | 9.32 | 13.4 | 5.98 | 1.05 | 9.51
STRONELAIRG | 132 | 52.46 | 20.05 | 8.59 | 36.95 | 59.76 | 24.13 | 7.91 | 42.03
TARLAND | 132 | 9.39 | 4.47 | 0.28 | 6.6 | 10.24 | 4.63 | 0.54 | 7.08
TAYNUILT | 132 | 15.16 | 7.29 | 0.62 | 10.93 | 14.37 | 6.67 | 0.98 | 10.41
TEALING | 132 | 45.41 | 18.27 | 8.39 | 34.23 | 50.25 | 20.56 | 7.02 | 36.1
THURSO SOUTH | 132 | 42.17 | 16.1 | 8.93 | 31.7 | 48.58 | 18.62 | 9.92 | 36.26
TOMATIN | 132 | 41.09 | 15.7 | 7.47 | 29.68 | 44.65 | 17.26 | 7.19 | 31.59
TUMMEL | 132 | 32.25 | 12.69 | 5.6 | 23.55 | 32.17 | 13.27 | 4.39 | 23.17
TUMMEL BRIDGE | 132 | 39.9 | 16.99 | 3.64 | 27.66 | 38.43 | 16.66 | 2.71 | 26.27
WILLOW | 132 | 18.33 | 8.27 | 0.4 | 12.1 | 17.5 | 7.63 | 0.88 | 11.67
WILLOWDALE | 132 | 37.86 | 15.48 | 3.85 | 25.74 | 46.06 | 19.11 | 4.04 | 31.07
WOODHILL | 132 | 37.42 | 15.41 | 3.36 | 25.16 | 45.14 | 18.89 | 3.48 | 30.19
ABERNETHY | 33 | 36.66 | 14.15 | 4.99 | 25 | 2.14 | 1.48 | 0 | 2.1
ALNESS | 33 | 53.63 | 20.78 | 9.27 | 38.66 | 2.18 | 1.51 | 0 | 2.13
ARBROATH | 33 | 36.14 | 14.67 | 2.31 | 23.07 | 2.16 | 1.5 | 0 | 2.12
ARDMORE | 33 | 21.87 | 8.73 | 3.5 | 15.85 | 1.08 | 0.75 | 0 | 1.06
BEAULY | 33 | 35.5 | 13.51 | 6.22 | 25.33 | 1.48 | 1.03 | 0 | 1.45
BERRY BURN | 33 | 41.08 | 15.33 | 7.78 | 29.46 | 1.08 | 0.75 | 0 | 1.06
BOAT OF GARTEN | 33 | 33.86 | 13.27 | 3.52 | 22.28 | 2.17 | 1.5 | 0 | 2.13
BRACO WEST | 33 | 59 | 22.59 | 10.5 | 42.45 | 2.19 | 1.52 | 0 | 2.15
BRIDGE OF DUN | 33 | 24.81 | 10.28 | 1.19 | 15.73 | 2.14 | 1.49 | 0 | 2.1
BROADFORD I | 33 | 8.94 | 4.09 | 0.1 | 5.88 | 1.07 | 0.74 | 0 | 1.05
BROADFORD II | 33 | 9.9 | 3.83 | 1.12 | 6.54 | 0.75 | 0.52 | 0 | 0.74
BRORA | 33 | 17.76 | 7.35 | 0.71 | 11.11 | 1.08 | 0.75 | 0 | 1.06
BURGHMUIR | 33 | 26.29 | 10.78 | 1.25 | 16.5 | 2.14 | 1.48 | 0 | 2.09
CAIRNFORD | 33 | 40.88 | 15.63 | 6.4 | 28.51 | 1.09 | 0.75 | 0 | 1.07
CARRADALE I | 33 | 40.58 | 15.85 | 6.56 | 28.98 | 2.19 | 1.52 | 0 | 2.15
CARRADALE II | 33 | 65.41 | 25.69 | 6.83 | 43.17 | 2.17 | 1.51 | 0 | 2.13
CASSLEY | 33 | 13.9 | 5.32 | 2.48 | 10 | 1.08 | 0.75 | 0 | 1.06
CEANNACROC | 33 | 3.47 | 1.36 | 0.36 | 2.28 | 3.37 | 1.33 | 0.26 | 2.15
CHARLESTON | 33 | 31.55 | 11.76 | 7.82 | 24.45 | 1.58 | 1.09 | 0 | 1.55
CLACHAN | 33 | 7.56 | 2.82 | 1.73 | 5.71 | 6.42 | 2.43 | 1.06 | 4.49
CLAYHILLS | 33 | 32.14 | 12.26 | 5.04 | 22.37 | 3.01 | 2.09 | 0 | 2.95
COUPAR ANGUS | 33 | 44.32 | 16.91 | 9.32 | 33.23 | 2.14 | 1.48 | 0 | 2.1
CRAIGIEBUCKLER | 33 | 26.95 | 10.52 | 2.6 | 17.47 | 1.52 | 1.06 | 0 | 1.49
DALLAS | 33 | 44.98 | 16.97 | 7.43 | 31.43 | 1.09 | 0.76 | 0 | 1.07
DOUNREAY | 33 | 41.9 | 15.63 | 8.92 | 31.03 | 2.18 | 1.51 | 0 | 2.14
DUDHOPE | 33 | 34.82 | 13.31 | 5.87 | 24.7 | 2.91 | 2.01 | 0 | 2.85
DUNBEATH | 33 | 12.72 | 4.96 | 1.11 | 8.12 | 0.4 | 0.28 | 0 | 0.39
DUNOON | 33 | 34.21 | 14.15 | 1.42 | 21.43 | 2.12 | 1.47 | 0 | 2.08
DUNVEGAN | 33 | 24.34 | 9.55 | 2.49 | 16 | 1.08 | 0.75 | 0 | 1.06
DYCE | 33 | 40.16 | 15.11 | 8.17 | 29.54 | 2.19 | 1.52 | 0 | 2.15
ELGIN | 33 | 30.5 | 12.04 | 3.45 | 20.48 | 1.81 | 1.26 | 0 | 1.78
FASNAKYLE | 33 | 55.88 | 20.58 | 13.3 | 42.41 | 2.19 | 1.52 | 0 | 2.15
FETTERESSO | 33 | 34.77 | 13.19 | 6.2 | 24.85 | 1.07 | 0.74 | 0 | 1.05
FIDDES | 33 | 64.66 | 23.96 | 16.48 | 50.37 | 2.18 | 1.51 | 0 | 2.14
FINSTOWN | 33 | 52.21 | 19.56 | 9.28 | 36.95 | 2.15 | 1.49 | 0 | 2.11
FORT AUGUSTUS | 33 | 20.23 | 7.61 | 3.44 | 14.21 | 1.1 | 0.76 | 0 | 1.08
FORT WILLIAM | 33 | 39.08 | 15.21 | 6.26 | 27.77 | 0.87 | 0.6 | 0 | 0.85
FRASERBURGH | 33 | 24.42 | 9.59 | 2.19 | 15.76 | 2.14 | 1.48 | 0 | 2.1
GLENFARCLAS | 33 | 23.9 | 9.71 | 1.04 | 14.77 | 1.07 | 0.75 | 0 | 1.05
GRUDIE BRIDGE | 33 | 39.95 | 14.83 | 9.14 | 30.11 | 2.18 | 1.51 | 0 | 2.14
INVERNESS | 33 | 56.41 | 22.1 | 7.79 | 39.05 | 3.3 | 2.29 | 0 | 3.23
KEITH I | 33 | 52.06 | 19.42 | 13.83 | 41.3 | 2.16 | 1.5 | 0 | 2.12
KEITH II | 33 | 39.32 | 14.72 | 8 | 28.82 | 2.16 | 1.5 | 0 | 2.12
KILLIN | 33 | 37.96 | 14.8 | 5.17 | 26.1 | 2.18 | 1.51 | 0 | 2.13
KINLOCHLEVEN | 33 | 16.14 | 6.39 | 2.19 | 11.22 | 0.71 | 0.49 | 0 | 0.69
KINTORE | 33 | 47.84 | 18.06 | 10.12 | 35.65 | 3.26 | 2.25 | 0 | 3.18
LAIRG | 33 | 26.72 | 10.13 | 4.99 | 19.32 | 1.08 | 0.75 | 0 | 1.06
LUNANHEAD | 33 | 32.74 | 12.63 | 5.38 | 23.24 | 2.18 | 1.51 | 0 | 2.14
LYNDHURST | 33 | 32.96 | 12.62 | 4.99 | 22.83 | 2.91 | 2.02 | 0 | 2.85
MACDUFF | 33 | 43.04 | 17.57 | 4.2 | 29.05 | 2.17 | 1.51 | 0 | 2.13
MILTON OF CRAIGIE | 33 | 36.1 | 13.74 | 7.04 | 26.47 | 3.31 | 2.3 | 0 | 3.25
MYBSTER I | 33 | 55.18 | 21.1 | 10.15 | 39.99 | 2.18 | 1.51 | 0 | 2.14
MYBSTER II | 33 | 56.24 | 21.43 | 10.1 | 40.41 | 2.18 | 1.51 | 0 | 2.14
MYBSTER III | 33 | 41.6 | 15.53 | 9 | 30.97 | 2.2 | 1.52 | 0 | 2.15
NAIRN | 33 | 26.99 | 10.58 | 2.44 | 17.4 | 3.01 | 2.09 | 0 | 2.95
PERSLEY | 33 | 32.33 | 12.08 | 8.15 | 25.23 | 2.18 | 1.51 | 0 | 2.13
PETERHEAD GRANGE | 33 | 31.31 | 12.1 | 5.26 | 22.36 | 2.15 | 1.49 | 0 | 2.11
PORT ANN | 33 | 38 | 14.81 | 5.83 | 26.78 | 1.85 | 1.28 | 0 | 1.81
RANNOCH | 33 | 39.34 | 15.4 | 4.29 | 26.07 | 2.16 | 1.5 | 0 | 2.12
REDMOSS | 33 | 38.72 | 15.32 | 5.17 | 26.83 | 3.01 | 2.09 | 0 | 2.95
ROTHIENORMAN | 33 | 43.54 | 16.43 | 12.81 | 36.05 | 2.12 | 1.47 | 0 | 2.07
SHIN | 33 | 54.81 | 21.76 | 3.79 | 34.56 | 2.17 | 1.5 | 0 | 2.13
ST FILLIANS | 33 | 6.71 | 2.44 | 2.38 | 5.83 | 6.77 | 2.44 | 2.6 | 6.05
STRICHEN | 33 | 34.87 | 13.23 | 6.15 | 24.86 | 2.17 | 1.51 | 0 | 2.13
TARLAND | 33 | 30.64 | 13 | 0.8 | 19.18 | 2.15 | 1.49 | 0 | 2.11
TAYNUILT | 33 | 37.13 | 14.09 | 6.49 | 26.42 | 2.18 | 1.51 | 0 | 2.14
THURSO SOUTH | 33 | 78.63 | 29.38 | 23.76 | 65.3 | 2.19 | 1.52 | 0 | 2.15
TUMMEL BRIDGE | 33 | 10.54 | 3.81 | 4.59 | 9.98 | 1.12 | 0.78 | 0 | 1.1
WILLOWDALE | 33 | 32.55 | 12.47 | 4.97 | 22.6 | 3.01 | 2.09 | 0 | 2.96
WOODHILL | 33 | 31.59 | 11.89 | 6.65 | 23.47 | 4.48 | 3.11 | 0 | 4.39

## D2.1
ETYS 19 Yr 1 - SPT Fault Levels (kA), Winter 2019/20
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
COAL4- | 400 | 53.53 | 20.13 | 9.71 | 38.18 | 46.17 | 18.33 | 7.86 | 33.78 | Back To Menu
CRYR4- | 400 | 57 | 20.61 | 12.97 | 42.11 | 53.62 | 20.48 | 11.54 | 40.49
DENN4- | 400 | 21.22 | 7.75 | 6.04 | 17 | 19.8 | 7.48 | 5.28 | 15.85
DEVM4- | 400 | 33.52 | 12.47 | 7.06 | 24.71 | 29.03 | 11.39 | 5.61 | 21.72
ECCL4A | 400 | 46.78 | 17.13 | 10.63 | 34.86 | 39.42 | 15.27 | 7.72 | 29.32
ECCL4B | 400 | 46.83 | 17.15 | 10.63 | 34.89 | 39.53 | 15.31 | 7.76 | 29.41
ELVA4- | 400 | 61.29 | 23.28 | 10.17 | 43.09 | 47.36 | 19.09 | 6.87 | 33.86
FALL4- | 400 | 49.97 | 18.14 | 10.93 | 36.58 | 44.8 | 17.23 | 9.17 | 33.54
GRNA4- | 400 | 52.09 | 19.93 | 8.23 | 36.42 | 41.95 | 16.63 | 7.77 | 31.29
HUCS4- | 400 | 61 | 21.69 | 15.44 | 46.12 | 73.59 | 27.37 | 19.02 | 57.73
HUER4- | 400 | 61.45 | 21.84 | 15.55 | 46.44 | 74.01 | 27.53 | 19.08 | 58.01
HUNE4- | 400 | 61.43 | 21.83 | 15.54 | 46.41 | 74.02 | 27.53 | 19.08 | 58.02
KILS4- | 400 | 49.17 | 17.97 | 9.3 | 34.72 | 44.92 | 17.48 | 8.54 | 33.26
KILS4T | 400 | 41.14 | 15.52 | 7.68 | 29.63 | 34.79 | 13.8 | 5.79 | 25.31
MOFF4- | 400 | 46.11 | 17.67 | 7.26 | 32.25 | 37.3 | 14.95 | 6.02 | 27.16
STHA4A | 400 | 61.99 | 22.79 | 11.92 | 44.15 | 57.47 | 22.29 | 11.13 | 42.66
STHA4B | 400 | 55.39 | 20.62 | 11.33 | 40.49 | 50.73 | 19.73 | 10.26 | 38.16
TORN4- | 400 | 67.31 | 24.07 | 16.38 | 50.42 | 67.96 | 25.38 | 18.28 | 54.17
WISH4- | 400 | 54.6 | 20.23 | 9.74 | 38.34 | 50.77 | 19.75 | 9.78 | 37.71
AUCH2- | 275 | 14.53 | 5.29 | 1.96 | 9.44 | 14.69 | 5.8 | 1.83 | 10.03
BUSB2- | 275 | 53.97 | 20.22 | 9.98 | 38.57 | 49.19 | 19.55 | 7.39 | 35.04
CLYM2- | 275 | 83.46 | 30.36 | 17.22 | 60.16 | 77.34 | 30.05 | 14.73 | 57.23
CLYN2Q | 275 | 18.62 | 7.55 | 5.89 | 16.56 | 18.58 | 7.12 | 6.06 | 16.13
CLYS2R | 275 | 16.27 | 6.3 | 4.91 | 13.82 | 16.01 | 6.16 | 4.73 | 13.43
COCK2- | 275 | 58.21 | 21.31 | 12.41 | 42.55 | 56.67 | 21.97 | 11.15 | 42.22
COYL2- | 275 | 43.07 | 15.16 | 9.23 | 30.67 | 44.3 | 16.92 | 8.46 | 32.39
CURR2- | 275 | 56.11 | 20.58 | 10.44 | 39.55 | 54.42 | 21.2 | 10.06 | 40.04
DALL2- | 275 | 34.72 | 12.47 | 7.23 | 24.86 | 30.67 | 11.88 | 5.85 | 22.66
DENN2- | 275 | 64.01 | 23.54 | 12.6 | 45.89 | 58.56 | 22.75 | 11.53 | 43.71
EERH2- | 275 | 72.13 | 26.42 | 14.47 | 51.84 | 63.34 | 24.79 | 11.09 | 46.15
EKIS2- | 275 | 67.38 | 25.24 | 13.22 | 48.92 | 65.5 | 26.08 | 10.82 | 47.7
ELVA2Q | 275 | 19.3 | 7.73 | 6.8 | 17.73 | 18.57 | 7.25 | 5.56 | 15.82
ELVA2R | 275 | 16.84 | 6.4 | 6.25 | 15.3 | 16.49 | 6.25 | 5.3 | 14.13
GLRO2- | 275 | 41.12 | 15.96 | 5.82 | 28.4 | 34.47 | 13.91 | 5.17 | 24.84
GRMO2- | 275 | 45.61 | 17.11 | 8.53 | 32.73 | 39.11 | 15.43 | 7.38 | 29.2
INVR2- | 275 | 34.73 | 12.97 | 6.07 | 24.42 | 30.92 | 12.27 | 5.1 | 22.44
KAIM2- | 275 | 58.64 | 21.38 | 11.66 | 41.89 | 59.44 | 23.03 | 10.62 | 43.19
KILG2- | 275 | 18.03 | 6.36 | 2.8 | 11.79 | 20.57 | 7.82 | 3.7 | 14.75
KILS2- | 275 | 48.12 | 16.9 | 11.66 | 35.55 | 51.57 | 19.36 | 12.08 | 39.45
KINC2- | 275 | 59.89 | 22.11 | 13.68 | 44.95 | 48.13 | 19 | 8.39 | 35.25
LAMB2- | 275 | 61.67 | 22.74 | 11.24 | 43.4 | 52.06 | 20.66 | 8.51 | 37.72
LOAN2- | 275 | 83.5 | 30.48 | 16.84 | 59.94 | 65.1 | 25.85 | 9.62 | 46.17
MAHI2- | 275 | 19.26 | 6.74 | 3.06 | 12.59 | 21.65 | 8.18 | 3.8 | 15.37
MOSM2- | 275 | 49.51 | 18.96 | 7.32 | 34.13 | 41.76 | 16.7 | 6.88 | 30.5
NEAR2Q | 275 | 53.78 | 20.1 | 9.32 | 37.74 | 48.49 | 19.18 | 7.89 | 35
NECU2- | 275 | 37.03 | 13.19 | 7.52 | 26.17 | 36.06 | 13.88 | 7.04 | 26.67
NEIL2- | 275 | 66.35 | 24.34 | 14.33 | 48.75 | 61.07 | 23.76 | 12.27 | 45.87
SMEA2- | 275 | 59.73 | 21.74 | 13.19 | 43.94 | 63.12 | 24.17 | 13.25 | 47.43
STHA2A | 275 | 69.68 | 25.59 | 15.12 | 51.31 | 70.9 | 27.25 | 15.3 | 53.84
STHA2B | 275 | 74.89 | 27.65 | 16.17 | 55.27 | 75.31 | 29.2 | 15.98 | 57.28
WFIE2- | 275 | 54.65 | 20.86 | 8.22 | 37.72 | 46.92 | 18.72 | 7.8 | 34.27
WISH2- | 275 | 54.94 | 20.01 | 12.18 | 40.48 | 58.51 | 22.24 | 13.54 | 44.99
WIYH2- | 275 | 64.84 | 23.58 | 13.27 | 46.61 | 63.05 | 24.35 | 13.24 | 47.67
WLEE2- | 275 | 58.5 | 22.85 | 7.68 | 39.99 | 49.74 | 22.28 | 9.8 | 41.31
WLEX2- | 275 | 46.62 | 18.6 | 5.21 | 31.52 | 38.16 | 17 | 8.55 | 32.58
AREC1- | 132 | 13.54 | 4.46 | 1.62 | 7.93 | 16.49 | 5.94 | 2.32 | 10.72
BLAH1- | 132 | 27.9 | 9.44 | 4.47 | 17.81 | 29.36 | 10.83 | 4.78 | 20.09
BLCW1- | 132 | 8.57 | 3.08 | 0.94 | 5.29 | 8.37 | 3.22 | 0.97 | 5.52
BONN1- | 132 | 49.99 | 18.28 | 8.44 | 34.29 | 59.71 | 23.07 | 9.58 | 42.21
BRAP1- | 132 | 29.4 | 11.33 | 3.22 | 19.23 | 33.2 | 13.48 | 3.45 | 22.5
CHAP1- | 132 | 30.61 | 12.15 | 1.3 | 18.48 | 31.23 | 13.13 | 1.68 | 20.25
COAL1- | 132 | 19.98 | 6.63 | 5.63 | 15.01 | 25.05 | 8.91 | 6.39 | 18.98
COAL1A | 132 | 33.76 | 11.73 | 9.23 | 25.81 | 41.71 | 14.73 | 11.17 | 32
COYL1- | 132 | 30.94 | 11.27 | 5.4 | 21.34 | 36.58 | 14.2 | 6.11 | 26.2
CRYR1- | 132 | 14.88 | 4.93 | 4.41 | 11.39 | 16.21 | 5.7 | 5.08 | 13.14
CRYR1A | 132 | 15.42 | 6.13 | 4.77 | 13.44 | 17.38 | 6.55 | 5.56 | 14.82
CURR1A | 132 | 28.78 | 10.2 | 7.57 | 21.99 | 34.74 | 12.74 | 8.9 | 26.92
CURR1B | 132 | 19.84 | 7.04 | 5.07 | 15.03 | 23.47 | 8.63 | 5.99 | 18.19
DALM1- | 132 | 26.08 | 9.16 | 7.1 | 20.06 | 31.51 | 11.53 | 8.68 | 24.98
DEVM1- | 132 | 31.29 | 11.83 | 7.35 | 24.08 | 37.94 | 14.77 | 8.47 | 29.36
DEVO1- | 132 | 27.9 | 11.5 | 1.15 | 17.42 | 27.75 | 12.05 | 2.12 | 19.17
DUMF1- | 132 | 20.19 | 8.13 | 0.51 | 12.01 | 23.44 | 9.78 | 0.83 | 14.67
DUNE1- | 132 | 17.78 | 7.38 | 0.95 | 11.38 | 18.99 | 8 | 1.42 | 12.73
ECCL1- | 132 | 31.14 | 11.57 | 8.45 | 24.81 | 38.82 | 14.82 | 10.02 | 30.98
GALA1- | 132 | 19.94 | 8.48 | 0.37 | 12.36 | 20.55 | 8.97 | 0.89 | 13.58
GAWH1Q | 132 | 26.62 | 9.62 | 4.19 | 17.79 | 31.59 | 12.16 | 3.81 | 21
GLLE1- | 132 | 15.57 | 6.37 | 0.83 | 9.84 | 16.05 | 6.91 | 0.76 | 10.54
GLNI1- | 132 | 45.2 | 17.38 | 5.72 | 30.29 | 52.55 | 21.16 | 6.19 | 36.11
GRNA1- | 132 | 37.67 | 14.01 | 7.58 | 27.4 | 45.25 | 17.45 | 8.79 | 33.46
HAWI1- | 132 | 10.21 | 4.82 | 0.03 | 6.85 | 11.03 | 5.04 | 0.16 | 7.29
HELE1- | 132 | 18.07 | 8.63 | 0.04 | 12.24 | 18.71 | 8.79 | 0.24 | 12.68
HUER1- | 132 | 36.84 | 13.69 | 8.97 | 28.34 | 43.35 | 16.59 | 10.86 | 34.32
KEOO1- | 132 | 15.57 | 6.29 | 1.45 | 10.35 | 16.37 | 6.84 | 1.51 | 11.18
KILS1- | 132 | 30.67 | 12 | 4.13 | 21.09 | 30.35 | 12.38 | 5.33 | 22.83
KILW1Q | 132 | 25.33 | 10.04 | 2.15 | 16.35 | 24.64 | 10.2 | 1.96 | 16.38
KILW1R | 132 | 24.99 | 9.96 | 1.95 | 16.03 | 24.05 | 10.01 | 1.8 | 15.96
MAHI1- | 132 | 14.72 | 4.84 | 2.85 | 9.7 | 17.25 | 6.18 | 3.62 | 12.36
MARG1- | 132 | 8.75 | 3.13 | 1.01 | 5.44 | 8.5 | 3.27 | 0.94 | 5.55
MAYB1- | 132 | 19.85 | 7.6 | 0.51 | 11.26 | 19.5 | 8.21 | 0.73 | 12.34
MEAD1- | 132 | 29.21 | 11.46 | 2.2 | 18.4 | 27.68 | 11.46 | 2.04 | 18.24
MOFF1- | 132 | 26.06 | 8.99 | 6.71 | 19.43 | 32.97 | 11.94 | 8.69 | 25.57
MOSM1A | 132 | 42.51 | 16.46 | 5.24 | 28.51 | 50.27 | 20.22 | 6.38 | 34.97
MOSM1B | 132 | 42.4 | 16.42 | 5.17 | 28.4 | 50.28 | 20.23 | 6.3 | 34.92
NECU1- | 132 | 35.13 | 11.7 | 8.28 | 24.83 | 39.78 | 14.31 | 8.82 | 29.06
NEIL1- | 132 | 43.27 | 15.51 | 10.4 | 32.34 | 53.46 | 20.12 | 12.71 | 41.17
NETS1- | 132 | 11.94 | 5 | 0.29 | 7.36 | 12.51 | 5.4 | 0.52 | 8.16
REDH1- | 132 | 31.65 | 13.29 | 1.03 | 19.83 | 32.99 | 14.24 | 1.44 | 21.58
SMEA1- | 132 | 19.06 | 7.44 | 4.85 | 15.38 | 20.25 | 7.93 | 5.67 | 16.89
STLE1- | 132 | 23.02 | 10.41 | 0.19 | 14.91 | 22.77 | 10.41 | 0.64 | 15.36
TONG1- | 132 | 11.43 | 5.15 | 0.25 | 7.54 | 15.96 | 7.28 | 0.35 | 10.64
TORN1- | 132 | 30.47 | 10.54 | 8.08 | 22.99 | 36.31 | 13.09 | 10.22 | 28.72
WESE1- | 132 | 15.04 | 6.03 | 4.19 | 12.72 | 16.79 | 6.4 | 4.64 | 13.68
WFIE1A | 132 | 31.07 | 12.74 | 4.3 | 22.32 | 32.66 | 13.6 | 5.21 | 24.44
WFIE1B | 132 | 41.44 | 16.37 | 4.51 | 27.67 | 44.7 | 18.51 | 5.28 | 31.47
WISH1- | 132 | 15.52 | 4.66 | 4.37 | 10.95 | 18.93 | 6.39 | 5.43 | 14.46
WIYH1- | 132 | 47.35 | 17.93 | 10.19 | 35.55 | 58.37 | 23.05 | 12.62 | 45.22
AYR-3- | 33 | 40.79 | 14.14 | 10.37 | 30.37 | 5.94 | 4.12 | 0 | 5.82
BAGA3- | 33 | 42.48 | 14.2 | 3.64 | 23.73 | 4.49 | 3.11 | 0 | 4.4
BAIN3- | 33 | 30.96 | 11.01 | 6.17 | 21.73 | 2.99 | 2.07 | 0 | 2.93
BERW3- | 33 | 40.7 | 14.61 | 1.47 | 22.12 | 4.63 | 3.18 | 0 | 4.5
BLAH3A | 33 | 37.42 | 11.58 | 8.39 | 24.77 | 4.5 | 3.12 | 0 | 4.41
BLAH3B | 33 | 26.81 | 9.47 | 7.39 | 20.78 | 4.48 | 3.11 | 0 | 4.39
BLCW3- | 33 | 26.11 | 7.79 | 2.96 | 13.98 | 2.26 | 1.56 | 0 | 2.21
BONN3- | 33 | 43.22 | 13.76 | 8.24 | 27.7 | 4.55 | 3.16 | 0 | 4.47
BPGR3- | 33 | 96.03 | 29.16 | 21.66 | 62.89 | 6.04 | 4.18 | 0 | 5.91
BRAP3- | 33 | 29.21 | 10.47 | 4.89 | 19.69 | 4.4 | 3.04 | 0 | 4.3
BROX3- | 33 | 28.31 | 10.02 | 3.73 | 17.91 | 4.4 | 3.05 | 0 | 4.31
CATY3- | 33 | 30.29 | 10.59 | 4.72 | 19.69 | 2.98 | 2.07 | 0 | 2.92
CHAP3- | 33 | 48.25 | 17.62 | 4.53 | 29.46 | 4.53 | 3.14 | 0 | 4.44
CHAS3- | 33 | 49.31 | 17.08 | 10.29 | 34.44 | 5.9 | 4.09 | 0 | 5.78
CLYM3- | 33 | 50.59 | 17.73 | 11.39 | 36.47 | 5.94 | 4.12 | 0 | 5.82
CLYN3A | 33 | 41.93 | 18.18 | 8.04 | 33.75 | 3.01 | 2.09 | 0 | 2.96
CLYN3B | 33 | 42.03 | 18.22 | 8.06 | 33.82 | 3.02 | 2.09 | 0 | 2.96
CLYN3C | 33 | 41.91 | 18.17 | 8.07 | 33.76 | 3.01 | 2.09 | 0 | 2.96
CLYN3D | 33 | 41.94 | 18.18 | 7.98 | 33.7 | 3.01 | 2.09 | 0 | 2.96
CLYS3A | 33 | 37.89 | 15.84 | 7.86 | 30.25 | 3.01 | 2.09 | 0 | 2.95
CLYS3B | 33 | 37.83 | 15.82 | 7.76 | 30.14 | 3.01 | 2.09 | 0 | 2.95
COAT3- | 33 | 39.33 | 13.48 | 11.79 | 30.85 | 5.83 | 4.04 | 0 | 5.71
COCK3- | 33 | 42.09 | 14.76 | 11.02 | 31.9 | 5.87 | 4.06 | 0 | 5.75
COYL3- | 33 | 40.76 | 14.69 | 4.6 | 25.38 | 3 | 2.08 | 0 | 2.94
CROO3J | 33 | 34.34 | 12.61 | 3.62 | 21.45 | 2.98 | 2.07 | 0 | 2.92
CROO3K | 33 | 32.52 | 11.88 | 3.79 | 20.59 | 3 | 2.08 | 0 | 2.94
CUMB3- | 33 | 36.28 | 12.82 | 4.58 | 22.72 | 4.45 | 3.08 | 0 | 4.35
CUPA3- | 33 | 27.83 | 10.31 | 1.18 | 15.76 | 4.39 | 3.04 | 0 | 4.29
DALM3- | 33 | 32.24 | 11.21 | 7.75 | 23.6 | 4.46 | 3.09 | 0 | 4.37
DESA3- | 33 | 36.64 | 10.95 | 5.35 | 20.84 | 2.27 | 1.58 | 0 | 2.23
DEVM3- | 33 | 35.67 | 13.13 | 4.6 | 23.17 | 3.02 | 2.09 | 0 | 2.96
DEVO3- | 33 | 41.36 | 15.19 | 3.62 | 25.1 | 4.53 | 3.14 | 0 | 4.44
DEWP3- | 33 | 47.09 | 15.86 | 12.47 | 34.9 | 7.78 | 5.38 | 0 | 7.61
DRCR3- | 33 | 28.11 | 10.31 | 3.06 | 17.64 | 4.39 | 3.04 | 0 | 4.31
DRUM3- | 33 | 39.74 | 13.62 | 11.2 | 30.46 | 5.8 | 4.02 | 0 | 5.68
DUMF3A | 33 | 39.1 | 14.11 | 1.9 | 21.85 | 4.43 | 3.07 | 0 | 4.34
DUMF3B | 33 | 36.35 | 13.5 | 2 | 21.09 | 4.45 | 3.08 | 0 | 4.36
DUMF3I | 33 | 19.59 | 6.96 | 1.78 | 11.61 | 1.51 | 1.05 | 0 | 1.48
DUNB3- | 33 | 61.73 | 16.88 | 4.09 | 27.96 | 3.13 | 2.17 | 0 | 3.07
DUNE3- | 33 | 41.99 | 15.24 | 3.18 | 24.73 | 4.51 | 3.12 | 0 | 4.42
DUNF3- | 33 | 32.43 | 11.78 | 3.8 | 20.46 | 4.48 | 3.1 | 0 | 4.38
DUNH3- | 33 | 42.54 | 12.62 | 8.9 | 26.75 | 4.49 | 3.11 | 0 | 4.4
ECCL3- | 33 | 35.87 | 13.93 | 5.47 | 25.16 | 5.19 | 3.57 | 0 | 5.05
EERH3- | 33 | 45.96 | 15.67 | 13.75 | 35.91 | 5.84 | 4.05 | 0 | 5.72
EKIL3- | 33 | 52.7 | 18.36 | 14.73 | 40.7 | 5.95 | 4.12 | 0 | 5.83
EKIS3- | 33 | 56.31 | 19.11 | 10.2 | 37.23 | 5.97 | 4.14 | 0 | 5.86
ELDE3- | 33 | 39.01 | 14.07 | 5.05 | 24.95 | 2.99 | 2.07 | 0 | 2.93
ERSK3- | 33 | 27.96 | 10.15 | 4.45 | 18.8 | 2.96 | 2.05 | 0 | 2.91
EWEH3- | 33 | 27.99 | 9.29 | 2.46 | 15.6 | 2.26 | 1.57 | 0 | 2.22
FINN3- | 33 | 31.45 | 11.18 | 6.27 | 22.08 | 4.4 | 3.05 | 0 | 4.31
GALA3- | 33 | 37.63 | 14.08 | 2.19 | 22.1 | 4.87 | 3.37 | 0 | 4.76
GAWH3- | 33 | 34.68 | 10.65 | 6.96 | 22.01 | 2.28 | 1.58 | 0 | 2.24
GIFF3A | 33 | 36.14 | 12.7 | 7.77 | 25.73 | 5.3 | 3.67 | 0 | 5.19
GIFF3B | 33 | 36.26 | 12.74 | 7.83 | 25.84 | 5.31 | 3.67 | 0 | 5.19
GLGL3- | 33 | 36.3 | 11.22 | 6.29 | 22.16 | 4.47 | 3.1 | 0 | 4.38
GLLU3- | 33 | 37.57 | 14.13 | 0.55 | 20.54 | 4.11 | 2.85 | 0 | 4.03
GLNI3- | 33 | 36.21 | 13.22 | 6.13 | 24.83 | 4.48 | 3.11 | 0 | 4.39
GLRO3A | 33 | 34.47 | 12.15 | 8.18 | 25.36 | 5.38 | 3.72 | 0 | 5.26
GLRO3B | 33 | 32.78 | 11.51 | 8 | 24.28 | 5.39 | 3.72 | 0 | 5.27
GORG3- | 33 | 29.07 | 10.28 | 5.09 | 19.63 | 3.01 | 2.09 | 0 | 2.95
GOVA3- | 33 | 30.93 | 10.91 | 5.75 | 21.18 | 4.38 | 3.03 | 0 | 4.29
GRMO3A | 33 | 40.86 | 14.12 | 9.37 | 29.34 | 5.88 | 4.07 | 0 | 5.76
GRMO3C | 33 | 40.94 | 14.14 | 9.52 | 29.52 | 5.88 | 4.08 | 0 | 5.76
HAGR3- | 33 | 30.79 | 10.98 | 4.75 | 20.28 | 3 | 2.08 | 0 | 2.94
HAWI3- | 33 | 22.57 | 9.25 | 0.26 | 13.34 | 2.97 | 2.06 | 0 | 2.91
HELE3- | 33 | 26.4 | 10.45 | 0.78 | 15.55 | 2.96 | 2.05 | 0 | 2.9
HUNF3- | 33 | 42.89 | 16.57 | 6.39 | 29.83 | 2.98 | 2.07 | 0 | 2.93
INKE3- | 33 | 30.22 | 11.08 | 2.33 | 18 | 4.44 | 3.08 | 0 | 4.35
JOHN3- | 33 | 29.55 | 10.33 | 5.65 | 20.25 | 2.96 | 2.05 | 0 | 2.9
KAIM3- | 33 | 36.01 | 11.01 | 8.39 | 23.96 | 5.63 | 3.89 | 0 | 5.5
KIER3- | 33 | 34.72 | 12.12 | 5.75 | 22.89 | 4.41 | 3.05 | 0 | 4.31
KILB3- | 33 | 33.75 | 12.33 | 5.3 | 22.73 | 2.97 | 2.06 | 0 | 2.92
KILS3- | 33 | 41.52 | 14.42 | 10.09 | 30.48 | 5.94 | 4.12 | 0 | 5.82
KILT3- | 33 | 51.64 | 17.81 | 10.38 | 35.57 | 5.98 | 4.14 | 0 | 5.86
KILW3- | 33 | 32.2 | 11.67 | 5.14 | 21.65 | 4.4 | 3.05 | 0 | 4.31
LEVE3- | 33 | 38.7 | 14.74 | 1.39 | 22.24 | 3.03 | 2.1 | 0 | 2.97
LING3- | 33 | 47.43 | 15.12 | 4.21 | 25.59 | 4.48 | 3.11 | 0 | 4.39
LINM3- | 33 | 57 | 18.91 | 6.67 | 33.41 | 4.5 | 3.13 | 0 | 4.42
MAHI3- | 33 | 47.65 | 14.73 | 6.03 | 26.86 | 3.05 | 2.11 | 0 | 2.99
MAYB3- | 33 | 29 | 10.26 | 1.26 | 15.78 | 1.54 | 1.07 | 0 | 1.51
NEAR3- | 33 | 51.48 | 17.75 | 10.45 | 35.55 | 5.91 | 4.09 | 0 | 5.79
NETS3- | 33 | 20.27 | 7.68 | 1.01 | 11.87 | 3.13 | 2.15 | 0 | 3.04
PAIS3- | 33 | 33.55 | 11.99 | 6.12 | 23.08 | 2.98 | 2.07 | 0 | 2.92
PART3- | 33 | 35.99 | 13.11 | 4.47 | 23.01 | 2.97 | 2.06 | 0 | 2.92
POOB3- | 33 | 55.11 | 19.17 | 12.36 | 39.47 | 5.92 | 4.1 | 0 | 5.8
PORD3- | 33 | 50.33 | 17.56 | 12.25 | 37.08 | 6.02 | 4.17 | 0 | 5.9
RAVE3- | 33 | 41.32 | 15.54 | 3.26 | 25.24 | 5.84 | 4.05 | 0 | 5.73
REDH3- | 33 | 38.41 | 14.31 | 3.07 | 23.31 | 3.75 | 2.6 | 0 | 3.68
SACO3J | 33 | 40.99 | 14.75 | 4.21 | 25.07 | 3.03 | 2.1 | 0 | 2.97
SACO3K | 33 | 40.38 | 15.05 | 3.94 | 25.23 | 3 | 2.08 | 0 | 2.94
SANX3- | 33 | 32.22 | 11.42 | 5.01 | 21.16 | 2.97 | 2.06 | 0 | 2.91
SHRU3- | 33 | 46.5 | 16.14 | 10.08 | 32.9 | 5.95 | 4.12 | 0 | 5.83
SIGH3A | 33 | 43.5 | 15 | 10.8 | 32.02 | 4.51 | 3.12 | 0 | 4.42
SIGH3B | 33 | 43.38 | 14.97 | 10.6 | 31.77 | 4.51 | 3.12 | 0 | 4.42
SPAV3- | 33 | 27.7 | 10 | 3.74 | 17.88 | 4.33 | 3 | 0 | 4.24
STHA3- | 33 | 53.84 | 19.24 | 11.79 | 39.01 | 6.02 | 4.17 | 0 | 5.9
STIR3- | 33 | 39.8 | 13.74 | 6.53 | 25.96 | 4.45 | 3.08 | 0 | 4.36
STLE3S | 33 | 34.66 | 12.98 | 2.2 | 20.56 | 3.01 | 2.09 | 0 | 2.96
TELR3- | 33 | 28.03 | 9.98 | 3.69 | 17.81 | 3.01 | 2.08 | 0 | 2.95
WFIE3- | 33 | 45.87 | 17.03 | 4.86 | 28.95 | 3.06 | 2.12 | 0 | 3
WGEO3- | 33 | 50.15 | 17.58 | 10.16 | 35.02 | 6 | 4.16 | 0 | 5.89
WHHO3- | 33 | 42.64 | 14.89 | 9.88 | 30.94 | 5.93 | 4.11 | 0 | 5.81
WHTL3- | 33 | 26.31 | 10.49 | 0.8 | 15.64 | 2.24 | 1.55 | 0 | 2.2
WISH3- | 33 | 42.98 | 14.8 | 10.17 | 31.09 | 5.89 | 4.08 | 0 | 5.77
WLEE3A | 33 | 50.18 | 20.97 | 10.43 | 40.09 | 3.04 | 2.11 | 0 | 2.98
WLEE3B | 33 | 50.38 | 21.05 | 10.42 | 40.19 | 3.04 | 2.11 | 0 | 2.98
WLEE3C | 33 | 49.8 | 20.78 | 10.37 | 39.76 | 3.04 | 2.11 | 0 | 2.98
WLEX3A | 33 | 57.86 | 20.28 | 9.27 | 37.96 | 3.07 | 2.13 | 0 | 3.01
WLEX3B | 33 | 58.11 | 20.37 | 9.27 | 38.08 | 3.07 | 2.13 | 0 | 3.01
WLEX3C | 33 | 55.63 | 19.49 | 9.26 | 36.82 | 3.07 | 2.13 | 0 | 3.01
BAGA0J | 25 | 16.26 | 5.95 | 3.62 | 12.04 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.25 | 5.95 | 3.62 | 12.03 | 0 | 0 | 0 | 0
BONN0J | 25 | 18.01 | 6.48 | 5.32 | 14.49 | 0 | 0 | 0 | 0
BONN0K | 25 | 18.01 | 6.48 | 5.32 | 14.49 | 0 | 0 | 0 | 0
BONN0L | 25 | 18.01 | 6.48 | 5.32 | 14.49 | 0 | 0 | 0 | 0
CATY0J | 25 | 10.05 | 3.71 | 1.72 | 6.97 | 0 | 0 | 0 | 0
CATY0K | 25 | 10.06 | 3.71 | 1.75 | 7 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.3 | 3 | 2.56 | 6.81 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.3 | 3 | 2.56 | 6.81 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.68 | 6.03 | 1.35 | 9.87 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.35 | 7.25 | 2.77 | 13.02 | 0 | 0 | 0 | 0
ELVA0J | 25 | 19.13 | 6.77 | 8.09 | 17.68 | 0 | 0 | 0 | 0
ELVA0K | 25 | 19.13 | 6.77 | 8.09 | 17.67 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.08 | 3.97 | 3.41 | 9.02 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.08 | 3.97 | 3.41 | 9.02 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.82 | 3.64 | 1.9 | 7.04 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.82 | 3.64 | 1.91 | 7.05 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.65 | 6.73 | 5.63 | 15.14 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.65 | 6.73 | 5.63 | 15.14 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.56 | 3.82 | 2.91 | 8.32 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.52 | 3.81 | 2.85 | 8.25 | 0 | 0 | 0 | 0
SANX0J | 25 | 16.97 | 6.09 | 4.68 | 13.29 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.95 | 6.08 | 4.62 | 13.22 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.43 | 3.81 | 2.31 | 7.69 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.43 | 3.81 | 2.31 | 7.69 | 0 | 0 | 0 | 0
WISH0J | 25 | 20.99 | 7.54 | 6.43 | 17.09 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.99 | 7.54 | 6.43 | 17.09 | 0 | 0 | 0 | 0
CAFA5- | 11 | 30.06 | 10.87 | 5.21 | 20.59 | 2.25 | 1.56 | 0 | 2.2
CURR5- | 11 | 34.63 | 12.47 | 5.74 | 23.38 | 4.48 | 3.1 | 0 | 4.39
EAST5- | 11 | 23.93 | 9.12 | 2.42 | 15.33 | 1.15 | 0.8 | 0 | 1.13
GLLE5- | 11 | 33.01 | 12.12 | 6.93 | 24.07 | 2.3 | 1.59 | 0 | 2.25
KEOO5- | 11 | 32.46 | 11.91 | 5.31 | 22.15 | 2.25 | 1.56 | 0 | 2.21
KILB5- | 11 | 29 | 10.59 | 4.14 | 19.11 | 3.01 | 2.08 | 0 | 2.95
TONG5- | 11 | 77.53 | 29.79 | 4.76 | 46.89 | 4.56 | 3.16 | 0 | 4.47

## D2.2
ETYS 19 Yr 2 - SPT Fault Levels (kA), Winter 2020/21
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
COAL4- | 400 | 54.72 | 20.51 | 9.94 | 38.95 | 47.04 | 18.67 | 8.01 | 34.41 | Back To Menu
CRYR4- | 400 | 57.46 | 20.76 | 13 | 42.36 | 53.94 | 20.6 | 11.57 | 40.7
DENN4- | 400 | 21.21 | 7.75 | 6.04 | 16.99 | 19.75 | 7.46 | 5.27 | 15.81
DEVM4- | 400 | 33.62 | 12.51 | 7.06 | 24.76 | 29.07 | 11.41 | 5.6 | 21.73
ECCL4A | 400 | 47.09 | 17.24 | 10.68 | 35.06 | 39.57 | 15.33 | 7.72 | 29.4
ECCL4B | 400 | 47.14 | 17.26 | 10.68 | 35.09 | 39.67 | 15.37 | 7.75 | 29.49
ELVA4- | 400 | 61.7 | 23.37 | 10.27 | 43.31 | 47.58 | 19.17 | 6.9 | 34.01
FALL4- | 400 | 50.26 | 18.24 | 10.95 | 36.74 | 44.95 | 17.29 | 9.19 | 33.63
GRNA4- | 400 | 52.01 | 19.85 | 8.26 | 36.34 | 41.85 | 16.58 | 7.76 | 31.21
HUCS4- | 400 | 61.4 | 21.81 | 15.44 | 46.28 | 73.93 | 27.5 | 18.96 | 57.84
HUER4- | 400 | 61.85 | 21.96 | 15.54 | 46.6 | 74.35 | 27.66 | 19.02 | 58.13
HUNE4- | 400 | 61.83 | 21.96 | 15.53 | 46.58 | 74.36 | 27.66 | 19.02 | 58.13
KILS4- | 400 | 51.72 | 18.88 | 10.88 | 37.58 | 47.27 | 18.31 | 9.88 | 35.77
KILS4T | 400 | 48.8 | 17.97 | 10.53 | 35.94 | 43.98 | 17.09 | 9.23 | 33.39
MOFF4- | 400 | 46.24 | 17.69 | 7.3 | 32.31 | 37.37 | 14.97 | 6.01 | 27.19
STHA4A | 400 | 62.44 | 22.96 | 12.13 | 44.6 | 57.81 | 22.42 | 11.28 | 42.99
STHA4B | 400 | 58.22 | 21.54 | 12 | 42.47 | 53.5 | 20.78 | 10.84 | 40.22
TORN4- | 400 | 67.87 | 24.25 | 16.43 | 50.72 | 68.4 | 25.54 | 18.34 | 54.46
WISH4- | 400 | 54.83 | 20.32 | 9.82 | 38.56 | 50.92 | 19.81 | 9.84 | 37.86
AUCH2- | 275 | 15 | 5.52 | 1.97 | 9.78 | 15.01 | 5.96 | 1.82 | 10.24
BUSB2- | 275 | 54.06 | 20.25 | 9.99 | 38.63 | 49.22 | 19.56 | 7.39 | 35.06
CLYM2- | 275 | 83.66 | 30.44 | 17.27 | 60.31 | 76.54 | 29.77 | 14.54 | 56.64
CLYN2Q | 275 | 18.66 | 7.56 | 5.91 | 16.6 | 18.62 | 7.14 | 6.08 | 16.17
CLYS2R | 275 | 16.65 | 6.38 | 4.99 | 14.01 | 16.37 | 6.28 | 4.81 | 13.69
COCK2- | 275 | 58.56 | 21.44 | 12.56 | 42.87 | 56.86 | 22.03 | 11.23 | 42.39
COYL2- | 275 | 52.56 | 18.67 | 11.38 | 37.78 | 51.81 | 19.94 | 9.69 | 37.89
CURR2- | 275 | 56.43 | 20.71 | 10.57 | 39.86 | 54.5 | 21.23 | 10.13 | 40.15
DALL2- | 275 | 34.69 | 12.46 | 7.23 | 24.85 | 30.65 | 11.88 | 5.85 | 22.65
DENN2- | 275 | 64.09 | 23.59 | 12.63 | 45.98 | 58.54 | 22.75 | 11.53 | 43.71
EERH2- | 275 | 72.26 | 26.47 | 14.5 | 51.94 | 63.14 | 24.72 | 11.07 | 46.03
EKIS2- | 275 | 67.58 | 25.3 | 13.32 | 49.1 | 65.62 | 26.11 | 10.89 | 47.81
ELVA2Q | 275 | 19.34 | 7.74 | 6.83 | 17.77 | 18.61 | 7.27 | 5.58 | 15.86
ELVA2R | 275 | 17.22 | 6.48 | 6.32 | 15.48 | 16.84 | 6.37 | 5.35 | 14.35
GLRO2- | 275 | 41.23 | 16.01 | 5.86 | 28.51 | 34.51 | 13.93 | 5.19 | 24.88
GRMO2- | 275 | 45.74 | 17.17 | 8.55 | 32.83 | 39.19 | 15.46 | 7.39 | 29.27
INVR2- | 275 | 34.69 | 12.96 | 6.07 | 24.4 | 30.88 | 12.25 | 5.1 | 22.42
KAIM2- | 275 | 59.02 | 21.52 | 11.83 | 42.27 | 59.49 | 23.05 | 10.71 | 43.31
KILG2- | 275 | 18.8 | 6.7 | 2.85 | 12.32 | 21.29 | 8.14 | 3.78 | 15.29
KILS2- | 275 | 62.25 | 21.91 | 15.92 | 46.9 | 65.89 | 24.76 | 15.84 | 50.86
KINC2- | 275 | 60.07 | 22.2 | 13.73 | 45.12 | 48.21 | 19.03 | 8.4 | 35.31
LAMB2- | 275 | 61.7 | 22.77 | 11.24 | 43.44 | 51.88 | 20.6 | 8.45 | 37.58
LOAN2- | 275 | 83.7 | 30.57 | 16.91 | 60.14 | 65.12 | 25.86 | 9.63 | 46.2
MAHI2- | 275 | 20.19 | 7.14 | 3.13 | 13.23 | 22.49 | 8.55 | 3.87 | 15.96
MOSM2- | 275 | 49.63 | 19.02 | 7.39 | 34.28 | 41.76 | 16.7 | 6.89 | 30.51
NEAR2Q | 275 | 53.85 | 20.13 | 9.33 | 37.8 | 48.48 | 19.17 | 7.9 | 35.02
NECU2- | 275 | 43.34 | 15.61 | 8.75 | 30.83 | 40.32 | 15.64 | 7.78 | 29.89
NEIL2- | 275 | 66.55 | 24.41 | 14.36 | 48.88 | 61.18 | 23.8 | 12.28 | 45.94
SMEA2- | 275 | 60.08 | 21.87 | 13.32 | 44.25 | 63.27 | 24.22 | 13.34 | 47.6
STHA2A | 275 | 69.78 | 25.63 | 15.14 | 51.38 | 70.82 | 27.22 | 15.3 | 53.8
STHA2B | 275 | 75.23 | 27.75 | 16.36 | 55.6 | 75.59 | 29.28 | 16.2 | 57.6
WFIE2- | 275 | 54.8 | 20.94 | 8.29 | 37.89 | 46.93 | 18.73 | 7.81 | 34.3
WISH2- | 275 | 55.04 | 20.06 | 12.24 | 40.6 | 58.57 | 22.26 | 13.6 | 45.08
WIYH2- | 275 | 64.86 | 23.59 | 13.27 | 46.63 | 63.01 | 24.34 | 13.23 | 47.65
WLEE2- | 275 | 58.66 | 22.9 | 7.72 | 40.11 | 49.84 | 22.32 | 9.83 | 41.4
WLEX2- | 275 | 46.66 | 18.62 | 5.2 | 31.53 | 37.94 | 16.96 | 8.59 | 32.58
AREC1- | 132 | 13.64 | 4.5 | 1.63 | 8 | 16.59 | 5.98 | 2.34 | 10.79
BLAH1- | 132 | 28.8 | 9.81 | 4.65 | 18.52 | 30.12 | 11.13 | 4.94 | 20.69
BLCW1- | 132 | 8.68 | 3.12 | 0.95 | 5.37 | 8.45 | 3.25 | 0.99 | 5.59
BONN1- | 132 | 49.95 | 18.29 | 8.44 | 34.31 | 59.6 | 23.05 | 9.56 | 42.15
BRAP1- | 132 | 29.78 | 11.49 | 3.23 | 19.47 | 33.38 | 13.56 | 3.45 | 22.63
CHAP1- | 132 | 30.89 | 12.3 | 1.27 | 18.67 | 31.53 | 13.3 | 1.65 | 20.45
COAL1- | 132 | 19.62 | 6.51 | 5.48 | 14.68 | 24.54 | 8.72 | 6.26 | 18.6
COAL1A | 132 | 33.06 | 11.46 | 9.19 | 25.4 | 40.69 | 14.35 | 11.23 | 31.53
COYL1- | 132 | 31.88 | 11.67 | 5.8 | 22.31 | 37.57 | 14.6 | 6.49 | 27.14
CRYR1- | 132 | 15.66 | 5.16 | 4.35 | 11.66 | 16.51 | 5.8 | 5.05 | 13.24
CRYR1A | 132 | 15.37 | 6.15 | 4.72 | 13.43 | 16.94 | 6.4 | 5.37 | 14.42
CURR1A | 132 | 36.1 | 12.6 | 9.19 | 27.01 | 44.61 | 16.33 | 11 | 34.09
CURR1B | 132 | 36.1 | 12.6 | 9.19 | 27.01 | 44.61 | 16.33 | 11 | 34.09
DALM1- | 132 | 26.22 | 9.22 | 7.11 | 20.15 | 31.66 | 11.59 | 8.69 | 25.08
DEVM1- | 132 | 31.44 | 11.91 | 7.37 | 24.21 | 38.02 | 14.81 | 8.48 | 29.43
DEVO1- | 132 | 27.88 | 11.51 | 1.15 | 17.43 | 27.71 | 12.04 | 2.12 | 19.15
DUMF1- | 132 | 20.17 | 8.17 | 0.5 | 12.06 | 23.46 | 9.82 | 0.81 | 14.7
DUNE1- | 132 | 17.83 | 7.4 | 0.95 | 11.41 | 19.03 | 8.02 | 1.42 | 12.76
ECCL1- | 132 | 31.24 | 11.61 | 8.48 | 24.89 | 38.94 | 14.87 | 10.05 | 31.08
GALA1- | 132 | 20 | 8.51 | 0.37 | 12.4 | 20.61 | 9 | 0.9 | 13.62
GAWH1Q | 132 | 26.23 | 9.45 | 4.27 | 17.64 | 31.06 | 11.91 | 3.88 | 20.72
GLLE1- | 132 | 15.64 | 6.4 | 0.83 | 9.88 | 16.11 | 6.94 | 0.76 | 10.58
GLNI1- | 132 | 45.76 | 17.6 | 5.94 | 30.84 | 52.84 | 21.27 | 6.32 | 36.4
GRNA1- | 132 | 38.43 | 14.28 | 7.63 | 27.83 | 46.35 | 17.86 | 8.84 | 34.09
HAWI1- | 132 | 10.24 | 4.85 | 0.03 | 6.89 | 10.99 | 5.03 | 0.16 | 7.28
HELE1- | 132 | 18.06 | 8.62 | 0.04 | 12.23 | 18.71 | 8.79 | 0.24 | 12.68
HUER1- | 132 | 37 | 13.78 | 8.99 | 28.47 | 43.55 | 16.68 | 10.87 | 34.47
KEOO1- | 132 | 15.67 | 6.33 | 1.46 | 10.42 | 16.45 | 6.87 | 1.52 | 11.24
KILS1- | 132 | 31.4 | 12.34 | 4.38 | 21.83 | 30.91 | 12.62 | 5.59 | 23.43
KILW1Q | 132 | 25.5 | 10.12 | 2.16 | 16.48 | 24.85 | 10.29 | 1.98 | 16.54
KILW1R | 132 | 25.16 | 10.04 | 1.96 | 16.16 | 24.26 | 10.1 | 1.83 | 16.11
MAHI1- | 132 | 14.81 | 4.89 | 2.81 | 9.73 | 17.19 | 6.19 | 3.52 | 12.27
MARG1- | 132 | 8.87 | 3.18 | 1.03 | 5.53 | 8.58 | 3.3 | 0.95 | 5.61
MAYB1- | 132 | 20.1 | 7.74 | 0.5 | 11.46 | 19.67 | 8.3 | 0.73 | 12.47
MEAD1- | 132 | 29.54 | 11.63 | 2.22 | 18.67 | 28.04 | 11.62 | 2.07 | 18.5
MOFF1- | 132 | 26.08 | 9 | 6.71 | 19.44 | 32.86 | 11.9 | 8.64 | 25.47
MOSM1A | 132 | 42.97 | 16.65 | 5.41 | 28.95 | 50.54 | 20.32 | 6.52 | 35.26
MOSM1B | 132 | 42.86 | 16.62 | 5.34 | 28.84 | 50.55 | 20.34 | 6.44 | 35.2
NECU1- | 132 | 36.66 | 12.3 | 8.92 | 26.31 | 41.04 | 14.81 | 9.3 | 30.24
NEIL1- | 132 | 43.61 | 15.65 | 10.43 | 32.55 | 53.74 | 20.23 | 12.74 | 41.35
NETS1- | 132 | 11.98 | 5.02 | 0.29 | 7.39 | 12.54 | 5.42 | 0.52 | 8.18
REDH1- | 132 | 31.75 | 13.37 | 1.03 | 19.93 | 33.01 | 14.26 | 1.45 | 21.61
SMEA1- | 132 | 19.11 | 7.47 | 4.87 | 15.43 | 20.3 | 7.95 | 5.69 | 16.93
STLE1- | 132 | 23 | 10.4 | 0.19 | 14.9 | 22.63 | 10.36 | 0.64 | 15.28
TONG1- | 132 | 11.45 | 5.15 | 0.24 | 7.52 | 16.03 | 7.32 | 0.33 | 10.68
TORN1- | 132 | 31.95 | 10.88 | 8.32 | 23.71 | 38.11 | 13.69 | 10.53 | 29.89
WESE1- | 132 | 15.01 | 6.06 | 4.18 | 12.75 | 16.42 | 6.26 | 4.63 | 13.48
WFIE1A | 132 | 31.06 | 12.77 | 4.29 | 22.35 | 32.55 | 13.56 | 5.19 | 24.37
WFIE1B | 132 | 41.77 | 16.53 | 4.58 | 27.96 | 44.81 | 18.57 | 5.36 | 31.62
WISH1- | 132 | 15.53 | 4.66 | 4.35 | 10.94 | 18.9 | 6.38 | 5.41 | 14.43
WIYH1- | 132 | 47.23 | 17.89 | 10.18 | 35.48 | 58.26 | 23.01 | 12.61 | 45.14
AYR-3- | 33 | 41.42 | 14.41 | 10.77 | 31.15 | 5.93 | 4.11 | 0 | 5.81
BAGA3- | 33 | 42.51 | 14.22 | 3.64 | 23.74 | 4.49 | 3.11 | 0 | 4.4
BAIN3- | 33 | 30.96 | 11.01 | 6.17 | 21.74 | 2.99 | 2.07 | 0 | 2.93
BERW3- | 33 | 40.78 | 14.64 | 1.47 | 22.17 | 4.64 | 3.19 | 0 | 4.51
BLAH3A | 33 | 37.88 | 11.8 | 8.49 | 25.17 | 4.49 | 3.11 | 0 | 4.4
BLAH3B | 33 | 26.9 | 9.53 | 7.48 | 20.96 | 4.47 | 3.09 | 0 | 4.38
BLCW3- | 33 | 26.19 | 7.86 | 2.93 | 14.05 | 2.24 | 1.56 | 0 | 2.2
BONN3- | 33 | 42.67 | 13.56 | 8.2 | 27.38 | 4.49 | 3.12 | 0 | 4.42
BPGR3- | 33 | 95.73 | 29.11 | 21.54 | 62.71 | 6.06 | 4.2 | 0 | 5.94
BRAP3- | 33 | 29.28 | 10.49 | 4.92 | 19.76 | 4.39 | 3.04 | 0 | 4.3
BROX3- | 33 | 28.56 | 10.12 | 3.8 | 18.11 | 4.35 | 3.01 | 0 | 4.26
CATY3- | 33 | 30.39 | 10.62 | 4.72 | 19.75 | 2.99 | 2.07 | 0 | 2.93
CHAP3- | 33 | 48.31 | 17.66 | 4.52 | 29.5 | 4.53 | 3.14 | 0 | 4.44
CHAS3A | 33 | 43.87 | 15.05 | 9.54 | 30.82 | 5.84 | 4.05 | 0 | 5.72
CHAS3B | 33 | 43.87 | 15.05 | 9.54 | 30.82 | 5.84 | 4.05 | 0 | 5.72
CLYM3- | 33 | 50.61 | 17.75 | 11.41 | 36.51 | 5.96 | 4.13 | 0 | 5.84
CLYN3A | 33 | 41.97 | 18.19 | 8.06 | 33.79 | 3.02 | 2.09 | 0 | 2.96
CLYN3B | 33 | 42.07 | 18.23 | 8.08 | 33.86 | 3.02 | 2.09 | 0 | 2.96
CLYN3C | 33 | 41.95 | 18.18 | 8.08 | 33.8 | 3.02 | 2.09 | 0 | 2.96
CLYN3D | 33 | 41.98 | 18.2 | 8 | 33.74 | 3.02 | 2.09 | 0 | 2.96
CLYS3A | 33 | 38.07 | 15.87 | 7.91 | 30.35 | 3.02 | 2.09 | 0 | 2.96
CLYS3B | 33 | 43.05 | 16.89 | 8.14 | 32.02 | 3.02 | 2.09 | 0 | 2.96
COAT3- | 33 | 39.36 | 13.49 | 11.8 | 30.88 | 5.85 | 4.05 | 0 | 5.73
COCK3- | 33 | 42.22 | 14.81 | 11.08 | 32.02 | 5.89 | 4.08 | 0 | 5.78
COYL3- | 33 | 41.04 | 14.82 | 4.71 | 25.67 | 2.99 | 2.08 | 0 | 2.94
CROO3J | 33 | 34.49 | 12.67 | 3.63 | 21.55 | 3 | 2.08 | 0 | 2.94
CROO3K | 33 | 32.7 | 11.95 | 3.8 | 20.7 | 3.02 | 2.09 | 0 | 2.96
CUMB3- | 33 | 36.33 | 12.84 | 4.58 | 22.74 | 4.46 | 3.09 | 0 | 4.37
CUPA3- | 33 | 27.52 | 10.18 | 1.24 | 15.65 | 4.31 | 2.98 | 0 | 4.22
DALM3- | 33 | 32.89 | 11.45 | 7.74 | 23.93 | 4.49 | 3.11 | 0 | 4.4
DESA3- | 33 | 36.97 | 11.13 | 5.33 | 21.07 | 2.26 | 1.56 | 0 | 2.21
DEVM3- | 33 | 35.55 | 13.09 | 4.57 | 23.08 | 2.98 | 2.07 | 0 | 2.92
DEVO3- | 33 | 41.35 | 15.19 | 3.62 | 25.11 | 4.52 | 3.13 | 0 | 4.43
DEWP3- | 33 | 48.63 | 16.52 | 12.34 | 35.7 | 7.8 | 5.4 | 0 | 7.64
DRCR3- | 33 | 28.1 | 10.31 | 3.05 | 17.64 | 4.4 | 3.05 | 0 | 4.31
DRUM3- | 33 | 39.74 | 13.62 | 11.21 | 30.47 | 5.84 | 4.04 | 0 | 5.72
DUMF3A | 33 | 38.66 | 14.07 | 1.89 | 21.79 | 4.43 | 3.07 | 0 | 4.34
DUMF3B | 33 | 35.92 | 13.47 | 1.99 | 21.03 | 4.45 | 3.08 | 0 | 4.36
DUMF3I | 33 | 19.59 | 6.96 | 1.77 | 11.62 | 1.51 | 1.05 | 0 | 1.48
DUNB3A | 33 | 45.91 | 13.68 | 3.65 | 22.99 | 3.04 | 2.11 | 0 | 2.99
DUNB3B | 33 | 44.15 | 13.3 | 5.72 | 24.54 | 4.53 | 3.14 | 0 | 4.44
DUNE3- | 33 | 42.05 | 15.27 | 3.18 | 24.77 | 4.51 | 3.12 | 0 | 4.42
DUNF3- | 33 | 32.05 | 11.64 | 3.84 | 20.3 | 4.39 | 3.04 | 0 | 4.3
DUNH3- | 33 | 42.98 | 12.84 | 8.99 | 27.15 | 4.47 | 3.09 | 0 | 4.38
ECCL3- | 33 | 36.01 | 13.98 | 5.48 | 25.26 | 5.21 | 3.58 | 0 | 5.06
EERH3- | 33 | 46.01 | 15.69 | 13.77 | 35.95 | 5.86 | 4.06 | 0 | 5.74
EKIL3- | 33 | 52.75 | 18.38 | 14.75 | 40.75 | 5.96 | 4.13 | 0 | 5.84
EKIS3- | 33 | 56.35 | 19.13 | 10.21 | 37.27 | 5.99 | 4.15 | 0 | 5.87
ELDE3- | 33 | 39.49 | 14.25 | 5.07 | 25.22 | 3.01 | 2.09 | 0 | 2.95
ERSK3- | 33 | 29.71 | 10.85 | 4.49 | 19.83 | 3.01 | 2.09 | 0 | 2.95
EWEH3- | 33 | 35.71 | 11.12 | 2.82 | 18.54 | 2.25 | 1.56 | 0 | 2.21
FINN3- | 33 | 31.49 | 11.2 | 6.28 | 22.12 | 4.42 | 3.06 | 0 | 4.33
GALA3- | 33 | 37.77 | 14.14 | 2.19 | 22.19 | 4.88 | 3.38 | 0 | 4.77
GAWH3- | 33 | 34.55 | 10.62 | 6.94 | 21.96 | 2.26 | 1.57 | 0 | 2.22
GIFF3A | 33 | 36.19 | 12.71 | 7.78 | 25.76 | 5.32 | 3.68 | 0 | 5.2
GIFF3B | 33 | 36.31 | 12.76 | 7.84 | 25.88 | 5.32 | 3.68 | 0 | 5.2
GLGL3- | 33 | 36.66 | 11.39 | 6.3 | 22.41 | 4.47 | 3.1 | 0 | 4.38
GLLU3- | 33 | 37.76 | 14.21 | 0.55 | 20.64 | 4.11 | 2.85 | 0 | 4.03
GLNI3- | 33 | 39.08 | 14.32 | 6.52 | 26.78 | 4.46 | 3.09 | 0 | 4.38
GLRO3A | 33 | 34.57 | 12.19 | 8.21 | 25.44 | 5.39 | 3.73 | 0 | 5.27
GLRO3B | 33 | 32.87 | 11.54 | 8.02 | 24.35 | 5.4 | 3.74 | 0 | 5.28
GORG3- | 33 | 28.93 | 10.25 | 5.15 | 19.64 | 2.97 | 2.06 | 0 | 2.91
GOVA3- | 33 | 31.11 | 10.97 | 5.79 | 21.3 | 4.41 | 3.05 | 0 | 4.32
GRMO3A | 33 | 40.95 | 14.15 | 9.4 | 29.41 | 5.91 | 4.09 | 0 | 5.79
GRMO3C | 33 | 41.04 | 14.17 | 9.54 | 29.59 | 5.91 | 4.09 | 0 | 5.79
HAGR3- | 33 | 30.52 | 10.87 | 4.81 | 20.18 | 2.97 | 2.06 | 0 | 2.91
HAWI3- | 33 | 22.62 | 9.26 | 0.27 | 13.37 | 2.93 | 2.03 | 0 | 2.87
HELE3- | 33 | 26.41 | 10.45 | 0.78 | 15.56 | 2.97 | 2.05 | 0 | 2.91
HUNF3- | 33 | 42.98 | 16.62 | 6.39 | 29.89 | 2.99 | 2.08 | 0 | 2.94
INKE3- | 33 | 29.91 | 10.96 | 2.38 | 17.87 | 4.36 | 3.02 | 0 | 4.27
JOHN3- | 33 | 29.68 | 10.38 | 5.67 | 20.35 | 2.98 | 2.06 | 0 | 2.92
KAIM3- | 33 | 35.91 | 10.97 | 8.39 | 23.9 | 5.63 | 3.88 | 0 | 5.49
KIER3- | 33 | 34.77 | 12.13 | 5.76 | 22.92 | 4.44 | 3.07 | 0 | 4.35
KILB3- | 33 | 33.8 | 12.34 | 5.31 | 22.77 | 2.99 | 2.07 | 0 | 2.93
KILS3- | 33 | 42.27 | 14.72 | 10.54 | 31.36 | 5.95 | 4.12 | 0 | 5.83
KILT3- | 33 | 52.85 | 18.29 | 10.92 | 36.78 | 6.03 | 4.18 | 0 | 5.91
KILW3- | 33 | 32.62 | 11.83 | 5.15 | 21.87 | 4.49 | 3.11 | 0 | 4.4
LEVE3- | 33 | 38.64 | 14.73 | 1.38 | 22.21 | 3.03 | 2.1 | 0 | 2.97
LING3- | 33 | 47.98 | 15.37 | 4.18 | 25.92 | 4.49 | 3.11 | 0 | 4.41
LINM3- | 33 | 57.63 | 19.18 | 6.69 | 33.82 | 4.51 | 3.13 | 0 | 4.43
MAHI3- | 33 | 47.66 | 14.75 | 6.09 | 26.95 | 3.03 | 2.11 | 0 | 2.98
MAYB3- | 33 | 29.03 | 10.29 | 1.26 | 15.82 | 1.53 | 1.06 | 0 | 1.51
NEAR3- | 33 | 51.52 | 17.76 | 10.46 | 35.57 | 5.93 | 4.1 | 0 | 5.81
NETS3- | 33 | 20.26 | 7.68 | 1.01 | 11.88 | 3.12 | 2.15 | 0 | 3.03
PAIS3- | 33 | 33.75 | 12.07 | 6.15 | 23.21 | 3 | 2.08 | 0 | 2.94
PART3- | 33 | 36.02 | 13.12 | 4.48 | 23.04 | 2.99 | 2.07 | 0 | 2.93
POOB3- | 33 | 55.5 | 19.31 | 12.4 | 39.72 | 5.96 | 4.13 | 0 | 5.84
PORD3- | 33 | 49.68 | 17.33 | 12.15 | 36.66 | 5.93 | 4.11 | 0 | 5.82
RAVE3- | 33 | 41.33 | 15.55 | 3.26 | 25.25 | 5.85 | 4.05 | 0 | 5.73
REDH3- | 33 | 38.6 | 14.39 | 3.06 | 23.41 | 3.78 | 2.62 | 0 | 3.7
SACO3J | 33 | 41.19 | 14.82 | 4.22 | 25.18 | 3.05 | 2.11 | 0 | 2.99
SACO3K | 33 | 40.46 | 15.09 | 3.95 | 25.28 | 3.01 | 2.09 | 0 | 2.95
SANX3- | 33 | 32.31 | 11.46 | 5.02 | 21.22 | 2.99 | 2.07 | 0 | 2.93
SHRU3- | 33 | 46.04 | 15.98 | 10.04 | 32.64 | 5.86 | 4.06 | 0 | 5.75
SIGH3A | 33 | 42.95 | 14.81 | 10.76 | 31.71 | 4.44 | 3.08 | 0 | 4.36
SIGH3B | 33 | 42.84 | 14.78 | 10.61 | 31.52 | 4.44 | 3.08 | 0 | 4.36
SPAV3- | 33 | 27.78 | 10.04 | 3.75 | 17.94 | 4.34 | 3.01 | 0 | 4.25
STHA3- | 33 | 53.17 | 19.02 | 11.67 | 38.56 | 5.92 | 4.11 | 0 | 5.81
STIR3- | 33 | 39.8 | 13.74 | 6.53 | 25.96 | 4.46 | 3.09 | 0 | 4.37
STLE3S | 33 | 34.47 | 12.88 | 2.29 | 20.51 | 2.98 | 2.07 | 0 | 2.93
TELR3- | 33 | 27.9 | 9.94 | 3.77 | 17.83 | 2.96 | 2.05 | 0 | 2.9
TONG3- | 33 | 21.44 | 8.36 | 1.04 | 12.86 | 2.93 | 2.03 | 0 | 2.88
WFIE3- | 33 | 45.38 | 16.85 | 4.84 | 28.67 | 3 | 2.08 | 0 | 2.94
WGEO3- | 33 | 49.51 | 17.36 | 10.07 | 34.62 | 5.91 | 4.1 | 0 | 5.79
WHHO3- | 33 | 42.13 | 14.72 | 9.88 | 30.69 | 5.86 | 4.06 | 0 | 5.74
WHTL3- | 33 | 26.28 | 10.48 | 0.77 | 15.6 | 2.24 | 1.55 | 0 | 2.2
WISH3- | 33 | 43.04 | 14.82 | 10.18 | 31.13 | 5.9 | 4.09 | 0 | 5.79
WLEE3A | 33 | 50.23 | 20.99 | 10.45 | 40.14 | 3.05 | 2.11 | 0 | 2.99
WLEE3B | 33 | 50.43 | 21.07 | 10.44 | 40.23 | 3.05 | 2.11 | 0 | 2.99
WLEE3C | 33 | 49.85 | 20.8 | 10.39 | 39.8 | 3.05 | 2.11 | 0 | 2.99
WLEX3A | 33 | 57.48 | 20.12 | 9.38 | 37.84 | 3.05 | 2.12 | 0 | 2.99
WLEX3B | 33 | 57.73 | 20.21 | 9.38 | 37.96 | 3.05 | 2.12 | 0 | 2.99
WLEX3C | 33 | 55.24 | 19.33 | 9.37 | 36.7 | 3.05 | 2.12 | 0 | 2.99
BAGA0J | 25 | 16.25 | 5.95 | 3.62 | 12.04 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.25 | 5.95 | 3.62 | 12.03 | 0 | 0 | 0 | 0
BONN0J | 25 | 18.01 | 6.48 | 5.32 | 14.48 | 0 | 0 | 0 | 0
BONN0K | 25 | 18.01 | 6.48 | 5.32 | 14.48 | 0 | 0 | 0 | 0
BONN0L | 25 | 18.01 | 6.48 | 5.32 | 14.48 | 0 | 0 | 0 | 0
CATY0J | 25 | 10.08 | 3.72 | 1.72 | 6.99 | 0 | 0 | 0 | 0
CATY0K | 25 | 10.09 | 3.72 | 1.75 | 7.02 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.33 | 3.01 | 2.57 | 6.83 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.33 | 3.01 | 2.57 | 6.83 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.71 | 6.04 | 1.35 | 9.89 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.39 | 7.26 | 2.77 | 13.04 | 0 | 0 | 0 | 0
ELVA0J | 25 | 19.18 | 6.79 | 8.12 | 17.72 | 0 | 0 | 0 | 0
ELVA0K | 25 | 19.18 | 6.79 | 8.12 | 17.72 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.03 | 3.94 | 3.39 | 8.97 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.03 | 3.94 | 3.39 | 8.97 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.85 | 3.65 | 1.9 | 7.06 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.85 | 3.65 | 1.92 | 7.07 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.71 | 6.75 | 5.65 | 15.2 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.71 | 6.75 | 5.65 | 15.2 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.58 | 3.83 | 2.92 | 8.33 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.54 | 3.82 | 2.86 | 8.26 | 0 | 0 | 0 | 0
SANX0J | 25 | 17.02 | 6.1 | 4.69 | 13.33 | 0 | 0 | 0 | 0
SANX0K | 25 | 17 | 6.1 | 4.63 | 13.26 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.46 | 3.81 | 2.31 | 7.71 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.46 | 3.81 | 2.31 | 7.71 | 0 | 0 | 0 | 0
WISH0J | 25 | 21 | 7.55 | 6.43 | 17.1 | 0 | 0 | 0 | 0
WISH0K | 25 | 21 | 7.55 | 6.43 | 17.1 | 0 | 0 | 0 | 0
CAFA5- | 11 | 30.05 | 10.87 | 5.22 | 20.59 | 2.25 | 1.56 | 0 | 2.2
CURR5- | 11 | 34.26 | 12.36 | 5.68 | 23.15 | 4.41 | 3.06 | 0 | 4.33
EAST5- | 11 | 23.94 | 9.13 | 2.42 | 15.33 | 1.15 | 0.8 | 0 | 1.13
GLLE5- | 11 | 33.02 | 12.12 | 6.93 | 24.07 | 2.3 | 1.59 | 0 | 2.25
KEOO5- | 11 | 32.45 | 11.91 | 5.32 | 22.15 | 2.25 | 1.56 | 0 | 2.21
KILB5- | 11 | 29.03 | 10.61 | 4.15 | 19.15 | 3.01 | 2.09 | 0 | 2.95
TONG5- | 11 | 71.52 | 28.04 | 4.84 | 44.49 | 4.51 | 3.12 | 0 | 4.42

## D2.3
ETYS 19 Yr 3 - SPT Fault Levels (kA), Winter 2021/22
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
COAL4- | 400 | 55.68 | 20.83 | 10.23 | 39.68 | 47.84 | 18.96 | 8.24 | 35.04 | Back To Menu
CRYR4- | 400 | 58.83 | 21.25 | 13.4 | 43.44 | 54.81 | 20.83 | 12.25 | 41.71
DENN4- | 400 | 22.69 | 8.28 | 6.7 | 18.42 | 20.91 | 7.9 | 5.65 | 16.82
DEVM4- | 400 | 33.91 | 12.63 | 7.14 | 25.01 | 29.23 | 11.47 | 5.63 | 21.86
ECCL4A | 400 | 47.76 | 17.5 | 10.78 | 35.53 | 39.75 | 15.41 | 7.75 | 29.53
ECCL4B | 400 | 47.81 | 17.52 | 10.78 | 35.56 | 39.85 | 15.45 | 7.78 | 29.62
ELVA4- | 400 | 62.39 | 23.62 | 10.39 | 43.79 | 48.01 | 19.34 | 6.95 | 34.3
FALL4- | 400 | 51.12 | 18.56 | 11.18 | 37.42 | 45.43 | 17.44 | 9.41 | 34.07
GRNA4- | 400 | 52.37 | 19.99 | 8.22 | 36.49 | 42.6 | 16.87 | 7.78 | 31.64
HUCS4- | 400 | 62.16 | 22.1 | 15.71 | 46.96 | 74.82 | 27.82 | 19.28 | 58.63
HUER4- | 400 | 62.62 | 22.25 | 15.82 | 47.29 | 75.26 | 27.98 | 19.35 | 58.92
HUNE4- | 400 | 62.6 | 22.25 | 15.8 | 47.27 | 75.26 | 27.99 | 19.35 | 58.93
KILS4- | 400 | 52.45 | 19.17 | 11.07 | 38.18 | 47.78 | 18.51 | 10.01 | 36.19
KILS4T | 400 | 49.39 | 18.2 | 10.69 | 36.43 | 44.38 | 17.24 | 9.33 | 33.71
MOFF4- | 400 | 46.54 | 17.8 | 7.32 | 32.49 | 37.63 | 15.08 | 6.01 | 27.35
STHA4A | 400 | 63.11 | 23.24 | 12.29 | 45.16 | 58.28 | 22.61 | 11.41 | 43.38
STHA4B | 400 | 58.99 | 21.83 | 12.23 | 43.1 | 54.03 | 20.98 | 11 | 40.66
TORN4- | 400 | 68.85 | 24.61 | 16.66 | 51.46 | 68.75 | 25.66 | 18.51 | 54.8
WISH4- | 400 | 55.34 | 20.54 | 9.93 | 38.97 | 51.28 | 19.96 | 9.94 | 38.16
AUCH2- | 275 | 15.14 | 5.59 | 1.97 | 9.87 | 15.18 | 6.03 | 1.84 | 10.37
BUSB2- | 275 | 54.53 | 20.45 | 10.14 | 39.07 | 49.52 | 19.69 | 7.47 | 35.31
CLYM2- | 275 | 84.37 | 30.77 | 17.55 | 61.06 | 75.93 | 29.59 | 14.42 | 56.27
CLYN2Q | 275 | 18.66 | 7.56 | 5.92 | 16.61 | 18.63 | 7.14 | 6.09 | 16.18
CLYS2R | 275 | 16.77 | 6.42 | 5.03 | 14.11 | 16.39 | 6.29 | 4.82 | 13.71
COCK2- | 275 | 59.05 | 21.65 | 12.7 | 43.32 | 57.14 | 22.15 | 11.32 | 42.64
COYL2- | 275 | 53.9 | 19.16 | 11.65 | 38.75 | 53.02 | 20.41 | 9.91 | 38.78
CURR2- | 275 | 56.7 | 20.88 | 10.66 | 40.19 | 54.71 | 21.33 | 10.2 | 40.38
DALL2- | 275 | 34.87 | 12.51 | 7.29 | 24.98 | 30.74 | 11.9 | 5.87 | 22.7
DENN2- | 275 | 76.64 | 28.13 | 15.48 | 55.26 | 66.87 | 26.12 | 13.03 | 49.97
EERH2- | 275 | 72.83 | 26.75 | 14.71 | 52.53 | 63.28 | 24.81 | 11.16 | 46.24
EKIS2- | 275 | 68.02 | 25.48 | 13.5 | 49.54 | 65.86 | 26.18 | 11.01 | 48.04
ELVA2Q | 275 | 19.35 | 7.74 | 6.84 | 17.79 | 18.62 | 7.27 | 5.59 | 15.87
ELVA2R | 275 | 17.35 | 6.53 | 6.37 | 15.6 | 16.87 | 6.37 | 5.37 | 14.38
GLRO2- | 275 | 41.04 | 16.12 | 5.91 | 28.71 | 34.57 | 14 | 5.23 | 25.02
GRMO2- | 275 | 45.78 | 17.29 | 8.63 | 33.07 | 39.16 | 15.49 | 7.38 | 29.28
INVR2- | 275 | 34.9 | 13.03 | 6.1 | 24.53 | 30.98 | 12.28 | 5.11 | 22.47
KAIM2- | 275 | 59.39 | 21.71 | 11.96 | 42.66 | 59.76 | 23.17 | 10.8 | 43.57
KILG2- | 275 | 18.84 | 6.74 | 2.8 | 12.32 | 21.32 | 8.17 | 3.72 | 15.27
KILS2- | 275 | 63.7 | 22.45 | 16.26 | 48.01 | 67.32 | 25.32 | 16.15 | 51.95
KINC2- | 275 | 59.93 | 22.36 | 13.87 | 45.49 | 48.28 | 19.1 | 8.51 | 35.52
LAMB2- | 275 | 61.54 | 22.74 | 11.39 | 43.55 | 52.85 | 20.97 | 8.68 | 38.33
LOAN2- | 275 | 83.74 | 30.83 | 17.15 | 60.76 | 65.52 | 26.06 | 9.78 | 46.64
MAHI2- | 275 | 20.3 | 7.2 | 3.1 | 13.29 | 22.6 | 8.6 | 3.89 | 16.05
MOSM2- | 275 | 49.48 | 19.13 | 7.45 | 34.51 | 41.87 | 16.79 | 6.94 | 30.69
NEAR2Q | 275 | 54.25 | 20.31 | 9.43 | 38.16 | 48.79 | 19.3 | 7.98 | 35.28
NECU2- | 275 | 44.61 | 16.07 | 9.01 | 31.75 | 41.37 | 16.05 | 8.01 | 30.7
NEIL2- | 275 | 67.46 | 24.75 | 14.8 | 49.8 | 61.76 | 24.01 | 12.52 | 46.48
SMEA2- | 275 | 60.57 | 22.09 | 13.49 | 44.72 | 63.62 | 24.37 | 13.48 | 47.94
STHA2A | 275 | 70.39 | 25.9 | 15.37 | 51.99 | 71.19 | 27.37 | 15.5 | 54.2
STHA2B | 275 | 75.82 | 28 | 16.61 | 56.21 | 75.95 | 29.42 | 16.41 | 58.01
WFIE2- | 275 | 54.45 | 21.05 | 8.35 | 38.11 | 46.94 | 18.8 | 7.86 | 34.44
WISH2- | 275 | 55.44 | 20.22 | 12.37 | 40.97 | 58.97 | 22.42 | 13.73 | 45.44
WIYH2- | 275 | 65.01 | 23.66 | 13.46 | 46.92 | 63.26 | 24.42 | 13.38 | 47.91
WLEE2- | 275 | 58.99 | 23.05 | 7.8 | 40.4 | 49.81 | 22.39 | 9.79 | 41.45
WLEX2- | 275 | 46.85 | 18.72 | 5.2 | 31.68 | 37.84 | 16.99 | 8.65 | 32.68
AREC1- | 132 | 13.71 | 4.53 | 1.63 | 8.04 | 16.66 | 6.01 | 2.34 | 10.84
BLAH1- | 132 | 33.03 | 11.03 | 5.33 | 20.92 | 34.46 | 12.67 | 5.61 | 23.52
BLCW1- | 132 | 8.71 | 3.13 | 0.95 | 5.38 | 8.5 | 3.27 | 0.99 | 5.61
BONN1- | 132 | 51.52 | 18.88 | 9.14 | 35.84 | 61.1 | 23.6 | 10.18 | 43.56
BRAP1- | 132 | 32.21 | 12.16 | 4.14 | 21.34 | 35.13 | 14.12 | 4.07 | 24.04
CHAP1- | 132 | 30.96 | 12.31 | 1.28 | 18.7 | 31.66 | 13.34 | 1.68 | 20.54
COAL1- | 132 | 21.78 | 7.1 | 5.99 | 16.04 | 27.31 | 9.64 | 6.86 | 20.49
COAL1A | 132 | 35.51 | 12.07 | 9.68 | 26.76 | 43.83 | 15.41 | 11.32 | 33.12
COYL1- | 132 | 32.07 | 11.75 | 5.84 | 22.47 | 37.81 | 14.7 | 6.55 | 27.33
CRYR1- | 132 | 15.69 | 5.18 | 4.37 | 11.7 | 16.54 | 5.81 | 5.07 | 13.28
CRYR1A | 132 | 15.43 | 6.13 | 4.8 | 13.47 | 17.33 | 6.53 | 5.57 | 14.8
CURR1A | 132 | 36.16 | 12.63 | 9.28 | 27.15 | 44.87 | 16.42 | 11.14 | 34.36
CURR1B | 132 | 36.16 | 12.63 | 9.28 | 27.15 | 44.87 | 16.42 | 11.14 | 34.36
DALM1- | 132 | 26.42 | 9.29 | 7.21 | 20.34 | 31.9 | 11.67 | 8.79 | 25.3
DEVM1- | 132 | 31.89 | 12.11 | 7.45 | 24.57 | 38.41 | 14.99 | 8.55 | 29.75
DEVO1- | 132 | 28.16 | 11.66 | 1.17 | 17.65 | 27.83 | 12.12 | 2.13 | 19.27
DUMF1- | 132 | 20.15 | 8.16 | 0.5 | 12.05 | 23.44 | 9.81 | 0.81 | 14.69
DUNE1- | 132 | 18.46 | 7.56 | 1.06 | 11.75 | 19.57 | 8.19 | 1.55 | 13.13
ECCL1- | 132 | 31.42 | 11.68 | 8.51 | 25.02 | 39.09 | 14.94 | 10.07 | 31.2
GALA1- | 132 | 20.22 | 8.59 | 0.37 | 12.52 | 20.78 | 9.07 | 0.9 | 13.73
GAWH1Q | 132 | 28.17 | 9.93 | 4.5 | 18.54 | 33.69 | 12.79 | 4.36 | 22.45
GLLE1- | 132 | 15.67 | 6.42 | 0.82 | 9.91 | 16.11 | 6.94 | 0.75 | 10.57
GLNI1- | 132 | 46.04 | 17.77 | 6.08 | 31.21 | 53.23 | 21.45 | 6.45 | 36.78
GRNA1- | 132 | 38.44 | 14.28 | 7.61 | 27.81 | 46.37 | 17.86 | 8.82 | 34.09
HAWI1- | 132 | 10.25 | 4.85 | 0.03 | 6.89 | 11.06 | 5.06 | 0.16 | 7.32
HELE1- | 132 | 18.11 | 8.65 | 0.04 | 12.28 | 18.7 | 8.79 | 0.24 | 12.67
HUER1- | 132 | 36.99 | 13.79 | 9.01 | 28.51 | 43.52 | 16.68 | 10.9 | 34.49
KEOO1- | 132 | 15.72 | 6.36 | 1.46 | 10.45 | 16.46 | 6.88 | 1.51 | 11.25
KILS1- | 132 | 31.54 | 12.4 | 4.47 | 22.01 | 31.14 | 12.7 | 5.72 | 23.68
KILW1Q | 132 | 25.47 | 10.13 | 2.15 | 16.47 | 24.74 | 10.26 | 1.96 | 16.46
KILW1R | 132 | 25.13 | 10.05 | 1.95 | 16.15 | 24.15 | 10.07 | 1.8 | 16.04
MAHI1- | 132 | 14.92 | 4.94 | 2.84 | 9.82 | 17.34 | 6.24 | 3.57 | 12.39
MARG1- | 132 | 8.9 | 3.19 | 1.02 | 5.53 | 8.63 | 3.32 | 0.95 | 5.64
MAYB1- | 132 | 20.17 | 7.78 | 0.5 | 11.51 | 19.73 | 8.33 | 0.73 | 12.51
MEAD1- | 132 | 29.52 | 11.64 | 2.2 | 18.66 | 27.9 | 11.57 | 2.04 | 18.41
MIDM1- | 132 | 18 | 6.29 | 1.91 | 10.81 | 21.07 | 8.37 | 1.98 | 13.82
MOFF1- | 132 | 26.12 | 9.01 | 6.7 | 19.44 | 32.88 | 11.91 | 8.62 | 25.47
MOSM1A | 132 | 43.23 | 16.81 | 5.53 | 29.3 | 50.95 | 20.5 | 6.68 | 35.67
MOSM1B | 132 | 43.12 | 16.77 | 5.46 | 29.18 | 50.95 | 20.51 | 6.6 | 35.61
NECU1- | 132 | 40.19 | 13.4 | 9.35 | 28.3 | 45.27 | 16.33 | 9.85 | 32.94
NEIL1- | 132 | 45.51 | 16.22 | 11.06 | 34 | 55.1 | 20.68 | 13.15 | 42.4
NETS1- | 132 | 11.98 | 5.03 | 0.29 | 7.4 | 12.5 | 5.41 | 0.51 | 8.16
REDH1- | 132 | 31.87 | 13.46 | 1.03 | 20.08 | 33.07 | 14.3 | 1.45 | 21.68
SMEA1- | 132 | 19.46 | 7.57 | 4.89 | 15.59 | 20.59 | 8.05 | 5.71 | 17.1
STLE1- | 132 | 23.06 | 10.45 | 0.18 | 14.97 | 22.62 | 10.36 | 0.63 | 15.28
TONG1- | 132 | 11.53 | 5.18 | 0.24 | 7.57 | 16.14 | 7.36 | 0.34 | 10.75
TORN1- | 132 | 32.02 | 10.91 | 8.35 | 23.77 | 38.16 | 13.71 | 10.56 | 29.94
WESE1- | 132 | 15.06 | 6.04 | 4.22 | 12.76 | 16.76 | 6.38 | 4.67 | 13.69
WFIE1A | 132 | 31.32 | 12.91 | 4.4 | 22.66 | 32.9 | 13.71 | 5.34 | 24.72
WFIE1B | 132 | 42 | 16.68 | 4.67 | 28.26 | 45.15 | 18.72 | 5.5 | 31.97
WISH1- | 132 | 15.59 | 4.68 | 4.39 | 11.02 | 19.01 | 6.42 | 5.46 | 14.54
WIYH1- | 132 | 47.74 | 18.07 | 10.33 | 35.9 | 58.8 | 23.19 | 12.78 | 45.58
AYR-3- | 33 | 41.01 | 14.27 | 10.73 | 30.91 | 5.87 | 4.07 | 0 | 5.75
BAGA3- | 33 | 42.7 | 14.29 | 3.76 | 23.97 | 4.47 | 3.1 | 0 | 4.38
BAIN3- | 33 | 31.45 | 11.2 | 6.33 | 22.16 | 3.02 | 2.09 | 0 | 2.96
BERW3- | 33 | 40.95 | 14.71 | 1.47 | 22.27 | 4.64 | 3.18 | 0 | 4.5
BLAH3A | 33 | 48.02 | 13.87 | 10.01 | 29.63 | 4.51 | 3.13 | 0 | 4.42
BLAH3B | 33 | 27.71 | 9.78 | 7.91 | 21.74 | 4.47 | 3.1 | 0 | 4.38
BLCW3- | 33 | 26.22 | 7.85 | 2.93 | 14.04 | 2.27 | 1.57 | 0 | 2.23
BONN3- | 33 | 43.14 | 13.74 | 8.41 | 27.84 | 4.53 | 3.15 | 0 | 4.45
BPGR3- | 33 | 95.74 | 29.08 | 21.75 | 62.87 | 6.02 | 4.17 | 0 | 5.9
BRAP3- | 33 | 43.64 | 13.66 | 9.71 | 29.04 | 4.5 | 3.11 | 0 | 4.4
BROX3- | 33 | 28.64 | 10.16 | 3.75 | 18.12 | 4.41 | 3.05 | 0 | 4.31
CATY3- | 33 | 30.46 | 10.65 | 4.74 | 19.8 | 3.01 | 2.09 | 0 | 2.96
CHAP3- | 33 | 48.72 | 17.85 | 4.42 | 29.66 | 4.55 | 3.15 | 0 | 4.46
CHAS3A | 33 | 33.99 | 11.87 | 8.67 | 25.45 | 3.01 | 2.09 | 0 | 2.95
CHAS3B | 33 | 33.99 | 11.87 | 8.67 | 25.45 | 3.01 | 2.09 | 0 | 2.95
CLYM3- | 33 | 50.2 | 17.61 | 11.36 | 36.27 | 5.9 | 4.09 | 0 | 5.79
CLYN3A | 33 | 41.95 | 18.18 | 8.06 | 33.78 | 3.02 | 2.09 | 0 | 2.96
CLYN3B | 33 | 42.05 | 18.22 | 8.08 | 33.85 | 3.02 | 2.09 | 0 | 2.96
CLYN3C | 33 | 41.93 | 18.17 | 8.09 | 33.79 | 3.02 | 2.09 | 0 | 2.96
CLYN3D | 33 | 41.96 | 18.19 | 8 | 33.73 | 3.02 | 2.09 | 0 | 2.96
CLYS3A | 33 | 37.72 | 15.72 | 7.84 | 30.07 | 2.99 | 2.07 | 0 | 2.93
CLYS3B | 33 | 42.7 | 16.74 | 8.08 | 31.76 | 3 | 2.08 | 0 | 2.94
COAT3- | 33 | 39.64 | 13.57 | 11.89 | 31.08 | 5.89 | 4.08 | 0 | 5.77
COCK3- | 33 | 42.39 | 14.88 | 11.13 | 32.17 | 5.92 | 4.1 | 0 | 5.8
COYL3- | 33 | 41.18 | 14.88 | 4.72 | 25.77 | 3 | 2.08 | 0 | 2.94
CROO3J | 33 | 34.58 | 12.69 | 3.64 | 21.6 | 2.99 | 2.07 | 0 | 2.93
CROO3K | 33 | 32.77 | 11.97 | 3.81 | 20.74 | 3.01 | 2.09 | 0 | 2.95
CUMB3- | 33 | 37.99 | 13.43 | 4.74 | 23.74 | 4.51 | 3.12 | 0 | 4.42
CUPA3- | 33 | 27.59 | 10.22 | 1.25 | 15.7 | 4.33 | 3 | 0 | 4.24
DALM3- | 33 | 33.38 | 11.64 | 7.72 | 24.18 | 4.47 | 3.09 | 0 | 4.38
DESA3- | 33 | 37 | 11.1 | 5.38 | 21.08 | 2.27 | 1.57 | 0 | 2.22
DEVM3- | 33 | 35.67 | 13.14 | 4.57 | 23.16 | 2.98 | 2.07 | 0 | 2.92
DEVO3- | 33 | 41.3 | 15.18 | 3.73 | 25.2 | 4.48 | 3.1 | 0 | 4.39
DEWP3- | 33 | 48.86 | 16.61 | 12.41 | 35.9 | 7.85 | 5.43 | 0 | 7.69
DRCR3- | 33 | 28.44 | 10.45 | 3.11 | 17.88 | 4.45 | 3.08 | 0 | 4.36
DRUM3- | 33 | 39.97 | 13.7 | 11.3 | 30.68 | 5.9 | 4.09 | 0 | 5.78
DUMF3A | 33 | 38.59 | 14.06 | 1.9 | 21.78 | 4.43 | 3.07 | 0 | 4.35
DUMF3B | 33 | 35.85 | 13.46 | 1.99 | 21.03 | 4.45 | 3.09 | 0 | 4.36
DUMF3I | 33 | 19.56 | 6.96 | 1.77 | 11.61 | 1.51 | 1.05 | 0 | 1.48
DUNB3A | 33 | 45.98 | 13.7 | 3.66 | 23.04 | 3.04 | 2.11 | 0 | 2.99
DUNB3B | 33 | 44.24 | 13.33 | 5.73 | 24.59 | 4.53 | 3.14 | 0 | 4.45
DUNE3- | 33 | 46.47 | 16.23 | 3.43 | 26.39 | 4.53 | 3.14 | 0 | 4.44
DUNF3- | 33 | 32.14 | 11.68 | 3.87 | 20.39 | 4.41 | 3.05 | 0 | 4.32
DUNH3- | 33 | 43.51 | 12.94 | 9.41 | 27.71 | 4.49 | 3.11 | 0 | 4.4
ECCL3- | 33 | 36.04 | 14 | 5.48 | 25.28 | 5.2 | 3.57 | 0 | 5.05
EERH3- | 33 | 46.32 | 15.81 | 13.88 | 36.24 | 5.91 | 4.1 | 0 | 5.79
EKIL3- | 33 | 53.03 | 18.49 | 14.86 | 41.01 | 6 | 4.16 | 0 | 5.88
EKIS3- | 33 | 56.49 | 19.19 | 10.26 | 37.4 | 6.01 | 4.17 | 0 | 5.9
ELDE3- | 33 | 39.87 | 14.37 | 5.11 | 25.44 | 3 | 2.08 | 0 | 2.94
ERSK3- | 33 | 30.04 | 10.93 | 4.79 | 20.24 | 3.01 | 2.09 | 0 | 2.95
EWEH3- | 33 | 35.72 | 11.11 | 2.82 | 18.52 | 2.26 | 1.57 | 0 | 2.22
FINN3- | 33 | 31.43 | 11.18 | 6.28 | 22.09 | 4.41 | 3.05 | 0 | 4.32
GALA3- | 33 | 37.93 | 14.2 | 2.21 | 22.29 | 4.88 | 3.38 | 0 | 4.77
GAWH3- | 33 | 35.01 | 10.71 | 7.1 | 22.25 | 2.29 | 1.59 | 0 | 2.24
GIFF3A | 33 | 36.21 | 12.75 | 7.82 | 25.85 | 5.35 | 3.7 | 0 | 5.23
GIFF3B | 33 | 36.34 | 12.79 | 7.87 | 25.97 | 5.35 | 3.7 | 0 | 5.23
GLGL3- | 33 | 43.27 | 13.11 | 7.01 | 25.55 | 4.5 | 3.12 | 0 | 4.42
GLLU3- | 33 | 37.89 | 14.27 | 0.55 | 20.73 | 4.12 | 2.85 | 0 | 4.04
GLNI3- | 33 | 39.14 | 14.36 | 6.56 | 26.87 | 4.46 | 3.1 | 0 | 4.38
GLRO3A | 33 | 34.94 | 12.33 | 8.28 | 25.71 | 5.43 | 3.75 | 0 | 5.31
GLRO3B | 33 | 33.2 | 11.67 | 8.09 | 24.59 | 5.46 | 3.78 | 0 | 5.34
GORG3- | 33 | 29.16 | 10.34 | 5.12 | 19.74 | 3 | 2.08 | 0 | 2.94
GOVA3- | 33 | 31.44 | 11.03 | 6.04 | 21.64 | 4.4 | 3.05 | 0 | 4.31
GRMO3A | 33 | 40.66 | 14.08 | 9.38 | 29.3 | 5.87 | 4.06 | 0 | 5.75
GRMO3C | 33 | 40.75 | 14.1 | 9.53 | 29.47 | 5.87 | 4.07 | 0 | 5.75
HAGR3- | 33 | 30.76 | 10.92 | 5.01 | 20.45 | 2.96 | 2.05 | 0 | 2.9
HAWI3- | 33 | 22.59 | 9.27 | 0.26 | 13.36 | 2.97 | 2.06 | 0 | 2.91
HELE3- | 33 | 26.39 | 10.45 | 0.78 | 15.55 | 2.96 | 2.05 | 0 | 2.9
HUNF3- | 33 | 42.96 | 16.61 | 6.39 | 29.89 | 2.98 | 2.07 | 0 | 2.93
INKE3- | 33 | 29.95 | 10.99 | 2.4 | 17.94 | 4.37 | 3.03 | 0 | 4.28
JOHN3- | 33 | 29.86 | 10.44 | 5.8 | 20.56 | 2.97 | 2.05 | 0 | 2.91
KAIM3- | 33 | 36.02 | 11.02 | 8.43 | 24.02 | 5.66 | 3.91 | 0 | 5.52
KIER3- | 33 | 34.7 | 12.12 | 5.76 | 22.9 | 4.45 | 3.08 | 0 | 4.35
KILB3- | 33 | 33.8 | 12.33 | 5.31 | 22.74 | 2.98 | 2.07 | 0 | 2.92
KILS3- | 33 | 41.95 | 14.62 | 10.49 | 31.16 | 5.88 | 4.08 | 0 | 5.77
KILT3- | 33 | 58.05 | 20.05 | 10.73 | 39.09 | 5.99 | 4.15 | 0 | 5.87
KILW3- | 33 | 32.39 | 11.74 | 5.15 | 21.75 | 4.41 | 3.06 | 0 | 4.32
LEVE3- | 33 | 38.52 | 14.68 | 1.42 | 22.18 | 3 | 2.08 | 0 | 2.94
LING3- | 33 | 47.81 | 15.28 | 4.23 | 25.84 | 4.47 | 3.1 | 0 | 4.39
LINM3- | 33 | 59.15 | 19.73 | 6.81 | 34.72 | 4.56 | 3.17 | 0 | 4.48
MAHI3- | 33 | 48.46 | 15.06 | 6.05 | 27.35 | 3.08 | 2.14 | 0 | 3.02
MAYB3- | 33 | 29.07 | 10.31 | 1.27 | 15.85 | 1.54 | 1.07 | 0 | 1.51
NEAR3- | 33 | 51.78 | 17.86 | 10.53 | 35.79 | 5.97 | 4.14 | 0 | 5.85
NETS3- | 33 | 20.22 | 7.65 | 1.05 | 11.87 | 3.1 | 2.13 | 0 | 3.02
PAIS3- | 33 | 33.98 | 12.12 | 6.33 | 23.47 | 2.99 | 2.07 | 0 | 2.93
PART3- | 33 | 35.95 | 13.1 | 4.48 | 23 | 2.98 | 2.07 | 0 | 2.93
POOB3- | 33 | 55.96 | 19.45 | 12.47 | 39.98 | 5.99 | 4.15 | 0 | 5.87
PORD3- | 33 | 50.16 | 17.47 | 12.28 | 36.99 | 6 | 4.16 | 0 | 5.88
RAVE3- | 33 | 41.55 | 15.64 | 3.28 | 25.39 | 5.88 | 4.08 | 0 | 5.77
REDH3- | 33 | 38.54 | 14.38 | 3.09 | 23.43 | 3.75 | 2.6 | 0 | 3.68
SACO3J | 33 | 41.02 | 14.76 | 4.23 | 25.1 | 3 | 2.08 | 0 | 2.94
SACO3K | 33 | 40.43 | 15.08 | 3.95 | 25.27 | 3.01 | 2.09 | 0 | 2.95
SANX3- | 33 | 32.15 | 11.41 | 5 | 21.13 | 2.96 | 2.05 | 0 | 2.9
SHRU3- | 33 | 46.9 | 16.08 | 11.76 | 34.5 | 5.9 | 4.09 | 0 | 5.78
SIGH3A | 33 | 43.19 | 14.9 | 10.83 | 31.91 | 4.47 | 3.1 | 0 | 4.39
SIGH3B | 33 | 43.07 | 14.87 | 10.68 | 31.71 | 4.47 | 3.1 | 0 | 4.38
SPAV3- | 33 | 27.6 | 10.05 | 3.74 | 17.95 | 4.34 | 3.01 | 0 | 4.25
STHA3- | 33 | 53.43 | 19.11 | 11.74 | 38.77 | 5.96 | 4.13 | 0 | 5.84
STIR3- | 33 | 39.75 | 13.73 | 6.67 | 26.09 | 4.5 | 3.12 | 0 | 4.41
STLE3S | 33 | 34.42 | 12.9 | 2.29 | 20.53 | 2.98 | 2.07 | 0 | 2.93
TELR3- | 33 | 27.97 | 10.02 | 3.73 | 17.9 | 2.99 | 2.07 | 0 | 2.93
TONG3- | 33 | 21.57 | 8.42 | 1.03 | 12.93 | 2.98 | 2.06 | 0 | 2.92
WFIE3- | 33 | 45.23 | 16.82 | 4.87 | 28.66 | 3.01 | 2.09 | 0 | 2.95
WGEO3- | 33 | 50.08 | 17.51 | 10.19 | 34.95 | 5.97 | 4.14 | 0 | 5.86
WHHO3- | 33 | 42.34 | 14.8 | 9.94 | 30.87 | 5.9 | 4.09 | 0 | 5.78
WHTL3- | 33 | 26.39 | 10.5 | 0.8 | 15.65 | 2.24 | 1.55 | 0 | 2.2
WISH3- | 33 | 43.26 | 14.9 | 10.23 | 31.3 | 5.95 | 4.12 | 0 | 5.83
WLEE3A | 33 | 49.65 | 20.76 | 10.45 | 39.81 | 3.03 | 2.1 | 0 | 2.97
WLEE3B | 33 | 49.85 | 20.83 | 10.44 | 39.91 | 3.03 | 2.1 | 0 | 2.97
WLEE3C | 33 | 49.27 | 20.56 | 10.39 | 39.47 | 3.03 | 2.1 | 0 | 2.97
WLEX3A | 33 | 57.06 | 19.96 | 9.47 | 37.7 | 3.02 | 2.1 | 0 | 2.96
WLEX3B | 33 | 57.31 | 20.05 | 9.47 | 37.82 | 3.02 | 2.09 | 0 | 2.96
WLEX3C | 33 | 54.84 | 19.17 | 9.46 | 36.57 | 3.02 | 2.1 | 0 | 2.96
BAGA0J | 25 | 16.45 | 6.03 | 3.67 | 12.2 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.45 | 6.02 | 3.67 | 12.19 | 0 | 0 | 0 | 0
BONN0J | 25 | 18.25 | 6.56 | 5.42 | 14.7 | 0 | 0 | 0 | 0
BONN0K | 25 | 18.25 | 6.56 | 5.42 | 14.7 | 0 | 0 | 0 | 0
BONN0L | 25 | 18.25 | 6.56 | 5.42 | 14.7 | 0 | 0 | 0 | 0
CATY0J | 25 | 10.01 | 3.69 | 1.71 | 6.93 | 0 | 0 | 0 | 0
CATY0K | 25 | 10.01 | 3.69 | 1.74 | 6.96 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.39 | 3.02 | 2.57 | 6.84 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.39 | 3.02 | 2.57 | 6.84 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.77 | 6.03 | 1.35 | 9.88 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.45 | 7.25 | 2.77 | 13.03 | 0 | 0 | 0 | 0
ELVA0J | 25 | 19.22 | 6.78 | 8.12 | 17.72 | 0 | 0 | 0 | 0
ELVA0K | 25 | 19.22 | 6.78 | 8.12 | 17.72 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.05 | 3.95 | 3.39 | 8.98 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.05 | 3.95 | 3.39 | 8.98 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.87 | 3.64 | 1.9 | 7.06 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.87 | 3.64 | 1.92 | 7.07 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.83 | 6.78 | 5.69 | 15.28 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.83 | 6.78 | 5.69 | 15.28 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.6 | 3.83 | 2.92 | 8.33 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.56 | 3.82 | 2.86 | 8.26 | 0 | 0 | 0 | 0
SANX0J | 25 | 16.97 | 6.06 | 4.67 | 13.25 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.95 | 6.06 | 4.61 | 13.19 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.44 | 3.81 | 2.31 | 7.69 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.44 | 3.81 | 2.31 | 7.69 | 0 | 0 | 0 | 0
WISH0J | 25 | 21.16 | 7.59 | 6.47 | 17.21 | 0 | 0 | 0 | 0
WISH0K | 25 | 21.16 | 7.59 | 6.47 | 17.21 | 0 | 0 | 0 | 0
CAFA5- | 11 | 29.89 | 10.81 | 5.22 | 20.51 | 2.22 | 1.54 | 0 | 2.18
CURR5- | 11 | 34.54 | 12.46 | 5.73 | 23.35 | 4.46 | 3.09 | 0 | 4.37
EAST5- | 11 | 23.76 | 9.07 | 2.41 | 15.24 | 1.13 | 0.79 | 0 | 1.11
GLLE5- | 11 | 32.78 | 12.05 | 6.91 | 23.95 | 2.26 | 1.57 | 0 | 2.22
KEOO5- | 11 | 32.52 | 11.93 | 5.33 | 22.2 | 2.26 | 1.57 | 0 | 2.22
KILB5- | 11 | 28.93 | 10.57 | 4.13 | 19.09 | 3 | 2.08 | 0 | 2.94
TONG5- | 11 | 71.83 | 28.16 | 4.86 | 44.69 | 4.55 | 3.15 | 0 | 4.46

## D2.4
ETYS 19 Yr 4 - SPT Fault Levels (kA), Winter 2022/23
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
COAL4- | 400 | 56.62 | 21.2 | 10.41 | 40.39 | 48.47 | 19.21 | 8.38 | 35.54 | Back To Menu
CRYR4- | 400 | 63.81 | 22.91 | 14.37 | 46.77 | 62.36 | 23.51 | 14.47 | 47.72
DENN4- | 400 | 22.5 | 8.25 | 6.67 | 18.35 | 20.69 | 7.83 | 5.6 | 16.67
DEVM4- | 400 | 38.38 | 14.25 | 8 | 28.15 | 31.9 | 12.54 | 6.06 | 23.79
ECCL4A | 400 | 49.74 | 18.27 | 11.1 | 36.94 | 40.68 | 15.8 | 7.8 | 30.15
ECCL4B | 400 | 49.81 | 18.3 | 11.1 | 36.98 | 40.77 | 15.83 | 7.83 | 30.22
ELVA4- | 400 | 63.2 | 23.94 | 10.47 | 44.34 | 48.47 | 19.52 | 7.21 | 34.81
FALL4- | 400 | 54.64 | 19.77 | 11.85 | 39.81 | 49.83 | 19.04 | 10.58 | 37.5
GRNA4- | 400 | 52.63 | 20.1 | 8.2 | 36.63 | 43.04 | 17.04 | 7.82 | 31.92
HUCS4- | 400 | 64.17 | 22.96 | 15.75 | 48.22 | 76.74 | 28.64 | 19.31 | 59.81
HUER4- | 400 | 64.66 | 23.13 | 15.86 | 48.57 | 77.19 | 28.81 | 19.37 | 60.11
HUNE4- | 400 | 64.64 | 23.12 | 15.85 | 48.55 | 77.2 | 28.81 | 19.37 | 60.12
KILS4- | 400 | 53.81 | 19.72 | 11.31 | 39.21 | 48.63 | 18.87 | 10.16 | 36.84
KILS4T | 400 | 50.33 | 18.61 | 10.84 | 37.15 | 44.96 | 17.49 | 9.42 | 34.15
MOFF4- | 400 | 46.74 | 17.89 | 7.31 | 32.61 | 37.67 | 15.11 | 6 | 27.37
STHA4A | 400 | 64.33 | 23.8 | 12.45 | 46.11 | 58.94 | 22.91 | 11.51 | 43.91
STHA4B | 400 | 59.99 | 22.26 | 12.41 | 43.89 | 54.6 | 21.22 | 11.11 | 41.12
TORN4- | 400 | 73.42 | 26.2 | 17.49 | 54.54 | 73.51 | 27.44 | 19.32 | 58.13
WISH4- | 400 | 56.39 | 21.04 | 10.01 | 39.76 | 51.78 | 20.2 | 10.01 | 38.57
AUCH2- | 275 | 16 | 5.83 | 2.11 | 10.36 | 15.98 | 6.32 | 1.93 | 10.87
BUSB2- | 275 | 56.77 | 21.38 | 10.49 | 40.73 | 51.2 | 20.41 | 7.57 | 36.44
CLYM2- | 275 | 86.42 | 31.8 | 17.8 | 62.77 | 76.85 | 30.06 | 14.53 | 57.04
CLYN2Q | 275 | 18.61 | 7.54 | 5.92 | 16.58 | 18.58 | 7.12 | 6.09 | 16.15
CLYS2R | 275 | 17.15 | 6.48 | 5.04 | 14.19 | 17.3 | 6.67 | 4.9 | 14.34
COCK2- | 275 | 67.38 | 25.05 | 13.8 | 49.23 | 59.75 | 23.32 | 11.63 | 44.61
COYL2- | 275 | 57.59 | 20.29 | 12.44 | 41.14 | 56.85 | 21.81 | 10.68 | 41.52
CURR2- | 275 | 60.63 | 22.67 | 10.83 | 42.89 | 55.93 | 21.94 | 10.3 | 41.33
DALL2- | 275 | 34.71 | 12.51 | 7.19 | 24.88 | 30.57 | 11.86 | 5.82 | 22.59
DENN2- | 275 | 77.48 | 28.87 | 15.64 | 56.46 | 66.95 | 26.28 | 13.05 | 50.21
EERH2- | 275 | 73.94 | 27.39 | 14.84 | 53.57 | 63.67 | 25.03 | 11.22 | 46.62
EKIS2- | 275 | 69.96 | 26.36 | 13.75 | 51.02 | 67.15 | 26.79 | 11.06 | 48.94
ELVA2Q | 275 | 19.3 | 7.72 | 6.85 | 17.76 | 18.56 | 7.25 | 5.6 | 15.85
ELVA2R | 275 | 17.71 | 6.57 | 6.34 | 15.63 | 18.06 | 6.78 | 5.85 | 15.44
GLRO2- | 275 | 41.71 | 16.87 | 6.16 | 30.01 | 34.66 | 14.14 | 5.34 | 25.35
GRMO2- | 275 | 46.72 | 17.9 | 8.63 | 33.95 | 39.4 | 15.64 | 7.43 | 29.55
INVR2- | 275 | 34.78 | 13.04 | 6.04 | 24.49 | 30.86 | 12.25 | 5.07 | 22.39
KAIM2- | 275 | 64.6 | 23.98 | 12.37 | 46.28 | 61.55 | 24.02 | 10.9 | 44.87
KILG2- | 275 | 20.32 | 7.15 | 3.12 | 13.24 | 23.1 | 8.79 | 4.08 | 16.51
KILS2- | 275 | 67.09 | 23.6 | 16.85 | 50.23 | 70.19 | 26.42 | 16.58 | 53.95
KINC2- | 275 | 61.44 | 23.4 | 14.1 | 47.18 | 48.62 | 19.35 | 8.53 | 35.9
LAMB2- | 275 | 61.55 | 22.95 | 11.31 | 43.76 | 52.67 | 20.95 | 8.66 | 38.29
LOAN2- | 275 | 85.83 | 32.28 | 17.6 | 63.25 | 66.43 | 26.59 | 9.9 | 47.52
MAHI2- | 275 | 21.96 | 7.65 | 3.47 | 14.3 | 24.64 | 9.28 | 4.37 | 17.5
MOSM2- | 275 | 50.2 | 19.87 | 7.66 | 35.76 | 41.96 | 16.94 | 7.08 | 31.03
NEAR2Q | 275 | 54.6 | 20.57 | 9.43 | 38.52 | 48.83 | 19.36 | 7.99 | 35.37
NECU2- | 275 | 48.34 | 17.21 | 9.92 | 34.26 | 47.45 | 18.14 | 10.1 | 35.75
NEIL2- | 275 | 76.09 | 27.8 | 17.44 | 56.76 | 72.78 | 28.09 | 15.62 | 55.35
SMEA2- | 275 | 66.58 | 24.61 | 14.2 | 49.01 | 66.07 | 25.46 | 13.81 | 49.82
STHA2A | 275 | 72.13 | 26.71 | 15.62 | 53.39 | 72.3 | 27.88 | 15.66 | 55.08
STHA2B | 275 | 77.66 | 28.87 | 16.88 | 57.7 | 77.1 | 29.95 | 16.56 | 58.92
WFIE2- | 275 | 55.63 | 22.16 | 8.7 | 40.04 | 47.25 | 19.08 | 8.09 | 35.07
WISH2- | 275 | 55.94 | 20.49 | 12.47 | 41.45 | 59.2 | 22.54 | 13.8 | 45.68
WIYH2- | 275 | 65 | 23.84 | 13.35 | 47.06 | 62.83 | 24.33 | 13.31 | 47.72
WLEE2- | 275 | 60.35 | 23.74 | 7.79 | 41.36 | 50.61 | 22.79 | 9.98 | 42.22
WLEX2- | 275 | 47.53 | 19.11 | 5.14 | 32.16 | 37.99 | 17.13 | 8.67 | 32.89
AREC1- | 132 | 13.81 | 4.56 | 1.68 | 8.14 | 16.73 | 6.03 | 2.4 | 10.93
BLAH1- | 132 | 32.24 | 10.8 | 5.46 | 20.74 | 34.33 | 12.62 | 5.71 | 23.55
BLCW1- | 132 | 12.03 | 4.7 | 0.72 | 7.36 | 11.33 | 4.62 | 0.86 | 7.39
BONN1- | 132 | 51.21 | 18.86 | 9.1 | 35.76 | 60.63 | 23.47 | 10.12 | 43.3
BRAP1- | 132 | 33.06 | 12.26 | 4.21 | 21.55 | 35.76 | 14.15 | 4.04 | 24.05
CHAP1- | 132 | 30.72 | 12.22 | 1.3 | 18.57 | 31.41 | 13.22 | 1.69 | 20.39
COAL1- | 132 | 23.53 | 7.53 | 6.16 | 16.81 | 29.79 | 10.49 | 6.97 | 21.8
COAL1A | 132 | 37.02 | 12.49 | 9.94 | 27.6 | 45.81 | 16.11 | 11.42 | 34.21
COYL1- | 132 | 27.58 | 9.27 | 6.75 | 19.85 | 32.3 | 11.66 | 8.27 | 24.75
CRYR1- | 132 | 15.73 | 5.19 | 4.41 | 11.75 | 16.59 | 5.82 | 5.11 | 13.35
CRYR1A | 132 | 15.53 | 6.18 | 4.85 | 13.59 | 17.38 | 6.55 | 5.6 | 14.87
CURR1A | 132 | 36.54 | 12.83 | 9.36 | 27.5 | 44.83 | 16.44 | 11.15 | 34.4
CURR1B | 132 | 36.54 | 12.83 | 9.36 | 27.5 | 44.83 | 16.44 | 11.15 | 34.4
DALM1- | 132 | 26.38 | 9.29 | 7.14 | 20.28 | 31.77 | 11.64 | 8.7 | 25.16
DEVM1- | 132 | 32.69 | 12.2 | 7.35 | 24.61 | 39.05 | 15.01 | 8.41 | 29.65
DEVO1- | 132 | 27.99 | 11.62 | 1.16 | 17.6 | 27.73 | 12.07 | 2.14 | 19.21
DUMF1- | 132 | 20.09 | 8.16 | 0.51 | 12.04 | 23.34 | 9.78 | 0.82 | 14.65
DUNE1- | 132 | 18.59 | 7.63 | 1.05 | 11.84 | 19.65 | 8.23 | 1.55 | 13.18
ECCL1- | 132 | 31.54 | 11.74 | 8.55 | 25.15 | 39.11 | 14.96 | 10.08 | 31.24
GALA1- | 132 | 20.36 | 8.66 | 0.37 | 12.61 | 20.89 | 9.12 | 0.91 | 13.81
GAWH1Q | 132 | 29.5 | 10.29 | 4.62 | 19.17 | 35.41 | 13.41 | 4.49 | 23.46
GLLE1- | 132 | 18.58 | 7.8 | 0.58 | 11.61 | 18.21 | 8 | 0.6 | 11.92
GLNI1- | 132 | 45.57 | 17.76 | 5.99 | 31.11 | 52.6 | 21.27 | 6.4 | 36.49
GRNA1- | 132 | 38 | 14.11 | 7.56 | 27.51 | 45.69 | 17.61 | 8.73 | 33.64
HAWI1- | 132 | 10.22 | 4.83 | 0.04 | 6.86 | 11.02 | 5.04 | 0.16 | 7.29
HELE1- | 132 | 18.11 | 8.66 | 0.04 | 12.28 | 18.71 | 8.8 | 0.24 | 12.68
HUER1- | 132 | 36.32 | 13.24 | 9.02 | 27.74 | 43.05 | 16.18 | 10.99 | 33.87
KEOO1- | 132 | 20.24 | 8.25 | 1.12 | 12.79 | 19.98 | 8.43 | 1.28 | 13.21
KILS1- | 132 | 23.46 | 9.07 | 4.59 | 17.42 | 23.56 | 9.23 | 5.49 | 18.54
KILW1Q | 132 | 24.29 | 9.41 | 2.14 | 15.45 | 23.88 | 9.71 | 1.94 | 15.67
KILW1R | 132 | 23.95 | 9.33 | 1.94 | 15.14 | 23.33 | 9.53 | 1.79 | 15.27
MAHI1- | 132 | 15.11 | 4.99 | 3.01 | 10.06 | 17.55 | 6.3 | 3.76 | 12.66
MAHI1B | 132 | 13.69 | 4.46 | 3.17 | 9.48 | 15.64 | 5.53 | 3.99 | 11.81
MARG1- | 132 | 12.51 | 4.86 | 0.79 | 7.66 | 11.64 | 4.75 | 0.8 | 7.51
MAYB1- | 132 | 17.89 | 6.43 | 0.59 | 9.67 | 18.03 | 7.26 | 0.78 | 11.05
MEAD1- | 132 | 26.38 | 10.04 | 2.35 | 16.55 | 25.63 | 10.3 | 2.12 | 16.68
MIDM1- | 132 | 20.11 | 6.78 | 2.42 | 12.01 | 24.1 | 9.28 | 3.05 | 16.17
MOFF1- | 132 | 26 | 8.96 | 6.67 | 19.35 | 32.34 | 11.73 | 8.45 | 25.04
MOSM1A | 132 | 42.79 | 16.79 | 5.43 | 29.17 | 50.27 | 20.31 | 6.53 | 35.26
MOSM1B | 132 | 42.68 | 16.75 | 5.37 | 29.06 | 50.28 | 20.33 | 6.46 | 35.21
NECU1- | 132 | 38.55 | 12.99 | 9.36 | 27.73 | 44.54 | 16.08 | 10.19 | 32.94
NECU1B | 132 | 36.34 | 13.19 | 8.75 | 27.41 | 41.62 | 15.59 | 10.11 | 32.15
NECU1C | 132 | 38.9 | 13.24 | 8.59 | 27.32 | 43 | 15.63 | 8.93 | 31.04
NEIL1- | 132 | 46.22 | 16.33 | 11.41 | 34.5 | 56.08 | 20.87 | 13.71 | 43.22
NETS1- | 132 | 13.07 | 5.64 | 0.23 | 8.2 | 13.29 | 5.84 | 0.47 | 8.73
REDH1- | 132 | 31.65 | 13.45 | 1.06 | 20.08 | 32.9 | 14.25 | 1.48 | 21.62
SMEA1- | 132 | 19.62 | 7.64 | 4.95 | 15.76 | 20.67 | 8.09 | 5.75 | 17.19
STLE1- | 132 | 23.04 | 10.45 | 0.19 | 14.97 | 22.62 | 10.36 | 0.64 | 15.28
TONG1- | 132 | 11.95 | 5.47 | 0.24 | 7.97 | 16.66 | 7.71 | 0.33 | 11.23
TORN1- | 132 | 32.25 | 10.99 | 8.44 | 23.98 | 38.41 | 13.8 | 10.66 | 30.18
WESE1- | 132 | 15.15 | 6.08 | 4.26 | 12.86 | 16.81 | 6.4 | 4.72 | 13.77
WFIE1A | 132 | 30.77 | 12.78 | 4.52 | 22.59 | 32.18 | 13.44 | 5.55 | 24.56
WFIE1B | 132 | 41.52 | 16.64 | 4.74 | 28.27 | 44.47 | 18.5 | 5.67 | 31.84
WISH1- | 132 | 15.44 | 4.63 | 4.35 | 10.91 | 18.77 | 6.34 | 5.4 | 14.36
WIYH1- | 132 | 47.37 | 18 | 10.21 | 35.67 | 58.23 | 23.02 | 12.61 | 45.17
AYR-3- | 33 | 41.49 | 14.44 | 10.87 | 31.29 | 5.91 | 4.09 | 0 | 5.79
BAGA3- | 33 | 42.58 | 14.26 | 3.69 | 23.86 | 4.47 | 3.1 | 0 | 4.39
BAIN3- | 33 | 31.05 | 11.06 | 6.25 | 21.89 | 2.97 | 2.06 | 0 | 2.92
BERW3- | 33 | 41.26 | 14.84 | 1.47 | 22.46 | 4.68 | 3.21 | 0 | 4.54
BLAH3A | 33 | 47.79 | 13.8 | 10.01 | 29.53 | 4.51 | 3.13 | 0 | 4.42
BLAH3B | 33 | 27.5 | 9.71 | 7.92 | 21.66 | 4.46 | 3.09 | 0 | 4.37
BLCW3- | 33 | 29.12 | 9.03 | 2.9 | 15.67 | 2.26 | 1.57 | 0 | 2.22
BONN3- | 33 | 42.75 | 13.6 | 8.34 | 27.58 | 4.48 | 3.11 | 0 | 4.4
BPGR3- | 33 | 95.86 | 29.17 | 21.65 | 62.9 | 6.02 | 4.17 | 0 | 5.89
BRAP3- | 33 | 43.41 | 13.55 | 9.76 | 28.93 | 4.45 | 3.07 | 0 | 4.35
BROX3- | 33 | 28.58 | 10.15 | 3.8 | 18.15 | 4.36 | 3.02 | 0 | 4.27
CATY3- | 33 | 30.27 | 10.6 | 4.7 | 19.68 | 2.97 | 2.06 | 0 | 2.91
CHAP3- | 33 | 48.68 | 17.83 | 4.39 | 29.61 | 4.53 | 3.14 | 0 | 4.44
CHAS3A | 33 | 34.03 | 11.89 | 8.64 | 25.45 | 3.01 | 2.09 | 0 | 2.95
CHAS3B | 33 | 34.03 | 11.89 | 8.64 | 25.45 | 3.01 | 2.09 | 0 | 2.95
CLYM3- | 33 | 50.26 | 17.65 | 11.37 | 36.33 | 5.91 | 4.1 | 0 | 5.79
CLYN3A | 33 | 41.84 | 18.13 | 8.06 | 33.7 | 3.01 | 2.09 | 0 | 2.95
CLYN3B | 33 | 41.94 | 18.17 | 8.07 | 33.77 | 3.01 | 2.09 | 0 | 2.95
CLYN3C | 33 | 41.82 | 18.12 | 8.08 | 33.71 | 3.01 | 2.09 | 0 | 2.95
CLYN3D | 33 | 41.85 | 18.14 | 8 | 33.65 | 3.01 | 2.09 | 0 | 2.95
CLYS3A | 33 | 43.12 | 17.02 | 7.74 | 31.81 | 3.02 | 2.1 | 0 | 2.96
CLYS3B | 33 | 46.84 | 17.75 | 7.89 | 33 | 3.02 | 2.09 | 0 | 2.96
COAT3- | 33 | 39.71 | 13.61 | 11.81 | 31.06 | 5.89 | 4.08 | 0 | 5.77
COCK3- | 33 | 42.57 | 14.97 | 11.23 | 32.4 | 5.89 | 4.08 | 0 | 5.78
COYL3- | 33 | 39.92 | 14.06 | 5.23 | 25.1 | 3.02 | 2.09 | 0 | 2.96
CROO3J | 33 | 34.69 | 12.71 | 3.63 | 21.61 | 3.02 | 2.09 | 0 | 2.96
CROO3K | 33 | 32.68 | 11.92 | 3.81 | 20.67 | 2.99 | 2.07 | 0 | 2.93
CUMB3- | 33 | 37.63 | 13.31 | 4.7 | 23.52 | 4.45 | 3.08 | 0 | 4.36
CUPA3- | 33 | 27.49 | 10.2 | 1.24 | 15.66 | 4.32 | 2.99 | 0 | 4.23
DALM3- | 33 | 34.03 | 11.89 | 7.67 | 24.49 | 4.49 | 3.11 | 0 | 4.4
DESA3- | 33 | 36.9 | 11.09 | 5.29 | 20.98 | 2.27 | 1.57 | 0 | 2.23
DEVM3- | 33 | 35.96 | 13.18 | 4.53 | 23.17 | 2.99 | 2.07 | 0 | 2.93
DEVO3- | 33 | 41.29 | 15.2 | 3.65 | 25.14 | 4.5 | 3.12 | 0 | 4.41
DEWP3- | 33 | 48.79 | 16.61 | 12.43 | 35.92 | 7.79 | 5.39 | 0 | 7.63
DRCR3- | 33 | 28.08 | 10.32 | 3.08 | 17.68 | 4.38 | 3.04 | 0 | 4.3
DRUM3- | 33 | 39.53 | 13.56 | 11.18 | 30.35 | 5.85 | 4.05 | 0 | 5.73
DUMF3A | 33 | 38.48 | 14.03 | 1.9 | 21.74 | 4.42 | 3.06 | 0 | 4.33
DUMF3B | 33 | 35.74 | 13.43 | 1.99 | 20.99 | 4.43 | 3.07 | 0 | 4.34
DUMF3I | 33 | 19.49 | 6.94 | 1.77 | 11.58 | 1.5 | 1.04 | 0 | 1.47
DUNB3A | 33 | 46.07 | 13.74 | 3.66 | 23.1 | 3.04 | 2.11 | 0 | 2.99
DUNB3B | 33 | 44.32 | 13.37 | 5.75 | 24.65 | 4.53 | 3.15 | 0 | 4.45
DUNE3- | 33 | 46.62 | 16.3 | 3.44 | 26.49 | 4.54 | 3.14 | 0 | 4.44
DUNF3- | 33 | 32.05 | 11.67 | 3.85 | 20.34 | 4.4 | 3.05 | 0 | 4.31
DUNH3- | 33 | 43.71 | 13.03 | 9.43 | 27.86 | 4.52 | 3.13 | 0 | 4.43
ECCL3- | 33 | 36.31 | 14.11 | 5.51 | 25.47 | 5.24 | 3.6 | 0 | 5.1
EERH3- | 33 | 46.66 | 15.94 | 13.9 | 36.44 | 5.91 | 4.1 | 0 | 5.8
EKIL3- | 33 | 52.43 | 18.29 | 14.72 | 40.59 | 5.92 | 4.1 | 0 | 5.8
EKIS3- | 33 | 56.2 | 19.09 | 10.24 | 37.23 | 5.96 | 4.14 | 0 | 5.85
ELDE3- | 33 | 40.1 | 14.42 | 5.14 | 25.54 | 3.03 | 2.1 | 0 | 2.97
ERSK3- | 33 | 30.18 | 10.91 | 5.1 | 20.54 | 3 | 2.08 | 0 | 2.94
EWEH3- | 33 | 35.71 | 11.11 | 2.79 | 18.5 | 2.26 | 1.57 | 0 | 2.22
FINN3- | 33 | 31.47 | 11.2 | 6.28 | 22.12 | 4.43 | 3.07 | 0 | 4.33
GALA3- | 33 | 38.18 | 14.3 | 2.22 | 22.44 | 4.9 | 3.39 | 0 | 4.8
GAWH3- | 33 | 34.89 | 10.64 | 7.18 | 22.23 | 2.27 | 1.57 | 0 | 2.23
GIFF3A | 33 | 35.95 | 12.67 | 7.79 | 25.7 | 5.29 | 3.66 | 0 | 5.17
GIFF3B | 33 | 36.08 | 12.71 | 7.84 | 25.82 | 5.29 | 3.66 | 0 | 5.18
GLGL3- | 33 | 43.39 | 13.17 | 6.99 | 25.62 | 4.51 | 3.13 | 0 | 4.43
GLLU3- | 33 | 38.86 | 14.76 | 0.5 | 21.38 | 4.11 | 2.85 | 0 | 4.03
GLNI3- | 33 | 39.38 | 14.47 | 6.54 | 27.01 | 4.49 | 3.11 | 0 | 4.4
GLRO3A | 33 | 34.46 | 12.18 | 8.19 | 25.42 | 5.38 | 3.72 | 0 | 5.26
GLRO3B | 33 | 32.79 | 11.55 | 8.02 | 24.35 | 5.38 | 3.72 | 0 | 5.26
GORG3- | 33 | 28.94 | 10.27 | 5.16 | 19.68 | 2.97 | 2.06 | 0 | 2.91
GOVA3- | 33 | 31.39 | 10.98 | 6.08 | 21.61 | 4.38 | 3.03 | 0 | 4.29
GRMO3A | 33 | 40.66 | 14.1 | 9.35 | 29.29 | 5.87 | 4.07 | 0 | 5.75
GRMO3C | 33 | 40.74 | 14.12 | 9.5 | 29.47 | 5.88 | 4.07 | 0 | 5.76
HAGR3- | 33 | 31.17 | 11.05 | 5.01 | 20.63 | 3 | 2.08 | 0 | 2.94
HAWI3- | 33 | 22.55 | 9.25 | 0.26 | 13.34 | 2.97 | 2.06 | 0 | 2.91
HELE3- | 33 | 26.41 | 10.46 | 0.78 | 15.57 | 2.97 | 2.06 | 0 | 2.91
HUNF3- | 33 | 42.95 | 16.5 | 6.47 | 29.81 | 3.03 | 2.11 | 0 | 2.98
INKE3- | 33 | 29.86 | 10.97 | 2.39 | 17.9 | 4.37 | 3.02 | 0 | 4.28
JOHN3- | 33 | 30.27 | 10.58 | 5.83 | 20.78 | 3 | 2.08 | 0 | 2.93
KAIM3- | 33 | 35.91 | 10.99 | 8.43 | 23.97 | 5.62 | 3.88 | 0 | 5.49
KIER3- | 33 | 34.32 | 11.98 | 5.76 | 22.71 | 4.4 | 3.05 | 0 | 4.31
KILB3- | 33 | 33.84 | 12.35 | 5.31 | 22.77 | 2.99 | 2.07 | 0 | 2.93
KILS3- | 33 | 42.27 | 14.74 | 10.56 | 31.4 | 5.93 | 4.11 | 0 | 5.81
KILT3- | 33 | 58.59 | 20.27 | 10.77 | 39.43 | 6 | 4.16 | 0 | 5.88
KILW3- | 33 | 32.08 | 11.56 | 5.2 | 21.55 | 4.42 | 3.06 | 0 | 4.33
LEVE3- | 33 | 38.43 | 14.67 | 1.42 | 22.17 | 2.99 | 2.07 | 0 | 2.93
LING3- | 33 | 47.98 | 15.37 | 4.24 | 25.98 | 4.46 | 3.1 | 0 | 4.38
LINM3- | 33 | 60.15 | 20.12 | 6.85 | 35.3 | 4.55 | 3.16 | 0 | 4.47
MAHI3- | 33 | 48.46 | 14.99 | 6.37 | 27.57 | 3.05 | 2.12 | 0 | 3
MAYB3- | 33 | 28.38 | 9.87 | 1.31 | 15.27 | 1.54 | 1.07 | 0 | 1.51
NEAR3- | 33 | 51.69 | 17.84 | 10.49 | 35.71 | 5.97 | 4.14 | 0 | 5.85
NETS3- | 33 | 20.72 | 7.89 | 0.98 | 12.14 | 3.13 | 2.15 | 0 | 3.04
PAIS3- | 33 | 34.29 | 12.2 | 6.36 | 23.62 | 3.02 | 2.09 | 0 | 2.96
PART3- | 33 | 35.98 | 13.12 | 4.48 | 23.03 | 3 | 2.08 | 0 | 2.94
POOB3- | 33 | 56.04 | 19.51 | 12.53 | 40.12 | 5.96 | 4.13 | 0 | 5.84
PORD3- | 33 | 50.15 | 17.49 | 12.23 | 36.96 | 6.02 | 4.17 | 0 | 5.9
RAVE3- | 33 | 41.49 | 15.62 | 3.28 | 25.37 | 5.87 | 4.07 | 0 | 5.76
REDH3- | 33 | 38.57 | 14.42 | 3.08 | 23.47 | 3.77 | 2.61 | 0 | 3.7
SACO3J | 33 | 40.95 | 14.68 | 4.25 | 25.01 | 2.99 | 2.08 | 0 | 2.94
SACO3K | 33 | 40.4 | 15 | 3.96 | 25.17 | 3 | 2.08 | 0 | 2.95
SANX3- | 33 | 32.17 | 11.42 | 4.99 | 21.14 | 2.97 | 2.06 | 0 | 2.91
SHRU3- | 33 | 48.11 | 16.54 | 12 | 35.39 | 5.97 | 4.13 | 0 | 5.85
SIGH3A | 33 | 43.65 | 15.1 | 10.89 | 32.24 | 4.5 | 3.12 | 0 | 4.41
SIGH3B | 33 | 43.52 | 15.06 | 10.69 | 31.99 | 4.5 | 3.12 | 0 | 4.41
SPAV3- | 33 | 27.77 | 10.08 | 3.72 | 17.97 | 4.35 | 3.01 | 0 | 4.26
STHA3- | 33 | 53.71 | 19.23 | 11.79 | 38.98 | 5.98 | 4.15 | 0 | 5.86
STIR3- | 33 | 39.37 | 13.61 | 6.62 | 25.86 | 4.45 | 3.08 | 0 | 4.35
STLE3S | 33 | 34.49 | 12.93 | 2.29 | 20.58 | 2.99 | 2.07 | 0 | 2.93
TELR3- | 33 | 28.04 | 9.96 | 4.66 | 18.74 | 2.96 | 2.05 | 0 | 2.9
TONG3- | 33 | 21.78 | 8.54 | 1.02 | 13.11 | 2.94 | 2.04 | 0 | 2.88
WFIE3- | 33 | 39 | 14.11 | 7.29 | 27.25 | 3.04 | 2.11 | 0 | 2.98
WGEO3- | 33 | 50.06 | 17.52 | 10.14 | 34.92 | 5.99 | 4.15 | 0 | 5.87
WHHO3- | 33 | 42.23 | 14.79 | 9.93 | 30.84 | 5.85 | 4.06 | 0 | 5.73
WHTL3- | 33 | 26.42 | 10.51 | 0.81 | 15.67 | 2.24 | 1.56 | 0 | 2.2
WISH3- | 33 | 43.36 | 14.95 | 10.15 | 31.29 | 5.94 | 4.12 | 0 | 5.82
WLEE3A | 33 | 50.13 | 20.95 | 10.47 | 40.1 | 3.04 | 2.11 | 0 | 2.98
WLEE3B | 33 | 50.33 | 21.03 | 10.46 | 40.2 | 3.04 | 2.11 | 0 | 2.98
WLEE3C | 33 | 49.75 | 20.76 | 10.41 | 39.77 | 3.04 | 2.11 | 0 | 2.98
WLEX3A | 33 | 56.91 | 19.9 | 9.46 | 37.6 | 3.02 | 2.1 | 0 | 2.97
WLEX3B | 33 | 57.16 | 19.99 | 9.46 | 37.73 | 3.02 | 2.1 | 0 | 2.97
WLEX3C | 33 | 54.67 | 19.1 | 9.44 | 36.46 | 3.03 | 2.1 | 0 | 2.97
BAGA0J | 25 | 16.22 | 5.94 | 3.63 | 12.03 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.21 | 5.94 | 3.63 | 12.03 | 0 | 0 | 0 | 0
BONN0J | 25 | 17.99 | 6.47 | 5.35 | 14.5 | 0 | 0 | 0 | 0
BONN0K | 25 | 17.99 | 6.47 | 5.35 | 14.5 | 0 | 0 | 0 | 0
BONN0L | 25 | 17.99 | 6.47 | 5.35 | 14.5 | 0 | 0 | 0 | 0
CATY0J | 25 | 10.03 | 3.7 | 1.71 | 6.94 | 0 | 0 | 0 | 0
CATY0K | 25 | 10.04 | 3.7 | 1.74 | 6.98 | 0 | 0 | 0 | 0
CURR0J | 25 | 21.09 | 7.64 | 6.44 | 17.25 | 0 | 0 | 0 | 0
CURR0K | 25 | 21.09 | 7.64 | 6.44 | 17.25 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.41 | 3.02 | 2.58 | 6.85 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.41 | 3.02 | 2.58 | 6.85 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.74 | 6.02 | 1.34 | 9.85 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.4 | 7.23 | 2.77 | 13 | 0 | 0 | 0 | 0
ELVA0J | 25 | 19.07 | 6.73 | 8.07 | 17.58 | 0 | 0 | 0 | 0
ELVA0K | 25 | 19.07 | 6.73 | 8.07 | 17.58 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.06 | 3.95 | 3.4 | 8.98 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.06 | 3.95 | 3.4 | 8.98 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.95 | 3.67 | 1.92 | 7.12 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.95 | 3.67 | 1.93 | 7.13 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.75 | 6.75 | 5.67 | 15.22 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.75 | 6.75 | 5.67 | 15.22 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.57 | 3.81 | 2.92 | 8.31 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.53 | 3.8 | 2.86 | 8.24 | 0 | 0 | 0 | 0
SANX0J | 25 | 16.99 | 6.08 | 4.67 | 13.26 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.97 | 6.07 | 4.62 | 13.2 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.46 | 3.81 | 2.31 | 7.71 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.46 | 3.81 | 2.31 | 7.71 | 0 | 0 | 0 | 0
WISH0J | 25 | 20.81 | 7.47 | 6.37 | 16.93 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.81 | 7.47 | 6.37 | 16.93 | 0 | 0 | 0 | 0
CAFA5- | 11 | 30.71 | 11.1 | 5.28 | 20.97 | 2.24 | 1.56 | 0 | 2.2
CURR5- | 11 | 34.73 | 12.53 | 5.76 | 23.49 | 4.49 | 3.11 | 0 | 4.4
EAST5- | 11 | 24.11 | 9.21 | 2.39 | 15.41 | 1.14 | 0.79 | 0 | 1.12
GLLE5- | 11 | 33.22 | 12.21 | 6.9 | 24.18 | 2.29 | 1.59 | 0 | 2.24
KEOO5- | 11 | 33.02 | 12.11 | 5.34 | 22.46 | 2.27 | 1.58 | 0 | 2.23
KILB5- | 11 | 29 | 10.6 | 4.14 | 19.14 | 3.01 | 2.08 | 0 | 2.95
TONG5- | 11 | 71.47 | 28.19 | 4.66 | 44.53 | 4.54 | 3.15 | 0 | 4.45

## D2.5
ETYS 19 Yr 5 - SPT Fault Levels (kA), Winter 2023/23
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
COAL4- | 400 | 55.12 | 20.57 | 9.95 | 39.04 | 47.57 | 18.83 | 8.16 | 34.79 | Back To Menu
CRYR4- | 400 | 63.21 | 22.68 | 14.17 | 46.25 | 61.73 | 23.27 | 14.3 | 47.21
DENN4- | 400 | 22.36 | 8.22 | 6.58 | 18.21 | 20.59 | 7.8 | 5.55 | 16.58
DEVM4- | 400 | 34.98 | 13.02 | 6.92 | 25.34 | 29.92 | 11.77 | 5.52 | 22.17
ECCL4A | 400 | 49.13 | 18.04 | 10.94 | 36.44 | 40.23 | 15.62 | 7.72 | 29.8
ECCL4B | 400 | 49.2 | 18.06 | 10.94 | 36.48 | 40.29 | 15.64 | 7.74 | 29.86
ELVA4- | 400 | 61.27 | 23.14 | 9.96 | 42.69 | 47.9 | 19.24 | 7.12 | 34.34
FALL4- | 400 | 54.14 | 19.57 | 11.71 | 39.39 | 49.44 | 18.88 | 10.5 | 37.2
GRNA4- | 400 | 51.8 | 19.74 | 8.03 | 35.95 | 42.56 | 16.84 | 7.69 | 31.5
HUCS4- | 400 | 48.79 | 18.02 | 9.08 | 34.56 | 57.25 | 21.9 | 11.1 | 42.07
HUER4- | 400 | 49.07 | 18.12 | 9.11 | 34.73 | 57.43 | 21.98 | 11.04 | 42.13
HUNE4- | 400 | 49.07 | 18.12 | 9.1 | 34.72 | 57.47 | 21.99 | 11.06 | 42.16
KILS4- | 400 | 49.3 | 18.15 | 9.42 | 35.09 | 45.32 | 17.63 | 8.94 | 33.87
KILS4T | 400 | 46.08 | 17.11 | 9.03 | 33.24 | 41.97 | 16.37 | 8.33 | 31.48
MOFF4- | 400 | 45.85 | 17.5 | 7.1 | 31.85 | 38.42 | 15.31 | 6.51 | 28.17
STHA4A | 400 | 61.1 | 22.61 | 11.28 | 43.26 | 56.48 | 21.97 | 10.72 | 41.79
STHA4B | 400 | 57.23 | 21.23 | 11.35 | 41.37 | 52.59 | 20.45 | 10.45 | 39.37
TORN4- | 400 | 72.69 | 25.93 | 17.22 | 53.89 | 72.59 | 27.11 | 18.98 | 57.31
WISH4- | 400 | 54.28 | 20.24 | 9.35 | 37.97 | 50.13 | 19.56 | 9.5 | 37.17
AUCH2- | 275 | 15.91 | 5.79 | 2.09 | 10.28 | 15.87 | 6.27 | 1.92 | 10.79
BUSB2- | 275 | 54.25 | 20.46 | 9.52 | 38.44 | 49.48 | 19.74 | 7.12 | 35.04
CLYM2- | 275 | 82.76 | 30.52 | 16.42 | 59.58 | 74.35 | 29.12 | 13.75 | 54.94
CLYN2Q | 275 | 18.51 | 7.5 | 5.86 | 16.46 | 18.46 | 7.08 | 6.02 | 16.03
CLYS2R | 275 | 17.04 | 6.43 | 4.98 | 14.08 | 17.19 | 6.63 | 4.85 | 14.23
COCK2- | 275 | 66.87 | 24.91 | 13.58 | 48.81 | 59.4 | 23.21 | 11.49 | 44.31
COYL2- | 275 | 55.94 | 19.69 | 11.44 | 39.29 | 55.3 | 21.23 | 10 | 40.02
CURR2- | 275 | 60.55 | 22.73 | 10.69 | 42.84 | 55.86 | 21.95 | 10.19 | 41.24
DALL2- | 275 | 36.12 | 12.89 | 7.68 | 25.91 | 34.16 | 13.12 | 6.73 | 25.29
DENN2- | 275 | 75.82 | 28.42 | 15.08 | 55.27 | 65.86 | 25.9 | 12.73 | 49.36
EERH2- | 275 | 71.47 | 26.53 | 13.94 | 51.46 | 62.06 | 24.42 | 10.76 | 45.3
EKIS2- | 275 | 67.2 | 25.35 | 12.64 | 48.48 | 64.93 | 25.93 | 10.43 | 47.1
ELVA2Q | 275 | 19.19 | 7.67 | 6.77 | 17.62 | 18.45 | 7.2 | 5.56 | 15.75
ELVA2R | 275 | 17.59 | 6.53 | 6.26 | 15.49 | 17.95 | 6.74 | 5.8 | 15.33
GLRO2- | 275 | 42.63 | 17.51 | 6.34 | 31.1 | 34.65 | 14.2 | 5.36 | 25.45
GRMO2- | 275 | 47.14 | 18.23 | 8.6 | 34.38 | 39.71 | 15.82 | 7.45 | 29.82
INVR2- | 275 | 35.07 | 13.09 | 6.16 | 24.67 | 31.65 | 12.55 | 5.13 | 22.88
KAIM2- | 275 | 64.36 | 23.97 | 12.18 | 46.08 | 61.41 | 24.01 | 10.79 | 44.74
KILG2- | 275 | 20.17 | 7.08 | 3.1 | 13.11 | 22.92 | 8.71 | 4.04 | 16.36
KILS2- | 275 | 63.8 | 22.51 | 14.58 | 46.42 | 66.94 | 25.28 | 14.77 | 50.53
KINC2- | 275 | 62.47 | 24.18 | 14.15 | 48.35 | 49.17 | 19.68 | 8.51 | 36.35
LAMB2- | 275 | 59.89 | 22.37 | 10.63 | 42.26 | 51.52 | 20.52 | 8.28 | 37.3
LOAN2- | 275 | 83.76 | 31.83 | 17.03 | 62.05 | 64.9 | 26.06 | 9.64 | 46.49
MAHI2- | 275 | 21.78 | 7.57 | 3.43 | 14.14 | 24.43 | 9.2 | 4.31 | 17.32
MOSM2- | 275 | 50.35 | 20.17 | 7.72 | 36.24 | 41.91 | 16.97 | 7.08 | 31.09
NEAR2Q | 275 | 53.24 | 20.06 | 9.01 | 37.38 | 47.85 | 18.98 | 7.74 | 34.58
NECU2- | 275 | 47.63 | 16.91 | 9.46 | 33.38 | 46.73 | 17.86 | 9.72 | 34.98
NEIL2- | 275 | 70 | 25.73 | 14.32 | 50.71 | 67.91 | 26.32 | 13.52 | 50.74
SMEA2- | 275 | 66.15 | 24.51 | 13.96 | 48.63 | 65.68 | 25.34 | 13.62 | 49.45
STHA2A | 275 | 69.03 | 25.6 | 14.3 | 50.5 | 69.63 | 26.9 | 14.61 | 52.65
STHA2B | 275 | 74.42 | 27.7 | 15.47 | 54.64 | 74.3 | 28.91 | 15.48 | 56.37
WFIE2- | 275 | 56.11 | 22.7 | 8.86 | 40.96 | 47.32 | 19.19 | 8.14 | 35.28
WISH2- | 275 | 54.53 | 19.98 | 11.86 | 40.11 | 57.76 | 22.01 | 13.22 | 44.35
WIYH2- | 275 | 62.71 | 23.02 | 12.25 | 44.8 | 60.89 | 23.61 | 12.48 | 45.87
WLEE2- | 275 | 58.29 | 22.92 | 7.3 | 39.71 | 49.21 | 22.14 | 9.53 | 40.84
WLEX2- | 275 | 46.35 | 18.6 | 4.97 | 31.27 | 37.49 | 16.81 | 8.39 | 32.16
AREC1- | 132 | 13.72 | 4.53 | 1.67 | 8.07 | 16.64 | 5.99 | 2.39 | 10.86
BLAH1- | 132 | 35.17 | 11.5 | 6.14 | 22.4 | 36.66 | 13.35 | 6.25 | 25.14
BLCW1- | 132 | 12.08 | 4.71 | 0.73 | 7.39 | 11.39 | 4.65 | 0.86 | 7.43
BONN1- | 132 | 51.18 | 18.9 | 9.02 | 35.74 | 60.43 | 23.42 | 10.04 | 43.16
BRAP1- | 132 | 32.68 | 12.1 | 4.06 | 21.18 | 35.34 | 13.98 | 3.93 | 23.7
CHAP1- | 132 | 30.86 | 12.28 | 1.3 | 18.66 | 31.5 | 13.26 | 1.69 | 20.45
COAL1- | 132 | 24.62 | 7.81 | 6.05 | 17.09 | 30.81 | 10.84 | 6.78 | 22.11
COAL1A | 132 | 38.76 | 12.8 | 10.13 | 28.23 | 47.75 | 16.66 | 11.66 | 35.22
COYL1- | 132 | 27.31 | 9.18 | 6.49 | 19.46 | 31.94 | 11.54 | 7.96 | 24.28
CRYR1- | 132 | 15.72 | 5.18 | 4.4 | 11.74 | 16.57 | 5.82 | 5.1 | 13.33
CRYR1A | 132 | 15.53 | 6.19 | 4.83 | 13.58 | 17.34 | 6.54 | 5.58 | 14.83
CURR1A | 132 | 36.6 | 12.86 | 9.29 | 27.48 | 44.77 | 16.43 | 11.03 | 34.27
CURR1B | 132 | 36.6 | 12.86 | 9.29 | 27.48 | 44.77 | 16.43 | 11.03 | 34.27
DALM1- | 132 | 26.4 | 9.3 | 7.03 | 20.18 | 31.81 | 11.67 | 8.58 | 25.08
DEVM1- | 132 | 32.59 | 12.14 | 7.12 | 24.29 | 38.91 | 14.96 | 8.16 | 29.32
DEVO1- | 132 | 28.15 | 11.71 | 1.17 | 17.73 | 27.79 | 12.12 | 2.13 | 19.28
DUMF1- | 132 | 20.22 | 8.22 | 0.51 | 12.12 | 23.46 | 9.84 | 0.82 | 14.73
DUNE1- | 132 | 18.7 | 7.65 | 1.05 | 11.87 | 19.72 | 8.23 | 1.54 | 13.18
ECCL1- | 132 | 31.6 | 11.74 | 8.46 | 25.06 | 39.1 | 14.92 | 9.95 | 31.05
GALA1- | 132 | 20.93 | 8.74 | 0.52 | 12.88 | 20.9 | 8.92 | 1.1 | 13.71
GAWH1Q | 132 | 30.47 | 10.48 | 4.56 | 19.39 | 36.38 | 13.75 | 4.38 | 23.83
GLGL1- | 132 | 26.64 | 9.09 | 2.93 | 15.78 | 26.05 | 9.84 | 3.08 | 16.99
GLLE1- | 132 | 18.76 | 7.85 | 0.58 | 11.68 | 18.76 | 8.25 | 0.58 | 12.24
GLNI1- | 132 | 46 | 17.99 | 6.11 | 31.56 | 52.91 | 21.42 | 6.48 | 36.78
GRNA1- | 132 | 38.01 | 14.14 | 7.44 | 27.43 | 45.39 | 17.53 | 8.58 | 33.38
HAWI1- | 132 | 10.26 | 4.85 | 0.04 | 6.89 | 11.07 | 5.06 | 0.17 | 7.32
HELE1- | 132 | 17.92 | 8.55 | 0.04 | 12.13 | 18.54 | 8.71 | 0.24 | 12.55
HUER1- | 132 | 34.85 | 12.74 | 7.85 | 25.86 | 41.21 | 15.55 | 9.64 | 31.63
KEOO1- | 132 | 20.3 | 8.26 | 1.1 | 12.78 | 20.76 | 8.76 | 1.25 | 13.64
KILS1- | 132 | 23.17 | 8.93 | 4.47 | 17.11 | 23.31 | 9.12 | 5.37 | 18.27
KILW1Q | 132 | 23.81 | 9.21 | 2.03 | 15.05 | 23.51 | 9.55 | 1.87 | 15.38
KILW1R | 132 | 23.48 | 9.13 | 1.85 | 14.77 | 22.97 | 9.38 | 1.73 | 14.99
MAHI1- | 132 | 15 | 4.94 | 3.01 | 9.99 | 17.51 | 6.27 | 3.79 | 12.66
MAHI1B | 132 | 13.66 | 4.44 | 3.16 | 9.44 | 15.87 | 5.64 | 3.99 | 11.97
MARG1- | 132 | 12.55 | 4.87 | 0.79 | 7.68 | 11.71 | 4.78 | 0.8 | 7.55
MAYB1- | 132 | 17.86 | 6.4 | 0.59 | 9.65 | 18.02 | 7.25 | 0.79 | 11.04
MEAD1- | 132 | 25.9 | 9.84 | 2.27 | 16.18 | 25.27 | 10.14 | 2.07 | 16.41
MIDM1- | 132 | 20.81 | 6.99 | 2.34 | 12.22 | 24.72 | 9.54 | 2.99 | 16.48
MOFF1- | 132 | 34.53 | 12.1 | 8.6 | 25.72 | 43.4 | 15.82 | 11.04 | 33.41
MOSM1A | 132 | 43.19 | 17.01 | 5.53 | 29.58 | 50.57 | 20.45 | 6.62 | 35.54
MOSM1B | 132 | 43.07 | 16.97 | 5.46 | 29.47 | 50.58 | 20.47 | 6.54 | 35.49
NECU1- | 132 | 40.29 | 13.42 | 9.31 | 28.3 | 46 | 16.57 | 10.07 | 33.51
NECU1B | 132 | 36.04 | 13.06 | 8.5 | 26.97 | 41.18 | 15.43 | 9.82 | 31.64
NECU1C | 132 | 38.06 | 12.93 | 8.29 | 26.58 | 42.01 | 15.26 | 8.64 | 30.22
NEIL1- | 132 | 45.08 | 15.91 | 10.7 | 33.21 | 54.89 | 20.43 | 13.02 | 41.9
NETS1- | 132 | 13.56 | 5.74 | 0.26 | 8.38 | 14.89 | 6.42 | 0.55 | 9.64
REDH1- | 132 | 31.94 | 13.62 | 1.07 | 20.34 | 32.99 | 14.3 | 1.48 | 21.71
SMEA1- | 132 | 19.67 | 7.65 | 4.91 | 15.74 | 20.7 | 8.1 | 5.72 | 17.17
STLE1- | 132 | 22.87 | 10.35 | 0.19 | 14.82 | 22.46 | 10.27 | 0.63 | 15.15
TONG1- | 132 | 12.03 | 5.5 | 0.24 | 8.02 | 16.78 | 7.77 | 0.33 | 11.31
TORN1- | 132 | 32.26 | 10.99 | 8.41 | 23.95 | 38.39 | 13.8 | 10.61 | 30.12
WESE1- | 132 | 15.15 | 6.09 | 4.25 | 12.86 | 16.78 | 6.39 | 4.71 | 13.74
WFIE1A | 132 | 31.17 | 12.97 | 4.67 | 23.02 | 32.46 | 13.56 | 5.66 | 24.85
WFIE1B | 132 | 41.96 | 16.87 | 4.89 | 28.75 | 44.81 | 18.65 | 5.78 | 32.16
WISH1- | 132 | 15.38 | 4.61 | 4.32 | 10.84 | 18.69 | 6.31 | 5.35 | 14.27
WIYH1- | 132 | 46.96 | 17.77 | 10.02 | 35.16 | 57.83 | 22.79 | 12.42 | 44.65
AYR-3- | 33 | 41.17 | 14.32 | 10.68 | 30.93 | 5.87 | 4.07 | 0 | 5.75
BAGA3- | 33 | 43.21 | 14.5 | 3.71 | 24.23 | 4.52 | 3.14 | 0 | 4.44
BAIN3- | 33 | 31.5 | 11.23 | 6.32 | 22.2 | 3.02 | 2.1 | 0 | 2.96
BERW3- | 33 | 41.4 | 14.89 | 1.46 | 22.52 | 4.65 | 3.2 | 0 | 4.52
BLAH3A | 33 | 48.48 | 13.99 | 10.37 | 30.15 | 4.51 | 3.13 | 0 | 4.43
BLAH3B | 33 | 47.9 | 13.95 | 10.03 | 29.76 | 4.54 | 3.15 | 0 | 4.45
BLCW3- | 33 | 29.24 | 9.08 | 2.91 | 15.74 | 2.27 | 1.57 | 0 | 2.22
BONN3- | 33 | 43.21 | 13.78 | 8.39 | 27.87 | 4.53 | 3.15 | 0 | 4.45
BPGR3- | 33 | 96.81 | 29.48 | 21.72 | 63.42 | 6.08 | 4.21 | 0 | 5.95
BRAP3- | 33 | 43.93 | 13.7 | 9.8 | 29.18 | 4.52 | 3.13 | 0 | 4.42
BROX3- | 33 | 28.88 | 10.25 | 3.83 | 18.33 | 4.42 | 3.06 | 0 | 4.33
CATY3- | 33 | 30.5 | 10.67 | 4.7 | 19.79 | 3.01 | 2.09 | 0 | 2.95
CHAP3- | 33 | 48.8 | 17.88 | 4.41 | 29.7 | 4.55 | 3.15 | 0 | 4.46
CHAS3A | 33 | 34.2 | 11.95 | 8.61 | 25.51 | 3.04 | 2.1 | 0 | 2.98
CHAS3B | 33 | 34.2 | 11.95 | 8.61 | 25.51 | 3.04 | 2.1 | 0 | 2.98
CLYM3- | 33 | 50.1 | 17.6 | 11.26 | 36.14 | 5.9 | 4.09 | 0 | 5.78
CLYN3A | 33 | 41.75 | 18.1 | 8.02 | 33.61 | 3.01 | 2.08 | 0 | 2.95
CLYN3B | 33 | 41.85 | 18.13 | 8.03 | 33.68 | 3.01 | 2.08 | 0 | 2.95
CLYN3C | 33 | 41.73 | 18.08 | 8.04 | 33.62 | 3.01 | 2.08 | 0 | 2.95
CLYN3D | 33 | 41.76 | 18.1 | 7.96 | 33.56 | 3.01 | 2.08 | 0 | 2.95
CLYS3A | 33 | 43.01 | 16.97 | 7.7 | 31.71 | 3.02 | 2.09 | 0 | 2.96
CLYS3B | 33 | 46.72 | 17.71 | 7.85 | 32.9 | 3.02 | 2.09 | 0 | 2.95
COAT3- | 33 | 39.57 | 13.56 | 11.7 | 30.88 | 5.87 | 4.07 | 0 | 5.75
COCK3- | 33 | 42.49 | 14.94 | 11.2 | 32.33 | 5.88 | 4.08 | 0 | 5.77
COYL3- | 33 | 40.13 | 14.13 | 5.17 | 25.15 | 3.04 | 2.11 | 0 | 2.98
CROO3J | 33 | 34.7 | 12.7 | 3.62 | 21.59 | 3.01 | 2.09 | 0 | 2.95
CROO3K | 33 | 32.63 | 11.89 | 3.83 | 20.65 | 2.98 | 2.07 | 0 | 2.92
CUMB3- | 33 | 37.79 | 13.37 | 4.75 | 23.66 | 4.46 | 3.09 | 0 | 4.37
CUPA3- | 33 | 27.59 | 10.22 | 1.33 | 15.77 | 4.32 | 2.99 | 0 | 4.22
DALM3- | 33 | 34.73 | 12.15 | 7.61 | 24.79 | 4.5 | 3.11 | 0 | 4.41
DESA3- | 33 | 36.92 | 11.09 | 5.29 | 20.98 | 2.27 | 1.58 | 0 | 2.23
DEVM3- | 33 | 35.88 | 13.15 | 4.46 | 23.06 | 2.98 | 2.06 | 0 | 2.92
DEVO3- | 33 | 41.37 | 15.22 | 3.73 | 25.26 | 4.49 | 3.11 | 0 | 4.4
DEWP3- | 33 | 48.71 | 16.59 | 12.39 | 35.85 | 7.78 | 5.39 | 0 | 7.62
DRCR3- | 33 | 28.46 | 10.46 | 3.12 | 17.92 | 4.45 | 3.09 | 0 | 4.36
DRUM3- | 33 | 39.7 | 13.61 | 11.14 | 30.4 | 5.89 | 4.08 | 0 | 5.77
DUMF3A | 33 | 38.61 | 14.09 | 1.9 | 21.82 | 4.42 | 3.07 | 0 | 4.34
DUMF3B | 33 | 35.87 | 13.48 | 2 | 21.07 | 4.44 | 3.08 | 0 | 4.35
DUMF3I | 33 | 19.55 | 6.96 | 1.77 | 11.61 | 1.51 | 1.04 | 0 | 1.48
DUNB3A | 33 | 46.24 | 13.82 | 3.63 | 23.17 | 3.07 | 2.13 | 0 | 3.02
DUNB3B | 33 | 44.33 | 13.37 | 5.75 | 24.65 | 4.52 | 3.14 | 0 | 4.44
DUNE3- | 33 | 46.68 | 16.3 | 3.46 | 26.51 | 4.53 | 3.14 | 0 | 4.44
DUNF3- | 33 | 32.2 | 11.72 | 3.92 | 20.5 | 4.4 | 3.05 | 0 | 4.31
DUNH3- | 33 | 44.35 | 13.21 | 9.75 | 28.43 | 4.53 | 3.14 | 0 | 4.44
ECCL3- | 33 | 36.27 | 14.09 | 5.47 | 25.4 | 5.21 | 3.58 | 0 | 5.07
EERH3- | 33 | 46.54 | 15.9 | 13.78 | 36.27 | 5.91 | 4.09 | 0 | 5.79
EKIL3- | 33 | 53.47 | 18.67 | 14.75 | 41.15 | 6.01 | 4.16 | 0 | 5.89
EKIS3- | 33 | 56.52 | 19.22 | 10.17 | 37.35 | 6.03 | 4.18 | 0 | 5.91
ELDE3- | 33 | 40.04 | 14.4 | 5.08 | 25.44 | 3.02 | 2.09 | 0 | 2.96
ERSK3- | 33 | 29.87 | 10.79 | 5.11 | 20.37 | 2.97 | 2.06 | 0 | 2.91
EWEH3- | 33 | 35.79 | 11.14 | 2.79 | 18.55 | 2.27 | 1.57 | 0 | 2.22
FINN3- | 33 | 31.33 | 11.14 | 6.24 | 22 | 4.41 | 3.05 | 0 | 4.32
GALA3- | 33 | 38.43 | 14.32 | 2.63 | 22.88 | 4.89 | 3.38 | 0 | 4.78
GAWH3- | 33 | 35.03 | 10.66 | 7.19 | 22.26 | 2.27 | 1.57 | 0 | 2.23
GIFF3A | 33 | 36.35 | 12.8 | 7.76 | 25.87 | 5.38 | 3.72 | 0 | 5.26
GIFF3B | 33 | 36.47 | 12.85 | 7.82 | 25.99 | 5.38 | 3.72 | 0 | 5.26
GLGL3- | 33 | 43.86 | 13.3 | 7.12 | 25.93 | 4.52 | 3.14 | 0 | 4.44
GLLU3- | 33 | 39.49 | 14.96 | 0.54 | 21.7 | 4.63 | 3.2 | 0 | 4.53
GLNI3- | 33 | 39.66 | 14.57 | 6.61 | 27.22 | 4.51 | 3.13 | 0 | 4.43
GLRO3A | 33 | 34.83 | 12.31 | 8.29 | 25.71 | 5.4 | 3.74 | 0 | 5.28
GLRO3B | 33 | 33.12 | 11.67 | 8.11 | 24.61 | 5.42 | 3.75 | 0 | 5.3
GORG3- | 33 | 29.25 | 10.38 | 5.2 | 19.88 | 3 | 2.08 | 0 | 2.94
GOVA3- | 33 | 31.61 | 11.05 | 6.07 | 21.7 | 4.42 | 3.06 | 0 | 4.33
GRMO3A | 33 | 40.74 | 14.14 | 9.37 | 29.37 | 5.89 | 4.08 | 0 | 5.77
GRMO3C | 33 | 40.82 | 14.16 | 9.52 | 29.54 | 5.89 | 4.08 | 0 | 5.77
HAGR3- | 33 | 30.91 | 10.94 | 5.02 | 20.49 | 2.98 | 2.06 | 0 | 2.92
HAWI3- | 33 | 22.65 | 9.29 | 0.26 | 13.4 | 2.98 | 2.07 | 0 | 2.92
HELE3- | 33 | 26.28 | 10.41 | 0.78 | 15.49 | 2.96 | 2.05 | 0 | 2.9
HUNF3- | 33 | 42.41 | 16.3 | 6.13 | 29.18 | 3 | 2.08 | 0 | 2.94
INKE3- | 33 | 30.05 | 11.04 | 2.47 | 18.08 | 4.36 | 3.02 | 0 | 4.27
JOHN3- | 33 | 29.97 | 10.46 | 5.8 | 20.59 | 2.99 | 2.07 | 0 | 2.92
KAIM3- | 33 | 36.32 | 11.13 | 8.5 | 24.24 | 5.7 | 3.93 | 0 | 5.56
KIER3- | 33 | 34.19 | 11.93 | 5.73 | 22.6 | 4.4 | 3.04 | 0 | 4.3
KILB3- | 33 | 34.06 | 12.42 | 5.31 | 22.88 | 3.03 | 2.1 | 0 | 2.97
KILS3- | 33 | 41.98 | 14.64 | 10.33 | 31.03 | 5.89 | 4.08 | 0 | 5.78
KILT3- | 33 | 58.83 | 20.35 | 10.58 | 39.35 | 6.05 | 4.2 | 0 | 5.93
KILW3- | 33 | 32.1 | 11.56 | 5.09 | 21.45 | 4.44 | 3.07 | 0 | 4.35
LEVE3- | 33 | 38.67 | 14.76 | 1.47 | 22.34 | 2.99 | 2.07 | 0 | 2.93
LING3- | 33 | 48.57 | 15.6 | 4.21 | 26.28 | 4.54 | 3.15 | 0 | 4.45
LINM3- | 33 | 61.27 | 20.55 | 6.82 | 35.89 | 4.54 | 3.15 | 0 | 4.46
MAHI3- | 33 | 48.38 | 14.95 | 6.34 | 27.48 | 3.05 | 2.12 | 0 | 3
MAYB3- | 33 | 28.49 | 9.9 | 1.31 | 15.32 | 1.55 | 1.07 | 0 | 1.52
NEAR3- | 33 | 51.48 | 17.76 | 10.38 | 35.49 | 5.96 | 4.13 | 0 | 5.84
NETS3- | 33 | 27.71 | 10.66 | 1.03 | 16.1 | 4.54 | 3.14 | 0 | 4.44
PAIS3- | 33 | 34.13 | 12.13 | 6.32 | 23.48 | 3 | 2.08 | 0 | 2.94
PART3- | 33 | 35.81 | 13.05 | 4.44 | 22.9 | 2.99 | 2.07 | 0 | 2.93
POOB3- | 33 | 55.97 | 19.49 | 12.49 | 40.05 | 5.95 | 4.12 | 0 | 5.83
PORD3- | 33 | 49.68 | 17.33 | 12.07 | 36.57 | 5.95 | 4.12 | 0 | 5.83
RAVE3- | 33 | 41.31 | 15.55 | 3.25 | 25.24 | 5.86 | 4.06 | 0 | 5.74
REDH3- | 33 | 38.62 | 14.44 | 3.17 | 23.59 | 3.72 | 2.58 | 0 | 3.64
SACO3J | 33 | 41.04 | 14.71 | 4.13 | 24.93 | 3.02 | 2.09 | 0 | 2.96
SACO3K | 33 | 40.39 | 15 | 3.83 | 25.04 | 3.02 | 2.1 | 0 | 2.96
SANX3- | 33 | 32.38 | 11.49 | 4.98 | 21.23 | 3.02 | 2.09 | 0 | 2.96
SHRU3- | 33 | 47.99 | 16.5 | 11.96 | 35.29 | 5.95 | 4.12 | 0 | 5.83
SIGH3A | 33 | 43.56 | 15.07 | 10.86 | 32.18 | 4.5 | 3.12 | 0 | 4.41
SIGH3B | 33 | 43.43 | 15.04 | 10.66 | 31.93 | 4.49 | 3.12 | 0 | 4.41
SPAV3- | 33 | 27.93 | 10.13 | 3.65 | 17.98 | 4.41 | 3.05 | 0 | 4.31
STHA3- | 33 | 53.56 | 19.17 | 11.63 | 38.75 | 5.96 | 4.13 | 0 | 5.85
STIR3- | 33 | 39.63 | 13.72 | 6.66 | 26.07 | 4.44 | 3.07 | 0 | 4.34
STLE3S | 33 | 34.57 | 12.96 | 2.28 | 20.62 | 2.99 | 2.07 | 0 | 2.93
TELR3- | 33 | 28.34 | 10.06 | 4.7 | 18.93 | 3 | 2.08 | 0 | 2.94
TONG3- | 33 | 22.17 | 8.68 | 1.05 | 13.33 | 2.94 | 2.04 | 0 | 2.88
WFIE3- | 33 | 41.75 | 15 | 8.32 | 29.53 | 3.03 | 2.1 | 0 | 2.97
WGEO3- | 33 | 50.2 | 17.57 | 10.1 | 34.94 | 6.02 | 4.17 | 0 | 5.9
WHHO3- | 33 | 42.8 | 15 | 9.96 | 31.17 | 5.95 | 4.12 | 0 | 5.83
WHTL3- | 33 | 26.34 | 10.45 | 0.85 | 15.63 | 2.24 | 1.55 | 0 | 2.2
WISH3- | 33 | 43.29 | 14.93 | 10.06 | 31.16 | 5.93 | 4.11 | 0 | 5.81
WLEE3A | 33 | 49.99 | 20.9 | 10.36 | 39.92 | 3.03 | 2.1 | 0 | 2.97
WLEE3B | 33 | 50.19 | 20.98 | 10.34 | 40.01 | 3.03 | 2.1 | 0 | 2.97
WLEE3C | 33 | 49.61 | 20.71 | 10.3 | 39.58 | 3.03 | 2.1 | 0 | 2.97
WLEX3A | 33 | 57.23 | 20.03 | 9.31 | 37.64 | 3.04 | 2.11 | 0 | 2.98
WLEX3B | 33 | 57.48 | 20.12 | 9.31 | 37.77 | 3.04 | 2.11 | 0 | 2.98
WLEX3C | 33 | 54.99 | 19.24 | 9.3 | 36.5 | 3.04 | 2.11 | 0 | 2.98
BAGA0J | 25 | 16.46 | 6.03 | 3.68 | 12.21 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.45 | 6.03 | 3.68 | 12.2 | 0 | 0 | 0 | 0
BONN0J | 25 | 18.26 | 6.57 | 5.42 | 14.71 | 0 | 0 | 0 | 0
BONN0K | 25 | 18.26 | 6.57 | 5.42 | 14.71 | 0 | 0 | 0 | 0
BONN0L | 25 | 18.26 | 6.57 | 5.42 | 14.71 | 0 | 0 | 0 | 0
CATY0J | 25 | 10.03 | 3.7 | 1.71 | 6.94 | 0 | 0 | 0 | 0
CATY0K | 25 | 10.03 | 3.7 | 1.74 | 6.97 | 0 | 0 | 0 | 0
CURR0J | 25 | 21.21 | 7.64 | 6.42 | 17.22 | 0 | 0 | 0 | 0
CURR0K | 25 | 21.21 | 7.64 | 6.42 | 17.22 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.39 | 3.01 | 2.57 | 6.83 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.39 | 3.01 | 2.57 | 6.83 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.81 | 6.05 | 1.35 | 9.9 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.48 | 7.27 | 2.78 | 13.06 | 0 | 0 | 0 | 0
ELVA0J | 25 | 18.98 | 6.7 | 8.02 | 17.49 | 0 | 0 | 0 | 0
ELVA0K | 25 | 18.98 | 6.7 | 8.02 | 17.49 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.04 | 3.94 | 3.39 | 8.96 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.04 | 3.94 | 3.39 | 8.97 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.9 | 3.66 | 1.91 | 7.08 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.91 | 3.66 | 1.92 | 7.1 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.71 | 6.74 | 5.65 | 15.18 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.71 | 6.74 | 5.65 | 15.18 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.62 | 3.83 | 2.91 | 8.33 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.59 | 3.82 | 2.85 | 8.26 | 0 | 0 | 0 | 0
SANX0J | 25 | 16.99 | 6.07 | 4.66 | 13.25 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.97 | 6.07 | 4.6 | 13.19 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.43 | 3.8 | 2.31 | 7.69 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.43 | 3.8 | 2.31 | 7.69 | 0 | 0 | 0 | 0
WISH0J | 25 | 20.75 | 7.44 | 6.34 | 16.86 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.75 | 7.44 | 6.34 | 16.86 | 0 | 0 | 0 | 0
CAFA5- | 11 | 30.99 | 11.2 | 5.3 | 21.14 | 2.27 | 1.57 | 0 | 2.23
CURR5- | 11 | 34.64 | 12.51 | 5.74 | 23.42 | 4.47 | 3.1 | 0 | 4.38
EAST5- | 11 | 24.33 | 9.29 | 2.41 | 15.54 | 1.16 | 0.8 | 0 | 1.14
GLLE5- | 11 | 33.18 | 12.2 | 6.92 | 24.17 | 2.28 | 1.58 | 0 | 2.23
KEOO5- | 11 | 32.91 | 12.07 | 5.33 | 22.39 | 2.25 | 1.56 | 0 | 2.21
KILB5- | 11 | 28.88 | 10.56 | 4.12 | 19.06 | 2.99 | 2.08 | 0 | 2.94
TONG5- | 11 | 72.51 | 28.58 | 4.72 | 45.14 | 4.55 | 3.16 | 0 | 4.46

## D2.6
ETYS 19 Yr 7 - SPT Fault Levels (kA), Winter 2025/26
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BRNX4- | 400 | 77.95 | 27.7 | 18.07 | 57.25 | 78.31 | 29.14 | 20.3 | 61.5 | Back To Menu
COAL4- | 400 | 60.09 | 22.12 | 11.02 | 42.3 | 50.9 | 20.08 | 8.66 | 37.06
CRYR4- | 400 | 63.13 | 22.65 | 13.66 | 45.69 | 60.42 | 22.74 | 14.04 | 46.2
DENN4- | 400 | 27.78 | 10.17 | 7.75 | 22.13 | 26.58 | 10.06 | 7.01 | 21.24
DEVM4- | 400 | 35.57 | 13.13 | 7.21 | 25.77 | 30.11 | 11.81 | 5.63 | 22.33
ECCL4A | 400 | 51.26 | 18.56 | 11.65 | 37.89 | 40.81 | 15.78 | 7.85 | 30.17
ECCL4B | 400 | 51.32 | 18.58 | 11.65 | 37.93 | 40.78 | 15.77 | 7.86 | 30.16
ELVA4- | 400 | 62.15 | 23.07 | 10.71 | 43.33 | 47.29 | 18.9 | 7.13 | 33.87
FALL4- | 400 | 54.56 | 19.69 | 11.55 | 39.39 | 49.21 | 18.77 | 10.4 | 36.94
GRNA4- | 400 | 49.05 | 18.41 | 7.76 | 33.8 | 39.99 | 15.75 | 7.24 | 29.5
HUCS4- | 400 | 52.83 | 19.02 | 10.83 | 37.73 | 61.98 | 23.35 | 13.16 | 46.17
HUER4- | 400 | 53.17 | 19.14 | 10.88 | 37.94 | 62.23 | 23.45 | 13.12 | 46.28
HUNE4- | 400 | 53.16 | 19.13 | 10.87 | 37.93 | 62.26 | 23.46 | 13.13 | 46.31
KILS4- | 400 | 52.61 | 19.13 | 10.53 | 37.58 | 47.5 | 18.39 | 9.65 | 35.66
KILS4T | 400 | 49.85 | 18.28 | 10 | 35.86 | 44.68 | 17.38 | 8.92 | 33.5
MOFF4- | 400 | 46.68 | 17.49 | 7.8 | 32.54 | 37.93 | 15.03 | 6.51 | 27.76
STHA4A | 400 | 72.6 | 26.32 | 14.07 | 51.29 | 65.03 | 25.09 | 13.57 | 49.04
STHA4B | 400 | 73.62 | 26.61 | 14.65 | 52.28 | 67.18 | 25.86 | 14.26 | 50.83
TORN4- | 400 | 77.31 | 27.47 | 18.02 | 56.87 | 77.87 | 28.97 | 20.26 | 61.23
WISH4- | 400 | 79.15 | 28.57 | 14.96 | 55.36 | 74.09 | 28.45 | 15.45 | 55.68
AUCH2- | 275 | 15.92 | 5.79 | 2.08 | 10.27 | 15.91 | 6.29 | 1.9 | 10.8
BUSB2- | 275 | 54.43 | 20.38 | 9.88 | 38.69 | 49.34 | 19.63 | 7.25 | 35
CLYM2- | 275 | 83.41 | 30.44 | 17.31 | 60.35 | 74.53 | 29.04 | 14.26 | 55.34
CLYN2Q | 275 | 18.54 | 7.49 | 5.97 | 16.56 | 18.41 | 7.05 | 6.07 | 16.03
CLYS2R | 275 | 17.99 | 6.68 | 5.21 | 14.66 | 17.98 | 6.93 | 5 | 14.8
COCK2- | 275 | 66.35 | 24.55 | 13.51 | 48.22 | 58.52 | 22.82 | 11.3 | 43.57
COYL2- | 275 | 59.82 | 20.79 | 12.76 | 42.16 | 58.31 | 22.26 | 10.75 | 42.23
CURR2- | 275 | 60.27 | 22.44 | 10.61 | 42.34 | 55.38 | 21.72 | 10.03 | 40.74
DALL2- | 275 | 35.71 | 12.76 | 7.45 | 25.49 | 33.67 | 12.94 | 6.55 | 24.85
DENN2- | 275 | 73.57 | 27.32 | 15.02 | 53.65 | 67.57 | 26.32 | 13.96 | 51.17
EERH2- | 275 | 71.91 | 26.46 | 14.56 | 51.97 | 62.08 | 24.34 | 11.06 | 45.47
EKIS2- | 275 | 67.48 | 25.24 | 13.23 | 48.92 | 65.09 | 25.89 | 10.87 | 47.48
ELVA2Q | 275 | 19.23 | 7.66 | 6.91 | 17.75 | 18.4 | 7.17 | 5.61 | 15.75
ELVA2R | 275 | 18.63 | 6.79 | 6.66 | 16.26 | 18.91 | 7.05 | 6.15 | 16.12
GLRO2- | 275 | 40.79 | 16.7 | 6.1 | 29.71 | 33.59 | 13.74 | 5.27 | 24.71
GRMO2- | 275 | 47.35 | 18.08 | 8.76 | 34.32 | 40.87 | 16.16 | 7.85 | 30.71
INVR2- | 275 | 34.79 | 12.97 | 5.98 | 24.32 | 31.26 | 12.39 | 5.01 | 22.53
KAIM2- | 275 | 64.12 | 23.68 | 12.12 | 45.61 | 61.08 | 23.82 | 10.64 | 44.33
KILG2- | 275 | 20.3 | 7.12 | 3.11 | 13.18 | 23.12 | 8.78 | 4.08 | 16.49
KILS2- | 275 | 67.59 | 23.56 | 16.19 | 49.52 | 70.26 | 26.37 | 15.98 | 53.28
KINC2- | 275 | 65.24 | 24.66 | 15.71 | 50.59 | 55.87 | 21.85 | 12.33 | 43.23
LAMB2- | 275 | 58.52 | 21.73 | 10.48 | 41.22 | 50.65 | 20.13 | 8.19 | 36.66
LOAN2- | 275 | 82.68 | 31.03 | 17.69 | 61.57 | 66.61 | 26.43 | 11.54 | 48.92
MAHI2- | 275 | 21.93 | 7.62 | 3.44 | 14.21 | 24.64 | 9.28 | 4.33 | 17.45
MOSM2- | 275 | 48.74 | 19.42 | 7.57 | 35.03 | 40.67 | 16.44 | 6.89 | 30.14
NEAR2Q | 275 | 55.01 | 20.55 | 9.91 | 38.97 | 48.88 | 19.32 | 8.14 | 35.46
NECU2- | 275 | 51.38 | 17.98 | 10.64 | 36.06 | 49.74 | 18.87 | 10.67 | 37.36
NEIL2- | 275 | 71.13 | 25.85 | 15.36 | 51.92 | 68.4 | 26.38 | 14.09 | 51.4
SMEA2- | 275 | 66.09 | 24.31 | 14.01 | 48.39 | 65.35 | 25.16 | 13.5 | 49.07
STHA2A | 275 | 70 | 25.7 | 15.35 | 51.69 | 70.53 | 27.05 | 15.87 | 54.12
STHA2B | 275 | 74.93 | 27.6 | 16.46 | 55.5 | 75.21 | 29.03 | 16.97 | 58.02
WFIE2- | 275 | 54.35 | 21.87 | 8.71 | 39.63 | 46.14 | 18.68 | 7.96 | 34.38
WISH2- | 275 | 60.49 | 21.76 | 15.44 | 46.21 | 64.77 | 24.31 | 17.14 | 51.52
WIYH2- | 275 | 61.92 | 22.61 | 12.27 | 44.24 | 59.99 | 23.21 | 12.42 | 45.25
WLEE2- | 275 | 58.25 | 22.77 | 7.46 | 39.66 | 48.84 | 22 | 9.6 | 40.72
WLEX2- | 275 | 46.09 | 18.42 | 4.98 | 31.03 | 37.27 | 16.66 | 8.34 | 31.9
AREC1- | 132 | 13.67 | 4.5 | 1.66 | 8.02 | 16.67 | 6 | 2.38 | 10.86
BLAH1- | 132 | 41.77 | 13.42 | 7.37 | 26.36 | 43.33 | 15.75 | 7.19 | 29.47
BLCW1- | 132 | 16.35 | 6.28 | 0.79 | 9.67 | 15.1 | 6.21 | 1.03 | 9.82
BONN1- | 132 | 49.72 | 18.28 | 8.83 | 34.69 | 58.67 | 22.69 | 9.92 | 42
BRAP1- | 132 | 32.47 | 11.96 | 4.1 | 21.02 | 35.17 | 13.87 | 3.95 | 23.57
CHAP1- | 132 | 29.6 | 11.45 | 1.31 | 17.5 | 30.51 | 12.65 | 1.67 | 19.56
COAL1- | 132 | 24.64 | 7.83 | 6.19 | 17.26 | 30.85 | 10.86 | 6.94 | 22.29
COAL1A | 132 | 41.83 | 13.78 | 10.78 | 30.27 | 51.3 | 17.93 | 12.15 | 37.5
COYL1- | 132 | 28.76 | 9.52 | 6.83 | 20.28 | 33.19 | 11.91 | 8.29 | 25.12
CRYR1- | 132 | 15.63 | 5.15 | 4.36 | 11.65 | 16.37 | 5.75 | 5.05 | 13.18
CRYR1A | 132 | 15.44 | 6.13 | 4.81 | 13.49 | 17.31 | 6.52 | 5.58 | 14.8
CURR1A | 132 | 35.59 | 12.46 | 9.08 | 26.7 | 43.38 | 15.89 | 10.7 | 33.18
CURR1B | 132 | 35.59 | 12.46 | 9.08 | 26.7 | 43.38 | 15.89 | 10.7 | 33.18
DALM1- | 132 | 25.97 | 9.14 | 6.86 | 19.79 | 31.22 | 11.46 | 8.33 | 24.53
DEVM1- | 132 | 31.56 | 11.74 | 6.96 | 23.56 | 37.69 | 14.49 | 7.98 | 28.47
DEVO1- | 132 | 27.8 | 11.52 | 1.18 | 17.47 | 27.53 | 11.98 | 2.14 | 19.07
DUMF1- | 132 | 17.52 | 6.88 | 0.48 | 10.21 | 20.5 | 8.39 | 0.76 | 12.62
DUNE1- | 132 | 18.72 | 7.65 | 1.06 | 11.88 | 19.72 | 8.23 | 1.56 | 13.19
ECCL1- | 132 | 31.37 | 11.64 | 8.42 | 24.88 | 38.58 | 14.72 | 9.82 | 30.64
GALA1- | 132 | 20.95 | 8.73 | 0.53 | 12.87 | 20.93 | 8.92 | 1.12 | 13.73
GAWH1Q | 132 | 32.17 | 11.1 | 4.57 | 20.26 | 38.17 | 14.54 | 4.36 | 24.92
GLGL1- | 132 | 34.7 | 11.29 | 4.91 | 20.88 | 35.56 | 13.13 | 4.37 | 22.94
GLLE1- | 132 | 26.46 | 9.46 | 2.66 | 16.04 | 25.17 | 10.01 | 1.87 | 16.02
GLNI1- | 132 | 44.01 | 17.2 | 5.62 | 29.94 | 50.63 | 20.52 | 6.02 | 35.04
GRNA1- | 132 | 38.4 | 13.8 | 7.45 | 26.97 | 45.65 | 17.28 | 8.56 | 32.99
HAWI1- | 132 | 10.65 | 4.95 | 0.04 | 7.05 | 11.44 | 5.22 | 0.17 | 7.55
HELE1- | 132 | 17.88 | 8.5 | 0.04 | 12.06 | 18.52 | 8.68 | 0.24 | 12.52
HUER1- | 132 | 35.32 | 12.86 | 8.24 | 26.43 | 41.77 | 15.72 | 10.07 | 32.31
KEOO1- | 132 | 25.82 | 9.24 | 2.56 | 15.62 | 25.22 | 9.88 | 2.22 | 16.18
KILS1- | 132 | 23.23 | 8.95 | 4.49 | 17.15 | 23.27 | 9.11 | 5.36 | 18.25
KILW1Q | 132 | 24.01 | 9.27 | 2.08 | 15.19 | 23.69 | 9.62 | 1.9 | 15.51
KILW1R | 132 | 23.67 | 9.2 | 1.89 | 14.89 | 23.15 | 9.45 | 1.75 | 15.11
MAHI1- | 132 | 14.87 | 4.89 | 2.98 | 9.89 | 17.43 | 6.24 | 3.76 | 12.58
MAHI1B | 132 | 13.6 | 4.42 | 3.14 | 9.4 | 15.49 | 5.48 | 3.93 | 11.68
MARG1- | 132 | 17.37 | 6.6 | 0.92 | 10.26 | 15.89 | 6.52 | 0.95 | 10.17
MAYB1- | 132 | 18.35 | 6.56 | 0.56 | 9.84 | 18.43 | 7.41 | 0.78 | 11.26
MEAD1- | 132 | 26.08 | 9.89 | 2.31 | 16.3 | 25.43 | 10.2 | 2.1 | 16.52
MIDM1- | 132 | 20.8 | 7 | 2.35 | 12.25 | 24.7 | 9.55 | 2.98 | 16.48
MOFF1- | 132 | 50.08 | 16.67 | 11.28 | 34.86 | 51.7 | 18.65 | 12.17 | 38.55
MOSM1A | 132 | 41.37 | 16.28 | 5.06 | 28.09 | 48.31 | 19.57 | 6.03 | 33.71
MOSM1B | 132 | 41.27 | 16.25 | 5 | 27.98 | 48.34 | 19.6 | 5.97 | 33.68
NECU1- | 132 | 44.33 | 14.75 | 9.74 | 30.6 | 50.05 | 18.12 | 10.27 | 35.89
NECU1B | 132 | 39.73 | 13.77 | 9.01 | 28.48 | 44.8 | 16.42 | 10.3 | 33.52
NECU1C | 132 | 40.84 | 13.65 | 9.13 | 28.43 | 45.67 | 16.45 | 9.6 | 32.86
NEIL1- | 132 | 44.9 | 15.76 | 10.9 | 33.19 | 54.61 | 20.26 | 13.17 | 41.82
NETS1- | 132 | 15.96 | 6.4 | 0.32 | 9.37 | 16.64 | 6.96 | 0.69 | 10.53
REDH1- | 132 | 31.54 | 13.37 | 1.19 | 20.09 | 32.49 | 14.05 | 1.53 | 21.39
SMEA1- | 132 | 19.6 | 7.63 | 4.88 | 15.67 | 20.47 | 8.01 | 5.61 | 16.94
STLE1- | 132 | 22.73 | 10.25 | 0.19 | 14.69 | 22.37 | 10.21 | 0.64 | 15.07
TONG1- | 132 | 14.11 | 5.71 | 0.52 | 8.59 | 15.53 | 6.42 | 0.88 | 9.96
TORN1- | 132 | 31.91 | 10.87 | 8.3 | 23.67 | 37.9 | 13.62 | 10.44 | 29.7
WESE1- | 132 | 15.07 | 6.04 | 4.23 | 12.77 | 16.74 | 6.37 | 4.67 | 13.68
WFIE1A | 132 | 30.24 | 12.59 | 4.24 | 22.04 | 31.18 | 13.07 | 5.12 | 23.61
WFIE1B | 132 | 40.22 | 16.15 | 4.51 | 27.35 | 42.93 | 17.91 | 5.24 | 30.56
WISH1- | 132 | 15.3 | 4.57 | 4.45 | 10.91 | 18.53 | 6.24 | 5.47 | 14.3
WIYH1- | 132 | 45.63 | 17.27 | 9.54 | 33.96 | 55.93 | 22.08 | 11.79 | 43.01
AYR-3- | 33 | 41.52 | 14.43 | 10.87 | 31.28 | 5.88 | 4.08 | 0 | 5.77
BAGA3- | 33 | 43.49 | 14.59 | 3.7 | 24.34 | 4.51 | 3.13 | 0 | 4.42
BAIN3- | 33 | 31.51 | 11.22 | 6.27 | 22.13 | 3.02 | 2.09 | 0 | 2.96
BERW3- | 33 | 42.01 | 15.13 | 1.47 | 22.86 | 4.68 | 3.21 | 0 | 4.55
BLAH3A | 33 | 50.11 | 14.54 | 10.99 | 31.55 | 4.54 | 3.15 | 0 | 4.45
BLAH3B | 33 | 49.29 | 14.46 | 10.58 | 31.03 | 4.54 | 3.15 | 0 | 4.46
BLCW3- | 33 | 31.65 | 9.84 | 3.44 | 17.35 | 2.28 | 1.58 | 0 | 2.24
BONN3- | 33 | 43.08 | 13.72 | 8.31 | 27.72 | 4.51 | 3.14 | 0 | 4.44
BPGR3- | 33 | 96.46 | 29.43 | 21.26 | 62.89 | 6.09 | 4.22 | 0 | 5.96
BRAP3- | 33 | 43.66 | 13.6 | 9.79 | 29.03 | 4.48 | 3.1 | 0 | 4.38
BROX3- | 33 | 28.71 | 10.18 | 3.81 | 18.2 | 4.41 | 3.05 | 0 | 4.32
CATY3- | 33 | 30.32 | 10.6 | 4.66 | 19.65 | 2.99 | 2.07 | 0 | 2.93
CHAP3- | 33 | 48.8 | 17.81 | 4.33 | 29.52 | 4.55 | 3.15 | 0 | 4.46
CHAS3A | 33 | 33.75 | 11.78 | 8.48 | 25.14 | 3.01 | 2.08 | 0 | 2.95
CHAS3B | 33 | 33.75 | 11.78 | 8.48 | 25.14 | 3.01 | 2.08 | 0 | 2.95
CLYM3- | 33 | 49.89 | 17.5 | 11.27 | 36.02 | 5.87 | 4.07 | 0 | 5.75
CLYN3A | 33 | 41.76 | 18.08 | 8.09 | 33.66 | 3 | 2.08 | 0 | 2.94
CLYN3B | 33 | 41.86 | 18.12 | 8.1 | 33.73 | 3 | 2.08 | 0 | 2.94
CLYN3C | 33 | 41.73 | 18.07 | 8.11 | 33.67 | 3 | 2.08 | 0 | 2.94
CLYN3D | 33 | 41.76 | 18.09 | 8.03 | 33.61 | 3 | 2.08 | 0 | 2.94
CLYS3A | 33 | 43.41 | 17.07 | 7.79 | 31.93 | 3.02 | 2.09 | 0 | 2.96
CLYS3B | 33 | 47.1 | 17.79 | 7.94 | 33.1 | 3.02 | 2.09 | 0 | 2.96
COAT3- | 33 | 39.69 | 13.59 | 11.83 | 31.05 | 5.82 | 4.03 | 0 | 5.7
COCK3- | 33 | 43.28 | 15.21 | 11.37 | 32.87 | 5.97 | 4.14 | 0 | 5.85
COYL3- | 33 | 51.01 | 16.48 | 6.56 | 29.86 | 3.06 | 2.12 | 0 | 3
CROO3J | 33 | 34.62 | 12.65 | 3.63 | 21.52 | 3.01 | 2.08 | 0 | 2.95
CROO3K | 33 | 32.8 | 11.93 | 3.84 | 20.72 | 2.98 | 2.07 | 0 | 2.92
CUMB3- | 33 | 37.64 | 13.31 | 4.72 | 23.54 | 4.44 | 3.08 | 0 | 4.35
CUPA3- | 33 | 27.65 | 10.23 | 1.34 | 15.81 | 4.34 | 3 | 0 | 4.25
DALM3- | 33 | 35.87 | 12.58 | 7.46 | 25.26 | 4.42 | 3.06 | 0 | 4.33
DESA3- | 33 | 37.1 | 11.15 | 5.33 | 21.09 | 2.27 | 1.58 | 0 | 2.23
DEVM3- | 33 | 35.83 | 13.11 | 4.47 | 23.02 | 3 | 2.08 | 0 | 2.94
DEVO3- | 33 | 41.5 | 15.27 | 3.72 | 25.31 | 4.48 | 3.11 | 0 | 4.39
DEWP3- | 33 | 49.45 | 16.83 | 12.29 | 36.1 | 7.87 | 5.45 | 0 | 7.71
DRCR3- | 33 | 28.32 | 10.4 | 3.11 | 17.82 | 4.44 | 3.07 | 0 | 4.35
DRUM3- | 33 | 39.56 | 13.57 | 10.91 | 30.11 | 5.85 | 4.05 | 0 | 5.73
DUMF3A | 33 | 36.8 | 13.24 | 1.68 | 20.41 | 4.43 | 3.07 | 0 | 4.34
DUMF3B | 33 | 34.17 | 12.67 | 1.78 | 19.7 | 4.45 | 3.08 | 0 | 4.36
DUMF3I | 33 | 18.99 | 6.7 | 1.65 | 11.12 | 1.51 | 1.05 | 0 | 1.48
DUNB3A | 33 | 46.47 | 13.9 | 3.65 | 23.31 | 3.09 | 2.14 | 0 | 3.03
DUNB3B | 33 | 44.53 | 13.44 | 5.77 | 24.77 | 4.54 | 3.15 | 0 | 4.46
DUNE3- | 33 | 46.79 | 16.34 | 3.48 | 26.59 | 4.56 | 3.16 | 0 | 4.46
DUNF3- | 33 | 32.18 | 11.71 | 3.85 | 20.42 | 4.42 | 3.06 | 0 | 4.33
DUNH3- | 33 | 54.98 | 15.51 | 11.33 | 33.26 | 4.55 | 3.16 | 0 | 4.47
ECCL3- | 33 | 36.54 | 14.19 | 5.48 | 25.55 | 5.23 | 3.6 | 0 | 5.09
EERH3- | 33 | 46.94 | 16.04 | 13.78 | 36.46 | 5.87 | 4.06 | 0 | 5.75
EKIL3- | 33 | 53.09 | 18.52 | 14.67 | 40.87 | 5.9 | 4.09 | 0 | 5.78
EKIS3- | 33 | 56.31 | 19.12 | 10.16 | 37.2 | 5.98 | 4.15 | 0 | 5.87
ELDE3- | 33 | 40.06 | 14.37 | 5.11 | 25.43 | 3.02 | 2.09 | 0 | 2.96
ERSK3- | 33 | 29.84 | 10.77 | 5.13 | 20.36 | 2.97 | 2.06 | 0 | 2.92
EWEH3- | 33 | 37.2 | 11.48 | 3.68 | 19.92 | 2.29 | 1.59 | 0 | 2.25
FINN3- | 33 | 31.21 | 11.1 | 6.17 | 21.87 | 4.42 | 3.06 | 0 | 4.32
GALA3- | 33 | 38.77 | 14.45 | 2.64 | 23.07 | 4.91 | 3.4 | 0 | 4.8
GAWH3- | 33 | 35.62 | 10.89 | 7.25 | 22.65 | 2.28 | 1.58 | 0 | 2.24
GIFF3A | 33 | 36.04 | 12.65 | 7.72 | 25.61 | 5.32 | 3.67 | 0 | 5.2
GIFF3B | 33 | 36.16 | 12.7 | 7.77 | 25.73 | 5.32 | 3.68 | 0 | 5.2
GLGL3- | 33 | 50.14 | 14.98 | 8.47 | 29.66 | 4.53 | 3.14 | 0 | 4.45
GLLU3- | 33 | 41.83 | 15.65 | 0.65 | 22.78 | 4.6 | 3.19 | 0 | 4.5
GLNI3- | 33 | 39.73 | 14.6 | 6.47 | 27.12 | 4.52 | 3.14 | 0 | 4.43
GLRO3A | 33 | 34.47 | 12.2 | 8.12 | 25.37 | 5.39 | 3.73 | 0 | 5.27
GLRO3B | 33 | 32.79 | 11.56 | 7.94 | 24.29 | 5.4 | 3.73 | 0 | 5.28
GORG3- | 33 | 29.03 | 10.28 | 5.17 | 19.71 | 2.99 | 2.07 | 0 | 2.93
GOVA3- | 33 | 31.58 | 11.02 | 6.09 | 21.67 | 4.42 | 3.06 | 0 | 4.33
GRMO3A | 33 | 40.42 | 14 | 9.29 | 29.09 | 5.87 | 4.07 | 0 | 5.75
GRMO3C | 33 | 40.5 | 14.02 | 9.43 | 29.26 | 5.87 | 4.07 | 0 | 5.75
HAGR3- | 33 | 30.87 | 10.9 | 5.04 | 20.45 | 2.97 | 2.06 | 0 | 2.91
HAWI3- | 33 | 23.24 | 9.43 | 0.31 | 13.64 | 2.95 | 2.05 | 0 | 2.89
HELE3- | 33 | 26.29 | 10.4 | 0.78 | 15.48 | 2.97 | 2.06 | 0 | 2.91
HUNF3- | 33 | 42.67 | 16.39 | 6.25 | 29.42 | 3.01 | 2.09 | 0 | 2.95
INKE3- | 33 | 30.18 | 11.09 | 2.39 | 18.07 | 4.44 | 3.07 | 0 | 4.34
JOHN3- | 33 | 29.89 | 10.42 | 5.81 | 20.54 | 2.98 | 2.06 | 0 | 2.92
KAIM3- | 33 | 36.35 | 11.14 | 8.48 | 24.23 | 5.7 | 3.94 | 0 | 5.57
KIER3- | 33 | 34.09 | 11.88 | 5.67 | 22.48 | 4.43 | 3.06 | 0 | 4.33
KILB3- | 33 | 33.6 | 12.25 | 5.22 | 22.55 | 2.99 | 2.07 | 0 | 2.93
KILS3- | 33 | 42.28 | 14.74 | 10.48 | 31.33 | 5.92 | 4.11 | 0 | 5.81
KILT3- | 33 | 59.29 | 20.47 | 10.77 | 39.72 | 6.1 | 4.23 | 0 | 5.98
KILW3- | 33 | 32.37 | 11.65 | 5.15 | 21.63 | 4.45 | 3.08 | 0 | 4.36
LEVE3- | 33 | 38.85 | 14.81 | 1.49 | 22.44 | 3.01 | 2.08 | 0 | 2.95
LING3- | 33 | 48.57 | 15.57 | 4.24 | 26.26 | 4.51 | 3.12 | 0 | 4.42
LINM3- | 33 | 63.57 | 21.51 | 6.84 | 37.26 | 4.54 | 3.15 | 0 | 4.46
MAHI3- | 33 | 48.11 | 14.84 | 6.35 | 27.34 | 3.03 | 2.11 | 0 | 2.98
MAYB3- | 33 | 28.82 | 10.02 | 1.29 | 15.47 | 1.56 | 1.09 | 0 | 1.54
NEAR3- | 33 | 51.33 | 17.68 | 10.61 | 35.6 | 5.9 | 4.09 | 0 | 5.78
NETS3- | 33 | 29.29 | 11.01 | 1.44 | 17.01 | 4.53 | 3.13 | 0 | 4.42
PAIS3- | 33 | 34.06 | 12.09 | 6.35 | 23.44 | 2.99 | 2.07 | 0 | 2.93
PART3- | 33 | 35.64 | 12.98 | 4.4 | 22.77 | 2.99 | 2.07 | 0 | 2.93
POOB3- | 33 | 57.16 | 19.89 | 12.64 | 40.77 | 6.01 | 4.17 | 0 | 5.89
PORD3- | 33 | 49.57 | 17.25 | 11.94 | 36.34 | 5.98 | 4.14 | 0 | 5.86
RAVE3- | 33 | 42.1 | 15.82 | 3.4 | 25.78 | 5.93 | 4.11 | 0 | 5.81
REDH3- | 33 | 41.53 | 15.53 | 3.51 | 25.47 | 3.74 | 2.59 | 0 | 3.67
SACO3J | 33 | 41.54 | 14.88 | 4.19 | 25.24 | 3.03 | 2.1 | 0 | 2.97
SACO3K | 33 | 40.65 | 15.09 | 3.89 | 25.23 | 3.01 | 2.09 | 0 | 2.95
SANX3- | 33 | 32.12 | 11.39 | 4.93 | 21.04 | 3 | 2.08 | 0 | 2.94
SHRU3- | 33 | 47.96 | 16.48 | 11.92 | 35.22 | 5.9 | 4.09 | 0 | 5.78
SIGH3A | 33 | 43.37 | 15.01 | 10.68 | 31.9 | 4.48 | 3.1 | 0 | 4.39
SIGH3B | 33 | 43.23 | 14.97 | 10.42 | 31.59 | 4.47 | 3.1 | 0 | 4.39
SPAV3- | 33 | 27.72 | 10.04 | 3.68 | 17.88 | 4.36 | 3.02 | 0 | 4.27
STHA3- | 33 | 53.93 | 19.29 | 11.73 | 39.01 | 5.98 | 4.15 | 0 | 5.86
STIR3- | 33 | 39.59 | 13.7 | 6.63 | 26 | 4.42 | 3.06 | 0 | 4.33
STLE3S | 33 | 34.74 | 13.02 | 2.28 | 20.69 | 2.99 | 2.07 | 0 | 2.93
TELR3- | 33 | 28.13 | 9.97 | 4.67 | 18.77 | 2.99 | 2.07 | 0 | 2.93
TONG3- | 33 | 23.76 | 8.81 | 2.03 | 14.48 | 2.97 | 2.06 | 0 | 2.92
WFIE3- | 33 | 41.63 | 14.96 | 8.16 | 29.31 | 3.04 | 2.11 | 0 | 2.98
WGEO3- | 33 | 49.4 | 17.25 | 9.89 | 34.28 | 5.95 | 4.13 | 0 | 5.83
WHHO3- | 33 | 42.87 | 15.01 | 9.82 | 31.04 | 5.96 | 4.13 | 0 | 5.84
WHTL3- | 33 | 26.51 | 10.48 | 0.88 | 15.7 | 2.25 | 1.56 | 0 | 2.2
WISH3- | 33 | 43.86 | 15.11 | 10.31 | 31.68 | 5.92 | 4.1 | 0 | 5.8
WLEE3A | 33 | 49.26 | 20.58 | 10.3 | 39.4 | 2.99 | 2.07 | 0 | 2.93
WLEE3B | 33 | 49.45 | 20.65 | 10.28 | 39.49 | 2.99 | 2.07 | 0 | 2.93
WLEE3C | 33 | 48.87 | 20.38 | 10.24 | 39.06 | 2.99 | 2.07 | 0 | 2.93
WLEX3A | 33 | 56.85 | 19.89 | 9.15 | 37.27 | 3.03 | 2.1 | 0 | 2.97
WLEX3B | 33 | 57.1 | 19.98 | 9.14 | 37.4 | 3.03 | 2.1 | 0 | 2.97
WLEX3C | 33 | 54.6 | 19.1 | 9.12 | 36.13 | 3.03 | 2.1 | 0 | 2.97
BAGA0J | 25 | 16.38 | 6 | 3.67 | 12.15 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.37 | 5.99 | 3.66 | 12.14 | 0 | 0 | 0 | 0
BONN0J | 25 | 18.16 | 6.53 | 5.38 | 14.62 | 0 | 0 | 0 | 0
BONN0K | 25 | 18.16 | 6.53 | 5.38 | 14.62 | 0 | 0 | 0 | 0
BONN0L | 25 | 18.16 | 6.53 | 5.38 | 14.62 | 0 | 0 | 0 | 0
CATY0J | 25 | 9.98 | 3.68 | 1.7 | 6.9 | 0 | 0 | 0 | 0
CATY0K | 25 | 9.99 | 3.68 | 1.73 | 6.93 | 0 | 0 | 0 | 0
CURR0J | 25 | 20.43 | 7.35 | 6.2 | 16.6 | 0 | 0 | 0 | 0
CURR0K | 25 | 20.43 | 7.35 | 6.2 | 16.6 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.42 | 3.03 | 2.58 | 6.85 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.42 | 3.03 | 2.58 | 6.85 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.8 | 6.02 | 1.35 | 9.87 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.45 | 7.23 | 2.77 | 13 | 0 | 0 | 0 | 0
ELVA0J | 25 | 18.96 | 6.69 | 8.04 | 17.5 | 0 | 0 | 0 | 0
ELVA0K | 25 | 18.96 | 6.69 | 8.04 | 17.5 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.12 | 3.97 | 3.41 | 9.02 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.12 | 3.97 | 3.41 | 9.03 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.95 | 3.67 | 1.92 | 7.12 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.95 | 3.67 | 1.94 | 7.13 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.26 | 6.58 | 5.53 | 14.83 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.26 | 6.58 | 5.53 | 14.83 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.65 | 3.84 | 2.93 | 8.36 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.61 | 3.83 | 2.87 | 8.28 | 0 | 0 | 0 | 0
SANX0J | 25 | 16.89 | 6.04 | 4.62 | 13.16 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.87 | 6.03 | 4.57 | 13.1 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.44 | 3.8 | 2.31 | 7.69 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.44 | 3.8 | 2.31 | 7.69 | 0 | 0 | 0 | 0
WISH0J | 25 | 20.4 | 7.31 | 6.32 | 16.66 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.4 | 7.31 | 6.32 | 16.66 | 0 | 0 | 0 | 0
CAFA5- | 11 | 31.17 | 11.15 | 5.97 | 21.74 | 2.24 | 1.55 | 0 | 2.2
CURR5- | 11 | 34.48 | 12.43 | 5.71 | 23.3 | 4.44 | 3.08 | 0 | 4.35
EAST5- | 11 | 24.49 | 9.27 | 2.7 | 15.81 | 1.14 | 0.79 | 0 | 1.12
GLLE5- | 11 | 33.88 | 12.36 | 7.67 | 25.16 | 2.32 | 1.61 | 0 | 2.27
KEOO5- | 11 | 33.35 | 12.16 | 5.65 | 22.85 | 2.27 | 1.58 | 0 | 2.23
KILB5- | 11 | 28.84 | 10.55 | 4.11 | 19.03 | 2.99 | 2.08 | 0 | 2.94
TONG5- | 11 | 74.5 | 28.24 | 6.58 | 46.52 | 4.61 | 3.19 | 0 | 4.52

## D2.7
ETYS 19 Yr 10 - SPT Fault Levels (kA), Winter 2028/29
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
BONN4- | 400 | 56.53 | 21.13 | 11.75 | 41.63 | 50.17 | 19.57 | 10.21 | 37.88 | Back To Menu
BRNX4- | 400 | 87.5 | 31.62 | 19.65 | 64.37 | 95.03 | 35.47 | 23.85 | 74.01
COAL4- | 400 | 65.02 | 24.15 | 11.76 | 45.91 | 54.5 | 21.58 | 9.2 | 39.71
CRYR4- | 400 | 68.24 | 24.85 | 14.36 | 49.5 | 66.03 | 25.04 | 14.65 | 50.05
DENN4- | 400 | 56.73 | 21.13 | 12.4 | 42.28 | 50.52 | 19.63 | 10.78 | 38.53
DEVM4- | 400 | 37.07 | 13.8 | 7.44 | 26.96 | 30.96 | 12.18 | 5.76 | 22.98
ECCL4A | 400 | 55.92 | 20.53 | 12.43 | 41.47 | 43.71 | 17.02 | 8.1 | 32.17
ECCL4B | 400 | 56 | 20.56 | 12.44 | 41.51 | 43.75 | 17.03 | 8.13 | 32.21
ELVA4- | 400 | 69.84 | 26.01 | 12.09 | 48.88 | 55.31 | 21.88 | 9.98 | 40.93
ELVN4- | 400 | 76.69 | 28.51 | 13.24 | 53.55 | 59.54 | 23.55 | 10.74 | 44.05
FALL4- | 400 | 58.03 | 21.23 | 11.98 | 42 | 51.88 | 19.93 | 10.55 | 38.74
GRNA4- | 400 | 51.34 | 19.35 | 8.09 | 35.46 | 40.73 | 16.1 | 7.29 | 30.07
HUCS4- | 400 | 55.85 | 20.35 | 11.27 | 40.05 | 65.01 | 24.61 | 13.64 | 48.45
HUER4- | 400 | 56.23 | 20.48 | 11.32 | 40.29 | 65.28 | 24.72 | 13.6 | 48.57
HUNE4- | 400 | 56.22 | 20.48 | 11.32 | 40.28 | 65.32 | 24.74 | 13.62 | 48.6
KILS4- | 400 | 55.36 | 20.38 | 10.87 | 39.69 | 49.01 | 19.09 | 9.82 | 36.82
KILS4T | 400 | 52.36 | 19.44 | 10.31 | 37.8 | 46.03 | 18.01 | 9.06 | 34.53
MOFF4- | 400 | 49.56 | 18.67 | 8.26 | 34.66 | 40.16 | 15.92 | 6.91 | 29.43
STHA4A | 400 | 81.1 | 29.78 | 15.31 | 57.43 | 71.12 | 27.62 | 14.36 | 53.42
STHA4B | 400 | 82.19 | 30.1 | 15.95 | 58.52 | 73.52 | 28.5 | 15.12 | 55.43
TORN4- | 400 | 86.66 | 31.31 | 19.58 | 63.85 | 94.15 | 35.15 | 23.56 | 73.27
WISH4- | 400 | 94.28 | 34.4 | 17.61 | 66.27 | 85.96 | 33.25 | 17.44 | 64.45
AUCH2- | 275 | 16.27 | 5.96 | 2.11 | 10.54 | 16.11 | 6.39 | 1.92 | 10.96
BUSB2- | 275 | 57.89 | 21.91 | 10.28 | 41.26 | 51.66 | 20.65 | 7.45 | 36.64
CLYM2- | 275 | 95.93 | 35.47 | 19.39 | 69.56 | 83.4 | 32.73 | 15.37 | 61.65
CLYN2Q | 275 | 18.66 | 7.49 | 6.11 | 16.71 | 18.67 | 7.13 | 6.25 | 16.32
CLYS2R | 275 | 19.32 | 7.11 | 5.42 | 15.48 | 19.09 | 7.36 | 5.18 | 15.59
COCK2- | 275 | 72.5 | 27.2 | 14.24 | 52.7 | 61.86 | 24.29 | 11.58 | 45.93
COYL2- | 275 | 62.17 | 21.9 | 13.03 | 43.99 | 59.72 | 22.94 | 10.88 | 43.32
CURR2- | 275 | 68.75 | 26.01 | 11.09 | 47.88 | 60.66 | 24.02 | 10.39 | 44.36
DALL2- | 275 | 37.1 | 13.32 | 7.69 | 26.53 | 34.78 | 13.4 | 6.75 | 25.7
DENN2- | 275 | 109 | 40.54 | 21.9 | 79.23 | 95.76 | 37.6 | 18.48 | 71.66
EERH2- | 275 | 87.96 | 32.82 | 17 | 63.41 | 74.83 | 29.6 | 12.48 | 54.35
EKIS2- | 275 | 72.53 | 27.45 | 13.93 | 52.74 | 68.89 | 27.57 | 11.22 | 50.22
ELVA2Q | 275 | 19.37 | 7.67 | 7.1 | 17.95 | 18.73 | 7.26 | 5.91 | 16.17
ELVA2R | 275 | 20.07 | 7.24 | 7.09 | 17.33 | 20.18 | 7.51 | 6.57 | 17.18
GLRO2- | 275 | 46.42 | 19.04 | 6.81 | 33.74 | 37.07 | 15.21 | 5.62 | 27.13
GRMO2- | 275 | 60.85 | 23.62 | 9.33 | 42.73 | 49.79 | 20.03 | 8.16 | 36.49
INVR2- | 275 | 36.22 | 13.59 | 6.15 | 25.37 | 32.27 | 12.82 | 5.14 | 23.27
KAIM2- | 275 | 71.68 | 26.9 | 12.69 | 50.74 | 65.77 | 25.88 | 10.91 | 47.51
KILG2- | 275 | 20.78 | 7.35 | 3.13 | 13.52 | 23.45 | 8.95 | 4.09 | 16.74
KILS2- | 275 | 70.37 | 24.83 | 16.76 | 51.87 | 72.27 | 27.28 | 16.36 | 54.93
KINC2- | 275 | 107.83 | 41.12 | 20.96 | 79.12 | 95.9 | 37.74 | 19.86 | 73.24
LAMB2- | 275 | 68.08 | 25.56 | 11.65 | 47.8 | 56.52 | 22.65 | 8.77 | 40.8
LOAN2- | 275 | 113.43 | 43.05 | 22.61 | 83.48 | 94.18 | 37.53 | 15.43 | 68.51
MAHI2- | 275 | 22.58 | 7.89 | 3.52 | 14.68 | 25.11 | 9.48 | 4.42 | 17.83
MOSM2- | 275 | 56.97 | 22.89 | 8.42 | 40.79 | 45.85 | 18.65 | 7.5 | 33.87
NEAR2Q | 275 | 68.58 | 25.76 | 12.39 | 48.82 | 61.72 | 24.41 | 10.42 | 44.94
NECU2- | 275 | 53.49 | 18.98 | 10.82 | 37.67 | 51.04 | 19.48 | 10.85 | 38.41
NEIL2- | 275 | 75.58 | 27.8 | 16.03 | 55.34 | 71.58 | 27.74 | 14.58 | 53.82
SMEA2- | 275 | 72.22 | 26.95 | 14.74 | 52.86 | 69.58 | 26.98 | 13.96 | 52.11
STHA2A | 275 | 76.67 | 28.5 | 16.54 | 56.84 | 76.05 | 29.31 | 16.91 | 58.37
STHA2B | 275 | 81.92 | 30.56 | 17.71 | 60.93 | 80.96 | 31.43 | 18.03 | 62.47
WFIE2- | 275 | 63.93 | 25.91 | 9.81 | 46.45 | 52.33 | 21.3 | 8.69 | 38.81
WISH2- | 275 | 67.89 | 24.7 | 17.44 | 52.37 | 70.76 | 26.68 | 18.81 | 56.54
WIYH2- | 275 | 68.68 | 25.35 | 13.16 | 49.01 | 64.88 | 25.25 | 13.22 | 48.93
WLEE2- | 275 | 62.07 | 24.56 | 7.66 | 42.39 | 51.39 | 23.25 | 10.1 | 42.98
WLEX2- | 275 | 48.52 | 19.6 | 5.08 | 32.8 | 38.86 | 17.4 | 8.57 | 33.18
AREC1- | 132 | 13.75 | 4.53 | 1.67 | 8.08 | 16.76 | 6.04 | 2.39 | 10.93
BLAH1- | 132 | 53.58 | 18.13 | 7.17 | 32.81 | 50.52 | 19.03 | 7.15 | 34.07
BLCW1- | 132 | 16.47 | 6.36 | 0.77 | 9.76 | 15.12 | 6.25 | 1.01 | 9.85
BONN1- | 132 | 54.93 | 20.32 | 10.58 | 39.31 | 64.6 | 24.9 | 12.53 | 47.74
BRAP1- | 132 | 32.97 | 12.22 | 4.11 | 21.39 | 35.62 | 14.1 | 3.95 | 23.89
CHAP1- | 132 | 31.57 | 12.17 | 1.21 | 18.42 | 31.86 | 13.28 | 1.63 | 20.41
COAL1- | 132 | 24.2 | 7.66 | 5.93 | 16.77 | 30.18 | 10.63 | 6.6 | 21.63
COAL1A | 132 | 41.14 | 13.56 | 10.67 | 29.85 | 50.3 | 17.61 | 12.09 | 36.99
COYL1- | 132 | 29.03 | 9.66 | 6.9 | 20.56 | 33.37 | 12 | 8.36 | 25.33
CRYR1- | 132 | 15.78 | 5.21 | 4.45 | 11.81 | 16.69 | 5.86 | 5.15 | 13.44
CRYR1A | 132 | 15.5 | 6.17 | 4.84 | 13.57 | 17.26 | 6.51 | 5.56 | 14.76
CURR1A | 132 | 37.82 | 13.32 | 9.64 | 28.47 | 46.08 | 16.92 | 11.32 | 35.25
CURR1B | 132 | 37.82 | 13.32 | 9.64 | 28.47 | 46.08 | 16.92 | 11.32 | 35.25
DALM1- | 132 | 27.33 | 9.66 | 7.23 | 20.9 | 32.65 | 11.99 | 8.76 | 25.72
DEVM1- | 132 | 32.49 | 12.13 | 7.17 | 24.32 | 38.76 | 14.91 | 8.21 | 29.3
DEVO1- | 132 | 29.09 | 12.16 | 1.21 | 18.41 | 28.52 | 12.45 | 2.22 | 19.83
DUMF1- | 132 | 18.05 | 7.1 | 0.45 | 10.49 | 20.98 | 8.62 | 0.73 | 12.92
DUNE1- | 132 | 18.85 | 7.73 | 1.04 | 11.98 | 19.8 | 8.28 | 1.54 | 13.25
ECCL1- | 132 | 32.37 | 12.06 | 8.67 | 25.72 | 39.78 | 15.2 | 10.1 | 31.6
ELVN1- | 132 | 50.35 | 18.06 | 11.37 | 36.91 | 55.07 | 20.5 | 12.52 | 41.51
GALA1- | 132 | 21.27 | 8.91 | 0.52 | 13.12 | 21.22 | 9.06 | 1.12 | 13.93
GAWH1Q | 132 | 31.8 | 10.97 | 4.59 | 20.1 | 37.64 | 14.34 | 4.36 | 24.63
GLGL1- | 132 | 55.75 | 18.36 | 6.32 | 32.29 | 51.45 | 19.36 | 5.11 | 32.5
GLLE1- | 132 | 26.88 | 9.66 | 2.64 | 16.3 | 25.46 | 10.15 | 1.84 | 16.2
GLNI1- | 132 | 48.18 | 18.98 | 6.22 | 33.06 | 54.64 | 22.22 | 6.54 | 37.97
GRNA1- | 132 | 42.72 | 15.01 | 7.25 | 28.49 | 48.69 | 18.47 | 8.19 | 34.3
HAWI1- | 132 | 14.18 | 5.91 | 0.11 | 8.47 | 14.75 | 6.42 | 0.33 | 9.4
HELE1- | 132 | 18.14 | 8.69 | 0.03 | 12.32 | 18.72 | 8.8 | 0.23 | 12.68
HUER1- | 132 | 34.97 | 12.79 | 8 | 26.09 | 41.21 | 15.56 | 9.74 | 31.74
KEOO1- | 132 | 26.15 | 9.4 | 2.53 | 15.83 | 25.51 | 10.01 | 2.21 | 16.37
KILS1- | 132 | 23.25 | 8.98 | 4.56 | 17.26 | 23.31 | 9.12 | 5.44 | 18.35
KILW1Q | 132 | 23.9 | 9.25 | 2.06 | 15.15 | 23.57 | 9.58 | 1.9 | 15.45
KILW1R | 132 | 23.56 | 9.18 | 1.88 | 14.86 | 23.03 | 9.41 | 1.76 | 15.06
MAHI1- | 132 | 15 | 4.93 | 3.05 | 10.03 | 17.59 | 6.3 | 3.85 | 12.76
MAHI1B | 132 | 15.81 | 5.12 | 3.19 | 10.44 | 17.61 | 6.31 | 4.05 | 12.97
MARG1- | 132 | 17.52 | 6.69 | 0.9 | 10.36 | 15.94 | 6.56 | 0.94 | 10.22
MAYB1- | 132 | 18.49 | 6.63 | 0.56 | 9.94 | 18.49 | 7.45 | 0.77 | 11.3
MEAD1- | 132 | 26 | 9.89 | 2.29 | 16.28 | 25.29 | 10.16 | 2.08 | 16.44
MIDM1- | 132 | 20.58 | 6.89 | 2.37 | 12.11 | 24.46 | 9.4 | 3.01 | 16.3
MOFF1- | 132 | 49.88 | 16.62 | 11.36 | 34.87 | 51.58 | 18.61 | 12.3 | 38.62
MOSM1A | 132 | 45.07 | 17.88 | 5.58 | 30.86 | 52.05 | 21.15 | 6.62 | 36.53
MOSM1B | 132 | 44.95 | 17.84 | 5.51 | 30.74 | 52.08 | 21.18 | 6.54 | 36.49
NECU1- | 132 | 51.47 | 17.99 | 9.81 | 35.25 | 55.99 | 20.83 | 10.58 | 40.04
NECU1B | 132 | 40.49 | 14.13 | 9.12 | 29.1 | 45.5 | 16.73 | 10.42 | 34.08
NECU1C | 132 | 41.71 | 13.99 | 9.29 | 29.08 | 46.6 | 16.81 | 9.77 | 33.55
NEIL1- | 132 | 45.82 | 16.18 | 11.06 | 33.95 | 55.58 | 20.68 | 13.35 | 42.6
NETS1- | 132 | 16.2 | 6.52 | 0.32 | 9.54 | 16.85 | 7.06 | 0.7 | 10.68
REDH1- | 132 | 33.46 | 14.34 | 1.19 | 21.46 | 33.97 | 14.76 | 1.55 | 22.42
SMEA1- | 132 | 19.85 | 7.74 | 4.97 | 15.92 | 20.84 | 8.15 | 5.77 | 17.3
STLE1- | 132 | 23.28 | 10.57 | 0.19 | 15.13 | 22.88 | 10.46 | 0.64 | 15.44
TONG1- | 132 | 14.24 | 5.79 | 0.5 | 8.68 | 15.59 | 6.47 | 0.86 | 10.01
TORN1- | 132 | 32.37 | 11.07 | 8.46 | 24.11 | 38.46 | 13.84 | 10.64 | 30.21
WESE1- | 132 | 15.13 | 6.08 | 4.25 | 12.85 | 16.7 | 6.36 | 4.69 | 13.68
WFIE1A | 132 | 32.18 | 13.49 | 4.74 | 23.82 | 33.05 | 13.86 | 5.7 | 25.31
WFIE1B | 132 | 43.75 | 17.72 | 4.99 | 30.05 | 46.06 | 19.26 | 5.84 | 33.08
WISH1- | 132 | 15.46 | 4.63 | 4.56 | 11.11 | 18.79 | 6.33 | 5.62 | 14.57
WIYH1- | 132 | 48.09 | 18.29 | 10.17 | 36.03 | 58.85 | 23.26 | 12.55 | 45.45
AYR-3- | 33 | 41.8 | 14.53 | 10.93 | 31.48 | 5.85 | 4.06 | 0 | 5.74
BAGA3- | 33 | 44.75 | 15.06 | 3.81 | 25.12 | 4.48 | 3.11 | 0 | 4.4
BAIN3- | 33 | 32.54 | 11.63 | 6.43 | 22.88 | 3.01 | 2.09 | 0 | 2.95
BERW3- | 33 | 43.39 | 15.69 | 1.41 | 23.6 | 4.72 | 3.24 | 0 | 4.59
BLAH3A | 33 | 51.3 | 15.11 | 11.17 | 32.54 | 4.52 | 3.14 | 0 | 4.44
BLAH3B | 33 | 50.6 | 15.04 | 10.8 | 32.07 | 4.56 | 3.17 | 0 | 4.48
BLCW3- | 33 | 31.52 | 9.77 | 3.51 | 17.33 | 2.27 | 1.57 | 0 | 2.22
BONN3- | 33 | 44.12 | 14.14 | 8.65 | 28.64 | 4.51 | 3.13 | 0 | 4.43
BPGR3- | 33 | 96.5 | 29.48 | 21.95 | 63.64 | 6.01 | 4.17 | 0 | 5.89
BRAP3- | 33 | 43.64 | 13.62 | 9.77 | 29.04 | 4.45 | 3.08 | 0 | 4.35
BROX3- | 33 | 29.15 | 10.36 | 3.85 | 18.5 | 4.39 | 3.04 | 0 | 4.3
CATY3- | 33 | 30.82 | 10.81 | 4.72 | 20.01 | 2.98 | 2.07 | 0 | 2.92
CHAP3- | 33 | 49.79 | 18.14 | 4.18 | 29.83 | 4.58 | 3.17 | 0 | 4.49
CHAS3A | 33 | 34.03 | 11.89 | 8.65 | 25.47 | 3.02 | 2.09 | 0 | 2.96
CHAS3B | 33 | 34.03 | 11.89 | 8.65 | 25.47 | 3.02 | 2.09 | 0 | 2.96
CLYM3- | 33 | 50.8 | 17.84 | 11.52 | 36.74 | 5.89 | 4.08 | 0 | 5.77
CLYN3A | 33 | 41.83 | 18.05 | 8.46 | 33.98 | 3.02 | 2.1 | 0 | 2.96
CLYN3B | 33 | 41.93 | 18.09 | 8.48 | 34.05 | 3.02 | 2.1 | 0 | 2.96
CLYN3C | 33 | 41.8 | 18.03 | 8.48 | 33.99 | 3.02 | 2.1 | 0 | 2.96
CLYN3D | 33 | 41.83 | 18.05 | 8.4 | 33.93 | 3.02 | 2.1 | 0 | 2.96
CLYS3A | 33 | 43.92 | 17.25 | 7.72 | 32.11 | 3.04 | 2.11 | 0 | 2.98
CLYS3B | 33 | 47.63 | 17.98 | 7.87 | 33.3 | 3.04 | 2.11 | 0 | 2.98
COAT3- | 33 | 40.87 | 14.03 | 12.23 | 32.08 | 5.89 | 4.08 | 0 | 5.77
COCK3- | 33 | 43.14 | 15.16 | 11.33 | 32.77 | 5.88 | 4.08 | 0 | 5.77
COYL3- | 33 | 51.25 | 16.61 | 6.51 | 30 | 3.03 | 2.1 | 0 | 2.97
CROO3J | 33 | 34.75 | 12.72 | 3.64 | 21.63 | 3 | 2.08 | 0 | 2.94
CROO3K | 33 | 33.68 | 12.28 | 3.82 | 21.19 | 3.02 | 2.09 | 0 | 2.96
CUMB3- | 33 | 38.25 | 13.57 | 4.82 | 24.01 | 4.43 | 3.07 | 0 | 4.34
CUPA3- | 33 | 28.72 | 10.66 | 1.31 | 16.38 | 4.35 | 3.01 | 0 | 4.25
DALM3- | 33 | 39.35 | 13.9 | 7.51 | 27.16 | 4.5 | 3.12 | 0 | 4.41
DESA3- | 33 | 36.77 | 11.02 | 5.36 | 20.94 | 2.25 | 1.56 | 0 | 2.21
DEVM3- | 33 | 36.33 | 13.31 | 4.52 | 23.34 | 3.02 | 2.09 | 0 | 2.96
DEVO3- | 33 | 42.65 | 15.72 | 3.73 | 25.97 | 4.51 | 3.13 | 0 | 4.43
DEWP3- | 33 | 49.3 | 16.8 | 12.53 | 36.29 | 7.81 | 5.41 | 0 | 7.65
DRCR3- | 33 | 28.57 | 10.52 | 3.17 | 18.05 | 4.37 | 3.03 | 0 | 4.28
DRUM3- | 33 | 40.4 | 13.87 | 11.27 | 30.88 | 5.86 | 4.06 | 0 | 5.74
DUMF3A | 33 | 37.17 | 13.39 | 1.61 | 20.54 | 4.43 | 3.07 | 0 | 4.34
DUMF3B | 33 | 34.5 | 12.8 | 1.73 | 19.83 | 4.42 | 3.06 | 0 | 4.33
DUMF3I | 33 | 18.96 | 6.69 | 1.63 | 11.09 | 1.49 | 1.03 | 0 | 1.46
DUNB3A | 33 | 46.78 | 14.02 | 3.71 | 23.54 | 3.07 | 2.13 | 0 | 3.01
DUNB3B | 33 | 44.95 | 13.61 | 5.79 | 25.04 | 4.56 | 3.16 | 0 | 4.47
DUNE3- | 33 | 46.74 | 16.33 | 3.46 | 26.56 | 4.53 | 3.14 | 0 | 4.43
DUNF3- | 33 | 33.15 | 12.09 | 3.92 | 21.02 | 4.43 | 3.07 | 0 | 4.34
DUNH3- | 33 | 55.67 | 15.86 | 11.47 | 33.9 | 4.53 | 3.15 | 0 | 4.45
ECCL3- | 33 | 36.99 | 14.39 | 5.47 | 25.82 | 5.21 | 3.58 | 0 | 5.06
EERH3- | 33 | 47.67 | 16.31 | 14.26 | 37.32 | 5.91 | 4.1 | 0 | 5.79
EKIL3- | 33 | 54.55 | 19.06 | 15.13 | 42.09 | 6.01 | 4.16 | 0 | 5.89
EKIS3- | 33 | 56.94 | 19.37 | 10.2 | 37.59 | 5.94 | 4.12 | 0 | 5.83
ELDE3- | 33 | 40.44 | 14.54 | 5.12 | 25.68 | 3.01 | 2.09 | 0 | 2.95
ERSK3- | 33 | 30.31 | 10.95 | 5.09 | 20.58 | 3 | 2.08 | 0 | 2.94
EWEH3- | 33 | 37.28 | 11.5 | 3.68 | 19.94 | 2.28 | 1.58 | 0 | 2.23
FINN3- | 33 | 31.42 | 11.18 | 6.24 | 22.05 | 4.38 | 3.04 | 0 | 4.29
GALA3- | 33 | 39.56 | 14.78 | 2.54 | 23.44 | 4.93 | 3.41 | 0 | 4.82
GAWH3- | 33 | 35.2 | 10.74 | 7.22 | 22.41 | 2.26 | 1.57 | 0 | 2.21
GIFF3A | 33 | 36.72 | 12.92 | 7.85 | 26.12 | 5.37 | 3.72 | 0 | 5.25
GIFF3B | 33 | 36.85 | 12.96 | 7.91 | 26.24 | 5.37 | 3.72 | 0 | 5.26
GLGL3- | 33 | 52.67 | 15.95 | 9.64 | 32.2 | 4.53 | 3.14 | 0 | 4.45
GLLU3- | 33 | 43.15 | 16.18 | 0.64 | 23.52 | 4.65 | 3.22 | 0 | 4.55
GLNI3- | 33 | 40.87 | 15.04 | 6.67 | 27.94 | 4.5 | 3.12 | 0 | 4.41
GLRO3A | 33 | 35.44 | 12.55 | 8.35 | 26.11 | 5.4 | 3.73 | 0 | 5.28
GLRO3B | 33 | 33.53 | 11.83 | 8.13 | 24.87 | 5.38 | 3.72 | 0 | 5.26
GORG3- | 33 | 29.8 | 10.59 | 5.22 | 20.19 | 3.04 | 2.11 | 0 | 2.98
GOVA3- | 33 | 31.68 | 11.07 | 6.09 | 21.75 | 4.4 | 3.05 | 0 | 4.31
GRMO3A | 33 | 41.51 | 14.4 | 9.64 | 30.01 | 5.89 | 4.08 | 0 | 5.77
GRMO3C | 33 | 41.6 | 14.43 | 9.79 | 30.2 | 5.89 | 4.08 | 0 | 5.77
HAGR3- | 33 | 31.4 | 11.12 | 5.01 | 20.73 | 3.01 | 2.08 | 0 | 2.95
HAWI3- | 33 | 26.27 | 10.11 | 0.66 | 14.95 | 2.99 | 2.07 | 0 | 2.93
HELE3- | 33 | 26.43 | 10.46 | 0.77 | 15.56 | 2.95 | 2.04 | 0 | 2.89
HUNF3- | 33 | 42.36 | 16.29 | 6.15 | 29.19 | 2.97 | 2.07 | 0 | 2.92
INKE3- | 33 | 30.85 | 11.39 | 2.38 | 18.49 | 4.42 | 3.06 | 0 | 4.33
JOHN3- | 33 | 30.05 | 10.48 | 5.83 | 20.64 | 2.96 | 2.05 | 0 | 2.9
KAIM3- | 33 | 36.7 | 11.28 | 8.56 | 24.51 | 5.64 | 3.9 | 0 | 5.51
KIER3- | 33 | 34.49 | 12.04 | 5.73 | 22.76 | 4.39 | 3.04 | 0 | 4.3
KILB3- | 33 | 34.32 | 12.53 | 5.31 | 23.04 | 3.02 | 2.09 | 0 | 2.96
KILS3- | 33 | 42.63 | 14.89 | 10.52 | 31.58 | 5.91 | 4.1 | 0 | 5.79
KILT3- | 33 | 59.33 | 20.53 | 10.71 | 39.75 | 6 | 4.16 | 0 | 5.88
KILW3- | 33 | 32.81 | 11.83 | 5.1 | 21.83 | 4.44 | 3.08 | 0 | 4.35
LEVE3- | 33 | 39.97 | 15.29 | 1.5 | 23.12 | 3.01 | 2.08 | 0 | 2.95
LING3- | 33 | 49.59 | 15.99 | 4.22 | 26.83 | 4.53 | 3.14 | 0 | 4.44
LINM3- | 33 | 67.77 | 23.23 | 6.65 | 39.5 | 4.57 | 3.17 | 0 | 4.49
MAHI3- | 33 | 48.29 | 14.95 | 6.4 | 27.55 | 3.02 | 2.1 | 0 | 2.97
MAYB3- | 33 | 28.91 | 10.07 | 1.29 | 15.53 | 1.55 | 1.07 | 0 | 1.52
NEAR3- | 33 | 52.94 | 18.31 | 10.96 | 36.84 | 5.95 | 4.12 | 0 | 5.83
NETS3- | 33 | 29.47 | 11.09 | 1.46 | 17.14 | 4.52 | 3.13 | 0 | 4.42
PAIS3- | 33 | 34.15 | 12.14 | 6.35 | 23.51 | 2.99 | 2.07 | 0 | 2.93
PART3- | 33 | 35.94 | 13.1 | 4.44 | 22.97 | 2.97 | 2.06 | 0 | 2.91
POOB3- | 33 | 56.65 | 19.74 | 12.61 | 40.54 | 5.94 | 4.11 | 0 | 5.82
PORD3- | 33 | 50.88 | 17.76 | 12.32 | 37.43 | 5.95 | 4.12 | 0 | 5.83
RAVE3- | 33 | 42.25 | 15.9 | 3.4 | 25.89 | 5.89 | 4.08 | 0 | 5.77
REDH3- | 33 | 42.37 | 15.87 | 3.56 | 26.01 | 3.75 | 2.6 | 0 | 3.67
SACO3J | 33 | 41.9 | 15.02 | 4.16 | 25.4 | 3 | 2.08 | 0 | 2.94
SACO3K | 33 | 40.84 | 15.18 | 3.85 | 25.31 | 3 | 2.08 | 0 | 2.95
SANX3- | 33 | 32.74 | 11.63 | 5 | 21.45 | 3 | 2.08 | 0 | 2.94
SHRU3- | 33 | 48.38 | 16.64 | 12.09 | 35.62 | 5.96 | 4.13 | 0 | 5.84
SIGH3A | 33 | 44.04 | 15.25 | 11 | 32.57 | 4.5 | 3.12 | 0 | 4.41
SIGH3B | 33 | 43.91 | 15.22 | 10.8 | 32.32 | 4.5 | 3.12 | 0 | 4.41
SPAV3- | 33 | 28.07 | 10.18 | 3.66 | 18.06 | 4.4 | 3.05 | 0 | 4.31
STHA3- | 33 | 54.86 | 19.63 | 11.86 | 39.62 | 5.98 | 4.15 | 0 | 5.87
STIR3- | 33 | 40.81 | 14.19 | 6.81 | 26.87 | 4.47 | 3.09 | 0 | 4.38
STLE3S | 33 | 35.72 | 13.44 | 2.21 | 21.21 | 3.01 | 2.09 | 0 | 2.95
TELR3- | 33 | 28.46 | 10.11 | 4.72 | 19.01 | 2.99 | 2.07 | 0 | 2.93
TONG3- | 33 | 24.09 | 8.95 | 2 | 14.65 | 2.98 | 2.06 | 0 | 2.92
WFIE3- | 33 | 42.42 | 15.26 | 8.4 | 29.98 | 3.02 | 2.09 | 0 | 2.96
WGEO3- | 33 | 50.3 | 17.6 | 10.19 | 35.08 | 5.94 | 4.12 | 0 | 5.83
WHHO3- | 33 | 43.34 | 15.19 | 10.06 | 31.55 | 5.94 | 4.11 | 0 | 5.82
WHTL3- | 33 | 26.58 | 10.53 | 0.87 | 15.76 | 2.24 | 1.55 | 0 | 2.2
WISH3- | 33 | 44.48 | 15.35 | 10.49 | 32.2 | 5.87 | 4.07 | 0 | 5.75
WLEE3A | 33 | 50.38 | 21.05 | 10.44 | 40.21 | 3.02 | 2.09 | 0 | 2.96
WLEE3B | 33 | 50.59 | 21.13 | 10.42 | 40.3 | 3.02 | 2.09 | 0 | 2.96
WLEE3C | 33 | 50.01 | 20.85 | 10.38 | 39.87 | 3.02 | 2.09 | 0 | 2.96
WLEX3A | 33 | 57.66 | 20.24 | 9.11 | 37.73 | 3.05 | 2.11 | 0 | 2.99
WLEX3B | 33 | 57.91 | 20.33 | 9.11 | 37.85 | 3.04 | 2.11 | 0 | 2.99
WLEX3C | 33 | 55.44 | 19.45 | 9.09 | 36.6 | 3.05 | 2.11 | 0 | 2.99
BAGA0J | 25 | 16.33 | 5.98 | 3.69 | 12.15 | 0 | 0 | 0 | 0
BAGA0K | 25 | 16.32 | 5.98 | 3.69 | 12.14 | 0 | 0 | 0 | 0
BONN0J | 25 | 18.13 | 6.52 | 5.44 | 14.66 | 0 | 0 | 0 | 0
BONN0K | 25 | 18.13 | 6.52 | 5.44 | 14.66 | 0 | 0 | 0 | 0
BONN0L | 25 | 18.13 | 6.52 | 5.44 | 14.66 | 0 | 0 | 0 | 0
CATY0J | 25 | 10.05 | 3.71 | 1.71 | 6.95 | 0 | 0 | 0 | 0
CATY0K | 25 | 10.06 | 3.71 | 1.74 | 6.98 | 0 | 0 | 0 | 0
CURR0J | 25 | 21.3 | 7.67 | 6.46 | 17.3 | 0 | 0 | 0 | 0
CURR0K | 25 | 21.3 | 7.67 | 6.46 | 17.3 | 0 | 0 | 0 | 0
DEVM0J | 25 | 8.38 | 3.01 | 2.57 | 6.83 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.38 | 3.01 | 2.57 | 6.83 | 0 | 0 | 0 | 0
ECCF0J | 25 | 15.74 | 6 | 1.33 | 9.82 | 0 | 0 | 0 | 0
ECCF0K | 25 | 19.42 | 7.21 | 2.74 | 12.94 | 0 | 0 | 0 | 0
ELVA0J | 25 | 18.81 | 6.63 | 8 | 17.39 | 0 | 0 | 0 | 0
ELVA0K | 25 | 18.81 | 6.63 | 8 | 17.38 | 0 | 0 | 0 | 0
INWI0J | 25 | 11.18 | 3.99 | 3.43 | 9.08 | 0 | 0 | 0 | 0
INWI0K | 25 | 11.18 | 3.99 | 3.43 | 9.08 | 0 | 0 | 0 | 0
MARM0J | 25 | 9.89 | 3.65 | 1.93 | 7.1 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.89 | 3.65 | 1.95 | 7.11 | 0 | 0 | 0 | 0
POOB0J | 25 | 18.77 | 6.76 | 5.68 | 15.24 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.77 | 6.76 | 5.68 | 15.24 | 0 | 0 | 0 | 0
SACO0J | 25 | 10.56 | 3.81 | 2.9 | 8.29 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.53 | 3.8 | 2.84 | 8.22 | 0 | 0 | 0 | 0
SANX0J | 25 | 17.03 | 6.09 | 4.67 | 13.29 | 0 | 0 | 0 | 0
SANX0K | 25 | 17.01 | 6.09 | 4.61 | 13.23 | 0 | 0 | 0 | 0
STLE0J | 25 | 10.42 | 3.8 | 2.32 | 7.69 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.42 | 3.8 | 2.32 | 7.69 | 0 | 0 | 0 | 0
WISH0J | 25 | 20.64 | 7.4 | 6.41 | 16.88 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.64 | 7.4 | 6.41 | 16.88 | 0 | 0 | 0 | 0
CAFA5- | 11 | 31.46 | 11.26 | 5.99 | 21.91 | 2.27 | 1.57 | 0 | 2.23
CURR5- | 11 | 35.35 | 12.71 | 5.84 | 23.81 | 4.48 | 3.11 | 0 | 4.39
EAST5- | 11 | 24.47 | 9.27 | 2.69 | 15.8 | 1.14 | 0.79 | 0 | 1.12
GLLE5- | 11 | 33.58 | 12.26 | 7.61 | 24.94 | 2.27 | 1.58 | 0 | 2.23
KEOO5- | 11 | 33.17 | 12.1 | 5.62 | 22.73 | 2.25 | 1.56 | 0 | 2.2
KILB5- | 11 | 28.85 | 10.55 | 4.12 | 19.04 | 3 | 2.08 | 0 | 2.94
TONG5- | 11 | 75.54 | 28.67 | 6.7 | 47.24 | 4.56 | 3.16 | 0 | 4.47

## D3.1
ETYS 19 Yr 1 - NGET Fault Levels (kA), Winter 2019/20
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 37.4023 | 13.6972 | 3.2487 | 22.6195 | 34.154 | 13.3617 | 2.3848 | 21.281 | Back To Menu
ABHA4B | 400 | 37.3852 | 13.6879 | 3.2477 | 22.6053 | 34.145 | 13.356 | 2.3794 | 21.2676
ABTH1 M1 | 132 | 29.3254 | 11.0103 | 6.7942 | 22.3652 | 28.678 | 11.2334 | 7.1543 | 23.0408
ABTH1 M2 | 132 | 26.8909 | 10.4447 | 8.221 | 22.992 | 24.1362 | 9.6039 | 7.4811 | 21.0631
ABTH1 R1 | 132 | 29.8186 | 11.4785 | 8.3191 | 24.5521 | 32.8452 | 12.9036 | 9.6344 | 27.8829
ABTH1 R2 | 132 | 29.8186 | 11.4785 | 8.3191 | 24.5521 | 32.8452 | 12.9036 | 9.6344 | 27.8829
ABTH2 M1 | 275 | 66.7493 | 23.9033 | 16.6583 | 50.4627 | 72.2906 | 27.1256 | 19.1667 | 57.5281
ABTH2 M2 | 275 | 66.7493 | 23.9033 | 16.6583 | 50.4627 | 72.2906 | 27.1256 | 19.1667 | 57.5281
ABTH2 M4 | 275 | 66.7493 | 23.9033 | 16.6583 | 50.4627 | 72.2906 | 27.1256 | 19.1667 | 57.5281
ABTH2 R | 275 | 49.7806 | 18.3192 | 7.724 | 33.6313 | 50.695 | 19.3966 | 8.5122 | 35.9432
ALDW2 MC1 | 275 | 62.9077 | 23.5243 | 9.9762 | 43.2446 | 61.7541 | 24.4962 | 9.8485 | 44.4914
ALDW2 MC2 | 275 | 62.9077 | 23.5243 | 9.9762 | 43.2446 | 61.7541 | 24.4962 | 9.8485 | 44.4914
ALDW2 MC3 | 275 | 62.9077 | 23.5243 | 9.9762 | 43.2446 | 61.7541 | 24.4962 | 9.8485 | 44.4914
ALDW2 MC4 | 275 | 62.9077 | 23.5243 | 9.9762 | 43.2446 | 61.7541 | 24.4962 | 9.8485 | 44.4914
AMEM1 M1 | 132 | 25.7091 | 9.1769 | 9.2236 | 22.2017 | 31.6674 | 11.6443 | 10.5099 | 26.9774
AMEM1 M2 | 132 | 25.7091 | 9.1769 | 9.2236 | 22.2017 | 31.6674 | 11.6443 | 10.5099 | 26.9774
AMEM1 R1 | 132 | 25.7091 | 9.1769 | 9.2236 | 22.2017 | 31.6674 | 11.6443 | 10.5099 | 26.9774
AMEM1 R2 | 132 | 25.7091 | 9.1769 | 9.2236 | 22.2017 | 31.6674 | 11.6443 | 10.5099 | 26.9774
AMEM4 M | 400 | 49.9584 | 18.64 | 4.2725 | 30.6335 | 41.9045 | 16.6455 | 2.9071 | 26.4473
AMEM4 R | 400 | 50.9735 | 18.9872 | 4.3763 | 31.2282 | 41.8067 | 16.5357 | 2.8748 | 26.2597
AXMI4 MC1 | 400 | 39.4305 | 14.648 | 7.9306 | 28.646 | 33.2927 | 13.0251 | 6.1661 | 24.5864
AXMI4 MC2 | 400 | 39.4305 | 14.648 | 7.9306 | 28.646 | 33.2927 | 13.0251 | 6.1661 | 24.5864
BAGB2 M1 | 275 | 53.352 | 19.5145 | 13.939 | 41.5366 | 50.9283 | 19.449 | 13.5755 | 41.0806
BAGB2 M2 | 275 | 53.352 | 19.5145 | 13.939 | 41.5366 | 50.9283 | 19.449 | 13.5755 | 41.0806
BAGB2 R1 | 275 | 53.352 | 19.5145 | 13.939 | 41.5366 | 50.9283 | 19.449 | 13.5755 | 41.0806
BAGB2 R2 | 275 | 53.352 | 19.5145 | 13.939 | 41.5366 | 50.9283 | 19.449 | 13.5755 | 41.0806
BARK2 M1 | 275 | 54.8856 | 19.9417 | 14.3814 | 42.5832 | 54.7752 | 20.8023 | 14.261 | 43.6798
BARK2 M2 | 275 | 53.0631 | 19.2847 | 14.1323 | 41.405 | 55.1741 | 20.9086 | 14.872 | 44.4413
BARK2 R1 | 275 | 54.8856 | 19.9417 | 14.3814 | 42.5832 | 54.7752 | 20.8023 | 14.261 | 43.6798
BARK2 R2 | 275 | 53.0631 | 19.2847 | 14.1323 | 41.405 | 55.1741 | 20.9086 | 14.872 | 44.4413
BARK4 M1 | 400 | 132.4389 | 46.5985 | 41.4293 | 107.3296 | 125.7025 | 48.6353 | 33.2595 | 102.0403
BARK4 M2 | 400 | 132.4389 | 46.5985 | 41.4293 | 107.3296 | 125.7025 | 48.6353 | 33.2595 | 102.0403
BARK4 R1 | 400 | 132.4389 | 46.5985 | 41.4293 | 107.3296 | 125.7025 | 48.6353 | 33.2595 | 102.0403
BARK4 R2 | 400 | 132.4389 | 46.5985 | 41.4293 | 107.3296 | 125.7025 | 48.6353 | 33.2595 | 102.0403
BEDD2 M1/4 | 275 | 60.6131 | 21.7252 | 13.8727 | 44.5968 | 63.6132 | 24.3143 | 13.7098 | 48.0954
BEDD2 M2/3 | 275 | 78.9109 | 27.9904 | 17.7481 | 57.3324 | 81.4223 | 31.0793 | 17.3393 | 61.2921
BEDD2 R1 | 275 | 50.9009 | 18.8857 | 11.2553 | 37.9637 | 51.105 | 19.6965 | 11.0803 | 38.9354
BEDD2 R2 | 275 | 78.9109 | 27.9904 | 17.7481 | 57.3324 | 81.4223 | 31.0793 | 17.3393 | 61.2921
BEDD2 R3 | 275 | 78.9109 | 27.9904 | 17.7481 | 57.3324 | 81.4223 | 31.0793 | 17.3393 | 61.2921
BEDD2 R4 | 275 | 50.9009 | 18.8857 | 11.2553 | 37.9637 | 51.105 | 19.6965 | 11.0803 | 38.9354
BEDD4B | 400 | 41.8441 | 15.6752 | 3.034 | 25.2022 | 37.0678 | 14.8506 | 3.6424 | 24.6444
BESW2 MC1 | 275 | 59.1575 | 21.7947 | 10.8571 | 41.6795 | 51.5447 | 20.5465 | 8.4478 | 37.505
BESW2 MC2 | 275 | 59.1575 | 21.7947 | 10.8571 | 41.6795 | 51.5447 | 20.5465 | 8.4478 | 37.505
BESW2 MC3 | 275 | 59.1575 | 21.7947 | 10.8571 | 41.6795 | 51.5447 | 20.5465 | 8.4478 | 37.505
BESW2 MC4 | 275 | 59.1575 | 21.7947 | 10.8571 | 41.6795 | 51.5447 | 20.5465 | 8.4478 | 37.505
BICF4A | 400 | 97.0789 | 35.4996 | 24.872 | 75.076 | 66.0962 | 26.3833 | 11.1704 | 48.4821
BICF4B | 400 | 97.0789 | 35.4996 | 24.872 | 75.076 | 66.0962 | 26.3833 | 11.1704 | 48.4821
BIRK2 MC1 | 275 | 61.1521 | 21.8029 | 16.8286 | 47.6626 | 60.4118 | 22.868 | 13.9164 | 46.2565
BIRK2 MC2 | 275 | 61.1521 | 21.8029 | 16.8286 | 47.6626 | 60.4118 | 22.868 | 13.9164 | 46.2565
BIRK2 MC3 | 275 | 61.1521 | 21.8029 | 16.8286 | 47.6626 | 60.4118 | 22.868 | 13.9164 | 46.2565
BIRK2 MC4 | 275 | 61.1521 | 21.8029 | 16.8286 | 47.6626 | 60.4118 | 22.868 | 13.9164 | 46.2565
BISW2 MC1 | 275 | 64.6599 | 23.7489 | 12.0845 | 45.6705 | 59.7163 | 23.513 | 9.7861 | 43.0385
BISW2 MC2 | 275 | 64.6599 | 23.7489 | 12.0845 | 45.6705 | 59.7163 | 23.513 | 9.7861 | 43.0385
BISW2 MC3 | 275 | 64.6599 | 23.7489 | 12.0845 | 45.6705 | 59.7163 | 23.513 | 9.7861 | 43.0385
BISW2 MC4 | 275 | 64.6599 | 23.7489 | 12.0845 | 45.6705 | 59.7163 | 23.513 | 9.7861 | 43.0385
BLYT1A | 132 | 30.0373 | 10.6267 | 4.4875 | 19.5159 | 31.4279 | 11.8247 | 5.1418 | 21.8644
BLYT1B | 132 | 29.8335 | 10.5801 | 4.4479 | 19.4104 | 31.2779 | 11.7798 | 5.1072 | 21.7664
BLYT2 M1 | 275 | 80.8268 | 29.6273 | 24.1663 | 66.0657 | 76.8005 | 29.7309 | 21.9003 | 63.9461
BLYT2 M2 | 275 | 80.8268 | 29.6273 | 24.1663 | 66.0657 | 76.8005 | 29.7309 | 21.9003 | 63.9461
BLYT2 R1 | 275 | 80.8268 | 29.6273 | 24.1663 | 66.0657 | 76.8005 | 29.7309 | 21.9003 | 63.9461
BLYT2 R2 | 275 | 80.8268 | 29.6273 | 24.1663 | 66.0657 | 76.8005 | 29.7309 | 21.9003 | 63.9461
BODE4 M1 | 400 | 87.8607 | 31.3471 | 22.0752 | 66.4067 | 73.1981 | 28.1558 | 16.3488 | 56.167
BODE4 R1 | 400 | 87.8607 | 31.3471 | 22.0752 | 66.4067 | 73.1981 | 28.1558 | 16.3488 | 56.167
BOLN4 M1 | 400 | 67.9951 | 25.1949 | 20.3493 | 55.9802 | 61.5044 | 23.7192 | 18.5044 | 52.0484
BOLN4 M2 | 400 | 67.9951 | 25.1949 | 20.3493 | 55.9802 | 61.5044 | 23.7192 | 18.5044 | 52.0484
BOLN4 R1 | 400 | 67.9951 | 25.1949 | 20.3493 | 55.9802 | 61.5044 | 23.7192 | 18.5044 | 52.0484
BOLN4 R2 | 400 | 67.9951 | 25.1949 | 20.3493 | 55.9802 | 61.5044 | 23.7192 | 18.5044 | 52.0484
BOTW4 MC1 | 400 | 71.4659 | 25.9256 | 14.1772 | 50.8415 | 60.5835 | 23.599 | 11.3962 | 44.7702
BOTW4 MC2 | 400 | 71.4659 | 25.9256 | 14.1772 | 50.8415 | 60.5835 | 23.599 | 11.3962 | 44.7702
BRAI4A | 400 | 63.6024 | 23.378 | 14.3581 | 47.4196 | 48.7516 | 19.0695 | 9.3923 | 36.3606
BRAI4A BRFO | 400 | 63.6024 | 23.378 | 14.3581 | 47.4196 | 48.7516 | 19.0695 | 9.3923 | 36.3606
BRAI4A RAYL | 400 | 63.6024 | 23.378 | 14.3581 | 47.4196 | 48.7516 | 19.0695 | 9.3923 | 36.3606
BRAI4B | 400 | 61.4602 | 22.6264 | 13.6548 | 45.6534 | 46.3784 | 18.0867 | 8.9308 | 34.5092
BRAI4B PELH | 400 | 61.4602 | 22.6264 | 13.6548 | 45.6534 | 46.3784 | 18.0867 | 8.9308 | 34.5092
BRAI4B RAYL | 400 | 61.4602 | 22.6264 | 13.6548 | 45.6534 | 46.3784 | 18.0867 | 8.9308 | 34.5092
BRAW2 MC1 | 275 | 64.8759 | 23.3858 | 14.8941 | 47.9666 | 65.7991 | 25.2433 | 13.9683 | 49.6677
BRAW2 MC2 | 275 | 64.8759 | 23.3858 | 14.8941 | 47.9666 | 65.7991 | 25.2433 | 13.9683 | 49.6677
BRAW2 MC3 | 275 | 64.8759 | 23.3858 | 14.8941 | 47.9666 | 65.7991 | 25.2433 | 13.9683 | 49.6677
BRAW2 MC4 | 275 | 64.8759 | 23.3858 | 14.8941 | 47.9666 | 65.7991 | 25.2433 | 13.9683 | 49.6677
BRAW4A | 400 | 34.9479 | 12.8053 | 4.4202 | 22.5296 | 30.5548 | 11.6255 | 4.2156 | 20.6566
BRED2 MC1 | 275 | 78.849 | 29.0369 | 15.8049 | 56.8693 | 75.26 | 29.5464 | 12.8241 | 54.609
BRED2 MC2 | 275 | 78.849 | 29.0369 | 15.8049 | 56.8693 | 75.26 | 29.5464 | 12.8241 | 54.609
BRED2 MC3 | 275 | 78.849 | 29.0369 | 15.8049 | 56.8693 | 75.26 | 29.5464 | 12.8241 | 54.609
BRED2 MC4 | 275 | 78.849 | 29.0369 | 15.8049 | 56.8693 | 75.26 | 29.5464 | 12.8241 | 54.609
BRFO4 M3 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 M5 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 M6 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 M7 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 MC1 | 400 | 85.9623 | 30.9755 | 21.0505 | 64.8565 | 78.2653 | 30.0198 | 16.4486 | 58.903
BRFO4 MC2 | 400 | 85.9623 | 30.9755 | 21.0505 | 64.8565 | 78.2653 | 30.0198 | 16.4486 | 58.903
BRFO4 MC3 | 400 | 85.9623 | 30.9755 | 21.0505 | 64.8565 | 78.2653 | 30.0198 | 16.4486 | 58.903
BRFO4 MC4 | 400 | 85.9623 | 30.9755 | 21.0505 | 64.8565 | 78.2653 | 30.0198 | 16.4486 | 58.903
BRFO4 R3 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 R5 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 R6 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRFO4 R7 | 400 | 85.9623 | 31.55 | 27.6567 | 72.2751 | 78.2653 | 30.1993 | 22.9183 | 65.6266
BRIM1 M1 | 132 | 52.966 | 17.9111 | 19.7916 | 45.1218 | 67.2075 | 24.1208 | 23.7097 | 57.8217
BRIM1 M2 | 132 | 52.966 | 17.9111 | 19.7916 | 45.1218 | 67.2075 | 24.1208 | 23.7097 | 57.8217
BRIM1 R1 | 132 | 52.966 | 17.9111 | 19.7916 | 45.1218 | 67.2075 | 24.1208 | 23.7097 | 57.8217
BRIM1 R2 | 132 | 52.966 | 17.9111 | 19.7916 | 45.1218 | 67.2075 | 24.1208 | 23.7097 | 57.8217
BRIN2 M1 | 275 | 64.7669 | 23.8171 | 13.948 | 47.6305 | 68.3789 | 26.77 | 12.9383 | 50.7968
BRIN2 M2 | 275 | 68.6515 | 25.2574 | 17.0421 | 52.7614 | 72.0391 | 27.8063 | 16.5464 | 55.8705
BRIN2 R1 | 275 | 64.7669 | 23.8171 | 13.948 | 47.6305 | 68.3789 | 26.77 | 12.9383 | 50.7968
BRIN2 R2 | 275 | 68.6515 | 25.2574 | 17.0421 | 52.7614 | 72.0391 | 27.8063 | 16.5464 | 55.8705
BRIN4 MC1 | 400 | 71.3002 | 26.1732 | 16.2815 | 53.296 | 55.5718 | 21.7476 | 11.3367 | 42.0925
BRIN4 MC4 | 400 | 71.3002 | 26.1732 | 16.2815 | 53.296 | 55.5718 | 21.7476 | 11.3367 | 42.0925
BRLE4 M1 | 400 | 122.8731 | 44.1463 | 25.1072 | 87.5396 | 105.8587 | 41.1241 | 21.6774 | 79.8356
BRLE4 M2 | 400 | 122.8731 | 44.1463 | 25.1072 | 87.5396 | 105.8587 | 41.1241 | 21.6774 | 79.8356
BRLE4 R1 | 400 | 122.8731 | 44.1463 | 25.1072 | 87.5396 | 105.8587 | 41.1241 | 21.6774 | 79.8356
BRLE4 R2 | 400 | 122.8731 | 44.1463 | 25.1072 | 87.5396 | 105.8587 | 41.1241 | 21.6774 | 79.8356
BULL4 MC1 | 400 | 69.1434 | 25.3103 | 15.2786 | 51.0728 | 52.0588 | 20.4506 | 9.1957 | 38.1172
BULL4 MC2 | 400 | 69.1434 | 25.3103 | 15.2786 | 51.0728 | 52.0588 | 20.4506 | 9.1957 | 38.1172
BURW4 MC1 | 400 | 93.6536 | 34.0385 | 22.7836 | 70.9212 | 62.6826 | 24.9736 | 11.3893 | 46.7073
BURW4 MC2 | 400 | 93.6536 | 34.0385 | 22.7836 | 70.9212 | 62.6826 | 24.9736 | 11.3893 | 46.7073
BURW4 MC3 | 400 | 93.6536 | 34.0385 | 22.7836 | 70.9212 | 62.6826 | 24.9736 | 11.3893 | 46.7073
BURW4 MC4 | 400 | 93.6536 | 34.0385 | 22.7836 | 70.9212 | 62.6826 | 24.9736 | 11.3893 | 46.7073
BUSH2 MC1 | 275 | 55.4063 | 20.3439 | 11.3258 | 40.0964 | 55.107 | 21.5005 | 10.3695 | 40.7758
BUSH2 MC2 | 275 | 55.4063 | 20.3439 | 11.3258 | 40.0964 | 55.107 | 21.5005 | 10.3695 | 40.7758
BUSH2 MC3 | 275 | 55.4063 | 20.3439 | 11.3258 | 40.0964 | 55.107 | 21.5005 | 10.3695 | 40.7758
BUSH2 MC4 | 275 | 55.4063 | 20.3439 | 11.3258 | 40.0964 | 55.107 | 21.5005 | 10.3695 | 40.7758
BUST2 M1 | 275 | 72.1222 | 26.0465 | 18.8141 | 55.6494 | 74.7192 | 28.527 | 17.5934 | 57.9367
BUST2 M2 | 275 | 72.1222 | 26.0465 | 18.8141 | 55.6494 | 74.7192 | 28.527 | 17.5934 | 57.9367
BUST2 R1 | 275 | 72.1222 | 26.0465 | 18.8141 | 55.6494 | 74.7192 | 28.527 | 17.5934 | 57.9367
BUST2 R2 | 275 | 72.1222 | 26.0465 | 18.8141 | 55.6494 | 74.7192 | 28.527 | 17.5934 | 57.9367
CANT4 MC1 | 400 | 85.996 | 31.2202 | 18.3648 | 62.5168 | 67.1032 | 26.5597 | 11.5977 | 49.1588
CANT4 MC2 | 400 | 85.996 | 31.2202 | 18.3648 | 62.5168 | 67.1032 | 26.5597 | 11.5977 | 49.1588
CANT4 MC3 | 400 | 85.996 | 31.2202 | 18.3648 | 62.5168 | 67.1032 | 26.5597 | 11.5977 | 49.1588
CANT4 MC4 | 400 | 85.996 | 31.2202 | 18.3648 | 62.5168 | 67.1032 | 26.5597 | 11.5977 | 49.1588
CANT4 R5 | 400 | 85.996 | 31.2202 | 18.3648 | 62.5168 | 67.1032 | 26.5597 | 11.5977 | 49.1588
CANT4 R5 | 400 | 86.0018 | 31.2235 | 18.3659 | 62.5226 | 67.1047 | 26.5606 | 11.5938 | 49.1561
CANT4 R5 | 400 | 86.0018 | 31.2235 | 18.3659 | 62.5226 | 67.1047 | 26.5606 | 11.5938 | 49.1561
CAPE2 M1 | 275 | 71.2978 | 24.9891 | 23.1331 | 58.4731 | 79.8102 | 29.252 | 24.3664 | 65.7349
CAPE2 M2 | 275 | 71.2978 | 24.9891 | 23.1331 | 58.4731 | 79.8102 | 29.252 | 24.3664 | 65.7349
CAPE2 R1 | 275 | 71.2978 | 24.9891 | 23.1331 | 58.4731 | 79.8102 | 29.252 | 24.3664 | 65.7349
CAPE2 R2 | 275 | 71.2978 | 24.9891 | 23.1331 | 58.4731 | 79.8102 | 29.252 | 24.3664 | 65.7349
CAPE4A | 400 | 97.3946 | 34.4147 | 26.0634 | 74.7332 | 88.5489 | 33.5611 | 20.3924 | 67.855
CAPE4B | 400 | 97.3998 | 34.4166 | 26.0639 | 74.7364 | 89.3385 | 33.8556 | 20.5215 | 68.4005
CARE2 MC1 | 275 | 50.0327 | 18.7826 | 8.9891 | 35.5517 | 41.8844 | 16.6413 | 7.4315 | 30.966
CARE2 MC2 | 275 | 50.0327 | 18.7826 | 8.9891 | 35.5517 | 41.8844 | 16.6413 | 7.4315 | 30.966
CARR1 M1 | 132 | 33.442 | 12.378 | 9.5437 | 27.0487 | 39.3214 | 15.0028 | 11.361 | 32.5782
CARR1 M2 | 132 | 33.442 | 12.378 | 9.5437 | 27.0487 | 39.3214 | 15.0028 | 11.361 | 32.5782
CARR1 M3 | 132 | 33.442 | 12.378 | 9.5437 | 27.0487 | 39.3214 | 15.0028 | 11.361 | 32.5782
CARR1 M4 | 132 | 41.8182 | 14.7072 | 14.0201 | 34.8192 | 53.6524 | 19.6723 | 17.485 | 45.3059
CARR1 R1 | 132 | 33.442 | 12.378 | 9.5437 | 27.0487 | 39.3214 | 15.0028 | 11.361 | 32.5782
CARR1 R2 | 132 | 33.442 | 12.378 | 9.5437 | 27.0487 | 39.3214 | 15.0028 | 11.361 | 32.5782
CARR1 R3 | 132 | 41.8182 | 14.7072 | 14.0201 | 34.8192 | 53.6524 | 19.6723 | 17.485 | 45.3059
CARR1 R4 | 132 | 41.8182 | 14.7072 | 14.0201 | 34.8192 | 53.6524 | 19.6723 | 17.485 | 45.3059
CARR1B | 132 | 41.0284 | 14.2702 | 7.9934 | 28.1745 | 50.7633 | 19.1445 | 6.9883 | 34.0627
CARR1C | 132 | 40.8587 | 14.2538 | 7.5867 | 27.7446 | 50.3099 | 19.0959 | 5.5419 | 32.5475
CARR1D | 132 | 41.1384 | 14.2892 | 8.2255 | 28.4335 | 51.1417 | 19.1944 | 7.3554 | 34.5003
CARR2 M1 | 275 | 81.897 | 29.6533 | 21.9941 | 63.9301 | 88.4418 | 33.3133 | 24.1842 | 71.2963
CARR2 M2 | 275 | 81.897 | 29.6533 | 21.9941 | 63.9301 | 88.4418 | 33.3133 | 24.1842 | 71.2963
CARR2 R1 | 275 | 81.897 | 29.6533 | 21.9941 | 63.9301 | 88.4418 | 33.3133 | 24.1842 | 71.2963
CARR2 R2 | 275 | 81.897 | 29.6533 | 21.9941 | 63.9301 | 88.4418 | 33.3133 | 24.1842 | 71.2963
CARR4 M1 | 400 | 122.8088 | 45.2516 | 36.4233 | 100.4188 | 107.2769 | 41.6685 | 31.084 | 90.0121
CARR4 M2/4 | 400 | 122.8088 | 45.2516 | 36.4233 | 100.4188 | 107.2769 | 41.6685 | 31.084 | 90.0121
CARR4 R1 | 400 | 122.8088 | 45.2516 | 36.4233 | 100.4188 | 107.2769 | 41.6685 | 31.084 | 90.0121
CARR4 R1/2 | 400 | 122.8088 | 45.2516 | 36.4233 | 100.4188 | 107.2769 | 41.6685 | 31.084 | 90.0121
CARR4 R2 | 400 | 122.8088 | 45.2516 | 36.4233 | 100.4188 | 107.2769 | 41.6685 | 31.084 | 90.0121
CARR4 R4 | 400 | 122.8088 | 45.2516 | 36.4233 | 100.4188 | 107.2769 | 41.6685 | 31.084 | 90.0121
CARR4A | 400 | 111.2713 | 39.5324 | 9.9673 | 65.8746 | 96.6947 | 37.1854 | 10.1804 | 62.7684
CARR4B | 400 | 111.4114 | 39.5952 | 9.8836 | 65.8796 | 93.8858 | 36.3673 | 8.8538 | 60.2849
CASK1 M1 | 132 | 48.5478 | 16.1534 | 13.3538 | 36.1981 | 53.8397 | 18.9068 | 16.0448 | 42.783
CELL1 M1 | 132 | 45.3631 | 16.8657 | 14.2435 | 38.0951 | 56.336 | 22.1848 | 16.7631 | 48.1372
CELL1 M2 | 132 | 43.3705 | 16.0901 | 12.0263 | 34.7811 | 48.0591 | 18.5959 | 12.8849 | 39.1834
CELL1 R1 | 132 | 45.3631 | 16.8657 | 14.2435 | 38.0951 | 56.336 | 22.1848 | 16.7631 | 48.1372
CELL1 R2 | 132 | 43.3705 | 16.0901 | 12.0263 | 34.7811 | 48.0591 | 18.5959 | 12.8849 | 39.1834
CELL1A | 132 | 37.8348 | 13.5707 | 6.9268 | 26.1187 | 46.6728 | 18.7025 | 8.2832 | 34.7325
CELL4 M1 | 400 | 91.5124 | 33.9336 | 16.3329 | 64.3223 | 75.2375 | 29.7561 | 14.0875 | 56.169
CELL4 M2 | 400 | 91.5124 | 33.9336 | 16.3329 | 64.3223 | 75.2375 | 29.7561 | 14.0875 | 56.169
CELL4 R1 | 400 | 91.5124 | 33.9336 | 16.3329 | 64.3223 | 75.2375 | 29.7561 | 14.0875 | 56.169
CELL4 R2 | 400 | 91.5124 | 33.9336 | 16.3329 | 64.3223 | 75.2375 | 29.7561 | 14.0875 | 56.169
CHIC4 MB1 | 400 | 36.5381 | 13.6263 | 7.3196 | 26.5901 | 30.1596 | 11.7781 | 5.7246 | 22.3814
CHIC4 MB2 | 400 | 36.5381 | 13.6263 | 7.3196 | 26.5901 | 30.1596 | 11.7781 | 5.7246 | 22.3814
CHIC4 R1/2 | 400 | 36.2138 | 13.6723 | 10.6085 | 29.9441 | 28.6339 | 11.2701 | 7.678 | 23.6163
CHSI2 MC1 | 275 | 85.4695 | 30.7672 | 18.5723 | 62.0836 | 74.2551 | 29.2871 | 12.1792 | 53.5974
CHSI2 MC2 | 275 | 85.4695 | 30.7672 | 18.5723 | 62.0836 | 74.2551 | 29.2871 | 12.1792 | 53.5974
CHSI2 MC3 | 275 | 85.4695 | 30.7672 | 18.5723 | 62.0836 | 74.2551 | 29.2871 | 12.1792 | 53.5974
CHSI2 MC4 | 275 | 85.4695 | 30.7672 | 18.5723 | 62.0836 | 74.2551 | 29.2871 | 12.1792 | 53.5974
CHTE2 MC1 | 275 | 69.7663 | 25.2299 | 16.7786 | 52.459 | 59.3338 | 23.5504 | 11.0335 | 44.3388
CHTE2 MC2 | 275 | 69.7663 | 25.2299 | 16.7786 | 52.459 | 59.3338 | 23.5504 | 11.0335 | 44.3388
CHTE2 MC3 | 275 | 69.7663 | 25.2299 | 16.7786 | 52.459 | 59.3338 | 23.5504 | 11.0335 | 44.3388
CHTE2 MC4 | 275 | 69.7663 | 25.2299 | 16.7786 | 52.459 | 59.3338 | 23.5504 | 11.0335 | 44.3388
CILF4 M1 | 400 | 84.9639 | 30.5803 | 21.1029 | 64.35 | 73.67 | 28.3955 | 14.8857 | 55.0429
CILF4 M2 | 400 | 84.9639 | 30.5803 | 21.1029 | 64.35 | 73.67 | 28.3955 | 14.8857 | 55.0429
CILF4 R1 | 400 | 84.9639 | 30.5803 | 21.1029 | 64.35 | 73.67 | 28.3955 | 14.8857 | 55.0429
CILF4 R2 | 400 | 84.9639 | 30.5803 | 21.1029 | 64.35 | 73.67 | 28.3955 | 14.8857 | 55.0429
CITR4 M5 | 400 | 114.183 | 38.7327 | 27.5537 | 82.33 | 127.1663 | 48.1988 | 25.2408 | 93.4042
CITR4 M6 | 400 | 114.183 | 38.7327 | 27.5537 | 82.33 | 127.1663 | 48.1988 | 25.2408 | 93.4042
CITR4 MC1 | 400 | 114.1879 | 38.734 | 27.5556 | 82.3337 | 127.1862 | 48.2016 | 25.2908 | 93.4582
CITR4 MC2 | 400 | 114.1879 | 38.734 | 27.5556 | 82.3337 | 127.1862 | 48.2016 | 25.2908 | 93.4582
CITR4 MC3 | 400 | 114.1879 | 38.734 | 27.5556 | 82.3337 | 127.1862 | 48.2016 | 25.2908 | 93.4582
CITR4 MC4 | 400 | 114.1879 | 38.734 | 27.5556 | 82.3337 | 127.1862 | 48.2016 | 25.2908 | 93.4582
CITR4 R5 | 400 | 114.183 | 38.7327 | 27.5537 | 82.33 | 127.1663 | 48.1988 | 25.2408 | 93.4042
CITR4 R6 | 400 | 114.183 | 38.7327 | 27.5537 | 82.33 | 127.1663 | 48.1988 | 25.2408 | 93.4042
CLEH4 M1 | 400 | 75.5999 | 27.4871 | 16.4655 | 55.3381 | 68.4069 | 26.8024 | 13.6814 | 51.5858
CLEH4 R1 | 400 | 75.5999 | 27.4871 | 16.4655 | 55.3381 | 68.4069 | 26.8024 | 13.6814 | 51.5858
CONQ4 M1 | 400 | 131.2742 | 45.6423 | 35.2069 | 99.7548 | 132.465 | 49.2738 | 36.4732 | 106.1568
CONQ4 M2 | 400 | 131.2742 | 45.6423 | 35.2069 | 99.7548 | 132.465 | 49.2738 | 36.4732 | 106.1568
CONQ4 M3 | 400 | 131.2742 | 45.6423 | 35.2069 | 99.7548 | 132.465 | 49.2738 | 36.4732 | 106.1568
CONQ4 M4 | 400 | 131.2742 | 45.6423 | 35.2069 | 99.7548 | 132.465 | 49.2738 | 36.4732 | 106.1568
CONQ4 R1/3 | 400 | 131.2742 | 45.6423 | 35.2069 | 99.7548 | 132.465 | 49.2738 | 36.4732 | 106.1568
CONQ4 R2/4 | 400 | 131.2742 | 45.6423 | 35.2069 | 99.7548 | 132.465 | 49.2738 | 36.4732 | 106.1568
COSO4 M | 400 | 99.0696 | 35.1682 | 22.0206 | 71.7559 | 87.0091 | 33.3835 | 19.3798 | 66.5912
COSO4 R | 400 | 99.0696 | 35.1682 | 22.0206 | 71.7559 | 87.0091 | 33.3835 | 19.3798 | 66.5912
COTT4 M1 | 400 | 107.9741 | 39.6224 | 25.766 | 81.8006 | 91.4139 | 35.3982 | 18.4568 | 68.5174
COTT4 M2 | 400 | 107.9741 | 39.6224 | 25.766 | 81.8006 | 91.4139 | 35.3982 | 18.4568 | 68.5174
COTT4 M3 | 400 | 97.8471 | 36.4554 | 30.6692 | 82.2249 | 82.0722 | 31.9127 | 24.0689 | 69.2003
COTT4 M4 | 400 | 97.8471 | 36.4554 | 30.6692 | 82.2249 | 82.0722 | 31.9127 | 24.0689 | 69.2003
COTT4 R1/2 | 400 | 97.8471 | 36.4554 | 30.6692 | 82.2249 | 82.0722 | 31.9127 | 24.0689 | 69.2003
COTT4 R3/4 | 400 | 97.8471 | 36.4554 | 30.6692 | 82.2249 | 82.0722 | 31.9127 | 24.0689 | 69.2003
COVE2 MC1 | 275 | 61.8361 | 22.5377 | 12.6293 | 44.5024 | 57.9806 | 22.517 | 11.8262 | 43.6701
COVE2 MC2 | 275 | 61.8361 | 22.5377 | 12.6293 | 44.5024 | 57.9806 | 22.517 | 11.8262 | 43.6701
COVE2 MC3 | 275 | 61.8361 | 22.5377 | 12.6293 | 44.5024 | 57.9806 | 22.517 | 11.8262 | 43.6701
COVE2 MC4 | 275 | 61.8361 | 22.5377 | 12.6293 | 44.5024 | 57.9806 | 22.517 | 11.8262 | 43.6701
COWL4 M1 | 400 | 130.2404 | 47.847 | 39.9069 | 107.5728 | 107.4876 | 41.8108 | 30.4871 | 89.6166
COWL4 M2 | 400 | 130.2404 | 47.847 | 39.9069 | 107.5728 | 107.4876 | 41.8108 | 30.4871 | 89.6166
COWL4 R1 | 400 | 130.2404 | 47.847 | 39.9069 | 107.5728 | 107.4876 | 41.8108 | 30.4871 | 89.6166
COWL4 R2 | 400 | 130.2404 | 47.847 | 39.9069 | 107.5728 | 107.4876 | 41.8108 | 30.4871 | 89.6166
CREB2A | 275 | 71.9434 | 25.5603 | 15.6851 | 51.8328 | 70.1004 | 26.0426 | 12.7772 | 49.607
CREB2B | 275 | 71.9538 | 25.5607 | 15.6929 | 51.8412 | 70.8858 | 26.3272 | 12.922 | 50.1543
CREB4 MB1 | 400 | 121.1419 | 43.4489 | 30.9282 | 92.3742 | 99.786 | 38.3759 | 22.4704 | 76.7421
CREB4 MB2 | 400 | 121.1419 | 43.4489 | 30.9282 | 92.3742 | 99.786 | 38.3759 | 22.4704 | 76.7421
CREB4 RB1 | 400 | 121.1419 | 43.4489 | 30.9282 | 92.3742 | 99.786 | 38.3759 | 22.4704 | 76.7421
CREB4 RB2 | 400 | 121.1419 | 43.4489 | 30.9282 | 92.3742 | 99.786 | 38.3759 | 22.4704 | 76.7421
DAIN4 M1 | 400 | 125.599 | 45.2048 | 26.5497 | 90.4789 | 108.7029 | 42.0292 | 22.7271 | 82.1654
DAIN4 M2 | 400 | 125.599 | 45.2048 | 26.5497 | 90.4789 | 108.7029 | 42.0292 | 22.7271 | 82.1654
DAIN4 R1 | 400 | 125.599 | 45.2048 | 26.5497 | 90.4789 | 108.7029 | 42.0292 | 22.7271 | 82.1654
DAIN4 R2 | 400 | 125.599 | 45.2048 | 26.5497 | 90.4789 | 108.7029 | 42.0292 | 22.7271 | 82.1654
DIDC4 M1 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 M2 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 M3 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 M4 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 M5 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 M6 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 R1/2 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 R3/4 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 R5 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DIDC4 R6 | 400 | 125.7773 | 45.0298 | 29.3373 | 93.0191 | 113.3903 | 42.9859 | 28.5425 | 89.3338
DINO4 1 | 400 | 72.5069 | 25.2862 | 20.686 | 56.4461 | 75.7169 | 27.8462 | 22.9014 | 62.2819
DINO4 2 | 400 | 72.5069 | 25.2862 | 20.686 | 56.4461 | 75.7169 | 27.8462 | 22.9014 | 62.2819
DINO4 3 | 400 | 72.5069 | 25.2862 | 20.686 | 56.4461 | 75.7169 | 27.8462 | 22.9014 | 62.2819
DRAK1 M1 | 132 | 31.1847 | 11.1648 | 12.6103 | 28.3998 | 38.5075 | 14.2169 | 15.6436 | 35.7493
DRAK1 M2 | 132 | 31.1847 | 11.1648 | 12.6103 | 28.3998 | 38.5075 | 14.2169 | 15.6436 | 35.7493
DRAK1 R1 | 132 | 31.1847 | 11.1648 | 12.6103 | 28.3998 | 38.5075 | 14.2169 | 15.6436 | 35.7493
DRAK1 R2 | 132 | 31.1847 | 11.1648 | 12.6103 | 28.3998 | 38.5075 | 14.2169 | 15.6436 | 35.7493
DRAK4 M1 | 400 | 122.8754 | 44.4828 | 22.9976 | 85.9059 | 109.4029 | 43.0226 | 18.4027 | 79.2458
DRAK4 M2 | 400 | 122.8754 | 44.4828 | 22.9976 | 85.9059 | 109.4029 | 43.0226 | 18.4027 | 79.2458
DRAK4 M3 | 400 | 122.8754 | 44.4828 | 22.9976 | 85.9059 | 109.4029 | 43.0226 | 18.4027 | 79.2458
DRAK4 R1/3 | 400 | 122.8754 | 44.4828 | 22.9976 | 85.9059 | 109.4029 | 43.0226 | 18.4027 | 79.2458
DRAK4 R2 | 400 | 122.8754 | 44.4828 | 22.9976 | 85.9059 | 109.4029 | 43.0226 | 18.4027 | 79.2458
DRAX1 M1 | 132 | 39.1384 | 11.8307 | 11.6737 | 28.4048 | 48.9798 | 16.6375 | 14.7586 | 38.2876
DRAX1 M2 | 132 | 39.1384 | 11.8307 | 11.6737 | 28.4048 | 48.9798 | 16.6375 | 14.7586 | 38.2876
DRAX1 R1 | 132 | 39.1384 | 11.8307 | 11.6737 | 28.4048 | 48.9798 | 16.6375 | 14.7586 | 38.2876
DRAX1 R2 | 132 | 39.1384 | 11.8307 | 11.6737 | 28.4048 | 48.9798 | 16.6375 | 14.7586 | 38.2876
DRAX4 M1 | 400 | 126.1365 | 44.006 | 35.1519 | 97.3858 | 130.6909 | 48.1229 | 37.5303 | 105.5864
DRAX4 M2 | 400 | 126.1365 | 44.006 | 35.1519 | 97.3858 | 130.6909 | 48.1229 | 37.5303 | 105.5864
DRAX4 M3 | 400 | 126.1365 | 44.006 | 35.1519 | 97.3858 | 130.6909 | 48.1229 | 37.5303 | 105.5864
DRAX4 M4 | 400 | 114.3552 | 40.0123 | 33.2592 | 89.8451 | 120.0801 | 44.1415 | 35.6494 | 98.0748
DRAX4 M5 | 400 | 114.3552 | 40.0123 | 33.2592 | 89.8451 | 120.0801 | 44.1415 | 35.6494 | 98.0748
DRAX4 M6 | 400 | 114.3552 | 40.0123 | 33.2592 | 89.8451 | 120.0801 | 44.1415 | 35.6494 | 98.0748
DRAX4 R1/2/3 | 400 | 126.1365 | 44.006 | 35.1519 | 97.3858 | 130.6909 | 48.1229 | 37.5303 | 105.5864
DRAX4 R4/5/6 | 400 | 114.3552 | 40.0123 | 33.2592 | 89.8451 | 120.0801 | 44.1415 | 35.6494 | 98.0748
DUNG2 M1 | 275 | 44.7242 | 15.9358 | 14.9705 | 37.5071 | 46.1305 | 16.9716 | 15.185 | 39.1865
DUNG2 M2 | 275 | 44.7242 | 15.9358 | 14.9705 | 37.5071 | 46.1305 | 16.9716 | 15.185 | 39.1865
DUNG2 R1 | 275 | 44.7242 | 15.9358 | 14.9705 | 37.5071 | 46.1305 | 16.9716 | 15.185 | 39.1865
DUNG2 R2 | 275 | 44.7242 | 15.9358 | 14.9705 | 37.5071 | 46.1305 | 16.9716 | 15.185 | 39.1865
DUNG4 M1 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
DUNG4 M2 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
DUNG4 M3 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
DUNG4 M4 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
DUNG4 M5 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
DUNG4 R1/2 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
DUNG4 R4/5 | 400 | 76.3346 | 27.0165 | 12.6001 | 50.8072 | 71.7858 | 26.9974 | 13.5804 | 51.7605
EALI2 MC1 | 275 | 59.8509 | 21.055 | 13.7664 | 43.5427 | 65.7517 | 25.5301 | 8.5025 | 44.6075
EALI2 MC2 | 275 | 59.8509 | 21.055 | 13.7664 | 43.5427 | 65.7517 | 25.5301 | 8.5025 | 44.6075
EALI2 MC3 | 275 | 59.8509 | 21.055 | 13.7664 | 43.5427 | 65.7517 | 25.5301 | 8.5025 | 44.6075
EALI2 MC4 | 275 | 59.8509 | 21.055 | 13.7664 | 43.5427 | 65.7517 | 25.5301 | 8.5025 | 44.6075
EASO4 M1 | 400 | 85.2034 | 30.9044 | 19.93 | 63.6354 | 75.0214 | 28.4057 | 20.1163 | 60.288
EASO4 M2 | 400 | 85.2034 | 30.9044 | 19.93 | 63.6354 | 75.0214 | 28.4057 | 20.1163 | 60.288
EASO4 R1 | 400 | 85.2034 | 30.9044 | 19.93 | 63.6354 | 75.0214 | 28.4057 | 20.1163 | 60.288
EASO4 R2 | 400 | 85.2034 | 30.9044 | 19.93 | 63.6354 | 75.0214 | 28.4057 | 20.1163 | 60.288
EASO4A | 400 | 85.2034 | 30.9044 | 19.93 | 63.6354 | 75.0214 | 28.4057 | 20.1163 | 60.288
EASO4B | 400 | 85.2034 | 30.9044 | 19.93 | 63.6354 | 75.0214 | 28.4057 | 20.1163 | 60.288
ECLA1 M1 | 132 | 45.0994 | 16.8933 | 13.0024 | 36.8931 | 47.5675 | 18.562 | 14.1865 | 40.4372
ECLA1 M2 | 132 | 45.0994 | 16.8933 | 13.0024 | 36.8931 | 47.5675 | 18.562 | 14.1865 | 40.4372
ECLA1 R1 | 132 | 45.6463 | 17.0436 | 13.1044 | 37.2077 | 54.3402 | 21.0027 | 15.7936 | 45.4958
ECLA1 R2 | 132 | 45.6463 | 17.0436 | 13.1044 | 37.2077 | 54.3402 | 21.0027 | 15.7936 | 45.4958
ECLA4 M1 | 400 | 113.8082 | 41.5189 | 23.9516 | 82.6681 | 91.6351 | 35.9619 | 17.4736 | 68.3314
ECLA4 M2 | 400 | 113.8082 | 41.5189 | 23.9516 | 82.6681 | 91.6351 | 35.9619 | 17.4736 | 68.3314
ECLA4 R1 | 400 | 113.8082 | 41.5189 | 23.9516 | 82.6681 | 91.6351 | 35.9619 | 17.4736 | 68.3314
ECLA4 R2 | 400 | 113.8082 | 41.5189 | 23.9516 | 82.6681 | 91.6351 | 35.9619 | 17.4736 | 68.3314
EGGB4 M1 | 400 | 103.0868 | 36.9058 | 25.6962 | 77.8888 | 94.306 | 35.8881 | 20.5292 | 71.2827
EGGB4 M2 | 400 | 103.0868 | 36.9058 | 25.6962 | 77.8888 | 94.306 | 35.8881 | 20.5292 | 71.2827
EGGB4 R1 | 400 | 93.2911 | 33.294 | 24.8833 | 71.9681 | 85.9738 | 32.581 | 19.5438 | 65.6203
EGGB4 R2 | 400 | 93.2911 | 33.294 | 24.8833 | 71.9681 | 85.9738 | 32.581 | 19.5438 | 65.6203
ELLA2 MC1 | 275 | 63.8555 | 23.1052 | 8.2439 | 40.9195 | 64.5323 | 24.8766 | 7.9405 | 43.1214
ELLA2 MC2 | 275 | 63.8555 | 23.1052 | 8.2439 | 40.9195 | 64.5323 | 24.8766 | 7.9405 | 43.1214
ELLA2 MC3 | 275 | 63.8555 | 23.1052 | 8.2439 | 40.9195 | 64.5323 | 24.8766 | 7.9405 | 43.1214
ELLA2 MC4 | 275 | 63.8555 | 23.1052 | 8.2439 | 40.9195 | 64.5323 | 24.8766 | 7.9405 | 43.1214
ELST1 M1 | 132 | 31.9407 | 11.6071 | 10.083 | 26.4979 | 39.0791 | 14.6479 | 12.1251 | 32.8404
ELST1 M2 | 132 | 43.8829 | 15.7204 | 13.2995 | 35.5314 | 53.5661 | 20.5092 | 15.6164 | 44.6208
ELST1 M3 | 132 | 29.0682 | 10.8319 | 6.3151 | 21.6338 | 32.4259 | 12.6024 | 7.3539 | 25.1764
ELST1 R1 | 132 | 31.9407 | 11.6071 | 10.083 | 26.4979 | 39.0791 | 14.6479 | 12.1251 | 32.8404
ELST1 R2 | 132 | 43.8829 | 15.7204 | 13.2995 | 35.5314 | 53.5661 | 20.5092 | 15.6164 | 44.6208
ELST1 R3 | 132 | 29.0682 | 10.8319 | 6.3151 | 21.6338 | 32.4259 | 12.6024 | 7.3539 | 25.1764
ELST2 M1 | 275 | 65.1839 | 23.5753 | 16.8001 | 50.1406 | 71.7419 | 27.0304 | 18.7081 | 56.9349
ELST2 M2 | 275 | 66.1867 | 24.1204 | 14.894 | 49.0054 | 73.3267 | 28.166 | 15.8345 | 55.6671
ELST2 R1 | 275 | 65.1839 | 23.5753 | 16.8001 | 50.1406 | 71.7419 | 27.0304 | 18.7081 | 56.9349
ELST2 R2 | 275 | 66.1867 | 24.1204 | 14.894 | 49.0054 | 73.3267 | 28.166 | 15.8345 | 55.6671
ELST4 M1 | 400 | 92.574 | 33.3492 | 28.9214 | 76.0843 | 109.8238 | 41.5591 | 33.5967 | 92.3702
ELST4 R1 | 400 | 92.574 | 33.3492 | 28.9214 | 76.0843 | 109.8238 | 41.5591 | 33.5967 | 92.3702
ELST4A | 400 | 56.8773 | 20.9348 | 7.5266 | 37.1329 | 54.0758 | 20.572 | 8.5174 | 37.6106
ENDE4 MC1 | 400 | 92.4711 | 34.2247 | 17.965 | 66.3661 | 62.6933 | 24.9615 | 10.8496 | 46.1505
ENDE4 MC2 | 400 | 92.4711 | 34.2247 | 17.965 | 66.3661 | 62.6933 | 24.9615 | 10.8496 | 46.1505
ENDE4 MC3 | 400 | 92.4711 | 34.2247 | 17.965 | 66.3661 | 62.6933 | 24.9615 | 10.8496 | 46.1505
ENDE4 MC4 | 400 | 92.4711 | 34.2247 | 17.965 | 66.3661 | 62.6933 | 24.9615 | 10.8496 | 46.1505
EXET4 M1 | 400 | 58.4199 | 21.3515 | 11.789 | 41.9845 | 55.2171 | 21.4387 | 11.1776 | 41.4965
EXET4 M2 | 400 | 58.4199 | 21.3515 | 11.789 | 41.9845 | 55.2171 | 21.4387 | 11.1776 | 41.4965
EXET4 R1 | 400 | 58.4199 | 21.3515 | 11.789 | 41.9845 | 55.2171 | 21.4387 | 11.1776 | 41.4965
EXET4 R2 | 400 | 58.4199 | 21.3515 | 11.789 | 41.9845 | 55.2171 | 21.4387 | 11.1776 | 41.4965
FAWL1 M1 | 132 | 49.9742 | 17.5635 | 18.0586 | 42.8972 | 63.7884 | 24.0167 | 21.4627 | 55.4275
FAWL1 M2 | 132 | 49.9742 | 17.5635 | 18.0586 | 42.8972 | 63.7884 | 24.0167 | 21.4627 | 55.4275
FAWL1 R1 | 132 | 49.9742 | 17.5635 | 18.0586 | 42.8972 | 63.7884 | 24.0167 | 21.4627 | 55.4275
FAWL1 R2 | 132 | 49.9742 | 17.5635 | 18.0586 | 42.8972 | 63.7884 | 24.0167 | 21.4627 | 55.4275
FAWL4 M1/3 | 400 | 74.3015 | 26.4767 | 9.677 | 47.1207 | 65.5922 | 25.3634 | 7.9871 | 43.8564
FAWL4 M1/3(1) | 400 | 74.3015 | 26.4767 | 9.677 | 47.1207 | 65.5922 | 25.3634 | 7.9871 | 43.8564
FAWL4 M2/4(2) | 400 | 74.3015 | 26.4767 | 9.677 | 47.1207 | 65.5922 | 25.3634 | 7.9871 | 43.8564
FAWL4 M2/4(3) | 400 | 74.3015 | 26.4767 | 9.677 | 47.1207 | 65.5922 | 25.3634 | 7.9871 | 43.8564
FAWL4 R1/3 | 400 | 74.3015 | 26.4767 | 9.677 | 47.1207 | 65.5922 | 25.3634 | 7.9871 | 43.8564
FAWL4 R2/4 | 400 | 74.3015 | 26.4767 | 9.677 | 47.1207 | 65.5922 | 25.3634 | 7.9871 | 43.8564
FECK2 M1 | 275 | 62.7321 | 23.1269 | 14.2785 | 46.985 | 61.9832 | 23.8975 | 14.0548 | 47.8509
FECK2 M2 | 275 | 62.7321 | 23.1269 | 14.2785 | 46.985 | 61.9832 | 23.8975 | 14.0548 | 47.8509
FECK2 R | 275 | 62.7321 | 23.1269 | 14.2785 | 46.985 | 61.9832 | 23.8975 | 14.0548 | 47.8509
FECK4 M1 | 400 | 79.1903 | 29.775 | 13.449 | 55.5572 | 66.7186 | 26.376 | 12.6902 | 49.9916
FECK4 M2 | 400 | 79.1903 | 29.775 | 13.449 | 55.5572 | 66.7186 | 26.376 | 12.6902 | 49.9916
FECK4 R1 | 400 | 79.1903 | 29.775 | 13.449 | 55.5572 | 66.7186 | 26.376 | 12.6902 | 49.9916
FECK4 R2 | 400 | 79.1903 | 29.775 | 13.449 | 55.5572 | 66.7186 | 26.376 | 12.6902 | 49.9916
FENW4A | 400 | 112.2991 | 39.5198 | 14.867 | 70.7564 | 95.8294 | 36.662 | 7.7734 | 59.6213
FERR2 M1 | 275 | 57.2857 | 20.7359 | 11.3039 | 40.6288 | 58.4134 | 22.0871 | 11.3901 | 42.6261
FERR2 M2 | 275 | 57.1202 | 20.608 | 15.1483 | 44.2924 | 60.862 | 22.8173 | 14.174 | 46.4425
FERR2 R1 | 275 | 61.924 | 22.3364 | 12.0392 | 43.6276 | 61.7298 | 23.5086 | 10.2941 | 43.5403
FERR2 R2 | 275 | 61.924 | 22.3364 | 12.0392 | 43.6276 | 61.7298 | 23.5086 | 10.2941 | 43.5403
FERR2A | 275 | 57.1497 | 20.5285 | 12.6618 | 41.6935 | 60.6845 | 22.7171 | 11.6095 | 43.7362
FERR2B | 275 | 56.7589 | 20.4116 | 9.1552 | 38.0215 | 57.6307 | 21.7997 | 8.8648 | 39.6943
FERR4A | 400 | 74.8485 | 26.773 | 9.551 | 47.4137 | 65.379 | 24.8555 | 8.0945 | 43.2456
FFES2 Term205 | 275 | 35.5343 | 13.3012 | 2.6733 | 21.484 | 34.4558 | 13.5281 | 2.3354 | 21.4669
FFES2 Term210 | 275 | 35.3502 | 13.2523 | 2.6457 | 21.3872 | 34.8051 | 13.6625 | 2.3507 | 21.6724
FIDF2 M1 | 275 | 56.36 | 20.0764 | 18.6226 | 47.015 | 58.5539 | 21.5102 | 19.0549 | 49.4749
FIDF2 M2 | 275 | 64.4814 | 22.4757 | 22.0186 | 53.804 | 69.1529 | 25.0747 | 23.3343 | 58.7953
FIDF2 M3 | 275 | 81.107 | 28.3939 | 23.5879 | 63.7429 | 83.7135 | 30.7828 | 24.7845 | 68.3179
FIDF2 M4 | 275 | 79.4314 | 27.9302 | 22.5291 | 62.0284 | 82.8417 | 30.555 | 23.9293 | 67.1406
FIDF2 R1 | 275 | 56.36 | 20.0764 | 18.6226 | 47.015 | 58.5539 | 21.5102 | 19.0549 | 49.4749
FIDF2 R2 | 275 | 79.4314 | 27.9302 | 22.5291 | 62.0284 | 82.8417 | 30.555 | 23.9293 | 67.1406
FLEE4 MC1 | 400 | 103.0151 | 37.1957 | 20.3654 | 72.968 | 84.2954 | 33.0253 | 15.851 | 62.5558
FLEE4 MC2 | 400 | 103.0151 | 37.1957 | 20.3654 | 72.968 | 84.2954 | 33.0253 | 15.851 | 62.5558
FLEE4 MC3 | 400 | 103.0151 | 37.1957 | 20.3654 | 72.968 | 84.2954 | 33.0253 | 15.851 | 62.5558
FLEE4 MC4 | 400 | 103.0151 | 37.1957 | 20.3654 | 72.968 | 84.2954 | 33.0253 | 15.851 | 62.5558
FLIB4 M1 | 400 | 121.1305 | 42.3546 | 32.4514 | 92.3498 | 123.3176 | 46.3541 | 31.0211 | 96.5757
FLIB4 M2 | 400 | 121.1305 | 42.3546 | 32.4514 | 92.3498 | 123.3176 | 46.3541 | 31.0211 | 96.5757
FOUR2 MC1 | 275 | 37.0311 | 14.5172 | 4.8655 | 25.3959 | 30.9519 | 12.6973 | 3.8533 | 21.81
FOUR2 MC2 | 275 | 37.0311 | 14.5172 | 4.8655 | 25.3959 | 30.9519 | 12.6973 | 3.8533 | 21.81
FROD2 MC1 | 275 | 55.3363 | 19.7057 | 18.8487 | 46.7167 | 58.5225 | 21.4354 | 19.6346 | 49.9488
FROD2 MC3 | 275 | 61.1625 | 21.206 | 14.4227 | 44.4125 | 63.8695 | 23.2702 | 13.2562 | 46.1652
FROD4 M1 | 400 | 94.6281 | 34.0086 | 32.6437 | 80.7391 | 88.6521 | 33.2715 | 30.1239 | 77.1768
FROD4 R1 | 400 | 94.6281 | 34.0086 | 32.6437 | 80.7391 | 88.6521 | 33.2715 | 30.1239 | 77.1768
GART4A | 400 | 101.597 | 36.1696 | 14.1035 | 65.255 | 83.3798 | 32.0168 | 6.9302 | 52.2087
GART4B | 400 | 105.2595 | 37.3982 | 14.8014 | 67.6904 | 90.6312 | 34.7265 | 8.3405 | 57.4512
GRAI4 M1 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 M2 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 M3 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 M4 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 M5 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 M6 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 M7 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 R1/2 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 R3 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 R4 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 R5 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 R6 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GRAI4 R7 | 400 | 136.369 | 47.8432 | 44.0498 | 111.7103 | 126.891 | 47.7731 | 40.548 | 108.1093
GREN1 M1 | 132 | 40.7084 | 14.9355 | 10.4732 | 31.5953 | 44.5478 | 17.7829 | 10.2592 | 35.4081
GREN1 M2 | 132 | 39.3083 | 14.5094 | 11.0433 | 31.5627 | 40.0426 | 15.7426 | 10.1626 | 32.426
GREN1 R1 | 132 | 40.7084 | 14.9355 | 10.4732 | 31.5953 | 44.5478 | 17.7829 | 10.2592 | 35.4081
GREN1 R2 | 132 | 39.3083 | 14.5094 | 11.0433 | 31.5627 | 40.0426 | 15.7426 | 10.1626 | 32.426
GREN4 M1 | 400 | 80.6087 | 30.3186 | 13.2936 | 56.1706 | 54.0707 | 21.9557 | 9.0047 | 40.0548
GREN4 M2 | 400 | 80.6087 | 30.3186 | 13.2936 | 56.1706 | 54.0707 | 21.9557 | 9.0047 | 40.0548
GREN4 R1 | 400 | 80.6087 | 30.3186 | 13.2936 | 56.1706 | 54.0707 | 21.9557 | 9.0047 | 40.0548
GREN4 R2 | 400 | 80.6087 | 30.3186 | 13.2936 | 56.1706 | 54.0707 | 21.9557 | 9.0047 | 40.0548
GRIW4 MC1 | 400 | 69.7563 | 25.2186 | 18.6901 | 54.3546 | 60.341 | 23.2299 | 12.3674 | 45.2194
GRIW4 MC2 | 400 | 69.7563 | 25.2186 | 18.6901 | 54.3546 | 60.341 | 23.2299 | 12.3674 | 45.2194
GRSA2 M1 | 275 | 54.3402 | 19.5355 | 16.0685 | 43.6958 | 56.4428 | 21.0749 | 15.219 | 45.0235
GRSA2 M2 | 275 | 54.3402 | 19.5355 | 16.0685 | 43.6958 | 56.4428 | 21.0749 | 15.219 | 45.0235
GRSA2 R1 | 275 | 54.3402 | 19.5355 | 16.0685 | 43.6958 | 56.4428 | 21.0749 | 15.219 | 45.0235
GRSA2 R2 | 275 | 54.3402 | 19.5355 | 16.0685 | 43.6958 | 56.4428 | 21.0749 | 15.219 | 45.0235
GRSB2 M3 | 275 | 54.6501 | 19.6337 | 16.2419 | 44.008 | 57.3328 | 21.3504 | 15.8742 | 46.0682
GRSB2 M4 | 275 | 54.6501 | 19.6337 | 16.2419 | 44.008 | 57.3328 | 21.3504 | 15.8742 | 46.0682
GRSB2 R3 | 275 | 54.6501 | 19.6337 | 16.2419 | 44.008 | 57.3328 | 21.3504 | 15.8742 | 46.0682
GRSB2 R4 | 275 | 54.6501 | 19.6337 | 16.2419 | 44.008 | 57.3328 | 21.3504 | 15.8742 | 46.0682
HACK2A | 275 | 69.6127 | 24.6221 | 11.8697 | 46.6906 | 71.0012 | 26.5803 | 12.1925 | 49.7827
HACK2B | 275 | 68.6087 | 24.2728 | 11.8676 | 46.1945 | 71.4156 | 26.7685 | 12.2518 | 50.1082
HACK4 M1 | 400 | 120.5372 | 40.7926 | 29.0664 | 86.7559 | 137.8584 | 51.1755 | 30.396 | 102.7691
HACK4 M2 | 400 | 120.5372 | 40.7926 | 29.0664 | 86.7559 | 137.8584 | 51.1755 | 30.396 | 102.7691
HACK4 R1 | 400 | 120.5372 | 40.7926 | 29.0664 | 86.7559 | 137.8584 | 51.1755 | 30.396 | 102.7691
HACK4 R2 | 400 | 120.5372 | 40.7926 | 29.0664 | 86.7559 | 137.8584 | 51.1755 | 30.396 | 102.7691
HAMB4A | 400 | 71.6508 | 25.5978 | 9.412 | 45.6127 | 59.2801 | 23.069 | 4.786 | 37.4106
HAMB4A_HEYS | 400 | 71.6508 | 25.5978 | 9.412 | 45.6127 | 59.2801 | 23.069 | 4.786 | 37.4106
HAMB4A_PEWO | 400 | 71.6508 | 25.5978 | 9.412 | 45.6127 | 59.2801 | 23.069 | 4.786 | 37.4106
HAMB4B | 400 | 71.6256 | 25.5891 | 9.4116 | 45.6 | 58.8029 | 22.8825 | 4.7924 | 37.1532
HAMB4B_HEYS | 400 | 71.6256 | 25.5891 | 9.4116 | 45.6 | 58.8029 | 22.8825 | 4.7924 | 37.1532
HAMB4B_PEWO | 400 | 71.6256 | 25.5891 | 9.4116 | 45.6 | 58.8029 | 22.8825 | 4.7924 | 37.1532
HAMH1B | 132 | 46.8521 | 16.2087 | 9.9401 | 32.8627 | 56.0798 | 21.1725 | 6.4121 | 36.3545
HAMH1C | 132 | 45.8521 | 15.975 | 8.6749 | 31.2669 | 54.2841 | 20.2022 | 8.0311 | 36.6013
HAMH4 M1 | 400 | 76.3763 | 28.4762 | 13.524 | 53.7954 | 71.4838 | 27.9328 | 13.7198 | 53.2227
HAMH4 M2 | 400 | 76.3763 | 28.4762 | 13.524 | 53.7954 | 71.4838 | 27.9328 | 13.7198 | 53.2227
HAMH4 R1 | 400 | 76.3763 | 28.4762 | 13.524 | 53.7954 | 71.4838 | 27.9328 | 13.7198 | 53.2227
HAMH4 R2 | 400 | 76.3763 | 28.4762 | 13.524 | 53.7954 | 71.4838 | 27.9328 | 13.7198 | 53.2227
HARK1 M1 | 132 | 28.4578 | 10.9266 | 7.0305 | 22.483 | 33.5495 | 13.2557 | 7.683 | 26.4294
HARK1 M2 | 132 | 28.4578 | 10.9266 | 7.0305 | 22.483 | 33.5495 | 13.2557 | 7.683 | 26.4294
HARK1 R1 | 132 | 26.7005 | 11.0754 | 6.4912 | 22.1543 | 29.8103 | 12.5295 | 7.5434 | 25.2628
HARK1 R2 | 132 | 30.8107 | 11.9556 | 7.7254 | 24.6331 | 36.1547 | 14.4438 | 9.0211 | 29.4476
HARK1 R3 | 132 | 30.8107 | 11.9556 | 7.7254 | 24.6331 | 36.1547 | 14.4438 | 9.0211 | 29.4476
HARK2 MC1 | 275 | 34.978 | 13.2366 | 8.7476 | 27.467 | 37.7156 | 14.4987 | 9.6951 | 30.1993
HARK2 MC11 | 275 | 38.1051 | 14.5842 | 11.5691 | 32.1943 | 42.0561 | 16.3388 | 12.8587 | 35.9653
HARK2 MC12 | 275 | 38.1051 | 14.5842 | 11.5691 | 32.1943 | 42.0561 | 16.3388 | 12.8587 | 35.9653
HARK2 MC13 | 275 | 38.1051 | 14.5842 | 11.5691 | 32.1943 | 42.0561 | 16.3388 | 12.8587 | 35.9653
HARK2 MC2 | 275 | 34.978 | 13.2366 | 8.7476 | 27.467 | 37.7156 | 14.4987 | 9.6951 | 30.1993
HARK2 MC3 | 275 | 34.978 | 13.2366 | 8.7476 | 27.467 | 37.7156 | 14.4987 | 9.6951 | 30.1993
HARK2 MC4 | 275 | 34.978 | 13.2366 | 8.7476 | 27.467 | 37.7156 | 14.4987 | 9.6951 | 30.1993
HARK2 MC6 | 275 | 34.978 | 13.2366 | 8.7476 | 27.467 | 37.7156 | 14.4987 | 9.6951 | 30.1993
HARK2 MC8 | 275 | 38.1051 | 14.5842 | 11.5691 | 32.1943 | 42.0561 | 16.3388 | 12.8587 | 35.9653
HARK2 MC9 | 275 | 38.1051 | 14.5842 | 11.5691 | 32.1943 | 42.0561 | 16.3388 | 12.8587 | 35.9653
HARK4 M1 | 400 | 69.394 | 26.0457 | 12.0607 | 48.8948 | 55.0307 | 21.5256 | 11.6331 | 42.0749
HARK4 M2 | 400 | 69.394 | 26.0457 | 12.0607 | 48.8948 | 55.0307 | 21.5256 | 11.6331 | 42.0749
HARK4 R1 | 400 | 69.394 | 26.0457 | 12.0607 | 48.8948 | 55.0307 | 21.5256 | 11.6331 | 42.0749
HARK4 R2 | 400 | 69.394 | 26.0457 | 12.0607 | 48.8948 | 55.0307 | 21.5256 | 11.6331 | 42.0749
HARM2 MC1 | 275 | 63.3216 | 22.7772 | 13.7388 | 45.9506 | 54.4368 | 21.2602 | 9.0433 | 39.1097
HARM2 MC2 | 275 | 63.3216 | 22.7772 | 13.7388 | 45.9506 | 54.4368 | 21.2602 | 9.0433 | 39.1097
HARM2 MC3 | 275 | 63.3216 | 22.7772 | 13.7388 | 45.9506 | 54.4368 | 21.2602 | 9.0433 | 39.1097
HARM2 MC4 | 275 | 63.3216 | 22.7772 | 13.7388 | 45.9506 | 54.4368 | 21.2602 | 9.0433 | 39.1097
HATL2 M1 | 275 | 87.3945 | 30.2303 | 23.3408 | 66.0929 | 90.4947 | 33.4782 | 24.9194 | 72.2646
HATL2 M2 | 275 | 87.3945 | 30.2303 | 23.3408 | 66.0929 | 90.4947 | 33.4782 | 24.9194 | 72.2646
HATL2 R1 | 275 | 87.3945 | 30.2303 | 23.3408 | 66.0929 | 90.4947 | 33.4782 | 24.9194 | 72.2646
HATL2 R2 | 275 | 87.3945 | 30.2303 | 23.3408 | 66.0929 | 90.4947 | 33.4782 | 24.9194 | 72.2646
HAWP2 MC1 | 275 | 76.0261 | 27.0208 | 17.8296 | 56.0428 | 68.6886 | 26.5772 | 12.6215 | 50.2073
HAWP2 MC2 | 275 | 76.0261 | 27.0208 | 17.8296 | 56.0428 | 68.6886 | 26.5772 | 12.6215 | 50.2073
HAWP2 MC3 | 275 | 76.0261 | 27.0208 | 17.8296 | 56.0428 | 68.6886 | 26.5772 | 12.6215 | 50.2073
HAWP2 MC4 | 275 | 76.0261 | 27.0208 | 17.8296 | 56.0428 | 68.6886 | 26.5772 | 12.6215 | 50.2073
HEDO2 M1 | 275 | 72.7371 | 25.8777 | 21.2677 | 57.8644 | 76.6543 | 28.3804 | 22.942 | 63.0779
HEDO2 M2 | 275 | 72.7371 | 25.8777 | 21.2677 | 57.8644 | 76.6543 | 28.3804 | 22.942 | 63.0779
HEDO2 R1 | 275 | 72.7371 | 25.8777 | 21.2677 | 57.8644 | 76.6543 | 28.3804 | 22.942 | 63.0779
HEDO2 R2 | 275 | 72.7371 | 25.8777 | 21.2677 | 57.8644 | 76.6543 | 28.3804 | 22.942 | 63.0779
HEYS1 M1 | 132 | 38.4284 | 12.9976 | 12.5762 | 30.9575 | 44.3991 | 16.2001 | 14.3101 | 37.2205
HEYS1 M2 | 132 | 38.4284 | 12.9976 | 12.5762 | 30.9575 | 44.3991 | 16.2001 | 14.3101 | 37.2205
HEYS1 R1 | 132 | 38.4284 | 12.9976 | 12.5762 | 30.9575 | 44.3991 | 16.2001 | 14.3101 | 37.2205
HEYS1 R2 | 132 | 38.4284 | 12.9976 | 12.5762 | 30.9575 | 44.3991 | 16.2001 | 14.3101 | 37.2205
HEYS4 M1 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 M2 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 M3 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 M4 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 M5 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 R1/2 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 R3/4 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HEYS4 R5 | 400 | 101.7021 | 36.6355 | 34.5345 | 86.345 | 105.5441 | 39.7636 | 36.3462 | 92.5804
HIBU4 M1 | 400 | 118.4233 | 40.0602 | 28.8481 | 85.5018 | 136.8656 | 50.5987 | 31.3576 | 102.9149
HIBU4 M2 | 400 | 118.4233 | 40.0602 | 28.8481 | 85.5018 | 136.8656 | 50.5987 | 31.3576 | 102.9149
HIBU4 R1 | 400 | 118.4233 | 40.0602 | 28.8481 | 85.5018 | 136.8656 | 50.5987 | 31.3576 | 102.9149
HIBU4 R2 | 400 | 118.4233 | 40.0602 | 28.8481 | 85.5018 | 136.8656 | 50.5987 | 31.3576 | 102.9149
HIGM2 M1 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM2 M2 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM2 M3 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM2 R1 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM2 R4 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM2 R5 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM2 R6 | 275 | 62.3557 | 23.1702 | 16.8274 | 49.595 | 57.9747 | 22.8622 | 12.4942 | 44.8262
HIGM4 MC1 | 400 | 84.4618 | 31.2181 | 19.4414 | 63.5904 | 70.4679 | 27.6957 | 11.8328 | 51.0005
HIGM4 MC2 | 400 | 84.4618 | 31.2181 | 19.4414 | 63.5904 | 70.4679 | 27.6957 | 11.8328 | 51.0005
HIGM4A | 400 | 66.6897 | 24.4456 | 9.915 | 44.4862 | 57.0876 | 22.086 | 5.0619 | 36.2962
HINP2 M1 | 275 | 23.4249 | 8.3721 | 7.8768 | 19.7167 | 25.2219 | 9.2717 | 8.3082 | 21.4204
HINP2 M2 | 275 | 23.7921 | 8.5122 | 7.9216 | 19.9596 | 27.9412 | 10.3206 | 8.7314 | 23.327
HINP4 M1 | 400 | 69.2683 | 25.0878 | 15.7319 | 51.2114 | 68.1578 | 25.8916 | 17.6849 | 54.3011
HINP4 M2 | 400 | 69.2683 | 25.0878 | 15.7319 | 51.2114 | 68.1578 | 25.8916 | 17.6849 | 54.3011
HINP4 M3 | 400 | 69.2683 | 25.0878 | 15.7319 | 51.2114 | 68.1578 | 25.8916 | 17.6849 | 54.3011
HINP4 M4 | 400 | 69.2683 | 25.0878 | 15.7319 | 51.2114 | 68.1578 | 25.8916 | 17.6849 | 54.3011
HINP4 R1/2 | 400 | 69.2683 | 25.0878 | 15.7319 | 51.2114 | 68.1578 | 25.8916 | 17.6849 | 54.3011
HINP4 R3/4 | 400 | 69.2683 | 25.0878 | 15.7319 | 51.2114 | 68.1578 | 25.8916 | 17.6849 | 54.3011
HUMR4 M1 | 400 | 99.837 | 35.2895 | 28.1896 | 78.0965 | 98.1518 | 36.5679 | 27.2161 | 78.9309
HUMR4 M2 | 400 | 99.837 | 35.2895 | 28.1896 | 78.0965 | 98.1518 | 36.5679 | 27.2161 | 78.9309
HUMR4 R1 | 400 | 99.837 | 35.2895 | 28.1896 | 78.0965 | 98.1518 | 36.5679 | 27.2161 | 78.9309
HUMR4 R2 | 400 | 99.837 | 35.2895 | 28.1896 | 78.0965 | 98.1518 | 36.5679 | 27.2161 | 78.9309
HURS2 MC1 | 275 | 70.5296 | 24.6519 | 19.0531 | 53.9161 | 74.5425 | 29.5107 | 16.2914 | 58.0258
HURS2 MC2 | 275 | 70.5296 | 24.6519 | 19.0531 | 53.9161 | 74.5425 | 29.5107 | 16.2914 | 58.0258
HURS2 MC3 | 275 | 70.5296 | 24.6519 | 19.0531 | 53.9161 | 74.5425 | 29.5107 | 16.2914 | 58.0258
HURS2 MC4 | 275 | 70.5296 | 24.6519 | 19.0531 | 53.9161 | 74.5425 | 29.5107 | 16.2914 | 58.0258
HUTT4 MC1 | 400 | 74.2713 | 27.9316 | 21.5647 | 61.0658 | 49.1133 | 19.9096 | 11.4473 | 39.6038
HUTT4 MC2 | 400 | 74.2713 | 27.9316 | 21.5647 | 61.0658 | 49.1133 | 19.9096 | 11.4473 | 39.6038
HUTT4 MC3 | 400 | 74.2713 | 27.9316 | 21.5647 | 61.0658 | 49.1133 | 19.9096 | 11.4473 | 39.6038
HUTT4 MC4 | 400 | 74.2713 | 27.9316 | 21.5647 | 61.0658 | 49.1133 | 19.9096 | 11.4473 | 39.6038
IMPP4 MC1 | 400 | 56.0976 | 20.7886 | 12.6694 | 42.0689 | 47.4296 | 18.3479 | 9.889 | 35.8369
IMPP4 MC2 | 400 | 56.0976 | 20.7886 | 12.6694 | 42.0689 | 47.4296 | 18.3479 | 9.889 | 35.8369
INDQ4 MC1 | 400 | 35.9519 | 13.5162 | 6.0625 | 25.1773 | 37.5908 | 14.6118 | 7.2893 | 27.9535
INDQ4 MC2 | 400 | 35.9519 | 13.5162 | 6.0625 | 25.1773 | 37.5908 | 14.6118 | 7.2893 | 27.9535
INDQ4 MC3 | 400 | 35.9519 | 13.5162 | 6.0625 | 25.1773 | 37.5908 | 14.6118 | 7.2893 | 27.9535
INDQ4 MC4 | 400 | 35.9519 | 13.5162 | 6.0625 | 25.1773 | 37.5908 | 14.6118 | 7.2893 | 27.9535
IROA1 M1 | 132 | 41.006 | 14.8173 | 10.1437 | 31.0985 | 49.5886 | 18.8309 | 11.6124 | 38.2432
IROA1 M2 | 132 | 41.006 | 14.8173 | 10.1437 | 31.0985 | 49.5886 | 18.8309 | 11.6124 | 38.2432
IROA1 R1 | 132 | 43.5289 | 15.6642 | 10.7119 | 32.8645 | 52.4179 | 19.8342 | 12.2963 | 40.3461
IROA1 R2 | 132 | 28.1883 | 10.2121 | 8.4908 | 22.9329 | 34.1002 | 12.7699 | 9.5272 | 27.5867
IROA2 MC1 | 275 | 58.6315 | 21.6599 | 11.1495 | 41.7812 | 56.5972 | 22.0258 | 11.2275 | 42.3767
IROA2 MC2 | 275 | 58.6315 | 21.6599 | 11.1495 | 41.7812 | 56.5972 | 22.0258 | 11.2275 | 42.3767
IROA2 MC3 | 275 | 58.6315 | 21.6599 | 11.1495 | 41.7812 | 56.5972 | 22.0258 | 11.2275 | 42.3767
IROA2 MC4 | 275 | 58.6315 | 21.6599 | 11.1495 | 41.7812 | 56.5972 | 22.0258 | 11.2275 | 42.3767
IROA2 MC5 | 275 | 58.6315 | 21.6599 | 11.1495 | 41.7812 | 56.5972 | 22.0258 | 11.2275 | 42.3767
IRON1 M1 | 132 | 27.3591 | 10.6145 | 8.9654 | 23.9765 | 30.3929 | 11.9229 | 9.96 | 26.8214
IRON1 M2 | 132 | 27.2385 | 10.5716 | 8.8674 | 23.8178 | 30.0656 | 11.8102 | 9.7703 | 26.4724
IRON1 R1 | 132 | 17.894 | 6.5077 | 6.396 | 15.5993 | 20.429 | 7.4678 | 7.3911 | 17.9521
IRON1 R2 | 132 | 17.894 | 6.5077 | 6.396 | 15.5993 | 20.429 | 7.4678 | 7.3911 | 17.9521
IRON4 M1 | 400 | 72.0354 | 26.7996 | 13.3038 | 51.2041 | 60.6249 | 23.9521 | 10.9733 | 44.8468
IRON4 M2 | 400 | 72.0354 | 26.7996 | 13.3038 | 51.2041 | 60.6249 | 23.9521 | 10.9733 | 44.8468
IRON4 R1 | 400 | 72.0354 | 26.7996 | 13.3038 | 51.2041 | 60.6249 | 23.9521 | 10.9733 | 44.8468
IRON4 R2 | 400 | 72.0354 | 26.7996 | 13.3038 | 51.2041 | 60.6249 | 23.9521 | 10.9733 | 44.8468
IVER2 M1 | 275 | 65.9331 | 24.0963 | 16.5351 | 50.6124 | 70.8656 | 27.0162 | 17.0228 | 55.2295
IVER2 M2 | 275 | 65.9331 | 24.0963 | 16.5351 | 50.6124 | 70.8656 | 27.0162 | 17.0228 | 55.2295
IVER2 R1 | 275 | 65.9331 | 24.0963 | 16.5351 | 50.6124 | 70.8656 | 27.0162 | 17.0228 | 55.2295
IVER2 R2 | 275 | 68.1257 | 24.7923 | 15.651 | 50.7125 | 68.5654 | 26.4894 | 14.4147 | 51.8764
IVER4A | 400 | 46.1626 | 17.0042 | 5.7734 | 29.821 | 43.7243 | 16.7681 | 5.9922 | 29.7058
IVER4B | 400 | 44.4075 | 16.4213 | 5.3832 | 28.6064 | 41.5011 | 16.145 | 5.1235 | 27.9559
JORD2 MC1 | 275 | 50.2295 | 18.9929 | 8.8734 | 35.7333 | 49.7399 | 20.5664 | 7.3975 | 36.4827
JORD2 MC2 | 275 | 50.2295 | 18.9929 | 8.8734 | 35.7333 | 49.7399 | 20.5664 | 7.3975 | 36.4827
KEAD4 M2 | 400 | 105.1055 | 37.9324 | 27.305 | 80.9495 | 95.7203 | 36.4341 | 22.6511 | 74.1767
KEAD4 M3 | 400 | 102.9346 | 37.1564 | 27.0418 | 79.5889 | 87.8473 | 33.5893 | 19.3438 | 66.8463
KEAD4 R2 | 400 | 105.1055 | 37.9324 | 27.305 | 80.9495 | 95.7203 | 36.4341 | 22.6511 | 74.1767
KEAD4 R3 | 400 | 98.308 | 35.9574 | 23.0902 | 73.9417 | 77.846 | 30.2442 | 16.5317 | 59.3035
KEAR2 M1 | 275 | 74.7855 | 26.9559 | 19.0558 | 57.1771 | 80.3782 | 30.4292 | 19.757 | 62.7904
KEAR2 M2 | 275 | 74.7855 | 26.9559 | 19.0558 | 57.1771 | 80.3782 | 30.4292 | 19.757 | 62.7904
KEAR2 R1 | 275 | 74.7855 | 26.9559 | 19.0558 | 57.1771 | 80.3782 | 30.4292 | 19.757 | 62.7904
KEAR2 R2 | 275 | 74.7855 | 26.9559 | 19.0558 | 57.1771 | 80.3782 | 30.4292 | 19.757 | 62.7904
KEMS4 M1 | 400 | 128.6613 | 44.1686 | 30.2285 | 92.6923 | 110.7228 | 42.3664 | 22.0502 | 81.9653
KEMS4 M2 | 400 | 128.6613 | 44.1686 | 30.2285 | 92.6923 | 110.7228 | 42.3664 | 22.0502 | 81.9653
KEMS4 R1 | 400 | 128.6613 | 44.1686 | 30.2285 | 92.6923 | 110.7228 | 42.3664 | 22.0502 | 81.9653
KEMS4 R2 | 400 | 128.6613 | 44.1686 | 30.2285 | 92.6923 | 110.7228 | 42.3664 | 22.0502 | 81.9653
KENG4 M1 | 400 | 112.9845 | 38.2569 | 28.3705 | 82.4739 | 131.0438 | 48.4948 | 30.7217 | 99.3037
KENG4 M2 | 400 | 112.9845 | 38.2569 | 28.3705 | 82.4739 | 131.0438 | 48.4948 | 30.7217 | 99.3037
KENG4 R1 | 400 | 112.9845 | 38.2569 | 28.3705 | 82.4739 | 131.0438 | 48.4948 | 30.7217 | 99.3037
KENG4 R2 | 400 | 112.9845 | 38.2569 | 28.3705 | 82.4739 | 131.0438 | 48.4948 | 30.7217 | 99.3037
KIBY2 M1 | 275 | 83.528 | 29.4566 | 21.6459 | 63.3038 | 85.7851 | 32.3856 | 19.4535 | 65.2536
KIBY2 M2 | 275 | 83.528 | 29.4566 | 21.6459 | 63.3038 | 85.7851 | 32.3856 | 19.4535 | 65.2536
KIBY2 R1 | 275 | 72.1386 | 25.8495 | 18.0753 | 54.632 | 68.0266 | 25.8218 | 15.486 | 52.0035
KIBY2 R2 | 275 | 72.1386 | 25.8495 | 18.0753 | 54.632 | 68.0266 | 25.8218 | 15.486 | 52.0035
KILL4 M1 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 M2 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 M3 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 M4 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 M5 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 M9 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 R1/2 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 R3/4 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 R5 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KILL4 R9 | 400 | 105.5987 | 37.851 | 37.7141 | 91.2435 | 107.1782 | 40.0294 | 37.0924 | 93.7026
KINO1 M1 | 132 | 29.069 | 10.239 | 10.5097 | 24.9897 | 35.6215 | 13.1729 | 12.6957 | 31.325
KINO1 M2 | 132 | 29.069 | 10.239 | 10.5097 | 24.9897 | 35.6215 | 13.1729 | 12.6957 | 31.325
KINO1 R1 | 132 | 29.069 | 10.239 | 10.5097 | 24.9897 | 35.6215 | 13.1729 | 12.6957 | 31.325
KINO1 R2 | 132 | 29.069 | 10.239 | 10.5097 | 24.9897 | 35.6215 | 13.1729 | 12.6957 | 31.325
KINO1A | 132 | 28.7294 | 10.0391 | 6.5341 | 20.7316 | 35.1166 | 13.0171 | 7.7236 | 26.1327
KINO1B | 132 | 24.0566 | 8.9525 | 1.6536 | 14.3143 | 25.9468 | 10.461 | 0.94328 | 15.7374
KINO4 M1 | 400 | 123.5962 | 43.8048 | 39.5335 | 101.4829 | 116.2198 | 44.1684 | 35.353 | 97.8166
KINO4 M2 | 400 | 123.5962 | 43.8048 | 39.5335 | 101.4829 | 116.2198 | 44.1684 | 35.353 | 97.8166
KINO4 M3 | 400 | 123.5962 | 43.8048 | 39.5335 | 101.4829 | 116.2198 | 44.1684 | 35.353 | 97.8166
KINO4 M4 | 400 | 123.5962 | 43.8048 | 39.5335 | 101.4829 | 116.2198 | 44.1684 | 35.353 | 97.8166
KINO4 R1/2 | 400 | 123.5962 | 43.8048 | 39.5335 | 101.4829 | 116.2198 | 44.1684 | 35.353 | 97.8166
KINO4 R3/4 | 400 | 123.5962 | 43.8048 | 39.5335 | 101.4829 | 116.2198 | 44.1684 | 35.353 | 97.8166
KIRK2 MC1 | 275 | 53.4319 | 19.467 | 12.0144 | 39.5449 | 54.1322 | 20.8712 | 12.5589 | 42.0752
KIRK2 MC2 | 275 | 53.4319 | 19.467 | 12.0144 | 39.5449 | 54.1322 | 20.8712 | 12.5589 | 42.0752
KIRK2 MC3 | 275 | 53.4319 | 19.467 | 12.0144 | 39.5449 | 54.1322 | 20.8712 | 12.5589 | 42.0752
KIRK2 MC4 | 275 | 53.4319 | 19.467 | 12.0144 | 39.5449 | 54.1322 | 20.8712 | 12.5589 | 42.0752
KIRK2A | 275 | 52.8895 | 18.8042 | 6.3548 | 32.948 | 50.4875 | 19.7861 | 7.6326 | 35.6143
KITW2 MC1 | 275 | 61.7224 | 22.5493 | 12.0442 | 43.9338 | 60.6518 | 23.7054 | 10.5807 | 44.1052
KITW2 MC2 | 275 | 61.7224 | 22.5493 | 12.0442 | 43.9338 | 60.6518 | 23.7054 | 10.5807 | 44.1052
KITW2 MC3 | 275 | 61.7224 | 22.5493 | 12.0442 | 43.9338 | 60.6518 | 23.7054 | 10.5807 | 44.1052
KITW2 MC4 | 275 | 61.7224 | 22.5493 | 12.0442 | 43.9338 | 60.6518 | 23.7054 | 10.5807 | 44.1052
KNAR2 MC1 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
KNAR2 MC1 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
KNAR2 MC1 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
KNAR2 MC1 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
KNAR2 MC2 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
KNAR2 MC2 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
KNAR2 MC2 | 275 | 28.9475 | 11.7077 | 2.4925 | 19.0498 | 26.2473 | 10.8574 | 3.5691 | 18.9238
LACK2 M1 | 275 | 57.1526 | 19.9405 | 14.9627 | 43.1629 | 58.4247 | 21.7652 | 15.1231 | 45.9037
LACK2 M2 | 275 | 57.1526 | 19.9405 | 14.9627 | 43.1629 | 58.4247 | 21.7652 | 15.1231 | 45.9037
LACK2 R1 | 275 | 57.1526 | 19.9405 | 14.9627 | 43.1629 | 58.4247 | 21.7652 | 15.1231 | 45.9037
LACK2 R2 | 275 | 57.1526 | 19.9405 | 14.9627 | 43.1629 | 58.4247 | 21.7652 | 15.1231 | 45.9037
LACK4 M1 | 400 | 71.8558 | 26.4714 | 22.2203 | 59.6565 | 64.7018 | 24.8197 | 19.8252 | 54.9255
LACK4 M2 | 400 | 71.8558 | 26.4714 | 22.2203 | 59.6565 | 64.7018 | 24.8197 | 19.8252 | 54.9255
LACK4 R1 | 400 | 71.8558 | 26.4714 | 22.2203 | 59.6565 | 64.7018 | 24.8197 | 19.8252 | 54.9255
LACK4 R2 | 400 | 71.8558 | 26.4714 | 22.2203 | 59.6565 | 64.7018 | 24.8197 | 19.8252 | 54.9255
LAGA4 M1 | 400 | 42.8441 | 15.7436 | 8.8692 | 31.134 | 44.1242 | 16.9304 | 10.0387 | 33.9819
LAGA4 M2 | 400 | 42.8441 | 15.7436 | 8.8692 | 31.134 | 44.1242 | 16.9304 | 10.0387 | 33.9819
LAGA4 R1 | 400 | 42.8441 | 15.7436 | 8.8692 | 31.134 | 44.1242 | 16.9304 | 10.0387 | 33.9819
LAGA4 R2 | 400 | 42.8441 | 15.7436 | 8.8692 | 31.134 | 44.1242 | 16.9304 | 10.0387 | 33.9819
LALE2 MC1 | 275 | 61.3214 | 21.8424 | 17.5393 | 48.429 | 67.3427 | 26.0045 | 16.724 | 53.4998
LALE2 MC2 | 275 | 61.3214 | 21.8424 | 17.5393 | 48.429 | 67.3427 | 26.0045 | 16.724 | 53.4998
LALE2 MC3 | 275 | 61.3214 | 21.8424 | 17.5393 | 48.429 | 67.3427 | 26.0045 | 16.724 | 53.4998
LALE2 MC4 | 275 | 61.3214 | 21.8424 | 17.5393 | 48.429 | 67.3427 | 26.0045 | 16.724 | 53.4998
LAND4 MC1 | 400 | 34.4119 | 12.8612 | 6.491 | 24.6795 | 33.7261 | 13.19 | 6.1067 | 24.7601
LAND4 MC2 | 400 | 34.4119 | 12.8612 | 6.491 | 24.6795 | 33.7261 | 13.19 | 6.1067 | 24.7601
LEGA4 M1 | 400 | 90.6846 | 32.8525 | 20.2565 | 66.7169 | 69.2059 | 27.3573 | 12.5869 | 51.276
LEGA4 M2 | 400 | 90.6846 | 32.8525 | 20.2565 | 66.7169 | 69.2059 | 27.3573 | 12.5869 | 51.276
LEGA4 R1 | 400 | 90.6846 | 32.8525 | 20.2565 | 66.7169 | 69.2059 | 27.3573 | 12.5869 | 51.276
LEGA4 R2 | 400 | 90.6846 | 32.8525 | 20.2565 | 66.7169 | 69.2059 | 27.3573 | 12.5869 | 51.276
LEIS1 M1 | 132 | 65.073 | 23.0453 | 21.2435 | 53.8344 | 75.2982 | 27.365 | 26.4616 | 65.1615
LEIS1 M2 | 132 | 65.073 | 23.0453 | 21.2435 | 53.8344 | 75.2982 | 27.365 | 26.4616 | 65.1615
LEIS1 R1 | 132 | 65.073 | 23.0453 | 21.2435 | 53.8344 | 75.2982 | 27.365 | 26.4616 | 65.1615
LEIS1 R2 | 132 | 65.073 | 23.0453 | 21.2435 | 53.8344 | 75.2982 | 27.365 | 26.4616 | 65.1615
LISD2 M1 | 275 | 75.7224 | 26.9141 | 18.9971 | 57.0594 | 78.8643 | 30.0497 | 17.5981 | 60.0947
LISD2 M2 | 275 | 75.7224 | 26.9141 | 18.9971 | 57.0594 | 78.8643 | 30.0497 | 17.5981 | 60.0947
LISD2 R1 | 275 | 75.7224 | 26.9141 | 18.9971 | 57.0594 | 78.8643 | 30.0497 | 17.5981 | 60.0947
LISD2 R2 | 275 | 75.7224 | 26.9141 | 18.9971 | 57.0594 | 78.8643 | 30.0497 | 17.5981 | 60.0947
LITB4 Term500 | 400 | 80.3681 | 28.7015 | 9.4735 | 50.0636 | 72.0939 | 27.2259 | 12.2873 | 50.7906
LITT4 M1 | 400 | 125.9532 | 43.2323 | 28.3069 | 89.4466 | 115.4467 | 44.1934 | 23.5159 | 86.0148
LITT4 M2 | 400 | 125.9532 | 43.2323 | 28.3069 | 89.4466 | 115.4467 | 44.1934 | 23.5159 | 86.0148
LITT4 M3 | 400 | 125.9532 | 43.2323 | 28.3069 | 89.4466 | 115.4467 | 44.1934 | 23.5159 | 86.0148
LITT4 R1 | 400 | 125.9532 | 43.2323 | 28.3069 | 89.4466 | 115.4467 | 44.1934 | 23.5159 | 86.0148
LITT4 R2 | 400 | 125.9532 | 43.2323 | 28.3069 | 89.4466 | 115.4467 | 44.1934 | 23.5159 | 86.0148
LITT4 R3 | 400 | 125.9532 | 43.2323 | 28.3069 | 89.4466 | 115.4467 | 44.1934 | 23.5159 | 86.0148
LOFI4A | 400 | 95.7518 | 33.0706 | 7.8564 | 54.6253 | 80.1174 | 31.2461 | 4.022 | 48.2106
LOFI4A_KEMS | 400 | 95.7518 | 33.0706 | 7.8564 | 54.6253 | 80.1174 | 31.2461 | 4.022 | 48.2106
LOFI4A_LITT | 400 | 95.7518 | 33.0706 | 7.8564 | 54.6253 | 80.1174 | 31.2461 | 4.022 | 48.2106
LOFI4A_ROWD | 400 | 95.7518 | 33.0706 | 7.8564 | 54.6253 | 80.1174 | 31.2461 | 4.022 | 48.2106
LOFI4B | 400 | 94.5497 | 32.7901 | 7.5749 | 53.9471 | 80.8512 | 31.568 | 3.9619 | 48.6058
LOFI4B_KEMS | 400 | 94.5497 | 32.7901 | 7.5749 | 53.9471 | 80.8512 | 31.568 | 3.9619 | 48.6058
LOFI4B_LITT | 400 | 94.5497 | 32.7901 | 7.5749 | 53.9471 | 80.8512 | 31.568 | 3.9619 | 48.6058
LOFI4B_ROWD | 400 | 94.5497 | 32.7901 | 7.5749 | 53.9471 | 80.8512 | 31.568 | 3.9619 | 48.6058
LOVE4 M1 | 400 | 90.6833 | 32.6238 | 17.4345 | 63.5715 | 82.1565 | 31.8271 | 15.335 | 60.3453
LOVE4 M2 | 400 | 90.6833 | 32.6238 | 17.4345 | 63.5715 | 82.1565 | 31.8271 | 15.335 | 60.3453
LOVE4 R1 | 400 | 90.6833 | 32.6238 | 17.4345 | 63.5715 | 82.1565 | 31.8271 | 15.335 | 60.3453
LOVE4 R2 | 400 | 90.6833 | 32.6238 | 17.4345 | 63.5715 | 82.1565 | 31.8271 | 15.335 | 60.3453
MACC2 MC1 | 275 | 56.2402 | 20.8303 | 13.7442 | 43.2027 | 52.7744 | 20.384 | 11.8188 | 40.6461
MACC2 MC2 | 275 | 56.2402 | 20.8303 | 13.7442 | 43.2027 | 52.7744 | 20.384 | 11.8188 | 40.6461
MACC4 MC1 | 400 | 81.9723 | 30.97 | 23.1417 | 66.9398 | 62.0261 | 24.8244 | 15.2088 | 50.3158
MACC4 MC2 | 400 | 81.9723 | 30.97 | 23.1417 | 66.9398 | 62.0261 | 24.8244 | 15.2088 | 50.3158
MACC4 MC3 | 400 | 81.9723 | 30.97 | 23.1417 | 66.9398 | 62.0261 | 24.8244 | 15.2088 | 50.3158
MACC4 MC4 | 400 | 81.9723 | 30.97 | 23.1417 | 66.9398 | 62.0261 | 24.8244 | 15.2088 | 50.3158
MAGA2 MC1 | 275 | 57.7069 | 21.2859 | 12.6645 | 42.7674 | 49.0827 | 19.4696 | 8.8111 | 36.3453
MAGA2 MC2 | 275 | 57.7069 | 21.2859 | 12.6645 | 42.7674 | 49.0827 | 19.4696 | 8.8111 | 36.3453
MANN4 M5 | 400 | 55.948 | 20.456 | 10.9072 | 39.8364 | 52.4911 | 20.1332 | 11.3148 | 39.7874
MANN4 MC1 | 400 | 55.948 | 20.456 | 10.9072 | 39.8364 | 52.4911 | 20.1332 | 11.3148 | 39.7874
MANN4 MC2 | 400 | 55.948 | 20.456 | 10.9072 | 39.8364 | 52.4911 | 20.1332 | 11.3148 | 39.7874
MANN4 MC3 | 400 | 55.948 | 20.456 | 10.9072 | 39.8364 | 52.4911 | 20.1332 | 11.3148 | 39.7874
MANN4 MC4 | 400 | 55.948 | 20.456 | 10.9072 | 39.8364 | 52.4911 | 20.1332 | 11.3148 | 39.7874
MANN4 R5 | 400 | 55.948 | 20.456 | 10.9072 | 39.8364 | 52.4911 | 20.1332 | 11.3148 | 39.7874
MAWO4 M | 400 | 60.8076 | 22.1701 | 11.8943 | 43.2476 | 56.7234 | 21.6958 | 12.4587 | 43.1412
MAWO4 R | 400 | 60.8076 | 22.1701 | 11.8943 | 43.2476 | 56.7234 | 21.6958 | 12.4587 | 43.1412
MEDW4 Term500 | 400 | 116.6363 | 40.2962 | 26.8917 | 83.8791 | 106.6296 | 40.2059 | 24.7709 | 81.6306
MELK1 M1 | 132 | 41.9285 | 14.6695 | 14.9202 | 35.6661 | 52.0005 | 19.1065 | 17.4738 | 44.4946
MELK1 M2 | 132 | 41.9285 | 14.6695 | 14.9202 | 35.6661 | 52.0005 | 19.1065 | 17.4738 | 44.4946
MELK1 R1 | 132 | 41.9285 | 14.6695 | 14.9202 | 35.6661 | 52.0005 | 19.1065 | 17.4738 | 44.4946
MELK1 R2 | 132 | 41.9285 | 14.6695 | 14.9202 | 35.6661 | 52.0005 | 19.1065 | 17.4738 | 44.4946
MELK4 M1 | 400 | 108.8281 | 39.9328 | 21.2225 | 77.696 | 89.4549 | 35.3898 | 14.9519 | 65.0007
MELK4 M2 | 400 | 108.8281 | 39.9328 | 21.2225 | 77.696 | 89.4549 | 35.3898 | 14.9519 | 65.0007
MELK4 M3 | 400 | 108.8281 | 39.9328 | 21.2225 | 77.696 | 89.4549 | 35.3898 | 14.9519 | 65.0007
MELK4 R1 | 400 | 108.8281 | 39.9328 | 21.2225 | 77.696 | 89.4549 | 35.3898 | 14.9519 | 65.0007
MELK4 R2 | 400 | 108.8281 | 39.9328 | 21.2225 | 77.696 | 89.4549 | 35.3898 | 14.9519 | 65.0007
MELK4 R3 | 400 | 108.8281 | 39.9328 | 21.2225 | 77.696 | 89.4549 | 35.3898 | 14.9519 | 65.0007
MILH1 M1 | 132 | 39.383 | 14.5241 | 9.0439 | 29.5841 | 45.6203 | 18.4476 | 9.0301 | 35.1189
MILH1 M2 | 132 | 39.383 | 14.5241 | 9.0439 | 29.5841 | 45.6203 | 18.4476 | 9.0301 | 35.1189
MILH1 R1 | 132 | 39.4151 | 14.551 | 8.9409 | 29.5191 | 45.5083 | 18.4562 | 8.7942 | 34.8953
MILH1 R2 | 132 | 39.4151 | 14.551 | 8.9409 | 29.5191 | 45.5083 | 18.4562 | 8.7942 | 34.8953
MITY4 MC1 | 400 | 82.3167 | 31.4415 | 21.8348 | 66.2998 | 61.9705 | 25.075 | 14.4133 | 49.8747
MITY4 MC2 | 400 | 82.3167 | 31.4415 | 21.8348 | 66.2998 | 61.9705 | 25.075 | 14.4133 | 49.8747
MITY4 MC3 | 400 | 82.3167 | 31.4415 | 21.8348 | 66.2998 | 61.9705 | 25.075 | 14.4133 | 49.8747
MITY4 MC4 | 400 | 82.3167 | 31.4415 | 21.8348 | 66.2998 | 61.9705 | 25.075 | 14.4133 | 49.8747
MONF2 M1 | 275 | 65.4952 | 23.7934 | 17.6365 | 51.2854 | 66.3476 | 25.2536 | 16.207 | 51.9209
MONF2 M2 | 275 | 65.4952 | 23.7934 | 17.6365 | 51.2854 | 66.3476 | 25.2536 | 16.207 | 51.9209
MONF2 R1 | 275 | 56.8633 | 20.6872 | 18.1268 | 47.3829 | 59.6501 | 22.4368 | 17.3809 | 49.1113
MONF2 R2 | 275 | 56.8633 | 20.6872 | 18.1268 | 47.3829 | 59.6501 | 22.4368 | 17.3809 | 49.1113
MONF4 MC2 | 400 | 80.0712 | 29.1894 | 19.0281 | 60.3081 | 70.3539 | 26.9576 | 15.6969 | 53.8207
MONF4 MC3 | 400 | 80.0712 | 29.1894 | 19.0281 | 60.3081 | 70.3539 | 26.9576 | 15.6969 | 53.8207
NECH2 MC1 | 275 | 73.0893 | 26.3574 | 18.7028 | 55.9778 | 73.8922 | 28.4534 | 16.1487 | 56.3879
NECH2 MC2 | 275 | 73.0893 | 26.3574 | 18.7028 | 55.9778 | 73.8922 | 28.4534 | 16.1487 | 56.3879
NECH2 MC3 | 275 | 73.0893 | 26.3574 | 18.7028 | 55.9778 | 73.8922 | 28.4534 | 16.1487 | 56.3879
NECH2 MC4 | 275 | 73.0893 | 26.3574 | 18.7028 | 55.9778 | 73.8922 | 28.4534 | 16.1487 | 56.3879
NECT4 M1 | 400 | 74.563 | 27.4867 | 17.5989 | 56.4709 | 54.5524 | 21.6258 | 10.9028 | 41.4863
NECT4 R1 | 400 | 74.563 | 27.4867 | 17.5989 | 56.4709 | 54.5524 | 21.6258 | 10.9028 | 41.4863
NEEP2 M1 | 275 | 59.3635 | 21.9907 | 12.8031 | 43.9026 | 62.5234 | 24.9051 | 12.0721 | 47.2932
NEEP2 M2 | 275 | 59.3635 | 21.9907 | 12.8031 | 43.9026 | 62.5234 | 24.9051 | 12.0721 | 47.2932
NEEP2 R1/R2 | 275 | 59.3635 | 21.9907 | 12.8031 | 43.9026 | 62.5234 | 24.9051 | 12.0721 | 47.2932
NEWX2 M5 | 275 | 76.7894 | 26.6406 | 19.6579 | 57.3333 | 85.1319 | 33.175 | 17.5682 | 64.4847
NEWX2 M5 | 275 | 76.7894 | 26.6406 | 19.6579 | 57.3333 | 85.1319 | 33.175 | 17.5682 | 64.4847
NEWX2 M6 | 275 | 76.7894 | 26.6406 | 19.6579 | 57.3333 | 85.1319 | 33.175 | 17.5682 | 64.4847
NEWX2 R6 | 275 | 76.7894 | 26.6406 | 19.6579 | 57.3333 | 85.1319 | 33.175 | 17.5682 | 64.4847
NEWX21 R5 | 275 | 76.7894 | 26.6406 | 19.6579 | 57.3333 | 85.1319 | 33.175 | 17.5682 | 64.4847
NFLE4 M1 | 400 | 106.2741 | 37.0662 | 23.3812 | 75.8007 | 86.1935 | 33.6348 | 15.3601 | 62.9269
NFLE4 M2 | 400 | 106.2741 | 37.0662 | 23.3812 | 75.8007 | 86.1935 | 33.6348 | 15.3601 | 62.9269
NFLE4 R1 | 400 | 106.2741 | 37.0662 | 23.3812 | 75.8007 | 86.1935 | 33.6348 | 15.3601 | 62.9269
NFLE4 R2 | 400 | 106.2741 | 37.0662 | 23.3812 | 75.8007 | 86.1935 | 33.6348 | 15.3601 | 62.9269
NHYD2A | 275 | 45.7198 | 17.3925 | 2.6169 | 27.2137 | 39.3346 | 18.5842 | 0.47383 | 26.7558
NHYD2B | 275 | 46.8024 | 17.689 | 2.3334 | 27.3495 | 40.3015 | 18.4875 | 1.0754 | 27.2206
NHYD2C | 275 | 46.8024 | 17.689 | 2.3334 | 27.3495 | 40.3015 | 18.4875 | 1.0754 | 27.2206
NINF4 M1 | 400 | 65.2926 | 23.6472 | 14.4516 | 47.8937 | 56.8848 | 21.8916 | 12.5536 | 43.513
NINF4 M2 | 400 | 65.2926 | 23.6472 | 14.4516 | 47.8937 | 56.8848 | 21.8916 | 12.5536 | 43.513
NINF4 R1 | 400 | 65.2926 | 23.6472 | 14.4516 | 47.8937 | 56.8848 | 21.8916 | 12.5536 | 43.513
NINF4 R2 | 400 | 65.2926 | 23.6472 | 14.4516 | 47.8937 | 56.8848 | 21.8916 | 12.5536 | 43.513
NORL2A | 275 | 51.8731 | 19.1695 | 3.9492 | 31.059 | 51.3285 | 21.1442 | 2.2982 | 32.2006
NORL2B | 275 | 51.0556 | 18.9425 | 3.4364 | 30.2251 | 50.4671 | 21.0787 | 2.0303 | 31.8401
NORM4 M1 | 400 | 70.0264 | 25.9169 | 15.5793 | 52.2314 | 53.1684 | 20.9602 | 11.3093 | 40.9515
NORM4 M2 | 400 | 70.0264 | 25.9169 | 15.5793 | 52.2314 | 53.1684 | 20.9602 | 11.3093 | 40.9515
NORM4 R1 | 400 | 70.0264 | 25.9169 | 15.5793 | 52.2314 | 53.1684 | 20.9602 | 11.3093 | 40.9515
NORM4 R2 | 400 | 70.0264 | 25.9169 | 15.5793 | 52.2314 | 53.1684 | 20.9602 | 11.3093 | 40.9515
NORT2 M1 | 275 | 82.8378 | 28.9809 | 22.3583 | 63.3435 | 83.675 | 31.5601 | 19.1483 | 63.7809
NORT2 M2 | 275 | 82.8378 | 28.9809 | 22.3583 | 63.3435 | 83.675 | 31.5601 | 19.1483 | 63.7809
NORT2 R1 | 275 | 82.8378 | 28.9809 | 22.3583 | 63.3435 | 83.675 | 31.5601 | 19.1483 | 63.7809
NORT2 R2 | 275 | 82.8378 | 28.9809 | 22.3583 | 63.3435 | 83.675 | 31.5601 | 19.1483 | 63.7809
NORT4 M1 | 400 | 88.2033 | 32.0315 | 27.7904 | 73.0898 | 75.4546 | 29.1481 | 21.5176 | 62.7393
NORT4 M2 | 400 | 88.2033 | 32.0315 | 27.7904 | 73.0898 | 75.4546 | 29.1481 | 21.5176 | 62.7393
NORT4 R1 | 400 | 88.2033 | 32.0315 | 27.7904 | 73.0898 | 75.4546 | 29.1481 | 21.5176 | 62.7393
NORT4 R2 | 400 | 88.2033 | 32.0315 | 27.7904 | 73.0898 | 75.4546 | 29.1481 | 21.5176 | 62.7393
NURS4 MC1 | 400 | 58.1231 | 21.0008 | 7.5651 | 37.2648 | 54.9774 | 20.9312 | 8.1115 | 37.7127
NURS4 MC2 | 400 | 58.1231 | 21.0008 | 7.5651 | 37.2648 | 54.9774 | 20.9312 | 8.1115 | 37.7127
NURS4A | 400 | 51.1401 | 18.8414 | 10.3021 | 36.9479 | 48.1029 | 18.413 | 10.5655 | 36.6054
OCKH1 M1 | 132 | 25.0214 | 8.9539 | 8.5765 | 21.2392 | 33.647 | 12.3341 | 11.2296 | 28.6726
OCKH1 M2 | 132 | 25.0214 | 8.9539 | 8.5765 | 21.2392 | 33.647 | 12.3341 | 11.2296 | 28.6726
OCKH1 R1 | 132 | 25.0214 | 8.9539 | 8.5765 | 21.2392 | 33.647 | 12.3341 | 11.2296 | 28.6726
OCKH1 R2 | 132 | 25.0214 | 8.9539 | 8.5765 | 21.2392 | 33.647 | 12.3341 | 11.2296 | 28.6726
OCKH2 MC1 | 275 | 55.241 | 20.2969 | 10.6588 | 39.363 | 57.2566 | 22.3753 | 10.8056 | 42.449
OCKH2 MC2 | 275 | 55.241 | 20.2969 | 10.6588 | 39.363 | 57.2566 | 22.3753 | 10.8056 | 42.449
OCKH2 MC3 | 275 | 55.241 | 20.2969 | 10.6588 | 39.363 | 57.2566 | 22.3753 | 10.8056 | 42.449
OCKH2 MC4 | 275 | 55.241 | 20.2969 | 10.6588 | 39.363 | 57.2566 | 22.3753 | 10.8056 | 42.449
OCKH2A | 275 | 48.7776 | 17.6078 | 4.3293 | 29.2304 | 48.98 | 18.9367 | 4.7371 | 31.5176
OFFE2 MC1 | 275 | 67.6427 | 24.4964 | 13.0464 | 47.6895 | 58.4037 | 23.2739 | 8.1657 | 41.08
OFFE2 MC2 | 275 | 67.6427 | 24.4964 | 13.0464 | 47.6895 | 58.4037 | 23.2739 | 8.1657 | 41.08
OLDB2 MC1 | 275 | 53.0566 | 19.5932 | 10.7026 | 38.4116 | 54.7383 | 21.2108 | 10.8845 | 40.8811
OLDB2 MC2 | 275 | 53.0566 | 19.5932 | 10.7026 | 38.4116 | 54.7383 | 21.2108 | 10.8845 | 40.8811
OSBA4 MC1 | 400 | 56.1018 | 20.7716 | 12.7281 | 42.1035 | 50.3953 | 19.2709 | 12.1513 | 39.4045
OSBA4 MC2 | 400 | 56.1018 | 20.7716 | 12.7281 | 42.1035 | 50.3953 | 19.2709 | 12.1513 | 39.4045
OSBA4 MC3/4 | 400 | 54.8638 | 20.3012 | 12.6482 | 41.3584 | 44.237 | 17.1316 | 9.4511 | 33.6789
PADI1 M1 | 132 | 29.7328 | 10.4492 | 10.4574 | 25.2347 | 36.9199 | 13.5287 | 12.6731 | 31.8055
PADI1 M2 | 132 | 29.7328 | 10.4492 | 10.4574 | 25.2347 | 36.9199 | 13.5287 | 12.6731 | 31.8055
PADI1 R1 | 132 | 29.7328 | 10.4492 | 10.4574 | 25.2347 | 36.9199 | 13.5287 | 12.6731 | 31.8055
PADI1 R2 | 132 | 29.7328 | 10.4492 | 10.4574 | 25.2347 | 36.9199 | 13.5287 | 12.6731 | 31.8055
PADI4 MC1 | 400 | 75.5357 | 27.8303 | 15.993 | 55.351 | 57.0083 | 22.5585 | 9.8245 | 41.7271
PADI4 MC2 | 400 | 75.5357 | 27.8303 | 15.993 | 55.351 | 57.0083 | 22.5585 | 9.8245 | 41.7271
PADI4 MC3 | 400 | 75.5357 | 27.8303 | 15.993 | 55.351 | 57.0083 | 22.5585 | 9.8245 | 41.7271
PADI4 MC4 | 400 | 75.5357 | 27.8303 | 15.993 | 55.351 | 57.0083 | 22.5585 | 9.8245 | 41.7271
PELH4 M1 | 400 | 139.7483 | 49.5292 | 33.7002 | 103.7452 | 114.1389 | 44.1469 | 22.3042 | 84.7374
PELH4 M2 | 400 | 139.7483 | 49.5292 | 33.7002 | 103.7452 | 114.1389 | 44.1469 | 22.3042 | 84.7374
PELH4 R1 | 400 | 139.7483 | 49.5292 | 33.7002 | 103.7452 | 114.1389 | 44.1469 | 22.3042 | 84.7374
PELH4 R2 | 400 | 139.7483 | 49.5292 | 33.7002 | 103.7452 | 114.1389 | 44.1469 | 22.3042 | 84.7374
PEMB4 M1 | 400 | 62.0869 | 21.9077 | 18.68 | 49.6621 | 66.0177 | 24.251 | 20.9918 | 55.2879
PEMB4 M2 | 400 | 62.0869 | 21.9077 | 18.68 | 49.6621 | 66.0177 | 24.251 | 20.9918 | 55.2879
PEMB4 M3 | 400 | 62.0869 | 21.9077 | 18.68 | 49.6621 | 66.0177 | 24.251 | 20.9918 | 55.2879
PEMB4 M4 | 400 | 62.0869 | 21.9077 | 18.68 | 49.6621 | 66.0177 | 24.251 | 20.9918 | 55.2879
PEMB4 R1/2 | 400 | 62.0869 | 21.9077 | 18.68 | 49.6621 | 66.0177 | 24.251 | 20.9918 | 55.2879
PEMB4 R3/4 | 400 | 62.0869 | 21.9077 | 18.68 | 49.6621 | 66.0177 | 24.251 | 20.9918 | 55.2879
PENN2 MC1 | 275 | 66.1921 | 24.1514 | 14.0333 | 48.1886 | 69.5089 | 26.6703 | 14.8119 | 52.5294
PENN2 MC2 | 275 | 66.1921 | 24.1514 | 14.0333 | 48.1886 | 69.5089 | 26.6703 | 14.8119 | 52.5294
PENN2 MC3 | 275 | 66.1921 | 24.1514 | 14.0333 | 48.1886 | 69.5089 | 26.6703 | 14.8119 | 52.5294
PENN2 MC4 | 275 | 66.1921 | 24.1514 | 14.0333 | 48.1886 | 69.5089 | 26.6703 | 14.8119 | 52.5294
PENT4 M1 | 400 | 75.4236 | 26.4129 | 20.9041 | 58.2576 | 76.3361 | 28.4082 | 20.5107 | 60.6859
PENT4 M2 | 400 | 75.4236 | 26.4129 | 20.9041 | 58.2576 | 76.3361 | 28.4082 | 20.5107 | 60.6859
PENT4 R1 | 400 | 75.4236 | 26.4129 | 20.9041 | 58.2576 | 76.3361 | 28.4082 | 20.5107 | 60.6859
PENT4 R2 | 400 | 75.4236 | 26.4129 | 20.9041 | 58.2576 | 76.3361 | 28.4082 | 20.5107 | 60.6859
PEWO2A | 275 | 69.249 | 24.9817 | 20.8801 | 56.2095 | 70.631 | 26.4451 | 19.9858 | 57.3848
PEWO2B | 275 | 70.2127 | 25.6494 | 25.389 | 61.6628 | 71.5637 | 26.9005 | 25.1168 | 63.1598
PEWO4 M1 | 400 | 104.7727 | 38.2124 | 33.5683 | 87.6088 | 93.8218 | 36.3214 | 27.6994 | 79.0657
PEWO4 M2 | 400 | 104.7727 | 38.2124 | 33.5683 | 87.6088 | 93.8218 | 36.3214 | 27.6994 | 79.0657
PEWO4 M3 | 400 | 104.7727 | 38.2124 | 33.5683 | 87.6088 | 93.8218 | 36.3214 | 27.6994 | 79.0657
PEWO4 M4 | 400 | 104.7727 | 38.2124 | 33.5683 | 87.6088 | 93.8218 | 36.3214 | 27.6994 | 79.0657
PEWO4 R1/2 | 400 | 104.7727 | 38.2124 | 33.5683 | 87.6088 | 93.8218 | 36.3214 | 27.6994 | 79.0657
PEWO4 R3/4 | 400 | 104.7727 | 38.2124 | 33.5683 | 87.6088 | 93.8218 | 36.3214 | 27.6994 | 79.0657
PITS2 MC1 | 275 | 61.0088 | 22.2928 | 8.6098 | 40.1366 | 65.8701 | 25.8941 | 7.6253 | 44.2451
PITS2 MC2 | 275 | 61.0088 | 22.2928 | 8.6098 | 40.1366 | 65.8701 | 25.8941 | 7.6253 | 44.2451
PITS2 MC3 | 275 | 61.0088 | 22.2928 | 8.6098 | 40.1366 | 65.8701 | 25.8941 | 7.6253 | 44.2451
PITS2 MC4 | 275 | 61.0088 | 22.2928 | 8.6098 | 40.1366 | 65.8701 | 25.8941 | 7.6253 | 44.2451
POPP2 MC1 | 275 | 26.9943 | 10.8194 | 2.8174 | 18.1183 | 22.84 | 9.4184 | 3.0946 | 16.4142
POPP2 MC2 | 275 | 26.9943 | 10.8194 | 2.8174 | 18.1183 | 22.84 | 9.4184 | 3.0946 | 16.4142
PUDM4 MC1 | 400 | 102.0937 | 35.1838 | 24.1267 | 73.8842 | 105.9793 | 41.7901 | 20.0998 | 79.1999
PUDM4 MC2 | 400 | 102.0937 | 35.1838 | 24.1267 | 73.8842 | 105.9793 | 41.7901 | 20.0998 | 79.1999
PYLE2 MC1 | 275 | 62.0499 | 22.9748 | 12.7255 | 45.2167 | 53.2461 | 21.1169 | 9.7156 | 39.5794
PYLE2 MC2 | 275 | 62.1093 | 22.9955 | 12.7409 | 45.2614 | 53.2943 | 21.134 | 9.7339 | 39.6219
QUER4A | 400 | 86.066 | 30.3291 | 12.5885 | 55.4803 | 73.8323 | 28.5656 | 5.6772 | 46.075
QUER4A_HEYS | 400 | 86.066 | 30.3291 | 12.5885 | 55.4803 | 73.8323 | 28.5656 | 5.6772 | 46.075
QUER4A_HUTT | 400 | 86.066 | 30.3291 | 12.5885 | 55.4803 | 73.8323 | 28.5656 | 5.6772 | 46.075
QUER4A_PEWO | 400 | 86.066 | 30.3291 | 12.5885 | 55.4803 | 73.8323 | 28.5656 | 5.6772 | 46.075
QUER4B | 400 | 86.9676 | 30.5993 | 12.9005 | 56.1743 | 75.9595 | 29.2661 | 6.3351 | 47.7237
QUER4B_HEYS | 400 | 86.9676 | 30.5993 | 12.9005 | 56.1743 | 75.9595 | 29.2661 | 6.3351 | 47.7237
QUER4B_HUTT | 400 | 86.9676 | 30.5993 | 12.9005 | 56.1743 | 75.9595 | 29.2661 | 6.3351 | 47.7237
QUER4B_PEWO | 400 | 86.9676 | 30.5993 | 12.9005 | 56.1743 | 75.9595 | 29.2661 | 6.3351 | 47.7237
RAIN2 MC1 | 275 | 96.7807 | 33.5405 | 27.3283 | 74.7618 | 95.0089 | 35.6202 | 21.858 | 72.2326
RAIN2 MC2 | 275 | 96.7807 | 33.5405 | 27.3283 | 74.7618 | 95.0089 | 35.6202 | 21.858 | 72.2326
RAIN2 MC3 | 275 | 96.7807 | 33.5405 | 27.3283 | 74.7618 | 95.0089 | 35.6202 | 21.858 | 72.2326
RAIN2 MC4 | 275 | 96.7807 | 33.5405 | 27.3283 | 74.7618 | 95.0089 | 35.6202 | 21.858 | 72.2326
RASS4 M1 | 400 | 54.6851 | 20.4752 | 16.8968 | 45.8531 | 43.8745 | 17.2118 | 11.8912 | 36.2324
RASS4 M2 | 400 | 54.6851 | 20.4752 | 16.8968 | 45.8531 | 43.8745 | 17.2118 | 11.8912 | 36.2324
RATS1 M1 | 132 | 43.8575 | 15.4751 | 14.288 | 36.1731 | 49.3439 | 18.337 | 16.5468 | 42.4792
RATS1 M2 | 132 | 43.8575 | 15.4751 | 14.288 | 36.1731 | 49.3439 | 18.337 | 16.5468 | 42.4792
RATS1 R1 | 132 | 40.5839 | 14.43 | 13.1391 | 33.5461 | 45.3327 | 16.9721 | 14.0569 | 38.059
RATS1 R2 | 132 | 40.5839 | 14.43 | 13.1391 | 33.5461 | 45.3327 | 16.9721 | 14.0569 | 38.059
RATS2A | 275 | 43.8139 | 15.8548 | 10.5263 | 32.9483 | 46.6352 | 16.8656 | 20.6754 | 44.5269
RATS4 M1 | 400 | 140.7552 | 50.2105 | 31.3715 | 102.3799 | 138.1087 | 52.4553 | 34.5337 | 108.7167
RATS4 M2 | 400 | 140.7552 | 50.2105 | 31.3715 | 102.3799 | 138.1087 | 52.4553 | 34.5337 | 108.7167
RATS4 M3 | 400 | 140.7552 | 50.2105 | 31.3715 | 102.3799 | 138.1087 | 52.4553 | 34.5337 | 108.7167
RATS4 M4 | 400 | 140.7552 | 50.2105 | 31.3715 | 102.3799 | 138.1087 | 52.4553 | 34.5337 | 108.7167
RATS4 R1/2 | 400 | 140.7552 | 50.2105 | 31.3715 | 102.3799 | 138.1087 | 52.4553 | 34.5337 | 108.7167
RATS4 R3/4 | 400 | 140.7552 | 50.2105 | 31.3715 | 102.3799 | 138.1087 | 52.4553 | 34.5337 | 108.7167
RAYL4 M1 | 400 | 103.704 | 37.8341 | 31.343 | 84.8485 | 83.0963 | 32.512 | 22.9553 | 68.9341
RAYL4 M2 | 400 | 103.704 | 37.8341 | 31.343 | 84.8485 | 83.0963 | 32.512 | 22.9553 | 68.9341
RAYL4 R1 | 400 | 103.704 | 37.8341 | 31.343 | 84.8485 | 83.0963 | 32.512 | 22.9553 | 68.9341
RAYL4 R2 | 400 | 103.704 | 37.8341 | 31.343 | 84.8485 | 83.0963 | 32.512 | 22.9553 | 68.9341
REBR2 MC1 | 275 | 66.4554 | 24.3991 | 21.9122 | 56.4177 | 63.5993 | 24.8636 | 17.6537 | 52.8161
REBR2 MC2 | 275 | 64.387 | 23.6478 | 21.42 | 54.863 | 63.2609 | 24.8621 | 17.2641 | 52.4245
REBR2 MC3 | 275 | 64.387 | 23.6478 | 21.42 | 54.863 | 63.2609 | 24.8621 | 17.2641 | 52.4245
REBR2 MC4 | 275 | 66.4554 | 24.3991 | 21.9122 | 56.4177 | 63.5993 | 24.8636 | 17.6537 | 52.8161
RHIG4 M1 | 400 | 56.4455 | 20.6802 | 13.5259 | 42.7721 | 49.076 | 18.9703 | 9.9322 | 36.7603
RHIG4 R1 | 400 | 56.4455 | 20.6802 | 13.5259 | 42.7721 | 49.076 | 18.9703 | 9.9322 | 36.7603
ROCH2 MC1 | 275 | 71.3141 | 25.9504 | 9.6727 | 46.3722 | 67.9301 | 26.3721 | 9.3265 | 46.6222
ROCH2 MC2 | 275 | 71.3141 | 25.9504 | 9.6727 | 46.3722 | 67.9301 | 26.3721 | 9.3265 | 46.6222
ROCH2 MC3 | 275 | 71.3141 | 25.9504 | 9.6727 | 46.3722 | 67.9301 | 26.3721 | 9.3265 | 46.6222
ROCH2 MC4 | 275 | 71.3141 | 25.9504 | 9.6727 | 46.3722 | 67.9301 | 26.3721 | 9.3265 | 46.6222
ROCK1A | 132 | 46.7201 | 16.1023 | 16.832 | 39.604 | 48.7105 | 17.5895 | 16.3567 | 41.2321
ROCK4 Term900 | 400 | 90.156 | 31.8789 | 24.1873 | 69.2708 | 84.8519 | 31.6849 | 23.0996 | 67.9087
RUGE4 M1 | 400 | 65.4384 | 24.7416 | 10.308 | 45.2979 | 51.0192 | 20.6213 | 7.0881 | 36.2511
RUGE4 M2 | 400 | 65.4384 | 24.7416 | 10.308 | 45.2979 | 51.0192 | 20.6213 | 7.0881 | 36.2511
RUGE4 R1 | 400 | 65.4384 | 24.7416 | 10.308 | 45.2979 | 51.0192 | 20.6213 | 7.0881 | 36.2511
RUGE4 R2 | 400 | 65.4384 | 24.7416 | 10.308 | 45.2979 | 51.0192 | 20.6213 | 7.0881 | 36.2511
RYEH4 M1 | 400 | 79.6853 | 28.5618 | 20.968 | 61.3605 | 80.5003 | 30.1192 | 22.0126 | 64.6075
RYEH4 R1 | 400 | 79.6853 | 28.5618 | 20.968 | 61.3605 | 80.5003 | 30.1192 | 22.0126 | 64.6075
RYHA41 MC1 | 400 | 44.2531 | 16.6483 | 9.6245 | 33.1688 | 28.7926 | 11.4942 | 4.1066 | 20.3618
RYHA4B_LOAD2 | 400 | 44.928 | 16.9092 | 9.7951 | 33.7083 | 30.7025 | 12.2595 | 4.3254 | 21.663
SAEN2 MC1 | 275 | 72.8111 | 25.8954 | 21.3175 | 57.9391 | 76.9074 | 28.4608 | 23.13 | 63.3797
SAEN2 MC2 | 275 | 72.8111 | 25.8954 | 21.3175 | 57.9391 | 76.9074 | 28.4608 | 23.13 | 63.3797
SAES2 M | 275 | 73.3654 | 26.0601 | 21.6012 | 58.4558 | 77.7914 | 28.7346 | 23.8771 | 64.5139
SAES2 R | 275 | 73.3654 | 26.0601 | 21.6012 | 58.4558 | 77.7914 | 28.7346 | 23.8771 | 64.5139
SALH2 MC1 | 275 | 75.0488 | 26.5774 | 17.9093 | 55.4954 | 73.5992 | 27.965 | 15.1894 | 54.7379
SALH2 MC2 | 275 | 75.0488 | 26.5774 | 17.9093 | 55.4954 | 73.5992 | 27.965 | 15.1894 | 54.7379
SEAB4 M1 | 400 | 63.409 | 23.3127 | 20.7838 | 53.753 | 64.9322 | 24.5033 | 21.9041 | 56.5569
SEAB4 M2 | 400 | 63.409 | 23.3127 | 20.7838 | 53.753 | 64.9322 | 24.5033 | 21.9041 | 56.5569
SEAB4 R1 | 400 | 63.409 | 23.3127 | 20.7838 | 53.753 | 64.9322 | 24.5033 | 21.9041 | 56.5569
SEAB4 R2 | 400 | 63.409 | 23.3127 | 20.7838 | 53.753 | 64.9322 | 24.5033 | 21.9041 | 56.5569
SELL4 M1 | 400 | 79.9428 | 29.0292 | 17.0016 | 58.0551 | 70.2248 | 26.9072 | 16.3789 | 54.4314
SELL4 M2 | 400 | 79.9428 | 29.0292 | 17.0016 | 58.0551 | 70.2248 | 26.9072 | 16.3789 | 54.4314
SELL4 R1 | 400 | 79.9428 | 29.0292 | 17.0016 | 58.0551 | 70.2248 | 26.9072 | 16.3789 | 54.4314
SELL4 R2 | 400 | 79.9428 | 29.0292 | 17.0016 | 58.0551 | 70.2248 | 26.9072 | 16.3789 | 54.4314
SELL4A | 400 | 79.863 | 28.3447 | 7.8207 | 47.9061 | 70.1553 | 26.7047 | 9.045 | 46.8111
SELL4B | 400 | 79.8628 | 28.3446 | 7.8207 | 47.906 | 70.1552 | 26.7046 | 9.0449 | 46.811
SELW4 M3 | 400 | 79.7509 | 28.9648 | 16.9506 | 57.913 | 69.8195 | 26.7712 | 16.1562 | 54.0164
SELW4 M4 | 400 | 79.7509 | 28.9648 | 16.9506 | 57.913 | 69.8195 | 26.7712 | 16.1562 | 54.0164
SELW4 R3 | 400 | 79.7509 | 28.9648 | 16.9506 | 57.913 | 69.8195 | 26.7712 | 16.1562 | 54.0164
SELW4 R4 | 400 | 79.7509 | 28.9648 | 16.9506 | 57.913 | 69.8195 | 26.7712 | 16.1562 | 54.0164
SETW4A | 400 | 79.7728 | 28.3148 | 7.809 | 47.8521 | 70.0986 | 26.6861 | 9.0158 | 46.7557
SETW4B | 400 | 79.7728 | 28.3147 | 7.8089 | 47.852 | 70.0984 | 26.6861 | 9.0157 | 46.7556
SHBA4 M1 | 400 | 82.2831 | 29.7148 | 29.4198 | 71.4429 | 81.4167 | 30.5109 | 28.4041 | 71.553
SHBA4 M2 | 400 | 82.2831 | 29.7148 | 29.4198 | 71.4429 | 81.4167 | 30.5109 | 28.4041 | 71.553
SHBA4 R1 | 400 | 82.2831 | 29.7148 | 29.4198 | 71.4429 | 81.4167 | 30.5109 | 28.4041 | 71.553
SHBA4 R2 | 400 | 82.2831 | 29.7148 | 29.4198 | 71.4429 | 81.4167 | 30.5109 | 28.4041 | 71.553
SHEC2 MC1 | 275 | 53.9118 | 20.2063 | 10.4153 | 38.9913 | 54.7236 | 22.5704 | 7.5191 | 39.4384
SHEC2 MC2 | 275 | 53.9118 | 20.2063 | 10.4153 | 38.9913 | 54.7236 | 22.5704 | 7.5191 | 39.4384
SHRE4B | 400 | 56.1387 | 21.09 | 10.5412 | 40.367 | 44.2849 | 17.6469 | 7.2589 | 32.2155
SING4 MC1 | 400 | 95.1216 | 33.5382 | 20.9414 | 68.3716 | 77.4907 | 30.2428 | 13.1599 | 55.9297
SING4 MC2 | 400 | 95.1216 | 33.5382 | 20.9414 | 68.3716 | 77.4907 | 30.2428 | 13.1599 | 55.9297
SIZE4 M1 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 M2 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 M3 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 M4 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 R1 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 R2 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 R3 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SIZE4 R4 | 400 | 70.816 | 25.3915 | 18.2048 | 54.1138 | 76.2696 | 28.284 | 21.9067 | 61.9063
SJOW2 MC1 | 275 | 86.1756 | 30.5966 | 22.9872 | 66.2573 | 94.5018 | 36.1668 | 26.3509 | 77.4984
SJOW2 MC2 | 275 | 86.1756 | 30.5966 | 22.9872 | 66.2573 | 94.5018 | 36.1668 | 26.3509 | 77.4984
SJOW2 MC3 | 275 | 86.1756 | 30.5966 | 22.9872 | 66.2573 | 94.5018 | 36.1668 | 26.3509 | 77.4984
SJOW2 MC4 | 275 | 86.1756 | 30.5966 | 22.9872 | 66.2573 | 94.5018 | 36.1668 | 26.3509 | 77.4984
SJOW4 M1 | 400 | 120.079 | 40.4607 | 29.6519 | 86.872 | 139.469 | 51.2297 | 34.1932 | 106.643
SJOW4 M2 | 400 | 120.079 | 40.4607 | 29.6519 | 86.872 | 139.469 | 51.2297 | 34.1932 | 106.643
SJOW4 M3 | 400 | 120.079 | 40.4607 | 29.6519 | 86.872 | 139.469 | 51.2297 | 34.1932 | 106.643
SJOW4 M4 | 400 | 120.079 | 40.4607 | 29.6519 | 86.872 | 139.469 | 51.2297 | 34.1932 | 106.643
SJOW4 R1/2 | 400 | 120.079 | 40.4607 | 29.6519 | 86.872 | 139.469 | 51.2297 | 34.1932 | 106.643
SJOW4 R3/4 | 400 | 120.079 | 40.4607 | 29.6519 | 86.872 | 139.469 | 51.2297 | 34.1932 | 106.643
SKLG2 MC1 | 275 | 58.1962 | 21.5543 | 17.6504 | 48.1328 | 55.7853 | 21.7612 | 15.7207 | 46.4957
SKLG2 MC2 | 275 | 58.1962 | 21.5543 | 17.6504 | 48.1328 | 55.7853 | 21.7612 | 15.7207 | 46.4957
SKLG2 MC3 | 275 | 58.1962 | 21.5543 | 17.6504 | 48.1328 | 55.7853 | 21.7612 | 15.7207 | 46.4957
SKLG2 MC4 | 275 | 58.1962 | 21.5543 | 17.6504 | 48.1328 | 55.7853 | 21.7612 | 15.7207 | 46.4957
SMAN2 MC1 | 275 | 76.3316 | 28.4699 | 23.2329 | 63.4954 | 75.0586 | 29.3259 | 21.0226 | 62.4957
SMAN2 MC2 | 275 | 76.3316 | 28.4699 | 23.2329 | 63.4954 | 75.0586 | 29.3259 | 21.0226 | 62.4957
SMAN2 MC3 | 275 | 76.3316 | 28.4699 | 23.2329 | 63.4954 | 75.0586 | 29.3259 | 21.0226 | 62.4957
SMAN2 MC4 | 275 | 76.3316 | 28.4699 | 23.2329 | 63.4954 | 75.0586 | 29.3259 | 21.0226 | 62.4957
SPEN4 MC3 | 400 | 60.3487 | 21.965 | 13.0647 | 44.1279 | 48.5444 | 18.867 | 9.0838 | 35.7658
SPEN4 MC4 | 400 | 60.3487 | 21.965 | 13.0647 | 44.1279 | 48.5444 | 18.867 | 9.0838 | 35.7658
SPEN41 MC1 | 400 | 60.3211 | 21.9548 | 13.0493 | 44.098 | 49.1893 | 19.0942 | 9.3289 | 36.3322
SPEN41 MC2 | 400 | 60.3211 | 21.9548 | 13.0493 | 44.098 | 49.1893 | 19.0942 | 9.3289 | 36.3322
SPLN4 M1 | 400 | 80.0706 | 29.2601 | 21.0778 | 62.4578 | 68.1563 | 26.1003 | 17.7696 | 54.6811
SPLN4 R1 | 400 | 80.0706 | 29.2601 | 21.0778 | 62.4578 | 68.1563 | 26.1003 | 17.7696 | 54.6811
SSHI2 MC1 | 275 | 64.691 | 23.5904 | 11.6543 | 45.0162 | 58.2655 | 23.0513 | 9.4383 | 42.0378
SSHI2 MC2 | 275 | 64.691 | 23.5904 | 11.6543 | 45.0162 | 58.2655 | 23.0513 | 9.4383 | 42.0378
STAL2 M1 | 275 | 82.5303 | 30.432 | 16.077 | 59.1143 | 76.6654 | 29.9581 | 14.5819 | 56.949
STAL2 M2 | 275 | 82.5303 | 30.432 | 16.077 | 59.1143 | 76.6654 | 29.9581 | 14.5819 | 56.949
STAL2 R1 | 275 | 82.5303 | 30.432 | 16.077 | 59.1143 | 76.6654 | 29.9581 | 14.5819 | 56.949
STAL2 R2 | 275 | 82.5303 | 30.432 | 16.077 | 59.1143 | 76.6654 | 29.9581 | 14.5819 | 56.949
STAL4 MC1 | 400 | 36.3895 | 13.4278 | 9.4596 | 28.4494 | 32.5367 | 12.5802 | 8.1168 | 25.9079
STAL4 MC2 | 400 | 51.9039 | 19.7067 | 9.9362 | 37.8057 | 39.594 | 15.7684 | 6.421 | 28.7208
STAY4 M1 | 400 | 116.2987 | 42.3648 | 27.8054 | 87.7184 | 110.2361 | 41.9366 | 28.5947 | 87.902
STAY4 M2 | 400 | 116.2987 | 42.3648 | 27.8054 | 87.7184 | 110.2361 | 41.9366 | 28.5947 | 87.902
STAY4 R1 | 400 | 116.2987 | 42.3648 | 27.8054 | 87.7184 | 110.2361 | 41.9366 | 28.5947 | 87.902
STAY4 R2 | 400 | 116.2987 | 42.3648 | 27.8054 | 87.7184 | 110.2361 | 41.9366 | 28.5947 | 87.902
STAY4A | 400 | 77.4409 | 28.4311 | 21.6259 | 61.8336 | 70.3258 | 26.6278 | 20.4447 | 58.1021
STEN1 M1 | 132 | 54.3189 | 19.1301 | 18.9208 | 45.9748 | 67.1978 | 24.7769 | 22.6591 | 57.699
STEN1 M2 | 132 | 54.3189 | 19.1301 | 18.9208 | 45.9748 | 67.1978 | 24.7769 | 22.6591 | 57.699
STEN1 R1 | 132 | 54.3189 | 19.1301 | 18.9208 | 45.9748 | 67.1978 | 24.7769 | 22.6591 | 57.699
STEN1 R2 | 132 | 54.3189 | 19.1301 | 18.9208 | 45.9748 | 67.1978 | 24.7769 | 22.6591 | 57.699
STES1 M1 | 132 | 54.5535 | 18.6893 | 14.9498 | 41.3804 | 67.1726 | 24.4904 | 17.2801 | 51.9148
STES1 M2 | 132 | 54.5535 | 18.6893 | 14.9498 | 41.3804 | 67.1726 | 24.4904 | 17.2801 | 51.9148
STES1 R1 | 132 | 54.5535 | 18.6893 | 14.9498 | 41.3804 | 67.1726 | 24.4904 | 17.2801 | 51.9148
STES1 R2 | 132 | 54.5535 | 18.6893 | 14.9498 | 41.3804 | 67.1726 | 24.4904 | 17.2801 | 51.9148
STEW2 M1 | 275 | 78.9915 | 29.0675 | 24.1596 | 65.2673 | 77.4801 | 29.7509 | 23.4196 | 65.4937
STEW2 M2 | 275 | 78.9915 | 29.0675 | 24.1596 | 65.2673 | 77.4801 | 29.7509 | 23.4196 | 65.4937
STEW2 R1 | 275 | 78.9915 | 29.0675 | 24.1596 | 65.2673 | 77.4801 | 29.7509 | 23.4196 | 65.4937
STEW2 R2 | 275 | 78.9915 | 29.0675 | 24.1596 | 65.2673 | 77.4801 | 29.7509 | 23.4196 | 65.4937
STEW4 M1 | 400 | 75.1999 | 27.4591 | 23.3008 | 62.1339 | 61.3287 | 23.7941 | 17.7551 | 51.4051
STEW4 M2 | 400 | 75.1999 | 27.4591 | 23.3008 | 62.1339 | 61.3287 | 23.7941 | 17.7551 | 51.4051
STEW4 R1 | 400 | 75.1999 | 27.4591 | 23.3008 | 62.1339 | 61.3287 | 23.7941 | 17.7551 | 51.4051
STEW4 R2a | 400 | 75.1999 | 27.4591 | 23.3008 | 62.1339 | 61.3287 | 23.7941 | 17.7551 | 51.4051
STOB4 M1 | 400 | 66.236 | 25.057 | 12.0909 | 47.5268 | 53.9789 | 21.6672 | 8.23 | 38.872
STOB4 R1 | 400 | 66.236 | 25.057 | 12.0909 | 47.5268 | 53.9789 | 21.6672 | 8.23 | 38.872
STSB4 MC1 | 400 | 57.5778 | 21.416 | 12.5478 | 42.8346 | 45.7918 | 18.0384 | 7.7675 | 33.2776
STSB4 MC2 | 400 | 57.5778 | 21.416 | 12.5478 | 42.8346 | 45.7918 | 18.0384 | 7.7675 | 33.2776
STSB4A | 400 | 53.385 | 19.6781 | 5.765 | 33.594 | 41.597 | 16.2703 | 3.1139 | 26.1236
SUND4 M1 | 400 | 113.2471 | 41.1096 | 24.6772 | 82.8149 | 94.4558 | 36.6562 | 18.5094 | 70.3491
SUND4 M2 | 400 | 89.3075 | 32.8455 | 19.0193 | 65.4699 | 75.3895 | 29.2194 | 15.1316 | 56.454
SUND4 R1 | 400 | 113.2471 | 41.1096 | 24.6772 | 82.8149 | 94.4558 | 36.6562 | 18.5094 | 70.3491
SUND4 R2 | 400 | 89.3075 | 32.8455 | 19.0193 | 65.4699 | 75.3895 | 29.2194 | 15.1316 | 56.454
SUTB4A | 400 | 88.4572 | 32.5239 | 20.334 | 66.3297 | 77.6506 | 29.9782 | 18.2516 | 60.6472
SWAN2 MC3 | 275 | 25.9096 | 9.412 | 8.5643 | 21.8749 | 28.3061 | 10.4806 | 8.8788 | 23.7006
SWAN2 MC4 | 275 | 25.9096 | 9.412 | 8.5643 | 21.8749 | 28.3061 | 10.4806 | 8.8788 | 23.7006
SWAN4 M1 | 400 | 39.1404 | 14.4813 | 9.3748 | 29.8545 | 34.2808 | 13.0891 | 8.1571 | 26.6679
SWAN4 M2 | 400 | 39.1404 | 14.4813 | 9.3748 | 29.8545 | 34.2808 | 13.0891 | 8.1571 | 26.6679
SWAN4 M3 | 400 | 63.0763 | 22.7769 | 16.3037 | 48.515 | 60.8957 | 23.0851 | 14.7398 | 47.387
SWAN4 M4 | 400 | 63.0763 | 22.7769 | 16.3037 | 48.515 | 60.8957 | 23.0851 | 14.7398 | 47.387
SWAN4 R3 | 400 | 63.0763 | 22.7769 | 16.3037 | 48.515 | 60.8957 | 23.0851 | 14.7398 | 47.387
SWAN4 R4 | 400 | 63.0763 | 22.7769 | 16.3037 | 48.515 | 60.8957 | 23.0851 | 14.7398 | 47.387
TAUN4 M1 | 400 | 49.8659 | 18.5425 | 9.6167 | 35.8397 | 43.4567 | 17.2182 | 6.7762 | 31.1264
TAUN4 M2 | 400 | 50.6376 | 18.788 | 9.762 | 36.3322 | 44.9997 | 17.777 | 7.3064 | 32.4469
TEMP2 MC1 | 275 | 59.8909 | 22.2029 | 12.271 | 43.6706 | 62.3339 | 24.7429 | 10.982 | 45.9737
TEMP2 MC2 | 275 | 59.8909 | 22.2029 | 12.271 | 43.6706 | 62.3339 | 24.7429 | 10.982 | 45.9737
TEMP2 MC3 | 275 | 60.1841 | 22.291 | 12.4129 | 43.9372 | 63.2396 | 25.0823 | 11.2117 | 46.6834
THOM2 M1 | 275 | 67.2615 | 24.6498 | 19.0602 | 53.9203 | 69.5329 | 26.3189 | 18.8766 | 56.0971
THOM2 R1 | 275 | 67.2615 | 24.6498 | 19.0602 | 53.9203 | 69.5329 | 26.3189 | 18.8766 | 56.0971
THOM4 MC1 | 400 | 93.1918 | 33.525 | 22.9246 | 70.3362 | 84.0971 | 32.2167 | 18.0135 | 63.5748
THOM4 MC2 | 400 | 93.1918 | 33.525 | 22.9246 | 70.3362 | 84.0971 | 32.2167 | 18.0135 | 63.5748
THOM4 MC3 | 400 | 93.1918 | 33.525 | 22.9246 | 70.3362 | 84.0971 | 32.2167 | 18.0135 | 63.5748
THOM4 MC4 | 400 | 93.1918 | 33.525 | 22.9246 | 70.3362 | 84.0971 | 32.2167 | 18.0135 | 63.5748
THOM4 R2(2) | 400 | 90.2534 | 33.0826 | 19.4014 | 66.1872 | 78.7738 | 30.4589 | 15.7744 | 58.8498
THOM4 R2(3) | 400 | 90.2534 | 33.0826 | 19.4014 | 66.1872 | 78.7738 | 30.4589 | 15.7744 | 58.8498
THOM42 M5 | 400 | 90.2534 | 33.0826 | 19.4014 | 66.1872 | 78.7738 | 30.4589 | 15.7744 | 58.8498
THTO4 M1 | 400 | 94.9555 | 34.3894 | 23.9757 | 72.6097 | 75.7745 | 29.3926 | 14.2947 | 55.8622
THTO4 M2 | 400 | 68.1529 | 25.0164 | 16.3885 | 51.7671 | 55.5476 | 21.494 | 10.9789 | 41.376
THTO4 M3 | 400 | 68.1529 | 25.0164 | 16.3885 | 51.7671 | 55.5476 | 21.494 | 10.9789 | 41.376
THTO4 M4 | 400 | 94.9555 | 34.3894 | 23.9757 | 72.6097 | 75.7745 | 29.3926 | 14.2947 | 55.8622
THTO4 R1/2 | 400 | 67.9629 | 24.9132 | 16.0464 | 51.2791 | 57.8489 | 22.2468 | 11.9185 | 43.3802
THTO4 R3/4 | 400 | 67.9629 | 24.9132 | 16.0464 | 51.2791 | 57.8489 | 22.2468 | 11.9185 | 43.3802
THUR2 MC1 | 275 | 64.8324 | 24.5205 | 10.5361 | 45.2134 | 65.8864 | 26.1441 | 10.9494 | 47.9227
THUR2 MC2 | 275 | 64.8324 | 24.5205 | 10.5361 | 45.2134 | 65.8864 | 26.1441 | 10.9494 | 47.9227
THUR2 MC3 | 275 | 64.8324 | 24.5205 | 10.5361 | 45.2134 | 65.8864 | 26.1441 | 10.9494 | 47.9227
THUR2 MC4 | 275 | 64.8324 | 24.5205 | 10.5361 | 45.2134 | 65.8864 | 26.1441 | 10.9494 | 47.9227
TILB2 M1 | 275 | 71.6022 | 25.6079 | 21.2795 | 57.4946 | 75.468 | 28.1825 | 21.4053 | 61.2613
TILB2 M2 | 275 | 71.6022 | 25.6079 | 21.2795 | 57.4946 | 75.468 | 28.1825 | 21.4053 | 61.2613
TILB2 R1 | 275 | 71.6022 | 25.6079 | 21.2795 | 57.4946 | 75.468 | 28.1825 | 21.4053 | 61.2613
TILB2 R2 | 275 | 71.6022 | 25.6079 | 21.2795 | 57.4946 | 75.468 | 28.1825 | 21.4053 | 61.2613
TILB4 M2 | 400 | 139.2337 | 49.1653 | 44.0128 | 113.5431 | 125.6578 | 48.2909 | 35.479 | 103.7726
TILB4 M3 | 400 | 139.2337 | 49.1653 | 44.0128 | 113.5431 | 125.6578 | 48.2909 | 35.479 | 103.7726
TILB4 R2 | 400 | 139.2337 | 49.1653 | 44.0128 | 113.5431 | 125.6578 | 48.2909 | 35.479 | 103.7726
TILB4 R3 | 400 | 139.2337 | 49.1653 | 44.0128 | 113.5431 | 125.6578 | 48.2909 | 35.479 | 103.7726
TINP2 M1 | 275 | 58.2833 | 21.3725 | 6.8518 | 37.0771 | 56.7354 | 22.1104 | 5.5144 | 36.7833
TINP2 M2 | 275 | 58.4519 | 21.3832 | 6.8648 | 37.1052 | 57.6702 | 22.45 | 5.6086 | 37.3577
TODP2 MC1 | 275 | 58.8416 | 20.6466 | 14.1783 | 43.3769 | 53.3992 | 20.4853 | 10.4274 | 39.3979
TODP2 MC2 | 275 | 58.8416 | 20.6466 | 14.1783 | 43.3769 | 53.3992 | 20.4853 | 10.4274 | 39.3979
TOTE2A | 275 | 75.6565 | 27.1265 | 20.0576 | 58.4203 | 78.6762 | 30.0286 | 17.623 | 60.0898
TOTE2B | 275 | 77.3304 | 27.7108 | 20.23 | 59.419 | 77.0901 | 29.385 | 17.2101 | 58.7668
TOTT2 MC1 | 275 | 75.7314 | 27.9375 | 23.7157 | 63.2253 | 76.128 | 31.2141 | 19.9422 | 64.0856
TOTT2 MC2A | 275 | 76.9813 | 28.3687 | 24.1393 | 64.2587 | 73.7677 | 30.7785 | 18.0433 | 61.5706
TOTT2 MC2B | 275 | 77.3304 | 27.7108 | 20.23 | 59.419 | 77.0901 | 29.385 | 17.2101 | 58.7668
TOTT2 MC3 | 275 | 76.9813 | 28.3687 | 24.1393 | 64.2587 | 73.7677 | 30.7785 | 18.0433 | 61.5706
TOTT2 MC4A | 275 | 75.7314 | 27.9375 | 23.7157 | 63.2253 | 76.128 | 31.2141 | 19.9422 | 64.0856
TOTT2 MC4B | 275 | 75.6565 | 27.1265 | 20.0576 | 58.4203 | 78.6762 | 30.0286 | 17.623 | 60.0898
TOTT2 MC5 | 275 | 77.3304 | 27.7108 | 20.23 | 59.419 | 77.0901 | 29.385 | 17.2101 | 58.7668
TOTT2 MC6 | 275 | 77.3304 | 27.7108 | 20.23 | 59.419 | 77.0901 | 29.385 | 17.2101 | 58.7668
TOTT2 MC7 | 275 | 75.6565 | 27.1265 | 20.0576 | 58.4203 | 78.6762 | 30.0286 | 17.623 | 60.0898
TOTT2 MC8 | 275 | 75.6565 | 27.1265 | 20.0576 | 58.4203 | 78.6762 | 30.0286 | 17.623 | 60.0898
TRAW2 M1 | 275 | 44.8999 | 16.1381 | 13.8365 | 36.6593 | 47.0677 | 17.6081 | 12.7478 | 37.6493
TRAW2 M2 | 275 | 44.8999 | 16.1381 | 13.8365 | 36.6593 | 47.0677 | 17.6081 | 12.7478 | 37.6493
TRAW2 R1 | 275 | 44.8999 | 16.1381 | 13.8365 | 36.6593 | 47.0677 | 17.6081 | 12.7478 | 37.6493
TRAW2 R2 | 275 | 44.8999 | 16.1381 | 13.8365 | 36.6593 | 47.0677 | 17.6081 | 12.7478 | 37.6493
TRAW4 MC1 | 400 | 59.0686 | 22.0154 | 18.0695 | 49.204 | 47.4319 | 18.775 | 12.4926 | 39.0445
TRAW4 MC2 | 400 | 59.0686 | 22.0154 | 18.0695 | 49.204 | 47.4319 | 18.775 | 12.4926 | 39.0445
TRAW4 MC3 | 400 | 59.0686 | 22.0154 | 18.0695 | 49.204 | 47.4319 | 18.775 | 12.4926 | 39.0445
TRAW4 MC4 | 400 | 59.0686 | 22.0154 | 18.0695 | 49.204 | 47.4319 | 18.775 | 12.4926 | 39.0445
TREM2 MC1 | 275 | 49.5025 | 18.1689 | 2.8985 | 28.5933 | 43.1915 | 17.1834 | 2.4321 | 26.7331
TREM2 MC2 | 275 | 49.5025 | 18.1689 | 2.8985 | 28.5933 | 43.1915 | 17.1834 | 2.4321 | 26.7331
TREU4A | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 73.8478 | 28.8646 | 4.6548 | 45.4755
TREU4A_DEES1 | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 73.8478 | 28.8646 | 4.6548 | 45.4755
TREU4A_LEGA1 | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 73.8478 | 28.8646 | 4.6548 | 45.4755
TREU4A_TRAW1 | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 73.8478 | 28.8646 | 4.6548 | 45.4755
TREU4B | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 74.0818 | 28.9544 | 4.6695 | 45.6173
TREU4B_DEES2 | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 74.0818 | 28.9544 | 4.6695 | 45.6173
TREU4B_LEGA2 | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 74.0818 | 28.9544 | 4.6695 | 45.6173
TREU4B_TRAW2 | 400 | 90.5175 | 32.0894 | 9.8243 | 55.2056 | 74.0818 | 28.9544 | 4.6695 | 45.6173
TYNE2 MC1 | 275 | 60.6085 | 22.2407 | 10.7201 | 42.1732 | 54.3875 | 21.4174 | 9.3106 | 39.5994
TYNE2 MC2 | 275 | 60.6085 | 22.2407 | 10.7201 | 42.1732 | 54.3875 | 21.4174 | 9.3106 | 39.5994
TYNE2A | 275 | 59.8917 | 21.6309 | 3.7245 | 34.3152 | 51.1357 | 20.2411 | 2.7679 | 31.3931
UPPB2 MC1 | 275 | 43.5082 | 16.1488 | 11.2298 | 34.0676 | 42.6217 | 16.4649 | 9.5908 | 32.8756
UPPB2 MC2 | 275 | 47.4014 | 17.5496 | 11.9266 | 36.7456 | 44.8043 | 17.3041 | 10.0044 | 34.476
UPPB2 MC3 | 275 | 47.4014 | 17.5496 | 11.9266 | 36.7456 | 44.8043 | 17.3041 | 10.0044 | 34.476
UPPB2 MC4 | 275 | 43.5082 | 16.1488 | 11.2298 | 34.0676 | 42.6217 | 16.4649 | 9.5908 | 32.8756
USKM2 M1 | 275 | 79.1749 | 28.2152 | 19.5515 | 59.4539 | 88.9052 | 33.3756 | 22.7055 | 69.9058
USKM2 M2 | 275 | 79.1749 | 28.2152 | 19.5515 | 59.4539 | 88.9052 | 33.3756 | 22.7055 | 69.9058
USKM2 R1 | 275 | 79.1749 | 28.2152 | 19.5515 | 59.4539 | 88.9052 | 33.3756 | 22.7055 | 69.9058
USKM2 R2 | 275 | 79.1749 | 28.2152 | 19.5515 | 59.4539 | 88.9052 | 33.3756 | 22.7055 | 69.9058
USKM2A | 275 | 76.8669 | 26.7627 | 10.8351 | 48.6832 | 84.2372 | 31.5317 | 11.5222 | 56.1147
WALH4 MC1 | 400 | 61.0553 | 22.8109 | 11.8079 | 44.0674 | 51.5576 | 20.2034 | 10.5809 | 39.1529
WALH4 MC2 | 400 | 61.0553 | 22.8109 | 11.8079 | 44.0674 | 51.5576 | 20.2034 | 10.5809 | 39.1529
WALH4 MC3 | 400 | 61.0553 | 22.8109 | 11.8079 | 44.0674 | 51.5576 | 20.2034 | 10.5809 | 39.1529
WALH4 MC4 | 400 | 61.0553 | 22.8109 | 11.8079 | 44.0674 | 51.5576 | 20.2034 | 10.5809 | 39.1529
WALP R4 | 132 | 69.0385 | 24.3592 | 20.521 | 54.9701 | 83.7746 | 32.0513 | 22.6743 | 68.0017
WALP1 M4 | 132 | 69.0385 | 24.3592 | 20.521 | 54.9701 | 83.7746 | 32.0513 | 22.6743 | 68.0017
WALP4 M1 | 400 | 106.247 | 38.4703 | 26.9463 | 81.3516 | 94.7824 | 36.1651 | 24.4729 | 75.6182
WALP4 M2 | 400 | 106.247 | 38.4703 | 26.9463 | 81.3516 | 94.7824 | 36.1651 | 24.4729 | 75.6182
WALP4 R1 | 400 | 106.247 | 38.4703 | 26.9463 | 81.3516 | 94.7824 | 36.1651 | 24.4729 | 75.6182
WALP4 R2 | 400 | 106.247 | 38.4703 | 26.9463 | 81.3516 | 94.7824 | 36.1651 | 24.4729 | 75.6182
WALPM3 | 132 | 69.0385 | 24.3592 | 20.521 | 54.9701 | 83.7746 | 32.0513 | 22.6743 | 68.0017
WALPR3 | 132 | 69.0385 | 24.3592 | 20.521 | 54.9701 | 83.7746 | 32.0513 | 22.6743 | 68.0017
WALX2 M1 | 275 | 91.2717 | 32.1719 | 19.145 | 64.643 | 91.098 | 34.3149 | 17.6763 | 66.2049
WALX2 M2 | 275 | 92.3977 | 32.5078 | 19.4556 | 65.4286 | 96.2843 | 36.1748 | 18.8458 | 70.0046
WALX2 R1 | 275 | 91.2717 | 32.1719 | 19.145 | 64.643 | 91.098 | 34.3149 | 17.6763 | 66.2049
WALX2 R2 | 275 | 92.3977 | 32.5078 | 19.4556 | 65.4286 | 96.2843 | 36.1748 | 18.8458 | 70.0046
WALX4A | 400 | 74.045 | 26.0973 | 11.7797 | 48.6868 | 73.3339 | 27.367 | 11.5114 | 50.2142
WALX4B | 400 | 69.7237 | 24.839 | 10.2972 | 45.4249 | 64.6484 | 24.3124 | 9.7058 | 44.0887
WARL2 MC1 | 275 | 65.104 | 23.6698 | 15.5555 | 49.0296 | 60.6423 | 23.5571 | 11.5424 | 44.8571
WARL2 MC2 | 275 | 65.104 | 23.6698 | 15.5555 | 49.0296 | 60.6423 | 23.5571 | 11.5424 | 44.8571
WARL2 MC3 | 275 | 65.104 | 23.6698 | 15.5555 | 49.0296 | 60.6423 | 23.5571 | 11.5424 | 44.8571
WARL2 MC4 | 275 | 65.104 | 23.6698 | 15.5555 | 49.0296 | 60.6423 | 23.5571 | 11.5424 | 44.8571
WASF2A | 275 | 60.6391 | 21.923 | 6.2372 | 37.241 | 51.0604 | 19.9351 | 3.3826 | 31.5751
WASF2B | 275 | 65.2235 | 23.4247 | 6.6213 | 39.7488 | 57.6059 | 22.5163 | 3.5446 | 35.3874
WBOL2 MC1 | 275 | 72.8104 | 26.1678 | 13.9503 | 50.9572 | 64.284 | 25.3302 | 10.5519 | 46.3743
WBOL2 MC2 | 275 | 72.8104 | 26.1678 | 13.9503 | 50.9572 | 64.284 | 25.3302 | 10.5519 | 46.3743
WBOL2 MC3 | 275 | 72.8104 | 26.1678 | 13.9503 | 50.9572 | 64.284 | 25.3302 | 10.5519 | 46.3743
WBOL2 MC4 | 275 | 72.8104 | 26.1678 | 13.9503 | 50.9572 | 64.284 | 25.3302 | 10.5519 | 46.3743
WBUR1 M1 | 132 | 21.479 | 7.6283 | 6.8367 | 17.6248 | 25.0574 | 9.2693 | 8.1868 | 21.2956
WBUR1 M2 | 132 | 21.479 | 7.6283 | 6.8367 | 17.6248 | 25.0574 | 9.2693 | 8.1868 | 21.2956
WBUR1 R1 | 132 | 21.479 | 7.6283 | 6.8367 | 17.6248 | 25.0574 | 9.2693 | 8.1868 | 21.2956
WBUR1 R2 | 132 | 21.2555 | 7.5684 | 6.7307 | 17.4341 | 24.8927 | 9.2083 | 8.0923 | 21.1148
WBUR4 M1 | 400 | 121.9328 | 43.192 | 36.7777 | 97.8604 | 124.1111 | 45.8064 | 38.3236 | 103.1036
WBUR4 M2 | 400 | 121.9328 | 43.192 | 36.7777 | 97.8604 | 124.1111 | 45.8064 | 38.3236 | 103.1036
WBUR4 M3 | 400 | 121.9328 | 43.192 | 36.7777 | 97.8604 | 124.1111 | 45.8064 | 38.3236 | 103.1036
WBUR4 M4 | 400 | 121.9328 | 43.192 | 36.7777 | 97.8604 | 124.1111 | 45.8064 | 38.3236 | 103.1036
WBUR4 R1/2 | 400 | 118.7454 | 42.9882 | 31.2444 | 92.0389 | 110.4611 | 41.6781 | 29.9712 | 88.9129
WBUR4 R3/4 | 400 | 118.7454 | 42.9882 | 31.2444 | 92.0389 | 110.4611 | 41.6781 | 29.9712 | 88.9129
WHAM4 M1 | 400 | 124.3298 | 43.6692 | 39.269 | 101.0265 | 138.6952 | 52.736 | 39.9258 | 114.5057
WHAM4 M2 | 400 | 124.3298 | 43.6692 | 39.269 | 101.0265 | 138.6952 | 52.736 | 39.9258 | 114.5057
WHAM4 R1 | 400 | 124.3298 | 43.6692 | 39.269 | 101.0265 | 138.6952 | 52.736 | 39.9258 | 114.5057
WHAM4 R2 | 400 | 124.3298 | 43.6692 | 39.269 | 101.0265 | 138.6952 | 52.736 | 39.9258 | 114.5057
WHAM4A | 400 | 99.798 | 33.2418 | 13.5171 | 60.5281 | 103.1159 | 39.7732 | 15.7475 | 71.9953
WHAM4B | 400 | 99.874 | 33.2634 | 13.5195 | 60.5611 | 103.2172 | 39.8128 | 15.7494 | 72.0533
WHGA2 MC1 | 275 | 70.4808 | 25.79 | 14.9952 | 51.4678 | 66.2244 | 25.9247 | 11.9762 | 48.6393
WHGA2 MC2 | 275 | 70.4808 | 25.79 | 14.9952 | 51.4678 | 66.2244 | 25.9247 | 11.9762 | 48.6393
WHGA2 MC3 | 275 | 70.4808 | 25.79 | 14.9952 | 51.4678 | 66.2244 | 25.9247 | 11.9762 | 48.6393
WHGA2 MC4 | 275 | 70.4808 | 25.79 | 14.9952 | 51.4678 | 66.2244 | 25.9247 | 11.9762 | 48.6393
WHSO2 M1 | 275 | 68.975 | 25.0122 | 14.879 | 50.2516 | 73.8932 | 28.2672 | 15.5358 | 55.5117
WHSO2 M2 | 275 | 68.975 | 25.0122 | 14.879 | 50.2516 | 73.8932 | 28.2672 | 15.5358 | 55.5117
WHSO2 R1 | 275 | 75.7606 | 27.1852 | 18.9858 | 57.4315 | 82.324 | 31.1353 | 20.0414 | 64.0734
WHSO2 R2 | 275 | 75.7606 | 27.1852 | 18.9858 | 57.4315 | 82.324 | 31.1353 | 20.0414 | 64.0734
WIBA2 MC1 | 275 | 59.8811 | 22.2002 | 12.2608 | 43.6566 | 63.5314 | 25.4563 | 10.3189 | 46.3196
WIBA2 MC1 | 275 | 59.8811 | 22.2002 | 12.2608 | 43.6566 | 63.5314 | 25.4563 | 10.3189 | 46.3196
WIBA2 MC2 | 275 | 59.8811 | 22.2002 | 12.2608 | 43.6566 | 63.5314 | 25.4563 | 10.3189 | 46.3196
WIBA2 MC2 | 275 | 59.8811 | 22.2002 | 12.2608 | 43.6566 | 63.5314 | 25.4563 | 10.3189 | 46.3196
WILE4 M1 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 M1 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 M2 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 M2 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 R1 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 R1 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 R2 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILE4 R2 | 400 | 109.2473 | 40.8203 | 30.0899 | 87.8185 | 93.6658 | 37.1983 | 24.0774 | 76.6837
WILL1 M2 | 132 | 50.0198 | 17.5309 | 15.691 | 40.4834 | 57.3226 | 21.7054 | 18.0935 | 48.7896
WILL1 R1 | 132 | 35.0772 | 13.003 | 10.7123 | 29.1014 | 38.9038 | 15.0027 | 12.2231 | 33.4401
WILL1 R2 | 132 | 50.0198 | 17.5309 | 15.691 | 40.4834 | 57.3226 | 21.7054 | 18.0935 | 48.7896
WILL2 M2 | 275 | 24.0229 | 8.6001 | 8.9435 | 21.1058 | 25.6753 | 9.373 | 9.2892 | 22.5446
WILL2 M2 | 275 | 24.0229 | 8.6001 | 8.9435 | 21.1058 | 25.6753 | 9.373 | 9.2892 | 22.5446
WILL2 R2 | 275 | 24.0229 | 8.6001 | 8.9435 | 21.1058 | 25.6753 | 9.373 | 9.2892 | 22.5446
WILL2 R2 | 275 | 24.0229 | 8.6001 | 8.9435 | 21.1058 | 25.6753 | 9.373 | 9.2892 | 22.5446
WILT2A | 275 | 53.819 | 19.1223 | 9.4936 | 36.5366 | 55.89 | 20.7699 | 8.4672 | 37.8403
WILT2A | 275 | 53.819 | 19.1223 | 9.4936 | 36.5366 | 55.89 | 20.7699 | 8.4672 | 37.8403
WILT2B | 275 | 53.819 | 19.1223 | 9.4936 | 36.5366 | 55.89 | 20.7699 | 8.4672 | 37.8403
WILT2B | 275 | 53.819 | 19.1223 | 9.4936 | 36.5366 | 55.89 | 20.7699 | 8.4672 | 37.8403
WILT2C | 275 | 54.1236 | 19.2165 | 9.6423 | 36.8185 | 56.7713 | 21.0406 | 9.0777 | 38.8336
WILT2C | 275 | 54.1236 | 19.2165 | 9.6423 | 36.8185 | 56.7713 | 21.0406 | 9.0777 | 38.8336
WILT2D | 275 | 54.1224 | 19.2163 | 9.6419 | 36.8178 | 56.7673 | 21.0393 | 9.076 | 38.8301
WILT2D | 275 | 54.1224 | 19.2163 | 9.6419 | 36.8178 | 56.7673 | 21.0393 | 9.076 | 38.8301
WIMB2 MC1 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC1 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC2 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC2 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC3 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC3 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC4 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2 MC4 | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2A | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB2A | 275 | 83.8468 | 28.9223 | 21.6561 | 62.5585 | 94.3659 | 35.712 | 23.5973 | 74.1017
WIMB4 MB2 | 400 | 96.9225 | 33.3363 | 24.1905 | 71.3351 | 111.3012 | 42.2902 | 21.7115 | 81.5188
WIMB4 MB2 | 400 | 96.9225 | 33.3363 | 24.1905 | 71.3351 | 111.3012 | 42.2902 | 21.7115 | 81.5188
WIMB4 RB2 | 400 | 96.9225 | 33.3363 | 24.1905 | 71.3351 | 111.3012 | 42.2902 | 21.7115 | 81.5188
WIMB4 RB2 | 400 | 96.9225 | 33.3363 | 24.1905 | 71.3351 | 111.3012 | 42.2902 | 21.7115 | 81.5188
WISD2 M1 | 275 | 70.1438 | 24.362 | 22.8919 | 57.3449 | 81.7679 | 30.1495 | 25.6393 | 68.2771
WISD2 M2 | 275 | 70.1438 | 24.362 | 22.8919 | 57.3449 | 81.7679 | 30.1495 | 25.6393 | 68.2771
WISD2 R1 | 275 | 70.1438 | 24.362 | 22.8919 | 57.3449 | 81.7679 | 30.1495 | 25.6393 | 68.2771
WISD2 R2 | 275 | 70.1438 | 24.362 | 22.8919 | 57.3449 | 81.7679 | 30.1495 | 25.6393 | 68.2771
WISD2A | 275 | 59.7527 | 20.7774 | 12.6408 | 42.0244 | 65.4133 | 24.9958 | 14.0579 | 49.4073
WISD6 M1 | 66 | 50.0665 | 16.9388 | 17.09 | 41.045 | 33.4973 | 12.5496 | 10.8201 | 28.5679
WISD6 M2 | 66 | 50.0665 | 16.9388 | 17.09 | 41.045 | 33.4973 | 12.5496 | 10.8201 | 28.5679
WISD6 R1 | 66 | 50.0665 | 16.9388 | 17.09 | 41.045 | 33.4973 | 12.5496 | 10.8201 | 28.5679
WISD6 R2 | 66 | 50.0665 | 16.9388 | 17.09 | 41.045 | 33.4973 | 12.5496 | 10.8201 | 28.5679
WMEL2 MC1 | 275 | 78.5084 | 28.906 | 14.4282 | 55.3074 | 74.8959 | 29.5764 | 12.0929 | 53.9203
WMEL2 MC2 | 275 | 78.5084 | 28.906 | 14.4282 | 55.3074 | 74.8959 | 29.5764 | 12.0929 | 53.9203
WMEL2 MC3 | 275 | 78.5084 | 28.906 | 14.4282 | 55.3074 | 74.8959 | 29.5764 | 12.0929 | 53.9203
WMEL2 MC4 | 275 | 78.5084 | 28.906 | 14.4282 | 55.3074 | 74.8959 | 29.5764 | 12.0929 | 53.9203
WTHU4A | 400 | 93.5693 | 32.1536 | 8.462 | 53.934 | 75.4533 | 29.461 | 4.8924 | 46.5566
WTHU4B | 400 | 93.5693 | 32.1536 | 8.462 | 53.934 | 77.1491 | 30.0958 | 5.0024 | 47.5643
WWEY2 M1 | 275 | 71.8835 | 26.0895 | 17.8654 | 54.7615 | 70.9228 | 27.0677 | 16.7133 | 54.9927
WWEY2 M2 | 275 | 71.8835 | 26.0895 | 17.8654 | 54.7615 | 70.9228 | 27.0677 | 16.7133 | 54.9927
WWEY2 R1 | 275 | 73.3517 | 26.7766 | 16.5161 | 54.384 | 73.3643 | 28.1228 | 16.5743 | 56.346
WWEY2 R2 | 275 | 73.3517 | 26.7766 | 16.5161 | 54.384 | 73.3643 | 28.1228 | 16.5743 | 56.346
WWEY4A | 400 | 50.0972 | 18.3001 | 6.2981 | 32.1783 | 44.9096 | 17.2312 | 6.1432 | 30.5117
WWEY4B | 400 | 50.7277 | 18.5214 | 6.5492 | 32.7424 | 44.9243 | 17.3034 | 6.376 | 30.8468
WYLF1 M1 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 M1 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 M2 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 M2 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 R1 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 R1 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 R2 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF1 R2 | 132 | 18.4174 | 5.7525 | 6.7579 | 14.8931 | 20.7403 | 7.1887 | 7.0106 | 17.1769
WYLF4 M1 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 M1 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 M2 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 M2 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 R1 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 R1 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 R2 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYLF4 R2 | 400 | 48.4353 | 17.4416 | 12.0642 | 36.7303 | 36.1142 | 14.0836 | 6.9333 | 26.8505
WYMO4 M1 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 M1 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 M2 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 M2 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 R1 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 R1 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 R2 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596
WYMO4 R2 | 400 | 111.7887 | 40.427 | 25.3051 | 82.4775 | 95.6995 | 36.9079 | 19.4004 | 71.596

## D3.2
ETYS 19 Yr 2 - NGET Fault Levels (kA), Winter 2020/21
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 37.6139 | 13.7867 | 3.2565 | 22.7538 | 34.2672 | 13.4126 | 2.3901 | 21.3585 | Back To Menu
ABHA4B | 400 | 37.5965 | 13.7772 | 3.2555 | 22.7394 | 34.2574 | 13.4066 | 2.3847 | 21.3445
ABTH1 M1 | 132 | 29.3362 | 11.0166 | 6.7948 | 22.3746 | 28.6837 | 11.2374 | 7.1548 | 23.0469
ABTH1 M2 | 132 | 26.8973 | 10.4487 | 8.2212 | 22.9979 | 24.1372 | 9.6056 | 7.4803 | 21.0647
ABTH1 R1 | 132 | 29.8291 | 11.4844 | 8.3201 | 24.5614 | 32.8523 | 12.908 | 9.6352 | 27.8898
ABTH1 R2 | 132 | 29.8291 | 11.4844 | 8.3201 | 24.5614 | 32.8523 | 12.908 | 9.6352 | 27.8898
ABTH2 M1 | 275 | 66.8632 | 23.9392 | 16.6895 | 50.5447 | 72.4106 | 27.1694 | 19.203 | 57.6263
ABTH2 M2 | 275 | 66.8632 | 23.9392 | 16.6895 | 50.5447 | 72.4106 | 27.1694 | 19.203 | 57.6263
ABTH2 M4 | 275 | 66.8632 | 23.9392 | 16.6895 | 50.5447 | 72.4106 | 27.1694 | 19.203 | 57.6263
ABTH2 R | 275 | 49.8971 | 18.3574 | 7.7443 | 33.7055 | 50.8229 | 19.4448 | 8.5359 | 36.0351
ALDW2 MC1 | 275 | 63.558 | 23.7599 | 10.0702 | 43.6718 | 62.2648 | 24.699 | 9.9228 | 44.8525
ALDW2 MC2 | 275 | 63.558 | 23.7599 | 10.0702 | 43.6718 | 62.2648 | 24.699 | 9.9228 | 44.8525
ALDW2 MC3 | 275 | 63.558 | 23.7599 | 10.0702 | 43.6718 | 62.2648 | 24.699 | 9.9228 | 44.8525
ALDW2 MC4 | 275 | 63.558 | 23.7599 | 10.0702 | 43.6718 | 62.2648 | 24.699 | 9.9228 | 44.8525
AMEM1 M1 | 132 | 25.8994 | 9.2461 | 9.2892 | 22.3652 | 31.8973 | 11.7308 | 10.5871 | 27.1769
AMEM1 M2 | 132 | 25.8994 | 9.2461 | 9.2892 | 22.3652 | 31.8973 | 11.7308 | 10.5871 | 27.1769
AMEM1 R1 | 132 | 25.8994 | 9.2461 | 9.2892 | 22.3652 | 31.8973 | 11.7308 | 10.5871 | 27.1769
AMEM1 R2 | 132 | 25.8994 | 9.2461 | 9.2892 | 22.3652 | 31.8973 | 11.7308 | 10.5871 | 27.1769
AMEM4 M | 400 | 51.4704 | 19.1582 | 4.4088 | 31.5026 | 43.1094 | 17.1045 | 3.0023 | 27.1917
AMEM4 R | 400 | 51.2572 | 19.0805 | 4.4217 | 31.4057 | 42.0876 | 16.6425 | 2.8993 | 26.4353
AXMI4 MC1 | 400 | 39.8877 | 14.8272 | 8.0217 | 28.9905 | 33.4767 | 13.1025 | 6.2024 | 24.7321
AXMI4 MC2 | 400 | 39.8877 | 14.8272 | 8.0217 | 28.9905 | 33.4767 | 13.1025 | 6.2024 | 24.7321
BAGB2 M1 | 275 | 53.4562 | 19.5445 | 14.013 | 41.6531 | 51.1878 | 19.5364 | 13.7175 | 41.3461
BAGB2 M2 | 275 | 53.4562 | 19.5445 | 14.013 | 41.6531 | 51.1878 | 19.5364 | 13.7175 | 41.3461
BAGB2 R1 | 275 | 53.4562 | 19.5445 | 14.013 | 41.6531 | 51.1878 | 19.5364 | 13.7175 | 41.3461
BAGB2 R2 | 275 | 53.4562 | 19.5445 | 14.013 | 41.6531 | 51.1878 | 19.5364 | 13.7175 | 41.3461
BARK2 M1 | 275 | 55.1888 | 20.057 | 14.5004 | 42.8653 | 54.9629 | 20.8792 | 14.3326 | 43.8602
BARK2 M2 | 275 | 53.3748 | 19.4035 | 14.2478 | 41.6884 | 55.3843 | 20.9943 | 14.948 | 44.6384
BARK2 R1 | 275 | 55.1888 | 20.057 | 14.5004 | 42.8653 | 54.9629 | 20.8792 | 14.3326 | 43.8602
BARK2 R2 | 275 | 53.3748 | 19.4035 | 14.2478 | 41.6884 | 55.3843 | 20.9943 | 14.948 | 44.6384
BARK4 M1 | 400 | 134.7931 | 47.3782 | 42.4127 | 109.4156 | 126.9853 | 49.1375 | 33.6474 | 103.1382
BARK4 M2 | 400 | 134.7931 | 47.3782 | 42.4127 | 109.4156 | 126.9853 | 49.1375 | 33.6474 | 103.1382
BARK4 R1 | 400 | 134.7931 | 47.3782 | 42.4127 | 109.4156 | 126.9853 | 49.1375 | 33.6474 | 103.1382
BARK4 R2 | 400 | 134.7931 | 47.3782 | 42.4127 | 109.4156 | 126.9853 | 49.1375 | 33.6474 | 103.1382
BEDD2 M1/4 | 275 | 61.0805 | 21.8924 | 14.0558 | 45.0163 | 64.9294 | 24.8158 | 14.0529 | 49.1478
BEDD2 M2/3 | 275 | 79.5668 | 28.2284 | 17.9465 | 57.8675 | 82.7947 | 31.5977 | 17.6673 | 62.3532
BEDD2 R1 | 275 | 51.3123 | 19.0424 | 11.3955 | 38.3255 | 51.4915 | 19.8488 | 11.2007 | 39.2711
BEDD2 R2 | 275 | 79.5668 | 28.2284 | 17.9465 | 57.8675 | 82.7947 | 31.5977 | 17.6673 | 62.3532
BEDD2 R3 | 275 | 79.5668 | 28.2284 | 17.9465 | 57.8675 | 82.7947 | 31.5977 | 17.6673 | 62.3532
BEDD2 R4 | 275 | 51.3123 | 19.0424 | 11.3955 | 38.3255 | 51.4915 | 19.8488 | 11.2007 | 39.2711
BEDD4B | 400 | 42.4542 | 15.8686 | 3.1503 | 25.5918 | 37.4669 | 14.9903 | 3.7288 | 24.9284
BESW2 MC1 | 275 | 59.6387 | 21.943 | 10.9627 | 41.9948 | 52.0081 | 20.7206 | 8.5309 | 37.8343
BESW2 MC2 | 275 | 59.6387 | 21.943 | 10.9627 | 41.9948 | 52.0081 | 20.7206 | 8.5309 | 37.8343
BESW2 MC3 | 275 | 59.6387 | 21.943 | 10.9627 | 41.9948 | 52.0081 | 20.7206 | 8.5309 | 37.8343
BESW2 MC4 | 275 | 59.6387 | 21.943 | 10.9627 | 41.9948 | 52.0081 | 20.7206 | 8.5309 | 37.8343
BICF4A | 400 | 98.4043 | 36.1905 | 33.1784 | 84.3595 | 65.487 | 26.1722 | 16.6471 | 53.6602
BICF4B | 400 | 98.4043 | 36.1905 | 33.1784 | 84.3595 | 65.487 | 26.1722 | 16.6471 | 53.6602
BIRK2 MC1 | 275 | 58.7963 | 20.9413 | 15.7159 | 45.3314 | 58.5836 | 22.1662 | 13.3284 | 44.6762
BIRK2 MC2 | 275 | 58.7963 | 20.9413 | 15.7159 | 45.3314 | 58.5836 | 22.1662 | 13.3284 | 44.6762
BIRK2 MC3 | 275 | 58.7963 | 20.9413 | 15.7159 | 45.3314 | 58.5836 | 22.1662 | 13.3284 | 44.6762
BIRK2 MC4 | 275 | 58.7963 | 20.9413 | 15.7159 | 45.3314 | 58.5836 | 22.1662 | 13.3284 | 44.6762
BISW2 MC1 | 275 | 65.2176 | 23.9202 | 12.1974 | 46.0257 | 60.3088 | 23.7342 | 9.8917 | 43.457
BISW2 MC2 | 275 | 65.2176 | 23.9202 | 12.1974 | 46.0257 | 60.3088 | 23.7342 | 9.8917 | 43.457
BISW2 MC3 | 275 | 65.2176 | 23.9202 | 12.1974 | 46.0257 | 60.3088 | 23.7342 | 9.8917 | 43.457
BISW2 MC4 | 275 | 65.2176 | 23.9202 | 12.1974 | 46.0257 | 60.3088 | 23.7342 | 9.8917 | 43.457
BLYT1A | 132 | 30.5514 | 10.7831 | 4.547 | 19.7966 | 31.8382 | 11.9772 | 5.2001 | 22.1385
BLYT1B | 132 | 30.3779 | 10.7419 | 4.5478 | 19.7392 | 31.8102 | 11.9669 | 5.1907 | 22.1145
BLYT2 M1 | 275 | 82.0748 | 30.116 | 24.4962 | 67.0866 | 77.5179 | 30.0376 | 22.0495 | 64.5291
BLYT2 M2 | 275 | 82.0748 | 30.116 | 24.4962 | 67.0866 | 77.5179 | 30.0376 | 22.0495 | 64.5291
BLYT2 R1 | 275 | 82.0748 | 30.116 | 24.4962 | 67.0866 | 77.5179 | 30.0376 | 22.0495 | 64.5291
BLYT2 R2 | 275 | 82.0748 | 30.116 | 24.4962 | 67.0866 | 77.5179 | 30.0376 | 22.0495 | 64.5291
BODE4 M1 | 400 | 86.3052 | 30.7211 | 21.4235 | 64.8698 | 72.5251 | 27.8745 | 16.1187 | 55.5393
BODE4 R1 | 400 | 86.3052 | 30.7211 | 21.4235 | 64.8698 | 72.5251 | 27.8745 | 16.1187 | 55.5393
BOLN4 M1 | 400 | 70.5954 | 26.1561 | 21.1775 | 58.1679 | 62.8138 | 24.2271 | 18.9463 | 53.2087
BOLN4 M2 | 400 | 70.5954 | 26.1561 | 21.1775 | 58.1679 | 62.8138 | 24.2271 | 18.9463 | 53.2087
BOLN4 R1 | 400 | 70.5954 | 26.1561 | 21.1775 | 58.1679 | 62.8138 | 24.2271 | 18.9463 | 53.2087
BOLN4 R2 | 400 | 70.5954 | 26.1561 | 21.1775 | 58.1679 | 62.8138 | 24.2271 | 18.9463 | 53.2087
BOTW4 MC1 | 400 | 79.3202 | 28.5849 | 15.9705 | 56.3956 | 64.359 | 24.9868 | 12.2596 | 47.5962
BOTW4 MC2 | 400 | 79.3202 | 28.5849 | 15.9705 | 56.3956 | 64.359 | 24.9868 | 12.2596 | 47.5962
BRAI4A | 400 | 64.402 | 23.6579 | 14.6279 | 48.0852 | 49.146 | 19.2243 | 9.4876 | 36.6748
BRAI4A BRFO | 400 | 64.402 | 23.6579 | 14.6279 | 48.0852 | 49.146 | 19.2243 | 9.4876 | 36.6748
BRAI4A RAYL | 400 | 64.402 | 23.6579 | 14.6279 | 48.0852 | 49.146 | 19.2243 | 9.4876 | 36.6748
BRAI4B | 400 | 62.2402 | 22.8989 | 13.9065 | 46.2905 | 46.7505 | 18.2323 | 9.0175 | 34.8018
BRAI4B PELH | 400 | 62.2402 | 22.8989 | 13.9065 | 46.2905 | 46.7505 | 18.2323 | 9.0175 | 34.8018
BRAI4B RAYL | 400 | 62.2402 | 22.8989 | 13.9065 | 46.2905 | 46.7505 | 18.2323 | 9.0175 | 34.8018
BRAW2 MC1 | 275 | 64.9656 | 23.4371 | 14.9103 | 48.0553 | 65.7244 | 25.2256 | 13.9489 | 49.6233
BRAW2 MC2 | 275 | 64.9656 | 23.4371 | 14.9103 | 48.0553 | 65.7244 | 25.2256 | 13.9489 | 49.6233
BRAW2 MC3 | 275 | 64.9656 | 23.4371 | 14.9103 | 48.0553 | 65.7244 | 25.2256 | 13.9489 | 49.6233
BRAW2 MC4 | 275 | 64.9656 | 23.4371 | 14.9103 | 48.0553 | 65.7244 | 25.2256 | 13.9489 | 49.6233
BRAW4A | 400 | 34.9056 | 12.7853 | 4.4277 | 22.5088 | 30.5098 | 11.6079 | 4.2168 | 20.6328
BRED2 MC1 | 275 | 78.9256 | 29.0193 | 15.8127 | 56.8522 | 75.4296 | 29.5971 | 12.8682 | 54.7248
BRED2 MC2 | 275 | 78.9256 | 29.0193 | 15.8127 | 56.8522 | 75.4296 | 29.5971 | 12.8682 | 54.7248
BRED2 MC3 | 275 | 78.9256 | 29.0193 | 15.8127 | 56.8522 | 75.4296 | 29.5971 | 12.8682 | 54.7248
BRED2 MC4 | 275 | 78.9256 | 29.0193 | 15.8127 | 56.8522 | 75.4296 | 29.5971 | 12.8682 | 54.7248
BRFO4 M3 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 M5 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 M6 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 M7 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 R3 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 R5 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 R6 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRFO4 R7 | 400 | 86.529 | 31.742 | 27.8907 | 72.7807 | 78.5753 | 30.3157 | 23.0339 | 65.9068
BRIM1 M1 | 132 | 53.1272 | 17.9673 | 19.8616 | 45.2713 | 67.3686 | 24.1823 | 23.776 | 57.9749
BRIM1 M2 | 132 | 53.1272 | 17.9673 | 19.8616 | 45.2713 | 67.3686 | 24.1823 | 23.776 | 57.9749
BRIM1 R1 | 132 | 53.1272 | 17.9673 | 19.8616 | 45.2713 | 67.3686 | 24.1823 | 23.776 | 57.9749
BRIM1 R2 | 132 | 53.1272 | 17.9673 | 19.8616 | 45.2713 | 67.3686 | 24.1823 | 23.776 | 57.9749
BRIN2 M1 | 275 | 65.2222 | 23.9766 | 14.0231 | 47.9311 | 68.7619 | 26.9179 | 13.0008 | 51.0685
BRIN2 M2 | 275 | 69.3131 | 25.4849 | 17.2444 | 53.2855 | 72.5955 | 28.0155 | 16.691 | 56.3109
BRIN2 R1 | 275 | 65.2222 | 23.9766 | 14.0231 | 47.9311 | 68.7619 | 26.9179 | 13.0008 | 51.0685
BRIN2 R2 | 275 | 69.3131 | 25.4849 | 17.2444 | 53.2855 | 72.5955 | 28.0155 | 16.691 | 56.3109
BRIN4 MC1 | 400 | 73.7011 | 27.0708 | 16.644 | 54.9278 | 56.5901 | 22.1831 | 11.4417 | 42.8133
BRIN4 MC4 | 400 | 73.7011 | 27.0708 | 16.644 | 54.9278 | 56.5901 | 22.1831 | 11.4417 | 42.8133
BRLE4 M1 | 400 | 123.8196 | 44.5157 | 24.9365 | 87.8912 | 105.7574 | 41.1716 | 21.3197 | 79.5451
BRLE4 M2 | 400 | 123.8196 | 44.5157 | 24.9365 | 87.8912 | 105.7574 | 41.1716 | 21.3197 | 79.5451
BRLE4 R1 | 400 | 123.8196 | 44.5157 | 24.9365 | 87.8912 | 105.7574 | 41.1716 | 21.3197 | 79.5451
BRLE4 R2 | 400 | 123.8196 | 44.5157 | 24.9365 | 87.8912 | 105.7574 | 41.1716 | 21.3197 | 79.5451
BULL4 MC1 | 400 | 70.2287 | 25.6875 | 15.646 | 51.9736 | 52.5766 | 20.6543 | 9.3077 | 38.5173
BULL4 MC2 | 400 | 70.2287 | 25.6875 | 15.646 | 51.9736 | 52.5766 | 20.6543 | 9.3077 | 38.5173
BURW4 MC1 | 400 | 94.1866 | 34.1867 | 23.016 | 71.3632 | 62.8054 | 25.0169 | 11.4283 | 46.8076
BURW4 MC2 | 400 | 94.1866 | 34.1867 | 23.016 | 71.3632 | 62.8054 | 25.0169 | 11.4283 | 46.8076
BURW4 MC3 | 400 | 94.1866 | 34.1867 | 23.016 | 71.3632 | 62.8054 | 25.0169 | 11.4283 | 46.8076
BURW4 MC4 | 400 | 94.1866 | 34.1867 | 23.016 | 71.3632 | 62.8054 | 25.0169 | 11.4283 | 46.8076
BUSH2 MC1 | 275 | 55.8691 | 20.4895 | 11.4245 | 40.401 | 55.5823 | 21.6771 | 10.4763 | 41.1322
BUSH2 MC2 | 275 | 55.8691 | 20.4895 | 11.4245 | 40.401 | 55.5823 | 21.6771 | 10.4763 | 41.1322
BUSH2 MC3 | 275 | 55.8691 | 20.4895 | 11.4245 | 40.401 | 55.5823 | 21.6771 | 10.4763 | 41.1322
BUSH2 MC4 | 275 | 55.8691 | 20.4895 | 11.4245 | 40.401 | 55.5823 | 21.6771 | 10.4763 | 41.1322
BUST2 M1 | 275 | 72.649 | 26.192 | 18.9736 | 56.0146 | 75.2954 | 28.7298 | 17.7414 | 58.3715
BUST2 M2 | 275 | 72.649 | 26.192 | 18.9736 | 56.0146 | 75.2954 | 28.7298 | 17.7414 | 58.3715
BUST2 R1 | 275 | 72.649 | 26.192 | 18.9736 | 56.0146 | 75.2954 | 28.7298 | 17.7414 | 58.3715
BUST2 R2 | 275 | 72.649 | 26.192 | 18.9736 | 56.0146 | 75.2954 | 28.7298 | 17.7414 | 58.3715
CANT4 MC1 | 400 | 89.3495 | 32.379 | 18.9673 | 64.7581 | 69.7255 | 27.467 | 12.932 | 51.7762
CANT4 MC2 | 400 | 89.3495 | 32.379 | 18.9673 | 64.7581 | 69.7255 | 27.467 | 12.932 | 51.7762
CANT4 MC3 | 400 | 89.3495 | 32.379 | 18.9673 | 64.7581 | 69.7255 | 27.467 | 12.932 | 51.7762
CANT4 MC4 | 400 | 89.3495 | 32.379 | 18.9673 | 64.7581 | 69.7255 | 27.467 | 12.932 | 51.7762
CANT4 R5 | 400 | 89.3495 | 32.379 | 18.9673 | 64.7581 | 69.7255 | 27.467 | 12.932 | 51.7762
CANT4 R5 | 400 | 89.3617 | 32.3841 | 18.9698 | 64.7679 | 69.7337 | 27.4696 | 12.9355 | 51.7834
CANT4 R5 | 400 | 89.3617 | 32.3841 | 18.9698 | 64.7679 | 69.7337 | 27.4696 | 12.9355 | 51.7834
CAPE2 M1 | 275 | 68.8552 | 24.1031 | 21.7908 | 55.8777 | 77.5273 | 28.4198 | 23.2722 | 63.4639
CAPE2 M2 | 275 | 68.8552 | 24.1031 | 21.7908 | 55.8777 | 77.5273 | 28.4198 | 23.2722 | 63.4639
CAPE2 R1 | 275 | 68.8552 | 24.1031 | 21.7908 | 55.8777 | 77.5273 | 28.4198 | 23.2722 | 63.4639
CAPE2 R2 | 275 | 68.8552 | 24.1031 | 21.7908 | 55.8777 | 77.5273 | 28.4198 | 23.2722 | 63.4639
CAPE4A | 400 | 93.4234 | 32.9881 | 24.1385 | 70.7906 | 85.8597 | 32.5372 | 19.5047 | 65.5193
CAPE4B | 400 | 93.4261 | 32.9892 | 24.138 | 70.7918 | 86.5822 | 32.8064 | 19.6186 | 66.0138
CARE2 MC1 | 275 | 50.0782 | 18.7981 | 8.9907 | 35.5753 | 41.9945 | 16.6843 | 7.4507 | 31.0458
CARE2 MC2 | 275 | 50.0782 | 18.7981 | 8.9907 | 35.5753 | 41.9945 | 16.6843 | 7.4507 | 31.0458
CARR1 M1 | 132 | 33.5969 | 12.4166 | 9.5773 | 27.1371 | 39.5466 | 15.0791 | 11.4159 | 32.7409
CARR1 M2 | 132 | 33.5969 | 12.4166 | 9.5773 | 27.1371 | 39.5466 | 15.0791 | 11.4159 | 32.7409
CARR1 M3 | 132 | 33.5969 | 12.4166 | 9.5773 | 27.1371 | 39.5466 | 15.0791 | 11.4159 | 32.7409
CARR1 M4 | 132 | 42.3727 | 14.8905 | 14.1666 | 35.2249 | 54.3536 | 19.9286 | 17.6619 | 45.8451
CARR1 R1 | 132 | 33.5969 | 12.4166 | 9.5773 | 27.1371 | 39.5466 | 15.0791 | 11.4159 | 32.7409
CARR1 R2 | 132 | 33.5969 | 12.4166 | 9.5773 | 27.1371 | 39.5466 | 15.0791 | 11.4159 | 32.7409
CARR1 R3 | 132 | 42.3727 | 14.8905 | 14.1666 | 35.2249 | 54.3536 | 19.9286 | 17.6619 | 45.8451
CARR1 R4 | 132 | 42.3727 | 14.8905 | 14.1666 | 35.2249 | 54.3536 | 19.9286 | 17.6619 | 45.8451
CARR1B | 132 | 41.5662 | 14.4416 | 8.0521 | 28.4757 | 51.4059 | 19.3885 | 7.0335 | 34.453
CARR1C | 132 | 41.3934 | 14.425 | 7.6397 | 28.0397 | 50.9446 | 19.3391 | 5.5686 | 32.9182
CARR1D | 132 | 41.6786 | 14.461 | 8.2876 | 28.7385 | 51.7918 | 19.4393 | 7.4038 | 34.8952
CARR2 M1 | 275 | 81.9234 | 29.6017 | 21.9458 | 63.809 | 88.6184 | 33.3553 | 24.1894 | 71.3609
CARR2 M2 | 275 | 81.9234 | 29.6017 | 21.9458 | 63.809 | 88.6184 | 33.3553 | 24.1894 | 71.3609
CARR2 R1 | 275 | 81.9234 | 29.6017 | 21.9458 | 63.809 | 88.6184 | 33.3553 | 24.1894 | 71.3609
CARR2 R2 | 275 | 81.9234 | 29.6017 | 21.9458 | 63.809 | 88.6184 | 33.3553 | 24.1894 | 71.3609
CARR4 M1 | 400 | 121.433 | 44.6151 | 35.9825 | 99.0778 | 106.7596 | 41.4175 | 30.9467 | 89.5199
CARR4 M2/4 | 400 | 121.433 | 44.6151 | 35.9825 | 99.0778 | 106.7596 | 41.4175 | 30.9467 | 89.5199
CARR4 R1 | 400 | 121.433 | 44.6151 | 35.9825 | 99.0778 | 106.7596 | 41.4175 | 30.9467 | 89.5199
CARR4 R1/2 | 400 | 121.433 | 44.6151 | 35.9825 | 99.0778 | 106.7596 | 41.4175 | 30.9467 | 89.5199
CARR4 R2 | 400 | 121.433 | 44.6151 | 35.9825 | 99.0778 | 106.7596 | 41.4175 | 30.9467 | 89.5199
CARR4 R4 | 400 | 121.433 | 44.6151 | 35.9825 | 99.0778 | 106.7596 | 41.4175 | 30.9467 | 89.5199
CARR4A | 400 | 102.0505 | 36.3619 | 8.9167 | 60.3402 | 83.7392 | 32.4886 | 8.5541 | 54.5
CARR4B | 400 | 103.8271 | 36.9234 | 9.1712 | 61.3888 | 86.3035 | 33.4888 | 8.5981 | 55.9583
CASK1 M1 | 132 | 48.3193 | 16.0671 | 12.9951 | 35.7175 | 53.6054 | 18.828 | 15.7186 | 42.3454
CELL1 M1 | 132 | 45.5746 | 16.9269 | 14.295 | 38.2333 | 56.6976 | 22.3161 | 16.8561 | 48.4159
CELL1 M2 | 132 | 43.5259 | 16.1302 | 12.0598 | 34.8713 | 48.2719 | 18.6753 | 12.931 | 39.3418
CELL1 R1 | 132 | 45.5746 | 16.9269 | 14.295 | 38.2333 | 56.6976 | 22.3161 | 16.8561 | 48.4159
CELL1 R2 | 132 | 43.5259 | 16.1302 | 12.0598 | 34.8713 | 48.2719 | 18.6753 | 12.931 | 39.3418
CELL1A | 132 | 38.1161 | 13.6435 | 6.9588 | 26.2536 | 47.101 | 18.8524 | 8.3335 | 34.9948
CELL4 M1 | 400 | 91.6497 | 33.8727 | 16.3918 | 64.2951 | 75.5904 | 29.8618 | 14.1731 | 56.4041
CELL4 M2 | 400 | 91.6497 | 33.8727 | 16.3918 | 64.2951 | 75.5904 | 29.8618 | 14.1731 | 56.4041
CELL4 R1 | 400 | 91.6497 | 33.8727 | 16.3918 | 64.2951 | 75.5904 | 29.8618 | 14.1731 | 56.4041
CELL4 R2 | 400 | 91.6497 | 33.8727 | 16.3918 | 64.2951 | 75.5904 | 29.8618 | 14.1731 | 56.4041
CHIC4 MB1 | 400 | 37.1274 | 13.854 | 7.4405 | 27.033 | 30.3786 | 11.8686 | 5.7692 | 22.5539
CHIC4 MB2 | 400 | 37.1274 | 13.854 | 7.4405 | 27.033 | 30.3786 | 11.8686 | 5.7692 | 22.5539
CHIC4 R1/2 | 400 | 36.7986 | 13.8969 | 10.7919 | 30.4452 | 28.8365 | 11.3531 | 7.7343 | 23.7899
CHSI2 MC1 | 275 | 86.3172 | 31.0887 | 18.717 | 62.683 | 74.884 | 29.5493 | 12.2648 | 54.0539
CHSI2 MC2 | 275 | 86.3172 | 31.0887 | 18.717 | 62.683 | 74.884 | 29.5493 | 12.2648 | 54.0539
CHSI2 MC3 | 275 | 86.3172 | 31.0887 | 18.717 | 62.683 | 74.884 | 29.5493 | 12.2648 | 54.0539
CHSI2 MC4 | 275 | 86.3172 | 31.0887 | 18.717 | 62.683 | 74.884 | 29.5493 | 12.2648 | 54.0539
CHTE2 MC1 | 275 | 70.1034 | 25.341 | 16.8345 | 52.6721 | 59.5769 | 23.6436 | 11.0796 | 44.5167
CHTE2 MC2 | 275 | 70.1034 | 25.341 | 16.8345 | 52.6721 | 59.5769 | 23.6436 | 11.0796 | 44.5167
CHTE2 MC3 | 275 | 70.1034 | 25.341 | 16.8345 | 52.6721 | 59.5769 | 23.6436 | 11.0796 | 44.5167
CHTE2 MC4 | 275 | 70.1034 | 25.341 | 16.8345 | 52.6721 | 59.5769 | 23.6436 | 11.0796 | 44.5167
CILF4 M1 | 400 | 84.8644 | 30.5125 | 21.1024 | 64.2535 | 73.3996 | 28.3059 | 14.6538 | 54.6845
CILF4 M2 | 400 | 84.8644 | 30.5125 | 21.1024 | 64.2535 | 73.3996 | 28.3059 | 14.6538 | 54.6845
CILF4 R1 | 400 | 84.8644 | 30.5125 | 21.1024 | 64.2535 | 73.3996 | 28.3059 | 14.6538 | 54.6845
CILF4 R2 | 400 | 84.8644 | 30.5125 | 21.1024 | 64.2535 | 73.3996 | 28.3059 | 14.6538 | 54.6845
CITR4 M5 | 400 | 115.5115 | 39.1708 | 27.9914 | 83.3872 | 128.1475 | 48.571 | 25.5052 | 94.195
CITR4 M6 | 400 | 115.5115 | 39.1708 | 27.9914 | 83.3872 | 128.1475 | 48.571 | 25.5052 | 94.195
CITR4 MC1 | 400 | 115.5165 | 39.172 | 27.9933 | 83.391 | 128.1676 | 48.5739 | 25.5559 | 94.2498
CITR4 MC2 | 400 | 115.5165 | 39.172 | 27.9933 | 83.391 | 128.1676 | 48.5739 | 25.5559 | 94.2498
CITR4 MC3 | 400 | 115.5165 | 39.172 | 27.9933 | 83.391 | 128.1676 | 48.5739 | 25.5559 | 94.2498
CITR4 MC4 | 400 | 115.5165 | 39.172 | 27.9933 | 83.391 | 128.1676 | 48.5739 | 25.5559 | 94.2498
CITR4 R5 | 400 | 115.5115 | 39.1708 | 27.9914 | 83.3872 | 128.1475 | 48.571 | 25.5052 | 94.195
CITR4 R6 | 400 | 115.5115 | 39.1708 | 27.9914 | 83.3872 | 128.1475 | 48.571 | 25.5052 | 94.195
CLEH4 M1 | 400 | 77.4974 | 28.1635 | 16.8461 | 56.6753 | 69.8383 | 27.3424 | 14.0774 | 52.7454
CLEH4 R1 | 400 | 77.4974 | 28.1635 | 16.8461 | 56.6753 | 69.8383 | 27.3424 | 14.0774 | 52.7454
CONQ4 M1 | 400 | 126.4937 | 43.9113 | 32.9222 | 95.0222 | 129.0409 | 47.9834 | 34.8526 | 102.7113
CONQ4 M2 | 400 | 126.4937 | 43.9113 | 32.9222 | 95.0222 | 129.0409 | 47.9834 | 34.8526 | 102.7113
CONQ4 M3 | 400 | 126.4937 | 43.9113 | 32.9222 | 95.0222 | 129.0409 | 47.9834 | 34.8526 | 102.7113
CONQ4 M4 | 400 | 126.4937 | 43.9113 | 32.9222 | 95.0222 | 129.0409 | 47.9834 | 34.8526 | 102.7113
CONQ4 R1/3 | 400 | 126.4937 | 43.9113 | 32.9222 | 95.0222 | 129.0409 | 47.9834 | 34.8526 | 102.7113
CONQ4 R2/4 | 400 | 126.4937 | 43.9113 | 32.9222 | 95.0222 | 129.0409 | 47.9834 | 34.8526 | 102.7113
COSO4 M | 400 | 103.8156 | 36.6524 | 24.0075 | 75.8418 | 90.4245 | 34.5842 | 20.8574 | 69.7669
COSO4 R | 400 | 103.8156 | 36.6524 | 24.0075 | 75.8418 | 90.4245 | 34.5842 | 20.8574 | 69.7669
COTT4 M1 | 400 | 104.2809 | 38.3292 | 24.2375 | 78.4432 | 83.988 | 32.6672 | 16.8293 | 63.0277
COTT4 M2 | 400 | 104.2809 | 38.3292 | 24.2375 | 78.4432 | 83.988 | 32.6672 | 16.8293 | 63.0277
COTT4 M3 | 400 | 104.6097 | 38.8538 | 32.9165 | 87.8641 | 85.3312 | 33.2305 | 24.9395 | 71.9346
COTT4 M4 | 400 | 104.6097 | 38.8538 | 32.9165 | 87.8641 | 85.3312 | 33.2305 | 24.9395 | 71.9346
COTT4 R1/2 | 400 | 104.6097 | 38.8538 | 32.9165 | 87.8641 | 85.3312 | 33.2305 | 24.9395 | 71.9346
COTT4 R3/4 | 400 | 104.6097 | 38.8538 | 32.9165 | 87.8641 | 85.3312 | 33.2305 | 24.9395 | 71.9346
COVE2 MC1 | 275 | 62.3214 | 22.6835 | 12.7496 | 44.8289 | 58.4953 | 22.7048 | 11.9456 | 44.055
COVE2 MC2 | 275 | 62.3214 | 22.6835 | 12.7496 | 44.8289 | 58.4953 | 22.7048 | 11.9456 | 44.055
COVE2 MC3 | 275 | 62.3214 | 22.6835 | 12.7496 | 44.8289 | 58.4953 | 22.7048 | 11.9456 | 44.055
COVE2 MC4 | 275 | 62.3214 | 22.6835 | 12.7496 | 44.8289 | 58.4953 | 22.7048 | 11.9456 | 44.055
COWL4 M1 | 400 | 126.6009 | 46.6659 | 38.1308 | 104.1263 | 105.6719 | 41.1595 | 29.7475 | 87.9558
COWL4 M2 | 400 | 126.6009 | 46.6659 | 38.1308 | 104.1263 | 105.6719 | 41.1595 | 29.7475 | 87.9558
COWL4 R1 | 400 | 126.6009 | 46.6659 | 38.1308 | 104.1263 | 105.6719 | 41.1595 | 29.7475 | 87.9558
COWL4 R2 | 400 | 126.6009 | 46.6659 | 38.1308 | 104.1263 | 105.6719 | 41.1595 | 29.7475 | 87.9558
CREB2A | 275 | 72.9458 | 25.9103 | 15.8999 | 52.5426 | 70.7773 | 26.301 | 12.868 | 50.0632
CREB2B | 275 | 72.9563 | 25.9108 | 15.9077 | 52.5511 | 71.5734 | 26.5895 | 13.0144 | 50.6176
CREB4 MB1 | 400 | 126.4095 | 45.2798 | 31.7964 | 95.8317 | 102.4709 | 39.4738 | 22.761 | 78.5854
CREB4 MB2 | 400 | 126.4095 | 45.2798 | 31.7964 | 95.8317 | 102.4709 | 39.4738 | 22.761 | 78.5854
CREB4 RB1 | 400 | 126.4095 | 45.2798 | 31.7964 | 95.8317 | 102.4709 | 39.4738 | 22.761 | 78.5854
CREB4 RB2 | 400 | 126.4095 | 45.2798 | 31.7964 | 95.8317 | 102.4709 | 39.4738 | 22.761 | 78.5854
DAIN4 M1 | 400 | 112.8866 | 40.8208 | 23.1682 | 80.8975 | 96.4244 | 37.4331 | 19.3248 | 72.2632
DAIN4 M2 | 400 | 112.8866 | 40.8208 | 23.1682 | 80.8975 | 96.4244 | 37.4331 | 19.3248 | 72.2632
DAIN4 R1 | 400 | 115.5328 | 41.6747 | 23.9642 | 82.9011 | 97.6716 | 37.9378 | 19.6652 | 73.3173
DAIN4 R2 | 400 | 115.5328 | 41.6747 | 23.9642 | 82.9011 | 97.6716 | 37.9378 | 19.6652 | 73.3173
DIDC4 M1 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 M2 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 M3 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 M4 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 M5 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 M6 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 R1/2 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 R3/4 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 R5 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DIDC4 R6 | 400 | 120.6763 | 43.4743 | 26.8052 | 88.2872 | 109.8924 | 41.7989 | 26.8205 | 85.9331
DINO4 1 | 400 | 71.9404 | 25.0372 | 20.4843 | 55.8922 | 75.3411 | 27.689 | 22.7501 | 61.9083
DINO4 2 | 400 | 71.9404 | 25.0372 | 20.4843 | 55.8922 | 75.3411 | 27.689 | 22.7501 | 61.9083
DINO4 3 | 400 | 71.9404 | 25.0372 | 20.4843 | 55.8922 | 75.3411 | 27.689 | 22.7501 | 61.9083
DRAK1 M1 | 132 | 31.7964 | 11.3852 | 12.8548 | 28.9559 | 39.2491 | 14.4889 | 15.9445 | 36.4349
DRAK1 M2 | 132 | 31.7964 | 11.3852 | 12.8548 | 28.9559 | 39.2491 | 14.4889 | 15.9445 | 36.4349
DRAK1 R1 | 132 | 31.7964 | 11.3852 | 12.8548 | 28.9559 | 39.2491 | 14.4889 | 15.9445 | 36.4349
DRAK1 R2 | 132 | 31.7964 | 11.3852 | 12.8548 | 28.9559 | 39.2491 | 14.4889 | 15.9445 | 36.4349
DRAK4 M1 | 400 | 122.7304 | 44.2456 | 23.0976 | 85.6704 | 109.4641 | 42.9839 | 18.4721 | 79.2605
DRAK4 M2 | 400 | 122.7304 | 44.2456 | 23.0976 | 85.6704 | 109.4641 | 42.9839 | 18.4721 | 79.2605
DRAK4 M3 | 400 | 122.7304 | 44.2456 | 23.0976 | 85.6704 | 109.4641 | 42.9839 | 18.4721 | 79.2605
DRAK4 R1/3 | 400 | 122.7304 | 44.2456 | 23.0976 | 85.6704 | 109.4641 | 42.9839 | 18.4721 | 79.2605
DRAK4 R2 | 400 | 122.7304 | 44.2456 | 23.0976 | 85.6704 | 109.4641 | 42.9839 | 18.4721 | 79.2605
DRAX1 M1 | 132 | 39.2879 | 11.8903 | 11.7315 | 28.5469 | 49.1817 | 16.7176 | 14.8316 | 38.474
DRAX1 M2 | 132 | 39.2879 | 11.8903 | 11.7315 | 28.5469 | 49.1817 | 16.7176 | 14.8316 | 38.474
DRAX1 R1 | 132 | 39.2879 | 11.8903 | 11.7315 | 28.5469 | 49.1817 | 16.7176 | 14.8316 | 38.474
DRAX1 R2 | 132 | 39.2879 | 11.8903 | 11.7315 | 28.5469 | 49.1817 | 16.7176 | 14.8316 | 38.474
DRAX4 M1 | 400 | 138.4162 | 48.3624 | 37.4922 | 105.8869 | 139.5892 | 51.5728 | 39.3335 | 112.2686
DRAX4 M2 | 400 | 138.4162 | 48.3624 | 37.4922 | 105.8869 | 139.5892 | 51.5728 | 39.3335 | 112.2686
DRAX4 M3 | 400 | 138.4162 | 48.3624 | 37.4922 | 105.8869 | 139.5892 | 51.5728 | 39.3335 | 112.2686
DRAX4 M4 | 400 | 114.265 | 39.883 | 33.4435 | 89.8465 | 120.4083 | 44.209 | 35.9205 | 98.4415
DRAX4 M5 | 400 | 114.265 | 39.883 | 33.4435 | 89.8465 | 120.4083 | 44.209 | 35.9205 | 98.4415
DRAX4 M6 | 400 | 114.265 | 39.883 | 33.4435 | 89.8465 | 120.4083 | 44.209 | 35.9205 | 98.4415
DRAX4 R1/2/3 | 400 | 138.4162 | 48.3624 | 37.4922 | 105.8869 | 139.5892 | 51.5728 | 39.3335 | 112.2686
DRAX4 R4/5/6 | 400 | 114.265 | 39.883 | 33.4435 | 89.8465 | 120.4083 | 44.209 | 35.9205 | 98.4415
DUNG2 M1 | 275 | 45.5992 | 16.2618 | 15.2658 | 38.2635 | 46.677 | 17.1908 | 15.4272 | 39.7387
DUNG2 M2 | 275 | 45.5992 | 16.2618 | 15.2658 | 38.2635 | 46.677 | 17.1908 | 15.4272 | 39.7387
DUNG2 R1 | 275 | 45.5992 | 16.2618 | 15.2658 | 38.2635 | 46.677 | 17.1908 | 15.4272 | 39.7387
DUNG2 R2 | 275 | 45.5992 | 16.2618 | 15.2658 | 38.2635 | 46.677 | 17.1908 | 15.4272 | 39.7387
DUNG4 M1 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
DUNG4 M2 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
DUNG4 M3 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
DUNG4 M4 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
DUNG4 M5 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
DUNG4 R1/2 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
DUNG4 R4/5 | 400 | 79.2493 | 28.0896 | 12.8551 | 52.5798 | 72.6435 | 27.3434 | 14.0871 | 52.7564
EALI2 MC1 | 275 | 60.3508 | 21.2299 | 13.9059 | 43.9295 | 66.1336 | 25.691 | 8.5339 | 44.8664
EALI2 MC2 | 275 | 60.3508 | 21.2299 | 13.9059 | 43.9295 | 66.1336 | 25.691 | 8.5339 | 44.8664
EALI2 MC3 | 275 | 60.3508 | 21.2299 | 13.9059 | 43.9295 | 66.1336 | 25.691 | 8.5339 | 44.8664
EALI2 MC4 | 275 | 60.3508 | 21.2299 | 13.9059 | 43.9295 | 66.1336 | 25.691 | 8.5339 | 44.8664
EASO4 M1 | 400 | 85.1859 | 30.8521 | 19.9789 | 63.6104 | 75.2124 | 28.4579 | 20.2098 | 60.4554
EASO4 M2 | 400 | 85.1859 | 30.8521 | 19.9789 | 63.6104 | 75.2124 | 28.4579 | 20.2098 | 60.4554
EASO4 R1 | 400 | 85.1859 | 30.8521 | 19.9789 | 63.6104 | 75.2124 | 28.4579 | 20.2098 | 60.4554
EASO4 R2 | 400 | 85.1859 | 30.8521 | 19.9789 | 63.6104 | 75.2124 | 28.4579 | 20.2098 | 60.4554
EASO4A | 400 | 85.1859 | 30.8521 | 19.9789 | 63.6104 | 75.2124 | 28.4579 | 20.2098 | 60.4554
EASO4B | 400 | 85.1859 | 30.8521 | 19.9789 | 63.6104 | 75.2124 | 28.4579 | 20.2098 | 60.4554
ECLA1 M1 | 132 | 45.2925 | 16.9698 | 13.0368 | 37.0357 | 47.7541 | 18.6396 | 14.2248 | 40.5852
ECLA1 M2 | 132 | 45.2925 | 16.9698 | 13.0368 | 37.0357 | 47.7541 | 18.6396 | 14.2248 | 40.5852
ECLA1 R1 | 132 | 45.8751 | 17.1259 | 13.2073 | 37.427 | 54.6464 | 21.114 | 15.9204 | 45.7801
ECLA1 R2 | 132 | 45.8751 | 17.1259 | 13.2073 | 37.427 | 54.6464 | 21.114 | 15.9204 | 45.7801
ECLA4 M1 | 400 | 113.8427 | 41.4938 | 23.7858 | 82.4669 | 91.8827 | 36.0563 | 17.4554 | 68.4468
ECLA4 M2 | 400 | 113.8427 | 41.4938 | 23.7858 | 82.4669 | 91.8827 | 36.0563 | 17.4554 | 68.4468
ECLA4 R1 | 400 | 113.8427 | 41.4938 | 23.7858 | 82.4669 | 91.8827 | 36.0563 | 17.4554 | 68.4468
ECLA4 R2 | 400 | 113.8427 | 41.4938 | 23.7858 | 82.4669 | 91.8827 | 36.0563 | 17.4554 | 68.4468
EGGB4 M1 | 400 | 108.169 | 38.8115 | 26.394 | 81.2818 | 97.1453 | 37.0655 | 20.7502 | 73.1688
EGGB4 M2 | 400 | 108.169 | 38.8115 | 26.394 | 81.2818 | 97.1453 | 37.0655 | 20.7502 | 73.1688
EGGB4 R1 | 400 | 93.3598 | 33.2602 | 25.0152 | 72.0522 | 86.0844 | 32.6063 | 19.596 | 65.7083
EGGB4 R2 | 400 | 93.3598 | 33.2602 | 25.0152 | 72.0522 | 86.0844 | 32.6063 | 19.596 | 65.7083
ELLA2 MC1 | 275 | 63.9376 | 23.154 | 8.2557 | 41.0004 | 64.4667 | 24.8619 | 7.9336 | 43.0935
ELLA2 MC2 | 275 | 63.9376 | 23.154 | 8.2557 | 41.0004 | 64.4667 | 24.8619 | 7.9336 | 43.0935
ELLA2 MC3 | 275 | 63.9376 | 23.154 | 8.2557 | 41.0004 | 64.4667 | 24.8619 | 7.9336 | 43.0935
ELLA2 MC4 | 275 | 63.9376 | 23.154 | 8.2557 | 41.0004 | 64.4667 | 24.8619 | 7.9336 | 43.0935
ELST1 M1 | 132 | 31.7475 | 11.5373 | 10.0957 | 26.4119 | 38.7728 | 14.5156 | 12.1239 | 32.652
ELST1 M2 | 132 | 45.6124 | 16.1733 | 13.5712 | 36.4437 | 56.7743 | 21.5722 | 15.9275 | 46.4352
ELST1 M3 | 132 | 39.3642 | 14.5554 | 9.8224 | 30.4069 | 45.5737 | 17.43 | 11.6941 | 36.3438
ELST1 R1 | 132 | 31.7475 | 11.5373 | 10.0957 | 26.4119 | 38.7728 | 14.5156 | 12.1239 | 32.652
ELST1 R2 | 132 | 45.6124 | 16.1733 | 13.5712 | 36.4437 | 56.7743 | 21.5722 | 15.9275 | 46.4352
ELST1 R3 | 132 | 39.3642 | 14.5554 | 9.8224 | 30.4069 | 45.5737 | 17.43 | 11.6941 | 36.3438
ELST2 M1 | 275 | 64.991 | 23.5482 | 16.8145 | 50.1166 | 71.2773 | 26.8695 | 18.6797 | 56.6789
ELST2 M2 | 275 | 67.0962 | 24.4529 | 14.9068 | 49.4884 | 73.9379 | 28.4347 | 15.7916 | 56.0043
ELST2 R1 | 275 | 64.991 | 23.5482 | 16.8145 | 50.1166 | 71.2773 | 26.8695 | 18.6797 | 56.6789
ELST2 R2 | 275 | 67.0962 | 24.4529 | 14.9068 | 49.4884 | 73.9379 | 28.4347 | 15.7916 | 56.0043
ELST4 M1 | 400 | 93.3904 | 33.6365 | 29.2126 | 76.7818 | 110.5067 | 41.8128 | 33.8531 | 92.9853
ELST4 R1 | 400 | 93.3904 | 33.6365 | 29.2126 | 76.7818 | 110.5067 | 41.8128 | 33.8531 | 92.9853
ELST4A | 400 | 57.22 | 21.0487 | 7.6009 | 37.3683 | 54.34 | 20.6714 | 8.5845 | 37.8183
ENDE4 MC1 | 400 | 92.6633 | 34.1912 | 18.1123 | 66.4659 | 63.0192 | 25.0714 | 10.927 | 46.3833
ENDE4 MC2 | 400 | 92.6633 | 34.1912 | 18.1123 | 66.4659 | 63.0192 | 25.0714 | 10.927 | 46.3833
ENDE4 MC3 | 400 | 92.6633 | 34.1912 | 18.1123 | 66.4659 | 63.0192 | 25.0714 | 10.927 | 46.3833
ENDE4 MC4 | 400 | 92.6633 | 34.1912 | 18.1123 | 66.4659 | 63.0192 | 25.0714 | 10.927 | 46.3833
EXET4 M1 | 400 | 59.0596 | 21.5992 | 11.9114 | 42.4572 | 55.5323 | 21.5703 | 11.2498 | 41.7548
EXET4 M2 | 400 | 59.0596 | 21.5992 | 11.9114 | 42.4572 | 55.5323 | 21.5703 | 11.2498 | 41.7548
EXET4 R1 | 400 | 59.0596 | 21.5992 | 11.9114 | 42.4572 | 55.5323 | 21.5703 | 11.2498 | 41.7548
EXET4 R2 | 400 | 59.0596 | 21.5992 | 11.9114 | 42.4572 | 55.5323 | 21.5703 | 11.2498 | 41.7548
FAWL1 M1 | 132 | 50.4134 | 17.7166 | 18.3192 | 43.3743 | 64.1348 | 24.1452 | 21.6769 | 55.8234
FAWL1 M2 | 132 | 50.4134 | 17.7166 | 18.3192 | 43.3743 | 64.1348 | 24.1452 | 21.6769 | 55.8234
FAWL1 R1 | 132 | 50.4134 | 17.7166 | 18.3192 | 43.3743 | 64.1348 | 24.1452 | 21.6769 | 55.8234
FAWL1 R2 | 132 | 50.4134 | 17.7166 | 18.3192 | 43.3743 | 64.1348 | 24.1452 | 21.6769 | 55.8234
FAWL4 M1/3 | 400 | 83.351 | 29.4757 | 10.8551 | 52.54 | 69.8514 | 26.946 | 8.5477 | 46.6552
FAWL4 M1/3(1) | 400 | 83.351 | 29.4757 | 10.8551 | 52.54 | 69.8514 | 26.946 | 8.5477 | 46.6552
FAWL4 M2/4(2) | 400 | 83.351 | 29.4757 | 10.8551 | 52.54 | 69.8514 | 26.946 | 8.5477 | 46.6552
FAWL4 M2/4(3) | 400 | 83.351 | 29.4757 | 10.8551 | 52.54 | 69.8514 | 26.946 | 8.5477 | 46.6552
FAWL4 R1/3 | 400 | 83.351 | 29.4757 | 10.8551 | 52.54 | 69.8514 | 26.946 | 8.5477 | 46.6552
FAWL4 R2/4 | 400 | 83.351 | 29.4757 | 10.8551 | 52.54 | 69.8514 | 26.946 | 8.5477 | 46.6552
FECK2 M1 | 275 | 63.3323 | 23.3181 | 14.4192 | 47.3959 | 62.604 | 24.1266 | 14.2 | 48.3201
FECK2 M2 | 275 | 63.3323 | 23.3181 | 14.4192 | 47.3959 | 62.604 | 24.1266 | 14.2 | 48.3201
FECK2 R | 275 | 63.3323 | 23.3181 | 14.4192 | 47.3959 | 62.604 | 24.1266 | 14.2 | 48.3201
FECK4 M1 | 400 | 79.6485 | 29.8891 | 13.5361 | 55.8056 | 67.2454 | 26.569 | 12.7964 | 50.3707
FECK4 M2 | 400 | 79.6485 | 29.8891 | 13.5361 | 55.8056 | 67.2454 | 26.569 | 12.7964 | 50.3707
FECK4 R1 | 400 | 79.6485 | 29.8891 | 13.5361 | 55.8056 | 67.2454 | 26.569 | 12.7964 | 50.3707
FECK4 R2 | 400 | 79.6485 | 29.8891 | 13.5361 | 55.8056 | 67.2454 | 26.569 | 12.7964 | 50.3707
FENW4A | 400 | 140.7451 | 49.2808 | 16.9227 | 86.6163 | 112.3373 | 43.4512 | 7.6019 | 69.0511
FERR2 M1 | 275 | 57.4886 | 20.8283 | 11.3785 | 40.8342 | 58.4748 | 22.1189 | 11.4223 | 42.7031
FERR2 M2 | 275 | 57.718 | 20.8414 | 15.3093 | 44.7835 | 61.2993 | 22.992 | 14.2554 | 46.771
FERR2 R1 | 275 | 61.9625 | 22.3682 | 12.0518 | 43.6853 | 61.6503 | 23.488 | 10.2763 | 43.4933
FERR2 R2 | 275 | 61.9625 | 22.3682 | 12.0518 | 43.6853 | 61.6503 | 23.488 | 10.2763 | 43.4933
FERR2A | 275 | 57.7455 | 20.7631 | 12.7625 | 42.126 | 61.114 | 22.89 | 11.6499 | 44.0212
FERR2B | 275 | 56.951 | 20.5025 | 9.2098 | 38.2047 | 57.6823 | 21.8293 | 8.8856 | 39.7569
FERR4A | 400 | 77.0983 | 27.6483 | 9.5314 | 48.632 | 66.4886 | 25.325 | 8.0881 | 43.903
FFES2 Term205 | 275 | 35.4519 | 13.2524 | 2.6736 | 21.4153 | 34.4234 | 13.5091 | 2.3382 | 21.4429
FFES2 Term210 | 275 | 35.2906 | 13.212 | 2.6477 | 21.3323 | 34.7945 | 13.652 | 2.3551 | 21.6619
FIDF2 M1 | 275 | 50.8208 | 18.2372 | 15.5461 | 41.3374 | 50.8636 | 18.9844 | 14.06 | 40.9079
FIDF2 M2 | 275 | 50.0451 | 17.9235 | 15.3837 | 40.7313 | 49.0308 | 18.2962 | 13.349 | 39.2237
FIDF2 M3 | 275 | 62.7427 | 22.4996 | 16.0487 | 47.8679 | 58.5731 | 22.2093 | 13.5219 | 44.9306
FIDF2 M4 | 275 | 63.3055 | 22.6973 | 16.185 | 48.2838 | 60.5666 | 22.9334 | 14.1745 | 46.6073
FIDF2 R1 | 275 | 50.8208 | 18.2372 | 15.5461 | 41.3374 | 50.8636 | 18.9844 | 14.06 | 40.9079
FIDF2 R2 | 275 | 63.3055 | 22.6973 | 16.185 | 48.2838 | 60.5666 | 22.9334 | 14.1745 | 46.6073
FLEE4 MC1 | 400 | 106.2246 | 38.2536 | 21.3571 | 75.4559 | 84.85 | 33.365 | 15.7452 | 62.9304
FLEE4 MC2 | 400 | 106.2246 | 38.2536 | 21.3571 | 75.4559 | 84.85 | 33.365 | 15.7452 | 62.9304
FLEE4 MC3 | 400 | 106.2246 | 38.2536 | 21.3571 | 75.4559 | 84.85 | 33.365 | 15.7452 | 62.9304
FLEE4 MC4 | 400 | 106.2246 | 38.2536 | 21.3571 | 75.4559 | 84.85 | 33.365 | 15.7452 | 62.9304
FLIB4 M1 | 400 | 117.0821 | 40.8695 | 30.5048 | 88.3029 | 120.3747 | 45.2199 | 29.7977 | 93.7483
FLIB4 M2 | 400 | 117.0821 | 40.8695 | 30.5048 | 88.3029 | 120.3747 | 45.2199 | 29.7977 | 93.7483
FOUR2 MC1 | 275 | 37.4324 | 14.6743 | 4.9048 | 25.6574 | 31.2252 | 12.8105 | 3.8821 | 21.9989
FOUR2 MC2 | 275 | 37.4324 | 14.6743 | 4.9048 | 25.6574 | 31.2252 | 12.8105 | 3.8821 | 21.9989
FROD2 MC1 | 275 | 50.7697 | 18.169 | 16.329 | 42.0238 | 53.9009 | 19.8315 | 17.4025 | 45.4486
FROD2 MC3 | 275 | 50.762 | 17.9267 | 10.7665 | 36.1187 | 53.2343 | 19.5447 | 10.6363 | 38.2766
FROD4 M1 | 400 | 88.9196 | 32.0609 | 29.6819 | 75.0228 | 83.3414 | 31.3921 | 27.6508 | 72.046
FROD4 R1 | 400 | 88.9196 | 32.0609 | 29.6819 | 75.0228 | 83.3414 | 31.3921 | 27.6508 | 72.046
GART4A | 400 | 102.3897 | 36.4867 | 13.7018 | 65.3018 | 83.6337 | 32.1523 | 6.8163 | 52.2865
GART4B | 400 | 143.4794 | 50.3561 | 19.0475 | 90.2618 | 116.1113 | 44.8502 | 8.8478 | 72.2755
GRAI4 M1 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 M2 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 M3 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 M4 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 M5 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 M6 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 M7 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 R1/2 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 R3 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 R4 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 R5 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 R6 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GRAI4 R7 | 400 | 139.2557 | 48.8031 | 45.2346 | 114.2526 | 128.6746 | 48.4328 | 41.2723 | 109.7667
GREN1 M1 | 132 | 40.7713 | 14.9495 | 10.5951 | 31.737 | 44.5741 | 17.7816 | 10.4194 | 35.5664
GREN1 M2 | 132 | 39.4761 | 14.5697 | 11.2127 | 31.8174 | 40.3599 | 15.85 | 10.3425 | 32.7578
GREN1 R1 | 132 | 40.7713 | 14.9495 | 10.5951 | 31.737 | 44.5741 | 17.7816 | 10.4194 | 35.5664
GREN1 R2 | 132 | 39.4761 | 14.5697 | 11.2127 | 31.8174 | 40.3599 | 15.85 | 10.3425 | 32.7578
GREN4 M1 | 400 | 80.7784 | 30.3526 | 13.337 | 56.2622 | 54.253 | 22.0256 | 9.0258 | 40.1747
GREN4 M2 | 400 | 80.7784 | 30.3526 | 13.337 | 56.2622 | 54.253 | 22.0256 | 9.0258 | 40.1747
GREN4 R1 | 400 | 80.7784 | 30.3526 | 13.337 | 56.2622 | 54.253 | 22.0256 | 9.0258 | 40.1747
GREN4 R2 | 400 | 80.7784 | 30.3526 | 13.337 | 56.2622 | 54.253 | 22.0256 | 9.0258 | 40.1747
GRIW4 MC1 | 400 | 75.72 | 27.4994 | 19.6189 | 58.5089 | 63.4269 | 24.5535 | 12.5287 | 47.2527
GRIW4 MC2 | 400 | 75.72 | 27.4994 | 19.6189 | 58.5089 | 63.4269 | 24.5535 | 12.5287 | 47.2527
GRSA2 M1 | 275 | 54.9586 | 19.7428 | 16.547 | 44.4675 | 57.4955 | 21.4148 | 15.9832 | 46.2682
GRSA2 M2 | 275 | 54.9586 | 19.7428 | 16.547 | 44.4675 | 57.4955 | 21.4148 | 15.9832 | 46.2682
GRSA2 R1 | 275 | 54.9586 | 19.7428 | 16.547 | 44.4675 | 57.4955 | 21.4148 | 15.9832 | 46.2682
GRSA2 R2 | 275 | 54.9586 | 19.7428 | 16.547 | 44.4675 | 57.4955 | 21.4148 | 15.9832 | 46.2682
GRSB2 M3 | 275 | 55.2755 | 19.843 | 16.7289 | 44.7911 | 58.4182 | 21.6989 | 16.6856 | 47.3725
GRSB2 M4 | 275 | 55.2755 | 19.843 | 16.7289 | 44.7911 | 58.4182 | 21.6989 | 16.6856 | 47.3725
GRSB2 R3 | 275 | 55.2755 | 19.843 | 16.7289 | 44.7911 | 58.4182 | 21.6989 | 16.6856 | 47.3725
GRSB2 R4 | 275 | 55.2755 | 19.843 | 16.7289 | 44.7911 | 58.4182 | 21.6989 | 16.6856 | 47.3725
HACK2A | 275 | 70.0651 | 24.7886 | 12.0067 | 47.0631 | 71.307 | 26.7006 | 12.294 | 50.0544
HACK2B | 275 | 69.0674 | 24.4417 | 12.0059 | 46.5717 | 71.7525 | 26.901 | 12.3567 | 50.4004
HACK4 M1 | 400 | 122.0813 | 41.2996 | 29.5684 | 87.9748 | 139.0342 | 51.6044 | 30.7689 | 103.7486
HACK4 M2 | 400 | 122.0813 | 41.2996 | 29.5684 | 87.9748 | 139.0342 | 51.6044 | 30.7689 | 103.7486
HACK4 R1 | 400 | 122.0813 | 41.2996 | 29.5684 | 87.9748 | 139.0342 | 51.6044 | 30.7689 | 103.7486
HACK4 R2 | 400 | 122.0813 | 41.2996 | 29.5684 | 87.9748 | 139.0342 | 51.6044 | 30.7689 | 103.7486
HAMB4A | 400 | 70.508 | 25.098 | 9.3362 | 44.8301 | 58.7097 | 22.8144 | 4.8028 | 37.0673
HAMB4A_HEYS | 400 | 70.508 | 25.098 | 9.3362 | 44.8301 | 58.7097 | 22.8144 | 4.8028 | 37.0673
HAMB4A_PEWO | 400 | 70.508 | 25.098 | 9.3362 | 44.8301 | 58.7097 | 22.8144 | 4.8028 | 37.0673
HAMB4B | 400 | 70.4825 | 25.0891 | 9.3357 | 44.8171 | 58.2388 | 22.6309 | 4.8085 | 36.8134
HAMB4B_HEYS | 400 | 70.4825 | 25.0891 | 9.3357 | 44.8171 | 58.2388 | 22.6309 | 4.8085 | 36.8134
HAMB4B_PEWO | 400 | 70.4825 | 25.0891 | 9.3357 | 44.8171 | 58.2388 | 22.6309 | 4.8085 | 36.8134
HAMH1B | 132 | 47.3472 | 16.3739 | 10.0542 | 33.2104 | 56.6767 | 21.3922 | 6.4788 | 36.7319
HAMH1C | 132 | 46.3404 | 16.139 | 8.7762 | 31.6002 | 54.8676 | 20.4142 | 8.1213 | 36.9913
HAMH4 M1 | 400 | 76.7663 | 28.5454 | 13.6338 | 54.0031 | 71.975 | 28.0997 | 13.8385 | 53.5775
HAMH4 M2 | 400 | 76.7663 | 28.5454 | 13.6338 | 54.0031 | 71.975 | 28.0997 | 13.8385 | 53.5775
HAMH4 R1 | 400 | 76.7663 | 28.5454 | 13.6338 | 54.0031 | 71.975 | 28.0997 | 13.8385 | 53.5775
HAMH4 R2 | 400 | 76.7663 | 28.5454 | 13.6338 | 54.0031 | 71.975 | 28.0997 | 13.8385 | 53.5775
HARK1 M1 | 132 | 28.4509 | 10.7228 | 7.1702 | 22.3346 | 33.4349 | 13.0491 | 7.8202 | 26.2744
HARK1 M2 | 132 | 28.4509 | 10.7228 | 7.1702 | 22.3346 | 33.4349 | 13.0491 | 7.8202 | 26.2744
HARK1 R1 | 132 | 27.5512 | 11.4104 | 6.8346 | 22.9713 | 30.714 | 12.9047 | 7.8819 | 26.1319
HARK1 R2 | 132 | 31.0028 | 11.8772 | 7.953 | 24.7499 | 36.3653 | 14.4159 | 9.2702 | 29.6574
HARK1 R3 | 132 | 31.0028 | 11.8772 | 7.953 | 24.7499 | 36.3653 | 14.4159 | 9.2702 | 29.6574
HARK2 MC1 | 275 | 35.2206 | 13.2957 | 8.8304 | 27.6334 | 37.9463 | 14.5676 | 9.7965 | 30.3982
HARK2 MC11 | 275 | 49.9969 | 18.9571 | 15.4336 | 42.243 | 52.8462 | 20.4208 | 16.4629 | 45.3422
HARK2 MC12 | 275 | 49.9969 | 18.9571 | 15.4336 | 42.243 | 52.8462 | 20.4208 | 16.4629 | 45.3422
HARK2 MC13 | 275 | 49.9969 | 18.9571 | 15.4336 | 42.243 | 52.8462 | 20.4208 | 16.4629 | 45.3422
HARK2 MC2 | 275 | 35.2206 | 13.2957 | 8.8304 | 27.6334 | 37.9463 | 14.5676 | 9.7965 | 30.3982
HARK2 MC3 | 275 | 35.2206 | 13.2957 | 8.8304 | 27.6334 | 37.9463 | 14.5676 | 9.7965 | 30.3982
HARK2 MC4 | 275 | 35.2206 | 13.2957 | 8.8304 | 27.6334 | 37.9463 | 14.5676 | 9.7965 | 30.3982
HARK2 MC6 | 275 | 35.2206 | 13.2957 | 8.8304 | 27.6334 | 37.9463 | 14.5676 | 9.7965 | 30.3982
HARK2 MC8 | 275 | 49.9969 | 18.9571 | 15.4336 | 42.243 | 52.8462 | 20.4208 | 16.4629 | 45.3422
HARK2 MC9 | 275 | 49.9969 | 18.9571 | 15.4336 | 42.243 | 52.8462 | 20.4208 | 16.4629 | 45.3422
HARK4 M1 | 400 | 70.4289 | 26.3707 | 12.0353 | 49.3291 | 56.4096 | 22.0471 | 11.7972 | 42.9765
HARK4 M2 | 400 | 70.4289 | 26.3707 | 12.0353 | 49.3291 | 56.4096 | 22.0471 | 11.7972 | 42.9765
HARK4 R1 | 400 | 70.4289 | 26.3707 | 12.0353 | 49.3291 | 56.4096 | 22.0471 | 11.7972 | 42.9765
HARK4 R2 | 400 | 70.4289 | 26.3707 | 12.0353 | 49.3291 | 56.4096 | 22.0471 | 11.7972 | 42.9765
HARM2 MC1 | 275 | 64.5772 | 23.2759 | 13.9955 | 46.9126 | 55.1856 | 21.5822 | 9.123 | 39.6448
HARM2 MC2 | 275 | 64.5772 | 23.2759 | 13.9955 | 46.9126 | 55.1856 | 21.5822 | 9.123 | 39.6448
HARM2 MC3 | 275 | 64.5772 | 23.2759 | 13.9955 | 46.9126 | 55.1856 | 21.5822 | 9.123 | 39.6448
HARM2 MC4 | 275 | 64.5772 | 23.2759 | 13.9955 | 46.9126 | 55.1856 | 21.5822 | 9.123 | 39.6448
HATL2 M1 | 275 | 90.3188 | 31.2899 | 24.2305 | 68.481 | 92.9966 | 34.4458 | 25.6148 | 74.3285
HATL2 M2 | 275 | 90.3188 | 31.2899 | 24.2305 | 68.481 | 92.9966 | 34.4458 | 25.6148 | 74.3285
HATL2 R1 | 275 | 90.3188 | 31.2899 | 24.2305 | 68.481 | 92.9966 | 34.4458 | 25.6148 | 74.3285
HATL2 R2 | 275 | 90.3188 | 31.2899 | 24.2305 | 68.481 | 92.9966 | 34.4458 | 25.6148 | 74.3285
HAWP2 MC1 | 275 | 77.3841 | 27.55 | 18.1738 | 57.1355 | 69.5748 | 26.9505 | 12.7615 | 50.8753
HAWP2 MC2 | 275 | 77.3841 | 27.55 | 18.1738 | 57.1355 | 69.5748 | 26.9505 | 12.7615 | 50.8753
HAWP2 MC3 | 275 | 77.3841 | 27.55 | 18.1738 | 57.1355 | 69.5748 | 26.9505 | 12.7615 | 50.8753
HAWP2 MC4 | 275 | 77.3841 | 27.55 | 18.1738 | 57.1355 | 69.5748 | 26.9505 | 12.7615 | 50.8753
HEDO2 M1 | 275 | 73.5027 | 26.1588 | 21.4174 | 58.4116 | 77.2034 | 28.5961 | 23.0511 | 63.4921
HEDO2 M2 | 275 | 73.5027 | 26.1588 | 21.4174 | 58.4116 | 77.2034 | 28.5961 | 23.0511 | 63.4921
HEDO2 R1 | 275 | 73.5027 | 26.1588 | 21.4174 | 58.4116 | 77.2034 | 28.5961 | 23.0511 | 63.4921
HEDO2 R2 | 275 | 73.5027 | 26.1588 | 21.4174 | 58.4116 | 77.2034 | 28.5961 | 23.0511 | 63.4921
HEYS1 M1 | 132 | 38.4746 | 13.0117 | 12.5763 | 30.9776 | 44.41 | 16.2048 | 14.3002 | 37.2172
HEYS1 M2 | 132 | 38.4746 | 13.0117 | 12.5763 | 30.9776 | 44.41 | 16.2048 | 14.3002 | 37.2172
HEYS1 R1 | 132 | 38.4746 | 13.0117 | 12.5763 | 30.9776 | 44.41 | 16.2048 | 14.3002 | 37.2172
HEYS1 R2 | 132 | 38.4746 | 13.0117 | 12.5763 | 30.9776 | 44.41 | 16.2048 | 14.3002 | 37.2172
HEYS4 M1 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 M2 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 M3 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 M4 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 M5 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 R1/2 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 R3/4 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HEYS4 R5 | 400 | 99.8269 | 35.9074 | 33.7969 | 84.5777 | 103.8469 | 39.1174 | 35.667 | 90.9874
HIBU4 M1 | 400 | 119.8615 | 40.5323 | 29.321 | 86.6422 | 137.985 | 51.0037 | 31.7347 | 103.8647
HIBU4 M2 | 400 | 119.8615 | 40.5323 | 29.321 | 86.6422 | 137.985 | 51.0037 | 31.7347 | 103.8647
HIBU4 R1 | 400 | 119.8615 | 40.5323 | 29.321 | 86.6422 | 137.985 | 51.0037 | 31.7347 | 103.8647
HIBU4 R2 | 400 | 119.8615 | 40.5323 | 29.321 | 86.6422 | 137.985 | 51.0037 | 31.7347 | 103.8647
HIGM2 M1 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM2 M2 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM2 M3 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM2 R1 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM2 R4 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM2 R5 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM2 R6 | 275 | 62.1966 | 23.1089 | 16.657 | 49.3379 | 57.6146 | 22.7337 | 12.3785 | 44.5288
HIGM4 MC1 | 400 | 80.4703 | 29.7324 | 18.5475 | 60.5954 | 66.8691 | 26.22 | 11.6634 | 48.744
HIGM4 MC2 | 400 | 80.4703 | 29.7324 | 18.5475 | 60.5954 | 66.8691 | 26.22 | 11.6634 | 48.744
HIGM4A | 400 | 64.8759 | 23.7668 | 9.4996 | 43.1108 | 55.2704 | 21.3744 | 5.0557 | 35.2836
HINP2 M1 | 275 | 23.4757 | 8.3934 | 7.8982 | 19.7683 | 25.2628 | 9.2897 | 8.3324 | 21.4701
HINP2 M2 | 275 | 23.8445 | 8.5341 | 7.9433 | 20.0123 | 27.9936 | 10.343 | 8.7571 | 23.3842
HINP4 M1 | 400 | 69.7497 | 25.2715 | 15.8346 | 51.574 | 68.5595 | 26.0472 | 17.8199 | 54.6562
HINP4 M2 | 400 | 69.7497 | 25.2715 | 15.8346 | 51.574 | 68.5595 | 26.0472 | 17.8199 | 54.6562
HINP4 M3 | 400 | 69.7497 | 25.2715 | 15.8346 | 51.574 | 68.5595 | 26.0472 | 17.8199 | 54.6562
HINP4 M4 | 400 | 69.7497 | 25.2715 | 15.8346 | 51.574 | 68.5595 | 26.0472 | 17.8199 | 54.6562
HINP4 R1/2 | 400 | 69.7497 | 25.2715 | 15.8346 | 51.574 | 68.5595 | 26.0472 | 17.8199 | 54.6562
HINP4 R3/4 | 400 | 69.7497 | 25.2715 | 15.8346 | 51.574 | 68.5595 | 26.0472 | 17.8199 | 54.6562
HUMR4 M1 | 400 | 105.9423 | 37.5756 | 28.9707 | 82.1107 | 102.3748 | 38.284 | 27.7936 | 81.9353
HUMR4 M2 | 400 | 105.9423 | 37.5756 | 28.9707 | 82.1107 | 102.3748 | 38.284 | 27.7936 | 81.9353
HUMR4 R1 | 400 | 105.9423 | 37.5756 | 28.9707 | 82.1107 | 102.3748 | 38.284 | 27.7936 | 81.9353
HUMR4 R2 | 400 | 105.9423 | 37.5756 | 28.9707 | 82.1107 | 102.3748 | 38.284 | 27.7936 | 81.9353
HURS2 MC1 | 275 | 71.0713 | 24.8447 | 19.2997 | 54.4354 | 74.8165 | 29.6293 | 16.4047 | 58.3068
HURS2 MC2 | 275 | 71.0713 | 24.8447 | 19.2997 | 54.4354 | 74.8165 | 29.6293 | 16.4047 | 58.3068
HURS2 MC3 | 275 | 71.0713 | 24.8447 | 19.2997 | 54.4354 | 74.8165 | 29.6293 | 16.4047 | 58.3068
HURS2 MC4 | 275 | 71.0713 | 24.8447 | 19.2997 | 54.4354 | 74.8165 | 29.6293 | 16.4047 | 58.3068
HUTT4 MC1 | 400 | 73.6423 | 27.6444 | 21.3703 | 60.4654 | 49.0642 | 19.8744 | 11.4438 | 39.5505
HUTT4 MC2 | 400 | 73.6423 | 27.6444 | 21.3703 | 60.4654 | 49.0642 | 19.8744 | 11.4438 | 39.5505
HUTT4 MC3 | 400 | 73.6423 | 27.6444 | 21.3703 | 60.4654 | 49.0642 | 19.8744 | 11.4438 | 39.5505
HUTT4 MC4 | 400 | 73.6423 | 27.6444 | 21.3703 | 60.4654 | 49.0642 | 19.8744 | 11.4438 | 39.5505
IMPP4 MC1 | 400 | 56.3109 | 20.8532 | 12.7184 | 42.2093 | 47.6352 | 18.426 | 9.9257 | 35.984
IMPP4 MC2 | 400 | 56.3109 | 20.8532 | 12.7184 | 42.2093 | 47.6352 | 18.426 | 9.9257 | 35.984
INDQ4 MC1 | 400 | 36.1176 | 13.5867 | 6.0808 | 25.2952 | 37.7081 | 14.6623 | 7.3107 | 28.0464
INDQ4 MC2 | 400 | 36.1176 | 13.5867 | 6.0808 | 25.2952 | 37.7081 | 14.6623 | 7.3107 | 28.0464
INDQ4 MC3 | 400 | 36.1176 | 13.5867 | 6.0808 | 25.2952 | 37.7081 | 14.6623 | 7.3107 | 28.0464
INDQ4 MC4 | 400 | 36.1176 | 13.5867 | 6.0808 | 25.2952 | 37.7081 | 14.6623 | 7.3107 | 28.0464
IROA1 M1 | 132 | 49.3889 | 18.1125 | 10.7356 | 36.3505 | 58.6394 | 22.675 | 12.0912 | 44.1585
IROA1 M2 | 132 | 49.3889 | 18.1125 | 10.7356 | 36.3505 | 58.6394 | 22.675 | 12.0912 | 44.1585
IROA1 R1 | 132 | 44.8846 | 16.293 | 10.8262 | 33.868 | 53.7633 | 20.4931 | 12.4126 | 41.3943
IROA1 R2 | 132 | 42.5844 | 16.0235 | 9.7951 | 32.4558 | 48.882 | 19.2165 | 10.6247 | 37.8009
IROA2 MC1 | 275 | 58.917 | 21.7494 | 11.1909 | 41.9493 | 56.9131 | 22.1416 | 11.2997 | 42.6127
IROA2 MC2 | 275 | 58.917 | 21.7494 | 11.1909 | 41.9493 | 56.9131 | 22.1416 | 11.2997 | 42.6127
IROA2 MC3 | 275 | 58.917 | 21.7494 | 11.1909 | 41.9493 | 56.9131 | 22.1416 | 11.2997 | 42.6127
IROA2 MC4 | 275 | 58.917 | 21.7494 | 11.1909 | 41.9493 | 56.9131 | 22.1416 | 11.2997 | 42.6127
IROA2 MC5 | 275 | 58.917 | 21.7494 | 11.1909 | 41.9493 | 56.9131 | 22.1416 | 11.2997 | 42.6127
IRON1 M1 | 132 | 27.5473 | 10.6892 | 9.0157 | 24.1325 | 30.5912 | 12.0036 | 10.0059 | 26.9816
IRON1 M2 | 132 | 27.4296 | 10.6473 | 8.9187 | 23.9762 | 30.2702 | 11.8932 | 9.8189 | 26.6384
IRON1 R1 | 132 | 18.1279 | 6.5948 | 6.4575 | 15.7839 | 20.637 | 7.5458 | 7.4413 | 18.1127
IRON1 R2 | 132 | 18.1279 | 6.5948 | 6.4575 | 15.7839 | 20.637 | 7.5458 | 7.4413 | 18.1127
IRON4 M1 | 400 | 72.277 | 26.8258 | 13.3262 | 51.2636 | 61.0182 | 24.0928 | 11.0201 | 45.0925
IRON4 M2 | 400 | 72.277 | 26.8258 | 13.3262 | 51.2636 | 61.0182 | 24.0928 | 11.0201 | 45.0925
IRON4 R1 | 400 | 72.277 | 26.8258 | 13.3262 | 51.2636 | 61.0182 | 24.0928 | 11.0201 | 45.0925
IRON4 R2 | 400 | 72.277 | 26.8258 | 13.3262 | 51.2636 | 61.0182 | 24.0928 | 11.0201 | 45.0925
IVER2 M1 | 275 | 69.602 | 25.4072 | 17.5204 | 53.4516 | 73.7318 | 28.0275 | 18.1041 | 57.741
IVER2 M2 | 275 | 69.602 | 25.4072 | 17.5204 | 53.4516 | 73.7318 | 28.0275 | 18.1041 | 57.741
IVER2 R1 | 275 | 69.602 | 25.4072 | 17.5204 | 53.4516 | 73.7318 | 28.0275 | 18.1041 | 57.741
IVER2 R2 | 275 | 68.7468 | 25.0255 | 15.8588 | 51.2502 | 69.0805 | 26.6883 | 14.616 | 52.3591
IVER4A | 400 | 46.6515 | 17.1687 | 5.9695 | 30.2497 | 44.2191 | 16.9402 | 6.192 | 30.149
IVER4B | 400 | 47.0099 | 17.2962 | 5.9554 | 30.416 | 44.057 | 17.0557 | 5.9228 | 30.0431
JORD2 MC1 | 275 | 50.5603 | 19.1133 | 8.9112 | 35.9415 | 49.9547 | 20.6698 | 7.3687 | 36.6003
JORD2 MC2 | 275 | 50.5603 | 19.1133 | 8.9112 | 35.9415 | 49.9547 | 20.6698 | 7.3687 | 36.6003
KEAD4 M2 | 400 | 166.8612 | 59.2191 | 42.415 | 126.1635 | 144.5131 | 55.3975 | 31.4501 | 109.7941
KEAD4 M3 | 400 | 102.4896 | 37.0562 | 26.3583 | 78.7637 | 87.2827 | 33.4088 | 19.0614 | 66.3086
KEAD4 R2 | 400 | 166.8612 | 59.2191 | 42.415 | 126.1635 | 144.5131 | 55.3975 | 31.4501 | 109.7941
KEAD4 R3 | 400 | 166.0402 | 58.9929 | 41.7983 | 125.2268 | 142.0107 | 54.685 | 29.2865 | 106.6228
KEAR2 M1 | 275 | 74.7631 | 26.9165 | 19.0223 | 57.0879 | 80.3724 | 30.4167 | 19.7339 | 62.7497
KEAR2 M2 | 275 | 74.7631 | 26.9165 | 19.0223 | 57.0879 | 80.3724 | 30.4167 | 19.7339 | 62.7497
KEAR2 R1 | 275 | 74.7631 | 26.9165 | 19.0223 | 57.0879 | 80.3724 | 30.4167 | 19.7339 | 62.7497
KEAR2 R2 | 275 | 74.7631 | 26.9165 | 19.0223 | 57.0879 | 80.3724 | 30.4167 | 19.7339 | 62.7497
KEMS4 M1 | 400 | 131.7267 | 45.1379 | 31.3373 | 95.172 | 112.6203 | 43.0654 | 22.5981 | 83.5019
KEMS4 M2 | 400 | 131.7267 | 45.1379 | 31.3373 | 95.172 | 112.6203 | 43.0654 | 22.5981 | 83.5019
KEMS4 R1 | 400 | 131.7267 | 45.1379 | 31.3373 | 95.172 | 112.6203 | 43.0654 | 22.5981 | 83.5019
KEMS4 R2 | 400 | 131.7267 | 45.1379 | 31.3373 | 95.172 | 112.6203 | 43.0654 | 22.5981 | 83.5019
KENG4 M1 | 400 | 114.2542 | 38.6743 | 28.8054 | 83.4991 | 132.0442 | 48.8576 | 31.0663 | 100.1615
KENG4 M2 | 400 | 114.2542 | 38.6743 | 28.8054 | 83.4991 | 132.0442 | 48.8576 | 31.0663 | 100.1615
KENG4 R1 | 400 | 114.2542 | 38.6743 | 28.8054 | 83.4991 | 132.0442 | 48.8576 | 31.0663 | 100.1615
KENG4 R2 | 400 | 114.2542 | 38.6743 | 28.8054 | 83.4991 | 132.0442 | 48.8576 | 31.0663 | 100.1615
KIBY2 M1 | 275 | 72.6582 | 25.7437 | 17.9681 | 54.3753 | 76.58 | 28.941 | 17.1258 | 58.0545
KIBY2 M2 | 275 | 72.6582 | 25.7437 | 17.9681 | 54.3753 | 76.58 | 28.941 | 17.1258 | 58.0545
KIBY2 R1 | 275 | 62.5154 | 22.5306 | 14.9513 | 46.8144 | 60.8411 | 23.1222 | 13.6747 | 46.3745
KIBY2 R2 | 275 | 62.5154 | 22.5306 | 14.9513 | 46.8144 | 60.8411 | 23.1222 | 13.6747 | 46.3745
KILL4 M1 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 M2 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 M3 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 M4 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 M5 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 M9 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 R1/2 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 R3/4 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 R5 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KILL4 R9 | 400 | 113.1982 | 40.7203 | 39.5948 | 97.182 | 112.8645 | 42.3257 | 38.4027 | 98.2602
KINO1 M1 | 132 | 29.4768 | 10.3896 | 10.6433 | 25.3365 | 36.0523 | 13.34 | 12.8383 | 31.7039
KINO1 M2 | 132 | 29.4768 | 10.3896 | 10.6433 | 25.3365 | 36.0523 | 13.34 | 12.8383 | 31.7039
KINO1 R1 | 132 | 29.4768 | 10.3896 | 10.6433 | 25.3365 | 36.0523 | 13.34 | 12.8383 | 31.7039
KINO1 R2 | 132 | 29.4768 | 10.3896 | 10.6433 | 25.3365 | 36.0523 | 13.34 | 12.8383 | 31.7039
KINO1A | 132 | 29.1264 | 10.1889 | 6.5806 | 20.9898 | 35.533 | 13.1836 | 7.7694 | 26.4138
KINO1B | 132 | 24.3174 | 9.0683 | 1.6261 | 14.4507 | 26.1416 | 10.5601 | 0.9206 | 15.8549
KINO4 M1 | 400 | 126.1046 | 44.6519 | 40.5659 | 103.7132 | 117.7293 | 44.7624 | 35.8718 | 99.1754
KINO4 M2 | 400 | 126.1046 | 44.6519 | 40.5659 | 103.7132 | 117.7293 | 44.7624 | 35.8718 | 99.1754
KINO4 M3 | 400 | 126.1046 | 44.6519 | 40.5659 | 103.7132 | 117.7293 | 44.7624 | 35.8718 | 99.1754
KINO4 M4 | 400 | 126.1046 | 44.6519 | 40.5659 | 103.7132 | 117.7293 | 44.7624 | 35.8718 | 99.1754
KINO4 R1/2 | 400 | 126.1046 | 44.6519 | 40.5659 | 103.7132 | 117.7293 | 44.7624 | 35.8718 | 99.1754
KINO4 R3/4 | 400 | 126.1046 | 44.6519 | 40.5659 | 103.7132 | 117.7293 | 44.7624 | 35.8718 | 99.1754
KIRK2 MC1 | 275 | 53.6111 | 19.5524 | 12.0604 | 39.7116 | 54.2611 | 20.9302 | 12.5938 | 42.1935
KIRK2 MC2 | 275 | 53.6111 | 19.5524 | 12.0604 | 39.7116 | 54.2611 | 20.9302 | 12.5938 | 42.1935
KIRK2 MC3 | 275 | 53.6111 | 19.5524 | 12.0604 | 39.7116 | 54.2611 | 20.9302 | 12.5938 | 42.1935
KIRK2 MC4 | 275 | 53.6111 | 19.5524 | 12.0604 | 39.7116 | 54.2611 | 20.9302 | 12.5938 | 42.1935
KIRK2A | 275 | 52.9121 | 18.8375 | 6.3541 | 32.9943 | 50.408 | 19.7676 | 7.6229 | 35.5786
KITW2 MC1 | 275 | 62.2442 | 22.7098 | 12.1576 | 44.2742 | 61.2121 | 23.913 | 10.6863 | 44.5044
KITW2 MC2 | 275 | 62.2442 | 22.7098 | 12.1576 | 44.2742 | 61.2121 | 23.913 | 10.6863 | 44.5044
KITW2 MC3 | 275 | 62.2442 | 22.7098 | 12.1576 | 44.2742 | 61.2121 | 23.913 | 10.6863 | 44.5044
KITW2 MC4 | 275 | 62.2442 | 22.7098 | 12.1576 | 44.2742 | 61.2121 | 23.913 | 10.6863 | 44.5044
KNAR2 MC1 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
KNAR2 MC1 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
KNAR2 MC1 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
KNAR2 MC1 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
KNAR2 MC2 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
KNAR2 MC2 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
KNAR2 MC2 | 275 | 28.9111 | 11.702 | 2.4803 | 19.0294 | 26.1901 | 10.8373 | 3.5578 | 18.8841
LACK2 M1 | 275 | 63.4032 | 21.9416 | 17.8299 | 48.86 | 68.3281 | 25.1119 | 19.7891 | 55.3027
LACK2 M2 | 275 | 63.4032 | 21.9416 | 17.8299 | 48.86 | 68.3281 | 25.1119 | 19.7891 | 55.3027
LACK2 R1 | 275 | 63.4032 | 21.9416 | 17.8299 | 48.86 | 68.3281 | 25.1119 | 19.7891 | 55.3027
LACK2 R2 | 275 | 63.4032 | 21.9416 | 17.8299 | 48.86 | 68.3281 | 25.1119 | 19.7891 | 55.3027
LACK4 M1 | 400 | 73.4313 | 27.0038 | 23.0779 | 61.2671 | 67.4026 | 25.7162 | 21.3575 | 57.7257
LACK4 M2 | 400 | 73.4313 | 27.0038 | 23.0779 | 61.2671 | 67.4026 | 25.7162 | 21.3575 | 57.7257
LACK4 R1 | 400 | 73.4313 | 27.0038 | 23.0779 | 61.2671 | 67.4026 | 25.7162 | 21.3575 | 57.7257
LACK4 R2 | 400 | 73.4313 | 27.0038 | 23.0779 | 61.2671 | 67.4026 | 25.7162 | 21.3575 | 57.7257
LAGA4 M1 | 400 | 43.0762 | 15.8395 | 8.9054 | 31.3057 | 44.2713 | 16.9932 | 10.0718 | 34.1038
LAGA4 M2 | 400 | 43.0762 | 15.8395 | 8.9054 | 31.3057 | 44.2713 | 16.9932 | 10.0718 | 34.1038
LAGA4 R1 | 400 | 43.0762 | 15.8395 | 8.9054 | 31.3057 | 44.2713 | 16.9932 | 10.0718 | 34.1038
LAGA4 R2 | 400 | 43.0762 | 15.8395 | 8.9054 | 31.3057 | 44.2713 | 16.9932 | 10.0718 | 34.1038
LALE2 MC1 | 275 | 61.8922 | 22.0394 | 17.7448 | 48.9132 | 67.8279 | 26.1887 | 16.8837 | 53.92
LALE2 MC2 | 275 | 61.8922 | 22.0394 | 17.7448 | 48.9132 | 67.8279 | 26.1887 | 16.8837 | 53.92
LALE2 MC3 | 275 | 61.8922 | 22.0394 | 17.7448 | 48.9132 | 67.8279 | 26.1887 | 16.8837 | 53.92
LALE2 MC4 | 275 | 61.8922 | 22.0394 | 17.7448 | 48.9132 | 67.8279 | 26.1887 | 16.8837 | 53.92
LAND4 MC1 | 400 | 34.5649 | 12.9269 | 6.5058 | 24.7872 | 33.8269 | 13.2345 | 6.1192 | 24.8356
LAND4 MC2 | 400 | 34.5649 | 12.9269 | 6.5058 | 24.7872 | 33.8269 | 13.2345 | 6.1192 | 24.8356
LEGA4 M1 | 400 | 89.3492 | 32.2808 | 19.7409 | 65.3928 | 68.9185 | 27.214 | 12.4973 | 50.9837
LEGA4 M2 | 400 | 89.3492 | 32.2808 | 19.7409 | 65.3928 | 68.9185 | 27.214 | 12.4973 | 50.9837
LEGA4 R1 | 400 | 89.3492 | 32.2808 | 19.7409 | 65.3928 | 68.9185 | 27.214 | 12.4973 | 50.9837
LEGA4 R2 | 400 | 89.3492 | 32.2808 | 19.7409 | 65.3928 | 68.9185 | 27.214 | 12.4973 | 50.9837
LEIS1 M1 | 132 | 65.2106 | 23.0764 | 21.2961 | 53.931 | 75.2198 | 27.3292 | 26.4796 | 65.1289
LEIS1 M2 | 132 | 65.2106 | 23.0764 | 21.2961 | 53.931 | 75.2198 | 27.3292 | 26.4796 | 65.1289
LEIS1 R1 | 132 | 65.2106 | 23.0764 | 21.2961 | 53.931 | 75.2198 | 27.3292 | 26.4796 | 65.1289
LEIS1 R2 | 132 | 65.2106 | 23.0764 | 21.2961 | 53.931 | 75.2198 | 27.3292 | 26.4796 | 65.1289
LISD2 M1 | 275 | 67.1248 | 23.9062 | 16.2839 | 50.0923 | 71.5051 | 27.2029 | 15.8743 | 54.3451
LISD2 M2 | 275 | 67.1248 | 23.9062 | 16.2839 | 50.0923 | 71.5051 | 27.2029 | 15.8743 | 54.3451
LISD2 R1 | 275 | 67.1248 | 23.9062 | 16.2839 | 50.0923 | 71.5051 | 27.2029 | 15.8743 | 54.3451
LISD2 R2 | 275 | 67.1248 | 23.9062 | 16.2839 | 50.0923 | 71.5051 | 27.2029 | 15.8743 | 54.3451
LITB4 Term500 | 400 | 80.3835 | 28.6521 | 9.5646 | 50.0847 | 72.2908 | 27.2754 | 12.3875 | 50.9607
LITT4 M1 | 400 | 128.8108 | 44.111 | 29.5439 | 91.9263 | 117.1787 | 44.8253 | 24.1359 | 87.5284
LITT4 M2 | 400 | 128.8108 | 44.111 | 29.5439 | 91.9263 | 117.1787 | 44.8253 | 24.1359 | 87.5284
LITT4 M3 | 400 | 128.8108 | 44.111 | 29.5439 | 91.9263 | 117.1787 | 44.8253 | 24.1359 | 87.5284
LITT4 R1 | 400 | 128.8108 | 44.111 | 29.5439 | 91.9263 | 117.1787 | 44.8253 | 24.1359 | 87.5284
LITT4 R2 | 400 | 128.8108 | 44.111 | 29.5439 | 91.9263 | 117.1787 | 44.8253 | 24.1359 | 87.5284
LITT4 R3 | 400 | 128.8108 | 44.111 | 29.5439 | 91.9263 | 117.1787 | 44.8253 | 24.1359 | 87.5284
LOFI4A | 400 | 99.0312 | 33.8736 | 9.6954 | 57.5998 | 82.0578 | 31.8167 | 4.6613 | 49.6569
LOFI4A_KEMS | 400 | 99.0312 | 33.8736 | 9.6954 | 57.5998 | 82.0578 | 31.8167 | 4.6613 | 49.6569
LOFI4A_LITT | 400 | 99.0312 | 33.8736 | 9.6954 | 57.5998 | 82.0578 | 31.8167 | 4.6613 | 49.6569
LOFI4A_ROWD | 400 | 99.0312 | 33.8736 | 9.6954 | 57.5998 | 82.0578 | 31.8167 | 4.6613 | 49.6569
LOFI4B | 400 | 97.8976 | 33.6052 | 9.4941 | 57.019 | 82.9948 | 32.1978 | 4.6814 | 50.216
LOFI4B_KEMS | 400 | 97.8976 | 33.6052 | 9.4941 | 57.019 | 82.9948 | 32.1978 | 4.6814 | 50.216
LOFI4B_LITT | 400 | 97.8976 | 33.6052 | 9.4941 | 57.019 | 82.9948 | 32.1978 | 4.6814 | 50.216
LOFI4B_ROWD | 400 | 97.8976 | 33.6052 | 9.4941 | 57.019 | 82.9948 | 32.1978 | 4.6814 | 50.216
LOVE4 M1 | 400 | 99.161 | 35.4786 | 19.3172 | 69.4916 | 86.1312 | 33.335 | 16.1531 | 63.2959
LOVE4 M2 | 400 | 99.161 | 35.4786 | 19.3172 | 69.4916 | 86.1312 | 33.335 | 16.1531 | 63.2959
LOVE4 R1 | 400 | 99.161 | 35.4786 | 19.3172 | 69.4916 | 86.1312 | 33.335 | 16.1531 | 63.2959
LOVE4 R2 | 400 | 99.161 | 35.4786 | 19.3172 | 69.4916 | 86.1312 | 33.335 | 16.1531 | 63.2959
MACC2 MC1 | 275 | 56.3415 | 20.8456 | 13.7518 | 43.2318 | 52.9202 | 20.4343 | 11.8444 | 40.7428
MACC2 MC2 | 275 | 56.3415 | 20.8456 | 13.7518 | 43.2318 | 52.9202 | 20.4343 | 11.8444 | 40.7428
MACC4 MC1 | 400 | 81.6622 | 30.8005 | 23.0531 | 66.6116 | 62.0063 | 24.7977 | 15.2253 | 50.2945
MACC4 MC2 | 400 | 81.6622 | 30.8005 | 23.0531 | 66.6116 | 62.0063 | 24.7977 | 15.2253 | 50.2945
MACC4 MC3 | 400 | 81.6622 | 30.8005 | 23.0531 | 66.6116 | 62.0063 | 24.7977 | 15.2253 | 50.2945
MACC4 MC4 | 400 | 81.6622 | 30.8005 | 23.0531 | 66.6116 | 62.0063 | 24.7977 | 15.2253 | 50.2945
MAGA2 MC1 | 275 | 57.8076 | 21.3166 | 12.7116 | 42.8578 | 49.2244 | 19.5227 | 8.845 | 36.4542
MAGA2 MC2 | 275 | 57.8076 | 21.3166 | 12.7116 | 42.8578 | 49.2244 | 19.5227 | 8.845 | 36.4542
MANN4 M5 | 400 | 58.2237 | 21.281 | 11.3645 | 41.4604 | 53.507 | 20.5265 | 11.5634 | 40.5923
MANN4 MC1 | 400 | 58.2237 | 21.281 | 11.3645 | 41.4604 | 53.507 | 20.5265 | 11.5634 | 40.5923
MANN4 MC2 | 400 | 58.2237 | 21.281 | 11.3645 | 41.4604 | 53.507 | 20.5265 | 11.5634 | 40.5923
MANN4 MC3 | 400 | 58.2237 | 21.281 | 11.3645 | 41.4604 | 53.507 | 20.5265 | 11.5634 | 40.5923
MANN4 MC4 | 400 | 58.2237 | 21.281 | 11.3645 | 41.4604 | 53.507 | 20.5265 | 11.5634 | 40.5923
MANN4 R5 | 400 | 58.2237 | 21.281 | 11.3645 | 41.4604 | 53.507 | 20.5265 | 11.5634 | 40.5923
MAWO4 M | 400 | 67.5808 | 24.4943 | 13.2431 | 47.8833 | 62.804 | 23.8763 | 14.3169 | 48.083
MAWO4 R | 400 | 67.5808 | 24.4943 | 13.2431 | 47.8833 | 62.804 | 23.8763 | 14.3169 | 48.083
MEDW4 Term500 | 400 | 118.7021 | 41.0037 | 27.4491 | 85.4371 | 107.7596 | 40.6489 | 25.0719 | 82.5581
MELK1 M1 | 132 | 42.1579 | 14.7492 | 14.9943 | 35.8529 | 52.2649 | 19.2052 | 17.5562 | 44.7165
MELK1 M2 | 132 | 42.1579 | 14.7492 | 14.9943 | 35.8529 | 52.2649 | 19.2052 | 17.5562 | 44.7165
MELK1 R1 | 132 | 42.1579 | 14.7492 | 14.9943 | 35.8529 | 52.2649 | 19.2052 | 17.5562 | 44.7165
MELK1 R2 | 132 | 42.1579 | 14.7492 | 14.9943 | 35.8529 | 52.2649 | 19.2052 | 17.5562 | 44.7165
MELK4 M1 | 400 | 109.2313 | 40.0745 | 21.1966 | 77.8705 | 89.6981 | 35.4893 | 14.9711 | 65.1606
MELK4 M2 | 400 | 109.2313 | 40.0745 | 21.1966 | 77.8705 | 89.6981 | 35.4893 | 14.9711 | 65.1606
MELK4 M3 | 400 | 109.2313 | 40.0745 | 21.1966 | 77.8705 | 89.6981 | 35.4893 | 14.9711 | 65.1606
MELK4 R1 | 400 | 109.2313 | 40.0745 | 21.1966 | 77.8705 | 89.6981 | 35.4893 | 14.9711 | 65.1606
MELK4 R2 | 400 | 109.2313 | 40.0745 | 21.1966 | 77.8705 | 89.6981 | 35.4893 | 14.9711 | 65.1606
MELK4 R3 | 400 | 109.2313 | 40.0745 | 21.1966 | 77.8705 | 89.6981 | 35.4893 | 14.9711 | 65.1606
MILH1 M1 | 132 | 40.4104 | 14.8342 | 9.1595 | 30.1381 | 46.7664 | 18.9825 | 9.222 | 36.0674
MILH1 M2 | 132 | 40.4104 | 14.8342 | 9.1595 | 30.1381 | 46.7664 | 18.9825 | 9.222 | 36.0674
MILH1 R1 | 132 | 40.4469 | 14.8626 | 9.0554 | 30.0743 | 46.6623 | 18.995 | 8.9773 | 35.8402
MILH1 R2 | 132 | 40.4469 | 14.8626 | 9.0554 | 30.0743 | 46.6623 | 18.995 | 8.9773 | 35.8402
MITY4 MC1 | 400 | 82.5684 | 31.5347 | 21.8523 | 66.4492 | 62.1568 | 25.1522 | 14.4477 | 50.0183
MITY4 MC2 | 400 | 82.5684 | 31.5347 | 21.8523 | 66.4492 | 62.1568 | 25.1522 | 14.4477 | 50.0183
MITY4 MC3 | 400 | 82.5684 | 31.5347 | 21.8523 | 66.4492 | 62.1568 | 25.1522 | 14.4477 | 50.0183
MITY4 MC4 | 400 | 82.5684 | 31.5347 | 21.8523 | 66.4492 | 62.1568 | 25.1522 | 14.4477 | 50.0183
MONF2 M1 | 275 | 65.5486 | 23.8276 | 17.6585 | 51.3557 | 66.2804 | 25.2362 | 16.1899 | 51.8792
MONF2 M2 | 275 | 65.5486 | 23.8276 | 17.6585 | 51.3557 | 66.2804 | 25.2362 | 16.1899 | 51.8792
MONF2 R1 | 275 | 57.4515 | 20.9161 | 18.3116 | 47.8914 | 60.0568 | 22.599 | 17.4778 | 49.4375
MONF2 R2 | 275 | 57.4515 | 20.9161 | 18.3116 | 47.8914 | 60.0568 | 22.599 | 17.4778 | 49.4375
MONF4 MC2 | 400 | 82.5816 | 30.1636 | 19.3237 | 61.9815 | 71.6321 | 27.494 | 15.8144 | 54.6968
MONF4 MC3 | 400 | 82.5816 | 30.1636 | 19.3237 | 61.9815 | 71.6321 | 27.494 | 15.8144 | 54.6968
NECH2 MC1 | 275 | 73.6159 | 26.5028 | 18.859 | 56.3395 | 74.469 | 28.6576 | 16.2891 | 56.8171
NECH2 MC2 | 275 | 73.6159 | 26.5028 | 18.859 | 56.3395 | 74.469 | 28.6576 | 16.2891 | 56.8171
NECH2 MC3 | 275 | 73.6159 | 26.5028 | 18.859 | 56.3395 | 74.469 | 28.6576 | 16.2891 | 56.8171
NECH2 MC4 | 275 | 73.6159 | 26.5028 | 18.859 | 56.3395 | 74.469 | 28.6576 | 16.2891 | 56.8171
NECT4 M1 | 400 | 75.0183 | 27.6156 | 17.801 | 56.8554 | 54.5989 | 21.6381 | 10.9326 | 41.5334
NECT4 R1 | 400 | 75.0183 | 27.6156 | 17.801 | 56.8554 | 54.5989 | 21.6381 | 10.9326 | 41.5334
NEEP2 M1 | 275 | 59.7995 | 22.1453 | 12.8842 | 44.2024 | 62.8775 | 25.0452 | 12.1294 | 47.5486
NEEP2 M2 | 275 | 59.7995 | 22.1453 | 12.8842 | 44.2024 | 62.8775 | 25.0452 | 12.1294 | 47.5486
NEEP2 R1/R2 | 275 | 59.7995 | 22.1453 | 12.8842 | 44.2024 | 62.8775 | 25.0452 | 12.1294 | 47.5486
NEWX2 M5 | 275 | 77.3759 | 26.8488 | 19.8972 | 57.8671 | 85.3372 | 33.2796 | 17.5748 | 64.6392
NEWX2 M5 | 275 | 77.3759 | 26.8488 | 19.8972 | 57.8671 | 85.3372 | 33.2796 | 17.5748 | 64.6392
NEWX2 M6 | 275 | 77.3759 | 26.8488 | 19.8972 | 57.8671 | 85.3372 | 33.2796 | 17.5748 | 64.6392
NEWX2 R6 | 275 | 77.3759 | 26.8488 | 19.8972 | 57.8671 | 85.3372 | 33.2796 | 17.5748 | 64.6392
NEWX21 R5 | 275 | 77.3759 | 26.8488 | 19.8972 | 57.8671 | 85.3372 | 33.2796 | 17.5748 | 64.6392
NFLE4 M1 | 400 | 108.2305 | 37.6911 | 24.3344 | 77.6376 | 86.4314 | 33.8502 | 15.2043 | 63.0757
NFLE4 M2 | 400 | 108.2305 | 37.6911 | 24.3344 | 77.6376 | 86.4314 | 33.8502 | 15.2043 | 63.0757
NFLE4 R1 | 400 | 108.2305 | 37.6911 | 24.3344 | 77.6376 | 86.4314 | 33.8502 | 15.2043 | 63.0757
NFLE4 R2 | 400 | 108.2305 | 37.6911 | 24.3344 | 77.6376 | 86.4314 | 33.8502 | 15.2043 | 63.0757
NHYD2A | 275 | 47.498 | 18.0914 | 2.6372 | 28.2223 | 40.3103 | 19.0972 | 0.46104 | 27.4686
NHYD2B | 275 | 47.1983 | 17.8484 | 2.3769 | 27.6183 | 40.5878 | 18.6277 | 1.0885 | 27.432
NHYD2C | 275 | 47.1983 | 17.8484 | 2.3769 | 27.6183 | 40.5878 | 18.6277 | 1.0885 | 27.432
NINF4 M1 | 400 | 67.3037 | 24.4081 | 14.8057 | 49.3239 | 58.0024 | 22.331 | 12.8159 | 44.3968
NINF4 M2 | 400 | 67.3037 | 24.4081 | 14.8057 | 49.3239 | 58.0024 | 22.331 | 12.8159 | 44.3968
NINF4 R1 | 400 | 67.3037 | 24.4081 | 14.8057 | 49.3239 | 58.0024 | 22.331 | 12.8159 | 44.3968
NINF4 R2 | 400 | 67.3037 | 24.4081 | 14.8057 | 49.3239 | 58.0024 | 22.331 | 12.8159 | 44.3968
NORL2A | 275 | 52.2563 | 19.3055 | 3.9686 | 31.2707 | 51.628 | 21.2712 | 2.3092 | 32.3912
NORL2B | 275 | 51.3942 | 19.0623 | 3.4425 | 30.4006 | 50.6912 | 21.1855 | 2.0084 | 31.9692
NORM4 M1 | 400 | 70.3579 | 26.0188 | 15.7107 | 52.5068 | 53.2509 | 20.9909 | 11.3442 | 41.0298
NORM4 M2 | 400 | 70.3579 | 26.0188 | 15.7107 | 52.5068 | 53.2509 | 20.9909 | 11.3442 | 41.0298
NORM4 R1 | 400 | 70.3579 | 26.0188 | 15.7107 | 52.5068 | 53.2509 | 20.9909 | 11.3442 | 41.0298
NORM4 R2 | 400 | 70.3579 | 26.0188 | 15.7107 | 52.5068 | 53.2509 | 20.9909 | 11.3442 | 41.0298
NORT2 M1 | 275 | 84.3641 | 29.5563 | 22.8566 | 64.6556 | 84.9211 | 32.0591 | 19.437 | 64.7754
NORT2 M2 | 275 | 84.3641 | 29.5563 | 22.8566 | 64.6556 | 84.9211 | 32.0591 | 19.437 | 64.7754
NORT2 R1 | 275 | 84.3641 | 29.5563 | 22.8566 | 64.6556 | 84.9211 | 32.0591 | 19.437 | 64.7754
NORT2 R2 | 275 | 84.3641 | 29.5563 | 22.8566 | 64.6556 | 84.9211 | 32.0591 | 19.437 | 64.7754
NORT4 M1 | 400 | 89.6925 | 32.553 | 28.4673 | 74.5042 | 76.4691 | 29.5375 | 21.8634 | 63.6358
NORT4 M2 | 400 | 89.6925 | 32.553 | 28.4673 | 74.5042 | 76.4691 | 29.5375 | 21.8634 | 63.6358
NORT4 R1 | 400 | 89.6925 | 32.553 | 28.4673 | 74.5042 | 76.4691 | 29.5375 | 21.8634 | 63.6358
NORT4 R2 | 400 | 89.6925 | 32.553 | 28.4673 | 74.5042 | 76.4691 | 29.5375 | 21.8634 | 63.6358
NURS4 MC1 | 400 | 63.6596 | 22.8887 | 8.3121 | 40.6816 | 59.1294 | 22.4577 | 8.7563 | 40.5162
NURS4 MC2 | 400 | 63.6596 | 22.8887 | 8.3121 | 40.6816 | 59.1294 | 22.4577 | 8.7563 | 40.5162
NURS4A | 400 | 53.329 | 19.6311 | 10.8161 | 38.5786 | 49.4437 | 18.9089 | 10.9333 | 37.6746
OCKH1 M1 | 132 | 25.2773 | 9.0426 | 8.6884 | 21.4765 | 34.0348 | 12.465 | 11.4416 | 29.0699
OCKH1 M2 | 132 | 25.2773 | 9.0426 | 8.6884 | 21.4765 | 34.0348 | 12.465 | 11.4416 | 29.0699
OCKH1 R1 | 132 | 25.2773 | 9.0426 | 8.6884 | 21.4765 | 34.0348 | 12.465 | 11.4416 | 29.0699
OCKH1 R2 | 132 | 25.2773 | 9.0426 | 8.6884 | 21.4765 | 34.0348 | 12.465 | 11.4416 | 29.0699
OCKH2 MC1 | 275 | 55.7259 | 20.4505 | 10.7639 | 39.6853 | 57.7604 | 22.5633 | 10.9115 | 42.8207
OCKH2 MC2 | 275 | 55.7259 | 20.4505 | 10.7639 | 39.6853 | 57.7604 | 22.5633 | 10.9115 | 42.8207
OCKH2 MC3 | 275 | 55.7259 | 20.4505 | 10.7639 | 39.6853 | 57.7604 | 22.5633 | 10.9115 | 42.8207
OCKH2 MC4 | 275 | 55.7259 | 20.4505 | 10.7639 | 39.6853 | 57.7604 | 22.5633 | 10.9115 | 42.8207
OCKH2A | 275 | 49.2113 | 17.7398 | 4.3812 | 29.4691 | 49.4297 | 19.1024 | 4.795 | 31.8098
OFFE2 MC1 | 275 | 68.6964 | 24.9242 | 13.2245 | 48.4726 | 59.0303 | 23.5535 | 8.2217 | 41.5314
OFFE2 MC2 | 275 | 68.6964 | 24.9242 | 13.2245 | 48.4726 | 59.0303 | 23.5535 | 8.2217 | 41.5314
OLDB2 MC1 | 275 | 53.5375 | 19.7462 | 10.8088 | 38.7342 | 55.2719 | 21.4078 | 11.0011 | 41.2764
OLDB2 MC2 | 275 | 53.5375 | 19.7462 | 10.8088 | 38.7342 | 55.2719 | 21.4078 | 11.0011 | 41.2764
OSBA4 MC1 | 400 | 57.1993 | 21.2043 | 12.8516 | 42.839 | 50.9963 | 19.517 | 12.237 | 39.8382
OSBA4 MC2 | 400 | 57.1993 | 21.2043 | 12.8516 | 42.839 | 50.9963 | 19.517 | 12.237 | 39.8382
OSBA4 MC3/4 | 400 | 55.4225 | 20.4994 | 12.8049 | 41.7954 | 44.5546 | 17.2557 | 9.5242 | 33.9275
PADI1 M1 | 132 | 29.7571 | 10.4557 | 10.461 | 25.2476 | 36.9591 | 13.5425 | 12.6817 | 31.8336
PADI1 M2 | 132 | 29.7571 | 10.4557 | 10.461 | 25.2476 | 36.9591 | 13.5425 | 12.6817 | 31.8336
PADI1 R1 | 132 | 29.7571 | 10.4557 | 10.461 | 25.2476 | 36.9591 | 13.5425 | 12.6817 | 31.8336
PADI1 R2 | 132 | 29.7571 | 10.4557 | 10.461 | 25.2476 | 36.9591 | 13.5425 | 12.6817 | 31.8336
PADI4 MC1 | 400 | 75.3015 | 27.6973 | 15.9332 | 55.1031 | 56.9427 | 22.5227 | 9.8171 | 41.669
PADI4 MC2 | 400 | 75.3015 | 27.6973 | 15.9332 | 55.1031 | 56.9427 | 22.5227 | 9.8171 | 41.669
PADI4 MC3 | 400 | 75.3015 | 27.6973 | 15.9332 | 55.1031 | 56.9427 | 22.5227 | 9.8171 | 41.669
PADI4 MC4 | 400 | 75.3015 | 27.6973 | 15.9332 | 55.1031 | 56.9427 | 22.5227 | 9.8171 | 41.669
PELH4 M1 | 400 | 140.5967 | 49.7774 | 34.0111 | 104.4069 | 114.5289 | 44.2875 | 22.4225 | 85.0546
PELH4 M2 | 400 | 140.5967 | 49.7774 | 34.0111 | 104.4069 | 114.5289 | 44.2875 | 22.4225 | 85.0546
PELH4 R1 | 400 | 140.5967 | 49.7774 | 34.0111 | 104.4069 | 114.5289 | 44.2875 | 22.4225 | 85.0546
PELH4 R2 | 400 | 140.5967 | 49.7774 | 34.0111 | 104.4069 | 114.5289 | 44.2875 | 22.4225 | 85.0546
PEMB4 M1 | 400 | 62.1286 | 21.8985 | 18.7283 | 49.6974 | 66.191 | 24.3023 | 21.0761 | 55.4447
PEMB4 M2 | 400 | 62.1286 | 21.8985 | 18.7283 | 49.6974 | 66.191 | 24.3023 | 21.0761 | 55.4447
PEMB4 M3 | 400 | 62.1286 | 21.8985 | 18.7283 | 49.6974 | 66.191 | 24.3023 | 21.0761 | 55.4447
PEMB4 M4 | 400 | 62.1286 | 21.8985 | 18.7283 | 49.6974 | 66.191 | 24.3023 | 21.0761 | 55.4447
PEMB4 R1/2 | 400 | 62.1286 | 21.8985 | 18.7283 | 49.6974 | 66.191 | 24.3023 | 21.0761 | 55.4447
PEMB4 R3/4 | 400 | 62.1286 | 21.8985 | 18.7283 | 49.6974 | 66.191 | 24.3023 | 21.0761 | 55.4447
PENN2 MC1 | 275 | 66.7268 | 24.3135 | 14.1365 | 48.521 | 70.1224 | 26.8937 | 14.9328 | 52.9663
PENN2 MC2 | 275 | 66.7268 | 24.3135 | 14.1365 | 48.521 | 70.1224 | 26.8937 | 14.9328 | 52.9663
PENN2 MC3 | 275 | 66.7268 | 24.3135 | 14.1365 | 48.521 | 70.1224 | 26.8937 | 14.9328 | 52.9663
PENN2 MC4 | 275 | 66.7268 | 24.3135 | 14.1365 | 48.521 | 70.1224 | 26.8937 | 14.9328 | 52.9663
PENT4 M1 | 400 | 74.7457 | 26.119 | 20.6581 | 57.5959 | 75.9152 | 28.2303 | 20.368 | 60.2917
PENT4 M2 | 400 | 74.7457 | 26.119 | 20.6581 | 57.5959 | 75.9152 | 28.2303 | 20.368 | 60.2917
PENT4 R1 | 400 | 74.7457 | 26.119 | 20.6581 | 57.5959 | 75.9152 | 28.2303 | 20.368 | 60.2917
PENT4 R2 | 400 | 74.7457 | 26.119 | 20.6581 | 57.5959 | 75.9152 | 28.2303 | 20.368 | 60.2917
PEWO2A | 275 | 66.346 | 23.861 | 20.0993 | 53.844 | 68.3487 | 25.5516 | 19.4479 | 55.5833
PEWO2B | 275 | 67.4692 | 24.5902 | 24.4186 | 59.1943 | 69.3963 | 26.0576 | 24.3952 | 61.2463
PEWO4 M1 | 400 | 101.7315 | 37.0376 | 32.4394 | 84.8186 | 92.0206 | 35.5923 | 27.1514 | 77.4866
PEWO4 M2 | 400 | 101.7315 | 37.0376 | 32.4394 | 84.8186 | 92.0206 | 35.5923 | 27.1514 | 77.4866
PEWO4 M3 | 400 | 101.7315 | 37.0376 | 32.4394 | 84.8186 | 92.0206 | 35.5923 | 27.1514 | 77.4866
PEWO4 M4 | 400 | 101.7315 | 37.0376 | 32.4394 | 84.8186 | 92.0206 | 35.5923 | 27.1514 | 77.4866
PEWO4 R1/2 | 400 | 101.7315 | 37.0376 | 32.4394 | 84.8186 | 92.0206 | 35.5923 | 27.1514 | 77.4866
PEWO4 R3/4 | 400 | 101.7315 | 37.0376 | 32.4394 | 84.8186 | 92.0206 | 35.5923 | 27.1514 | 77.4866
PITS2 MC1 | 275 | 61.4289 | 22.4379 | 8.6508 | 40.3828 | 66.2068 | 26.0266 | 7.6471 | 44.4543
PITS2 MC2 | 275 | 61.4289 | 22.4379 | 8.6508 | 40.3828 | 66.2068 | 26.0266 | 7.6471 | 44.4543
PITS2 MC3 | 275 | 61.4289 | 22.4379 | 8.6508 | 40.3828 | 66.2068 | 26.0266 | 7.6471 | 44.4543
PITS2 MC4 | 275 | 61.4289 | 22.4379 | 8.6508 | 40.3828 | 66.2068 | 26.0266 | 7.6471 | 44.4543
POPP2 MC1 | 275 | 27.0165 | 10.8396 | 2.8028 | 18.1323 | 22.7704 | 9.3979 | 3.0574 | 16.3481
POPP2 MC2 | 275 | 27.0165 | 10.8396 | 2.8028 | 18.1323 | 22.7704 | 9.3979 | 3.0574 | 16.3481
PUDM4 MC1 | 400 | 103.219 | 35.5642 | 24.4903 | 74.7857 | 106.7308 | 42.0981 | 20.2879 | 79.8236
PUDM4 MC2 | 400 | 103.219 | 35.5642 | 24.4903 | 74.7857 | 106.7308 | 42.0981 | 20.2879 | 79.8236
PYLE2 MC1 | 275 | 62.1559 | 23.0075 | 12.7661 | 45.3036 | 53.3722 | 21.1651 | 9.7416 | 39.6735
PYLE2 MC2 | 275 | 62.2155 | 23.0282 | 12.7816 | 45.3484 | 53.4206 | 21.1823 | 9.7599 | 39.7162
QUER4A | 400 | 84.7295 | 29.7483 | 12.4693 | 54.5397 | 73.1055 | 28.2434 | 5.7164 | 45.6586
QUER4A_HEYS | 400 | 84.7295 | 29.7483 | 12.4693 | 54.5397 | 73.1055 | 28.2434 | 5.7164 | 45.6586
QUER4A_HUTT | 400 | 84.7295 | 29.7483 | 12.4693 | 54.5397 | 73.1055 | 28.2434 | 5.7164 | 45.6586
QUER4A_PEWO | 400 | 84.7295 | 29.7483 | 12.4693 | 54.5397 | 73.1055 | 28.2434 | 5.7164 | 45.6586
QUER4B | 400 | 85.601 | 30.0076 | 12.7736 | 55.2108 | 75.1818 | 28.9252 | 6.3703 | 47.2766
QUER4B_HEYS | 400 | 85.601 | 30.0076 | 12.7736 | 55.2108 | 75.1818 | 28.9252 | 6.3703 | 47.2766
QUER4B_HUTT | 400 | 85.601 | 30.0076 | 12.7736 | 55.2108 | 75.1818 | 28.9252 | 6.3703 | 47.2766
QUER4B_PEWO | 400 | 85.601 | 30.0076 | 12.7736 | 55.2108 | 75.1818 | 28.9252 | 6.3703 | 47.2766
RAIN2 MC1 | 275 | 77.1876 | 27.2294 | 19.7369 | 58.2451 | 75.8593 | 28.7119 | 16.5847 | 57.1894
RAIN2 MC2 | 275 | 77.1876 | 27.2294 | 19.7369 | 58.2451 | 75.8593 | 28.7119 | 16.5847 | 57.1894
RAIN2 MC3 | 275 | 77.1876 | 27.2294 | 19.7369 | 58.2451 | 75.8593 | 28.7119 | 16.5847 | 57.1894
RAIN2 MC4 | 275 | 77.1876 | 27.2294 | 19.7369 | 58.2451 | 75.8593 | 28.7119 | 16.5847 | 57.1894
RASS4 M1 | 400 | 54.1661 | 20.26 | 16.8132 | 45.4652 | 43.1752 | 16.925 | 11.7545 | 35.6901
RASS4 M2 | 400 | 54.1661 | 20.26 | 16.8132 | 45.4652 | 43.1752 | 16.925 | 11.7545 | 35.6901
RATS1 M1 | 132 | 44.0706 | 15.5408 | 14.4249 | 36.4028 | 49.6845 | 18.4455 | 16.7185 | 42.8044
RATS1 M2 | 132 | 44.0706 | 15.5408 | 14.4249 | 36.4028 | 49.6845 | 18.4455 | 16.7185 | 42.8044
RATS1 R1 | 132 | 40.5462 | 14.3992 | 13.1951 | 33.5587 | 45.571 | 17.0379 | 14.2004 | 38.2957
RATS1 R2 | 132 | 40.5462 | 14.3992 | 13.1951 | 33.5587 | 45.571 | 17.0379 | 14.2004 | 38.2957
RATS2A | 275 | 44.1263 | 15.9436 | 10.6555 | 33.2032 | 47.0229 | 16.9953 | 20.9194 | 44.9543
RATS4 M1 | 400 | 140.4538 | 49.843 | 31.7003 | 102.1889 | 138.7946 | 52.5721 | 35.006 | 109.3542
RATS4 M2 | 400 | 140.4538 | 49.843 | 31.7003 | 102.1889 | 138.7946 | 52.5721 | 35.006 | 109.3542
RATS4 M3 | 400 | 140.4538 | 49.843 | 31.7003 | 102.1889 | 138.7946 | 52.5721 | 35.006 | 109.3542
RATS4 M4 | 400 | 140.4538 | 49.843 | 31.7003 | 102.1889 | 138.7946 | 52.5721 | 35.006 | 109.3542
RATS4 R1/2 | 400 | 140.4538 | 49.843 | 31.7003 | 102.1889 | 138.7946 | 52.5721 | 35.006 | 109.3542
RATS4 R3/4 | 400 | 140.4538 | 49.843 | 31.7003 | 102.1889 | 138.7946 | 52.5721 | 35.006 | 109.3542
RAYL4 M1 | 400 | 106.6667 | 38.8319 | 32.5448 | 87.4614 | 84.6677 | 33.1083 | 23.4832 | 70.3055
RAYL4 M2 | 400 | 106.6667 | 38.8319 | 32.5448 | 87.4614 | 84.6677 | 33.1083 | 23.4832 | 70.3055
RAYL4 R1 | 400 | 106.6667 | 38.8319 | 32.5448 | 87.4614 | 84.6677 | 33.1083 | 23.4832 | 70.3055
RAYL4 R2 | 400 | 106.6667 | 38.8319 | 32.5448 | 87.4614 | 84.6677 | 33.1083 | 23.4832 | 70.3055
REBR2 MC1 | 275 | 66.8584 | 24.548 | 22.0816 | 56.7977 | 63.7972 | 24.9485 | 17.7022 | 52.9847
REBR2 MC2 | 275 | 64.7921 | 23.7981 | 21.5876 | 55.2432 | 63.5099 | 24.9662 | 17.3319 | 52.6394
REBR2 MC3 | 275 | 64.7921 | 23.7981 | 21.5876 | 55.2432 | 63.5099 | 24.9662 | 17.3319 | 52.6394
REBR2 MC4 | 275 | 66.8584 | 24.548 | 22.0816 | 56.7977 | 63.7972 | 24.9485 | 17.7022 | 52.9847
RHIG4 M1 | 400 | 56.3012 | 20.6066 | 13.5497 | 42.6918 | 49.2468 | 19.0261 | 9.9948 | 36.9018
RHIG4 R1 | 400 | 56.3012 | 20.6066 | 13.5497 | 42.6918 | 49.2468 | 19.0261 | 9.9948 | 36.9018
ROCH2 MC1 | 275 | 71.4168 | 25.9556 | 9.69 | 46.3967 | 68.0966 | 26.4244 | 9.3512 | 46.7209
ROCH2 MC2 | 275 | 71.4168 | 25.9556 | 9.69 | 46.3967 | 68.0966 | 26.4244 | 9.3512 | 46.7209
ROCH2 MC3 | 275 | 71.4168 | 25.9556 | 9.69 | 46.3967 | 68.0966 | 26.4244 | 9.3512 | 46.7209
ROCH2 MC4 | 275 | 71.4168 | 25.9556 | 9.69 | 46.3967 | 68.0966 | 26.4244 | 9.3512 | 46.7209
ROCK1A | 132 | 46.4997 | 16.0225 | 16.5798 | 39.239 | 48.5014 | 17.5204 | 16.1559 | 40.9334
ROCK4 Term900 | 400 | 84.9901 | 30.1112 | 21.5543 | 64.1381 | 80.0142 | 29.967 | 21.0245 | 63.4042
RUGE4 M1 | 400 | 65.7863 | 24.8098 | 10.3912 | 45.4776 | 51.4016 | 20.7619 | 7.1443 | 36.5061
RUGE4 M2 | 400 | 65.7863 | 24.8098 | 10.3912 | 45.4776 | 51.4016 | 20.7619 | 7.1443 | 36.5061
RUGE4 R1 | 400 | 65.7863 | 24.8098 | 10.3912 | 45.4776 | 51.4016 | 20.7619 | 7.1443 | 36.5061
RUGE4 R2 | 400 | 65.7863 | 24.8098 | 10.3912 | 45.4776 | 51.4016 | 20.7619 | 7.1443 | 36.5061
RYEH4 M1 | 400 | 80.333 | 28.7975 | 21.1464 | 61.8721 | 80.9719 | 30.2999 | 22.152 | 65.0026
RYEH4 R1 | 400 | 80.333 | 28.7975 | 21.1464 | 61.8721 | 80.9719 | 30.2999 | 22.152 | 65.0026
RYHA41 MC1 | 400 | 44.5982 | 16.7637 | 9.7105 | 33.4179 | 28.9231 | 11.547 | 4.1267 | 20.4567
RYHA4B_LOAD2 | 400 | 44.6647 | 16.7976 | 9.7231 | 33.4784 | 30.5059 | 12.1786 | 4.3187 | 21.5417
SAEN2 MC1 | 275 | 73.5774 | 26.1766 | 21.4675 | 58.4868 | 77.459 | 28.6774 | 23.241 | 63.7969
SAEN2 MC2 | 275 | 73.5774 | 26.1766 | 21.4675 | 58.4868 | 77.459 | 28.6774 | 23.241 | 63.7969
SAES2 M | 275 | 74.1379 | 26.3433 | 21.7534 | 59.0085 | 78.3516 | 28.9539 | 23.9951 | 64.9421
SAES2 R | 275 | 74.1379 | 26.3433 | 21.7534 | 59.0085 | 78.3516 | 28.9539 | 23.9951 | 64.9421
SALH2 MC1 | 275 | 76.7551 | 27.2347 | 18.3216 | 56.8373 | 75.2066 | 28.6 | 15.4758 | 55.9223
SALH2 MC2 | 275 | 76.7551 | 27.2347 | 18.3216 | 56.8373 | 75.2066 | 28.6 | 15.4758 | 55.9223
SEAB4 M1 | 400 | 63.6202 | 23.3786 | 20.8573 | 53.9197 | 65.1397 | 24.5778 | 21.9807 | 56.7389
SEAB4 M2 | 400 | 63.6202 | 23.3786 | 20.8573 | 53.9197 | 65.1397 | 24.5778 | 21.9807 | 56.7389
SEAB4 R1 | 400 | 63.6202 | 23.3786 | 20.8573 | 53.9197 | 65.1397 | 24.5778 | 21.9807 | 56.7389
SEAB4 R2 | 400 | 63.6202 | 23.3786 | 20.8573 | 53.9197 | 65.1397 | 24.5778 | 21.9807 | 56.7389
SELL4 M1 | 400 | 84.3557 | 30.6078 | 17.6901 | 60.9761 | 64.9432 | 25.3147 | 13.5815 | 49.3818
SELL4 M2 | 400 | 84.3557 | 30.6078 | 17.6901 | 60.9761 | 64.9432 | 25.3147 | 13.5815 | 49.3818
SELL4 R1 | 400 | 84.3557 | 30.6078 | 17.6901 | 60.9761 | 64.9432 | 25.3147 | 13.5815 | 49.3818
SELL4 R2 | 400 | 84.3557 | 30.6078 | 17.6901 | 60.9761 | 64.9432 | 25.3147 | 13.5815 | 49.3818
SELL4A | 400 | 84.2692 | 29.8738 | 8.0067 | 50.2546 | 64.8878 | 25.1467 | 7.6106 | 43.1734
SELL4B | 400 | 84.269 | 29.8737 | 8.0067 | 50.2545 | 64.8877 | 25.1466 | 7.6106 | 43.1733
SELW4 M3 | 400 | 84.17 | 30.5455 | 17.6401 | 60.8379 | 64.616 | 25.1999 | 13.4356 | 49.0736
SELW4 M4 | 400 | 84.17 | 30.5455 | 17.6401 | 60.8379 | 64.616 | 25.1999 | 13.4356 | 49.0736
SELW4 R3 | 400 | 84.17 | 30.5455 | 17.6401 | 60.8379 | 64.616 | 25.1999 | 13.4356 | 49.0736
SELW4 R4 | 400 | 84.17 | 30.5455 | 17.6401 | 60.8379 | 64.616 | 25.1999 | 13.4356 | 49.0736
SETW4A | 400 | 84.1694 | 29.8411 | 7.994 | 50.1957 | 64.8413 | 25.1305 | 7.5936 | 43.1335
SETW4B | 400 | 84.1693 | 29.8411 | 7.994 | 50.1957 | 64.8411 | 25.1305 | 7.5936 | 43.1334
SHBA4 M1 | 400 | 86.9458 | 31.5864 | 30.3638 | 75.0337 | 84.4522 | 31.8012 | 28.9507 | 73.9244
SHBA4 M2 | 400 | 86.9458 | 31.5864 | 30.3638 | 75.0337 | 84.4522 | 31.8012 | 28.9507 | 73.9244
SHBA4 R1 | 400 | 86.9458 | 31.5864 | 30.3638 | 75.0337 | 84.4522 | 31.8012 | 28.9507 | 73.9244
SHBA4 R2 | 400 | 86.9458 | 31.5864 | 30.3638 | 75.0337 | 84.4522 | 31.8012 | 28.9507 | 73.9244
SHEC2 MC1 | 275 | 54.3087 | 20.35 | 10.478 | 39.2573 | 55.0327 | 22.7019 | 7.5386 | 39.6439
SHEC2 MC2 | 275 | 54.3087 | 20.35 | 10.478 | 39.2573 | 55.0327 | 22.7019 | 7.5386 | 39.6439
SHRE4B | 400 | 56.3594 | 21.1315 | 10.5568 | 40.4413 | 44.6106 | 17.7685 | 7.2973 | 32.4256
SING4 MC1 | 400 | 96.9193 | 34.0988 | 22.0011 | 70.224 | 77.4537 | 30.3837 | 12.6887 | 55.6576
SING4 MC2 | 400 | 96.9193 | 34.0988 | 22.0011 | 70.224 | 77.4537 | 30.3837 | 12.6887 | 55.6576
SIZE4 M1 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 M2 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 M3 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 M4 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 R1 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 R2 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 R3 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SIZE4 R4 | 400 | 71.1979 | 25.5195 | 18.3309 | 54.4209 | 76.5188 | 28.3746 | 22.0122 | 62.1399
SJOW2 MC1 | 275 | 86.8051 | 30.8215 | 23.2071 | 66.7953 | 94.9849 | 36.3567 | 26.5343 | 77.9504
SJOW2 MC2 | 275 | 86.8051 | 30.8215 | 23.2071 | 66.7953 | 94.9849 | 36.3567 | 26.5343 | 77.9504
SJOW2 MC3 | 275 | 86.8051 | 30.8215 | 23.2071 | 66.7953 | 94.9849 | 36.3567 | 26.5343 | 77.9504
SJOW2 MC4 | 275 | 86.8051 | 30.8215 | 23.2071 | 66.7953 | 94.9849 | 36.3567 | 26.5343 | 77.9504
SJOW4 M1 | 400 | 121.5002 | 40.9244 | 30.128 | 88.0038 | 140.5871 | 51.6292 | 34.6106 | 107.6253
SJOW4 M2 | 400 | 121.5002 | 40.9244 | 30.128 | 88.0038 | 140.5871 | 51.6292 | 34.6106 | 107.6253
SJOW4 M3 | 400 | 121.5002 | 40.9244 | 30.128 | 88.0038 | 140.5871 | 51.6292 | 34.6106 | 107.6253
SJOW4 M4 | 400 | 121.5002 | 40.9244 | 30.128 | 88.0038 | 140.5871 | 51.6292 | 34.6106 | 107.6253
SJOW4 R1/2 | 400 | 121.5002 | 40.9244 | 30.128 | 88.0038 | 140.5871 | 51.6292 | 34.6106 | 107.6253
SJOW4 R3/4 | 400 | 121.5002 | 40.9244 | 30.128 | 88.0038 | 140.5871 | 51.6292 | 34.6106 | 107.6253
SKLG2 MC1 | 275 | 58.2658 | 21.5952 | 17.6722 | 48.2123 | 55.7373 | 21.75 | 15.7045 | 46.4637
SKLG2 MC2 | 275 | 58.2658 | 21.5952 | 17.6722 | 48.2123 | 55.7373 | 21.75 | 15.7045 | 46.4637
SKLG2 MC3 | 275 | 58.2658 | 21.5952 | 17.6722 | 48.2123 | 55.7373 | 21.75 | 15.7045 | 46.4637
SKLG2 MC4 | 275 | 58.2658 | 21.5952 | 17.6722 | 48.2123 | 55.7373 | 21.75 | 15.7045 | 46.4637
SMAN2 MC1 | 275 | 76.3919 | 28.4558 | 23.2161 | 63.4587 | 75.1534 | 29.36 | 21.0011 | 62.5223
SMAN2 MC2 | 275 | 76.3919 | 28.4558 | 23.2161 | 63.4587 | 75.1534 | 29.36 | 21.0011 | 62.5223
SMAN2 MC3 | 275 | 76.3919 | 28.4558 | 23.2161 | 63.4587 | 75.1534 | 29.36 | 21.0011 | 62.5223
SMAN2 MC4 | 275 | 76.3919 | 28.4558 | 23.2161 | 63.4587 | 75.1534 | 29.36 | 21.0011 | 62.5223
SPEN4 MC3 | 400 | 61.0706 | 22.2276 | 13.3009 | 44.7354 | 48.9624 | 19.0328 | 9.1784 | 36.0949
SPEN4 MC4 | 400 | 61.0706 | 22.2276 | 13.3009 | 44.7354 | 48.9624 | 19.0328 | 9.1784 | 36.0949
SPEN41 MC1 | 400 | 61.0491 | 22.2201 | 13.2966 | 44.7207 | 49.6139 | 19.262 | 9.4336 | 36.6742
SPEN41 MC2 | 400 | 61.0491 | 22.2201 | 13.2966 | 44.7207 | 49.6139 | 19.262 | 9.4336 | 36.6742
SPLN4 M1 | 400 | 80.6838 | 29.3698 | 21.3845 | 62.9197 | 67.8101 | 25.9447 | 17.6982 | 54.3896
SPLN4 R1 | 400 | 80.6838 | 29.3698 | 21.3845 | 62.9197 | 67.8101 | 25.9447 | 17.6982 | 54.3896
SSHI2 MC1 | 275 | 65.6265 | 23.9746 | 11.7878 | 45.693 | 58.828 | 23.303 | 9.4985 | 42.4539
SSHI2 MC2 | 275 | 65.6265 | 23.9746 | 11.7878 | 45.693 | 58.828 | 23.303 | 9.4985 | 42.4539
STAL2 M1 | 275 | 82.5932 | 30.4265 | 16.1042 | 59.1337 | 76.6401 | 29.94 | 14.6234 | 56.965
STAL2 M2 | 275 | 82.5932 | 30.4265 | 16.1042 | 59.1337 | 76.6401 | 29.94 | 14.6234 | 56.965
STAL2 R1 | 275 | 82.5932 | 30.4265 | 16.1042 | 59.1337 | 76.6401 | 29.94 | 14.6234 | 56.965
STAL2 R2 | 275 | 82.5932 | 30.4265 | 16.1042 | 59.1337 | 76.6401 | 29.94 | 14.6234 | 56.965
STAL4 MC1 | 400 | 36.4925 | 13.4591 | 9.4879 | 28.522 | 32.619 | 12.612 | 8.133 | 25.9691
STAL4 MC2 | 400 | 52.1626 | 19.7837 | 9.9902 | 37.9685 | 39.7753 | 15.8364 | 6.4524 | 28.8484
STAY4 M1 | 400 | 114.138 | 41.4281 | 27.5744 | 86.1625 | 108.8309 | 41.2814 | 28.6815 | 87.0622
STAY4 M2 | 400 | 114.138 | 41.4281 | 27.5744 | 86.1625 | 108.8309 | 41.2814 | 28.6815 | 87.0622
STAY4 R1 | 400 | 114.138 | 41.4281 | 27.5744 | 86.1625 | 108.8309 | 41.2814 | 28.6815 | 87.0622
STAY4 R2 | 400 | 114.138 | 41.4281 | 27.5744 | 86.1625 | 108.8309 | 41.2814 | 28.6815 | 87.0622
STAY4A | 400 | 76.9618 | 28.1855 | 21.5374 | 61.3977 | 70.0761 | 26.4927 | 20.5554 | 58.0218
STEN1 M1 | 132 | 54.9031 | 19.3404 | 19.1284 | 46.4799 | 67.7406 | 24.9757 | 22.8697 | 58.1907
STEN1 M2 | 132 | 54.9031 | 19.3404 | 19.1284 | 46.4799 | 67.7406 | 24.9757 | 22.8697 | 58.1907
STEN1 R1 | 132 | 54.9031 | 19.3404 | 19.1284 | 46.4799 | 67.7406 | 24.9757 | 22.8697 | 58.1907
STEN1 R2 | 132 | 54.9031 | 19.3404 | 19.1284 | 46.4799 | 67.7406 | 24.9757 | 22.8697 | 58.1907
STES1 M1 | 132 | 55.1433 | 18.8976 | 15.1225 | 41.8477 | 67.7145 | 24.6887 | 17.4518 | 52.3669
STES1 M2 | 132 | 55.1433 | 18.8976 | 15.1225 | 41.8477 | 67.7145 | 24.6887 | 17.4518 | 52.3669
STES1 R1 | 132 | 55.1433 | 18.8976 | 15.1225 | 41.8477 | 67.7145 | 24.6887 | 17.4518 | 52.3669
STES1 R2 | 132 | 55.1433 | 18.8976 | 15.1225 | 41.8477 | 67.7145 | 24.6887 | 17.4518 | 52.3669
STEW2 M1 | 275 | 80.5723 | 29.6844 | 24.5224 | 66.5024 | 78.4803 | 30.1638 | 23.6428 | 66.3009
STEW2 M2 | 275 | 80.5723 | 29.6844 | 24.5224 | 66.5024 | 78.4803 | 30.1638 | 23.6428 | 66.3009
STEW2 R1 | 275 | 80.5723 | 29.6844 | 24.5224 | 66.5024 | 78.4803 | 30.1638 | 23.6428 | 66.3009
STEW2 R2 | 275 | 80.5723 | 29.6844 | 24.5224 | 66.5024 | 78.4803 | 30.1638 | 23.6428 | 66.3009
STEW4 M1 | 400 | 76.0056 | 27.7458 | 23.5855 | 62.824 | 61.4591 | 23.8505 | 17.796 | 51.5258
STEW4 M2 | 400 | 76.0056 | 27.7458 | 23.5855 | 62.824 | 61.4591 | 23.8505 | 17.796 | 51.5258
STEW4 R1 | 400 | 76.0056 | 27.7458 | 23.5855 | 62.824 | 61.4591 | 23.8505 | 17.796 | 51.5258
STEW4 R2a | 400 | 76.0056 | 27.7458 | 23.5855 | 62.824 | 61.4591 | 23.8505 | 17.796 | 51.5258
STOB4 M1 | 400 | 65.9369 | 24.8828 | 12.0902 | 47.2798 | 53.8673 | 21.5968 | 8.2743 | 38.8168
STOB4 R1 | 400 | 65.9369 | 24.8828 | 12.0902 | 47.2798 | 53.8673 | 21.5968 | 8.2743 | 38.8168
STSB4 MC1 | 400 | 58.32 | 21.6991 | 12.6352 | 43.3225 | 46.1514 | 18.19 | 7.7868 | 33.5114
STSB4 MC2 | 400 | 58.32 | 21.6991 | 12.6352 | 43.3225 | 46.1514 | 18.19 | 7.7868 | 33.5114
STSB4A | 400 | 53.9384 | 19.8761 | 5.7878 | 33.8968 | 41.8781 | 16.3835 | 3.1163 | 26.2861
SUND4 M1 | 400 | 113.4115 | 41.1224 | 24.6805 | 82.8363 | 94.6005 | 36.7058 | 18.5184 | 70.4283
SUND4 M2 | 400 | 89.3733 | 32.8552 | 18.9765 | 65.4407 | 75.4743 | 29.2541 | 15.1233 | 56.4947
SUND4 R1 | 400 | 113.4115 | 41.1224 | 24.6805 | 82.8363 | 94.6005 | 36.7058 | 18.5184 | 70.4283
SUND4 R2 | 400 | 89.3733 | 32.8552 | 18.9765 | 65.4407 | 75.4743 | 29.2541 | 15.1233 | 56.4947
SUTB4A | 400 | 89.1683 | 32.6996 | 20.6734 | 66.9177 | 77.8334 | 30.0136 | 18.413 | 60.8587
SWAN2 MC3 | 275 | 26.0894 | 9.4748 | 8.626 | 22.0254 | 28.5069 | 10.5546 | 8.9427 | 23.8691
SWAN2 MC4 | 275 | 26.0894 | 9.4748 | 8.626 | 22.0254 | 28.5069 | 10.5546 | 8.9427 | 23.8691
SWAN4 M1 | 400 | 39.3228 | 14.5389 | 9.4255 | 29.9867 | 34.4725 | 13.1604 | 8.2041 | 26.8157
SWAN4 M2 | 400 | 39.3228 | 14.5389 | 9.4255 | 29.9867 | 34.4725 | 13.1604 | 8.2041 | 26.8157
SWAN4 M3 | 400 | 63.1605 | 22.785 | 16.3574 | 48.5802 | 61.0889 | 23.1504 | 14.7978 | 47.5374
SWAN4 M4 | 400 | 63.1605 | 22.785 | 16.3574 | 48.5802 | 61.0889 | 23.1504 | 14.7978 | 47.5374
SWAN4 R3 | 400 | 63.1605 | 22.785 | 16.3574 | 48.5802 | 61.0889 | 23.1504 | 14.7978 | 47.5374
SWAN4 R4 | 400 | 63.1605 | 22.785 | 16.3574 | 48.5802 | 61.0889 | 23.1504 | 14.7978 | 47.5374
TAUN4 M1 | 400 | 50.2033 | 18.6792 | 9.6679 | 36.0843 | 43.6319 | 17.2947 | 6.7987 | 31.2571
TAUN4 M2 | 400 | 50.9765 | 18.9256 | 9.814 | 36.5789 | 45.1794 | 17.8556 | 7.3318 | 32.5834
TEMP2 MC1 | 275 | 60.3122 | 22.3522 | 12.3363 | 43.947 | 62.6853 | 24.8799 | 11.0361 | 46.2216
TEMP2 MC2 | 275 | 60.3122 | 22.3522 | 12.3363 | 43.947 | 62.6853 | 24.8799 | 11.0361 | 46.2216
TEMP2 MC3 | 275 | 60.6057 | 22.4403 | 12.479 | 44.2143 | 63.5915 | 25.2193 | 11.2661 | 46.9316
THOM2 M1 | 275 | 67.7518 | 24.8139 | 19.2256 | 54.3177 | 70.0124 | 26.5021 | 18.9431 | 56.4227
THOM2 R1 | 275 | 67.7518 | 24.8139 | 19.2256 | 54.3177 | 70.0124 | 26.5021 | 18.9431 | 56.4227
THOM4 MC1 | 400 | 93.5592 | 33.6037 | 23.0988 | 70.6217 | 84.3405 | 32.3216 | 17.8788 | 63.5884
THOM4 MC2 | 400 | 93.5592 | 33.6037 | 23.0988 | 70.6217 | 84.3405 | 32.3216 | 17.8788 | 63.5884
THOM4 MC3 | 400 | 93.5592 | 33.6037 | 23.0988 | 70.6217 | 84.3405 | 32.3216 | 17.8788 | 63.5884
THOM4 MC4 | 400 | 93.5592 | 33.6037 | 23.0988 | 70.6217 | 84.3405 | 32.3216 | 17.8788 | 63.5884
THOM4 R2(2) | 400 | 102.709 | 37.7831 | 20.7963 | 74.2297 | 85.679 | 33.4141 | 16.2241 | 63.4788
THOM4 R2(3) | 400 | 102.709 | 37.7831 | 20.7963 | 74.2297 | 85.679 | 33.4141 | 16.2241 | 63.4788
THOM42 M5 | 400 | 102.709 | 37.7831 | 20.7963 | 74.2297 | 85.679 | 33.4141 | 16.2241 | 63.4788
THTO4 M1 | 400 | 94.8852 | 34.2833 | 24.0484 | 72.5324 | 75.9181 | 29.4292 | 14.3488 | 55.968
THTO4 M2 | 400 | 69.1731 | 25.376 | 16.6489 | 52.5359 | 56.0579 | 21.695 | 11.0674 | 41.7487
THTO4 M3 | 400 | 69.1731 | 25.376 | 16.6489 | 52.5359 | 56.0579 | 21.695 | 11.0674 | 41.7487
THTO4 M4 | 400 | 94.8852 | 34.2833 | 24.0484 | 72.5324 | 75.9181 | 29.4292 | 14.3488 | 55.968
THTO4 R1/2 | 400 | 70.2668 | 25.8141 | 16.3114 | 52.8181 | 58.8841 | 22.683 | 11.9806 | 44.0591
THTO4 R3/4 | 400 | 70.2668 | 25.8141 | 16.3114 | 52.8181 | 58.8841 | 22.683 | 11.9806 | 44.0591
THUR2 MC1 | 275 | 65.4102 | 24.7282 | 10.6303 | 45.6012 | 66.325 | 26.3183 | 11.0096 | 48.2293
THUR2 MC2 | 275 | 65.4102 | 24.7282 | 10.6303 | 45.6012 | 66.325 | 26.3183 | 11.0096 | 48.2293
THUR2 MC3 | 275 | 65.4102 | 24.7282 | 10.6303 | 45.6012 | 66.325 | 26.3183 | 11.0096 | 48.2293
THUR2 MC4 | 275 | 65.4102 | 24.7282 | 10.6303 | 45.6012 | 66.325 | 26.3183 | 11.0096 | 48.2293
TILB2 M1 | 275 | 70.6818 | 25.317 | 21.3521 | 57.1558 | 73.9343 | 27.6286 | 21.2029 | 60.2756
TILB2 M2 | 275 | 70.6818 | 25.317 | 21.3521 | 57.1558 | 73.9343 | 27.6286 | 21.2029 | 60.2756
TILB2 R1 | 275 | 70.6818 | 25.317 | 21.3521 | 57.1558 | 73.9343 | 27.6286 | 21.2029 | 60.2756
TILB2 R2 | 275 | 70.6818 | 25.317 | 21.3521 | 57.1558 | 73.9343 | 27.6286 | 21.2029 | 60.2756
TILB4 M2 | 400 | 143.2732 | 50.4947 | 45.6857 | 117.0959 | 127.8688 | 49.1494 | 36.0945 | 105.6022
TILB4 M3 | 400 | 143.2732 | 50.4947 | 45.6857 | 117.0959 | 127.8688 | 49.1494 | 36.0945 | 105.6022
TILB4 R2 | 400 | 143.2732 | 50.4947 | 45.6857 | 117.0959 | 127.8688 | 49.1494 | 36.0945 | 105.6022
TILB4 R3 | 400 | 143.2732 | 50.4947 | 45.6857 | 117.0959 | 127.8688 | 49.1494 | 36.0945 | 105.6022
TINP2 M1 | 275 | 58.8105 | 21.5547 | 6.9438 | 37.4267 | 57.1583 | 22.2727 | 5.5701 | 37.0684
TINP2 M2 | 275 | 58.9805 | 21.5653 | 6.9569 | 37.4549 | 58.1008 | 22.615 | 5.6654 | 37.6478
TODP2 MC1 | 275 | 63.6735 | 22.2574 | 16.0546 | 47.5313 | 58.6982 | 22.4272 | 11.8168 | 43.5337
TODP2 MC2 | 275 | 63.6735 | 22.2574 | 16.0546 | 47.5313 | 58.6982 | 22.4272 | 11.8168 | 43.5337
TOTE2A | 275 | 76.1634 | 27.3118 | 20.2443 | 58.869 | 79.0351 | 30.1706 | 17.7321 | 60.3998
TOTE2B | 275 | 77.8337 | 27.8944 | 20.4172 | 59.8658 | 77.3946 | 29.5062 | 17.3075 | 59.0356
TOTT2 MC1 | 275 | 76.2353 | 28.1238 | 23.8998 | 63.6728 | 76.4843 | 31.3665 | 20.046 | 64.4049
TOTT2 MC2A | 275 | 77.4888 | 28.5559 | 24.3253 | 64.7095 | 74.1037 | 30.9253 | 18.1336 | 61.8686
TOTT2 MC2B | 275 | 77.8337 | 27.8944 | 20.4172 | 59.8658 | 77.3946 | 29.5062 | 17.3075 | 59.0356
TOTT2 MC3 | 275 | 77.4888 | 28.5559 | 24.3253 | 64.7095 | 74.1037 | 30.9253 | 18.1336 | 61.8686
TOTT2 MC4A | 275 | 76.2353 | 28.1238 | 23.8998 | 63.6728 | 76.4843 | 31.3665 | 20.046 | 64.4049
TOTT2 MC4B | 275 | 76.1634 | 27.3118 | 20.2443 | 58.869 | 79.0351 | 30.1706 | 17.7321 | 60.3998
TOTT2 MC5 | 275 | 77.8337 | 27.8944 | 20.4172 | 59.8658 | 77.3946 | 29.5062 | 17.3075 | 59.0356
TOTT2 MC6 | 275 | 77.8337 | 27.8944 | 20.4172 | 59.8658 | 77.3946 | 29.5062 | 17.3075 | 59.0356
TOTT2 MC7 | 275 | 76.1634 | 27.3118 | 20.2443 | 58.869 | 79.0351 | 30.1706 | 17.7321 | 60.3998
TOTT2 MC8 | 275 | 76.1634 | 27.3118 | 20.2443 | 58.869 | 79.0351 | 30.1706 | 17.7321 | 60.3998
TRAW2 M1 | 275 | 44.7682 | 16.0757 | 13.7497 | 36.4842 | 47.0017 | 17.579 | 12.7067 | 37.5672
TRAW2 M2 | 275 | 44.7682 | 16.0757 | 13.7497 | 36.4842 | 47.0017 | 17.579 | 12.7067 | 37.5672
TRAW2 R1 | 275 | 44.7682 | 16.0757 | 13.7497 | 36.4842 | 47.0017 | 17.579 | 12.7067 | 37.5672
TRAW2 R2 | 275 | 44.7682 | 16.0757 | 13.7497 | 36.4842 | 47.0017 | 17.579 | 12.7067 | 37.5672
TRAW4 MC1 | 400 | 58.5863 | 21.8037 | 17.8797 | 48.7148 | 47.2984 | 18.7118 | 12.4545 | 38.917
TRAW4 MC2 | 400 | 58.5863 | 21.8037 | 17.8797 | 48.7148 | 47.2984 | 18.7118 | 12.4545 | 38.917
TRAW4 MC3 | 400 | 58.5863 | 21.8037 | 17.8797 | 48.7148 | 47.2984 | 18.7118 | 12.4545 | 38.917
TRAW4 MC4 | 400 | 58.5863 | 21.8037 | 17.8797 | 48.7148 | 47.2984 | 18.7118 | 12.4545 | 38.917
TREM2 MC1 | 275 | 49.5963 | 18.1981 | 2.9066 | 28.6426 | 43.2667 | 17.2138 | 2.4357 | 26.7797
TREM2 MC2 | 275 | 49.5963 | 18.1981 | 2.9066 | 28.6426 | 43.2667 | 17.2138 | 2.4357 | 26.7797
TREU4A | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.2532 | 28.5864 | 4.6077 | 45.035
TREU4A_DEES1 | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.2532 | 28.5864 | 4.6077 | 45.035
TREU4A_LEGA1 | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.2532 | 28.5864 | 4.6077 | 45.035
TREU4A_TRAW1 | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.2532 | 28.5864 | 4.6077 | 45.035
TREU4B | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.4763 | 28.6717 | 4.6217 | 45.1697
TREU4B_DEES2 | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.4763 | 28.6717 | 4.6217 | 45.1697
TREU4B_LEGA2 | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.4763 | 28.6717 | 4.6217 | 45.1697
TREU4B_TRAW2 | 400 | 88.8626 | 31.3775 | 9.4611 | 53.8355 | 73.4763 | 28.6717 | 4.6217 | 45.1697
TYNE2 MC1 | 275 | 61.4199 | 22.5762 | 10.8323 | 42.7598 | 54.8706 | 21.6317 | 9.3679 | 39.9598
TYNE2 MC2 | 275 | 61.4199 | 22.5762 | 10.8323 | 42.7598 | 54.8706 | 21.6317 | 9.3679 | 39.9598
TYNE2A | 275 | 60.7023 | 21.9676 | 3.7615 | 34.8284 | 51.6002 | 20.45 | 2.7863 | 31.707
UPPB2 MC1 | 275 | 43.6926 | 16.2126 | 11.2786 | 34.2067 | 42.7975 | 16.5338 | 9.617 | 32.9994
UPPB2 MC2 | 275 | 47.5765 | 17.61 | 11.9703 | 36.8746 | 44.9629 | 17.3667 | 10.025 | 34.5853
UPPB2 MC3 | 275 | 47.5765 | 17.61 | 11.9703 | 36.8746 | 44.9629 | 17.3667 | 10.025 | 34.5853
UPPB2 MC4 | 275 | 43.6926 | 16.2126 | 11.2786 | 34.2067 | 42.7975 | 16.5338 | 9.617 | 32.9994
USKM2 M1 | 275 | 79.4217 | 28.2821 | 19.6708 | 59.6677 | 89.2732 | 33.4979 | 22.8741 | 70.2473
USKM2 M2 | 275 | 79.4217 | 28.2821 | 19.6708 | 59.6677 | 89.2732 | 33.4979 | 22.8741 | 70.2473
USKM2 R1 | 275 | 79.4217 | 28.2821 | 19.6708 | 59.6677 | 89.2732 | 33.4979 | 22.8741 | 70.2473
USKM2 R2 | 275 | 79.4217 | 28.2821 | 19.6708 | 59.6677 | 89.2732 | 33.4979 | 22.8741 | 70.2473
USKM2A | 275 | 77.0989 | 26.8206 | 10.9311 | 48.8611 | 84.5612 | 31.6388 | 11.6295 | 56.3735
WALH4 MC1 | 400 | 61.1609 | 22.8318 | 11.8189 | 44.108 | 51.7412 | 20.2708 | 10.6161 | 39.2833
WALH4 MC2 | 400 | 61.1609 | 22.8318 | 11.8189 | 44.108 | 51.7412 | 20.2708 | 10.6161 | 39.2833
WALH4 MC3 | 400 | 61.1609 | 22.8318 | 11.8189 | 44.108 | 51.7412 | 20.2708 | 10.6161 | 39.2833
WALH4 MC4 | 400 | 61.1609 | 22.8318 | 11.8189 | 44.108 | 51.7412 | 20.2708 | 10.6161 | 39.2833
WALP R4 | 132 | 72.5087 | 25.6423 | 21.7577 | 58.0213 | 87.1938 | 33.3541 | 23.672 | 70.8418
WALP1 M4 | 132 | 72.5087 | 25.6423 | 21.7577 | 58.0213 | 87.1938 | 33.3541 | 23.672 | 70.8418
WALP4 M1 | 400 | 107.2443 | 38.7082 | 27.4761 | 82.2177 | 94.908 | 36.17 | 24.627 | 75.7791
WALP4 M2 | 400 | 107.2443 | 38.7082 | 27.4761 | 82.2177 | 94.908 | 36.17 | 24.627 | 75.7791
WALP4 R1 | 400 | 107.2443 | 38.7082 | 27.4761 | 82.2177 | 94.908 | 36.17 | 24.627 | 75.7791
WALP4 R2 | 400 | 107.2443 | 38.7082 | 27.4761 | 82.2177 | 94.908 | 36.17 | 24.627 | 75.7791
WALPM3 | 132 | 72.5087 | 25.6423 | 21.7577 | 58.0213 | 87.1938 | 33.3541 | 23.672 | 70.8418
WALPR3 | 132 | 72.5087 | 25.6423 | 21.7577 | 58.0213 | 87.1938 | 33.3541 | 23.672 | 70.8418
WALX2 M1 | 275 | 91.8981 | 32.3964 | 19.3277 | 65.1431 | 91.5295 | 34.4832 | 17.7925 | 66.5591
WALX2 M2 | 275 | 93.019 | 32.7297 | 19.6388 | 65.9256 | 96.7455 | 36.3536 | 18.9728 | 70.3845
WALX2 R1 | 275 | 91.8981 | 32.3964 | 19.3277 | 65.1431 | 91.5295 | 34.4832 | 17.7925 | 66.5591
WALX2 R2 | 275 | 93.019 | 32.7297 | 19.6388 | 65.9256 | 96.7455 | 36.3536 | 18.9728 | 70.3845
WALX4A | 400 | 74.6251 | 26.3078 | 11.8879 | 49.0927 | 73.7478 | 27.5277 | 11.5926 | 50.5227
WALX4B | 400 | 70.2082 | 25.0093 | 10.4023 | 45.7708 | 64.95 | 24.4283 | 9.7755 | 44.3223
WARL2 MC1 | 275 | 64.6693 | 23.5295 | 15.6956 | 48.9713 | 60.2335 | 23.3869 | 11.6407 | 44.7148
WARL2 MC2 | 275 | 64.6693 | 23.5295 | 15.6956 | 48.9713 | 60.2335 | 23.3869 | 11.6407 | 44.7148
WARL2 MC3 | 275 | 64.6693 | 23.5295 | 15.6956 | 48.9713 | 60.2335 | 23.3869 | 11.6407 | 44.7148
WARL2 MC4 | 275 | 64.6693 | 23.5295 | 15.6956 | 48.9713 | 60.2335 | 23.3869 | 11.6407 | 44.7148
WASF2A | 275 | 55.2701 | 20.277 | 12.3473 | 41.0233 | 47.8809 | 18.7398 | 8.2601 | 34.7622
WASF2B | 275 | 59.8549 | 21.8266 | 13.309 | 44.1765 | 54.2133 | 21.2514 | 8.9858 | 39.0398
WBOL2 MC1 | 275 | 73.9684 | 26.635 | 14.1361 | 51.8037 | 64.9491 | 25.6276 | 10.6244 | 46.8673
WBOL2 MC2 | 275 | 73.9684 | 26.635 | 14.1361 | 51.8037 | 64.9491 | 25.6276 | 10.6244 | 46.8673
WBOL2 MC3 | 275 | 73.9684 | 26.635 | 14.1361 | 51.8037 | 64.9491 | 25.6276 | 10.6244 | 46.8673
WBOL2 MC4 | 275 | 73.9684 | 26.635 | 14.1361 | 51.8037 | 64.9491 | 25.6276 | 10.6244 | 46.8673
WBUR1 M1 | 132 | 21.4866 | 7.6319 | 6.8224 | 17.6155 | 25.0325 | 9.2656 | 8.144 | 21.2475
WBUR1 M2 | 132 | 21.4866 | 7.6319 | 6.8224 | 17.6155 | 25.0325 | 9.2656 | 8.144 | 21.2475
WBUR1 R1 | 132 | 21.4866 | 7.6319 | 6.8224 | 17.6155 | 25.0325 | 9.2656 | 8.144 | 21.2475
WBUR1 R2 | 132 | 21.2632 | 7.572 | 6.7168 | 17.4252 | 24.8702 | 9.2052 | 8.0518 | 21.0699
WBUR4 M1 | 400 | 109.6677 | 39.1411 | 31.7098 | 87.0636 | 103.8049 | 38.7815 | 30.2313 | 85.0766
WBUR4 M2 | 400 | 109.6677 | 39.1411 | 31.7098 | 87.0636 | 103.8049 | 38.7815 | 30.2313 | 85.0766
WBUR4 M3 | 400 | 109.6677 | 39.1411 | 31.7098 | 87.0636 | 103.8049 | 38.7815 | 30.2313 | 85.0766
WBUR4 M4 | 400 | 109.6677 | 39.1411 | 31.7098 | 87.0636 | 103.8049 | 38.7815 | 30.2313 | 85.0766
WBUR4 R1/2 | 400 | 114.9485 | 41.8108 | 28.8294 | 87.9588 | 95.0884 | 36.5023 | 22.9566 | 74.5786
WBUR4 R3/4 | 400 | 114.9485 | 41.8108 | 28.8294 | 87.9588 | 95.0884 | 36.5023 | 22.9566 | 74.5786
WHAM4 M1 | 400 | 126.0604 | 44.2506 | 39.9603 | 102.5401 | 139.9523 | 53.2038 | 40.3797 | 115.6212
WHAM4 M2 | 400 | 126.0604 | 44.2506 | 39.9603 | 102.5401 | 139.9523 | 53.2038 | 40.3797 | 115.6212
WHAM4 R1 | 400 | 126.0604 | 44.2506 | 39.9603 | 102.5401 | 139.9523 | 53.2038 | 40.3797 | 115.6212
WHAM4 R2 | 400 | 126.0604 | 44.2506 | 39.9603 | 102.5401 | 139.9523 | 53.2038 | 40.3797 | 115.6212
WHAM4A | 400 | 100.8879 | 33.6045 | 13.764 | 61.2879 | 103.8398 | 40.0679 | 15.958 | 72.6226
WHAM4B | 400 | 100.9651 | 33.6264 | 13.7665 | 61.3214 | 103.9422 | 40.108 | 15.9599 | 72.6811
WHGA2 MC1 | 275 | 70.521 | 25.7773 | 14.9985 | 51.4532 | 66.2806 | 25.9394 | 11.9803 | 48.6641
WHGA2 MC2 | 275 | 70.521 | 25.7773 | 14.9985 | 51.4532 | 66.2806 | 25.9394 | 11.9803 | 48.6641
WHGA2 MC3 | 275 | 70.521 | 25.7773 | 14.9985 | 51.4532 | 66.2806 | 25.9394 | 11.9803 | 48.6641
WHGA2 MC4 | 275 | 70.521 | 25.7773 | 14.9985 | 51.4532 | 66.2806 | 25.9394 | 11.9803 | 48.6641
WHSO2 M1 | 275 | 69.1728 | 25.0693 | 14.9513 | 50.4046 | 74.1134 | 28.3462 | 15.5959 | 55.6835
WHSO2 M2 | 275 | 69.1728 | 25.0693 | 14.9513 | 50.4046 | 74.1134 | 28.3462 | 15.5959 | 55.6835
WHSO2 R1 | 275 | 75.9916 | 27.2511 | 19.0737 | 57.6127 | 82.5842 | 31.2277 | 20.1163 | 64.279
WHSO2 R2 | 275 | 75.9916 | 27.2511 | 19.0737 | 57.6127 | 82.5842 | 31.2277 | 20.1163 | 64.279
WIBA2 MC1 | 275 | 60.2956 | 22.3469 | 12.3255 | 43.9288 | 63.8649 | 25.5903 | 10.3506 | 46.5407
WIBA2 MC1 | 275 | 60.2956 | 22.3469 | 12.3255 | 43.9288 | 63.8649 | 25.5903 | 10.3506 | 46.5407
WIBA2 MC2 | 275 | 60.2956 | 22.3469 | 12.3255 | 43.9288 | 63.8649 | 25.5903 | 10.3506 | 46.5407
WIBA2 MC2 | 275 | 60.2956 | 22.3469 | 12.3255 | 43.9288 | 63.8649 | 25.5903 | 10.3506 | 46.5407
WILE4 M1 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 M1 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 M2 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 M2 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 R1 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 R1 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 R2 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILE4 R2 | 400 | 109.356 | 40.7377 | 30.2202 | 87.832 | 94.0754 | 37.3193 | 24.2189 | 76.9964
WILL1 M2 | 132 | 50.3956 | 17.656 | 15.8265 | 40.7959 | 57.7844 | 21.874 | 18.2535 | 49.188
WILL1 R1 | 132 | 35.3629 | 13.1051 | 10.8029 | 29.3362 | 39.2373 | 15.1296 | 12.3301 | 33.7265
WILL1 R2 | 132 | 50.3956 | 17.656 | 15.8265 | 40.7959 | 57.7844 | 21.874 | 18.2535 | 49.188
WILL2 M2 | 275 | 24.2237 | 8.6667 | 9.025 | 21.2816 | 25.8969 | 9.452 | 9.3742 | 22.7414
WILL2 M2 | 275 | 24.2237 | 8.6667 | 9.025 | 21.2816 | 25.8969 | 9.452 | 9.3742 | 22.7414
WILL2 R2 | 275 | 24.2237 | 8.6667 | 9.025 | 21.2816 | 25.8969 | 9.452 | 9.3742 | 22.7414
WILL2 R2 | 275 | 24.2237 | 8.6667 | 9.025 | 21.2816 | 25.8969 | 9.452 | 9.3742 | 22.7414
WILT2A | 275 | 54.4263 | 19.3274 | 10.0632 | 37.3962 | 56.9222 | 21.1027 | 9.2808 | 39.1245
WILT2A | 275 | 54.4263 | 19.3274 | 10.0632 | 37.3962 | 56.9222 | 21.1027 | 9.2808 | 39.1245
WILT2B | 275 | 54.4263 | 19.3274 | 10.0632 | 37.3962 | 56.9222 | 21.1027 | 9.2808 | 39.1245
WILT2B | 275 | 54.4263 | 19.3274 | 10.0632 | 37.3962 | 56.9222 | 21.1027 | 9.2808 | 39.1245
WILT2C | 275 | 54.7377 | 19.4236 | 10.2242 | 37.6934 | 57.8353 | 21.3818 | 9.9592 | 40.1976
WILT2C | 275 | 54.7377 | 19.4236 | 10.2242 | 37.6934 | 57.8353 | 21.3818 | 9.9592 | 40.1976
WILT2D | 275 | 54.7365 | 19.4234 | 10.2237 | 37.6926 | 57.8312 | 21.3805 | 9.9574 | 40.194
WILT2D | 275 | 54.7365 | 19.4234 | 10.2237 | 37.6926 | 57.8312 | 21.3805 | 9.9574 | 40.194
WIMB2 MC1 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC1 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC2 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC2 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC3 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC3 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC4 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2 MC4 | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2A | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB2A | 275 | 84.5418 | 29.1615 | 21.943 | 63.1836 | 94.6883 | 35.8342 | 23.7807 | 74.4579
WIMB4 MB2 | 400 | 97.9106 | 33.6698 | 24.5222 | 72.1385 | 112.0748 | 42.5856 | 21.9079 | 82.1331
WIMB4 MB2 | 400 | 97.9106 | 33.6698 | 24.5222 | 72.1385 | 112.0748 | 42.5856 | 21.9079 | 82.1331
WIMB4 RB2 | 400 | 97.9106 | 33.6698 | 24.5222 | 72.1385 | 112.0748 | 42.5856 | 21.9079 | 82.1331
WIMB4 RB2 | 400 | 97.9106 | 33.6698 | 24.5222 | 72.1385 | 112.0748 | 42.5856 | 21.9079 | 82.1331
WISD2 M1 | 275 | 70.6287 | 24.5285 | 23.1027 | 57.7912 | 82.1866 | 30.3061 | 25.8211 | 68.6804
WISD2 M2 | 275 | 70.6287 | 24.5285 | 23.1027 | 57.7912 | 82.1866 | 30.3061 | 25.8211 | 68.6804
WISD2 R1 | 275 | 70.6287 | 24.5285 | 23.1027 | 57.7912 | 82.1866 | 30.3061 | 25.8211 | 68.6804
WISD2 R2 | 275 | 70.6287 | 24.5285 | 23.1027 | 57.7912 | 82.1866 | 30.3061 | 25.8211 | 68.6804
WISD2A | 275 | 60.2255 | 20.9424 | 12.7533 | 42.3703 | 65.7876 | 25.1466 | 14.1602 | 49.7228
WISD2B | 275 | 60.2255 | 20.9424 | 12.7533 | 42.3703 | 65.7876 | 25.1466 | 14.1602 | 49.7228
WISD6 M1 | 66 | 50.2857 | 17.0245 | 17.1774 | 41.2537 | 33.2562 | 12.4755 | 10.7417 | 28.3848
WISD6 M2 | 66 | 50.2857 | 17.0245 | 17.1774 | 41.2537 | 33.2562 | 12.4755 | 10.7417 | 28.3848
WISD6 R1 | 66 | 50.2857 | 17.0245 | 17.1774 | 41.2537 | 33.2562 | 12.4755 | 10.7417 | 28.3848
WISD6 R2 | 66 | 50.2857 | 17.0245 | 17.1774 | 41.2537 | 33.2562 | 12.4755 | 10.7417 | 28.3848
WMEL2 MC1 | 275 | 79.5355 | 29.2694 | 14.6245 | 56.0178 | 75.653 | 29.8761 | 12.2085 | 54.4597
WMEL2 MC2 | 275 | 79.5355 | 29.2694 | 14.6245 | 56.0178 | 75.653 | 29.8761 | 12.2085 | 54.4597
WMEL2 MC3 | 275 | 79.5355 | 29.2694 | 14.6245 | 56.0178 | 75.653 | 29.8761 | 12.2085 | 54.4597
WMEL2 MC4 | 275 | 79.5355 | 29.2694 | 14.6245 | 56.0178 | 75.653 | 29.8761 | 12.2085 | 54.4597
WTHU4A | 400 | 95.0031 | 32.6335 | 8.8117 | 54.9625 | 75.8006 | 29.6588 | 5.0028 | 46.9467
WTHU4B | 400 | 95.0031 | 32.6335 | 8.8117 | 54.9625 | 77.5107 | 30.3006 | 5.1157 | 47.9673
WWEY2 M1 | 275 | 72.4007 | 26.2903 | 17.9545 | 55.1346 | 71.2858 | 27.2175 | 16.7807 | 55.272
WWEY2 M2 | 275 | 72.4007 | 26.2903 | 17.9545 | 55.1346 | 71.2858 | 27.2175 | 16.7807 | 55.272
WWEY2 R1 | 275 | 74.4501 | 27.2023 | 16.6299 | 55.0998 | 74.1334 | 28.4353 | 16.682 | 56.8956
WWEY2 R2 | 275 | 74.4501 | 27.2023 | 16.6299 | 55.0998 | 74.1334 | 28.4353 | 16.682 | 56.8956
WWEY4A | 400 | 50.4373 | 18.4328 | 6.2889 | 32.3567 | 45.0916 | 17.3083 | 6.1507 | 30.6284
WWEY4B | 400 | 50.9754 | 18.6175 | 6.5408 | 32.87 | 45.0547 | 17.3604 | 6.3867 | 30.938
WYLF1 M1 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 M1 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 M2 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 M2 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 R1 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 R1 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 R2 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF1 R2 | 132 | 18.4449 | 5.7597 | 6.7695 | 14.9149 | 20.7747 | 7.1989 | 7.0267 | 17.2075
WYLF4 M1 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 M1 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 M2 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 M2 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 R1 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 R1 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 R2 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYLF4 R2 | 400 | 48.2046 | 17.3284 | 11.9964 | 36.5024 | 36.0709 | 14.0587 | 6.9312 | 26.8132
WYMO4 M1 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 M1 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 M2 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 M2 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 R1 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 R1 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 R2 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466
WYMO4 R2 | 400 | 111.9578 | 40.4341 | 25.3755 | 82.5579 | 95.7792 | 36.9279 | 19.4227 | 71.6466

## D3.3
ETYS 19 Yr 3 - NGET Fault Levels (kA), Winter 2021/22
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 37.4824 | 13.7198 | 3.2562 | 22.659 | 34.1705 | 13.366 | 2.3897 | 21.292 | Back To Menu
ABHA4B | 400 | 37.4652 | 13.7104 | 3.2552 | 22.6447 | 34.1597 | 13.3595 | 2.3842 | 21.2774
ABTH1 M1 | 132 | 27.9775 | 10.5026 | 6.1203 | 20.9732 | 26.9148 | 10.6138 | 6.1085 | 21.1187
ABTH1 M2 | 132 | 25.7537 | 10.0218 | 7.6359 | 21.8088 | 22.7826 | 9.1322 | 6.6646 | 19.5795
ABTH1 R1 | 132 | 28.4383 | 10.9635 | 7.6582 | 23.163 | 31.1946 | 12.3117 | 8.7777 | 26.1891
ABTH1 R2 | 132 | 28.4383 | 10.9635 | 7.6582 | 23.163 | 31.1946 | 12.3117 | 8.7777 | 26.1891
ABTH2 M1 | 275 | 48.1517 | 17.9376 | 8.8288 | 34.1963 | 43.7228 | 17.3058 | 7.3025 | 31.7766
ABTH2 M2 | 275 | 48.1517 | 17.9376 | 8.8288 | 34.1963 | 43.7228 | 17.3058 | 7.3025 | 31.7766
ABTH2 M4 | 275 | 48.1517 | 17.9376 | 8.8288 | 34.1963 | 43.7228 | 17.3058 | 7.3025 | 31.7766
ABTH2 R | 275 | 39.6322 | 14.9854 | 4.4961 | 25.6886 | 33.8827 | 13.5844 | 2.7992 | 22.0104
ALDW2 MC1 | 275 | 62.6777 | 23.395 | 9.9582 | 43.0437 | 61.5845 | 24.4127 | 9.8357 | 44.3605
ALDW2 MC2 | 275 | 62.6777 | 23.395 | 9.9582 | 43.0437 | 61.5845 | 24.4127 | 9.8357 | 44.3605
ALDW2 MC3 | 275 | 62.6777 | 23.395 | 9.9582 | 43.0437 | 61.5845 | 24.4127 | 9.8357 | 44.3605
ALDW2 MC4 | 275 | 62.6777 | 23.395 | 9.9582 | 43.0437 | 61.5845 | 24.4127 | 9.8357 | 44.3605
AMEM1 M1 | 132 | 25.7518 | 9.1906 | 9.2306 | 22.2282 | 31.7159 | 11.6617 | 10.5184 | 27.0105
AMEM1 M2 | 132 | 25.7518 | 9.1906 | 9.2306 | 22.2282 | 31.7159 | 11.6617 | 10.5184 | 27.0105
AMEM1 R1 | 132 | 25.7518 | 9.1906 | 9.2306 | 22.2282 | 31.7159 | 11.6617 | 10.5184 | 27.0105
AMEM1 R2 | 132 | 25.7518 | 9.1906 | 9.2306 | 22.2282 | 31.7159 | 11.6617 | 10.5184 | 27.0105
AMEM4 M | 400 | 49.8893 | 18.5832 | 4.2398 | 30.5204 | 41.8923 | 16.6327 | 2.9009 | 26.4231
AMEM4 R | 400 | 50.9496 | 18.9555 | 4.3387 | 31.1459 | 41.8104 | 16.5334 | 2.8662 | 26.2479
AXMI4 MC1 | 400 | 39.6343 | 14.7167 | 7.9746 | 28.7872 | 33.3185 | 13.0336 | 6.1774 | 24.6096
AXMI4 MC2 | 400 | 39.6343 | 14.7167 | 7.9746 | 28.7872 | 33.3185 | 13.0336 | 6.1774 | 24.6096
BAGB2 M1 | 275 | 49.7412 | 18.1554 | 12.9789 | 38.6546 | 48.298 | 18.4124 | 12.8998 | 38.9387
BAGB2 M2 | 275 | 49.7412 | 18.1554 | 12.9789 | 38.6546 | 48.298 | 18.4124 | 12.8998 | 38.9387
BAGB2 R1 | 275 | 49.7412 | 18.1554 | 12.9789 | 38.6546 | 48.298 | 18.4124 | 12.8998 | 38.9387
BAGB2 R2 | 275 | 49.7412 | 18.1554 | 12.9789 | 38.6546 | 48.298 | 18.4124 | 12.8998 | 38.9387
BARK2 M1 | 275 | 55.1007 | 20.0056 | 14.4215 | 42.7136 | 54.9548 | 20.8659 | 14.3097 | 43.8186
BARK2 M2 | 275 | 53.1807 | 19.3133 | 14.1515 | 41.4647 | 55.2568 | 20.936 | 14.8916 | 44.4996
BARK2 R1 | 275 | 55.1007 | 20.0056 | 14.4215 | 42.7136 | 54.9548 | 20.8659 | 14.3097 | 43.8186
BARK2 R2 | 275 | 53.1807 | 19.3133 | 14.1515 | 41.4647 | 55.2568 | 20.936 | 14.8916 | 44.4996
BARK4 M1 | 400 | 133.1155 | 46.7616 | 41.5795 | 107.7104 | 125.6886 | 48.6035 | 33.253 | 101.9888
BARK4 M2 | 400 | 133.1155 | 46.7616 | 41.5795 | 107.7104 | 125.6886 | 48.6035 | 33.253 | 101.9888
BARK4 R1 | 400 | 133.1155 | 46.7616 | 41.5795 | 107.7104 | 125.6886 | 48.6035 | 33.253 | 101.9888
BARK4 R2 | 400 | 133.1155 | 46.7616 | 41.5795 | 107.7104 | 125.6886 | 48.6035 | 33.253 | 101.9888
BEDD2 M1/4 | 275 | 60.7229 | 21.7196 | 13.9198 | 44.6359 | 63.6617 | 24.3134 | 13.7461 | 48.1304
BEDD2 M2/3 | 275 | 79.0978 | 27.9921 | 17.8088 | 57.3955 | 81.511 | 31.0861 | 17.3892 | 61.3516
BEDD2 R1 | 275 | 50.952 | 18.8794 | 11.3053 | 38.0048 | 51.1072 | 19.6864 | 11.1127 | 38.9535
BEDD2 R2 | 275 | 79.0978 | 27.9921 | 17.8088 | 57.3955 | 81.511 | 31.0861 | 17.3892 | 61.3516
BEDD2 R3 | 275 | 79.0978 | 27.9921 | 17.8088 | 57.3955 | 81.511 | 31.0861 | 17.3892 | 61.3516
BEDD2 R4 | 275 | 50.952 | 18.8794 | 11.3053 | 38.0048 | 51.1072 | 19.6864 | 11.1127 | 38.9535
BEDD4B | 400 | 42.1102 | 15.7151 | 3.1227 | 25.3472 | 37.1776 | 14.8622 | 3.6975 | 24.7159
BESW2 MC1 | 275 | 59.2149 | 21.7937 | 10.8719 | 41.6928 | 51.603 | 20.5655 | 8.4566 | 37.5407
BESW2 MC2 | 275 | 59.2149 | 21.7937 | 10.8719 | 41.6928 | 51.603 | 20.5655 | 8.4566 | 37.5407
BESW2 MC3 | 275 | 59.2149 | 21.7937 | 10.8719 | 41.6928 | 51.603 | 20.5655 | 8.4566 | 37.5407
BESW2 MC4 | 275 | 59.2149 | 21.7937 | 10.8719 | 41.6928 | 51.603 | 20.5655 | 8.4566 | 37.5407
BICF4A | 400 | 100.4761 | 36.7506 | 34.0004 | 85.9736 | 65.4234 | 26.123 | 16.6248 | 53.5683
BICF4B | 400 | 100.4761 | 36.7506 | 34.0004 | 85.9736 | 65.4234 | 26.123 | 16.6248 | 53.5683
BIRK2 MC1 | 275 | 61.7018 | 21.9063 | 16.5979 | 47.5781 | 60.679 | 22.9235 | 13.9539 | 46.3727
BIRK2 MC2 | 275 | 61.7018 | 21.9063 | 16.5979 | 47.5781 | 60.679 | 22.9235 | 13.9539 | 46.3727
BIRK2 MC3 | 275 | 61.7018 | 21.9063 | 16.5979 | 47.5781 | 60.679 | 22.9235 | 13.9539 | 46.3727
BIRK2 MC4 | 275 | 61.7018 | 21.9063 | 16.5979 | 47.5781 | 60.679 | 22.9235 | 13.9539 | 46.3727
BISW2 MC1 | 275 | 64.7188 | 23.756 | 12.0979 | 45.6939 | 59.7075 | 23.5065 | 9.7887 | 43.0319
BISW2 MC2 | 275 | 64.7188 | 23.756 | 12.0979 | 45.6939 | 59.7075 | 23.5065 | 9.7887 | 43.0319
BISW2 MC3 | 275 | 64.7188 | 23.756 | 12.0979 | 45.6939 | 59.7075 | 23.5065 | 9.7887 | 43.0319
BISW2 MC4 | 275 | 64.7188 | 23.756 | 12.0979 | 45.6939 | 59.7075 | 23.5065 | 9.7887 | 43.0319
BLYT1A | 132 | 30.3061 | 10.743 | 4.5574 | 19.7503 | 31.7166 | 11.9451 | 5.1815 | 22.0744
BLYT1B | 132 | 30.1001 | 10.6956 | 4.518 | 19.6439 | 31.5644 | 11.8994 | 5.1474 | 21.9756
BLYT2 M1 | 275 | 85.7256 | 31.4768 | 25.5439 | 70.0588 | 78.6044 | 30.4945 | 22.3135 | 65.4392
BLYT2 M2 | 275 | 85.7256 | 31.4768 | 25.5439 | 70.0588 | 78.6044 | 30.4945 | 22.3135 | 65.4392
BLYT2 R1 | 275 | 85.7256 | 31.4768 | 25.5439 | 70.0588 | 78.6044 | 30.4945 | 22.3135 | 65.4392
BLYT2 R2 | 275 | 85.7256 | 31.4768 | 25.5439 | 70.0588 | 78.6044 | 30.4945 | 22.3135 | 65.4392
BODE4 M1 | 400 | 86.1728 | 30.6507 | 21.4606 | 64.8072 | 72.4374 | 27.831 | 16.1258 | 55.4848
BODE4 R1 | 400 | 86.1728 | 30.6507 | 21.4606 | 64.8072 | 72.4374 | 27.831 | 16.1258 | 55.4848
BOLN4 M1 | 400 | 69.6071 | 25.7709 | 20.8522 | 57.2978 | 61.8917 | 23.862 | 18.6637 | 52.4097
BOLN4 M2 | 400 | 69.6071 | 25.7709 | 20.8522 | 57.2978 | 61.8917 | 23.862 | 18.6637 | 52.4097
BOLN4 R1 | 400 | 69.6071 | 25.7709 | 20.8522 | 57.2978 | 61.8917 | 23.862 | 18.6637 | 52.4097
BOLN4 R2 | 400 | 69.6071 | 25.7709 | 20.8522 | 57.2978 | 61.8917 | 23.862 | 18.6637 | 52.4097
BOTW4 MC1 | 400 | 76.6634 | 27.6304 | 15.4127 | 54.4879 | 62.0007 | 24.0674 | 11.9428 | 45.9793
BOTW4 MC2 | 400 | 76.6634 | 27.6304 | 15.4127 | 54.4879 | 62.0007 | 24.0674 | 11.9428 | 45.9793
BRAI4A | 400 | 63.6503 | 23.373 | 14.3492 | 47.4037 | 48.3478 | 18.9229 | 9.2526 | 36.0136
BRAI4A BRFO | 400 | 63.6503 | 23.373 | 14.3492 | 47.4037 | 48.3478 | 18.9229 | 9.2526 | 36.0136
BRAI4A RAYL | 400 | 63.6503 | 23.373 | 14.3492 | 47.4037 | 48.3478 | 18.9229 | 9.2526 | 36.0136
BRAI4B | 400 | 61.4565 | 22.602 | 13.6158 | 45.5798 | 46.1159 | 17.9911 | 8.8284 | 34.2717
BRAI4B PELH | 400 | 61.4565 | 22.602 | 13.6158 | 45.5798 | 46.1159 | 17.9911 | 8.8284 | 34.2717
BRAI4B RAYL | 400 | 61.4565 | 22.602 | 13.6158 | 45.5798 | 46.1159 | 17.9911 | 8.8284 | 34.2717
BRAW2 MC1 | 275 | 65.0921 | 23.4068 | 14.9808 | 48.0831 | 66.1184 | 25.3382 | 14.0729 | 49.9064
BRAW2 MC2 | 275 | 65.0921 | 23.4068 | 14.9808 | 48.0831 | 66.1184 | 25.3382 | 14.0729 | 49.9064
BRAW2 MC3 | 275 | 65.0921 | 23.4068 | 14.9808 | 48.0831 | 66.1184 | 25.3382 | 14.0729 | 49.9064
BRAW2 MC4 | 275 | 65.0921 | 23.4068 | 14.9808 | 48.0831 | 66.1184 | 25.3382 | 14.0729 | 49.9064
BRAW4A | 400 | 35.0239 | 12.7978 | 4.4517 | 22.5506 | 30.6845 | 11.6651 | 4.2469 | 20.7439
BRED2 MC1 | 275 | 78.8876 | 28.9637 | 15.8485 | 56.8094 | 75.469 | 29.5929 | 12.8957 | 54.7464
BRED2 MC2 | 275 | 78.8876 | 28.9637 | 15.8485 | 56.8094 | 75.469 | 29.5929 | 12.8957 | 54.7464
BRED2 MC3 | 275 | 78.8876 | 28.9637 | 15.8485 | 56.8094 | 75.469 | 29.5929 | 12.8957 | 54.7464
BRED2 MC4 | 275 | 78.8876 | 28.9637 | 15.8485 | 56.8094 | 75.469 | 29.5929 | 12.8957 | 54.7464
BRFO4 M3 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 M5 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 M6 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 M7 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 R3 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 R5 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 R6 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRFO4 R7 | 400 | 86.0619 | 31.5547 | 27.6665 | 72.2915 | 78.1033 | 30.1326 | 22.8527 | 65.4666
BRIM1 M1 | 132 | 64.2823 | 23.5451 | 23.0663 | 56.3641 | 79.387 | 30.3773 | 27.0329 | 69.9929
BRIM1 M2 | 132 | 64.2823 | 23.5451 | 23.0663 | 56.3641 | 79.387 | 30.3773 | 27.0329 | 69.9929
BRIM1 R1 | 132 | 64.2823 | 23.5451 | 23.0663 | 56.3641 | 79.387 | 30.3773 | 27.0329 | 69.9929
BRIM1 R2 | 132 | 64.2823 | 23.5451 | 23.0663 | 56.3641 | 79.387 | 30.3773 | 27.0329 | 69.9929
BRIN2 M1 | 275 | 64.5293 | 23.6896 | 13.8918 | 47.3939 | 68.2044 | 26.6865 | 12.8985 | 50.6389
BRIN2 M2 | 275 | 68.2892 | 25.0766 | 16.9409 | 52.4046 | 71.7337 | 27.6691 | 16.4733 | 55.6033
BRIN2 R1 | 275 | 64.5293 | 23.6896 | 13.8918 | 47.3939 | 68.2044 | 26.6865 | 12.8985 | 50.6389
BRIN2 R2 | 275 | 68.2892 | 25.0766 | 16.9409 | 52.4046 | 71.7337 | 27.6691 | 16.4733 | 55.6033
BRIN4 MC1 | 400 | 70.76 | 25.9027 | 16.1737 | 52.8057 | 55.3237 | 21.6316 | 11.2985 | 41.8902
BRIN4 MC4 | 400 | 70.76 | 25.9027 | 16.1737 | 52.8057 | 55.3237 | 21.6316 | 11.2985 | 41.8902
BRLE4 M1 | 400 | 122.1162 | 43.8105 | 24.6234 | 86.5809 | 104.6582 | 40.7036 | 21.1264 | 78.6899
BRLE4 M2 | 400 | 122.1162 | 43.8105 | 24.6234 | 86.5809 | 104.6582 | 40.7036 | 21.1264 | 78.6899
BRLE4 R1 | 400 | 122.1162 | 43.8105 | 24.6234 | 86.5809 | 104.6582 | 40.7036 | 21.1264 | 78.6899
BRLE4 R2 | 400 | 122.1162 | 43.8105 | 24.6234 | 86.5809 | 104.6582 | 40.7036 | 21.1264 | 78.6899
BULL4 MC1 | 400 | 69.2025 | 25.3084 | 15.2602 | 51.0517 | 51.4854 | 20.2485 | 8.9603 | 37.5961
BULL4 MC2 | 400 | 69.2025 | 25.3084 | 15.2602 | 51.0517 | 51.4854 | 20.2485 | 8.9603 | 37.5961
BURW4 MC1 | 400 | 93.8213 | 34.001 | 22.8118 | 70.8964 | 62.5388 | 24.8994 | 11.3691 | 46.5822
BURW4 MC2 | 400 | 93.8213 | 34.001 | 22.8118 | 70.8964 | 62.5388 | 24.8994 | 11.3691 | 46.5822
BURW4 MC3 | 400 | 93.8213 | 34.001 | 22.8118 | 70.8964 | 62.5388 | 24.8994 | 11.3691 | 46.5822
BURW4 MC4 | 400 | 93.8213 | 34.001 | 22.8118 | 70.8964 | 62.5388 | 24.8994 | 11.3691 | 46.5822
BUSH2 MC1 | 275 | 55.4227 | 20.3389 | 11.3288 | 40.0924 | 55.0891 | 21.4898 | 10.3813 | 40.7725
BUSH2 MC2 | 275 | 55.4227 | 20.3389 | 11.3288 | 40.0924 | 55.0891 | 21.4898 | 10.3813 | 40.7725
BUSH2 MC3 | 275 | 55.4227 | 20.3389 | 11.3288 | 40.0924 | 55.0891 | 21.4898 | 10.3813 | 40.7725
BUSH2 MC4 | 275 | 55.4227 | 20.3389 | 11.3288 | 40.0924 | 55.0891 | 21.4898 | 10.3813 | 40.7725
BUST2 M1 | 275 | 72.2257 | 26.0423 | 18.8363 | 55.6657 | 74.8978 | 28.5792 | 17.6382 | 58.0553
BUST2 M2 | 275 | 72.2257 | 26.0423 | 18.8363 | 55.6657 | 74.8978 | 28.5792 | 17.6382 | 58.0553
BUST2 R1 | 275 | 72.2257 | 26.0423 | 18.8363 | 55.6657 | 74.8978 | 28.5792 | 17.6382 | 58.0553
BUST2 R2 | 275 | 72.2257 | 26.0423 | 18.8363 | 55.6657 | 74.8978 | 28.5792 | 17.6382 | 58.0553
CANT4 MC1 | 400 | 88.1533 | 31.9972 | 18.621 | 63.8718 | 66.9414 | 26.5165 | 11.5363 | 49.0363
CANT4 MC2 | 400 | 88.1533 | 31.9972 | 18.621 | 63.8718 | 66.9414 | 26.5165 | 11.5363 | 49.0363
CANT4 MC3 | 400 | 88.1533 | 31.9972 | 18.621 | 63.8718 | 66.9414 | 26.5165 | 11.5363 | 49.0363
CANT4 MC4 | 400 | 88.1533 | 31.9972 | 18.621 | 63.8718 | 66.9414 | 26.5165 | 11.5363 | 49.0363
CANT4 R5 | 400 | 88.1533 | 31.9972 | 18.621 | 63.8718 | 66.9414 | 26.5165 | 11.5363 | 49.0363
CANT4 R5 | 400 | 88.1584 | 32.0003 | 18.622 | 63.8772 | 66.9424 | 26.5172 | 11.5323 | 49.0332
CANT4 R5 | 400 | 88.1584 | 32.0003 | 18.622 | 63.8772 | 66.9424 | 26.5172 | 11.5323 | 49.0332
CAPE2 M1 | 275 | 70.5946 | 24.688 | 22.193 | 57.1071 | 79.0866 | 28.9882 | 23.6064 | 64.6018
CAPE2 M2 | 275 | 70.5946 | 24.688 | 22.193 | 57.1071 | 79.0866 | 28.9882 | 23.6064 | 64.6018
CAPE2 R1 | 275 | 70.5946 | 24.688 | 22.193 | 57.1071 | 79.0866 | 28.9882 | 23.6064 | 64.6018
CAPE2 R2 | 275 | 70.5946 | 24.688 | 22.193 | 57.1071 | 79.0866 | 28.9882 | 23.6064 | 64.6018
CAPE4A | 400 | 93.3823 | 32.9071 | 24.2799 | 70.8176 | 85.9344 | 32.5381 | 19.5605 | 65.5764
CAPE4B | 400 | 93.3841 | 32.908 | 24.2792 | 70.8181 | 86.6678 | 32.811 | 19.6767 | 66.0784
CARE2 MC1 | 275 | 46.656 | 17.5025 | 8.1957 | 32.9479 | 39.6663 | 15.739 | 7.093 | 29.3513
CARE2 MC2 | 275 | 46.656 | 17.5025 | 8.1957 | 32.9479 | 39.6663 | 15.739 | 7.093 | 29.3513
CARR1 M1 | 132 | 34.6653 | 12.8217 | 9.8494 | 27.9821 | 40.4676 | 15.4362 | 11.659 | 33.489
CARR1 M2 | 132 | 34.6653 | 12.8217 | 9.8494 | 27.9821 | 40.4676 | 15.4362 | 11.659 | 33.489
CARR1 M3 | 132 | 34.6653 | 12.8217 | 9.8494 | 27.9821 | 40.4676 | 15.4362 | 11.659 | 33.489
CARR1 M4 | 132 | 41.946 | 14.7439 | 14.0588 | 34.9098 | 53.8245 | 19.729 | 17.5423 | 45.4432
CARR1 R1 | 132 | 34.6653 | 12.8217 | 9.8494 | 27.9821 | 40.4676 | 15.4362 | 11.659 | 33.489
CARR1 R2 | 132 | 34.6653 | 12.8217 | 9.8494 | 27.9821 | 40.4676 | 15.4362 | 11.659 | 33.489
CARR1 R3 | 132 | 41.946 | 14.7439 | 14.0588 | 34.9098 | 53.8245 | 19.729 | 17.5423 | 45.4432
CARR1 R4 | 132 | 41.946 | 14.7439 | 14.0588 | 34.9098 | 53.8245 | 19.729 | 17.5423 | 45.4432
CARR1B | 132 | 41.1554 | 14.3038 | 8.023 | 28.2516 | 50.9314 | 19.1993 | 7.0208 | 34.1727
CARR1C | 132 | 40.9855 | 14.2874 | 7.6155 | 27.821 | 50.477 | 19.1506 | 5.5705 | 32.6536
CARR1D | 132 | 41.2656 | 14.3228 | 8.2556 | 28.511 | 51.3104 | 19.2491 | 7.3895 | 34.6118
CARR2 M1 | 275 | 81.8769 | 29.5554 | 22.0043 | 63.802 | 88.573 | 33.3188 | 24.2406 | 71.3605
CARR2 M2 | 275 | 81.8769 | 29.5554 | 22.0043 | 63.802 | 88.573 | 33.3188 | 24.2406 | 71.3605
CARR2 R1 | 275 | 81.8769 | 29.5554 | 22.0043 | 63.802 | 88.573 | 33.3188 | 24.2406 | 71.3605
CARR2 R2 | 275 | 81.8769 | 29.5554 | 22.0043 | 63.802 | 88.573 | 33.3188 | 24.2406 | 71.3605
CARR4 M1 | 400 | 121.0244 | 44.4 | 35.9514 | 98.7425 | 106.6971 | 41.3661 | 30.9762 | 89.4767
CARR4 M2/4 | 400 | 121.0244 | 44.4 | 35.9514 | 98.7425 | 106.6971 | 41.3661 | 30.9762 | 89.4767
CARR4 R1 | 400 | 121.0244 | 44.4 | 35.9514 | 98.7425 | 106.6971 | 41.3661 | 30.9762 | 89.4767
CARR4 R1/2 | 400 | 121.0244 | 44.4 | 35.9514 | 98.7425 | 106.6971 | 41.3661 | 30.9762 | 89.4767
CARR4 R2 | 400 | 121.0244 | 44.4 | 35.9514 | 98.7425 | 106.6971 | 41.3661 | 30.9762 | 89.4767
CARR4 R4 | 400 | 121.0244 | 44.4 | 35.9514 | 98.7425 | 106.6971 | 41.3661 | 30.9762 | 89.4767
CARR4A | 400 | 101.8034 | 36.2007 | 8.996 | 60.1915 | 83.7612 | 32.4712 | 8.6025 | 54.5236
CARR4B | 400 | 103.482 | 36.7212 | 9.2481 | 61.1797 | 86.1994 | 33.4199 | 8.6369 | 55.8997
CASK1 M1 | 132 | 48.2664 | 16.0412 | 13.0262 | 35.7119 | 53.5811 | 18.8126 | 15.7511 | 42.3561
CELL1 M1 | 132 | 45.3751 | 16.8639 | 14.2045 | 38.0536 | 56.4166 | 22.2166 | 16.7434 | 48.1624
CELL1 M2 | 132 | 43.5988 | 16.1509 | 12.103 | 34.9438 | 48.3454 | 18.6933 | 12.9736 | 39.4099
CELL1 R1 | 132 | 45.3751 | 16.8639 | 14.2045 | 38.0536 | 56.4166 | 22.2166 | 16.7434 | 48.1624
CELL1 R2 | 132 | 43.5988 | 16.1509 | 12.103 | 34.9438 | 48.3454 | 18.6933 | 12.9736 | 39.4099
CELL1A | 132 | 37.9365 | 13.5906 | 6.9165 | 26.1365 | 46.8513 | 18.7634 | 8.2801 | 34.8156
CELL4 M1 | 400 | 91.1262 | 33.6588 | 16.3262 | 63.9269 | 75.1762 | 29.6924 | 14.1055 | 56.0969
CELL4 M2 | 400 | 91.1262 | 33.6588 | 16.3262 | 63.9269 | 75.1762 | 29.6924 | 14.1055 | 56.0969
CELL4 R1 | 400 | 91.1262 | 33.6588 | 16.3262 | 63.9269 | 75.1762 | 29.6924 | 14.1055 | 56.0969
CELL4 R2 | 400 | 91.1262 | 33.6588 | 16.3262 | 63.9269 | 75.1762 | 29.6924 | 14.1055 | 56.0969
CHIC4 MB1 | 400 | 36.8292 | 13.7279 | 7.3811 | 26.7953 | 30.1972 | 11.7911 | 5.7396 | 22.4148
CHIC4 MB2 | 400 | 36.8292 | 13.7279 | 7.3811 | 26.7953 | 30.1972 | 11.7911 | 5.7396 | 22.4148
CHIC4 R1/2 | 400 | 36.5021 | 13.7753 | 10.697 | 30.1782 | 28.6672 | 11.282 | 7.6913 | 23.6464
CHSI2 MC1 | 275 | 85.5149 | 30.7283 | 18.5417 | 61.998 | 74.2314 | 29.26 | 12.183 | 53.5629
CHSI2 MC2 | 275 | 85.5149 | 30.7283 | 18.5417 | 61.998 | 74.2314 | 29.26 | 12.183 | 53.5629
CHSI2 MC3 | 275 | 85.5149 | 30.7283 | 18.5417 | 61.998 | 74.2314 | 29.26 | 12.183 | 53.5629
CHSI2 MC4 | 275 | 85.5149 | 30.7283 | 18.5417 | 61.998 | 74.2314 | 29.26 | 12.183 | 53.5629
CHTE2 MC1 | 275 | 69.3195 | 25.0299 | 16.6336 | 52.0313 | 59.023 | 23.4119 | 10.9806 | 44.09
CHTE2 MC2 | 275 | 69.3195 | 25.0299 | 16.6336 | 52.0313 | 59.023 | 23.4119 | 10.9806 | 44.09
CHTE2 MC3 | 275 | 69.3195 | 25.0299 | 16.6336 | 52.0313 | 59.023 | 23.4119 | 10.9806 | 44.09
CHTE2 MC4 | 275 | 69.3195 | 25.0299 | 16.6336 | 52.0313 | 59.023 | 23.4119 | 10.9806 | 44.09
CILF4 M1 | 400 | 79.7334 | 28.6874 | 19.0669 | 59.6371 | 70.1359 | 27.0518 | 13.8564 | 52.1134
CILF4 M2 | 400 | 79.7334 | 28.6874 | 19.0669 | 59.6371 | 70.1359 | 27.0518 | 13.8564 | 52.1134
CILF4 R1 | 400 | 79.7334 | 28.6874 | 19.0669 | 59.6371 | 70.1359 | 27.0518 | 13.8564 | 52.1134
CILF4 R2 | 400 | 79.7334 | 28.6874 | 19.0669 | 59.6371 | 70.1359 | 27.0518 | 13.8564 | 52.1134
CITR4 M5 | 400 | 114.6617 | 38.7862 | 27.6219 | 82.4739 | 127.2835 | 48.1815 | 25.2876 | 93.4265
CITR4 M6 | 400 | 114.6617 | 38.7862 | 27.6219 | 82.4739 | 127.2835 | 48.1815 | 25.2876 | 93.4265
CITR4 MC1 | 400 | 114.6666 | 38.7874 | 27.6238 | 82.4775 | 127.3036 | 48.1843 | 25.3381 | 93.481
CITR4 MC2 | 400 | 114.6666 | 38.7874 | 27.6238 | 82.4775 | 127.3036 | 48.1843 | 25.3381 | 93.481
CITR4 MC3 | 400 | 114.6666 | 38.7874 | 27.6238 | 82.4775 | 127.3036 | 48.1843 | 25.3381 | 93.481
CITR4 MC4 | 400 | 114.6666 | 38.7874 | 27.6238 | 82.4775 | 127.3036 | 48.1843 | 25.3381 | 93.481
CITR4 R5 | 400 | 114.6617 | 38.7862 | 27.6219 | 82.4739 | 127.2835 | 48.1815 | 25.2876 | 93.4265
CITR4 R6 | 400 | 114.6617 | 38.7862 | 27.6219 | 82.4739 | 127.2835 | 48.1815 | 25.2876 | 93.4265
CLEH4 M1 | 400 | 76.6551 | 27.8734 | 16.5836 | 56.0026 | 68.4092 | 26.8225 | 13.6646 | 51.5973
CLEH4 R1 | 400 | 76.6551 | 27.8734 | 16.5836 | 56.0026 | 68.4092 | 26.8225 | 13.6646 | 51.5973
CONQ4 M1 | 400 | 126.1521 | 43.7107 | 33.0519 | 94.8682 | 128.877 | 47.8807 | 34.9273 | 102.6409
CONQ4 M2 | 400 | 126.1521 | 43.7107 | 33.0519 | 94.8682 | 128.877 | 47.8807 | 34.9273 | 102.6409
CONQ4 M3 | 400 | 126.1521 | 43.7107 | 33.0519 | 94.8682 | 128.877 | 47.8807 | 34.9273 | 102.6409
CONQ4 M4 | 400 | 126.1521 | 43.7107 | 33.0519 | 94.8682 | 128.877 | 47.8807 | 34.9273 | 102.6409
CONQ4 R1/3 | 400 | 126.1521 | 43.7107 | 33.0519 | 94.8682 | 128.877 | 47.8807 | 34.9273 | 102.6409
CONQ4 R2/4 | 400 | 126.1521 | 43.7107 | 33.0519 | 94.8682 | 128.877 | 47.8807 | 34.9273 | 102.6409
COSO4 M | 400 | 99.303 | 35.2234 | 21.9725 | 71.786 | 86.6715 | 33.2528 | 19.3458 | 66.3723
COSO4 R | 400 | 99.303 | 35.2234 | 21.9725 | 71.786 | 86.6715 | 33.2528 | 19.3458 | 66.3723
COTT4 M1 | 400 | 99.9118 | 36.768 | 23.0647 | 75.0625 | 80.0892 | 31.1576 | 16.2726 | 60.3361
COTT4 M2 | 400 | 99.9118 | 36.768 | 23.0647 | 75.0625 | 80.0892 | 31.1576 | 16.2726 | 60.3361
COTT4 M3 | 400 | 95.8857 | 35.6825 | 29.97 | 80.4328 | 80.2974 | 31.2303 | 23.4964 | 67.6627
COTT4 M4 | 400 | 95.8857 | 35.6825 | 29.97 | 80.4328 | 80.2974 | 31.2303 | 23.4964 | 67.6627
COTT4 R1/2 | 400 | 95.8857 | 35.6825 | 29.97 | 80.4328 | 80.2974 | 31.2303 | 23.4964 | 67.6627
COTT4 R3/4 | 400 | 95.8857 | 35.6825 | 29.97 | 80.4328 | 80.2974 | 31.2303 | 23.4964 | 67.6627
COVE2 MC1 | 275 | 61.8997 | 22.5353 | 12.6458 | 44.5155 | 58.0638 | 22.5416 | 11.8465 | 43.7251
COVE2 MC2 | 275 | 61.8997 | 22.5353 | 12.6458 | 44.5155 | 58.0638 | 22.5416 | 11.8465 | 43.7251
COVE2 MC3 | 275 | 61.8997 | 22.5353 | 12.6458 | 44.5155 | 58.0638 | 22.5416 | 11.8465 | 43.7251
COVE2 MC4 | 275 | 61.8997 | 22.5353 | 12.6458 | 44.5155 | 58.0638 | 22.5416 | 11.8465 | 43.7251
COWL4 M1 | 400 | 125.5043 | 46.22 | 37.7401 | 103.1051 | 104.9411 | 40.8607 | 29.5265 | 87.3124
COWL4 M2 | 400 | 125.5043 | 46.22 | 37.7401 | 103.1051 | 104.9411 | 40.8607 | 29.5265 | 87.3124
COWL4 R1 | 400 | 125.5043 | 46.22 | 37.7401 | 103.1051 | 104.9411 | 40.8607 | 29.5265 | 87.3124
COWL4 R2 | 400 | 125.5043 | 46.22 | 37.7401 | 103.1051 | 104.9411 | 40.8607 | 29.5265 | 87.3124
CREB2A | 275 | 71.6686 | 25.428 | 15.6421 | 51.6028 | 69.776 | 25.9117 | 12.7344 | 49.379
CREB2B | 275 | 71.6789 | 25.4285 | 15.6499 | 51.6112 | 70.5548 | 26.1936 | 12.8781 | 49.9215
CREB4 MB1 | 400 | 119.882 | 42.8809 | 30.6752 | 91.318 | 98.6576 | 37.9044 | 22.2906 | 75.8955
CREB4 MB2 | 400 | 119.882 | 42.8809 | 30.6752 | 91.318 | 98.6576 | 37.9044 | 22.2906 | 75.8955
CREB4 RB1 | 400 | 119.882 | 42.8809 | 30.6752 | 91.318 | 98.6576 | 37.9044 | 22.2906 | 75.8955
CREB4 RB2 | 400 | 119.882 | 42.8809 | 30.6752 | 91.318 | 98.6576 | 37.9044 | 22.2906 | 75.8955
DAIN4 M1 | 400 | 112.6223 | 40.6547 | 23.2342 | 80.7286 | 96.5122 | 37.4393 | 19.3992 | 72.3463
DAIN4 M2 | 400 | 112.6223 | 40.6547 | 23.2342 | 80.7286 | 96.5122 | 37.4393 | 19.3992 | 72.3463
DAIN4 R1 | 400 | 115.1247 | 41.4511 | 24.0078 | 82.6286 | 97.5714 | 37.8696 | 19.7063 | 73.2619
DAIN4 R2 | 400 | 115.1247 | 41.4511 | 24.0078 | 82.6286 | 97.5714 | 37.8696 | 19.7063 | 73.2619
DIDC4 M1 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 M2 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 M3 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 M4 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 M5 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 M6 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 R1/2 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 R3/4 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 R5 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DIDC4 R6 | 400 | 119.6961 | 43.061 | 26.6032 | 87.5006 | 109.2268 | 41.5206 | 26.6769 | 85.396
DINO4 1 | 400 | 71.8581 | 25.0272 | 20.4225 | 55.8163 | 75.125 | 27.6246 | 22.6419 | 61.7089
DINO4 2 | 400 | 71.8581 | 25.0272 | 20.4225 | 55.8163 | 75.125 | 27.6246 | 22.6419 | 61.7089
DINO4 3 | 400 | 71.8581 | 25.0272 | 20.4225 | 55.8163 | 75.125 | 27.6246 | 22.6419 | 61.7089
DRAK1 M1 | 132 | 31.3714 | 11.2289 | 12.6819 | 28.5619 | 38.7362 | 14.3001 | 15.7322 | 35.9556
DRAK1 M2 | 132 | 31.3714 | 11.2289 | 12.6819 | 28.5619 | 38.7362 | 14.3001 | 15.7322 | 35.9556
DRAK1 R1 | 132 | 31.3714 | 11.2289 | 12.6819 | 28.5619 | 38.7362 | 14.3001 | 15.7322 | 35.9556
DRAK1 R2 | 132 | 31.3714 | 11.2289 | 12.6819 | 28.5619 | 38.7362 | 14.3001 | 15.7322 | 35.9556
DRAK4 M1 | 400 | 122.0163 | 44.002 | 22.9221 | 85.1503 | 108.7855 | 42.7202 | 18.3604 | 78.7758
DRAK4 M2 | 400 | 122.0163 | 44.002 | 22.9221 | 85.1503 | 108.7855 | 42.7202 | 18.3604 | 78.7758
DRAK4 M3 | 400 | 122.0163 | 44.002 | 22.9221 | 85.1503 | 108.7855 | 42.7202 | 18.3604 | 78.7758
DRAK4 R1/3 | 400 | 122.0163 | 44.002 | 22.9221 | 85.1503 | 108.7855 | 42.7202 | 18.3604 | 78.7758
DRAK4 R2 | 400 | 122.0163 | 44.002 | 22.9221 | 85.1503 | 108.7855 | 42.7202 | 18.3604 | 78.7758
DRAX1 M1 | 132 | 39.0181 | 11.7908 | 11.6386 | 28.3133 | 48.8334 | 16.5851 | 14.7119 | 38.1668
DRAX1 M2 | 132 | 39.0181 | 11.7908 | 11.6386 | 28.3133 | 48.8334 | 16.5851 | 14.7119 | 38.1668
DRAX1 R1 | 132 | 39.0181 | 11.7908 | 11.6386 | 28.3133 | 48.8334 | 16.5851 | 14.7119 | 38.1668
DRAX1 R2 | 132 | 39.0181 | 11.7908 | 11.6386 | 28.3133 | 48.8334 | 16.5851 | 14.7119 | 38.1668
DRAX4 M1 | 400 | 124.8193 | 43.3544 | 35.009 | 96.3213 | 130.1975 | 47.8289 | 37.6393 | 105.2796
DRAX4 M2 | 400 | 124.8193 | 43.3544 | 35.009 | 96.3213 | 130.1975 | 47.8289 | 37.6393 | 105.2796
DRAX4 M3 | 400 | 124.8193 | 43.3544 | 35.009 | 96.3213 | 130.1975 | 47.8289 | 37.6393 | 105.2796
DRAX4 M4 | 400 | 113.8047 | 39.6733 | 33.2011 | 89.3076 | 119.9367 | 44.0135 | 35.7384 | 97.9829
DRAX4 M5 | 400 | 113.8047 | 39.6733 | 33.2011 | 89.3076 | 119.9367 | 44.0135 | 35.7384 | 97.9829
DRAX4 M6 | 400 | 113.8047 | 39.6733 | 33.2011 | 89.3076 | 119.9367 | 44.0135 | 35.7384 | 97.9829
DRAX4 R1/2/3 | 400 | 124.8193 | 43.3544 | 35.009 | 96.3213 | 130.1975 | 47.8289 | 37.6393 | 105.2796
DRAX4 R4/5/6 | 400 | 113.8047 | 39.6733 | 33.2011 | 89.3076 | 119.9367 | 44.0135 | 35.7384 | 97.9829
DUNG2 M1 | 275 | 45.3076 | 16.1478 | 15.1536 | 37.9901 | 46.3347 | 17.0547 | 15.2217 | 39.3406
DUNG2 M2 | 275 | 45.3076 | 16.1478 | 15.1536 | 37.9901 | 46.3347 | 17.0547 | 15.2217 | 39.3406
DUNG2 R1 | 275 | 45.3076 | 16.1478 | 15.1536 | 37.9901 | 46.3347 | 17.0547 | 15.2217 | 39.3406
DUNG2 R2 | 275 | 45.3076 | 16.1478 | 15.1536 | 37.9901 | 46.3347 | 17.0547 | 15.2217 | 39.3406
DUNG4 M1 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
DUNG4 M2 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
DUNG4 M3 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
DUNG4 M4 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
DUNG4 M5 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
DUNG4 R1/2 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
DUNG4 R4/5 | 400 | 78.7003 | 27.8673 | 12.7575 | 52.1678 | 72.1711 | 27.178 | 13.5604 | 51.996
EALI2 MC1 | 275 | 59.8937 | 21.0312 | 13.743 | 43.4856 | 65.8629 | 25.5466 | 8.542 | 44.6704
EALI2 MC2 | 275 | 59.8937 | 21.0312 | 13.743 | 43.4856 | 65.8629 | 25.5466 | 8.542 | 44.6704
EALI2 MC3 | 275 | 59.8937 | 21.0312 | 13.743 | 43.4856 | 65.8629 | 25.5466 | 8.542 | 44.6704
EALI2 MC4 | 275 | 59.8937 | 21.0312 | 13.743 | 43.4856 | 65.8629 | 25.5466 | 8.542 | 44.6704
EASO4 M1 | 400 | 81.9191 | 29.8125 | 18.5533 | 60.7146 | 72.9803 | 27.6806 | 19.1844 | 58.3307
EASO4 M2 | 400 | 81.9191 | 29.8125 | 18.5533 | 60.7146 | 72.9803 | 27.6806 | 19.1844 | 58.3307
EASO4 R1 | 400 | 81.9191 | 29.8125 | 18.5533 | 60.7146 | 72.9803 | 27.6806 | 19.1844 | 58.3307
EASO4 R2 | 400 | 81.9191 | 29.8125 | 18.5533 | 60.7146 | 72.9803 | 27.6806 | 19.1844 | 58.3307
EASO4A | 400 | 81.9191 | 29.8125 | 18.5533 | 60.7146 | 72.9803 | 27.6806 | 19.1844 | 58.3307
EASO4B | 400 | 81.9191 | 29.8125 | 18.5533 | 60.7146 | 72.9803 | 27.6806 | 19.1844 | 58.3307
ECLA1 M1 | 132 | 45.1697 | 16.913 | 12.9994 | 36.9181 | 47.6439 | 18.5903 | 14.1903 | 40.4809
ECLA1 M2 | 132 | 45.1697 | 16.913 | 12.9994 | 36.9181 | 47.6439 | 18.5903 | 14.1903 | 40.4809
ECLA1 R1 | 132 | 45.7179 | 17.0637 | 13.1021 | 37.2338 | 54.4195 | 21.0315 | 15.7941 | 45.5372
ECLA1 R2 | 132 | 45.7179 | 17.0637 | 13.1021 | 37.2338 | 54.4195 | 21.0315 | 15.7941 | 45.5372
ECLA4 M1 | 400 | 112.7334 | 41.0565 | 23.482 | 81.5446 | 91.1339 | 35.7488 | 17.3132 | 67.8697
ECLA4 M2 | 400 | 112.7334 | 41.0565 | 23.482 | 81.5446 | 91.1339 | 35.7488 | 17.3132 | 67.8697
ECLA4 R1 | 400 | 112.7334 | 41.0565 | 23.482 | 81.5446 | 91.1339 | 35.7488 | 17.3132 | 67.8697
ECLA4 R2 | 400 | 112.7334 | 41.0565 | 23.482 | 81.5446 | 91.1339 | 35.7488 | 17.3132 | 67.8697
EGGB4 M1 | 400 | 102.1833 | 36.4312 | 25.5845 | 77.106 | 93.8521 | 35.66 | 20.4905 | 70.9213
EGGB4 M2 | 400 | 102.1833 | 36.4312 | 25.5845 | 77.106 | 93.8521 | 35.66 | 20.4905 | 70.9213
EGGB4 R1 | 400 | 92.8833 | 33.0368 | 24.8194 | 71.5404 | 85.8286 | 32.489 | 19.5297 | 65.4761
EGGB4 R2 | 400 | 92.8833 | 33.0368 | 24.8194 | 71.5404 | 85.8286 | 32.489 | 19.5297 | 65.4761
ELLA2 MC1 | 275 | 64.0666 | 23.1161 | 8.3116 | 41.0027 | 64.7996 | 24.9503 | 8.0179 | 43.303
ELLA2 MC2 | 275 | 64.0666 | 23.1161 | 8.3116 | 41.0027 | 64.7996 | 24.9503 | 8.0179 | 43.303
ELLA2 MC3 | 275 | 64.0666 | 23.1161 | 8.3116 | 41.0027 | 64.7996 | 24.9503 | 8.0179 | 43.303
ELLA2 MC4 | 275 | 64.0666 | 23.1161 | 8.3116 | 41.0027 | 64.7996 | 24.9503 | 8.0179 | 43.303
ELST1 M1 | 132 | 102.7871 | 37.4122 | 27.0666 | 79.9754 | 127.0055 | 49.1368 | 33.1303 | 102.6202
ELST1 M2 | 132 | 102.7871 | 37.4122 | 27.0666 | 79.9754 | 127.0055 | 49.1368 | 33.1303 | 102.6202
ELST1 M3 | 132 | 102.7871 | 37.4122 | 27.0666 | 79.9754 | 127.0055 | 49.1368 | 33.1303 | 102.6202
ELST1 R1 | 132 | 102.7871 | 37.4122 | 27.0666 | 79.9754 | 127.0055 | 49.1368 | 33.1303 | 102.6202
ELST1 R2 | 132 | 102.7871 | 37.4122 | 27.0666 | 79.9754 | 127.0055 | 49.1368 | 33.1303 | 102.6202
ELST1 R3 | 132 | 102.7871 | 37.4122 | 27.0666 | 79.9754 | 127.0055 | 49.1368 | 33.1303 | 102.6202
ELST2 M1 | 275 | 69.3483 | 25.0954 | 18.3787 | 53.869 | 75.3236 | 28.3919 | 20.1479 | 60.3002
ELST2 M2 | 275 | 68.9532 | 25.2147 | 15.6938 | 51.3528 | 75.8536 | 29.2298 | 16.6771 | 58.0143
ELST2 R1 | 275 | 69.3483 | 25.0954 | 18.3787 | 53.869 | 75.3236 | 28.3919 | 20.1479 | 60.3002
ELST2 R2 | 275 | 68.9532 | 25.2147 | 15.6938 | 51.3528 | 75.8536 | 29.2298 | 16.6771 | 58.0143
ELST4 M1 | 400 | 93.135 | 33.4973 | 29.0855 | 76.4578 | 110.1547 | 41.6527 | 33.7415 | 92.6473
ELST4 R1 | 400 | 93.135 | 33.4973 | 29.0855 | 76.4578 | 110.1547 | 41.6527 | 33.7415 | 92.6473
ELST4A | 400 | 56.7979 | 20.8612 | 7.5536 | 37.0558 | 54.0017 | 20.5286 | 8.5431 | 37.5748
ENDE4 MC1 | 400 | 92.1081 | 34.0007 | 17.9296 | 66.0138 | 62.6487 | 24.9249 | 10.8585 | 46.1077
ENDE4 MC2 | 400 | 92.1081 | 34.0007 | 17.9296 | 66.0138 | 62.6487 | 24.9249 | 10.8585 | 46.1077
ENDE4 MC3 | 400 | 92.1081 | 34.0007 | 17.9296 | 66.0138 | 62.6487 | 24.9249 | 10.8585 | 46.1077
ENDE4 MC4 | 400 | 92.1081 | 34.0007 | 17.9296 | 66.0138 | 62.6487 | 24.9249 | 10.8585 | 46.1077
EXET4 M1 | 400 | 58.6917 | 21.4353 | 11.8518 | 42.1659 | 55.2754 | 21.4569 | 11.2048 | 41.5495
EXET4 M2 | 400 | 58.6917 | 21.4353 | 11.8518 | 42.1659 | 55.2754 | 21.4569 | 11.2048 | 41.5495
EXET4 R1 | 400 | 58.6917 | 21.4353 | 11.8518 | 42.1659 | 55.2754 | 21.4569 | 11.2048 | 41.5495
EXET4 R2 | 400 | 58.6917 | 21.4353 | 11.8518 | 42.1659 | 55.2754 | 21.4569 | 11.2048 | 41.5495
FAWL1 M1 | 132 | 50.1925 | 17.6344 | 18.1932 | 43.132 | 63.8439 | 24.0355 | 21.524 | 55.5153
FAWL1 M2 | 132 | 50.1925 | 17.6344 | 18.1932 | 43.132 | 63.8439 | 24.0355 | 21.524 | 55.5153
FAWL1 R1 | 132 | 50.1925 | 17.6344 | 18.1932 | 43.132 | 63.8439 | 24.0355 | 21.524 | 55.5153
FAWL1 R2 | 132 | 50.1925 | 17.6344 | 18.1932 | 43.132 | 63.8439 | 24.0355 | 21.524 | 55.5153
FAWL4 M1/3 | 400 | 80.0902 | 28.3396 | 10.4159 | 50.4941 | 66.7993 | 25.7731 | 8.3102 | 44.7588
FAWL4 M1/3(1) | 400 | 80.0902 | 28.3396 | 10.4159 | 50.4941 | 66.7993 | 25.7731 | 8.3102 | 44.7588
FAWL4 M2/4(2) | 400 | 80.0902 | 28.3396 | 10.4159 | 50.4941 | 66.7993 | 25.7731 | 8.3102 | 44.7588
FAWL4 M2/4(3) | 400 | 80.0902 | 28.3396 | 10.4159 | 50.4941 | 66.7993 | 25.7731 | 8.3102 | 44.7588
FAWL4 R1/3 | 400 | 80.0902 | 28.3396 | 10.4159 | 50.4941 | 66.7993 | 25.7731 | 8.3102 | 44.7588
FAWL4 R2/4 | 400 | 80.0902 | 28.3396 | 10.4159 | 50.4941 | 66.7993 | 25.7731 | 8.3102 | 44.7588
FECK2 M1 | 275 | 62.7751 | 23.1215 | 14.2777 | 46.9764 | 62.0498 | 23.9167 | 14.0658 | 47.889
FECK2 M2 | 275 | 62.7751 | 23.1215 | 14.2777 | 46.9764 | 62.0498 | 23.9167 | 14.0658 | 47.889
FECK2 R | 275 | 62.7751 | 23.1215 | 14.2777 | 46.9764 | 62.0498 | 23.9167 | 14.0658 | 47.889
FECK4 M1 | 400 | 78.9764 | 29.6189 | 13.4297 | 55.3171 | 66.7607 | 26.3716 | 12.7058 | 50.0008
FECK4 M2 | 400 | 78.9764 | 29.6189 | 13.4297 | 55.3171 | 66.7607 | 26.3716 | 12.7058 | 50.0008
FECK4 R1 | 400 | 78.9764 | 29.6189 | 13.4297 | 55.3171 | 66.7607 | 26.3716 | 12.7058 | 50.0008
FECK4 R2 | 400 | 78.9764 | 29.6189 | 13.4297 | 55.3171 | 66.7607 | 26.3716 | 12.7058 | 50.0008
FENW4A | 400 | 109.9369 | 38.5166 | 14.6831 | 69.1538 | 94.1523 | 35.9518 | 7.7673 | 58.6108
FERR2 M1 | 275 | 57.4668 | 20.7439 | 11.3707 | 40.707 | 58.7008 | 22.1709 | 11.4704 | 42.8248
FERR2 M2 | 275 | 57.048 | 20.5238 | 15.1586 | 44.1837 | 61.0207 | 22.8493 | 14.2385 | 46.5523
FERR2 R1 | 275 | 62.1271 | 22.3284 | 12.1047 | 43.6818 | 62.1581 | 23.639 | 10.3783 | 43.8089
FERR2 R2 | 275 | 62.1271 | 22.3284 | 12.1047 | 43.6818 | 62.1581 | 23.639 | 10.3783 | 43.8089
FERR2A | 275 | 57.0682 | 20.4344 | 12.6978 | 41.5965 | 60.8345 | 22.7427 | 11.6809 | 43.8439
FERR2B | 275 | 56.9433 | 20.4151 | 9.2307 | 38.1019 | 57.9191 | 21.8818 | 8.942 | 39.8875
FERR4A | 400 | 74.4321 | 26.5052 | 9.5959 | 47.0799 | 65.2307 | 24.762 | 8.1225 | 43.1412
FFES2 Term205 | 275 | 35.4523 | 13.2496 | 2.6779 | 21.4157 | 34.418 | 13.5052 | 2.3395 | 21.4388
FFES2 Term210 | 275 | 35.2759 | 13.2036 | 2.6509 | 21.3235 | 34.7732 | 13.6419 | 2.3553 | 21.6479
FIDF2 M1 | 275 | 51.1222 | 18.319 | 15.7067 | 41.6138 | 51.2703 | 19.1213 | 14.2105 | 41.2522
FIDF2 M2 | 275 | 50.3655 | 18.0131 | 15.5373 | 41.0116 | 49.4414 | 18.438 | 13.4843 | 39.5595
FIDF2 M3 | 275 | 63.2302 | 22.6386 | 16.2403 | 48.2561 | 59.2237 | 22.436 | 13.7128 | 45.4421
FIDF2 M4 | 275 | 63.7695 | 22.8283 | 16.3697 | 48.6538 | 61.1915 | 23.1493 | 14.3634 | 47.1015
FIDF2 R1 | 275 | 51.1222 | 18.319 | 15.7067 | 41.6138 | 51.2703 | 19.1213 | 14.2105 | 41.2522
FIDF2 R2 | 275 | 63.7695 | 22.8283 | 16.3697 | 48.6538 | 61.1915 | 23.1493 | 14.3634 | 47.1015
FLEE4 MC1 | 400 | 104.4646 | 37.5484 | 21.0464 | 74.148 | 83.7986 | 32.9124 | 15.6129 | 62.158
FLEE4 MC2 | 400 | 104.4646 | 37.5484 | 21.0464 | 74.148 | 83.7986 | 32.9124 | 15.6129 | 62.158
FLEE4 MC3 | 400 | 104.4646 | 37.5484 | 21.0464 | 74.148 | 83.7986 | 32.9124 | 15.6129 | 62.158
FLEE4 MC4 | 400 | 104.4646 | 37.5484 | 21.0464 | 74.148 | 83.7986 | 32.9124 | 15.6129 | 62.158
FLIB4 M1 | 400 | 116.7822 | 40.693 | 30.6149 | 88.1634 | 120.2209 | 45.1248 | 29.858 | 93.6741
FLIB4 M2 | 400 | 116.7822 | 40.693 | 30.6149 | 88.1634 | 120.2209 | 45.1248 | 29.858 | 93.6741
FOUR2 MC1 | 275 | 38.8177 | 15.2669 | 4.9129 | 26.5035 | 31.9025 | 13.1188 | 3.8848 | 22.4376
FOUR2 MC2 | 275 | 38.8177 | 15.2669 | 4.9129 | 26.5035 | 31.9025 | 13.1188 | 3.8848 | 22.4376
FROD2 MC1 | 275 | 51.0228 | 18.2333 | 16.4798 | 42.2656 | 54.369 | 19.9816 | 17.6533 | 45.9116
FROD2 MC3 | 275 | 51.019 | 17.9862 | 10.9155 | 36.3519 | 53.697 | 19.6921 | 10.8383 | 38.6872
FROD4 M1 | 400 | 88.9937 | 32.0177 | 29.8494 | 75.1293 | 84.153 | 31.6443 | 28.0657 | 72.8175
FROD4 R1 | 400 | 88.9937 | 32.0177 | 29.8494 | 75.1293 | 84.153 | 31.6443 | 28.0657 | 72.8175
GART4A | 400 | 99.5692 | 35.2484 | 13.9984 | 63.8472 | 81.4286 | 31.2008 | 6.9711 | 51.0957
GART4B | 400 | 102.4541 | 36.3173 | 14.1869 | 65.5473 | 88.4719 | 33.867 | 8.1907 | 56.0858
GRAI4 M1 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 M2 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 M3 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 M4 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 M5 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 M6 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 M7 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 R1/2 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 R3 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 R4 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 R5 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 R6 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GRAI4 R7 | 400 | 137.5014 | 48.2259 | 44.2893 | 112.491 | 126.2587 | 47.5586 | 40.3106 | 107.5686
GREN1 M1 | 132 | 40.7092 | 14.9166 | 10.535 | 31.6303 | 44.5403 | 17.766 | 10.3563 | 35.4813
GREN1 M2 | 132 | 39.2054 | 14.468 | 11.0434 | 31.5043 | 40.0654 | 15.7434 | 10.2044 | 32.469
GREN1 R1 | 132 | 40.7092 | 14.9166 | 10.535 | 31.6303 | 44.5403 | 17.766 | 10.3563 | 35.4813
GREN1 R2 | 132 | 39.2054 | 14.468 | 11.0434 | 31.5043 | 40.0654 | 15.7434 | 10.2044 | 32.469
GREN4 M1 | 400 | 80.0497 | 30.0495 | 13.194 | 55.6905 | 53.9092 | 21.8753 | 8.9723 | 39.9086
GREN4 M2 | 400 | 80.0497 | 30.0495 | 13.194 | 55.6905 | 53.9092 | 21.8753 | 8.9723 | 39.9086
GREN4 R1 | 400 | 80.0497 | 30.0495 | 13.194 | 55.6905 | 53.9092 | 21.8753 | 8.9723 | 39.9086
GREN4 R2 | 400 | 80.0497 | 30.0495 | 13.194 | 55.6905 | 53.9092 | 21.8753 | 8.9723 | 39.9086
GRIW4 MC1 | 400 | 68.2548 | 24.6322 | 18.1702 | 53.0054 | 59.1257 | 22.7457 | 12.1125 | 44.2798
GRIW4 MC2 | 400 | 68.2548 | 24.6322 | 18.1702 | 53.0054 | 59.1257 | 22.7457 | 12.1125 | 44.2798
GRSA2 M1 | 275 | 54.9341 | 19.7521 | 16.4396 | 44.3732 | 57.3223 | 21.3682 | 15.8268 | 46.046
GRSA2 M2 | 275 | 54.9341 | 19.7521 | 16.4396 | 44.3732 | 57.3223 | 21.3682 | 15.8268 | 46.046
GRSA2 R1 | 275 | 54.9341 | 19.7521 | 16.4396 | 44.3732 | 57.3223 | 21.3682 | 15.8268 | 46.046
GRSA2 R2 | 275 | 54.9341 | 19.7521 | 16.4396 | 44.3732 | 57.3223 | 21.3682 | 15.8268 | 46.046
GRSB2 M3 | 275 | 55.2768 | 19.8612 | 16.6303 | 44.7183 | 58.2607 | 21.6577 | 16.5365 | 47.165
GRSB2 M4 | 275 | 55.2768 | 19.8612 | 16.6303 | 44.7183 | 58.2607 | 21.6577 | 16.5365 | 47.165
GRSB2 R3 | 275 | 55.2768 | 19.8612 | 16.6303 | 44.7183 | 58.2607 | 21.6577 | 16.5365 | 47.165
GRSB2 R4 | 275 | 55.2768 | 19.8612 | 16.6303 | 44.7183 | 58.2607 | 21.6577 | 16.5365 | 47.165
HACK2A | 275 | 69.899 | 24.6969 | 11.9002 | 46.8268 | 71.214 | 26.6571 | 12.2094 | 49.9081
HACK2B | 275 | 68.8244 | 24.3158 | 11.8963 | 46.2841 | 71.5693 | 26.8168 | 12.2705 | 50.1952
HACK4 M1 | 400 | 121.0389 | 40.8483 | 29.1326 | 86.9007 | 137.9287 | 51.1392 | 30.4175 | 102.7392
HACK4 M2 | 400 | 121.0389 | 40.8483 | 29.1326 | 86.9007 | 137.9287 | 51.1392 | 30.4175 | 102.7392
HACK4 R1 | 400 | 121.0389 | 40.8483 | 29.1326 | 86.9007 | 137.9287 | 51.1392 | 30.4175 | 102.7392
HACK4 R2 | 400 | 121.0389 | 40.8483 | 29.1326 | 86.9007 | 137.9287 | 51.1392 | 30.4175 | 102.7392
HAMB4A | 400 | 70.4852 | 25.0406 | 9.3638 | 44.7766 | 58.7277 | 22.8083 | 4.8017 | 37.0576
HAMB4A_HEYS | 400 | 70.4852 | 25.0406 | 9.3638 | 44.7766 | 58.7277 | 22.8083 | 4.8017 | 37.0576
HAMB4A_PEWO | 400 | 70.4852 | 25.0406 | 9.3638 | 44.7766 | 58.7277 | 22.8083 | 4.8017 | 37.0576
HAMB4B | 400 | 70.4597 | 25.0318 | 9.3634 | 44.7637 | 58.253 | 22.6235 | 4.8074 | 36.8018
HAMB4B_HEYS | 400 | 70.4597 | 25.0318 | 9.3634 | 44.7637 | 58.253 | 22.6235 | 4.8074 | 36.8018
HAMB4B_PEWO | 400 | 70.4597 | 25.0318 | 9.3634 | 44.7637 | 58.253 | 22.6235 | 4.8074 | 36.8018
HAMH1B | 132 | 47.0539 | 16.272 | 9.9833 | 32.9953 | 56.3207 | 21.2568 | 6.4335 | 36.4951
HAMH1C | 132 | 46.0523 | 16.0382 | 8.7147 | 31.3961 | 54.5197 | 20.2841 | 8.0646 | 36.7506
HAMH4 M1 | 400 | 76.2808 | 28.3651 | 13.5388 | 53.6531 | 71.5273 | 27.9248 | 13.747 | 53.2386
HAMH4 M2 | 400 | 76.2808 | 28.3651 | 13.5388 | 53.6531 | 71.5273 | 27.9248 | 13.747 | 53.2386
HAMH4 R1 | 400 | 76.2808 | 28.3651 | 13.5388 | 53.6531 | 71.5273 | 27.9248 | 13.747 | 53.2386
HAMH4 R2 | 400 | 76.2808 | 28.3651 | 13.5388 | 53.6531 | 71.5273 | 27.9248 | 13.747 | 53.2386
HARK1 M1 | 132 | 28.4151 | 10.8289 | 7.2124 | 22.5268 | 33.3825 | 13.1214 | 7.8397 | 26.3962
HARK1 M2 | 132 | 28.4151 | 10.8289 | 7.2124 | 22.5268 | 33.3825 | 13.1214 | 7.8397 | 26.3962
HARK1 R1 | 132 | 27.3801 | 11.3431 | 6.7959 | 22.8374 | 30.5222 | 12.8238 | 7.8377 | 25.9733
HARK1 R2 | 132 | 30.7908 | 11.8486 | 7.9431 | 24.6996 | 36.129 | 14.3574 | 9.2275 | 29.532
HARK1 R3 | 132 | 30.7908 | 11.8486 | 7.9431 | 24.6996 | 36.129 | 14.3574 | 9.2275 | 29.532
HARK2 MC1 | 275 | 41.0598 | 15.4033 | 10.5698 | 32.3534 | 43.8313 | 16.7701 | 11.4657 | 35.1822
HARK2 MC11 | 275 | 49.6959 | 18.8553 | 15.3062 | 41.9717 | 52.7502 | 20.3849 | 16.4211 | 45.2497
HARK2 MC12 | 275 | 49.6959 | 18.8553 | 15.3062 | 41.9717 | 52.7502 | 20.3849 | 16.4211 | 45.2497
HARK2 MC13 | 275 | 49.6959 | 18.8553 | 15.3062 | 41.9717 | 52.7502 | 20.3849 | 16.4211 | 45.2497
HARK2 MC2 | 275 | 41.0598 | 15.4033 | 10.5698 | 32.3534 | 43.8313 | 16.7701 | 11.4657 | 35.1822
HARK2 MC3 | 275 | 41.0598 | 15.4033 | 10.5698 | 32.3534 | 43.8313 | 16.7701 | 11.4657 | 35.1822
HARK2 MC4 | 275 | 41.0598 | 15.4033 | 10.5698 | 32.3534 | 43.8313 | 16.7701 | 11.4657 | 35.1822
HARK2 MC6 | 275 | 41.0598 | 15.4033 | 10.5698 | 32.3534 | 43.8313 | 16.7701 | 11.4657 | 35.1822
HARK2 MC8 | 275 | 49.6959 | 18.8553 | 15.3062 | 41.9717 | 52.7502 | 20.3849 | 16.4211 | 45.2497
HARK2 MC9 | 275 | 49.6959 | 18.8553 | 15.3062 | 41.9717 | 52.7502 | 20.3849 | 16.4211 | 45.2497
HARK4 M1 | 400 | 70.906 | 26.5273 | 11.9931 | 49.5085 | 57.7943 | 22.572 | 11.9261 | 43.8477
HARK4 M2 | 400 | 70.906 | 26.5273 | 11.9931 | 49.5085 | 57.7943 | 22.572 | 11.9261 | 43.8477
HARK4 R1 | 400 | 70.906 | 26.5273 | 11.9931 | 49.5085 | 57.7943 | 22.572 | 11.9261 | 43.8477
HARK4 R2 | 400 | 70.906 | 26.5273 | 11.9931 | 49.5085 | 57.7943 | 22.572 | 11.9261 | 43.8477
HARM2 MC1 | 275 | 65.0644 | 23.4942 | 14.0189 | 47.2447 | 55.2925 | 21.6406 | 9.1155 | 39.72
HARM2 MC2 | 275 | 65.0644 | 23.4942 | 14.0189 | 47.2447 | 55.2925 | 21.6406 | 9.1155 | 39.72
HARM2 MC3 | 275 | 65.0644 | 23.4942 | 14.0189 | 47.2447 | 55.2925 | 21.6406 | 9.1155 | 39.72
HARM2 MC4 | 275 | 65.0644 | 23.4942 | 14.0189 | 47.2447 | 55.2925 | 21.6406 | 9.1155 | 39.72
HATL2 M1 | 275 | 91.192 | 31.6388 | 24.4012 | 69.1452 | 93.694 | 34.7057 | 25.9069 | 74.9881
HATL2 M2 | 275 | 91.192 | 31.6388 | 24.4012 | 69.1452 | 93.694 | 34.7057 | 25.9069 | 74.9881
HATL2 R1 | 275 | 91.192 | 31.6388 | 24.4012 | 69.1452 | 93.694 | 34.7057 | 25.9069 | 74.9881
HATL2 R2 | 275 | 91.192 | 31.6388 | 24.4012 | 69.1452 | 93.694 | 34.7057 | 25.9069 | 74.9881
HAWP2 MC1 | 275 | 78.3477 | 27.9568 | 18.2566 | 57.7935 | 69.7346 | 27.0455 | 12.7422 | 50.9904
HAWP2 MC2 | 275 | 78.3477 | 27.9568 | 18.2566 | 57.7935 | 69.7346 | 27.0455 | 12.7422 | 50.9904
HAWP2 MC3 | 275 | 78.3477 | 27.9568 | 18.2566 | 57.7935 | 69.7346 | 27.0455 | 12.7422 | 50.9904
HAWP2 MC4 | 275 | 78.3477 | 27.9568 | 18.2566 | 57.7935 | 69.7346 | 27.0455 | 12.7422 | 50.9904
HEDO2 M1 | 275 | 72.5311 | 25.7821 | 21.2193 | 57.6807 | 76.3624 | 28.2642 | 22.867 | 62.8387
HEDO2 M2 | 275 | 72.5311 | 25.7821 | 21.2193 | 57.6807 | 76.3624 | 28.2642 | 22.867 | 62.8387
HEDO2 R1 | 275 | 72.5311 | 25.7821 | 21.2193 | 57.6807 | 76.3624 | 28.2642 | 22.867 | 62.8387
HEDO2 R2 | 275 | 72.5311 | 25.7821 | 21.2193 | 57.6807 | 76.3624 | 28.2642 | 22.867 | 62.8387
HEYS1 M1 | 132 | 38.4359 | 12.9951 | 12.5699 | 30.9478 | 44.3849 | 16.1928 | 14.2983 | 37.1983
HEYS1 M2 | 132 | 38.4359 | 12.9951 | 12.5699 | 30.9478 | 44.3849 | 16.1928 | 14.2983 | 37.1983
HEYS1 R1 | 132 | 38.4359 | 12.9951 | 12.5699 | 30.9478 | 44.3849 | 16.1928 | 14.2983 | 37.1983
HEYS1 R2 | 132 | 38.4359 | 12.9951 | 12.5699 | 30.9478 | 44.3849 | 16.1928 | 14.2983 | 37.1983
HEYS4 M1 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 M2 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 M3 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 M4 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 M5 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 R1/2 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 R3/4 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HEYS4 R5 | 400 | 99.8757 | 35.8687 | 33.8409 | 84.567 | 104.1181 | 39.1849 | 35.7939 | 91.2097
HIBU4 M1 | 400 | 118.9231 | 40.1155 | 28.919 | 85.6509 | 136.9623 | 50.5707 | 31.41 | 102.9278
HIBU4 M2 | 400 | 118.9231 | 40.1155 | 28.919 | 85.6509 | 136.9623 | 50.5707 | 31.41 | 102.9278
HIBU4 R1 | 400 | 118.9231 | 40.1155 | 28.919 | 85.6509 | 136.9623 | 50.5707 | 31.41 | 102.9278
HIBU4 R2 | 400 | 118.9231 | 40.1155 | 28.919 | 85.6509 | 136.9623 | 50.5707 | 31.41 | 102.9278
HIGM2 M1 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM2 M2 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM2 M3 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM2 R1 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM2 R4 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM2 R5 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM2 R6 | 275 | 61.7351 | 22.9151 | 16.5345 | 48.9413 | 57.1748 | 22.5527 | 12.2802 | 44.1745
HIGM4 MC1 | 400 | 80.3557 | 29.6728 | 18.4703 | 60.434 | 66.4417 | 26.0515 | 11.5912 | 48.4337
HIGM4 MC2 | 400 | 80.3557 | 29.6728 | 18.4703 | 60.434 | 66.4417 | 26.0515 | 11.5912 | 48.4337
HIGM4A | 400 | 64.6786 | 23.6819 | 9.4338 | 42.9251 | 54.931 | 21.2415 | 5.0301 | 35.0702
HINP2 M1 | 275 | 23.4133 | 8.3654 | 7.8761 | 19.7066 | 25.2082 | 9.265 | 8.31 | 21.4126
HINP2 M2 | 275 | 23.7802 | 8.5053 | 7.921 | 19.9493 | 27.9269 | 10.3133 | 8.7342 | 23.3194
HINP4 M1 | 400 | 69.318 | 25.0752 | 15.7744 | 51.2362 | 68.2291 | 25.9014 | 17.7483 | 54.3785
HINP4 M2 | 400 | 69.318 | 25.0752 | 15.7744 | 51.2362 | 68.2291 | 25.9014 | 17.7483 | 54.3785
HINP4 M3 | 400 | 69.318 | 25.0752 | 15.7744 | 51.2362 | 68.2291 | 25.9014 | 17.7483 | 54.3785
HINP4 M4 | 400 | 69.318 | 25.0752 | 15.7744 | 51.2362 | 68.2291 | 25.9014 | 17.7483 | 54.3785
HINP4 R1/2 | 400 | 69.318 | 25.0752 | 15.7744 | 51.2362 | 68.2291 | 25.9014 | 17.7483 | 54.3785
HINP4 R3/4 | 400 | 69.318 | 25.0752 | 15.7744 | 51.2362 | 68.2291 | 25.9014 | 17.7483 | 54.3785
HUMR4 M1 | 400 | 100.0526 | 35.0592 | 28.547 | 78.1282 | 96.6905 | 35.9339 | 26.8548 | 77.6731
HUMR4 M2 | 400 | 100.0526 | 35.0592 | 28.547 | 78.1282 | 96.6905 | 35.9339 | 26.8548 | 77.6731
HUMR4 R1 | 400 | 100.0526 | 35.0592 | 28.547 | 78.1282 | 96.6905 | 35.9339 | 26.8548 | 77.6731
HUMR4 R2 | 400 | 100.0526 | 35.0592 | 28.547 | 78.1282 | 96.6905 | 35.9339 | 26.8548 | 77.6731
HURS2 MC1 | 275 | 70.6792 | 24.651 | 19.106 | 53.9677 | 74.736 | 29.5568 | 16.2614 | 58.061
HURS2 MC2 | 275 | 70.6792 | 24.651 | 19.106 | 53.9677 | 74.736 | 29.5568 | 16.2614 | 58.061
HURS2 MC3 | 275 | 70.6792 | 24.651 | 19.106 | 53.9677 | 74.736 | 29.5568 | 16.2614 | 58.061
HURS2 MC4 | 275 | 70.6792 | 24.651 | 19.106 | 53.9677 | 74.736 | 29.5568 | 16.2614 | 58.061
HUTT4 MC1 | 400 | 73.706 | 27.6374 | 21.3147 | 60.3998 | 48.5585 | 19.6802 | 11.2659 | 39.098
HUTT4 MC2 | 400 | 73.706 | 27.6374 | 21.3147 | 60.3998 | 48.5585 | 19.6802 | 11.2659 | 39.098
HUTT4 MC3 | 400 | 73.706 | 27.6374 | 21.3147 | 60.3998 | 48.5585 | 19.6802 | 11.2659 | 39.098
HUTT4 MC4 | 400 | 73.706 | 27.6374 | 21.3147 | 60.3998 | 48.5585 | 19.6802 | 11.2659 | 39.098
IMPP4 MC1 | 400 | 54.4631 | 20.1469 | 12.0959 | 40.5879 | 46.5693 | 18.0075 | 9.6506 | 35.117
IMPP4 MC2 | 400 | 54.4631 | 20.1469 | 12.0959 | 40.5879 | 46.5693 | 18.0075 | 9.6506 | 35.117
INDQ4 MC1 | 400 | 36.0089 | 13.5331 | 6.0708 | 25.2095 | 37.6048 | 14.615 | 7.297 | 27.9658
INDQ4 MC2 | 400 | 36.0089 | 13.5331 | 6.0708 | 25.2095 | 37.6048 | 14.615 | 7.297 | 27.9658
INDQ4 MC3 | 400 | 36.0089 | 13.5331 | 6.0708 | 25.2095 | 37.6048 | 14.615 | 7.297 | 27.9658
INDQ4 MC4 | 400 | 36.0089 | 13.5331 | 6.0708 | 25.2095 | 37.6048 | 14.615 | 7.297 | 27.9658
IROA1 M1 | 132 | 40.9053 | 14.7617 | 10.1262 | 31.0024 | 49.4767 | 18.7772 | 11.5965 | 38.1515
IROA1 M2 | 132 | 40.9053 | 14.7617 | 10.1262 | 31.0024 | 49.4767 | 18.7772 | 11.5965 | 38.1515
IROA1 R1 | 132 | 43.3885 | 15.5954 | 10.6904 | 32.7455 | 52.2484 | 19.7598 | 12.2705 | 40.2152
IROA1 R2 | 132 | 28.1026 | 10.1729 | 8.4712 | 22.8579 | 33.9922 | 12.725 | 9.5049 | 27.5008
IROA2 MC1 | 275 | 57.9639 | 21.3439 | 11.1485 | 41.3334 | 56.1014 | 21.7988 | 11.2066 | 42.0348
IROA2 MC2 | 275 | 57.9639 | 21.3439 | 11.1485 | 41.3334 | 56.1014 | 21.7988 | 11.2066 | 42.0348
IROA2 MC3 | 275 | 57.9639 | 21.3439 | 11.1485 | 41.3334 | 56.1014 | 21.7988 | 11.2066 | 42.0348
IROA2 MC4 | 275 | 57.9639 | 21.3439 | 11.1485 | 41.3334 | 56.1014 | 21.7988 | 11.2066 | 42.0348
IROA2 MC5 | 275 | 57.9639 | 21.3439 | 11.1485 | 41.3334 | 56.1014 | 21.7988 | 11.2066 | 42.0348
IRON1 M1 | 132 | 27.3955 | 10.6293 | 8.9657 | 23.9977 | 30.4207 | 11.9359 | 9.9499 | 26.8298
IRON1 M2 | 132 | 27.2783 | 10.5875 | 8.8696 | 23.8425 | 30.1012 | 11.8259 | 9.7641 | 26.4885
IRON1 R1 | 132 | 17.8723 | 6.4982 | 6.3943 | 15.5841 | 20.4025 | 7.457 | 7.382 | 17.9278
IRON1 R2 | 132 | 17.8723 | 6.4982 | 6.3943 | 15.5841 | 20.4025 | 7.457 | 7.382 | 17.9278
IRON4 M1 | 400 | 71.8482 | 26.6612 | 13.2631 | 50.9678 | 60.6518 | 23.9451 | 10.9631 | 44.8266
IRON4 M2 | 400 | 71.8482 | 26.6612 | 13.2631 | 50.9678 | 60.6518 | 23.9451 | 10.9631 | 44.8266
IRON4 R1 | 400 | 71.8482 | 26.6612 | 13.2631 | 50.9678 | 60.6518 | 23.9451 | 10.9631 | 44.8266
IRON4 R2 | 400 | 71.8482 | 26.6612 | 13.2631 | 50.9678 | 60.6518 | 23.9451 | 10.9631 | 44.8266
IVER2 M1 | 275 | 66.0102 | 24.1078 | 16.4882 | 50.5817 | 70.9184 | 27.0341 | 16.993 | 55.225
IVER2 M2 | 275 | 66.0102 | 24.1078 | 16.4882 | 50.5817 | 70.9184 | 27.0341 | 16.993 | 55.225
IVER2 R1 | 275 | 66.0102 | 24.1078 | 16.4882 | 50.5817 | 70.9184 | 27.0341 | 16.993 | 55.225
IVER2 R2 | 275 | 69.5327 | 25.4378 | 15.6775 | 51.6519 | 69.4824 | 26.9542 | 14.4157 | 52.5346
IVER4A | 400 | 46.2296 | 17.0156 | 5.7419 | 29.8055 | 43.7793 | 16.7886 | 5.9768 | 29.7195
IVER4B | 400 | 44.3925 | 16.3902 | 5.3553 | 28.5346 | 41.5127 | 16.1423 | 5.1134 | 27.942
JORD2 MC1 | 275 | 50.0889 | 18.9121 | 8.8533 | 35.5991 | 49.6528 | 20.5203 | 7.3829 | 36.4029
JORD2 MC2 | 275 | 50.0889 | 18.9121 | 8.8533 | 35.5991 | 49.6528 | 20.5203 | 7.3829 | 36.4029
KEAD4 M2 | 400 | 101.4338 | 36.6103 | 25.9749 | 77.7496 | 92.8775 | 35.3522 | 21.934 | 71.9296
KEAD4 M3 | 400 | 100.2758 | 36.0556 | 26.3594 | 77.3497 | 85.1637 | 32.5105 | 18.984 | 64.9608
KEAD4 R2 | 400 | 101.4338 | 36.6103 | 25.9749 | 77.7496 | 92.8775 | 35.3522 | 21.934 | 71.9296
KEAD4 R3 | 400 | 94.9328 | 34.6782 | 22.0178 | 71.0601 | 74.3583 | 28.9129 | 15.8696 | 56.7587
KEAR2 M1 | 275 | 74.6117 | 26.8212 | 19.0491 | 56.98 | 80.3778 | 30.3906 | 19.7857 | 62.7644
KEAR2 M2 | 275 | 74.6117 | 26.8212 | 19.0491 | 56.98 | 80.3778 | 30.3906 | 19.7857 | 62.7644
KEAR2 R1 | 275 | 74.6117 | 26.8212 | 19.0491 | 56.98 | 80.3778 | 30.3906 | 19.7857 | 62.7644
KEAR2 R2 | 275 | 74.6117 | 26.8212 | 19.0491 | 56.98 | 80.3778 | 30.3906 | 19.7857 | 62.7644
KEMS4 M1 | 400 | 130.092 | 44.5851 | 30.6196 | 93.6725 | 110.622 | 42.316 | 22.1456 | 81.9895
KEMS4 M2 | 400 | 130.092 | 44.5851 | 30.6196 | 93.6725 | 110.622 | 42.316 | 22.1456 | 81.9895
KEMS4 R1 | 400 | 130.092 | 44.5851 | 30.6196 | 93.6725 | 110.622 | 42.316 | 22.1456 | 81.9895
KEMS4 R2 | 400 | 130.092 | 44.5851 | 30.6196 | 93.6725 | 110.622 | 42.316 | 22.1456 | 81.9895
KENG4 M1 | 400 | 113.4381 | 38.3032 | 28.4385 | 82.6074 | 131.1462 | 48.4716 | 30.7906 | 99.3398
KENG4 M2 | 400 | 113.4381 | 38.3032 | 28.4385 | 82.6074 | 131.1462 | 48.4716 | 30.7906 | 99.3398
KENG4 R1 | 400 | 113.4381 | 38.3032 | 28.4385 | 82.6074 | 131.1462 | 48.4716 | 30.7906 | 99.3398
KENG4 R2 | 400 | 113.4381 | 38.3032 | 28.4385 | 82.6074 | 131.1462 | 48.4716 | 30.7906 | 99.3398
KIBY2 M1 | 275 | 74.0759 | 26.1791 | 18.5091 | 55.532 | 77.6957 | 29.3169 | 17.509 | 58.9694
KIBY2 M2 | 275 | 74.0759 | 26.1791 | 18.5091 | 55.532 | 77.6957 | 29.3169 | 17.509 | 58.9694
KIBY2 R1 | 275 | 62.9039 | 22.6361 | 15.1154 | 47.1277 | 61.2969 | 23.2763 | 13.8166 | 46.7343
KIBY2 R2 | 275 | 62.9039 | 22.6361 | 15.1154 | 47.1277 | 61.2969 | 23.2763 | 13.8166 | 46.7343
KILL4 M1 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 M2 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 M3 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 M4 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 M5 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 M9 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 R1/2 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 R3/4 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 R5 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KILL4 R9 | 400 | 106.0691 | 37.741 | 38.0843 | 91.4581 | 105.4347 | 39.2987 | 36.4996 | 92.0764
KINO1 M1 | 132 | 28.4571 | 10.0147 | 10.3296 | 24.4925 | 34.9463 | 12.9127 | 12.4922 | 30.7535
KINO1 M2 | 132 | 28.4571 | 10.0147 | 10.3296 | 24.4925 | 34.9463 | 12.9127 | 12.4922 | 30.7535
KINO1 R1 | 132 | 28.4571 | 10.0147 | 10.3296 | 24.4925 | 34.9463 | 12.9127 | 12.4922 | 30.7535
KINO1 R2 | 132 | 28.4571 | 10.0147 | 10.3296 | 24.4925 | 34.9463 | 12.9127 | 12.4922 | 30.7535
KINO1A | 132 | 28.1353 | 9.8185 | 6.4884 | 20.3739 | 34.4656 | 12.7608 | 7.6739 | 25.7204
KINO1B | 132 | 23.6831 | 8.7881 | 1.7051 | 14.1334 | 25.6657 | 10.3186 | 0.98457 | 15.5773
KINO4 M1 | 400 | 124.3571 | 44.0693 | 39.6017 | 101.9251 | 116.02 | 44.1035 | 35.2433 | 97.6151
KINO4 M2 | 400 | 124.3571 | 44.0693 | 39.6017 | 101.9251 | 116.02 | 44.1035 | 35.2433 | 97.6151
KINO4 M3 | 400 | 124.3571 | 44.0693 | 39.6017 | 101.9251 | 116.02 | 44.1035 | 35.2433 | 97.6151
KINO4 M4 | 400 | 124.3571 | 44.0693 | 39.6017 | 101.9251 | 116.02 | 44.1035 | 35.2433 | 97.6151
KINO4 R1/2 | 400 | 124.3571 | 44.0693 | 39.6017 | 101.9251 | 116.02 | 44.1035 | 35.2433 | 97.6151
KINO4 R3/4 | 400 | 124.3571 | 44.0693 | 39.6017 | 101.9251 | 116.02 | 44.1035 | 35.2433 | 97.6151
KIRK2 MC1 | 275 | 53.7436 | 19.5355 | 12.1183 | 39.7456 | 54.8481 | 21.1003 | 13.0215 | 42.8619
KIRK2 MC2 | 275 | 53.7436 | 19.5355 | 12.1183 | 39.7456 | 54.8481 | 21.1003 | 13.0215 | 42.8619
KIRK2 MC3 | 275 | 53.7436 | 19.5355 | 12.1183 | 39.7456 | 54.8481 | 21.1003 | 13.0215 | 42.8619
KIRK2 MC4 | 275 | 53.7436 | 19.5355 | 12.1183 | 39.7456 | 54.8481 | 21.1003 | 13.0215 | 42.8619
KIRK2A | 275 | 53.1612 | 18.8434 | 6.422 | 33.0706 | 50.9435 | 19.9309 | 8.022 | 36.2085
KITW2 MC1 | 275 | 61.8253 | 22.577 | 12.0684 | 43.9972 | 60.671 | 23.7109 | 10.5891 | 44.1213
KITW2 MC2 | 275 | 61.8253 | 22.577 | 12.0684 | 43.9972 | 60.671 | 23.7109 | 10.5891 | 44.1213
KITW2 MC3 | 275 | 61.8253 | 22.577 | 12.0684 | 43.9972 | 60.671 | 23.7109 | 10.5891 | 44.1213
KITW2 MC4 | 275 | 61.8253 | 22.577 | 12.0684 | 43.9972 | 60.671 | 23.7109 | 10.5891 | 44.1213
KNAR2 MC1 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
KNAR2 MC1 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
KNAR2 MC1 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
KNAR2 MC1 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
KNAR2 MC2 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
KNAR2 MC2 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
KNAR2 MC2 | 275 | 29.1137 | 11.7372 | 2.4446 | 19.0435 | 26.8479 | 11.0993 | 3.5295 | 19.2262
LACK2 M1 | 275 | 63.0641 | 21.8992 | 17.4151 | 48.3853 | 67.08 | 24.7384 | 19.024 | 54.0094
LACK2 M2 | 275 | 63.0641 | 21.8992 | 17.4151 | 48.3853 | 67.08 | 24.7384 | 19.024 | 54.0094
LACK2 R1 | 275 | 63.0641 | 21.8992 | 17.4151 | 48.3853 | 67.08 | 24.7384 | 19.024 | 54.0094
LACK2 R2 | 275 | 63.0641 | 21.8992 | 17.4151 | 48.3853 | 67.08 | 24.7384 | 19.024 | 54.0094
LACK4 M1 | 400 | 73.7366 | 27.1712 | 22.9709 | 61.3969 | 66.9809 | 25.5987 | 21.0606 | 57.2626
LACK4 M2 | 400 | 73.7366 | 27.1712 | 22.9709 | 61.3969 | 66.9809 | 25.5987 | 21.0606 | 57.2626
LACK4 R1 | 400 | 73.7366 | 27.1712 | 22.9709 | 61.3969 | 66.9809 | 25.5987 | 21.0606 | 57.2626
LACK4 R2 | 400 | 73.7366 | 27.1712 | 22.9709 | 61.3969 | 66.9809 | 25.5987 | 21.0606 | 57.2626
LAGA4 M1 | 400 | 42.9352 | 15.7708 | 8.8875 | 31.1908 | 44.1438 | 16.9352 | 10.0511 | 34.0011
LAGA4 M2 | 400 | 42.9352 | 15.7708 | 8.8875 | 31.1908 | 44.1438 | 16.9352 | 10.0511 | 34.0011
LAGA4 R1 | 400 | 42.9352 | 15.7708 | 8.8875 | 31.1908 | 44.1438 | 16.9352 | 10.0511 | 34.0011
LAGA4 R2 | 400 | 42.9352 | 15.7708 | 8.8875 | 31.1908 | 44.1438 | 16.9352 | 10.0511 | 34.0011
LALE2 MC1 | 275 | 61.3537 | 21.8226 | 17.5072 | 48.369 | 67.3863 | 26.0135 | 16.714 | 53.5027
LALE2 MC2 | 275 | 61.3537 | 21.8226 | 17.5072 | 48.369 | 67.3863 | 26.0135 | 16.714 | 53.5027
LALE2 MC3 | 275 | 61.3537 | 21.8226 | 17.5072 | 48.369 | 67.3863 | 26.0135 | 16.714 | 53.5027
LALE2 MC4 | 275 | 61.3537 | 21.8226 | 17.5072 | 48.369 | 67.3863 | 26.0135 | 16.714 | 53.5027
LAND4 MC1 | 400 | 34.4696 | 12.8787 | 6.5009 | 24.7142 | 33.7409 | 13.194 | 6.1131 | 24.7723
LAND4 MC2 | 400 | 34.4696 | 12.8787 | 6.5009 | 24.7142 | 33.7409 | 13.194 | 6.1131 | 24.7723
LEGA4 M1 | 400 | 89.0705 | 32.1464 | 19.7562 | 65.218 | 68.7293 | 27.1285 | 12.4832 | 50.8486
LEGA4 M2 | 400 | 89.0705 | 32.1464 | 19.7562 | 65.218 | 68.7293 | 27.1285 | 12.4832 | 50.8486
LEGA4 R1 | 400 | 89.0705 | 32.1464 | 19.7562 | 65.218 | 68.7293 | 27.1285 | 12.4832 | 50.8486
LEGA4 R2 | 400 | 89.0705 | 32.1464 | 19.7562 | 65.218 | 68.7293 | 27.1285 | 12.4832 | 50.8486
LEIS1 M1 | 132 | 65.0586 | 23.0136 | 21.2272 | 53.7734 | 75.0466 | 27.2611 | 26.3968 | 64.9498
LEIS1 M2 | 132 | 65.0586 | 23.0136 | 21.2272 | 53.7734 | 75.0466 | 27.2611 | 26.3968 | 64.9498
LEIS1 R1 | 132 | 65.0586 | 23.0136 | 21.2272 | 53.7734 | 75.0466 | 27.2611 | 26.3968 | 64.9498
LEIS1 R2 | 132 | 65.0586 | 23.0136 | 21.2272 | 53.7734 | 75.0466 | 27.2611 | 26.3968 | 64.9498
LISD2 M1 | 275 | 69.0087 | 24.4973 | 17.002 | 51.6464 | 72.9457 | 27.7115 | 16.3728 | 55.5629
LISD2 M2 | 275 | 69.0087 | 24.4973 | 17.002 | 51.6464 | 72.9457 | 27.7115 | 16.3728 | 55.5629
LISD2 R1 | 275 | 69.0087 | 24.4973 | 17.002 | 51.6464 | 72.9457 | 27.7115 | 16.3728 | 55.5629
LISD2 R2 | 275 | 69.0087 | 24.4973 | 17.002 | 51.6464 | 72.9457 | 27.7115 | 16.3728 | 55.5629
LITB4 Term500 | 400 | 77.1099 | 27.6559 | 8.3089 | 47.4202 | 70.0184 | 26.4961 | 11.3248 | 48.7959
LITT4 M1 | 400 | 126.9483 | 43.4314 | 28.8118 | 90.233 | 115.6051 | 44.1963 | 23.7027 | 86.2057
LITT4 M2 | 400 | 126.9483 | 43.4314 | 28.8118 | 90.233 | 115.6051 | 44.1963 | 23.7027 | 86.2057
LITT4 M3 | 400 | 126.9483 | 43.4314 | 28.8118 | 90.233 | 115.6051 | 44.1963 | 23.7027 | 86.2057
LITT4 R1 | 400 | 126.9483 | 43.4314 | 28.8118 | 90.233 | 115.6051 | 44.1963 | 23.7027 | 86.2057
LITT4 R2 | 400 | 126.9483 | 43.4314 | 28.8118 | 90.233 | 115.6051 | 44.1963 | 23.7027 | 86.2057
LITT4 R3 | 400 | 126.9483 | 43.4314 | 28.8118 | 90.233 | 115.6051 | 44.1963 | 23.7027 | 86.2057
LOFI4A | 400 | 97.8632 | 33.4136 | 9.477 | 56.731 | 81.1503 | 31.4356 | 4.6053 | 49.0619
LOFI4A_KEMS | 400 | 97.8632 | 33.4136 | 9.477 | 56.731 | 81.1503 | 31.4356 | 4.6053 | 49.0619
LOFI4A_LITT | 400 | 97.8632 | 33.4136 | 9.477 | 56.731 | 81.1503 | 31.4356 | 4.6053 | 49.0619
LOFI4A_ROWD | 400 | 97.8632 | 33.4136 | 9.477 | 56.731 | 81.1503 | 31.4356 | 4.6053 | 49.0619
LOFI4B | 400 | 96.7352 | 33.1492 | 9.2819 | 56.1618 | 82.0632 | 31.8072 | 4.6255 | 49.6076
LOFI4B_KEMS | 400 | 96.7352 | 33.1492 | 9.2819 | 56.1618 | 82.0632 | 31.8072 | 4.6255 | 49.6076
LOFI4B_LITT | 400 | 96.7352 | 33.1492 | 9.2819 | 56.1618 | 82.0632 | 31.8072 | 4.6255 | 49.6076
LOFI4B_ROWD | 400 | 96.7352 | 33.1492 | 9.2819 | 56.1618 | 82.0632 | 31.8072 | 4.6255 | 49.6076
LOVE4 M1 | 400 | 95.7771 | 34.2682 | 18.6283 | 67.0908 | 83.2093 | 32.1809 | 15.8053 | 61.316
LOVE4 M2 | 400 | 95.7771 | 34.2682 | 18.6283 | 67.0908 | 83.2093 | 32.1809 | 15.8053 | 61.316
LOVE4 R1 | 400 | 95.7771 | 34.2682 | 18.6283 | 67.0908 | 83.2093 | 32.1809 | 15.8053 | 61.316
LOVE4 R2 | 400 | 95.7771 | 34.2682 | 18.6283 | 67.0908 | 83.2093 | 32.1809 | 15.8053 | 61.316
MACC2 MC1 | 275 | 56.3063 | 20.8116 | 13.7583 | 43.1904 | 52.9317 | 20.4296 | 11.8577 | 40.7495
MACC2 MC2 | 275 | 56.3063 | 20.8116 | 13.7583 | 43.1904 | 52.9317 | 20.4296 | 11.8577 | 40.7495
MACC4 MC1 | 400 | 81.185 | 30.588 | 22.9487 | 66.2067 | 61.7642 | 24.6899 | 15.1827 | 50.0995
MACC4 MC2 | 400 | 81.185 | 30.588 | 22.9487 | 66.2067 | 61.7642 | 24.6899 | 15.1827 | 50.0995
MACC4 MC3 | 400 | 81.185 | 30.588 | 22.9487 | 66.2067 | 61.7642 | 24.6899 | 15.1827 | 50.0995
MACC4 MC4 | 400 | 81.185 | 30.588 | 22.9487 | 66.2067 | 61.7642 | 24.6899 | 15.1827 | 50.0995
MAGA2 MC1 | 275 | 51.8795 | 19.1313 | 11.27 | 38.3258 | 45.2929 | 17.914 | 8.3255 | 33.6598
MAGA2 MC2 | 275 | 51.8795 | 19.1313 | 11.27 | 38.3258 | 45.2929 | 17.914 | 8.3255 | 33.6598
MANN4 M5 | 400 | 57.2805 | 20.9123 | 11.174 | 40.7485 | 52.7743 | 20.2331 | 11.4259 | 40.0399
MANN4 MC1 | 400 | 57.2805 | 20.9123 | 11.174 | 40.7485 | 52.7743 | 20.2331 | 11.4259 | 40.0399
MANN4 MC2 | 400 | 57.2805 | 20.9123 | 11.174 | 40.7485 | 52.7743 | 20.2331 | 11.4259 | 40.0399
MANN4 MC3 | 400 | 57.2805 | 20.9123 | 11.174 | 40.7485 | 52.7743 | 20.2331 | 11.4259 | 40.0399
MANN4 MC4 | 400 | 57.2805 | 20.9123 | 11.174 | 40.7485 | 52.7743 | 20.2331 | 11.4259 | 40.0399
MANN4 R5 | 400 | 57.2805 | 20.9123 | 11.174 | 40.7485 | 52.7743 | 20.2331 | 11.4259 | 40.0399
MAWO4 M | 400 | 63.6056 | 23.1332 | 12.4379 | 45.1532 | 56.8373 | 21.7426 | 12.4778 | 43.2265
MAWO4 R | 400 | 63.6056 | 23.1332 | 12.4379 | 45.1532 | 56.8373 | 21.7426 | 12.4778 | 43.2265
MEDW4 Term500 | 400 | 117.2863 | 40.5325 | 26.7884 | 84.1099 | 105.5803 | 39.8732 | 24.259 | 80.6482
MELK1 M1 | 132 | 41.909 | 14.656 | 14.8818 | 35.6085 | 51.9669 | 19.0918 | 17.434 | 44.4339
MELK1 M2 | 132 | 41.909 | 14.656 | 14.8818 | 35.6085 | 51.9669 | 19.0918 | 17.434 | 44.4339
MELK1 R1 | 132 | 41.909 | 14.656 | 14.8818 | 35.6085 | 51.9669 | 19.0918 | 17.434 | 44.4339
MELK1 R2 | 132 | 41.909 | 14.656 | 14.8818 | 35.6085 | 51.9669 | 19.0918 | 17.434 | 44.4339
MELK4 M1 | 400 | 107.2297 | 39.2438 | 20.8206 | 76.3198 | 88.5734 | 35.008 | 14.8155 | 64.3243
MELK4 M2 | 400 | 107.2297 | 39.2438 | 20.8206 | 76.3198 | 88.5734 | 35.008 | 14.8155 | 64.3243
MELK4 M3 | 400 | 107.2297 | 39.2438 | 20.8206 | 76.3198 | 88.5734 | 35.008 | 14.8155 | 64.3243
MELK4 R1 | 400 | 107.2297 | 39.2438 | 20.8206 | 76.3198 | 88.5734 | 35.008 | 14.8155 | 64.3243
MELK4 R2 | 400 | 107.2297 | 39.2438 | 20.8206 | 76.3198 | 88.5734 | 35.008 | 14.8155 | 64.3243
MELK4 R3 | 400 | 107.2297 | 39.2438 | 20.8206 | 76.3198 | 88.5734 | 35.008 | 14.8155 | 64.3243
MILH1 M1 | 132 | 60.151 | 23.846 | 9.3529 | 43.0762 | 64.1133 | 28.2899 | 9.5831 | 49.5911
MILH1 M2 | 132 | 60.151 | 23.846 | 9.3529 | 43.0762 | 64.1133 | 28.2899 | 9.5831 | 49.5911
MILH1 R1 | 132 | 60.1754 | 23.8778 | 9.2089 | 42.9772 | 63.8937 | 28.2865 | 9.2701 | 49.2733
MILH1 R2 | 132 | 60.1754 | 23.8778 | 9.2089 | 42.9772 | 63.8937 | 28.2865 | 9.2701 | 49.2733
MITY4 MC1 | 400 | 81.5175 | 31.0927 | 21.56 | 65.5317 | 61.606 | 24.915 | 14.3281 | 49.5632
MITY4 MC2 | 400 | 81.5175 | 31.0927 | 21.56 | 65.5317 | 61.606 | 24.915 | 14.3281 | 49.5632
MITY4 MC3 | 400 | 81.5175 | 31.0927 | 21.56 | 65.5317 | 61.606 | 24.915 | 14.3281 | 49.5632
MITY4 MC4 | 400 | 81.5175 | 31.0927 | 21.56 | 65.5317 | 61.606 | 24.915 | 14.3281 | 49.5632
MONF2 M1 | 275 | 65.6604 | 23.7732 | 17.7122 | 51.3326 | 66.7858 | 25.3869 | 16.3346 | 52.2371
MONF2 M2 | 275 | 65.6604 | 23.7732 | 17.7122 | 51.3326 | 66.7858 | 25.3869 | 16.3346 | 52.2371
MONF2 R1 | 275 | 56.7403 | 20.5911 | 18.1135 | 47.2336 | 59.7056 | 22.4348 | 17.4185 | 49.1462
MONF2 R2 | 275 | 56.7403 | 20.5911 | 18.1135 | 47.2336 | 59.7056 | 22.4348 | 17.4185 | 49.1462
MONF4 MC2 | 400 | 79.5611 | 28.8997 | 18.9724 | 59.8427 | 70.1215 | 26.8362 | 15.6715 | 53.6237
MONF4 MC3 | 400 | 79.5611 | 28.8997 | 18.9724 | 59.8427 | 70.1215 | 26.8362 | 15.6715 | 53.6237
NECH2 MC1 | 275 | 73.1913 | 26.3523 | 18.7259 | 55.9937 | 74.0808 | 28.508 | 16.206 | 56.5225
NECH2 MC2 | 275 | 73.1913 | 26.3523 | 18.7259 | 55.9937 | 74.0808 | 28.508 | 16.206 | 56.5225
NECH2 MC3 | 275 | 73.1913 | 26.3523 | 18.7259 | 55.9937 | 74.0808 | 28.508 | 16.206 | 56.5225
NECH2 MC4 | 275 | 73.1913 | 26.3523 | 18.7259 | 55.9937 | 74.0808 | 28.508 | 16.206 | 56.5225
NECT4 M1 | 400 | 74.9191 | 27.5331 | 17.7277 | 56.6653 | 54.4656 | 21.5761 | 10.8932 | 41.4065
NECT4 R1 | 400 | 74.9191 | 27.5331 | 17.7277 | 56.6653 | 54.4656 | 21.5761 | 10.8932 | 41.4065
NEEP2 M1 | 275 | 59.1795 | 21.8868 | 12.7661 | 43.7187 | 62.3998 | 24.8411 | 12.0431 | 47.1737
NEEP2 M2 | 275 | 59.1795 | 21.8868 | 12.7661 | 43.7187 | 62.3998 | 24.8411 | 12.0431 | 47.1737
NEEP2 R1/R2 | 275 | 59.1795 | 21.8868 | 12.7661 | 43.7187 | 62.3998 | 24.8411 | 12.0431 | 47.1737
NEWX2 M5 | 275 | 76.9881 | 26.6415 | 19.7217 | 57.3984 | 85.4669 | 33.2393 | 17.632 | 64.6394
NEWX2 M5 | 275 | 76.9881 | 26.6415 | 19.7217 | 57.3984 | 85.4669 | 33.2393 | 17.632 | 64.6394
NEWX2 M6 | 275 | 76.9881 | 26.6415 | 19.7217 | 57.3984 | 85.4669 | 33.2393 | 17.632 | 64.6394
NEWX2 R6 | 275 | 76.9881 | 26.6415 | 19.7217 | 57.3984 | 85.4669 | 33.2393 | 17.632 | 64.6394
NEWX21 R5 | 275 | 76.9881 | 26.6415 | 19.7217 | 57.3984 | 85.4669 | 33.2393 | 17.632 | 64.6394
NFLE4 M1 | 400 | 106.6976 | 37.18 | 23.3373 | 75.9178 | 86.0724 | 33.5835 | 15.303 | 62.7972
NFLE4 M2 | 400 | 106.6976 | 37.18 | 23.3373 | 75.9178 | 86.0724 | 33.5835 | 15.303 | 62.7972
NFLE4 R1 | 400 | 106.6976 | 37.18 | 23.3373 | 75.9178 | 86.0724 | 33.5835 | 15.303 | 62.7972
NFLE4 R2 | 400 | 106.6976 | 37.18 | 23.3373 | 75.9178 | 86.0724 | 33.5835 | 15.303 | 62.7972
NHYD2A | 275 | 45.7927 | 17.4069 | 2.6034 | 27.2204 | 39.388 | 18.6049 | 0.47343 | 26.7847
NHYD2B | 275 | 47.422 | 18.0037 | 2.3111 | 27.7722 | 40.6811 | 18.6995 | 1.0721 | 27.5171
NHYD2C | 275 | 47.422 | 18.0037 | 2.3111 | 27.7722 | 40.6811 | 18.6995 | 1.0721 | 27.5171
NINF4 M1 | 400 | 66.7251 | 24.1721 | 14.6754 | 48.86 | 57.1816 | 22.0141 | 12.6215 | 43.7542
NINF4 M2 | 400 | 66.7251 | 24.1721 | 14.6754 | 48.86 | 57.1816 | 22.0141 | 12.6215 | 43.7542
NINF4 R1 | 400 | 66.7251 | 24.1721 | 14.6754 | 48.86 | 57.1816 | 22.0141 | 12.6215 | 43.7542
NINF4 R2 | 400 | 66.7251 | 24.1721 | 14.6754 | 48.86 | 57.1816 | 22.0141 | 12.6215 | 43.7542
NORL2A | 275 | 51.7251 | 19.076 | 3.9534 | 30.931 | 51.2333 | 21.09 | 2.3006 | 32.1263
NORL2B | 275 | 50.912 | 18.8513 | 3.4405 | 30.1002 | 50.3827 | 21.0271 | 2.0306 | 31.7675
NORM4 M1 | 400 | 70.2139 | 25.9331 | 15.642 | 52.3169 | 53.1142 | 20.9295 | 11.3003 | 40.8991
NORM4 M2 | 400 | 70.2139 | 25.9331 | 15.642 | 52.3169 | 53.1142 | 20.9295 | 11.3003 | 40.8991
NORM4 R1 | 400 | 70.2139 | 25.9331 | 15.642 | 52.3169 | 53.1142 | 20.9295 | 11.3003 | 40.8991
NORM4 R2 | 400 | 70.2139 | 25.9331 | 15.642 | 52.3169 | 53.1142 | 20.9295 | 11.3003 | 40.8991
NORT2 M1 | 275 | 85.1753 | 29.8947 | 22.9567 | 65.2342 | 85.0843 | 32.155 | 19.4219 | 64.8959
NORT2 M2 | 275 | 85.1753 | 29.8947 | 22.9567 | 65.2342 | 85.0843 | 32.155 | 19.4219 | 64.8959
NORT2 R1 | 275 | 85.1753 | 29.8947 | 22.9567 | 65.2342 | 85.0843 | 32.155 | 19.4219 | 64.8959
NORT2 R2 | 275 | 85.1753 | 29.8947 | 22.9567 | 65.2342 | 85.0843 | 32.155 | 19.4219 | 64.8959
NORT4 M1 | 400 | 91.5168 | 33.2918 | 28.7654 | 75.8471 | 76.7279 | 29.6731 | 21.8561 | 63.8201
NORT4 M2 | 400 | 91.5168 | 33.2918 | 28.7654 | 75.8471 | 76.7279 | 29.6731 | 21.8561 | 63.8201
NORT4 R1 | 400 | 91.5168 | 33.2918 | 28.7654 | 75.8471 | 76.7279 | 29.6731 | 21.8561 | 63.8201
NORT4 R2 | 400 | 91.5168 | 33.2918 | 28.7654 | 75.8471 | 76.7279 | 29.6731 | 21.8561 | 63.8201
NURS4 MC1 | 400 | 60.5473 | 21.8196 | 7.8943 | 38.7519 | 55.2566 | 21.0276 | 8.2346 | 37.9721
NURS4 MC2 | 400 | 60.5473 | 21.8196 | 7.8943 | 38.7519 | 55.2566 | 21.0276 | 8.2346 | 37.9721
NURS4A | 400 | 52.4015 | 19.2716 | 10.6039 | 37.8581 | 48.3383 | 18.4938 | 10.6798 | 36.834
OCKH1 M1 | 132 | 24.8904 | 8.9032 | 8.5519 | 21.143 | 33.534 | 12.282 | 11.2745 | 28.6439
OCKH1 M2 | 132 | 24.8904 | 8.9032 | 8.5519 | 21.143 | 33.534 | 12.282 | 11.2745 | 28.6439
OCKH1 R1 | 132 | 24.8904 | 8.9032 | 8.5519 | 21.143 | 33.534 | 12.282 | 11.2745 | 28.6439
OCKH1 R2 | 132 | 24.8904 | 8.9032 | 8.5519 | 21.143 | 33.534 | 12.282 | 11.2745 | 28.6439
OCKH2 MC1 | 275 | 55.4808 | 20.3785 | 10.7102 | 39.5298 | 57.4964 | 22.467 | 10.8643 | 42.6375
OCKH2 MC2 | 275 | 55.4808 | 20.3785 | 10.7102 | 39.5298 | 57.4964 | 22.467 | 10.8643 | 42.6375
OCKH2 MC3 | 275 | 55.4808 | 20.3785 | 10.7102 | 39.5298 | 57.4964 | 22.467 | 10.8643 | 42.6375
OCKH2 MC4 | 275 | 55.4808 | 20.3785 | 10.7102 | 39.5298 | 57.4964 | 22.467 | 10.8643 | 42.6375
OCKH2A | 275 | 48.8059 | 17.6103 | 4.3442 | 29.2489 | 49.0177 | 18.9483 | 4.7598 | 31.5567
OFFE2 MC1 | 275 | 69.7247 | 25.3606 | 13.2865 | 49.1518 | 59.1874 | 23.6488 | 8.2005 | 41.6451
OFFE2 MC2 | 275 | 69.7247 | 25.3606 | 13.2865 | 49.1518 | 59.1874 | 23.6488 | 8.2005 | 41.6451
OLDB2 MC1 | 275 | 53.0992 | 19.5998 | 10.7141 | 38.4324 | 54.7622 | 21.2171 | 10.8962 | 40.9017
OLDB2 MC2 | 275 | 53.0992 | 19.5998 | 10.7141 | 38.4324 | 54.7622 | 21.2171 | 10.8962 | 40.9017
OSBA4 MC1 | 400 | 55.9455 | 20.6922 | 12.7027 | 41.9658 | 50.219 | 19.1976 | 12.1163 | 39.2658
OSBA4 MC2 | 400 | 55.9455 | 20.6922 | 12.7027 | 41.9658 | 50.219 | 19.1976 | 12.1163 | 39.2658
OSBA4 MC3/4 | 400 | 55.0573 | 20.3754 | 12.7069 | 41.5222 | 44.3069 | 17.1594 | 9.4806 | 33.7477
PADI1 M1 | 132 | 29.7757 | 10.4551 | 10.4789 | 25.2647 | 36.9985 | 13.5503 | 12.7092 | 31.8722
PADI1 M2 | 132 | 29.7757 | 10.4551 | 10.4789 | 25.2647 | 36.9985 | 13.5503 | 12.7092 | 31.8722
PADI1 R1 | 132 | 29.7757 | 10.4551 | 10.4789 | 25.2647 | 36.9985 | 13.5503 | 12.7092 | 31.8722
PADI1 R2 | 132 | 29.7757 | 10.4551 | 10.4789 | 25.2647 | 36.9985 | 13.5503 | 12.7092 | 31.8722
PADI4 MC1 | 400 | 74.9485 | 27.4979 | 15.9208 | 54.8087 | 56.8999 | 22.4845 | 9.8369 | 41.6348
PADI4 MC2 | 400 | 74.9485 | 27.4979 | 15.9208 | 54.8087 | 56.8999 | 22.4845 | 9.8369 | 41.6348
PADI4 MC3 | 400 | 74.9485 | 27.4979 | 15.9208 | 54.8087 | 56.8999 | 22.4845 | 9.8369 | 41.6348
PADI4 MC4 | 400 | 74.9485 | 27.4979 | 15.9208 | 54.8087 | 56.8999 | 22.4845 | 9.8369 | 41.6348
PELH4 M1 | 400 | 139.2199 | 49.2352 | 33.3502 | 102.9793 | 113.6956 | 43.95 | 22.1746 | 84.3293
PELH4 M2 | 400 | 139.2199 | 49.2352 | 33.3502 | 102.9793 | 113.6956 | 43.95 | 22.1746 | 84.3293
PELH4 R1 | 400 | 139.2199 | 49.2352 | 33.3502 | 102.9793 | 113.6956 | 43.95 | 22.1746 | 84.3293
PELH4 R2 | 400 | 139.2199 | 49.2352 | 33.3502 | 102.9793 | 113.6956 | 43.95 | 22.1746 | 84.3293
PEMB4 M1 | 400 | 60.8497 | 21.412 | 18.2697 | 48.5508 | 65.1625 | 23.9168 | 20.6723 | 54.4957
PEMB4 M2 | 400 | 60.8497 | 21.412 | 18.2697 | 48.5508 | 65.1625 | 23.9168 | 20.6723 | 54.4957
PEMB4 M3 | 400 | 60.8497 | 21.412 | 18.2697 | 48.5508 | 65.1625 | 23.9168 | 20.6723 | 54.4957
PEMB4 M4 | 400 | 60.8497 | 21.412 | 18.2697 | 48.5508 | 65.1625 | 23.9168 | 20.6723 | 54.4957
PEMB4 R1/2 | 400 | 60.8497 | 21.412 | 18.2697 | 48.5508 | 65.1625 | 23.9168 | 20.6723 | 54.4957
PEMB4 R3/4 | 400 | 60.8497 | 21.412 | 18.2697 | 48.5508 | 65.1625 | 23.9168 | 20.6723 | 54.4957
PENN2 MC1 | 275 | 66.2083 | 24.1363 | 14.0256 | 48.1594 | 69.5314 | 26.6724 | 14.807 | 52.5274
PENN2 MC2 | 275 | 66.2083 | 24.1363 | 14.0256 | 48.1594 | 69.5314 | 26.6724 | 14.807 | 52.5274
PENN2 MC3 | 275 | 66.2083 | 24.1363 | 14.0256 | 48.1594 | 69.5314 | 26.6724 | 14.807 | 52.5274
PENN2 MC4 | 275 | 66.2083 | 24.1363 | 14.0256 | 48.1594 | 69.5314 | 26.6724 | 14.807 | 52.5274
PENT4 M1 | 400 | 74.7327 | 26.1277 | 20.634 | 57.5842 | 75.7943 | 28.1845 | 20.4011 | 60.2601
PENT4 M2 | 400 | 74.7327 | 26.1277 | 20.634 | 57.5842 | 75.7943 | 28.1845 | 20.4011 | 60.2601
PENT4 R1 | 400 | 74.7327 | 26.1277 | 20.634 | 57.5842 | 75.7943 | 28.1845 | 20.4011 | 60.2601
PENT4 R2 | 400 | 74.7327 | 26.1277 | 20.634 | 57.5842 | 75.7943 | 28.1845 | 20.4011 | 60.2601
PEWO2A | 275 | 66.62 | 23.9234 | 20.2348 | 54.0676 | 68.7314 | 25.6759 | 19.5883 | 55.8995
PEWO2B | 275 | 67.9242 | 24.7294 | 24.6005 | 59.5731 | 69.9315 | 26.2452 | 24.5929 | 61.7092
PEWO4 M1 | 400 | 101.5997 | 36.932 | 32.4229 | 84.6527 | 91.9976 | 35.5652 | 27.1403 | 77.4371
PEWO4 M2 | 400 | 101.5997 | 36.932 | 32.4229 | 84.6527 | 91.9976 | 35.5652 | 27.1403 | 77.4371
PEWO4 M3 | 400 | 101.5997 | 36.932 | 32.4229 | 84.6527 | 91.9976 | 35.5652 | 27.1403 | 77.4371
PEWO4 M4 | 400 | 101.5997 | 36.932 | 32.4229 | 84.6527 | 91.9976 | 35.5652 | 27.1403 | 77.4371
PEWO4 R1/2 | 400 | 101.5997 | 36.932 | 32.4229 | 84.6527 | 91.9976 | 35.5652 | 27.1403 | 77.4371
PEWO4 R3/4 | 400 | 101.5997 | 36.932 | 32.4229 | 84.6527 | 91.9976 | 35.5652 | 27.1403 | 77.4371
PITS2 MC1 | 275 | 60.8177 | 22.179 | 8.5821 | 39.9479 | 65.7787 | 25.829 | 7.6605 | 44.1882
PITS2 MC2 | 275 | 60.8177 | 22.179 | 8.5821 | 39.9479 | 65.7787 | 25.829 | 7.6605 | 44.1882
PITS2 MC3 | 275 | 60.8177 | 22.179 | 8.5821 | 39.9479 | 65.7787 | 25.829 | 7.6605 | 44.1882
PITS2 MC4 | 275 | 60.8177 | 22.179 | 8.5821 | 39.9479 | 65.7787 | 25.829 | 7.6605 | 44.1882
POPP2 MC1 | 275 | 27.3325 | 10.9325 | 2.8437 | 18.3047 | 23.1242 | 9.5396 | 3.0801 | 16.571
POPP2 MC2 | 275 | 27.3325 | 10.9325 | 2.8437 | 18.3047 | 23.1242 | 9.5396 | 3.0801 | 16.571
PUDM4 MC1 | 400 | 102.4509 | 35.2195 | 24.1711 | 73.979 | 106.0206 | 41.7657 | 20.0986 | 79.1642
PUDM4 MC2 | 400 | 102.4509 | 35.2195 | 24.1711 | 73.979 | 106.0206 | 41.7657 | 20.0986 | 79.1642
PYLE2 MC1 | 275 | 54.1153 | 20.075 | 10.8848 | 39.2751 | 47.7486 | 18.89 | 8.9026 | 35.6171
PYLE2 MC2 | 275 | 54.1696 | 20.0939 | 10.8982 | 39.3153 | 47.7935 | 18.9061 | 8.9187 | 35.6559
QUER4A | 400 | 84.7223 | 29.6775 | 12.5051 | 54.4754 | 73.0765 | 28.2151 | 5.6953 | 45.5974
QUER4A_HEYS | 400 | 84.7223 | 29.6775 | 12.5051 | 54.4754 | 73.0765 | 28.2151 | 5.6953 | 45.5974
QUER4A_HUTT | 400 | 84.7223 | 29.6775 | 12.5051 | 54.4754 | 73.0765 | 28.2151 | 5.6953 | 45.5974
QUER4A_PEWO | 400 | 84.7223 | 29.6775 | 12.5051 | 54.4754 | 73.0765 | 28.2151 | 5.6953 | 45.5974
QUER4B | 400 | 85.5964 | 29.9365 | 12.8128 | 55.1494 | 75.1578 | 28.8973 | 6.3497 | 47.2167
QUER4B_HEYS | 400 | 85.5964 | 29.9365 | 12.8128 | 55.1494 | 75.1578 | 28.8973 | 6.3497 | 47.2167
QUER4B_HUTT | 400 | 85.5964 | 29.9365 | 12.8128 | 55.1494 | 75.1578 | 28.8973 | 6.3497 | 47.2167
QUER4B_PEWO | 400 | 85.5964 | 29.9365 | 12.8128 | 55.1494 | 75.1578 | 28.8973 | 6.3497 | 47.2167
RAIN2 MC1 | 275 | 77.531 | 27.3084 | 19.9407 | 58.5606 | 76.1294 | 28.7984 | 16.643 | 57.3702
RAIN2 MC2 | 275 | 77.531 | 27.3084 | 19.9407 | 58.5606 | 76.1294 | 28.7984 | 16.643 | 57.3702
RAIN2 MC3 | 275 | 77.531 | 27.3084 | 19.9407 | 58.5606 | 76.1294 | 28.7984 | 16.643 | 57.3702
RAIN2 MC4 | 275 | 77.531 | 27.3084 | 19.9407 | 58.5606 | 76.1294 | 28.7984 | 16.643 | 57.3702
RASS4 M1 | 400 | 53.2305 | 19.9139 | 16.2642 | 44.4267 | 43.2399 | 16.96 | 11.6785 | 35.6636
RASS4 M2 | 400 | 53.2305 | 19.9139 | 16.2642 | 44.4267 | 43.2399 | 16.96 | 11.6785 | 35.6636
RATS1 M1 | 132 | 43.8915 | 15.4832 | 14.3137 | 36.2103 | 49.4172 | 18.3593 | 16.5817 | 42.5457
RATS1 M2 | 132 | 43.8915 | 15.4832 | 14.3137 | 36.2103 | 49.4172 | 18.3593 | 16.5817 | 42.5457
RATS1 R1 | 132 | 40.5969 | 14.4319 | 13.1601 | 33.5699 | 45.3652 | 16.9803 | 14.0888 | 38.1025
RATS1 R2 | 132 | 40.5969 | 14.4319 | 13.1601 | 33.5699 | 45.3652 | 16.9803 | 14.0888 | 38.1025
RATS2A | 275 | 43.8635 | 15.8532 | 10.5386 | 32.9584 | 46.6951 | 16.8813 | 20.6784 | 44.5521
RATS4 M1 | 400 | 139.5659 | 49.604 | 31.2118 | 101.3625 | 137.2826 | 52.067 | 34.389 | 108.0229
RATS4 M2 | 400 | 139.5659 | 49.604 | 31.2118 | 101.3625 | 137.2826 | 52.067 | 34.389 | 108.0229
RATS4 M3 | 400 | 139.5659 | 49.604 | 31.2118 | 101.3625 | 137.2826 | 52.067 | 34.389 | 108.0229
RATS4 M4 | 400 | 139.5659 | 49.604 | 31.2118 | 101.3625 | 137.2826 | 52.067 | 34.389 | 108.0229
RATS4 R1/2 | 400 | 139.5659 | 49.604 | 31.2118 | 101.3625 | 137.2826 | 52.067 | 34.389 | 108.0229
RATS4 R3/4 | 400 | 139.5659 | 49.604 | 31.2118 | 101.3625 | 137.2826 | 52.067 | 34.389 | 108.0229
RAYL4 M1 | 400 | 103.9172 | 37.886 | 31.3218 | 84.9008 | 80.8013 | 31.7569 | 21.6168 | 66.5278
RAYL4 M2 | 400 | 103.9172 | 37.886 | 31.3218 | 84.9008 | 80.8013 | 31.7569 | 21.6168 | 66.5278
RAYL4 R1 | 400 | 103.9172 | 37.886 | 31.3218 | 84.9008 | 80.8013 | 31.7569 | 21.6168 | 66.5278
RAYL4 R2 | 400 | 103.9172 | 37.886 | 31.3218 | 84.9008 | 80.8013 | 31.7569 | 21.6168 | 66.5278
REBR2 MC1 | 275 | 66.7424 | 24.5018 | 21.9643 | 56.6151 | 63.8439 | 24.9607 | 17.7246 | 53.0243
REBR2 MC2 | 275 | 64.5626 | 23.7043 | 21.4498 | 54.9728 | 63.3587 | 24.9029 | 17.2776 | 52.4956
REBR2 MC3 | 275 | 64.5626 | 23.7043 | 21.4498 | 54.9728 | 63.3587 | 24.9029 | 17.2776 | 52.4956
REBR2 MC4 | 275 | 66.7424 | 24.5018 | 21.9643 | 56.6151 | 63.8439 | 24.9607 | 17.7246 | 53.0243
RHIG4 M1 | 400 | 54.3674 | 19.8853 | 12.7764 | 40.8984 | 47.9017 | 18.5068 | 9.6374 | 35.81
RHIG4 R1 | 400 | 54.3674 | 19.8853 | 12.7764 | 40.8984 | 47.9017 | 18.5068 | 9.6374 | 35.81
ROCH2 MC1 | 275 | 71.0707 | 25.7807 | 9.696 | 46.1555 | 67.7245 | 26.2634 | 9.3387 | 46.4808
ROCH2 MC2 | 275 | 71.0707 | 25.7807 | 9.696 | 46.1555 | 67.7245 | 26.2634 | 9.3387 | 46.4808
ROCH2 MC3 | 275 | 71.0707 | 25.7807 | 9.696 | 46.1555 | 67.7245 | 26.2634 | 9.3387 | 46.4808
ROCH2 MC4 | 275 | 71.0707 | 25.7807 | 9.696 | 46.1555 | 67.7245 | 26.2634 | 9.3387 | 46.4808
ROCK1A | 132 | 46.4478 | 15.9977 | 16.5868 | 39.211 | 48.4855 | 17.5084 | 16.1826 | 40.9433
ROCK4 Term900 | 400 | 85.1131 | 30.0679 | 21.8194 | 64.3419 | 80.9268 | 30.239 | 21.5151 | 64.2794
RUGE4 M1 | 400 | 65.4102 | 24.6687 | 10.3314 | 45.2183 | 51.0945 | 20.6367 | 7.1036 | 36.2883
RUGE4 M2 | 400 | 65.4102 | 24.6687 | 10.3314 | 45.2183 | 51.0945 | 20.6367 | 7.1036 | 36.2883
RUGE4 R1 | 400 | 65.4102 | 24.6687 | 10.3314 | 45.2183 | 51.0945 | 20.6367 | 7.1036 | 36.2883
RUGE4 R2 | 400 | 65.4102 | 24.6687 | 10.3314 | 45.2183 | 51.0945 | 20.6367 | 7.1036 | 36.2883
RYEH4 M1 | 400 | 80.0367 | 28.6794 | 20.8948 | 61.4536 | 80.6192 | 30.1735 | 21.9217 | 64.5935
RYEH4 R1 | 400 | 80.0367 | 28.6794 | 20.8948 | 61.4536 | 80.6192 | 30.1735 | 21.9217 | 64.5935
RYHA42 MC1 | 400 | 43.7112 | 16.4384 | 9.4434 | 32.6908 | 28.6053 | 11.4169 | 4.0849 | 20.2309
RYHA4B_LOAD2 | 400 | 44.0604 | 16.5806 | 9.5124 | 32.9609 | 30.2033 | 12.0573 | 4.2809 | 21.3325
SAEN2 MC1 | 275 | 72.6052 | 25.7998 | 21.269 | 57.7554 | 76.6141 | 28.3442 | 23.054 | 63.1388
SAEN2 MC2 | 275 | 72.6052 | 25.7998 | 21.269 | 57.7554 | 76.6141 | 28.3442 | 23.054 | 63.1388
SAES2 M | 275 | 73.158 | 25.964 | 21.5521 | 58.2707 | 77.4936 | 28.6165 | 23.7971 | 64.2669
SAES2 R | 275 | 73.158 | 25.964 | 21.5521 | 58.2707 | 77.4936 | 28.6165 | 23.7971 | 64.2669
SALH2 MC1 | 275 | 77.351 | 27.494 | 18.3677 | 57.2501 | 75.3257 | 28.6704 | 15.4686 | 56.0146
SALH2 MC2 | 275 | 77.351 | 27.494 | 18.3677 | 57.2501 | 75.3257 | 28.6704 | 15.4686 | 56.0146
SEAB4 M1 | 400 | 62.4939 | 22.9368 | 20.4371 | 52.8747 | 64.3291 | 24.2615 | 21.6749 | 55.9859
SEAB4 M2 | 400 | 62.4939 | 22.9368 | 20.4371 | 52.8747 | 64.3291 | 24.2615 | 21.6749 | 55.9859
SEAB4 R1 | 400 | 62.4939 | 22.9368 | 20.4371 | 52.8747 | 64.3291 | 24.2615 | 21.6749 | 55.9859
SEAB4 R2 | 400 | 62.4939 | 22.9368 | 20.4371 | 52.8747 | 64.3291 | 24.2615 | 21.6749 | 55.9859
SELL4 M1 | 400 | 83.8105 | 30.3934 | 17.5609 | 60.5437 | 71.2373 | 27.2991 | 16.6381 | 55.2449
SELL4 M2 | 400 | 83.8105 | 30.3934 | 17.5609 | 60.5437 | 71.2373 | 27.2991 | 16.6381 | 55.2449
SELL4 R1 | 400 | 83.8105 | 30.3934 | 17.5609 | 60.5437 | 71.2373 | 27.2991 | 16.6381 | 55.2449
SELL4 R2 | 400 | 83.8105 | 30.3934 | 17.5609 | 60.5437 | 71.2373 | 27.2991 | 16.6381 | 55.2449
SELL4A | 400 | 83.7238 | 29.6562 | 7.9652 | 49.9054 | 71.1662 | 27.096 | 9.2072 | 47.5267
SELL4B | 400 | 83.7236 | 29.6562 | 7.9652 | 49.9053 | 71.1661 | 27.096 | 9.2071 | 47.5266
SELW4 M3 | 400 | 83.6256 | 30.3314 | 17.5113 | 60.4064 | 70.8347 | 27.1642 | 16.4157 | 54.8317
SELW4 M4 | 400 | 83.6256 | 30.3314 | 17.5113 | 60.4064 | 70.8347 | 27.1642 | 16.4157 | 54.8317
SELW4 R3 | 400 | 83.6256 | 30.3314 | 17.5113 | 60.4064 | 70.8347 | 27.1642 | 16.4157 | 54.8317
SELW4 R4 | 400 | 83.6256 | 30.3314 | 17.5113 | 60.4064 | 70.8347 | 27.1642 | 16.4157 | 54.8317
SETW4A | 400 | 83.6252 | 29.6239 | 7.9527 | 49.8472 | 71.1082 | 27.0772 | 9.1769 | 47.4698
SETW4B | 400 | 83.6251 | 29.6238 | 7.9527 | 49.8471 | 71.1081 | 27.0771 | 9.1769 | 47.4697
SHBA4 M1 | 400 | 80.133 | 28.9083 | 28.4845 | 69.367 | 79.0789 | 29.6377 | 27.4541 | 69.3681
SHBA4 M2 | 400 | 80.133 | 28.9083 | 28.4845 | 69.367 | 79.0789 | 29.6377 | 27.4541 | 69.3681
SHBA4 R1 | 400 | 80.133 | 28.9083 | 28.4845 | 69.367 | 79.0789 | 29.6377 | 27.4541 | 69.3681
SHBA4 R2 | 400 | 80.133 | 28.9083 | 28.4845 | 69.367 | 79.0789 | 29.6377 | 27.4541 | 69.3681
SHEC2 MC1 | 275 | 53.7548 | 20.1165 | 10.3904 | 38.8395 | 54.6205 | 22.5157 | 7.5058 | 39.3478
SHEC2 MC2 | 275 | 53.7548 | 20.1165 | 10.3904 | 38.8395 | 54.6205 | 22.5157 | 7.5058 | 39.3478
SHRE4B | 400 | 56.0461 | 21.0085 | 10.5116 | 40.2221 | 44.3576 | 17.6651 | 7.2614 | 32.2437
SING4 MC1 | 400 | 95.4351 | 33.6288 | 20.8915 | 68.4498 | 77.3437 | 30.1847 | 13.1103 | 55.7979
SING4 MC2 | 400 | 95.4351 | 33.6288 | 20.8915 | 68.4498 | 77.3437 | 30.1847 | 13.1103 | 55.7979
SIZE4 M1 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 M2 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 M3 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 M4 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 R1 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 R2 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 R3 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SIZE4 R4 | 400 | 70.9041 | 25.3946 | 18.2143 | 54.1276 | 76.1837 | 28.2439 | 21.877 | 61.8199
SJOW2 MC1 | 275 | 86.3002 | 30.6207 | 22.9575 | 66.2617 | 94.6124 | 36.2067 | 26.3072 | 77.5112
SJOW2 MC2 | 275 | 86.3002 | 30.6207 | 22.9575 | 66.2617 | 94.6124 | 36.2067 | 26.3072 | 77.5112
SJOW2 MC3 | 275 | 86.3002 | 30.6207 | 22.9575 | 66.2617 | 94.6124 | 36.2067 | 26.3072 | 77.5112
SJOW2 MC4 | 275 | 86.3002 | 30.6207 | 22.9575 | 66.2617 | 94.6124 | 36.2067 | 26.3072 | 77.5112
SJOW4 M1 | 400 | 120.6193 | 40.5233 | 29.7355 | 87.0441 | 139.6064 | 51.2121 | 34.2897 | 106.7146
SJOW4 M2 | 400 | 120.6193 | 40.5233 | 29.7355 | 87.0441 | 139.6064 | 51.2121 | 34.2897 | 106.7146
SJOW4 M3 | 400 | 120.6193 | 40.5233 | 29.7355 | 87.0441 | 139.6064 | 51.2121 | 34.2897 | 106.7146
SJOW4 M4 | 400 | 120.6193 | 40.5233 | 29.7355 | 87.0441 | 139.6064 | 51.2121 | 34.2897 | 106.7146
SJOW4 R1/2 | 400 | 120.6193 | 40.5233 | 29.7355 | 87.0441 | 139.6064 | 51.2121 | 34.2897 | 106.7146
SJOW4 R3/4 | 400 | 120.6193 | 40.5233 | 29.7355 | 87.0441 | 139.6064 | 51.2121 | 34.2897 | 106.7146
SKLG2 MC1 | 275 | 58.4554 | 21.6089 | 17.748 | 48.3076 | 56.2659 | 21.9244 | 15.9049 | 46.9107
SKLG2 MC2 | 275 | 58.4554 | 21.6089 | 17.748 | 48.3076 | 56.2659 | 21.9244 | 15.9049 | 46.9107
SKLG2 MC3 | 275 | 58.4554 | 21.6089 | 17.748 | 48.3076 | 56.2659 | 21.9244 | 15.9049 | 46.9107
SKLG2 MC4 | 275 | 58.4554 | 21.6089 | 17.748 | 48.3076 | 56.2659 | 21.9244 | 15.9049 | 46.9107
SMAN2 MC1 | 275 | 76.3592 | 28.4192 | 23.2504 | 63.4412 | 75.1215 | 29.3348 | 21.0147 | 62.5004
SMAN2 MC2 | 275 | 76.3592 | 28.4192 | 23.2504 | 63.4412 | 75.1215 | 29.3348 | 21.0147 | 62.5004
SMAN2 MC3 | 275 | 76.3592 | 28.4192 | 23.2504 | 63.4412 | 75.1215 | 29.3348 | 21.0147 | 62.5004
SMAN2 MC4 | 275 | 76.3592 | 28.4192 | 23.2504 | 63.4412 | 75.1215 | 29.3348 | 21.0147 | 62.5004
SPEN4 MC3 | 400 | 62.4719 | 22.7972 | 13.3843 | 45.6244 | 49.1698 | 19.1377 | 9.1654 | 36.2302
SPEN4 MC4 | 400 | 62.4719 | 22.7972 | 13.3843 | 45.6244 | 49.1698 | 19.1377 | 9.1654 | 36.2302
SPEN41 MC1 | 400 | 62.4479 | 22.7888 | 13.3798 | 45.6081 | 49.8172 | 19.3656 | 9.4194 | 36.8065
SPEN41 MC2 | 400 | 62.4479 | 22.7888 | 13.3798 | 45.6081 | 49.8172 | 19.3656 | 9.4194 | 36.8065
SPLN4 M1 | 400 | 81.3514 | 29.5052 | 21.5904 | 63.3171 | 67.6093 | 25.8508 | 17.6124 | 54.1709
SPLN4 R1 | 400 | 81.3514 | 29.5052 | 21.5904 | 63.3171 | 67.6093 | 25.8508 | 17.6124 | 54.1709
SSHI2 MC1 | 275 | 66.961 | 24.5232 | 11.8989 | 46.5799 | 59.0815 | 23.4353 | 9.4971 | 42.6396
SSHI2 MC2 | 275 | 66.961 | 24.5232 | 11.8989 | 46.5799 | 59.0815 | 23.4353 | 9.4971 | 42.6396
STAL2 M1 | 275 | 82.5671 | 30.351 | 16.1403 | 59.0631 | 76.7956 | 29.9717 | 14.6886 | 57.075
STAL2 M2 | 275 | 82.5671 | 30.351 | 16.1403 | 59.0631 | 76.7956 | 29.9717 | 14.6886 | 57.075
STAL2 R1 | 275 | 82.5671 | 30.351 | 16.1403 | 59.0631 | 76.7956 | 29.9717 | 14.6886 | 57.075
STAL2 R2 | 275 | 82.5671 | 30.351 | 16.1403 | 59.0631 | 76.7956 | 29.9717 | 14.6886 | 57.075
STAL4 MC1 | 400 | 36.4519 | 13.4271 | 9.4785 | 28.4673 | 32.623 | 12.6078 | 8.1349 | 25.965
STAL4 MC2 | 400 | 51.7245 | 19.5863 | 9.9362 | 37.6354 | 39.5512 | 15.7377 | 6.4306 | 28.6871
STAY4 M1 | 400 | 113.3329 | 41.1796 | 27.1291 | 85.3658 | 107.516 | 40.8347 | 28.1136 | 85.8627
STAY4 M2 | 400 | 113.3329 | 41.1796 | 27.1291 | 85.3658 | 107.516 | 40.8347 | 28.1136 | 85.8627
STAY4 R1 | 400 | 113.3329 | 41.1796 | 27.1291 | 85.3658 | 107.516 | 40.8347 | 28.1136 | 85.8627
STAY4 R2 | 400 | 113.3329 | 41.1796 | 27.1291 | 85.3658 | 107.516 | 40.8347 | 28.1136 | 85.8627
STAY4A | 400 | 76.5771 | 28.0634 | 21.2763 | 60.964 | 69.5594 | 26.3219 | 20.2507 | 57.4755
STEN1 M1 | 132 | 55.2591 | 19.482 | 19.2903 | 46.842 | 67.9157 | 25.0527 | 22.9522 | 58.3821
STEN1 M2 | 132 | 55.2591 | 19.482 | 19.2903 | 46.842 | 67.9157 | 25.0527 | 22.9522 | 58.3821
STEN1 R1 | 132 | 55.2591 | 19.482 | 19.2903 | 46.842 | 67.9157 | 25.0527 | 22.9522 | 58.3821
STEN1 R2 | 132 | 55.2591 | 19.482 | 19.2903 | 46.842 | 67.9157 | 25.0527 | 22.9522 | 58.3821
STES1 M1 | 132 | 55.5067 | 19.0469 | 15.2703 | 42.2068 | 67.8959 | 24.7731 | 17.5307 | 52.5651
STES1 M2 | 132 | 55.5067 | 19.0469 | 15.2703 | 42.2068 | 67.8959 | 24.7731 | 17.5307 | 52.5651
STES1 R1 | 132 | 55.5067 | 19.0469 | 15.2703 | 42.2068 | 67.8959 | 24.7731 | 17.5307 | 52.5651
STES1 R2 | 132 | 55.5067 | 19.0469 | 15.2703 | 42.2068 | 67.8959 | 24.7731 | 17.5307 | 52.5651
STEW2 M1 | 275 | 83.4793 | 30.8137 | 25.2459 | 68.8231 | 79.6431 | 30.6555 | 23.904 | 67.2574
STEW2 M2 | 275 | 83.4793 | 30.8137 | 25.2459 | 68.8231 | 79.6431 | 30.6555 | 23.904 | 67.2574
STEW2 R1 | 275 | 83.4793 | 30.8137 | 25.2459 | 68.8231 | 79.6431 | 30.6555 | 23.904 | 67.2574
STEW2 R2 | 275 | 83.4793 | 30.8137 | 25.2459 | 68.8231 | 79.6431 | 30.6555 | 23.904 | 67.2574
STEW4 M1 | 400 | 81.2808 | 29.7427 | 24.7289 | 66.7914 | 62.888 | 24.45 | 18.0822 | 52.6597
STEW4 M2 | 400 | 81.2808 | 29.7427 | 24.7289 | 66.7914 | 62.888 | 24.45 | 18.0822 | 52.6597
STEW4 R1 | 400 | 81.2808 | 29.7427 | 24.7289 | 66.7914 | 62.888 | 24.45 | 18.0822 | 52.6597
STEW4 R2a | 400 | 81.2808 | 29.7427 | 24.7289 | 66.7914 | 62.888 | 24.45 | 18.0822 | 52.6597
STOB4 M1 | 400 | 65.6031 | 24.7614 | 12.0038 | 47.0217 | 53.5347 | 21.4644 | 8.2238 | 38.5791
STOB4 R1 | 400 | 65.6031 | 24.7614 | 12.0038 | 47.0217 | 53.5347 | 21.4644 | 8.2238 | 38.5791
STSB4 MC1 | 400 | 57.353 | 21.2767 | 12.5238 | 42.6135 | 45.7044 | 17.9887 | 7.7653 | 33.2051
STSB4 MC2 | 400 | 57.353 | 21.2767 | 12.5238 | 42.6135 | 45.7044 | 17.9887 | 7.7653 | 33.2051
STSB4A | 400 | 53.2075 | 19.5484 | 5.7863 | 33.4319 | 41.5375 | 16.2302 | 3.123 | 26.076
SUND4 M1 | 400 | 111.9001 | 40.5517 | 24.1557 | 81.5045 | 93.7313 | 36.3576 | 18.3011 | 69.7184
SUND4 M2 | 400 | 88.8513 | 32.6266 | 18.8272 | 64.9682 | 75.1 | 29.0968 | 15.0489 | 56.198
SUND4 R1 | 400 | 111.9001 | 40.5517 | 24.1557 | 81.5045 | 93.7313 | 36.3576 | 18.3011 | 69.7184
SUND4 R2 | 400 | 88.8513 | 32.6266 | 18.8272 | 64.9682 | 75.1 | 29.0968 | 15.0489 | 56.198
SUTB4A | 400 | 89.2383 | 32.6517 | 20.5894 | 66.7658 | 77.328 | 29.8177 | 18.1738 | 60.3425
SWAN2 MC3 | 275 | 25.8026 | 9.3654 | 8.4677 | 21.7124 | 28.2524 | 10.4608 | 8.8191 | 23.6128
SWAN2 MC4 | 275 | 25.8026 | 9.3654 | 8.4677 | 21.7124 | 28.2524 | 10.4608 | 8.8191 | 23.6128
SWAN4 M1 | 400 | 38.4388 | 14.1936 | 9.1337 | 29.2065 | 33.9485 | 12.9569 | 8.0476 | 26.3715
SWAN4 M2 | 400 | 38.4388 | 14.1936 | 9.1337 | 29.2065 | 33.9485 | 12.9569 | 8.0476 | 26.3715
SWAN4 M3 | 400 | 60.6716 | 21.8656 | 15.4195 | 46.3422 | 59.2637 | 22.4553 | 14.2372 | 45.9938
SWAN4 M4 | 400 | 60.6716 | 21.8656 | 15.4195 | 46.3422 | 59.2637 | 22.4553 | 14.2372 | 45.9938
SWAN4 R3 | 400 | 60.6716 | 21.8656 | 15.4195 | 46.3422 | 59.2637 | 22.4553 | 14.2372 | 45.9938
SWAN4 R4 | 400 | 60.6716 | 21.8656 | 15.4195 | 46.3422 | 59.2637 | 22.4553 | 14.2372 | 45.9938
TAUN4 M1 | 400 | 49.9512 | 18.5613 | 9.6385 | 35.8882 | 43.4657 | 17.218 | 6.7832 | 31.1332
TAUN4 M2 | 400 | 50.7229 | 18.8064 | 9.7841 | 36.3804 | 45.0079 | 17.7763 | 7.314 | 32.4536
TEMP2 MC1 | 275 | 59.6934 | 22.0939 | 12.2299 | 43.4753 | 62.2117 | 24.6799 | 10.9571 | 45.8598
TEMP2 MC2 | 275 | 59.6934 | 22.0939 | 12.2299 | 43.4753 | 62.2117 | 24.6799 | 10.9571 | 45.8598
TEMP2 MC3 | 275 | 59.9856 | 22.1816 | 12.3711 | 43.7406 | 63.1145 | 25.0179 | 11.1857 | 46.5664
THOM2 M1 | 275 | 67.111 | 24.5451 | 19.0363 | 53.7483 | 69.3784 | 26.2485 | 18.7874 | 55.9083
THOM2 R1 | 275 | 67.111 | 24.5451 | 19.0363 | 53.7483 | 69.3784 | 26.2485 | 18.7874 | 55.9083
THOM4 MC1 | 400 | 92.4887 | 33.1597 | 22.7888 | 69.6837 | 83.4572 | 31.9565 | 17.7415 | 62.9349
THOM4 MC2 | 400 | 92.4887 | 33.1597 | 22.7888 | 69.6837 | 83.4572 | 31.9565 | 17.7415 | 62.9349
THOM4 MC3 | 400 | 92.4887 | 33.1597 | 22.7888 | 69.6837 | 83.4572 | 31.9565 | 17.7415 | 62.9349
THOM4 MC4 | 400 | 92.4887 | 33.1597 | 22.7888 | 69.6837 | 83.4572 | 31.9565 | 17.7415 | 62.9349
THOM4 R2(2) | 400 | 88.8985 | 32.4812 | 19.1699 | 65.1052 | 77.7867 | 30.043 | 15.5832 | 58.0704
THOM4 R2(3) | 400 | 88.8985 | 32.4812 | 19.1699 | 65.1052 | 77.7867 | 30.043 | 15.5832 | 58.0704
THOM42 M5 | 400 | 88.8985 | 32.4812 | 19.1699 | 65.1052 | 77.7867 | 30.043 | 15.5832 | 58.0704
THTO4 M1 | 400 | 94.6151 | 34.1874 | 23.9554 | 72.3036 | 75.4923 | 29.2605 | 14.2825 | 55.663
THTO4 M2 | 400 | 68.287 | 25.0567 | 16.451 | 51.8865 | 55.5771 | 21.5018 | 11.0108 | 41.4189
THTO4 M3 | 400 | 68.287 | 25.0567 | 16.451 | 51.8865 | 55.5771 | 21.5018 | 11.0108 | 41.4189
THTO4 M4 | 400 | 94.6151 | 34.1874 | 23.9554 | 72.3036 | 75.4923 | 29.2605 | 14.2825 | 55.663
THTO4 R1/2 | 400 | 67.6208 | 24.7396 | 16.0049 | 50.992 | 57.6926 | 22.1721 | 11.9062 | 43.2624
THTO4 R3/4 | 400 | 67.6208 | 24.7396 | 16.0049 | 50.992 | 57.6926 | 22.1721 | 11.9062 | 43.2624
THUR2 MC1 | 275 | 64.514 | 24.3515 | 10.5036 | 44.9418 | 65.6325 | 26.0227 | 10.9251 | 47.7267
THUR2 MC2 | 275 | 64.514 | 24.3515 | 10.5036 | 44.9418 | 65.6325 | 26.0227 | 10.9251 | 47.7267
THUR2 MC3 | 275 | 64.514 | 24.3515 | 10.5036 | 44.9418 | 65.6325 | 26.0227 | 10.9251 | 47.7267
THUR2 MC4 | 275 | 64.514 | 24.3515 | 10.5036 | 44.9418 | 65.6325 | 26.0227 | 10.9251 | 47.7267
TILB2 M1 | 275 | 71.8795 | 25.7338 | 21.2768 | 57.6698 | 75.5322 | 28.2351 | 21.3618 | 61.2922
TILB2 M2 | 275 | 71.8795 | 25.7338 | 21.2768 | 57.6698 | 75.5322 | 28.2351 | 21.3618 | 61.2922
TILB2 R1 | 275 | 71.8795 | 25.7338 | 21.2768 | 57.6698 | 75.5322 | 28.2351 | 21.3618 | 61.2922
TILB2 R2 | 275 | 71.8795 | 25.7338 | 21.2768 | 57.6698 | 75.5322 | 28.2351 | 21.3618 | 61.2922
TILB4 M2 | 400 | 139.9836 | 49.3981 | 44.0809 | 113.9404 | 125.3263 | 48.1679 | 35.3457 | 103.4653
TILB4 M3 | 400 | 139.9836 | 49.3981 | 44.0809 | 113.9404 | 125.3263 | 48.1679 | 35.3457 | 103.4653
TILB4 R2 | 400 | 139.9836 | 49.3981 | 44.0809 | 113.9404 | 125.3263 | 48.1679 | 35.3457 | 103.4653
TILB4 R3 | 400 | 139.9836 | 49.3981 | 44.0809 | 113.9404 | 125.3263 | 48.1679 | 35.3457 | 103.4653
TINP2 M1 | 275 | 58.0275 | 21.2298 | 6.8355 | 36.859 | 56.5532 | 22.0212 | 5.5091 | 36.6518
TINP2 M2 | 275 | 58.1955 | 21.2404 | 6.8484 | 36.8868 | 57.4823 | 22.358 | 5.6029 | 37.222
TODP2 MC1 | 275 | 63.5969 | 22.2866 | 15.8297 | 47.3478 | 58.2792 | 22.3 | 11.6733 | 43.2103
TODP2 MC2 | 275 | 63.5969 | 22.2866 | 15.8297 | 47.3478 | 58.2792 | 22.3 | 11.6733 | 43.2103
TOTE2A | 275 | 75.9077 | 27.1977 | 20.0887 | 58.5521 | 78.8242 | 30.0867 | 17.6341 | 60.1831
TOTE2B | 275 | 77.713 | 27.8391 | 20.2791 | 59.6495 | 77.3639 | 29.4983 | 17.2368 | 58.9537
TOTT2 MC1 | 275 | 75.8709 | 27.9854 | 23.7022 | 63.2795 | 76.2014 | 31.2543 | 19.9271 | 64.1274
TOTT2 MC2A | 275 | 77.2786 | 28.4885 | 24.1676 | 64.4563 | 73.9807 | 30.8775 | 18.101 | 61.7684
TOTT2 MC2B | 275 | 77.713 | 27.8391 | 20.2791 | 59.6495 | 77.3639 | 29.4983 | 17.2368 | 58.9537
TOTT2 MC3 | 275 | 77.2786 | 28.4885 | 24.1676 | 64.4563 | 73.9807 | 30.8775 | 18.101 | 61.7684
TOTT2 MC4A | 275 | 75.8709 | 27.9854 | 23.7022 | 63.2795 | 76.2014 | 31.2543 | 19.9271 | 64.1274
TOTT2 MC4B | 275 | 75.9077 | 27.1977 | 20.0887 | 58.5521 | 78.8242 | 30.0867 | 17.6341 | 60.1831
TOTT2 MC5 | 275 | 77.713 | 27.8391 | 20.2791 | 59.6495 | 77.3639 | 29.4983 | 17.2368 | 58.9537
TOTT2 MC6 | 275 | 77.713 | 27.8391 | 20.2791 | 59.6495 | 77.3639 | 29.4983 | 17.2368 | 58.9537
TOTT2 MC7 | 275 | 75.9077 | 27.1977 | 20.0887 | 58.5521 | 78.8242 | 30.0867 | 17.6341 | 60.1831
TOTT2 MC8 | 275 | 75.9077 | 27.1977 | 20.0887 | 58.5521 | 78.8242 | 30.0867 | 17.6341 | 60.1831
TRAW2 M1 | 275 | 44.7494 | 16.0667 | 13.7481 | 36.4698 | 46.9747 | 17.5673 | 12.7031 | 37.547
TRAW2 M2 | 275 | 44.7494 | 16.0667 | 13.7481 | 36.4698 | 46.9747 | 17.5673 | 12.7031 | 37.547
TRAW2 R1 | 275 | 44.7494 | 16.0667 | 13.7481 | 36.4698 | 46.9747 | 17.5673 | 12.7031 | 37.547
TRAW2 R2 | 275 | 44.7494 | 16.0667 | 13.7481 | 36.4698 | 46.9747 | 17.5673 | 12.7031 | 37.547
TRAW4 MC1 | 400 | 58.5052 | 21.7666 | 17.8711 | 48.6538 | 47.2245 | 18.6792 | 12.443 | 38.8595
TRAW4 MC2 | 400 | 58.5052 | 21.7666 | 17.8711 | 48.6538 | 47.2245 | 18.6792 | 12.443 | 38.8595
TRAW4 MC3 | 400 | 58.5052 | 21.7666 | 17.8711 | 48.6538 | 47.2245 | 18.6792 | 12.443 | 38.8595
TRAW4 MC4 | 400 | 58.5052 | 21.7666 | 17.8711 | 48.6538 | 47.2245 | 18.6792 | 12.443 | 38.8595
TREM2 MC1 | 275 | 46.4619 | 17.0316 | 2.6668 | 26.7531 | 41.101 | 16.3194 | 2.3434 | 25.4225
TREM2 MC2 | 275 | 46.4619 | 17.0316 | 2.6668 | 26.7531 | 41.101 | 16.3194 | 2.3434 | 25.4225
TREU4A | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.1049 | 28.5124 | 4.6181 | 44.9407
TREU4A_DEES1 | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.1049 | 28.5124 | 4.6181 | 44.9407
TREU4A_LEGA1 | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.1049 | 28.5124 | 4.6181 | 44.9407
TREU4A_TRAW1 | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.1049 | 28.5124 | 4.6181 | 44.9407
TREU4B | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.3283 | 28.5977 | 4.6322 | 45.0755
TREU4B_DEES2 | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.3283 | 28.5977 | 4.6322 | 45.0755
TREU4B_LEGA2 | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.3283 | 28.5977 | 4.6322 | 45.0755
TREU4B_TRAW2 | 400 | 88.633 | 31.2501 | 9.5253 | 53.7196 | 73.3283 | 28.5977 | 4.6322 | 45.0755
TYNE2 MC1 | 275 | 62.7855 | 23.1326 | 10.9587 | 43.6732 | 55.1462 | 21.7692 | 9.3797 | 40.166
TYNE2 MC2 | 275 | 62.7855 | 23.1326 | 10.9587 | 43.6732 | 55.1462 | 21.7692 | 9.3797 | 40.166
TYNE2A | 275 | 62.0533 | 22.5204 | 3.7621 | 35.6107 | 51.8453 | 20.5792 | 2.7781 | 31.8814
UPPB2 MC1 | 275 | 39.2792 | 14.6475 | 9.7904 | 30.5051 | 38.4824 | 14.9048 | 8.5375 | 29.616
UPPB2 MC2 | 275 | 41.7611 | 15.5388 | 10.1558 | 32.131 | 40.2625 | 15.5684 | 8.987 | 31.0041
UPPB2 MC3 | 275 | 41.7611 | 15.5388 | 10.1558 | 32.131 | 40.2625 | 15.5684 | 8.987 | 31.0041
UPPB2 MC4 | 275 | 39.2792 | 14.6475 | 9.7904 | 30.5051 | 38.4824 | 14.9048 | 8.5375 | 29.616
USKM2 M1 | 275 | 77.056 | 27.3244 | 19.7356 | 58.3781 | 86.9961 | 32.5278 | 22.931 | 68.9322
USKM2 M2 | 275 | 77.056 | 27.3244 | 19.7356 | 58.3781 | 86.9961 | 32.5278 | 22.931 | 68.9322
USKM2 R1 | 275 | 77.056 | 27.3244 | 19.7356 | 58.3781 | 86.9961 | 32.5278 | 22.931 | 68.9322
USKM2 R2 | 275 | 77.056 | 27.3244 | 19.7356 | 58.3781 | 86.9961 | 32.5278 | 22.931 | 68.9322
USKM2A | 275 | 74.6724 | 25.8568 | 11.3101 | 47.8772 | 82.3047 | 30.6806 | 11.9539 | 55.3428
WALH4 MC1 | 400 | 60.4778 | 22.5462 | 11.6313 | 43.5163 | 51.4862 | 20.1631 | 10.5376 | 39.0525
WALH4 MC2 | 400 | 60.4778 | 22.5462 | 11.6313 | 43.5163 | 51.4862 | 20.1631 | 10.5376 | 39.0525
WALH4 MC3 | 400 | 60.4778 | 22.5462 | 11.6313 | 43.5163 | 51.4862 | 20.1631 | 10.5376 | 39.0525
WALH4 MC4 | 400 | 60.4778 | 22.5462 | 11.6313 | 43.5163 | 51.4862 | 20.1631 | 10.5376 | 39.0525
WALP R4 | 132 | 69.0934 | 24.3655 | 20.556 | 55.014 | 83.7592 | 32.0414 | 22.6628 | 67.9762
WALP1 M4 | 132 | 69.0934 | 24.3655 | 20.556 | 55.014 | 83.7592 | 32.0414 | 22.6628 | 67.9762
WALP4 M1 | 400 | 107.4099 | 38.655 | 27.3966 | 82.0631 | 94.3538 | 35.9455 | 24.3822 | 75.2167
WALP4 M2 | 400 | 107.4099 | 38.655 | 27.3966 | 82.0631 | 94.3538 | 35.9455 | 24.3822 | 75.2167
WALP4 R1 | 400 | 107.4099 | 38.655 | 27.3966 | 82.0631 | 94.3538 | 35.9455 | 24.3822 | 75.2167
WALP4 R2 | 400 | 107.4099 | 38.655 | 27.3966 | 82.0631 | 94.3538 | 35.9455 | 24.3822 | 75.2167
WALPM3 | 132 | 69.0934 | 24.3655 | 20.556 | 55.014 | 83.7592 | 32.0414 | 22.6628 | 67.9762
WALPR3 | 132 | 69.0934 | 24.3655 | 20.556 | 55.014 | 83.7592 | 32.0414 | 22.6628 | 67.9762
WALX2 M1 | 275 | 91.5531 | 32.2478 | 19.1149 | 64.7201 | 91.2189 | 34.3654 | 17.6495 | 66.2495
WALX2 M2 | 275 | 92.9289 | 32.7008 | 19.4494 | 65.6953 | 96.6179 | 36.327 | 18.8362 | 70.2103
WALX2 R1 | 275 | 91.5531 | 32.2478 | 19.1149 | 64.7201 | 91.2189 | 34.3654 | 17.6495 | 66.2495
WALX2 R2 | 275 | 92.9289 | 32.7008 | 19.4494 | 65.6953 | 96.6179 | 36.327 | 18.8362 | 70.2103
WALX4A | 400 | 74.3381 | 26.1805 | 11.7187 | 48.7435 | 73.4623 | 27.4162 | 11.4808 | 50.2532
WALX4B | 400 | 69.7869 | 24.8272 | 10.2644 | 45.3754 | 64.6317 | 24.2987 | 9.6878 | 44.0514
WARL2 MC1 | 275 | 65.4865 | 23.8449 | 15.5464 | 49.2682 | 60.8157 | 23.6504 | 11.5513 | 44.998
WARL2 MC2 | 275 | 65.4865 | 23.8449 | 15.5464 | 49.2682 | 60.8157 | 23.6504 | 11.5513 | 44.998
WARL2 MC3 | 275 | 65.4865 | 23.8449 | 15.5464 | 49.2682 | 60.8157 | 23.6504 | 11.5513 | 44.998
WARL2 MC4 | 275 | 65.4865 | 23.8449 | 15.5464 | 49.2682 | 60.8157 | 23.6504 | 11.5513 | 44.998
WASF2A | 275 | 55.7223 | 20.0923 | 5.7167 | 34.1315 | 48.3992 | 18.8382 | 3.2828 | 29.9241
WASF2B | 275 | 60.8306 | 21.7466 | 6.1965 | 36.9509 | 55.0642 | 21.444 | 3.4726 | 33.7991
WBOL2 MC1 | 275 | 75.5235 | 27.2641 | 14.2796 | 52.8368 | 65.2202 | 25.7753 | 10.6107 | 47.0624
WBOL2 MC2 | 275 | 75.5235 | 27.2641 | 14.2796 | 52.8368 | 65.2202 | 25.7753 | 10.6107 | 47.0624
WBOL2 MC3 | 275 | 75.5235 | 27.2641 | 14.2796 | 52.8368 | 65.2202 | 25.7753 | 10.6107 | 47.0624
WBOL2 MC4 | 275 | 75.5235 | 27.2641 | 14.2796 | 52.8368 | 65.2202 | 25.7753 | 10.6107 | 47.0624
WBUR1 M1 | 132 | 21.354 | 7.5828 | 6.7636 | 17.4874 | 24.875 | 9.2076 | 8.0755 | 21.097
WBUR1 M2 | 132 | 21.354 | 7.5828 | 6.7636 | 17.4874 | 24.875 | 9.2076 | 8.0755 | 21.097
WBUR1 R1 | 132 | 21.354 | 7.5828 | 6.7636 | 17.4874 | 24.875 | 9.2076 | 8.0755 | 21.097
WBUR1 R2 | 132 | 21.1322 | 7.5234 | 6.6595 | 17.2992 | 24.7144 | 9.1478 | 7.9848 | 20.9217
WBUR4 M1 | 400 | 109.9569 | 39.174 | 31.8559 | 87.2562 | 103.3044 | 38.572 | 30.1887 | 84.7377
WBUR4 M2 | 400 | 109.9569 | 39.174 | 31.8559 | 87.2562 | 103.3044 | 38.572 | 30.1887 | 84.7377
WBUR4 M3 | 400 | 109.9569 | 39.174 | 31.8559 | 87.2562 | 103.3044 | 38.572 | 30.1887 | 84.7377
WBUR4 M4 | 400 | 109.9569 | 39.174 | 31.8559 | 87.2562 | 103.3044 | 38.572 | 30.1887 | 84.7377
WBUR4 R1/2 | 400 | 106.3109 | 38.7712 | 26.3214 | 81.1522 | 86.9937 | 33.4562 | 21.1182 | 68.4324
WBUR4 R3/4 | 400 | 106.3109 | 38.7712 | 26.3214 | 81.1522 | 86.9937 | 33.4562 | 21.1182 | 68.4324
WHAM4 M1 | 400 | 124.8875 | 43.7822 | 39.3893 | 101.3067 | 138.7718 | 52.7199 | 39.9385 | 114.4957
WHAM4 M2 | 400 | 124.8875 | 43.7822 | 39.3893 | 101.3067 | 138.7718 | 52.7199 | 39.9385 | 114.4957
WHAM4 R1 | 400 | 124.8875 | 43.7822 | 39.3893 | 101.3067 | 138.7718 | 52.7199 | 39.9385 | 114.4957
WHAM4 R2 | 400 | 124.8875 | 43.7822 | 39.3893 | 101.3067 | 138.7718 | 52.7199 | 39.9385 | 114.4957
WHAM4A | 400 | 100.1334 | 33.2433 | 13.5502 | 60.5634 | 103.1453 | 39.7347 | 15.7601 | 71.9535
WHAM4B | 400 | 100.2101 | 33.265 | 13.5528 | 60.5965 | 103.2469 | 39.7743 | 15.7621 | 72.0115
WHGA2 MC1 | 275 | 70.3146 | 25.6613 | 15.0144 | 51.3049 | 66.201 | 25.8855 | 12.0113 | 48.6189
WHGA2 MC2 | 275 | 70.3146 | 25.6613 | 15.0144 | 51.3049 | 66.201 | 25.8855 | 12.0113 | 48.6189
WHGA2 MC3 | 275 | 70.3146 | 25.6613 | 15.0144 | 51.3049 | 66.201 | 25.8855 | 12.0113 | 48.6189
WHGA2 MC4 | 275 | 70.3146 | 25.6613 | 15.0144 | 51.3049 | 66.201 | 25.8855 | 12.0113 | 48.6189
WHSO2 M1 | 275 | 67.3452 | 24.3063 | 15.023 | 49.3974 | 72.5144 | 27.6474 | 15.6482 | 54.7476
WHSO2 M2 | 275 | 67.3452 | 24.3063 | 15.023 | 49.3974 | 72.5144 | 27.6474 | 15.6482 | 54.7476
WHSO2 R1 | 275 | 73.8125 | 26.3699 | 18.9323 | 56.225 | 80.6333 | 30.4024 | 19.9972 | 62.9926
WHSO2 R2 | 275 | 73.8125 | 26.3699 | 18.9323 | 56.225 | 80.6333 | 30.4024 | 19.9972 | 62.9926
WIBA2 MC1 | 275 | 59.6919 | 22.0941 | 12.223 | 43.4688 | 63.4285 | 25.3943 | 10.3155 | 46.2285
WIBA2 MC1 | 275 | 59.6919 | 22.0941 | 12.223 | 43.4688 | 63.4285 | 25.3943 | 10.3155 | 46.2285
WIBA2 MC2 | 275 | 59.6919 | 22.0941 | 12.223 | 43.4688 | 63.4285 | 25.3943 | 10.3155 | 46.2285
WIBA2 MC2 | 275 | 59.6919 | 22.0941 | 12.223 | 43.4688 | 63.4285 | 25.3943 | 10.3155 | 46.2285
WILE4 M1 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 M1 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 M2 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 M2 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 R1 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 R1 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 R2 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILE4 R2 | 400 | 108.7144 | 40.5242 | 29.9673 | 87.2773 | 93.4393 | 37.0746 | 24.0447 | 76.476
WILL1 M2 | 132 | 50.1749 | 17.5776 | 15.74 | 40.5985 | 57.5102 | 21.7705 | 18.1528 | 48.941
WILL1 R1 | 132 | 35.1973 | 13.0435 | 10.7454 | 29.1917 | 39.0424 | 15.0539 | 12.2632 | 33.5527
WILL1 R2 | 132 | 50.1749 | 17.5776 | 15.74 | 40.5985 | 57.5102 | 21.7705 | 18.1528 | 48.941
WILL2 M2 | 275 | 24.1077 | 8.6256 | 8.9713 | 21.1698 | 25.763 | 9.4033 | 9.3186 | 22.6168
WILL2 M2 | 275 | 24.1077 | 8.6256 | 8.9713 | 21.1698 | 25.763 | 9.4033 | 9.3186 | 22.6168
WILL2 R2 | 275 | 24.1077 | 8.6256 | 8.9713 | 21.1698 | 25.763 | 9.4033 | 9.3186 | 22.6168
WILL2 R2 | 275 | 24.1077 | 8.6256 | 8.9713 | 21.1698 | 25.763 | 9.4033 | 9.3186 | 22.6168
WILT2A | 275 | 54.4047 | 19.3395 | 9.9264 | 37.2766 | 56.7549 | 21.0592 | 9.1217 | 38.9039
WILT2A | 275 | 54.4047 | 19.3395 | 9.9264 | 37.2766 | 56.7549 | 21.0592 | 9.1217 | 38.9039
WILT2B | 275 | 54.4063 | 19.34 | 9.9263 | 37.2772 | 56.757 | 21.0599 | 9.1215 | 38.9048
WILT2B | 275 | 54.4063 | 19.34 | 9.9263 | 37.2772 | 56.757 | 21.0599 | 9.1215 | 38.9048
WILT2C | 275 | 54.7427 | 19.4448 | 10.0925 | 37.5916 | 57.6852 | 21.3442 | 9.8024 | 39.9876
WILT2C | 275 | 54.7427 | 19.4448 | 10.0925 | 37.5916 | 57.6852 | 21.3442 | 9.8024 | 39.9876
WILT2D | 275 | 54.7415 | 19.4446 | 10.092 | 37.5908 | 57.6811 | 21.3429 | 9.8006 | 39.984
WILT2D | 275 | 54.7415 | 19.4446 | 10.092 | 37.5908 | 57.6811 | 21.3429 | 9.8006 | 39.984
WIMB2 MC1 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC1 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC2 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC2 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC3 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC3 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC4 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2 MC4 | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2A | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB2A | 275 | 84.0658 | 28.9196 | 21.7279 | 62.6263 | 94.5416 | 35.7495 | 23.649 | 74.2064
WIMB4 MB2 | 400 | 97.2266 | 33.3597 | 24.2318 | 71.4096 | 111.3426 | 42.2609 | 21.7344 | 81.5003
WIMB4 MB2 | 400 | 97.2266 | 33.3597 | 24.2318 | 71.4096 | 111.3426 | 42.2609 | 21.7344 | 81.5003
WIMB4 RB2 | 400 | 97.2266 | 33.3597 | 24.2318 | 71.4096 | 111.3426 | 42.2609 | 21.7344 | 81.5003
WIMB4 RB2 | 400 | 97.2266 | 33.3597 | 24.2318 | 71.4096 | 111.3426 | 42.2609 | 21.7344 | 81.5003
WISD2 M1 | 275 | 70.2202 | 24.3432 | 22.8888 | 57.3153 | 81.8548 | 30.1599 | 25.6407 | 68.2932
WISD2 M2 | 275 | 70.2202 | 24.3432 | 22.8888 | 57.3153 | 81.8548 | 30.1599 | 25.6407 | 68.2932
WISD2 R1 | 275 | 70.2202 | 24.3432 | 22.8888 | 57.3153 | 81.8548 | 30.1599 | 25.6407 | 68.2932
WISD2 R2 | 275 | 70.2202 | 24.3432 | 22.8888 | 57.3153 | 81.8548 | 30.1599 | 25.6407 | 68.2932
WISD2A | 275 | 59.7984 | 20.7489 | 12.6337 | 41.9771 | 65.4934 | 25.0066 | 14.0621 | 49.4268
WISD2B | 275 | 59.7984 | 20.7489 | 12.6337 | 41.9771 | 65.4934 | 25.0066 | 14.0621 | 49.4268
WISD6 M1 | 66 | 51.3753 | 17.3998 | 17.3643 | 41.9713 | 33.8623 | 12.7025 | 10.8814 | 28.8454
WISD6 M2 | 66 | 51.3753 | 17.3998 | 17.3643 | 41.9713 | 33.8623 | 12.7025 | 10.8814 | 28.8454
WISD6 R1 | 66 | 51.3753 | 17.3998 | 17.3643 | 41.9713 | 33.8623 | 12.7025 | 10.8814 | 28.8454
WISD6 R2 | 66 | 51.3753 | 17.3998 | 17.3643 | 41.9713 | 33.8623 | 12.7025 | 10.8814 | 28.8454
WMEL2 MC1 | 275 | 78.1299 | 28.704 | 14.3822 | 54.9758 | 74.6413 | 29.4518 | 12.0746 | 53.7257
WMEL2 MC2 | 275 | 78.1299 | 28.704 | 14.3822 | 54.9758 | 74.6413 | 29.4518 | 12.0746 | 53.7257
WMEL2 MC3 | 275 | 78.1299 | 28.704 | 14.3822 | 54.9758 | 74.6413 | 29.4518 | 12.0746 | 53.7257
WMEL2 MC4 | 275 | 78.1299 | 28.704 | 14.3822 | 54.9758 | 74.6413 | 29.4518 | 12.0746 | 53.7257
WTHU4A | 400 | 93.8467 | 32.2021 | 8.4218 | 53.9625 | 75.335 | 29.4057 | 4.8586 | 46.4445
WTHU4B | 400 | 93.8467 | 32.2021 | 8.4218 | 53.9625 | 77.0314 | 30.0404 | 4.968 | 47.4515
WWEY2 M1 | 275 | 71.9441 | 26.0725 | 17.8295 | 54.7016 | 70.9117 | 27.0502 | 16.7066 | 54.9613
WWEY2 M2 | 275 | 71.9441 | 26.0725 | 17.8295 | 54.7016 | 70.9117 | 27.0502 | 16.7066 | 54.9613
WWEY2 R1 | 275 | 73.3648 | 26.7472 | 16.4553 | 54.2816 | 73.3209 | 28.0972 | 16.5322 | 56.2676
WWEY2 R2 | 275 | 73.3648 | 26.7472 | 16.4553 | 54.2816 | 73.3209 | 28.0972 | 16.5322 | 56.2676
WWEY4A | 400 | 50.0542 | 18.255 | 6.2453 | 32.0617 | 44.8282 | 17.192 | 6.124 | 30.4372
WWEY4B | 400 | 50.6789 | 18.4725 | 6.5 | 32.6241 | 44.8448 | 17.2646 | 6.3619 | 30.7777
WYLF1 M1 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 M1 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 M2 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 M2 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 R1 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 R1 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 R2 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF1 R2 | 132 | 18.4064 | 5.7484 | 6.7501 | 14.8796 | 20.7283 | 7.1841 | 7.0042 | 17.1641
WYLF4 M1 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 M1 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 M2 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 M2 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 R1 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 R1 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 R2 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYLF4 R2 | 400 | 48.1537 | 17.3163 | 11.9822 | 36.4711 | 35.9973 | 14.0288 | 6.9283 | 26.7681
WYMO4 M1 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 M1 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 M2 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 M2 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 R1 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 R1 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 R2 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525
WYMO4 R2 | 400 | 109.5301 | 39.5969 | 24.3967 | 80.3952 | 94.446 | 36.4211 | 19.0178 | 70.525

## D3.4
ETYS 19 Yr 4 - NGET Fault Levels (kA), Winter 2022/23
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 37.4816 | 13.7201 | 3.2566 | 22.6597 | 34.1688 | 13.3655 | 2.3905 | 21.2922 | Back To Menu
ABHA4B | 400 | 37.4643 | 13.7107 | 3.2557 | 22.6455 | 34.1585 | 13.3593 | 2.3851 | 21.278
ABTH1 M1 | 132 | 27.9967 | 10.5095 | 6.1249 | 20.9877 | 26.9354 | 10.6218 | 6.1135 | 21.1351
ABTH1 M2 | 132 | 25.7729 | 10.0291 | 7.6417 | 21.825 | 22.8018 | 9.1398 | 6.6704 | 19.596
ABTH1 R1 | 132 | 28.4583 | 10.9709 | 7.6639 | 23.1792 | 31.2188 | 12.3212 | 8.7847 | 26.2095
ABTH1 R2 | 132 | 28.4583 | 10.9709 | 7.6639 | 23.1792 | 31.2188 | 12.3212 | 8.7847 | 26.2095
ABTH2 M1 | 275 | 48.1322 | 17.9288 | 8.8308 | 34.1859 | 43.7222 | 17.3049 | 7.306 | 31.7788
ABTH2 M2 | 275 | 48.1322 | 17.9288 | 8.8308 | 34.1859 | 43.7222 | 17.3049 | 7.306 | 31.7788
ABTH2 M4 | 275 | 48.1322 | 17.9288 | 8.8308 | 34.1859 | 43.7222 | 17.3049 | 7.306 | 31.7788
ABTH2 R | 275 | 39.612 | 14.9755 | 4.4991 | 25.6777 | 33.8751 | 13.5805 | 2.8011 | 22.0068
ALDW2 MC1 | 275 | 63.0108 | 23.5073 | 10.001 | 43.2453 | 61.8495 | 24.5138 | 9.8742 | 44.5419
ALDW2 MC2 | 275 | 63.0108 | 23.5073 | 10.001 | 43.2453 | 61.8495 | 24.5138 | 9.8742 | 44.5419
ALDW2 MC3 | 275 | 63.0108 | 23.5073 | 10.001 | 43.2453 | 61.8495 | 24.5138 | 9.8742 | 44.5419
ALDW2 MC4 | 275 | 63.0108 | 23.5073 | 10.001 | 43.2453 | 61.8495 | 24.5138 | 9.8742 | 44.5419
AMEM1 M1 | 132 | 25.7348 | 9.1836 | 9.2183 | 22.2059 | 31.7056 | 11.6578 | 10.5092 | 26.9959
AMEM1 M2 | 132 | 25.7348 | 9.1836 | 9.2183 | 22.2059 | 31.7056 | 11.6578 | 10.5092 | 26.9959
AMEM1 R1 | 132 | 25.7348 | 9.1836 | 9.2183 | 22.2059 | 31.7056 | 11.6578 | 10.5092 | 26.9959
AMEM1 R2 | 132 | 25.7348 | 9.1836 | 9.2183 | 22.2059 | 31.7056 | 11.6578 | 10.5092 | 26.9959
AMEM4 M | 400 | 49.69 | 18.4928 | 4.1894 | 30.3422 | 41.779 | 16.5835 | 2.8828 | 26.3355
AMEM4 R | 400 | 50.7038 | 18.8378 | 4.2911 | 30.9317 | 41.6875 | 16.477 | 2.8509 | 26.1528
AXMI4 MC1 | 400 | 39.6433 | 14.7208 | 7.976 | 28.7944 | 33.3149 | 13.0325 | 6.1772 | 24.608
AXMI4 MC2 | 400 | 39.6433 | 14.7208 | 7.976 | 28.7944 | 33.3149 | 13.0325 | 6.1772 | 24.608
BAGB2 M1 | 275 | 49.6644 | 18.1274 | 12.9696 | 38.6056 | 48.253 | 18.3946 | 12.894 | 38.9079
BAGB2 M2 | 275 | 49.6644 | 18.1274 | 12.9696 | 38.6056 | 48.253 | 18.3946 | 12.894 | 38.9079
BAGB2 R1 | 275 | 49.6644 | 18.1274 | 12.9696 | 38.6056 | 48.253 | 18.3946 | 12.894 | 38.9079
BAGB2 R2 | 275 | 49.6644 | 18.1274 | 12.9696 | 38.6056 | 48.253 | 18.3946 | 12.894 | 38.9079
BARK2 M1 | 275 | 53.4002 | 19.3099 | 14.2373 | 41.5457 | 53.6971 | 20.3157 | 14.1442 | 42.8749
BARK2 M2 | 275 | 51.5377 | 18.6475 | 13.9583 | 40.3298 | 53.6339 | 20.2304 | 14.6222 | 43.2323
BARK2 R1 | 275 | 53.4002 | 19.3099 | 14.2373 | 41.5457 | 53.6971 | 20.3157 | 14.1442 | 42.8749
BARK2 R2 | 275 | 51.5377 | 18.6475 | 13.9583 | 40.3298 | 53.6339 | 20.2304 | 14.6222 | 43.2323
BARK4 M1 | 400 | 129.1859 | 45.3227 | 40.0251 | 104.1211 | 123.2525 | 47.6137 | 32.5313 | 99.8673
BARK4 M2 | 400 | 129.1859 | 45.3227 | 40.0251 | 104.1211 | 123.2525 | 47.6137 | 32.5313 | 99.8673
BARK4 R1 | 400 | 129.1859 | 45.3227 | 40.0251 | 104.1211 | 123.2525 | 47.6137 | 32.5313 | 99.8673
BARK4 R2 | 400 | 129.1859 | 45.3227 | 40.0251 | 104.1211 | 123.2525 | 47.6137 | 32.5313 | 99.8673
BEDD2 M1/4 | 275 | 60.3994 | 21.6 | 13.7917 | 44.3387 | 63.3955 | 24.2123 | 13.6435 | 47.885
BEDD2 M2/3 | 275 | 78.5415 | 27.7911 | 17.5938 | 56.8963 | 81.0661 | 30.9195 | 17.2091 | 60.9359
BEDD2 R1 | 275 | 50.7848 | 18.8131 | 11.2337 | 37.8394 | 51.0206 | 19.6543 | 11.0573 | 38.8527
BEDD2 R2 | 275 | 78.5415 | 27.7911 | 17.5938 | 56.8963 | 81.0661 | 30.9195 | 17.2091 | 60.9359
BEDD2 R3 | 275 | 78.5415 | 27.7911 | 17.5938 | 56.8963 | 81.0661 | 30.9195 | 17.2091 | 60.9359
BEDD2 R4 | 275 | 50.7848 | 18.8131 | 11.2337 | 37.8394 | 51.0206 | 19.6543 | 11.0573 | 38.8527
BEDD4B | 400 | 41.9502 | 15.6233 | 3.0962 | 25.1909 | 37.1492 | 14.8412 | 3.6763 | 24.6649
BESW2 MC1 | 275 | 59.2204 | 21.7883 | 10.9856 | 41.799 | 51.4885 | 20.5177 | 8.4813 | 37.4977
BESW2 MC2 | 275 | 59.2204 | 21.7883 | 10.9856 | 41.799 | 51.4885 | 20.5177 | 8.4813 | 37.4977
BESW2 MC3 | 275 | 59.2204 | 21.7883 | 10.9856 | 41.799 | 51.4885 | 20.5177 | 8.4813 | 37.4977
BESW2 MC4 | 275 | 59.2204 | 21.7883 | 10.9856 | 41.799 | 51.4885 | 20.5177 | 8.4813 | 37.4977
BICF4A | 400 | 99.941 | 36.5139 | 33.7782 | 85.4166 | 65.3275 | 26.0774 | 16.5913 | 53.4704
BICF4B | 400 | 99.941 | 36.5139 | 33.7782 | 85.4166 | 65.3275 | 26.0774 | 16.5913 | 53.4704
BIRK2 MC1 | 275 | 59.4389 | 21.1813 | 15.9384 | 45.8934 | 59.2157 | 22.4101 | 13.4586 | 45.1512
BIRK2 MC2 | 275 | 59.4389 | 21.1813 | 15.9384 | 45.8934 | 59.2157 | 22.4101 | 13.4586 | 45.1512
BIRK2 MC3 | 275 | 59.4389 | 21.1813 | 15.9384 | 45.8934 | 59.2157 | 22.4101 | 13.4586 | 45.1512
BIRK2 MC4 | 275 | 59.4389 | 21.1813 | 15.9384 | 45.8934 | 59.2157 | 22.4101 | 13.4586 | 45.1512
BISW2 MC1 | 275 | 64.6916 | 23.7481 | 12.2167 | 45.8016 | 59.4874 | 23.4184 | 9.8093 | 42.9279
BISW2 MC2 | 275 | 64.6916 | 23.7481 | 12.2167 | 45.8016 | 59.4874 | 23.4184 | 9.8093 | 42.9279
BISW2 MC3 | 275 | 64.6916 | 23.7481 | 12.2167 | 45.8016 | 59.4874 | 23.4184 | 9.8093 | 42.9279
BISW2 MC4 | 275 | 64.6916 | 23.7481 | 12.2167 | 45.8016 | 59.4874 | 23.4184 | 9.8093 | 42.9279
BLYT1A | 132 | 30.2277 | 10.7034 | 4.5298 | 19.6666 | 31.6472 | 11.9115 | 5.1634 | 22.0087
BLYT1B | 132 | 30.0234 | 10.6566 | 4.4903 | 19.561 | 31.4963 | 11.8663 | 5.129 | 21.9105
BLYT2 M1 | 275 | 79.7577 | 29.2866 | 23.7804 | 65.1978 | 73.8708 | 28.5959 | 21.1885 | 61.6293
BLYT2 M2 | 275 | 79.7577 | 29.2866 | 23.7804 | 65.1978 | 73.8708 | 28.5959 | 21.1885 | 61.6293
BLYT2 R1 | 275 | 79.7577 | 29.2866 | 23.7804 | 65.1978 | 73.8708 | 28.5959 | 21.1885 | 61.6293
BLYT2 R2 | 275 | 79.7577 | 29.2866 | 23.7804 | 65.1978 | 73.8708 | 28.5959 | 21.1885 | 61.6293
BODE4 M1 | 400 | 92.6158 | 33.0071 | 23.0669 | 69.7459 | 76.0149 | 29.2804 | 16.8066 | 58.2153
BODE4 R1 | 400 | 92.6158 | 33.0071 | 23.0669 | 69.7459 | 76.0149 | 29.2804 | 16.8066 | 58.2153
BOLN4 M1 | 400 | 69.722 | 25.8091 | 20.891 | 57.3906 | 61.9328 | 23.8781 | 18.6764 | 52.4451
BOLN4 M2 | 400 | 69.722 | 25.8091 | 20.891 | 57.3906 | 61.9328 | 23.8781 | 18.6764 | 52.4451
BOLN4 R1 | 400 | 69.722 | 25.8091 | 20.891 | 57.3906 | 61.9328 | 23.8781 | 18.6764 | 52.4451
BOLN4 R2 | 400 | 69.722 | 25.8091 | 20.891 | 57.3906 | 61.9328 | 23.8781 | 18.6764 | 52.4451
BOTW4 MC1 | 400 | 76.7412 | 27.6579 | 15.4226 | 54.5368 | 62.0091 | 24.0717 | 11.9402 | 45.9827
BOTW4 MC2 | 400 | 76.7412 | 27.6579 | 15.4226 | 54.5368 | 62.0091 | 24.0717 | 11.9402 | 45.9827
BRAI4A | 400 | 63.1416 | 23.1533 | 14.1937 | 46.9374 | 48.5168 | 18.9662 | 9.3318 | 36.1541
BRAI4A BRFO | 400 | 63.1416 | 23.1533 | 14.1937 | 46.9374 | 48.5168 | 18.9662 | 9.3318 | 36.1541
BRAI4A RAYL | 400 | 63.1416 | 23.1533 | 14.1937 | 46.9374 | 48.5168 | 18.9662 | 9.3318 | 36.1541
BRAI4B | 400 | 60.788 | 22.3321 | 13.3899 | 44.9722 | 46.1032 | 17.9712 | 8.8431 | 34.2582
BRAI4B PELH | 400 | 60.788 | 22.3321 | 13.3899 | 44.9722 | 46.1032 | 17.9712 | 8.8431 | 34.2582
BRAI4B RAYL | 400 | 60.788 | 22.3321 | 13.3899 | 44.9722 | 46.1032 | 17.9712 | 8.8431 | 34.2582
BRAW2 MC1 | 275 | 65.371 | 23.4999 | 15.0494 | 48.2833 | 66.4607 | 25.4631 | 14.1418 | 50.1521
BRAW2 MC2 | 275 | 65.371 | 23.4999 | 15.0494 | 48.2833 | 66.4607 | 25.4631 | 14.1418 | 50.1521
BRAW2 MC3 | 275 | 65.371 | 23.4999 | 15.0494 | 48.2833 | 66.4607 | 25.4631 | 14.1418 | 50.1521
BRAW2 MC4 | 275 | 65.371 | 23.4999 | 15.0494 | 48.2833 | 66.4607 | 25.4631 | 14.1418 | 50.1521
BRAW4A | 400 | 35.2513 | 12.882 | 4.4703 | 22.6882 | 30.8785 | 11.7396 | 4.2646 | 20.8669
BRED2 MC1 | 275 | 79.4436 | 29.186 | 15.9362 | 57.2115 | 75.8817 | 29.7622 | 12.9502 | 55.0403
BRED2 MC2 | 275 | 79.4436 | 29.186 | 15.9362 | 57.2115 | 75.8817 | 29.7622 | 12.9502 | 55.0403
BRED2 MC3 | 275 | 79.4436 | 29.186 | 15.9362 | 57.2115 | 75.8817 | 29.7622 | 12.9502 | 55.0403
BRED2 MC4 | 275 | 79.4436 | 29.186 | 15.9362 | 57.2115 | 75.8817 | 29.7622 | 12.9502 | 55.0403
BRFO4 M3 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 M5 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 M6 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 M7 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 R3 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 R5 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 R6 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRFO4 R7 | 400 | 85.1063 | 31.1884 | 27.2773 | 71.3844 | 77.5111 | 29.8982 | 22.6542 | 64.9367
BRIM1 M1 | 132 | 51.6615 | 17.4688 | 19.1185 | 43.8232 | 65.6766 | 23.5764 | 23.0055 | 56.3475
BRIM1 M2 | 132 | 51.6615 | 17.4688 | 19.1185 | 43.8232 | 65.6766 | 23.5764 | 23.0055 | 56.3475
BRIM1 R1 | 132 | 51.6615 | 17.4688 | 19.1185 | 43.8232 | 65.6766 | 23.5764 | 23.0055 | 56.3475
BRIM1 R2 | 132 | 51.6615 | 17.4688 | 19.1185 | 43.8232 | 65.6766 | 23.5764 | 23.0055 | 56.3475
BRIN2 M1 | 275 | 64.8525 | 23.797 | 13.9574 | 47.6114 | 68.4803 | 26.7903 | 12.946 | 50.8332
BRIN2 M2 | 275 | 68.6582 | 25.1964 | 17.0294 | 52.6625 | 72.0296 | 27.7772 | 16.5383 | 55.8212
BRIN2 R1 | 275 | 64.8525 | 23.797 | 13.9574 | 47.6114 | 68.4803 | 26.7903 | 12.946 | 50.8332
BRIN2 R2 | 275 | 68.6582 | 25.1964 | 17.0294 | 52.6625 | 72.0296 | 27.7772 | 16.5383 | 55.8212
BRIN4 MC1 | 400 | 71.2382 | 26.0472 | 16.267 | 53.1034 | 55.5805 | 21.7249 | 11.3475 | 42.0712
BRIN4 MC4 | 400 | 71.2382 | 26.0472 | 16.267 | 53.1034 | 55.5805 | 21.7249 | 11.3475 | 42.0712
BRLE4 M1 | 400 | 121.6712 | 43.6314 | 24.467 | 86.1711 | 104.3816 | 40.593 | 21.041 | 78.4482
BRLE4 M2 | 400 | 121.6712 | 43.6314 | 24.467 | 86.1711 | 104.3816 | 40.593 | 21.041 | 78.4482
BRLE4 R1 | 400 | 121.6712 | 43.6314 | 24.467 | 86.1711 | 104.3816 | 40.593 | 21.041 | 78.4482
BRLE4 R2 | 400 | 121.6712 | 43.6314 | 24.467 | 86.1711 | 104.3816 | 40.593 | 21.041 | 78.4482
BULL4 MC1 | 400 | 68.6101 | 25.0499 | 15.0878 | 50.5137 | 51.8211 | 20.3433 | 9.137 | 37.9068
BULL4 MC2 | 400 | 68.6101 | 25.0499 | 15.0878 | 50.5137 | 51.8211 | 20.3433 | 9.137 | 37.9068
BURW4 MC1 | 400 | 90.9621 | 32.9542 | 21.8019 | 68.4063 | 61.8496 | 24.6134 | 11.1872 | 45.9959
BURW4 MC2 | 400 | 90.9621 | 32.9542 | 21.8019 | 68.4063 | 61.8496 | 24.6134 | 11.1872 | 45.9959
BURW4 MC3 | 400 | 90.9621 | 32.9542 | 21.8019 | 68.4063 | 61.8496 | 24.6134 | 11.1872 | 45.9959
BURW4 MC4 | 400 | 90.9621 | 32.9542 | 21.8019 | 68.4063 | 61.8496 | 24.6134 | 11.1872 | 45.9959
BUSH2 MC1 | 275 | 55.2078 | 20.2612 | 11.4011 | 40.0548 | 54.8108 | 21.3775 | 10.3711 | 40.6035
BUSH2 MC2 | 275 | 55.2078 | 20.2612 | 11.4011 | 40.0548 | 54.8108 | 21.3775 | 10.3711 | 40.6035
BUSH2 MC3 | 275 | 55.2078 | 20.2612 | 11.4011 | 40.0548 | 54.8108 | 21.3775 | 10.3711 | 40.6035
BUSH2 MC4 | 275 | 55.2078 | 20.2612 | 11.4011 | 40.0548 | 54.8108 | 21.3775 | 10.3711 | 40.6035
BUST2 M1 | 275 | 72.6408 | 26.1581 | 19.4467 | 56.4398 | 75.1742 | 28.6426 | 18.0323 | 58.5391
BUST2 M2 | 275 | 72.6408 | 26.1581 | 19.4467 | 56.4398 | 75.1742 | 28.6426 | 18.0323 | 58.5391
BUST2 R1 | 275 | 72.6408 | 26.1581 | 19.4467 | 56.4398 | 75.1742 | 28.6426 | 18.0323 | 58.5391
BUST2 R2 | 275 | 72.6408 | 26.1581 | 19.4467 | 56.4398 | 75.1742 | 28.6426 | 18.0323 | 58.5391
CANT4 MC1 | 400 | 88.2961 | 31.9129 | 18.643 | 63.7746 | 70.039 | 27.5298 | 12.7085 | 51.6415
CANT4 MC2 | 400 | 88.2961 | 31.9129 | 18.643 | 63.7746 | 70.039 | 27.5298 | 12.7085 | 51.6415
CANT4 MC3 | 400 | 88.2961 | 31.9129 | 18.643 | 63.7746 | 70.039 | 27.5298 | 12.7085 | 51.6415
CANT4 MC4 | 400 | 88.2961 | 31.9129 | 18.643 | 63.7746 | 70.039 | 27.5298 | 12.7085 | 51.6415
CANT4 R5 | 400 | 88.2961 | 31.9129 | 18.643 | 63.7746 | 70.039 | 27.5298 | 12.7085 | 51.6415
CANT4 R5 | 400 | 88.3082 | 31.918 | 18.6454 | 63.7843 | 70.0468 | 27.5322 | 12.7119 | 51.6484
CANT4 R5 | 400 | 88.3082 | 31.918 | 18.6454 | 63.7843 | 70.0468 | 27.5322 | 12.7119 | 51.6484
CAPE2 M1 | 275 | 69.5069 | 24.3411 | 22.1478 | 56.5713 | 78.242 | 28.6742 | 23.6053 | 64.1568
CAPE2 M2 | 275 | 69.5069 | 24.3411 | 22.1478 | 56.5713 | 78.242 | 28.6742 | 23.6053 | 64.1568
CAPE2 R1 | 275 | 69.5069 | 24.3411 | 22.1478 | 56.5713 | 78.242 | 28.6742 | 23.6053 | 64.1568
CAPE2 R2 | 275 | 69.5069 | 24.3411 | 22.1478 | 56.5713 | 78.242 | 28.6742 | 23.6053 | 64.1568
CAPE4A | 400 | 96.1599 | 34.0135 | 24.8498 | 72.9522 | 87.5704 | 33.2177 | 19.8059 | 66.7828
CAPE4B | 400 | 96.1632 | 34.0148 | 24.8497 | 72.954 | 88.3246 | 33.4993 | 19.9235 | 67.2986
CARE2 MC1 | 275 | 46.7502 | 17.5438 | 8.2003 | 33.0111 | 39.7371 | 15.7699 | 7.0998 | 29.4018
CARE2 MC2 | 275 | 46.7502 | 17.5438 | 8.2003 | 33.0111 | 39.7371 | 15.7699 | 7.0998 | 29.4018
CARR1 M1 | 132 | 34.9947 | 12.9454 | 9.9187 | 28.2263 | 40.7592 | 15.551 | 11.7191 | 33.7115
CARR1 M2 | 132 | 34.9947 | 12.9454 | 9.9187 | 28.2263 | 40.7592 | 15.551 | 11.7191 | 33.7115
CARR1 M3 | 132 | 34.9947 | 12.9454 | 9.9187 | 28.2263 | 40.7592 | 15.551 | 11.7191 | 33.7115
CARR1 M4 | 132 | 42.1509 | 14.8197 | 14.1272 | 35.0854 | 54.0527 | 19.815 | 17.6129 | 45.6356
CARR1 R1 | 132 | 34.9947 | 12.9454 | 9.9187 | 28.2263 | 40.7592 | 15.551 | 11.7191 | 33.7115
CARR1 R2 | 132 | 34.9947 | 12.9454 | 9.9187 | 28.2263 | 40.7592 | 15.551 | 11.7191 | 33.7115
CARR1 R3 | 132 | 42.1509 | 14.8197 | 14.1272 | 35.0854 | 54.0527 | 19.815 | 17.6129 | 45.6356
CARR1 R4 | 132 | 42.1509 | 14.8197 | 14.1272 | 35.0854 | 54.0527 | 19.815 | 17.6129 | 45.6356
CARR1B | 132 | 41.3559 | 14.3789 | 8.0513 | 28.3862 | 51.1469 | 19.2842 | 7.04 | 34.312
CARR1C | 132 | 41.1852 | 14.3624 | 7.6418 | 27.9533 | 50.6904 | 19.2354 | 5.5834 | 32.7863
CARR1D | 132 | 41.4667 | 14.398 | 8.2851 | 28.6469 | 51.5275 | 19.3343 | 7.4096 | 34.7524
CARR2 M1 | 275 | 82.5508 | 29.827 | 22.1546 | 64.3364 | 89.0837 | 33.5285 | 24.3249 | 71.7414
CARR2 M2 | 275 | 82.5508 | 29.827 | 22.1546 | 64.3364 | 89.0837 | 33.5285 | 24.3249 | 71.7414
CARR2 R1 | 275 | 82.5508 | 29.827 | 22.1546 | 64.3364 | 89.0837 | 33.5285 | 24.3249 | 71.7414
CARR2 R2 | 275 | 82.5508 | 29.827 | 22.1546 | 64.3364 | 89.0837 | 33.5285 | 24.3249 | 71.7414
CARR4 M1 | 400 | 122.4591 | 45.0333 | 36.2254 | 99.9121 | 107.0005 | 41.5511 | 30.8959 | 89.658
CARR4 M2/4 | 400 | 122.4591 | 45.0333 | 36.2254 | 99.9121 | 107.0005 | 41.5511 | 30.8959 | 89.658
CARR4 R1 | 400 | 122.4591 | 45.0333 | 36.2254 | 99.9121 | 107.0005 | 41.5511 | 30.8959 | 89.658
CARR4 R1/2 | 400 | 122.4591 | 45.0333 | 36.2254 | 99.9121 | 107.0005 | 41.5511 | 30.8959 | 89.658
CARR4 R2 | 400 | 122.4591 | 45.0333 | 36.2254 | 99.9121 | 107.0005 | 41.5511 | 30.8959 | 89.658
CARR4 R4 | 400 | 122.4591 | 45.0333 | 36.2254 | 99.9121 | 107.0005 | 41.5511 | 30.8959 | 89.658
CARR4A | 400 | 102.9998 | 36.7603 | 8.8819 | 60.8688 | 84.1044 | 32.6599 | 8.5573 | 54.7453
CARR4B | 400 | 104.6749 | 37.2816 | 9.1155 | 61.8396 | 86.5493 | 33.6143 | 8.5836 | 56.1214
CASK1 M1 | 132 | 48.5692 | 16.1577 | 13.0958 | 35.9462 | 53.8636 | 18.919 | 15.8271 | 42.5826
CELL1 M1 | 132 | 45.1677 | 16.7782 | 14.1891 | 37.917 | 56.1518 | 22.1013 | 16.7153 | 47.9713
CELL1 M2 | 132 | 43.1777 | 16.0014 | 12.0024 | 34.6319 | 47.8598 | 18.5127 | 12.8508 | 39.0317
CELL1 R1 | 132 | 45.1677 | 16.7782 | 14.1891 | 37.917 | 56.1518 | 22.1013 | 16.7153 | 47.9713
CELL1 R2 | 132 | 43.1777 | 16.0014 | 12.0024 | 34.6319 | 47.8598 | 18.5127 | 12.8508 | 39.0317
CELL1A | 132 | 37.7521 | 13.5196 | 6.9326 | 26.0522 | 46.6174 | 18.6629 | 8.2877 | 34.681
CELL4 M1 | 400 | 92.6885 | 34.2333 | 16.8885 | 65.3017 | 76.0538 | 30.0357 | 14.355 | 56.8319
CELL4 M2 | 400 | 92.6885 | 34.2333 | 16.8885 | 65.3017 | 76.0538 | 30.0357 | 14.355 | 56.8319
CELL4 R1 | 400 | 92.6885 | 34.2333 | 16.8885 | 65.3017 | 76.0538 | 30.0357 | 14.355 | 56.8319
CELL4 R2 | 400 | 92.6885 | 34.2333 | 16.8885 | 65.3017 | 76.0538 | 30.0357 | 14.355 | 56.8319
CHIC4 MB1 | 400 | 36.8473 | 13.7357 | 7.3843 | 26.8095 | 30.1953 | 11.7908 | 5.7393 | 22.414
CHIC4 MB2 | 400 | 36.8473 | 13.7357 | 7.3843 | 26.8095 | 30.1953 | 11.7908 | 5.7393 | 22.414
CHIC4 R1/2 | 400 | 36.5207 | 13.783 | 10.7021 | 30.1942 | 28.6658 | 11.2817 | 7.691 | 23.6457
CHSI2 MC1 | 275 | 85.0834 | 30.5635 | 18.395 | 61.6183 | 74.018 | 29.1724 | 12.1273 | 53.3833
CHSI2 MC2 | 275 | 85.0834 | 30.5635 | 18.395 | 61.6183 | 74.018 | 29.1724 | 12.1273 | 53.3833
CHSI2 MC3 | 275 | 85.0834 | 30.5635 | 18.395 | 61.6183 | 74.018 | 29.1724 | 12.1273 | 53.3833
CHSI2 MC4 | 275 | 85.0834 | 30.5635 | 18.395 | 61.6183 | 74.018 | 29.1724 | 12.1273 | 53.3833
CHTE2 MC1 | 275 | 69.661 | 25.1379 | 16.7154 | 52.2658 | 59.236 | 23.4929 | 11.0184 | 44.2424
CHTE2 MC2 | 275 | 69.661 | 25.1379 | 16.7154 | 52.2658 | 59.236 | 23.4929 | 11.0184 | 44.2424
CHTE2 MC3 | 275 | 69.661 | 25.1379 | 16.7154 | 52.2658 | 59.236 | 23.4929 | 11.0184 | 44.2424
CHTE2 MC4 | 275 | 69.661 | 25.1379 | 16.7154 | 52.2658 | 59.236 | 23.4929 | 11.0184 | 44.2424
CILF4 M1 | 400 | 80.0407 | 28.7953 | 19.1221 | 59.8448 | 70.2746 | 27.1078 | 13.8691 | 52.2053
CILF4 M2 | 400 | 80.0407 | 28.7953 | 19.1221 | 59.8448 | 70.2746 | 27.1078 | 13.8691 | 52.2053
CILF4 R1 | 400 | 80.0407 | 28.7953 | 19.1221 | 59.8448 | 70.2746 | 27.1078 | 13.8691 | 52.2053
CILF4 R2 | 400 | 80.0407 | 28.7953 | 19.1221 | 59.8448 | 70.2746 | 27.1078 | 13.8691 | 52.2053
CITR4 M5 | 400 | 108.6187 | 36.6878 | 25.5772 | 77.4616 | 121.5734 | 45.9299 | 23.9714 | 88.9262
CITR4 M6 | 400 | 108.6187 | 36.6878 | 25.5772 | 77.4616 | 121.5734 | 45.9299 | 23.9714 | 88.9262
CITR4 MC1 | 400 | 108.6231 | 36.6889 | 25.5788 | 77.4648 | 121.5919 | 45.9326 | 24.0175 | 88.976
CITR4 MC2 | 400 | 108.6231 | 36.6889 | 25.5788 | 77.4648 | 121.5919 | 45.9326 | 24.0175 | 88.976
CITR4 MC3 | 400 | 108.6231 | 36.6889 | 25.5788 | 77.4648 | 121.5919 | 45.9326 | 24.0175 | 88.976
CITR4 MC4 | 400 | 108.6231 | 36.6889 | 25.5788 | 77.4648 | 121.5919 | 45.9326 | 24.0175 | 88.976
CITR4 R5 | 400 | 108.6187 | 36.6878 | 25.5772 | 77.4616 | 121.5734 | 45.9299 | 23.9714 | 88.9262
CITR4 R6 | 400 | 108.6187 | 36.6878 | 25.5772 | 77.4616 | 121.5734 | 45.9299 | 23.9714 | 88.9262
CLEH4 M1 | 400 | 76.4813 | 27.7266 | 16.5055 | 55.7168 | 69.0014 | 26.9827 | 13.7335 | 51.8928
CLEH4 R1 | 400 | 76.4813 | 27.7266 | 16.5055 | 55.7168 | 69.0014 | 26.9827 | 13.7335 | 51.8928
CONQ4 M1 | 400 | 132.202 | 45.9769 | 34.4127 | 99.4339 | 133.2918 | 49.6207 | 36.0115 | 106.1859
CONQ4 M2 | 400 | 132.202 | 45.9769 | 34.4127 | 99.4339 | 133.2918 | 49.6207 | 36.0115 | 106.1859
CONQ4 M3 | 400 | 132.202 | 45.9769 | 34.4127 | 99.4339 | 133.2918 | 49.6207 | 36.0115 | 106.1859
CONQ4 M4 | 400 | 132.202 | 45.9769 | 34.4127 | 99.4339 | 133.2918 | 49.6207 | 36.0115 | 106.1859
CONQ4 R1/3 | 400 | 132.202 | 45.9769 | 34.4127 | 99.4339 | 133.2918 | 49.6207 | 36.0115 | 106.1859
CONQ4 R2/4 | 400 | 132.202 | 45.9769 | 34.4127 | 99.4339 | 133.2918 | 49.6207 | 36.0115 | 106.1859
COSO4 M | 400 | 98.1491 | 34.7081 | 21.7159 | 70.8006 | 87.0378 | 33.3171 | 19.5316 | 66.6491
COSO4 R | 400 | 98.1491 | 34.7081 | 21.7159 | 70.8006 | 87.0378 | 33.3171 | 19.5316 | 66.6491
COTT4 M1 | 400 | 99.9575 | 36.7327 | 23.0455 | 74.9934 | 80.0609 | 31.1377 | 16.2375 | 60.2728
COTT4 M2 | 400 | 99.9575 | 36.7327 | 23.0455 | 74.9934 | 80.0609 | 31.1377 | 16.2375 | 60.2728
COTT4 M3 | 400 | 96.1264 | 35.7072 | 29.9808 | 80.4785 | 79.5205 | 30.9553 | 23.055 | 66.8324
COTT4 M4 | 400 | 96.1264 | 35.7072 | 29.9808 | 80.4785 | 79.5205 | 30.9553 | 23.055 | 66.8324
COTT4 R1/2 | 400 | 96.1264 | 35.7072 | 29.9808 | 80.4785 | 79.5205 | 30.9553 | 23.055 | 66.8324
COTT4 R3/4 | 400 | 96.1264 | 35.7072 | 29.9808 | 80.4785 | 79.5205 | 30.9553 | 23.055 | 66.8324
COVE2 MC1 | 275 | 61.9786 | 22.5481 | 12.8241 | 44.712 | 58.0037 | 22.5063 | 11.9305 | 43.7592
COVE2 MC2 | 275 | 61.9786 | 22.5481 | 12.8241 | 44.712 | 58.0037 | 22.5063 | 11.9305 | 43.7592
COVE2 MC3 | 275 | 61.9786 | 22.5481 | 12.8241 | 44.712 | 58.0037 | 22.5063 | 11.9305 | 43.7592
COVE2 MC4 | 275 | 61.9786 | 22.5481 | 12.8241 | 44.712 | 58.0037 | 22.5063 | 11.9305 | 43.7592
COWL4 M1 | 400 | 124.7237 | 45.9051 | 37.4361 | 102.3558 | 104.3908 | 40.6413 | 29.3461 | 86.8216
COWL4 M2 | 400 | 124.7237 | 45.9051 | 37.4361 | 102.3558 | 104.3908 | 40.6413 | 29.3461 | 86.8216
COWL4 R1 | 400 | 124.7237 | 45.9051 | 37.4361 | 102.3558 | 104.3908 | 40.6413 | 29.3461 | 86.8216
COWL4 R2 | 400 | 124.7237 | 45.9051 | 37.4361 | 102.3558 | 104.3908 | 40.6413 | 29.3461 | 86.8216
CREB2A | 275 | 73.7364 | 25.7491 | 16.8111 | 53.2258 | 70.4891 | 26.0462 | 13.0303 | 49.8651
CREB2B | 275 | 73.747 | 25.7495 | 16.8191 | 53.2344 | 71.2809 | 26.3304 | 13.1782 | 50.4151
CREB4 MB1 | 400 | 130.8269 | 44.9245 | 34.9447 | 98.4776 | 101.068 | 38.4308 | 23.0307 | 77.3801
CREB4 MB2 | 400 | 130.8269 | 44.9245 | 34.9447 | 98.4776 | 101.068 | 38.4308 | 23.0307 | 77.3801
CREB4 RB1 | 400 | 130.8269 | 44.9245 | 34.9447 | 98.4776 | 101.068 | 38.4308 | 23.0307 | 77.3801
CREB4 RB2 | 400 | 130.8269 | 44.9245 | 34.9447 | 98.4776 | 101.068 | 38.4308 | 23.0307 | 77.3801
DAIN4 M1 | 400 | 114.0471 | 41.2926 | 23.3151 | 81.7117 | 96.9421 | 37.6656 | 19.3646 | 72.6319
DAIN4 M2 | 400 | 114.0471 | 41.2926 | 23.3151 | 81.7117 | 96.9421 | 37.6656 | 19.3646 | 72.6319
DAIN4 R1 | 400 | 116.5542 | 42.094 | 24.0681 | 83.598 | 97.9615 | 38.0848 | 19.6385 | 73.4986
DAIN4 R2 | 400 | 116.5542 | 42.094 | 24.0681 | 83.598 | 97.9615 | 38.0848 | 19.6385 | 73.4986
DIDC4 M1 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 M2 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 M3 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 M4 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 M5 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 M6 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 R1/2 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 R3/4 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 R5 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DIDC4 R6 | 400 | 118.9778 | 42.7623 | 26.3487 | 86.8238 | 108.5515 | 41.2606 | 26.4337 | 84.785
DINO4 1 | 400 | 83.7016 | 28.9599 | 24.6822 | 65.6376 | 86.6603 | 31.8895 | 26.0581 | 71.1565
DINO4 2 | 400 | 83.7016 | 28.9599 | 24.6822 | 65.6376 | 86.6603 | 31.8895 | 26.0581 | 71.1565
DINO4 3 | 400 | 83.7016 | 28.9599 | 24.6822 | 65.6376 | 86.6603 | 31.8895 | 26.0581 | 71.1565
DRAK1 M1 | 132 | 30.9772 | 11.083 | 12.5796 | 28.2533 | 38.2797 | 14.1177 | 15.6449 | 35.6103
DRAK1 M2 | 132 | 30.9772 | 11.083 | 12.5796 | 28.2533 | 38.2797 | 14.1177 | 15.6449 | 35.6103
DRAK1 R1 | 132 | 30.9772 | 11.083 | 12.5796 | 28.2533 | 38.2797 | 14.1177 | 15.6449 | 35.6103
DRAK1 R2 | 132 | 30.9772 | 11.083 | 12.5796 | 28.2533 | 38.2797 | 14.1177 | 15.6449 | 35.6103
DRAK4 M1 | 400 | 129.6549 | 46.3742 | 26.3145 | 91.8976 | 121.2159 | 46.8996 | 24.0708 | 90.3968
DRAK4 M2 | 400 | 129.6549 | 46.3742 | 26.3145 | 91.8976 | 121.2159 | 46.8996 | 24.0708 | 90.3968
DRAK4 M3 | 400 | 129.6549 | 46.3742 | 26.3145 | 91.8976 | 121.2159 | 46.8996 | 24.0708 | 90.3968
DRAK4 R1/3 | 400 | 129.6549 | 46.3742 | 26.3145 | 91.8976 | 121.2159 | 46.8996 | 24.0708 | 90.3968
DRAK4 R2 | 400 | 129.6549 | 46.3742 | 26.3145 | 91.8976 | 121.2159 | 46.8996 | 24.0708 | 90.3968
DRAX1 M1 | 132 | 39.2871 | 11.8693 | 11.7188 | 28.5045 | 49.131 | 16.6836 | 14.8042 | 38.3983
DRAX1 M2 | 132 | 39.2871 | 11.8693 | 11.7188 | 28.5045 | 49.131 | 16.6836 | 14.8042 | 38.3983
DRAX1 R1 | 132 | 39.2871 | 11.8693 | 11.7188 | 28.5045 | 49.131 | 16.6836 | 14.8042 | 38.3983
DRAX1 R2 | 132 | 39.2871 | 11.8693 | 11.7188 | 28.5045 | 49.131 | 16.6836 | 14.8042 | 38.3983
DRAX4 M1 | 400 | 125.2447 | 43.4736 | 35.0292 | 96.5102 | 130.0218 | 47.767 | 37.476 | 105.0288
DRAX4 M2 | 400 | 125.2447 | 43.4736 | 35.0292 | 96.5102 | 130.0218 | 47.767 | 37.476 | 105.0288
DRAX4 M3 | 400 | 125.2447 | 43.4736 | 35.0292 | 96.5102 | 130.0218 | 47.767 | 37.476 | 105.0288
DRAX4 M4 | 400 | 115.0814 | 39.9722 | 33.5445 | 90.0737 | 120.1709 | 44.0574 | 35.7482 | 98.0548
DRAX4 M5 | 400 | 115.0814 | 39.9722 | 33.5445 | 90.0737 | 120.1709 | 44.0574 | 35.7482 | 98.0548
DRAX4 M6 | 400 | 115.0814 | 39.9722 | 33.5445 | 90.0737 | 120.1709 | 44.0574 | 35.7482 | 98.0548
DRAX4 R1/2/3 | 400 | 125.2447 | 43.4736 | 35.0292 | 96.5102 | 130.0218 | 47.767 | 37.476 | 105.0288
DRAX4 R4/5/6 | 400 | 115.0814 | 39.9722 | 33.5445 | 90.0737 | 120.1709 | 44.0574 | 35.7482 | 98.0548
DUNG2 M1 | 275 | 45.2626 | 16.1188 | 15.1677 | 37.9631 | 46.3447 | 17.0463 | 15.2923 | 39.3994
DUNG2 M2 | 275 | 45.2626 | 16.1188 | 15.1677 | 37.9631 | 46.3447 | 17.0463 | 15.2923 | 39.3994
DUNG2 R1 | 275 | 45.2626 | 16.1188 | 15.1677 | 37.9631 | 46.3447 | 17.0463 | 15.2923 | 39.3994
DUNG2 R2 | 275 | 45.2626 | 16.1188 | 15.1677 | 37.9631 | 46.3447 | 17.0463 | 15.2923 | 39.3994
DUNG4 M1 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
DUNG4 M2 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
DUNG4 M3 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
DUNG4 M4 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
DUNG4 M5 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
DUNG4 R1/2 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
DUNG4 R4/5 | 400 | 78.7969 | 27.8369 | 12.8206 | 52.1879 | 72.6723 | 27.3253 | 13.7667 | 52.4105
EALI2 MC1 | 275 | 59.4749 | 20.8891 | 13.4887 | 43.0304 | 65.3488 | 25.3608 | 8.3713 | 44.2368
EALI2 MC2 | 275 | 59.4749 | 20.8891 | 13.4887 | 43.0304 | 65.3488 | 25.3608 | 8.3713 | 44.2368
EALI2 MC3 | 275 | 59.4749 | 20.8891 | 13.4887 | 43.0304 | 65.3488 | 25.3608 | 8.3713 | 44.2368
EALI2 MC4 | 275 | 59.4749 | 20.8891 | 13.4887 | 43.0304 | 65.3488 | 25.3608 | 8.3713 | 44.2368
EASO4 M1 | 400 | 80.8981 | 29.4281 | 18.1878 | 59.8054 | 72.2709 | 27.4161 | 18.9067 | 57.6789
EASO4 M2 | 400 | 80.8981 | 29.4281 | 18.1878 | 59.8054 | 72.2709 | 27.4161 | 18.9067 | 57.6789
EASO4 R1 | 400 | 80.8981 | 29.4281 | 18.1878 | 59.8054 | 72.2709 | 27.4161 | 18.9067 | 57.6789
EASO4 R2 | 400 | 80.8981 | 29.4281 | 18.1878 | 59.8054 | 72.2709 | 27.4161 | 18.9067 | 57.6789
EASO4A | 400 | 80.8981 | 29.4281 | 18.1878 | 59.8054 | 72.2709 | 27.4161 | 18.9067 | 57.6789
EASO4B | 400 | 80.8981 | 29.4281 | 18.1878 | 59.8054 | 72.2709 | 27.4161 | 18.9067 | 57.6789
ECLA1 M1 | 132 | 45.1396 | 16.8996 | 12.9831 | 36.8828 | 47.6428 | 18.5893 | 14.1845 | 40.4737
ECLA1 M2 | 132 | 45.1396 | 16.8996 | 12.9831 | 36.8828 | 47.6428 | 18.5893 | 14.1845 | 40.4737
ECLA1 R1 | 132 | 45.6876 | 17.0502 | 13.0859 | 37.1986 | 54.4148 | 21.029 | 15.7856 | 45.5251
ECLA1 R2 | 132 | 45.6876 | 17.0502 | 13.0859 | 37.1986 | 54.4148 | 21.029 | 15.7856 | 45.5251
ECLA4 M1 | 400 | 111.9773 | 40.7324 | 23.214 | 80.8183 | 90.738 | 35.5808 | 17.2032 | 67.522
ECLA4 M2 | 400 | 111.9773 | 40.7324 | 23.214 | 80.8183 | 90.738 | 35.5808 | 17.2032 | 67.522
ECLA4 R1 | 400 | 111.9773 | 40.7324 | 23.214 | 80.8183 | 90.738 | 35.5808 | 17.2032 | 67.522
ECLA4 R2 | 400 | 111.9773 | 40.7324 | 23.214 | 80.8183 | 90.738 | 35.5808 | 17.2032 | 67.522
EGGB4 M1 | 400 | 102.7189 | 36.6078 | 25.6706 | 77.4418 | 94.1676 | 35.7745 | 20.5394 | 71.1321
EGGB4 M2 | 400 | 102.7189 | 36.6078 | 25.6706 | 77.4418 | 94.1676 | 35.7745 | 20.5394 | 71.1321
EGGB4 R1 | 400 | 93.7696 | 33.2711 | 25.0257 | 72.0782 | 86.2142 | 32.6104 | 19.6152 | 65.7333
EGGB4 R2 | 400 | 93.7696 | 33.2711 | 25.0257 | 72.0782 | 86.2142 | 32.6104 | 19.6152 | 65.7333
ELLA2 MC1 | 275 | 64.3941 | 23.2272 | 8.3602 | 41.2084 | 65.1571 | 25.0823 | 8.0619 | 43.5336
ELLA2 MC2 | 275 | 64.3941 | 23.2272 | 8.3602 | 41.2084 | 65.1571 | 25.0823 | 8.0619 | 43.5336
ELLA2 MC3 | 275 | 64.3941 | 23.2272 | 8.3602 | 41.2084 | 65.1571 | 25.0823 | 8.0619 | 43.5336
ELLA2 MC4 | 275 | 64.3941 | 23.2272 | 8.3602 | 41.2084 | 65.1571 | 25.0823 | 8.0619 | 43.5336
ELST1 M1 | 132 | 31.5885 | 11.4705 | 10.0122 | 26.2339 | 38.6098 | 14.4495 | 12.0381 | 32.4728
ELST1 M2 | 132 | 45.3522 | 16.0669 | 13.4442 | 36.1662 | 56.466 | 21.4459 | 15.791 | 46.1201
ELST1 M3 | 132 | 38.8916 | 14.3468 | 9.6931 | 29.9825 | 45.0913 | 17.2283 | 11.5442 | 35.9087
ELST1 R1 | 132 | 31.5885 | 11.4705 | 10.0122 | 26.2339 | 38.6098 | 14.4495 | 12.0381 | 32.4728
ELST1 R2 | 132 | 45.3522 | 16.0669 | 13.4442 | 36.1662 | 56.466 | 21.4459 | 15.791 | 46.1201
ELST1 R3 | 132 | 38.8916 | 14.3468 | 9.6931 | 29.9825 | 45.0913 | 17.2283 | 11.5442 | 35.9087
ELST2 M1 | 275 | 64.2946 | 23.2521 | 16.415 | 49.2983 | 70.3459 | 26.5166 | 18.258 | 55.7582
ELST2 M2 | 275 | 66.4464 | 24.1716 | 14.6238 | 48.8076 | 72.9833 | 28.0678 | 15.4608 | 55.1546
ELST2 R1 | 275 | 64.2946 | 23.2521 | 16.415 | 49.2983 | 70.3459 | 26.5166 | 18.258 | 55.7582
ELST2 R2 | 275 | 66.4464 | 24.1716 | 14.6238 | 48.8076 | 72.9833 | 28.0678 | 15.4608 | 55.1546
ELST4 M1 | 400 | 89.56 | 32.1627 | 27.7384 | 73.2233 | 106.243 | 40.1704 | 32.2876 | 89.0972
ELST4 R1 | 400 | 89.56 | 32.1627 | 27.7384 | 73.2233 | 106.243 | 40.1704 | 32.2876 | 89.0972
ELST4A | 400 | 56.2135 | 20.6167 | 7.2463 | 36.4027 | 53.5594 | 20.3627 | 8.2811 | 37.0782
ENDE4 MC1 | 400 | 92.2526 | 34.0054 | 18.0953 | 66.1862 | 61.5697 | 24.4946 | 10.6998 | 45.3403
ENDE4 MC2 | 400 | 92.2526 | 34.0054 | 18.0953 | 66.1862 | 61.5697 | 24.4946 | 10.6998 | 45.3403
ENDE4 MC3 | 400 | 92.2526 | 34.0054 | 18.0953 | 66.1862 | 61.5697 | 24.4946 | 10.6998 | 45.3403
ENDE4 MC4 | 400 | 92.2526 | 34.0054 | 18.0953 | 66.1862 | 61.5697 | 24.4946 | 10.6998 | 45.3403
EXET4 M1 | 400 | 58.6786 | 21.4316 | 11.8484 | 42.1572 | 55.2424 | 21.4448 | 11.1997 | 41.5273
EXET4 M2 | 400 | 58.6786 | 21.4316 | 11.8484 | 42.1572 | 55.2424 | 21.4448 | 11.1997 | 41.5273
EXET4 R1 | 400 | 58.6786 | 21.4316 | 11.8484 | 42.1572 | 55.2424 | 21.4448 | 11.1997 | 41.5273
EXET4 R2 | 400 | 58.6786 | 21.4316 | 11.8484 | 42.1572 | 55.2424 | 21.4448 | 11.1997 | 41.5273
FAWL1 M1 | 132 | 50.2126 | 17.6439 | 18.1981 | 43.1503 | 63.8571 | 24.0424 | 21.5264 | 55.5275
FAWL1 M2 | 132 | 50.2126 | 17.6439 | 18.1981 | 43.1503 | 63.8571 | 24.0424 | 21.5264 | 55.5275
FAWL1 R1 | 132 | 50.2126 | 17.6439 | 18.1981 | 43.1503 | 63.8571 | 24.0424 | 21.5264 | 55.5275
FAWL1 R2 | 132 | 50.2126 | 17.6439 | 18.1981 | 43.1503 | 63.8571 | 24.0424 | 21.5264 | 55.5275
FAWL4 M1/3 | 400 | 80.1826 | 28.3715 | 10.4224 | 50.5458 | 66.8118 | 25.7791 | 8.3077 | 44.7649
FAWL4 M1/3(1) | 400 | 80.1826 | 28.3715 | 10.4224 | 50.5458 | 66.8118 | 25.7791 | 8.3077 | 44.7649
FAWL4 M2/4(2) | 400 | 80.1826 | 28.3715 | 10.4224 | 50.5458 | 66.8118 | 25.7791 | 8.3077 | 44.7649
FAWL4 M2/4(3) | 400 | 80.1826 | 28.3715 | 10.4224 | 50.5458 | 66.8118 | 25.7791 | 8.3077 | 44.7649
FAWL4 R1/3 | 400 | 80.1826 | 28.3715 | 10.4224 | 50.5458 | 66.8118 | 25.7791 | 8.3077 | 44.7649
FAWL4 R2/4 | 400 | 80.1826 | 28.3715 | 10.4224 | 50.5458 | 66.8118 | 25.7791 | 8.3077 | 44.7649
FECK2 M1 | 275 | 62.6383 | 23.0743 | 14.3636 | 46.9956 | 61.7707 | 23.8067 | 14.0737 | 47.7414
FECK2 M2 | 275 | 62.6383 | 23.0743 | 14.3636 | 46.9956 | 61.7707 | 23.8067 | 14.0737 | 47.7414
FECK2 R | 275 | 62.6383 | 23.0743 | 14.3636 | 46.9956 | 61.7707 | 23.8067 | 14.0737 | 47.7414
FECK4 M1 | 400 | 79.2381 | 29.7302 | 13.6111 | 55.656 | 66.6543 | 26.3344 | 12.744 | 49.9865
FECK4 M2 | 400 | 79.2381 | 29.7302 | 13.6111 | 55.656 | 66.6543 | 26.3344 | 12.744 | 49.9865
FECK4 R1 | 400 | 79.2381 | 29.7302 | 13.6111 | 55.656 | 66.6543 | 26.3344 | 12.744 | 49.9865
FECK4 R2 | 400 | 79.2381 | 29.7302 | 13.6111 | 55.656 | 66.6543 | 26.3344 | 12.744 | 49.9865
FENW4A | 400 | 110.4701 | 38.6478 | 14.692 | 69.3482 | 94.4142 | 36.0363 | 7.7798 | 58.7429
FERR2 M1 | 275 | 57.8571 | 20.8718 | 11.4578 | 40.975 | 59.1469 | 22.3301 | 11.5654 | 43.1449
FERR2 M2 | 275 | 57.3543 | 20.6388 | 15.2228 | 44.4105 | 61.2655 | 22.9447 | 14.2616 | 46.7103
FERR2 R1 | 275 | 62.4916 | 22.4508 | 12.1778 | 43.928 | 62.4983 | 23.7637 | 10.4251 | 44.0321
FERR2 R2 | 275 | 62.4916 | 22.4508 | 12.1778 | 43.928 | 62.4983 | 23.7637 | 10.4251 | 44.0321
FERR2A | 275 | 57.3762 | 20.5504 | 12.7388 | 41.8014 | 61.0817 | 22.8393 | 11.6877 | 43.9874
FERR2B | 275 | 57.3308 | 20.5406 | 9.2881 | 38.3368 | 58.3619 | 22.0396 | 9.0065 | 40.1752
FERR4A | 400 | 74.8651 | 26.6491 | 9.6172 | 47.3047 | 65.54 | 24.8755 | 8.1406 | 43.3199
FFES2 Term205 | 275 | 36.0144 | 13.4921 | 2.6815 | 21.7622 | 34.8152 | 13.6785 | 2.3403 | 21.6846
FFES2 Term210 | 275 | 35.8521 | 13.4515 | 2.6555 | 21.6789 | 35.1992 | 13.8266 | 2.3577 | 21.9115
FIDF2 M1 | 275 | 51.4298 | 18.4487 | 15.8012 | 41.8915 | 51.5286 | 19.2245 | 14.2813 | 41.4688
FIDF2 M2 | 275 | 50.6683 | 18.1416 | 15.6262 | 41.2823 | 49.6846 | 18.5357 | 13.546 | 39.7595
FIDF2 M3 | 275 | 63.1642 | 22.6327 | 16.2505 | 48.2579 | 59.2557 | 22.4518 | 13.7404 | 45.492
FIDF2 M4 | 275 | 63.7131 | 22.8254 | 16.3844 | 48.6644 | 61.227 | 23.1664 | 14.394 | 47.1563
FIDF2 R1 | 275 | 51.4298 | 18.4487 | 15.8012 | 41.8915 | 51.5286 | 19.2245 | 14.2813 | 41.4688
FIDF2 R2 | 275 | 63.7131 | 22.8254 | 16.3844 | 48.6644 | 61.227 | 23.1664 | 14.394 | 47.1563
FLEE4 MC1 | 400 | 104.2629 | 37.4678 | 20.9636 | 73.9511 | 83.7138 | 32.8799 | 15.5723 | 62.0715
FLEE4 MC2 | 400 | 104.2629 | 37.4678 | 20.9636 | 73.9511 | 83.7138 | 32.8799 | 15.5723 | 62.0715
FLEE4 MC3 | 400 | 104.2629 | 37.4678 | 20.9636 | 73.9511 | 83.7138 | 32.8799 | 15.5723 | 62.0715
FLEE4 MC4 | 400 | 104.2629 | 37.4678 | 20.9636 | 73.9511 | 83.7138 | 32.8799 | 15.5723 | 62.0715
FLIB4 M1 | 400 | 121.9643 | 42.6566 | 31.7827 | 92.1082 | 124.0656 | 46.6706 | 30.6373 | 96.6395
FLIB4 M2 | 400 | 121.9643 | 42.6566 | 31.7827 | 92.1082 | 124.0656 | 46.6706 | 30.6373 | 96.6395
FOUR2 MC1 | 275 | 38.9664 | 15.3022 | 4.9501 | 26.5908 | 31.9223 | 13.1174 | 3.9039 | 22.4547
FOUR2 MC2 | 275 | 38.9664 | 15.3022 | 4.9501 | 26.5908 | 31.9223 | 13.1174 | 3.9039 | 22.4547
FROD2 MC1 | 275 | 51.4051 | 18.39 | 16.6208 | 42.6283 | 54.6859 | 20.106 | 17.7591 | 46.1934
FROD2 MC3 | 275 | 51.406 | 18.1518 | 10.9805 | 36.651 | 54.0131 | 19.8199 | 10.8751 | 38.9047
FROD4 M1 | 400 | 91.2204 | 32.9107 | 30.5179 | 77.0608 | 85.3468 | 32.1377 | 28.3969 | 73.8465
FROD4 R1 | 400 | 91.2204 | 32.9107 | 30.5179 | 77.0608 | 85.3468 | 32.1377 | 28.3969 | 73.8465
GART4A | 400 | 102.8145 | 35.8201 | 14.5914 | 65.2487 | 82.2005 | 31.3719 | 7.0275 | 51.3941
GART4B | 400 | 105.5128 | 36.8303 | 14.7049 | 66.7908 | 89.114 | 33.9761 | 8.2318 | 56.2812
GRAI4 M1 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 M2 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 M3 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 M4 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 M5 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 M6 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 M7 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 R1/2 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 R3 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 R4 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 R5 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 R6 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GRAI4 R7 | 400 | 134.1737 | 46.989 | 43.031 | 109.4835 | 125.7871 | 47.2992 | 40.1598 | 107.0509
GREN1 M1 | 132 | 40.5284 | 14.8472 | 10.4806 | 31.4777 | 44.3604 | 17.6911 | 10.3089 | 35.3279
GREN1 M2 | 132 | 39.0504 | 14.4076 | 10.9893 | 31.3647 | 39.9246 | 15.6872 | 10.162 | 32.3471
GREN1 R1 | 132 | 40.5284 | 14.8472 | 10.4806 | 31.4777 | 44.3604 | 17.6911 | 10.3089 | 35.3279
GREN1 R2 | 132 | 39.0504 | 14.4076 | 10.9893 | 31.3647 | 39.9246 | 15.6872 | 10.162 | 32.3471
GREN4 M1 | 400 | 79.2881 | 29.7298 | 13.0235 | 55.0679 | 53.563 | 21.7267 | 8.9065 | 39.6327
GREN4 M2 | 400 | 79.2881 | 29.7298 | 13.0235 | 55.0679 | 53.563 | 21.7267 | 8.9065 | 39.6327
GREN4 R1 | 400 | 79.2881 | 29.7298 | 13.0235 | 55.0679 | 53.563 | 21.7267 | 8.9065 | 39.6327
GREN4 R2 | 400 | 79.2881 | 29.7298 | 13.0235 | 55.0679 | 53.563 | 21.7267 | 8.9065 | 39.6327
GRIW4 MC1 | 400 | 69.4543 | 24.9287 | 18.5049 | 53.7594 | 59.4262 | 22.8297 | 12.1626 | 44.4488
GRIW4 MC2 | 400 | 69.4543 | 24.9287 | 18.5049 | 53.7594 | 59.4262 | 22.8297 | 12.1626 | 44.4488
GRSA2 M1 | 275 | 55.4868 | 19.8967 | 16.738 | 44.8761 | 57.7781 | 21.5047 | 16.0872 | 46.4995
GRSA2 M2 | 275 | 55.4868 | 19.8967 | 16.738 | 44.8761 | 57.7781 | 21.5047 | 16.0872 | 46.4995
GRSA2 R1 | 275 | 55.4868 | 19.8967 | 16.738 | 44.8761 | 57.7781 | 21.5047 | 16.0872 | 46.4995
GRSA2 R2 | 275 | 55.4868 | 19.8967 | 16.738 | 44.8761 | 57.7781 | 21.5047 | 16.0872 | 46.4995
GRSB2 M3 | 275 | 55.8291 | 20.0054 | 16.93 | 45.2219 | 58.7121 | 21.7923 | 16.7984 | 47.6173
GRSB2 M4 | 275 | 55.8291 | 20.0054 | 16.93 | 45.2219 | 58.7121 | 21.7923 | 16.7984 | 47.6173
GRSB2 R3 | 275 | 55.8291 | 20.0054 | 16.93 | 45.2219 | 58.7121 | 21.7923 | 16.7984 | 47.6173
GRSB2 R4 | 275 | 55.8291 | 20.0054 | 16.93 | 45.2219 | 58.7121 | 21.7923 | 16.7984 | 47.6173
HACK2A | 275 | 66.8976 | 23.5231 | 11.5208 | 44.7876 | 68.8905 | 25.656 | 11.9014 | 48.1844
HACK2B | 275 | 65.814 | 23.1589 | 11.5065 | 44.2582 | 68.4307 | 25.4744 | 11.8393 | 47.8656
HACK4 M1 | 400 | 115.9624 | 39.083 | 27.2153 | 82.487 | 132.7967 | 49.2029 | 28.8501 | 98.4336
HACK4 M2 | 400 | 115.9624 | 39.083 | 27.2153 | 82.487 | 132.7967 | 49.2029 | 28.8501 | 98.4336
HACK4 R1 | 400 | 115.9624 | 39.083 | 27.2153 | 82.487 | 132.7967 | 49.2029 | 28.8501 | 98.4336
HACK4 R2 | 400 | 115.9624 | 39.083 | 27.2153 | 82.487 | 132.7967 | 49.2029 | 28.8501 | 98.4336
HAMB4A | 400 | 70.276 | 25.0146 | 9.2528 | 44.6288 | 58.6107 | 22.7718 | 4.7919 | 36.9961
HAMB4A_HEYS | 400 | 70.276 | 25.0146 | 9.2528 | 44.6288 | 58.6107 | 22.7718 | 4.7919 | 36.9961
HAMB4A_PEWO | 400 | 70.276 | 25.0146 | 9.2528 | 44.6288 | 58.6107 | 22.7718 | 4.7919 | 36.9961
HAMB4B | 400 | 70.2512 | 25.0059 | 9.2526 | 44.6164 | 58.1369 | 22.5871 | 4.7973 | 36.7402
HAMB4B_HEYS | 400 | 70.2512 | 25.0059 | 9.2526 | 44.6164 | 58.1369 | 22.5871 | 4.7973 | 36.7402
HAMB4B_PEWO | 400 | 70.2512 | 25.0059 | 9.2526 | 44.6164 | 58.1369 | 22.5871 | 4.7973 | 36.7402
HAMH1B | 132 | 46.3261 | 16.0066 | 9.9904 | 32.6272 | 55.3816 | 20.8851 | 6.4976 | 36.0336
HAMH1C | 132 | 45.3467 | 15.7783 | 8.7329 | 31.0468 | 53.6223 | 19.939 | 8.1018 | 36.2998
HAMH4 M1 | 400 | 77.4933 | 28.7815 | 14.139 | 54.8423 | 72.5243 | 28.2848 | 14.1016 | 54.1024
HAMH4 M2 | 400 | 77.4933 | 28.7815 | 14.139 | 54.8423 | 72.5243 | 28.2848 | 14.1016 | 54.1024
HAMH4 R1 | 400 | 77.4933 | 28.7815 | 14.139 | 54.8423 | 72.5243 | 28.2848 | 14.1016 | 54.1024
HAMH4 R2 | 400 | 77.4933 | 28.7815 | 14.139 | 54.8423 | 72.5243 | 28.2848 | 14.1016 | 54.1024
HARK1 M1 | 132 | 27.6031 | 10.3383 | 7.0101 | 21.6307 | 32.6561 | 12.7143 | 7.6763 | 25.657
HARK1 M2 | 132 | 27.6031 | 10.3383 | 7.0101 | 21.6307 | 32.6561 | 12.7143 | 7.6763 | 25.657
HARK1 R1 | 132 | 27.2038 | 11.2119 | 6.8709 | 22.7269 | 30.5118 | 12.7358 | 7.9786 | 25.9897
HARK1 R2 | 132 | 30.1633 | 11.4861 | 7.7899 | 24.0337 | 35.3323 | 13.9741 | 9.048 | 28.8104
HARK1 R3 | 132 | 30.1633 | 11.4861 | 7.7899 | 24.0337 | 35.3323 | 13.9741 | 9.048 | 28.8104
HARK2 MC1 | 275 | 41.2036 | 15.4426 | 10.6058 | 32.4448 | 43.611 | 16.696 | 11.3116 | 34.9234
HARK2 MC11 | 275 | 38.5198 | 14.6886 | 11.8098 | 32.5825 | 40.4479 | 15.5811 | 12.9994 | 35.0344
HARK2 MC12 | 275 | 38.5198 | 14.6886 | 11.8098 | 32.5825 | 40.4479 | 15.5811 | 12.9994 | 35.0344
HARK2 MC13 | 275 | 38.5198 | 14.6886 | 11.8098 | 32.5825 | 40.4479 | 15.5811 | 12.9994 | 35.0344
HARK2 MC2 | 275 | 41.2036 | 15.4426 | 10.6058 | 32.4448 | 43.611 | 16.696 | 11.3116 | 34.9234
HARK2 MC3 | 275 | 41.2036 | 15.4426 | 10.6058 | 32.4448 | 43.611 | 16.696 | 11.3116 | 34.9234
HARK2 MC4 | 275 | 41.2036 | 15.4426 | 10.6058 | 32.4448 | 43.611 | 16.696 | 11.3116 | 34.9234
HARK2 MC6 | 275 | 41.2036 | 15.4426 | 10.6058 | 32.4448 | 43.611 | 16.696 | 11.3116 | 34.9234
HARK2 MC8 | 275 | 38.5198 | 14.6886 | 11.8098 | 32.5825 | 40.4479 | 15.5811 | 12.9994 | 35.0344
HARK2 MC9 | 275 | 38.5198 | 14.6886 | 11.8098 | 32.5825 | 40.4479 | 15.5811 | 12.9994 | 35.0344
HARK4 M1 | 400 | 70.5411 | 26.4488 | 12.0755 | 49.4797 | 55.0845 | 21.5779 | 11.4203 | 41.936
HARK4 M2 | 400 | 70.5411 | 26.4488 | 12.0755 | 49.4797 | 55.0845 | 21.5779 | 11.4203 | 41.936
HARK4 R1 | 400 | 70.5411 | 26.4488 | 12.0755 | 49.4797 | 55.0845 | 21.5779 | 11.4203 | 41.936
HARK4 R2 | 400 | 70.5411 | 26.4488 | 12.0755 | 49.4797 | 55.0845 | 21.5779 | 11.4203 | 41.936
HARM2 MC1 | 275 | 66.3789 | 23.836 | 14.7063 | 48.4155 | 57.2482 | 22.3319 | 9.6453 | 41.2274
HARM2 MC2 | 275 | 66.3789 | 23.836 | 14.7063 | 48.4155 | 57.2482 | 22.3319 | 9.6453 | 41.2274
HARM2 MC3 | 275 | 66.3789 | 23.836 | 14.7063 | 48.4155 | 57.2482 | 22.3319 | 9.6453 | 41.2274
HARM2 MC4 | 275 | 66.3789 | 23.836 | 14.7063 | 48.4155 | 57.2482 | 22.3319 | 9.6453 | 41.2274
HATL2 M1 | 275 | 91.7907 | 31.765 | 24.6665 | 69.589 | 93.1922 | 34.5139 | 25.6748 | 74.4849
HATL2 M2 | 275 | 91.7907 | 31.765 | 24.6665 | 69.589 | 93.1922 | 34.5139 | 25.6748 | 74.4849
HATL2 R1 | 275 | 91.7907 | 31.765 | 24.6665 | 69.589 | 93.1922 | 34.5139 | 25.6748 | 74.4849
HATL2 R2 | 275 | 91.7907 | 31.765 | 24.6665 | 69.589 | 93.1922 | 34.5139 | 25.6748 | 74.4849
HAWP2 MC1 | 275 | 88.9304 | 31.2475 | 21.3257 | 65.5164 | 77.7883 | 30.1352 | 14.0464 | 56.664
HAWP2 MC2 | 275 | 88.9304 | 31.2475 | 21.3257 | 65.5164 | 77.7883 | 30.1352 | 14.0464 | 56.664
HAWP2 MC3 | 275 | 88.9304 | 31.2475 | 21.3257 | 65.5164 | 77.7883 | 30.1352 | 14.0464 | 56.664
HAWP2 MC4 | 275 | 88.9304 | 31.2475 | 21.3257 | 65.5164 | 77.7883 | 30.1352 | 14.0464 | 56.664
HEDO2 M1 | 275 | 74.1205 | 26.1078 | 21.8839 | 58.8059 | 77.0005 | 28.4112 | 23.1337 | 63.3132
HEDO2 M2 | 275 | 74.1205 | 26.1078 | 21.8839 | 58.8059 | 77.0005 | 28.4112 | 23.1337 | 63.3132
HEDO2 R1 | 275 | 74.1205 | 26.1078 | 21.8839 | 58.8059 | 77.0005 | 28.4112 | 23.1337 | 63.3132
HEDO2 R2 | 275 | 74.1205 | 26.1078 | 21.8839 | 58.8059 | 77.0005 | 28.4112 | 23.1337 | 63.3132
HEYS1 M1 | 132 | 38.5385 | 13.0344 | 12.5896 | 31.023 | 44.447 | 16.2197 | 14.304 | 37.2421
HEYS1 M2 | 132 | 38.5385 | 13.0344 | 12.5896 | 31.023 | 44.447 | 16.2197 | 14.304 | 37.2421
HEYS1 R1 | 132 | 38.5385 | 13.0344 | 12.5896 | 31.023 | 44.447 | 16.2197 | 14.304 | 37.2421
HEYS1 R2 | 132 | 38.5385 | 13.0344 | 12.5896 | 31.023 | 44.447 | 16.2197 | 14.304 | 37.2421
HEYS4 M1 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 M2 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 M3 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 M4 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 M5 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 R1/2 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 R3/4 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HEYS4 R5 | 400 | 99.1107 | 35.6665 | 33.4812 | 83.9212 | 102.8853 | 38.7745 | 35.2699 | 90.1053
HIBU4 M1 | 400 | 113.016 | 38.079 | 26.7577 | 80.6095 | 130.8889 | 48.3172 | 29.4487 | 97.7796
HIBU4 M2 | 400 | 113.016 | 38.079 | 26.7577 | 80.6095 | 130.8889 | 48.3172 | 29.4487 | 97.7796
HIBU4 R1 | 400 | 113.016 | 38.079 | 26.7577 | 80.6095 | 130.8889 | 48.3172 | 29.4487 | 97.7796
HIBU4 R2 | 400 | 113.016 | 38.079 | 26.7577 | 80.6095 | 130.8889 | 48.3172 | 29.4487 | 97.7796
HIGM2 M1 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM2 M2 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM2 M3 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM2 R1 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM2 R4 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM2 R5 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM2 R6 | 275 | 61.9936 | 22.9956 | 16.6102 | 49.1309 | 57.314 | 22.6033 | 12.3094 | 44.2753
HIGM4 MC1 | 400 | 80.7686 | 29.7742 | 18.5298 | 60.6369 | 66.4947 | 26.062 | 11.5865 | 48.4438
HIGM4 MC2 | 400 | 80.7686 | 29.7742 | 18.5298 | 60.6369 | 66.4947 | 26.062 | 11.5865 | 48.4438
HIGM4A | 400 | 64.9264 | 23.742 | 9.4343 | 43.0105 | 54.9751 | 21.2528 | 5.0201 | 35.0762
HINP2 M1 | 275 | 23.4016 | 8.3624 | 7.8725 | 19.6988 | 25.1913 | 9.2606 | 8.3087 | 21.4052
HINP2 M2 | 275 | 23.7684 | 8.5022 | 7.9174 | 19.9414 | 27.9112 | 10.3092 | 8.7317 | 23.3111
HINP4 M1 | 400 | 69.2701 | 25.0586 | 15.763 | 51.2012 | 68.181 | 25.886 | 17.7426 | 54.3508
HINP4 M2 | 400 | 69.2701 | 25.0586 | 15.763 | 51.2012 | 68.181 | 25.886 | 17.7426 | 54.3508
HINP4 M3 | 400 | 69.2701 | 25.0586 | 15.763 | 51.2012 | 68.181 | 25.886 | 17.7426 | 54.3508
HINP4 M4 | 400 | 69.2701 | 25.0586 | 15.763 | 51.2012 | 68.181 | 25.886 | 17.7426 | 54.3508
HINP4 R1/2 | 400 | 69.2701 | 25.0586 | 15.763 | 51.2012 | 68.181 | 25.886 | 17.7426 | 54.3508
HINP4 R3/4 | 400 | 69.2701 | 25.0586 | 15.763 | 51.2012 | 68.181 | 25.886 | 17.7426 | 54.3508
HUMR4 M1 | 400 | 103.4971 | 35.8866 | 29.7125 | 80.4638 | 97.588 | 36.1684 | 27.1018 | 78.2516
HUMR4 M2 | 400 | 103.4971 | 35.8866 | 29.7125 | 80.4638 | 97.588 | 36.1684 | 27.1018 | 78.2516
HUMR4 R1 | 400 | 103.4971 | 35.8866 | 29.7125 | 80.4638 | 97.588 | 36.1684 | 27.1018 | 78.2516
HUMR4 R2 | 400 | 103.4971 | 35.8866 | 29.7125 | 80.4638 | 97.588 | 36.1684 | 27.1018 | 78.2516
HURS2 MC1 | 275 | 70.2319 | 24.4915 | 18.8818 | 53.518 | 74.2096 | 29.3465 | 16.1817 | 57.6839
HURS2 MC2 | 275 | 70.2319 | 24.4915 | 18.8818 | 53.518 | 74.2096 | 29.3465 | 16.1817 | 57.6839
HURS2 MC3 | 275 | 70.2319 | 24.4915 | 18.8818 | 53.518 | 74.2096 | 29.3465 | 16.1817 | 57.6839
HURS2 MC4 | 275 | 70.2319 | 24.4915 | 18.8818 | 53.518 | 74.2096 | 29.3465 | 16.1817 | 57.6839
HUTT4 MC1 | 400 | 72.9901 | 27.4081 | 21.1777 | 59.9386 | 48.0738 | 19.4727 | 11.2312 | 38.7698
HUTT4 MC2 | 400 | 72.9901 | 27.4081 | 21.1777 | 59.9386 | 48.0738 | 19.4727 | 11.2312 | 38.7698
HUTT4 MC3 | 400 | 72.9901 | 27.4081 | 21.1777 | 59.9386 | 48.0738 | 19.4727 | 11.2312 | 38.7698
HUTT4 MC4 | 400 | 72.9901 | 27.4081 | 21.1777 | 59.9386 | 48.0738 | 19.4727 | 11.2312 | 38.7698
IMPP4 MC1 | 400 | 54.5255 | 20.1692 | 12.1001 | 40.6236 | 46.5851 | 18.0139 | 9.6503 | 35.1258
IMPP4 MC2 | 400 | 54.5255 | 20.1692 | 12.1001 | 40.6236 | 46.5851 | 18.0139 | 9.6503 | 35.1258
INDQ4 MC1 | 400 | 36.0068 | 13.5326 | 6.0706 | 25.2086 | 37.6029 | 14.6147 | 7.2968 | 27.9651
INDQ4 MC2 | 400 | 36.0068 | 13.5326 | 6.0706 | 25.2086 | 37.6029 | 14.6147 | 7.2968 | 27.9651
INDQ4 MC3 | 400 | 36.0068 | 13.5326 | 6.0706 | 25.2086 | 37.6029 | 14.6147 | 7.2968 | 27.9651
INDQ4 MC4 | 400 | 36.0068 | 13.5326 | 6.0706 | 25.2086 | 37.6029 | 14.6147 | 7.2968 | 27.9651
IROA1 M1 | 132 | 49.1274 | 17.9821 | 10.7408 | 36.1713 | 58.3539 | 22.5397 | 12.0897 | 43.9655
IROA1 M2 | 132 | 49.1274 | 17.9821 | 10.7408 | 36.1713 | 58.3539 | 22.5397 | 12.0897 | 43.9655
IROA1 R1 | 132 | 44.7416 | 16.2184 | 10.8086 | 33.7449 | 53.6333 | 20.4284 | 12.3967 | 41.2869
IROA1 R2 | 132 | 42.4245 | 15.9421 | 9.77 | 32.3154 | 48.67 | 19.1228 | 10.5797 | 37.6234
IROA2 MC1 | 275 | 58.1352 | 21.399 | 11.1578 | 41.4206 | 56.2925 | 21.8726 | 11.2254 | 42.1579
IROA2 MC2 | 275 | 58.1352 | 21.399 | 11.1578 | 41.4206 | 56.2925 | 21.8726 | 11.2254 | 42.1579
IROA2 MC3 | 275 | 58.1352 | 21.399 | 11.1578 | 41.4206 | 56.2925 | 21.8726 | 11.2254 | 42.1579
IROA2 MC4 | 275 | 58.1352 | 21.399 | 11.1578 | 41.4206 | 56.2925 | 21.8726 | 11.2254 | 42.1579
IROA2 MC5 | 275 | 58.1352 | 21.399 | 11.1578 | 41.4206 | 56.2925 | 21.8726 | 11.2254 | 42.1579
IRON1 M1 | 132 | 27.2917 | 10.5878 | 8.9486 | 23.922 | 30.3078 | 11.8888 | 9.9365 | 26.7498
IRON1 M2 | 132 | 27.1712 | 10.545 | 8.8506 | 23.7635 | 29.9812 | 11.7764 | 9.7471 | 26.4013
IRON1 R1 | 132 | 17.839 | 6.4872 | 6.3823 | 15.5566 | 20.3617 | 7.4426 | 7.372 | 17.8974
IRON1 R2 | 132 | 17.839 | 6.4872 | 6.3823 | 15.5566 | 20.3617 | 7.4426 | 7.372 | 17.8974
IRON4 M1 | 400 | 72.5309 | 26.9557 | 13.4827 | 51.6038 | 60.8105 | 24.0203 | 11.0314 | 45.0012
IRON4 M2 | 400 | 72.5309 | 26.9557 | 13.4827 | 51.6038 | 60.8105 | 24.0203 | 11.0314 | 45.0012
IRON4 R1 | 400 | 72.5309 | 26.9557 | 13.4827 | 51.6038 | 60.8105 | 24.0203 | 11.0314 | 45.0012
IRON4 R2 | 400 | 72.5309 | 26.9557 | 13.4827 | 51.6038 | 60.8105 | 24.0203 | 11.0314 | 45.0012
IVER2 M1 | 275 | 65.6609 | 23.9618 | 16.3574 | 50.2445 | 70.5944 | 26.904 | 16.8811 | 54.9292
IVER2 M2 | 275 | 65.6609 | 23.9618 | 16.3574 | 50.2445 | 70.5944 | 26.904 | 16.8811 | 54.9292
IVER2 R1 | 275 | 65.6609 | 23.9618 | 16.3574 | 50.2445 | 70.5944 | 26.904 | 16.8811 | 54.9292
IVER2 R2 | 275 | 67.9728 | 24.701 | 15.484 | 50.4164 | 68.3761 | 26.4085 | 14.3129 | 51.6602
IVER4A | 400 | 45.9646 | 16.8918 | 5.6683 | 29.557 | 43.5841 | 16.7047 | 5.9231 | 29.5471
IVER4B | 400 | 44.2079 | 16.3106 | 5.2848 | 28.3515 | 41.3681 | 16.0835 | 5.0673 | 27.8127
JORD2 MC1 | 275 | 50.3293 | 18.9963 | 8.8913 | 35.7561 | 49.8526 | 20.6014 | 7.4089 | 36.5437
JORD2 MC2 | 275 | 50.3293 | 18.9963 | 8.8913 | 35.7561 | 49.8526 | 20.6014 | 7.4089 | 36.5437
KEAD4 M2 | 400 | 103.8117 | 37.1148 | 26.6409 | 79.1291 | 93.3407 | 35.437 | 22.0202 | 72.1357
KEAD4 M3 | 400 | 103.0782 | 36.6783 | 27.2129 | 79.0839 | 85.8939 | 32.7013 | 19.1435 | 65.3901
KEAD4 R2 | 400 | 103.8117 | 37.1148 | 26.6409 | 79.1291 | 93.3407 | 35.437 | 22.0202 | 72.1357
KEAD4 R3 | 400 | 95.3415 | 34.7857 | 22.1047 | 71.2991 | 74.6722 | 29.0183 | 15.974 | 57.0121
KEAR2 M1 | 275 | 75.1485 | 27.0267 | 19.1475 | 57.369 | 80.8688 | 30.5832 | 19.8777 | 63.1289
KEAR2 M2 | 275 | 75.1485 | 27.0267 | 19.1475 | 57.369 | 80.8688 | 30.5832 | 19.8777 | 63.1289
KEAR2 R1 | 275 | 75.1485 | 27.0267 | 19.1475 | 57.369 | 80.8688 | 30.5832 | 19.8777 | 63.1289
KEAR2 R2 | 275 | 75.1485 | 27.0267 | 19.1475 | 57.369 | 80.8688 | 30.5832 | 19.8777 | 63.1289
KEMS4 M1 | 400 | 127.602 | 43.6055 | 29.8571 | 91.5246 | 110.2016 | 42.0813 | 21.886 | 81.3979
KEMS4 M2 | 400 | 127.602 | 43.6055 | 29.8571 | 91.5246 | 110.2016 | 42.0813 | 21.886 | 81.3979
KEMS4 R1 | 400 | 127.602 | 43.6055 | 29.8571 | 91.5246 | 110.2016 | 42.0813 | 21.886 | 81.3979
KEMS4 R2 | 400 | 127.602 | 43.6055 | 29.8571 | 91.5246 | 110.2016 | 42.0813 | 21.886 | 81.3979
KENG4 M1 | 400 | 107.3603 | 36.2122 | 26.1897 | 77.4015 | 124.8655 | 46.147 | 28.7144 | 93.976
KENG4 M2 | 400 | 107.3603 | 36.2122 | 26.1897 | 77.4015 | 124.8655 | 46.147 | 28.7144 | 93.976
KENG4 R1 | 400 | 107.3603 | 36.2122 | 26.1897 | 77.4015 | 124.8655 | 46.147 | 28.7144 | 93.976
KENG4 R2 | 400 | 107.3603 | 36.2122 | 26.1897 | 77.4015 | 124.8655 | 46.147 | 28.7144 | 93.976
KIBY2 M1 | 275 | 72.7174 | 25.7536 | 18.0761 | 54.4972 | 76.7987 | 29.0102 | 17.2442 | 58.2708
KIBY2 M2 | 275 | 72.7174 | 25.7536 | 18.0761 | 54.4972 | 76.7987 | 29.0102 | 17.2442 | 58.2708
KIBY2 R1 | 275 | 62.7406 | 22.5937 | 15.0638 | 47.0161 | 61.2691 | 23.2732 | 13.8062 | 46.7194
KIBY2 R2 | 275 | 62.7406 | 22.5937 | 15.0638 | 47.0161 | 61.2691 | 23.2732 | 13.8062 | 46.7194
KILL4 M1 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 M2 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 M3 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 M4 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 M5 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 M9 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 R1/2 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 R3/4 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 R5 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KILL4 R9 | 400 | 110.1431 | 38.8465 | 39.7676 | 94.7048 | 106.6365 | 39.6486 | 36.9533 | 93.0249
KINO1 M1 | 132 | 29.3341 | 10.3327 | 10.5626 | 25.1752 | 35.8934 | 13.2756 | 12.7565 | 31.5311
KINO1 M2 | 132 | 29.3341 | 10.3327 | 10.5626 | 25.1752 | 35.8934 | 13.2756 | 12.7565 | 31.5311
KINO1 R1 | 132 | 29.3341 | 10.3327 | 10.5626 | 25.1752 | 35.8934 | 13.2756 | 12.7565 | 31.5311
KINO1 R2 | 132 | 29.3341 | 10.3327 | 10.5626 | 25.1752 | 35.8934 | 13.2756 | 12.7565 | 31.5311
KINO1A | 132 | 28.986 | 10.13 | 6.5166 | 20.8425 | 35.3772 | 13.1176 | 7.7082 | 26.2592
KINO1B | 132 | 24.2072 | 9.0176 | 1.616 | 14.3688 | 26.0381 | 10.5104 | 0.91701 | 15.781
KINO4 M1 | 400 | 121.7589 | 43.0641 | 38.643 | 99.5448 | 114.9605 | 43.6566 | 34.8548 | 96.5945
KINO4 M2 | 400 | 121.7589 | 43.0641 | 38.643 | 99.5448 | 114.9605 | 43.6566 | 34.8548 | 96.5945
KINO4 M3 | 400 | 121.7589 | 43.0641 | 38.643 | 99.5448 | 114.9605 | 43.6566 | 34.8548 | 96.5945
KINO4 M4 | 400 | 121.7589 | 43.0641 | 38.643 | 99.5448 | 114.9605 | 43.6566 | 34.8548 | 96.5945
KINO4 R1/2 | 400 | 121.7589 | 43.0641 | 38.643 | 99.5448 | 114.9605 | 43.6566 | 34.8548 | 96.5945
KINO4 R3/4 | 400 | 121.7589 | 43.0641 | 38.643 | 99.5448 | 114.9605 | 43.6566 | 34.8548 | 96.5945
KIRK2 MC1 | 275 | 53.8624 | 19.5694 | 12.1512 | 39.8265 | 55.0268 | 21.157 | 13.1156 | 43.0361
KIRK2 MC2 | 275 | 53.8624 | 19.5694 | 12.1512 | 39.8265 | 55.0268 | 21.157 | 13.1156 | 43.0361
KIRK2 MC3 | 275 | 53.8624 | 19.5694 | 12.1512 | 39.8265 | 55.0268 | 21.157 | 13.1156 | 43.0361
KIRK2 MC4 | 275 | 53.8624 | 19.5694 | 12.1512 | 39.8265 | 55.0268 | 21.157 | 13.1156 | 43.0361
KIRK2A | 275 | 53.4256 | 18.9266 | 6.4541 | 33.2203 | 51.2314 | 20.0293 | 8.1308 | 36.4565
KITW2 MC1 | 275 | 61.8253 | 22.5717 | 12.2269 | 44.148 | 60.5042 | 23.6391 | 10.6469 | 44.0777
KITW2 MC2 | 275 | 61.8253 | 22.5717 | 12.2269 | 44.148 | 60.5042 | 23.6391 | 10.6469 | 44.0777
KITW2 MC3 | 275 | 61.8253 | 22.5717 | 12.2269 | 44.148 | 60.5042 | 23.6391 | 10.6469 | 44.0777
KITW2 MC4 | 275 | 61.8253 | 22.5717 | 12.2269 | 44.148 | 60.5042 | 23.6391 | 10.6469 | 44.0777
KNAR2 MC1 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
KNAR2 MC1 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
KNAR2 MC1 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
KNAR2 MC1 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
KNAR2 MC2 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
KNAR2 MC2 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
KNAR2 MC2 | 275 | 29.345 | 11.8324 | 2.4885 | 19.222 | 26.9002 | 11.1196 | 3.5746 | 19.3001
LACK2 M1 | 275 | 63.93 | 22.1162 | 17.9213 | 49.1983 | 68.3342 | 25.113 | 19.7646 | 55.2798
LACK2 M2 | 275 | 63.93 | 22.1162 | 17.9213 | 49.1983 | 68.3342 | 25.113 | 19.7646 | 55.2798
LACK2 R1 | 275 | 63.93 | 22.1162 | 17.9213 | 49.1983 | 68.3342 | 25.113 | 19.7646 | 55.2798
LACK2 R2 | 275 | 63.93 | 22.1162 | 17.9213 | 49.1983 | 68.3342 | 25.113 | 19.7646 | 55.2798
LACK4 M1 | 400 | 75.0517 | 27.5375 | 23.5583 | 62.5022 | 67.8352 | 25.8587 | 21.5289 | 58.0986
LACK4 M2 | 400 | 75.0517 | 27.5375 | 23.5583 | 62.5022 | 67.8352 | 25.8587 | 21.5289 | 58.0986
LACK4 R1 | 400 | 75.0517 | 27.5375 | 23.5583 | 62.5022 | 67.8352 | 25.8587 | 21.5289 | 58.0986
LACK4 R2 | 400 | 75.0517 | 27.5375 | 23.5583 | 62.5022 | 67.8352 | 25.8587 | 21.5289 | 58.0986
LAGA4 M1 | 400 | 42.9331 | 15.7707 | 8.887 | 31.1901 | 44.1401 | 16.9343 | 10.0502 | 33.9989
LAGA4 M2 | 400 | 42.9331 | 15.7707 | 8.887 | 31.1901 | 44.1401 | 16.9343 | 10.0502 | 33.9989
LAGA4 R1 | 400 | 42.9331 | 15.7707 | 8.887 | 31.1901 | 44.1401 | 16.9343 | 10.0502 | 33.9989
LAGA4 R2 | 400 | 42.9331 | 15.7707 | 8.887 | 31.1901 | 44.1401 | 16.9343 | 10.0502 | 33.9989
LALE2 MC1 | 275 | 60.9649 | 21.6878 | 17.2953 | 47.9665 | 66.9713 | 25.8478 | 16.5388 | 53.0931
LALE2 MC2 | 275 | 60.9649 | 21.6878 | 17.2953 | 47.9665 | 66.9713 | 25.8478 | 16.5388 | 53.0931
LALE2 MC3 | 275 | 60.9649 | 21.6878 | 17.2953 | 47.9665 | 66.9713 | 25.8478 | 16.5388 | 53.0931
LALE2 MC4 | 275 | 60.9649 | 21.6878 | 17.2953 | 47.9665 | 66.9713 | 25.8478 | 16.5388 | 53.0931
LAND4 MC1 | 400 | 34.4684 | 12.8787 | 6.5007 | 24.7139 | 33.7389 | 13.1936 | 6.1128 | 24.7714
LAND4 MC2 | 400 | 34.4684 | 12.8787 | 6.5007 | 24.7139 | 33.7389 | 13.1936 | 6.1128 | 24.7714
LEGA4 M1 | 400 | 91.855 | 33.2698 | 20.2649 | 67.3156 | 69.8068 | 27.6076 | 12.5997 | 51.6427
LEGA4 M2 | 400 | 91.855 | 33.2698 | 20.2649 | 67.3156 | 69.8068 | 27.6076 | 12.5997 | 51.6427
LEGA4 R1 | 400 | 91.855 | 33.2698 | 20.2649 | 67.3156 | 69.8068 | 27.6076 | 12.5997 | 51.6427
LEGA4 R2 | 400 | 91.855 | 33.2698 | 20.2649 | 67.3156 | 69.8068 | 27.6076 | 12.5997 | 51.6427
LEIS1 M1 | 132 | 64.8912 | 22.9475 | 21.1442 | 53.5968 | 74.835 | 27.1834 | 26.2924 | 64.7354
LEIS1 M2 | 132 | 64.8912 | 22.9475 | 21.1442 | 53.5968 | 74.835 | 27.1834 | 26.2924 | 64.7354
LEIS1 R1 | 132 | 64.8912 | 22.9475 | 21.1442 | 53.5968 | 74.835 | 27.1834 | 26.2924 | 64.7354
LEIS1 R2 | 132 | 64.8912 | 22.9475 | 21.1442 | 53.5968 | 74.835 | 27.1834 | 26.2924 | 64.7354
LISD2 M1 | 275 | 67.3112 | 23.9632 | 16.4158 | 50.3049 | 71.7898 | 27.3073 | 15.922 | 54.5403
LISD2 M2 | 275 | 67.3112 | 23.9632 | 16.4158 | 50.3049 | 71.7898 | 27.3073 | 15.922 | 54.5403
LISD2 R1 | 275 | 67.3112 | 23.9632 | 16.4158 | 50.3049 | 71.7898 | 27.3073 | 15.922 | 54.5403
LISD2 R2 | 275 | 67.3112 | 23.9632 | 16.4158 | 50.3049 | 71.7898 | 27.3073 | 15.922 | 54.5403
LITB4 Term500 | 400 | 76.1914 | 27.3074 | 8.0721 | 46.6906 | 69.3584 | 26.249 | 11.1013 | 48.2231
LITT4 M1 | 400 | 124.2727 | 42.4006 | 27.9488 | 87.9123 | 114.1657 | 43.5963 | 23.3026 | 84.957
LITT4 M2 | 400 | 124.2727 | 42.4006 | 27.9488 | 87.9123 | 114.1657 | 43.5963 | 23.3026 | 84.957
LITT4 M3 | 400 | 124.2727 | 42.4006 | 27.9488 | 87.9123 | 114.1657 | 43.5963 | 23.3026 | 84.957
LITT4 R1 | 400 | 124.2727 | 42.4006 | 27.9488 | 87.9123 | 114.1657 | 43.5963 | 23.3026 | 84.957
LITT4 R2 | 400 | 124.2727 | 42.4006 | 27.9488 | 87.9123 | 114.1657 | 43.5963 | 23.3026 | 84.957
LITT4 R3 | 400 | 124.2727 | 42.4006 | 27.9488 | 87.9123 | 114.1657 | 43.5963 | 23.3026 | 84.957
LOFI4A | 400 | 96.4218 | 32.8014 | 9.2098 | 55.5981 | 80.591 | 31.1771 | 4.5523 | 48.6434
LOFI4A_KEMS | 400 | 96.4218 | 32.8014 | 9.2098 | 55.5981 | 80.591 | 31.1771 | 4.5523 | 48.6434
LOFI4A_LITT | 400 | 96.4218 | 32.8014 | 9.2098 | 55.5981 | 80.591 | 31.1771 | 4.5523 | 48.6434
LOFI4A_ROWD | 400 | 96.4218 | 32.8014 | 9.2098 | 55.5981 | 80.591 | 31.1771 | 4.5523 | 48.6434
LOFI4B | 400 | 95.3375 | 32.5499 | 9.0331 | 55.0655 | 81.4921 | 31.5423 | 4.5745 | 49.182
LOFI4B_KEMS | 400 | 95.3375 | 32.5499 | 9.0331 | 55.0655 | 81.4921 | 31.5423 | 4.5745 | 49.182
LOFI4B_LITT | 400 | 95.3375 | 32.5499 | 9.0331 | 55.0655 | 81.4921 | 31.5423 | 4.5745 | 49.182
LOFI4B_ROWD | 400 | 95.3375 | 32.5499 | 9.0331 | 55.0655 | 81.4921 | 31.5423 | 4.5745 | 49.182
LOVE4 M1 | 400 | 95.8629 | 34.2948 | 18.636 | 67.1362 | 83.2113 | 32.1832 | 15.7977 | 61.3115
LOVE4 M2 | 400 | 95.8629 | 34.2948 | 18.636 | 67.1362 | 83.2113 | 32.1832 | 15.7977 | 61.3115
LOVE4 R1 | 400 | 95.8629 | 34.2948 | 18.636 | 67.1362 | 83.2113 | 32.1832 | 15.7977 | 61.3115
LOVE4 R2 | 400 | 95.8629 | 34.2948 | 18.636 | 67.1362 | 83.2113 | 32.1832 | 15.7977 | 61.3115
MACC2 MC1 | 275 | 56.6053 | 20.932 | 13.8427 | 43.4449 | 53.1403 | 20.5132 | 11.9078 | 40.9178
MACC2 MC2 | 275 | 56.6053 | 20.932 | 13.8427 | 43.4449 | 53.1403 | 20.5132 | 11.9078 | 40.9178
MACC4 MC1 | 400 | 81.8997 | 30.8814 | 23.1756 | 66.8485 | 61.9808 | 24.7861 | 15.2295 | 50.2822
MACC4 MC2 | 400 | 81.8997 | 30.8814 | 23.1756 | 66.8485 | 61.9808 | 24.7861 | 15.2295 | 50.2822
MACC4 MC3 | 400 | 81.8997 | 30.8814 | 23.1756 | 66.8485 | 61.9808 | 24.7861 | 15.2295 | 50.2822
MACC4 MC4 | 400 | 81.8997 | 30.8814 | 23.1756 | 66.8485 | 61.9808 | 24.7861 | 15.2295 | 50.2822
MAGA2 MC1 | 275 | 51.7577 | 19.0898 | 11.2518 | 38.2488 | 45.2441 | 17.894 | 8.3224 | 33.6284
MAGA2 MC2 | 275 | 51.7577 | 19.0898 | 11.2518 | 38.2488 | 45.2441 | 17.894 | 8.3224 | 33.6284
MANN4 M5 | 400 | 57.3226 | 20.9301 | 11.1809 | 40.7805 | 52.7598 | 20.229 | 11.4217 | 40.0298
MANN4 MC1 | 400 | 57.3226 | 20.9301 | 11.1809 | 40.7805 | 52.7598 | 20.229 | 11.4217 | 40.0298
MANN4 MC2 | 400 | 57.3226 | 20.9301 | 11.1809 | 40.7805 | 52.7598 | 20.229 | 11.4217 | 40.0298
MANN4 MC3 | 400 | 57.3226 | 20.9301 | 11.1809 | 40.7805 | 52.7598 | 20.229 | 11.4217 | 40.0298
MANN4 MC4 | 400 | 57.3226 | 20.9301 | 11.1809 | 40.7805 | 52.7598 | 20.229 | 11.4217 | 40.0298
MANN4 R5 | 400 | 57.3226 | 20.9301 | 11.1809 | 40.7805 | 52.7598 | 20.229 | 11.4217 | 40.0298
MAWO4 M | 400 | 63.6775 | 23.1582 | 12.4489 | 45.1995 | 56.9197 | 21.7721 | 12.507 | 43.2974
MAWO4 R | 400 | 63.6775 | 23.1582 | 12.4489 | 45.1995 | 56.9197 | 21.7721 | 12.507 | 43.2974
MEDW4 Term500 | 400 | 114.1597 | 39.4007 | 25.7184 | 81.4394 | 105.2203 | 39.655 | 24.139 | 80.2196
MELK1 M1 | 132 | 41.925 | 14.6591 | 14.8766 | 35.6077 | 52.0138 | 19.1106 | 17.4354 | 44.4619
MELK1 M2 | 132 | 41.925 | 14.6591 | 14.8766 | 35.6077 | 52.0138 | 19.1106 | 17.4354 | 44.4619
MELK1 R1 | 132 | 41.925 | 14.6591 | 14.8766 | 35.6077 | 52.0138 | 19.1106 | 17.4354 | 44.4619
MELK1 R2 | 132 | 41.925 | 14.6591 | 14.8766 | 35.6077 | 52.0138 | 19.1106 | 17.4354 | 44.4619
MELK4 M1 | 400 | 107.0452 | 39.1655 | 20.7651 | 76.1536 | 88.4983 | 34.9754 | 14.7999 | 64.2625
MELK4 M2 | 400 | 107.0452 | 39.1655 | 20.7651 | 76.1536 | 88.4983 | 34.9754 | 14.7999 | 64.2625
MELK4 M3 | 400 | 107.0452 | 39.1655 | 20.7651 | 76.1536 | 88.4983 | 34.9754 | 14.7999 | 64.2625
MELK4 R1 | 400 | 107.0452 | 39.1655 | 20.7651 | 76.1536 | 88.4983 | 34.9754 | 14.7999 | 64.2625
MELK4 R2 | 400 | 107.0452 | 39.1655 | 20.7651 | 76.1536 | 88.4983 | 34.9754 | 14.7999 | 64.2625
MELK4 R3 | 400 | 107.0452 | 39.1655 | 20.7651 | 76.1536 | 88.4983 | 34.9754 | 14.7999 | 64.2625
MILH1 M1 | 132 | 40.1913 | 14.7399 | 9.0886 | 29.934 | 46.5254 | 18.8739 | 9.1597 | 35.8515
MILH1 M2 | 132 | 40.1913 | 14.7399 | 9.0886 | 29.934 | 46.5254 | 18.8739 | 9.1597 | 35.8515
MILH1 R1 | 132 | 40.2274 | 14.7681 | 8.9847 | 29.87 | 46.4214 | 18.8862 | 8.9162 | 35.6253
MILH1 R2 | 132 | 40.2274 | 14.7681 | 8.9847 | 29.87 | 46.4214 | 18.8862 | 8.9162 | 35.6253
MITY4 MC1 | 400 | 81.3439 | 31.023 | 21.5122 | 65.3854 | 61.5051 | 24.8736 | 14.3042 | 49.4808
MITY4 MC2 | 400 | 81.3439 | 31.023 | 21.5122 | 65.3854 | 61.5051 | 24.8736 | 14.3042 | 49.4808
MITY4 MC3 | 400 | 81.3439 | 31.023 | 21.5122 | 65.3854 | 61.5051 | 24.8736 | 14.3042 | 49.4808
MITY4 MC4 | 400 | 81.3439 | 31.023 | 21.5122 | 65.3854 | 61.5051 | 24.8736 | 14.3042 | 49.4808
MONF2 M1 | 275 | 66.0719 | 23.9138 | 17.8238 | 51.6431 | 67.2113 | 25.5421 | 16.436 | 52.558
MONF2 M2 | 275 | 66.0719 | 23.9138 | 17.8238 | 51.6431 | 67.2113 | 25.5421 | 16.436 | 52.558
MONF2 R1 | 275 | 57.0598 | 20.7118 | 18.1986 | 47.4895 | 60.01 | 22.5513 | 17.4797 | 49.3721
MONF2 R2 | 275 | 57.0598 | 20.7118 | 18.1986 | 47.4895 | 60.01 | 22.5513 | 17.4797 | 49.3721
MONF4 MC2 | 400 | 79.9994 | 29.0536 | 19.048 | 60.1361 | 70.4486 | 26.9569 | 15.7395 | 53.8623
MONF4 MC3 | 400 | 79.9994 | 29.0536 | 19.048 | 60.1361 | 70.4486 | 26.9569 | 15.7395 | 53.8623
NECH2 MC1 | 275 | 73.5693 | 26.4589 | 19.2784 | 56.6969 | 74.241 | 28.5468 | 16.4388 | 56.8102
NECH2 MC2 | 275 | 73.5693 | 26.4589 | 19.2784 | 56.6969 | 74.241 | 28.5468 | 16.4388 | 56.8102
NECH2 MC3 | 275 | 73.5693 | 26.4589 | 19.2784 | 56.6969 | 74.241 | 28.5468 | 16.4388 | 56.8102
NECH2 MC4 | 275 | 73.5693 | 26.4589 | 19.2784 | 56.6969 | 74.241 | 28.5468 | 16.4388 | 56.8102
NECT4 M1 | 400 | 74.3031 | 27.2732 | 17.5266 | 56.0967 | 54.2147 | 21.4696 | 10.8267 | 41.1892
NECT4 R1 | 400 | 74.3031 | 27.2732 | 17.5266 | 56.0967 | 54.2147 | 21.4696 | 10.8267 | 41.1892
NEEP2 M1 | 275 | 59.4699 | 21.9856 | 12.8251 | 43.9175 | 62.651 | 24.9383 | 12.0874 | 47.3554
NEEP2 M2 | 275 | 59.4699 | 21.9856 | 12.8251 | 43.9175 | 62.651 | 24.9383 | 12.0874 | 47.3554
NEEP2 R1/R2 | 275 | 59.4699 | 21.9856 | 12.8251 | 43.9175 | 62.651 | 24.9383 | 12.0874 | 47.3554
NEWX2 M5 | 275 | 76.4111 | 26.4441 | 19.4497 | 56.8473 | 84.6263 | 32.9546 | 17.3348 | 63.9396
NEWX2 M5 | 275 | 76.4111 | 26.4441 | 19.4497 | 56.8473 | 84.6263 | 32.9546 | 17.3348 | 63.9396
NEWX2 M6 | 275 | 76.4111 | 26.4441 | 19.4497 | 56.8473 | 84.6263 | 32.9546 | 17.3348 | 63.9396
NEWX2 R6 | 275 | 76.4111 | 26.4441 | 19.4497 | 56.8473 | 84.6263 | 32.9546 | 17.3348 | 63.9396
NEWX21 R5 | 275 | 76.4111 | 26.4441 | 19.4497 | 56.8473 | 84.6263 | 32.9546 | 17.3348 | 63.9396
NFLE4 M1 | 400 | 104.6446 | 36.3537 | 22.7434 | 74.1552 | 85.3086 | 33.2415 | 15.1475 | 62.158
NFLE4 M2 | 400 | 104.6446 | 36.3537 | 22.7434 | 74.1552 | 85.3086 | 33.2415 | 15.1475 | 62.158
NFLE4 R1 | 400 | 104.6446 | 36.3537 | 22.7434 | 74.1552 | 85.3086 | 33.2415 | 15.1475 | 62.158
NFLE4 R2 | 400 | 104.6446 | 36.3537 | 22.7434 | 74.1552 | 85.3086 | 33.2415 | 15.1475 | 62.158
NHYD2A | 275 | 45.6248 | 17.3249 | 2.5907 | 27.0917 | 39.2887 | 18.5398 | 0.47365 | 26.6929
NHYD2B | 275 | 46.7567 | 17.6393 | 2.3102 | 27.2559 | 40.2668 | 18.4526 | 1.0723 | 27.1683
NHYD2C | 275 | 46.7567 | 17.6393 | 2.3102 | 27.2559 | 40.2668 | 18.4526 | 1.0723 | 27.1683
NINF4 M1 | 400 | 66.8183 | 24.1841 | 14.7183 | 48.9198 | 57.2962 | 22.055 | 12.6456 | 43.836
NINF4 M2 | 400 | 66.8183 | 24.1841 | 14.7183 | 48.9198 | 57.2962 | 22.055 | 12.6456 | 43.836
NINF4 R1 | 400 | 66.8183 | 24.1841 | 14.7183 | 48.9198 | 57.2962 | 22.055 | 12.6456 | 43.836
NINF4 R2 | 400 | 66.8183 | 24.1841 | 14.7183 | 48.9198 | 57.2962 | 22.055 | 12.6456 | 43.836
NORL2A | 275 | 51.9737 | 19.1594 | 3.9649 | 31.0603 | 51.4373 | 21.172 | 2.3066 | 32.2484
NORL2B | 275 | 51.157 | 18.9335 | 3.4499 | 30.2259 | 50.5861 | 21.1099 | 2.0358 | 31.8897
NORM4 M1 | 400 | 69.6761 | 25.7069 | 15.4785 | 51.8336 | 52.8338 | 20.8133 | 11.2256 | 40.6601
NORM4 M2 | 400 | 69.6761 | 25.7069 | 15.4785 | 51.8336 | 52.8338 | 20.8133 | 11.2256 | 40.6601
NORM4 R1 | 400 | 69.6761 | 25.7069 | 15.4785 | 51.8336 | 52.8338 | 20.8133 | 11.2256 | 40.6601
NORM4 R2 | 400 | 69.6761 | 25.7069 | 15.4785 | 51.8336 | 52.8338 | 20.8133 | 11.2256 | 40.6601
NORT2 M1 | 275 | 86.6392 | 30.2923 | 23.5967 | 66.4365 | 85.9876 | 32.4433 | 19.7485 | 65.6303
NORT2 M2 | 275 | 86.6392 | 30.2923 | 23.5967 | 66.4365 | 85.9876 | 32.4433 | 19.7485 | 65.6303
NORT2 R1 | 275 | 86.6392 | 30.2923 | 23.5967 | 66.4365 | 85.9876 | 32.4433 | 19.7485 | 65.6303
NORT2 R2 | 275 | 86.6392 | 30.2923 | 23.5967 | 66.4365 | 85.9876 | 32.4433 | 19.7485 | 65.6303
NORT4 M1 | 400 | 93.2059 | 33.7967 | 29.4803 | 77.276 | 77.3734 | 29.8847 | 22.133 | 64.3964
NORT4 M2 | 400 | 93.2059 | 33.7967 | 29.4803 | 77.276 | 77.3734 | 29.8847 | 22.133 | 64.3964
NORT4 R1 | 400 | 93.2059 | 33.7967 | 29.4803 | 77.276 | 77.3734 | 29.8847 | 22.133 | 64.3964
NORT4 R2 | 400 | 93.2059 | 33.7967 | 29.4803 | 77.276 | 77.3734 | 29.8847 | 22.133 | 64.3964
NURS4 MC1 | 400 | 60.6077 | 21.8408 | 7.8991 | 38.7866 | 55.3071 | 21.0471 | 8.24 | 38.0051
NURS4 MC2 | 400 | 60.6077 | 21.8408 | 7.8991 | 38.7866 | 55.3071 | 21.0471 | 8.24 | 38.0051
NURS4A | 400 | 52.4449 | 19.2889 | 10.6109 | 37.8896 | 48.336 | 18.4937 | 10.6785 | 36.8326
OCKH1 M1 | 132 | 24.6844 | 8.8344 | 8.4626 | 20.9564 | 33.1628 | 12.1656 | 11.0142 | 28.219
OCKH1 M2 | 132 | 24.6844 | 8.8344 | 8.4626 | 20.9564 | 33.1628 | 12.1656 | 11.0142 | 28.219
OCKH1 R1 | 132 | 24.6844 | 8.8344 | 8.4626 | 20.9564 | 33.1628 | 12.1656 | 11.0142 | 28.219
OCKH1 R2 | 132 | 24.6844 | 8.8344 | 8.4626 | 20.9564 | 33.1628 | 12.1656 | 11.0142 | 28.219
OCKH2 MC1 | 275 | 55.4001 | 20.3474 | 10.8144 | 39.59 | 57.3599 | 22.4063 | 10.9075 | 42.5949
OCKH2 MC2 | 275 | 55.4001 | 20.3474 | 10.8144 | 39.59 | 57.3599 | 22.4063 | 10.9075 | 42.5949
OCKH2 MC3 | 275 | 55.4001 | 20.3474 | 10.8144 | 39.59 | 57.3599 | 22.4063 | 10.9075 | 42.5949
OCKH2 MC4 | 275 | 55.4001 | 20.3474 | 10.8144 | 39.59 | 57.3599 | 22.4063 | 10.9075 | 42.5949
OCKH2A | 275 | 48.6087 | 17.5438 | 4.4411 | 29.2518 | 48.7643 | 18.847 | 4.8029 | 31.4565
OFFE2 MC1 | 275 | 70.1203 | 25.308 | 14.0976 | 49.8885 | 60.677 | 24.1402 | 8.675 | 42.8143
OFFE2 MC2 | 275 | 70.1203 | 25.308 | 14.0976 | 49.8885 | 60.677 | 24.1402 | 8.675 | 42.8143
OLDB2 MC1 | 275 | 53.0342 | 19.5711 | 10.8465 | 38.5243 | 54.5936 | 21.1416 | 10.9728 | 40.8715
OLDB2 MC2 | 275 | 53.0342 | 19.5711 | 10.8465 | 38.5243 | 54.5936 | 21.1416 | 10.9728 | 40.8715
OSBA4 MC1 | 400 | 56.1106 | 20.7301 | 12.7422 | 42.0589 | 50.1697 | 19.1713 | 12.1103 | 39.2225
OSBA4 MC2 | 400 | 56.1106 | 20.7301 | 12.7422 | 42.0589 | 50.1697 | 19.1713 | 12.1103 | 39.2225
OSBA4 MC3/4 | 400 | 56.3133 | 20.6601 | 13.1063 | 42.3241 | 44.6729 | 17.2624 | 9.5809 | 33.9935
PADI1 M1 | 132 | 29.9699 | 10.5265 | 10.5319 | 25.4186 | 37.2287 | 13.6387 | 12.7702 | 32.0582
PADI1 M2 | 132 | 29.9699 | 10.5265 | 10.5319 | 25.4186 | 37.2287 | 13.6387 | 12.7702 | 32.0582
PADI1 R1 | 132 | 29.9699 | 10.5265 | 10.5319 | 25.4186 | 37.2287 | 13.6387 | 12.7702 | 32.0582
PADI1 R2 | 132 | 29.9699 | 10.5265 | 10.5319 | 25.4186 | 37.2287 | 13.6387 | 12.7702 | 32.0582
PADI4 MC1 | 400 | 75.3036 | 27.6533 | 15.9461 | 55.0537 | 57.1233 | 22.5784 | 9.8612 | 41.7918
PADI4 MC2 | 400 | 75.3036 | 27.6533 | 15.9461 | 55.0537 | 57.1233 | 22.5784 | 9.8612 | 41.7918
PADI4 MC3 | 400 | 75.3036 | 27.6533 | 15.9461 | 55.0537 | 57.1233 | 22.5784 | 9.8612 | 41.7918
PADI4 MC4 | 400 | 75.3036 | 27.6533 | 15.9461 | 55.0537 | 57.1233 | 22.5784 | 9.8612 | 41.7918
PELH4 M1 | 400 | 130.8245 | 46.4591 | 30.1881 | 95.8911 | 109.5008 | 42.345 | 21.0338 | 80.9186
PELH4 M2 | 400 | 130.8245 | 46.4591 | 30.1881 | 95.8911 | 109.5008 | 42.345 | 21.0338 | 80.9186
PELH4 R1 | 400 | 130.8245 | 46.4591 | 30.1881 | 95.8911 | 109.5008 | 42.345 | 21.0338 | 80.9186
PELH4 R2 | 400 | 130.8245 | 46.4591 | 30.1881 | 95.8911 | 109.5008 | 42.345 | 21.0338 | 80.9186
PEMB4 M1 | 400 | 60.86 | 21.4176 | 18.2654 | 48.5544 | 65.1579 | 23.9157 | 20.6665 | 54.4884
PEMB4 M2 | 400 | 60.86 | 21.4176 | 18.2654 | 48.5544 | 65.1579 | 23.9157 | 20.6665 | 54.4884
PEMB4 M3 | 400 | 60.86 | 21.4176 | 18.2654 | 48.5544 | 65.1579 | 23.9157 | 20.6665 | 54.4884
PEMB4 M4 | 400 | 60.86 | 21.4176 | 18.2654 | 48.5544 | 65.1579 | 23.9157 | 20.6665 | 54.4884
PEMB4 R1/2 | 400 | 60.86 | 21.4176 | 18.2654 | 48.5544 | 65.1579 | 23.9157 | 20.6665 | 54.4884
PEMB4 R3/4 | 400 | 60.86 | 21.4176 | 18.2654 | 48.5544 | 65.1579 | 23.9157 | 20.6665 | 54.4884
PENN2 MC1 | 275 | 66.1738 | 24.1337 | 14.1567 | 48.2869 | 69.3049 | 26.5835 | 14.857 | 52.4517
PENN2 MC2 | 275 | 66.1738 | 24.1337 | 14.1567 | 48.2869 | 69.3049 | 26.5835 | 14.857 | 52.4517
PENN2 MC3 | 275 | 66.1738 | 24.1337 | 14.1567 | 48.2869 | 69.3049 | 26.5835 | 14.857 | 52.4517
PENN2 MC4 | 275 | 66.1738 | 24.1337 | 14.1567 | 48.2869 | 69.3049 | 26.5835 | 14.857 | 52.4517
PENT4 M1 | 400 | 89.0361 | 30.8193 | 25.9047 | 69.4898 | 89.285 | 33.105 | 24.1688 | 70.9865
PENT4 M2 | 400 | 89.0361 | 30.8193 | 25.9047 | 69.4898 | 89.285 | 33.105 | 24.1688 | 70.9865
PENT4 R1 | 400 | 89.0361 | 30.8193 | 25.9047 | 69.4898 | 89.285 | 33.105 | 24.1688 | 70.9865
PENT4 R2 | 400 | 89.0361 | 30.8193 | 25.9047 | 69.4898 | 89.285 | 33.105 | 24.1688 | 70.9865
PEWO2A | 275 | 66.6145 | 23.9404 | 20.184 | 54.0409 | 68.7617 | 25.6942 | 19.5722 | 55.9093
PEWO2B | 275 | 67.7293 | 24.6709 | 24.5261 | 59.416 | 69.8142 | 26.2046 | 24.5567 | 61.6156
PEWO4 M1 | 400 | 101.1875 | 36.8361 | 32.2455 | 84.3396 | 91.7437 | 35.4762 | 27.0808 | 77.2517
PEWO4 M2 | 400 | 101.1875 | 36.8361 | 32.2455 | 84.3396 | 91.7437 | 35.4762 | 27.0808 | 77.2517
PEWO4 M3 | 400 | 101.1875 | 36.8361 | 32.2455 | 84.3396 | 91.7437 | 35.4762 | 27.0808 | 77.2517
PEWO4 M4 | 400 | 101.1875 | 36.8361 | 32.2455 | 84.3396 | 91.7437 | 35.4762 | 27.0808 | 77.2517
PEWO4 R1/2 | 400 | 101.1875 | 36.8361 | 32.2455 | 84.3396 | 91.7437 | 35.4762 | 27.0808 | 77.2517
PEWO4 R3/4 | 400 | 101.1875 | 36.8361 | 32.2455 | 84.3396 | 91.7437 | 35.4762 | 27.0808 | 77.2517
PITS2 MC1 | 275 | 61.1191 | 22.2779 | 8.6208 | 40.1266 | 66.0555 | 25.9314 | 7.6992 | 44.3716
PITS2 MC2 | 275 | 61.1191 | 22.2779 | 8.6208 | 40.1266 | 66.0555 | 25.9314 | 7.6992 | 44.3716
PITS2 MC3 | 275 | 61.1191 | 22.2779 | 8.6208 | 40.1266 | 66.0555 | 25.9314 | 7.6992 | 44.3716
PITS2 MC4 | 275 | 61.1191 | 22.2779 | 8.6208 | 40.1266 | 66.0555 | 25.9314 | 7.6992 | 44.3716
POPP2 MC1 | 275 | 27.5541 | 11.024 | 2.8795 | 18.4698 | 24.2682 | 9.9392 | 3.5865 | 17.6426
POPP2 MC2 | 275 | 27.5541 | 11.024 | 2.8795 | 18.4698 | 24.2682 | 9.9392 | 3.5865 | 17.6426
PUDM4 MC1 | 400 | 97.9301 | 33.5856 | 22.7292 | 70.2265 | 102.3191 | 40.1652 | 19.3555 | 76.1578
PUDM4 MC2 | 400 | 97.9301 | 33.5856 | 22.7292 | 70.2265 | 102.3191 | 40.1652 | 19.3555 | 76.1578
PYLE2 MC1 | 275 | 54.0184 | 20.0407 | 10.8744 | 39.2162 | 47.7083 | 18.8735 | 8.9004 | 35.5915
PYLE2 MC2 | 275 | 54.0723 | 20.0595 | 10.8878 | 39.2563 | 47.753 | 18.8895 | 8.9164 | 35.6302
QUER4A | 400 | 84.206 | 29.5762 | 12.2941 | 54.1211 | 72.6225 | 28.0581 | 5.6802 | 45.3603
QUER4A_HEYS | 400 | 84.206 | 29.5762 | 12.2941 | 54.1211 | 72.6225 | 28.0581 | 5.6802 | 45.3603
QUER4A_HUTT | 400 | 84.206 | 29.5762 | 12.2941 | 54.1211 | 72.6225 | 28.0581 | 5.6802 | 45.3603
QUER4A_PEWO | 400 | 84.206 | 29.5762 | 12.2941 | 54.1211 | 72.6225 | 28.0581 | 5.6802 | 45.3603
QUER4B | 400 | 85.0662 | 29.8325 | 12.5912 | 54.7807 | 74.6627 | 28.7275 | 6.326 | 46.9528
QUER4B_HEYS | 400 | 85.0662 | 29.8325 | 12.5912 | 54.7807 | 74.6627 | 28.7275 | 6.326 | 46.9528
QUER4B_HUTT | 400 | 85.0662 | 29.8325 | 12.5912 | 54.7807 | 74.6627 | 28.7275 | 6.326 | 46.9528
QUER4B_PEWO | 400 | 85.0662 | 29.8325 | 12.5912 | 54.7807 | 74.6627 | 28.7275 | 6.326 | 46.9528
RAIN2 MC1 | 275 | 77.1545 | 27.2047 | 19.8493 | 58.3225 | 76.004 | 28.7574 | 16.6446 | 57.3137
RAIN2 MC2 | 275 | 77.1545 | 27.2047 | 19.8493 | 58.3225 | 76.004 | 28.7574 | 16.6446 | 57.3137
RAIN2 MC3 | 275 | 77.1545 | 27.2047 | 19.8493 | 58.3225 | 76.004 | 28.7574 | 16.6446 | 57.3137
RAIN2 MC4 | 275 | 77.1545 | 27.2047 | 19.8493 | 58.3225 | 76.004 | 28.7574 | 16.6446 | 57.3137
RASS4 M1 | 400 | 54.3477 | 20.3451 | 16.5918 | 45.3642 | 43.7452 | 17.1726 | 11.7856 | 36.0712
RASS4 M2 | 400 | 54.3477 | 20.3451 | 16.5918 | 45.3642 | 43.7452 | 17.1726 | 11.7856 | 36.0712
RATS1 M1 | 132 | 44.2438 | 15.5907 | 14.4646 | 36.5133 | 49.8138 | 18.4986 | 16.7446 | 42.9056
RATS1 M2 | 132 | 44.2438 | 15.5907 | 14.4646 | 36.5133 | 49.8138 | 18.4986 | 16.7446 | 42.9056
RATS1 R1 | 132 | 40.4661 | 14.3609 | 13.1315 | 33.4409 | 45.4211 | 16.9924 | 14.1057 | 38.1365
RATS1 R2 | 132 | 40.4661 | 14.3609 | 13.1315 | 33.4409 | 45.4211 | 16.9924 | 14.1057 | 38.1365
RATS2A | 275 | 43.9198 | 15.8698 | 10.7005 | 33.1439 | 46.6792 | 16.8696 | 20.9002 | 44.7574
RATS4 M1 | 400 | 142.1834 | 50.4185 | 32.3934 | 103.6959 | 138.9397 | 52.6607 | 35.1009 | 109.5744
RATS4 M2 | 400 | 142.1834 | 50.4185 | 32.3934 | 103.6959 | 138.9397 | 52.6607 | 35.1009 | 109.5744
RATS4 M3 | 400 | 142.1834 | 50.4185 | 32.3934 | 103.6959 | 138.9397 | 52.6607 | 35.1009 | 109.5744
RATS4 M4 | 400 | 142.1834 | 50.4185 | 32.3934 | 103.6959 | 138.9397 | 52.6607 | 35.1009 | 109.5744
RATS4 R1/2 | 400 | 142.1834 | 50.4185 | 32.3934 | 103.6959 | 138.9397 | 52.6607 | 35.1009 | 109.5744
RATS4 R3/4 | 400 | 142.1834 | 50.4185 | 32.3934 | 103.6959 | 138.9397 | 52.6607 | 35.1009 | 109.5744
RAYL4 M1 | 400 | 102.532 | 37.3168 | 30.8423 | 83.6162 | 82.6155 | 32.2991 | 22.7779 | 68.4557
RAYL4 M2 | 400 | 102.532 | 37.3168 | 30.8423 | 83.6162 | 82.6155 | 32.2991 | 22.7779 | 68.4557
RAYL4 R1 | 400 | 102.532 | 37.3168 | 30.8423 | 83.6162 | 82.6155 | 32.2991 | 22.7779 | 68.4557
RAYL4 R2 | 400 | 102.532 | 37.3168 | 30.8423 | 83.6162 | 82.6155 | 32.2991 | 22.7779 | 68.4557
REBR2 MC1 | 275 | 63.3893 | 23.1381 | 21.4955 | 54.2177 | 61.4241 | 23.8674 | 17.4508 | 51.2044
REBR2 MC2 | 275 | 61.3386 | 22.4048 | 20.9758 | 52.661 | 60.0814 | 23.4001 | 16.9022 | 49.995
REBR2 MC3 | 275 | 61.3386 | 22.4048 | 20.9758 | 52.661 | 60.0814 | 23.4001 | 16.9022 | 49.995
REBR2 MC4 | 275 | 63.3893 | 23.1381 | 21.4955 | 54.2177 | 61.4241 | 23.8674 | 17.4508 | 51.2044
RHIG4 M1 | 400 | 54.4461 | 19.9137 | 12.788 | 40.9502 | 47.941 | 18.5231 | 9.6405 | 35.8362
RHIG4 R1 | 400 | 54.4461 | 19.9137 | 12.788 | 40.9502 | 47.941 | 18.5231 | 9.6405 | 35.8362
ROCH2 MC1 | 275 | 71.5967 | 25.9812 | 9.7362 | 46.4791 | 68.1476 | 26.4321 | 9.383 | 46.7636
ROCH2 MC2 | 275 | 71.5967 | 25.9812 | 9.7362 | 46.4791 | 68.1476 | 26.4321 | 9.383 | 46.7636
ROCH2 MC3 | 275 | 71.5967 | 25.9812 | 9.7362 | 46.4791 | 68.1476 | 26.4321 | 9.383 | 46.7636
ROCH2 MC4 | 275 | 71.5967 | 25.9812 | 9.7362 | 46.4791 | 68.1476 | 26.4321 | 9.383 | 46.7636
ROCK1A | 132 | 46.7397 | 16.1099 | 16.6944 | 39.4772 | 48.7333 | 17.6031 | 16.261 | 41.1556
ROCK4 Term900 | 400 | 87.1186 | 30.8973 | 22.1307 | 65.826 | 81.9763 | 30.6895 | 21.6479 | 65.0494
RUGE4 M1 | 400 | 66.4747 | 25.0467 | 10.7573 | 46.1787 | 51.9875 | 20.9689 | 7.3097 | 36.9642
RUGE4 M2 | 400 | 66.4747 | 25.0467 | 10.7573 | 46.1787 | 51.9875 | 20.9689 | 7.3097 | 36.9642
RUGE4 R1 | 400 | 66.4747 | 25.0467 | 10.7573 | 46.1787 | 51.9875 | 20.9689 | 7.3097 | 36.9642
RUGE4 R2 | 400 | 66.4747 | 25.0467 | 10.7573 | 46.1787 | 51.9875 | 20.9689 | 7.3097 | 36.9642
RYEH4 M1 | 400 | 70.0456 | 25.4579 | 16.772 | 52.7749 | 73.1828 | 27.5367 | 18.8059 | 57.7486
RYEH4 R1 | 400 | 70.0456 | 25.4579 | 16.772 | 52.7749 | 73.1828 | 27.5367 | 18.8059 | 57.7486
RYHA41 MC1 | 400 | 43.5331 | 16.359 | 9.3811 | 32.5162 | 28.5101 | 11.3779 | 4.0667 | 20.1575
RYHA4B_LOAD2 | 400 | 43.8604 | 16.4958 | 9.4503 | 32.7789 | 30.1182 | 12.0218 | 4.2682 | 21.2695
SAEN2 MC1 | 275 | 74.1955 | 26.1255 | 21.9349 | 58.8819 | 77.2555 | 28.4918 | 23.3237 | 63.6172
SAEN2 MC2 | 275 | 74.1955 | 26.1255 | 21.9349 | 58.8819 | 77.2555 | 28.4918 | 23.3237 | 63.6172
SAES2 M | 275 | 74.7612 | 26.2919 | 22.2262 | 59.4085 | 78.144 | 28.7656 | 24.0779 | 64.7586
SAES2 R | 275 | 74.7612 | 26.2919 | 22.2262 | 59.4085 | 78.144 | 28.7656 | 24.0779 | 64.7586
SALH2 MC1 | 275 | 77.9204 | 27.615 | 18.7207 | 57.7742 | 75.4816 | 28.6754 | 15.6924 | 56.2456
SALH2 MC2 | 275 | 77.9204 | 27.615 | 18.7207 | 57.7742 | 75.4816 | 28.6754 | 15.6924 | 56.2456
SEAB4 M1 | 400 | 62.3598 | 22.895 | 20.359 | 52.7374 | 64.0924 | 24.1814 | 21.5563 | 55.754
SEAB4 M2 | 400 | 62.3598 | 22.895 | 20.359 | 52.7374 | 64.0924 | 24.1814 | 21.5563 | 55.754
SEAB4 R1 | 400 | 62.3598 | 22.895 | 20.359 | 52.7374 | 64.0924 | 24.1814 | 21.5563 | 55.754
SEAB4 R2 | 400 | 62.3598 | 22.895 | 20.359 | 52.7374 | 64.0924 | 24.1814 | 21.5563 | 55.754
SELL4 M1 | 400 | 83.7131 | 30.2971 | 17.5358 | 60.3823 | 71.4308 | 27.358 | 16.5681 | 55.2581
SELL4 M2 | 400 | 83.7131 | 30.2971 | 17.5358 | 60.3823 | 71.4308 | 27.358 | 16.5681 | 55.2581
SELL4 R1 | 400 | 83.7131 | 30.2971 | 17.5358 | 60.3823 | 71.4308 | 27.358 | 16.5681 | 55.2581
SELL4 R2 | 400 | 83.7131 | 30.2971 | 17.5358 | 60.3823 | 71.4308 | 27.358 | 16.5681 | 55.2581
SELL4A | 400 | 83.6262 | 29.5421 | 7.9456 | 49.7245 | 71.3597 | 27.1469 | 9.1259 | 47.5174
SELL4B | 400 | 83.626 | 29.5421 | 7.9455 | 49.7244 | 71.3596 | 27.1469 | 9.1258 | 47.5173
SELW4 M3 | 400 | 83.5283 | 30.2353 | 17.4862 | 60.2454 | 71.0238 | 27.2216 | 16.3456 | 54.8428
SELW4 M4 | 400 | 83.5283 | 30.2353 | 17.4862 | 60.2454 | 71.0238 | 27.2216 | 16.3456 | 54.8428
SELW4 R3 | 400 | 83.5283 | 30.2353 | 17.4862 | 60.2454 | 71.0238 | 27.2216 | 16.3456 | 54.8428
SELW4 R4 | 400 | 83.5283 | 30.2353 | 17.4862 | 60.2454 | 71.0238 | 27.2216 | 16.3456 | 54.8428
SETW4A | 400 | 83.5278 | 29.5102 | 7.9333 | 49.667 | 71.3008 | 27.1279 | 9.0959 | 47.4606
SETW4B | 400 | 83.5277 | 29.5101 | 7.9333 | 49.6669 | 71.3006 | 27.1279 | 9.0958 | 47.4605
SHBA4 M1 | 400 | 81.8918 | 29.3984 | 29.1626 | 70.7381 | 79.6354 | 29.8033 | 27.6582 | 69.8065
SHBA4 M2 | 400 | 81.8918 | 29.3984 | 29.1626 | 70.7381 | 79.6354 | 29.8033 | 27.6582 | 69.8065
SHBA4 R1 | 400 | 81.8918 | 29.3984 | 29.1626 | 70.7381 | 79.6354 | 29.8033 | 27.6582 | 69.8065
SHBA4 R2 | 400 | 81.8918 | 29.3984 | 29.1626 | 70.7381 | 79.6354 | 29.8033 | 27.6582 | 69.8065
SHEC2 MC1 | 275 | 54.0145 | 20.2065 | 10.4363 | 39.0126 | 54.8386 | 22.6039 | 7.5312 | 39.498
SHEC2 MC2 | 275 | 54.0145 | 20.2065 | 10.4363 | 39.0126 | 54.8386 | 22.6039 | 7.5312 | 39.498
SHRE4B | 400 | 56.4141 | 21.1819 | 10.6133 | 40.5691 | 44.3624 | 17.6771 | 7.2717 | 32.271
SING4 MC1 | 400 | 93.8968 | 32.9891 | 20.4534 | 67.107 | 76.818 | 29.9433 | 13.0081 | 55.3543
SING4 MC2 | 400 | 93.8968 | 32.9891 | 20.4534 | 67.107 | 76.818 | 29.9433 | 13.0081 | 55.3543
SIZE4 M1 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 M2 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 M3 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 M4 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 R1 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 R2 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 R3 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SIZE4 R4 | 400 | 70.3438 | 25.1724 | 18.0191 | 53.6182 | 75.6664 | 28.0479 | 21.6732 | 61.339
SJOW2 MC1 | 275 | 23.2967 | 8.2094 | 9.248 | 20.8578 | 27.8213 | 9.9947 | 10.8687 | 25.0033
SJOW2 MC2 | 275 | 23.2967 | 8.2094 | 9.248 | 20.8578 | 27.8213 | 9.9947 | 10.8687 | 25.0033
SJOW2 MC3 | 275 | 23.2967 | 8.2094 | 9.248 | 20.8578 | 27.8213 | 9.9947 | 10.8687 | 25.0033
SJOW2 MC4 | 275 | 23.2967 | 8.2094 | 9.248 | 20.8578 | 27.8213 | 9.9947 | 10.8687 | 25.0033
SJOW4 M1 | 400 | 113.5391 | 38.1167 | 27.1921 | 81.0972 | 132.2747 | 48.5439 | 31.6547 | 100.3061
SJOW4 M2 | 400 | 113.5391 | 38.1167 | 27.1921 | 81.0972 | 132.2747 | 48.5439 | 31.6547 | 100.3061
SJOW4 M3 | 400 | 113.5391 | 38.1167 | 27.1921 | 81.0972 | 132.2747 | 48.5439 | 31.6547 | 100.3061
SJOW4 M4 | 400 | 113.5391 | 38.1167 | 27.1921 | 81.0972 | 132.2747 | 48.5439 | 31.6547 | 100.3061
SJOW4 R1/2 | 400 | 113.5391 | 38.1167 | 27.1921 | 81.0972 | 132.2747 | 48.5439 | 31.6547 | 100.3061
SJOW4 R3/4 | 400 | 113.5391 | 38.1167 | 27.1921 | 81.0972 | 132.2747 | 48.5439 | 31.6547 | 100.3061
SKLG2 MC1 | 275 | 58.6751 | 21.6793 | 17.8466 | 48.5058 | 56.4832 | 22.0046 | 15.9674 | 47.0865
SKLG2 MC2 | 275 | 58.6751 | 21.6793 | 17.8466 | 48.5058 | 56.4832 | 22.0046 | 15.9674 | 47.0865
SKLG2 MC3 | 275 | 58.6751 | 21.6793 | 17.8466 | 48.5058 | 56.4832 | 22.0046 | 15.9674 | 47.0865
SKLG2 MC4 | 275 | 58.6751 | 21.6793 | 17.8466 | 48.5058 | 56.4832 | 22.0046 | 15.9674 | 47.0865
SMAN2 MC1 | 275 | 76.9377 | 28.6509 | 23.4203 | 63.9388 | 75.5421 | 29.5073 | 21.1205 | 62.8501
SMAN2 MC2 | 275 | 76.9377 | 28.6509 | 23.4203 | 63.9388 | 75.5421 | 29.5073 | 21.1205 | 62.8501
SMAN2 MC3 | 275 | 76.9377 | 28.6509 | 23.4203 | 63.9388 | 75.5421 | 29.5073 | 21.1205 | 62.8501
SMAN2 MC4 | 275 | 76.9377 | 28.6509 | 23.4203 | 63.9388 | 75.5421 | 29.5073 | 21.1205 | 62.8501
SPEN4 MC3 | 400 | 63.1427 | 23.0146 | 13.5723 | 46.1199 | 49.18 | 19.1278 | 9.2061 | 36.2569
SPEN4 MC4 | 400 | 63.1427 | 23.0146 | 13.5723 | 46.1199 | 49.18 | 19.1278 | 9.2061 | 36.2569
SPEN41 MC1 | 400 | 63.1186 | 23.0061 | 13.5679 | 46.1035 | 49.8205 | 19.3529 | 9.4591 | 36.8283
SPEN41 MC2 | 400 | 63.1186 | 23.0061 | 13.5679 | 46.1035 | 49.8205 | 19.3529 | 9.4591 | 36.8283
SPLN4 M1 | 400 | 80.8979 | 29.3018 | 21.4271 | 62.8661 | 67.4328 | 25.7744 | 17.5427 | 53.9932
SPLN4 R1 | 400 | 80.8979 | 29.3018 | 21.4271 | 62.8661 | 67.4328 | 25.7744 | 17.5427 | 53.9932
SSHI2 MC1 | 275 | 67.072 | 24.4054 | 12.4798 | 46.9943 | 59.3522 | 23.4614 | 9.7893 | 42.9687
SSHI2 MC2 | 275 | 67.072 | 24.4054 | 12.4798 | 46.9943 | 59.3522 | 23.4614 | 9.7893 | 42.9687
STAL2 M1 | 275 | 83.1486 | 30.5713 | 16.2286 | 59.4629 | 77.2415 | 30.1481 | 14.7565 | 57.3923
STAL2 M2 | 275 | 83.1486 | 30.5713 | 16.2286 | 59.4629 | 77.2415 | 30.1481 | 14.7565 | 57.3923
STAL2 R1 | 275 | 83.1486 | 30.5713 | 16.2286 | 59.4629 | 77.2415 | 30.1481 | 14.7565 | 57.3923
STAL2 R2 | 275 | 83.1486 | 30.5713 | 16.2286 | 59.4629 | 77.2415 | 30.1481 | 14.7565 | 57.3923
STAL4 MC1 | 400 | 36.7133 | 13.5177 | 9.5427 | 28.6596 | 32.8088 | 12.6782 | 8.1784 | 26.1081
STAL4 MC2 | 400 | 51.9727 | 19.6932 | 9.9688 | 37.8192 | 39.641 | 15.7773 | 6.4381 | 28.7506
STAY4 M1 | 400 | 113.4515 | 41.1609 | 27.1217 | 85.332 | 107.3691 | 40.7594 | 28.0895 | 85.732
STAY4 M2 | 400 | 113.4515 | 41.1609 | 27.1217 | 85.332 | 107.3691 | 40.7594 | 28.0895 | 85.732
STAY4 R1 | 400 | 113.4515 | 41.1609 | 27.1217 | 85.332 | 107.3691 | 40.7594 | 28.0895 | 85.732
STAY4 R2 | 400 | 113.4515 | 41.1609 | 27.1217 | 85.332 | 107.3691 | 40.7594 | 28.0895 | 85.732
STAY4A | 400 | 76.7564 | 28.1134 | 21.286 | 61.0444 | 69.589 | 26.3299 | 20.2459 | 57.482
STEN1 M1 | 132 | 55.5993 | 19.5711 | 19.4708 | 47.1485 | 68.1457 | 25.1156 | 23.0815 | 58.6004
STEN1 M2 | 132 | 55.5993 | 19.5711 | 19.4708 | 47.1485 | 68.1457 | 25.1156 | 23.0815 | 58.6004
STEN1 R1 | 132 | 55.5993 | 19.5711 | 19.4708 | 47.1485 | 68.1457 | 25.1156 | 23.0815 | 58.6004
STEN1 R2 | 132 | 55.5993 | 19.5711 | 19.4708 | 47.1485 | 68.1457 | 25.1156 | 23.0815 | 58.6004
STES1 M1 | 132 | 55.8422 | 19.1253 | 15.43 | 42.4773 | 68.1168 | 24.8285 | 17.6415 | 52.7543
STES1 M2 | 132 | 55.8422 | 19.1253 | 15.43 | 42.4773 | 68.1168 | 24.8285 | 17.6415 | 52.7543
STES1 R1 | 132 | 55.8422 | 19.1253 | 15.43 | 42.4773 | 68.1168 | 24.8285 | 17.6415 | 52.7543
STES1 R2 | 132 | 55.8422 | 19.1253 | 15.43 | 42.4773 | 68.1168 | 24.8285 | 17.6415 | 52.7543
STEW2 M1 | 275 | 83.1013 | 30.5488 | 25.5601 | 68.7626 | 78.512 | 30.1552 | 23.8159 | 66.4617
STEW2 M2 | 275 | 83.1013 | 30.5488 | 25.5601 | 68.7626 | 78.512 | 30.1552 | 23.8159 | 66.4617
STEW2 R1 | 275 | 83.1013 | 30.5488 | 25.5601 | 68.7626 | 78.512 | 30.1552 | 23.8159 | 66.4617
STEW2 R2 | 275 | 83.1013 | 30.5488 | 25.5601 | 68.7626 | 78.512 | 30.1552 | 23.8159 | 66.4617
STEW4 M1 | 400 | 81.6531 | 29.8918 | 24.9708 | 67.2441 | 60.8694 | 23.6416 | 17.725 | 51.1593
STEW4 M2 | 400 | 81.6531 | 29.8918 | 24.9708 | 67.2441 | 60.8694 | 23.6416 | 17.725 | 51.1593
STEW4 R1 | 400 | 81.6531 | 29.8918 | 24.9708 | 67.2441 | 60.8694 | 23.6416 | 17.725 | 51.1593
STEW4 R2a | 400 | 81.6531 | 29.8918 | 24.9708 | 67.2441 | 60.8694 | 23.6416 | 17.725 | 51.1593
STOB4 M1 | 400 | 65.9468 | 24.8795 | 12.0817 | 47.2666 | 53.6515 | 21.5115 | 8.2404 | 38.6622
STOB4 R1 | 400 | 65.9468 | 24.8795 | 12.0817 | 47.2666 | 53.6515 | 21.5115 | 8.2404 | 38.6622
STSB4 MC1 | 400 | 57.6444 | 21.3862 | 12.5769 | 42.8215 | 45.854 | 18.0482 | 7.7855 | 33.3096
STSB4 MC2 | 400 | 57.6444 | 21.3862 | 12.5769 | 42.8215 | 45.854 | 18.0482 | 7.7855 | 33.3096
STSB4A | 400 | 53.4671 | 19.6501 | 5.7961 | 33.5856 | 41.6602 | 16.2802 | 3.1262 | 26.1499
SUND4 M1 | 400 | 110.443 | 39.9807 | 23.6605 | 80.2018 | 92.9126 | 36.03 | 18.0768 | 69.0309
SUND4 M2 | 400 | 87.3513 | 32.0553 | 18.3318 | 63.6649 | 74.2042 | 28.7476 | 14.7912 | 55.4464
SUND4 R1 | 400 | 110.443 | 39.9807 | 23.6605 | 80.2018 | 92.9126 | 36.03 | 18.0768 | 69.0309
SUND4 R2 | 400 | 87.3513 | 32.0553 | 18.3318 | 63.6649 | 74.2042 | 28.7476 | 14.7912 | 55.4464
SUTB4A | 400 | 88.3586 | 32.2719 | 20.3579 | 65.9972 | 77.1945 | 29.7326 | 18.2089 | 60.2571
SWAN2 MC3 | 275 | 25.7903 | 9.3612 | 8.4644 | 21.7032 | 28.2344 | 10.4541 | 8.8137 | 23.5981
SWAN2 MC4 | 275 | 25.7903 | 9.3612 | 8.4644 | 21.7032 | 28.2344 | 10.4541 | 8.8137 | 23.5981
SWAN4 M1 | 400 | 38.4631 | 14.2035 | 9.1346 | 29.2214 | 33.95 | 12.958 | 8.0454 | 26.3707
SWAN4 M2 | 400 | 38.4631 | 14.2035 | 9.1346 | 29.2214 | 33.95 | 12.958 | 8.0454 | 26.3707
SWAN4 M3 | 400 | 60.7084 | 21.8789 | 15.4226 | 46.364 | 59.2757 | 22.4604 | 14.2344 | 45.9982
SWAN4 M4 | 400 | 60.7084 | 21.8789 | 15.4226 | 46.364 | 59.2757 | 22.4604 | 14.2344 | 45.9982
SWAN4 R3 | 400 | 60.7084 | 21.8789 | 15.4226 | 46.364 | 59.2757 | 22.4604 | 14.2344 | 45.9982
SWAN4 R4 | 400 | 60.7084 | 21.8789 | 15.4226 | 46.364 | 59.2757 | 22.4604 | 14.2344 | 45.9982
TAUN4 M1 | 400 | 49.9316 | 18.5544 | 9.635 | 35.8749 | 43.4476 | 17.2114 | 6.7832 | 31.1238
TAUN4 M2 | 400 | 50.7001 | 18.7989 | 9.7805 | 36.3661 | 44.9864 | 17.7686 | 7.314 | 32.4426
TEMP2 MC1 | 275 | 59.9882 | 22.1935 | 12.286 | 43.6722 | 62.4664 | 24.7776 | 10.9976 | 46.0384
TEMP2 MC2 | 275 | 59.9882 | 22.1935 | 12.286 | 43.6722 | 62.4664 | 24.7776 | 10.9976 | 46.0384
TEMP2 MC3 | 275 | 60.282 | 22.2816 | 12.428 | 43.9389 | 63.373 | 25.1169 | 11.227 | 46.7477
THOM2 M1 | 275 | 67.565 | 24.689 | 19.162 | 54.0775 | 69.7119 | 26.367 | 18.8736 | 56.1622
THOM2 R1 | 275 | 67.565 | 24.689 | 19.162 | 54.0775 | 69.7119 | 26.367 | 18.8736 | 56.1622
THOM4 MC1 | 400 | 93.3105 | 33.3835 | 22.9585 | 70.1699 | 83.8366 | 32.0806 | 17.8195 | 63.1883
THOM4 MC2 | 400 | 93.3105 | 33.3835 | 22.9585 | 70.1699 | 83.8366 | 32.0806 | 17.8195 | 63.1883
THOM4 MC3 | 400 | 93.3105 | 33.3835 | 22.9585 | 70.1699 | 83.8366 | 32.0806 | 17.8195 | 63.1883
THOM4 MC4 | 400 | 93.3105 | 33.3835 | 22.9585 | 70.1699 | 83.8366 | 32.0806 | 17.8195 | 63.1883
THOM4 R2(2) | 400 | 89.3905 | 32.6271 | 19.2505 | 65.3922 | 78.0755 | 30.1444 | 15.6353 | 58.2659
THOM4 R2(3) | 400 | 89.3905 | 32.6271 | 19.2505 | 65.3922 | 78.0755 | 30.1444 | 15.6353 | 58.2659
THOM42 M5 | 400 | 89.3905 | 32.6271 | 19.2505 | 65.3922 | 78.0755 | 30.1444 | 15.6353 | 58.2659
THTO4 M1 | 400 | 97.2735 | 34.7497 | 24.8844 | 74.0279 | 76.0902 | 29.4066 | 14.4189 | 56.0062
THTO4 M2 | 400 | 70.5233 | 25.5308 | 17.2325 | 53.3385 | 56.1804 | 21.6608 | 11.161 | 41.7941
THTO4 M3 | 400 | 70.5233 | 25.5308 | 17.2325 | 53.3385 | 56.1804 | 21.6608 | 11.161 | 41.7941
THTO4 M4 | 400 | 97.2735 | 34.7497 | 24.8844 | 74.0279 | 76.0902 | 29.4066 | 14.4189 | 56.0062
THTO4 R1/2 | 400 | 67.8857 | 24.8143 | 16.0566 | 51.1493 | 57.8658 | 22.2317 | 11.9419 | 43.3823
THTO4 R3/4 | 400 | 67.8857 | 24.8143 | 16.0566 | 51.1493 | 57.8658 | 22.2317 | 11.9419 | 43.3823
THUR2 MC1 | 275 | 64.8585 | 24.4679 | 10.5489 | 45.1518 | 65.9041 | 26.1255 | 10.9662 | 47.9132
THUR2 MC2 | 275 | 64.8585 | 24.4679 | 10.5489 | 45.1518 | 65.9041 | 26.1255 | 10.9662 | 47.9132
THUR2 MC3 | 275 | 64.8585 | 24.4679 | 10.5489 | 45.1518 | 65.9041 | 26.1255 | 10.9662 | 47.9132
THUR2 MC4 | 275 | 64.8585 | 24.4679 | 10.5489 | 45.1518 | 65.9041 | 26.1255 | 10.9662 | 47.9132
TILB2 M1 | 275 | 71.2622 | 25.4426 | 21.0597 | 57.041 | 75.1655 | 28.0585 | 21.2459 | 60.9266
TILB2 M2 | 275 | 71.2622 | 25.4426 | 21.0597 | 57.041 | 75.1655 | 28.0585 | 21.2459 | 60.9266
TILB2 R1 | 275 | 71.2622 | 25.4426 | 21.0597 | 57.041 | 75.1655 | 28.0585 | 21.2459 | 60.9266
TILB2 R2 | 275 | 71.2622 | 25.4426 | 21.0597 | 57.041 | 75.1655 | 28.0585 | 21.2459 | 60.9266
TILB4 M2 | 400 | 136.9748 | 48.2422 | 42.9684 | 111.1931 | 124.1758 | 47.6779 | 34.9388 | 102.3656
TILB4 M3 | 400 | 136.9748 | 48.2422 | 42.9684 | 111.1931 | 124.1758 | 47.6779 | 34.9388 | 102.3656
TILB4 R2 | 400 | 136.9748 | 48.2422 | 42.9684 | 111.1931 | 124.1758 | 47.6779 | 34.9388 | 102.3656
TILB4 R3 | 400 | 136.9748 | 48.2422 | 42.9684 | 111.1931 | 124.1758 | 47.6779 | 34.9388 | 102.3656
TINP2 M1 | 275 | 58.3326 | 21.3271 | 6.8609 | 37.022 | 56.7868 | 22.1074 | 5.5275 | 36.7921
TINP2 M2 | 275 | 58.5013 | 21.3377 | 6.8739 | 37.05 | 57.7197 | 22.4456 | 5.6216 | 37.3644
TODP2 MC1 | 275 | 64.2917 | 22.467 | 16.1423 | 47.9154 | 58.804 | 22.4645 | 11.8299 | 43.5995
TODP2 MC2 | 275 | 64.2917 | 22.467 | 16.1423 | 47.9154 | 58.804 | 22.4645 | 11.8299 | 43.5995
TOTE2A | 275 | 70.9203 | 25.2908 | 19.5549 | 55.3215 | 72.8418 | 27.5398 | 16.9826 | 55.9297
TOTE2B | 275 | 72.6302 | 25.8713 | 19.7754 | 56.3629 | 73.3823 | 27.7811 | 16.8924 | 56.1809
TOTT2 MC1 | 275 | 41.9296 | 15.8957 | 12.3593 | 34.8392 | 43.0543 | 16.7818 | 12.0578 | 35.7908
TOTT2 MC2A | 275 | 44.0015 | 16.6431 | 12.9976 | 36.5345 | 40.1155 | 15.7718 | 10.9507 | 33.2553
TOTT2 MC2B | 275 | 72.6302 | 25.8713 | 19.7754 | 56.3629 | 73.3823 | 27.7811 | 16.8924 | 56.1809
TOTT2 MC3 | 275 | 44.0015 | 16.6431 | 12.9976 | 36.5345 | 40.1155 | 15.7718 | 10.9507 | 33.2553
TOTT2 MC4A | 275 | 41.9296 | 15.8957 | 12.3593 | 34.8392 | 43.0543 | 16.7818 | 12.0578 | 35.7908
TOTT2 MC4B | 275 | 70.9203 | 25.2908 | 19.5549 | 55.3215 | 72.8418 | 27.5398 | 16.9826 | 55.9297
TOTT2 MC5 | 275 | 72.6302 | 25.8713 | 19.7754 | 56.3629 | 73.3823 | 27.7811 | 16.8924 | 56.1809
TOTT2 MC6 | 275 | 72.6302 | 25.8713 | 19.7754 | 56.3629 | 73.3823 | 27.7811 | 16.8924 | 56.1809
TOTT2 MC7 | 275 | 70.9203 | 25.2908 | 19.5549 | 55.3215 | 72.8418 | 27.5398 | 16.9826 | 55.9297
TOTT2 MC8 | 275 | 70.9203 | 25.2908 | 19.5549 | 55.3215 | 72.8418 | 27.5398 | 16.9826 | 55.9297
TRAW2 M1 | 275 | 45.7113 | 16.4278 | 14.1657 | 37.3981 | 47.785 | 17.8783 | 12.9606 | 38.2443
TRAW2 M2 | 275 | 45.7113 | 16.4278 | 14.1657 | 37.3981 | 47.785 | 17.8783 | 12.9606 | 38.2443
TRAW2 R1 | 275 | 45.7113 | 16.4278 | 14.1657 | 37.3981 | 47.785 | 17.8783 | 12.9606 | 38.2443
TRAW2 R2 | 275 | 45.7113 | 16.4278 | 14.1657 | 37.3981 | 47.785 | 17.8783 | 12.9606 | 38.2443
TRAW4 MC1 | 400 | 61.5326 | 22.9292 | 18.8261 | 51.253 | 48.7806 | 19.3378 | 12.7646 | 40.1123
TRAW4 MC2 | 400 | 61.5326 | 22.9292 | 18.8261 | 51.253 | 48.7806 | 19.3378 | 12.7646 | 40.1123
TRAW4 MC3 | 400 | 61.5326 | 22.9292 | 18.8261 | 51.253 | 48.7806 | 19.3378 | 12.7646 | 40.1123
TRAW4 MC4 | 400 | 61.5326 | 22.9292 | 18.8261 | 51.253 | 48.7806 | 19.3378 | 12.7646 | 40.1123
TREM2 MC1 | 275 | 46.6292 | 17.1046 | 2.6646 | 26.8542 | 41.2251 | 16.3742 | 2.3451 | 25.5017
TREM2 MC2 | 275 | 46.6292 | 17.1046 | 2.6646 | 26.8542 | 41.2251 | 16.3742 | 2.3451 | 25.5017
TREU4A | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.5926 | 29.1711 | 4.5789 | 45.8331
TREU4A_DEES1 | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.5926 | 29.1711 | 4.5789 | 45.8331
TREU4A_LEGA1 | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.5926 | 29.1711 | 4.5789 | 45.8331
TREU4A_TRAW1 | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.5926 | 29.1711 | 4.5789 | 45.8331
TREU4B | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.8243 | 29.26 | 4.5931 | 45.973
TREU4B_DEES2 | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.8243 | 29.26 | 4.5931 | 45.973
TREU4B_LEGA2 | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.8243 | 29.26 | 4.5931 | 45.973
TREU4B_TRAW2 | 400 | 91.789 | 32.5266 | 9.5944 | 55.5941 | 74.8243 | 29.26 | 4.5931 | 45.973
TYNE2 MC1 | 275 | 61.9371 | 22.7131 | 11.1524 | 43.2736 | 54.8747 | 21.5971 | 9.4963 | 40.0393
TYNE2 MC2 | 275 | 61.9371 | 22.7131 | 11.1524 | 43.2736 | 54.8747 | 21.5971 | 9.4963 | 40.0393
TYNE2A | 275 | 61.22 | 22.102 | 3.9792 | 35.2362 | 51.7015 | 20.4551 | 2.875 | 31.8028
UPPB2 MC1 | 275 | 39.2691 | 14.6404 | 9.7989 | 30.5036 | 38.4759 | 14.9007 | 8.5427 | 29.6155
UPPB2 MC2 | 275 | 41.7486 | 15.5303 | 10.1644 | 32.1275 | 40.2591 | 15.5655 | 8.9936 | 31.0065
UPPB2 MC3 | 275 | 41.7486 | 15.5303 | 10.1644 | 32.1275 | 40.2591 | 15.5655 | 8.9936 | 31.0065
UPPB2 MC4 | 275 | 39.2691 | 14.6404 | 9.7989 | 30.5036 | 38.4759 | 14.9007 | 8.5427 | 29.6155
USKM2 M1 | 275 | 77.72 | 27.5878 | 19.8445 | 58.8596 | 87.6088 | 32.7765 | 23.0413 | 69.3943
USKM2 M2 | 275 | 77.72 | 27.5878 | 19.8445 | 58.8596 | 87.6088 | 32.7765 | 23.0413 | 69.3943
USKM2 R1 | 275 | 77.72 | 27.5878 | 19.8445 | 58.8596 | 87.6088 | 32.7765 | 23.0413 | 69.3943
USKM2 R2 | 275 | 77.72 | 27.5878 | 19.8445 | 58.8596 | 87.6088 | 32.7765 | 23.0413 | 69.3943
USKM2A | 275 | 75.2828 | 26.1002 | 11.3397 | 48.251 | 82.849 | 30.9051 | 11.9806 | 55.687
WALH4 MC1 | 400 | 60.5375 | 22.5763 | 11.6378 | 43.5655 | 51.4112 | 20.1372 | 10.5228 | 39.0011
WALH4 MC2 | 400 | 60.5375 | 22.5763 | 11.6378 | 43.5655 | 51.4112 | 20.1372 | 10.5228 | 39.0011
WALH4 MC3 | 400 | 60.5375 | 22.5763 | 11.6378 | 43.5655 | 51.4112 | 20.1372 | 10.5228 | 39.0011
WALH4 MC4 | 400 | 60.5375 | 22.5763 | 11.6378 | 43.5655 | 51.4112 | 20.1372 | 10.5228 | 39.0011
WALP R4 | 132 | 68.9673 | 24.3043 | 20.5272 | 54.8987 | 83.6545 | 31.988 | 22.647 | 67.8848
WALP1 M4 | 132 | 68.9673 | 24.3043 | 20.5272 | 54.8987 | 83.6545 | 31.988 | 22.647 | 67.8848
WALP4 M1 | 400 | 106.04 | 38.0999 | 26.924 | 80.8054 | 93.8732 | 35.7358 | 24.2059 | 74.744
WALP4 M2 | 400 | 106.04 | 38.0999 | 26.924 | 80.8054 | 93.8732 | 35.7358 | 24.2059 | 74.744
WALP4 R1 | 400 | 106.04 | 38.0999 | 26.924 | 80.8054 | 93.8732 | 35.7358 | 24.2059 | 74.744
WALP4 R2 | 400 | 106.04 | 38.0999 | 26.924 | 80.8054 | 93.8732 | 35.7358 | 24.2059 | 74.744
WALPM3 | 132 | 68.9673 | 24.3043 | 20.5272 | 54.8987 | 83.6545 | 31.988 | 22.647 | 67.8848
WALPR3 | 132 | 68.9673 | 24.3043 | 20.5272 | 54.8987 | 83.6545 | 31.988 | 22.647 | 67.8848
WALX2 M1 | 275 | 73.5485 | 26.0577 | 16.4212 | 53.2722 | 77.556 | 28.9166 | 15.9874 | 56.8816
WALX2 M2 | 275 | 75.727 | 26.7358 | 16.945 | 54.7551 | 81.7459 | 30.355 | 17.1011 | 60.0296
WALX2 R1 | 275 | 73.5485 | 26.0577 | 16.4212 | 53.2722 | 77.556 | 28.9166 | 15.9874 | 56.8816
WALX2 R2 | 275 | 75.727 | 26.7358 | 16.945 | 54.7551 | 81.7459 | 30.355 | 17.1011 | 60.0296
WALX4A | 400 | 65.7952 | 23.5023 | 8.6295 | 41.8668 | 67.0248 | 25.1222 | 9.3136 | 44.8417
WALX4B | 400 | 65.7866 | 23.5206 | 8.6655 | 41.9286 | 61.6211 | 23.1707 | 8.6851 | 41.4534
WARL2 MC1 | 275 | 64.8483 | 23.5389 | 15.4141 | 48.7031 | 60.4532 | 23.4741 | 11.4804 | 44.6778
WARL2 MC2 | 275 | 64.8483 | 23.5389 | 15.4141 | 48.7031 | 60.4532 | 23.4741 | 11.4804 | 44.6778
WARL2 MC3 | 275 | 64.8483 | 23.5389 | 15.4141 | 48.7031 | 60.4532 | 23.4741 | 11.4804 | 44.6778
WARL2 MC4 | 275 | 64.8483 | 23.5389 | 15.4141 | 48.7031 | 60.4532 | 23.4741 | 11.4804 | 44.6778
WASF2A | 275 | 55.6545 | 20.3982 | 12.4689 | 41.3163 | 48.4213 | 18.9403 | 8.3646 | 35.1501
WASF2B | 275 | 60.2459 | 21.9492 | 13.4434 | 44.4842 | 54.8081 | 21.4704 | 9.1039 | 39.4677
WBOL2 MC1 | 275 | 76.3978 | 27.3481 | 15.3737 | 54.0497 | 66.404 | 26.1313 | 11.1661 | 48.1213
WBOL2 MC2 | 275 | 76.3978 | 27.3481 | 15.3737 | 54.0497 | 66.404 | 26.1313 | 11.1661 | 48.1213
WBOL2 MC3 | 275 | 76.3978 | 27.3481 | 15.3737 | 54.0497 | 66.404 | 26.1313 | 11.1661 | 48.1213
WBOL2 MC4 | 275 | 76.3978 | 27.3481 | 15.3737 | 54.0497 | 66.404 | 26.1313 | 11.1661 | 48.1213
WBUR1 M1 | 132 | 21.4074 | 7.6018 | 6.7744 | 17.5249 | 24.9405 | 9.2338 | 8.091 | 21.1496
WBUR1 M2 | 132 | 21.4074 | 7.6018 | 6.7744 | 17.5249 | 24.9405 | 9.2338 | 8.091 | 21.1496
WBUR1 R1 | 132 | 21.4074 | 7.6018 | 6.7744 | 17.5249 | 24.9405 | 9.2338 | 8.091 | 21.1496
WBUR1 R2 | 132 | 21.1846 | 7.5417 | 6.6699 | 17.3355 | 24.7795 | 9.1735 | 8.0001 | 20.9734
WBUR4 M1 | 400 | 110.8411 | 39.3561 | 32.0639 | 87.7218 | 103.4232 | 38.5801 | 30.2051 | 84.7656
WBUR4 M2 | 400 | 110.8411 | 39.3561 | 32.0639 | 87.7218 | 103.4232 | 38.5801 | 30.2051 | 84.7656
WBUR4 M3 | 400 | 110.8411 | 39.3561 | 32.0639 | 87.7218 | 103.4232 | 38.5801 | 30.2051 | 84.7656
WBUR4 M4 | 400 | 110.8411 | 39.3561 | 32.0639 | 87.7218 | 103.4232 | 38.5801 | 30.2051 | 84.7656
WBUR4 R1/2 | 400 | 106.4482 | 38.7612 | 26.3323 | 81.1489 | 87.0545 | 33.4656 | 21.1268 | 68.4544
WBUR4 R3/4 | 400 | 106.4482 | 38.7612 | 26.3323 | 81.1489 | 87.0545 | 33.4656 | 21.1268 | 68.4544
WHAM4 M1 | 400 | 119.9174 | 42.0199 | 37.3457 | 96.7709 | 134.0217 | 50.8686 | 38.3853 | 110.3244
WHAM4 M2 | 400 | 119.9174 | 42.0199 | 37.3457 | 96.7709 | 134.0217 | 50.8686 | 38.3853 | 110.3244
WHAM4 R1 | 400 | 119.9174 | 42.0199 | 37.3457 | 96.7709 | 134.0217 | 50.8686 | 38.3853 | 110.3244
WHAM4 R2 | 400 | 119.9174 | 42.0199 | 37.3457 | 96.7709 | 134.0217 | 50.8686 | 38.3853 | 110.3244
WHAM4A | 400 | 95.8995 | 31.7218 | 12.4956 | 57.357 | 99.7265 | 38.2736 | 14.8957 | 69.0227
WHAM4B | 400 | 95.9676 | 31.7408 | 12.4967 | 57.3849 | 99.8193 | 38.3096 | 14.8965 | 69.0744
WHGA2 MC1 | 275 | 70.8212 | 25.8561 | 15.0877 | 51.6537 | 66.6033 | 26.0478 | 12.0645 | 48.9017
WHGA2 MC2 | 275 | 70.8212 | 25.8561 | 15.0877 | 51.6537 | 66.6033 | 26.0478 | 12.0645 | 48.9017
WHGA2 MC3 | 275 | 70.8212 | 25.8561 | 15.0877 | 51.6537 | 66.6033 | 26.0478 | 12.0645 | 48.9017
WHGA2 MC4 | 275 | 70.8212 | 25.8561 | 15.0877 | 51.6537 | 66.6033 | 26.0478 | 12.0645 | 48.9017
WHSO2 M1 | 275 | 67.8393 | 24.5079 | 15.079 | 49.7385 | 72.9515 | 27.8296 | 15.7007 | 55.0576
WHSO2 M2 | 275 | 67.8393 | 24.5079 | 15.079 | 49.7385 | 72.9515 | 27.8296 | 15.7007 | 55.0576
WHSO2 R1 | 275 | 74.2818 | 26.5628 | 18.9717 | 56.5371 | 81.0547 | 30.5792 | 20.0378 | 63.2833
WHSO2 R2 | 275 | 74.2818 | 26.5628 | 18.9717 | 56.5371 | 81.0547 | 30.5792 | 20.0378 | 63.2833
WIBA2 MC1 | 275 | 59.9866 | 22.1938 | 12.279 | 43.6658 | 63.6917 | 25.4954 | 10.3564 | 46.4123
WIBA2 MC1 | 275 | 59.9866 | 22.1938 | 12.279 | 43.6658 | 63.6917 | 25.4954 | 10.3564 | 46.4123
WIBA2 MC2 | 275 | 59.9866 | 22.1938 | 12.279 | 43.6658 | 63.6917 | 25.4954 | 10.3564 | 46.4123
WIBA2 MC2 | 275 | 59.9866 | 22.1938 | 12.279 | 43.6658 | 63.6917 | 25.4954 | 10.3564 | 46.4123
WILE4 M1 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 M1 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 M2 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 M2 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 R1 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 R1 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 R2 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILE4 R2 | 400 | 111.8296 | 41.5692 | 31.3861 | 90.1739 | 95.775 | 37.9441 | 24.824 | 78.485
WILL1 M2 | 132 | 51.755 | 18.1475 | 16.28 | 41.9444 | 58.9018 | 22.3128 | 18.6402 | 50.1954
WILL1 R1 | 132 | 35.9764 | 13.3411 | 10.9995 | 29.8666 | 39.6797 | 15.2999 | 12.486 | 34.1234
WILL1 R2 | 132 | 51.755 | 18.1475 | 16.28 | 41.9444 | 58.9018 | 22.3128 | 18.6402 | 50.1954
WILL2 M2 | 275 | 24.1957 | 8.6555 | 9.0792 | 21.3199 | 25.8314 | 9.4222 | 9.4033 | 22.7282
WILL2 M2 | 275 | 24.1957 | 8.6555 | 9.0792 | 21.3199 | 25.8314 | 9.4222 | 9.4033 | 22.7282
WILL2 R2 | 275 | 24.1957 | 8.6555 | 9.0792 | 21.3199 | 25.8314 | 9.4222 | 9.4033 | 22.7282
WILL2 R2 | 275 | 24.1957 | 8.6555 | 9.0792 | 21.3199 | 25.8314 | 9.4222 | 9.4033 | 22.7282
WILT2A | 275 | 54.949 | 19.4703 | 10.1862 | 37.7214 | 57.2045 | 21.1898 | 9.3475 | 39.3144
WILT2A | 275 | 54.949 | 19.4703 | 10.1862 | 37.7214 | 57.2045 | 21.1898 | 9.3475 | 39.3144
WILT2B | 275 | 54.949 | 19.4703 | 10.1862 | 37.7214 | 57.2045 | 21.1898 | 9.3475 | 39.3144
WILT2B | 275 | 54.949 | 19.4703 | 10.1862 | 37.7214 | 57.2045 | 21.1898 | 9.3475 | 39.3144
WILT2C | 275 | 55.2851 | 19.5746 | 10.3548 | 38.0374 | 58.1285 | 21.472 | 10.0346 | 40.4006
WILT2C | 275 | 55.2851 | 19.5746 | 10.3548 | 38.0374 | 58.1285 | 21.472 | 10.0346 | 40.4006
WILT2D | 275 | 55.2839 | 19.5744 | 10.3543 | 38.0367 | 58.1244 | 21.4707 | 10.0328 | 40.3971
WILT2D | 275 | 55.2839 | 19.5744 | 10.3543 | 38.0367 | 58.1244 | 21.4707 | 10.0328 | 40.3971
WIMB2 MC1 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC1 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC2 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC2 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC3 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC3 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC4 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2 MC4 | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2A | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB2A | 275 | 83.3975 | 28.6879 | 21.4077 | 61.9785 | 93.8205 | 35.4634 | 23.3774 | 73.5303
WIMB4 MB2 | 400 | 92.9352 | 31.8297 | 22.6514 | 67.6655 | 106.9853 | 40.555 | 20.6995 | 78.0529
WIMB4 MB2 | 400 | 92.9352 | 31.8297 | 22.6514 | 67.6655 | 106.9853 | 40.555 | 20.6995 | 78.0529
WIMB4 RB2 | 400 | 92.9352 | 31.8297 | 22.6514 | 67.6655 | 106.9853 | 40.555 | 20.6995 | 78.0529
WIMB4 RB2 | 400 | 92.9352 | 31.8297 | 22.6514 | 67.6655 | 106.9853 | 40.555 | 20.6995 | 78.0529
WISD2 M1 | 275 | 69.3504 | 24.0378 | 22.2974 | 56.292 | 80.9312 | 29.8312 | 25.0772 | 67.2649
WISD2 M2 | 275 | 69.3504 | 24.0378 | 22.2974 | 56.292 | 80.9312 | 29.8312 | 25.0772 | 67.2649
WISD2 R1 | 275 | 69.3504 | 24.0378 | 22.2974 | 56.292 | 80.9312 | 29.8312 | 25.0772 | 67.2649
WISD2 R2 | 275 | 69.3504 | 24.0378 | 22.2974 | 56.292 | 80.9312 | 29.8312 | 25.0772 | 67.2649
WISD2A | 275 | 59.3534 | 20.597 | 12.2432 | 41.3718 | 65.0146 | 24.8249 | 13.724 | 48.8318
WISD2B | 275 | 59.3534 | 20.597 | 12.2432 | 41.3718 | 65.0146 | 24.8249 | 13.724 | 48.8318
WISD6 M1 | 66 | 50.0955 | 16.9531 | 17.0622 | 41.0375 | 33.0081 | 12.3827 | 10.6432 | 28.1551
WISD6 M2 | 66 | 50.0955 | 16.9531 | 17.0622 | 41.0375 | 33.0081 | 12.3827 | 10.6432 | 28.1551
WISD6 R1 | 66 | 50.0955 | 16.9531 | 17.0622 | 41.0375 | 33.0081 | 12.3827 | 10.6432 | 28.1551
WISD6 R2 | 66 | 50.0955 | 16.9531 | 17.0622 | 41.0375 | 33.0081 | 12.3827 | 10.6432 | 28.1551
WMEL2 MC1 | 275 | 78.5702 | 28.8455 | 14.4491 | 55.2428 | 74.9704 | 29.575 | 12.1227 | 53.9481
WMEL2 MC2 | 275 | 78.5702 | 28.8455 | 14.4491 | 55.2428 | 74.9704 | 29.575 | 12.1227 | 53.9481
WMEL2 MC3 | 275 | 78.5702 | 28.8455 | 14.4491 | 55.2428 | 74.9704 | 29.575 | 12.1227 | 53.9481
WMEL2 MC4 | 275 | 78.5702 | 28.8455 | 14.4491 | 55.2428 | 74.9704 | 29.575 | 12.1227 | 53.9481
WTHU4A | 400 | 92.2243 | 31.5165 | 8.1597 | 52.7307 | 74.7423 | 29.1267 | 4.823 | 46.0144
WTHU4B | 400 | 92.2243 | 31.5165 | 8.1597 | 52.7307 | 76.4017 | 29.7452 | 4.9301 | 46.9961
WWEY2 M1 | 275 | 71.615 | 25.9549 | 17.6977 | 54.4035 | 70.6455 | 26.9536 | 16.5964 | 54.7145
WWEY2 M2 | 275 | 71.615 | 25.9549 | 17.6977 | 54.4035 | 70.6455 | 26.9536 | 16.5964 | 54.7145
WWEY2 R1 | 275 | 73.0246 | 26.6156 | 16.3457 | 53.9857 | 73.0557 | 27.9943 | 16.4511 | 56.0411
WWEY2 R2 | 275 | 73.0246 | 26.6156 | 16.3457 | 53.9857 | 73.0557 | 27.9943 | 16.4511 | 56.0411
WWEY4A | 400 | 49.9118 | 18.199 | 6.1865 | 31.9238 | 44.7298 | 17.1558 | 6.0798 | 30.3417
WWEY4B | 400 | 50.5143 | 18.4077 | 6.4169 | 32.4493 | 44.7335 | 17.2227 | 6.3037 | 30.6603
WYLF1 M1 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 M1 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 M2 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 M2 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 R1 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 R1 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 R2 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF1 R2 | 132 | 27.5775 | 9.6245 | 8.0773 | 21.6884 | 30.7839 | 11.2677 | 9.1256 | 25.0606
WYLF4 M1 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 M1 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 M2 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 M2 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 R1 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 R1 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 R2 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYLF4 R2 | 400 | 64.8038 | 22.6241 | 18.5813 | 50.5766 | 63.6339 | 23.4597 | 18.8842 | 52.0612
WYMO4 M1 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 M1 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 M2 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 M2 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 R1 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 R1 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 R2 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289
WYMO4 R2 | 400 | 107.308 | 38.7804 | 23.633 | 78.4768 | 93.2459 | 35.955 | 18.6809 | 69.5289

## D3.5
ETYS 19 Yr 5 - NGET Fault Levels (kA), Winter 2023/24
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 35.4107 | 12.9586 | 2.7766 | 21.1029 | 32.9454 | 12.8833 | 2.1867 | 20.4064 | Back To Menu
ABHA4B | 400 | 35.3986 | 12.9511 | 2.7772 | 21.0929 | 32.9386 | 12.8785 | 2.1825 | 20.3954
ABTH1 M1 | 132 | 28.0505 | 10.5271 | 6.1331 | 21.0207 | 26.9837 | 10.6401 | 6.1228 | 21.1701
ABTH1 M2 | 132 | 25.8225 | 10.0468 | 7.6537 | 21.862 | 22.8438 | 9.1562 | 6.6816 | 19.6305
ABTH1 R1 | 132 | 28.5129 | 10.9901 | 7.6756 | 23.218 | 31.2727 | 12.3418 | 8.7977 | 26.2516
ABTH1 R2 | 132 | 28.5129 | 10.9901 | 7.6756 | 23.218 | 31.2727 | 12.3418 | 8.7977 | 26.2516
ABTH2 M1 | 275 | 48.1608 | 17.9285 | 8.8142 | 34.1689 | 43.7373 | 17.3075 | 7.3047 | 31.7812
ABTH2 M2 | 275 | 48.1608 | 17.9285 | 8.8142 | 34.1689 | 43.7373 | 17.3075 | 7.3047 | 31.7812
ABTH2 M4 | 275 | 48.1608 | 17.9285 | 8.8142 | 34.1689 | 43.7373 | 17.3075 | 7.3047 | 31.7812
ABTH2 R | 275 | 39.6543 | 14.984 | 4.4868 | 25.6774 | 33.901 | 13.5889 | 2.8013 | 22.0189
ALDW2 MC1 | 275 | 62.0766 | 23.098 | 9.8254 | 42.4909 | 60.8883 | 24.1119 | 9.7125 | 43.8119
ALDW2 MC2 | 275 | 62.0766 | 23.098 | 9.8254 | 42.4909 | 60.8883 | 24.1119 | 9.7125 | 43.8119
ALDW2 MC3 | 275 | 62.0766 | 23.098 | 9.8254 | 42.4909 | 60.8883 | 24.1119 | 9.7125 | 43.8119
ALDW2 MC4 | 275 | 62.0766 | 23.098 | 9.8254 | 42.4909 | 60.8883 | 24.1119 | 9.7125 | 43.8119
AMEM1 M1 | 132 | 25.6858 | 9.1636 | 9.1959 | 22.1551 | 31.63 | 11.6293 | 10.4789 | 26.9252
AMEM1 M2 | 132 | 25.6858 | 9.1636 | 9.1959 | 22.1551 | 31.63 | 11.6293 | 10.4789 | 26.9252
AMEM1 R1 | 132 | 25.6858 | 9.1636 | 9.1959 | 22.1551 | 31.63 | 11.6293 | 10.4789 | 26.9252
AMEM1 R2 | 132 | 25.6858 | 9.1636 | 9.1959 | 22.1551 | 31.63 | 11.6293 | 10.4789 | 26.9252
AMEM4 M | 400 | 49.1977 | 18.2592 | 4.16 | 29.9825 | 41.4292 | 16.4298 | 2.8689 | 26.1041
AMEM4 R | 400 | 50.3263 | 18.6487 | 4.2551 | 30.6284 | 41.4154 | 16.3566 | 2.8361 | 25.9678
AXMI4 MC1 | 400 | 37.6437 | 13.9918 | 7.1816 | 26.969 | 32.2808 | 12.6321 | 5.8481 | 23.7126
AXMI4 MC2 | 400 | 37.6437 | 13.9918 | 7.1816 | 26.969 | 32.2808 | 12.6321 | 5.8481 | 23.7126
BAGB2 M1 | 275 | 49.7647 | 18.161 | 12.9624 | 38.6459 | 48.2905 | 18.4088 | 12.8926 | 38.9266
BAGB2 M2 | 275 | 49.7647 | 18.161 | 12.9624 | 38.6459 | 48.2905 | 18.4088 | 12.8926 | 38.9266
BAGB2 R1 | 275 | 49.7647 | 18.161 | 12.9624 | 38.6459 | 48.2905 | 18.4088 | 12.8926 | 38.9266
BAGB2 R2 | 275 | 49.7647 | 18.161 | 12.9624 | 38.6459 | 48.2905 | 18.4088 | 12.8926 | 38.9266
BARK2 M1 | 275 | 53.656 | 19.37 | 14.3576 | 41.751 | 53.8691 | 20.3771 | 14.1778 | 42.9953
BARK2 M2 | 275 | 51.7534 | 18.6969 | 14.0733 | 40.5147 | 53.7615 | 20.2745 | 14.6611 | 43.3336
BARK2 R1 | 275 | 53.656 | 19.37 | 14.3576 | 41.751 | 53.8691 | 20.3771 | 14.1778 | 42.9953
BARK2 R2 | 275 | 51.7534 | 18.6969 | 14.0733 | 40.5147 | 53.7615 | 20.2745 | 14.6611 | 43.3336
BARK4 M1 | 400 | 124.6569 | 43.8542 | 39.1254 | 101.1446 | 116.8396 | 45.2961 | 31.4486 | 95.507
BARK4 M2 | 400 | 124.6569 | 43.8542 | 39.1254 | 101.1446 | 116.8396 | 45.2961 | 31.4486 | 95.507
BARK4 R1 | 400 | 124.6569 | 43.8542 | 39.1254 | 101.1446 | 116.8396 | 45.2961 | 31.4486 | 95.507
BARK4 R2 | 400 | 124.6569 | 43.8542 | 39.1254 | 101.1446 | 116.8396 | 45.2961 | 31.4486 | 95.507
BEDD2 M1/4 | 275 | 56.9147 | 20.6136 | 13.9636 | 43.1156 | 57.8177 | 22.4725 | 14.2436 | 46.0246
BEDD2 M2/3 | 275 | 86.9464 | 31.0174 | 20.4182 | 64.2834 | 87.5439 | 33.6486 | 20.1159 | 67.7022
BEDD2 R1 | 275 | 51.3477 | 19.0677 | 11.4987 | 38.4645 | 51.4195 | 19.8344 | 11.5603 | 39.6103
BEDD2 R2 | 275 | 86.9464 | 31.0174 | 20.4182 | 64.2834 | 87.5439 | 33.6486 | 20.1159 | 67.7022
BEDD2 R3 | 275 | 86.9464 | 31.0174 | 20.4182 | 64.2834 | 87.5439 | 33.6486 | 20.1159 | 67.7022
BEDD2 R4 | 275 | 51.3477 | 19.0677 | 11.4987 | 38.4645 | 51.4195 | 19.8344 | 11.5603 | 39.6103
BEDD4B | 400 | 48.8062 | 17.8189 | 5.3514 | 30.5512 | 43.927 | 17.238 | 5.9572 | 30.3355
BESW2 MC1 | 275 | 57.8507 | 21.2286 | 10.5361 | 40.5578 | 50.5059 | 20.1135 | 8.2421 | 36.6868
BESW2 MC2 | 275 | 57.8507 | 21.2286 | 10.5361 | 40.5578 | 50.5059 | 20.1135 | 8.2421 | 36.6868
BESW2 MC3 | 275 | 57.8507 | 21.2286 | 10.5361 | 40.5578 | 50.5059 | 20.1135 | 8.2421 | 36.6868
BESW2 MC4 | 275 | 57.8507 | 21.2286 | 10.5361 | 40.5578 | 50.5059 | 20.1135 | 8.2421 | 36.6868
BICF4A | 400 | 130.1259 | 43.4042 | 46.8697 | 108.2525 | 68.4023 | 26.8879 | 17.3345 | 55.3598
BICF4B | 400 | 130.1259 | 43.4042 | 46.8697 | 108.2525 | 68.4023 | 26.8879 | 17.3345 | 55.3598
BIRK2 MC1 | 275 | 58.5566 | 20.8231 | 15.6769 | 45.1253 | 58.5269 | 22.132 | 13.3083 | 44.6076
BIRK2 MC2 | 275 | 58.5566 | 20.8231 | 15.6769 | 45.1253 | 58.5269 | 22.132 | 13.3083 | 44.6076
BIRK2 MC3 | 275 | 58.5566 | 20.8231 | 15.6769 | 45.1253 | 58.5269 | 22.132 | 13.3083 | 44.6076
BIRK2 MC4 | 275 | 58.5566 | 20.8231 | 15.6769 | 45.1253 | 58.5269 | 22.132 | 13.3083 | 44.6076
BISW2 MC1 | 275 | 63.3719 | 23.1928 | 11.8189 | 44.6185 | 58.4302 | 22.9803 | 9.5756 | 42.0747
BISW2 MC2 | 275 | 63.3719 | 23.1928 | 11.8189 | 44.6185 | 58.4302 | 22.9803 | 9.5756 | 42.0747
BISW2 MC3 | 275 | 63.3719 | 23.1928 | 11.8189 | 44.6185 | 58.4302 | 22.9803 | 9.5756 | 42.0747
BISW2 MC4 | 275 | 63.3719 | 23.1928 | 11.8189 | 44.6185 | 58.4302 | 22.9803 | 9.5756 | 42.0747
BLYT1A | 132 | 32.5425 | 11.5419 | 4.6427 | 20.9653 | 33.3107 | 12.5761 | 5.2643 | 23.0496
BLYT1B | 132 | 32.2764 | 11.4782 | 4.5982 | 20.8309 | 33.1225 | 12.5185 | 5.2256 | 22.9294
BLYT2 M1 | 275 | 85.6512 | 31.2867 | 25.9539 | 70.1999 | 77.5048 | 29.992 | 22.224 | 64.6392
BLYT2 M2 | 275 | 85.6512 | 31.2867 | 25.9539 | 70.1999 | 77.5048 | 29.992 | 22.224 | 64.6392
BLYT2 R1 | 275 | 85.6512 | 31.2867 | 25.9539 | 70.1999 | 77.5048 | 29.992 | 22.224 | 64.6392
BLYT2 R2 | 275 | 85.6512 | 31.2867 | 25.9539 | 70.1999 | 77.5048 | 29.992 | 22.224 | 64.6392
BODE4 M1 | 400 | 85.992 | 30.6472 | 21.3075 | 64.6492 | 72.1945 | 27.7622 | 16.0402 | 55.3019
BODE4 R1 | 400 | 85.992 | 30.6472 | 21.3075 | 64.6492 | 72.1945 | 27.7622 | 16.0402 | 55.3019
BOLN4 M1 | 400 | 69.4611 | 25.6808 | 20.7904 | 57.1085 | 63.795 | 24.5157 | 19.4413 | 54.1117
BOLN4 M2 | 400 | 69.4611 | 25.6808 | 20.7904 | 57.1085 | 63.795 | 24.5157 | 19.4413 | 54.1117
BOLN4 R1 | 400 | 69.4611 | 25.6808 | 20.7904 | 57.1085 | 63.795 | 24.5157 | 19.4413 | 54.1117
BOLN4 R2 | 400 | 69.4611 | 25.6808 | 20.7904 | 57.1085 | 63.795 | 24.5157 | 19.4413 | 54.1117
BOTW4 MC1 | 400 | 76.0482 | 27.3527 | 15.1254 | 53.8079 | 61.6882 | 23.9377 | 11.8006 | 45.6537
BOTW4 MC2 | 400 | 76.0482 | 27.3527 | 15.1254 | 53.8079 | 61.6882 | 23.9377 | 11.8006 | 45.6537
BRAI4A | 400 | 64.5959 | 23.5688 | 14.7271 | 48.0584 | 48.7372 | 19.0325 | 9.4057 | 36.3217
BRAI4A BRFO | 400 | 64.5959 | 23.5688 | 14.7271 | 48.0584 | 48.7372 | 19.0325 | 9.4057 | 36.3217
BRAI4A RAYL | 400 | 64.5959 | 23.5688 | 14.7271 | 48.0584 | 48.7372 | 19.0325 | 9.4057 | 36.3217
BRAI4B | 400 | 61.3859 | 22.5075 | 13.5995 | 45.4299 | 46.2799 | 18.0315 | 8.8971 | 34.3975
BRAI4B PELH | 400 | 61.3859 | 22.5075 | 13.5995 | 45.4299 | 46.2799 | 18.0315 | 8.8971 | 34.3975
BRAI4B RAYL | 400 | 61.3859 | 22.5075 | 13.5995 | 45.4299 | 46.2799 | 18.0315 | 8.8971 | 34.3975
BRAW2 MC1 | 275 | 64.497 | 23.1475 | 14.7865 | 47.522 | 65.6071 | 25.1249 | 13.9223 | 49.4543
BRAW2 MC2 | 275 | 64.497 | 23.1475 | 14.7865 | 47.522 | 65.6071 | 25.1249 | 13.9223 | 49.4543
BRAW2 MC3 | 275 | 64.497 | 23.1475 | 14.7865 | 47.522 | 65.6071 | 25.1249 | 13.9223 | 49.4543
BRAW2 MC4 | 275 | 64.497 | 23.1475 | 14.7865 | 47.522 | 65.6071 | 25.1249 | 13.9223 | 49.4543
BRAW4A | 400 | 34.8597 | 12.7111 | 4.4052 | 22.3815 | 30.5673 | 11.6141 | 4.2109 | 20.6357
BRED2 MC1 | 275 | 78.2921 | 28.6804 | 15.6611 | 56.2214 | 74.9868 | 29.3814 | 12.7925 | 54.344
BRED2 MC2 | 275 | 78.2921 | 28.6804 | 15.6611 | 56.2214 | 74.9868 | 29.3814 | 12.7925 | 54.344
BRED2 MC3 | 275 | 78.2921 | 28.6804 | 15.6611 | 56.2214 | 74.9868 | 29.3814 | 12.7925 | 54.344
BRED2 MC4 | 275 | 78.2921 | 28.6804 | 15.6611 | 56.2214 | 74.9868 | 29.3814 | 12.7925 | 54.344
BRFO4 M3 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 M5 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 M6 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 M7 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 R3 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 R5 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 R6 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRFO4 R7 | 400 | 93.6726 | 33.6905 | 30.8983 | 78.5439 | 79.5537 | 30.5475 | 23.3933 | 66.594
BRIM1 M1 | 132 | 51.6867 | 17.4698 | 19.1284 | 43.8344 | 65.735 | 23.5959 | 23.0051 | 56.3747
BRIM1 M2 | 132 | 51.6867 | 17.4698 | 19.1284 | 43.8344 | 65.735 | 23.5959 | 23.0051 | 56.3747
BRIM1 R1 | 132 | 51.6867 | 17.4698 | 19.1284 | 43.8344 | 65.735 | 23.5959 | 23.0051 | 56.3747
BRIM1 R2 | 132 | 51.6867 | 17.4698 | 19.1284 | 43.8344 | 65.735 | 23.5959 | 23.0051 | 56.3747
BRIN2 M1 | 275 | 63.8987 | 23.3813 | 13.7481 | 46.8143 | 67.3887 | 26.3367 | 12.7486 | 49.9944
BRIN2 M2 | 275 | 67.6788 | 24.7685 | 16.7063 | 51.7343 | 70.8735 | 27.3097 | 16.2251 | 54.8468
BRIN2 R1 | 275 | 63.8987 | 23.3813 | 13.7481 | 46.8143 | 67.3887 | 26.3367 | 12.7486 | 49.9944
BRIN2 R2 | 275 | 67.6788 | 24.7685 | 16.7063 | 51.7343 | 70.8735 | 27.3097 | 16.2251 | 54.8468
BRIN4 MC1 | 400 | 69.5135 | 25.3306 | 15.7501 | 51.573 | 54.2828 | 21.1891 | 11.0881 | 41.0539
BRIN4 MC4 | 400 | 69.5135 | 25.3306 | 15.7501 | 51.573 | 54.2828 | 21.1891 | 11.0881 | 41.0539
BRLE4 M1 | 400 | 119.7214 | 42.803 | 23.9335 | 84.4661 | 103.3785 | 40.1631 | 20.7877 | 77.5869
BRLE4 M2 | 400 | 119.7214 | 42.803 | 23.9335 | 84.4661 | 103.3785 | 40.1631 | 20.7877 | 77.5869
BRLE4 R1 | 400 | 119.7214 | 42.803 | 23.9335 | 84.4661 | 103.3785 | 40.1631 | 20.7877 | 77.5869
BRLE4 R2 | 400 | 119.7214 | 42.803 | 23.9335 | 84.4661 | 103.3785 | 40.1631 | 20.7877 | 77.5869
BULL4 MC1 | 400 | 69.7744 | 25.3858 | 15.5215 | 51.4225 | 51.987 | 20.3931 | 9.1972 | 38.0375
BULL4 MC2 | 400 | 69.7744 | 25.3858 | 15.5215 | 51.4225 | 51.987 | 20.3931 | 9.1972 | 38.0375
BURW4 MC1 | 400 | 94.6518 | 33.6955 | 22.996 | 70.6486 | 62.389 | 24.7415 | 11.2883 | 46.278
BURW4 MC2 | 400 | 94.6518 | 33.6955 | 22.996 | 70.6486 | 62.389 | 24.7415 | 11.2883 | 46.278
BURW4 MC3 | 400 | 94.6518 | 33.6955 | 22.996 | 70.6486 | 62.389 | 24.7415 | 11.2883 | 46.278
BURW4 MC4 | 400 | 94.6518 | 33.6955 | 22.996 | 70.6486 | 62.389 | 24.7415 | 11.2883 | 46.278
BUSH2 MC1 | 275 | 54.1376 | 19.8152 | 11.0374 | 39.0603 | 53.7965 | 20.9655 | 10.1041 | 39.7539
BUSH2 MC2 | 275 | 54.1376 | 19.8152 | 11.0374 | 39.0603 | 53.7965 | 20.9655 | 10.1041 | 39.7539
BUSH2 MC3 | 275 | 54.1376 | 19.8152 | 11.0374 | 39.0603 | 53.7965 | 20.9655 | 10.1041 | 39.7539
BUSH2 MC4 | 275 | 54.1376 | 19.8152 | 11.0374 | 39.0603 | 53.7965 | 20.9655 | 10.1041 | 39.7539
BUST2 M1 | 275 | 70.5421 | 25.3486 | 18.353 | 54.2013 | 73.2426 | 27.8984 | 17.2741 | 56.7284
BUST2 M2 | 275 | 70.5421 | 25.3486 | 18.353 | 54.2013 | 73.2426 | 27.8984 | 17.2741 | 56.7284
BUST2 R1 | 275 | 70.5421 | 25.3486 | 18.353 | 54.2013 | 73.2426 | 27.8984 | 17.2741 | 56.7284
BUST2 R2 | 275 | 70.5421 | 25.3486 | 18.353 | 54.2013 | 73.2426 | 27.8984 | 17.2741 | 56.7284
CANT4 MC1 | 400 | 88.2631 | 31.9624 | 18.7647 | 63.9665 | 66.9166 | 26.4805 | 11.5626 | 49.0116
CANT4 MC2 | 400 | 88.2631 | 31.9624 | 18.7647 | 63.9665 | 66.9166 | 26.4805 | 11.5626 | 49.0116
CANT4 MC3 | 400 | 88.2631 | 31.9624 | 18.7647 | 63.9665 | 66.9166 | 26.4805 | 11.5626 | 49.0116
CANT4 MC4 | 400 | 88.2631 | 31.9624 | 18.7647 | 63.9665 | 66.9166 | 26.4805 | 11.5626 | 49.0116
CANT4 R5 | 400 | 88.2631 | 31.9624 | 18.7647 | 63.9665 | 66.9166 | 26.4805 | 11.5626 | 49.0116
CANT4 R5 | 400 | 88.2683 | 31.9655 | 18.7658 | 63.9719 | 66.9173 | 26.4811 | 11.5585 | 49.0084
CANT4 R5 | 400 | 88.2683 | 31.9655 | 18.7658 | 63.9719 | 66.9173 | 26.4811 | 11.5585 | 49.0084
CAPE2 M1 | 275 | 68.2907 | 23.8679 | 21.6478 | 55.4021 | 77.0793 | 28.2314 | 23.1815 | 63.1067
CAPE2 M2 | 275 | 68.2907 | 23.8679 | 21.6478 | 55.4021 | 77.0793 | 28.2314 | 23.1815 | 63.1067
CAPE2 R1 | 275 | 68.2907 | 23.8679 | 21.6478 | 55.4021 | 77.0793 | 28.2314 | 23.1815 | 63.1067
CAPE2 R2 | 275 | 68.2907 | 23.8679 | 21.6478 | 55.4021 | 77.0793 | 28.2314 | 23.1815 | 63.1067
CAPE4A | 400 | 92.567 | 32.6361 | 23.9282 | 70.0827 | 85.2495 | 32.2876 | 19.3685 | 65.0301
CAPE4B | 400 | 92.5701 | 32.6374 | 23.928 | 70.0843 | 85.963 | 32.5531 | 19.4801 | 65.5171
CARE2 MC1 | 275 | 46.6526 | 17.4848 | 8.1855 | 32.9128 | 39.7002 | 15.748 | 7.0978 | 29.3688
CARE2 MC2 | 275 | 46.6526 | 17.4848 | 8.1855 | 32.9128 | 39.7002 | 15.748 | 7.0978 | 29.3688
CARR1 M1 | 132 | 34.6845 | 12.826 | 9.8294 | 27.9681 | 40.4956 | 15.4475 | 11.6452 | 33.4912
CARR1 M2 | 132 | 34.6845 | 12.826 | 9.8294 | 27.9681 | 40.4956 | 15.4475 | 11.6452 | 33.4912
CARR1 M3 | 132 | 34.6845 | 12.826 | 9.8294 | 27.9681 | 40.4956 | 15.4475 | 11.6452 | 33.4912
CARR1 M4 | 132 | 41.9452 | 14.7344 | 14.0242 | 34.8617 | 53.8718 | 19.7448 | 17.5152 | 45.4385
CARR1 R1 | 132 | 34.6845 | 12.826 | 9.8294 | 27.9681 | 40.4956 | 15.4475 | 11.6452 | 33.4912
CARR1 R2 | 132 | 34.6845 | 12.826 | 9.8294 | 27.9681 | 40.4956 | 15.4475 | 11.6452 | 33.4912
CARR1 R3 | 132 | 41.9452 | 14.7344 | 14.0242 | 34.8617 | 53.8718 | 19.7448 | 17.5152 | 45.4385
CARR1 R4 | 132 | 41.9452 | 14.7344 | 14.0242 | 34.8617 | 53.8718 | 19.7448 | 17.5152 | 45.4385
CARR1B | 132 | 41.158 | 14.2904 | 7.9939 | 28.2035 | 50.989 | 19.2133 | 7.0232 | 34.1949
CARR1C | 132 | 40.9887 | 14.274 | 7.5895 | 27.776 | 50.5354 | 19.1648 | 5.5756 | 32.6786
CARR1D | 132 | 41.2677 | 14.3092 | 8.2245 | 28.4608 | 51.3667 | 19.2629 | 7.3895 | 34.6313
CARR2 M1 | 275 | 81.3748 | 29.319 | 21.762 | 63.2253 | 88.0002 | 33.0903 | 23.9669 | 70.7637
CARR2 M2 | 275 | 81.3748 | 29.319 | 21.762 | 63.2253 | 88.0002 | 33.0903 | 23.9669 | 70.7637
CARR2 R1 | 275 | 81.3748 | 29.319 | 21.762 | 63.2253 | 88.0002 | 33.0903 | 23.9669 | 70.7637
CARR2 R2 | 275 | 81.3748 | 29.319 | 21.762 | 63.2253 | 88.0002 | 33.0903 | 23.9669 | 70.7637
CARR4 M1 | 400 | 119.051 | 43.6172 | 35.1787 | 96.8627 | 104.683 | 40.5959 | 30.2193 | 87.6306
CARR4 M2/4 | 400 | 119.051 | 43.6172 | 35.1787 | 96.8627 | 104.683 | 40.5959 | 30.2193 | 87.6306
CARR4 R1 | 400 | 119.051 | 43.6172 | 35.1787 | 96.8627 | 104.683 | 40.5959 | 30.2193 | 87.6306
CARR4 R1/2 | 400 | 119.051 | 43.6172 | 35.1787 | 96.8627 | 104.683 | 40.5959 | 30.2193 | 87.6306
CARR4 R2 | 400 | 119.051 | 43.6172 | 35.1787 | 96.8627 | 104.683 | 40.5959 | 30.2193 | 87.6306
CARR4 R4 | 400 | 119.051 | 43.6172 | 35.1787 | 96.8627 | 104.683 | 40.5959 | 30.2193 | 87.6306
CARR4A | 400 | 100.4237 | 35.5911 | 8.7417 | 59.0752 | 82.5776 | 31.9881 | 8.4592 | 53.6972
CARR4B | 400 | 102.043 | 36.0913 | 8.9735 | 60.0142 | 84.9619 | 32.9148 | 8.4895 | 55.038
CASK1 M1 | 132 | 48.1946 | 16.0175 | 12.971 | 35.6231 | 53.4936 | 18.7838 | 15.6958 | 42.26
CELL1 M1 | 132 | 44.6045 | 16.5487 | 13.9257 | 37.3292 | 55.7127 | 21.9207 | 16.487 | 47.4875
CELL1 M2 | 132 | 42.7961 | 15.8197 | 11.8587 | 34.2311 | 47.7144 | 18.4413 | 12.7643 | 38.8442
CELL1 R1 | 132 | 44.6045 | 16.5487 | 13.9257 | 37.3292 | 55.7127 | 21.9207 | 16.487 | 47.4875
CELL1 R2 | 132 | 42.7961 | 15.8197 | 11.8587 | 34.2311 | 47.7144 | 18.4413 | 12.7643 | 38.8442
CELL1A | 132 | 37.4669 | 13.372 | 6.7891 | 25.7 | 46.474 | 18.5701 | 8.1519 | 34.414
CELL4 M1 | 400 | 89.0929 | 32.7123 | 16.1534 | 62.4156 | 74.0087 | 29.1735 | 13.9633 | 55.2208
CELL4 M2 | 400 | 89.0929 | 32.7123 | 16.1534 | 62.4156 | 74.0087 | 29.1735 | 13.9633 | 55.2208
CELL4 R1 | 400 | 89.0929 | 32.7123 | 16.1534 | 62.4156 | 74.0087 | 29.1735 | 13.9633 | 55.2208
CELL4 R2 | 400 | 89.0929 | 32.7123 | 16.1534 | 62.4156 | 74.0087 | 29.1735 | 13.9633 | 55.2208
CHIC4 MB1 | 400 | 35.634 | 13.2774 | 6.8981 | 25.6752 | 29.6591 | 11.5825 | 5.542 | 21.9221
CHIC4 MB2 | 400 | 35.634 | 13.2774 | 6.8981 | 25.6752 | 29.6591 | 11.5825 | 5.542 | 21.9221
CHIC4 R1/2 | 400 | 35.3557 | 13.3516 | 10.1658 | 29.0478 | 28.1713 | 11.0911 | 7.4993 | 23.1845
CHSI2 MC1 | 275 | 87.6042 | 31.6572 | 18.6947 | 63.4648 | 75.4728 | 29.847 | 12.2597 | 54.4697
CHSI2 MC2 | 275 | 87.6042 | 31.6572 | 18.6947 | 63.4648 | 75.4728 | 29.847 | 12.2597 | 54.4697
CHSI2 MC3 | 275 | 87.6042 | 31.6572 | 18.6947 | 63.4648 | 75.4728 | 29.847 | 12.2597 | 54.4697
CHSI2 MC4 | 275 | 87.6042 | 31.6572 | 18.6947 | 63.4648 | 75.4728 | 29.847 | 12.2597 | 54.4697
CHTE2 MC1 | 275 | 68.7879 | 24.7488 | 16.4642 | 51.4644 | 58.4052 | 23.1431 | 10.8568 | 43.586
CHTE2 MC2 | 275 | 68.7879 | 24.7488 | 16.4642 | 51.4644 | 58.4052 | 23.1431 | 10.8568 | 43.586
CHTE2 MC3 | 275 | 68.7879 | 24.7488 | 16.4642 | 51.4644 | 58.4052 | 23.1431 | 10.8568 | 43.586
CHTE2 MC4 | 275 | 68.7879 | 24.7488 | 16.4642 | 51.4644 | 58.4052 | 23.1431 | 10.8568 | 43.586
CILF4 M1 | 400 | 79.4633 | 28.5696 | 18.7682 | 59.1716 | 69.7752 | 26.9099 | 13.7402 | 51.7965
CILF4 M2 | 400 | 79.4633 | 28.5696 | 18.7682 | 59.1716 | 69.7752 | 26.9099 | 13.7402 | 51.7965
CILF4 R1 | 400 | 79.4633 | 28.5696 | 18.7682 | 59.1716 | 69.7752 | 26.9099 | 13.7402 | 51.7965
CILF4 R2 | 400 | 79.4633 | 28.5696 | 18.7682 | 59.1716 | 69.7752 | 26.9099 | 13.7402 | 51.7965
CITR4 M5 | 400 | 107.0075 | 35.7025 | 26.7389 | 77.2298 | 122.2616 | 45.9374 | 24.5506 | 89.5159
CITR4 M6 | 400 | 107.0075 | 35.7025 | 26.7389 | 77.2298 | 122.2616 | 45.9374 | 24.5506 | 89.5159
CITR4 MC1 | 400 | 107.0112 | 35.7033 | 26.7404 | 77.2326 | 122.279 | 45.9397 | 24.5981 | 89.5666
CITR4 MC2 | 400 | 107.0112 | 35.7033 | 26.7404 | 77.2326 | 122.279 | 45.9397 | 24.5981 | 89.5666
CITR4 MC3 | 400 | 107.0112 | 35.7033 | 26.7404 | 77.2326 | 122.279 | 45.9397 | 24.5981 | 89.5666
CITR4 MC4 | 400 | 107.0112 | 35.7033 | 26.7404 | 77.2326 | 122.279 | 45.9397 | 24.5981 | 89.5666
CITR4 R5 | 400 | 107.0075 | 35.7025 | 26.7389 | 77.2298 | 122.2616 | 45.9374 | 24.5506 | 89.5159
CITR4 R6 | 400 | 107.0075 | 35.7025 | 26.7389 | 77.2298 | 122.2616 | 45.9374 | 24.5506 | 89.5159
CLEH4 M1 | 400 | 76.7271 | 27.8446 | 16.6982 | 56.0764 | 68.4102 | 26.7867 | 13.7161 | 51.5982
CLEH4 R1 | 400 | 76.7271 | 27.8446 | 16.6982 | 56.0764 | 68.4102 | 26.7867 | 13.7161 | 51.5982
CONQ4 M1 | 400 | 125.1223 | 43.3824 | 32.5531 | 93.905 | 127.8145 | 47.5045 | 34.5328 | 101.7143
CONQ4 M2 | 400 | 125.1223 | 43.3824 | 32.5531 | 93.905 | 127.8145 | 47.5045 | 34.5328 | 101.7143
CONQ4 M3 | 400 | 125.1223 | 43.3824 | 32.5531 | 93.905 | 127.8145 | 47.5045 | 34.5328 | 101.7143
CONQ4 M4 | 400 | 125.1223 | 43.3824 | 32.5531 | 93.905 | 127.8145 | 47.5045 | 34.5328 | 101.7143
CONQ4 R1/3 | 400 | 125.1223 | 43.3824 | 32.5531 | 93.905 | 127.8145 | 47.5045 | 34.5328 | 101.7143
CONQ4 R2/4 | 400 | 125.1223 | 43.3824 | 32.5531 | 93.905 | 127.8145 | 47.5045 | 34.5328 | 101.7143
COSO4 M | 400 | 98.4779 | 34.8169 | 21.9567 | 71.1952 | 86.5343 | 33.1407 | 19.3771 | 66.2452
COSO4 R | 400 | 98.4779 | 34.8169 | 21.9567 | 71.1952 | 86.5343 | 33.1407 | 19.3771 | 66.2452
COTT4 M1 | 400 | 101.9969 | 37.0266 | 23.5173 | 75.8808 | 79.9865 | 31.0152 | 16.2172 | 60.0793
COTT4 M2 | 400 | 101.9969 | 37.0266 | 23.5173 | 75.8808 | 79.9865 | 31.0152 | 16.2172 | 60.0793
COTT4 M3 | 400 | 98.8958 | 36.4916 | 31.1411 | 82.748 | 80.6865 | 31.36 | 23.4352 | 67.7848
COTT4 M4 | 400 | 98.8958 | 36.4916 | 31.1411 | 82.748 | 80.6865 | 31.36 | 23.4352 | 67.7848
COTT4 R1/2 | 400 | 98.8958 | 36.4916 | 31.1411 | 82.748 | 80.6865 | 31.36 | 23.4352 | 67.7848
COTT4 R3/4 | 400 | 98.8958 | 36.4916 | 31.1411 | 82.748 | 80.6865 | 31.36 | 23.4352 | 67.7848
COVE2 MC1 | 275 | 60.3404 | 21.9034 | 12.1881 | 43.1642 | 56.671 | 21.9788 | 11.4914 | 42.5741
COVE2 MC2 | 275 | 60.3404 | 21.9034 | 12.1881 | 43.1642 | 56.671 | 21.9788 | 11.4914 | 42.5741
COVE2 MC3 | 275 | 60.3404 | 21.9034 | 12.1881 | 43.1642 | 56.671 | 21.9788 | 11.4914 | 42.5741
COVE2 MC4 | 275 | 60.3404 | 21.9034 | 12.1881 | 43.1642 | 56.671 | 21.9788 | 11.4914 | 42.5741
COWL4 M1 | 400 | 122.8904 | 45.1216 | 36.775 | 100.5866 | 102.943 | 40.0748 | 28.7855 | 85.4598
COWL4 M2 | 400 | 122.8904 | 45.1216 | 36.775 | 100.5866 | 102.943 | 40.0748 | 28.7855 | 85.4598
COWL4 R1 | 400 | 122.8904 | 45.1216 | 36.775 | 100.5866 | 102.943 | 40.0748 | 28.7855 | 85.4598
COWL4 R2 | 400 | 122.8904 | 45.1216 | 36.775 | 100.5866 | 102.943 | 40.0748 | 28.7855 | 85.4598
CREB2A | 275 | 78.5675 | 26.6149 | 19.6548 | 57.2939 | 72.0706 | 26.3806 | 13.7908 | 51.0986
CREB2B | 275 | 78.5793 | 26.6156 | 19.6635 | 57.3036 | 72.8968 | 26.6727 | 13.9503 | 51.6712
CREB4 MB1 | 400 | 167.8898 | 52.4149 | 49.6598 | 123.7857 | 108.8591 | 40.5808 | 25.2351 | 82.6251
CREB4 MB2 | 400 | 167.8898 | 52.4149 | 49.6598 | 123.7857 | 108.8591 | 40.5808 | 25.2351 | 82.6251
CREB4 RB1 | 400 | 167.8898 | 52.4149 | 49.6598 | 123.7857 | 108.8591 | 40.5808 | 25.2351 | 82.6251
CREB4 RB2 | 400 | 167.8898 | 52.4149 | 49.6598 | 123.7857 | 108.8591 | 40.5808 | 25.2351 | 82.6251
DAIN4 M1 | 400 | 110.9387 | 39.9494 | 22.7209 | 79.2179 | 94.9442 | 36.8145 | 19.0169 | 71.0805
DAIN4 M2 | 400 | 110.9387 | 39.9494 | 22.7209 | 79.2179 | 94.9442 | 36.8145 | 19.0169 | 71.0805
DAIN4 R1 | 400 | 113.3439 | 40.7126 | 23.4532 | 81.0294 | 95.9526 | 37.2279 | 19.2881 | 71.9363
DAIN4 R2 | 400 | 113.3439 | 40.7126 | 23.4532 | 81.0294 | 95.9526 | 37.2279 | 19.2881 | 71.9363
DIDC4 M1 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 M2 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 M3 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 M4 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 M5 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 M6 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 R1/2 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 R3/4 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 R5 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DIDC4 R6 | 400 | 117.4799 | 42.0912 | 25.9398 | 85.4657 | 107.5018 | 40.8277 | 26.1338 | 83.8728
DINO4 1 | 400 | 72.5488 | 25.3726 | 20.5802 | 56.4625 | 75.8791 | 27.9372 | 22.9177 | 62.4269
DINO4 2 | 400 | 72.5488 | 25.3726 | 20.5802 | 56.4625 | 75.8791 | 27.9372 | 22.9177 | 62.4269
DINO4 3 | 400 | 72.5488 | 25.3726 | 20.5802 | 56.4625 | 75.8791 | 27.9372 | 22.9177 | 62.4269
DRAK1 M1 | 132 | 30.8276 | 11.0277 | 12.4586 | 28.0542 | 37.9778 | 14.0117 | 15.4589 | 35.2744
DRAK1 M2 | 132 | 30.8276 | 11.0277 | 12.4586 | 28.0542 | 37.9778 | 14.0117 | 15.4589 | 35.2744
DRAK1 R1 | 132 | 30.8276 | 11.0277 | 12.4586 | 28.0542 | 37.9778 | 14.0117 | 15.4589 | 35.2744
DRAK1 R2 | 132 | 30.8276 | 11.0277 | 12.4586 | 28.0542 | 37.9778 | 14.0117 | 15.4589 | 35.2744
DRAK4 M1 | 400 | 118.4321 | 42.305 | 22.6658 | 82.4942 | 111.4611 | 43.1005 | 21.7487 | 82.702
DRAK4 M2 | 400 | 118.4321 | 42.305 | 22.6658 | 82.4942 | 111.4611 | 43.1005 | 21.7487 | 82.702
DRAK4 M3 | 400 | 118.4321 | 42.305 | 22.6658 | 82.4942 | 111.4611 | 43.1005 | 21.7487 | 82.702
DRAK4 R1/3 | 400 | 118.4321 | 42.305 | 22.6658 | 82.4942 | 111.4611 | 43.1005 | 21.7487 | 82.702
DRAK4 R2 | 400 | 118.4321 | 42.305 | 22.6658 | 82.4942 | 111.4611 | 43.1005 | 21.7487 | 82.702
DRAX1 M1 | 132 | 38.982 | 11.7771 | 11.652 | 28.3074 | 48.7016 | 16.5388 | 14.692 | 38.0815
DRAX1 M2 | 132 | 38.982 | 11.7771 | 11.652 | 28.3074 | 48.7016 | 16.5388 | 14.692 | 38.0815
DRAX1 R1 | 132 | 38.982 | 11.7771 | 11.652 | 28.3074 | 48.7016 | 16.5388 | 14.692 | 38.0815
DRAX1 R2 | 132 | 38.982 | 11.7771 | 11.652 | 28.3074 | 48.7016 | 16.5388 | 14.692 | 38.0815
DRAX4 M1 | 400 | 129.1198 | 44.43 | 36.5588 | 99.3924 | 130.2648 | 47.8351 | 37.3358 | 104.9849
DRAX4 M2 | 400 | 129.1198 | 44.43 | 36.5588 | 99.3924 | 130.2648 | 47.8351 | 37.3358 | 104.9849
DRAX4 M3 | 400 | 129.1198 | 44.43 | 36.5588 | 99.3924 | 130.2648 | 47.8351 | 37.3358 | 104.9849
DRAX4 M4 | 400 | 102.2937 | 35.831 | 27.992 | 78.6646 | 97.603 | 36.2493 | 27.1216 | 78.3859
DRAX4 M5 | 400 | 102.2937 | 35.831 | 27.992 | 78.6646 | 97.603 | 36.2493 | 27.1216 | 78.3859
DRAX4 M6 | 400 | 102.2937 | 35.831 | 27.992 | 78.6646 | 97.603 | 36.2493 | 27.1216 | 78.3859
DRAX4 R1/2/3 | 400 | 129.1198 | 44.43 | 36.5588 | 99.3924 | 130.2648 | 47.8351 | 37.3358 | 104.9849
DRAX4 R4/5/6 | 400 | 102.2937 | 35.831 | 27.992 | 78.6646 | 97.603 | 36.2493 | 27.1216 | 78.3859
DUNG2 M1 | 275 | 45.4044 | 16.1571 | 15.2831 | 38.1328 | 46.5245 | 17.0976 | 15.4441 | 39.6238
DUNG2 M2 | 275 | 45.4044 | 16.1571 | 15.2831 | 38.1328 | 46.5245 | 17.0976 | 15.4441 | 39.6238
DUNG2 R1 | 275 | 45.4044 | 16.1571 | 15.2831 | 38.1328 | 46.5245 | 17.0976 | 15.4441 | 39.6238
DUNG2 R2 | 275 | 45.4044 | 16.1571 | 15.2831 | 38.1328 | 46.5245 | 17.0976 | 15.4441 | 39.6238
DUNG4 M1 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
DUNG4 M2 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
DUNG4 M3 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
DUNG4 M4 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
DUNG4 M5 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
DUNG4 R1/2 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
DUNG4 R4/5 | 400 | 79.0726 | 27.879 | 13.0261 | 52.453 | 73.3836 | 27.5456 | 14.0698 | 53.0252
EALI2 MC1 | 275 | 57.1907 | 20.0819 | 13.0567 | 41.4569 | 63.4927 | 24.5971 | 8.3052 | 43.0907
EALI2 MC2 | 275 | 57.1907 | 20.0819 | 13.0567 | 41.4569 | 63.4927 | 24.5971 | 8.3052 | 43.0907
EALI2 MC3 | 275 | 57.1907 | 20.0819 | 13.0567 | 41.4569 | 63.4927 | 24.5971 | 8.3052 | 43.0907
EALI2 MC4 | 275 | 57.1907 | 20.0819 | 13.0567 | 41.4569 | 63.4927 | 24.5971 | 8.3052 | 43.0907
EASO4 M1 | 400 | 83.7645 | 30.1979 | 19.3311 | 62.0374 | 73.2528 | 27.7149 | 19.4705 | 58.6652
EASO4 M2 | 400 | 83.7645 | 30.1979 | 19.3311 | 62.0374 | 73.2528 | 27.7149 | 19.4705 | 58.6652
EASO4 R1 | 400 | 83.7645 | 30.1979 | 19.3311 | 62.0374 | 73.2528 | 27.7149 | 19.4705 | 58.6652
EASO4 R2 | 400 | 83.7645 | 30.1979 | 19.3311 | 62.0374 | 73.2528 | 27.7149 | 19.4705 | 58.6652
EASO4A | 400 | 83.7645 | 30.1979 | 19.3311 | 62.0374 | 73.2528 | 27.7149 | 19.4705 | 58.6652
EASO4B | 400 | 83.7645 | 30.1979 | 19.3311 | 62.0374 | 73.2528 | 27.7149 | 19.4705 | 58.6652
ECLA1 M1 | 132 | 44.9045 | 16.8117 | 12.8568 | 36.6322 | 47.4125 | 18.5061 | 14.0664 | 40.2379
ECLA1 M2 | 132 | 44.9045 | 16.8117 | 12.8568 | 36.6322 | 47.4125 | 18.5061 | 14.0664 | 40.2379
ECLA1 R1 | 132 | 45.4423 | 16.9288 | 13.088 | 37.0288 | 54.4317 | 20.999 | 15.8684 | 45.5655
ECLA1 R2 | 132 | 45.4423 | 16.9288 | 13.088 | 37.0288 | 54.4317 | 20.999 | 15.8684 | 45.5655
ECLA4 M1 | 400 | 109.4514 | 39.6528 | 22.5722 | 78.6498 | 88.7307 | 34.7504 | 16.8072 | 65.9517
ECLA4 M2 | 400 | 109.4514 | 39.6528 | 22.5722 | 78.6498 | 88.7307 | 34.7504 | 16.8072 | 65.9517
ECLA4 R1 | 400 | 109.4514 | 39.6528 | 22.5722 | 78.6498 | 88.7307 | 34.7504 | 16.8072 | 65.9517
ECLA4 R2 | 400 | 109.4514 | 39.6528 | 22.5722 | 78.6498 | 88.7307 | 34.7504 | 16.8072 | 65.9517
EGGB4 M1 | 400 | 103.2281 | 36.586 | 25.8733 | 77.6136 | 93.6764 | 35.5398 | 20.4502 | 70.7111
EGGB4 M2 | 400 | 103.2281 | 36.586 | 25.8733 | 77.6136 | 93.6764 | 35.5398 | 20.4502 | 70.7111
EGGB4 R1 | 400 | 86.6616 | 30.8212 | 22.3595 | 65.9472 | 77.7631 | 29.4497 | 17.8065 | 59.4547
EGGB4 R2 | 400 | 86.6616 | 30.8212 | 22.3595 | 65.9472 | 77.7631 | 29.4497 | 17.8065 | 59.4547
ELLA2 MC1 | 275 | 63.5655 | 22.8757 | 8.2131 | 40.5643 | 64.373 | 24.7624 | 7.9444 | 42.9638
ELLA2 MC2 | 275 | 63.5655 | 22.8757 | 8.2131 | 40.5643 | 64.373 | 24.7624 | 7.9444 | 42.9638
ELLA2 MC3 | 275 | 63.5655 | 22.8757 | 8.2131 | 40.5643 | 64.373 | 24.7624 | 7.9444 | 42.9638
ELLA2 MC4 | 275 | 63.5655 | 22.8757 | 8.2131 | 40.5643 | 64.373 | 24.7624 | 7.9444 | 42.9638
ELST1 M1 | 132 | 31.5342 | 11.4488 | 9.9974 | 26.1884 | 38.5613 | 14.4307 | 12.0234 | 32.4315
ELST1 M2 | 132 | 45.3283 | 16.0554 | 13.4675 | 36.1733 | 56.4233 | 21.4189 | 15.8213 | 46.1122
ELST1 M3 | 132 | 38.7823 | 14.2824 | 9.7104 | 29.9087 | 44.977 | 17.1693 | 11.5541 | 35.8351
ELST1 R1 | 132 | 31.5342 | 11.4488 | 9.9974 | 26.1884 | 38.5613 | 14.4307 | 12.0234 | 32.4315
ELST1 R2 | 132 | 45.3283 | 16.0554 | 13.4675 | 36.1733 | 56.4233 | 21.4189 | 15.8213 | 46.1122
ELST1 R3 | 132 | 38.7823 | 14.2824 | 9.7104 | 29.9087 | 44.977 | 17.1693 | 11.5541 | 35.8351
ELST2 M1 | 275 | 64.2115 | 23.1971 | 16.418 | 49.2237 | 70.2898 | 26.4881 | 18.2482 | 55.7081
ELST2 M2 | 275 | 66.5186 | 24.1677 | 14.6616 | 48.8398 | 72.9333 | 28.0379 | 15.4585 | 55.1101
ELST2 R1 | 275 | 64.2115 | 23.1971 | 16.418 | 49.2237 | 70.2898 | 26.4881 | 18.2482 | 55.7081
ELST2 R2 | 275 | 66.5186 | 24.1677 | 14.6616 | 48.8398 | 72.9333 | 28.0379 | 15.4585 | 55.1101
ELST4 M1 | 400 | 87.441 | 31.1742 | 27.7812 | 71.8682 | 104.8847 | 39.5049 | 32.3821 | 88.2504
ELST4 R1 | 400 | 87.441 | 31.1742 | 27.7812 | 71.8682 | 104.8847 | 39.5049 | 32.3821 | 88.2504
ELST4A | 400 | 55.8283 | 20.3975 | 7.296 | 36.1424 | 53.3085 | 20.2453 | 8.2799 | 36.9111
ENDE4 MC1 | 400 | 84.0591 | 31.1459 | 14.8784 | 58.9254 | 57.851 | 23.0784 | 9.8959 | 42.5337
ENDE4 MC2 | 400 | 84.0591 | 31.1459 | 14.8784 | 58.9254 | 57.851 | 23.0784 | 9.8959 | 42.5337
ENDE4 MC3 | 400 | 84.0591 | 31.1459 | 14.8784 | 58.9254 | 57.851 | 23.0784 | 9.8959 | 42.5337
ENDE4 MC4 | 400 | 84.0591 | 31.1459 | 14.8784 | 58.9254 | 57.851 | 23.0784 | 9.8959 | 42.5337
EXET4 M1 | 400 | 52.8815 | 19.4198 | 9.685 | 37.1488 | 51.0613 | 19.8536 | 9.8936 | 37.9709
EXET4 M2 | 400 | 52.8815 | 19.4198 | 9.685 | 37.1488 | 51.0613 | 19.8536 | 9.8936 | 37.9709
EXET4 R1 | 400 | 52.8815 | 19.4198 | 9.685 | 37.1488 | 51.0613 | 19.8536 | 9.8936 | 37.9709
EXET4 R2 | 400 | 52.8815 | 19.4198 | 9.685 | 37.1488 | 51.0613 | 19.8536 | 9.8936 | 37.9709
FAWL1 M1 | 132 | 50.2632 | 17.6606 | 18.1947 | 43.1706 | 63.8742 | 24.0498 | 21.5103 | 55.5219
FAWL1 M2 | 132 | 50.2632 | 17.6606 | 18.1947 | 43.1706 | 63.8742 | 24.0498 | 21.5103 | 55.5219
FAWL1 R1 | 132 | 50.2632 | 17.6606 | 18.1947 | 43.1706 | 63.8742 | 24.0498 | 21.5103 | 55.5219
FAWL1 R2 | 132 | 50.2632 | 17.6606 | 18.1947 | 43.1706 | 63.8742 | 24.0498 | 21.5103 | 55.5219
FAWL4 M1/3 | 400 | 79.3734 | 28.0104 | 10.1471 | 49.7598 | 66.3938 | 25.6026 | 8.1685 | 44.3761
FAWL4 M1/3(1) | 400 | 79.3734 | 28.0104 | 10.1471 | 49.7598 | 66.3938 | 25.6026 | 8.1685 | 44.3761
FAWL4 M2/4(2) | 400 | 79.3734 | 28.0104 | 10.1471 | 49.7598 | 66.3938 | 25.6026 | 8.1685 | 44.3761
FAWL4 M2/4(3) | 400 | 79.3734 | 28.0104 | 10.1471 | 49.7598 | 66.3938 | 25.6026 | 8.1685 | 44.3761
FAWL4 R1/3 | 400 | 79.3734 | 28.0104 | 10.1471 | 49.7598 | 66.3938 | 25.6026 | 8.1685 | 44.3761
FAWL4 R2/4 | 400 | 79.3734 | 28.0104 | 10.1471 | 49.7598 | 66.3938 | 25.6026 | 8.1685 | 44.3761
FECK2 M1 | 275 | 61.3112 | 22.5242 | 13.8872 | 45.7413 | 60.5674 | 23.3276 | 13.6938 | 46.6841
FECK2 M2 | 275 | 61.3112 | 22.5242 | 13.8872 | 45.7413 | 60.5674 | 23.3276 | 13.6938 | 46.6841
FECK2 R | 275 | 61.3112 | 22.5242 | 13.8872 | 45.7413 | 60.5674 | 23.3276 | 13.6938 | 46.6841
FECK4 M1 | 400 | 77.013 | 28.7833 | 13.0352 | 53.7409 | 65.1545 | 25.713 | 12.3641 | 48.7277
FECK4 M2 | 400 | 77.013 | 28.7833 | 13.0352 | 53.7409 | 65.1545 | 25.713 | 12.3641 | 48.7277
FECK4 R1 | 400 | 77.013 | 28.7833 | 13.0352 | 53.7409 | 65.1545 | 25.713 | 12.3641 | 48.7277
FECK4 R2 | 400 | 77.013 | 28.7833 | 13.0352 | 53.7409 | 65.1545 | 25.713 | 12.3641 | 48.7277
FENW4A | 400 | 111.5815 | 38.6474 | 14.7867 | 69.4424 | 94.0194 | 35.8011 | 7.7499 | 58.3803
FERR2 M1 | 275 | 57.2111 | 20.5952 | 11.3294 | 40.4554 | 58.4206 | 22.0428 | 11.4309 | 42.6041
FERR2 M2 | 275 | 56.9035 | 20.4347 | 15.124 | 44.023 | 60.6791 | 22.7098 | 14.1222 | 46.2388
FERR2 R1 | 275 | 61.3863 | 22.0222 | 11.7808 | 42.9249 | 61.3378 | 23.3216 | 10.1353 | 43.117
FERR2 R2 | 275 | 61.3863 | 22.0222 | 11.7808 | 42.9249 | 61.3378 | 23.3216 | 10.1353 | 43.117
FERR2A | 275 | 56.9246 | 20.3423 | 12.6306 | 41.3989 | 60.5005 | 22.6049 | 11.5545 | 43.5226
FERR2B | 275 | 56.6885 | 20.2625 | 9.1909 | 37.8464 | 57.6429 | 21.7533 | 8.9099 | 39.6737
FERR4A | 400 | 74.7385 | 26.4774 | 9.5171 | 46.9618 | 65.0352 | 24.6539 | 8.0401 | 42.9059
FFES2 Term205 | 275 | 35.2134 | 13.1702 | 2.654 | 21.2796 | 34.1493 | 13.4042 | 2.3186 | 21.275
FFES2 Term210 | 275 | 35.164 | 13.1716 | 2.6366 | 21.2641 | 34.6332 | 13.5914 | 2.3432 | 21.5643
FIDF2 M1 | 275 | 50.7937 | 18.1919 | 15.5653 | 41.2925 | 50.9999 | 19.0186 | 14.1195 | 41.0159
FIDF2 M2 | 275 | 50.0359 | 17.8866 | 15.3941 | 40.6896 | 49.1778 | 18.3381 | 13.397 | 39.331
FIDF2 M3 | 275 | 62.3288 | 22.2875 | 16.0055 | 47.5248 | 58.627 | 22.1992 | 13.5872 | 44.9816
FIDF2 M4 | 275 | 62.8726 | 22.4781 | 16.1377 | 47.9266 | 60.5695 | 22.9026 | 14.2305 | 46.6196
FIDF2 R1 | 275 | 50.7937 | 18.1919 | 15.5653 | 41.2925 | 50.9999 | 19.0186 | 14.1195 | 41.0159
FIDF2 R2 | 275 | 62.8726 | 22.4781 | 16.1377 | 47.9266 | 60.5695 | 22.9026 | 14.2305 | 46.6196
FLEE4 MC1 | 400 | 102.9618 | 36.8989 | 20.5636 | 72.7465 | 83.2029 | 32.6521 | 15.4367 | 61.6137
FLEE4 MC2 | 400 | 102.9618 | 36.8989 | 20.5636 | 72.7465 | 83.2029 | 32.6521 | 15.4367 | 61.6137
FLEE4 MC3 | 400 | 102.9618 | 36.8989 | 20.5636 | 72.7465 | 83.2029 | 32.6521 | 15.4367 | 61.6137
FLEE4 MC4 | 400 | 102.9618 | 36.8989 | 20.5636 | 72.7465 | 83.2029 | 32.6521 | 15.4367 | 61.6137
FLIB4 M1 | 400 | 115.8554 | 40.3938 | 30.1743 | 87.2998 | 119.2493 | 44.7755 | 29.5351 | 92.8572
FLIB4 M2 | 400 | 115.8554 | 40.3938 | 30.1743 | 87.2998 | 119.2493 | 44.7755 | 29.5351 | 92.8572
FOUR2 MC1 | 275 | 38.504 | 15.0926 | 4.9008 | 26.2449 | 31.6361 | 12.9936 | 3.8621 | 22.2378
FOUR2 MC2 | 275 | 38.504 | 15.0926 | 4.9008 | 26.2449 | 31.6361 | 12.9936 | 3.8621 | 22.2378
FROD2 MC1 | 275 | 50.7483 | 18.1278 | 16.3526 | 41.9892 | 54.073 | 19.875 | 17.5062 | 45.6136
FROD2 MC3 | 275 | 50.7397 | 17.8773 | 10.8016 | 36.0839 | 53.4094 | 19.5872 | 10.7236 | 38.424
FROD4 M1 | 400 | 88.2535 | 31.7765 | 29.4683 | 74.407 | 83.1231 | 31.2843 | 27.6145 | 71.8572
FROD4 R1 | 400 | 88.2535 | 31.7765 | 29.4683 | 74.407 | 83.1231 | 31.2843 | 27.6145 | 71.8572
GART4A | 400 | 112.6266 | 38.1004 | 16.0239 | 69.9061 | 86.3258 | 32.6423 | 7.7179 | 53.8811
GART4B | 400 | 121.774 | 40.9186 | 18.9146 | 76.7822 | 101.0309 | 37.9173 | 10.376 | 63.9992
GRAI4 M1 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 M2 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 M3 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 M4 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 M5 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 M6 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 M7 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 R1/2 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 R3 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 R4 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 R5 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 R6 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GRAI4 R7 | 400 | 135.56 | 47.4037 | 44.0708 | 111.1097 | 126.0405 | 47.3545 | 40.6078 | 107.5771
GREN1 M1 | 132 | 40.5309 | 14.8492 | 10.3897 | 31.3896 | 44.4166 | 17.7189 | 10.1737 | 35.232
GREN1 M2 | 132 | 38.8754 | 14.3441 | 10.8473 | 31.133 | 39.6253 | 15.5848 | 10.0041 | 32.0444
GREN1 R1 | 132 | 40.5309 | 14.8492 | 10.3897 | 31.3896 | 44.4166 | 17.7189 | 10.1737 | 35.232
GREN1 R2 | 132 | 38.8754 | 14.3441 | 10.8473 | 31.133 | 39.6253 | 15.5848 | 10.0041 | 32.0444
GREN4 M1 | 400 | 79.2826 | 29.6137 | 12.9708 | 54.8509 | 53.3183 | 21.6115 | 8.8713 | 39.4345
GREN4 M2 | 400 | 79.2826 | 29.6137 | 12.9708 | 54.8509 | 53.3183 | 21.6115 | 8.8713 | 39.4345
GREN4 R1 | 400 | 79.2826 | 29.6137 | 12.9708 | 54.8509 | 53.3183 | 21.6115 | 8.8713 | 39.4345
GREN4 R2 | 400 | 79.2826 | 29.6137 | 12.9708 | 54.8509 | 53.3183 | 21.6115 | 8.8713 | 39.4345
GRIW4 MC1 | 400 | 73.9897 | 26.3401 | 19.904 | 57.1545 | 61.5648 | 23.6251 | 12.5691 | 45.9801
GRIW4 MC2 | 400 | 73.9897 | 26.3401 | 19.904 | 57.1545 | 61.5648 | 23.6251 | 12.5691 | 45.9801
GRSA2 M1 | 275 | 56.8364 | 20.2898 | 17.3526 | 46.0467 | 58.4426 | 21.7253 | 16.3578 | 47.0821
GRSA2 M2 | 275 | 56.8364 | 20.2898 | 17.3526 | 46.0467 | 58.4426 | 21.7253 | 16.3578 | 47.0821
GRSA2 R1 | 275 | 56.8364 | 20.2898 | 17.3526 | 46.0467 | 58.4426 | 21.7253 | 16.3578 | 47.0821
GRSA2 R2 | 275 | 56.8364 | 20.2898 | 17.3526 | 46.0467 | 58.4426 | 21.7253 | 16.3578 | 47.0821
GRSB2 M3 | 275 | 57.1932 | 20.402 | 17.5566 | 46.4093 | 59.4028 | 22.0198 | 17.0949 | 48.2356
GRSB2 M4 | 275 | 57.1932 | 20.402 | 17.5566 | 46.4093 | 59.4028 | 22.0198 | 17.0949 | 48.2356
GRSB2 R3 | 275 | 57.1932 | 20.402 | 17.5566 | 46.4093 | 59.4028 | 22.0198 | 17.0949 | 48.2356
GRSB2 R4 | 275 | 57.1932 | 20.402 | 17.5566 | 46.4093 | 59.4028 | 22.0198 | 17.0949 | 48.2356
HACK2A | 275 | 66.3095 | 23.2618 | 11.2384 | 44.1356 | 68.4478 | 25.5179 | 11.1225 | 47.2102
HACK2B | 275 | 65.1746 | 22.8891 | 11.2119 | 43.582 | 67.8548 | 25.2906 | 11.0561 | 46.8223
HACK4 M1 | 400 | 95.2789 | 32.2021 | 24.2059 | 69.7466 | 112.0648 | 41.7971 | 24.2975 | 83.4075
HACK4 M2 | 400 | 95.2789 | 32.2021 | 24.2059 | 69.7466 | 112.0648 | 41.7971 | 24.2975 | 83.4075
HACK4 R1 | 400 | 95.2789 | 32.2021 | 24.2059 | 69.7466 | 112.0648 | 41.7971 | 24.2975 | 83.4075
HACK4 R2 | 400 | 95.2789 | 32.2021 | 24.2059 | 69.7466 | 112.0648 | 41.7971 | 24.2975 | 83.4075
HAMB4A | 400 | 69.097 | 24.5111 | 9.1713 | 43.8352 | 57.9016 | 22.4649 | 4.7799 | 36.5501
HAMB4A_HEYS | 400 | 69.097 | 24.5111 | 9.1713 | 43.8352 | 57.9016 | 22.4649 | 4.7799 | 36.5501
HAMB4A_PEWO | 400 | 69.097 | 24.5111 | 9.1713 | 43.8352 | 57.9016 | 22.4649 | 4.7799 | 36.5501
HAMB4B | 400 | 69.0735 | 24.5029 | 9.1713 | 43.8235 | 57.4344 | 22.2832 | 4.7848 | 36.298
HAMB4B_HEYS | 400 | 69.0735 | 24.5029 | 9.1713 | 43.8235 | 57.4344 | 22.2832 | 4.7848 | 36.298
HAMB4B_PEWO | 400 | 69.0735 | 24.5029 | 9.1713 | 43.8235 | 57.4344 | 22.2832 | 4.7848 | 36.298
HAMH1B | 132 | 45.824 | 15.8096 | 9.676 | 32.0342 | 54.6755 | 20.6122 | 6.3192 | 35.4692
HAMH1C | 132 | 44.8587 | 15.5851 | 8.4635 | 30.5042 | 52.9475 | 19.6836 | 7.8778 | 35.7146
HAMH4 M1 | 400 | 73.9382 | 27.3736 | 13.0621 | 51.7743 | 69.6688 | 27.1469 | 13.3324 | 51.7239
HAMH4 M2 | 400 | 73.9382 | 27.3736 | 13.0621 | 51.7743 | 69.6688 | 27.1469 | 13.3324 | 51.7239
HAMH4 R1 | 400 | 73.9382 | 27.3736 | 13.0621 | 51.7743 | 69.6688 | 27.1469 | 13.3324 | 51.7239
HAMH4 R2 | 400 | 73.9382 | 27.3736 | 13.0621 | 51.7743 | 69.6688 | 27.1469 | 13.3324 | 51.7239
HARK1 M1 | 132 | 26.1835 | 9.8163 | 6.2542 | 20.1365 | 30.9742 | 12.0872 | 6.9552 | 24.0491
HARK1 M2 | 132 | 26.1835 | 9.8163 | 6.2542 | 20.1365 | 30.9742 | 12.0872 | 6.9552 | 24.0491
HARK1 R1 | 132 | 25.4657 | 10.677 | 5.4318 | 20.5313 | 28.286 | 12.0318 | 6.4086 | 23.4241
HARK1 R2 | 132 | 28.7919 | 10.9845 | 6.9028 | 22.4372 | 33.836 | 13.4317 | 8.1276 | 27.1228
HARK1 R3 | 132 | 28.7919 | 10.9845 | 6.9028 | 22.4372 | 33.836 | 13.4317 | 8.1276 | 27.1228
HARK2 MC1 | 275 | 40.67 | 15.2353 | 10.4198 | 31.9659 | 43.2985 | 16.5741 | 11.0755 | 34.5148
HARK2 MC11 | 275 | 21.2457 | 8.3995 | 5.1384 | 17.0171 | 22.9391 | 9.102 | 6.1107 | 18.9829
HARK2 MC12 | 275 | 21.2457 | 8.3995 | 5.1384 | 17.0171 | 22.9391 | 9.102 | 6.1107 | 18.9829
HARK2 MC13 | 275 | 21.2457 | 8.3995 | 5.1384 | 17.0171 | 22.9391 | 9.102 | 6.1107 | 18.9829
HARK2 MC2 | 275 | 40.67 | 15.2353 | 10.4198 | 31.9659 | 43.2985 | 16.5741 | 11.0755 | 34.5148
HARK2 MC3 | 275 | 40.67 | 15.2353 | 10.4198 | 31.9659 | 43.2985 | 16.5741 | 11.0755 | 34.5148
HARK2 MC4 | 275 | 40.67 | 15.2353 | 10.4198 | 31.9659 | 43.2985 | 16.5741 | 11.0755 | 34.5148
HARK2 MC6 | 275 | 40.67 | 15.2353 | 10.4198 | 31.9659 | 43.2985 | 16.5741 | 11.0755 | 34.5148
HARK2 MC8 | 275 | 21.2457 | 8.3995 | 5.1384 | 17.0171 | 22.9391 | 9.102 | 6.1107 | 18.9829
HARK2 MC9 | 275 | 21.2457 | 8.3995 | 5.1384 | 17.0171 | 22.9391 | 9.102 | 6.1107 | 18.9829
HARK4 M1 | 400 | 65.3619 | 24.4966 | 11.3865 | 46.03 | 51.5832 | 20.2221 | 10.3119 | 38.9102
HARK4 M2 | 400 | 65.3619 | 24.4966 | 11.3865 | 46.03 | 51.5832 | 20.2221 | 10.3119 | 38.9102
HARK4 R1 | 400 | 65.3619 | 24.4966 | 11.3865 | 46.03 | 51.5832 | 20.2221 | 10.3119 | 38.9102
HARK4 R2 | 400 | 65.3619 | 24.4966 | 11.3865 | 46.03 | 51.5832 | 20.2221 | 10.3119 | 38.9102
HARM2 MC1 | 275 | 67.6927 | 24.3528 | 14.8326 | 49.2726 | 58.1874 | 22.7188 | 9.6788 | 41.8081
HARM2 MC2 | 275 | 67.6927 | 24.3528 | 14.8326 | 49.2726 | 58.1874 | 22.7188 | 9.6788 | 41.8081
HARM2 MC3 | 275 | 67.6927 | 24.3528 | 14.8326 | 49.2726 | 58.1874 | 22.7188 | 9.6788 | 41.8081
HARM2 MC4 | 275 | 67.6927 | 24.3528 | 14.8326 | 49.2726 | 58.1874 | 22.7188 | 9.6788 | 41.8081
HATL2 M1 | 275 | 93.9641 | 32.5324 | 24.9934 | 71.0011 | 94.3583 | 34.9832 | 25.8111 | 75.2848
HATL2 M2 | 275 | 93.9641 | 32.5324 | 24.9934 | 71.0011 | 94.3583 | 34.9832 | 25.8111 | 75.2848
HATL2 R1 | 275 | 93.9641 | 32.5324 | 24.9934 | 71.0011 | 94.3583 | 34.9832 | 25.8111 | 75.2848
HATL2 R2 | 275 | 93.9641 | 32.5324 | 24.9934 | 71.0011 | 94.3583 | 34.9832 | 25.8111 | 75.2848
HAWP2 MC1 | 275 | 89.2531 | 31.4519 | 21.623 | 66.1027 | 81.073 | 31.1872 | 15.4691 | 59.5745
HAWP2 MC2 | 275 | 89.2531 | 31.4519 | 21.623 | 66.1027 | 81.073 | 31.1872 | 15.4691 | 59.5745
HAWP2 MC3 | 275 | 89.2531 | 31.4519 | 21.623 | 66.1027 | 81.073 | 31.1872 | 15.4691 | 59.5745
HAWP2 MC4 | 275 | 89.2531 | 31.4519 | 21.623 | 66.1027 | 81.073 | 31.1872 | 15.4691 | 59.5745
HEDO2 M1 | 275 | 77.6833 | 26.9135 | 23.3181 | 61.3796 | 78.3826 | 28.7609 | 23.7384 | 64.4124
HEDO2 M2 | 275 | 77.6833 | 26.9135 | 23.3181 | 61.3796 | 78.3826 | 28.7609 | 23.7384 | 64.4124
HEDO2 R1 | 275 | 77.6833 | 26.9135 | 23.3181 | 61.3796 | 78.3826 | 28.7609 | 23.7384 | 64.4124
HEDO2 R2 | 275 | 77.6833 | 26.9135 | 23.3181 | 61.3796 | 78.3826 | 28.7609 | 23.7384 | 64.4124
HEYS1 M1 | 132 | 38.3836 | 12.9761 | 12.5332 | 30.8843 | 44.3367 | 16.1765 | 14.2637 | 37.1407
HEYS1 M2 | 132 | 38.3836 | 12.9761 | 12.5332 | 30.8843 | 44.3367 | 16.1765 | 14.2637 | 37.1407
HEYS1 R1 | 132 | 38.3836 | 12.9761 | 12.5332 | 30.8843 | 44.3367 | 16.1765 | 14.2637 | 37.1407
HEYS1 R2 | 132 | 38.3836 | 12.9761 | 12.5332 | 30.8843 | 44.3367 | 16.1765 | 14.2637 | 37.1407
HEYS4 M1 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 M2 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 M3 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 M4 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 M5 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 R1/2 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 R3/4 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HEYS4 R5 | 400 | 96.8642 | 34.7982 | 32.7543 | 81.9664 | 100.8047 | 37.9662 | 34.5753 | 88.2676
HIBU4 M1 | 400 | 101.9691 | 34.1783 | 25.8861 | 74.2215 | 120.5491 | 44.4513 | 27.8348 | 90.6984
HIBU4 M2 | 400 | 101.9691 | 34.1783 | 25.8861 | 74.2215 | 120.5491 | 44.4513 | 27.8348 | 90.6984
HIBU4 R1 | 400 | 101.9691 | 34.1783 | 25.8861 | 74.2215 | 120.5491 | 44.4513 | 27.8348 | 90.6984
HIBU4 R2 | 400 | 101.9691 | 34.1783 | 25.8861 | 74.2215 | 120.5491 | 44.4513 | 27.8348 | 90.6984
HIGM2 M1 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM2 M2 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM2 M3 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM2 R1 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM2 R4 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM2 R5 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM2 R6 | 275 | 61.4006 | 22.6973 | 16.4276 | 48.5265 | 56.5244 | 22.271 | 12.1233 | 43.6192
HIGM4 MC1 | 400 | 81.0371 | 29.627 | 18.2953 | 60.1942 | 65.4974 | 25.6184 | 11.3604 | 47.5903
HIGM4 MC2 | 400 | 81.0371 | 29.627 | 18.2953 | 60.1942 | 65.4974 | 25.6184 | 11.3604 | 47.5903
HIGM4A | 400 | 64.0276 | 23.2255 | 9.1752 | 42.021 | 53.795 | 20.7466 | 4.9082 | 34.2483
HINP2 M1 | 275 | 22.0289 | 7.9251 | 6.7237 | 17.9315 | 22.6523 | 8.4841 | 6.0511 | 18.0495
HINP2 M2 | 275 | 22.3522 | 8.0505 | 6.7469 | 18.1321 | 24.7478 | 9.328 | 6.1467 | 19.3385
HINP4 M1 | 400 | 53.4477 | 19.9539 | 8.7614 | 36.9805 | 40.7185 | 16.4493 | 5.7876 | 29.0504
HINP4 M2 | 400 | 53.4477 | 19.9539 | 8.7614 | 36.9805 | 40.7185 | 16.4493 | 5.7876 | 29.0504
HINP4 M3 | 400 | 53.4477 | 19.9539 | 8.7614 | 36.9805 | 40.7185 | 16.4493 | 5.7876 | 29.0504
HINP4 M4 | 400 | 53.4477 | 19.9539 | 8.7614 | 36.9805 | 40.7185 | 16.4493 | 5.7876 | 29.0504
HINP4 R1/2 | 400 | 53.4477 | 19.9539 | 8.7614 | 36.9805 | 40.7185 | 16.4493 | 5.7876 | 29.0504
HINP4 R3/4 | 400 | 53.4477 | 19.9539 | 8.7614 | 36.9805 | 40.7185 | 16.4493 | 5.7876 | 29.0504
HUMR4 M1 | 400 | 116.7966 | 39.8013 | 34.5435 | 90.831 | 105.2936 | 38.8274 | 29.9296 | 84.8398
HUMR4 M2 | 400 | 116.7966 | 39.8013 | 34.5435 | 90.831 | 105.2936 | 38.8274 | 29.9296 | 84.8398
HUMR4 R1 | 400 | 116.7966 | 39.8013 | 34.5435 | 90.831 | 105.2936 | 38.8274 | 29.9296 | 84.8398
HUMR4 R2 | 400 | 116.7966 | 39.8013 | 34.5435 | 90.831 | 105.2936 | 38.8274 | 29.9296 | 84.8398
HURS2 MC1 | 275 | 74.6652 | 26.3296 | 20.0719 | 57.3076 | 77.495 | 30.8439 | 16.7546 | 60.3745
HURS2 MC2 | 275 | 74.6652 | 26.3296 | 20.0719 | 57.3076 | 77.495 | 30.8439 | 16.7546 | 60.3745
HURS2 MC3 | 275 | 74.6652 | 26.3296 | 20.0719 | 57.3076 | 77.495 | 30.8439 | 16.7546 | 60.3745
HURS2 MC4 | 275 | 74.6652 | 26.3296 | 20.0719 | 57.3076 | 77.495 | 30.8439 | 16.7546 | 60.3745
HUTT4 MC1 | 400 | 70.3723 | 26.389 | 20.4856 | 57.8054 | 46.9806 | 19.0083 | 11.0285 | 37.9104
HUTT4 MC2 | 400 | 70.3723 | 26.389 | 20.4856 | 57.8054 | 46.9806 | 19.0083 | 11.0285 | 37.9104
HUTT4 MC3 | 400 | 70.3723 | 26.389 | 20.4856 | 57.8054 | 46.9806 | 19.0083 | 11.0285 | 37.9104
HUTT4 MC4 | 400 | 70.3723 | 26.389 | 20.4856 | 57.8054 | 46.9806 | 19.0083 | 11.0285 | 37.9104
IMPP4 MC1 | 400 | 54.0547 | 19.9791 | 11.8786 | 40.1333 | 46.2956 | 17.8994 | 9.5581 | 34.8718
IMPP4 MC2 | 400 | 54.0547 | 19.9791 | 11.8786 | 40.1333 | 46.2956 | 17.8994 | 9.5581 | 34.8718
INDQ4 MC1 | 400 | 34.0571 | 12.8041 | 5.481 | 23.5888 | 36.1626 | 14.0676 | 6.7728 | 26.6675
INDQ4 MC2 | 400 | 34.0571 | 12.8041 | 5.481 | 23.5888 | 36.1626 | 14.0676 | 6.7728 | 26.6675
INDQ4 MC3 | 400 | 34.0571 | 12.8041 | 5.481 | 23.5888 | 36.1626 | 14.0676 | 6.7728 | 26.6675
INDQ4 MC4 | 400 | 34.0571 | 12.8041 | 5.481 | 23.5888 | 36.1626 | 14.0676 | 6.7728 | 26.6675
IROA1 M1 | 132 | 41.8666 | 15.1127 | 10.3864 | 31.759 | 51.3409 | 19.5207 | 11.8584 | 39.4648
IROA1 M2 | 132 | 41.8666 | 15.1127 | 10.3864 | 31.759 | 51.3409 | 19.5207 | 11.8584 | 39.4648
IROA1 R1 | 132 | 43.6795 | 15.706 | 10.6853 | 32.8969 | 52.6224 | 19.9104 | 12.2908 | 40.4483
IROA1 R2 | 132 | 30.3449 | 10.9666 | 8.8507 | 24.3598 | 37.2886 | 14.0336 | 9.921 | 29.7674
IROA2 MC1 | 275 | 57.6142 | 21.1767 | 10.983 | 40.9314 | 55.9782 | 21.7399 | 11.1227 | 41.8676
IROA2 MC2 | 275 | 57.6142 | 21.1767 | 10.983 | 40.9314 | 55.9782 | 21.7399 | 11.1227 | 41.8676
IROA2 MC3 | 275 | 57.6142 | 21.1767 | 10.983 | 40.9314 | 55.9782 | 21.7399 | 11.1227 | 41.8676
IROA2 MC4 | 275 | 57.6142 | 21.1767 | 10.983 | 40.9314 | 55.9782 | 21.7399 | 11.1227 | 41.8676
IROA2 MC5 | 275 | 57.6142 | 21.1767 | 10.983 | 40.9314 | 55.9782 | 21.7399 | 11.1227 | 41.8676
IRON1 M1 | 132 | 26.9468 | 10.4484 | 8.8239 | 23.6002 | 29.8654 | 11.714 | 9.7809 | 26.3471
IRON1 M2 | 132 | 26.8292 | 10.4066 | 8.7277 | 23.4448 | 29.5452 | 11.6038 | 9.5951 | 26.0054
IRON1 R1 | 132 | 17.6113 | 6.4022 | 6.2895 | 15.3435 | 20.0532 | 7.3292 | 7.2505 | 17.6155
IRON1 R2 | 132 | 17.6113 | 6.4022 | 6.2895 | 15.3435 | 20.0532 | 7.3292 | 7.2505 | 17.6155
IRON4 M1 | 400 | 70.577 | 26.1187 | 12.9303 | 49.8677 | 59.3732 | 23.4248 | 10.7008 | 43.8285
IRON4 M2 | 400 | 70.577 | 26.1187 | 12.9303 | 49.8677 | 59.3732 | 23.4248 | 10.7008 | 43.8285
IRON4 R1 | 400 | 70.577 | 26.1187 | 12.9303 | 49.8677 | 59.3732 | 23.4248 | 10.7008 | 43.8285
IRON4 R2 | 400 | 70.577 | 26.1187 | 12.9303 | 49.8677 | 59.3732 | 23.4248 | 10.7008 | 43.8285
IVER2 M1 | 275 | 65.6277 | 23.9507 | 16.2951 | 50.1665 | 70.5227 | 26.8831 | 16.8229 | 54.8413
IVER2 M2 | 275 | 65.6277 | 23.9507 | 16.2951 | 50.1665 | 70.5227 | 26.8831 | 16.8229 | 54.8413
IVER2 R1 | 275 | 65.6277 | 23.9507 | 16.2951 | 50.1665 | 70.5227 | 26.8831 | 16.8229 | 54.8413
IVER2 R2 | 275 | 67.911 | 24.6513 | 15.466 | 50.3282 | 68.2491 | 26.352 | 14.281 | 51.5484
IVER4A | 400 | 45.7269 | 16.7709 | 5.6357 | 29.3533 | 43.3703 | 16.613 | 5.8929 | 29.3872
IVER4B | 400 | 43.7907 | 16.1215 | 5.2536 | 28.0529 | 41.0398 | 15.944 | 5.039 | 27.5872
JORD2 MC1 | 275 | 49.6302 | 18.6878 | 8.7734 | 35.2019 | 49.1428 | 20.2836 | 7.3293 | 36.0146
JORD2 MC2 | 275 | 49.6302 | 18.6878 | 8.7734 | 35.2019 | 49.1428 | 20.2836 | 7.3293 | 36.0146
KEAD4 M2 | 400 | 121.2799 | 42.0398 | 33.5113 | 92.9646 | 111.9964 | 41.5966 | 30.3884 | 89.2149
KEAD4 M3 | 400 | 111.645 | 38.9625 | 29.6237 | 84.725 | 90.5538 | 34.1629 | 21.2631 | 69.5768
KEAD4 R2 | 400 | 121.2799 | 42.0398 | 33.5113 | 92.9646 | 111.9964 | 41.5966 | 30.3884 | 89.2149
KEAD4 R3 | 400 | 96.4746 | 34.8836 | 22.5208 | 71.8537 | 75.6748 | 29.2519 | 16.8291 | 58.1975
KEAR2 M1 | 275 | 74.1315 | 26.5987 | 18.8337 | 56.4499 | 79.8933 | 30.1924 | 19.6011 | 62.2996
KEAR2 M2 | 275 | 74.1315 | 26.5987 | 18.8337 | 56.4499 | 79.8933 | 30.1924 | 19.6011 | 62.2996
KEAR2 R1 | 275 | 74.1315 | 26.5987 | 18.8337 | 56.4499 | 79.8933 | 30.1924 | 19.6011 | 62.2996
KEAR2 R2 | 275 | 74.1315 | 26.5987 | 18.8337 | 56.4499 | 79.8933 | 30.1924 | 19.6011 | 62.2996
KEMS4 M1 | 400 | 128.5795 | 43.9292 | 30.6638 | 92.7891 | 110.0774 | 42.0299 | 22.1739 | 81.6132
KEMS4 M2 | 400 | 128.5795 | 43.9292 | 30.6638 | 92.7891 | 110.0774 | 42.0299 | 22.1739 | 81.6132
KEMS4 R1 | 400 | 128.5795 | 43.9292 | 30.6638 | 92.7891 | 110.0774 | 42.0299 | 22.1739 | 81.6132
KEMS4 R2 | 400 | 128.5795 | 43.9292 | 30.6638 | 92.7891 | 110.0774 | 42.0299 | 22.1739 | 81.6132
KENG4 M1 | 400 | 105.1832 | 35.0838 | 26.7 | 76.316 | 124.5752 | 45.691 | 29.7955 | 94.4124
KENG4 M2 | 400 | 105.1832 | 35.0838 | 26.7 | 76.316 | 124.5752 | 45.691 | 29.7955 | 94.4124
KENG4 R1 | 400 | 105.1832 | 35.0838 | 26.7 | 76.316 | 124.5752 | 45.691 | 29.7955 | 94.4124
KENG4 R2 | 400 | 105.1832 | 35.0838 | 26.7 | 76.316 | 124.5752 | 45.691 | 29.7955 | 94.4124
KIBY2 M1 | 275 | 71.7213 | 25.3376 | 17.8045 | 53.6373 | 75.9476 | 28.6611 | 17.0509 | 57.5838
KIBY2 M2 | 275 | 71.7213 | 25.3376 | 17.8045 | 53.6373 | 75.9476 | 28.6611 | 17.0509 | 57.5838
KIBY2 R1 | 275 | 61.94 | 22.2586 | 14.865 | 46.3435 | 60.6288 | 23.0129 | 13.6656 | 46.2108
KIBY2 R2 | 275 | 61.94 | 22.2586 | 14.865 | 46.3435 | 60.6288 | 23.0129 | 13.6656 | 46.2108
KILL4 M1 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 M2 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 M3 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 M4 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 M5 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 M9 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 R1/2 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 R3/4 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 R5 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KILL4 R9 | 400 | 123.777 | 43.0659 | 45.4584 | 106.3628 | 115.095 | 42.6009 | 40.341 | 100.5877
KINO1 M1 | 132 | 29.0615 | 10.2403 | 10.5116 | 24.9936 | 35.5985 | 13.1622 | 12.6944 | 31.3085
KINO1 M2 | 132 | 29.0615 | 10.2403 | 10.5116 | 24.9936 | 35.5985 | 13.1622 | 12.6944 | 31.3085
KINO1 R1 | 132 | 29.0615 | 10.2403 | 10.5116 | 24.9936 | 35.5985 | 13.1622 | 12.6944 | 31.3085
KINO1 R2 | 132 | 29.0615 | 10.2403 | 10.5116 | 24.9936 | 35.5985 | 13.1622 | 12.6944 | 31.3085
KINO1A | 132 | 28.7235 | 10.0425 | 6.537 | 20.7391 | 35.0964 | 13.0082 | 7.7269 | 26.1233
KINO1B | 132 | 24.0664 | 8.9592 | 1.6585 | 14.3287 | 25.9608 | 10.4638 | 0.94757 | 15.7457
KINO4 M1 | 400 | 121.5491 | 42.9731 | 39.0264 | 99.7996 | 114.4033 | 43.4039 | 35.0335 | 96.4159
KINO4 M2 | 400 | 121.5491 | 42.9731 | 39.0264 | 99.7996 | 114.4033 | 43.4039 | 35.0335 | 96.4159
KINO4 M3 | 400 | 121.5491 | 42.9731 | 39.0264 | 99.7996 | 114.4033 | 43.4039 | 35.0335 | 96.4159
KINO4 M4 | 400 | 121.5491 | 42.9731 | 39.0264 | 99.7996 | 114.4033 | 43.4039 | 35.0335 | 96.4159
KINO4 R1/2 | 400 | 121.5491 | 42.9731 | 39.0264 | 99.7996 | 114.4033 | 43.4039 | 35.0335 | 96.4159
KINO4 R3/4 | 400 | 121.5491 | 42.9731 | 39.0264 | 99.7996 | 114.4033 | 43.4039 | 35.0335 | 96.4159
KIRK2 MC1 | 275 | 53.183 | 19.2949 | 11.9569 | 39.244 | 54.3522 | 20.8898 | 12.9195 | 42.4622
KIRK2 MC2 | 275 | 53.183 | 19.2949 | 11.9569 | 39.244 | 54.3522 | 20.8898 | 12.9195 | 42.4622
KIRK2 MC3 | 275 | 53.183 | 19.2949 | 11.9569 | 39.244 | 54.3522 | 20.8898 | 12.9195 | 42.4622
KIRK2 MC4 | 275 | 53.183 | 19.2949 | 11.9569 | 39.244 | 54.3522 | 20.8898 | 12.9195 | 42.4622
KIRK2A | 275 | 52.7183 | 18.6405 | 6.3175 | 32.6792 | 50.5686 | 19.757 | 7.9838 | 35.9245
KITW2 MC1 | 275 | 60.5546 | 22.0452 | 11.8016 | 42.9783 | 59.3641 | 23.1747 | 10.3585 | 43.1326
KITW2 MC2 | 275 | 60.5546 | 22.0452 | 11.8016 | 42.9783 | 59.3641 | 23.1747 | 10.3585 | 43.1326
KITW2 MC3 | 275 | 60.5546 | 22.0452 | 11.8016 | 42.9783 | 59.3641 | 23.1747 | 10.3585 | 43.1326
KITW2 MC4 | 275 | 60.5546 | 22.0452 | 11.8016 | 42.9783 | 59.3641 | 23.1747 | 10.3585 | 43.1326
KNAR2 MC1 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
KNAR2 MC1 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
KNAR2 MC1 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
KNAR2 MC1 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
KNAR2 MC2 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
KNAR2 MC2 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
KNAR2 MC2 | 275 | 28.9438 | 11.666 | 2.4415 | 18.9398 | 26.5787 | 10.9863 | 3.5065 | 19.0434
LACK2 M1 | 275 | 64.1287 | 22.1682 | 18.0281 | 49.3787 | 68.2412 | 25.0763 | 19.7717 | 55.235
LACK2 M2 | 275 | 64.1287 | 22.1682 | 18.0281 | 49.3787 | 68.2412 | 25.0763 | 19.7717 | 55.235
LACK2 R1 | 275 | 64.1287 | 22.1682 | 18.0281 | 49.3787 | 68.2412 | 25.0763 | 19.7717 | 55.235
LACK2 R2 | 275 | 64.1287 | 22.1682 | 18.0281 | 49.3787 | 68.2412 | 25.0763 | 19.7717 | 55.235
LACK4 M1 | 400 | 77.1961 | 28.1243 | 24.3853 | 64.1591 | 68.516 | 26.081 | 21.7631 | 58.6473
LACK4 M2 | 400 | 77.1961 | 28.1243 | 24.3853 | 64.1591 | 68.516 | 26.081 | 21.7631 | 58.6473
LACK4 R1 | 400 | 77.1961 | 28.1243 | 24.3853 | 64.1591 | 68.516 | 26.081 | 21.7631 | 58.6473
LACK4 R2 | 400 | 77.1961 | 28.1243 | 24.3853 | 64.1591 | 68.516 | 26.081 | 21.7631 | 58.6473
LAGA4 M1 | 400 | 40.3661 | 14.8455 | 7.9447 | 28.9394 | 42.1596 | 16.2007 | 9.2323 | 32.1436
LAGA4 M2 | 400 | 40.3661 | 14.8455 | 7.9447 | 28.9394 | 42.1596 | 16.2007 | 9.2323 | 32.1436
LAGA4 R1 | 400 | 40.3661 | 14.8455 | 7.9447 | 28.9394 | 42.1596 | 16.2007 | 9.2323 | 32.1436
LAGA4 R2 | 400 | 40.3661 | 14.8455 | 7.9447 | 28.9394 | 42.1596 | 16.2007 | 9.2323 | 32.1436
LALE2 MC1 | 275 | 59.1036 | 20.9948 | 16.9539 | 46.6451 | 65.4546 | 25.2162 | 16.3406 | 52.0016
LALE2 MC2 | 275 | 59.1036 | 20.9948 | 16.9539 | 46.6451 | 65.4546 | 25.2162 | 16.3406 | 52.0016
LALE2 MC3 | 275 | 59.1036 | 20.9948 | 16.9539 | 46.6451 | 65.4546 | 25.2162 | 16.3406 | 52.0016
LALE2 MC4 | 275 | 59.1036 | 20.9948 | 16.9539 | 46.6451 | 65.4546 | 25.2162 | 16.3406 | 52.0016
LAND4 MC1 | 400 | 32.8114 | 12.2602 | 5.948 | 23.2866 | 32.6547 | 12.7739 | 5.7788 | 23.8439
LAND4 MC2 | 400 | 32.8114 | 12.2602 | 5.948 | 23.2866 | 32.6547 | 12.7739 | 5.7788 | 23.8439
LEGA4 M1 | 400 | 88.1633 | 31.8187 | 19.4218 | 64.4203 | 67.8132 | 26.774 | 12.2823 | 50.1465
LEGA4 M2 | 400 | 88.1633 | 31.8187 | 19.4218 | 64.4203 | 67.8132 | 26.774 | 12.2823 | 50.1465
LEGA4 R1 | 400 | 88.1633 | 31.8187 | 19.4218 | 64.4203 | 67.8132 | 26.774 | 12.2823 | 50.1465
LEGA4 R2 | 400 | 88.1633 | 31.8187 | 19.4218 | 64.4203 | 67.8132 | 26.774 | 12.2823 | 50.1465
LEIS1 M1 | 132 | 65.9958 | 23.265 | 21.7804 | 54.6821 | 75.252 | 27.307 | 26.5646 | 65.1826
LEIS1 M2 | 132 | 65.9958 | 23.265 | 21.7804 | 54.6821 | 75.252 | 27.307 | 26.5646 | 65.1826
LEIS1 R1 | 132 | 65.9958 | 23.265 | 21.7804 | 54.6821 | 75.252 | 27.307 | 26.5646 | 65.1826
LEIS1 R2 | 132 | 65.9958 | 23.265 | 21.7804 | 54.6821 | 75.252 | 27.307 | 26.5646 | 65.1826
LISD2 M1 | 275 | 66.4208 | 23.5881 | 16.1766 | 49.5352 | 71.0238 | 26.9878 | 15.7602 | 53.9267
LISD2 M2 | 275 | 66.4208 | 23.5881 | 16.1766 | 49.5352 | 71.0238 | 26.9878 | 15.7602 | 53.9267
LISD2 R1 | 275 | 66.4208 | 23.5881 | 16.1766 | 49.5352 | 71.0238 | 26.9878 | 15.7602 | 53.9267
LISD2 R2 | 275 | 66.4208 | 23.5881 | 16.1766 | 49.5352 | 71.0238 | 26.9878 | 15.7602 | 53.9267
LITB4 Term500 | 400 | 79.0589 | 28.0198 | 9.0167 | 48.6427 | 70.4384 | 26.5723 | 11.7918 | 49.3708
LITT4 M1 | 400 | 123.6507 | 42.2561 | 28.3776 | 88.1368 | 113.2837 | 43.2389 | 23.5435 | 84.6925
LITT4 M2 | 400 | 123.6507 | 42.2561 | 28.3776 | 88.1368 | 113.2837 | 43.2389 | 23.5435 | 84.6925
LITT4 M3 | 400 | 123.6507 | 42.2561 | 28.3776 | 88.1368 | 113.2837 | 43.2389 | 23.5435 | 84.6925
LITT4 R1 | 400 | 123.6507 | 42.2561 | 28.3776 | 88.1368 | 113.2837 | 43.2389 | 23.5435 | 84.6925
LITT4 R2 | 400 | 123.6507 | 42.2561 | 28.3776 | 88.1368 | 113.2837 | 43.2389 | 23.5435 | 84.6925
LITT4 R3 | 400 | 123.6507 | 42.2561 | 28.3776 | 88.1368 | 113.2837 | 43.2389 | 23.5435 | 84.6925
LOFI4A | 400 | 96.2261 | 32.8216 | 9.5545 | 55.9713 | 80.3672 | 31.087 | 4.6785 | 48.6422
LOFI4A_KEMS | 400 | 96.2261 | 32.8216 | 9.5545 | 55.9713 | 80.3672 | 31.087 | 4.6785 | 48.6422
LOFI4A_LITT | 400 | 96.2261 | 32.8216 | 9.5545 | 55.9713 | 80.3672 | 31.087 | 4.6785 | 48.6422
LOFI4A_ROWD | 400 | 96.2261 | 32.8216 | 9.5545 | 55.9713 | 80.3672 | 31.087 | 4.6785 | 48.6422
LOFI4B | 400 | 96.9451 | 33.0738 | 9.5382 | 56.3115 | 82.6433 | 31.9971 | 4.6941 | 49.9449
LOFI4B_KEMS | 400 | 96.9451 | 33.0738 | 9.5382 | 56.3115 | 82.6433 | 31.9971 | 4.6941 | 49.9449
LOFI4B_LITT | 400 | 96.9451 | 33.0738 | 9.5382 | 56.3115 | 82.6433 | 31.9971 | 4.6941 | 49.9449
LOFI4B_ROWD | 400 | 96.9451 | 33.0738 | 9.5382 | 56.3115 | 82.6433 | 31.9971 | 4.6941 | 49.9449
LOVE4 M1 | 400 | 94.7411 | 33.8128 | 18.2138 | 66.0322 | 82.6681 | 31.9569 | 15.5598 | 60.7537
LOVE4 M2 | 400 | 94.7411 | 33.8128 | 18.2138 | 66.0322 | 82.6681 | 31.9569 | 15.5598 | 60.7537
LOVE4 R1 | 400 | 94.7411 | 33.8128 | 18.2138 | 66.0322 | 82.6681 | 31.9569 | 15.5598 | 60.7537
LOVE4 R2 | 400 | 94.7411 | 33.8128 | 18.2138 | 66.0322 | 82.6681 | 31.9569 | 15.5598 | 60.7537
MACC2 MC1 | 275 | 55.8415 | 20.605 | 13.6147 | 42.7545 | 52.5753 | 20.2816 | 11.7665 | 40.4491
MACC2 MC2 | 275 | 55.8415 | 20.605 | 13.6147 | 42.7545 | 52.5753 | 20.2816 | 11.7665 | 40.4491
MACC4 MC1 | 400 | 79.2757 | 29.7792 | 22.5051 | 64.6192 | 60.7255 | 24.2446 | 14.9795 | 49.2665
MACC4 MC2 | 400 | 79.2757 | 29.7792 | 22.5051 | 64.6192 | 60.7255 | 24.2446 | 14.9795 | 49.2665
MACC4 MC3 | 400 | 79.2757 | 29.7792 | 22.5051 | 64.6192 | 60.7255 | 24.2446 | 14.9795 | 49.2665
MACC4 MC4 | 400 | 79.2757 | 29.7792 | 22.5051 | 64.6192 | 60.7255 | 24.2446 | 14.9795 | 49.2665
MAGA2 MC1 | 275 | 51.8375 | 19.1131 | 11.2431 | 38.2731 | 45.2745 | 17.9043 | 8.3255 | 33.646
MAGA2 MC2 | 275 | 51.8375 | 19.1131 | 11.2431 | 38.2731 | 45.2745 | 17.9043 | 8.3255 | 33.646
MANN4 M5 | 400 | 55.8386 | 20.3622 | 10.592 | 39.3885 | 51.8961 | 19.9009 | 11.0322 | 39.1763
MANN4 MC1 | 400 | 55.8386 | 20.3622 | 10.592 | 39.3885 | 51.8961 | 19.9009 | 11.0322 | 39.1763
MANN4 MC2 | 400 | 55.8386 | 20.3622 | 10.592 | 39.3885 | 51.8961 | 19.9009 | 11.0322 | 39.1763
MANN4 MC3 | 400 | 55.8386 | 20.3622 | 10.592 | 39.3885 | 51.8961 | 19.9009 | 11.0322 | 39.1763
MANN4 MC4 | 400 | 55.8386 | 20.3622 | 10.592 | 39.3885 | 51.8961 | 19.9009 | 11.0322 | 39.1763
MANN4 R5 | 400 | 55.8386 | 20.3622 | 10.592 | 39.3885 | 51.8961 | 19.9009 | 11.0322 | 39.1763
MAWO4 M | 400 | 63.3244 | 22.985 | 12.2793 | 44.785 | 56.858 | 21.7331 | 12.4637 | 43.199
MAWO4 R | 400 | 63.3244 | 22.985 | 12.2793 | 44.785 | 56.858 | 21.7331 | 12.4637 | 43.199
MEDW4 Term500 | 400 | 116.0382 | 39.9553 | 26.9403 | 83.4457 | 105.9074 | 39.8707 | 24.7553 | 81.141
MELK1 M1 | 132 | 41.6863 | 14.5735 | 14.6454 | 35.2555 | 51.7591 | 19.0245 | 17.2024 | 44.1071
MELK1 M2 | 132 | 41.6863 | 14.5735 | 14.6454 | 35.2555 | 51.7591 | 19.0245 | 17.2024 | 44.1071
MELK1 R1 | 132 | 41.6863 | 14.5735 | 14.6454 | 35.2555 | 51.7591 | 19.0245 | 17.2024 | 44.1071
MELK1 R2 | 132 | 41.6863 | 14.5735 | 14.6454 | 35.2555 | 51.7591 | 19.0245 | 17.2024 | 44.1071
MELK4 M1 | 400 | 101.1393 | 37.0018 | 18.781 | 71.1094 | 84.8387 | 33.5198 | 14.0162 | 61.4203
MELK4 M2 | 400 | 101.1393 | 37.0018 | 18.781 | 71.1094 | 84.8387 | 33.5198 | 14.0162 | 61.4203
MELK4 M3 | 400 | 101.1393 | 37.0018 | 18.781 | 71.1094 | 84.8387 | 33.5198 | 14.0162 | 61.4203
MELK4 R1 | 400 | 101.1393 | 37.0018 | 18.781 | 71.1094 | 84.8387 | 33.5198 | 14.0162 | 61.4203
MELK4 R2 | 400 | 101.1393 | 37.0018 | 18.781 | 71.1094 | 84.8387 | 33.5198 | 14.0162 | 61.4203
MELK4 R3 | 400 | 101.1393 | 37.0018 | 18.781 | 71.1094 | 84.8387 | 33.5198 | 14.0162 | 61.4203
MILH1 M1 | 132 | 40.2011 | 14.7432 | 9.0737 | 29.9238 | 46.499 | 18.8708 | 9.098 | 35.7853
MILH1 M2 | 132 | 40.2011 | 14.7432 | 9.0737 | 29.9238 | 46.499 | 18.8708 | 9.098 | 35.7853
MILH1 R1 | 132 | 40.2341 | 14.7706 | 8.968 | 29.8567 | 46.3857 | 18.881 | 8.8565 | 35.5583
MILH1 R2 | 132 | 40.2341 | 14.7706 | 8.968 | 29.8567 | 46.3857 | 18.881 | 8.8565 | 35.5583
MITY4 MC1 | 400 | 78.6615 | 29.9706 | 20.5546 | 62.9394 | 60.2617 | 24.3544 | 13.9875 | 48.4299
MITY4 MC2 | 400 | 78.6615 | 29.9706 | 20.5546 | 62.9394 | 60.2617 | 24.3544 | 13.9875 | 48.4299
MITY4 MC3 | 400 | 78.6615 | 29.9706 | 20.5546 | 62.9394 | 60.2617 | 24.3544 | 13.9875 | 48.4299
MITY4 MC4 | 400 | 78.6615 | 29.9706 | 20.5546 | 62.9394 | 60.2617 | 24.3544 | 13.9875 | 48.4299
MONF2 M1 | 275 | 64.8083 | 23.4331 | 17.2639 | 50.4033 | 65.7882 | 25.0092 | 15.9456 | 51.3139
MONF2 M2 | 275 | 64.8083 | 23.4331 | 17.2639 | 50.4033 | 65.7882 | 25.0092 | 15.9456 | 51.3139
MONF2 R1 | 275 | 56.6116 | 20.512 | 18.0757 | 47.0841 | 59.4503 | 22.3279 | 17.3175 | 48.8939
MONF2 R2 | 275 | 56.6116 | 20.512 | 18.0757 | 47.0841 | 59.4503 | 22.3279 | 17.3175 | 48.8939
MONF4 MC2 | 400 | 79.9335 | 28.9148 | 19.0458 | 59.9375 | 70.0119 | 26.7599 | 15.6451 | 53.4893
MONF4 MC3 | 400 | 79.9335 | 28.9148 | 19.0458 | 59.9375 | 70.0119 | 26.7599 | 15.6451 | 53.4893
NECH2 MC1 | 275 | 71.4747 | 25.6473 | 18.2153 | 54.486 | 72.4305 | 27.8308 | 15.8208 | 55.1796
NECH2 MC2 | 275 | 71.4747 | 25.6473 | 18.2153 | 54.486 | 72.4305 | 27.8308 | 15.8208 | 55.1796
NECH2 MC3 | 275 | 71.4747 | 25.6473 | 18.2153 | 54.486 | 72.4305 | 27.8308 | 15.8208 | 55.1796
NECH2 MC4 | 275 | 71.4747 | 25.6473 | 18.2153 | 54.486 | 72.4305 | 27.8308 | 15.8208 | 55.1796
NECT4 M1 | 400 | 78.821 | 28.3154 | 18.9233 | 58.9674 | 54.8755 | 21.6366 | 10.9769 | 41.5756
NECT4 R1 | 400 | 78.821 | 28.3154 | 18.9233 | 58.9674 | 54.8755 | 21.6366 | 10.9769 | 41.5756
NEEP2 M1 | 275 | 58.5713 | 21.5978 | 12.6348 | 43.1787 | 61.653 | 24.5158 | 11.9064 | 46.577
NEEP2 M2 | 275 | 58.5713 | 21.5978 | 12.6348 | 43.1787 | 61.653 | 24.5158 | 11.9064 | 46.577
NEEP2 R1/R2 | 275 | 58.5713 | 21.5978 | 12.6348 | 43.1787 | 61.653 | 24.5158 | 11.9064 | 46.577
NEWX2 M5 | 275 | 83.9292 | 29.3957 | 21.8982 | 63.47 | 90.3754 | 35.4436 | 18.5308 | 68.6556
NEWX2 M5 | 275 | 83.9292 | 29.3957 | 21.8982 | 63.47 | 90.3754 | 35.4436 | 18.5308 | 68.6556
NEWX2 M6 | 275 | 83.9292 | 29.3957 | 21.8982 | 63.47 | 90.3754 | 35.4436 | 18.5308 | 68.6556
NEWX2 R6 | 275 | 83.9292 | 29.3957 | 21.8982 | 63.47 | 90.3754 | 35.4436 | 18.5308 | 68.6556
NEWX21 R5 | 275 | 83.9292 | 29.3957 | 21.8982 | 63.47 | 90.3754 | 35.4436 | 18.5308 | 68.6556
NFLE4 M1 | 400 | 103.2935 | 35.9377 | 22.8749 | 73.6984 | 84.1565 | 32.7752 | 15.289 | 61.6401
NFLE4 M2 | 400 | 103.2935 | 35.9377 | 22.8749 | 73.6984 | 84.1565 | 32.7752 | 15.289 | 61.6401
NFLE4 R1 | 400 | 103.2935 | 35.9377 | 22.8749 | 73.6984 | 84.1565 | 32.7752 | 15.289 | 61.6401
NFLE4 R2 | 400 | 103.2935 | 35.9377 | 22.8749 | 73.6984 | 84.1565 | 32.7752 | 15.289 | 61.6401
NHYD2A | 275 | 45.6279 | 17.3236 | 2.5878 | 27.087 | 39.2829 | 18.5347 | 0.47461 | 26.6866
NHYD2B | 275 | 46.7115 | 17.6043 | 2.3037 | 27.1999 | 40.2015 | 18.415 | 1.0708 | 27.1136
NHYD2C | 275 | 46.7115 | 17.6043 | 2.3037 | 27.1999 | 40.2015 | 18.415 | 1.0708 | 27.1136
NINF4 M1 | 400 | 66.7092 | 24.1039 | 14.7486 | 48.8367 | 59.6551 | 22.8465 | 13.5472 | 45.857
NINF4 M2 | 400 | 66.7092 | 24.1039 | 14.7486 | 48.8367 | 59.6551 | 22.8465 | 13.5472 | 45.857
NINF4 R1 | 400 | 66.7092 | 24.1039 | 14.7486 | 48.8367 | 59.6551 | 22.8465 | 13.5472 | 45.857
NINF4 R2 | 400 | 66.7092 | 24.1039 | 14.7486 | 48.8367 | 59.6551 | 22.8465 | 13.5472 | 45.857
NORL2A | 275 | 51.2296 | 18.8254 | 3.912 | 30.5351 | 50.6683 | 20.8272 | 2.2826 | 31.7366
NORL2B | 275 | 50.442 | 18.6095 | 3.4032 | 29.721 | 49.8571 | 20.7743 | 2.0161 | 31.3954
NORM4 M1 | 400 | 73.4246 | 26.6703 | 16.5538 | 54.2713 | 53.4344 | 20.9828 | 11.3832 | 41.0573
NORM4 M2 | 400 | 73.4246 | 26.6703 | 16.5538 | 54.2713 | 53.4344 | 20.9828 | 11.3832 | 41.0573
NORM4 R1 | 400 | 73.4246 | 26.6703 | 16.5538 | 54.2713 | 53.4344 | 20.9828 | 11.3832 | 41.0573
NORM4 R2 | 400 | 73.4246 | 26.6703 | 16.5538 | 54.2713 | 53.4344 | 20.9828 | 11.3832 | 41.0573
NORT2 M1 | 275 | 76.4531 | 26.8441 | 21.5793 | 59.5426 | 76.9922 | 28.9549 | 18.8473 | 59.7956
NORT2 M2 | 275 | 76.4531 | 26.8441 | 21.5793 | 59.5426 | 76.9922 | 28.9549 | 18.8473 | 59.7956
NORT2 R1 | 275 | 76.4531 | 26.8441 | 21.5793 | 59.5426 | 76.9922 | 28.9549 | 18.8473 | 59.7956
NORT2 R2 | 275 | 76.4531 | 26.8441 | 21.5793 | 59.5426 | 76.9922 | 28.9549 | 18.8473 | 59.7956
NORT4 M1 | 400 | 95.6502 | 34.4262 | 30.3328 | 79.0187 | 79.5151 | 30.6755 | 22.5596 | 65.9413
NORT4 M2 | 400 | 95.6502 | 34.4262 | 30.3328 | 79.0187 | 79.5151 | 30.6755 | 22.5596 | 65.9413
NORT4 R1 | 400 | 95.6502 | 34.4262 | 30.3328 | 79.0187 | 79.5151 | 30.6755 | 22.5596 | 65.9413
NORT4 R2 | 400 | 95.6502 | 34.4262 | 30.3328 | 79.0187 | 79.5151 | 30.6755 | 22.5596 | 65.9413
NURS4 MC1 | 400 | 60.2886 | 21.6763 | 7.7683 | 38.4232 | 55.169 | 20.9831 | 8.1548 | 37.8294
NURS4 MC2 | 400 | 60.2886 | 21.6763 | 7.7683 | 38.4232 | 55.169 | 20.9831 | 8.1548 | 37.8294
NURS4A | 400 | 51.8007 | 19.0206 | 10.3373 | 37.2365 | 47.9879 | 18.3574 | 10.5064 | 36.4676
OCKH1 M1 | 132 | 24.4856 | 8.7548 | 8.3591 | 20.7402 | 32.8353 | 12.0433 | 10.868 | 27.8998
OCKH1 M2 | 132 | 24.4856 | 8.7548 | 8.3591 | 20.7402 | 32.8353 | 12.0433 | 10.868 | 27.8998
OCKH1 R1 | 132 | 24.4856 | 8.7548 | 8.3591 | 20.7402 | 32.8353 | 12.0433 | 10.868 | 27.8998
OCKH1 R2 | 132 | 24.4856 | 8.7548 | 8.3591 | 20.7402 | 32.8353 | 12.0433 | 10.868 | 27.8998
OCKH2 MC1 | 275 | 54.3293 | 19.8988 | 10.4619 | 38.603 | 56.2997 | 21.9732 | 10.6212 | 41.696
OCKH2 MC2 | 275 | 54.3293 | 19.8988 | 10.4619 | 38.603 | 56.2997 | 21.9732 | 10.6212 | 41.696
OCKH2 MC3 | 275 | 54.3293 | 19.8988 | 10.4619 | 38.603 | 56.2997 | 21.9732 | 10.6212 | 41.696
OCKH2 MC4 | 275 | 54.3293 | 19.8988 | 10.4619 | 38.603 | 56.2997 | 21.9732 | 10.6212 | 41.696
OCKH2A | 275 | 47.7486 | 17.1697 | 4.2493 | 28.5308 | 47.9308 | 18.5024 | 4.6501 | 30.8164
OFFE2 MC1 | 275 | 70.6391 | 25.5438 | 14.2636 | 50.388 | 61.6816 | 24.5073 | 8.8523 | 43.5108
OFFE2 MC2 | 275 | 70.6391 | 25.5438 | 14.2636 | 50.388 | 61.6816 | 24.5073 | 8.8523 | 43.5108
OLDB2 MC1 | 275 | 52.0277 | 19.1523 | 10.4934 | 37.5788 | 53.5932 | 20.7413 | 10.6779 | 40.0104
OLDB2 MC2 | 275 | 52.0277 | 19.1523 | 10.4934 | 37.5788 | 53.5932 | 20.7413 | 10.6779 | 40.0104
OSBA4 MC1 | 400 | 60.1787 | 22.0034 | 14.4905 | 45.608 | 53.0101 | 20.1943 | 13.1262 | 41.6851
OSBA4 MC2 | 400 | 60.1787 | 22.0034 | 14.4905 | 45.608 | 53.0101 | 20.1943 | 13.1262 | 41.6851
OSBA4 MC3/4 | 400 | 65.4231 | 23.4707 | 16.407 | 49.5996 | 50.2596 | 19.263 | 11.5653 | 38.8073
PADI1 M1 | 132 | 29.7318 | 10.4396 | 10.4504 | 25.2142 | 36.9582 | 13.5382 | 12.6786 | 31.8244
PADI1 M2 | 132 | 29.7318 | 10.4396 | 10.4504 | 25.2142 | 36.9582 | 13.5382 | 12.6786 | 31.8244
PADI1 R1 | 132 | 29.7318 | 10.4396 | 10.4504 | 25.2142 | 36.9582 | 13.5382 | 12.6786 | 31.8244
PADI1 R2 | 132 | 29.7318 | 10.4396 | 10.4504 | 25.2142 | 36.9582 | 13.5382 | 12.6786 | 31.8244
PADI4 MC1 | 400 | 74.3411 | 27.1973 | 15.8375 | 54.3003 | 56.5192 | 22.3119 | 9.7955 | 41.3493
PADI4 MC2 | 400 | 74.3411 | 27.1973 | 15.8375 | 54.3003 | 56.5192 | 22.3119 | 9.7955 | 41.3493
PADI4 MC3 | 400 | 74.3411 | 27.1973 | 15.8375 | 54.3003 | 56.5192 | 22.3119 | 9.7955 | 41.3493
PADI4 MC4 | 400 | 74.3411 | 27.1973 | 15.8375 | 54.3003 | 56.5192 | 22.3119 | 9.7955 | 41.3493
PELH4 M1 | 400 | 134.7294 | 47.2915 | 31.4522 | 98.3325 | 110.2791 | 42.5264 | 21.2228 | 81.3641
PELH4 M2 | 400 | 134.7294 | 47.2915 | 31.4522 | 98.3325 | 110.2791 | 42.5264 | 21.2228 | 81.3641
PELH4 R1 | 400 | 134.7294 | 47.2915 | 31.4522 | 98.3325 | 110.2791 | 42.5264 | 21.2228 | 81.3641
PELH4 R2 | 400 | 134.7294 | 47.2915 | 31.4522 | 98.3325 | 110.2791 | 42.5264 | 21.2228 | 81.3641
PEMB4 M1 | 400 | 62.5528 | 22.0372 | 18.3592 | 49.5244 | 65.3103 | 24.0058 | 20.5224 | 54.4716
PEMB4 M2 | 400 | 62.5528 | 22.0372 | 18.3592 | 49.5244 | 65.3103 | 24.0058 | 20.5224 | 54.4716
PEMB4 M3 | 400 | 62.5528 | 22.0372 | 18.3592 | 49.5244 | 65.3103 | 24.0058 | 20.5224 | 54.4716
PEMB4 M4 | 400 | 62.5528 | 22.0372 | 18.3592 | 49.5244 | 65.3103 | 24.0058 | 20.5224 | 54.4716
PEMB4 R1/2 | 400 | 62.5528 | 22.0372 | 18.3592 | 49.5244 | 65.3103 | 24.0058 | 20.5224 | 54.4716
PEMB4 R3/4 | 400 | 62.5528 | 22.0372 | 18.3592 | 49.5244 | 65.3103 | 24.0058 | 20.5224 | 54.4716
PENN2 MC1 | 275 | 64.7614 | 23.5443 | 13.6994 | 46.9961 | 67.8716 | 26.0097 | 14.4464 | 51.2296
PENN2 MC2 | 275 | 64.7614 | 23.5443 | 13.6994 | 46.9961 | 67.8716 | 26.0097 | 14.4464 | 51.2296
PENN2 MC3 | 275 | 64.7614 | 23.5443 | 13.6994 | 46.9961 | 67.8716 | 26.0097 | 14.4464 | 51.2296
PENN2 MC4 | 275 | 64.7614 | 23.5443 | 13.6994 | 46.9961 | 67.8716 | 26.0097 | 14.4464 | 51.2296
PENT4 M1 | 400 | 75.5015 | 26.5216 | 20.785 | 58.2922 | 76.5655 | 28.5186 | 20.603 | 60.9343
PENT4 M2 | 400 | 75.5015 | 26.5216 | 20.785 | 58.2922 | 76.5655 | 28.5186 | 20.603 | 60.9343
PENT4 R1 | 400 | 75.5015 | 26.5216 | 20.785 | 58.2922 | 76.5655 | 28.5186 | 20.603 | 60.9343
PENT4 R2 | 400 | 75.5015 | 26.5216 | 20.785 | 58.2922 | 76.5655 | 28.5186 | 20.603 | 60.9343
PEWO2A | 275 | 65.7679 | 23.5903 | 19.9295 | 53.2913 | 68.0252 | 25.4018 | 19.3755 | 55.299
PEWO2B | 275 | 66.8904 | 24.3314 | 24.2095 | 58.6193 | 69.0936 | 25.9219 | 24.3003 | 60.9594
PEWO4 M1 | 400 | 99.0328 | 35.9594 | 31.6281 | 82.4824 | 90.2637 | 34.8602 | 26.7163 | 76.0161
PEWO4 M2 | 400 | 99.0328 | 35.9594 | 31.6281 | 82.4824 | 90.2637 | 34.8602 | 26.7163 | 76.0161
PEWO4 M3 | 400 | 99.0328 | 35.9594 | 31.6281 | 82.4824 | 90.2637 | 34.8602 | 26.7163 | 76.0161
PEWO4 M4 | 400 | 99.0328 | 35.9594 | 31.6281 | 82.4824 | 90.2637 | 34.8602 | 26.7163 | 76.0161
PEWO4 R1/2 | 400 | 99.0328 | 35.9594 | 31.6281 | 82.4824 | 90.2637 | 34.8602 | 26.7163 | 76.0161
PEWO4 R3/4 | 400 | 99.0328 | 35.9594 | 31.6281 | 82.4824 | 90.2637 | 34.8602 | 26.7163 | 76.0161
PITS2 MC1 | 275 | 60.2159 | 21.8798 | 8.4947 | 39.4374 | 65.0071 | 25.4892 | 7.5859 | 43.6331
PITS2 MC2 | 275 | 60.2159 | 21.8798 | 8.4947 | 39.4374 | 65.0071 | 25.4892 | 7.5859 | 43.6331
PITS2 MC3 | 275 | 60.2159 | 21.8798 | 8.4947 | 39.4374 | 65.0071 | 25.4892 | 7.5859 | 43.6331
PITS2 MC4 | 275 | 60.2159 | 21.8798 | 8.4947 | 39.4374 | 65.0071 | 25.4892 | 7.5859 | 43.6331
POPP2 MC1 | 275 | 27.2656 | 10.8997 | 2.8449 | 18.2594 | 24.4199 | 9.9748 | 3.7136 | 17.8201
POPP2 MC2 | 275 | 27.2656 | 10.8997 | 2.8449 | 18.2594 | 24.4199 | 9.9748 | 3.7136 | 17.8201
PUDM4 MC1 | 400 | 97.7009 | 33.1624 | 23.3465 | 70.2452 | 102.393 | 40.8624 | 18.6397 | 76.4278
PUDM4 MC2 | 400 | 97.7009 | 33.1624 | 23.3465 | 70.2452 | 102.393 | 40.8624 | 18.6397 | 76.4278
PYLE2 MC1 | 275 | 54.0853 | 20.057 | 10.8632 | 39.2281 | 47.732 | 18.8804 | 8.9018 | 35.6027
PYLE2 MC2 | 275 | 54.1392 | 20.0758 | 10.8766 | 39.2681 | 47.7767 | 18.8964 | 8.9178 | 35.6413
QUER4A | 400 | 82.3256 | 28.8168 | 12.1268 | 52.8798 | 71.41 | 27.5459 | 5.6702 | 44.626
QUER4A_HEYS | 400 | 82.3256 | 28.8168 | 12.1268 | 52.8798 | 71.41 | 27.5459 | 5.6702 | 44.626
QUER4A_HUTT | 400 | 82.3256 | 28.8168 | 12.1268 | 52.8798 | 71.41 | 27.5459 | 5.6702 | 44.626
QUER4A_PEWO | 400 | 82.3256 | 28.8168 | 12.1268 | 52.8798 | 71.41 | 27.5459 | 5.6702 | 44.626
QUER4B | 400 | 83.1651 | 29.0659 | 12.417 | 53.5224 | 73.3928 | 28.1946 | 6.3084 | 46.1815
QUER4B_HEYS | 400 | 83.1651 | 29.0659 | 12.417 | 53.5224 | 73.3928 | 28.1946 | 6.3084 | 46.1815
QUER4B_HUTT | 400 | 83.1651 | 29.0659 | 12.417 | 53.5224 | 73.3928 | 28.1946 | 6.3084 | 46.1815
QUER4B_PEWO | 400 | 83.1651 | 29.0659 | 12.417 | 53.5224 | 73.3928 | 28.1946 | 6.3084 | 46.1815
RAIN2 MC1 | 275 | 76.0528 | 26.7525 | 19.5297 | 57.3634 | 75.1286 | 28.4013 | 16.4537 | 56.6192
RAIN2 MC2 | 275 | 76.0528 | 26.7525 | 19.5297 | 57.3634 | 75.1286 | 28.4013 | 16.4537 | 56.6192
RAIN2 MC3 | 275 | 76.0528 | 26.7525 | 19.5297 | 57.3634 | 75.1286 | 28.4013 | 16.4537 | 56.6192
RAIN2 MC4 | 275 | 76.0528 | 26.7525 | 19.5297 | 57.3634 | 75.1286 | 28.4013 | 16.4537 | 56.6192
RASS4 M1 | 400 | 53.048 | 19.8376 | 16.1299 | 44.1845 | 43.0702 | 16.8922 | 11.617 | 35.5063
RASS4 M2 | 400 | 53.048 | 19.8376 | 16.1299 | 44.1845 | 43.0702 | 16.8922 | 11.617 | 35.5063
RATS1 M1 | 132 | 42.5564 | 14.9959 | 13.5376 | 34.7451 | 47.6778 | 17.7579 | 15.5253 | 40.6388
RATS1 M2 | 132 | 42.5564 | 14.9959 | 13.5376 | 34.7451 | 47.6778 | 17.7579 | 15.5253 | 40.6388
RATS1 R1 | 132 | 38.4718 | 13.6598 | 12.125 | 31.4428 | 42.8442 | 16.0966 | 12.7415 | 35.5056
RATS1 R2 | 132 | 38.4718 | 13.6598 | 12.125 | 31.4428 | 42.8442 | 16.0966 | 12.7415 | 35.5056
RATS2A | 275 | 41.9537 | 15.1766 | 9.1223 | 30.5853 | 43.1632 | 15.7537 | 16.1099 | 38.389
RATS4 M1 | 400 | 116.8466 | 42.2479 | 21.5872 | 81.3348 | 98.7025 | 38.9032 | 17.7733 | 72.7908
RATS4 M2 | 400 | 116.8466 | 42.2479 | 21.5872 | 81.3348 | 98.7025 | 38.9032 | 17.7733 | 72.7908
RATS4 M3 | 400 | 116.8466 | 42.2479 | 21.5872 | 81.3348 | 98.7025 | 38.9032 | 17.7733 | 72.7908
RATS4 M4 | 400 | 116.8466 | 42.2479 | 21.5872 | 81.3348 | 98.7025 | 38.9032 | 17.7733 | 72.7908
RATS4 R1/2 | 400 | 116.8466 | 42.2479 | 21.5872 | 81.3348 | 98.7025 | 38.9032 | 17.7733 | 72.7908
RATS4 R3/4 | 400 | 116.8466 | 42.2479 | 21.5872 | 81.3348 | 98.7025 | 38.9032 | 17.7733 | 72.7908
RAYL4 M1 | 400 | 103.5602 | 37.621 | 31.4104 | 84.6145 | 82.7028 | 32.313 | 22.8922 | 68.5897
RAYL4 M2 | 400 | 103.5602 | 37.621 | 31.4104 | 84.6145 | 82.7028 | 32.313 | 22.8922 | 68.5897
RAYL4 R1 | 400 | 103.5602 | 37.621 | 31.4104 | 84.6145 | 82.7028 | 32.313 | 22.8922 | 68.5897
RAYL4 R2 | 400 | 103.5602 | 37.621 | 31.4104 | 84.6145 | 82.7028 | 32.313 | 22.8922 | 68.5897
REBR2 MC1 | 275 | 63.4446 | 23.1174 | 21.5649 | 54.2578 | 61.5523 | 23.9037 | 17.4986 | 51.3036
REBR2 MC2 | 275 | 61.3605 | 22.3762 | 21.0374 | 52.6822 | 60.1181 | 23.4026 | 16.9231 | 50.0194
REBR2 MC3 | 275 | 61.3605 | 22.3762 | 21.0374 | 52.6822 | 60.1181 | 23.4026 | 16.9231 | 50.0194
REBR2 MC4 | 275 | 63.4446 | 23.1174 | 21.5649 | 54.2578 | 61.5523 | 23.9037 | 17.4986 | 51.3036
RHIG4 M1 | 400 | 54.4692 | 19.9175 | 12.6813 | 40.8489 | 47.8336 | 18.4811 | 9.6014 | 35.7376
RHIG4 R1 | 400 | 54.4692 | 19.9175 | 12.6813 | 40.8489 | 47.8336 | 18.4811 | 9.6014 | 35.7376
ROCH2 MC1 | 275 | 70.5546 | 25.5258 | 9.5269 | 45.6259 | 67.3293 | 26.0881 | 9.2362 | 46.1303
ROCH2 MC2 | 275 | 70.5546 | 25.5258 | 9.5269 | 45.6259 | 67.3293 | 26.0881 | 9.2362 | 46.1303
ROCH2 MC3 | 275 | 70.5546 | 25.5258 | 9.5269 | 45.6259 | 67.3293 | 26.0881 | 9.2362 | 46.1303
ROCH2 MC4 | 275 | 70.5546 | 25.5258 | 9.5269 | 45.6259 | 67.3293 | 26.0881 | 9.2362 | 46.1303
ROCK1A | 132 | 46.3794 | 15.9748 | 16.5391 | 39.1309 | 48.4034 | 17.4811 | 16.1316 | 40.8537
ROCK4 Term900 | 400 | 84.4026 | 29.8426 | 21.4649 | 63.6688 | 79.8735 | 29.8787 | 21.0708 | 63.3256
RUGE4 M1 | 400 | 63.8648 | 23.9697 | 10.1198 | 44.0181 | 50.3648 | 20.2814 | 7.0582 | 35.7404
RUGE4 M2 | 400 | 63.8648 | 23.9697 | 10.1198 | 44.0181 | 50.3648 | 20.2814 | 7.0582 | 35.7404
RUGE4 R1 | 400 | 63.8648 | 23.9697 | 10.1198 | 44.0181 | 50.3648 | 20.2814 | 7.0582 | 35.7404
RUGE4 R2 | 400 | 63.8648 | 23.9697 | 10.1198 | 44.0181 | 50.3648 | 20.2814 | 7.0582 | 35.7404
RYEH4 M1 | 400 | 70.8555 | 25.6198 | 17.0417 | 53.2736 | 73.454 | 27.5929 | 18.9113 | 57.9335
RYEH4 R1 | 400 | 70.8555 | 25.6198 | 17.0417 | 53.2736 | 73.454 | 27.5929 | 18.9113 | 57.9335
RYHA41 MC1 | 400 | 43.8618 | 16.4293 | 9.5118 | 32.7464 | 28.4717 | 11.3562 | 4.0663 | 20.1264
RYHA4B_LOAD2 | 400 | 44.2855 | 16.5859 | 9.5875 | 33.0435 | 30.1292 | 12.0158 | 4.276 | 21.2689
SAEN2 MC1 | 275 | 77.764 | 26.9325 | 23.3727 | 61.4611 | 78.6454 | 28.8433 | 23.936 | 64.7266
SAEN2 MC2 | 275 | 77.764 | 26.9325 | 23.3727 | 61.4611 | 78.6454 | 28.8433 | 23.936 | 64.7266
SAES2 M | 275 | 78.3626 | 27.1057 | 23.6835 | 62.0168 | 79.5622 | 29.1237 | 24.7216 | 65.9088
SAES2 R | 275 | 78.3626 | 27.1057 | 23.6835 | 62.0168 | 79.5622 | 29.1237 | 24.7216 | 65.9088
SALH2 MC1 | 275 | 77.4007 | 27.4553 | 18.6051 | 57.4328 | 74.6534 | 28.3668 | 15.5747 | 55.6914
SALH2 MC2 | 275 | 77.4007 | 27.4553 | 18.6051 | 57.4328 | 74.6534 | 28.3668 | 15.5747 | 55.6914
SEAB4 M1 | 400 | 61.6261 | 22.6151 | 19.9963 | 51.9789 | 63.4891 | 23.9562 | 21.2733 | 55.1525
SEAB4 M2 | 400 | 61.6261 | 22.6151 | 19.9963 | 51.9789 | 63.4891 | 23.9562 | 21.2733 | 55.1525
SEAB4 R1 | 400 | 61.6261 | 22.6151 | 19.9963 | 51.9789 | 63.4891 | 23.9562 | 21.2733 | 55.1525
SEAB4 R2 | 400 | 61.6261 | 22.6151 | 19.9963 | 51.9789 | 63.4891 | 23.9562 | 21.2733 | 55.1525
SELL4 M1 | 400 | 84.0732 | 30.4078 | 17.7414 | 60.7445 | 71.0324 | 27.1976 | 16.6217 | 55.0849
SELL4 M2 | 400 | 84.0732 | 30.4078 | 17.7414 | 60.7445 | 71.0324 | 27.1976 | 16.6217 | 55.0849
SELL4 R1 | 400 | 84.0732 | 30.4078 | 17.7414 | 60.7445 | 71.0324 | 27.1976 | 16.6217 | 55.0849
SELL4 R2 | 400 | 84.0732 | 30.4078 | 17.7414 | 60.7445 | 71.0324 | 27.1976 | 16.6217 | 55.0849
SELL4A | 400 | 83.985 | 29.6516 | 8.0977 | 50.0314 | 70.9611 | 26.9888 | 9.2386 | 47.4066
SELL4B | 400 | 83.9848 | 29.6515 | 8.0977 | 50.0313 | 70.961 | 26.9888 | 9.2385 | 47.4064
SELW4 M3 | 400 | 83.8865 | 30.3456 | 17.6907 | 60.6058 | 70.6285 | 27.0624 | 16.3981 | 54.6702
SELW4 M4 | 400 | 83.8865 | 30.3456 | 17.6907 | 60.6058 | 70.6285 | 27.0624 | 16.3981 | 54.6702
SELW4 R3 | 400 | 83.8865 | 30.3456 | 17.6907 | 60.6058 | 70.6285 | 27.0624 | 16.3981 | 54.6702
SELW4 R4 | 400 | 83.8865 | 30.3456 | 17.6907 | 60.6058 | 70.6285 | 27.0624 | 16.3981 | 54.6702
SETW4A | 400 | 83.8857 | 29.619 | 8.0851 | 49.9727 | 70.9042 | 26.9703 | 9.2082 | 47.35
SETW4B | 400 | 83.8856 | 29.619 | 8.0851 | 49.9727 | 70.904 | 26.9702 | 9.2082 | 47.3499
SHBA4 M1 | 400 | 87.9932 | 31.3731 | 31.5596 | 75.928 | 83.254 | 31.0991 | 29.0484 | 73.0292
SHBA4 M2 | 400 | 87.9932 | 31.3731 | 31.5596 | 75.928 | 83.254 | 31.0991 | 29.0484 | 73.0292
SHBA4 R1 | 400 | 87.9932 | 31.3731 | 31.5596 | 75.928 | 83.254 | 31.0991 | 29.0484 | 73.0292
SHBA4 R2 | 400 | 87.9932 | 31.3731 | 31.5596 | 75.928 | 83.254 | 31.0991 | 29.0484 | 73.0292
SHEC2 MC1 | 275 | 53.2278 | 19.8636 | 10.2913 | 38.3826 | 54.0014 | 22.2344 | 7.4334 | 38.8775
SHEC2 MC2 | 275 | 53.2278 | 19.8636 | 10.2913 | 38.3826 | 54.0014 | 22.2344 | 7.4334 | 38.8775
SHRE4B | 400 | 55.2803 | 20.6855 | 10.2702 | 39.5239 | 43.496 | 17.3184 | 7.0922 | 31.584
SING4 MC1 | 400 | 93.1038 | 32.7409 | 20.6234 | 66.926 | 76.1201 | 29.6532 | 13.1321 | 55.0681
SING4 MC2 | 400 | 93.1038 | 32.7409 | 20.6234 | 66.926 | 76.1201 | 29.6532 | 13.1321 | 55.0681
SIZE4 M1 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 M2 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 M3 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 M4 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 R1 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 R2 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 R3 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SIZE4 R4 | 400 | 75.0521 | 26.4654 | 19.7249 | 57.1526 | 77.1449 | 28.4689 | 22.3135 | 62.5746
SJOW2 MC1 | 275 | 22.871 | 8.0372 | 9.1724 | 20.5388 | 27.3987 | 9.8299 | 10.7931 | 24.6947
SJOW2 MC2 | 275 | 22.871 | 8.0372 | 9.1724 | 20.5388 | 27.3987 | 9.8299 | 10.7931 | 24.6947
SJOW2 MC3 | 275 | 22.871 | 8.0372 | 9.1724 | 20.5388 | 27.3987 | 9.8299 | 10.7931 | 24.6947
SJOW2 MC4 | 275 | 22.871 | 8.0372 | 9.1724 | 20.5388 | 27.3987 | 9.8299 | 10.7931 | 24.6947
SJOW4 M1 | 400 | 108.9301 | 36.198 | 27.6746 | 78.8663 | 129.2151 | 47.1218 | 32.074 | 98.7143
SJOW4 M2 | 400 | 108.9301 | 36.198 | 27.6746 | 78.8663 | 129.2151 | 47.1218 | 32.074 | 98.7143
SJOW4 M3 | 400 | 108.9301 | 36.198 | 27.6746 | 78.8663 | 129.2151 | 47.1218 | 32.074 | 98.7143
SJOW4 M4 | 400 | 108.9301 | 36.198 | 27.6746 | 78.8663 | 129.2151 | 47.1218 | 32.074 | 98.7143
SJOW4 R1/2 | 400 | 108.9301 | 36.198 | 27.6746 | 78.8663 | 129.2151 | 47.1218 | 32.074 | 98.7143
SJOW4 R3/4 | 400 | 108.9301 | 36.198 | 27.6746 | 78.8663 | 129.2151 | 47.1218 | 32.074 | 98.7143
SKLG2 MC1 | 275 | 57.8747 | 21.3644 | 17.5578 | 47.7717 | 55.7238 | 21.7042 | 15.7307 | 46.4251
SKLG2 MC2 | 275 | 57.8747 | 21.3644 | 17.5578 | 47.7717 | 55.7238 | 21.7042 | 15.7307 | 46.4251
SKLG2 MC3 | 275 | 57.8747 | 21.3644 | 17.5578 | 47.7717 | 55.7238 | 21.7042 | 15.7307 | 46.4251
SKLG2 MC4 | 275 | 57.8747 | 21.3644 | 17.5578 | 47.7717 | 55.7238 | 21.7042 | 15.7307 | 46.4251
SMAN2 MC1 | 275 | 75.886 | 28.2068 | 23.0475 | 62.938 | 74.7233 | 29.1682 | 20.8741 | 62.1242
SMAN2 MC2 | 275 | 75.886 | 28.2068 | 23.0475 | 62.938 | 74.7233 | 29.1682 | 20.8741 | 62.1242
SMAN2 MC3 | 275 | 75.886 | 28.2068 | 23.0475 | 62.938 | 74.7233 | 29.1682 | 20.8741 | 62.1242
SMAN2 MC4 | 275 | 75.886 | 28.2068 | 23.0475 | 62.938 | 74.7233 | 29.1682 | 20.8741 | 62.1242
SPEN4 MC3 | 400 | 63.4223 | 22.9918 | 13.6331 | 46.1484 | 49.3837 | 19.1961 | 9.1579 | 36.3053
SPEN4 MC4 | 400 | 63.4223 | 22.9918 | 13.6331 | 46.1484 | 49.3837 | 19.1961 | 9.1579 | 36.3053
SPEN41 MC1 | 400 | 63.3987 | 22.9836 | 13.6288 | 46.1325 | 50.0183 | 19.418 | 9.411 | 36.8722
SPEN41 MC2 | 400 | 63.3987 | 22.9836 | 13.6288 | 46.1325 | 50.0183 | 19.418 | 9.411 | 36.8722
SPLN4 M1 | 400 | 91.8444 | 31.428 | 25.3346 | 69.7806 | 69.1632 | 26.0828 | 18.0804 | 54.967
SPLN4 R1 | 400 | 91.8444 | 31.428 | 25.3346 | 69.7806 | 69.1632 | 26.0828 | 18.0804 | 54.967
SSHI2 MC1 | 275 | 68.3313 | 24.88 | 12.7256 | 47.9112 | 60.1242 | 23.7832 | 9.8476 | 43.4821
SSHI2 MC2 | 275 | 68.3313 | 24.88 | 12.7256 | 47.9112 | 60.1242 | 23.7832 | 9.8476 | 43.4821
STAL2 M1 | 275 | 81.8338 | 30.0064 | 15.869 | 58.3045 | 76.1856 | 29.7127 | 14.507 | 56.5272
STAL2 M2 | 275 | 81.8338 | 30.0064 | 15.869 | 58.3045 | 76.1856 | 29.7127 | 14.507 | 56.5272
STAL2 R1 | 275 | 81.8338 | 30.0064 | 15.869 | 58.3045 | 76.1856 | 29.7127 | 14.507 | 56.5272
STAL2 R2 | 275 | 81.8338 | 30.0064 | 15.869 | 58.3045 | 76.1856 | 29.7127 | 14.507 | 56.5272
STAL4 MC1 | 400 | 35.9622 | 13.2196 | 9.304 | 27.9993 | 32.1941 | 12.4313 | 8.0323 | 25.6128
STAL4 MC2 | 400 | 49.4397 | 18.6753 | 9.7109 | 36.1218 | 38.4567 | 15.2773 | 6.3536 | 27.959
STAY4 M1 | 400 | 112.628 | 40.7416 | 25.9787 | 83.596 | 104.4054 | 39.6953 | 26.6971 | 82.8347
STAY4 M2 | 400 | 112.628 | 40.7416 | 25.9787 | 83.596 | 104.4054 | 39.6953 | 26.6971 | 82.8347
STAY4 R1 | 400 | 112.628 | 40.7416 | 25.9787 | 83.596 | 104.4054 | 39.6953 | 26.6971 | 82.8347
STAY4 R2 | 400 | 112.628 | 40.7416 | 25.9787 | 83.596 | 104.4054 | 39.6953 | 26.6971 | 82.8347
STAY4A | 400 | 73.993 | 27.134 | 19.3039 | 57.6772 | 66.7473 | 25.3195 | 18.7063 | 54.5134
STEN1 M1 | 132 | 55.0204 | 19.3451 | 19.2472 | 46.6053 | 67.5931 | 24.9051 | 22.8561 | 58.0772
STEN1 M2 | 132 | 55.0204 | 19.3451 | 19.2472 | 46.6053 | 67.5931 | 24.9051 | 22.8561 | 58.0772
STEN1 R1 | 132 | 55.0204 | 19.3451 | 19.2472 | 46.6053 | 67.5931 | 24.9051 | 22.8561 | 58.0772
STEN1 R2 | 132 | 55.0204 | 19.3451 | 19.2472 | 46.6053 | 67.5931 | 24.9051 | 22.8561 | 58.0772
STES1 M1 | 132 | 55.2597 | 18.8935 | 15.2507 | 41.9701 | 67.568 | 24.6149 | 17.4682 | 52.279
STES1 M2 | 132 | 55.2597 | 18.8935 | 15.2507 | 41.9701 | 67.568 | 24.6149 | 17.4682 | 52.279
STES1 R1 | 132 | 55.2597 | 18.8935 | 15.2507 | 41.9701 | 67.568 | 24.6149 | 17.4682 | 52.279
STES1 R2 | 132 | 55.2597 | 18.8935 | 15.2507 | 41.9701 | 67.568 | 24.6149 | 17.4682 | 52.279
STEW2 M1 | 275 | 80.6151 | 29.5543 | 24.8893 | 66.6854 | 76.8665 | 29.4701 | 23.4025 | 65.0796
STEW2 M2 | 275 | 80.6151 | 29.5543 | 24.8893 | 66.6854 | 76.8665 | 29.4701 | 23.4025 | 65.0796
STEW2 R1 | 275 | 80.6151 | 29.5543 | 24.8893 | 66.6854 | 76.8665 | 29.4701 | 23.4025 | 65.0796
STEW2 R2 | 275 | 80.6151 | 29.5543 | 24.8893 | 66.6854 | 76.8665 | 29.4701 | 23.4025 | 65.0796
STEW4 M1 | 400 | 81.1994 | 29.61 | 24.767 | 66.6419 | 61.3949 | 23.8532 | 17.6761 | 51.4096
STEW4 M2 | 400 | 81.1994 | 29.61 | 24.767 | 66.6419 | 61.3949 | 23.8532 | 17.6761 | 51.4096
STEW4 R1 | 400 | 81.1994 | 29.61 | 24.767 | 66.6419 | 61.3949 | 23.8532 | 17.6761 | 51.4096
STEW4 R2a | 400 | 81.1994 | 29.61 | 24.767 | 66.6419 | 61.3949 | 23.8532 | 17.6761 | 51.4096
STOB4 M1 | 400 | 61.6421 | 23.2502 | 10.7649 | 43.6457 | 49.6054 | 19.9167 | 7.5947 | 35.7612
STOB4 R1 | 400 | 61.6421 | 23.2502 | 10.7649 | 43.6457 | 49.6054 | 19.9167 | 7.5947 | 35.7612
STSB4 MC1 | 400 | 55.8151 | 20.6058 | 12.4353 | 41.5763 | 44.831 | 17.6013 | 7.7234 | 32.6154
STSB4 MC2 | 400 | 55.8151 | 20.6058 | 12.4353 | 41.5763 | 44.831 | 17.6013 | 7.7234 | 32.6154
STSB4A | 400 | 48.7502 | 17.8727 | 5.8643 | 31.1401 | 39.3679 | 15.3357 | 3.1823 | 24.8702
SUND4 M1 | 400 | 110.328 | 39.7038 | 23.6951 | 79.8448 | 92.1477 | 35.679 | 17.9502 | 68.4079
SUND4 M2 | 400 | 87.6391 | 32.022 | 18.4095 | 63.6955 | 74.0136 | 28.6408 | 14.7626 | 55.2668
SUND4 R1 | 400 | 110.328 | 39.7038 | 23.6951 | 79.8448 | 92.1477 | 35.679 | 17.9502 | 68.4079
SUND4 R2 | 400 | 87.6391 | 32.022 | 18.4095 | 63.6955 | 74.0136 | 28.6408 | 14.7626 | 55.2668
SUTB4A | 400 | 95.864 | 33.8445 | 22.4028 | 70.2661 | 78.7146 | 30.0503 | 18.6246 | 61.1222
SWAN2 MC3 | 275 | 25.9206 | 9.4095 | 8.4741 | 21.7812 | 28.3107 | 10.4841 | 8.82 | 23.6468
SWAN2 MC4 | 275 | 25.9206 | 9.4095 | 8.4741 | 21.7812 | 28.3107 | 10.4841 | 8.82 | 23.6468
SWAN4 M1 | 400 | 38.6971 | 14.2926 | 9.1109 | 29.3237 | 33.9971 | 12.9782 | 8.0376 | 26.3915
SWAN4 M2 | 400 | 38.6971 | 14.2926 | 9.1109 | 29.3237 | 33.9971 | 12.9782 | 8.0376 | 26.3915
SWAN4 M3 | 400 | 61.1093 | 22.0288 | 15.3403 | 46.4938 | 59.2575 | 22.4602 | 14.179 | 45.9426
SWAN4 M4 | 400 | 61.1093 | 22.0288 | 15.3403 | 46.4938 | 59.2575 | 22.4602 | 14.179 | 45.9426
SWAN4 R3 | 400 | 61.1093 | 22.0288 | 15.3403 | 46.4938 | 59.2575 | 22.4602 | 14.179 | 45.9426
SWAN4 R4 | 400 | 61.1093 | 22.0288 | 15.3403 | 46.4938 | 59.2575 | 22.4602 | 14.179 | 45.9426
TAUN4 M1 | 400 | 43.4174 | 16.3145 | 7.1627 | 30.235 | 36.6413 | 14.6656 | 5.2946 | 26.0348
TAUN4 M2 | 400 | 44.0305 | 16.51 | 7.2358 | 30.5844 | 37.9572 | 15.1486 | 5.7082 | 27.1315
TEMP2 MC1 | 275 | 59.1182 | 21.8135 | 12.1085 | 42.9575 | 61.4939 | 24.3677 | 10.8378 | 45.2989
TEMP2 MC2 | 275 | 59.1182 | 21.8135 | 12.1085 | 42.9575 | 61.4939 | 24.3677 | 10.8378 | 45.2989
TEMP2 MC3 | 275 | 59.4061 | 21.8995 | 12.2479 | 43.2185 | 62.3825 | 24.6997 | 11.063 | 45.9936
THOM2 M1 | 275 | 65.7643 | 24.0048 | 18.312 | 52.2599 | 67.5286 | 25.5532 | 18.1019 | 54.2396
THOM2 R1 | 275 | 65.7643 | 24.0048 | 18.312 | 52.2599 | 67.5286 | 25.5532 | 18.1019 | 54.2396
THOM4 MC1 | 400 | 87.5696 | 31.3221 | 21.0665 | 65.3626 | 77.9166 | 29.7828 | 16.7938 | 58.913
THOM4 MC2 | 400 | 87.5696 | 31.3221 | 21.0665 | 65.3626 | 77.9166 | 29.7828 | 16.7938 | 58.913
THOM4 MC3 | 400 | 87.5696 | 31.3221 | 21.0665 | 65.3626 | 77.9166 | 29.7828 | 16.7938 | 58.913
THOM4 MC4 | 400 | 87.5696 | 31.3221 | 21.0665 | 65.3626 | 77.9166 | 29.7828 | 16.7938 | 58.913
THOM4 R2(2) | 400 | 89.1604 | 32.3707 | 19.0659 | 64.845 | 77.2613 | 29.7897 | 15.456 | 57.585
THOM4 R2(3) | 400 | 89.1604 | 32.3707 | 19.0659 | 64.845 | 77.2613 | 29.7897 | 15.456 | 57.585
THOM42 M5 | 400 | 89.1604 | 32.3707 | 19.0659 | 64.845 | 77.2613 | 29.7897 | 15.456 | 57.585
THTO4 M1 | 400 | 104.359 | 36.2368 | 28.2844 | 79.531 | 77.3115 | 29.647 | 15.3925 | 57.3197
THTO4 M2 | 400 | 92.9507 | 32.1965 | 26.7166 | 72.2494 | 69.9418 | 26.5899 | 15.4036 | 53.0074
THTO4 M3 | 400 | 92.9507 | 32.1965 | 26.7166 | 72.2494 | 69.9418 | 26.5899 | 15.4036 | 53.0074
THTO4 M4 | 400 | 104.359 | 36.2368 | 28.2844 | 79.531 | 77.3115 | 29.647 | 15.3925 | 57.3197
THTO4 R1/2 | 400 | 77.8957 | 27.9688 | 20.6705 | 60.2245 | 65.3602 | 24.9512 | 14.3187 | 49.605
THTO4 R3/4 | 400 | 77.8957 | 27.9688 | 20.6705 | 60.2245 | 65.3602 | 24.9512 | 14.3187 | 49.605
THUR2 MC1 | 275 | 63.9516 | 24.0587 | 10.3615 | 44.3857 | 64.8894 | 25.6997 | 10.7819 | 47.1268
THUR2 MC2 | 275 | 63.9516 | 24.0587 | 10.3615 | 44.3857 | 64.8894 | 25.6997 | 10.7819 | 47.1268
THUR2 MC3 | 275 | 63.9516 | 24.0587 | 10.3615 | 44.3857 | 64.8894 | 25.6997 | 10.7819 | 47.1268
THUR2 MC4 | 275 | 63.9516 | 24.0587 | 10.3615 | 44.3857 | 64.8894 | 25.6997 | 10.7819 | 47.1268
TILB2 M1 | 275 | 71.5956 | 25.5649 | 21.187 | 57.3412 | 75.3443 | 28.1294 | 21.3112 | 61.0922
TILB2 M2 | 275 | 71.5956 | 25.5649 | 21.187 | 57.3412 | 75.3443 | 28.1294 | 21.3112 | 61.0922
TILB2 R1 | 275 | 71.5956 | 25.5649 | 21.187 | 57.3412 | 75.3443 | 28.1294 | 21.3112 | 61.0922
TILB2 R2 | 275 | 71.5956 | 25.5649 | 21.187 | 57.3412 | 75.3443 | 28.1294 | 21.3112 | 61.0922
TILB4 M2 | 400 | 136.9762 | 48.2158 | 43.4557 | 111.6431 | 123.5717 | 47.4044 | 35.1111 | 102.1509
TILB4 M3 | 400 | 136.9762 | 48.2158 | 43.4557 | 111.6431 | 123.5717 | 47.4044 | 35.1111 | 102.1509
TILB4 R2 | 400 | 136.9762 | 48.2158 | 43.4557 | 111.6431 | 123.5717 | 47.4044 | 35.1111 | 102.1509
TILB4 R3 | 400 | 136.9762 | 48.2158 | 43.4557 | 111.6431 | 123.5717 | 47.4044 | 35.1111 | 102.1509
TINP2 M1 | 275 | 57.5351 | 20.9655 | 6.6977 | 36.3475 | 55.9492 | 21.7594 | 5.42 | 36.1924
TINP2 M2 | 275 | 57.7015 | 20.9761 | 6.7104 | 36.3751 | 56.8646 | 22.0905 | 5.5119 | 36.7525
TODP2 MC1 | 275 | 64.5882 | 22.5677 | 16.1967 | 48.1123 | 58.7384 | 22.4475 | 11.7961 | 43.5416
TODP2 MC2 | 275 | 64.5882 | 22.5677 | 16.1967 | 48.1123 | 58.7384 | 22.4475 | 11.7961 | 43.5416
TOTE2A | 275 | 70.6929 | 25.1519 | 19.5352 | 55.1054 | 72.6374 | 27.4533 | 16.8503 | 55.6751
TOTE2B | 275 | 72.4499 | 25.7427 | 19.7642 | 56.1698 | 73.3189 | 27.7438 | 16.8017 | 56.0374
TOTT2 MC1 | 275 | 41.9283 | 15.8692 | 12.3864 | 34.8289 | 42.9693 | 16.7507 | 11.9834 | 35.6725
TOTT2 MC2A | 275 | 43.998 | 16.6144 | 13.0218 | 36.5182 | 39.9927 | 15.7316 | 10.8424 | 33.0902
TOTT2 MC2B | 275 | 72.4499 | 25.7427 | 19.7642 | 56.1698 | 73.3189 | 27.7438 | 16.8017 | 56.0374
TOTT2 MC3 | 275 | 43.998 | 16.6144 | 13.0218 | 36.5182 | 39.9927 | 15.7316 | 10.8424 | 33.0902
TOTT2 MC4A | 275 | 41.9283 | 15.8692 | 12.3864 | 34.8289 | 42.9693 | 16.7507 | 11.9834 | 35.6725
TOTT2 MC4B | 275 | 70.6929 | 25.1519 | 19.5352 | 55.1054 | 72.6374 | 27.4533 | 16.8503 | 55.6751
TOTT2 MC5 | 275 | 72.4499 | 25.7427 | 19.7642 | 56.1698 | 73.3189 | 27.7438 | 16.8017 | 56.0374
TOTT2 MC6 | 275 | 72.4499 | 25.7427 | 19.7642 | 56.1698 | 73.3189 | 27.7438 | 16.8017 | 56.0374
TOTT2 MC7 | 275 | 70.6929 | 25.1519 | 19.5352 | 55.1054 | 72.6374 | 27.4533 | 16.8503 | 55.6751
TOTT2 MC8 | 275 | 70.6929 | 25.1519 | 19.5352 | 55.1054 | 72.6374 | 27.4533 | 16.8503 | 55.6751
TRAW2 M1 | 275 | 44.534 | 15.9996 | 13.6721 | 36.2989 | 46.7112 | 17.4735 | 12.6287 | 37.3399
TRAW2 M2 | 275 | 44.534 | 15.9996 | 13.6721 | 36.2989 | 46.7112 | 17.4735 | 12.6287 | 37.3399
TRAW2 R1 | 275 | 44.534 | 15.9996 | 13.6721 | 36.2989 | 46.7112 | 17.4735 | 12.6287 | 37.3399
TRAW2 R2 | 275 | 44.534 | 15.9996 | 13.6721 | 36.2989 | 46.7112 | 17.4735 | 12.6287 | 37.3399
TRAW4 MC1 | 400 | 58.2614 | 21.7027 | 17.7546 | 48.4468 | 46.9427 | 18.5786 | 12.3503 | 38.6244
TRAW4 MC2 | 400 | 58.2614 | 21.7027 | 17.7546 | 48.4468 | 46.9427 | 18.5786 | 12.3503 | 38.6244
TRAW4 MC3 | 400 | 58.2614 | 21.7027 | 17.7546 | 48.4468 | 46.9427 | 18.5786 | 12.3503 | 38.6244
TRAW4 MC4 | 400 | 58.2614 | 21.7027 | 17.7546 | 48.4468 | 46.9427 | 18.5786 | 12.3503 | 38.6244
TREM2 MC1 | 275 | 46.4512 | 17.0016 | 2.674 | 26.7179 | 41.1396 | 16.3262 | 2.3522 | 25.441
TREM2 MC2 | 275 | 46.4512 | 17.0016 | 2.674 | 26.7179 | 41.1396 | 16.3262 | 2.3522 | 25.441
TREU4A | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.3295 | 28.2166 | 4.5563 | 44.4606
TREU4A_DEES1 | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.3295 | 28.2166 | 4.5563 | 44.4606
TREU4A_LEGA1 | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.3295 | 28.2166 | 4.5563 | 44.4606
TREU4A_TRAW1 | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.3295 | 28.2166 | 4.5563 | 44.4606
TREU4B | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.5632 | 28.3059 | 4.571 | 44.6016
TREU4B_DEES2 | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.5632 | 28.3059 | 4.571 | 44.6016
TREU4B_LEGA2 | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.5632 | 28.3059 | 4.571 | 44.6016
TREU4B_TRAW2 | 400 | 87.8544 | 30.9808 | 9.3701 | 53.1836 | 72.5632 | 28.3059 | 4.571 | 44.6016
TYNE2 MC1 | 275 | 63.5411 | 23.2997 | 11.4366 | 44.3873 | 55.7012 | 21.9363 | 9.5873 | 40.61
TYNE2 MC2 | 275 | 63.5411 | 23.2997 | 11.4366 | 44.3873 | 55.7012 | 21.9363 | 9.5873 | 40.61
TYNE2A | 275 | 62.8074 | 22.6737 | 4.0434 | 36.1088 | 52.4688 | 20.7748 | 2.8667 | 32.2467
UPPB2 MC1 | 275 | 39.3056 | 14.6513 | 9.7644 | 30.4845 | 38.4858 | 14.905 | 8.5268 | 29.6057
UPPB2 MC2 | 275 | 41.7864 | 15.5402 | 10.128 | 32.1052 | 40.269 | 15.5695 | 8.976 | 30.9946
UPPB2 MC3 | 275 | 41.7864 | 15.5402 | 10.128 | 32.1052 | 40.269 | 15.5695 | 8.976 | 30.9946
UPPB2 MC4 | 275 | 39.3056 | 14.6513 | 9.7644 | 30.4845 | 38.4858 | 14.905 | 8.5268 | 29.6057
USKM2 M1 | 275 | 76.743 | 27.1787 | 19.5618 | 57.9983 | 86.717 | 32.4133 | 22.7849 | 68.6243
USKM2 M2 | 275 | 76.743 | 27.1787 | 19.5618 | 57.9983 | 86.717 | 32.4133 | 22.7849 | 68.6243
USKM2 R1 | 275 | 76.743 | 27.1787 | 19.5618 | 57.9983 | 86.717 | 32.4133 | 22.7849 | 68.6243
USKM2 R2 | 275 | 76.743 | 27.1787 | 19.5618 | 57.9983 | 86.717 | 32.4133 | 22.7849 | 68.6243
USKM2A | 275 | 74.3902 | 25.7094 | 11.2185 | 47.577 | 82.0762 | 30.5768 | 11.8981 | 55.1402
WALH4 MC1 | 400 | 59.9261 | 22.3021 | 11.4621 | 43.002 | 51.0074 | 19.9666 | 10.4222 | 38.6591
WALH4 MC2 | 400 | 59.9261 | 22.3021 | 11.4621 | 43.002 | 51.0074 | 19.9666 | 10.4222 | 38.6591
WALH4 MC3 | 400 | 59.9261 | 22.3021 | 11.4621 | 43.002 | 51.0074 | 19.9666 | 10.4222 | 38.6591
WALH4 MC4 | 400 | 59.9261 | 22.3021 | 11.4621 | 43.002 | 51.0074 | 19.9666 | 10.4222 | 38.6591
WALP R4 | 132 | 69.3878 | 24.3874 | 20.8433 | 55.3322 | 83.8393 | 32.0282 | 22.7755 | 68.0702
WALP1 M4 | 132 | 69.3878 | 24.3874 | 20.8433 | 55.3322 | 83.8393 | 32.0282 | 22.7755 | 68.0702
WALP4 M1 | 400 | 117.3794 | 40.3816 | 30.8025 | 87.9107 | 96.258 | 36.2244 | 25.0454 | 76.2744
WALP4 M2 | 400 | 117.3794 | 40.3816 | 30.8025 | 87.9107 | 96.258 | 36.2244 | 25.0454 | 76.2744
WALP4 R1 | 400 | 117.3794 | 40.3816 | 30.8025 | 87.9107 | 96.258 | 36.2244 | 25.0454 | 76.2744
WALP4 R2 | 400 | 117.3794 | 40.3816 | 30.8025 | 87.9107 | 96.258 | 36.2244 | 25.0454 | 76.2744
WALPM3 | 132 | 69.3878 | 24.3874 | 20.8433 | 55.3322 | 83.8393 | 32.0282 | 22.7755 | 68.0702
WALPR3 | 132 | 69.3878 | 24.3874 | 20.8433 | 55.3322 | 83.8393 | 32.0282 | 22.7755 | 68.0702
WALX2 M1 | 275 | 73.6072 | 25.983 | 16.5936 | 53.3392 | 77.5646 | 28.8833 | 16.0462 | 56.8934
WALX2 M2 | 275 | 75.8072 | 26.6648 | 17.114 | 54.8237 | 81.7023 | 30.3015 | 17.1421 | 59.9949
WALX2 R1 | 275 | 73.6072 | 25.983 | 16.5936 | 53.3392 | 77.5646 | 28.8833 | 16.0462 | 56.8934
WALX2 R2 | 275 | 75.8072 | 26.6648 | 17.114 | 54.8237 | 81.7023 | 30.3015 | 17.1421 | 59.9949
WALX4A | 400 | 66.4531 | 23.5981 | 8.7494 | 42.1221 | 67.2319 | 25.1549 | 9.3555 | 44.9299
WALX4B | 400 | 66.42 | 23.6082 | 8.7902 | 42.1773 | 61.8054 | 23.202 | 8.7247 | 41.5372
WARL2 MC1 | 275 | 65.1376 | 23.643 | 15.4966 | 48.9329 | 60.5883 | 23.5286 | 11.506 | 44.7805
WARL2 MC2 | 275 | 65.1376 | 23.643 | 15.4966 | 48.9329 | 60.5883 | 23.5286 | 11.506 | 44.7805
WARL2 MC3 | 275 | 65.1376 | 23.643 | 15.4966 | 48.9329 | 60.5883 | 23.5286 | 11.506 | 44.7805
WARL2 MC4 | 275 | 65.1376 | 23.643 | 15.4966 | 48.9329 | 60.5883 | 23.5286 | 11.506 | 44.7805
WASF2A | 275 | 54.987 | 20.1146 | 12.3288 | 40.7751 | 47.9572 | 18.746 | 8.2977 | 34.8086
WASF2B | 275 | 59.4957 | 21.629 | 13.2815 | 43.8694 | 54.2644 | 21.2407 | 9.0268 | 39.0657
WBOL2 MC1 | 275 | 77.6692 | 27.8321 | 15.6709 | 55.0313 | 67.3638 | 26.5182 | 11.2568 | 48.7592
WBOL2 MC2 | 275 | 77.6692 | 27.8321 | 15.6709 | 55.0313 | 67.3638 | 26.5182 | 11.2568 | 48.7592
WBOL2 MC3 | 275 | 77.6692 | 27.8321 | 15.6709 | 55.0313 | 67.3638 | 26.5182 | 11.2568 | 48.7592
WBOL2 MC4 | 275 | 77.6692 | 27.8321 | 15.6709 | 55.0313 | 67.3638 | 26.5182 | 11.2568 | 48.7592
WBUR1 M1 | 132 | 21.2948 | 7.5568 | 6.7461 | 17.433 | 24.7912 | 9.1766 | 8.0448 | 21.0225
WBUR1 M2 | 132 | 21.2948 | 7.5568 | 6.7461 | 17.433 | 24.7912 | 9.1766 | 8.0448 | 21.0225
WBUR1 R1 | 132 | 21.2948 | 7.5568 | 6.7461 | 17.433 | 24.7912 | 9.1766 | 8.0448 | 21.0225
WBUR1 R2 | 132 | 21.0731 | 7.497 | 6.6417 | 17.2441 | 24.6313 | 9.1167 | 7.9543 | 20.8472
WBUR4 M1 | 400 | 114.9805 | 40.1667 | 33.1847 | 89.9889 | 103.3698 | 38.4082 | 29.9541 | 84.2715
WBUR4 M2 | 400 | 114.9805 | 40.1667 | 33.1847 | 89.9889 | 103.3698 | 38.4082 | 29.9541 | 84.2715
WBUR4 M3 | 400 | 114.9805 | 40.1667 | 33.1847 | 89.9889 | 103.3698 | 38.4082 | 29.9541 | 84.2715
WBUR4 M4 | 400 | 114.9805 | 40.1667 | 33.1847 | 89.9889 | 103.3698 | 38.4082 | 29.9541 | 84.2715
WBUR4 R1/2 | 400 | 109.6414 | 39.2689 | 27.3781 | 82.9126 | 87.2529 | 33.4042 | 21.1784 | 68.4191
WBUR4 R3/4 | 400 | 109.6414 | 39.2689 | 27.3781 | 82.9126 | 87.2529 | 33.4042 | 21.1784 | 68.4191
WHAM4 M1 | 400 | 111.4212 | 39.3218 | 34.9786 | 90.588 | 115.0725 | 44.6801 | 31.674 | 94.8612
WHAM4 M2 | 400 | 111.4212 | 39.3218 | 34.9786 | 90.588 | 115.0725 | 44.6801 | 31.674 | 94.8612
WHAM4 R1 | 400 | 111.4212 | 39.3218 | 34.9786 | 90.588 | 115.0725 | 44.6801 | 31.674 | 94.8612
WHAM4 R2 | 400 | 111.4212 | 39.3218 | 34.9786 | 90.588 | 115.0725 | 44.6801 | 31.674 | 94.8612
WHAM4A | 400 | 95.7241 | 31.3315 | 12.0394 | 56.3488 | 99.1574 | 38.9895 | 14.4965 | 69.636
WHAM4B | 400 | 95.7912 | 31.3488 | 12.0499 | 56.3838 | 99.2624 | 39.0262 | 14.4973 | 69.6887
WHGA2 MC1 | 275 | 69.8528 | 25.4407 | 14.8322 | 50.8107 | 65.8789 | 25.7419 | 11.9281 | 48.3326
WHGA2 MC2 | 275 | 69.8528 | 25.4407 | 14.8322 | 50.8107 | 65.8789 | 25.7419 | 11.9281 | 48.3326
WHGA2 MC3 | 275 | 69.8528 | 25.4407 | 14.8322 | 50.8107 | 65.8789 | 25.7419 | 11.9281 | 48.3326
WHGA2 MC4 | 275 | 69.8528 | 25.4407 | 14.8322 | 50.8107 | 65.8789 | 25.7419 | 11.9281 | 48.3326
WHSO2 M1 | 275 | 67.1328 | 24.1973 | 14.92 | 49.1402 | 72.3753 | 27.5832 | 15.5909 | 54.5995
WHSO2 M2 | 275 | 67.1328 | 24.1973 | 14.92 | 49.1402 | 72.3753 | 27.5832 | 15.5909 | 54.5995
WHSO2 R1 | 275 | 73.5238 | 26.2327 | 18.7596 | 55.8582 | 80.4102 | 30.3079 | 19.8826 | 62.7445
WHSO2 R2 | 275 | 73.5238 | 26.2327 | 18.7596 | 55.8582 | 80.4102 | 30.3079 | 19.8826 | 62.7445
WIBA2 MC1 | 275 | 59.1094 | 21.8116 | 12.1015 | 42.9477 | 62.6927 | 25.0688 | 10.2086 | 45.6613
WIBA2 MC1 | 275 | 59.1094 | 21.8116 | 12.1015 | 42.9477 | 62.6927 | 25.0688 | 10.2086 | 45.6613
WIBA2 MC2 | 275 | 59.1094 | 21.8116 | 12.1015 | 42.9477 | 62.6927 | 25.0688 | 10.2086 | 45.6613
WIBA2 MC2 | 275 | 59.1094 | 21.8116 | 12.1015 | 42.9477 | 62.6927 | 25.0688 | 10.2086 | 45.6613
WILE4 M1 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 M1 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 M2 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 M2 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 R1 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 R1 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 R2 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILE4 R2 | 400 | 99.7271 | 37.2638 | 26.6697 | 79.3686 | 84.4598 | 33.6244 | 21.4956 | 69.0476
WILL1 M2 | 132 | 52.5007 | 18.392 | 16.1294 | 42.1396 | 58.9912 | 22.4242 | 18.3261 | 50.0388
WILL1 R1 | 132 | 36.3312 | 13.46 | 10.8976 | 29.9329 | 39.6059 | 15.2992 | 12.2847 | 33.9211
WILL1 R2 | 132 | 52.5007 | 18.392 | 16.1294 | 42.1396 | 58.9912 | 22.4242 | 18.3261 | 50.0388
WILL2 M2 | 275 | 23.8585 | 8.5379 | 8.753 | 20.8273 | 25.2722 | 9.2368 | 9.0224 | 22.0852
WILL2 M2 | 275 | 23.8585 | 8.5379 | 8.753 | 20.8273 | 25.2722 | 9.2368 | 9.0224 | 22.0852
WILL2 R2 | 275 | 23.8585 | 8.5379 | 8.753 | 20.8273 | 25.2722 | 9.2368 | 9.0224 | 22.0852
WILL2 R2 | 275 | 23.8585 | 8.5379 | 8.753 | 20.8273 | 25.2722 | 9.2368 | 9.0224 | 22.0852
WILT2A | 275 | 56.2726 | 19.8325 | 10.6814 | 38.7288 | 57.854 | 21.398 | 9.5804 | 39.8417
WILT2A | 275 | 56.2726 | 19.8325 | 10.6814 | 38.7288 | 57.854 | 21.398 | 9.5804 | 39.8417
WILT2B | 275 | 56.2726 | 19.8325 | 10.6814 | 38.7288 | 57.854 | 21.398 | 9.5804 | 39.8417
WILT2B | 275 | 56.2726 | 19.8325 | 10.6814 | 38.7288 | 57.854 | 21.398 | 9.5804 | 39.8417
WILT2C | 275 | 56.6233 | 19.94 | 10.8637 | 39.0631 | 58.804 | 21.6869 | 10.2992 | 40.9691
WILT2C | 275 | 56.6233 | 19.94 | 10.8637 | 39.0631 | 58.804 | 21.6869 | 10.2992 | 40.9691
WILT2D | 275 | 56.6213 | 19.9395 | 10.863 | 39.0617 | 58.7994 | 21.6854 | 10.2972 | 40.965
WILT2D | 275 | 56.6213 | 19.9395 | 10.863 | 39.0617 | 58.7994 | 21.6854 | 10.2972 | 40.965
WIMB4 MB2 | 400 | 94.1129 | 31.75 | 23.7832 | 68.6844 | 110.5896 | 41.3002 | 24.2727 | 82.68
WIMB4 MB2 | 400 | 94.1129 | 31.75 | 23.7832 | 68.6844 | 110.5896 | 41.3002 | 24.2727 | 82.68
WIMB4 RB2 | 400 | 94.1129 | 31.75 | 23.7832 | 68.6844 | 110.5896 | 41.3002 | 24.2727 | 82.68
WIMB4 RB2 | 400 | 94.1129 | 31.75 | 23.7832 | 68.6844 | 110.5896 | 41.3002 | 24.2727 | 82.68
WISD2 M1 | 275 | 67.71 | 23.3876 | 22.1361 | 55.2112 | 79.5507 | 29.248 | 24.9823 | 66.3452
WISD2 M2 | 275 | 67.71 | 23.3876 | 22.1361 | 55.2112 | 79.5507 | 29.248 | 24.9823 | 66.3452
WISD2 R1 | 275 | 67.71 | 23.3876 | 22.1361 | 55.2112 | 79.5507 | 29.248 | 24.9823 | 66.3452
WISD2 R2 | 275 | 67.71 | 23.3876 | 22.1361 | 55.2112 | 79.5507 | 29.248 | 24.9823 | 66.3452
WISD2A | 275 | 56.7021 | 19.6915 | 11.7906 | 39.6385 | 62.8844 | 23.9769 | 13.3396 | 47.2481
WISD2B | 275 | 56.7021 | 19.6915 | 11.7906 | 39.6385 | 62.8844 | 23.9769 | 13.3396 | 47.2481
WISD6 M1 | 66 | 50.232 | 16.987 | 17.0863 | 41.1096 | 33.4741 | 12.5452 | 10.7925 | 28.5341
WISD6 M2 | 66 | 50.232 | 16.987 | 17.0863 | 41.1096 | 33.4741 | 12.5452 | 10.7925 | 28.5341
WISD6 R1 | 66 | 50.232 | 16.987 | 17.0863 | 41.1096 | 33.4741 | 12.5452 | 10.7925 | 28.5341
WISD6 R2 | 66 | 50.232 | 16.987 | 17.0863 | 41.1096 | 33.4741 | 12.5452 | 10.7925 | 28.5341
WMEL2 MC1 | 275 | 77.2625 | 28.2829 | 14.1321 | 54.1302 | 73.665 | 29.0317 | 11.8948 | 52.9518
WMEL2 MC2 | 275 | 77.2625 | 28.2829 | 14.1321 | 54.1302 | 73.665 | 29.0317 | 11.8948 | 52.9518
WMEL2 MC3 | 275 | 77.2625 | 28.2829 | 14.1321 | 54.1302 | 73.665 | 29.0317 | 11.8948 | 52.9518
WMEL2 MC4 | 275 | 77.2625 | 28.2829 | 14.1321 | 54.1302 | 73.665 | 29.0317 | 11.8948 | 52.9518
WTHU4A | 400 | 90.7878 | 31.1165 | 8.3024 | 52.3078 | 73.4754 | 28.6397 | 4.971 | 45.4736
WTHU4B | 400 | 90.7878 | 31.1165 | 8.3024 | 52.3078 | 75.0739 | 29.2365 | 5.0791 | 46.4258
WWEY2 M1 | 275 | 72.4564 | 26.3353 | 17.7331 | 54.9768 | 71.3197 | 27.2513 | 16.6512 | 55.1904
WWEY2 M2 | 275 | 72.4564 | 26.3353 | 17.7331 | 54.9768 | 71.3197 | 27.2513 | 16.6512 | 55.1904
WWEY2 R1 | 275 | 73.8532 | 26.9868 | 16.3977 | 54.5629 | 73.6963 | 28.2773 | 16.5172 | 56.5074
WWEY2 R2 | 275 | 73.8532 | 26.9868 | 16.3977 | 54.5629 | 73.6963 | 28.2773 | 16.5172 | 56.5074
WWEY4A | 400 | 50.0861 | 18.2581 | 6.186 | 32.0068 | 44.8841 | 17.2153 | 6.0919 | 30.438
WWEY4B | 400 | 50.2873 | 18.302 | 6.393 | 32.2759 | 44.6635 | 17.19 | 6.2955 | 30.6058
WYLF1 M1 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 M1 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 M2 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 M2 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 R1 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 R1 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 R2 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF1 R2 | 132 | 26.7984 | 9.3574 | 7.6773 | 20.9107 | 29.7289 | 10.9172 | 8.4187 | 23.8579
WYLF4 M1 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 M1 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 M2 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 M2 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 R1 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 R1 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 R2 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYLF4 R2 | 400 | 48.9668 | 17.7498 | 12.1171 | 37.2192 | 36.6014 | 14.2864 | 7.0901 | 27.2941
WYMO4 M1 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 M1 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 M2 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 M2 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 R1 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 R1 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 R2 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478
WYMO4 R2 | 400 | 109.4535 | 39.2403 | 24.3917 | 79.8858 | 93.8072 | 36.0922 | 18.9057 | 69.9478

## D3.6
ETYS 19 Yr 7 - NGET Fault Levels (kA), Winter 2025/26
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 36.6247 | 13.4867 | 2.8497 | 21.9228 | 33.9749 | 13.3292 | 2.1907 | 21.041 | Back To Menu
ABHA4B | 400 | 36.6096 | 13.4778 | 2.8502 | 21.9107 | 33.9664 | 13.3237 | 2.1866 | 21.0292
ABTH1 M1 | 132 | 28.0864 | 10.5407 | 6.1402 | 21.047 | 27.0165 | 10.6533 | 6.1299 | 21.196
ABTH1 M2 | 132 | 25.8564 | 10.06 | 7.6633 | 21.8903 | 22.8727 | 9.168 | 6.6899 | 19.6555
ABTH1 R1 | 132 | 28.5499 | 11.0044 | 7.6852 | 23.2478 | 31.311 | 12.3572 | 8.8082 | 26.284
ABTH1 R2 | 132 | 28.5499 | 11.0044 | 7.6852 | 23.2478 | 31.311 | 12.3572 | 8.8082 | 26.284
ABTH2 M1 | 275 | 48.1923 | 17.9427 | 8.8142 | 34.1891 | 43.7572 | 17.3166 | 7.3072 | 31.7965
ABTH2 M2 | 275 | 48.1923 | 17.9427 | 8.8142 | 34.1891 | 43.7572 | 17.3166 | 7.3072 | 31.7965
ABTH2 M4 | 275 | 48.1923 | 17.9427 | 8.8142 | 34.1891 | 43.7572 | 17.3166 | 7.3072 | 31.7965
ABTH2 R | 275 | 39.6787 | 14.9955 | 4.4861 | 25.693 | 33.9135 | 13.5949 | 2.8021 | 22.0283
ALDW2 MC1 | 275 | 62.837 | 23.376 | 9.9576 | 43.0163 | 61.3666 | 24.3139 | 9.7536 | 44.1387
ALDW2 MC2 | 275 | 62.837 | 23.376 | 9.9576 | 43.0163 | 61.3666 | 24.3139 | 9.7536 | 44.1387
ALDW2 MC3 | 275 | 62.837 | 23.376 | 9.9576 | 43.0163 | 61.3666 | 24.3139 | 9.7536 | 44.1387
ALDW2 MC4 | 275 | 62.837 | 23.376 | 9.9576 | 43.0163 | 61.3666 | 24.3139 | 9.7536 | 44.1387
AMEM1 M1 | 132 | 25.6561 | 9.1527 | 9.1864 | 22.1303 | 31.598 | 11.6169 | 10.4702 | 26.899
AMEM1 M2 | 132 | 25.6561 | 9.1527 | 9.1864 | 22.1303 | 31.598 | 11.6169 | 10.4702 | 26.899
AMEM1 R1 | 132 | 25.6561 | 9.1527 | 9.1864 | 22.1303 | 31.598 | 11.6169 | 10.4702 | 26.899
AMEM1 R2 | 132 | 25.6561 | 9.1527 | 9.1864 | 22.1303 | 31.598 | 11.6169 | 10.4702 | 26.899
AMEM4 M | 400 | 49.162 | 18.2174 | 4.1265 | 29.8897 | 41.345 | 16.3914 | 2.8559 | 26.0369
AMEM4 R | 400 | 50.2031 | 18.5689 | 4.2319 | 30.4923 | 41.3142 | 16.3097 | 2.8292 | 25.8946
AXMI4 MC1 | 400 | 39.0325 | 14.5869 | 7.4133 | 28.0422 | 33.8624 | 13.2603 | 6.01 | 24.7628
AXMI4 MC2 | 400 | 39.0325 | 14.5869 | 7.4133 | 28.0422 | 33.8624 | 13.2603 | 6.01 | 24.7628
BAGB2 M1 | 275 | 49.7845 | 18.1722 | 12.9375 | 38.6369 | 48.2334 | 18.3934 | 12.8411 | 38.8533
BAGB2 M2 | 275 | 49.7845 | 18.1722 | 12.9375 | 38.6369 | 48.2334 | 18.3934 | 12.8411 | 38.8533
BAGB2 R1 | 275 | 49.7845 | 18.1722 | 12.9375 | 38.6369 | 48.2334 | 18.3934 | 12.8411 | 38.8533
BAGB2 R2 | 275 | 49.7845 | 18.1722 | 12.9375 | 38.6369 | 48.2334 | 18.3934 | 12.8411 | 38.8533
BARK2 M1 | 275 | 53.4357 | 19.2846 | 14.1662 | 41.4387 | 53.6627 | 20.2991 | 14.0726 | 42.7798
BARK2 M2 | 275 | 51.5369 | 18.6099 | 13.9051 | 40.2234 | 53.5539 | 20.1938 | 14.5607 | 43.119
BARK2 R1 | 275 | 53.4357 | 19.2846 | 14.1662 | 41.4387 | 53.6627 | 20.2991 | 14.0726 | 42.7798
BARK2 R2 | 275 | 51.5369 | 18.6099 | 13.9051 | 40.2234 | 53.5539 | 20.1938 | 14.5607 | 43.119
BARK4 M1 | 400 | 131.4433 | 45.9662 | 40.1016 | 105.1077 | 123.5181 | 47.772 | 32.2094 | 99.7693
BARK4 M2 | 400 | 131.4433 | 45.9662 | 40.1016 | 105.1077 | 123.5181 | 47.772 | 32.2094 | 99.7693
BARK4 R1 | 400 | 131.4433 | 45.9662 | 40.1016 | 105.1077 | 123.5181 | 47.772 | 32.2094 | 99.7693
BARK4 R2 | 400 | 131.4433 | 45.9662 | 40.1016 | 105.1077 | 123.5181 | 47.772 | 32.2094 | 99.7693
BEDD2 M1/4 | 275 | 56.3331 | 20.3845 | 13.7388 | 42.5669 | 57.2769 | 22.2503 | 14.0086 | 45.4753
BEDD2 M2/3 | 275 | 79.2001 | 28.4057 | 17.911 | 58.0827 | 79.3717 | 30.6472 | 17.8006 | 61.1424
BEDD2 R1 | 275 | 51.3762 | 19.0764 | 11.3378 | 38.3158 | 51.3125 | 19.8103 | 11.1815 | 39.1975
BEDD2 R2 | 275 | 79.2001 | 28.4057 | 17.911 | 58.0827 | 79.3717 | 30.6472 | 17.8006 | 61.1424
BEDD2 R3 | 275 | 79.2001 | 28.4057 | 17.911 | 58.0827 | 79.3717 | 30.6472 | 17.8006 | 61.1424
BEDD2 R4 | 275 | 51.3762 | 19.0764 | 11.3378 | 38.3158 | 51.3125 | 19.8103 | 11.1815 | 39.1975
BEDD4B | 400 | 42.2818 | 15.7507 | 3.1021 | 25.377 | 37.2746 | 14.8967 | 3.7021 | 24.7692
BESW2 MC1 | 275 | 57.8544 | 21.1583 | 10.5298 | 40.4522 | 50.642 | 20.145 | 8.2657 | 36.755
BESW2 MC2 | 275 | 57.8544 | 21.1583 | 10.5298 | 40.4522 | 50.642 | 20.145 | 8.2657 | 36.755
BESW2 MC3 | 275 | 57.8544 | 21.1583 | 10.5298 | 40.4522 | 50.642 | 20.145 | 8.2657 | 36.755
BESW2 MC4 | 275 | 57.8544 | 21.1583 | 10.5298 | 40.4522 | 50.642 | 20.145 | 8.2657 | 36.755
BICF4A | 400 | 129.009 | 42.9256 | 46.4455 | 107.1515 | 68.087 | 26.7448 | 17.2615 | 55.0844
BICF4B | 400 | 129.009 | 42.9256 | 46.4455 | 107.1515 | 68.087 | 26.7448 | 17.2615 | 55.0844
BIRK2 MC1 | 275 | 56.4478 | 20.0295 | 14.6176 | 42.9436 | 56.875 | 21.5013 | 12.6801 | 43.0876
BIRK2 MC2 | 275 | 56.4478 | 20.0295 | 14.6176 | 42.9436 | 56.875 | 21.5013 | 12.6801 | 43.0876
BIRK2 MC3 | 275 | 56.4478 | 20.0295 | 14.6176 | 42.9436 | 56.875 | 21.5013 | 12.6801 | 43.0876
BIRK2 MC4 | 275 | 56.4478 | 20.0295 | 14.6176 | 42.9436 | 56.875 | 21.5013 | 12.6801 | 43.0876
BISW2 MC1 | 275 | 63.2387 | 23.045 | 11.7619 | 44.3524 | 58.5298 | 22.9849 | 9.5883 | 42.0939
BISW2 MC2 | 275 | 63.2387 | 23.045 | 11.7619 | 44.3524 | 58.5298 | 22.9849 | 9.5883 | 42.0939
BISW2 MC3 | 275 | 63.2387 | 23.045 | 11.7619 | 44.3524 | 58.5298 | 22.9849 | 9.5883 | 42.0939
BISW2 MC4 | 275 | 63.2387 | 23.045 | 11.7619 | 44.3524 | 58.5298 | 22.9849 | 9.5883 | 42.0939
BLYT1A | 132 | 32.2256 | 11.3921 | 4.5717 | 20.6826 | 33.0288 | 12.4563 | 5.1976 | 22.8134
BLYT1B | 132 | 31.9612 | 11.329 | 4.5272 | 20.5488 | 32.8412 | 12.3989 | 5.1585 | 22.6931
BLYT2 M1 | 275 | 77.4433 | 28.0566 | 23.2597 | 62.9377 | 71.445 | 27.5304 | 20.5348 | 59.4687
BLYT2 M2 | 275 | 77.4433 | 28.0566 | 23.2597 | 62.9377 | 71.445 | 27.5304 | 20.5348 | 59.4687
BLYT2 R1 | 275 | 77.4433 | 28.0566 | 23.2597 | 62.9377 | 71.445 | 27.5304 | 20.5348 | 59.4687
BLYT2 R2 | 275 | 77.4433 | 28.0566 | 23.2597 | 62.9377 | 71.445 | 27.5304 | 20.5348 | 59.4687
BODE4 M1 | 400 | 78.5767 | 28.044 | 18.449 | 58.1092 | 68.3479 | 26.2811 | 14.8177 | 51.9848
BODE4 R1 | 400 | 78.5767 | 28.044 | 18.449 | 58.1092 | 68.3479 | 26.2811 | 14.8177 | 51.9848
BOLN4 M1 | 400 | 70.6488 | 26.2049 | 21.0947 | 58.1539 | 64.26 | 24.7385 | 19.5044 | 54.4899
BOLN4 M2 | 400 | 70.6488 | 26.2049 | 21.0947 | 58.1539 | 64.26 | 24.7385 | 19.5044 | 54.4899
BOLN4 R1 | 400 | 70.6488 | 26.2049 | 21.0947 | 58.1539 | 64.26 | 24.7385 | 19.5044 | 54.4899
BOLN4 R2 | 400 | 70.6488 | 26.2049 | 21.0947 | 58.1539 | 64.26 | 24.7385 | 19.5044 | 54.4899
BOTW4 MC1 | 400 | 78.1267 | 28.2298 | 15.4815 | 55.4046 | 61.889 | 24.0714 | 11.8422 | 45.8843
BOTW4 MC2 | 400 | 78.1267 | 28.2298 | 15.4815 | 55.4046 | 61.889 | 24.0714 | 11.8422 | 45.8843
BRAI4A | 400 | 63.6771 | 23.1976 | 14.3812 | 47.1876 | 47.7567 | 18.659 | 9.1452 | 35.5331
BRAI4A BRFO | 400 | 63.6771 | 23.1976 | 14.3812 | 47.1876 | 47.7567 | 18.659 | 9.1452 | 35.5331
BRAI4A RAYL | 400 | 63.6771 | 23.1976 | 14.3812 | 47.1876 | 47.7567 | 18.659 | 9.1452 | 35.5331
BRAI4B | 400 | 60.7236 | 22.2259 | 13.3064 | 44.7386 | 45.7301 | 17.8244 | 8.7214 | 33.929
BRAI4B PELH | 400 | 60.7236 | 22.2259 | 13.3064 | 44.7386 | 45.7301 | 17.8244 | 8.7214 | 33.929
BRAI4B RAYL | 400 | 60.7236 | 22.2259 | 13.3064 | 44.7386 | 45.7301 | 17.8244 | 8.7214 | 33.929
BRAW2 MC1 | 275 | 64.4373 | 23.1011 | 14.8182 | 47.4881 | 65.3762 | 25.0366 | 13.8456 | 49.2527
BRAW2 MC2 | 275 | 64.4373 | 23.1011 | 14.8182 | 47.4881 | 65.3762 | 25.0366 | 13.8456 | 49.2527
BRAW2 MC3 | 275 | 64.4373 | 23.1011 | 14.8182 | 47.4881 | 65.3762 | 25.0366 | 13.8456 | 49.2527
BRAW2 MC4 | 275 | 64.4373 | 23.1011 | 14.8182 | 47.4881 | 65.3762 | 25.0366 | 13.8456 | 49.2527
BRAW4A | 400 | 34.4396 | 12.5231 | 4.3781 | 22.0884 | 30.2487 | 11.4862 | 4.1674 | 20.4114
BRED2 MC1 | 275 | 77.5741 | 28.3341 | 15.4515 | 55.5219 | 74.3892 | 29.1255 | 12.6273 | 53.817
BRED2 MC2 | 275 | 77.5741 | 28.3341 | 15.4515 | 55.5219 | 74.3892 | 29.1255 | 12.6273 | 53.817
BRED2 MC3 | 275 | 77.5741 | 28.3341 | 15.4515 | 55.5219 | 74.3892 | 29.1255 | 12.6273 | 53.817
BRED2 MC4 | 275 | 77.5741 | 28.3341 | 15.4515 | 55.5219 | 74.3892 | 29.1255 | 12.6273 | 53.817
BRFO4 M3 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 M5 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 M6 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 M7 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 R3 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 R5 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 R6 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRFO4 R7 | 400 | 92.2608 | 33.1482 | 30.2968 | 77.1755 | 78.1642 | 30.0119 | 22.9377 | 65.3809
BRIM1 M1 | 132 | 52.0323 | 17.5716 | 19.2139 | 44.0639 | 66.0158 | 23.689 | 23.1132 | 56.6145
BRIM1 M2 | 132 | 52.0323 | 17.5716 | 19.2139 | 44.0639 | 66.0158 | 23.689 | 23.1132 | 56.6145
BRIM1 R1 | 132 | 52.0323 | 17.5716 | 19.2139 | 44.0639 | 66.0158 | 23.689 | 23.1132 | 56.6145
BRIM1 R2 | 132 | 52.0323 | 17.5716 | 19.2139 | 44.0639 | 66.0158 | 23.689 | 23.1132 | 56.6145
BRIN2 M1 | 275 | 64.5783 | 23.6238 | 13.8784 | 47.2875 | 67.8585 | 26.5322 | 12.7795 | 50.3017
BRIN2 M2 | 275 | 68.5531 | 25.0703 | 17.028 | 52.4829 | 71.5118 | 27.5619 | 16.3511 | 55.3296
BRIN2 R1 | 275 | 64.5783 | 23.6238 | 13.8784 | 47.2875 | 67.8585 | 26.5322 | 12.7795 | 50.3017
BRIN2 R2 | 275 | 68.5531 | 25.0703 | 17.028 | 52.4829 | 71.5118 | 27.5619 | 16.3511 | 55.3296
BRIN4 MC1 | 400 | 71.9859 | 26.1677 | 16.4433 | 53.45 | 55.4019 | 21.6549 | 11.2159 | 41.8406
BRIN4 MC4 | 400 | 71.9859 | 26.1677 | 16.4433 | 53.45 | 55.4019 | 21.6549 | 11.2159 | 41.8406
BRLE4 M1 | 400 | 122.758 | 43.8987 | 24.8742 | 86.9563 | 104.3813 | 40.5786 | 21.1681 | 78.555
BRLE4 M2 | 400 | 122.758 | 43.8987 | 24.8742 | 86.9563 | 104.3813 | 40.5786 | 21.1681 | 78.555
BRLE4 R1 | 400 | 122.758 | 43.8987 | 24.8742 | 86.9563 | 104.3813 | 40.5786 | 21.1681 | 78.555
BRLE4 R2 | 400 | 122.758 | 43.8987 | 24.8742 | 86.9563 | 104.3813 | 40.5786 | 21.1681 | 78.555
BULL4 MC1 | 400 | 68.9598 | 25.0501 | 15.1459 | 50.572 | 50.861 | 19.976 | 8.8397 | 37.09
BULL4 MC2 | 400 | 68.9598 | 25.0501 | 15.1459 | 50.572 | 50.861 | 19.976 | 8.8397 | 37.09
BURW4 MC1 | 400 | 92.8177 | 32.9441 | 22.4013 | 68.9912 | 61.5211 | 24.3771 | 11.1198 | 45.5942
BURW4 MC2 | 400 | 92.8177 | 32.9441 | 22.4013 | 68.9912 | 61.5211 | 24.3771 | 11.1198 | 45.5942
BURW4 MC3 | 400 | 92.8177 | 32.9441 | 22.4013 | 68.9912 | 61.5211 | 24.3771 | 11.1198 | 45.5942
BURW4 MC4 | 400 | 92.8177 | 32.9441 | 22.4013 | 68.9912 | 61.5211 | 24.3771 | 11.1198 | 45.5942
BUSH2 MC1 | 275 | 53.9742 | 19.6752 | 10.9683 | 38.7932 | 53.7935 | 20.9353 | 10.0925 | 39.6995
BUSH2 MC2 | 275 | 53.9742 | 19.6752 | 10.9683 | 38.7932 | 53.7935 | 20.9353 | 10.0925 | 39.6995
BUSH2 MC3 | 275 | 53.9742 | 19.6752 | 10.9683 | 38.7932 | 53.7935 | 20.9353 | 10.0925 | 39.6995
BUSH2 MC4 | 275 | 53.9742 | 19.6752 | 10.9683 | 38.7932 | 53.7935 | 20.9353 | 10.0925 | 39.6995
BUST2 M1 | 275 | 70.3056 | 25.1866 | 18.2612 | 53.8805 | 73.0858 | 27.8082 | 17.2289 | 56.5557
BUST2 M2 | 275 | 70.3056 | 25.1866 | 18.2612 | 53.8805 | 73.0858 | 27.8082 | 17.2289 | 56.5557
BUST2 R1 | 275 | 70.3056 | 25.1866 | 18.2612 | 53.8805 | 73.0858 | 27.8082 | 17.2289 | 56.5557
BUST2 R2 | 275 | 70.3056 | 25.1866 | 18.2612 | 53.8805 | 73.0858 | 27.8082 | 17.2289 | 56.5557
CANT4 MC1 | 400 | 90.9173 | 32.8627 | 19.1972 | 65.672 | 67.3257 | 26.6605 | 11.5665 | 49.2702
CANT4 MC2 | 400 | 90.9173 | 32.8627 | 19.1972 | 65.672 | 67.3257 | 26.6605 | 11.5665 | 49.2702
CANT4 MC3 | 400 | 90.9173 | 32.8627 | 19.1972 | 65.672 | 67.3257 | 26.6605 | 11.5665 | 49.2702
CANT4 MC4 | 400 | 90.9173 | 32.8627 | 19.1972 | 65.672 | 67.3257 | 26.6605 | 11.5665 | 49.2702
CANT4 R5 | 400 | 90.9173 | 32.8627 | 19.1972 | 65.672 | 67.3257 | 26.6605 | 11.5665 | 49.2702
CANT4 R5 | 400 | 90.9288 | 32.8676 | 19.2005 | 65.6823 | 67.3278 | 26.6616 | 11.5628 | 49.2681
CANT4 R5 | 400 | 90.9288 | 32.8676 | 19.2005 | 65.6823 | 67.3278 | 26.6616 | 11.5628 | 49.2681
CAPE2 M1 | 275 | 65.5045 | 22.8793 | 19.7744 | 52.1305 | 74.5034 | 27.3206 | 21.606 | 60.2432
CAPE2 M2 | 275 | 65.5045 | 22.8793 | 19.7744 | 52.1305 | 74.5034 | 27.3206 | 21.606 | 60.2432
CAPE2 R1 | 275 | 65.5045 | 22.8793 | 19.7744 | 52.1305 | 74.5034 | 27.3206 | 21.606 | 60.2432
CAPE2 R2 | 275 | 65.5045 | 22.8793 | 19.7744 | 52.1305 | 74.5034 | 27.3206 | 21.606 | 60.2432
CAPE4A | 400 | 82.9548 | 29.3806 | 19.795 | 61.3454 | 79.2288 | 30.0604 | 17.2597 | 59.7715
CAPE4B | 400 | 82.9571 | 29.3816 | 19.7946 | 61.3465 | 79.8381 | 30.2871 | 17.3482 | 60.1806
CARE2 MC1 | 275 | 46.6835 | 17.5001 | 8.1849 | 32.9338 | 39.7227 | 15.7581 | 7.1014 | 29.3866
CARE2 MC2 | 275 | 46.6835 | 17.5001 | 8.1849 | 32.9338 | 39.7227 | 15.7581 | 7.1014 | 29.3866
CARR1 M1 | 132 | 34.8701 | 12.873 | 9.848 | 28.0531 | 40.6814 | 15.5085 | 11.6606 | 33.593
CARR1 M2 | 132 | 34.8701 | 12.873 | 9.848 | 28.0531 | 40.6814 | 15.5085 | 11.6606 | 33.593
CARR1 M3 | 132 | 34.8701 | 12.873 | 9.848 | 28.0531 | 40.6814 | 15.5085 | 11.6606 | 33.593
CARR1 M4 | 132 | 41.6949 | 14.6353 | 13.8676 | 34.5651 | 53.5453 | 19.623 | 17.326 | 45.0771
CARR1 R1 | 132 | 34.8701 | 12.873 | 9.848 | 28.0531 | 40.6814 | 15.5085 | 11.6606 | 33.593
CARR1 R2 | 132 | 34.8701 | 12.873 | 9.848 | 28.0531 | 40.6814 | 15.5085 | 11.6606 | 33.593
CARR1 R3 | 132 | 41.6949 | 14.6353 | 13.8676 | 34.5651 | 53.5453 | 19.623 | 17.326 | 45.0771
CARR1 R4 | 132 | 41.6949 | 14.6353 | 13.8676 | 34.5651 | 53.5453 | 19.623 | 17.326 | 45.0771
CARR1B | 132 | 40.9124 | 14.1886 | 7.8637 | 27.9294 | 50.6799 | 19.0911 | 6.947 | 33.9459
CARR1C | 132 | 40.7424 | 14.1722 | 7.4641 | 27.5066 | 50.2213 | 19.0421 | 5.4818 | 32.4115
CARR1D | 132 | 41.0215 | 14.2073 | 8.0908 | 28.1829 | 51.0553 | 19.1404 | 7.3028 | 34.3714
CARR2 M1 | 275 | 80.05 | 28.7627 | 21.0411 | 61.7177 | 86.6967 | 32.5876 | 23.2892 | 69.3751
CARR2 M2 | 275 | 80.05 | 28.7627 | 21.0411 | 61.7177 | 86.6967 | 32.5876 | 23.2892 | 69.3751
CARR2 R1 | 275 | 80.05 | 28.7627 | 21.0411 | 61.7177 | 86.6967 | 32.5876 | 23.2892 | 69.3751
CARR2 R2 | 275 | 80.05 | 28.7627 | 21.0411 | 61.7177 | 86.6967 | 32.5876 | 23.2892 | 69.3751
CARR4 M1 | 400 | 112.912 | 41.2503 | 32.8622 | 91.1988 | 100.7701 | 39.0518 | 28.839 | 84.0666
CARR4 M2/4 | 400 | 112.912 | 41.2503 | 32.8622 | 91.1988 | 100.7701 | 39.0518 | 28.839 | 84.0666
CARR4 R1 | 400 | 112.912 | 41.2503 | 32.8622 | 91.1988 | 100.7701 | 39.0518 | 28.839 | 84.0666
CARR4 R1/2 | 400 | 112.912 | 41.2503 | 32.8622 | 91.1988 | 100.7701 | 39.0518 | 28.839 | 84.0666
CARR4 R2 | 400 | 112.912 | 41.2503 | 32.8622 | 91.1988 | 100.7701 | 39.0518 | 28.839 | 84.0666
CARR4 R4 | 400 | 112.912 | 41.2503 | 32.8622 | 91.1988 | 100.7701 | 39.0518 | 28.839 | 84.0666
CARR4A | 400 | 95.9687 | 33.7605 | 8.0647 | 55.8093 | 80.0557 | 30.9373 | 8.0806 | 51.8325
CARR4B | 400 | 97.5616 | 34.2497 | 8.2758 | 56.7122 | 82.3695 | 31.8328 | 8.1133 | 53.1317
CASK1 M1 | 132 | 47.6078 | 15.8029 | 12.4652 | 34.8139 | 52.9511 | 18.5931 | 15.2153 | 41.5099
CELL1 M1 | 132 | 44.2641 | 16.417 | 13.8157 | 37.0328 | 55.365 | 21.7797 | 16.3802 | 47.1814
CELL1 M2 | 132 | 42.4971 | 15.6986 | 11.7638 | 33.9649 | 47.4667 | 18.3399 | 12.6869 | 38.6235
CELL1 R1 | 132 | 44.2641 | 16.417 | 13.8157 | 37.0328 | 55.365 | 21.7797 | 16.3802 | 47.1814
CELL1 R2 | 132 | 42.4971 | 15.6986 | 11.7638 | 33.9649 | 47.4667 | 18.3399 | 12.6869 | 38.6235
CELL1A | 132 | 37.1903 | 13.2674 | 6.7306 | 25.4935 | 46.1896 | 18.4507 | 8.0943 | 34.1875
CELL4 M1 | 400 | 87.4337 | 31.9435 | 15.7447 | 60.9197 | 73.1278 | 28.7844 | 13.7432 | 54.4506
CELL4 M2 | 400 | 87.4337 | 31.9435 | 15.7447 | 60.9197 | 73.1278 | 28.7844 | 13.7432 | 54.4506
CELL4 R1 | 400 | 87.4337 | 31.9435 | 15.7447 | 60.9197 | 73.1278 | 28.7844 | 13.7432 | 54.4506
CELL4 R2 | 400 | 87.4337 | 31.9435 | 15.7447 | 60.9197 | 73.1278 | 28.7844 | 13.7432 | 54.4506
CHIC4 MB1 | 400 | 36.5691 | 13.6937 | 7.0575 | 26.4233 | 30.1567 | 11.8009 | 5.5589 | 22.2479
CHIC4 MB2 | 400 | 36.5691 | 13.6937 | 7.0575 | 26.4233 | 30.1567 | 11.8009 | 5.5589 | 22.2479
CHIC4 R1/2 | 400 | 36.2489 | 13.7362 | 10.4161 | 29.8421 | 28.6356 | 11.2915 | 7.5747 | 23.5432
CHSI2 MC1 | 275 | 86.6804 | 31.2674 | 18.7246 | 62.9434 | 74.8163 | 29.5501 | 12.2866 | 54.0768
CHSI2 MC2 | 275 | 86.6804 | 31.2674 | 18.7246 | 62.9434 | 74.8163 | 29.5501 | 12.2866 | 54.0768
CHSI2 MC3 | 275 | 86.6804 | 31.2674 | 18.7246 | 62.9434 | 74.8163 | 29.5501 | 12.2866 | 54.0768
CHSI2 MC4 | 275 | 86.6804 | 31.2674 | 18.7246 | 62.9434 | 74.8163 | 29.5501 | 12.2866 | 54.0768
CHTE2 MC1 | 275 | 69.4645 | 24.9773 | 16.6482 | 51.9715 | 58.6992 | 23.2703 | 10.8785 | 43.7878
CHTE2 MC2 | 275 | 69.4645 | 24.9773 | 16.6482 | 51.9715 | 58.6992 | 23.2703 | 10.8785 | 43.7878
CHTE2 MC3 | 275 | 69.4645 | 24.9773 | 16.6482 | 51.9715 | 58.6992 | 23.2703 | 10.8785 | 43.7878
CHTE2 MC4 | 275 | 69.4645 | 24.9773 | 16.6482 | 51.9715 | 58.6992 | 23.2703 | 10.8785 | 43.7878
CILF4 M1 | 400 | 79.5044 | 28.5956 | 18.7612 | 59.2015 | 69.7118 | 26.8903 | 13.7265 | 51.7552
CILF4 M2 | 400 | 79.5044 | 28.5956 | 18.7612 | 59.2015 | 69.7118 | 26.8903 | 13.7265 | 51.7552
CILF4 R1 | 400 | 79.5044 | 28.5956 | 18.7612 | 59.2015 | 69.7118 | 26.8903 | 13.7265 | 51.7552
CILF4 R2 | 400 | 79.5044 | 28.5956 | 18.7612 | 59.2015 | 69.7118 | 26.8903 | 13.7265 | 51.7552
CITR4 M5 | 400 | 112.6207 | 37.6785 | 25.9274 | 79.2128 | 125.4859 | 47.4373 | 23.8352 | 90.9217
CITR4 M6 | 400 | 112.6207 | 37.6785 | 25.9274 | 79.2128 | 125.4859 | 47.4373 | 23.8352 | 90.9217
CITR4 MC1 | 400 | 112.6254 | 37.6796 | 25.9291 | 79.2161 | 125.5051 | 47.4401 | 23.8834 | 90.9738
CITR4 MC2 | 400 | 112.6254 | 37.6796 | 25.9291 | 79.2161 | 125.5051 | 47.4401 | 23.8834 | 90.9738
CITR4 MC3 | 400 | 112.6254 | 37.6796 | 25.9291 | 79.2161 | 125.5051 | 47.4401 | 23.8834 | 90.9738
CITR4 MC4 | 400 | 112.6254 | 37.6796 | 25.9291 | 79.2161 | 125.5051 | 47.4401 | 23.8834 | 90.9738
CITR4 R5 | 400 | 112.6207 | 37.6785 | 25.9274 | 79.2128 | 125.4859 | 47.4373 | 23.8352 | 90.9217
CITR4 R6 | 400 | 112.6207 | 37.6785 | 25.9274 | 79.2128 | 125.4859 | 47.4373 | 23.8352 | 90.9217
CLEH4 M1 | 400 | 78.1377 | 28.3466 | 16.6821 | 56.7703 | 68.447 | 26.8277 | 13.5699 | 51.51
CLEH4 R1 | 400 | 78.1377 | 28.3466 | 16.6821 | 56.7703 | 68.447 | 26.8277 | 13.5699 | 51.51
CONQ4 M1 | 400 | 106.4768 | 37.357 | 24.5879 | 77.4187 | 113.3069 | 42.3712 | 28.1383 | 88.0602
CONQ4 M2 | 400 | 106.4768 | 37.357 | 24.5879 | 77.4187 | 113.3069 | 42.3712 | 28.1383 | 88.0602
CONQ4 M3 | 400 | 106.4768 | 37.357 | 24.5879 | 77.4187 | 113.3069 | 42.3712 | 28.1383 | 88.0602
CONQ4 M4 | 400 | 106.4768 | 37.357 | 24.5879 | 77.4187 | 113.3069 | 42.3712 | 28.1383 | 88.0602
CONQ4 R1/3 | 400 | 106.4768 | 37.357 | 24.5879 | 77.4187 | 113.3069 | 42.3712 | 28.1383 | 88.0602
CONQ4 R2/4 | 400 | 106.4768 | 37.357 | 24.5879 | 77.4187 | 113.3069 | 42.3712 | 28.1383 | 88.0602
COSO4 M | 400 | 98.7491 | 34.843 | 21.4052 | 70.6806 | 85.3872 | 32.748 | 18.8407 | 65.1534
COSO4 R | 400 | 98.7491 | 34.843 | 21.4052 | 70.6806 | 85.3872 | 32.748 | 18.8407 | 65.1534
COTT4 M1 | 400 | 101.479 | 36.6639 | 23.4521 | 75.3027 | 80.3654 | 31.112 | 16.2086 | 60.2076
COTT4 M2 | 400 | 101.479 | 36.6639 | 23.4521 | 75.3027 | 80.3654 | 31.112 | 16.2086 | 60.2076
COTT4 M3 | 400 | 95.8575 | 35.3034 | 29.8817 | 79.8083 | 78.518 | 30.4995 | 22.7384 | 65.8713
COTT4 M4 | 400 | 95.8575 | 35.3034 | 29.8817 | 79.8083 | 78.518 | 30.4995 | 22.7384 | 65.8713
COTT4 R1/2 | 400 | 95.8575 | 35.3034 | 29.8817 | 79.8083 | 78.518 | 30.4995 | 22.7384 | 65.8713
COTT4 R3/4 | 400 | 95.8575 | 35.3034 | 29.8817 | 79.8083 | 78.518 | 30.4995 | 22.7384 | 65.8713
COVE2 MC1 | 275 | 60.3445 | 21.8321 | 12.1806 | 43.0559 | 56.7987 | 22.0037 | 11.5161 | 42.634
COVE2 MC2 | 275 | 60.3445 | 21.8321 | 12.1806 | 43.0559 | 56.7987 | 22.0037 | 11.5161 | 42.634
COVE2 MC3 | 275 | 60.3445 | 21.8321 | 12.1806 | 43.0559 | 56.7987 | 22.0037 | 11.5161 | 42.634
COVE2 MC4 | 275 | 60.3445 | 21.8321 | 12.1806 | 43.0559 | 56.7987 | 22.0037 | 11.5161 | 42.634
COWL4 M1 | 400 | 126.8777 | 46.3735 | 38.5673 | 104.1494 | 104.608 | 40.6668 | 29.4613 | 86.9729
COWL4 M2 | 400 | 126.8777 | 46.3735 | 38.5673 | 104.1494 | 104.608 | 40.6668 | 29.4613 | 86.9729
COWL4 R1 | 400 | 126.8777 | 46.3735 | 38.5673 | 104.1494 | 104.608 | 40.6668 | 29.4613 | 86.9729
COWL4 R2 | 400 | 126.8777 | 46.3735 | 38.5673 | 104.1494 | 104.608 | 40.6668 | 29.4613 | 86.9729
CREB2A | 275 | 78.3597 | 26.4191 | 19.6404 | 57.0027 | 71.4876 | 26.1458 | 13.6145 | 50.5902
CREB2B | 275 | 78.3717 | 26.4198 | 19.6492 | 57.0124 | 72.3073 | 26.435 | 13.772 | 51.1568
CREB4 MB1 | 400 | 167.6546 | 51.7373 | 49.7606 | 122.9282 | 107.1584 | 39.8892 | 24.7087 | 81.1206
CREB4 MB2 | 400 | 167.6546 | 51.7373 | 49.7606 | 122.9282 | 107.1584 | 39.8892 | 24.7087 | 81.1206
CREB4 RB1 | 400 | 167.6546 | 51.7373 | 49.7606 | 122.9282 | 107.1584 | 39.8892 | 24.7087 | 81.1206
CREB4 RB2 | 400 | 167.6546 | 51.7373 | 49.7606 | 122.9282 | 107.1584 | 39.8892 | 24.7087 | 81.1206
DAIN4 M1 | 400 | 105.4945 | 37.7974 | 21.1273 | 74.5809 | 91.6347 | 35.4739 | 18.1585 | 68.3262
DAIN4 M2 | 400 | 105.4945 | 37.7974 | 21.1273 | 74.5809 | 91.6347 | 35.4739 | 18.1585 | 68.3262
DAIN4 R1 | 400 | 107.8104 | 38.5301 | 21.7965 | 76.2863 | 92.6612 | 35.8928 | 18.4255 | 69.1855
DAIN4 R2 | 400 | 107.8104 | 38.5301 | 21.7965 | 76.2863 | 92.6612 | 35.8928 | 18.4255 | 69.1855
DIDC4 M1 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 M2 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 M3 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 M4 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 M5 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 M6 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 R1/2 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 R3/4 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 R5 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DIDC4 R6 | 400 | 123.3697 | 43.8898 | 28.4701 | 90.5396 | 110.8993 | 41.9914 | 27.7907 | 87.1754
DINO4 1 | 400 | 69.0695 | 24.0733 | 19.3664 | 53.4113 | 72.9615 | 26.8404 | 21.8162 | 59.7742
DINO4 2 | 400 | 69.0695 | 24.0733 | 19.3664 | 53.4113 | 72.9615 | 26.8404 | 21.8162 | 59.7742
DINO4 3 | 400 | 69.0695 | 24.0733 | 19.3664 | 53.4113 | 72.9615 | 26.8404 | 21.8162 | 59.7742
DRAK1 M1 | 132 | 30.5999 | 10.9363 | 12.3511 | 27.8174 | 37.6867 | 13.9051 | 15.3201 | 34.9849
DRAK1 M2 | 132 | 30.5999 | 10.9363 | 12.3511 | 27.8174 | 37.6867 | 13.9051 | 15.3201 | 34.9849
DRAK1 R1 | 132 | 30.5999 | 10.9363 | 12.3511 | 27.8174 | 37.6867 | 13.9051 | 15.3201 | 34.9849
DRAK1 R2 | 132 | 30.5999 | 10.9363 | 12.3511 | 27.8174 | 37.6867 | 13.9051 | 15.3201 | 34.9849
DRAK4 M1 | 400 | 116.9851 | 41.5308 | 22.3614 | 81.0948 | 110.6405 | 42.6875 | 21.5746 | 81.944
DRAK4 M2 | 400 | 116.9851 | 41.5308 | 22.3614 | 81.0948 | 110.6405 | 42.6875 | 21.5746 | 81.944
DRAK4 M3 | 400 | 116.9851 | 41.5308 | 22.3614 | 81.0948 | 110.6405 | 42.6875 | 21.5746 | 81.944
DRAK4 R1/3 | 400 | 116.9851 | 41.5308 | 22.3614 | 81.0948 | 110.6405 | 42.6875 | 21.5746 | 81.944
DRAK4 R2 | 400 | 116.9851 | 41.5308 | 22.3614 | 81.0948 | 110.6405 | 42.6875 | 21.5746 | 81.944
DRAX1 M1 | 132 | 39.2518 | 11.8641 | 11.7406 | 28.519 | 49.0421 | 16.661 | 14.7923 | 38.3544
DRAX1 M2 | 132 | 39.2518 | 11.8641 | 11.7406 | 28.519 | 49.0421 | 16.661 | 14.7923 | 38.3544
DRAX1 R1 | 132 | 39.2518 | 11.8641 | 11.7406 | 28.519 | 49.0421 | 16.661 | 14.7923 | 38.3544
DRAX1 R2 | 132 | 39.2518 | 11.8641 | 11.7406 | 28.519 | 49.0421 | 16.661 | 14.7923 | 38.3544
DRAX4 M1 | 400 | 133.9371 | 45.7756 | 38.4719 | 103.2084 | 135.4074 | 49.5437 | 39.324 | 109.3894
DRAX4 M2 | 400 | 133.9371 | 45.7756 | 38.4719 | 103.2084 | 135.4074 | 49.5437 | 39.324 | 109.3894
DRAX4 M3 | 400 | 133.9371 | 45.7756 | 38.4719 | 103.2084 | 135.4074 | 49.5437 | 39.324 | 109.3894
DRAX4 M4 | 400 | 118.1781 | 40.7335 | 34.7177 | 92.3236 | 120.5065 | 44.367 | 34.3951 | 97.1395
DRAX4 M5 | 400 | 118.1781 | 40.7335 | 34.7177 | 92.3236 | 120.5065 | 44.367 | 34.3951 | 97.1395
DRAX4 M6 | 400 | 118.1781 | 40.7335 | 34.7177 | 92.3236 | 120.5065 | 44.367 | 34.3951 | 97.1395
DRAX4 R1/2/3 | 400 | 133.9371 | 45.7756 | 38.4719 | 103.2084 | 135.4074 | 49.5437 | 39.324 | 109.3894
DRAX4 R4/5/6 | 400 | 118.1781 | 40.7335 | 34.7177 | 92.3236 | 120.5065 | 44.367 | 34.3951 | 97.1395
DUNG2 M1 | 275 | 45.6583 | 16.2832 | 15.3034 | 38.3314 | 46.3929 | 17.0783 | 15.2769 | 39.4293
DUNG2 M2 | 275 | 45.6583 | 16.2832 | 15.3034 | 38.3314 | 46.3929 | 17.0783 | 15.2769 | 39.4293
DUNG2 R1 | 275 | 45.6583 | 16.2832 | 15.3034 | 38.3314 | 46.3929 | 17.0783 | 15.2769 | 39.4293
DUNG2 R2 | 275 | 45.6583 | 16.2832 | 15.3034 | 38.3314 | 46.3929 | 17.0783 | 15.2769 | 39.4293
DUNG4 M1 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
DUNG4 M2 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
DUNG4 M3 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
DUNG4 M4 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
DUNG4 M5 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
DUNG4 R1/2 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
DUNG4 R4/5 | 400 | 80.1455 | 28.3811 | 12.9786 | 53.1156 | 73.0183 | 27.5165 | 13.6949 | 52.609
EALI2 MC1 | 275 | 59.3897 | 20.8205 | 13.3608 | 42.8055 | 65.32 | 25.3352 | 8.315 | 44.1444
EALI2 MC2 | 275 | 59.3897 | 20.8205 | 13.3608 | 42.8055 | 65.32 | 25.3352 | 8.315 | 44.1444
EALI2 MC3 | 275 | 59.3897 | 20.8205 | 13.3608 | 42.8055 | 65.32 | 25.3352 | 8.315 | 44.1444
EALI2 MC4 | 275 | 59.3897 | 20.8205 | 13.3608 | 42.8055 | 65.32 | 25.3352 | 8.315 | 44.1444
EASO4 M1 | 400 | 74.5112 | 27.1798 | 15.6256 | 54.0636 | 67.9369 | 25.8328 | 17.0567 | 53.5898
EASO4 M2 | 400 | 74.5112 | 27.1798 | 15.6256 | 54.0636 | 67.9369 | 25.8328 | 17.0567 | 53.5898
EASO4 R1 | 400 | 74.5112 | 27.1798 | 15.6256 | 54.0636 | 67.9369 | 25.8328 | 17.0567 | 53.5898
EASO4 R2 | 400 | 74.5112 | 27.1798 | 15.6256 | 54.0636 | 67.9369 | 25.8328 | 17.0567 | 53.5898
EASO4A | 400 | 74.5112 | 27.1798 | 15.6256 | 54.0636 | 67.9369 | 25.8328 | 17.0567 | 53.5898
EASO4B | 400 | 74.5112 | 27.1798 | 15.6256 | 54.0636 | 67.9369 | 25.8328 | 17.0567 | 53.5898
ECLA1 M1 | 132 | 45.0976 | 16.8766 | 12.9394 | 36.8066 | 47.6613 | 18.5943 | 14.1717 | 40.4679
ECLA1 M2 | 132 | 45.0976 | 16.8766 | 12.9394 | 36.8066 | 47.6613 | 18.5943 | 14.1717 | 40.4679
ECLA1 R1 | 132 | 45.4532 | 16.9397 | 13.0468 | 37.0032 | 54.4803 | 21.026 | 15.8414 | 45.5767
ECLA1 R2 | 132 | 45.4532 | 16.9397 | 13.0468 | 37.0032 | 54.4803 | 21.026 | 15.8414 | 45.5767
ECLA4 M1 | 400 | 108.8266 | 39.3041 | 22.3886 | 77.973 | 88.2042 | 34.5162 | 16.7037 | 65.5169
ECLA4 M2 | 400 | 108.8266 | 39.3041 | 22.3886 | 77.973 | 88.2042 | 34.5162 | 16.7037 | 65.5169
ECLA4 R1 | 400 | 108.8266 | 39.3041 | 22.3886 | 77.973 | 88.2042 | 34.5162 | 16.7037 | 65.5169
ECLA4 R2 | 400 | 108.8266 | 39.3041 | 22.3886 | 77.973 | 88.2042 | 34.5162 | 16.7037 | 65.5169
EGGB4 M1 | 400 | 105.5823 | 37.2644 | 26.6 | 79.2998 | 95.0415 | 36.0428 | 20.6173 | 71.5896
EGGB4 M2 | 400 | 105.5823 | 37.2644 | 26.6 | 79.2998 | 95.0415 | 36.0428 | 20.6173 | 71.5896
EGGB4 R1 | 400 | 95.0837 | 33.5348 | 25.4317 | 72.857 | 85.9401 | 32.5783 | 19.048 | 65.1206
EGGB4 R2 | 400 | 95.0837 | 33.5348 | 25.4317 | 72.857 | 85.9401 | 32.5783 | 19.048 | 65.1206
ELLA2 MC1 | 275 | 63.526 | 22.8356 | 8.2598 | 40.5542 | 64.1255 | 24.668 | 7.8982 | 42.784
ELLA2 MC2 | 275 | 63.526 | 22.8356 | 8.2598 | 40.5542 | 64.1255 | 24.668 | 7.8982 | 42.784
ELLA2 MC3 | 275 | 63.526 | 22.8356 | 8.2598 | 40.5542 | 64.1255 | 24.668 | 7.8982 | 42.784
ELLA2 MC4 | 275 | 63.526 | 22.8356 | 8.2598 | 40.5542 | 64.1255 | 24.668 | 7.8982 | 42.784
ELST1 M1 | 132 | 31.6688 | 11.4855 | 10.0365 | 26.2795 | 38.8596 | 14.537 | 12.0977 | 32.6561
ELST1 M2 | 132 | 45.4876 | 16.1066 | 13.4965 | 36.2747 | 56.6236 | 21.4944 | 15.8629 | 46.2605
ELST1 M3 | 132 | 38.4469 | 14.1266 | 9.636 | 29.6139 | 44.6408 | 17.0243 | 11.462 | 35.538
ELST1 R1 | 132 | 31.6688 | 11.4855 | 10.0365 | 26.2795 | 38.8596 | 14.537 | 12.0977 | 32.6561
ELST1 R2 | 132 | 45.4876 | 16.1066 | 13.4965 | 36.2747 | 56.6236 | 21.4944 | 15.8629 | 46.2605
ELST1 R3 | 132 | 38.4469 | 14.1266 | 9.636 | 29.6139 | 44.6408 | 17.0243 | 11.462 | 35.538
ELST2 M1 | 275 | 64.543 | 23.2835 | 16.4403 | 49.3681 | 70.5781 | 26.5834 | 18.2924 | 55.887
ELST2 M2 | 275 | 66.5724 | 24.1441 | 14.6237 | 48.7686 | 72.945 | 28.0263 | 15.4381 | 55.0733
ELST2 R1 | 275 | 64.543 | 23.2835 | 16.4403 | 49.3681 | 70.5781 | 26.5834 | 18.2924 | 55.887
ELST2 R2 | 275 | 66.5724 | 24.1441 | 14.6237 | 48.7686 | 72.945 | 28.0263 | 15.4381 | 55.0733
ELST4 M1 | 400 | 91.5149 | 32.7283 | 28.047 | 74.3318 | 108.8044 | 41.1213 | 32.5728 | 90.727
ELST4 R1 | 400 | 91.5149 | 32.7283 | 28.047 | 74.3318 | 108.8044 | 41.1213 | 32.5728 | 90.727
ELST4A | 400 | 55.7476 | 20.3266 | 7.1438 | 35.89 | 53.2424 | 20.2033 | 8.1631 | 36.7349
ENDE4 MC1 | 400 | 82.9937 | 30.6094 | 14.7292 | 58.0174 | 56.1841 | 22.4061 | 9.5875 | 41.2745
ENDE4 MC2 | 400 | 82.9937 | 30.6094 | 14.7292 | 58.0174 | 56.1841 | 22.4061 | 9.5875 | 41.2745
ENDE4 MC3 | 400 | 82.9937 | 30.6094 | 14.7292 | 58.0174 | 56.1841 | 22.4061 | 9.5875 | 41.2745
ENDE4 MC4 | 400 | 82.9937 | 30.6094 | 14.7292 | 58.0174 | 56.1841 | 22.4061 | 9.5875 | 41.2745
EXET4 M1 | 400 | 56.6525 | 20.9444 | 10.2624 | 39.8823 | 62.5627 | 23.9766 | 13.3157 | 47.2237
EXET4 M2 | 400 | 56.6525 | 20.9444 | 10.2624 | 39.8823 | 62.5627 | 23.9766 | 13.3157 | 47.2237
EXET4 R1 | 400 | 56.6525 | 20.9444 | 10.2624 | 39.8823 | 62.5627 | 23.9766 | 13.3157 | 47.2237
EXET4 R2 | 400 | 56.6525 | 20.9444 | 10.2624 | 39.8823 | 62.5627 | 23.9766 | 13.3157 | 47.2237
FAWL1 M1 | 132 | 50.3048 | 17.6888 | 18.2273 | 43.2431 | 63.7778 | 24.0249 | 21.4865 | 55.4628
FAWL1 M2 | 132 | 50.3048 | 17.6888 | 18.2273 | 43.2431 | 63.7778 | 24.0249 | 21.4865 | 55.4628
FAWL1 R1 | 132 | 50.3048 | 17.6888 | 18.2273 | 43.2431 | 63.7778 | 24.0249 | 21.4865 | 55.4628
FAWL1 R2 | 132 | 50.3048 | 17.6888 | 18.2273 | 43.2431 | 63.7778 | 24.0249 | 21.4865 | 55.4628
FAWL4 M1/3 | 400 | 81.5704 | 28.9498 | 10.3696 | 51.3108 | 66.6195 | 25.7647 | 8.1991 | 44.6359
FAWL4 M1/3(1) | 400 | 81.5704 | 28.9498 | 10.3696 | 51.3108 | 66.6195 | 25.7647 | 8.1991 | 44.6359
FAWL4 M2/4(2) | 400 | 81.5704 | 28.9498 | 10.3696 | 51.3108 | 66.6195 | 25.7647 | 8.1991 | 44.6359
FAWL4 M2/4(3) | 400 | 81.5704 | 28.9498 | 10.3696 | 51.3108 | 66.6195 | 25.7647 | 8.1991 | 44.6359
FAWL4 R1/3 | 400 | 81.5704 | 28.9498 | 10.3696 | 51.3108 | 66.6195 | 25.7647 | 8.1991 | 44.6359
FAWL4 R2/4 | 400 | 81.5704 | 28.9498 | 10.3696 | 51.3108 | 66.6195 | 25.7647 | 8.1991 | 44.6359
FECK2 M1 | 275 | 61.2284 | 22.4175 | 13.8538 | 45.5569 | 60.6036 | 23.3118 | 13.7169 | 46.6848
FECK2 M2 | 275 | 61.2284 | 22.4175 | 13.8538 | 45.5569 | 60.6036 | 23.3118 | 13.7169 | 46.6848
FECK2 R | 275 | 61.2284 | 22.4175 | 13.8538 | 45.5569 | 60.6036 | 23.3118 | 13.7169 | 46.6848
FECK4 M1 | 400 | 76.3794 | 28.4539 | 12.9059 | 53.1458 | 64.8848 | 25.5735 | 12.3361 | 48.5026
FECK4 M2 | 400 | 76.3794 | 28.4539 | 12.9059 | 53.1458 | 64.8848 | 25.5735 | 12.3361 | 48.5026
FECK4 R1 | 400 | 76.3794 | 28.4539 | 12.9059 | 53.1458 | 64.8848 | 25.5735 | 12.3361 | 48.5026
FECK4 R2 | 400 | 76.3794 | 28.4539 | 12.9059 | 53.1458 | 64.8848 | 25.5735 | 12.3361 | 48.5026
FENW4A | 400 | 116.9367 | 40.1192 | 16.1693 | 72.9063 | 98.4585 | 37.4321 | 7.9603 | 60.8973
FERR2 M1 | 275 | 57.3718 | 20.6372 | 11.4423 | 40.6277 | 58.433 | 22.0472 | 11.4168 | 42.5963
FERR2 M2 | 275 | 57.2729 | 20.5388 | 15.3078 | 44.3541 | 60.9172 | 22.794 | 14.1662 | 46.4018
FERR2 R1 | 275 | 61.9339 | 22.1936 | 12.1061 | 43.4926 | 61.7149 | 23.4622 | 10.2097 | 43.3903
FERR2 R2 | 275 | 61.9339 | 22.1936 | 12.1061 | 43.4926 | 61.7149 | 23.4622 | 10.2097 | 43.3903
FERR2A | 275 | 57.2942 | 20.4438 | 12.8271 | 41.739 | 60.7352 | 22.687 | 11.6095 | 43.6938
FERR2B | 275 | 56.8436 | 20.3026 | 9.3061 | 38.0184 | 57.6522 | 21.7569 | 8.9102 | 39.6791
FERR4A | 400 | 75.8795 | 26.793 | 9.7721 | 47.6631 | 65.5816 | 24.8541 | 8.0909 | 43.24
FFES2 Term205 | 275 | 34.5941 | 12.9022 | 2.6053 | 20.8517 | 33.7185 | 13.2205 | 2.2936 | 20.9902
FFES2 Term210 | 275 | 34.5452 | 12.9034 | 2.5881 | 20.8363 | 34.1897 | 13.4024 | 2.3175 | 21.2714
FIDF2 M1 | 275 | 49.331 | 17.6315 | 14.6798 | 39.6144 | 49.8457 | 18.591 | 13.5493 | 39.8409
FIDF2 M2 | 275 | 48.5195 | 17.3046 | 14.5209 | 38.9933 | 48.0351 | 17.9094 | 12.8746 | 38.2023
FIDF2 M3 | 275 | 59.9889 | 21.3617 | 14.9758 | 45.1857 | 56.9488 | 21.5444 | 12.9895 | 43.4579
FIDF2 M4 | 275 | 60.5455 | 21.5564 | 15.1064 | 45.5917 | 58.8294 | 22.2248 | 13.5972 | 45.0278
FIDF2 R1 | 275 | 49.331 | 17.6315 | 14.6798 | 39.6144 | 49.8457 | 18.591 | 13.5493 | 39.8409
FIDF2 R2 | 275 | 60.5455 | 21.5564 | 15.1064 | 45.5917 | 58.8294 | 22.2248 | 13.5972 | 45.0278
FLEE4 MC1 | 400 | 105.3773 | 37.8421 | 21.1945 | 74.7113 | 83.9117 | 32.9691 | 15.6638 | 62.2891
FLEE4 MC2 | 400 | 105.3773 | 37.8421 | 21.1945 | 74.7113 | 83.9117 | 32.9691 | 15.6638 | 62.2891
FLEE4 MC3 | 400 | 105.3773 | 37.8421 | 21.1945 | 74.7113 | 83.9117 | 32.9691 | 15.6638 | 62.2891
FLEE4 MC4 | 400 | 105.3773 | 37.8421 | 21.1945 | 74.7113 | 83.9117 | 32.9691 | 15.6638 | 62.2891
FLIB4 M1 | 400 | 99.6865 | 35.1176 | 23.2126 | 72.8764 | 106.5111 | 40.1833 | 24.5231 | 81.3509
FLIB4 M2 | 400 | 99.6865 | 35.1176 | 23.2126 | 72.8764 | 106.5111 | 40.1833 | 24.5231 | 81.3509
FOUR2 MC1 | 275 | 38.3605 | 14.9494 | 4.8719 | 26.0135 | 31.3557 | 12.8562 | 3.8363 | 22.0177
FOUR2 MC2 | 275 | 38.3605 | 14.9494 | 4.8719 | 26.0135 | 31.3557 | 12.8562 | 3.8363 | 22.0177
FROD2 MC1 | 275 | 49.2115 | 17.5514 | 15.3616 | 40.1831 | 52.6829 | 19.3789 | 16.6467 | 44.0527
FROD2 MC3 | 275 | 49.1359 | 17.2549 | 9.8099 | 34.2121 | 52.0085 | 19.0718 | 9.969 | 36.9406
FROD4 M1 | 400 | 80.3209 | 29.0159 | 25.8937 | 66.9284 | 77.5824 | 29.2756 | 25.1684 | 66.5704
FROD4 R1 | 400 | 80.3209 | 29.0159 | 25.8937 | 66.9284 | 77.5824 | 29.2756 | 25.1684 | 66.5704
GART4A | 400 | 108.9436 | 36.5864 | 15.4224 | 67.1633 | 83.5636 | 31.5703 | 7.4325 | 52.0797
GART4B | 400 | 112.8212 | 37.9145 | 16.3634 | 69.9827 | 92.055 | 34.6933 | 8.8621 | 57.9258
GRAI4 M1 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 M2 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 M3 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 M4 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 M5 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 M6 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 M7 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 R1/2 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 R3 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 R4 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 R5 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 R6 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GRAI4 R7 | 400 | 138.0065 | 48.2929 | 42.9564 | 111.2529 | 125.3495 | 47.1975 | 39.5918 | 106.3392
GREN1 M1 | 132 | 40.5998 | 14.8603 | 10.5798 | 31.5955 | 44.4362 | 17.7042 | 10.4314 | 35.469
GREN1 M2 | 132 | 39.5134 | 14.577 | 11.1486 | 31.7636 | 40.0741 | 15.7478 | 10.208 | 32.4787
GREN1 R1 | 132 | 40.5998 | 14.8603 | 10.5798 | 31.5955 | 44.4362 | 17.7042 | 10.4314 | 35.469
GREN1 R2 | 132 | 39.5134 | 14.577 | 11.1486 | 31.7636 | 40.0741 | 15.7478 | 10.208 | 32.4787
GREN4 M1 | 400 | 77.2555 | 28.754 | 12.579 | 53.2433 | 51.0983 | 20.6951 | 8.4837 | 37.751
GREN4 M2 | 400 | 77.2555 | 28.754 | 12.579 | 53.2433 | 51.0983 | 20.6951 | 8.4837 | 37.751
GREN4 R1 | 400 | 77.2555 | 28.754 | 12.579 | 53.2433 | 51.0983 | 20.6951 | 8.4837 | 37.751
GREN4 R2 | 400 | 77.2555 | 28.754 | 12.579 | 53.2433 | 51.0983 | 20.6951 | 8.4837 | 37.751
GRIW4 MC1 | 400 | 65.3871 | 23.4277 | 16.5684 | 49.7001 | 56.4042 | 21.6661 | 11.2799 | 41.9204
GRIW4 MC2 | 400 | 65.3871 | 23.4277 | 16.5684 | 49.7001 | 56.4042 | 21.6661 | 11.2799 | 41.9204
GRSA2 M1 | 275 | 62.047 | 20.9786 | 20.3569 | 50.0251 | 59.3356 | 21.7008 | 16.768 | 47.4575
GRSA2 M2 | 275 | 62.047 | 20.9786 | 20.3569 | 50.0251 | 59.3356 | 21.7008 | 16.768 | 47.4575
GRSA2 R1 | 275 | 62.047 | 20.9786 | 20.3569 | 50.0251 | 59.3356 | 21.7008 | 16.768 | 47.4575
GRSA2 R2 | 275 | 62.047 | 20.9786 | 20.3569 | 50.0251 | 59.3356 | 21.7008 | 16.768 | 47.4575
GRSB2 M3 | 275 | 62.4847 | 21.1018 | 20.6349 | 50.4774 | 60.3514 | 22.0019 | 17.5597 | 48.675
GRSB2 M4 | 275 | 62.4847 | 21.1018 | 20.6349 | 50.4774 | 60.3514 | 22.0019 | 17.5597 | 48.675
GRSB2 R3 | 275 | 62.4847 | 21.1018 | 20.6349 | 50.4774 | 60.3514 | 22.0019 | 17.5597 | 48.675
GRSB2 R4 | 275 | 62.4847 | 21.1018 | 20.6349 | 50.4774 | 60.3514 | 22.0019 | 17.5597 | 48.675
HACK2A | 275 | 67.1454 | 23.512 | 11.4631 | 44.714 | 69.1546 | 25.7287 | 11.8078 | 48.1937
HACK2B | 275 | 65.9677 | 23.1227 | 11.4399 | 44.1404 | 68.4943 | 25.4736 | 11.7405 | 47.7656
HACK4 M1 | 400 | 119.4233 | 39.8955 | 27.4671 | 83.8878 | 136.3592 | 50.5046 | 28.6657 | 100.09
HACK4 M2 | 400 | 119.4233 | 39.8955 | 27.4671 | 83.8878 | 136.3592 | 50.5046 | 28.6657 | 100.09
HACK4 R1 | 400 | 119.4233 | 39.8955 | 27.4671 | 83.8878 | 136.3592 | 50.5046 | 28.6657 | 100.09
HACK4 R2 | 400 | 119.4233 | 39.8955 | 27.4671 | 83.8878 | 136.3592 | 50.5046 | 28.6657 | 100.09
HAMB4A | 400 | 60.1446 | 21.3984 | 6.4833 | 36.7452 | 51.342 | 19.9931 | 3.4825 | 31.7571
HAMB4A_HEYS | 400 | 60.1446 | 21.3984 | 6.4833 | 36.7452 | 51.342 | 19.9931 | 3.4825 | 31.7571
HAMB4A_PEWO | 400 | 60.1446 | 21.3984 | 6.4833 | 36.7452 | 51.342 | 19.9931 | 3.4825 | 31.7571
HAMB4B | 400 | 60.9877 | 21.6338 | 6.662 | 37.2569 | 52.2518 | 20.3033 | 3.7755 | 32.4887
HAMB4B_HEYS | 400 | 60.9877 | 21.6338 | 6.662 | 37.2569 | 52.2518 | 20.3033 | 3.7755 | 32.4887
HAMB4B_PEWO | 400 | 60.9877 | 21.6338 | 6.662 | 37.2569 | 52.2518 | 20.3033 | 3.7755 | 32.4887
HAMH1B | 132 | 45.0009 | 15.4818 | 9.481 | 31.3756 | 53.7546 | 20.2239 | 6.3538 | 34.9548
HAMH1C | 132 | 44.0843 | 15.2701 | 8.3305 | 29.9257 | 52.1074 | 19.3445 | 7.8429 | 35.2002
HAMH4 M1 | 400 | 73.3743 | 27.0501 | 12.9583 | 51.2129 | 69.3668 | 26.9883 | 13.2805 | 51.4477
HAMH4 M2 | 400 | 73.3743 | 27.0501 | 12.9583 | 51.2129 | 69.3668 | 26.9883 | 13.2805 | 51.4477
HAMH4 R1 | 400 | 73.3743 | 27.0501 | 12.9583 | 51.2129 | 69.3668 | 26.9883 | 13.2805 | 51.4477
HAMH4 R2 | 400 | 73.3743 | 27.0501 | 12.9583 | 51.2129 | 69.3668 | 26.9883 | 13.2805 | 51.4477
HARK1 M1 | 132 | 27.2561 | 10.1891 | 6.9093 | 21.3188 | 32.2777 | 12.564 | 7.545 | 25.3132
HARK1 M2 | 132 | 27.2561 | 10.1891 | 6.9093 | 21.3188 | 32.2777 | 12.564 | 7.545 | 25.3132
HARK1 R1 | 132 | 26.7238 | 10.8733 | 6.4594 | 21.8366 | 29.4515 | 12.2585 | 7.3766 | 24.7127
HARK1 R2 | 132 | 29.6889 | 11.2954 | 7.6349 | 23.609 | 34.769 | 13.7638 | 8.824 | 28.2889
HARK1 R3 | 132 | 29.6889 | 11.2954 | 7.6349 | 23.609 | 34.769 | 13.7638 | 8.824 | 28.2889
HARK2 MC1 | 275 | 40.3639 | 15.0244 | 10.4005 | 31.6482 | 42.4571 | 16.2173 | 10.9775 | 33.9122
HARK2 MC11 | 275 | 38.0196 | 14.4082 | 11.6755 | 32.0519 | 39.7018 | 15.2607 | 12.7318 | 34.3137
HARK2 MC12 | 275 | 38.0196 | 14.4082 | 11.6755 | 32.0519 | 39.7018 | 15.2607 | 12.7318 | 34.3137
HARK2 MC13 | 275 | 38.0196 | 14.4082 | 11.6755 | 32.0519 | 39.7018 | 15.2607 | 12.7318 | 34.3137
HARK2 MC2 | 275 | 40.3639 | 15.0244 | 10.4005 | 31.6482 | 42.4571 | 16.2173 | 10.9775 | 33.9122
HARK2 MC3 | 275 | 40.3639 | 15.0244 | 10.4005 | 31.6482 | 42.4571 | 16.2173 | 10.9775 | 33.9122
HARK2 MC4 | 275 | 40.3639 | 15.0244 | 10.4005 | 31.6482 | 42.4571 | 16.2173 | 10.9775 | 33.9122
HARK2 MC6 | 275 | 40.3639 | 15.0244 | 10.4005 | 31.6482 | 42.4571 | 16.2173 | 10.9775 | 33.9122
HARK2 MC8 | 275 | 38.0196 | 14.4082 | 11.6755 | 32.0519 | 39.7018 | 15.2607 | 12.7318 | 34.3137
HARK2 MC9 | 275 | 38.0196 | 14.4082 | 11.6755 | 32.0519 | 39.7018 | 15.2607 | 12.7318 | 34.3137
HARK4 M1 | 400 | 66.5509 | 24.5544 | 11.4641 | 46.1893 | 51.1932 | 19.9689 | 10.5268 | 38.767
HARK4 M2 | 400 | 66.5509 | 24.5544 | 11.4641 | 46.1893 | 51.1932 | 19.9689 | 10.5268 | 38.767
HARK4 R1 | 400 | 66.5509 | 24.5544 | 11.4641 | 46.1893 | 51.1932 | 19.9689 | 10.5268 | 38.767
HARK4 R2 | 400 | 66.5509 | 24.5544 | 11.4641 | 46.1893 | 51.1932 | 19.9689 | 10.5268 | 38.767
HARM2 MC1 | 275 | 59.743 | 21.2185 | 12.2281 | 42.2355 | 53.0862 | 20.6109 | 8.5671 | 37.7153
HARM2 MC2 | 275 | 59.743 | 21.2185 | 12.2281 | 42.2355 | 53.0862 | 20.6109 | 8.5671 | 37.7153
HARM2 MC3 | 275 | 59.743 | 21.2185 | 12.2281 | 42.2355 | 53.0862 | 20.6109 | 8.5671 | 37.7153
HARM2 MC4 | 275 | 59.743 | 21.2185 | 12.2281 | 42.2355 | 53.0862 | 20.6109 | 8.5671 | 37.7153
HATL2 M1 | 275 | 74.2276 | 25.702 | 16.4315 | 52.7797 | 77.753 | 28.9075 | 18.4186 | 59.3
HATL2 M2 | 275 | 74.2276 | 25.702 | 16.4315 | 52.7797 | 77.753 | 28.9075 | 18.4186 | 59.3
HATL2 R1 | 275 | 74.2276 | 25.702 | 16.4315 | 52.7797 | 77.753 | 28.9075 | 18.4186 | 59.3
HATL2 R2 | 275 | 74.2276 | 25.702 | 16.4315 | 52.7797 | 77.753 | 28.9075 | 18.4186 | 59.3
HAWP2 MC1 | 275 | 81.2855 | 28.0662 | 19.1414 | 58.8331 | 75.1749 | 28.6907 | 14.1152 | 54.69
HAWP2 MC2 | 275 | 81.2855 | 28.0662 | 19.1414 | 58.8331 | 75.1749 | 28.6907 | 14.1152 | 54.69
HAWP2 MC3 | 275 | 81.2855 | 28.0662 | 19.1414 | 58.8331 | 75.1749 | 28.6907 | 14.1152 | 54.69
HAWP2 MC4 | 275 | 81.2855 | 28.0662 | 19.1414 | 58.8331 | 75.1749 | 28.6907 | 14.1152 | 54.69
HEDO2 M1 | 275 | 77.5149 | 26.7801 | 23.2822 | 61.155 | 77.9003 | 28.5685 | 23.5519 | 63.9538
HEDO2 M2 | 275 | 77.5149 | 26.7801 | 23.2822 | 61.155 | 77.9003 | 28.5685 | 23.5519 | 63.9538
HEDO2 R1 | 275 | 77.5149 | 26.7801 | 23.2822 | 61.155 | 77.9003 | 28.5685 | 23.5519 | 63.9538
HEDO2 R2 | 275 | 77.5149 | 26.7801 | 23.2822 | 61.155 | 77.9003 | 28.5685 | 23.5519 | 63.9538
HEYS1 M1 | 132 | 36.0482 | 12.1294 | 11.4375 | 28.5911 | 41.5089 | 15.1426 | 12.9885 | 34.4033
HEYS1 M2 | 132 | 36.0482 | 12.1294 | 11.4375 | 28.5911 | 41.5089 | 15.1426 | 12.9885 | 34.4033
HEYS1 R1 | 132 | 36.0482 | 12.1294 | 11.4375 | 28.5911 | 41.5089 | 15.1426 | 12.9885 | 34.4033
HEYS1 R2 | 132 | 36.0482 | 12.1294 | 11.4375 | 28.5911 | 41.5089 | 15.1426 | 12.9885 | 34.4033
HEYS4 M1 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 M2 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 M3 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 M4 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 M5 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 R1/2 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 R3/4 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HEYS4 R5 | 400 | 78.8641 | 28.6792 | 24.6055 | 65.164 | 84.9454 | 32.2632 | 27.4019 | 73.029
HIBU4 M1 | 400 | 116.9947 | 39.039 | 27.1409 | 82.3504 | 135.2928 | 49.864 | 29.4373 | 99.9556
HIBU4 M2 | 400 | 116.9947 | 39.039 | 27.1409 | 82.3504 | 135.2928 | 49.864 | 29.4373 | 99.9556
HIBU4 R1 | 400 | 116.9947 | 39.039 | 27.1409 | 82.3504 | 135.2928 | 49.864 | 29.4373 | 99.9556
HIBU4 R2 | 400 | 116.9947 | 39.039 | 27.1409 | 82.3504 | 135.2928 | 49.864 | 29.4373 | 99.9556
HIGM2 M1 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM2 M2 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM2 M3 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM2 R1 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM2 R4 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM2 R5 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM2 R6 | 275 | 61.675 | 22.7901 | 16.4805 | 48.7105 | 56.5712 | 22.2979 | 12.0997 | 43.6337
HIGM4 MC1 | 400 | 80.6217 | 29.3751 | 18.2697 | 59.8124 | 65.1118 | 25.4427 | 11.349 | 47.3304
HIGM4 MC2 | 400 | 80.6217 | 29.3751 | 18.2697 | 59.8124 | 65.1118 | 25.4427 | 11.349 | 47.3304
HIGM4A | 400 | 63.7439 | 23.0364 | 9.1838 | 41.7621 | 53.4545 | 20.5961 | 4.9136 | 34.0409
HINP2 M1 | 275 | 22.1377 | 7.9767 | 6.7696 | 18.0503 | 22.72 | 8.5138 | 6.0666 | 18.107
HINP2 M2 | 275 | 22.4646 | 8.1039 | 6.7933 | 18.2539 | 24.8371 | 9.3674 | 6.1627 | 19.4102
HINP4 M1 | 400 | 54.9591 | 20.6266 | 8.9279 | 38.0983 | 41.4984 | 16.8182 | 5.7683 | 29.5528
HINP4 M2 | 400 | 54.9591 | 20.6266 | 8.9279 | 38.0983 | 41.4984 | 16.8182 | 5.7683 | 29.5528
HINP4 M3 | 400 | 54.9591 | 20.6266 | 8.9279 | 38.0983 | 41.4984 | 16.8182 | 5.7683 | 29.5528
HINP4 M4 | 400 | 54.9591 | 20.6266 | 8.9279 | 38.0983 | 41.4984 | 16.8182 | 5.7683 | 29.5528
HINP4 R1/2 | 400 | 54.9591 | 20.6266 | 8.9279 | 38.0983 | 41.4984 | 16.8182 | 5.7683 | 29.5528
HINP4 R3/4 | 400 | 54.9591 | 20.6266 | 8.9279 | 38.0983 | 41.4984 | 16.8182 | 5.7683 | 29.5528
HUMR4 M1 | 400 | 107.5764 | 36.6529 | 30.9469 | 82.7819 | 98.1232 | 36.2179 | 27.2009 | 78.4207
HUMR4 M2 | 400 | 107.5764 | 36.6529 | 30.9469 | 82.7819 | 98.1232 | 36.2179 | 27.2009 | 78.4207
HUMR4 R1 | 400 | 107.5764 | 36.6529 | 30.9469 | 82.7819 | 98.1232 | 36.2179 | 27.2009 | 78.4207
HUMR4 R2 | 400 | 107.5764 | 36.6529 | 30.9469 | 82.7819 | 98.1232 | 36.2179 | 27.2009 | 78.4207
HURS2 MC1 | 275 | 73.7268 | 25.9594 | 19.804 | 56.5161 | 76.5972 | 30.4483 | 16.5791 | 59.6394
HURS2 MC2 | 275 | 73.7268 | 25.9594 | 19.804 | 56.5161 | 76.5972 | 30.4483 | 16.5791 | 59.6394
HURS2 MC3 | 275 | 73.7268 | 25.9594 | 19.804 | 56.5161 | 76.5972 | 30.4483 | 16.5791 | 59.6394
HURS2 MC4 | 275 | 73.7268 | 25.9594 | 19.804 | 56.5161 | 76.5972 | 30.4483 | 16.5791 | 59.6394
HUTT4 MC1 | 400 | 64.5739 | 24.16 | 18.211 | 52.3783 | 44.2563 | 17.8942 | 10.2644 | 35.5707
HUTT4 MC2 | 400 | 64.5739 | 24.16 | 18.211 | 52.3783 | 44.2563 | 17.8942 | 10.2644 | 35.5707
HUTT4 MC3 | 400 | 64.5739 | 24.16 | 18.211 | 52.3783 | 44.2563 | 17.8942 | 10.2644 | 35.5707
HUTT4 MC4 | 400 | 64.5739 | 24.16 | 18.211 | 52.3783 | 44.2563 | 17.8942 | 10.2644 | 35.5707
IMPP4 MC1 | 400 | 54.0909 | 20.003 | 11.878 | 40.1666 | 46.2576 | 17.8886 | 9.5511 | 34.8494
IMPP4 MC2 | 400 | 54.0909 | 20.003 | 11.878 | 40.1666 | 46.2576 | 17.8886 | 9.5511 | 34.8494
INDQ4 MC1 | 400 | 34.8777 | 13.1692 | 5.578 | 24.202 | 36.4824 | 14.2246 | 6.8356 | 26.9522
INDQ4 MC2 | 400 | 34.8777 | 13.1692 | 5.578 | 24.202 | 36.4824 | 14.2246 | 6.8356 | 26.9522
INDQ4 MC3 | 400 | 34.8777 | 13.1692 | 5.578 | 24.202 | 36.4824 | 14.2246 | 6.8356 | 26.9522
INDQ4 MC4 | 400 | 34.8777 | 13.1692 | 5.578 | 24.202 | 36.4824 | 14.2246 | 6.8356 | 26.9522
IROA1 M1 | 132 | 40.9413 | 14.7603 | 10.1401 | 31.0144 | 49.6144 | 18.8196 | 11.6407 | 38.2556
IROA1 M2 | 132 | 40.9413 | 14.7603 | 10.1401 | 31.0144 | 49.6144 | 18.8196 | 11.6407 | 38.2556
IROA1 R1 | 132 | 43.5376 | 15.639 | 10.6907 | 32.8076 | 52.4832 | 19.8452 | 12.2945 | 40.3598
IROA1 R2 | 132 | 28.2277 | 10.2161 | 8.4895 | 22.9373 | 34.151 | 12.7845 | 9.5333 | 27.6134
IROA2 MC1 | 275 | 57.57 | 21.1803 | 10.9758 | 40.9293 | 55.898 | 21.7171 | 11.1134 | 41.826
IROA2 MC2 | 275 | 57.57 | 21.1803 | 10.9758 | 40.9293 | 55.898 | 21.7171 | 11.1134 | 41.826
IROA2 MC3 | 275 | 57.57 | 21.1803 | 10.9758 | 40.9293 | 55.898 | 21.7171 | 11.1134 | 41.826
IROA2 MC4 | 275 | 57.57 | 21.1803 | 10.9758 | 40.9293 | 55.898 | 21.7171 | 11.1134 | 41.826
IROA2 MC5 | 275 | 57.57 | 21.1803 | 10.9758 | 40.9293 | 55.898 | 21.7171 | 11.1134 | 41.826
IRON1 M1 | 132 | 26.8099 | 10.3797 | 8.7883 | 23.4674 | 29.8363 | 11.6953 | 9.771 | 26.3106
IRON1 M2 | 132 | 26.8519 | 10.4212 | 8.6493 | 23.3871 | 29.5062 | 11.6041 | 9.4893 | 25.9
IRON1 R1 | 132 | 17.3076 | 6.287 | 6.1869 | 15.0781 | 19.765 | 7.2218 | 7.1502 | 17.3633
IRON1 R2 | 132 | 17.3076 | 6.287 | 6.1869 | 15.0781 | 19.765 | 7.2218 | 7.1502 | 17.3633
IRON4 M1 | 400 | 68.3768 | 25.1979 | 12.4171 | 48.0523 | 58.2463 | 22.9467 | 10.4447 | 42.8963
IRON4 M2 | 400 | 68.3768 | 25.1979 | 12.4171 | 48.0523 | 58.2463 | 22.9467 | 10.4447 | 42.8963
IRON4 R1 | 400 | 68.3768 | 25.1979 | 12.4171 | 48.0523 | 58.2463 | 22.9467 | 10.4447 | 42.8963
IRON4 R2 | 400 | 68.3768 | 25.1979 | 12.4171 | 48.0523 | 58.2463 | 22.9467 | 10.4447 | 42.8963
IVER2 M1 | 275 | 65.4544 | 23.8648 | 16.2648 | 50.0147 | 70.2217 | 26.7569 | 16.7762 | 54.6162
IVER2 M2 | 275 | 65.4544 | 23.8648 | 16.2648 | 50.0147 | 70.2217 | 26.7569 | 16.7762 | 54.6162
IVER2 R1 | 275 | 65.4544 | 23.8648 | 16.2648 | 50.0147 | 70.2217 | 26.7569 | 16.7762 | 54.6162
IVER2 R2 | 275 | 68.0625 | 24.6687 | 15.4599 | 50.3467 | 68.3929 | 26.3992 | 14.2982 | 51.6323
IVER4A | 400 | 45.6292 | 16.7089 | 5.6118 | 29.2418 | 43.2566 | 16.5632 | 5.8779 | 29.3018
IVER4B | 400 | 43.8309 | 16.1169 | 5.2184 | 28.0111 | 40.9766 | 15.9166 | 5.0151 | 27.5246
JORD2 MC1 | 275 | 50.0438 | 18.8443 | 8.8206 | 35.4705 | 49.3994 | 20.403 | 7.3334 | 36.1875
JORD2 MC2 | 275 | 50.0438 | 18.8443 | 8.8206 | 35.4705 | 49.3994 | 20.403 | 7.3334 | 36.1875
KEAD4 M2 | 400 | 110.6076 | 38.5096 | 29.1288 | 83.5896 | 97.9539 | 36.7666 | 24.2364 | 76.2322
KEAD4 M3 | 400 | 107.9888 | 37.4969 | 28.4958 | 81.5244 | 87.4299 | 32.9984 | 20.1832 | 66.85
KEAD4 R2 | 400 | 110.6076 | 38.5096 | 29.1288 | 83.5896 | 97.9539 | 36.7666 | 24.2364 | 76.2322
KEAD4 R3 | 400 | 102.862 | 36.7253 | 25.1652 | 77.1025 | 87.3071 | 33.1938 | 21.7943 | 68.7375
KEAR2 M1 | 275 | 73.1063 | 26.139 | 18.4198 | 55.3859 | 78.8815 | 29.778 | 19.1839 | 61.2964
KEAR2 M2 | 275 | 73.1063 | 26.139 | 18.4198 | 55.3859 | 78.8815 | 29.778 | 19.1839 | 61.2964
KEAR2 R1 | 275 | 73.1063 | 26.139 | 18.4198 | 55.3859 | 78.8815 | 29.778 | 19.1839 | 61.2964
KEAR2 R2 | 275 | 73.1063 | 26.139 | 18.4198 | 55.3859 | 78.8815 | 29.778 | 19.1839 | 61.2964
KEMS4 M1 | 400 | 130.8899 | 44.6431 | 29.4222 | 92.557 | 109.4432 | 41.861 | 21.4152 | 80.6155
KEMS4 M2 | 400 | 130.8899 | 44.6431 | 29.4222 | 92.557 | 109.4432 | 41.861 | 21.4152 | 80.6155
KEMS4 R1 | 400 | 130.8899 | 44.6431 | 29.4222 | 92.557 | 109.4432 | 41.861 | 21.4152 | 80.6155
KEMS4 R2 | 400 | 130.8899 | 44.6431 | 29.4222 | 92.557 | 109.4432 | 41.861 | 21.4152 | 80.6155
KENG4 M1 | 400 | 109.0522 | 36.5082 | 25.7643 | 77.3947 | 126.8773 | 46.9858 | 27.5081 | 93.956
KENG4 M2 | 400 | 109.0522 | 36.5082 | 25.7643 | 77.3947 | 126.8773 | 46.9858 | 27.5081 | 93.956
KENG4 R1 | 400 | 109.0522 | 36.5082 | 25.7643 | 77.3947 | 126.8773 | 46.9858 | 27.5081 | 93.956
KENG4 R2 | 400 | 109.0522 | 36.5082 | 25.7643 | 77.3947 | 126.8773 | 46.9858 | 27.5081 | 93.956
KIBY2 M1 | 275 | 68.618 | 24.1244 | 16.503 | 50.62 | 73.2642 | 27.613 | 16.1098 | 55.1604
KIBY2 M2 | 275 | 68.618 | 24.1244 | 16.503 | 50.62 | 73.2642 | 27.613 | 16.1098 | 55.1604
KIBY2 R1 | 275 | 59.4508 | 21.2622 | 13.8997 | 43.969 | 58.68 | 22.2483 | 13.0119 | 44.4757
KIBY2 R2 | 275 | 59.4508 | 21.2622 | 13.8997 | 43.969 | 58.68 | 22.2483 | 13.0119 | 44.4757
KILL4 M1 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 M2 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 M3 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 M4 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 M5 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 M9 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 R1/2 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 R3/4 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 R5 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KILL4 R9 | 400 | 112.5247 | 39.2302 | 40.4756 | 95.9555 | 105.9784 | 39.3026 | 36.5344 | 92.1166
KINO1 M1 | 132 | 28.881 | 10.1747 | 10.4342 | 24.8234 | 35.3677 | 13.0768 | 12.5962 | 31.0896
KINO1 M2 | 132 | 28.881 | 10.1747 | 10.4342 | 24.8234 | 35.3677 | 13.0768 | 12.5962 | 31.0896
KINO1 R1 | 132 | 28.881 | 10.1747 | 10.4342 | 24.8234 | 35.3677 | 13.0768 | 12.5962 | 31.0896
KINO1 R2 | 132 | 28.881 | 10.1747 | 10.4342 | 24.8234 | 35.3677 | 13.0768 | 12.5962 | 31.0896
KINO1A | 132 | 28.5485 | 9.9777 | 6.4936 | 20.6042 | 34.8739 | 12.9242 | 7.678 | 25.9557
KINO1B | 132 | 23.9416 | 8.9045 | 1.6706 | 14.2634 | 25.8378 | 10.4057 | 0.96044 | 15.6763
KINO4 M1 | 400 | 123.794 | 43.7371 | 38.5472 | 100.4007 | 114.388 | 43.4747 | 34.4187 | 95.9012
KINO4 M2 | 400 | 123.794 | 43.7371 | 38.5472 | 100.4007 | 114.388 | 43.4747 | 34.4187 | 95.9012
KINO4 M3 | 400 | 123.794 | 43.7371 | 38.5472 | 100.4007 | 114.388 | 43.4747 | 34.4187 | 95.9012
KINO4 M4 | 400 | 123.794 | 43.7371 | 38.5472 | 100.4007 | 114.388 | 43.4747 | 34.4187 | 95.9012
KINO4 R1/2 | 400 | 123.794 | 43.7371 | 38.5472 | 100.4007 | 114.388 | 43.4747 | 34.4187 | 95.9012
KINO4 R3/4 | 400 | 123.794 | 43.7371 | 38.5472 | 100.4007 | 114.388 | 43.4747 | 34.4187 | 95.9012
KIRK2 MC1 | 275 | 53.1544 | 19.2721 | 12.0079 | 39.2628 | 54.2106 | 20.8353 | 12.8843 | 42.3498
KIRK2 MC2 | 275 | 53.1544 | 19.2721 | 12.0079 | 39.2628 | 54.2106 | 20.8353 | 12.8843 | 42.3498
KIRK2 MC3 | 275 | 53.1544 | 19.2721 | 12.0079 | 39.2628 | 54.2106 | 20.8353 | 12.8843 | 42.3498
KIRK2 MC4 | 275 | 53.1544 | 19.2721 | 12.0079 | 39.2628 | 54.2106 | 20.8353 | 12.8843 | 42.3498
KIRK2A | 275 | 52.8477 | 18.6849 | 6.3968 | 32.8212 | 50.5857 | 19.7744 | 7.9762 | 35.9414
KITW2 MC1 | 275 | 60.4192 | 21.8997 | 11.7456 | 42.7165 | 59.4841 | 23.1828 | 10.3761 | 43.1616
KITW2 MC2 | 275 | 60.4192 | 21.8997 | 11.7456 | 42.7165 | 59.4841 | 23.1828 | 10.3761 | 43.1616
KITW2 MC3 | 275 | 60.4192 | 21.8997 | 11.7456 | 42.7165 | 59.4841 | 23.1828 | 10.3761 | 43.1616
KITW2 MC4 | 275 | 60.4192 | 21.8997 | 11.7456 | 42.7165 | 59.4841 | 23.1828 | 10.3761 | 43.1616
KNAR2 MC1 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
KNAR2 MC1 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
KNAR2 MC1 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
KNAR2 MC1 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
KNAR2 MC2 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
KNAR2 MC2 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
KNAR2 MC2 | 275 | 29.0254 | 11.693 | 2.4581 | 18.9945 | 26.5691 | 10.983 | 3.5215 | 19.0538
LACK2 M1 | 275 | 61.6035 | 20.7103 | 17.9205 | 47.2093 | 64.3955 | 23.4337 | 18.6732 | 51.8135
LACK2 M2 | 275 | 61.6035 | 20.7103 | 17.9205 | 47.2093 | 64.3955 | 23.4337 | 18.6732 | 51.8135
LACK2 R1 | 275 | 61.6035 | 20.7103 | 17.9205 | 47.2093 | 64.3955 | 23.4337 | 18.6732 | 51.8135
LACK2 R2 | 275 | 61.6035 | 20.7103 | 17.9205 | 47.2093 | 64.3955 | 23.4337 | 18.6732 | 51.8135
LACK4 M1 | 400 | 94.2356 | 31.4362 | 31.6642 | 76.1218 | 70.6246 | 26.2912 | 22.5675 | 59.7488
LACK4 M2 | 400 | 94.2356 | 31.4362 | 31.6642 | 76.1218 | 70.6246 | 26.2912 | 22.5675 | 59.7488
LACK4 R1 | 400 | 94.2356 | 31.4362 | 31.6642 | 76.1218 | 70.6246 | 26.2912 | 22.5675 | 59.7488
LACK4 R2 | 400 | 94.2356 | 31.4362 | 31.6642 | 76.1218 | 70.6246 | 26.2912 | 22.5675 | 59.7488
LAGA4 M1 | 400 | 41.7516 | 15.4234 | 8.2048 | 30.0167 | 43.0321 | 16.5832 | 9.4238 | 32.876
LAGA4 M2 | 400 | 41.7516 | 15.4234 | 8.2048 | 30.0167 | 43.0321 | 16.5832 | 9.4238 | 32.876
LAGA4 R1 | 400 | 41.7516 | 15.4234 | 8.2048 | 30.0167 | 43.0321 | 16.5832 | 9.4238 | 32.876
LAGA4 R2 | 400 | 41.7516 | 15.4234 | 8.2048 | 30.0167 | 43.0321 | 16.5832 | 9.4238 | 32.876
LALE2 MC1 | 275 | 60.8589 | 21.6164 | 17.1778 | 47.748 | 66.8616 | 25.806 | 16.4577 | 52.9529
LALE2 MC2 | 275 | 60.8589 | 21.6164 | 17.1778 | 47.748 | 66.8616 | 25.806 | 16.4577 | 52.9529
LALE2 MC3 | 275 | 60.8589 | 21.6164 | 17.1778 | 47.748 | 66.8616 | 25.806 | 16.4577 | 52.9529
LALE2 MC4 | 275 | 60.8589 | 21.6164 | 17.1778 | 47.748 | 66.8616 | 25.806 | 16.4577 | 52.9529
LAND4 MC1 | 400 | 33.6496 | 12.6254 | 6.075 | 23.93 | 33.0095 | 12.9455 | 5.8256 | 24.1333
LAND4 MC2 | 400 | 33.6496 | 12.6254 | 6.075 | 23.93 | 33.0095 | 12.9455 | 5.8256 | 24.1333
LEGA4 M1 | 400 | 80.7947 | 29.1742 | 16.9582 | 58.2168 | 64.7747 | 25.5444 | 11.523 | 47.6482
LEGA4 M2 | 400 | 80.7947 | 29.1742 | 16.9582 | 58.2168 | 64.7747 | 25.5444 | 11.523 | 47.6482
LEGA4 R1 | 400 | 80.7947 | 29.1742 | 16.9582 | 58.2168 | 64.7747 | 25.5444 | 11.523 | 47.6482
LEGA4 R2 | 400 | 80.7947 | 29.1742 | 16.9582 | 58.2168 | 64.7747 | 25.5444 | 11.523 | 47.6482
LEIS1 M1 | 132 | 65.7657 | 23.1783 | 21.6363 | 54.4153 | 74.858 | 27.1699 | 26.3489 | 64.7729
LEIS1 M2 | 132 | 65.7657 | 23.1783 | 21.6363 | 54.4153 | 74.858 | 27.1699 | 26.3489 | 64.7729
LEIS1 R1 | 132 | 65.7657 | 23.1783 | 21.6363 | 54.4153 | 74.858 | 27.1699 | 26.3489 | 64.7729
LEIS1 R2 | 132 | 65.7657 | 23.1783 | 21.6363 | 54.4153 | 74.858 | 27.1699 | 26.3489 | 64.7729
LISD2 M1 | 275 | 63.7103 | 22.5203 | 15.069 | 46.9175 | 68.6374 | 26.0449 | 14.9481 | 51.7811
LISD2 M2 | 275 | 63.7103 | 22.5203 | 15.069 | 46.9175 | 68.6374 | 26.0449 | 14.9481 | 51.7811
LISD2 R1 | 275 | 63.7103 | 22.5203 | 15.069 | 46.9175 | 68.6374 | 26.0449 | 14.9481 | 51.7811
LISD2 R2 | 275 | 63.7103 | 22.5203 | 15.069 | 46.9175 | 68.6374 | 26.0449 | 14.9481 | 51.7811
LITB4 Term500 | 400 | 69.8079 | 25.12 | 5.9372 | 41.4623 | 64.9405 | 24.6454 | 9.2653 | 44.1192
LITT4 M1 | 400 | 125.7256 | 42.809 | 27.6104 | 88.1515 | 113.4391 | 43.3357 | 22.986 | 84.2719
LITT4 M2 | 400 | 125.7256 | 42.809 | 27.6104 | 88.1515 | 113.4391 | 43.3357 | 22.986 | 84.2719
LITT4 M3 | 400 | 125.7256 | 42.809 | 27.6104 | 88.1515 | 113.4391 | 43.3357 | 22.986 | 84.2719
LITT4 R1 | 400 | 125.7256 | 42.809 | 27.6104 | 88.1515 | 113.4391 | 43.3357 | 22.986 | 84.2719
LITT4 R2 | 400 | 125.7256 | 42.809 | 27.6104 | 88.1515 | 113.4391 | 43.3357 | 22.986 | 84.2719
LITT4 R3 | 400 | 125.7256 | 42.809 | 27.6104 | 88.1515 | 113.4391 | 43.3357 | 22.986 | 84.2719
LOFI4A | 400 | 97.4835 | 33.1223 | 9.0444 | 55.8865 | 80.3949 | 31.1149 | 4.5418 | 48.545
LOFI4A_KEMS | 400 | 97.4835 | 33.1223 | 9.0444 | 55.8865 | 80.3949 | 31.1149 | 4.5418 | 48.545
LOFI4A_LITT | 400 | 97.4835 | 33.1223 | 9.0444 | 55.8865 | 80.3949 | 31.1149 | 4.5418 | 48.545
LOFI4A_ROWD | 400 | 97.4835 | 33.1223 | 9.0444 | 55.8865 | 80.3949 | 31.1149 | 4.5418 | 48.545
LOFI4B | 400 | 96.4557 | 32.8751 | 8.8094 | 55.3018 | 81.2979 | 31.4789 | 4.5402 | 49.0581
LOFI4B_KEMS | 400 | 96.4557 | 32.8751 | 8.8094 | 55.3018 | 81.2979 | 31.4789 | 4.5402 | 49.0581
LOFI4B_LITT | 400 | 96.4557 | 32.8751 | 8.8094 | 55.3018 | 81.2979 | 31.4789 | 4.5402 | 49.0581
LOFI4B_ROWD | 400 | 96.4557 | 32.8751 | 8.8094 | 55.3018 | 81.2979 | 31.4789 | 4.5402 | 49.0581
LOVE4 M1 | 400 | 98.1711 | 35.1934 | 18.7505 | 68.5214 | 83.251 | 32.2711 | 15.6661 | 61.3043
LOVE4 M2 | 400 | 98.1711 | 35.1934 | 18.7505 | 68.5214 | 83.251 | 32.2711 | 15.6661 | 61.3043
LOVE4 R1 | 400 | 98.1711 | 35.1934 | 18.7505 | 68.5214 | 83.251 | 32.2711 | 15.6661 | 61.3043
LOVE4 R2 | 400 | 98.1711 | 35.1934 | 18.7505 | 68.5214 | 83.251 | 32.2711 | 15.6661 | 61.3043
MACC2 MC1 | 275 | 55.4138 | 20.4003 | 13.4512 | 42.3016 | 52.2572 | 20.1478 | 11.6543 | 40.1476
MACC2 MC2 | 275 | 55.4138 | 20.4003 | 13.4512 | 42.3016 | 52.2572 | 20.1478 | 11.6543 | 40.1476
MACC4 MC1 | 400 | 78.501 | 29.4082 | 22.0884 | 63.6779 | 60.1705 | 24.0145 | 14.77 | 48.7316
MACC4 MC2 | 400 | 78.501 | 29.4082 | 22.0884 | 63.6779 | 60.1705 | 24.0145 | 14.77 | 48.7316
MACC4 MC3 | 400 | 78.501 | 29.4082 | 22.0884 | 63.6779 | 60.1705 | 24.0145 | 14.77 | 48.7316
MACC4 MC4 | 400 | 78.501 | 29.4082 | 22.0884 | 63.6779 | 60.1705 | 24.0145 | 14.77 | 48.7316
MAGA2 MC1 | 275 | 51.867 | 19.1275 | 11.2312 | 38.2815 | 45.2665 | 17.9037 | 8.3183 | 33.638
MAGA2 MC2 | 275 | 51.867 | 19.1275 | 11.2312 | 38.2815 | 45.2665 | 17.9037 | 8.3183 | 33.638
MANN4 M5 | 400 | 57.3532 | 21.0303 | 10.8386 | 40.5799 | 52.2603 | 20.0962 | 11.0916 | 39.5119
MANN4 MC1 | 400 | 57.3532 | 21.0303 | 10.8386 | 40.5799 | 52.2603 | 20.0962 | 11.0916 | 39.5119
MANN4 MC2 | 400 | 57.3532 | 21.0303 | 10.8386 | 40.5799 | 52.2603 | 20.0962 | 11.0916 | 39.5119
MANN4 MC3 | 400 | 57.3532 | 21.0303 | 10.8386 | 40.5799 | 52.2603 | 20.0962 | 11.0916 | 39.5119
MANN4 MC4 | 400 | 57.3532 | 21.0303 | 10.8386 | 40.5799 | 52.2603 | 20.0962 | 11.0916 | 39.5119
MANN4 R5 | 400 | 57.3532 | 21.0303 | 10.8386 | 40.5799 | 52.2603 | 20.0962 | 11.0916 | 39.5119
MAWO4 M | 400 | 64.5654 | 23.5425 | 12.4782 | 45.7724 | 56.8256 | 21.7741 | 12.4232 | 43.2165
MAWO4 R | 400 | 64.5654 | 23.5425 | 12.4782 | 45.7724 | 56.8256 | 21.7741 | 12.4232 | 43.2165
MEDW4 Term500 | 400 | 115.1535 | 39.8152 | 24.1232 | 80.4303 | 103.8274 | 39.2396 | 22.9813 | 78.4745
MELK1 M1 | 132 | 41.9437 | 14.6686 | 14.7636 | 35.5081 | 52.0403 | 19.1218 | 17.323 | 44.3652
MELK1 M2 | 132 | 41.9437 | 14.6686 | 14.7636 | 35.5081 | 52.0403 | 19.1218 | 17.323 | 44.3652
MELK1 R1 | 132 | 41.9437 | 14.6686 | 14.7636 | 35.5081 | 52.0403 | 19.1218 | 17.323 | 44.3652
MELK1 R2 | 132 | 41.9437 | 14.6686 | 14.7636 | 35.5081 | 52.0403 | 19.1218 | 17.323 | 44.3652
MELK4 M1 | 400 | 102.0633 | 37.4224 | 18.8993 | 71.8226 | 84.9937 | 33.6187 | 14.0297 | 61.5738
MELK4 M2 | 400 | 102.0633 | 37.4224 | 18.8993 | 71.8226 | 84.9937 | 33.6187 | 14.0297 | 61.5738
MELK4 M3 | 400 | 102.0633 | 37.4224 | 18.8993 | 71.8226 | 84.9937 | 33.6187 | 14.0297 | 61.5738
MELK4 R1 | 400 | 102.0633 | 37.4224 | 18.8993 | 71.8226 | 84.9937 | 33.6187 | 14.0297 | 61.5738
MELK4 R2 | 400 | 102.0633 | 37.4224 | 18.8993 | 71.8226 | 84.9937 | 33.6187 | 14.0297 | 61.5738
MELK4 R3 | 400 | 102.0633 | 37.4224 | 18.8993 | 71.8226 | 84.9937 | 33.6187 | 14.0297 | 61.5738
MILH1 M1 | 132 | 40.3331 | 14.7879 | 9.0879 | 30.0011 | 46.6595 | 18.9363 | 9.1195 | 35.8995
MILH1 M2 | 132 | 40.3331 | 14.7879 | 9.0879 | 30.0011 | 46.6595 | 18.9363 | 9.1195 | 35.8995
MILH1 R1 | 132 | 40.3663 | 14.8153 | 8.9819 | 29.9339 | 46.5458 | 18.9466 | 8.8772 | 35.6717
MILH1 R2 | 132 | 40.3663 | 14.8153 | 8.9819 | 29.9339 | 46.5458 | 18.9466 | 8.8772 | 35.6717
MITY4 MC1 | 400 | 79.0533 | 30.1392 | 20.6495 | 63.2727 | 60.2649 | 24.3651 | 13.9885 | 48.446
MITY4 MC2 | 400 | 79.0533 | 30.1392 | 20.6495 | 63.2727 | 60.2649 | 24.3651 | 13.9885 | 48.446
MITY4 MC3 | 400 | 79.0533 | 30.1392 | 20.6495 | 63.2727 | 60.2649 | 24.3651 | 13.9885 | 48.446
MITY4 MC4 | 400 | 79.0533 | 30.1392 | 20.6495 | 63.2727 | 60.2649 | 24.3651 | 13.9885 | 48.446
MONF2 M1 | 275 | 65.5146 | 23.6543 | 17.7136 | 51.1658 | 66.408 | 25.2353 | 16.1329 | 51.8209
MONF2 M2 | 275 | 65.5146 | 23.6543 | 17.7136 | 51.1658 | 66.408 | 25.2353 | 16.1329 | 51.8209
MONF2 R1 | 275 | 56.9746 | 20.6179 | 18.2582 | 47.4163 | 59.68 | 22.4105 | 17.3691 | 49.0623
MONF2 R2 | 275 | 56.9746 | 20.6179 | 18.2582 | 47.4163 | 59.68 | 22.4105 | 17.3691 | 49.0623
MONF4 MC2 | 400 | 80.9775 | 29.2 | 19.35 | 60.6451 | 70.4572 | 26.9236 | 15.6873 | 53.7631
MONF4 MC3 | 400 | 80.9775 | 29.2 | 19.35 | 60.6451 | 70.4572 | 26.9236 | 15.6873 | 53.7631
NECH2 MC1 | 275 | 71.246 | 25.4859 | 18.1295 | 54.1721 | 72.2653 | 27.7403 | 15.7648 | 54.9955
NECH2 MC2 | 275 | 71.246 | 25.4859 | 18.1295 | 54.1721 | 72.2653 | 27.7403 | 15.7648 | 54.9955
NECH2 MC3 | 275 | 71.246 | 25.4859 | 18.1295 | 54.1721 | 72.2653 | 27.7403 | 15.7648 | 54.9955
NECH2 MC4 | 275 | 71.246 | 25.4859 | 18.1295 | 54.1721 | 72.2653 | 27.7403 | 15.7648 | 54.9955
NECT4 M1 | 400 | 78.0805 | 27.9825 | 18.6914 | 58.2647 | 54.5833 | 21.5082 | 10.9184 | 41.3357
NECT4 R1 | 400 | 78.0805 | 27.9825 | 18.6914 | 58.2647 | 54.5833 | 21.5082 | 10.9184 | 41.3357
NEEP2 M1 | 275 | 59.1657 | 21.8118 | 12.7392 | 43.5857 | 62.053 | 24.6889 | 11.9298 | 46.8451
NEEP2 M2 | 275 | 59.1657 | 21.8118 | 12.7392 | 43.5857 | 62.053 | 24.6889 | 11.9298 | 46.8451
NEEP2 R1/R2 | 275 | 59.1657 | 21.8118 | 12.7392 | 43.5857 | 62.053 | 24.6889 | 11.9298 | 46.8451
NEWX2 M5 | 275 | 82.1475 | 28.7393 | 21.3917 | 62.0352 | 88.6899 | 34.7251 | 18.2503 | 67.3591
NEWX2 M5 | 275 | 82.1475 | 28.7393 | 21.3917 | 62.0352 | 88.6899 | 34.7251 | 18.2503 | 67.3591
NEWX2 M6 | 275 | 82.1475 | 28.7393 | 21.3917 | 62.0352 | 88.6899 | 34.7251 | 18.2503 | 67.3591
NEWX2 R6 | 275 | 82.1475 | 28.7393 | 21.3917 | 62.0352 | 88.6899 | 34.7251 | 18.2503 | 67.3591
NEWX21 R5 | 275 | 82.1475 | 28.7393 | 21.3917 | 62.0352 | 88.6899 | 34.7251 | 18.2503 | 67.3591
NFLE4 M1 | 400 | 106.1133 | 36.7746 | 22.4301 | 74.4372 | 85.2029 | 33.2198 | 14.9739 | 61.9538
NFLE4 M2 | 400 | 106.1133 | 36.7746 | 22.4301 | 74.4372 | 85.2029 | 33.2198 | 14.9739 | 61.9538
NFLE4 R1 | 400 | 106.1133 | 36.7746 | 22.4301 | 74.4372 | 85.2029 | 33.2198 | 14.9739 | 61.9538
NFLE4 R2 | 400 | 106.1133 | 36.7746 | 22.4301 | 74.4372 | 85.2029 | 33.2198 | 14.9739 | 61.9538
NHYD2A | 275 | 45.5063 | 17.266 | 2.5614 | 26.9793 | 39.0684 | 18.4612 | 0.4645 | 26.5726
NHYD2B | 275 | 46.8002 | 17.6121 | 2.3073 | 27.2145 | 40.3662 | 18.4543 | 1.0758 | 27.1741
NHYD2C | 275 | 46.8002 | 17.6121 | 2.3073 | 27.2145 | 40.3662 | 18.4543 | 1.0758 | 27.1741
NINF4 M1 | 400 | 67.7932 | 24.5981 | 14.8729 | 49.6598 | 63.4864 | 24.2014 | 14.896 | 49.1221
NINF4 M2 | 400 | 67.7932 | 24.5981 | 14.8729 | 49.6598 | 63.4864 | 24.2014 | 14.896 | 49.1221
NINF4 R1 | 400 | 67.7932 | 24.5981 | 14.8729 | 49.6598 | 63.4864 | 24.2014 | 14.896 | 49.1221
NINF4 R2 | 400 | 67.7932 | 24.5981 | 14.8729 | 49.6598 | 63.4864 | 24.2014 | 14.896 | 49.1221
NORL2A | 275 | 51.6788 | 18.9899 | 3.9239 | 30.7797 | 50.943 | 20.9554 | 2.2758 | 31.9111
NORL2B | 275 | 50.8699 | 18.7683 | 3.412 | 29.9544 | 50.1207 | 20.901 | 2.0107 | 31.5692
NORM4 M1 | 400 | 72.7671 | 26.3751 | 16.3604 | 53.6605 | 53.196 | 20.8786 | 11.3242 | 40.851
NORM4 M2 | 400 | 72.7671 | 26.3751 | 16.3604 | 53.6605 | 53.196 | 20.8786 | 11.3242 | 40.851
NORM4 R1 | 400 | 72.7671 | 26.3751 | 16.3604 | 53.6605 | 53.196 | 20.8786 | 11.3242 | 40.851
NORM4 R2 | 400 | 72.7671 | 26.3751 | 16.3604 | 53.6605 | 53.196 | 20.8786 | 11.3242 | 40.851
NORT2 M1 | 275 | 71.7839 | 24.6382 | 20.1211 | 54.9648 | 72.023 | 26.8628 | 17.4417 | 55.4314
NORT2 M2 | 275 | 71.7839 | 24.6382 | 20.1211 | 54.9648 | 72.023 | 26.8628 | 17.4417 | 55.4314
NORT2 R1 | 275 | 71.7839 | 24.6382 | 20.1211 | 54.9648 | 72.023 | 26.8628 | 17.4417 | 55.4314
NORT2 R2 | 275 | 71.7839 | 24.6382 | 20.1211 | 54.9648 | 72.023 | 26.8628 | 17.4417 | 55.4314
NORT4 M1 | 400 | 98.009 | 34.1316 | 30.6044 | 78.8738 | 77.5951 | 29.6853 | 21.6627 | 63.6441
NORT4 M2 | 400 | 98.009 | 34.1316 | 30.6044 | 78.8738 | 77.5951 | 29.6853 | 21.6627 | 63.6441
NORT4 R1 | 400 | 98.009 | 34.1316 | 30.6044 | 78.8738 | 77.5951 | 29.6853 | 21.6627 | 63.6441
NORT4 R2 | 400 | 98.009 | 34.1316 | 30.6044 | 78.8738 | 77.5951 | 29.6853 | 21.6627 | 63.6441
NURS4 MC1 | 400 | 61.45 | 22.2079 | 7.8854 | 39.2921 | 55.2449 | 21.0632 | 8.1705 | 37.9583
NURS4 MC2 | 400 | 61.45 | 22.2079 | 7.8854 | 39.2921 | 55.2449 | 21.0632 | 8.1705 | 37.9583
NURS4A | 400 | 52.8656 | 19.502 | 10.5197 | 38.0998 | 48.1083 | 18.4418 | 10.5344 | 36.615
OCKH1 M1 | 132 | 24.7775 | 8.8549 | 8.4524 | 20.9752 | 33.1946 | 12.1718 | 10.9696 | 28.1832
OCKH1 M2 | 132 | 24.7775 | 8.8549 | 8.4524 | 20.9752 | 33.1946 | 12.1718 | 10.9696 | 28.1832
OCKH1 R1 | 132 | 24.7775 | 8.8549 | 8.4524 | 20.9752 | 33.1946 | 12.1718 | 10.9696 | 28.1832
OCKH1 R2 | 132 | 24.7775 | 8.8549 | 8.4524 | 20.9752 | 33.1946 | 12.1718 | 10.9696 | 28.1832
OCKH2 MC1 | 275 | 54.1102 | 19.7379 | 10.3935 | 38.3071 | 56.1616 | 21.8882 | 10.5702 | 41.5247
OCKH2 MC2 | 275 | 54.1102 | 19.7379 | 10.3935 | 38.3071 | 56.1616 | 21.8882 | 10.5702 | 41.5247
OCKH2 MC3 | 275 | 54.1102 | 19.7379 | 10.3935 | 38.3071 | 56.1616 | 21.8882 | 10.5702 | 41.5247
OCKH2 MC4 | 275 | 54.1102 | 19.7379 | 10.3935 | 38.3071 | 56.1616 | 21.8882 | 10.5702 | 41.5247
OCKH2A | 275 | 47.7364 | 17.0762 | 4.2371 | 28.3865 | 48.0113 | 18.5 | 4.6447 | 30.8076
OFFE2 MC1 | 275 | 65.827 | 23.3658 | 13.209 | 46.2532 | 58.4604 | 23.0533 | 8.4265 | 41.0289
OFFE2 MC2 | 275 | 65.827 | 23.3658 | 13.209 | 46.2532 | 58.4604 | 23.0533 | 8.4265 | 41.0289
OLDB2 MC1 | 275 | 52.0332 | 19.0812 | 10.4748 | 37.4597 | 53.7269 | 20.7646 | 10.6951 | 40.0607
OLDB2 MC2 | 275 | 52.0332 | 19.0812 | 10.4748 | 37.4597 | 53.7269 | 20.7646 | 10.6951 | 40.0607
OSBA4 MC1 | 400 | 60.7547 | 22.0276 | 14.6456 | 45.7973 | 52.9042 | 20.1166 | 13.0495 | 41.4986
OSBA4 MC2 | 400 | 60.7547 | 22.0276 | 14.6456 | 45.7973 | 52.9042 | 20.1166 | 13.0495 | 41.4986
OSBA4 MC3/4 | 400 | 66.331 | 23.3912 | 16.6539 | 49.7341 | 50.0677 | 19.1142 | 11.4567 | 38.4882
PADI1 M1 | 132 | 29.2399 | 10.2565 | 10.2434 | 24.7482 | 36.4111 | 13.3367 | 12.4513 | 31.3122
PADI1 M2 | 132 | 29.2399 | 10.2565 | 10.2434 | 24.7482 | 36.4111 | 13.3367 | 12.4513 | 31.3122
PADI1 R1 | 132 | 29.2399 | 10.2565 | 10.2434 | 24.7482 | 36.4111 | 13.3367 | 12.4513 | 31.3122
PADI1 R2 | 132 | 29.2399 | 10.2565 | 10.2434 | 24.7482 | 36.4111 | 13.3367 | 12.4513 | 31.3122
PADI4 MC1 | 400 | 71.7513 | 26.1446 | 14.9827 | 51.9567 | 55.1612 | 21.7541 | 9.4816 | 40.2466
PADI4 MC2 | 400 | 71.7513 | 26.1446 | 14.9827 | 51.9567 | 55.1612 | 21.7541 | 9.4816 | 40.2466
PADI4 MC3 | 400 | 71.7513 | 26.1446 | 14.9827 | 51.9567 | 55.1612 | 21.7541 | 9.4816 | 40.2466
PADI4 MC4 | 400 | 71.7513 | 26.1446 | 14.9827 | 51.9567 | 55.1612 | 21.7541 | 9.4816 | 40.2466
PELH4 M1 | 400 | 130.515 | 45.6762 | 30.0136 | 94.6095 | 107.6963 | 41.4928 | 20.5978 | 79.2776
PELH4 M2 | 400 | 130.515 | 45.6762 | 30.0136 | 94.6095 | 107.6963 | 41.4928 | 20.5978 | 79.2776
PELH4 R1 | 400 | 130.515 | 45.6762 | 30.0136 | 94.6095 | 107.6963 | 41.4928 | 20.5978 | 79.2776
PELH4 R2 | 400 | 130.515 | 45.6762 | 30.0136 | 94.6095 | 107.6963 | 41.4928 | 20.5978 | 79.2776
PEMB4 M1 | 400 | 62.5191 | 22.0254 | 18.3423 | 49.491 | 65.2917 | 23.9993 | 20.5149 | 54.4551
PEMB4 M2 | 400 | 62.5191 | 22.0254 | 18.3423 | 49.491 | 65.2917 | 23.9993 | 20.5149 | 54.4551
PEMB4 M3 | 400 | 62.5191 | 22.0254 | 18.3423 | 49.491 | 65.2917 | 23.9993 | 20.5149 | 54.4551
PEMB4 M4 | 400 | 62.5191 | 22.0254 | 18.3423 | 49.491 | 65.2917 | 23.9993 | 20.5149 | 54.4551
PEMB4 R1/2 | 400 | 62.5191 | 22.0254 | 18.3423 | 49.491 | 65.2917 | 23.9993 | 20.5149 | 54.4551
PEMB4 R3/4 | 400 | 62.5191 | 22.0254 | 18.3423 | 49.491 | 65.2917 | 23.9993 | 20.5149 | 54.4551
PENN2 MC1 | 275 | 64.3485 | 23.2998 | 13.4985 | 46.4494 | 67.7267 | 25.9176 | 14.3393 | 50.9924
PENN2 MC2 | 275 | 64.3485 | 23.2998 | 13.4985 | 46.4494 | 67.7267 | 25.9176 | 14.3393 | 50.9924
PENN2 MC3 | 275 | 64.3485 | 23.2998 | 13.4985 | 46.4494 | 67.7267 | 25.9176 | 14.3393 | 50.9924
PENN2 MC4 | 275 | 64.3485 | 23.2998 | 13.4985 | 46.4494 | 67.7267 | 25.9176 | 14.3393 | 50.9924
PENT4 M1 | 400 | 71.3805 | 24.9967 | 19.3484 | 54.6992 | 73.2796 | 27.283 | 19.4195 | 58.0035
PENT4 M2 | 400 | 71.3805 | 24.9967 | 19.3484 | 54.6992 | 73.2796 | 27.283 | 19.4195 | 58.0035
PENT4 R1 | 400 | 71.3805 | 24.9967 | 19.3484 | 54.6992 | 73.2796 | 27.283 | 19.4195 | 58.0035
PENT4 R2 | 400 | 71.3805 | 24.9967 | 19.3484 | 54.6992 | 73.2796 | 27.283 | 19.4195 | 58.0035
PEWO2A | 275 | 61.8718 | 22.1442 | 17.8007 | 49.1173 | 64.5781 | 24.138 | 17.7257 | 51.862
PEWO2B | 275 | 62.9342 | 22.8863 | 22.1216 | 54.4878 | 65.6181 | 24.66 | 22.5944 | 57.4689
PEWO4 M1 | 400 | 86.3113 | 31.4491 | 26.1791 | 70.6549 | 81.3609 | 31.4877 | 23.3967 | 67.9271
PEWO4 M2 | 400 | 86.3113 | 31.4491 | 26.1791 | 70.6549 | 81.3609 | 31.4877 | 23.3967 | 67.9271
PEWO4 M3 | 400 | 86.3113 | 31.4491 | 26.1791 | 70.6549 | 81.3609 | 31.4877 | 23.3967 | 67.9271
PEWO4 M4 | 400 | 86.3113 | 31.4491 | 26.1791 | 70.6549 | 81.3609 | 31.4877 | 23.3967 | 67.9271
PEWO4 R1/2 | 400 | 86.3113 | 31.4491 | 26.1791 | 70.6549 | 81.3609 | 31.4877 | 23.3967 | 67.9271
PEWO4 R3/4 | 400 | 86.3113 | 31.4491 | 26.1791 | 70.6549 | 81.3609 | 31.4877 | 23.3967 | 67.9271
PITS2 MC1 | 275 | 60.8272 | 22.0971 | 8.5596 | 39.8096 | 65.4448 | 25.6745 | 7.5836 | 43.8927
PITS2 MC2 | 275 | 60.8272 | 22.0971 | 8.5596 | 39.8096 | 65.4448 | 25.6745 | 7.5836 | 43.8927
PITS2 MC3 | 275 | 60.8272 | 22.0971 | 8.5596 | 39.8096 | 65.4448 | 25.6745 | 7.5836 | 43.8927
PITS2 MC4 | 275 | 60.8272 | 22.0971 | 8.5596 | 39.8096 | 65.4448 | 25.6745 | 7.5836 | 43.8927
POPP2 MC1 | 275 | 27.3331 | 10.9221 | 2.8529 | 18.2991 | 24.4881 | 10.0006 | 3.7285 | 17.8715
POPP2 MC2 | 275 | 27.3331 | 10.9221 | 2.8529 | 18.2991 | 24.4881 | 10.0006 | 3.7285 | 17.8715
PUDM4 MC1 | 400 | 100.9783 | 34.3673 | 22.9229 | 71.5256 | 104.8089 | 41.2303 | 19.2545 | 77.563
PUDM4 MC2 | 400 | 100.9783 | 34.3673 | 22.9229 | 71.5256 | 104.8089 | 41.2303 | 19.2545 | 77.563
PYLE2 MC1 | 275 | 54.1183 | 20.0729 | 10.8546 | 39.2419 | 47.7355 | 18.8838 | 8.8994 | 35.6051
PYLE2 MC2 | 275 | 54.1722 | 20.0917 | 10.8678 | 39.2819 | 47.7801 | 18.8998 | 8.9154 | 35.6437
QUER4A | 400 | 70.5125 | 24.7678 | 8.0716 | 43.0985 | 63.7769 | 24.6255 | 4.4803 | 39.3061
QUER4A_HEYS | 400 | 70.5125 | 24.7678 | 8.0716 | 43.0985 | 63.7769 | 24.6255 | 4.4803 | 39.3061
QUER4A_HUTT | 400 | 70.5125 | 24.7678 | 8.0716 | 43.0985 | 63.7769 | 24.6255 | 4.4803 | 39.3061
QUER4A_PEWO | 400 | 70.5125 | 24.7678 | 8.0716 | 43.0985 | 63.7769 | 24.6255 | 4.4803 | 39.3061
QUER4B | 400 | 71.0247 | 24.9211 | 8.2028 | 43.4466 | 65.2849 | 25.1148 | 4.9248 | 40.4426
QUER4B_HEYS | 400 | 71.0247 | 24.9211 | 8.2028 | 43.4466 | 65.2849 | 25.1148 | 4.9248 | 40.4426
QUER4B_HUTT | 400 | 71.0247 | 24.9211 | 8.2028 | 43.4466 | 65.2849 | 25.1148 | 4.9248 | 40.4426
QUER4B_PEWO | 400 | 71.0247 | 24.9211 | 8.2028 | 43.4466 | 65.2849 | 25.1148 | 4.9248 | 40.4426
RAIN2 MC1 | 275 | 72.7613 | 25.4725 | 18.0712 | 54.0948 | 72.6203 | 27.4165 | 15.6105 | 54.3833
RAIN2 MC2 | 275 | 72.7613 | 25.4725 | 18.0712 | 54.0948 | 72.6203 | 27.4165 | 15.6105 | 54.3833
RAIN2 MC3 | 275 | 72.7613 | 25.4725 | 18.0712 | 54.0948 | 72.6203 | 27.4165 | 15.6105 | 54.3833
RAIN2 MC4 | 275 | 72.7613 | 25.4725 | 18.0712 | 54.0948 | 72.6203 | 27.4165 | 15.6105 | 54.3833
RASS4 M1 | 400 | 53.0594 | 19.8413 | 16.1363 | 44.1961 | 43.0286 | 16.8768 | 11.6046 | 35.4721
RASS4 M2 | 400 | 53.0594 | 19.8413 | 16.1363 | 44.1961 | 43.0286 | 16.8768 | 11.6046 | 35.4721
RATS1 M1 | 132 | 42.11 | 14.8181 | 13.4449 | 34.4008 | 47.3432 | 17.614 | 15.4695 | 40.3794
RATS1 M2 | 132 | 42.11 | 14.8181 | 13.4449 | 34.4008 | 47.3432 | 17.614 | 15.4695 | 40.3794
RATS1 R1 | 132 | 38.6879 | 13.7141 | 12.2819 | 31.6765 | 43.3111 | 16.2376 | 12.9858 | 35.9492
RATS1 R2 | 132 | 38.6879 | 13.7141 | 12.2819 | 31.6765 | 43.3111 | 16.2376 | 12.9858 | 35.9492
RATS2A | 275 | 42.0156 | 15.1583 | 9.1504 | 30.5874 | 43.2322 | 15.7668 | 16.1309 | 38.4286
RATS4 M1 | 400 | 115.4166 | 41.4718 | 21.4631 | 80.1131 | 97.7229 | 38.4391 | 17.6647 | 72.0258
RATS4 M2 | 400 | 115.4166 | 41.4718 | 21.4631 | 80.1131 | 97.7229 | 38.4391 | 17.6647 | 72.0258
RATS4 M3 | 400 | 115.4166 | 41.4718 | 21.4631 | 80.1131 | 97.7229 | 38.4391 | 17.6647 | 72.0258
RATS4 M4 | 400 | 115.4166 | 41.4718 | 21.4631 | 80.1131 | 97.7229 | 38.4391 | 17.6647 | 72.0258
RATS4 R1/2 | 400 | 115.4166 | 41.4718 | 21.4631 | 80.1131 | 97.7229 | 38.4391 | 17.6647 | 72.0258
RATS4 R3/4 | 400 | 115.4166 | 41.4718 | 21.4631 | 80.1131 | 97.7229 | 38.4391 | 17.6647 | 72.0258
RAYL4 M1 | 400 | 103.2317 | 37.4694 | 30.813 | 83.8027 | 79.7804 | 31.3359 | 21.2553 | 65.5709
RAYL4 M2 | 400 | 103.2317 | 37.4694 | 30.813 | 83.8027 | 79.7804 | 31.3359 | 21.2553 | 65.5709
RAYL4 R1 | 400 | 103.2317 | 37.4694 | 30.813 | 83.8027 | 79.7804 | 31.3359 | 21.2553 | 65.5709
RAYL4 R2 | 400 | 103.2317 | 37.4694 | 30.813 | 83.8027 | 79.7804 | 31.3359 | 21.2553 | 65.5709
REBR2 MC1 | 275 | 63.5028 | 23.1333 | 21.4825 | 54.1979 | 61.5124 | 23.8946 | 17.4439 | 51.236
REBR2 MC2 | 275 | 61.3759 | 22.3757 | 20.9492 | 52.5932 | 59.9781 | 23.3547 | 16.8375 | 49.866
REBR2 MC3 | 275 | 61.3759 | 22.3757 | 20.9492 | 52.5932 | 59.9781 | 23.3547 | 16.8375 | 49.866
REBR2 MC4 | 275 | 63.5028 | 23.1333 | 21.4825 | 54.1979 | 61.5124 | 23.8946 | 17.4439 | 51.236
RHIG4 M1 | 400 | 54.4729 | 19.9236 | 12.6734 | 40.8496 | 47.7986 | 18.4697 | 9.593 | 35.7132
RHIG4 R1 | 400 | 54.4729 | 19.9236 | 12.6734 | 40.8496 | 47.7986 | 18.4697 | 9.593 | 35.7132
ROCH2 MC1 | 275 | 70.2419 | 25.3114 | 9.5335 | 45.3293 | 67.0898 | 25.9636 | 9.1782 | 45.8963
ROCH2 MC2 | 275 | 70.2419 | 25.3114 | 9.5335 | 45.3293 | 67.0898 | 25.9636 | 9.1782 | 45.8963
ROCH2 MC3 | 275 | 70.2419 | 25.3114 | 9.5335 | 45.3293 | 67.0898 | 25.9636 | 9.1782 | 45.8963
ROCH2 MC4 | 275 | 70.2419 | 25.3114 | 9.5335 | 45.3293 | 67.0898 | 25.9636 | 9.1782 | 45.8963
ROCK1A | 132 | 45.8136 | 15.7704 | 16.1205 | 38.4232 | 47.9335 | 17.3146 | 15.8242 | 40.3107
ROCK4 Term900 | 400 | 77.1624 | 27.328 | 18.5336 | 57.1812 | 74.7057 | 28.0017 | 18.9225 | 58.5229
RUGE4 M1 | 400 | 63.2208 | 23.6268 | 10.0115 | 43.4248 | 50.0895 | 20.1427 | 7.033 | 35.519
RUGE4 M2 | 400 | 63.2208 | 23.6268 | 10.0115 | 43.4248 | 50.0895 | 20.1427 | 7.033 | 35.519
RUGE4 R1 | 400 | 63.2208 | 23.6268 | 10.0115 | 43.4248 | 50.0895 | 20.1427 | 7.033 | 35.519
RUGE4 R2 | 400 | 63.2208 | 23.6268 | 10.0115 | 43.4248 | 50.0895 | 20.1427 | 7.033 | 35.519
RYEH4 M1 | 400 | 69.7798 | 25.1759 | 16.6656 | 52.2698 | 72.4575 | 27.2048 | 18.5689 | 57.0423
RYEH4 R1 | 400 | 69.7798 | 25.1759 | 16.6656 | 52.2698 | 72.4575 | 27.2048 | 18.5689 | 57.0423
RYHA42 MC1 | 400 | 42.0718 | 15.7669 | 8.9102 | 31.208 | 27.7671 | 11.0756 | 3.939 | 19.6023
RYHA4B_LOAD2 | 400 | 42.5579 | 15.9478 | 9.0195 | 31.573 | 29.4189 | 11.7336 | 4.1422 | 20.7361
SAEN2 MC1 | 275 | 77.5963 | 26.7994 | 23.337 | 61.2371 | 78.1618 | 28.6504 | 23.7478 | 64.2656
SAEN2 MC2 | 275 | 77.5963 | 26.7994 | 23.337 | 61.2371 | 78.1618 | 28.6504 | 23.7478 | 64.2656
SAES2 M | 275 | 78.1945 | 26.972 | 23.6475 | 61.7917 | 79.0735 | 28.9292 | 24.526 | 65.4381
SAES2 R | 275 | 78.1945 | 26.972 | 23.6475 | 61.7917 | 79.0735 | 28.9292 | 24.526 | 65.4381
SALH2 MC1 | 275 | 67.3338 | 23.5639 | 15.1399 | 48.4643 | 66.3456 | 25.0829 | 13.241 | 48.7136
SALH2 MC2 | 275 | 67.3338 | 23.5639 | 15.1399 | 48.4643 | 66.3456 | 25.0829 | 13.241 | 48.7136
SEAB4 M1 | 400 | 61.6419 | 22.64 | 19.9777 | 51.9955 | 63.3197 | 23.9046 | 21.1957 | 55.0019
SEAB4 M2 | 400 | 61.6419 | 22.64 | 19.9777 | 51.9955 | 63.3197 | 23.9046 | 21.1957 | 55.0019
SEAB4 R1 | 400 | 61.6419 | 22.64 | 19.9777 | 51.9955 | 63.3197 | 23.9046 | 21.1957 | 55.0019
SEAB4 R2 | 400 | 61.6419 | 22.64 | 19.9777 | 51.9955 | 63.3197 | 23.9046 | 21.1957 | 55.0019
SELL4 M1 | 400 | 85.7346 | 31.0599 | 17.9276 | 61.8529 | 70.8131 | 27.1623 | 16.4955 | 54.9088
SELL4 M2 | 400 | 85.7346 | 31.0599 | 17.9276 | 61.8529 | 70.8131 | 27.1623 | 16.4955 | 54.9088
SELL4 R1 | 400 | 85.7346 | 31.0599 | 17.9276 | 61.8529 | 70.8131 | 27.1623 | 16.4955 | 54.9088
SELL4 R2 | 400 | 85.7346 | 31.0599 | 17.9276 | 61.8529 | 70.8131 | 27.1623 | 16.4955 | 54.9088
SELL4A | 400 | 85.6438 | 30.2984 | 8.1521 | 51.0005 | 70.7417 | 26.9625 | 9.1461 | 47.2768
SELL4B | 400 | 85.6436 | 30.2984 | 8.1521 | 51.0004 | 70.7416 | 26.9625 | 9.146 | 47.2767
SELW4 M3 | 400 | 85.5395 | 30.9947 | 17.8756 | 61.7087 | 70.4078 | 27.026 | 16.2739 | 54.4944
SELW4 M4 | 400 | 85.5395 | 30.9947 | 17.8756 | 61.7087 | 70.4078 | 27.026 | 16.2739 | 54.4944
SELW4 R3 | 400 | 85.5395 | 30.9947 | 17.8756 | 61.7087 | 70.4078 | 27.026 | 16.2739 | 54.4944
SELW4 R4 | 400 | 85.5395 | 30.9947 | 17.8756 | 61.7087 | 70.4078 | 27.026 | 16.2739 | 54.4944
SETW4A | 400 | 85.537 | 30.2638 | 8.1384 | 50.9379 | 70.6848 | 26.9441 | 9.1161 | 47.2208
SETW4B | 400 | 85.5369 | 30.2638 | 8.1383 | 50.9378 | 70.6847 | 26.944 | 9.1161 | 47.2207
SHBA4 M1 | 400 | 73.5641 | 26.5594 | 25.0792 | 62.6398 | 72.3307 | 27.1851 | 24.3583 | 62.8039
SHBA4 M2 | 400 | 73.5641 | 26.5594 | 25.0792 | 62.6398 | 72.3307 | 27.1851 | 24.3583 | 62.8039
SHBA4 R1 | 400 | 73.5641 | 26.5594 | 25.0792 | 62.6398 | 72.3307 | 27.1851 | 24.3583 | 62.8039
SHBA4 R2 | 400 | 73.5641 | 26.5594 | 25.0792 | 62.6398 | 72.3307 | 27.1851 | 24.3583 | 62.8039
SHEC2 MC1 | 275 | 53.7151 | 20.0438 | 10.3575 | 38.7037 | 54.3114 | 22.3782 | 7.4319 | 39.0794
SHEC2 MC2 | 275 | 53.7151 | 20.0438 | 10.3575 | 38.7037 | 54.3114 | 22.3782 | 7.4319 | 39.0794
SHRE4B | 400 | 53.4613 | 19.9365 | 9.8491 | 38.0436 | 42.6963 | 16.9781 | 6.9447 | 30.9554
SING4 MC1 | 400 | 95.1119 | 33.3554 | 20.1872 | 67.3588 | 76.7228 | 29.9213 | 12.8704 | 55.1856
SING4 MC2 | 400 | 95.1119 | 33.3554 | 20.1872 | 67.3588 | 76.7228 | 29.9213 | 12.8704 | 55.1856
SIZE4 M1 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 M2 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 M3 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 M4 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 R1 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 R2 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 R3 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SIZE4 R4 | 400 | 74.0919 | 26.1078 | 19.3066 | 56.2286 | 75.7779 | 27.9774 | 21.7729 | 61.339
SJOW2 MC1 | 275 | 23.2526 | 8.1788 | 9.2742 | 20.8407 | 27.7935 | 9.9774 | 10.8993 | 25.0095
SJOW2 MC2 | 275 | 23.2526 | 8.1788 | 9.2742 | 20.8407 | 27.7935 | 9.9774 | 10.8993 | 25.0095
SJOW2 MC3 | 275 | 23.2526 | 8.1788 | 9.2742 | 20.8407 | 27.7935 | 9.9774 | 10.8993 | 25.0095
SJOW2 MC4 | 275 | 23.2526 | 8.1788 | 9.2742 | 20.8407 | 27.7935 | 9.9774 | 10.8993 | 25.0095
SJOW4 M1 | 400 | 118.2047 | 39.2533 | 27.724 | 83.2366 | 137.6771 | 50.3761 | 31.9574 | 103.2
SJOW4 M2 | 400 | 118.2047 | 39.2533 | 27.724 | 83.2366 | 137.6771 | 50.3761 | 31.9574 | 103.2
SJOW4 M3 | 400 | 118.2047 | 39.2533 | 27.724 | 83.2366 | 137.6771 | 50.3761 | 31.9574 | 103.2
SJOW4 M4 | 400 | 118.2047 | 39.2533 | 27.724 | 83.2366 | 137.6771 | 50.3761 | 31.9574 | 103.2
SJOW4 R1/2 | 400 | 118.2047 | 39.2533 | 27.724 | 83.2366 | 137.6771 | 50.3761 | 31.9574 | 103.2
SJOW4 R3/4 | 400 | 118.2047 | 39.2533 | 27.724 | 83.2366 | 137.6771 | 50.3761 | 31.9574 | 103.2
SKLG2 MC1 | 275 | 58.1502 | 21.4583 | 17.7052 | 48.0518 | 55.8698 | 21.7546 | 15.8205 | 46.5862
SKLG2 MC2 | 275 | 58.1502 | 21.4583 | 17.7052 | 48.0518 | 55.8698 | 21.7546 | 15.8205 | 46.5862
SKLG2 MC3 | 275 | 58.1502 | 21.4583 | 17.7052 | 48.0518 | 55.8698 | 21.7546 | 15.8205 | 46.5862
SKLG2 MC4 | 275 | 58.1502 | 21.4583 | 17.7052 | 48.0518 | 55.8698 | 21.7546 | 15.8205 | 46.5862
SMAN2 MC1 | 275 | 74.8843 | 27.7865 | 22.5926 | 61.8887 | 73.8662 | 28.8263 | 20.5287 | 61.2952
SMAN2 MC2 | 275 | 74.8843 | 27.7865 | 22.5926 | 61.8887 | 73.8662 | 28.8263 | 20.5287 | 61.2952
SMAN2 MC3 | 275 | 74.8843 | 27.7865 | 22.5926 | 61.8887 | 73.8662 | 28.8263 | 20.5287 | 61.2952
SMAN2 MC4 | 275 | 74.8843 | 27.7865 | 22.5926 | 61.8887 | 73.8662 | 28.8263 | 20.5287 | 61.2952
SPEN4 MC3 | 400 | 63.673 | 22.4974 | 13.4564 | 45.2726 | 48.3241 | 18.6578 | 8.8565 | 35.2426
SPEN4 MC4 | 400 | 63.673 | 22.4974 | 13.4564 | 45.2726 | 48.3241 | 18.6578 | 8.8565 | 35.2426
SPEN41 MC1 | 400 | 63.6543 | 22.492 | 13.4632 | 45.2717 | 48.9161 | 18.8608 | 9.0993 | 35.7725
SPEN41 MC2 | 400 | 63.6543 | 22.492 | 13.4632 | 45.2717 | 48.9161 | 18.8608 | 9.0993 | 35.7725
SPLN4 M1 | 400 | 91.1925 | 31.1181 | 25.1269 | 69.1346 | 68.7548 | 25.9087 | 17.9729 | 54.6133
SPLN4 R1 | 400 | 91.1925 | 31.1181 | 25.1269 | 69.1346 | 68.7548 | 25.9087 | 17.9729 | 54.6133
SSHI2 MC1 | 275 | 63.9038 | 22.8729 | 11.9445 | 44.2917 | 57.1668 | 22.4542 | 9.4063 | 41.1614
SSHI2 MC2 | 275 | 63.9038 | 22.8729 | 11.9445 | 44.2917 | 57.1668 | 22.4542 | 9.4063 | 41.1614
STAL2 M1 | 275 | 81.6724 | 29.8572 | 15.9436 | 58.168 | 75.9328 | 29.5928 | 14.4313 | 56.2819
STAL2 M2 | 275 | 81.6724 | 29.8572 | 15.9436 | 58.168 | 75.9328 | 29.5928 | 14.4313 | 56.2819
STAL2 R1 | 275 | 81.6724 | 29.8572 | 15.9436 | 58.168 | 75.9328 | 29.5928 | 14.4313 | 56.2819
STAL2 R2 | 275 | 81.6724 | 29.8572 | 15.9436 | 58.168 | 75.9328 | 29.5928 | 14.4313 | 56.2819
STAL4 MC1 | 400 | 36.432 | 13.3782 | 9.4388 | 28.3583 | 32.4678 | 12.5466 | 8.0386 | 25.7822
STAL4 MC2 | 400 | 51.0014 | 19.2049 | 9.8114 | 36.9713 | 38.9997 | 15.4964 | 6.3412 | 28.2563
STAY4 M1 | 400 | 110.8686 | 39.8821 | 25.7272 | 82.129 | 103.3084 | 39.1885 | 26.5255 | 81.9464
STAY4 M2 | 400 | 110.8686 | 39.8821 | 25.7272 | 82.129 | 103.3084 | 39.1885 | 26.5255 | 81.9464
STAY4 R1 | 400 | 110.8686 | 39.8821 | 25.7272 | 82.129 | 103.3084 | 39.1885 | 26.5255 | 81.9464
STAY4 R2 | 400 | 110.8686 | 39.8821 | 25.7272 | 82.129 | 103.3084 | 39.1885 | 26.5255 | 81.9464
STAY4A | 400 | 73.7791 | 26.853 | 20.2153 | 58.1912 | 66.6801 | 25.2033 | 19.2375 | 54.8804
STEN1 M1 | 132 | 55.0759 | 19.2996 | 19.3066 | 46.6003 | 67.57 | 24.8673 | 22.8282 | 57.9959
STEN1 M2 | 132 | 55.0759 | 19.2996 | 19.3066 | 46.6003 | 67.57 | 24.8673 | 22.8282 | 57.9959
STEN1 R1 | 132 | 55.0759 | 19.2996 | 19.3066 | 46.6003 | 67.57 | 24.8673 | 22.8282 | 57.9959
STEN1 R2 | 132 | 55.0759 | 19.2996 | 19.3066 | 46.6003 | 67.57 | 24.8673 | 22.8282 | 57.9959
STES1 M1 | 132 | 55.321 | 18.8286 | 15.3206 | 41.9482 | 67.5464 | 24.566 | 17.4416 | 52.1831
STES1 M2 | 132 | 55.321 | 18.8286 | 15.3206 | 41.9482 | 67.5464 | 24.566 | 17.4416 | 52.1831
STES1 R1 | 132 | 55.321 | 18.8286 | 15.3206 | 41.9482 | 67.5464 | 24.566 | 17.4416 | 52.1831
STES1 R2 | 132 | 55.321 | 18.8286 | 15.3206 | 41.9482 | 67.5464 | 24.566 | 17.4416 | 52.1831
STEW2 M1 | 275 | 81.5766 | 29.601 | 25.2521 | 67.1142 | 76.5606 | 29.2767 | 23.2569 | 64.6604
STEW2 M2 | 275 | 81.5766 | 29.601 | 25.2521 | 67.1142 | 76.5606 | 29.2767 | 23.2569 | 64.6604
STEW2 R1 | 275 | 81.5766 | 29.601 | 25.2521 | 67.1142 | 76.5606 | 29.2767 | 23.2569 | 64.6604
STEW2 R2 | 275 | 81.5766 | 29.601 | 25.2521 | 67.1142 | 76.5606 | 29.2767 | 23.2569 | 64.6604
STEW4 M1 | 400 | 81.2195 | 29.1626 | 24.8251 | 66.0673 | 59.5311 | 23.0118 | 17.28 | 49.8237
STEW4 M2 | 400 | 81.2195 | 29.1626 | 24.8251 | 66.0673 | 59.5311 | 23.0118 | 17.28 | 49.8237
STEW4 R1 | 400 | 81.2195 | 29.1626 | 24.8251 | 66.0673 | 59.5311 | 23.0118 | 17.28 | 49.8237
STEW4 R2a | 400 | 81.2195 | 29.1626 | 24.8251 | 66.0673 | 59.5311 | 23.0118 | 17.28 | 49.8237
STOB4 M1 | 400 | 61.3634 | 23.0635 | 10.7501 | 43.3668 | 49.444 | 19.8293 | 7.5885 | 35.6314
STOB4 R1 | 400 | 61.3634 | 23.0635 | 10.7501 | 43.3668 | 49.444 | 19.8293 | 7.5885 | 35.6314
STSB4 MC1 | 400 | 57.2995 | 21.1461 | 12.5061 | 42.4112 | 45.3177 | 17.8174 | 7.6753 | 32.8729
STSB4 MC2 | 400 | 57.2995 | 21.1461 | 12.5061 | 42.4112 | 45.3177 | 17.8174 | 7.6753 | 32.8729
STSB4A | 400 | 52.9779 | 19.3343 | 5.7765 | 33.1193 | 41.1135 | 16.039 | 3.0858 | 25.7684
SUND4 M1 | 400 | 107.0356 | 38.4467 | 22.5203 | 76.8922 | 89.9769 | 34.8259 | 17.3494 | 66.6007
SUND4 M2 | 400 | 86.5456 | 31.5116 | 18.1397 | 62.7038 | 72.9201 | 28.1918 | 14.5358 | 54.4051
SUND4 R1 | 400 | 107.0356 | 38.4467 | 22.5203 | 76.8922 | 89.9769 | 34.8259 | 17.3494 | 66.6007
SUND4 R2 | 400 | 86.5456 | 31.5116 | 18.1397 | 62.7038 | 72.9201 | 28.1918 | 14.5358 | 54.4051
SUTB4A | 400 | 94.76 | 33.3749 | 22.0317 | 69.231 | 77.5143 | 29.6009 | 18.1708 | 60.0327
SWAN2 MC3 | 275 | 25.9097 | 9.406 | 8.47 | 21.7721 | 28.2946 | 10.4786 | 8.815 | 23.634
SWAN2 MC4 | 275 | 25.9097 | 9.406 | 8.47 | 21.7721 | 28.2946 | 10.4786 | 8.815 | 23.634
SWAN4 M1 | 400 | 38.6851 | 14.2899 | 9.1045 | 29.3134 | 33.9751 | 12.9706 | 8.0321 | 26.3753
SWAN4 M2 | 400 | 38.6851 | 14.2899 | 9.1045 | 29.3134 | 33.9751 | 12.9706 | 8.0321 | 26.3753
SWAN4 M3 | 400 | 61.0995 | 22.0296 | 15.3258 | 46.4803 | 59.2141 | 22.4462 | 14.1656 | 45.9093
SWAN4 M4 | 400 | 61.0995 | 22.0296 | 15.3258 | 46.4803 | 59.2141 | 22.4462 | 14.1656 | 45.9093
SWAN4 R3 | 400 | 61.0995 | 22.0296 | 15.3258 | 46.4803 | 59.2141 | 22.4462 | 14.1656 | 45.9093
SWAN4 R4 | 400 | 61.0995 | 22.0296 | 15.3258 | 46.4803 | 59.2141 | 22.4462 | 14.1656 | 45.9093
TAUN4 M1 | 400 | 44.9006 | 16.9657 | 7.3374 | 31.3305 | 38.1045 | 15.2912 | 5.3367 | 26.9617
TAUN4 M2 | 400 | 45.5299 | 17.1671 | 7.4115 | 31.6894 | 39.4332 | 15.7796 | 5.754 | 28.0697
TEMP2 MC1 | 275 | 59.7046 | 22.0261 | 12.2084 | 43.358 | 61.895 | 24.5382 | 10.8622 | 45.5644
TEMP2 MC2 | 275 | 59.7046 | 22.0261 | 12.2084 | 43.358 | 61.895 | 24.5382 | 10.8622 | 45.5644
TEMP2 MC3 | 275 | 59.9946 | 22.1127 | 12.3473 | 43.6194 | 62.7882 | 24.8726 | 11.0847 | 46.2599
THOM2 M1 | 275 | 67.5674 | 24.6097 | 19.2042 | 54.0075 | 69.2936 | 26.2116 | 18.5704 | 55.6392
THOM2 R1 | 275 | 67.5674 | 24.6097 | 19.2042 | 54.0075 | 69.2936 | 26.2116 | 18.5704 | 55.6392
THOM4 MC1 | 400 | 94.4511 | 33.5783 | 23.2527 | 70.7395 | 83.6215 | 32.0395 | 17.3985 | 62.7092
THOM4 MC2 | 400 | 94.4511 | 33.5783 | 23.2527 | 70.7395 | 83.6215 | 32.0395 | 17.3985 | 62.7092
THOM4 MC3 | 400 | 94.4511 | 33.5783 | 23.2527 | 70.7395 | 83.6215 | 32.0395 | 17.3985 | 62.7092
THOM4 MC4 | 400 | 94.4511 | 33.5783 | 23.2527 | 70.7395 | 83.6215 | 32.0395 | 17.3985 | 62.7092
THOM4 R2(2) | 400 | 92.4693 | 33.423 | 19.9633 | 67.2305 | 79.4872 | 30.6647 | 15.7187 | 59.0851
THOM4 R2(3) | 400 | 92.4693 | 33.423 | 19.9633 | 67.2305 | 79.4872 | 30.6647 | 15.7187 | 59.0851
THOM42 M5 | 400 | 92.4693 | 33.423 | 19.9633 | 67.2305 | 79.4872 | 30.6647 | 15.7187 | 59.0851
THTO4 M1 | 400 | 110.8162 | 37.8967 | 30.56 | 84.1541 | 80.7435 | 30.9251 | 15.6667 | 59.4014
THTO4 M2 | 400 | 95.1905 | 32.2731 | 27.6039 | 73.245 | 70.1299 | 26.5258 | 15.3813 | 52.8944
THTO4 M3 | 400 | 95.1905 | 32.2731 | 27.6039 | 73.245 | 70.1299 | 26.5258 | 15.3813 | 52.8944
THTO4 M4 | 400 | 110.8162 | 37.8967 | 30.56 | 84.1541 | 80.7435 | 30.9251 | 15.6667 | 59.4014
THTO4 R1/2 | 400 | 79.2313 | 28.2325 | 21.1333 | 61.0601 | 65.7619 | 25.072 | 14.3469 | 49.804
THTO4 R3/4 | 400 | 79.2313 | 28.2325 | 21.1333 | 61.0601 | 65.7619 | 25.072 | 14.3469 | 49.804
THUR2 MC1 | 275 | 64.7208 | 24.3399 | 10.5051 | 44.9269 | 65.4062 | 25.9165 | 10.8328 | 47.4842
THUR2 MC2 | 275 | 64.7208 | 24.3399 | 10.5051 | 44.9269 | 65.4062 | 25.9165 | 10.8328 | 47.4842
THUR2 MC3 | 275 | 64.7208 | 24.3399 | 10.5051 | 44.9269 | 65.4062 | 25.9165 | 10.8328 | 47.4842
THUR2 MC4 | 275 | 64.7208 | 24.3399 | 10.5051 | 44.9269 | 65.4062 | 25.9165 | 10.8328 | 47.4842
TILB2 M1 | 275 | 71.4594 | 25.4646 | 20.9949 | 57.0072 | 75.1409 | 28.0431 | 21.1305 | 60.7894
TILB2 M2 | 275 | 71.4594 | 25.4646 | 20.9949 | 57.0072 | 75.1409 | 28.0431 | 21.1305 | 60.7894
TILB2 R1 | 275 | 71.4594 | 25.4646 | 20.9949 | 57.0072 | 75.1409 | 28.0431 | 21.1305 | 60.7894
TILB2 R2 | 275 | 71.4594 | 25.4646 | 20.9949 | 57.0072 | 75.1409 | 28.0431 | 21.1305 | 60.7894
TILB4 M2 | 400 | 138.8221 | 48.7999 | 42.8187 | 111.8322 | 122.8273 | 47.2049 | 34.2862 | 101.044
TILB4 M3 | 400 | 138.8221 | 48.7999 | 42.8187 | 111.8322 | 122.8273 | 47.2049 | 34.2862 | 101.044
TILB4 R2 | 400 | 138.8221 | 48.7999 | 42.8187 | 111.8322 | 122.8273 | 47.2049 | 34.2862 | 101.044
TILB4 R3 | 400 | 138.8221 | 48.7999 | 42.8187 | 111.8322 | 122.8273 | 47.2049 | 34.2862 | 101.044
TINP2 M1 | 275 | 58.1684 | 21.1874 | 6.8488 | 36.8124 | 56.3472 | 21.922 | 5.4588 | 36.4611
TINP2 M2 | 275 | 58.3364 | 21.1981 | 6.8617 | 36.8404 | 57.2746 | 22.2577 | 5.5519 | 37.0291
TODP2 MC1 | 275 | 60.3173 | 20.5858 | 15.2621 | 44.3748 | 54.9072 | 20.7999 | 11.0412 | 40.4567
TODP2 MC2 | 275 | 60.3173 | 20.5858 | 15.2621 | 44.3748 | 54.9072 | 20.7999 | 11.0412 | 40.4567
TOTE2A | 275 | 71.0215 | 25.2446 | 19.5006 | 55.2018 | 72.7132 | 27.4754 | 16.8746 | 55.7307
TOTE2B | 275 | 72.8571 | 25.8628 | 19.7474 | 56.3229 | 73.532 | 27.8186 | 16.847 | 56.1884
TOTT2 MC1 | 275 | 41.8303 | 15.8312 | 12.3107 | 34.6995 | 42.9414 | 16.7312 | 12.0134 | 35.6749
TOTT2 MC2A | 275 | 43.9422 | 16.5904 | 12.9701 | 36.4324 | 40.065 | 15.7398 | 10.9631 | 33.2226
TOTT2 MC2B | 275 | 72.8571 | 25.8628 | 19.7474 | 56.3229 | 73.532 | 27.8186 | 16.847 | 56.1884
TOTT2 MC3 | 275 | 43.9422 | 16.5904 | 12.9701 | 36.4324 | 40.065 | 15.7398 | 10.9631 | 33.2226
TOTT2 MC4A | 275 | 41.8303 | 15.8312 | 12.3107 | 34.6995 | 42.9414 | 16.7312 | 12.0134 | 35.6749
TOTT2 MC4B | 275 | 71.0215 | 25.2446 | 19.5006 | 55.2018 | 72.7132 | 27.4754 | 16.8746 | 55.7307
TOTT2 MC5 | 275 | 72.8571 | 25.8628 | 19.7474 | 56.3229 | 73.532 | 27.8186 | 16.847 | 56.1884
TOTT2 MC6 | 275 | 72.8571 | 25.8628 | 19.7474 | 56.3229 | 73.532 | 27.8186 | 16.847 | 56.1884
TOTT2 MC7 | 275 | 71.0215 | 25.2446 | 19.5006 | 55.2018 | 72.7132 | 27.4754 | 16.8746 | 55.7307
TOTT2 MC8 | 275 | 71.0215 | 25.2446 | 19.5006 | 55.2018 | 72.7132 | 27.4754 | 16.8746 | 55.7307
TRAW2 M1 | 275 | 43.5248 | 15.6184 | 13.1589 | 35.2467 | 45.8986 | 17.1671 | 12.301 | 36.579
TRAW2 M2 | 275 | 43.5248 | 15.6184 | 13.1589 | 35.2467 | 45.8986 | 17.1671 | 12.301 | 36.579
TRAW2 R1 | 275 | 43.5248 | 15.6184 | 13.1589 | 35.2467 | 45.8986 | 17.1671 | 12.301 | 36.579
TRAW2 R2 | 275 | 43.5248 | 15.6184 | 13.1589 | 35.2467 | 45.8986 | 17.1671 | 12.301 | 36.579
TRAW4 MC1 | 400 | 55.3694 | 20.5965 | 16.7097 | 45.8376 | 45.5834 | 18.0211 | 11.9803 | 37.466
TRAW4 MC2 | 400 | 55.3694 | 20.5965 | 16.7097 | 45.8376 | 45.5834 | 18.0211 | 11.9803 | 37.466
TRAW4 MC3 | 400 | 55.3694 | 20.5965 | 16.7097 | 45.8376 | 45.5834 | 18.0211 | 11.9803 | 37.466
TRAW4 MC4 | 400 | 55.3694 | 20.5965 | 16.7097 | 45.8376 | 45.5834 | 18.0211 | 11.9803 | 37.466
TREM2 MC1 | 275 | 46.477 | 17.0169 | 2.6708 | 26.7364 | 41.1588 | 16.3359 | 2.3529 | 25.4554
TREM2 MC2 | 275 | 46.477 | 17.0169 | 2.6708 | 26.7364 | 41.1588 | 16.3359 | 2.3529 | 25.4554
TREU4A | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.2567 | 26.5919 | 4.1063 | 41.7129
TREU4A_DEES1 | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.2567 | 26.5919 | 4.1063 | 41.7129
TREU4A_LEGA1 | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.2567 | 26.5919 | 4.1063 | 41.7129
TREU4A_TRAW1 | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.2567 | 26.5919 | 4.1063 | 41.7129
TREU4B | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.4601 | 26.6695 | 4.1186 | 41.8349
TREU4B_DEES2 | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.4601 | 26.6695 | 4.1186 | 41.8349
TREU4B_LEGA2 | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.4601 | 26.6695 | 4.1186 | 41.8349
TREU4B_TRAW2 | 400 | 79.7081 | 28.1247 | 7.5057 | 47.2801 | 68.4601 | 26.6695 | 4.1186 | 41.8349
TYNE2 MC1 | 275 | 59.5935 | 21.5184 | 10.8024 | 41.234 | 53.1615 | 20.8051 | 9.1939 | 38.6168
TYNE2 MC2 | 275 | 59.5935 | 21.5184 | 10.8024 | 41.234 | 53.1615 | 20.8051 | 9.1939 | 38.6168
TYNE2A | 275 | 58.8966 | 20.8368 | 3.8832 | 33.3509 | 50.1538 | 19.7029 | 2.7857 | 30.6499
UPPB2 MC1 | 275 | 39.3226 | 14.6593 | 9.7666 | 30.498 | 38.4875 | 14.9067 | 8.5271 | 29.6084
UPPB2 MC2 | 275 | 41.8075 | 15.5499 | 10.1309 | 32.1217 | 40.2739 | 15.5725 | 8.977 | 30.9998
UPPB2 MC3 | 275 | 41.8075 | 15.5499 | 10.1309 | 32.1217 | 40.2739 | 15.5725 | 8.977 | 30.9998
UPPB2 MC4 | 275 | 39.3226 | 14.6593 | 9.7666 | 30.498 | 38.4875 | 14.9067 | 8.5271 | 29.6084
USKM2 M1 | 275 | 76.7148 | 27.1862 | 19.515 | 57.9621 | 86.5925 | 32.3801 | 22.7155 | 68.508
USKM2 M2 | 275 | 76.7148 | 27.1862 | 19.515 | 57.9621 | 86.5925 | 32.3801 | 22.7155 | 68.508
USKM2 R1 | 275 | 76.7148 | 27.1862 | 19.515 | 57.9621 | 86.5925 | 32.3801 | 22.7155 | 68.508
USKM2 R2 | 275 | 76.7148 | 27.1862 | 19.515 | 57.9621 | 86.5925 | 32.3801 | 22.7155 | 68.508
USKM2A | 275 | 74.3682 | 25.7221 | 11.172 | 47.5486 | 81.9755 | 30.5531 | 11.8521 | 55.0608
WALH4 MC1 | 400 | 59.9462 | 22.2936 | 11.4878 | 43.0158 | 50.9231 | 19.93 | 10.4181 | 38.6034
WALH4 MC2 | 400 | 59.9462 | 22.2936 | 11.4878 | 43.0158 | 50.9231 | 19.93 | 10.4181 | 38.6034
WALH4 MC3 | 400 | 59.9462 | 22.2936 | 11.4878 | 43.0158 | 50.9231 | 19.93 | 10.4181 | 38.6034
WALH4 MC4 | 400 | 59.9462 | 22.2936 | 11.4878 | 43.0158 | 50.9231 | 19.93 | 10.4181 | 38.6034
WALP R4 | 132 | 69.2672 | 24.335 | 20.791 | 55.2059 | 83.6724 | 31.9624 | 22.7071 | 67.9088
WALP1 M4 | 132 | 69.2672 | 24.335 | 20.791 | 55.2059 | 83.6724 | 31.9624 | 22.7071 | 67.9088
WALP4 M1 | 400 | 115.7983 | 39.7204 | 30.2516 | 86.4247 | 94.838 | 35.6775 | 24.5933 | 75.0489
WALP4 M2 | 400 | 115.7983 | 39.7204 | 30.2516 | 86.4247 | 94.838 | 35.6775 | 24.5933 | 75.0489
WALP4 R1 | 400 | 115.7983 | 39.7204 | 30.2516 | 86.4247 | 94.838 | 35.6775 | 24.5933 | 75.0489
WALP4 R2 | 400 | 115.7983 | 39.7204 | 30.2516 | 86.4247 | 94.838 | 35.6775 | 24.5933 | 75.0489
WALPM3 | 132 | 69.2672 | 24.335 | 20.791 | 55.2059 | 83.6724 | 31.9624 | 22.7071 | 67.9088
WALPR3 | 132 | 69.2672 | 24.335 | 20.791 | 55.2059 | 83.6724 | 31.9624 | 22.7071 | 67.9088
WALX2 M1 | 275 | 73.473 | 25.9097 | 16.3554 | 52.9972 | 77.239 | 28.7649 | 15.8581 | 56.5378
WALX2 M2 | 275 | 75.7495 | 26.6171 | 16.892 | 54.5342 | 81.4628 | 30.2134 | 16.9669 | 59.695
WALX2 R1 | 275 | 73.473 | 25.9097 | 16.3554 | 52.9972 | 77.239 | 28.7649 | 15.8581 | 56.5378
WALX2 R2 | 275 | 75.7495 | 26.6171 | 16.892 | 54.5342 | 81.4628 | 30.2134 | 16.9669 | 59.695
WALX4A | 400 | 65.5335 | 23.2063 | 8.52 | 41.3388 | 66.4157 | 24.8299 | 9.1897 | 44.3045
WALX4B | 400 | 65.4279 | 23.194 | 8.5641 | 41.3654 | 61.0848 | 22.9137 | 8.5882 | 40.9931
WARL2 MC1 | 275 | 64.897 | 23.5102 | 15.3344 | 48.5829 | 60.2181 | 23.3896 | 11.2959 | 44.3738
WARL2 MC2 | 275 | 64.897 | 23.5102 | 15.3344 | 48.5829 | 60.2181 | 23.3896 | 11.2959 | 44.3738
WARL2 MC3 | 275 | 64.897 | 23.5102 | 15.3344 | 48.5829 | 60.2181 | 23.3896 | 11.2959 | 44.3738
WARL2 MC4 | 275 | 64.897 | 23.5102 | 15.3344 | 48.5829 | 60.2181 | 23.3896 | 11.2959 | 44.3738
WASF2A | 275 | 52.7115 | 19.198 | 11.5343 | 38.6844 | 46.4531 | 18.1341 | 7.9748 | 33.6204
WASF2B | 275 | 56.9526 | 20.6109 | 12.3821 | 41.5303 | 52.4841 | 20.5125 | 8.6541 | 37.6631
WBOL2 MC1 | 275 | 72.0817 | 25.3553 | 14.5113 | 50.3691 | 63.7111 | 24.8898 | 10.6569 | 45.8563
WBOL2 MC2 | 275 | 72.0817 | 25.3553 | 14.5113 | 50.3691 | 63.7111 | 24.8898 | 10.6569 | 45.8563
WBOL2 MC3 | 275 | 72.0817 | 25.3553 | 14.5113 | 50.3691 | 63.7111 | 24.8898 | 10.6569 | 45.8563
WBOL2 MC4 | 275 | 72.0817 | 25.3553 | 14.5113 | 50.3691 | 63.7111 | 24.8898 | 10.6569 | 45.8563
WBUR1 M1 | 132 | 21.2054 | 7.5234 | 6.7221 | 17.3618 | 24.7306 | 9.1533 | 8.0288 | 20.9734
WBUR1 M2 | 132 | 21.2054 | 7.5234 | 6.7221 | 17.3618 | 24.7306 | 9.1533 | 8.0288 | 20.9734
WBUR1 R1 | 132 | 21.2054 | 7.5234 | 6.7221 | 17.3618 | 24.7306 | 9.1533 | 8.0288 | 20.9734
WBUR1 R2 | 132 | 20.9847 | 7.4638 | 6.618 | 17.1735 | 24.5713 | 9.0935 | 7.9384 | 20.7986
WBUR4 M1 | 400 | 113.6531 | 39.5424 | 32.8271 | 88.7484 | 101.721 | 37.7791 | 29.4071 | 82.8348
WBUR4 M2 | 400 | 113.6531 | 39.5424 | 32.8271 | 88.7484 | 101.721 | 37.7791 | 29.4071 | 82.8348
WBUR4 M3 | 400 | 113.6531 | 39.5424 | 32.8271 | 88.7484 | 101.721 | 37.7791 | 29.4071 | 82.8348
WBUR4 M4 | 400 | 113.6531 | 39.5424 | 32.8271 | 88.7484 | 101.721 | 37.7791 | 29.4071 | 82.8348
WBUR4 R1/2 | 400 | 110.1004 | 39.2103 | 27.7074 | 83.1591 | 88.7068 | 33.8745 | 21.519 | 69.4249
WBUR4 R3/4 | 400 | 110.1004 | 39.2103 | 27.7074 | 83.1591 | 88.7068 | 33.8745 | 21.519 | 69.4249
WHAM4 M1 | 400 | 123.0082 | 42.8761 | 37.8542 | 98.4901 | 136.7065 | 52.013 | 38.2807 | 111.8382
WHAM4 M2 | 400 | 123.0082 | 42.8761 | 37.8542 | 98.4901 | 136.7065 | 52.013 | 38.2807 | 111.8382
WHAM4 R1 | 400 | 123.0082 | 42.8761 | 37.8542 | 98.4901 | 136.7065 | 52.013 | 38.2807 | 111.8382
WHAM4 R2 | 400 | 123.0082 | 42.8761 | 37.8542 | 98.4901 | 136.7065 | 52.013 | 38.2807 | 111.8382
WHAM4A | 400 | 98.7683 | 32.3324 | 12.3795 | 58.1044 | 102.0411 | 39.1948 | 14.869 | 70.2989
WHAM4B | 400 | 98.8418 | 32.3524 | 12.3802 | 58.1334 | 102.1396 | 39.233 | 14.8698 | 70.3536
WHGA2 MC1 | 275 | 69.2953 | 25.1517 | 14.6962 | 50.266 | 65.4471 | 25.5464 | 11.8017 | 47.9297
WHGA2 MC2 | 275 | 69.2953 | 25.1517 | 14.6962 | 50.266 | 65.4471 | 25.5464 | 11.8017 | 47.9297
WHGA2 MC3 | 275 | 69.2953 | 25.1517 | 14.6962 | 50.266 | 65.4471 | 25.5464 | 11.8017 | 47.9297
WHGA2 MC4 | 275 | 69.2953 | 25.1517 | 14.6962 | 50.266 | 65.4471 | 25.5464 | 11.8017 | 47.9297
WHSO2 M1 | 275 | 67.1211 | 24.2066 | 14.8945 | 49.1278 | 72.324 | 27.5708 | 15.5729 | 54.5638
WHSO2 M2 | 275 | 67.1211 | 24.2066 | 14.8945 | 49.1278 | 72.324 | 27.5708 | 15.5729 | 54.5638
WHSO2 R1 | 275 | 73.5116 | 26.2436 | 18.7314 | 55.8455 | 80.3468 | 30.2924 | 19.8592 | 62.6991
WHSO2 R2 | 275 | 73.5116 | 26.2436 | 18.7314 | 55.8455 | 80.3468 | 30.2924 | 19.8592 | 62.6991
WIBA2 MC1 | 275 | 59.6953 | 22.0241 | 12.1974 | 43.3442 | 63.1004 | 25.247 | 10.2189 | 45.9236
WIBA2 MC1 | 275 | 59.6953 | 22.0241 | 12.1974 | 43.3442 | 63.1004 | 25.247 | 10.2189 | 45.9236
WIBA2 MC2 | 275 | 59.6953 | 22.0241 | 12.1974 | 43.3442 | 63.1004 | 25.247 | 10.2189 | 45.9236
WIBA2 MC2 | 275 | 59.6953 | 22.0241 | 12.1974 | 43.3442 | 63.1004 | 25.247 | 10.2189 | 45.9236
WILE4 M1 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 M1 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 M2 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 M2 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 R1 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 R1 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 R2 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILE4 R2 | 400 | 98.8077 | 36.7751 | 26.4433 | 78.4511 | 83.9719 | 33.3866 | 21.3817 | 68.5974
WILL1 M2 | 132 | 52.5573 | 18.3967 | 16.1433 | 42.1602 | 59.0605 | 22.4442 | 18.3428 | 50.0837
WILL1 R1 | 132 | 36.383 | 13.47 | 10.9119 | 29.9613 | 39.6654 | 15.3191 | 12.3012 | 33.9657
WILL1 R2 | 132 | 52.5573 | 18.3967 | 16.1433 | 42.1602 | 59.0605 | 22.4442 | 18.3428 | 50.0837
WILL2 M2 | 275 | 23.8785 | 8.5367 | 8.7573 | 20.83 | 25.2979 | 9.2437 | 9.0285 | 22.1011
WILL2 M2 | 275 | 23.8785 | 8.5367 | 8.7573 | 20.83 | 25.2979 | 9.2437 | 9.0285 | 22.1011
WILL2 R2 | 275 | 23.8785 | 8.5367 | 8.7573 | 20.83 | 25.2979 | 9.2437 | 9.0285 | 22.1011
WILL2 R2 | 275 | 23.8785 | 8.5367 | 8.7573 | 20.83 | 25.2979 | 9.2437 | 9.0285 | 22.1011
WILT2A | 275 | 61.3681 | 20.1973 | 13.6646 | 42.2279 | 58.7231 | 21.2748 | 9.9644 | 40.0516
WILT2A | 275 | 61.3681 | 20.1973 | 13.6646 | 42.2279 | 58.7231 | 21.2748 | 9.9644 | 40.0516
WILT2B | 275 | 61.3704 | 20.198 | 13.6644 | 42.2288 | 58.7255 | 21.2757 | 9.9642 | 40.0526
WILT2B | 275 | 61.3704 | 20.198 | 13.6644 | 42.2288 | 58.7255 | 21.2757 | 9.9642 | 40.0526
WILT2C | 275 | 61.7996 | 20.3123 | 13.94 | 42.6659 | 59.73 | 21.5683 | 10.7481 | 41.2502
WILT2C | 275 | 61.7996 | 20.3123 | 13.94 | 42.6659 | 59.73 | 21.5683 | 10.7481 | 41.2502
WILT2D | 275 | 61.7972 | 20.3117 | 13.9391 | 42.6642 | 59.725 | 21.5667 | 10.746 | 41.2459
WILT2D | 275 | 61.7972 | 20.3117 | 13.9391 | 42.6642 | 59.725 | 21.5667 | 10.746 | 41.2459
WIMB4 MB2 | 400 | 96.7821 | 32.7638 | 23.0056 | 69.3407 | 112.0395 | 42.2052 | 23.0005 | 82.6877
WIMB4 MB2 | 400 | 96.7821 | 32.7638 | 23.0056 | 69.3407 | 112.0395 | 42.2052 | 23.0005 | 82.6877
WIMB4 RB2 | 400 | 96.7821 | 32.7638 | 23.0056 | 69.3407 | 112.0395 | 42.2052 | 23.0005 | 82.6877
WIMB4 RB2 | 400 | 96.7821 | 32.7638 | 23.0056 | 69.3407 | 112.0395 | 42.2052 | 23.0005 | 82.6877
WISD2 M1 | 275 | 69.4766 | 24.0431 | 22.1102 | 56.1123 | 81.0776 | 29.8977 | 24.6894 | 66.971
WISD2 M2 | 275 | 69.4766 | 24.0431 | 22.1102 | 56.1123 | 81.0776 | 29.8977 | 24.6894 | 66.971
WISD2 R1 | 275 | 69.4766 | 24.0431 | 22.1102 | 56.1123 | 81.0776 | 29.8977 | 24.6894 | 66.971
WISD2 R2 | 275 | 69.4766 | 24.0431 | 22.1102 | 56.1123 | 81.0776 | 29.8977 | 24.6894 | 66.971
WISD2A | 275 | 59.2837 | 20.5302 | 12.0674 | 41.1015 | 64.9835 | 24.8021 | 13.4024 | 48.4778
WISD2B | 275 | 59.2837 | 20.5302 | 12.0674 | 41.1015 | 64.9835 | 24.8021 | 13.4024 | 48.4778
WISD6 M1 | 66 | 50.874 | 17.2337 | 17.1842 | 41.5564 | 33.4666 | 12.5611 | 10.7473 | 28.5113
WISD6 M2 | 66 | 50.874 | 17.2337 | 17.1842 | 41.5564 | 33.4666 | 12.5611 | 10.7473 | 28.5113
WISD6 R1 | 66 | 50.874 | 17.2337 | 17.1842 | 41.5564 | 33.4666 | 12.5611 | 10.7473 | 28.5113
WISD6 R2 | 66 | 50.874 | 17.2337 | 17.1842 | 41.5564 | 33.4666 | 12.5611 | 10.7473 | 28.5113
WMEL2 MC1 | 275 | 78.573 | 28.741 | 14.4482 | 55.0941 | 74.4781 | 29.3705 | 11.9705 | 53.5066
WMEL2 MC2 | 275 | 78.573 | 28.741 | 14.4482 | 55.0941 | 74.4781 | 29.3705 | 11.9705 | 53.5066
WMEL2 MC3 | 275 | 78.573 | 28.741 | 14.4482 | 55.0941 | 74.4781 | 29.3705 | 11.9705 | 53.5066
WMEL2 MC4 | 275 | 78.573 | 28.741 | 14.4482 | 55.0941 | 74.4781 | 29.3705 | 11.9705 | 53.5066
WTHU4A | 400 | 93.3995 | 31.8032 | 7.866 | 52.8426 | 74.781 | 29.1525 | 4.7496 | 45.9775
WTHU4B | 400 | 93.3995 | 31.8032 | 7.866 | 52.8426 | 76.4342 | 29.7678 | 4.8546 | 46.9526
WWEY2 M1 | 275 | 72.3073 | 26.2552 | 17.8329 | 54.9633 | 71.1612 | 27.1756 | 16.7103 | 55.1424
WWEY2 M2 | 275 | 72.3073 | 26.2552 | 17.8329 | 54.9633 | 71.1612 | 27.1756 | 16.7103 | 55.1424
WWEY2 R1 | 275 | 73.53 | 26.8373 | 16.4263 | 54.38 | 73.365 | 28.134 | 16.5159 | 56.3034
WWEY2 R2 | 275 | 73.53 | 26.8373 | 16.4263 | 54.38 | 73.365 | 28.134 | 16.5159 | 56.3034
WWEY4A | 400 | 50.2104 | 18.3141 | 6.2434 | 32.1435 | 44.8946 | 17.2239 | 6.1238 | 30.482
WWEY4B | 400 | 50.6503 | 18.4473 | 6.4351 | 32.5236 | 44.7998 | 17.2496 | 6.3233 | 30.7179
WYLF1 M1 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 M1 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 M2 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 M2 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 R1 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 R1 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 R2 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF1 R2 | 132 | 26.9863 | 9.4202 | 7.715 | 21.0371 | 29.9528 | 10.9985 | 8.4708 | 24.025
WYLF4 M1 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 M1 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 M2 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 M2 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 R1 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 R1 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 R2 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYLF4 R2 | 400 | 47.4444 | 17.1367 | 11.6631 | 35.8981 | 36.0897 | 14.0663 | 7.0006 | 26.8934
WYMO4 M1 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 M1 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 M2 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 M2 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 R1 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 R1 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 R2 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937
WYMO4 R2 | 400 | 102.5993 | 36.861 | 21.8297 | 73.9591 | 89.5434 | 34.4859 | 17.6233 | 66.3937

## D3.7
ETYS 19 Yr 10 - NGET Fault Levels (kA), Winter 2028/29
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 40.6974 | 15.0302 | 3.0994 | 24.3553 | 35.8548 | 14.0861 | 2.2517 | 22.1725 | Back To Menu
ABHA4B | 400 | 40.6705 | 15.017 | 3.0983 | 24.3356 | 35.849 | 14.0817 | 2.2467 | 22.1613
ABTH1 M1 | 132 | 28.1643 | 10.5739 | 6.1504 | 21.1042 | 27.0598 | 10.6718 | 6.1346 | 21.2268
ABTH1 M2 | 132 | 25.746 | 10.0125 | 7.6501 | 21.81 | 22.7664 | 9.1157 | 6.6945 | 19.5861
ABTH1 R1 | 132 | 28.4558 | 10.9603 | 7.6928 | 23.193 | 31.2417 | 12.3206 | 8.8219 | 26.2459
ABTH1 R2 | 132 | 28.4558 | 10.9603 | 7.6928 | 23.193 | 31.2417 | 12.3206 | 8.8219 | 26.2459
ABTH2 M1 | 275 | 48.6004 | 18.1185 | 8.8457 | 34.4691 | 43.8773 | 17.3742 | 7.2872 | 31.858
ABTH2 M2 | 275 | 48.6004 | 18.1185 | 8.8457 | 34.4691 | 43.8773 | 17.3742 | 7.2872 | 31.858
ABTH2 M4 | 275 | 48.6004 | 18.1185 | 8.8457 | 34.4691 | 43.8773 | 17.3742 | 7.2872 | 31.858
ABTH2 R | 275 | 40.0169 | 15.1471 | 4.4957 | 25.9169 | 34.0655 | 13.662 | 2.799 | 22.12
ALDW2 MC1 | 275 | 63.2266 | 23.4682 | 9.9095 | 43.0986 | 61.479 | 24.338 | 9.738 | 44.1572
ALDW2 MC2 | 275 | 63.2266 | 23.4682 | 9.9095 | 43.0986 | 61.479 | 24.338 | 9.738 | 44.1572
ALDW2 MC3 | 275 | 63.2266 | 23.4682 | 9.9095 | 43.0986 | 61.479 | 24.338 | 9.738 | 44.1572
ALDW2 MC4 | 275 | 63.2266 | 23.4682 | 9.9095 | 43.0986 | 61.479 | 24.338 | 9.738 | 44.1572
AMEM1 M1 | 132 | 24.5941 | 8.767 | 8.7971 | 21.1955 | 30.3482 | 11.1547 | 10.044 | 25.8192
AMEM1 M2 | 132 | 24.5941 | 8.767 | 8.7971 | 21.1955 | 30.3482 | 11.1547 | 10.044 | 25.8192
AMEM1 R1 | 132 | 24.5941 | 8.767 | 8.7971 | 21.1955 | 30.3482 | 11.1547 | 10.044 | 25.8192
AMEM1 R2 | 132 | 24.5941 | 8.767 | 8.7971 | 21.1955 | 30.3482 | 11.1547 | 10.044 | 25.8192
AMEM4 M | 400 | 47.1697 | 17.4657 | 3.8343 | 28.5344 | 39.7904 | 15.7704 | 2.7022 | 25.005
AMEM4 R | 400 | 48.1595 | 17.8051 | 3.9248 | 29.105 | 39.7245 | 15.6806 | 2.6717 | 24.8474
AXMI4 MC1 | 400 | 42.8903 | 16.0244 | 8.4271 | 31.089 | 35.3751 | 13.8493 | 6.3707 | 25.9565
AXMI4 MC2 | 400 | 42.8903 | 16.0244 | 8.4271 | 31.089 | 35.3751 | 13.8493 | 6.3707 | 25.9565
BAGB2 M1 | 275 | 50.1572 | 18.3248 | 13.0318 | 38.9469 | 48.5625 | 18.5141 | 12.9698 | 39.1527
BAGB2 M2 | 275 | 50.1572 | 18.3248 | 13.0318 | 38.9469 | 48.5625 | 18.5141 | 12.9698 | 39.1527
BAGB2 R1 | 275 | 50.1572 | 18.3248 | 13.0318 | 38.9469 | 48.5625 | 18.5141 | 12.9698 | 39.1527
BAGB2 R2 | 275 | 50.1572 | 18.3248 | 13.0318 | 38.9469 | 48.5625 | 18.5141 | 12.9698 | 39.1527
BARK2 M1 | 275 | 52.8358 | 19.108 | 14.1104 | 41.1331 | 52.6768 | 19.9461 | 13.8224 | 42.0304
BARK2 M2 | 275 | 50.9141 | 18.4263 | 13.8329 | 39.8916 | 52.4217 | 19.788 | 14.2668 | 42.2513
BARK2 R1 | 275 | 52.8358 | 19.108 | 14.1104 | 41.1331 | 52.6768 | 19.9461 | 13.8224 | 42.0304
BARK2 R2 | 275 | 50.9141 | 18.4263 | 13.8329 | 39.8916 | 52.4217 | 19.788 | 14.2668 | 42.2513
BARK4 M1 | 400 | 132.522 | 46.7647 | 40.9411 | 107.0764 | 115.9287 | 45.1938 | 30.8146 | 94.7283
BARK4 M2 | 400 | 132.522 | 46.7647 | 40.9411 | 107.0764 | 115.9287 | 45.1938 | 30.8146 | 94.7283
BARK4 R1 | 400 | 132.522 | 46.7647 | 40.9411 | 107.0764 | 115.9287 | 45.1938 | 30.8146 | 94.7283
BARK4 R2 | 400 | 132.522 | 46.7647 | 40.9411 | 107.0764 | 115.9287 | 45.1938 | 30.8146 | 94.7283
BEDD2 M1/4 | 275 | 57.0754 | 20.7596 | 14.0128 | 43.3714 | 57.0844 | 22.2322 | 13.9713 | 45.4124
BEDD2 M2/3 | 275 | 79.426 | 28.641 | 18.0116 | 58.5161 | 78.3685 | 30.3503 | 17.5004 | 60.4222
BEDD2 R1 | 275 | 51.2281 | 19.0921 | 11.3168 | 38.317 | 50.7816 | 19.6376 | 11.0258 | 38.7977
BEDD2 R2 | 275 | 79.426 | 28.641 | 18.0116 | 58.5161 | 78.3685 | 30.3503 | 17.5004 | 60.4222
BEDD2 R3 | 275 | 79.426 | 28.641 | 18.0116 | 58.5161 | 78.3685 | 30.3503 | 17.5004 | 60.4222
BEDD2 R4 | 275 | 51.2281 | 19.0921 | 11.3168 | 38.317 | 50.7816 | 19.6376 | 11.0258 | 38.7977
BEDD4B | 400 | 43.8045 | 16.4613 | 3.1378 | 26.4177 | 37.6107 | 15.1015 | 3.688 | 25.0447
BESW2 MC1 | 275 | 56.8995 | 20.7251 | 10.3679 | 39.6776 | 49.6483 | 19.6964 | 8.1009 | 35.9559
BESW2 MC2 | 275 | 56.8995 | 20.7251 | 10.3679 | 39.6776 | 49.6483 | 19.6964 | 8.1009 | 35.9559
BESW2 MC3 | 275 | 56.8995 | 20.7251 | 10.3679 | 39.6776 | 49.6483 | 19.6964 | 8.1009 | 35.9559
BESW2 MC4 | 275 | 56.8995 | 20.7251 | 10.3679 | 39.6776 | 49.6483 | 19.6964 | 8.1009 | 35.9559
BICF4A | 400 | 129.121 | 42.8637 | 46.5185 | 107.1368 | 67.4649 | 26.5149 | 17.028 | 54.5257
BICF4B | 400 | 129.121 | 42.8637 | 46.5185 | 107.1368 | 67.4649 | 26.5149 | 17.028 | 54.5257
BIRK2 MC1 | 275 | 56.738 | 20.118 | 14.6959 | 43.1471 | 56.9127 | 21.5125 | 12.6749 | 43.0982
BIRK2 MC2 | 275 | 56.738 | 20.118 | 14.6959 | 43.1471 | 56.9127 | 21.5125 | 12.6749 | 43.0982
BIRK2 MC3 | 275 | 56.738 | 20.118 | 14.6959 | 43.1471 | 56.9127 | 21.5125 | 12.6749 | 43.0982
BIRK2 MC4 | 275 | 56.738 | 20.118 | 14.6959 | 43.1471 | 56.9127 | 21.5125 | 12.6749 | 43.0982
BISW2 MC1 | 275 | 62.3407 | 22.631 | 11.6117 | 43.6168 | 57.7535 | 22.6473 | 9.4226 | 41.4506
BISW2 MC2 | 275 | 62.3407 | 22.631 | 11.6117 | 43.6168 | 57.7535 | 22.6473 | 9.4226 | 41.4506
BISW2 MC3 | 275 | 62.3407 | 22.631 | 11.6117 | 43.6168 | 57.7535 | 22.6473 | 9.4226 | 41.4506
BISW2 MC4 | 275 | 62.3407 | 22.631 | 11.6117 | 43.6168 | 57.7535 | 22.6473 | 9.4226 | 41.4506
BLYT1A | 132 | 32.4496 | 11.5084 | 4.599 | 20.8743 | 33.2177 | 12.5445 | 5.2227 | 22.9633
BLYT1B | 132 | 32.1832 | 11.4446 | 4.5544 | 20.7395 | 33.0294 | 12.4869 | 5.1836 | 22.8427
BLYT2 M1 | 275 | 82.7944 | 30.4148 | 24.6259 | 67.6389 | 74.2783 | 28.7942 | 21.2221 | 61.9432
BLYT2 M2 | 275 | 82.7944 | 30.4148 | 24.6259 | 67.6389 | 74.2783 | 28.7942 | 21.2221 | 61.9432
BLYT2 R1 | 275 | 82.7944 | 30.4148 | 24.6259 | 67.6389 | 74.2783 | 28.7942 | 21.2221 | 61.9432
BLYT2 R2 | 275 | 82.7944 | 30.4148 | 24.6259 | 67.6389 | 74.2783 | 28.7942 | 21.2221 | 61.9432
BODE4 M1 | 400 | 81.2668 | 28.8719 | 18.5974 | 59.4284 | 68.8525 | 26.4514 | 14.8292 | 52.237
BODE4 R1 | 400 | 81.2668 | 28.8719 | 18.5974 | 59.4284 | 68.8525 | 26.4514 | 14.8292 | 52.237
BOLN4 M1 | 400 | 69.9487 | 26.0985 | 20.4051 | 57.3139 | 63.1132 | 24.3667 | 18.9048 | 53.3644
BOLN4 M2 | 400 | 69.9487 | 26.0985 | 20.4051 | 57.3139 | 63.1132 | 24.3667 | 18.9048 | 53.3644
BOLN4 R1 | 400 | 69.9487 | 26.0985 | 20.4051 | 57.3139 | 63.1132 | 24.3667 | 18.9048 | 53.3644
BOLN4 R2 | 400 | 69.9487 | 26.0985 | 20.4051 | 57.3139 | 63.1132 | 24.3667 | 18.9048 | 53.3644
BOTW4 MC1 | 400 | 79.5533 | 28.8087 | 15.3267 | 56.0683 | 63.1175 | 24.5886 | 11.7381 | 46.5117
BOTW4 MC2 | 400 | 79.5533 | 28.8087 | 15.3267 | 56.0683 | 63.1175 | 24.5886 | 11.7381 | 46.5117
BRAI4A | 400 | 62.3351 | 22.7969 | 14.129 | 46.3687 | 43.8597 | 17.2914 | 7.9316 | 32.3853
BRAI4A BRFO | 400 | 62.3351 | 22.7969 | 14.129 | 46.3687 | 43.8597 | 17.2914 | 7.9316 | 32.3853
BRAI4A RAYL | 400 | 62.3351 | 22.7969 | 14.129 | 46.3687 | 43.8597 | 17.2914 | 7.9316 | 32.3853
BRAI4B | 400 | 54.7171 | 20.0939 | 12.566 | 40.9831 | 37.8106 | 14.8985 | 7.0285 | 28.0982
BRAI4B PELH | 400 | 54.7171 | 20.0939 | 12.566 | 40.9831 | 37.8106 | 14.8985 | 7.0285 | 28.0982
BRAI4B RAYL | 400 | 54.7171 | 20.0939 | 12.566 | 40.9831 | 37.8106 | 14.8985 | 7.0285 | 28.0982
BRAW2 MC1 | 275 | 65.7304 | 23.5631 | 15.1 | 48.4233 | 66.1946 | 25.3512 | 14.0191 | 49.871
BRAW2 MC2 | 275 | 65.7304 | 23.5631 | 15.1 | 48.4233 | 66.1946 | 25.3512 | 14.0191 | 49.871
BRAW2 MC3 | 275 | 65.7304 | 23.5631 | 15.1 | 48.4233 | 66.1946 | 25.3512 | 14.0191 | 49.871
BRAW2 MC4 | 275 | 65.7304 | 23.5631 | 15.1 | 48.4233 | 66.1946 | 25.3512 | 14.0191 | 49.871
BRAW4A | 400 | 35.1215 | 12.753 | 4.4622 | 22.4976 | 30.7941 | 11.6871 | 4.2451 | 20.7731
BRED2 MC1 | 275 | 77.9529 | 28.4483 | 15.4566 | 55.6886 | 74.4354 | 29.1351 | 12.6056 | 53.8089
BRED2 MC2 | 275 | 77.9529 | 28.4483 | 15.4566 | 55.6886 | 74.4354 | 29.1351 | 12.6056 | 53.8089
BRED2 MC3 | 275 | 77.9529 | 28.4483 | 15.4566 | 55.6886 | 74.4354 | 29.1351 | 12.6056 | 53.8089
BRED2 MC4 | 275 | 77.9529 | 28.4483 | 15.4566 | 55.6886 | 74.4354 | 29.1351 | 12.6056 | 53.8089
BRFO4 M3 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 M5 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 M6 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 M7 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 R3 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 R5 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 R6 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRFO4 R7 | 400 | 108.998 | 39.158 | 35.074 | 90.4518 | 83.2076 | 32.29 | 23.2778 | 68.9427
BRIM1 M1 | 132 | 51.7205 | 17.4761 | 19.0505 | 43.7654 | 65.4029 | 23.476 | 22.8544 | 56.0545
BRIM1 M2 | 132 | 51.7205 | 17.4761 | 19.0505 | 43.7654 | 65.4029 | 23.476 | 22.8544 | 56.0545
BRIM1 R1 | 132 | 51.7205 | 17.4761 | 19.0505 | 43.7654 | 65.4029 | 23.476 | 22.8544 | 56.0545
BRIM1 R2 | 132 | 51.7205 | 17.4761 | 19.0505 | 43.7654 | 65.4029 | 23.476 | 22.8544 | 56.0545
BRIN2 M1 | 275 | 64.824 | 23.6574 | 13.8469 | 47.3036 | 67.7336 | 26.4562 | 12.7455 | 50.1603
BRIN2 M2 | 275 | 68.9049 | 25.1432 | 16.9884 | 52.5462 | 71.5064 | 27.5389 | 16.2892 | 55.2351
BRIN2 R1 | 275 | 64.824 | 23.6574 | 13.8469 | 47.3036 | 67.7336 | 26.4562 | 12.7455 | 50.1603
BRIN2 R2 | 275 | 68.9049 | 25.1432 | 16.9884 | 52.5462 | 71.5064 | 27.5389 | 16.2892 | 55.2351
BRIN4 MC1 | 400 | 73.0662 | 26.5086 | 16.2959 | 53.7847 | 55.3863 | 21.641 | 11.1343 | 41.7392
BRIN4 MC4 | 400 | 73.0662 | 26.5086 | 16.2959 | 53.7847 | 55.3863 | 21.641 | 11.1343 | 41.7392
BRLE4 M1 | 400 | 114.2705 | 41.1666 | 21.2985 | 79.5168 | 98.751 | 38.5307 | 19.0975 | 73.588
BRLE4 M2 | 400 | 114.2705 | 41.1666 | 21.2985 | 79.5168 | 98.751 | 38.5307 | 19.0975 | 73.588
BRLE4 R1 | 400 | 114.2705 | 41.1666 | 21.2985 | 79.5168 | 98.751 | 38.5307 | 19.0975 | 73.588
BRLE4 R2 | 400 | 114.2705 | 41.1666 | 21.2985 | 79.5168 | 98.751 | 38.5307 | 19.0975 | 73.588
BULL4 MC1 | 400 | 67.291 | 24.5644 | 14.8578 | 49.5971 | 46.9565 | 18.5584 | 7.9951 | 34.2407
BULL4 MC2 | 400 | 67.291 | 24.5644 | 14.8578 | 49.5971 | 46.9565 | 18.5584 | 7.9951 | 34.2407
BURW4 MC1 | 400 | 90.3746 | 32.0406 | 21.8641 | 67.1764 | 59.8584 | 23.7029 | 10.8169 | 44.3378
BURW4 MC2 | 400 | 90.3746 | 32.0406 | 21.8641 | 67.1764 | 59.8584 | 23.7029 | 10.8169 | 44.3378
BURW4 MC3 | 400 | 90.3746 | 32.0406 | 21.8641 | 67.1764 | 59.8584 | 23.7029 | 10.8169 | 44.3378
BURW4 MC4 | 400 | 90.3746 | 32.0406 | 21.8641 | 67.1764 | 59.8584 | 23.7029 | 10.8169 | 44.3378
BUSH2 MC1 | 275 | 53.5028 | 19.4478 | 10.8726 | 38.376 | 53.2899 | 20.7123 | 10.0388 | 39.3304
BUSH2 MC2 | 275 | 53.5028 | 19.4478 | 10.8726 | 38.376 | 53.2899 | 20.7123 | 10.0388 | 39.3304
BUSH2 MC3 | 275 | 53.5028 | 19.4478 | 10.8726 | 38.376 | 53.2899 | 20.7123 | 10.0388 | 39.3304
BUSH2 MC4 | 275 | 53.5028 | 19.4478 | 10.8726 | 38.376 | 53.2899 | 20.7123 | 10.0388 | 39.3304
BUST2 M1 | 275 | 69.5594 | 24.815 | 18.0295 | 53.1231 | 72.4681 | 27.5235 | 17.0654 | 55.9895
BUST2 M2 | 275 | 69.5594 | 24.815 | 18.0295 | 53.1231 | 72.4681 | 27.5235 | 17.0654 | 55.9895
BUST2 R1 | 275 | 69.5594 | 24.815 | 18.0295 | 53.1231 | 72.4681 | 27.5235 | 17.0654 | 55.9895
BUST2 R2 | 275 | 69.5594 | 24.815 | 18.0295 | 53.1231 | 72.4681 | 27.5235 | 17.0654 | 55.9895
CANT4 MC1 | 400 | 93.7966 | 33.9128 | 19.4654 | 67.4253 | 69.7233 | 27.5246 | 12.4374 | 51.3631
CANT4 MC2 | 400 | 93.7966 | 33.9128 | 19.4654 | 67.4253 | 69.7233 | 27.5246 | 12.4374 | 51.3631
CANT4 MC3 | 400 | 93.7966 | 33.9128 | 19.4654 | 67.4253 | 69.7233 | 27.5246 | 12.4374 | 51.3631
CANT4 MC4 | 400 | 93.7966 | 33.9128 | 19.4654 | 67.4253 | 69.7233 | 27.5246 | 12.4374 | 51.3631
CANT4 R5 | 400 | 93.7966 | 33.9128 | 19.4654 | 67.4253 | 69.7233 | 27.5246 | 12.4374 | 51.3631
CANT4 R5 | 400 | 93.8152 | 33.9197 | 19.47 | 67.4398 | 69.7319 | 27.5273 | 12.441 | 51.3705
CANT4 R5 | 400 | 93.8152 | 33.9197 | 19.47 | 67.4398 | 69.7319 | 27.5273 | 12.441 | 51.3705
CAPE2 M1 | 275 | 65.8966 | 22.983 | 19.9263 | 52.4291 | 74.6331 | 27.3472 | 21.6963 | 60.3711
CAPE2 M2 | 275 | 65.8966 | 22.983 | 19.9263 | 52.4291 | 74.6331 | 27.3472 | 21.6963 | 60.3711
CAPE2 R1 | 275 | 65.8966 | 22.983 | 19.9263 | 52.4291 | 74.6331 | 27.3472 | 21.6963 | 60.3711
CAPE2 R2 | 275 | 65.8966 | 22.983 | 19.9263 | 52.4291 | 74.6331 | 27.3472 | 21.6963 | 60.3711
CAPE4A | 400 | 84.0241 | 29.645 | 19.8846 | 61.809 | 79.4209 | 30.097 | 17.2596 | 59.8232
CAPE4B | 400 | 84.0268 | 29.6461 | 19.8845 | 61.8104 | 80.0332 | 30.3242 | 17.3479 | 60.2328
CARE2 MC1 | 275 | 47.1068 | 17.6914 | 8.2099 | 33.2294 | 39.9899 | 15.8709 | 7.12 | 29.5648
CARE2 MC2 | 275 | 47.1068 | 17.6914 | 8.2099 | 33.2294 | 39.9899 | 15.8709 | 7.12 | 29.5648
CARR1 M1 | 132 | 34.6913 | 12.8152 | 9.7947 | 27.9181 | 40.544 | 15.4611 | 11.6253 | 33.4907
CARR1 M2 | 132 | 34.6913 | 12.8152 | 9.7947 | 27.9181 | 40.544 | 15.4611 | 11.6253 | 33.4907
CARR1 M3 | 132 | 34.6913 | 12.8152 | 9.7947 | 27.9181 | 40.544 | 15.4611 | 11.6253 | 33.4907
CARR1 M4 | 132 | 42.1072 | 14.7767 | 14.0119 | 34.9092 | 54.0287 | 19.7991 | 17.4728 | 45.4729
CARR1 R1 | 132 | 34.6913 | 12.8152 | 9.7947 | 27.9181 | 40.544 | 15.4611 | 11.6253 | 33.4907
CARR1 R2 | 132 | 34.6913 | 12.8152 | 9.7947 | 27.9181 | 40.544 | 15.4611 | 11.6253 | 33.4907
CARR1 R3 | 132 | 42.1072 | 14.7767 | 14.0119 | 34.9092 | 54.0287 | 19.7991 | 17.4728 | 45.4729
CARR1 R4 | 132 | 42.1072 | 14.7767 | 14.0119 | 34.9092 | 54.0287 | 19.7991 | 17.4728 | 45.4729
CARR1B | 132 | 41.3013 | 14.3239 | 7.9041 | 28.1612 | 51.0804 | 19.2558 | 6.9277 | 34.1595
CARR1C | 132 | 41.1272 | 14.3072 | 7.4948 | 27.7282 | 50.6135 | 19.2059 | 5.444 | 32.6052
CARR1D | 132 | 41.4136 | 14.3432 | 8.1371 | 28.4214 | 51.4662 | 19.3066 | 7.2874 | 34.5911
CARR2 M1 | 275 | 80.3033 | 28.814 | 21.061 | 61.8102 | 86.6559 | 32.5498 | 23.2982 | 69.3306
CARR2 M2 | 275 | 80.3033 | 28.814 | 21.061 | 61.8102 | 86.6559 | 32.5498 | 23.2982 | 69.3306
CARR2 R1 | 275 | 80.3033 | 28.814 | 21.061 | 61.8102 | 86.6559 | 32.5498 | 23.2982 | 69.3306
CARR2 R2 | 275 | 80.3033 | 28.814 | 21.061 | 61.8102 | 86.6559 | 32.5498 | 23.2982 | 69.3306
CARR4 M1 | 400 | 112.9604 | 41.1476 | 32.7438 | 90.9352 | 100.3923 | 38.8571 | 28.7493 | 83.7015
CARR4 M2/4 | 400 | 112.9604 | 41.1476 | 32.7438 | 90.9352 | 100.3923 | 38.8571 | 28.7493 | 83.7015
CARR4 R1 | 400 | 112.9604 | 41.1476 | 32.7438 | 90.9352 | 100.3923 | 38.8571 | 28.7493 | 83.7015
CARR4 R1/2 | 400 | 112.9604 | 41.1476 | 32.7438 | 90.9352 | 100.3923 | 38.8571 | 28.7493 | 83.7015
CARR4 R2 | 400 | 112.9604 | 41.1476 | 32.7438 | 90.9352 | 100.3923 | 38.8571 | 28.7493 | 83.7015
CARR4 R4 | 400 | 112.9604 | 41.1476 | 32.7438 | 90.9352 | 100.3923 | 38.8571 | 28.7493 | 83.7015
CARR4A | 400 | 103.2299 | 35.8093 | 8.8055 | 59.4475 | 91.1553 | 34.7824 | 9.4806 | 58.6703
CARR4B | 400 | 103.3525 | 35.8619 | 8.7358 | 59.4521 | 88.6415 | 34.062 | 8.2957 | 56.4666
CASK1 M1 | 132 | 47.3196 | 15.7304 | 12.4466 | 34.6927 | 52.4296 | 18.42 | 15.1134 | 41.1633
CELL1 M1 | 132 | 46.9799 | 17.4346 | 14.8308 | 39.487 | 58.3167 | 22.9467 | 17.4608 | 49.9124
CELL1 M2 | 132 | 44.976 | 16.6417 | 12.5197 | 36.0546 | 50.2119 | 19.3701 | 13.5675 | 40.961
CELL1 R1 | 132 | 46.9799 | 17.4346 | 14.8308 | 39.487 | 58.3167 | 22.9467 | 17.4608 | 49.9124
CELL1 R2 | 132 | 44.976 | 16.6417 | 12.5197 | 36.0546 | 50.2119 | 19.3701 | 13.5675 | 40.961
CELL1A | 132 | 38.7904 | 13.9005 | 7.2285 | 26.8868 | 47.8358 | 19.1865 | 8.6946 | 35.8284
CELL4 M1 | 400 | 85.478 | 31.0398 | 15.2931 | 59.1899 | 72.048 | 28.3248 | 13.425 | 53.4824
CELL4 M2 | 400 | 85.478 | 31.0398 | 15.2931 | 59.1899 | 72.048 | 28.3248 | 13.425 | 53.4824
CELL4 R1 | 400 | 85.478 | 31.0398 | 15.2931 | 59.1899 | 72.048 | 28.3248 | 13.425 | 53.4824
CELL4 R2 | 400 | 85.478 | 31.0398 | 15.2931 | 59.1899 | 72.048 | 28.3248 | 13.425 | 53.4824
CHIC4 MB1 | 400 | 38.6606 | 14.4968 | 7.6043 | 28.1058 | 30.8058 | 12.057 | 5.7209 | 22.7721
CHIC4 MB2 | 400 | 38.6606 | 14.4968 | 7.6043 | 28.1058 | 30.8058 | 12.057 | 5.7209 | 22.7721
CHIC4 R1/2 | 400 | 38.3583 | 14.5385 | 11.1991 | 31.7597 | 29.1897 | 11.5096 | 7.757 | 24.0339
CHSI2 MC1 | 275 | 85.8855 | 31.1262 | 18.3851 | 62.4041 | 73.5275 | 29.1014 | 11.9786 | 53.1341
CHSI2 MC2 | 275 | 85.8855 | 31.1262 | 18.3851 | 62.4041 | 73.5275 | 29.1014 | 11.9786 | 53.1341
CHSI2 MC3 | 275 | 85.8855 | 31.1262 | 18.3851 | 62.4041 | 73.5275 | 29.1014 | 11.9786 | 53.1341
CHSI2 MC4 | 275 | 85.8855 | 31.1262 | 18.3851 | 62.4041 | 73.5275 | 29.1014 | 11.9786 | 53.1341
CHTE2 MC1 | 275 | 69.6251 | 24.9784 | 16.576 | 51.9008 | 58.6375 | 23.228 | 10.8427 | 43.692
CHTE2 MC2 | 275 | 69.6251 | 24.9784 | 16.576 | 51.9008 | 58.6375 | 23.228 | 10.8427 | 43.692
CHTE2 MC3 | 275 | 69.6251 | 24.9784 | 16.576 | 51.9008 | 58.6375 | 23.228 | 10.8427 | 43.692
CHTE2 MC4 | 275 | 69.6251 | 24.9784 | 16.576 | 51.9008 | 58.6375 | 23.228 | 10.8427 | 43.692
CILF4 M1 | 400 | 83.2935 | 29.9946 | 19.5021 | 61.9209 | 71.5127 | 27.6218 | 13.9287 | 52.9917
CILF4 M2 | 400 | 83.2935 | 29.9946 | 19.5021 | 61.9209 | 71.5127 | 27.6218 | 13.9287 | 52.9917
CILF4 R1 | 400 | 83.2935 | 29.9946 | 19.5021 | 61.9209 | 71.5127 | 27.6218 | 13.9287 | 52.9917
CILF4 R2 | 400 | 83.2935 | 29.9946 | 19.5021 | 61.9209 | 71.5127 | 27.6218 | 13.9287 | 52.9917
CITR4 M5 | 400 | 110.4795 | 37.0429 | 26.7397 | 79.1262 | 120.5759 | 45.6531 | 23.4516 | 88.0149
CITR4 M6 | 400 | 110.4795 | 37.0429 | 26.7397 | 79.1262 | 120.5759 | 45.6531 | 23.4516 | 88.0149
CITR4 MC1 | 400 | 110.4832 | 37.0437 | 26.7413 | 79.129 | 120.5928 | 45.6554 | 23.4964 | 88.0628
CITR4 MC2 | 400 | 110.4832 | 37.0437 | 26.7413 | 79.129 | 120.5928 | 45.6554 | 23.4964 | 88.0628
CITR4 MC3 | 400 | 110.4832 | 37.0437 | 26.7413 | 79.129 | 120.5928 | 45.6554 | 23.4964 | 88.0628
CITR4 MC4 | 400 | 110.4832 | 37.0437 | 26.7413 | 79.129 | 120.5928 | 45.6554 | 23.4964 | 88.0628
CITR4 R5 | 400 | 110.4795 | 37.0429 | 26.7397 | 79.1262 | 120.5759 | 45.6531 | 23.4516 | 88.0149
CITR4 R6 | 400 | 110.4795 | 37.0429 | 26.7397 | 79.1262 | 120.5759 | 45.6531 | 23.4516 | 88.0149
CLEH4 M1 | 400 | 77.9979 | 28.3798 | 16.5156 | 56.6507 | 67.2472 | 26.385 | 13.233 | 50.5469
CLEH4 R1 | 400 | 77.9979 | 28.3798 | 16.5156 | 56.6507 | 67.2472 | 26.385 | 13.233 | 50.5469
CONQ4 M1 | 400 | 108.1695 | 37.7607 | 24.5862 | 77.9879 | 113.1617 | 42.2483 | 28.0356 | 87.7837
CONQ4 M2 | 400 | 108.1695 | 37.7607 | 24.5862 | 77.9879 | 113.1617 | 42.2483 | 28.0356 | 87.7837
CONQ4 M3 | 400 | 108.1695 | 37.7607 | 24.5862 | 77.9879 | 113.1617 | 42.2483 | 28.0356 | 87.7837
CONQ4 M4 | 400 | 108.1695 | 37.7607 | 24.5862 | 77.9879 | 113.1617 | 42.2483 | 28.0356 | 87.7837
CONQ4 R1/3 | 400 | 108.1695 | 37.7607 | 24.5862 | 77.9879 | 113.1617 | 42.2483 | 28.0356 | 87.7837
CONQ4 R2/4 | 400 | 108.1695 | 37.7607 | 24.5862 | 77.9879 | 113.1617 | 42.2483 | 28.0356 | 87.7837
COSO4 M | 400 | 99.4425 | 35.3664 | 21.8319 | 71.8476 | 82.2606 | 31.6508 | 18.4306 | 63.1916
COSO4 R | 400 | 99.4425 | 35.3664 | 21.8319 | 71.8476 | 82.2606 | 31.6508 | 18.4306 | 63.1916
COTT4 M1 | 400 | 96.4663 | 34.7904 | 21.8765 | 71.0776 | 76.2374 | 29.521 | 15.3653 | 57.1144
COTT4 M2 | 400 | 96.4663 | 34.7904 | 21.8765 | 71.0776 | 76.2374 | 29.521 | 15.3653 | 57.1144
COTT4 M3 | 400 | 87.3503 | 32.248 | 26.4772 | 72.0827 | 73.1915 | 28.4685 | 20.8764 | 61.137
COTT4 M4 | 400 | 87.3503 | 32.248 | 26.4772 | 72.0827 | 73.1915 | 28.4685 | 20.8764 | 61.137
COTT4 R1/2 | 400 | 87.3503 | 32.248 | 26.4772 | 72.0827 | 73.1915 | 28.4685 | 20.8764 | 61.137
COTT4 R3/4 | 400 | 87.3503 | 32.248 | 26.4772 | 72.0827 | 73.1915 | 28.4685 | 20.8764 | 61.137
COVE2 MC1 | 275 | 59.6596 | 21.5025 | 12.0375 | 42.4466 | 56.3902 | 21.8016 | 11.4429 | 42.2749
COVE2 MC2 | 275 | 59.6596 | 21.5025 | 12.0375 | 42.4466 | 56.3902 | 21.8016 | 11.4429 | 42.2749
COVE2 MC3 | 275 | 59.6596 | 21.5025 | 12.0375 | 42.4466 | 56.3902 | 21.8016 | 11.4429 | 42.2749
COVE2 MC4 | 275 | 59.6596 | 21.5025 | 12.0375 | 42.4466 | 56.3902 | 21.8016 | 11.4429 | 42.2749
COWL4 M1 | 400 | 109.5446 | 40.5378 | 31.3029 | 88.632 | 94.5204 | 36.9272 | 25.7654 | 77.9884
COWL4 M2 | 400 | 109.5446 | 40.5378 | 31.3029 | 88.632 | 94.5204 | 36.9272 | 25.7654 | 77.9884
COWL4 R1 | 400 | 109.5446 | 40.5378 | 31.3029 | 88.632 | 94.5204 | 36.9272 | 25.7654 | 77.9884
COWL4 R2 | 400 | 109.5446 | 40.5378 | 31.3029 | 88.632 | 94.5204 | 36.9272 | 25.7654 | 77.9884
CREB2A | 275 | 81.1568 | 26.9901 | 20.9946 | 59.1644 | 72.394 | 26.3838 | 13.8535 | 51.1658
CREB2B | 275 | 81.1689 | 26.9907 | 21.0036 | 59.1742 | 73.2248 | 26.6753 | 14.0141 | 51.7386
CREB4 MB1 | 400 | 193.1622 | 56.5713 | 59.4609 | 139.4647 | 110.661 | 40.8979 | 25.354 | 83.1923
CREB4 MB2 | 400 | 193.1622 | 56.5713 | 59.4609 | 139.4647 | 110.661 | 40.8979 | 25.354 | 83.1923
CREB4 RB1 | 400 | 193.1622 | 56.5713 | 59.4609 | 139.4647 | 110.661 | 40.8979 | 25.354 | 83.1923
CREB4 RB2 | 400 | 193.1622 | 56.5713 | 59.4609 | 139.4647 | 110.661 | 40.8979 | 25.354 | 83.1923
DAIN4 M1 | 400 | 115.2078 | 40.7307 | 23.4762 | 81.0782 | 101.4914 | 39.0075 | 20.9174 | 76.0823
DAIN4 M2 | 400 | 115.2078 | 40.7307 | 23.4762 | 81.0782 | 101.4914 | 39.0075 | 20.9174 | 76.0823
DAIN4 R1 | 400 | 115.2078 | 40.7307 | 23.4762 | 81.0782 | 101.4914 | 39.0075 | 20.9174 | 76.0823
DAIN4 R2 | 400 | 115.2078 | 40.7307 | 23.4762 | 81.0782 | 101.4914 | 39.0075 | 20.9174 | 76.0823
DIDC4 M1 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 M2 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 M3 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 M4 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 M5 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 M6 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 R1/2 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 R3/4 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 R5 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DIDC4 R6 | 400 | 102.3483 | 37.2004 | 19.8857 | 72.495 | 96.7842 | 37.0167 | 21.7244 | 74.074
DINO4 1 | 400 | 74.6099 | 25.8035 | 20.0049 | 56.4966 | 74.4551 | 27.3653 | 21.9157 | 60.6161
DINO4 2 | 400 | 74.6099 | 25.8035 | 20.0049 | 56.4966 | 74.4551 | 27.3653 | 21.9157 | 60.6161
DINO4 3 | 400 | 74.6099 | 25.8035 | 20.0049 | 56.4966 | 74.4551 | 27.3653 | 21.9157 | 60.6161
DRAK1 M1 | 132 | 30.5658 | 10.9159 | 12.3295 | 27.767 | 37.679 | 13.8976 | 15.3045 | 34.9587
DRAK1 M2 | 132 | 30.5658 | 10.9159 | 12.3295 | 27.767 | 37.679 | 13.8976 | 15.3045 | 34.9587
DRAK1 R1 | 132 | 30.5658 | 10.9159 | 12.3295 | 27.767 | 37.679 | 13.8976 | 15.3045 | 34.9587
DRAK1 R2 | 132 | 30.5658 | 10.9159 | 12.3295 | 27.767 | 37.679 | 13.8976 | 15.3045 | 34.9587
DRAK4 M1 | 400 | 113.2205 | 39.893 | 21.4992 | 77.9163 | 107.5274 | 41.3587 | 20.9226 | 79.4126
DRAK4 M2 | 400 | 113.2205 | 39.893 | 21.4992 | 77.9163 | 107.5274 | 41.3587 | 20.9226 | 79.4126
DRAK4 M3 | 400 | 113.2205 | 39.893 | 21.4992 | 77.9163 | 107.5274 | 41.3587 | 20.9226 | 79.4126
DRAK4 R1/3 | 400 | 113.2205 | 39.893 | 21.4992 | 77.9163 | 107.5274 | 41.3587 | 20.9226 | 79.4126
DRAK4 R2 | 400 | 113.2205 | 39.893 | 21.4992 | 77.9163 | 107.5274 | 41.3587 | 20.9226 | 79.4126
DRAX1 M1 | 132 | 39.2535 | 11.8607 | 11.7208 | 28.4943 | 48.937 | 16.6271 | 14.734 | 38.2483
DRAX1 M2 | 132 | 39.2535 | 11.8607 | 11.7208 | 28.4943 | 48.937 | 16.6271 | 14.734 | 38.2483
DRAX1 R1 | 132 | 39.2535 | 11.8607 | 11.7208 | 28.4943 | 48.937 | 16.6271 | 14.734 | 38.2483
DRAX1 R2 | 132 | 39.2535 | 11.8607 | 11.7208 | 28.4943 | 48.937 | 16.6271 | 14.734 | 38.2483
DRAX4 M1 | 400 | 135.9904 | 46.5112 | 37.2642 | 103.041 | 130.5491 | 47.9292 | 36.8179 | 104.6
DRAX4 M2 | 400 | 135.9904 | 46.5112 | 37.2642 | 103.041 | 130.5491 | 47.9292 | 36.8179 | 104.6
DRAX4 M3 | 400 | 135.9904 | 46.5112 | 37.2642 | 103.041 | 130.5491 | 47.9292 | 36.8179 | 104.6
DRAX4 M4 | 400 | 130.1811 | 44.4103 | 36.2686 | 99.0742 | 124.048 | 45.6792 | 34.4273 | 99.0274
DRAX4 M5 | 400 | 130.1811 | 44.4103 | 36.2686 | 99.0742 | 124.048 | 45.6792 | 34.4273 | 99.0274
DRAX4 M6 | 400 | 130.1811 | 44.4103 | 36.2686 | 99.0742 | 124.048 | 45.6792 | 34.4273 | 99.0274
DRAX4 R1/2/3 | 400 | 135.9904 | 46.5112 | 37.2642 | 103.041 | 130.5491 | 47.9292 | 36.8179 | 104.6
DRAX4 R4/5/6 | 400 | 130.1811 | 44.4103 | 36.2686 | 99.0742 | 124.048 | 45.6792 | 34.4273 | 99.0274
DUNG2 M1 | 275 | 44.9751 | 16.2225 | 14.1708 | 37.1128 | 41.5043 | 15.7015 | 10.0301 | 32.2353
DUNG2 M2 | 275 | 44.9751 | 16.2225 | 14.1708 | 37.1128 | 41.5043 | 15.7015 | 10.0301 | 32.2353
DUNG2 R1 | 275 | 44.9751 | 16.2225 | 14.1708 | 37.1128 | 41.5043 | 15.7015 | 10.0301 | 32.2353
DUNG2 R2 | 275 | 44.9751 | 16.2225 | 14.1708 | 37.1128 | 41.5043 | 15.7015 | 10.0301 | 32.2353
DUNG4 M1 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
DUNG4 M2 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
DUNG4 M3 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
DUNG4 M4 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
DUNG4 M5 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
DUNG4 R1/2 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
DUNG4 R4/5 | 400 | 76.7902 | 27.9483 | 9.8619 | 49.3867 | 54.5965 | 21.769 | 4.223 | 35.0089
EALI2 MC1 | 275 | 58.1748 | 20.4208 | 13.1196 | 41.9991 | 63.6909 | 24.7146 | 8.1031 | 43.0549
EALI2 MC2 | 275 | 58.1748 | 20.4208 | 13.1196 | 41.9991 | 63.6909 | 24.7146 | 8.1031 | 43.0549
EALI2 MC3 | 275 | 58.1748 | 20.4208 | 13.1196 | 41.9991 | 63.6909 | 24.7146 | 8.1031 | 43.0549
EALI2 MC4 | 275 | 58.1748 | 20.4208 | 13.1196 | 41.9991 | 63.6909 | 24.7146 | 8.1031 | 43.0549
EASO4 M1 | 400 | 69.689 | 25.3376 | 14.4751 | 50.3078 | 63.823 | 24.2476 | 15.9084 | 50.1997
EASO4 M2 | 400 | 69.689 | 25.3376 | 14.4751 | 50.3078 | 63.823 | 24.2476 | 15.9084 | 50.1997
EASO4 R1 | 400 | 69.689 | 25.3376 | 14.4751 | 50.3078 | 63.823 | 24.2476 | 15.9084 | 50.1997
EASO4 R2 | 400 | 69.689 | 25.3376 | 14.4751 | 50.3078 | 63.823 | 24.2476 | 15.9084 | 50.1997
EASO4A | 400 | 69.689 | 25.3376 | 14.4751 | 50.3078 | 63.823 | 24.2476 | 15.9084 | 50.1997
EASO4B | 400 | 69.689 | 25.3376 | 14.4751 | 50.3078 | 63.823 | 24.2476 | 15.9084 | 50.1997
ECLA1 M1 | 132 | 43.8092 | 16.3713 | 12.481 | 35.6336 | 46.3488 | 18.0794 | 13.6971 | 39.2652
ECLA1 M2 | 132 | 43.8092 | 16.3713 | 12.481 | 35.6336 | 46.3488 | 18.0794 | 13.6971 | 39.2652
ECLA1 R1 | 132 | 44.4579 | 16.5382 | 12.7375 | 36.1261 | 53.3002 | 20.5577 | 15.4631 | 44.5361
ECLA1 R2 | 132 | 44.4579 | 16.5382 | 12.7375 | 36.1261 | 53.3002 | 20.5577 | 15.4631 | 44.5361
ECLA4 M1 | 400 | 101.1408 | 36.5092 | 20.051 | 71.6827 | 82.986 | 32.4816 | 15.3981 | 61.334
ECLA4 M2 | 400 | 101.1408 | 36.5092 | 20.051 | 71.6827 | 82.986 | 32.4816 | 15.3981 | 61.334
ECLA4 R1 | 400 | 101.1408 | 36.5092 | 20.051 | 71.6827 | 82.986 | 32.4816 | 15.3981 | 61.334
ECLA4 R2 | 400 | 101.1408 | 36.5092 | 20.051 | 71.6827 | 82.986 | 32.4816 | 15.3981 | 61.334
EGGB4 M1 | 400 | 115.8168 | 40.6027 | 28.7688 | 86.1897 | 103.047 | 38.9509 | 22.5275 | 77.6124
EGGB4 M2 | 400 | 115.8168 | 40.6027 | 28.7688 | 86.1897 | 103.047 | 38.9509 | 22.5275 | 77.6124
EGGB4 R1 | 400 | 116.6702 | 40.4462 | 29.8511 | 87.0507 | 99.8476 | 37.7378 | 21.6433 | 75.0126
EGGB4 R2 | 400 | 116.6702 | 40.4462 | 29.8511 | 87.0507 | 99.8476 | 37.7378 | 21.6433 | 75.0126
ELLA2 MC1 | 275 | 64.5549 | 23.2078 | 8.3577 | 41.1786 | 64.7161 | 24.8993 | 7.9576 | 43.1706
ELLA2 MC2 | 275 | 64.5549 | 23.2078 | 8.3577 | 41.1786 | 64.7161 | 24.8993 | 7.9576 | 43.1706
ELLA2 MC3 | 275 | 64.5549 | 23.2078 | 8.3577 | 41.1786 | 64.7161 | 24.8993 | 7.9576 | 43.1706
ELLA2 MC4 | 275 | 64.5549 | 23.2078 | 8.3577 | 41.1786 | 64.7161 | 24.8993 | 7.9576 | 43.1706
ELST1 M1 | 132 | 31.2969 | 11.3658 | 9.8762 | 25.9499 | 38.2156 | 14.3069 | 11.8439 | 32.0769
ELST1 M2 | 132 | 44.6116 | 15.8053 | 13.2077 | 35.5598 | 55.3354 | 21.0159 | 15.4363 | 45.1573
ELST1 M3 | 132 | 37.5796 | 13.7952 | 9.384 | 28.8935 | 43.5435 | 16.604 | 11.1322 | 34.6139
ELST1 R1 | 132 | 31.2969 | 11.3658 | 9.8762 | 25.9499 | 38.2156 | 14.3069 | 11.8439 | 32.0769
ELST1 R2 | 132 | 44.6116 | 15.8053 | 13.2077 | 35.5598 | 55.3354 | 21.0159 | 15.4363 | 45.1573
ELST1 R3 | 132 | 37.5796 | 13.7952 | 9.384 | 28.8935 | 43.5435 | 16.604 | 11.1322 | 34.6139
ELST2 M1 | 275 | 63.6256 | 23.0208 | 16.1579 | 48.7142 | 69.0022 | 26.0372 | 17.7999 | 54.622
ELST2 M2 | 275 | 65.0973 | 23.659 | 14.176 | 47.6348 | 70.7413 | 27.2128 | 14.8619 | 53.3466
ELST2 R1 | 275 | 63.6256 | 23.0208 | 16.1579 | 48.7142 | 69.0022 | 26.0372 | 17.7999 | 54.622
ELST2 R2 | 275 | 65.0973 | 23.659 | 14.176 | 47.6348 | 70.7413 | 27.2128 | 14.8619 | 53.3466
ELST4 M1 | 400 | 87.8379 | 31.451 | 27.4541 | 71.9325 | 102.3114 | 38.7196 | 31.1205 | 85.8783
ELST4 R1 | 400 | 87.8379 | 31.451 | 27.4541 | 71.9325 | 102.3114 | 38.7196 | 31.1205 | 85.8783
ELST4A | 400 | 53.3896 | 19.4722 | 6.8695 | 34.4073 | 50.8248 | 19.3003 | 7.7879 | 35.0826
ENDE4 MC1 | 400 | 79.8707 | 29.3103 | 14.0381 | 55.489 | 55.7564 | 22.1522 | 9.557 | 40.8849
ENDE4 MC2 | 400 | 79.8707 | 29.3103 | 14.0381 | 55.489 | 55.7564 | 22.1522 | 9.557 | 40.8849
ENDE4 MC3 | 400 | 79.8707 | 29.3103 | 14.0381 | 55.489 | 55.7564 | 22.1522 | 9.557 | 40.8849
ENDE4 MC4 | 400 | 79.8707 | 29.3103 | 14.0381 | 55.489 | 55.7564 | 22.1522 | 9.557 | 40.8849
EXET4 M1 | 400 | 69.6395 | 25.5474 | 13.4312 | 49.5607 | 72.2862 | 27.5702 | 16.474 | 55.4642
EXET4 M2 | 400 | 69.6395 | 25.5474 | 13.4312 | 49.5607 | 72.2862 | 27.5702 | 16.474 | 55.4642
EXET4 R1 | 400 | 69.6395 | 25.5474 | 13.4312 | 49.5607 | 72.2862 | 27.5702 | 16.474 | 55.4642
EXET4 R2 | 400 | 69.6395 | 25.5474 | 13.4312 | 49.5607 | 72.2862 | 27.5702 | 16.474 | 55.4642
FAWL1 M1 | 132 | 45.7841 | 16.1585 | 16.5029 | 39.3544 | 58.5038 | 22.0372 | 19.7577 | 50.923
FAWL1 M2 | 132 | 45.7841 | 16.1585 | 16.5029 | 39.3544 | 58.5038 | 22.0372 | 19.7577 | 50.923
FAWL1 R1 | 132 | 45.7841 | 16.1585 | 16.5029 | 39.3544 | 58.5038 | 22.0372 | 19.7577 | 50.923
FAWL1 R2 | 132 | 45.7841 | 16.1585 | 16.5029 | 39.3544 | 58.5038 | 22.0372 | 19.7577 | 50.923
FAWL4 M1/3 | 400 | 83.5713 | 29.7106 | 10.1845 | 52.2016 | 68.4893 | 26.5262 | 8.0752 | 45.589
FAWL4 M1/3(1) | 400 | 83.5713 | 29.7106 | 10.1845 | 52.2016 | 68.4893 | 26.5262 | 8.0752 | 45.589
FAWL4 M2/4(2) | 400 | 83.5713 | 29.7106 | 10.1845 | 52.2016 | 68.4893 | 26.5262 | 8.0752 | 45.589
FAWL4 M2/4(3) | 400 | 83.5713 | 29.7106 | 10.1845 | 52.2016 | 68.4893 | 26.5262 | 8.0752 | 45.589
FAWL4 R1/3 | 400 | 83.5713 | 29.7106 | 10.1845 | 52.2016 | 68.4893 | 26.5262 | 8.0752 | 45.589
FAWL4 R2/4 | 400 | 83.5713 | 29.7106 | 10.1845 | 52.2016 | 68.4893 | 26.5262 | 8.0752 | 45.589
FECK2 M1 | 275 | 60.5342 | 22.0748 | 13.7001 | 44.9186 | 60.0752 | 23.0636 | 13.6145 | 46.2314
FECK2 M2 | 275 | 60.5342 | 22.0748 | 13.7001 | 44.9186 | 60.0752 | 23.0636 | 13.6145 | 46.2314
FECK2 R | 275 | 60.5342 | 22.0748 | 13.7001 | 44.9186 | 60.0752 | 23.0636 | 13.6145 | 46.2314
FECK4 M1 | 400 | 74.6435 | 27.6914 | 12.5321 | 51.6936 | 63.6685 | 25.0533 | 12.0844 | 47.5151
FECK4 M2 | 400 | 74.6435 | 27.6914 | 12.5321 | 51.6936 | 63.6685 | 25.0533 | 12.0844 | 47.5151
FECK4 R1 | 400 | 74.6435 | 27.6914 | 12.5321 | 51.6936 | 63.6685 | 25.0533 | 12.0844 | 47.5151
FECK4 R2 | 400 | 74.6435 | 27.6914 | 12.5321 | 51.6936 | 63.6685 | 25.0533 | 12.0844 | 47.5151
FENW4A | 400 | 112.6137 | 38.8054 | 14.0351 | 68.9143 | 92.5847 | 35.2558 | 7.3758 | 57.235
FERR2 M1 | 275 | 58.4135 | 20.9842 | 11.6942 | 41.3704 | 59.2481 | 22.333 | 11.6496 | 43.2332
FERR2 M2 | 275 | 58.6813 | 21.0086 | 15.7723 | 45.483 | 61.9765 | 23.1694 | 14.4904 | 47.2569
FERR2 R1 | 275 | 63.3965 | 22.6791 | 12.4608 | 44.5339 | 62.6417 | 23.7967 | 10.4033 | 44.0568
FERR2 R2 | 275 | 63.3965 | 22.6791 | 12.4608 | 44.5339 | 62.6417 | 23.7967 | 10.4033 | 44.0568
FERR2A | 275 | 58.7042 | 20.9093 | 13.2319 | 42.802 | 61.7927 | 23.0603 | 11.8745 | 44.4867
FERR2B | 275 | 57.8652 | 20.6397 | 9.5025 | 38.6914 | 58.4409 | 22.0345 | 9.0651 | 40.2266
FERR4A | 400 | 80.4388 | 28.2776 | 10.1434 | 50.1339 | 68.2399 | 25.8478 | 8.2511 | 44.8055
FFES2 Term205 | 275 | 34.8307 | 12.976 | 2.5832 | 20.934 | 33.7371 | 13.2229 | 2.2849 | 20.9849
FFES2 Term210 | 275 | 34.7816 | 12.9772 | 2.566 | 20.9186 | 34.2094 | 13.4051 | 2.3087 | 21.2664
FIDF2 M1 | 275 | 49.4852 | 17.6698 | 14.7765 | 39.7653 | 49.9126 | 18.604 | 13.6028 | 39.9128
FIDF2 M2 | 275 | 48.6995 | 17.3537 | 14.6132 | 39.155 | 48.112 | 17.929 | 12.9196 | 38.275
FIDF2 M3 | 275 | 60.4172 | 21.5066 | 15.1066 | 45.5216 | 57.236 | 21.6471 | 13.0686 | 43.6823
FIDF2 M4 | 275 | 60.9482 | 21.6925 | 15.2318 | 45.9096 | 59.1042 | 22.3223 | 13.6758 | 45.2443
FIDF2 R1 | 275 | 49.4852 | 17.6698 | 14.7765 | 39.7653 | 49.9126 | 18.604 | 13.6028 | 39.9128
FIDF2 R2 | 275 | 60.9482 | 21.6925 | 15.2318 | 45.9096 | 59.1042 | 22.3223 | 13.6758 | 45.2443
FLEE4 MC1 | 400 | 100.6615 | 36.3347 | 18.949 | 70.334 | 80.6793 | 31.7942 | 14.5033 | 59.4671
FLEE4 MC2 | 400 | 100.6615 | 36.3347 | 18.949 | 70.334 | 80.6793 | 31.7942 | 14.5033 | 59.4671
FLEE4 MC3 | 400 | 100.6615 | 36.3347 | 18.949 | 70.334 | 80.6793 | 31.7942 | 14.5033 | 59.4671
FLEE4 MC4 | 400 | 100.6615 | 36.3347 | 18.949 | 70.334 | 80.6793 | 31.7942 | 14.5033 | 59.4671
FLIB4 M1 | 400 | 101.2035 | 35.4831 | 23.2239 | 73.4047 | 106.3991 | 40.0817 | 24.4266 | 81.1107
FLIB4 M2 | 400 | 101.2035 | 35.4831 | 23.2239 | 73.4047 | 106.3991 | 40.0817 | 24.4266 | 81.1107
FOUR2 MC1 | 275 | 39.3896 | 15.4705 | 4.9579 | 26.8364 | 31.8809 | 13.1008 | 3.8941 | 22.4214
FOUR2 MC2 | 275 | 39.3896 | 15.4705 | 4.9579 | 26.8364 | 31.8809 | 13.1008 | 3.8941 | 22.4214
FROD2 MC1 | 275 | 49.3658 | 17.5862 | 15.4695 | 40.3402 | 52.7999 | 19.4025 | 16.781 | 44.2203
FROD2 MC3 | 275 | 49.3098 | 17.2942 | 9.9185 | 34.3762 | 52.1315 | 19.0983 | 10.0975 | 37.1065
FROD4 M1 | 400 | 81.404 | 29.3225 | 26.1998 | 67.668 | 78.4337 | 29.5419 | 25.5365 | 67.3151
FROD4 R1 | 400 | 81.404 | 29.3225 | 26.1998 | 67.668 | 78.4337 | 29.5419 | 25.5365 | 67.3151
GART4A | 400 | 110.8977 | 36.7289 | 15.3637 | 67.3062 | 83.7819 | 31.5463 | 7.4003 | 52.0135
GART4B | 400 | 112.5024 | 37.3283 | 15.6689 | 68.459 | 92.8345 | 34.7826 | 9.0347 | 58.2247
GRAI4 M1 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 M2 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 M3 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 M4 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 M5 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 M6 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 M7 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 R1/2 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 R3 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 R4 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 R5 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 R6 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GRAI4 R7 | 400 | 140.5076 | 49.3771 | 44.2233 | 114.053 | 121.0426 | 45.765 | 38.2883 | 103.0098
GREN1 M1 | 132 | 39.4304 | 14.3185 | 10.5202 | 30.7696 | 43.3782 | 17.1653 | 10.45 | 34.7254
GREN1 M2 | 132 | 38.2608 | 14.0739 | 10.5859 | 30.4894 | 39.1172 | 15.3691 | 9.8001 | 31.5353
GREN1 R1 | 132 | 39.4304 | 14.3185 | 10.5202 | 30.7696 | 43.3782 | 17.1653 | 10.45 | 34.7254
GREN1 R2 | 132 | 38.2608 | 14.0739 | 10.5859 | 30.4894 | 39.1172 | 15.3691 | 9.8001 | 31.5353
GREN4 M1 | 400 | 72.5321 | 26.8898 | 11.6683 | 49.6961 | 48.486 | 19.6052 | 8.0173 | 35.7433
GREN4 M2 | 400 | 72.5321 | 26.8898 | 11.6683 | 49.6961 | 48.486 | 19.6052 | 8.0173 | 35.7433
GREN4 R1 | 400 | 72.5321 | 26.8898 | 11.6683 | 49.6961 | 48.486 | 19.6052 | 8.0173 | 35.7433
GREN4 R2 | 400 | 72.5321 | 26.8898 | 11.6683 | 49.6961 | 48.486 | 19.6052 | 8.0173 | 35.7433
GRIW4 MC1 | 400 | 65.008 | 23.1985 | 16.3142 | 49.1218 | 55.8597 | 21.4411 | 11.1131 | 41.4353
GRIW4 MC2 | 400 | 65.008 | 23.1985 | 16.3142 | 49.1218 | 55.8597 | 21.4411 | 11.1131 | 41.4353
GRSA2 M1 | 275 | 68.7367 | 22.8539 | 23.7125 | 56.0329 | 62.1034 | 22.6429 | 17.7437 | 49.7656
GRSA2 M2 | 275 | 68.7367 | 22.8539 | 23.7125 | 56.0329 | 62.1034 | 22.6429 | 17.7437 | 49.7656
GRSA2 R1 | 275 | 68.7367 | 22.8539 | 23.7125 | 56.0329 | 62.1034 | 22.6429 | 17.7437 | 49.7656
GRSA2 R2 | 275 | 68.7367 | 22.8539 | 23.7125 | 56.0329 | 62.1034 | 22.6429 | 17.7437 | 49.7656
GRSB2 M3 | 275 | 69.2716 | 22.9996 | 24.0765 | 56.6027 | 63.2056 | 22.9675 | 18.6131 | 51.094
GRSB2 M4 | 275 | 69.2716 | 22.9996 | 24.0765 | 56.6027 | 63.2056 | 22.9675 | 18.6131 | 51.094
GRSB2 R3 | 275 | 69.2716 | 22.9996 | 24.0765 | 56.6027 | 63.2056 | 22.9675 | 18.6131 | 51.094
GRSB2 R4 | 275 | 69.2716 | 22.9996 | 24.0765 | 56.6027 | 63.2056 | 22.9675 | 18.6131 | 51.094
HACK2A | 275 | 65.1726 | 22.9155 | 10.9446 | 43.3521 | 66.7508 | 24.9258 | 10.7167 | 45.9671
HACK2B | 275 | 64.0407 | 22.5454 | 10.9246 | 42.8086 | 65.9802 | 24.6307 | 10.6504 | 45.4836
HACK4 M1 | 400 | 97.1155 | 33.0011 | 24.0137 | 70.6843 | 110.1022 | 41.332 | 23.3376 | 81.7899
HACK4 M2 | 400 | 97.1155 | 33.0011 | 24.0137 | 70.6843 | 110.1022 | 41.332 | 23.3376 | 81.7899
HACK4 R1 | 400 | 97.1155 | 33.0011 | 24.0137 | 70.6843 | 110.1022 | 41.332 | 23.3376 | 81.7899
HACK4 R2 | 400 | 97.1155 | 33.0011 | 24.0137 | 70.6843 | 110.1022 | 41.332 | 23.3376 | 81.7899
HAMB4A | 400 | 61.9649 | 21.9167 | 6.8331 | 37.828 | 53.8409 | 20.8678 | 4.0695 | 33.581
HAMB4A_HEYS | 400 | 61.9649 | 21.9167 | 6.8331 | 37.828 | 53.8409 | 20.8678 | 4.0695 | 33.581
HAMB4A_PEWO | 400 | 61.9649 | 21.9167 | 6.8331 | 37.828 | 53.8409 | 20.8678 | 4.0695 | 33.581
HAMB4B | 400 | 61.9612 | 21.9151 | 6.8494 | 37.8421 | 53.445 | 20.7138 | 4.0825 | 33.3763
HAMB4B_HEYS | 400 | 61.9612 | 21.9151 | 6.8494 | 37.8421 | 53.445 | 20.7138 | 4.0825 | 33.3763
HAMB4B_PEWO | 400 | 61.9612 | 21.9151 | 6.8494 | 37.8421 | 53.445 | 20.7138 | 4.0825 | 33.3763
HAMH1B | 132 | 44.5847 | 15.3055 | 9.3131 | 30.9583 | 53.1545 | 19.9719 | 6.3239 | 34.5684
HAMH1C | 132 | 43.6888 | 15.0995 | 8.1977 | 29.5516 | 51.5537 | 19.1209 | 7.7732 | 34.8142
HAMH4 M1 | 400 | 71.6327 | 26.2596 | 12.5933 | 49.7299 | 67.9885 | 26.3912 | 13.0009 | 50.3236
HAMH4 M2 | 400 | 71.6327 | 26.2596 | 12.5933 | 49.7299 | 67.9885 | 26.3912 | 13.0009 | 50.3236
HAMH4 R1 | 400 | 71.6327 | 26.2596 | 12.5933 | 49.7299 | 67.9885 | 26.3912 | 13.0009 | 50.3236
HAMH4 R2 | 400 | 71.6327 | 26.2596 | 12.5933 | 49.7299 | 67.9885 | 26.3912 | 13.0009 | 50.3236
HARK1 M1 | 132 | 27.4243 | 10.2639 | 7.0637 | 21.579 | 32.1545 | 12.5033 | 7.6629 | 25.3453
HARK1 M2 | 132 | 27.4243 | 10.2639 | 7.0637 | 21.579 | 32.1545 | 12.5033 | 7.6629 | 25.3453
HARK1 R1 | 132 | 28.3139 | 11.5966 | 6.6566 | 23.0566 | 30.8536 | 12.9657 | 7.5621 | 25.8983
HARK1 R2 | 132 | 29.9976 | 11.4156 | 7.8543 | 23.9984 | 34.9296 | 13.7987 | 9.0548 | 28.569
HARK1 R3 | 132 | 29.9976 | 11.4156 | 7.8543 | 23.9984 | 34.9296 | 13.7987 | 9.0548 | 28.569
HARK2 MC1 | 275 | 41.2027 | 15.3883 | 10.7175 | 32.4799 | 42.2467 | 16.1317 | 11.2102 | 34.0239
HARK2 MC11 | 275 | 43.9496 | 16.605 | 13.895 | 37.378 | 44.9349 | 17.2807 | 14.3972 | 38.8359
HARK2 MC12 | 275 | 43.9496 | 16.605 | 13.895 | 37.378 | 44.9349 | 17.2807 | 14.3972 | 38.8359
HARK2 MC13 | 275 | 43.9496 | 16.605 | 13.895 | 37.378 | 44.9349 | 17.2807 | 14.3972 | 38.8359
HARK2 MC2 | 275 | 41.2027 | 15.3883 | 10.7175 | 32.4799 | 42.2467 | 16.1317 | 11.2102 | 34.0239
HARK2 MC3 | 275 | 41.2027 | 15.3883 | 10.7175 | 32.4799 | 42.2467 | 16.1317 | 11.2102 | 34.0239
HARK2 MC4 | 275 | 41.2027 | 15.3883 | 10.7175 | 32.4799 | 42.2467 | 16.1317 | 11.2102 | 34.0239
HARK2 MC6 | 275 | 41.2027 | 15.3883 | 10.7175 | 32.4799 | 42.2467 | 16.1317 | 11.2102 | 34.0239
HARK2 MC8 | 275 | 43.9496 | 16.605 | 13.895 | 37.378 | 44.9349 | 17.2807 | 14.3972 | 38.8359
HARK2 MC9 | 275 | 43.9496 | 16.605 | 13.895 | 37.378 | 44.9349 | 17.2807 | 14.3972 | 38.8359
HARK4 M1 | 400 | 71.7051 | 26.5253 | 12.1271 | 49.6394 | 55.4022 | 21.6345 | 11.2604 | 41.8562
HARK4 M2 | 400 | 71.7051 | 26.5253 | 12.1271 | 49.6394 | 55.4022 | 21.6345 | 11.2604 | 41.8562
HARK4 R1 | 400 | 71.7051 | 26.5253 | 12.1271 | 49.6394 | 55.4022 | 21.6345 | 11.2604 | 41.8562
HARK4 R2 | 400 | 71.7051 | 26.5253 | 12.1271 | 49.6394 | 55.4022 | 21.6345 | 11.2604 | 41.8562
HARM2 MC1 | 275 | 64.0642 | 23.0879 | 13.0425 | 45.6936 | 55.0107 | 21.4991 | 8.8002 | 39.2045
HARM2 MC2 | 275 | 64.0642 | 23.0879 | 13.0425 | 45.6936 | 55.0107 | 21.4991 | 8.8002 | 39.2045
HARM2 MC3 | 275 | 64.0642 | 23.0879 | 13.0425 | 45.6936 | 55.0107 | 21.4991 | 8.8002 | 39.2045
HARM2 MC4 | 275 | 64.0642 | 23.0879 | 13.0425 | 45.6936 | 55.0107 | 21.4991 | 8.8002 | 39.2045
HATL2 M1 | 275 | 80.599 | 28.3 | 17.8321 | 57.8544 | 81.3507 | 30.4612 | 19.2756 | 62.3542
HATL2 M2 | 275 | 80.599 | 28.3 | 17.8321 | 57.8544 | 81.3507 | 30.4612 | 19.2756 | 62.3542
HATL2 R1 | 275 | 80.599 | 28.3 | 17.8321 | 57.8544 | 81.3507 | 30.4612 | 19.2756 | 62.3542
HATL2 R2 | 275 | 80.599 | 28.3 | 17.8321 | 57.8544 | 81.3507 | 30.4612 | 19.2756 | 62.3542
HAWP2 MC1 | 275 | 89.8505 | 31.6025 | 21.1863 | 65.8789 | 79.0658 | 30.4503 | 14.741 | 57.8042
HAWP2 MC2 | 275 | 89.8505 | 31.6025 | 21.1863 | 65.8789 | 79.0658 | 30.4503 | 14.741 | 57.8042
HAWP2 MC3 | 275 | 89.8505 | 31.6025 | 21.1863 | 65.8789 | 79.0658 | 30.4503 | 14.741 | 57.8042
HAWP2 MC4 | 275 | 89.8505 | 31.6025 | 21.1863 | 65.8789 | 79.0658 | 30.4503 | 14.741 | 57.8042
HEDO2 M1 | 275 | 79.4521 | 27.2746 | 23.8776 | 62.4497 | 78.3295 | 28.6902 | 23.6436 | 64.2177
HEDO2 M2 | 275 | 79.4521 | 27.2746 | 23.8776 | 62.4497 | 78.3295 | 28.6902 | 23.6436 | 64.2177
HEDO2 R1 | 275 | 79.4521 | 27.2746 | 23.8776 | 62.4497 | 78.3295 | 28.6902 | 23.6436 | 64.2177
HEDO2 R2 | 275 | 79.4521 | 27.2746 | 23.8776 | 62.4497 | 78.3295 | 28.6902 | 23.6436 | 64.2177
HEYS1 M1 | 132 | 35.9467 | 12.1023 | 11.457 | 28.5722 | 41.0948 | 14.9935 | 12.8961 | 34.1001
HEYS1 M2 | 132 | 35.9467 | 12.1023 | 11.457 | 28.5722 | 41.0948 | 14.9935 | 12.8961 | 34.1001
HEYS1 R1 | 132 | 35.9467 | 12.1023 | 11.457 | 28.5722 | 41.0948 | 14.9935 | 12.8961 | 34.1001
HEYS1 R2 | 132 | 35.9467 | 12.1023 | 11.457 | 28.5722 | 41.0948 | 14.9935 | 12.8961 | 34.1001
HEYS4 M1 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 M2 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 M3 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 M4 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 M5 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 R1/2 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 R3/4 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HEYS4 R5 | 400 | 80.6222 | 29.2448 | 25.2368 | 66.5951 | 86.9434 | 32.9726 | 28.1275 | 74.7577
HIBU4 M1 | 400 | 104.277 | 35.1394 | 25.6946 | 75.3891 | 118.4609 | 43.9897 | 26.6733 | 88.884
HIBU4 M2 | 400 | 104.277 | 35.1394 | 25.6946 | 75.3891 | 118.4609 | 43.9897 | 26.6733 | 88.884
HIBU4 R1 | 400 | 104.277 | 35.1394 | 25.6946 | 75.3891 | 118.4609 | 43.9897 | 26.6733 | 88.884
HIBU4 R2 | 400 | 104.277 | 35.1394 | 25.6946 | 75.3891 | 118.4609 | 43.9897 | 26.6733 | 88.884
HIGM2 M1 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM2 M2 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM2 M3 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM2 R1 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM2 R4 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM2 R5 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM2 R6 | 275 | 61.534 | 22.6919 | 16.3538 | 48.4449 | 56.1894 | 22.1341 | 11.9793 | 43.2817
HIGM4 MC1 | 400 | 79.6778 | 28.9245 | 17.9206 | 58.826 | 64.0524 | 25.0027 | 11.1553 | 46.5145
HIGM4 MC2 | 400 | 79.6778 | 28.9245 | 17.9206 | 58.826 | 64.0524 | 25.0027 | 11.1553 | 46.5145
HIGM4A | 400 | 62.8815 | 22.6192 | 8.9511 | 40.9395 | 52.6421 | 20.2575 | 4.8248 | 33.4731
HINP2 M1 | 275 | 21.4762 | 7.6105 | 8.06 | 18.8229 | 23.0977 | 8.3696 | 8.4189 | 20.2553
HINP2 M2 | 275 | 21.9192 | 7.7776 | 8.1267 | 19.1258 | 26.383 | 9.6166 | 9.0596 | 22.6594
HINP4 M1 | 400 | 102.6802 | 35.6056 | 26.653 | 77.007 | 112.8903 | 41.6005 | 30.4356 | 89.2676
HINP4 M2 | 400 | 102.6802 | 35.6056 | 26.653 | 77.007 | 112.8903 | 41.6005 | 30.4356 | 89.2676
HINP4 M3 | 400 | 102.6802 | 35.6056 | 26.653 | 77.007 | 112.8903 | 41.6005 | 30.4356 | 89.2676
HINP4 M4 | 400 | 102.6802 | 35.6056 | 26.653 | 77.007 | 112.8903 | 41.6005 | 30.4356 | 89.2676
HINP4 R1/2 | 400 | 102.6802 | 35.6056 | 26.653 | 77.007 | 112.8903 | 41.6005 | 30.4356 | 89.2676
HINP4 R3/4 | 400 | 102.6802 | 35.6056 | 26.653 | 77.007 | 112.8903 | 41.6005 | 30.4356 | 89.2676
HUMR4 M1 | 400 | 107.4181 | 36.4098 | 30.4233 | 81.9146 | 96.1759 | 35.5225 | 26.1802 | 76.4165
HUMR4 M2 | 400 | 107.4181 | 36.4098 | 30.4233 | 81.9146 | 96.1759 | 35.5225 | 26.1802 | 76.4165
HUMR4 R1 | 400 | 107.4181 | 36.4098 | 30.4233 | 81.9146 | 96.1759 | 35.5225 | 26.1802 | 76.4165
HUMR4 R2 | 400 | 107.4181 | 36.4098 | 30.4233 | 81.9146 | 96.1759 | 35.5225 | 26.1802 | 76.4165
HURS2 MC1 | 275 | 75.0747 | 26.5834 | 20.4022 | 57.9967 | 76.2302 | 30.4417 | 16.446 | 59.4971
HURS2 MC2 | 275 | 75.0747 | 26.5834 | 20.4022 | 57.9967 | 76.2302 | 30.4417 | 16.446 | 59.4971
HURS2 MC3 | 275 | 75.0747 | 26.5834 | 20.4022 | 57.9967 | 76.2302 | 30.4417 | 16.446 | 59.4971
HURS2 MC4 | 275 | 75.0747 | 26.5834 | 20.4022 | 57.9967 | 76.2302 | 30.4417 | 16.446 | 59.4971
HUTT4 MC1 | 400 | 66.4295 | 24.8567 | 18.7005 | 53.8531 | 44.3165 | 17.9382 | 10.2321 | 35.6006
HUTT4 MC2 | 400 | 66.4295 | 24.8567 | 18.7005 | 53.8531 | 44.3165 | 17.9382 | 10.2321 | 35.6006
HUTT4 MC3 | 400 | 66.4295 | 24.8567 | 18.7005 | 53.8531 | 44.3165 | 17.9382 | 10.2321 | 35.6006
HUTT4 MC4 | 400 | 66.4295 | 24.8567 | 18.7005 | 53.8531 | 44.3165 | 17.9382 | 10.2321 | 35.6006
IMPP4 MC1 | 400 | 55.2486 | 20.4445 | 12.1309 | 41.0438 | 46.8394 | 18.1215 | 9.6417 | 35.2694
IMPP4 MC2 | 400 | 55.2486 | 20.4445 | 12.1309 | 41.0438 | 46.8394 | 18.1215 | 9.6417 | 35.2694
INDQ4 MC1 | 400 | 38.6175 | 14.6034 | 6.2245 | 26.8769 | 38.6474 | 15.0667 | 7.3506 | 28.6581
INDQ4 MC2 | 400 | 38.6175 | 14.6034 | 6.2245 | 26.8769 | 38.6474 | 15.0667 | 7.3506 | 28.6581
INDQ4 MC3 | 400 | 38.6175 | 14.6034 | 6.2245 | 26.8769 | 38.6474 | 15.0667 | 7.3506 | 28.6581
INDQ4 MC4 | 400 | 38.6175 | 14.6034 | 6.2245 | 26.8769 | 38.6474 | 15.0667 | 7.3506 | 28.6581
IROA1 M1 | 132 | 40.9012 | 14.7537 | 10.1711 | 31.0361 | 49.5196 | 18.7817 | 11.6592 | 38.2206
IROA1 M2 | 132 | 40.9012 | 14.7537 | 10.1711 | 31.0361 | 49.5196 | 18.7817 | 11.6592 | 38.2206
IROA1 R1 | 132 | 43.4537 | 15.6181 | 10.7164 | 32.8038 | 52.3334 | 19.7872 | 12.3038 | 40.2871
IROA1 R2 | 132 | 28.1362 | 10.1859 | 8.4929 | 22.898 | 34.0433 | 12.7412 | 9.5332 | 27.5519
IROA2 MC1 | 275 | 58.1382 | 21.4116 | 11.1434 | 41.4239 | 56.1696 | 21.823 | 11.2175 | 42.0799
IROA2 MC2 | 275 | 58.1382 | 21.4116 | 11.1434 | 41.4239 | 56.1696 | 21.823 | 11.2175 | 42.0799
IROA2 MC3 | 275 | 58.1382 | 21.4116 | 11.1434 | 41.4239 | 56.1696 | 21.823 | 11.2175 | 42.0799
IROA2 MC4 | 275 | 58.1382 | 21.4116 | 11.1434 | 41.4239 | 56.1696 | 21.823 | 11.2175 | 42.0799
IROA2 MC5 | 275 | 58.1382 | 21.4116 | 11.1434 | 41.4239 | 56.1696 | 21.823 | 11.2175 | 42.0799
IRON1 M1 | 132 | 26.9308 | 10.4409 | 8.7435 | 23.5091 | 29.8235 | 11.7051 | 9.6951 | 26.2485
IRON1 M2 | 132 | 26.814 | 10.3992 | 8.6503 | 23.357 | 29.5078 | 11.5961 | 9.5143 | 25.9138
IRON1 R1 | 132 | 17.6317 | 6.4016 | 6.2887 | 15.3419 | 20.045 | 7.3225 | 7.2352 | 17.5907
IRON1 R2 | 132 | 17.6317 | 6.4016 | 6.2887 | 15.3419 | 20.045 | 7.3225 | 7.2352 | 17.5907
IRON4 M1 | 400 | 66.9497 | 24.5431 | 12.0934 | 46.8027 | 57.1998 | 22.4937 | 10.2404 | 42.0513
IRON4 M2 | 400 | 66.9497 | 24.5431 | 12.0934 | 46.8027 | 57.1998 | 22.4937 | 10.2404 | 42.0513
IRON4 R1 | 400 | 66.9497 | 24.5431 | 12.0934 | 46.8027 | 57.1998 | 22.4937 | 10.2404 | 42.0513
IRON4 R2 | 400 | 66.9497 | 24.5431 | 12.0934 | 46.8027 | 57.1998 | 22.4937 | 10.2404 | 42.0513
IVER2 M1 | 275 | 63.9003 | 23.3394 | 15.7012 | 48.708 | 68.2182 | 26.023 | 16.1429 | 52.9449
IVER2 M2 | 275 | 63.9003 | 23.3394 | 15.7012 | 48.708 | 68.2182 | 26.023 | 16.1429 | 52.9449
IVER2 R1 | 275 | 63.9003 | 23.3394 | 15.7012 | 48.708 | 68.2182 | 26.023 | 16.1429 | 52.9449
IVER2 R2 | 275 | 66.6637 | 24.2216 | 14.986 | 49.2405 | 66.5322 | 25.7153 | 13.7954 | 50.1623
IVER4A | 400 | 43.9844 | 16.113 | 5.2857 | 28.0729 | 41.6274 | 15.9446 | 5.5651 | 28.1142
IVER4B | 400 | 42.2683 | 15.5405 | 4.9272 | 26.9048 | 39.5117 | 15.3476 | 4.7651 | 26.4699
JORD2 MC1 | 275 | 50.2688 | 18.8912 | 8.8124 | 35.5287 | 49.3327 | 20.3713 | 7.2673 | 36.0767
JORD2 MC2 | 275 | 50.2688 | 18.8912 | 8.8124 | 35.5287 | 49.3327 | 20.3713 | 7.2673 | 36.0767
KEAD4 M2 | 400 | 108.6702 | 37.5799 | 27.9985 | 81.1445 | 99.8029 | 37.1989 | 25.423 | 78.0302
KEAD4 M3 | 400 | 109.151 | 37.5761 | 28.524 | 81.6646 | 87.5971 | 32.977 | 20.1992 | 66.8358
KEAD4 R2 | 400 | 108.6702 | 37.5799 | 27.9985 | 81.1445 | 99.8029 | 37.1989 | 25.423 | 78.0302
KEAD4 R3 | 400 | 93.0135 | 33.6786 | 20.6783 | 68.307 | 71.7856 | 27.8539 | 15.2055 | 54.5969
KEAR2 M1 | 275 | 74.0623 | 26.4831 | 18.5628 | 56.0156 | 79.4951 | 30.0158 | 19.297 | 61.7457
KEAR2 M2 | 275 | 74.0623 | 26.4831 | 18.5628 | 56.0156 | 79.4951 | 30.0158 | 19.297 | 61.7457
KEAR2 R1 | 275 | 74.0623 | 26.4831 | 18.5628 | 56.0156 | 79.4951 | 30.0158 | 19.297 | 61.7457
KEAR2 R2 | 275 | 74.0623 | 26.4831 | 18.5628 | 56.0156 | 79.4951 | 30.0158 | 19.297 | 61.7457
KEMS4 M1 | 400 | 131.3676 | 45.1411 | 29.8075 | 93.6466 | 105.406 | 40.4797 | 20.7075 | 77.9545
KEMS4 M2 | 400 | 131.3676 | 45.1411 | 29.8075 | 93.6466 | 105.406 | 40.4797 | 20.7075 | 77.9545
KEMS4 R1 | 400 | 131.3676 | 45.1411 | 29.8075 | 93.6466 | 105.406 | 40.4797 | 20.7075 | 77.9545
KEMS4 R2 | 400 | 131.3676 | 45.1411 | 29.8075 | 93.6466 | 105.406 | 40.4797 | 20.7075 | 77.9545
KENG4 M1 | 400 | 107.6457 | 36.1002 | 26.4881 | 77.5415 | 122.3343 | 45.2128 | 28.4161 | 92.3566
KENG4 M2 | 400 | 107.6457 | 36.1002 | 26.4881 | 77.5415 | 122.3343 | 45.2128 | 28.4161 | 92.3566
KENG4 R1 | 400 | 107.6457 | 36.1002 | 26.4881 | 77.5415 | 122.3343 | 45.2128 | 28.4161 | 92.3566
KENG4 R2 | 400 | 107.6457 | 36.1002 | 26.4881 | 77.5415 | 122.3343 | 45.2128 | 28.4161 | 92.3566
KIBY2 M1 | 275 | 69.1471 | 24.3082 | 16.6505 | 51.0274 | 73.5787 | 27.7276 | 16.2072 | 55.42
KIBY2 M2 | 275 | 69.1471 | 24.3082 | 16.6505 | 51.0274 | 73.5787 | 27.7276 | 16.2072 | 55.42
KIBY2 R1 | 275 | 59.9454 | 21.4364 | 14.0248 | 44.3405 | 59.0349 | 22.3813 | 13.0852 | 44.7371
KIBY2 R2 | 275 | 59.9454 | 21.4364 | 14.0248 | 44.3405 | 59.0349 | 22.3813 | 13.0852 | 44.7371
KILL4 M1 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 M2 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 M3 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 M4 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 M5 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 M9 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 R1/2 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 R3/4 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 R5 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KILL4 R9 | 400 | 112.4475 | 39.0523 | 40.1388 | 95.367 | 104.2917 | 38.6837 | 35.6846 | 90.3917
KINO1 M1 | 132 | 29.2182 | 10.3062 | 10.5963 | 25.1715 | 35.4554 | 13.1164 | 12.6371 | 31.1865
KINO1 M2 | 132 | 29.2182 | 10.3062 | 10.5963 | 25.1715 | 35.4554 | 13.1164 | 12.6371 | 31.1865
KINO1 R1 | 132 | 29.2182 | 10.3062 | 10.5963 | 25.1715 | 35.4554 | 13.1164 | 12.6371 | 31.1865
KINO1 R2 | 132 | 29.2182 | 10.3062 | 10.5963 | 25.1715 | 35.4554 | 13.1164 | 12.6371 | 31.1865
KINO1A | 132 | 28.8769 | 10.1118 | 6.606 | 20.9062 | 34.9559 | 12.9656 | 7.6952 | 26.0314
KINO1B | 132 | 24.1756 | 9.0146 | 1.6653 | 14.4139 | 25.8653 | 10.4312 | 0.9445 | 15.6964
KINO4 M1 | 400 | 131.8683 | 46.6216 | 42.2337 | 108.1665 | 112.6982 | 42.964 | 34.2571 | 95.0174
KINO4 M2 | 400 | 131.8683 | 46.6216 | 42.2337 | 108.1665 | 112.6982 | 42.964 | 34.2571 | 95.0174
KINO4 M3 | 400 | 131.8683 | 46.6216 | 42.2337 | 108.1665 | 112.6982 | 42.964 | 34.2571 | 95.0174
KINO4 M4 | 400 | 131.8683 | 46.6216 | 42.2337 | 108.1665 | 112.6982 | 42.964 | 34.2571 | 95.0174
KINO4 R1/2 | 400 | 131.8683 | 46.6216 | 42.2337 | 108.1665 | 112.6982 | 42.964 | 34.2571 | 95.0174
KINO4 R3/4 | 400 | 131.8683 | 46.6216 | 42.2337 | 108.1665 | 112.6982 | 42.964 | 34.2571 | 95.0174
KIRK2 MC1 | 275 | 54.1975 | 19.652 | 12.2394 | 40.0315 | 55.0879 | 21.1686 | 13.1276 | 43.0646
KIRK2 MC2 | 275 | 54.1975 | 19.652 | 12.2394 | 40.0315 | 55.0879 | 21.1686 | 13.1276 | 43.0646
KIRK2 MC3 | 275 | 54.1975 | 19.652 | 12.2394 | 40.0315 | 55.0879 | 21.1686 | 13.1276 | 43.0646
KIRK2 MC4 | 275 | 54.1975 | 19.652 | 12.2394 | 40.0315 | 55.0879 | 21.1686 | 13.1276 | 43.0646
KIRK2A | 275 | 53.6086 | 18.9414 | 6.4517 | 33.2389 | 50.958 | 19.9082 | 8.1037 | 36.2582
KITW2 MC1 | 275 | 59.8575 | 21.622 | 11.6472 | 42.2254 | 59.0224 | 22.9647 | 10.3076 | 42.7847
KITW2 MC2 | 275 | 59.8575 | 21.622 | 11.6472 | 42.2254 | 59.0224 | 22.9647 | 10.3076 | 42.7847
KITW2 MC3 | 275 | 59.8575 | 21.622 | 11.6472 | 42.2254 | 59.0224 | 22.9647 | 10.3076 | 42.7847
KITW2 MC4 | 275 | 59.8575 | 21.622 | 11.6472 | 42.2254 | 59.0224 | 22.9647 | 10.3076 | 42.7847
KNAR2 MC1 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
KNAR2 MC1 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
KNAR2 MC1 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
KNAR2 MC1 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
KNAR2 MC2 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
KNAR2 MC2 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
KNAR2 MC2 | 275 | 29.4105 | 11.8621 | 2.4519 | 19.2274 | 26.8219 | 11.0932 | 3.5292 | 19.2173
LACK2 M1 | 275 | 65.7498 | 22.1823 | 19.6226 | 50.9932 | 66.895 | 24.4062 | 19.6035 | 54.119
LACK2 M2 | 275 | 65.7498 | 22.1823 | 19.6226 | 50.9932 | 66.895 | 24.4062 | 19.6035 | 54.119
LACK2 R1 | 275 | 65.7498 | 22.1823 | 19.6226 | 50.9932 | 66.895 | 24.4062 | 19.6035 | 54.119
LACK2 R2 | 275 | 65.7498 | 22.1823 | 19.6226 | 50.9932 | 66.895 | 24.4062 | 19.6035 | 54.119
LACK4 M1 | 400 | 121.3391 | 38.9354 | 42.261 | 97.3239 | 76.5562 | 28.3902 | 24.5131 | 64.6629
LACK4 M2 | 400 | 121.3391 | 38.9354 | 42.261 | 97.3239 | 76.5562 | 28.3902 | 24.5131 | 64.6629
LACK4 R1 | 400 | 121.3391 | 38.9354 | 42.261 | 97.3239 | 76.5562 | 28.3902 | 24.5131 | 64.6629
LACK4 R2 | 400 | 121.3391 | 38.9354 | 42.261 | 97.3239 | 76.5562 | 28.3902 | 24.5131 | 64.6629
LAGA4 M1 | 400 | 46.7002 | 17.2774 | 9.2611 | 33.695 | 45.8521 | 17.6647 | 10.216 | 35.1976
LAGA4 M2 | 400 | 46.7002 | 17.2774 | 9.2611 | 33.695 | 45.8521 | 17.6647 | 10.216 | 35.1976
LAGA4 R1 | 400 | 46.7002 | 17.2774 | 9.2611 | 33.695 | 45.8521 | 17.6647 | 10.216 | 35.1976
LAGA4 R2 | 400 | 46.7002 | 17.2774 | 9.2611 | 33.695 | 45.8521 | 17.6647 | 10.216 | 35.1976
LALE2 MC1 | 275 | 59.4077 | 21.1245 | 16.7258 | 46.6004 | 64.9817 | 25.1135 | 15.7686 | 51.2845
LALE2 MC2 | 275 | 59.4077 | 21.1245 | 16.7258 | 46.6004 | 64.9817 | 25.1135 | 15.7686 | 51.2845
LALE2 MC3 | 275 | 59.4077 | 21.1245 | 16.7258 | 46.6004 | 64.9817 | 25.1135 | 15.7686 | 51.2845
LALE2 MC4 | 275 | 59.4077 | 21.1245 | 16.7258 | 46.6004 | 64.9817 | 25.1135 | 15.7686 | 51.2845
LAND4 MC1 | 400 | 36.8537 | 13.8625 | 6.6784 | 26.2829 | 34.6659 | 13.6018 | 6.1383 | 25.3742
LAND4 MC2 | 400 | 36.8537 | 13.8625 | 6.6784 | 26.2829 | 34.6659 | 13.6018 | 6.1383 | 25.3742
LEGA4 M1 | 400 | 80.4849 | 28.9334 | 16.6606 | 57.5786 | 63.8183 | 25.139 | 11.308 | 46.8599
LEGA4 M2 | 400 | 80.4849 | 28.9334 | 16.6606 | 57.5786 | 63.8183 | 25.139 | 11.308 | 46.8599
LEGA4 R1 | 400 | 80.4849 | 28.9334 | 16.6606 | 57.5786 | 63.8183 | 25.139 | 11.308 | 46.8599
LEGA4 R2 | 400 | 80.4849 | 28.9334 | 16.6606 | 57.5786 | 63.8183 | 25.139 | 11.308 | 46.8599
LEIS1 M1 | 132 | 67.9339 | 23.9538 | 22.5915 | 56.4674 | 77.4024 | 28.1031 | 27.3835 | 67.1272
LEIS1 M2 | 132 | 67.9339 | 23.9538 | 22.5915 | 56.4674 | 77.4024 | 28.1031 | 27.3835 | 67.1272
LEIS1 R1 | 132 | 67.9339 | 23.9538 | 22.5915 | 56.4674 | 77.4024 | 28.1031 | 27.3835 | 67.1272
LEIS1 R2 | 132 | 67.9339 | 23.9538 | 22.5915 | 56.4674 | 77.4024 | 28.1031 | 27.3835 | 67.1272
LISD2 M1 | 275 | 64.1867 | 22.6876 | 15.1967 | 47.2818 | 68.8993 | 26.1472 | 14.9916 | 51.9693
LISD2 M2 | 275 | 64.1867 | 22.6876 | 15.1967 | 47.2818 | 68.8993 | 26.1472 | 14.9916 | 51.9693
LISD2 R1 | 275 | 64.1867 | 22.6876 | 15.1967 | 47.2818 | 68.8993 | 26.1472 | 14.9916 | 51.9693
LISD2 R2 | 275 | 64.1867 | 22.6876 | 15.1967 | 47.2818 | 68.8993 | 26.1472 | 14.9916 | 51.9693
LITB4 Term500 | 400 | 65.4893 | 23.4608 | 5.4433 | 38.6218 | 61.1352 | 23.1701 | 8.5902 | 41.3577
LITT4 M1 | 400 | 135.1433 | 46.3188 | 30.38 | 95.8847 | 114.7989 | 44.0835 | 23.4215 | 85.765
LITT4 M2 | 400 | 135.1433 | 46.3188 | 30.38 | 95.8847 | 114.7989 | 44.0835 | 23.4215 | 85.765
LITT4 M3 | 400 | 135.1433 | 46.3188 | 30.38 | 95.8847 | 114.7989 | 44.0835 | 23.4215 | 85.765
LITT4 R1 | 400 | 135.1433 | 46.3188 | 30.38 | 95.8847 | 114.7989 | 44.0835 | 23.4215 | 85.765
LITT4 R2 | 400 | 135.1433 | 46.3188 | 30.38 | 95.8847 | 114.7989 | 44.0835 | 23.4215 | 85.765
LITT4 R3 | 400 | 135.1433 | 46.3188 | 30.38 | 95.8847 | 114.7989 | 44.0835 | 23.4215 | 85.765
LOFI4A | 400 | 108.5422 | 37.0621 | 10.767 | 63.1807 | 85.9798 | 33.3008 | 5.1441 | 52.2385
LOFI4A_KEMS | 400 | 108.5422 | 37.0621 | 10.767 | 63.1807 | 85.9798 | 33.3008 | 5.1441 | 52.2385
LOFI4A_LITT | 400 | 108.5422 | 37.0621 | 10.767 | 63.1807 | 85.9798 | 33.3008 | 5.1441 | 52.2385
LOFI4A_ROWD | 400 | 108.5422 | 37.0621 | 10.767 | 63.1807 | 85.9798 | 33.3008 | 5.1441 | 52.2385
LOFI4B | 400 | 107.4116 | 36.7818 | 10.5132 | 62.5305 | 86.9311 | 33.6788 | 5.1532 | 52.7822
LOFI4B_KEMS | 400 | 107.4116 | 36.7818 | 10.5132 | 62.5305 | 86.9311 | 33.6788 | 5.1532 | 52.7822
LOFI4B_LITT | 400 | 107.4116 | 36.7818 | 10.5132 | 62.5305 | 86.9311 | 33.6788 | 5.1532 | 52.7822
LOFI4B_ROWD | 400 | 107.4116 | 36.7818 | 10.5132 | 62.5305 | 86.9311 | 33.6788 | 5.1532 | 52.7822
LOVE4 M1 | 400 | 99.1532 | 35.6351 | 18.2483 | 68.644 | 83.646 | 32.5203 | 15.1589 | 61.1495
LOVE4 M2 | 400 | 99.1532 | 35.6351 | 18.2483 | 68.644 | 83.646 | 32.5203 | 15.1589 | 61.1495
LOVE4 R1 | 400 | 99.1532 | 35.6351 | 18.2483 | 68.644 | 83.646 | 32.5203 | 15.1589 | 61.1495
LOVE4 R2 | 400 | 99.1532 | 35.6351 | 18.2483 | 68.644 | 83.646 | 32.5203 | 15.1589 | 61.1495
MACC2 MC1 | 275 | 55.5881 | 20.4419 | 13.4711 | 42.3803 | 52.2838 | 20.1512 | 11.6476 | 40.1458
MACC2 MC2 | 275 | 55.5881 | 20.4419 | 13.4711 | 42.3803 | 52.2838 | 20.1512 | 11.6476 | 40.1458
MACC4 MC1 | 400 | 78.6132 | 29.3596 | 22.0426 | 63.5634 | 60.2158 | 24.0194 | 14.7367 | 48.7053
MACC4 MC2 | 400 | 78.6132 | 29.3596 | 22.0426 | 63.5634 | 60.2158 | 24.0194 | 14.7367 | 48.7053
MACC4 MC3 | 400 | 78.6132 | 29.3596 | 22.0426 | 63.5634 | 60.2158 | 24.0194 | 14.7367 | 48.7053
MACC4 MC4 | 400 | 78.6132 | 29.3596 | 22.0426 | 63.5634 | 60.2158 | 24.0194 | 14.7367 | 48.7053
MAGA2 MC1 | 275 | 52.3587 | 19.329 | 11.2962 | 38.6315 | 45.51 | 18.0068 | 8.3293 | 33.7947
MAGA2 MC2 | 275 | 52.3587 | 19.329 | 11.2962 | 38.6315 | 45.51 | 18.0068 | 8.3293 | 33.7947
MANN4 M5 | 400 | 60.0605 | 22.079 | 11.3817 | 42.6062 | 53.3598 | 20.5326 | 11.3597 | 40.3972
MANN4 MC1 | 400 | 60.0605 | 22.079 | 11.3817 | 42.6062 | 53.3598 | 20.5326 | 11.3597 | 40.3972
MANN4 MC2 | 400 | 60.0605 | 22.079 | 11.3817 | 42.6062 | 53.3598 | 20.5326 | 11.3597 | 40.3972
MANN4 MC3 | 400 | 60.0605 | 22.079 | 11.3817 | 42.6062 | 53.3598 | 20.5326 | 11.3597 | 40.3972
MANN4 MC4 | 400 | 60.0605 | 22.079 | 11.3817 | 42.6062 | 53.3598 | 20.5326 | 11.3597 | 40.3972
MANN4 R5 | 400 | 60.0605 | 22.079 | 11.3817 | 42.6062 | 53.3598 | 20.5326 | 11.3597 | 40.3972
MAWO4 M | 400 | 67.7517 | 24.67 | 12.8302 | 47.7188 | 61.8606 | 23.5925 | 13.8233 | 47.1881
MAWO4 R | 400 | 67.7517 | 24.67 | 12.8302 | 47.7188 | 61.8606 | 23.5925 | 13.8233 | 47.1881
MEDW4 Term500 | 400 | 116.966 | 40.718 | 24.903 | 82.4869 | 100.8584 | 38.2891 | 22.4642 | 76.6132
MELK1 M1 | 132 | 42.6304 | 14.8986 | 15.1021 | 36.172 | 52.7679 | 19.3609 | 17.6523 | 45.0327
MELK1 M2 | 132 | 42.6304 | 14.8986 | 15.1021 | 36.172 | 52.7679 | 19.3609 | 17.6523 | 45.0327
MELK1 R1 | 132 | 42.6304 | 14.8986 | 15.1021 | 36.172 | 52.7679 | 19.3609 | 17.6523 | 45.0327
MELK1 R2 | 132 | 42.6304 | 14.8986 | 15.1021 | 36.172 | 52.7679 | 19.3609 | 17.6523 | 45.0327
MELK4 M1 | 400 | 104.0111 | 38.0067 | 19.8919 | 73.6416 | 86.6656 | 34.2012 | 14.4674 | 62.8352
MELK4 M2 | 400 | 104.0111 | 38.0067 | 19.8919 | 73.6416 | 86.6656 | 34.2012 | 14.4674 | 62.8352
MELK4 M3 | 400 | 104.0111 | 38.0067 | 19.8919 | 73.6416 | 86.6656 | 34.2012 | 14.4674 | 62.8352
MELK4 R1 | 400 | 104.0111 | 38.0067 | 19.8919 | 73.6416 | 86.6656 | 34.2012 | 14.4674 | 62.8352
MELK4 R2 | 400 | 104.0111 | 38.0067 | 19.8919 | 73.6416 | 86.6656 | 34.2012 | 14.4674 | 62.8352
MELK4 R3 | 400 | 104.0111 | 38.0067 | 19.8919 | 73.6416 | 86.6656 | 34.2012 | 14.4674 | 62.8352
MILH1 M1 | 132 | 39.505 | 14.4914 | 8.9011 | 29.3951 | 45.5628 | 18.4894 | 8.9463 | 35.0943
MILH1 M2 | 132 | 39.505 | 14.4914 | 8.9011 | 29.3951 | 45.5628 | 18.4894 | 8.9463 | 35.0943
MILH1 R1 | 132 | 39.4739 | 14.4898 | 8.8213 | 29.3129 | 45.452 | 18.4795 | 8.7827 | 34.9167
MILH1 R2 | 132 | 39.4739 | 14.4898 | 8.8213 | 29.3129 | 45.452 | 18.4795 | 8.7827 | 34.9167
MITY4 MC1 | 400 | 78.5789 | 29.9193 | 20.6663 | 62.9787 | 59.8275 | 24.1769 | 13.9007 | 48.0919
MITY4 MC2 | 400 | 78.5789 | 29.9193 | 20.6663 | 62.9787 | 59.8275 | 24.1769 | 13.9007 | 48.0919
MITY4 MC3 | 400 | 78.5789 | 29.9193 | 20.6663 | 62.9787 | 59.8275 | 24.1769 | 13.9007 | 48.0919
MITY4 MC4 | 400 | 78.5789 | 29.9193 | 20.6663 | 62.9787 | 59.8275 | 24.1769 | 13.9007 | 48.0919
MONF2 M1 | 275 | 67.2981 | 24.2512 | 18.3037 | 52.6001 | 67.6777 | 25.6885 | 16.5525 | 52.8816
MONF2 M2 | 275 | 67.2981 | 24.2512 | 18.3037 | 52.6001 | 67.6777 | 25.6885 | 16.5525 | 52.8816
MONF2 R1 | 275 | 58.3918 | 21.0992 | 18.7809 | 48.6196 | 60.7399 | 22.7879 | 17.7527 | 49.9796
MONF2 R2 | 275 | 58.3918 | 21.0992 | 18.7809 | 48.6196 | 60.7399 | 22.7879 | 17.7527 | 49.9796
MONF4 MC2 | 400 | 86.1174 | 30.9463 | 20.3142 | 64.0789 | 73.6868 | 28.1418 | 16.2559 | 56.0545
MONF4 MC3 | 400 | 86.1174 | 30.9463 | 20.3142 | 64.0789 | 73.6868 | 28.1418 | 16.2559 | 56.0545
NECH2 MC1 | 275 | 70.4805 | 25.1059 | 17.8984 | 53.4034 | 71.6688 | 27.4609 | 15.6213 | 54.4568
NECH2 MC2 | 275 | 70.4805 | 25.1059 | 17.8984 | 53.4034 | 71.6688 | 27.4609 | 15.6213 | 54.4568
NECH2 MC3 | 275 | 70.4805 | 25.1059 | 17.8984 | 53.4034 | 71.6688 | 27.4609 | 15.6213 | 54.4568
NECH2 MC4 | 275 | 70.4805 | 25.1059 | 17.8984 | 53.4034 | 71.6688 | 27.4609 | 15.6213 | 54.4568
NECT4 M1 | 400 | 88.1171 | 31.1935 | 22.2956 | 66.4099 | 56.8151 | 22.3965 | 11.367 | 43.0405
NECT4 R1 | 400 | 88.1171 | 31.1935 | 22.2956 | 66.4099 | 56.8151 | 22.3965 | 11.367 | 43.0405
NEEP2 M1 | 275 | 59.452 | 21.867 | 12.7474 | 43.672 | 62.0069 | 24.6396 | 11.9328 | 46.7785
NEEP2 M2 | 275 | 59.452 | 21.867 | 12.7474 | 43.672 | 62.0069 | 24.6396 | 11.9328 | 46.7785
NEEP2 R1/R2 | 275 | 59.452 | 21.867 | 12.7474 | 43.672 | 62.0069 | 24.6396 | 11.9328 | 46.7785
NEWX2 M5 | 275 | 83.4878 | 29.3785 | 21.9613 | 63.5087 | 88.2515 | 34.6787 | 18.1079 | 67.151
NEWX2 M5 | 275 | 83.4878 | 29.3785 | 21.9613 | 63.5087 | 88.2515 | 34.6787 | 18.1079 | 67.151
NEWX2 M6 | 275 | 83.4878 | 29.3785 | 21.9613 | 63.5087 | 88.2515 | 34.6787 | 18.1079 | 67.151
NEWX2 R6 | 275 | 83.4878 | 29.3785 | 21.9613 | 63.5087 | 88.2515 | 34.6787 | 18.1079 | 67.151
NEWX21 R5 | 275 | 83.4878 | 29.3785 | 21.9613 | 63.5087 | 88.2515 | 34.6787 | 18.1079 | 67.151
NFLE4 M1 | 400 | 109.4453 | 38.2417 | 23.872 | 77.954 | 83.2984 | 32.6105 | 14.9872 | 61.1053
NFLE4 M2 | 400 | 109.4453 | 38.2417 | 23.872 | 77.954 | 83.2984 | 32.6105 | 14.9872 | 61.1053
NFLE4 R1 | 400 | 109.4453 | 38.2417 | 23.872 | 77.954 | 83.2984 | 32.6105 | 14.9872 | 61.1053
NFLE4 R2 | 400 | 109.4453 | 38.2417 | 23.872 | 77.954 | 83.2984 | 32.6105 | 14.9872 | 61.1053
NHYD2A | 275 | 44.5132 | 16.9108 | 2.4599 | 26.3753 | 38.1059 | 17.9713 | 0.45452 | 25.8697
NHYD2B | 275 | 45.9094 | 17.3152 | 2.2076 | 26.695 | 39.3664 | 18.0013 | 1.0376 | 26.4953
NHYD2C | 275 | 45.9094 | 17.3152 | 2.2076 | 26.695 | 39.3664 | 18.0013 | 1.0376 | 26.4953
NINF4 M1 | 400 | 66.3675 | 24.416 | 13.2578 | 47.7872 | 60.8666 | 23.3693 | 13.5695 | 46.6187
NINF4 M2 | 400 | 66.3675 | 24.416 | 13.2578 | 47.7872 | 60.8666 | 23.3693 | 13.5695 | 46.6187
NINF4 R1 | 400 | 66.3675 | 24.416 | 13.2578 | 47.7872 | 60.8666 | 23.3693 | 13.5695 | 46.6187
NINF4 R2 | 400 | 66.3675 | 24.416 | 13.2578 | 47.7872 | 60.8666 | 23.3693 | 13.5695 | 46.6187
NORL2A | 275 | 51.95 | 19.0385 | 3.9017 | 30.8262 | 50.968 | 20.9418 | 2.2758 | 31.892
NORL2B | 275 | 51.0993 | 18.8029 | 3.3854 | 29.9767 | 50.0588 | 20.8611 | 2.0034 | 31.5055
NORM4 M1 | 400 | 79.266 | 28.6516 | 18.0688 | 58.5884 | 54.6077 | 21.4804 | 11.6125 | 41.9903
NORM4 M2 | 400 | 79.266 | 28.6516 | 18.0688 | 58.5884 | 54.6077 | 21.4804 | 11.6125 | 41.9903
NORM4 R1 | 400 | 79.266 | 28.6516 | 18.0688 | 58.5884 | 54.6077 | 21.4804 | 11.6125 | 41.9903
NORM4 R2 | 400 | 79.266 | 28.6516 | 18.0688 | 58.5884 | 54.6077 | 21.4804 | 11.6125 | 41.9903
NORT2 M1 | 275 | 78.0503 | 27.1054 | 22.0943 | 60.4271 | 75.3307 | 28.2745 | 18.2275 | 58.2137
NORT2 M2 | 275 | 78.0503 | 27.1054 | 22.0943 | 60.4271 | 75.3307 | 28.2745 | 18.2275 | 58.2137
NORT2 R1 | 275 | 78.0503 | 27.1054 | 22.0943 | 60.4271 | 75.3307 | 28.2745 | 18.2275 | 58.2137
NORT2 R2 | 275 | 78.0503 | 27.1054 | 22.0943 | 60.4271 | 75.3307 | 28.2745 | 18.2275 | 58.2137
NORT4 M1 | 400 | 120.0635 | 42.5165 | 36.332 | 96.4595 | 84.2103 | 32.5546 | 23.0159 | 69.0551
NORT4 M2 | 400 | 120.0635 | 42.5165 | 36.332 | 96.4595 | 84.2103 | 32.5546 | 23.0159 | 69.0551
NORT4 R1 | 400 | 120.0635 | 42.5165 | 36.332 | 96.4595 | 84.2103 | 32.5546 | 23.0159 | 69.0551
NORT4 R2 | 400 | 120.0635 | 42.5165 | 36.332 | 96.4595 | 84.2103 | 32.5546 | 23.0159 | 69.0551
NURS4 MC1 | 400 | 63.8041 | 23.0542 | 7.9479 | 40.5514 | 58.2596 | 22.1996 | 8.3833 | 39.7783
NURS4 MC2 | 400 | 63.8041 | 23.0542 | 7.9479 | 40.5514 | 58.2596 | 22.1996 | 8.3833 | 39.7783
NURS4A | 400 | 53.9963 | 19.9814 | 10.644 | 38.9019 | 48.7459 | 18.6929 | 10.6126 | 37.0484
OCKH1 M1 | 132 | 24.7198 | 8.827 | 8.4551 | 20.9383 | 33.1521 | 12.1409 | 11.0444 | 28.2142
OCKH1 M2 | 132 | 24.7198 | 8.827 | 8.4551 | 20.9383 | 33.1521 | 12.1409 | 11.0444 | 28.2142
OCKH1 R1 | 132 | 24.7198 | 8.827 | 8.4551 | 20.9383 | 33.1521 | 12.1409 | 11.0444 | 28.2142
OCKH1 R2 | 132 | 24.7198 | 8.827 | 8.4551 | 20.9383 | 33.1521 | 12.1409 | 11.0444 | 28.2142
OCKH2 MC1 | 275 | 53.886 | 19.5943 | 10.3613 | 38.0718 | 56.0289 | 21.8007 | 10.5727 | 41.4035
OCKH2 MC2 | 275 | 53.886 | 19.5943 | 10.3613 | 38.0718 | 56.0289 | 21.8007 | 10.5727 | 41.4035
OCKH2 MC3 | 275 | 53.886 | 19.5943 | 10.3613 | 38.0718 | 56.0289 | 21.8007 | 10.5727 | 41.4035
OCKH2 MC4 | 275 | 53.886 | 19.5943 | 10.3613 | 38.0718 | 56.0289 | 21.8007 | 10.5727 | 41.4035
OCKH2A | 275 | 47.4146 | 16.9056 | 4.2052 | 28.1133 | 47.7464 | 18.3679 | 4.6408 | 30.617
OFFE2 MC1 | 275 | 70.9514 | 25.6253 | 14.1071 | 50.3467 | 60.7108 | 24.121 | 8.6579 | 42.7702
OFFE2 MC2 | 275 | 70.9514 | 25.6253 | 14.1071 | 50.3467 | 60.7108 | 24.121 | 8.6579 | 42.7702
OLDB2 MC1 | 275 | 51.6378 | 18.877 | 10.3993 | 37.0954 | 53.4006 | 20.6073 | 10.6401 | 39.7832
OLDB2 MC2 | 275 | 51.6378 | 18.877 | 10.3993 | 37.0954 | 53.4006 | 20.6073 | 10.6401 | 39.7832
OSBA4 MC1 | 400 | 83.4555 | 29.9675 | 20.0373 | 62.4178 | 71.0405 | 27.0675 | 16.437 | 54.7162
OSBA4 MC2 | 400 | 83.4555 | 29.9675 | 20.0373 | 62.4178 | 71.0405 | 27.0675 | 16.437 | 54.7162
OSBA4 MC3/4 | 400 | 97.7426 | 34.0796 | 23.7887 | 71.9846 | 71.8246 | 27.5016 | 15.1002 | 53.9933
PADI1 M1 | 132 | 31.2156 | 10.9728 | 10.9084 | 26.4263 | 38.6001 | 14.1415 | 13.167 | 33.166
PADI1 M2 | 132 | 31.2156 | 10.9728 | 10.9084 | 26.4263 | 38.6001 | 14.1415 | 13.167 | 33.166
PADI1 R1 | 132 | 31.2156 | 10.9728 | 10.9084 | 26.4263 | 38.6001 | 14.1415 | 13.167 | 33.166
PADI1 R2 | 132 | 31.2156 | 10.9728 | 10.9084 | 26.4263 | 38.6001 | 14.1415 | 13.167 | 33.166
PADI4 MC1 | 400 | 72.4818 | 26.3419 | 15.0784 | 52.3314 | 54.9228 | 21.6566 | 9.3894 | 40.0164
PADI4 MC2 | 400 | 72.4818 | 26.3419 | 15.0784 | 52.3314 | 54.9228 | 21.6566 | 9.3894 | 40.0164
PADI4 MC3 | 400 | 72.4818 | 26.3419 | 15.0784 | 52.3314 | 54.9228 | 21.6566 | 9.3894 | 40.0164
PADI4 MC4 | 400 | 72.4818 | 26.3419 | 15.0784 | 52.3314 | 54.9228 | 21.6566 | 9.3894 | 40.0164
PELH4 M1 | 400 | 117.7321 | 41.3908 | 26.7579 | 85.2933 | 97.7465 | 37.6968 | 18.6287 | 71.9401
PELH4 M2 | 400 | 117.7321 | 41.3908 | 26.7579 | 85.2933 | 97.7465 | 37.6968 | 18.6287 | 71.9401
PELH4 R1 | 400 | 117.7321 | 41.3908 | 26.7579 | 85.2933 | 97.7465 | 37.6968 | 18.6287 | 71.9401
PELH4 R2 | 400 | 117.7321 | 41.3908 | 26.7579 | 85.2933 | 97.7465 | 37.6968 | 18.6287 | 71.9401
PEMB4 M1 | 400 | 63.284 | 22.3046 | 18.5353 | 50.0788 | 66.0988 | 24.2863 | 20.7721 | 55.1181
PEMB4 M2 | 400 | 63.284 | 22.3046 | 18.5353 | 50.0788 | 66.0988 | 24.2863 | 20.7721 | 55.1181
PEMB4 M3 | 400 | 63.284 | 22.3046 | 18.5353 | 50.0788 | 66.0988 | 24.2863 | 20.7721 | 55.1181
PEMB4 M4 | 400 | 63.284 | 22.3046 | 18.5353 | 50.0788 | 66.0988 | 24.2863 | 20.7721 | 55.1181
PEMB4 R1/2 | 400 | 63.284 | 22.3046 | 18.5353 | 50.0788 | 66.0988 | 24.2863 | 20.7721 | 55.1181
PEMB4 R3/4 | 400 | 63.284 | 22.3046 | 18.5353 | 50.0788 | 66.0988 | 24.2863 | 20.7721 | 55.1181
PENN2 MC1 | 275 | 63.6779 | 22.9718 | 13.3605 | 45.8475 | 67.0034 | 25.5967 | 14.1986 | 50.3978
PENN2 MC2 | 275 | 63.6779 | 22.9718 | 13.3605 | 45.8475 | 67.0034 | 25.5967 | 14.1986 | 50.3978
PENN2 MC3 | 275 | 63.6779 | 22.9718 | 13.3605 | 45.8475 | 67.0034 | 25.5967 | 14.1986 | 50.3978
PENN2 MC4 | 275 | 63.6779 | 22.9718 | 13.3605 | 45.8475 | 67.0034 | 25.5967 | 14.1986 | 50.3978
PENT4 M1 | 400 | 78.0581 | 27.0542 | 20.1865 | 58.4469 | 75.15 | 27.9144 | 19.741 | 59.218
PENT4 M2 | 400 | 78.0581 | 27.0542 | 20.1865 | 58.4469 | 75.15 | 27.9144 | 19.741 | 59.218
PENT4 R1 | 400 | 78.0581 | 27.0542 | 20.1865 | 58.4469 | 75.15 | 27.9144 | 19.741 | 59.218
PENT4 R2 | 400 | 78.0581 | 27.0542 | 20.1865 | 58.4469 | 75.15 | 27.9144 | 19.741 | 59.218
PEWO2A | 275 | 62.7786 | 22.4381 | 18.1302 | 49.8624 | 65.3459 | 24.4028 | 18.0011 | 52.5119
PEWO2B | 275 | 63.8055 | 23.1755 | 22.4858 | 55.261 | 66.3442 | 24.9115 | 22.9034 | 58.1336
PEWO4 M1 | 400 | 86.9438 | 31.6097 | 26.4055 | 71.1084 | 81.4329 | 31.494 | 23.4232 | 67.9625
PEWO4 M2 | 400 | 86.9438 | 31.6097 | 26.4055 | 71.1084 | 81.4329 | 31.494 | 23.4232 | 67.9625
PEWO4 M3 | 400 | 86.9438 | 31.6097 | 26.4055 | 71.1084 | 81.4329 | 31.494 | 23.4232 | 67.9625
PEWO4 M4 | 400 | 86.9438 | 31.6097 | 26.4055 | 71.1084 | 81.4329 | 31.494 | 23.4232 | 67.9625
PEWO4 R1/2 | 400 | 86.9438 | 31.6097 | 26.4055 | 71.1084 | 81.4329 | 31.494 | 23.4232 | 67.9625
PEWO4 R3/4 | 400 | 86.9438 | 31.6097 | 26.4055 | 71.1084 | 81.4329 | 31.494 | 23.4232 | 67.9625
PITS2 MC1 | 275 | 61.0658 | 22.1238 | 8.53 | 39.8178 | 65.2501 | 25.5823 | 7.4832 | 43.662
PITS2 MC2 | 275 | 61.0658 | 22.1238 | 8.53 | 39.8178 | 65.2501 | 25.5823 | 7.4832 | 43.662
PITS2 MC3 | 275 | 61.0658 | 22.1238 | 8.53 | 39.8178 | 65.2501 | 25.5823 | 7.4832 | 43.662
PITS2 MC4 | 275 | 61.0658 | 22.1238 | 8.53 | 39.8178 | 65.2501 | 25.5823 | 7.4832 | 43.662
POPP2 MC1 | 275 | 27.6821 | 11.0693 | 2.858 | 18.5124 | 24.6781 | 10.0817 | 3.7451 | 18.0027
POPP2 MC2 | 275 | 27.6821 | 11.0693 | 2.858 | 18.5124 | 24.6781 | 10.0817 | 3.7451 | 18.0027
PUDM4 MC1 | 400 | 101.6005 | 34.6392 | 23.6792 | 72.6664 | 101.5503 | 40.8122 | 18.0941 | 75.8112
PUDM4 MC2 | 400 | 101.6005 | 34.6392 | 23.6792 | 72.6664 | 101.5503 | 40.8122 | 18.0941 | 75.8112
PYLE2 MC1 | 275 | 54.6612 | 20.3008 | 10.9034 | 39.6131 | 48.0045 | 18.9991 | 8.9101 | 35.7788
PYLE2 MC2 | 275 | 54.7162 | 20.3201 | 10.9169 | 39.6539 | 48.0497 | 19.0153 | 8.9262 | 35.8178
QUER4A | 400 | 71.9934 | 25.2106 | 8.3353 | 43.9884 | 64.9149 | 25.0459 | 4.549 | 39.9694
QUER4A_HEYS | 400 | 71.9934 | 25.2106 | 8.3353 | 43.9884 | 64.9149 | 25.0459 | 4.549 | 39.9694
QUER4A_HUTT | 400 | 71.9934 | 25.2106 | 8.3353 | 43.9884 | 64.9149 | 25.0459 | 4.549 | 39.9694
QUER4A_PEWO | 400 | 71.9934 | 25.2106 | 8.3353 | 43.9884 | 64.9149 | 25.0459 | 4.549 | 39.9694
QUER4B | 400 | 72.513 | 25.3637 | 8.4738 | 44.3435 | 66.4661 | 25.5476 | 5.0064 | 41.1362
QUER4B_HEYS | 400 | 72.513 | 25.3637 | 8.4738 | 44.3435 | 66.4661 | 25.5476 | 5.0064 | 41.1362
QUER4B_HUTT | 400 | 72.513 | 25.3637 | 8.4738 | 44.3435 | 66.4661 | 25.5476 | 5.0064 | 41.1362
QUER4B_PEWO | 400 | 72.513 | 25.3637 | 8.4738 | 44.3435 | 66.4661 | 25.5476 | 5.0064 | 41.1362
RAIN2 MC1 | 275 | 73.35 | 25.6727 | 18.2504 | 54.5571 | 73.0358 | 27.5662 | 15.7272 | 54.7117
RAIN2 MC2 | 275 | 73.35 | 25.6727 | 18.2504 | 54.5571 | 73.0358 | 27.5662 | 15.7272 | 54.7117
RAIN2 MC3 | 275 | 73.35 | 25.6727 | 18.2504 | 54.5571 | 73.0358 | 27.5662 | 15.7272 | 54.7117
RAIN2 MC4 | 275 | 73.35 | 25.6727 | 18.2504 | 54.5571 | 73.0358 | 27.5662 | 15.7272 | 54.7117
RASS4 M1 | 400 | 53.8201 | 20.1406 | 16.352 | 44.8351 | 43.2191 | 16.9594 | 11.6275 | 35.6117
RASS4 M2 | 400 | 53.8201 | 20.1406 | 16.352 | 44.8351 | 43.2191 | 16.9594 | 11.6275 | 35.6117
RATS1 M1 | 132 | 41.7033 | 14.6448 | 13.261 | 33.9718 | 46.9161 | 17.4474 | 15.2925 | 39.9669
RATS1 M2 | 132 | 41.7033 | 14.6448 | 13.261 | 33.9718 | 46.9161 | 17.4474 | 15.2925 | 39.9669
RATS1 R1 | 132 | 38.3313 | 13.5594 | 12.105 | 31.2809 | 42.9515 | 16.0988 | 12.8028 | 35.5699
RATS1 R2 | 132 | 38.3313 | 13.5594 | 12.105 | 31.2809 | 42.9515 | 16.0988 | 12.8028 | 35.5699
RATS2A | 275 | 41.5771 | 14.9501 | 9.0094 | 30.152 | 42.8754 | 15.6157 | 15.9362 | 38.0202
RATS4 M1 | 400 | 111.2959 | 39.7128 | 20.4936 | 76.6561 | 95.0311 | 37.2797 | 17.0756 | 69.797
RATS4 M2 | 400 | 111.2959 | 39.7128 | 20.4936 | 76.6561 | 95.0311 | 37.2797 | 17.0756 | 69.797
RATS4 M3 | 400 | 111.2959 | 39.7128 | 20.4936 | 76.6561 | 95.0311 | 37.2797 | 17.0756 | 69.797
RATS4 M4 | 400 | 111.2959 | 39.7128 | 20.4936 | 76.6561 | 95.0311 | 37.2797 | 17.0756 | 69.797
RATS4 R1/2 | 400 | 111.2959 | 39.7128 | 20.4936 | 76.6561 | 95.0311 | 37.2797 | 17.0756 | 69.797
RATS4 R3/4 | 400 | 111.2959 | 39.7128 | 20.4936 | 76.6561 | 95.0311 | 37.2797 | 17.0756 | 69.797
RAYL4 M1 | 400 | 101.7411 | 37.142 | 30.5476 | 83.0744 | 74.4256 | 29.3386 | 19.8861 | 61.3772
RAYL4 M2 | 400 | 101.7411 | 37.142 | 30.5476 | 83.0744 | 74.4256 | 29.3386 | 19.8861 | 61.3772
RAYL4 R1 | 400 | 101.7411 | 37.142 | 30.5476 | 83.0744 | 74.4256 | 29.3386 | 19.8861 | 61.3772
RAYL4 R2 | 400 | 101.7411 | 37.142 | 30.5476 | 83.0744 | 74.4256 | 29.3386 | 19.8861 | 61.3772
REBR2 MC1 | 275 | 62.2561 | 22.7112 | 21.122 | 53.2405 | 60.0251 | 23.3324 | 17.0198 | 50.0168
REBR2 MC2 | 275 | 60.1919 | 21.9777 | 20.6023 | 51.6834 | 58.4314 | 22.7658 | 16.4158 | 48.6115
REBR2 MC3 | 275 | 60.1919 | 21.9777 | 20.6023 | 51.6834 | 58.4314 | 22.7658 | 16.4158 | 48.6115
REBR2 MC4 | 275 | 62.2561 | 22.7112 | 21.122 | 53.2405 | 60.0251 | 23.3324 | 17.0198 | 50.0168
RHIG4 M1 | 400 | 55.785 | 20.4384 | 12.887 | 41.7913 | 48.3671 | 18.7047 | 9.6362 | 36.0886
RHIG4 R1 | 400 | 55.785 | 20.4384 | 12.887 | 41.7913 | 48.3671 | 18.7047 | 9.6362 | 36.0886
ROCH2 MC1 | 275 | 71.2473 | 25.6735 | 9.5979 | 45.9057 | 67.5222 | 26.1372 | 9.2104 | 46.1739
ROCH2 MC2 | 275 | 71.2473 | 25.6735 | 9.5979 | 45.9057 | 67.5222 | 26.1372 | 9.2104 | 46.1739
ROCH2 MC3 | 275 | 71.2473 | 25.6735 | 9.5979 | 45.9057 | 67.5222 | 26.1372 | 9.2104 | 46.1739
ROCH2 MC4 | 275 | 71.2473 | 25.6735 | 9.5979 | 45.9057 | 67.5222 | 26.1372 | 9.2104 | 46.1739
ROCK1A | 132 | 45.5958 | 15.7048 | 16.094 | 38.3039 | 47.6023 | 17.1912 | 15.7979 | 40.1099
ROCK4 Term900 | 400 | 78.2079 | 27.5864 | 18.7841 | 57.7971 | 75.6534 | 28.2835 | 19.3473 | 59.3461
RUGE4 M1 | 400 | 62.2261 | 23.129 | 9.8132 | 42.5226 | 49.5199 | 19.8746 | 6.9591 | 35.0661
RUGE4 M2 | 400 | 62.2261 | 23.129 | 9.8132 | 42.5226 | 49.5199 | 19.8746 | 6.9591 | 35.0661
RUGE4 R1 | 400 | 62.2261 | 23.129 | 9.8132 | 42.5226 | 49.5199 | 19.8746 | 6.9591 | 35.0661
RUGE4 R2 | 400 | 62.2261 | 23.129 | 9.8132 | 42.5226 | 49.5199 | 19.8746 | 6.9591 | 35.0661
RYEH4 M1 | 400 | 66.1002 | 23.877 | 15.7281 | 49.4952 | 68.708 | 25.8086 | 17.5391 | 54.038
RYEH4 R1 | 400 | 66.1002 | 23.877 | 15.7281 | 49.4952 | 68.708 | 25.8086 | 17.5391 | 54.038
RYHA41 MC1 | 400 | 39.8415 | 14.8997 | 8.3458 | 29.4172 | 26.5901 | 10.5987 | 3.7621 | 18.7509
RYHA4B_LOAD2 | 400 | 40.6651 | 15.2024 | 8.5724 | 30.0719 | 28.3407 | 11.2945 | 3.9943 | 19.9672
SAEN2 MC1 | 275 | 79.5316 | 27.2931 | 23.9316 | 62.5299 | 78.583 | 28.7696 | 23.8338 | 64.5201
SAEN2 MC2 | 275 | 79.5316 | 27.2931 | 23.9316 | 62.5299 | 78.583 | 28.7696 | 23.8338 | 64.5201
SAES2 M | 275 | 80.1377 | 27.4673 | 24.2435 | 63.0881 | 79.4653 | 29.0394 | 24.5866 | 65.6545
SAES2 R | 275 | 80.1377 | 27.4673 | 24.2435 | 63.0881 | 79.4653 | 29.0394 | 24.5866 | 65.6545
SALH2 MC1 | 275 | 72.5683 | 25.7405 | 16.2809 | 52.6834 | 69.0824 | 26.2893 | 13.7195 | 50.8982
SALH2 MC2 | 275 | 72.5683 | 25.7405 | 16.2809 | 52.6834 | 69.0824 | 26.2893 | 13.7195 | 50.8982
SEAB4 M1 | 400 | 93.9948 | 34.0342 | 31.0852 | 79.2168 | 88.0817 | 33.383 | 29.0219 | 76.2326
SEAB4 M2 | 400 | 93.9948 | 34.0342 | 31.0852 | 79.2168 | 88.0817 | 33.383 | 29.0219 | 76.2326
SEAB4 R1 | 400 | 93.9948 | 34.0342 | 31.0852 | 79.2168 | 88.0817 | 33.383 | 29.0219 | 76.2326
SEAB4 R2 | 400 | 93.9948 | 34.0342 | 31.0852 | 79.2168 | 88.0817 | 33.383 | 29.0219 | 76.2326
SELL4 M1 | 400 | 100.3179 | 36.1708 | 20.8311 | 71.9843 | 78.5364 | 30.2932 | 17.7722 | 60.6133
SELL4 M2 | 400 | 100.3179 | 36.1708 | 20.8311 | 71.9843 | 78.5364 | 30.2932 | 17.7722 | 60.6133
SELL4 R1 | 400 | 100.3179 | 36.1708 | 20.8311 | 71.9843 | 78.5364 | 30.2932 | 17.7722 | 60.6133
SELL4 R2 | 400 | 100.3179 | 36.1708 | 20.8311 | 71.9843 | 78.5364 | 30.2932 | 17.7722 | 60.6133
SELL4A | 400 | 100.2106 | 35.2177 | 9.202 | 59.0074 | 78.46 | 30.0727 | 9.7743 | 52.3036
SELL4B | 400 | 100.2104 | 35.2177 | 9.202 | 59.0073 | 78.4599 | 30.0727 | 9.7743 | 52.3035
SELW4 M3 | 400 | 100.3074 | 36.165 | 20.8398 | 71.9848 | 78.2782 | 30.2104 | 17.5815 | 60.3054
SELW4 M4 | 400 | 100.3074 | 36.165 | 20.8398 | 71.9848 | 78.2782 | 30.2104 | 17.5815 | 60.3054
SELW4 R3 | 400 | 100.3074 | 36.165 | 20.8398 | 71.9848 | 78.2782 | 30.2104 | 17.5815 | 60.3054
SELW4 R4 | 400 | 100.3074 | 36.165 | 20.8398 | 71.9848 | 78.2782 | 30.2104 | 17.5815 | 60.3054
SETW4A | 400 | 100.0331 | 35.1645 | 9.1667 | 58.8967 | 78.3617 | 30.0424 | 9.7222 | 52.2086
SETW4B | 400 | 100.033 | 35.1645 | 9.1666 | 58.8967 | 78.3616 | 30.0424 | 9.7222 | 52.2085
SHBA4 M1 | 400 | 73.3054 | 26.3891 | 24.8589 | 62.1787 | 71.5841 | 26.8943 | 24.0087 | 62.0429
SHBA4 M2 | 400 | 73.3054 | 26.3891 | 24.8589 | 62.1787 | 71.5841 | 26.8943 | 24.0087 | 62.0429
SHBA4 R1 | 400 | 73.3054 | 26.3891 | 24.8589 | 62.1787 | 71.5841 | 26.8943 | 24.0087 | 62.0429
SHBA4 R2 | 400 | 73.3054 | 26.3891 | 24.8589 | 62.1787 | 71.5841 | 26.8943 | 24.0087 | 62.0429
SHEC2 MC1 | 275 | 53.9923 | 20.1048 | 10.3621 | 38.7946 | 54.3183 | 22.3557 | 7.4414 | 39.0571
SHEC2 MC2 | 275 | 53.9923 | 20.1048 | 10.3621 | 38.7946 | 54.3183 | 22.3557 | 7.4414 | 39.0571
SHRE4B | 400 | 52.7515 | 19.5844 | 9.6694 | 37.3659 | 42.0224 | 16.696 | 6.7741 | 30.3858
SING4 MC1 | 400 | 98.3621 | 34.7435 | 21.5517 | 70.6865 | 75.3538 | 29.4909 | 12.8927 | 54.5991
SING4 MC2 | 400 | 98.3621 | 34.7435 | 21.5517 | 70.6865 | 75.3538 | 29.4909 | 12.8927 | 54.5991
SIZE4 M1 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 M2 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 M3 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 M4 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 R1 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 R2 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 R3 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SIZE4 R4 | 400 | 87.3538 | 30.7277 | 22.1048 | 65.5604 | 82.3639 | 30.4941 | 23.5306 | 66.6558
SJOW2 MC1 | 275 | 23.0189 | 8.1064 | 9.2203 | 20.6844 | 27.4203 | 9.8477 | 10.7687 | 24.6954
SJOW2 MC2 | 275 | 23.0189 | 8.1064 | 9.2203 | 20.6844 | 27.4203 | 9.8477 | 10.7687 | 24.6954
SJOW2 MC3 | 275 | 23.0189 | 8.1064 | 9.2203 | 20.6844 | 27.4203 | 9.8477 | 10.7687 | 24.6954
SJOW2 MC4 | 275 | 23.0189 | 8.1064 | 9.2203 | 20.6844 | 27.4203 | 9.8477 | 10.7687 | 24.6954
SJOW4 M1 | 400 | 111.7392 | 37.3251 | 27.4802 | 80.2658 | 126.9753 | 46.6568 | 30.6709 | 96.6535
SJOW4 M2 | 400 | 111.7392 | 37.3251 | 27.4802 | 80.2658 | 126.9753 | 46.6568 | 30.6709 | 96.6535
SJOW4 M3 | 400 | 111.7392 | 37.3251 | 27.4802 | 80.2658 | 126.9753 | 46.6568 | 30.6709 | 96.6535
SJOW4 M4 | 400 | 111.7392 | 37.3251 | 27.4802 | 80.2658 | 126.9753 | 46.6568 | 30.6709 | 96.6535
SJOW4 R1/2 | 400 | 111.7392 | 37.3251 | 27.4802 | 80.2658 | 126.9753 | 46.6568 | 30.6709 | 96.6535
SJOW4 R3/4 | 400 | 111.7392 | 37.3251 | 27.4802 | 80.2658 | 126.9753 | 46.6568 | 30.6709 | 96.6535
SKLG2 MC1 | 275 | 58.921 | 21.7238 | 17.9722 | 48.6943 | 56.1407 | 21.8709 | 15.8159 | 46.746
SKLG2 MC2 | 275 | 58.921 | 21.7238 | 17.9722 | 48.6943 | 56.1407 | 21.8709 | 15.8159 | 46.746
SKLG2 MC3 | 275 | 58.921 | 21.7238 | 17.9722 | 48.6943 | 56.1407 | 21.8709 | 15.8159 | 46.746
SKLG2 MC4 | 275 | 58.921 | 21.7238 | 17.9722 | 48.6943 | 56.1407 | 21.8709 | 15.8159 | 46.746
SMAN2 MC1 | 275 | 75.1513 | 27.8631 | 22.6544 | 62.0588 | 73.9308 | 28.8319 | 20.5795 | 61.354
SMAN2 MC2 | 275 | 75.1513 | 27.8631 | 22.6544 | 62.0588 | 73.9308 | 28.8319 | 20.5795 | 61.354
SMAN2 MC3 | 275 | 75.1513 | 27.8631 | 22.6544 | 62.0588 | 73.9308 | 28.8319 | 20.5795 | 61.354
SMAN2 MC4 | 275 | 75.1513 | 27.8631 | 22.6544 | 62.0588 | 73.9308 | 28.8319 | 20.5795 | 61.354
SPEN4 MC3 | 400 | 71.1591 | 25.5831 | 14.7034 | 50.8833 | 50.8012 | 19.7616 | 9.1858 | 37.1328
SPEN4 MC4 | 400 | 71.1591 | 25.5831 | 14.7034 | 50.8833 | 50.8012 | 19.7616 | 9.1858 | 37.1328
SPEN41 MC1 | 400 | 71.1314 | 25.5734 | 14.6985 | 50.8648 | 51.4767 | 19.9982 | 9.4449 | 37.7266
SPEN41 MC2 | 400 | 71.1314 | 25.5734 | 14.6985 | 50.8648 | 51.4767 | 19.9982 | 9.4449 | 37.7266
SPLN4 M1 | 400 | 91.9107 | 31.3046 | 25.3607 | 69.6321 | 67.8468 | 25.62 | 17.4626 | 53.6948
SPLN4 R1 | 400 | 91.9107 | 31.3046 | 25.3607 | 69.6321 | 67.8468 | 25.62 | 17.4626 | 53.6948
SSHI2 MC1 | 275 | 68.2408 | 24.8425 | 12.5856 | 47.7182 | 59.0982 | 23.3757 | 9.6403 | 42.6986
SSHI2 MC2 | 275 | 68.2408 | 24.8425 | 12.5856 | 47.7182 | 59.0982 | 23.3757 | 9.6403 | 42.6986
STAL2 M1 | 275 | 82.5641 | 30.1663 | 16.033 | 58.6945 | 76.0619 | 29.6405 | 14.4617 | 56.3796
STAL2 M2 | 275 | 82.5641 | 30.1663 | 16.033 | 58.6945 | 76.0619 | 29.6405 | 14.4617 | 56.3796
STAL2 R1 | 275 | 82.5641 | 30.1663 | 16.033 | 58.6945 | 76.0619 | 29.6405 | 14.4617 | 56.3796
STAL2 R2 | 275 | 82.5641 | 30.1663 | 16.033 | 58.6945 | 76.0619 | 29.6405 | 14.4617 | 56.3796
STAL4 MC1 | 400 | 37.0926 | 13.6106 | 9.5205 | 28.7688 | 32.7085 | 12.6415 | 8.0464 | 25.9242
STAL4 MC2 | 400 | 51.422 | 19.3148 | 9.8339 | 37.1491 | 39.1309 | 15.5405 | 6.3412 | 28.3188
STAY4 M1 | 400 | 104.5467 | 37.541 | 23.6345 | 76.7255 | 96.9643 | 36.8314 | 24.3757 | 76.4632
STAY4 M2 | 400 | 104.5467 | 37.541 | 23.6345 | 76.7255 | 96.9643 | 36.8314 | 24.3757 | 76.4632
STAY4 R1 | 400 | 104.5467 | 37.541 | 23.6345 | 76.7255 | 96.9643 | 36.8314 | 24.3757 | 76.4632
STAY4 R2 | 400 | 104.5467 | 37.541 | 23.6345 | 76.7255 | 96.9643 | 36.8314 | 24.3757 | 76.4632
STAY4A | 400 | 71.1095 | 25.8175 | 19.0664 | 55.5778 | 64.1347 | 24.2616 | 18.1437 | 52.4548
STEN1 M1 | 132 | 56.0072 | 19.7185 | 19.6736 | 47.5597 | 68.204 | 25.1464 | 23.1292 | 58.6916
STEN1 M2 | 132 | 56.0072 | 19.7185 | 19.6736 | 47.5597 | 68.204 | 25.1464 | 23.1292 | 58.6916
STEN1 R1 | 132 | 56.0072 | 19.7185 | 19.6736 | 47.5597 | 68.204 | 25.1464 | 23.1292 | 58.6916
STEN1 R2 | 132 | 56.0072 | 19.7185 | 19.6736 | 47.5597 | 68.204 | 25.1464 | 23.1292 | 58.6916
STES1 M1 | 132 | 56.2652 | 19.2734 | 15.6499 | 42.9066 | 68.1754 | 24.8613 | 17.7096 | 52.8688
STES1 M2 | 132 | 56.2652 | 19.2734 | 15.6499 | 42.9066 | 68.1754 | 24.8613 | 17.7096 | 52.8688
STES1 R1 | 132 | 56.2652 | 19.2734 | 15.6499 | 42.9066 | 68.1754 | 24.8613 | 17.7096 | 52.8688
STES1 R2 | 132 | 56.2652 | 19.2734 | 15.6499 | 42.9066 | 68.1754 | 24.8613 | 17.7096 | 52.8688
STEW2 M1 | 275 | 86.7907 | 31.8897 | 26.6664 | 71.7653 | 79.4393 | 30.5454 | 24.0033 | 67.201
STEW2 M2 | 275 | 86.7907 | 31.8897 | 26.6664 | 71.7653 | 79.4393 | 30.5454 | 24.0033 | 67.201
STEW2 R1 | 275 | 86.7907 | 31.8897 | 26.6664 | 71.7653 | 79.4393 | 30.5454 | 24.0033 | 67.201
STEW2 R2 | 275 | 86.7907 | 31.8897 | 26.6664 | 71.7653 | 79.4393 | 30.5454 | 24.0033 | 67.201
STEW4 M1 | 400 | 90.2809 | 32.9686 | 27.1433 | 73.7679 | 62.6172 | 24.3744 | 18.0137 | 52.4843
STEW4 M2 | 400 | 90.2809 | 32.9686 | 27.1433 | 73.7679 | 62.6172 | 24.3744 | 18.0137 | 52.4843
STEW4 R1 | 400 | 90.2809 | 32.9686 | 27.1433 | 73.7679 | 62.6172 | 24.3744 | 18.0137 | 52.4843
STEW4 R2a | 400 | 90.2809 | 32.9686 | 27.1433 | 73.7679 | 62.6172 | 24.3744 | 18.0137 | 52.4843
STOB4 M1 | 400 | 59.8523 | 22.3942 | 10.4337 | 42.1039 | 48.1152 | 19.2733 | 7.3726 | 34.6291
STOB4 R1 | 400 | 59.8523 | 22.3942 | 10.4337 | 42.1039 | 48.1152 | 19.2733 | 7.3726 | 34.6291
STSB4 MC1 | 400 | 58.3952 | 21.5059 | 12.6215 | 43.0354 | 45.5981 | 17.9236 | 7.6765 | 33.0243
STSB4 MC2 | 400 | 58.3952 | 21.5059 | 12.6215 | 43.0354 | 45.5981 | 17.9236 | 7.6765 | 33.0243
STSB4A | 400 | 53.7936 | 19.5721 | 5.7869 | 33.4661 | 41.295 | 16.0988 | 3.0799 | 25.8472
SUND4 M1 | 400 | 100.009 | 35.8496 | 20.6564 | 71.3553 | 84.5462 | 32.7072 | 16.1732 | 62.4281
SUND4 M2 | 400 | 81.2463 | 29.5729 | 16.6279 | 58.4503 | 68.9046 | 26.6399 | 13.568 | 51.2425
SUND4 R1 | 400 | 100.009 | 35.8496 | 20.6564 | 71.3553 | 84.5462 | 32.7072 | 16.1732 | 62.4281
SUND4 R2 | 400 | 81.2463 | 29.5729 | 16.6279 | 58.4503 | 68.9046 | 26.6399 | 13.568 | 51.2425
SUTB4A | 400 | 99.6574 | 34.8535 | 23.8748 | 73.1651 | 82.4476 | 31.2417 | 20.4455 | 64.628
SWAN2 MC3 | 275 | 25.9356 | 9.4198 | 8.4937 | 21.8154 | 28.2698 | 10.4683 | 8.8165 | 23.621
SWAN2 MC4 | 275 | 25.9356 | 9.4198 | 8.4937 | 21.8154 | 28.2698 | 10.4683 | 8.8165 | 23.621
SWAN4 M1 | 400 | 39.1128 | 14.4681 | 9.1564 | 29.6175 | 34.1174 | 13.0297 | 8.0408 | 26.4676
SWAN4 M2 | 400 | 39.1128 | 14.4681 | 9.1564 | 29.6175 | 34.1174 | 13.0297 | 8.0408 | 26.4676
SWAN4 M3 | 400 | 62.3338 | 22.5108 | 15.5409 | 47.3759 | 59.8957 | 22.7177 | 14.2568 | 46.3845
SWAN4 M4 | 400 | 62.3338 | 22.5108 | 15.5409 | 47.3759 | 59.8957 | 22.7177 | 14.2568 | 46.3845
SWAN4 R3 | 400 | 62.3338 | 22.5108 | 15.5409 | 47.3759 | 59.8957 | 22.7177 | 14.2568 | 46.3845
SWAN4 R4 | 400 | 62.3338 | 22.5108 | 15.5409 | 47.3759 | 59.8957 | 22.7177 | 14.2568 | 46.3845
TAUN4 M1 | 400 | 59.9513 | 22.1882 | 11.3672 | 42.7461 | 50.7951 | 20.2007 | 7.1228 | 35.6909
TAUN4 M2 | 400 | 61.3373 | 22.6621 | 11.6595 | 43.7086 | 52.8172 | 20.9329 | 7.821 | 37.4246
TEMP2 MC1 | 275 | 59.9523 | 22.0676 | 12.1887 | 43.3971 | 61.8003 | 24.4763 | 10.8419 | 45.4567
TEMP2 MC2 | 275 | 59.9523 | 22.0676 | 12.1887 | 43.3971 | 61.8003 | 24.4763 | 10.8419 | 45.4567
TEMP2 MC3 | 275 | 60.2423 | 22.1537 | 12.3278 | 43.6578 | 62.6848 | 24.8066 | 11.0633 | 46.1452
THOM2 M1 | 275 | 69.353 | 25.1725 | 19.658 | 55.2574 | 70.1873 | 26.5157 | 18.8236 | 56.3225
THOM2 R1 | 275 | 69.353 | 25.1725 | 19.658 | 55.2574 | 70.1873 | 26.5157 | 18.8236 | 56.3225
THOM4 MC1 | 400 | 102.275 | 36.1173 | 24.1316 | 75.2092 | 86.5549 | 33.158 | 17.6576 | 64.5501
THOM4 MC2 | 400 | 102.275 | 36.1173 | 24.1316 | 75.2092 | 86.5549 | 33.158 | 17.6576 | 64.5501
THOM4 MC3 | 400 | 102.275 | 36.1173 | 24.1316 | 75.2092 | 86.5549 | 33.158 | 17.6576 | 64.5501
THOM4 MC4 | 400 | 102.275 | 36.1173 | 24.1316 | 75.2092 | 86.5549 | 33.158 | 17.6576 | 64.5501
THOM4 R2(2) | 400 | 90.7148 | 32.8183 | 19.04 | 65.4521 | 77.0339 | 29.6977 | 15.2404 | 57.2392
THOM4 R2(3) | 400 | 90.7148 | 32.8183 | 19.04 | 65.4521 | 77.0339 | 29.6977 | 15.2404 | 57.2392
THOM42 M5 | 400 | 90.7148 | 32.8183 | 19.04 | 65.4521 | 77.0339 | 29.6977 | 15.2404 | 57.2392
THTO4 M1 | 400 | 116.6524 | 39.3245 | 31.929 | 87.5422 | 82.3778 | 31.4126 | 15.9712 | 60.3954
THTO4 M2 | 400 | 116.2139 | 38.9972 | 32.6525 | 87.8028 | 80.4326 | 30.5534 | 16.4029 | 59.612
THTO4 M3 | 400 | 116.2139 | 38.9972 | 32.6525 | 87.8028 | 80.4326 | 30.5534 | 16.4029 | 59.612
THTO4 M4 | 400 | 116.6524 | 39.3245 | 31.929 | 87.5422 | 82.3778 | 31.4126 | 15.9712 | 60.3954
THTO4 R1/2 | 400 | 88.1979 | 31.3491 | 23.1598 | 67.4941 | 70.9004 | 27.0981 | 14.8911 | 53.2136
THTO4 R3/4 | 400 | 88.1979 | 31.3491 | 23.1598 | 67.4941 | 70.9004 | 27.0981 | 14.8911 | 53.2136
THUR2 MC1 | 275 | 65.0544 | 24.4146 | 10.4471 | 44.9746 | 65.4501 | 25.9133 | 10.8028 | 47.4498
THUR2 MC2 | 275 | 65.0544 | 24.4146 | 10.4471 | 44.9746 | 65.4501 | 25.9133 | 10.8028 | 47.4498
THUR2 MC3 | 275 | 65.0544 | 24.4146 | 10.4471 | 44.9746 | 65.4501 | 25.9133 | 10.8028 | 47.4498
THUR2 MC4 | 275 | 65.0544 | 24.4146 | 10.4471 | 44.9746 | 65.4501 | 25.9133 | 10.8028 | 47.4498
TILB2 M1 | 275 | 71.6109 | 25.6362 | 21.2029 | 57.4579 | 73.9165 | 27.6505 | 20.8052 | 59.9089
TILB2 M2 | 275 | 71.6109 | 25.6362 | 21.2029 | 57.4579 | 73.9165 | 27.6505 | 20.8052 | 59.9089
TILB2 R1 | 275 | 71.6109 | 25.6362 | 21.2029 | 57.4579 | 73.9165 | 27.6505 | 20.8052 | 59.9089
TILB2 R2 | 275 | 71.6109 | 25.6362 | 21.2029 | 57.4579 | 73.9165 | 27.6505 | 20.8052 | 59.9089
TILB4 M2 | 400 | 143.7003 | 50.7588 | 44.9742 | 116.758 | 119.3861 | 46.0511 | 33.6292 | 98.7553
TILB4 M3 | 400 | 143.7003 | 50.7588 | 44.9742 | 116.758 | 119.3861 | 46.0511 | 33.6292 | 98.7553
TILB4 R2 | 400 | 143.7003 | 50.7588 | 44.9742 | 116.758 | 119.3861 | 46.0511 | 33.6292 | 98.7553
TILB4 R3 | 400 | 143.7003 | 50.7588 | 44.9742 | 116.758 | 119.3861 | 46.0511 | 33.6292 | 98.7553
TINP2 M1 | 275 | 58.4662 | 21.2408 | 6.7717 | 36.8107 | 56.4068 | 21.9258 | 5.4245 | 36.4322
TINP2 M2 | 275 | 58.635 | 21.2516 | 6.7844 | 36.8387 | 57.332 | 22.2602 | 5.5167 | 36.9974
TODP2 MC1 | 275 | 64.2773 | 22.0768 | 16.5211 | 47.7424 | 56.7627 | 21.5902 | 11.4138 | 41.947
TODP2 MC2 | 275 | 64.2773 | 22.0768 | 16.5211 | 47.7424 | 56.7627 | 21.5902 | 11.4138 | 41.947
TOTE2A | 275 | 69.2568 | 24.682 | 19.0438 | 53.9494 | 70.4234 | 26.6531 | 16.2322 | 53.9254
TOTE2B | 275 | 70.9741 | 25.2552 | 19.2762 | 54.9924 | 71.3086 | 27.0219 | 16.1901 | 54.4049
TOTT2 MC1 | 275 | 40.6332 | 15.3876 | 11.9462 | 33.7075 | 41.5805 | 16.2156 | 11.5625 | 34.4948
TOTT2 MC2A | 275 | 42.7503 | 16.1494 | 12.6038 | 35.4424 | 38.8254 | 15.2697 | 10.5391 | 32.1337
TOTT2 MC2B | 275 | 70.9741 | 25.2552 | 19.2762 | 54.9924 | 71.3086 | 27.0219 | 16.1901 | 54.4049
TOTT2 MC3 | 275 | 42.7503 | 16.1494 | 12.6038 | 35.4424 | 38.8254 | 15.2697 | 10.5391 | 32.1337
TOTT2 MC4A | 275 | 40.6332 | 15.3876 | 11.9462 | 33.7075 | 41.5805 | 16.2156 | 11.5625 | 34.4948
TOTT2 MC4B | 275 | 69.2568 | 24.682 | 19.0438 | 53.9494 | 70.4234 | 26.6531 | 16.2322 | 53.9254
TOTT2 MC5 | 275 | 70.9741 | 25.2552 | 19.2762 | 54.9924 | 71.3086 | 27.0219 | 16.1901 | 54.4049
TOTT2 MC6 | 275 | 70.9741 | 25.2552 | 19.2762 | 54.9924 | 71.3086 | 27.0219 | 16.1901 | 54.4049
TOTT2 MC7 | 275 | 69.2568 | 24.682 | 19.0438 | 53.9494 | 70.4234 | 26.6531 | 16.2322 | 53.9254
TOTT2 MC8 | 275 | 69.2568 | 24.682 | 19.0438 | 53.9494 | 70.4234 | 26.6531 | 16.2322 | 53.9254
TRAW2 M1 | 275 | 43.9324 | 15.7407 | 13.2193 | 35.48 | 45.9578 | 17.1808 | 12.294 | 36.5913
TRAW2 M2 | 275 | 43.9324 | 15.7407 | 13.2193 | 35.48 | 45.9578 | 17.1808 | 12.294 | 36.5913
TRAW2 R1 | 275 | 43.9324 | 15.7407 | 13.2193 | 35.48 | 45.9578 | 17.1808 | 12.294 | 36.5913
TRAW2 R2 | 275 | 43.9324 | 15.7407 | 13.2193 | 35.48 | 45.9578 | 17.1808 | 12.294 | 36.5913
TRAW4 MC1 | 400 | 56.6508 | 21.0374 | 16.8851 | 46.6365 | 45.763 | 18.0869 | 11.9844 | 37.5631
TRAW4 MC2 | 400 | 56.6508 | 21.0374 | 16.8851 | 46.6365 | 45.763 | 18.0869 | 11.9844 | 37.5631
TRAW4 MC3 | 400 | 56.6508 | 21.0374 | 16.8851 | 46.6365 | 45.763 | 18.0869 | 11.9844 | 37.5631
TRAW4 MC4 | 400 | 56.6508 | 21.0374 | 16.8851 | 46.6365 | 45.763 | 18.0869 | 11.9844 | 37.5631
TREM2 MC1 | 275 | 47.0456 | 17.268 | 2.6397 | 27.0603 | 41.4159 | 16.4508 | 2.3363 | 25.6012
TREM2 MC2 | 275 | 47.0456 | 17.268 | 2.6397 | 27.0603 | 41.4159 | 16.4508 | 2.3363 | 25.6012
TREU4A | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 67.8384 | 26.389 | 4.0573 | 41.377
TREU4A_DEES1 | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 67.8384 | 26.389 | 4.0573 | 41.377
TREU4A_LEGA1 | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 67.8384 | 26.389 | 4.0573 | 41.377
TREU4A_TRAW1 | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 67.8384 | 26.389 | 4.0573 | 41.377
TREU4B | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 68.068 | 26.4764 | 4.0711 | 41.5144
TREU4B_DEES2 | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 68.068 | 26.4764 | 4.0711 | 41.5144
TREU4B_LEGA2 | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 68.068 | 26.4764 | 4.0711 | 41.5144
TREU4B_TRAW2 | 400 | 80.2479 | 28.152 | 7.3631 | 47.176 | 68.068 | 26.4764 | 4.0711 | 41.5144
TYNE2 MC1 | 275 | 63.1328 | 23.1626 | 11.2818 | 44.0387 | 54.7694 | 21.5731 | 9.3954 | 39.9044
TYNE2 MC2 | 275 | 63.1328 | 23.1626 | 11.2818 | 44.0387 | 54.7694 | 21.5731 | 9.3954 | 39.9044
TYNE2A | 275 | 62.4133 | 22.5079 | 3.996 | 35.827 | 51.6537 | 20.4416 | 2.8285 | 31.7373
UPPB2 MC1 | 275 | 39.6139 | 14.7809 | 9.8578 | 30.7612 | 38.684 | 14.9784 | 8.6292 | 29.8119
UPPB2 MC2 | 275 | 42.2376 | 15.7244 | 10.2539 | 32.4916 | 40.5025 | 15.6617 | 9.0423 | 31.1914
UPPB2 MC3 | 275 | 42.2376 | 15.7244 | 10.2539 | 32.4916 | 40.5025 | 15.6617 | 9.0423 | 31.1914
UPPB2 MC4 | 275 | 39.6139 | 14.7809 | 9.8578 | 30.7612 | 38.684 | 14.9784 | 8.6292 | 29.8119
USKM2 M1 | 275 | 78.6259 | 27.8841 | 20.2546 | 59.6887 | 88.2367 | 32.9774 | 23.4031 | 70.0402
USKM2 M2 | 275 | 78.6259 | 27.8841 | 20.2546 | 59.6887 | 88.2367 | 32.9774 | 23.4031 | 70.0402
USKM2 R1 | 275 | 78.6259 | 27.8841 | 20.2546 | 59.6887 | 88.2367 | 32.9774 | 23.4031 | 70.0402
USKM2 R2 | 275 | 78.6259 | 27.8841 | 20.2546 | 59.6887 | 88.2367 | 32.9774 | 23.4031 | 70.0402
USKM2A | 275 | 76.137 | 26.3822 | 11.5338 | 48.8438 | 83.41 | 31.0891 | 12.1406 | 56.1072
WALH4 MC1 | 400 | 58.4656 | 21.7271 | 11.0703 | 41.7971 | 49.9004 | 19.5238 | 10.1586 | 37.7694
WALH4 MC2 | 400 | 58.4656 | 21.7271 | 11.0703 | 41.7971 | 49.9004 | 19.5238 | 10.1586 | 37.7694
WALH4 MC3 | 400 | 58.4656 | 21.7271 | 11.0703 | 41.7971 | 49.9004 | 19.5238 | 10.1586 | 37.7694
WALH4 MC4 | 400 | 58.4656 | 21.7271 | 11.0703 | 41.7971 | 49.9004 | 19.5238 | 10.1586 | 37.7694
WALP R4 | 132 | 68.8351 | 24.0701 | 20.7515 | 54.7918 | 83.4515 | 31.7837 | 22.6715 | 67.6204
WALP1 M4 | 132 | 68.8351 | 24.0701 | 20.7515 | 54.7918 | 83.4515 | 31.7837 | 22.6715 | 67.6204
WALP4 M1 | 400 | 121.7624 | 41.4499 | 32.705 | 91.324 | 98.6202 | 36.9548 | 25.8852 | 78.1472
WALP4 M2 | 400 | 121.7624 | 41.4499 | 32.705 | 91.324 | 98.6202 | 36.9548 | 25.8852 | 78.1472
WALP4 R1 | 400 | 121.7624 | 41.4499 | 32.705 | 91.324 | 98.6202 | 36.9548 | 25.8852 | 78.1472
WALP4 R2 | 400 | 121.7624 | 41.4499 | 32.705 | 91.324 | 98.6202 | 36.9548 | 25.8852 | 78.1472
WALPM3 | 132 | 68.8351 | 24.0701 | 20.7515 | 54.7918 | 83.4515 | 31.7837 | 22.6715 | 67.6204
WALPR3 | 132 | 68.8351 | 24.0701 | 20.7515 | 54.7918 | 83.4515 | 31.7837 | 22.6715 | 67.6204
WALX2 M1 | 275 | 71.1128 | 25.1345 | 15.7162 | 51.2618 | 74.6022 | 27.8126 | 15.2045 | 54.5374
WALX2 M2 | 275 | 73.335 | 25.8234 | 16.2323 | 52.7521 | 78.5967 | 29.1821 | 16.2437 | 57.5134
WALX2 R1 | 275 | 71.1128 | 25.1345 | 15.7162 | 51.2618 | 74.6022 | 27.8126 | 15.2045 | 54.5374
WALX2 R2 | 275 | 73.335 | 25.8234 | 16.2323 | 52.7521 | 78.5967 | 29.1821 | 16.2437 | 57.5134
WALX4A | 400 | 62.3073 | 22.0985 | 8.0057 | 39.2577 | 63.2289 | 23.6501 | 8.6639 | 42.1103
WALX4B | 400 | 62.1679 | 22.0729 | 8.0435 | 39.2593 | 58.2873 | 21.871 | 8.127 | 39.0573
WARL2 MC1 | 275 | 64.8159 | 23.5772 | 15.3708 | 48.714 | 59.2534 | 23.0536 | 11.1249 | 43.7276
WARL2 MC2 | 275 | 64.8159 | 23.5772 | 15.3708 | 48.714 | 59.2534 | 23.0536 | 11.1249 | 43.7276
WARL2 MC3 | 275 | 64.8159 | 23.5772 | 15.3708 | 48.714 | 59.2534 | 23.0536 | 11.1249 | 43.7276
WARL2 MC4 | 275 | 64.8159 | 23.5772 | 15.3708 | 48.714 | 59.2534 | 23.0536 | 11.1249 | 43.7276
WASF2A | 275 | 53.2566 | 19.3895 | 11.6539 | 39.0747 | 46.8416 | 18.2868 | 7.9991 | 33.8606
WASF2B | 275 | 57.5135 | 20.8061 | 12.5113 | 41.9355 | 52.8842 | 20.6679 | 8.6869 | 37.9157
WBOL2 MC1 | 275 | 77.7534 | 27.8459 | 15.4835 | 54.8636 | 66.1272 | 26.0368 | 10.97 | 47.7916
WBOL2 MC2 | 275 | 77.7534 | 27.8459 | 15.4835 | 54.8636 | 66.1272 | 26.0368 | 10.97 | 47.7916
WBOL2 MC3 | 275 | 77.7534 | 27.8459 | 15.4835 | 54.8636 | 66.1272 | 26.0368 | 10.97 | 47.7916
WBOL2 MC4 | 275 | 77.7534 | 27.8459 | 15.4835 | 54.8636 | 66.1272 | 26.0368 | 10.97 | 47.7916
WBUR1 M1 | 132 | 21.0155 | 7.4437 | 6.6579 | 17.1849 | 24.491 | 9.0632 | 7.9531 | 20.7704
WBUR1 M2 | 132 | 21.0155 | 7.4437 | 6.6579 | 17.1849 | 24.491 | 9.0632 | 7.9531 | 20.7704
WBUR1 R1 | 132 | 21.0155 | 7.4437 | 6.6579 | 17.1849 | 24.491 | 9.0632 | 7.9531 | 20.7704
WBUR1 R2 | 132 | 20.822 | 7.3895 | 6.6243 | 17.0746 | 24.3723 | 9.0138 | 7.934 | 20.6815
WBUR4 M1 | 400 | 112.3847 | 38.9528 | 32.072 | 87.1597 | 99.3333 | 36.8927 | 28.378 | 80.5521
WBUR4 M2 | 400 | 112.3847 | 38.9528 | 32.072 | 87.1597 | 99.3333 | 36.8927 | 28.378 | 80.5521
WBUR4 M3 | 400 | 112.3847 | 38.9528 | 32.072 | 87.1597 | 99.3333 | 36.8927 | 28.378 | 80.5521
WBUR4 M4 | 400 | 112.3847 | 38.9528 | 32.072 | 87.1597 | 99.3333 | 36.8927 | 28.378 | 80.5521
WBUR4 R1/2 | 400 | 104.4985 | 37.1975 | 25.6326 | 78.2379 | 83.3352 | 31.8885 | 19.9378 | 65.035
WBUR4 R3/4 | 400 | 104.4985 | 37.1975 | 25.6326 | 78.2379 | 83.3352 | 31.8885 | 19.9378 | 65.035
WHAM4 M1 | 400 | 117.4454 | 41.5694 | 36.2629 | 95.0509 | 114.3566 | 44.6387 | 31.0771 | 94.2057
WHAM4 M2 | 400 | 117.4454 | 41.5694 | 36.2629 | 95.0509 | 114.3566 | 44.6387 | 31.0771 | 94.2057
WHAM4 R1 | 400 | 117.4454 | 41.5694 | 36.2629 | 95.0509 | 114.3566 | 44.6387 | 31.0771 | 94.2057
WHAM4 R2 | 400 | 117.4454 | 41.5694 | 36.2629 | 95.0509 | 114.3566 | 44.6387 | 31.0771 | 94.2057
WHAM4A | 400 | 99.8603 | 32.841 | 12.141 | 58.5852 | 98.5956 | 39.0586 | 14.2439 | 69.4811
WHAM4B | 400 | 99.9242 | 32.8574 | 12.1489 | 58.6163 | 98.6949 | 39.0937 | 14.2423 | 69.5292
WHGA2 MC1 | 275 | 70.1669 | 25.4735 | 14.7916 | 50.8166 | 65.7345 | 25.6709 | 11.8016 | 48.1057
WHGA2 MC2 | 275 | 70.1669 | 25.4735 | 14.7916 | 50.8166 | 65.7345 | 25.6709 | 11.8016 | 48.1057
WHGA2 MC3 | 275 | 70.1669 | 25.4735 | 14.7916 | 50.8166 | 65.7345 | 25.6709 | 11.8016 | 48.1057
WHGA2 MC4 | 275 | 70.1669 | 25.4735 | 14.7916 | 50.8166 | 65.7345 | 25.6709 | 11.8016 | 48.1057
WHSO2 M1 | 275 | 68.4757 | 24.7268 | 15.3011 | 50.27 | 73.3447 | 27.9617 | 15.8504 | 55.3941
WHSO2 M2 | 275 | 68.4757 | 24.7268 | 15.3011 | 50.27 | 73.3447 | 27.9617 | 15.8504 | 55.3941
WHSO2 R1 | 275 | 75.5575 | 26.983 | 19.6324 | 57.792 | 81.9862 | 30.8918 | 20.5294 | 64.217
WHSO2 R2 | 275 | 75.5575 | 26.983 | 19.6324 | 57.792 | 81.9862 | 30.8918 | 20.5294 | 64.217
WIBA2 MC1 | 275 | 59.9395 | 22.0642 | 12.1809 | 43.3843 | 62.9602 | 25.171 | 10.1772 | 45.7743
WIBA2 MC1 | 275 | 59.9395 | 22.0642 | 12.1809 | 43.3843 | 62.9602 | 25.171 | 10.1772 | 45.7743
WIBA2 MC2 | 275 | 59.9395 | 22.0642 | 12.1809 | 43.3843 | 62.9602 | 25.171 | 10.1772 | 45.7743
WIBA2 MC2 | 275 | 59.9395 | 22.0642 | 12.1809 | 43.3843 | 62.9602 | 25.171 | 10.1772 | 45.7743
WILE4 M1 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 M1 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 M2 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 M2 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 R1 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 R1 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 R2 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILE4 R2 | 400 | 95.9225 | 35.5348 | 25.5839 | 75.8377 | 82.1517 | 32.6059 | 20.8812 | 66.9929
WILL1 M2 | 132 | 52.0553 | 18.2078 | 15.9801 | 41.7298 | 58.5422 | 22.233 | 18.1732 | 49.6154
WILL1 R1 | 132 | 36.0644 | 13.3425 | 10.8081 | 29.6773 | 39.3584 | 15.1939 | 12.1983 | 33.6857
WILL1 R2 | 132 | 52.0553 | 18.2078 | 15.9801 | 41.7298 | 58.5422 | 22.233 | 18.1732 | 49.6154
WILL2 M2 | 275 | 23.6625 | 8.4487 | 8.6686 | 20.6168 | 25.1032 | 9.1673 | 8.951 | 21.9156
WILL2 M2 | 275 | 23.6625 | 8.4487 | 8.6686 | 20.6168 | 25.1032 | 9.1673 | 8.951 | 21.9156
WILL2 R2 | 275 | 23.6625 | 8.4487 | 8.6686 | 20.6168 | 25.1032 | 9.1673 | 8.951 | 21.9156
WILL2 R2 | 275 | 23.6625 | 8.4487 | 8.6686 | 20.6168 | 25.1032 | 9.1673 | 8.951 | 21.9156
WILT2A | 275 | 67.9079 | 21.8844 | 16.7576 | 47.7068 | 61.4381 | 22.1705 | 10.6845 | 42.0382
WILT2A | 275 | 67.9079 | 21.8844 | 16.7576 | 47.7068 | 61.4381 | 22.1705 | 10.6845 | 42.0382
WILT2B | 275 | 67.9104 | 21.8852 | 16.7574 | 47.7078 | 61.4406 | 22.1714 | 10.6842 | 42.0393
WILT2B | 275 | 67.9104 | 21.8852 | 16.7574 | 47.7078 | 61.4406 | 22.1714 | 10.6842 | 42.0393
WILT2C | 275 | 68.4335 | 22.0185 | 17.1405 | 48.2794 | 62.5295 | 22.4859 | 11.5573 | 43.3571
WILT2C | 275 | 68.4335 | 22.0185 | 17.1405 | 48.2794 | 62.5295 | 22.4859 | 11.5573 | 43.3571
WILT2D | 275 | 68.4308 | 22.0179 | 17.1394 | 48.2774 | 62.5242 | 22.4842 | 11.5549 | 43.3524
WILT2D | 275 | 68.4308 | 22.0179 | 17.1394 | 48.2774 | 62.5242 | 22.4842 | 11.5549 | 43.3524
WIMB4 MB2 | 400 | 95.7847 | 32.5079 | 23.5641 | 69.5371 | 108.41 | 40.8062 | 22.906 | 80.6147
WIMB4 MB2 | 400 | 95.7847 | 32.5079 | 23.5641 | 69.5371 | 108.41 | 40.8062 | 22.906 | 80.6147
WIMB4 RB2 | 400 | 95.7847 | 32.5079 | 23.5641 | 69.5371 | 108.41 | 40.8062 | 22.906 | 80.6147
WIMB4 RB2 | 400 | 95.7847 | 32.5079 | 23.5641 | 69.5371 | 108.41 | 40.8062 | 22.906 | 80.6147
WISD2 M1 | 275 | 68.6126 | 23.7844 | 22.0614 | 55.6976 | 79.459 | 29.3149 | 24.5069 | 65.9644
WISD2 M2 | 275 | 68.6126 | 23.7844 | 22.0614 | 55.6976 | 79.459 | 29.3149 | 24.5069 | 65.9644
WISD2 R1 | 275 | 68.6126 | 23.7844 | 22.0614 | 55.6976 | 79.459 | 29.3149 | 24.5069 | 65.9644
WISD2 R2 | 275 | 68.6126 | 23.7844 | 22.0614 | 55.6976 | 79.459 | 29.3149 | 24.5069 | 65.9644
WISD2A | 275 | 58.1895 | 20.1827 | 11.9537 | 40.4964 | 63.5133 | 24.2435 | 13.2832 | 47.5687
WISD2B | 275 | 58.1895 | 20.1827 | 11.9537 | 40.4964 | 63.5133 | 24.2435 | 13.2832 | 47.5687
WISD6 M1 | 66 | 50.0295 | 16.9289 | 17.035 | 40.9761 | 33.5127 | 12.5539 | 10.809 | 28.5629
WISD6 M2 | 66 | 50.0295 | 16.9289 | 17.035 | 40.9761 | 33.5127 | 12.5539 | 10.809 | 28.5629
WISD6 R1 | 66 | 50.0295 | 16.9289 | 17.035 | 40.9761 | 33.5127 | 12.5539 | 10.809 | 28.5629
WISD6 R2 | 66 | 50.0295 | 16.9289 | 17.035 | 40.9761 | 33.5127 | 12.5539 | 10.809 | 28.5629
WMEL2 MC1 | 275 | 79.0279 | 28.8319 | 14.339 | 55.1135 | 74.4224 | 29.3275 | 11.8909 | 53.3663
WMEL2 MC2 | 275 | 79.0279 | 28.8319 | 14.339 | 55.1135 | 74.4224 | 29.3275 | 11.8909 | 53.3663
WMEL2 MC3 | 275 | 79.0279 | 28.8319 | 14.339 | 55.1135 | 74.4224 | 29.3275 | 11.8909 | 53.3663
WMEL2 MC4 | 275 | 79.0279 | 28.8319 | 14.339 | 55.1135 | 74.4224 | 29.3275 | 11.8909 | 53.3663
WTHU4A | 400 | 95.2915 | 32.8829 | 8.4176 | 54.9211 | 72.8541 | 28.5612 | 4.8493 | 45.2409
WTHU4B | 400 | 95.2915 | 32.8829 | 8.4176 | 54.9211 | 74.4273 | 29.1533 | 4.954 | 46.183
WWEY2 M1 | 275 | 71.1513 | 25.929 | 17.2808 | 53.9499 | 69.7204 | 26.6735 | 16.1789 | 53.9009
WWEY2 M2 | 275 | 71.1513 | 25.929 | 17.2808 | 53.9499 | 69.7204 | 26.6735 | 16.1789 | 53.9009
WWEY2 R1 | 275 | 72.2942 | 26.4746 | 15.9423 | 53.383 | 71.7572 | 27.5633 | 15.9976 | 54.978
WWEY2 R2 | 275 | 72.2942 | 26.4746 | 15.9423 | 53.383 | 71.7572 | 27.5633 | 15.9976 | 54.978
WWEY4A | 400 | 48.8283 | 17.8671 | 5.8313 | 31.0992 | 43.6861 | 16.7833 | 5.805 | 29.5402
WWEY4B | 400 | 49.2694 | 17.9911 | 6.0213 | 31.4646 | 43.6356 | 16.822 | 6.004 | 29.7938
WYLF1 M1 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 M1 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 M2 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 M2 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 R1 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 R1 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 R2 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF1 R2 | 132 | 26.8175 | 9.3627 | 7.6703 | 20.9112 | 29.7096 | 10.9093 | 8.4086 | 23.8367
WYLF4 M1 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 M1 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 M2 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 M2 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 R1 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 R1 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 R2 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYLF4 R2 | 400 | 50.1179 | 18.0151 | 11.8962 | 37.3733 | 36.4505 | 14.1981 | 7.0153 | 27.0945
WYMO4 M1 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 M1 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 M2 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 M2 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 R1 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 R1 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 R2 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634
WYMO4 R2 | 400 | 95.3411 | 34.1838 | 20.0359 | 68.379 | 83.9903 | 32.3222 | 16.4529 | 62.1634