## cInterconnectorStorage
|  | National Storage Profile | Scotland, the North and West Interconnector Profile | The South and East of England Interconnector Profile
| 2017/18 | 2905.9 | 585 | 1000
Community Renewables | 2020/21 | 2987.8 | 755 | 3000
| 2025/26 | 3837.26 | 2905 | 5800
| 2030/31 | 5165.86 | 4305 | 9200
| 2035/36 | 7265.66 | 4305 | 9200
Two Degrees | 2020/21 | 3138.66 | 755 | 3000
| 2025/26 | 5016.86 | 4305 | 9200
| 2030/31 | 7815.66 | 5055 | 10600
| 2035/36 | 8525.56 | 5055 | 10600
Steady Progression | 2020/21 | 2987.8 | 755 | 3000
| 2025/26 | 3586.86 | 2905 | 4400
| 2030/31 | 4905.86 | 4305 | 7200
| 2035/36 | 5827.66 | 4305 | 7200
Consumer Evolution | 2020/21 | 2905.9 | 755 | 2000
| 2025/26 | 3138.66 | 2405 | 3000
| 2030/31 | 3736.86 | 2905 | 5800
| 2035/36 | 4468.56 | 2905 | 5800

## PeakMin_Data
Electricity: Peak inc Losses (non-transmission generation deducted)
Data in Electricity years - 2005 in the chart equates to 2005/06
"National Demand" is National Grid ESO's view of underlying ACS Peak consumer demand, after reduction by on-site and behind the meter generation
Note this is not a good measure of system utilisation and energy flows around GB
| Electricity Year Beginning |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51
| Electricity: ACS Peak Unrestricted National Demand (GW) |  | 2006/07: Peak CHART
Net ACS Peak demand on the transmission system - Does not add demand from interconnectors, pumping, storage or power stations
Triad response is not deducted from this total
Note this is not a good measure of system utilisation and energy flows around GB
Key non-transmission Generation Assumptions: Solar 0%, wind ~23%, storage ~87%
Electricity Year Beginning | time axis 2005-01-01 to 2050-01-01
|  | History | 2005-01-01: 60.9; 2006-01-01: 60.5; 2007-01-01: 60.5; 2008-01-01: 58.2; 2009-01-01: 58; 2010-01-01: 57.9; 2011-01-01: 56.4; 2012-01-01: 55.9; 2013-01-01: 54.9; 2014-01-01: 54.5; 2015-01-01: 53.1; 2016-01-01: 52.3; 2017-01-01: 51.4; 2018-01-01: 50.2
|  | Community Renewables | [13 empty] | 50.2 | 47.2 | 45.2 | 43.6 | 42.2 | 40.8 | 39.4 | 37.7 | 35.8 | 34.6 | 33.6 | 32.7 | 32.2 | 32.1 | 31.7 | 31.3 | 30.6 | 29.9 | 29 | 28 | 27.2 | 26.3 | 26 | 25.8 | 25.7 | 25.4 | 25.3 | 25.2 | 25 | 24.9 | 24.8 | 24.5 | 24.3
|  | Two Degrees | [13 empty] | 50.2 | 47.6 | 46.2 | 45.6 | 45.3 | 45.4 | 45.6 | 45.3 | 45.1 | 45.7 | 46.4 | 47.2 | 48.1 | 48.6 | 49.2 | 49.9 | 50.2 | 50.7 | 50.9 | 50.7 | 50.2 | 49.4 | 49.2 | 48.7 | 48.6 | 48.7 | 48.9 | 49 | 49.1 | 49.2 | 49.4 | 49.2 | 49
|  | Steady Progression | [13 empty] | 50.2 | 48 | 48.1 | 48 | 48.5 | 49 | 49.5 | 49.3 | 49.3 | 49.4 | 49.6 | 50 | 50.1 | 50.2 | 50.4 | 50.6 | 50.7 | 50.7 | 50.8 | 50.8 | 50.7 | 50.5 | 50.5 | 50.3 | 50.2 | 50.1 | 49.8 | 49.6 | 49.4 | 49.1 | 48.8 | 48.6 | 49.2
|  | Consumer Evolution | [13 empty] | 50.2 | 47.6 | 47 | 46.4 | 46 | 45.4 | 44.5 | 43.5 | 42.5 | 41.6 | 41 | 40.5 | 39.9 | 39.2 | 38.4 | 37.8 | 37.1 | 36.7 | 36.1 | 35.5 | 34.9 | 34.5 | 33.8 | 33.1 | 32.5 | 31.8 | 31.1 | 30.4 | 29.4 | 28.7 | 28.1 | 27.5 | 27.4
|  | 5 Year Forecast | 2018-01-01: 50.228; 2019-01-01: 47.5; 2020-01-01: 46.588; 2021-01-01: 46.003; 2022-01-01: 45.673; 2023-01-01: 45.525
Electricity: ACS Peak Restricted National Demand (GW)
Net ACS Peak demand on the transmission system - Does not add demand from interconnectors, pumping, storage or power stations
Triad response is deducted from this total
Note this is not a good measure of system utilisation and energy flows around GB
Key non-transmission Generation Assumptions: Solar 0%, wind ~23%, storage ~87%
Electricity Year Beginning | time axis 2005-01-01 to 2050-01-01
|  | History | 2005-01-01: 60.1; 2006-01-01: 59.7; 2007-01-01: 59.7; 2008-01-01: 57.4; 2009-01-01: 57.2; 2010-01-01: 57.1; 2011-01-01: 55.4; 2012-01-01: 54.7; 2013-01-01: 53.7; 2014-01-01: 53; 2015-01-01: 51.1; 2016-01-01: 50.3; 2017-01-01: 49.4; 2018-01-01: 47.8
|  | Community Renewables | [13 empty] | 47.8 | 44.805 | 42.74 | 40.888 | 39.165 | 37.275 | 35.324 | 33.39 | 31.291 | 29.602 | 27.93 | 26.267 | 25.296 | 24.16 | 23.088 | 21.845 | 20.191 | 18.616 | 16.716 | 15.13 | 13.663 | 12.267 | 11.489 | 10.627 | 10.382 | 9.944 | 9.682 | 9.528 | 9.332 | 9.137 | 8.957 | 8.671 | 8.412
|  | Two Degrees | [13 empty] | 47.8 | 45.197 | 43.797 | 43.133 | 42.681 | 42.508 | 42.318 | 41.717 | 41.3 | 41.724 | 42.292 | 42.732 | 43.264 | 43.305 | 43.595 | 44.043 | 44.008 | 44.052 | 43.96 | 43.557 | 42.889 | 42.024 | 41.698 | 41.152 | 40.94 | 40.974 | 41.065 | 41.119 | 41.126 | 41.223 | 41.305 | 41.135 | 40.911
|  | Steady Progression | [13 empty] | 47.8 | 45.558 | 45.682 | 45.627 | 46.133 | 46.547 | 47.071 | 46.882 | 46.83 | 46.892 | 46.981 | 47.185 | 47.28 | 47.335 | 47.446 | 47.654 | 47.629 | 47.599 | 47.605 | 47.542 | 47.403 | 47.159 | 47.071 | 46.892 | 46.787 | 46.593 | 46.361 | 46.151 | 45.921 | 45.623 | 45.336 | 45.107 | 45.694
|  | Consumer Evolution | [13 empty] | 47.8 | 45.161 | 44.621 | 44.003 | 43.576 | 42.947 | 42.04 | 40.976 | 39.876 | 38.726 | 37.879 | 37.247 | 36.552 | 35.788 | 34.886 | 34.245 | 33.396 | 32.902 | 32.19 | 31.374 | 30.795 | 30.29 | 29.628 | 28.918 | 28.259 | 27.508 | 26.886 | 26.126 | 25.183 | 24.47 | 23.845 | 23.256 | 23.149
|  | 5 Year Forecast | 2018-01-01: 47.8; 2019-01-01: 45.12; 2020-01-01: 44.143; 2021-01-01: 43.54; 2022-01-01: 43.147; 2023-01-01: 42.979
Electricity: Summer Minimum 0600 Unrestricted National Demand (GW, Normal Conditions)
Net ACS Peak demand on the transmission system - Does not add demand from interconnectors, pumping, storage or power stations
No DSR or TRIAD assumed in hour ending 0600
Note this is not a good measure of system utilisation and energy flows around GB
Key non-transmission Generation Assumptions: Solar 2.3%, Onshore Wind ~18%, Offshore Wind ~29%
Electricity Year Beginning | time axis 2005-01-01 to 2050-01-01
|  | History | 2005-01-01: 21.7; 2006-01-01: 22.1; 2007-01-01: 21.9; 2008-01-01: 21.4; 2009-01-01: 20; 2010-01-01: 19.6; 2011-01-01: 19.2; 2012-01-01: 19.2; 2013-01-01: 18.6; 2014-01-01: 18.1; 2015-01-01: 17.9; 2016-01-01: 16.9; 2017-01-01: 16.5; 2018-01-01: 15.8
|  | Community Renewables | [13 empty] | 15.8 | 15.4 | 14.4 | 13.9 | 13.5 | 12.9 | 12.6 | 12.4 | 11.8 | 11.4 | 10.9 | 10.5 | 10.1 | 9.9 | 9.7 | 9.6 | 9.5 | 9.4 | 9.1 | 8.9 | 8.6 | 8.4 | 8.3 | 8.3 | 8.4 | 8.4 | 8.6 | 8.8 | 9 | 9.2 | 9.5 | 9.9 | 10.1
|  | Two Degrees | [13 empty] | 15.8 | 15.7 | 15.1 | 14.9 | 14.5 | 14.2 | 14 | 14 | 13.8 | 13.7 | 13.7 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.7 | 13.7 | 13.8 | 13.8 | 13.9 | 13.9 | 14.1 | 14.3 | 14.5 | 14.6 | 14.8 | 14.7 | 14.7 | 14.7 | 14.6 | 14.5
|  | Steady Progression | [13 empty] | 15.8 | 15.9 | 16.1 | 16.3 | 16.1 | 16.1 | 16.1 | 16.1 | 15.9 | 15.6 | 15.5 | 15.3 | 15.2 | 15.2 | 15.1 | 15 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 15 | 15 | 15 | 15.1 | 14.9 | 15 | 15 | 15 | 15.1 | 15.1 | 15.1
|  | Consumer Evolution | [13 empty] | 15.8 | 15.6 | 15.7 | 15.2 | 15 | 14.8 | 14.4 | 14.2 | 13.9 | 13.8 | 13.7 | 13.6 | 13.6 | 13.4 | 13.2 | 13 | 12.8 | 12.6 | 12.4 | 12.3 | 12.2 | 12.1 | 12 | 12 | 11.9 | 11.9 | 11.9 | 12 | 12 | 12 | 12 | 12 | 12.1
|  | 5 Year Forecast | 2018-01-01: 15.8; 2019-01-01: 15.8; 2020-01-01: 15.6; 2021-01-01: 15.3; 2022-01-01: 14.9; 2023-01-01: 14.6
Electricity: Summer Minimum 1400 National Demand (GW, Normal Conditions)
Net ACS Peak demand on the transmission system - Does not add demand from interconnectors, pumping, storage or power stations
No DSR or TRIAD assumed in hour ending 1400
Note this is not a good measure of system utilisation and energy flows around GB
Negative demands indicate the need for system balancing options such as market rules, interconnection, storage, demand turn-up or generation turn-down
Key non-transmission Generation Assumptions: Solar 55%, Onshore Wind ~18%, Offshore Wind ~29%. Solar upto 71% modelled in ETYS.
Electricity Year Beginning | time axis 2005-01-01 to 2050-01-01
|  | History | 2005-01-01: 32.9; 2006-01-01: 33.1; 2007-01-01: 32.8; 2008-01-01: 32.7; 2009-01-01: 30.6; 2010-01-01: 30.2; 2011-01-01: 30.899; 2012-01-01: 29.7; 2013-01-01: 28.9; 2014-01-01: 26.8; 2015-01-01: 24.4; 2016-01-01: 20.3; 2017-01-01: 20.799; 2018-01-01: 16.6
|  | Community Renewables | [13 empty] | 16.6 | 15.6 | 14.6 | 13.6 | 12.5 | 11.2 | 10 | 8.5 | 6.9 | 5.8 | 4.7 | 3.7 | 2.6 | 2.1 | 1.5 | 0.7 | 0.2 | -0.1 | -0.2 | -0.4 | -0.3 | -0.1 | 0.2 | 0.7 | 0.8 | 1.1 | 1.3 | 1.5 | 1.8 | 2 | 2.4 | 2.8 | 3
|  | Two Degrees | [13 empty] | 16.6 | 15.7 | 15.2 | 14.8 | 14.4 | 14.2 | 13.8 | 13.3 | 12.7 | 12.5 | 12.4 | 12.4 | 12.1 | 11.8 | 11.3 | 10.9 | 10.5 | 10.3 | 10.5 | 10.8 | 11.2 | 11.7 | 12.1 | 12.5 | 12.8 | 13.1 | 13.5 | 13.8 | 14 | 14.2 | 14.3 | 14.3 | 14.2
|  | Steady Progression | [13 empty] | 16.6 | 16.1 | 16.3 | 16.3 | 16.2 | 16.1 | 16 | 16.1 | 16.1 | 16.1 | 16.2 | 16.3 | 16.3 | 16.2 | 16.2 | 15.9 | 15.5 | 14.9 | 14.5 | 14.4 | 14.6 | 15 | 15.5 | 16.1 | 16.6 | 17.2 | 17.7 | 18.3 | 18.7 | 19.3 | 19.6 | 19.8 | 20
|  | Consumer Evolution | [13 empty] | 16.6 | 15.9 | 15.7 | 15.4 | 15 | 14.6 | 14.3 | 13.9 | 13.4 | 12.9 | 12.3 | 11.7 | 11 | 10.4 | 9.8 | 9 | 8.1 | 7 | 6.2 | 5.7 | 5.5 | 5.4 | 5.6 | 5.9 | 6.3 | 6.7 | 7 | 7.4 | 8 | 8.4 | 8.7 | 8.8 | 9.2
|  | 5 Year Forecast | 2018-01-01: 16.6; 2019-01-01: 15.9; 2020-01-01: 15.8; 2021-01-01: 15.5; 2022-01-01: 15.3; 2023-01-01: 14.9
Electricity: Peak inc Losses (non-transmission generation not deducted)
Electricity: Summer AM 0600 (non-transmission generation not deducted)
Electricity: Summer AM 1400 (non-transmission generation not deducted)
This data now published in the FES Data workbook, table ED1
Filter: | Tab = Component
Filter: | Peak/Annual/Minimum = Peak or Summer AM 0600hrs or Summer PM 1400hrs
Data in Electricity years - 2005 in the table equates to 2005/06
National Grid ESO's view of underlying ACS Peak consumer demand, before reduction by on-site and behind the meter generation
Demand from generators (station demand), pumping demand (pumped hydro storage sites) and electricity storage (mostly batteries) is not included in the numbers above
Residential demand includes appliances, light, resistive heat, hot water, heat pumps, EV, Smart meter reduction, district heat. Air conditioners assumed to be off at winter peak
Residential air conditioning included in the summer data - awaiting academic confirmation of climate modelling
Industrial and Commercial peak demand includes commercial EVs, industrial district heat, and indirect rail. Electrolysis for hydrogen assumed to be zero at peak.
New: Direct Connects are large Industrial and Commercial demands directly connected to the transmission system (and direct connect rail sites)
Large sites directly connected to the transmission system was ~1GW at peak - now ~800MW
Generation output and storage is not deducted from these figures - this is a view of underlying demand
Industrial and Commercial Demand side response has not been deducted
Residential demand side response has been deducted

## Annual_Data
Electricity: Annual Demand Breakdown (non-transmission generation deducted)
Electricity: Net Annual National Demand (TWh, Weather Corrected)
Net demand on the transmission system - Does not add demand from interconnectors, pumping, storage or power stations
Note this is not a good measure of system utilisation and energy flows around GB
National Demand is defined in the Grid code as: demand on the transmission system but does not add station demand, pumping demand, storage demand, interconnector exports
Key non-transmission Generation Assumptions: Solar 12.4%, onshore wind ~27%, offshore wind ~31%
Annual chart data
Electricity Year Beginning | time axis 2005-01-01 to 2050-01-01
| History | 2005-01-01: 343; 2006-01-01: 338; 2007-01-01: 337; 2008-01-01: 324; 2009-01-01: 313; 2010-01-01: 310; 2011-01-01: 308; 2012-01-01: 304; 2013-01-01: 298; 2014-01-01: 289; 2015-01-01: 283; 2016-01-01: 271; 2017-01-01: 263; 2018-01-01: 255
| Community Renewables | [13 empty] | 255 | 241 | 234 | 227 | 221 | 216 | 210 | 206 | 200 | 197 | 195 | 194 | 193 | 194 | 196 | 197 | 198 | 200 | 201 | 201 | 202 | 204 | 206 | 206 | 207 | 207 | 208 | 208 | 208 | 208 | 209 | 210 | 211
| Two Degrees | [13 empty] | 255 | 243 | 239 | 236 | 233 | 231 | 230 | 228 | 227 | 229 | 232 | 236 | 240 | 244 | 248 | 253 | 257 | 261 | 266 | 270 | 273 | 277 | 280 | 283 | 286 | 288 | 290 | 292 | 294 | 296 | 298 | 299 | 299
| Steady Progression | [13 empty] | 255 | 245 | 248 | 249 | 250 | 250 | 250 | 251 | 251 | 251 | 252 | 254 | 255 | 257 | 258 | 259 | 261 | 262 | 264 | 267 | 271 | 275 | 280 | 285 | 290 | 296 | 301 | 305 | 310 | 314 | 317 | 320 | 322
| Consumer Evolution | [13 empty] | 255 | 244 | 244 | 242 | 241 | 239 | 237 | 235 | 233 | 230 | 229 | 228 | 226 | 225 | 224 | 223 | 222 | 222 | 222 | 223 | 225 | 228 | 231 | 236 | 240 | 245 | 250 | 254 | 259 | 263 | 267 | 270 | 273
| 5 Year Forecast | 2018-01-01: 255; 2019-01-01: 243; 2020-01-01: 242; 2021-01-01: 239; 2022-01-01: 237; 2023-01-01: 235
Electricity: Annual Demand Breakdown (non-transmission generation not deducted)
This data now published in the FES Data workbook, table ED1
Filter: | Tab = Component
Filter: | Peak/Annual/Minimum = Annual
Data in Electricity years - 2005 in the table equates to 2005/06
Shown in the table is National Grid ESO's view of underlying weather corrected consumer demand, before reduction by on-site and behind the meter generation
Generation output and storage is not deducted from these figures - this is a view of underlying demand
Demand from generators (station demand), pumping demand (pumped hydro storage sites) and electricity storage (mostly batteries) is not included in the numbers below
Residential demand includes appliances, light, resistive heat, hot water, heat pumps, EV, Smart meter reduction, air conditioners, district heat
Industrial demand includes sites directly connected to the transmission system ~5TWh/year. Also includes industrial district heat and hydrogen production
Commercial demand includes commercial Evs, commercial district heat and rail transport
Numbers may not match other publications due to data source differences and generation output assumptions