## E&R Implementation Timeline
| Year | E&R Ref | Task ID | Topic | Duration | Start | Finish | Links | 2016 |  |  | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022 | [11 empty] | 2023 | [11 empty] | 2024
| Month | [7 empty] | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
EU Commission Positive Vote | bar: 2016 Oct
Entry Into Force - Sep 2017 (estimated) | bar: 2017 Sep
System Defence Plan Development by EIF+12months | bar: 2018 Sep
Workgroup design phase of System Defence Plan | bar: 2017 May to 2018 Feb
1m | Consultation | bar: 2018 Mar to 2018 Apr
Report to Authority | bar: 2018 May
1m | Decision | bar: 2018 Jun; 2018 Sep
System Defence Plan Implementation by EIF+24months | bar: 2019 Sep
Implementation of System Defence Plan including GB Code Mods | bar: 2018 Jun to 2019 Feb
1m | Consultation | bar: 2019 Mar to 2019 Apr
Report to Authority | bar: 2019 May
1m | Decision | bar: 2019 Jun; 2019 Sep
Restoration Plan Development by EIF+12months | bar: 2018 Sep
Workgroup design phase of Restoration Plan | bar: 2017 May to 2018 Feb
1m | Consultation | bar: 2018 Mar to 2018 Apr
Report to Authority | bar: 2018 May
1m | Decision | bar: 2018 Jun; 2018 Sep
Restoration Plan Implementation by EIF+24months | bar: 2019 Sep
Implementation of System Defence Plan including GB Code Mods | bar: 2018 Jun to 2019 Feb
1m | Consultation | bar: 2019 Mar to 2019 Apr
Report to Authority | bar: 2019 May
1m | Decision | bar: 2019 Jun; 2019 Sep
Market Interactions by EIF+12months | bar: 2018 Sep
Develop Proposals for rules concerning the suspension and restoration of market activities | bar: 2017 May to 2018 Feb
1m | Consultation | bar: 2018 Mar to 2018 Apr
Report to Authority | bar: 2018 May
1m | Decision | bar: 2018 Jun; 2018 Sep
1m | Publish on TSO Website | bar: 2018 Jul; 2018 Sep
EIF + 5 Years | bar: 2022 Sep
Automatic under-frequency control scheme | bar: 2022 Sep
Communications, Tools and Facilities | bar: 2022 Sep
Define Compliance Testing Plan | bar: 2022 Sep

## High Level Plan
Chapter | Section | Notes | EIF | EIF+12month | EIF+18month | EIF+24months | EIF+30months | EIF+3years | EIF+5years
CHAPTER I GENERAL PROVISIONS | [5 empty] | Article 10 currently n/a in GB
CHAPTER II SYSTEM DEFENCE PLAN | SECTION 1 GENERAL PROVISIONS
CHAPTER II SYSTEM DEFENCE PLAN | SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN |  |  | 12m notify DSOs,SGUs measures |  | Implement measures |  |  | aLFDD
CHAPTER III RESTORATION PLAN | SECTION 1 GENERAL PROVISIONS |  |  | Design Plan and notify |  | Implement measures
CHAPTER III RESTORATION PLAN | SECTION 2 RE-ENERGISATION | Procedure within restoration plan |  | Design Plan and notify |  | Implement measures
CHAPTER III RESTORATION PLAN | SECTION 3 FREQUENCY MANAGEMENT | Procedure within restoration plan |  | Design Plan and notify |  | Implement measures
CHAPTER III RESTORATION PLAN | SECTION 4 RESYNCHRONISATION | Procedure within restoration plan |  | Design Plan and notify |  | Implement measures
CHAPTER IV MARKET INTERACTIONS |  | No timescale defined for NRA approval |  | Develop proposal for market suspensions rules and settlement |  |  |  | ENTSOE report
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | [8 empty] | Critical comms, tools and facilities
CHAPTER VI COMPLIANCE AND REVIEW | SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | [7 empty] | Define test plan
CHAPTER VI COMPLIANCE AND REVIEW | SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | [7 empty] | System Defence and Restoration Plans to be reviewed every 5 years
CHAPTER VII FINAL PROVISIONS

## Code mapping
|  | ER October 2016 as voted text |  | GC No | Mapping GB Codes: | F:TF:WF:V | [5 empty] | Notes | Comments/Action |  | Responsible Party: | [5 empty] | Obligation
Chapter/Section | Article | Clause | System Restoration Plan |  | Grid Code | SQSS | STC (Note LSP Issue 6 has been used) | Dcode | BSC | EU Codes | Other |  |  |  | DECC | Ofgem | TSO | DSO | Generator | Other | Timescale | Grid Code High Level | Grid Code Proposed Change | STCP Highlevel | STC Proposed Change
CHAPTER I GENERAL PROVISIONS | Article 1 Subject matter | For the purposes of safeguarding operational security, preventing the propagation or deterioration of an incident to avoid a widespread disturbance and the blackout state as well to allow for the efficient and rapid restoration of the electricity system from the emergency or blackout states, this Regulation establishes a network code which lays down the requirements on: |  | GC0127 / GC0128 | OC9 | [6 empty] | Description - no specific action | [8 empty] | EIF
CHAPTER I GENERAL PROVISIONS | Article 1 Subject matter | (a) the management by TSOs of the emergency, blackout and restoration states; |  | GC0127 / GC0128 | OC9
CHAPTER I GENERAL PROVISIONS | Article 1 Subject matter | (b) the coordination of system operation across the Union in the emergency, blackout and restoration states; |  | GC0127 / GC0128
CHAPTER I GENERAL PROVISIONS | Article 1 Subject matter | (c) the simulations and tests to guarantee a reliable, efficient and fast restoration of the interconnected transmission systems to the normal state from the emergency or blackout states; |  | GC0127 / GC0128 | OC5.7 | [16 empty] | Testing is covered under OC5.7 however further check need to be considered with regard to simulations | Need to include simulations
CHAPTER I GENERAL PROVISIONS | Article 1 Subject matter | (d) the tools and facilities needed to guarantee a reliable, efficient and fast restoration of the interconnected transmission systems to the normal state from the emergency or blackout states. |  | GC0127 / GC0128
GC0127 / GC0128
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 1. This Regulation shall apply to TSOs, DSOs, SGUs, defence service providers, restoration service providers, balance responsible parties, balancing service providers, nominated electricity market operators (‘NEMO’) and other entities designated to execute market functions pursuant to Commission Regulation (EU) 2015/1222 and to Commission Regulation (EU) 2016/1719 . |  | GC0127 / GC0128 | OC9.3 | [16 empty] | TO obligations are covered in the STC and STCP's.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 2. In particular, this Regulation shall apply to the following SGUs: |  | GC0127 / GC0128 | [7 empty] | Need to fully explore SGUs in Scope
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | (a) existing and new power generating modules classified as type C and D in accordance with the criteria set out in Article 5 of Commission Regulation (EU) 2016/631 ; |  | GC0127 / GC0128 | OC9.4.5 |  |  |  |  | RfG | [12 empty] | This is tricky for two reasons. RfG requires Black Start to only be provided by Type C and Type D Power Generating Modules. There is no mandatory obligation to provide Black Start but if a Black start service is provided then the conditions of RfG must be applied to those Stations. There is also a slight terminology issue between Type C and Type D and Black Start Stations. Issue for discussion.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | (b) existing and new power generating modules classified as type B in accordance with the criteria set out in Article 5 of Commission Regulation (EU) 2016/631, where they are identified as SGUs in accordance with Article 11(4) and Article 23(4); |  | GC0127 / GC0128 | ? |  |  |  |  | RfG | [12 empty] | Not sure about this. Black Start is not mandatory and even then it applies to Type C and D which in GB is 10MW and above.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | (c) existing and new transmission-connected demand facilities; |  | GC0127 / GC0128 | OC9.4.7.11 | [16 empty] | Network Operators and Non Embedded Customers need to be part of the LJRP | It is not clear if OC9.4.7.11 fully covers all the implications of ERC.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | (d) existing and new transmission connected closed distribution systems; |  | GC0127 / GC0128 | 0C9.4.7.11 | [17 empty] | It is not clear if the requirements of OC9.4.7.11 includes Closed Distribuiton Systems - if it does the Grid Code will need to be updated.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | (e) providers of redispatching of power generating modules or demand facilities by means of aggregation and providers of active power reserve in accordance with Title 8 of Regulation (EU) 2017/XXX [SO GLs]; and |  | GC0127 / GC0128 | OC9 |  |  |  |  | TSOG | [11 empty] | Redespatch is generaly covered under OC9 | OC9 generally does not apply to Aggregators and those with commercial demand contracts.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | (f) existing and new high voltage direct current ('HVDC') systems and direct current-connected power park modules in accordance with the criteria set out in Article 4(1) of Commission Regulation (EU) 2016/1447 . |  | GC0127 / GC0128 | ? | [17 empty] | OC9 does generally not apply to HVDC Systems. Where they are capable of Black Start they can be used but OC9 does not explicity apply to HVDC Systems. HVDC Systems are not included in the definition of a Black Start Station.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 3. This Regulation shall apply to existing and new type A power generating modules, in accordance with the criteria set out in Article 5 of Regulation (EU) 2016/631, to existing and new type B power generating modules other than those referred to in paragraph 2(b), as well as to existing and new demand facilities, closed distribution systems and third parties providing demand response where they qualify as defence service providers or restoration service providers pursuant to Article 4(4). |  | GC0127 / GC0128 | ? | [17 empty] | The current Grid Code applies only to Black Start Stations. There is loose reference to non-Black Start Power Stations as part of the LJRP but this is not specific. In addiiton, OC9 does not include contributions from commerical demand providers.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 4. Type A and type B power generating modules referred to in paragraph 3, demand facilities and closed distribution systems providing demand response may fulfil the requirements of this Regulation either directly or indirectly through a third party, under the terms and conditions set in accordance with Article 4(4). |  | GC0127 / GC0128 | ? | [17 empty] | This would need to be added to the Grid Code.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 5. This Regulation shall apply to energy storage units of a SGU, a defence service provider or a restoration service provider, which can be used to balance the system, provided that they are identified as such in the system defence plans, restoration plans or in the relevant service contract. |  | GC0127 / GC0128 | OC9? | [17 empty] | Techncially this should already be included but will be contigent upon the implementation of GC0096 (Storage). GC0096 basically treats Storage as a subset of generation so any obligation which applies to Generation will also apply to Storage. GC0096 however needs to be approved by Ofgem and even then it will apply based on Ofgem's decision date and its connection date which would be 12 months after Ofgem's decsion date.
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 6. This Regulation shall apply to all transmission systems, distribution systems and interconnections in the Union except transmission systems and distribution systems or parts of the transmission systems and distribution systems of islands of Member States of which the systems are not operated synchronously with Continental Europe, Great Britain, Nordic, Ireland and Northern Ireland or Baltic synchronous area, provided that this non synchronous operation does not result from a disturbance |  | GC0127 / GC0128 | [18 empty] | EU Specific - No requirement to change Grid Code
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 7. In Member States where more than one transmission system operator exists, this Regulation shall apply to all transmission system operators within that Member State. Where a transmission system operator does not have a function relevant to one or more obligations under this Regulation, Member States may provide that the responsibility for complying with those obligations is assigned to one or more different, specific transmission system operators. |  | GC0127 / GC0128 | [18 empty] | Not applicable in GB
CHAPTER I GENERAL PROVISIONS | Article 2 Scope | 8. The TSOs of Lithuania, Latvia and Estonia are, as long as and to the extent that they are operating in a synchronous mode in a synchronous area where not all countries are bound by Union legislation, exempted from the application of Articles 15, 29 and 33, unless otherwise provided for in a cooperation agreement with third country TSOs constituting the basis for their cooperation concerning secure system operation in accordance with Article 10. |  | GC0127 / GC0128 | [18 empty] | Not applicable
GC0127 / GC0128
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | For the purposes of this Regulation, the definitions provided for in Article 2 of Directive 2009/72/EC of the European Parliament and of the Council , Article 2 of Regulation (EC) No 714/2009, Article 2 of Commission Regulation (EU) No 543/2013 , Article 2 of Regulation (EU) 2015/1222, Article 2 of Regulation (EU) 2016/631, Article 2 of Regulation (EU) 2016/1388 , Article 2 of Regulation (EU) 2016/1447 Article 2 of Regulation (EU) 2016/1719, and Article 2 of Regulation (EU) 2017/XXX [SO GLs] shall apply. |  | GC0127 / GC0128 | [18 empty] | Not applicable
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | In addition, the following definitions shall apply: |  | GC0127 / GC0128
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (1) ‘defence service provider’ means a legal entity with a legal or contractual obligation to provide a service contributing to one or several measures of the system defence plan; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (2) ‘restoration service provider’ means a legal entity with a legal or contractual obligation to provide a service contributing to one or several measures of the restoration plan; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (3) ‘high priority significant grid user’ means the significant grid user for which special conditions apply for disconnection and re-energisation; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (4) ‘netted demand’ means the netted value of active power seen from a given point of the system, computed as (load – generation), generally expressed in kilowatts (kW) or megawatts (MW), at a given instant or averaged over any designated interval of time; |  | GC0127 / GC0128 | [18 empty] | ?
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (5) ‘restoration plan’ means all technical and organisational measures necessary for the restoration of the system back to normal state; |  | GC0127 / GC0128 | [18 empty] | Covered in LJRP?
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (6) ‘re-energisation’ means reconnecting generation and load to energise the parts of the system that have been disconnected; |  | GC0127 / GC0128 | [18 empty] | To be added to the Grid Code where required
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (7) ‘top-down re-energisation strategy’ means a strategy that requires the assistance of other TSOs to re-energise parts of the system of a TSO; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (8) ‘bottom-up re-energisation strategy’ means a strategy where part of the system of a TSO can be re-energised without the assistance from other TSOs; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (9) ‘resynchronisation’ means synchronising and connecting again two synchronised regions at the resynchronisation point; |  | GC0127 / GC0128 | [17 empty] | Included in GB Code | This may need to be added to the Grid Code however Re-Synchronisation is used in other sections of the code and we need to make sure there are no unintended consequences
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (10) ‘frequency leader’ means the TSO appointed and responsible for managing the system frequency within a synchronised region or a synchronous area in order to restore system frequency back to the nominal frequency; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (11) ‘synchronised region’ means the fraction of a synchronous area covered by interconnected TSOs with a common system frequency and which is not synchronised with the rest of the synchronous area; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (12) ‘resynchronisation leader’ means the TSO appointed and responsible for the resynchronisation of two synchronised regions; |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 3 Definitions | (13) ‘resynchronisation point’ means the device used to connect two synchronised regions, usually a circuit breaker. |  | GC0127 / GC0128 | [18 empty] | This may need to be added to the Grid Code
GC0127 / GC0128
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 1. When applying this Regulation, Member States, regulatory authorities, competent entities and system operators shall: |  | GC0127 / GC0128 | [16 empty] | EIF?
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (a) apply the principles of proportionality and non-discrimination; |  | GC0127 / GC0128 | [18 empty] | Not applicable - Generally covered in principles of the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (b) ensure transparency; |  | GC0127 / GC0128 | [18 empty] | Not applicable - Generally covered in principles of the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (c) apply the principle of optimisation between the highest overall efficiency and lowest total costs for all parties involved; |  | GC0127 / GC0128 | [18 empty] | Not applicable - Generally covered in principles of the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (d) ensure that TSOs make use of market-based mechanisms as far as is possible to ensure network security and stability; |  | GC0127 / GC0128 | BC1, BC2, BC3 | [17 empty] | BC1, BC2, BC3 cover market arrangements. OC9 covers black start where it is assumed that the Market has been suspended. OC7 covers System Warnings.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (e) respect technical, legal, personal safety and security constraints; |  | GC0127 / GC0128 | [9 empty] | How is this not applicable? Surely in licence obligations to comply with law? | [8 empty] | Not applicable in GB Code
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (f) respect the responsibility assigned to the relevant TSO in order to ensure system security, including as required by national legislation; |  | GC0127 / GC0128 | [18 empty] | Already covered in GB Code
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (g) consult with relevant DSOs and take account of potential impacts on their system; and |  | GC0127 / GC0128 | OC7, OC9 | [17 empty] | Part of Grid Code Governance Process
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (h) take into consideration agreed European standards and technical specifications. |  | GC0127 / GC0128 | [9 empty] | Don't think they mean Network codes here, I think it is technical specifications and EN standards that are meant | [8 empty] | Grid Code to be updated to include other Network Codes
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 2. Each TSO shall submit the following proposals to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72 for approval: |  | GC0127 / GC0128 | [18 empty] | Already established Grid Code process
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (a) the terms and conditions to act as defence service providers on a contractual basis in accordance with paragraph 4; |  | GC0127 / GC0128 | [9 empty] | This is defence rather than restoration, Black Satrt contracts are not relevant here, these are to do with mandatoryservice agreements along with the sections of when system is in abnormal or emergency state, in-which NGESO will issue emergency injstructions in compliance with BSC/ GC and may suspend the market. Where will these T&Cs sit? | [8 empty] | Black Start only covers Black Start Stations and no other commercial providers. The Grid Code may need to be updated to incldue this
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (b) the terms and conditions to act as restoration service providers on a contractual basis in accordance with paragraph 4; |  | GC0127 / GC0128 | [9 empty] | Thse are the Black Start providers in GB terms. Where will these sit?
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (c) the list of SGUs responsible for implementing on their installations the measures that result from mandatory requirements set out in Regulations (EU) 2016/631, (EU) 2016/1388 and (EU) 2016/1447and/or from national legislation and the list of the measures to be implemented by these SGUs, identified by the TSOs under Art. 11(4)(c) and 23(4)(c); |  | GC0127 / GC0128 | ECC, ECP, DRSC | [8 empty] | This is a list, not a set of criteria that mean you could be on the list, I think this is a list of all power stations that are captured by this code and then whether they have obligations that they must meet. | [7 empty] | Already captured through RfG, HVDC and DCC Implementation
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (d) the list of high priority significant grid users referred to in Articles 11(4)(d) and 23(4)(d) or the principles applied to define those and the terms and conditions for disconnecting and re-energizing the high priority grid users, unless defined by the national legislation of Member States. |  | GC0127 / GC0128 | OC9 | [8 empty] | This is a list, not a set of criteria that mean you could be on the list, I think this is a list of all power stations that are captured by this code and then whether they have obligations that they must meet. | [8 empty] | Believed to be covered in OC9.3 Scope.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (e) the rules for suspension and restoration of market activities in accordance with Article 36(1); |  | GC0127 / GC0128 | OC9.4.6, BC2 and BSC | [17 empty] | The Grid Code and BSC detail the provisions for when the market will be suspended
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (f) specific rules for imbalance settlement and settlement of balancing energy in case of suspension of market activities, in accordance with Article 39(1); |  | GC0127 / GC0128 | OC9.4.6, BC2 and BSC | [17 empty] | The Grid Code and BSC detail the provisions for when the market will be suspended
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (g) the test plan in accordance with Article 43(2). |  | GC0127 / GC0128 | ? | [8 empty] | Partly to do with OC5 in respect of defence plan and restoration plan This then needs to be an obligation on NGESO to submit the test plans to Ofgem. Need to confirm that OC9.7 and RFG blackstart testing requirements are aligned.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 3. Where a Member State has so provided, the proposals referred to in points (a) to (d) and (g) of paragraph 2 may be submitted for approval to an entity other than the regulatory authority. Regulatory authorities and entities designated by the Member States pursuant to this paragraph shall decide on the proposals referred to in paragraph 2 within six months from the date of submission by the TSO. |  | GC0127 / GC0128 | ? | [8 empty] | Could be designated back to NGESO?
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 4. The terms and conditions to act as defence service provider and as restoration service provider shall be established either in the national legal framework or on a contractual basis. If established on a contractual basis, each TSO shall develop by [12 months after entry into force of this Regulation] a proposal for the relevant terms and conditions, which shall define at least: |  | GC0127 / GC0128 | OC9 | [8 empty] | I would disagree that these are the T&Cs in OC9, these are separately called out below | [6 empty] | EIF+12months |  | Defence Service Providers are not currently not defined in the Grid Code. These will need to be explicity defined.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (a) the characteristics of the service to be provided; |  | GC0127 / GC0128 | [6 empty] | CUSC 4.1.1.1 Contractual Terms and Conditions Licence Condition C16 - Standard Contract Terms? | See also Terms and Condiitons related to Emergecny and restoration |  | ok | [8 empty] | These will need to be explicity defined
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (b) the possibility of and conditions for aggregation; and |  | GC0127 / GC0128 | [6 empty] | Standard Contract Terms | See also Terms and Condiitons related to Emergecny and restoration | [10 empty] | Aggregation will need to be defined and included in the Grid Code. It is unclear if this would be achieved by referring to a TEERE party.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (c) for restoration service providers, the target geographical distribution of power sources with black start and island operation capabilities. |  | GC0127 / GC0128 | OC.9.4.7.2 | [5 empty] | Black Start Contracts | See also Terms and Condiitons related to Emergecny and restoration |  | Is this not already defined through LRJPs? I assume the geographic area is related to GSPs and system boundaries? | [8 empty] | Again this needs some thought. It is probably too much of a step to include the definition of these within the definition of a Black Start Station.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 5. By [12 months after entry into force of this Regulation],each TSO shall notify the regulatory authority or the entity designated by the Member State the system defence plan designed pursuant to Article 11 and the restoration plan designed pursuant to Article 23, or at least the following elements of those plans: |  | GC0127 / GC0128 | OC9 | [8 empty] | But you issued a separate pair of plans instead of referencing OC9 | [6 empty] | EIF+12months |  | OC9 covers this and the LJRP.
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (a) the objectives of the system defence plan and the restoration plan, including the phenomena to be managed or the situations to be solved; |  | GC0127 / GC0128 | OC9.2 | [16 empty] | OC9.2 covers the Objective
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (b) the conditions triggering the activation of the measures of the system defence plan and the restoration plan; |  | GC0127 / GC0128 | OC9.2.5
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (c) the rationale of each measure, explaining how it contributes to the objectives of the system defence plan and the restoration plan, and the party responsible for implementing those measures; and |  | GC0127 / GC0128 | OC9.2.5
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | (d) the deadlines set out pursuant to Articles 11 and 23 for the implementation of the measures. |  | GC0127 / GC0128 | ? | [8 empty] | Already active expect that SGUs not notified
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 6. Where a TSO is required or permitted under this Regulation to specify, establish or agree on requirements, terms and conditions or methodologies that are not subject to approval in accordance with paragraph 2, Member States may require prior approval by the regulatory authority, the entity designated by the Member State or other competent authorities of the Member States of these requirements, terms and conditions or methodologies. |  | GC0127 / GC0128 | [18 empty] | Not required
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 7. If a TSO deems an amendment to the documents, approved in accordance with paragraph 3, to be necessary, the requirements provided for in paragraphs 2 to 5 shall apply to the proposed amendment. TSOs proposing an amendment shall take into account the legitimate expectations, where necessary, of power generating facility owners, demand facility owners and other stakeholders based on the initially specified or agreed requirements or methodologies. |  | GC0127 / GC0128 | [18 empty] | Demand Providers not included in Black Start Plans
CHAPTER I GENERAL PROVISIONS | Article 4 Regulatory aspects | 8. Any party can complain against a relevant system operator or TSO in relation to that relevant system operator’s or TSO's obligations or decisions under this Regulation and may refer the complaint to the regulatory authority which, acting as dispute settlement authority, shall issue a decision within two months after receipt of the complaint. That period may be extended by a further two months where additional information is sought by the regulatory authority. That extended period may be further extended with the agreement of the complainant. The regulatory authority's decision shall be binding unless and until overruled on appeal. |  | GC0127 / GC0128 | GR | [17 empty] | Covered under the Governance Rules and Ofgem's processes.
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | 1. Where this Regulation provides that a TSO shall consult concerned parties for actions it defines before real-time or in real-time, the following procedure shall apply: |  | GC0127 / GC0128 | GR |  |  |  | X |  |  | We need a national procedure Operational timescales. |  | This is real-time or near real-time not a GCGP timescales. | [6 empty] | EIF or when first needed |  | Part of Grid Code Governance Process
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (a) the TSO shall liaise with at least the parties identified in the Articles of this Regulation requiring consultation; |  | GC0127 / GC0128 | GR | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Part of Grid Code Governance Process
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (b) the TSO shall explain the rationale and objective of the consultation and of the decision that it has to take; |  | GC0127 / GC0128 | GR | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Part of Grid Code Governance Process
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (c) the TSO shall collect from the parties referred to in point (a) any relevant information and their assessment; |  | GC0127 / GC0128 | ? | [8 empty] | This is real-time or near real-time not a GCGP timescales.
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (d) the TSO shall duly take into account the views, situations and constraints of the parties consulted; |  | GC0127 / GC0128 | GR | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Part of Grid Code Governance Process
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (e) before taking a decision, the TSO shall provide an explanation to the parties consulted of the reasons for following or not their views. |  | GC0127 / GC0128 | GR | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Part of Grid Code Governance Process
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | 2. Where this Regulation provides that a TSO shall coordinate the execution of a set of actions in real-time with several parties, the following procedure shall apply: |  | GC0127 / GC0128 | OC7 | [8 empty] | This is real-time or near real-time not a GCGP timescales.
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (a) the TSO shall liaise at least with the parties identified in the Articles of this Regulation requiring real time coordination; |  | GC0127 / GC0128 | OC7 | [8 empty] | This is real-time or near real-time not a GCGP timescales.
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (b) the TSO shall explain the rationale and objective of the coordination and of the actions to be taken; |  | GC0127 / GC0128 | OC7 | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Information about specific actions are generally covered under OC7
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (c) the TSO shall make an initial proposal on actions to be taken by each party; |  | GC0127 / GC0128 | ? | [8 empty] | This is real-time or near real-time not a GCGP timescales.
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (d) the TSO shall collect from the parties referred to in point (a) any relevant information and their assessment; |  | GC0127 / GC0128 | DRC, ECC6.5.6, BC1, BC2 | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Real time data (ECC.6.5.6), Balancing data (BC1, BC2), Static Data (DRC) are all covered under the Grid Code
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (e) the TSO shall make a final proposal on actions to be taken by each party, duly taking into account the views, situations and constraints of the concerned parties and setting a deadline for parties to express their opposition to the actions proposed by the TSO; |  | GC0127 / GC0128 | OC7, OC9 | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Under the Grid Code instructions are given by the System Operator
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (f) where the concerned parties do not oppose executing the actions proposed by the TSO, each party, including the TSO, shall execute the actions in line with the proposal; |  | GC0127 / GC0128 | OC7, OC9 | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Under the Grid Code instructions are generally given by the System Operator
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (g) where one or more of the parties refuse the action proposed by the TSO within the set deadline, the TSO shall refer the action proposed to the relevant authority for decision, together with a justification of the rationale and objectives of the action proposed by the TSO and of the assessment and position of the parties; |  | GC0127 / GC0128 | ? | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Under this situation a User would be in breach of the the Grid Code and the matter could be referred to Ofgem.
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | (h) if real-time referral to the relevant authority is not possible, the TSO shall initiate an equivalent action that has the least or no impact on the parties that refused to execute the action proposed. |  | GC0127 / GC0128 | [9 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | In real time, the System Operator would need to manage the System with the constraints at that time
CHAPTER I GENERAL PROVISIONS | Article 5 Consultation and coordination | 3. A party may refuse to execute real time actions proposed by the TSO under the coordination procedure described in paragraph 2 if it justifies that the proposed action would lead to the violation of one or more technical, legal, personal safety or security constraint(s). |  | GC0127 / GC0128 | ? | [8 empty] | This is real-time or near real-time not a GCGP timescales. | [8 empty] | Under the Governance arrangements the Grid Code should not inculde statemements of this type. Appropriate dispute procedures are in place to address such concerns
GC0127 / GC0128
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | 1. When designing its system defence plan pursuant to Article 11 and its restoration plan pursuant to Article 23 or when reviewing its system defence plan pursuant to Article 50 and its restoration plan pursuant to Article 51, each TSO shall ensure the consistency with the corresponding measures in the plans of TSOs within its synchronous area and in the plans of neighbouring TSOs belonging to another synchronous area of at least the following measures : |  | GC0127 / GC0128 | OC9 |  |  |  |  | TSOG |  | New - managed by RSC? Agreed with neighbouring TSOs. | [10 empty] | Covered in OC9 and Local Joint Restoration Plan
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (a) inter-TSO assistance and coordination in emergency state, pursuant to Article 14; |  | GC0127 / GC0128 | [18 empty] | Additional wording in Grid Code required. The scope of OC9 does not extend to Interconnectors.
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (b) frequency management procedures, pursuant to Article 18 and Article 28, excluding the establishment of target frequency in case of bottom-up re-energisation strategy before any resynchronisation to the interconnected transmission system; |  | GC0127 / GC0128 | ? | [17 empty] | BC3 covers frequency management though not really under emergency cirumstances. OC9 does not really cover frequency management. This is probably an area which requires further expansion.
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (c) assistance for active power procedure, pursuant to Article 21; |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (d) top-down re-energisation strategy, pursuant to Article 27. |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | 2. The consistency assessment of the system defence plan and the restoration plan in accordance with paragraph 1 shall include the following tasks: |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (a) exchange of information and data related to the measures referred to in paragraph 1 among the TSOs concerned; |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (b) identification of incompatibilities of measures referred to in paragraph 1, in the plans of the involved TSOs; |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (c) identification of potential threats to operational security in the capacity calculation region. These threats include, inter alia, regional common mode failures with significant impact on the transmission systems of the involved TSOs; |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (d) assessment of the effectiveness of measures referred to in paragraph 1 specified in the system defence plans and the restoration plans of the involved TSOs, to manage the potential threats referred to in point (c); |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (e) consultation with RSCs to assess the consistency of measures referred to in paragraph 1 within the entire concerned synchronous area; |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | (f) identification of mitigation actions in case of incompatibilities in the system defence plans and the restoration plans of the involved TSOs or in case that measures are missing in the system defence plans and the restoration plans of the involved TSOs. |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | 3. By [12 months after the entry into force of this Regulation], each TSO shall transmit the measures referred to in paragraph 1 to the relevant RSC(s) set up pursuant to Article 77 of Regulation (EU)2017/XXX [SO GLs]. Within 3 months from the submission of the measures, the RSC(s) shall produce a technical report on the consistency of the measures based on the criteria set out in paragraph 2. Each TSO shall ensure the availability of its own skilled experts to assist the RSC(s) in preparing this report. |  | GC0127 / GC0128 | ? |  |  |  |  | TSOG | [10 empty] | EIF+12months
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | 4. The RSC(s) shall transmit without delay the technical report referred to in paragraph 3 to all the TSOs involved, which shall in turn transmit it to the relevant regulatory authorities, as well as to ENTSO for Electricity, for the purposes of Article 52. |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 6 Regional coordination | 5. All TSOs of each capacity calculation region shall agree on a threshold above which the impact of actions of one or more TSOs in the emergency, blackout or restoration states is considered significant for other TSOs within the capacity calculation region. |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 7 Public consultation | 1. The relevant TSOs shall consult stakeholders, including the competent authorities of each Member State, on proposals subject to approval in accordance with points (a), (b), (e), (f) and (g) of Article 4(2). The consultation shall last for a period of not less than one month. |  | GC0127 / GC0128 | GR | [17 empty] | Covered by Goverance Rules
CHAPTER I GENERAL PROVISIONS | Article 7 Public consultation | 2. The relevant TSOs shall duly take into account the views of the stakeholders resulting from the consultations prior to the submission of the draft proposal. In all cases, a sound justification for including or not including the views of the stakeholders shall be provided and published in a timely manner before, or simultaneously with, the publication of the proposal. |  | GC0127 / GC0128 | GR | [17 empty] | Covered by Goveranance Rules
CHAPTER I GENERAL PROVISIONS | Article 8 Recovery of costs | 1. The costs borne by system operators subject to network tariff regulation and stemming from the obligations laid down in this Regulation shall be assessed by the relevant regulatory authorities in accordance with Article 37 of Directive 2009/72. Costs assessed as reasonable, efficient and proportionate shall be recovered through network tariffs or other appropriate mechanisms. |  | GC0127 / GC0128 | ?
CHAPTER I GENERAL PROVISIONS | Article 8 Recovery of costs | 2. If requested by the relevant regulatory authorities, system operators referred to in paragraph 1 shall, within three months of the request, provide the information necessary to facilitate assessment of the costs incurred. |  | GC0127 / GC0128 | ? | [17 empty] | Ofgem Direction?
CHAPTER I GENERAL PROVISIONS | Article 9 Confidentiality obligations | 1. Any confidential information received, exchanged or transmitted pursuant to this Regulation shall be subject to the conditions of professional secrecy laid down in paragraphs 2, 3 and 4. |  | GC0127 / GC0128 | [18 empty] | The Grid Code covers data confidentiality. Confidentiality is covered in the Planning Code, OC12, Goverance Rules (GC12)
CHAPTER I GENERAL PROVISIONS | Article 9 Confidentiality obligations | 2. The obligation of professional secrecy shall apply to any persons subject to the provisions of this Regulation. |  | GC0127 / GC0128 | [18 empty] | The Grid Code covers data confidentiality. Confidentiality is covered in the Planning Code, OC12, Goverance Rules (GC12)
CHAPTER I GENERAL PROVISIONS | Article 9 Confidentiality obligations | 3. Confidential information received by the persons referred to in paragraph 2 in the course of their duties may not be divulged to any other person or authority, without prejudice to cases covered by national legislation, the other provisions of this Regulation or other relevant Union legislation. |  | GC0127 / GC0128 | [18 empty] | The Grid Code covers data confidentiality. Confidentiality is covered in the Planning Code, OC12, Goverance Rules (GC12)
CHAPTER I GENERAL PROVISIONS | Article 9 Confidentiality obligations | 4. Without prejudice to cases covered by national or Union legislation, regulatory authorities, bodies or persons who receive confidential information pursuant to this Regulation may use it only for the purpose of carrying out their duties under this Regulation. |  | GC0127 / GC0128 | [18 empty] | The Grid Code covers data confidentiality. Confidentiality is covered in the Planning Code, OC12, Goverance Rules (GC12)
CHAPTER I GENERAL PROVISIONS | Article 10 Agreement with TSOs not bound by this Regulation | Where a synchronous area encompasses both Union and third country TSOs, by [18 months after entry into force of this Regulation], all Union TSOs in that synchronous area shall endeavour to conclude with the third country TSOs not bound by this Regulation an agreement setting the basis for their cooperation concerning secure system operation and setting out arrangements for the compliance of the third country TSOs with the obligations set in this Regulation. |  | GC0127 / GC0128 | [7 empty] | Not applicable in GB? | [8 empty] | EIF+18months |  | GB is one Synchronous Area with only one SO. The LJRP places obligations on Transmission Licensee's and DNO's.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | 1. By [12 months after entry into force of this Regulation], each TSO shall design a system defence plan in consultation with relevant DSOs, SGUs, national regulatory authorities, or entities referred to in Article 4(3), , neighbouring TSOs and the other TSOs in its synchronous area. |  | GC0127 | [6 empty] | System Defence Plan (Ref 1) or shortened to SDP (1) | Likely to contain actions already in GB Captured in System Defence Plan | [8 empty] | EIF+12months
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | 2. When designing its system defence plan, each TSO shall take into account at least the following elements: |  | GC0127 | [6 empty] | SDP (1) | Covered in section 1 System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (a) the operational security limits set out in accordance with Article 25 of Regulation (EU) 2017/XXX [SO GLs]; |  | GC0127 | ECC's | X |  | TSOG |  | TSOG | SDP (1) | Covered in section 1 System Defence Plan | [10 empty] | SQSS covers these requirements together with the User's requirements in the ECC's.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (b) the behaviour and capabilities of load and generation within the synchronous area; |  | GC0127 | ECC's, DRSC, DRC | [5 empty] | SDP (1) | Covered in section 1 System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (c) the specific needs of the high priority significant grid users listed pursuant to point (d) of paragraph 4; and |  | GC0127 | [6 empty] | SDP (1) | Covered in section 1 System Defence Plan | [10 empty] | Needs discussion but specific provision already exisits in the Grid Code to specific User's eg BC3 - AGR / Magnos plant. This is a specific case and the Grid Code probably needs updating in this respect.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (d) the characteristics of its transmission system and of the underlying DSOs systems. |  | GC0127 | PC,CC, ECC? | X |  |  |  |  | SDP (1) | Covered in section 1 System Defence Plan | [10 empty] | Not sure if we need to make reference to the DRSC here but these are purely commercial arrangements.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | 3. The system defence plan shall contain at least the following provisions: |  | GC0127 | [18 empty] | .
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (a) the conditions under which the system defence plan is activated, in accordance with Article 13; |  | GC0127 | OC7, OC9 | [5 empty] | SDP (2.1.1) | Covered in section 2.1.1 System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (b) the system defence plan instructions to be issued by the TSO; and |  | GC0127 | OC6,OC7 |  |  | DOC6 |  |  | SDP (2.1.2) | Covered in section 2.1.2 System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (c) the measures subject to real-time consultation or coordination with the identified parties. |  | GC0127 | BC3,CC, ECC, LFDD,OC6, OC7, OC9 | [5 empty] | SDP (2.1.3) | Covered in section 2.1.3 System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | 4. In particular, the system defence plan shall include the following elements: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (a) a list of the measures to be implemented by the TSO on its installations; |  | GC0127 |  | X | X |  |  |  | SDP (3.4.3, 3.4.4, 3.4.5, 3.4.6, 4.4.4, 4.4.6, 4.4.7, 4.5.4, 4.5.6, 4.8.2(b), 5) | Covered in sections 3.4.3, 3.4.4, 3.4.5, 3.4.6, 4.4.4, 4.4.6, 4.4.7, 4.5.4, 4.5.6, 4.8.2(b) and 5 of the System Defence Plan | [10 empty] | To be discussed
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (b) a list of the measures to be implemented by DSOs and of the DSOs responsible for implementing those measures on their installations; |  | GC0127 | OC6, OC9, BC2 |  |  | DOC9 |  |  | SDP (3.2.1, 3.2.2, 4.2.1, 4.3.1, 4.5.2, 4.5.3, 4.7.1, 4.8, 4.9.2) | Covered in sections 3.2.1, 3.2.2, 4.2.1, 4.3.1, 4.5.2, 4.5.3, 4.7.1, 4.8 and 4.9.2 of the System Defence Plan | [10 empty] | This may require more expansion
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (c) a list of the SGUs responsible for implementing on their installations the measures that result from the mandatory requirements set out in Regulation (EU) 2016/631, (EU) 2016/1388 and (EU) 2016/1447 or from national legislation and a list of the measures to be implemented by those SGUs; |  | GC0127 | [6 empty] | SDP (Appendix B) | Covered in sections Appendix B of the System Defence Plan | [10 empty] | The ECC's detail the obligations on SGU's as specified in RfG, HVDC and DCC. It is not clear if ERC requires a list of SGU's which would be more of a challenge.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (d) a list of high priority significant grid users and the terms and conditions for their disconnection, and |  | GC0127 | [6 empty] | SDP (Appendix C) | Covered in sections Appendix C of the System Defence Plan | [10 empty] | It is not clear if a list of SGU's are required. If so this could be a challenge
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (e) the implementation deadlines for each measure listed in the system defence plan. |  | GC0127 | [6 empty] | SDP (8) | Covered in section 8 of the System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | 5. The system defence plan shall include at least the following technical and organisational measures specified in Section 2 of Chapter II: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (a) system protection schemes including at least: |  | GC0127 | [18 empty] | The Grid Code details high level protection and control schemes (CC and ECC refers) but the details are captured in the Bilateral Agreement.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (i) automatic under-frequency control scheme in accordance with Article 15; |  | GC0127 | CC/ECC6.4.3, CC/ECC.A.5 and OC6.6 | [5 empty] | SDP (3.1, 3.2) | Covered in sections 3.1 and 3.2 of the System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (ii) automatic over-frequency control scheme in accordance with Article 16; and |  | GC0127 | ECC.6.3.7.1 and BC3 | [5 empty] | SDP (3.3) | Covered in section 3.3 of the System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (iii) automatic scheme against voltage collapse in accordance with Article 17. |  | GC0127 | [6 empty] | SDP (3.4) | Covered in section 3.4 of the System Defence Plan. LVDD is not mandated in GB although specific requirements on a case by case basis are defined in the Bilateral Agreement | [10 empty] | LVDC is not used in GB and has been switched off as part of DCC implementation. Looking at ERC this does not look as though it is a mandatory requirement.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (b) system defence plan procedures, including at least: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (i) frequency deviation management procedure in accordance with Article 18; |  | GC0127 | ECC.6.3.7, BC3 | SQSS |  |  |  | TSOG | BPs, SDP (4.1) | Covered in section 4.1 of the System Defence Plan and local Business Procedures
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (ii) voltage deviation management procedure in accordance with Article 19; |  | GC0127 | BC2 | SQSS |  |  |  |  | BPs, SDP (4.4) | Covered in section 4.4 of the System Defence Plan and local schemes covered in Business Procedures | [10 empty] | BC2 covers reactive instructions and the CC and ECC's detail the capability that User's (eg Generators, HVDC or Demand Customers) should have. The obligations on DSO's are more limited and hence this area may need some more work.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (iii) power flow management procedure in accordance with Article 20; |  | GC0127 | OC2,BC2,OC6 | SQSS |  |  |  | TSOG | SDP (4.5) | Covered in section 4.5 of the System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (iv) assistance for active power procedure in accordance with Article 21; and |  | GC0127 | BC2.9.6 |  |  |  |  | TSOG | SDP(4.6) and Interconnector Agreements | Between TSOs. Seek assistance from neighbouring TSOs ahead of demand reduction as defined in BC.2.9.6. Covered also in System Defence Plan 4.6
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (v) manual demand disconnection procedure in accordance with Article 22. |  | GC0127 | OC6 |  |  |  |  | TSOG | SDP (4.8) | Covered in section 4.6 of the System Defence Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | 6. The measures contained in the system defence plan shall comply with the following principles : |  | GC0127 | [7 empty] | Not specifically covered. It is assumed these general principles are covered in the Transmission License and Grid Code Objectives
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (a) their impact on the system users shall be minimal; |  | GC0127 | [7 empty] | Not specifically covered. It is assumed these general principles are covered in the Transmission License and Grid Code Objectives
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (b) they shall be economically efficient; |  | GC0127 | [7 empty] | Not specifically covered. It is assumed these general principles are covered in the Transmission License and Grid Code Objectives
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (c) only those measures that are necessary shall be activated; and |  | GC0127 | [7 empty] | Not specifically covered. It is assumed these general principles are covered in the Transmission License and Grid Code Objectives
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 11 Design of the system defence plan | (d) they shall not lead the TSO's transmission system or the interconnected transmission systems into emergency state or blackout state. |  | GC0127 | [7 empty] | Not specifically covered. It is assumed these general principles are covered in the Transmission License and Grid Code Objectives
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | 1. By [24 months after entry into force of Regulation] each TSO shall implement those measures of its system defence plan that are to be implemented on the transmission system. It shall maintain the implemented measures henceforth. |  | GC0127 | OC6, OC9 | [6 empty] | Possible amendment to Section 1 of the System Defence Plan. | Notification Process Ongong | [7 empty] | EIF+24months |  | This is again tricky. We have a defence plan and Black Start arrangements in place, however as to whether these arrangements exactly match the ERC is more questionable
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | 2. By [12 months after entry into force of Regulation] each TSO shall notify the transmission connected DSOs of the measures, including the deadlines for implementation, which are to be implemented on: |  | GC0127 | OC6, OC9 | [5 empty] | Amendmen to SDP? | Possible amendment to Section 1 of the System Defence Plan. | Notification Process Ongong | [7 empty] | EIF+12months |  | OC6 and OC9 detail these requirements but requires further thought
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (a) the DSO's installations pursuant to Article 11(4); or |  | GC0127 | [7 empty] | Requires further discussion - Notification could be included as a standard clause as part of the covering letter to future connectees. Writing to exisiting User's may be required but requires further discusison | Notification Process Ongong
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (b) the installations of SGU identified pursuant to Article 11(4) connected to their distribution systems; or |  | GC0127 | [7 empty] | Requires further discussion - Notification could be included as a standard clause as part of the covering letter to future connectees. Writing to exisiting User's may be required but requires further discusison | Notification Process Ongong
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (c) the installations of defence service providers connected to their distribution systems; or |  | GC0127 | [7 empty] | Requires further discussion - Notification could be included as a standard clause as part of the covering letter to future connectees / contract providers. Writing to exisiting User's / contract providers may be required but requires further discusison | Notification Process Onoing How do you identify who the defence service providers are? SDP abd SRP updated to include revised definitions. System Defence Plan and System Restoration Plan updated to define what an SGU is in GB and the definition of a System Defence Provider and System Restoration Provider
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (d) the installations of DSOs connected to their distribution systems. |  | GC0127 | [7 empty] | Requires further discussion - Notification could be included as a standard clause as part of the covering letter to future connectees. Writing to exisiting User's may be required but requires further discusison with the DNO's | Notificaiton Process ongoing Any IDNOs or Closed Distribution Systems connected to that DNO Notify 14 DNOs (1 letter) to capture a) to d) - Tony/Mark What is a Closed Distribution System Operator and where is the list set out - need to confirm with Ofgem? At the time of writing, a Closed Distribution System is treated as a Non-Embedded Customer. Dialogue needs to held with Ofgem to discuss this further, and as part of an informal discussion with Ofgem it has been proposed they attend key GC0127/GC0128 meetings so these points and others can be addressed
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | 3. By [12 months after entry into force of Regulation] each TSO shall notify the SGUs identified pursuant to point (c) of Article 11(4) or the defence service providers directly connected to its transmission system of the measures which are to be implemented on their installations, including the deadlines for the implementation. |  | GC0127 | [7 empty] | ESO Obligaiton - to be discussed - Check the mechanism for implementing | Notificaton Process Ongoing | [7 empty] | EIF+12months
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | 4. When provided for in national legislation, the TSO shall notify directly SGUs identified pursuant to point (c) of Article 11(4), defence service providers or DSOs connected to distribution systems of the measures which are to be implemented on their installations, including the deadlines for their implementation. It shall inform the concerned DSO of this notification. |  | GC0127 | X |  |  | X |  |  |  | ESO Obligaiton - to be discussed - Check the mechanism for implementing | Notification Process Ongoing Notification letter to be sent to SGUs How do you identify who the defence service providers and DSOs are? SGU's identifed as part of System Defence and System Restoration Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | 5. Where a TSO notifies a DSO in accordance with paragraph 2, the DSO shall notify in turn, without delay, the SGUs, the defence service providers and the DSOs connected to its distribution system of the measures of the system defence plan that they have to implement on their respective installations, including the deadlines for their implementation. |  | GC0127 | X |  |  | X |  |  |  | ESO Obligaiton - to be discussed - Check the mechanism for implementing | Notifcation Process Ongoing DSO will receive letter under 12(2) and they will notify the IDNOs, Closed Distribution Systems How do you identify who the defence service providers and DSOs are? SGU's have been clarified in System Defence and System Restoration Plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | 6. Each notified DSO, SGU and defence service provider shall: |  | GC0127 | X |  |  | X |  |  |  | DSO / SGU / Defence Service Provder obligation - Check the mechanism for implementing
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (a) implement the measures notified pursuant to this Article no later than 12 months from the date of notification; |  | GC0127 | X |  |  | X |  |  |  | DSO / SGU / Defence Service Provder obligation - Check the mechanism for implementing
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (b) confirm the implementation of the measures to the notifying system operator, who shall, when different from the TSO, notify the confirmation to the TSO; and |  | GC0127 | X |  |  | X |  |  |  | DSO / SGU / Defence Service Provder obligation - Check the mechanism for implementing
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 12 Implementation of the system defence plan | (c) maintain the measures implemented on its installations. |  | GC0127 | X |  |  | X |  |  |  | DSO / SGU / Defence Service Provder obligation - Check the mechanism for implementing
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 13 Activation of the system defence plan | 1. Each TSO shall activate the procedures of its system defence plan in coordination with DSOs and SGU identified pursuant to Article 11(4) and with defence service providers. |  | GC0127 | OC7, OC9 |  | STCP-06-1 |  |  |  | SDP (2.1) | Covered in Section 2.1 of the System Defence Plan | Tony/Mark consider updating System Defence Plan to reflect Article 18(2) of SOGL Completed see SDP section 2.1.1 How will the coordination work in practice? - This would be achieved through Operational Liaison under OC7, OC9 and the STC
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 13 Activation of the system defence plan | 2. In addition to the automatically activated schemes of the system defence plan, pursuant to point (a) of Article 11(5), each TSO shall activate a procedure of the system defence plan when: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 13 Activation of the system defence plan | (a) the system is in emergency state in accordance with the criteria set out in Article 18(3) of Regulation (EU) 2017/XXX [SO GLs] and there are no remedial actions available to restore the system to the normal state; or |  | GC0127 | OC9 |  |  |  | Section G3 | TSOG | SDP (2.1.1) | Covered in Section 2.1.1 of the System Defence Plan | [10 empty] | Is OC9 relevant here as this defines then the system is in an emergency condition
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 13 Activation of the system defence plan | (b) based on the operational security analysis, the operational security of the transmission system requires the activation of a measure of the system defence plan pursuant to Article 11(5) in addition to the available remedial actions. |  | GC0127 | OC7, OC9, BC2.9 | SQSS |  |  |  |  | BPs | Covered in Relevant Code and Business Procedures
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 13 Activation of the system defence plan | 3. Each DSO and SGU identified pursuant to Article 11(4), as well as each defence service provider shall execute without undue delay the system defence plan instructions issued by the TSO pursuant to point (c) of Article 11(3), in accordance with the system defence plan procedures provided for in point (b) of Article 11(5). |  | GC0127 | OC7, OC9, BC2.9 |  | STCP06-1 |  | Section G3 |  | SDP (2.1.3) | Covered in Section 2.1.3 of the System Defence Plan | How will the instructions work in practice for those not normally in receipt of these instructions? Resolved - The defintion of an SGU from the proposers perspective is any party who has a CUSC Contract or is a BM Participant
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 13 Activation of the system defence plan | 4. Each TSO shall activate procedures of its system defence plan referred to in point (b) of Article 11(5) having a significant cross-border impact in coordination with the impacted TSOs. |  | GC0127 | [6 empty] | SDP (2.1.4) and BPs | Covered in Section 2.1.4 of the System Defence Plan and Business Procedures | Paul C comment addressed | Maybe with interconnectors need to inform TSOs that you will be wanting as much power as possible? | [8 empty] | Is this relevant in GB as GB is on Synchronous Area
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | 1. Upon request from a TSO in emergency state, each TSO shall provide through interconnectors any possible assistance to the requesting TSO, provided this does not cause its transmission system or the interconnected transmission systems to enter into emergency or blackout state. |  | GC0127 | OC.9.4.7.4(b), BC2.6.4, BC.2.9.1.2€(i), BC.2.9.2.1, BC2.12.1, BC.3.7.3, BC3.7.7, BC2.9.2.1, BC2.9.6 |  |  |  |  | CACM? | SDP (2.1.2, 2.1.3) and Interconnector Agreements | Covered in Interconnector Agreements and Section 2.1.2 / 2.1.3 of the System Defence Plan | Paul C comment addressed | These references say this,"2.1.2 Procedures in this System Defence Plan will be activated by the NETSONGESO in coordination with DSOs, SGUs and Defence Service Providers. 2.1.3 All instructions issued by the NETSONGESO under this System Defence Plan must be executed by each DSO, SGU and Defence Service Provider without undue delay." Not sure interconnectors are covered by these definitions, and I don't think this is the intention of the E&R clause. IMO the clause is generally dealing with AC interconnected TSOs but in GB sense this would be we will be requesting all possible power through the interconnector from connected TSOs (i'm not sure how this works under interconnector contracts though)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | 2. When the assistance needs to be provided through direct current interconnectors, it may consist in carrying out the following actions, taking into account the technical characteristics and capability of HVDC system: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (a) manual regulation actions of the transmitted active power to help the TSO in emergency state to bring power flows within operational security limits or frequency of neighbouring synchronous area within system frequency limits for alert state defined pursuant to Article 18(2) of Regulation (EU) 2017/XXX [ SO GLs] ; |  | GC0127 | BC2.9.1.2, BC2.12.1(c ), BC.3.7.3(e )(f) and BC.3.7.7. |  |  |  |  | TSOG | BPs
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (b) automatic control functions of the transmitted active power based on the signals and criteria set out in Article 13 of Regulation 2016/1447; |  | GC0127 | ECC.6.3.7.1, BC3.7.2.2 |  |  |  |  | HVDC
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (c) automatic frequency control pursuant to Articles 15 to 18 of Regulation 2016/XXX [NC HVDC] in case of islanded operation; |  | GC0127 | ECC.6.3.7 / BC3.7.2.2 |  |  |  |  | HVDC | [12 empty] | The ECC contains the techncial requirements on HVDC Systems
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (d) voltage and reactive power control pursuant to Article 24 of Regulation 2016/XXX [NC HVDC], and |  | GC0127 | ECC.6.3.2.4, / ECC.6.3.8.4 |  |  |  |  | HVDC |  | Error in E&R Code. Art 24 should be Art 20 - 22
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (e) any other appropriate action. |  | GC0127 | BC2./ BC3
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | 3. Each TSO may proceed to a manual disconnection of any transmission system element having a significant cross-border impact, including an interconnector, subject to the following requirements: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (a) the TSO shall coordinate with neighbouring TSOs; and |  | GC0127 | OC7, OC9, BC2.9.6 |  | STC / STC Procedures |  |  |  | BPs Interconnector agreements
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | (b) this action shall not lead the remaining interconnected transmission system into emergency state or blackout state. |  | GC0127 | BC.2.9.6 | [5 empty] | BPs
CHAPTER II SYSTEM DEFENCE PLAN SECTION 1 GENERAL PROVISIONS | Article 14 Inter-TSO assistance and coordination in emergency state | 4. Notwithstanding paragraph 3, a TSO may manually disconnect any transmission system element having a significant cross-border impact, including an interconnector, without coordination, in exceptional circumstances implying a violation of the operational security limits, to prevent endangering personnel safety or damaging equipment. Within 30 days of the incident, the TSO shall prepare a report at least in English containing a detailed explanation of the rationale, implementation and impact of this action and submit it to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72 and neighbouring TSOs, and make it available to the significantly affected system users. |  | GC0127 | BC.2.9.1.2€(iii) |  |  |  |  | TSOG | SDP (4.8) and Interconnector protocols | New. Not currently allowed to disconnect interconnectors |  | Surely under the safe operation of the system they are allowed to do this This is disconnetion for saety reasons not for system reasons.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 1. The scheme for the automatic control of under-frequency of the system defence plan shall include a scheme for the automatic low frequency demand disconnection and the settings of the limited frequency sensitive mode–underfrequency in the TSO load frequency control (LFC) area. |  | GC0127 | CC/ECC.6.4.3, CC/ECC.A.5, OC6.6 and BC3 | [5 empty] | SDP (4.1.8) |  | Update as per GC0096 - Completed
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 2. In the design of its system defence plan, each TSO shall provide for the activation of the limited frequency sensitive mode–underfrequency prior to the activation of the scheme for the automatic low frequency demand disconnection, where the rate of change of frequency allows it. |  | GC0127 | ECC.6.3.7.2, BC3, OC6 | [5 empty] | SDP (3.1.6)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 3. Prior to the activation of the automatic low frequency demand disconnection scheme, each TSO and DSO identified pursuant to Article 11(4) shall foresee that energy storage units acting as load connected to its system: |  | GC0127 | OC.6.6.6 updated in line with GC0096 | [6 empty] | SDP(3.1.5) updated. | Section 3.1.5 of the System Defence Plan updated. Proposals of GC0096 adopted and inclued in legal text. The extracts copied from GC0096 are in highlighted blue text | Is this in GC0096?#
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (a) automatically switch to generation mode within the time limit and at an active power set-point established by the TSO in the system defence plan; or |  | GC0127 | OC.6.6.6 updated in line with GC0096 | [6 empty] | SDP(3.1.5) updated. | Section 3.1.5 of the System Defence Plan updated. Proposals of GC0096 adopted and inclued in legal text. The extracts copied from GC0096 are in highlighted blue text | Is this in GC0096?#
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (b) when the energy storage unit is not capable of switching within the time limit established by the TSO in the system defence plan, automatically disconnect the energy storage unit acting as load. |  | GC0127 | OC.6.6.6 updated in line with GC0096 | [6 empty] | SDP(3.1.5) updated. | Section 3.1.5 of the System Defence Plan updated. Proposals of GC0096 adopted and inclued in legal text. The extracts copied from GC0096 are in highlighted blue text | Is this in GC0096?#
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 4. Each TSO shall establish in its system defence plan the frequency thresholds at which the automatic switching or disconnection of energy storage units shall occur. These frequency thresholds shall be lower or equal to the system frequency limit defined for the emergency state in Article 18(3) of Regulation (EU) 2017/XXX [SO GLs] and higher than the frequency limit for demand disconnection starting mandatory level laid down in the Annex. |  | GC0127 | OC.6.6.6 updated in line with GC0096 |  |  |  |  | TSOG |  | SDP(3.1.5) updated. | Section 3.1.5 of the System Defence Plan updated. Proposals of GC0096 adopted and inclued in legal text. The extracts copied from GC0096 are in highlighted blue text | Is this in GC0096?#
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 5. Each TSO shall design the scheme for the automatic low frequency demand disconnection in accordance with the parameters for shedding load in real-time laid down in the Annex. The scheme shall include the disconnection of demand at different frequencies, from a 'starting mandatory level' to a 'final mandatory level', within an implementation range whilst respecting a minimum number and maximum size of steps. The implementation range shall define the maximum admissible deviation of netted demand to be disconnected from the target netted demand to be disconnected at a given frequency, calculated through a linear interpolation between starting and final mandatory levels. The implementation range shall not allow the disconnection of less netted demand than the amount of netted demand to be disconnected at the starting mandatory level. A step cannot be considered as such if no netted demand is disconnected when this step is reached. |  | GC0127 | CC/ECC.6.4.3, CC/ECC.A.5, OC6.6 | [5 empty] | SDP (3.2) |  | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 6. Each TSO or DSO shall install the relays necessary for low frequency demand disconnection taking into account at least load behaviour and dispersed generation. |  | GC0127 | CC/ECC.A.5 |  |  | X |  |  |  |  | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 7. When implementing the scheme for the automatic low frequency demand disconnection pursuant to the notification under Article 12(2), each TSO or DSO shall: |  | GC0127 | [6 empty] | SDP (3.2) |  | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (a) avoid setting an intentional time delay in addition to the operating time of the relays and circuit breakers; |  | GC0127 | CC/ECC.A.5.3.2 | [6 empty] | No time delay is set. Operation must commence within 200ms. | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (b) minimise the disconnection of power generating modules, especially those providing inertia; and |  | GC0127 | New Text Proposed - CC/ECC.A.5.3.1(c ) | [6 empty] | Grid Code text proposed to be updayed see CC/ECC.A.5.3.1(c ) | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (c) limit the risk that the scheme leads to power flow deviations and voltage deviations outside operational security limits. |  | GC0127 | CC/ECC.A.5.1.1 | X | [6 empty] | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | If a DSO cannot fulfil the requirements under points (b) and (c), it shall notify the TSO and propose which requirement shall apply. The TSO, in consultation with the DSO shall establish the applicable requirements based on a joint cost-benefit analysis. |  | GC0127 | OC6, OC9 |  |  | X |  |  |  |  | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 8. The scheme for the automatic low frequency demand disconnection of the system defence plan may provide for demand disconnection based on frequency gradient provided that: |  | GC0127 | OC.6.5.1 |  |  | X |  |  | SDC (4.8.3, 4.8.4, 4.8.5) | This is not a mandatory requirement so it is not clear that any form of code change is actually required. | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (a) it is activated only: |  | GC0127 | [7 empty] | This is not a mandatory requirement so it is not clear that any form of code change is actually required. | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (i) when the frequency deviation is higher than the maximum steady state frequency deviation and the frequency gradient is higher than the one produced by the reference incident; |  | GC0127 | CC/ECC.A.5 and OC6.5 | [6 empty] | This is not a mandatory requirement so it is not clear that any form of code change is actually required. | Phase 2 | [7 empty] | EIF+5years |  | The LFDD scheme only relies on frequency deviation not rate of change of frequency
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (ii). until the frequency reaches the frequency of the demand disconnection starting mandatory level; |  | GC0127 | CC/ECC.A.5 and OC6.5 | [6 empty] | This is not a mandatory requirement so it is not clear that any form of code change is actually required. | Phase 2 | [7 empty] | EIF+5years |  | The LFDD scheme is graded at set frequency operating limits, starting at 48.8Hz andf then in stages down to 47Hz. Details of the settings and substations are available in the System Reference document
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (b) it complies with the Annex; and |  | GC0127 | [7 empty] | Needs checking but believed to be consistent with values in Annex - will need to check System Reference Document | Phase 2 | [7 empty] | EIF+5years
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | (c) it is necessary and justified in order to maintain efficiently the operational security. |  | GC0127 | OC.6.5.1 | [6 empty] | Studies are undetaken to check suitability of LFDD Scheme but this would require checking | Phase 2 | [7 empty] | EIF+5years |  | The justificaiton is generally demonstrated as part of a Code change
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 9. In case the scheme for the automatic low frequency demand disconnection of the system defence plan includes netted demand disconnection based on frequency gradient, as described in paragraph 8, the TSO shall submit , within 30 days of the implementation, a report containing a detailed explanation of the rationale, implementation and impact of this measure to the national regulatory authority. |  | GC0127 | [7 empty] | Not applicable in GB | Phase 2
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 10. A TSO may include in the scheme for automatic low frequency demand disconnection of its system defence plan additional steps for netted demand disconnection below the final mandatory level of demand disconnection set out in the Annex. |  | GC0127 | OC6.5.3 | [5 empty] | SDP (4.8.3, 4.8.4 and 4.8.5)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 15 Automatic under-frequency control scheme | 11. Each TSO shall be entitled to implement additional system protection schemes that are triggered by a frequency smaller or equal to the frequency of the final mandatory level of demand disconnection and which aim at a faster restoration process. The TSO shall ensure that such additional schemes do not further deteriorate frequency. |  | GC0127 | [6 empty] | SDP (4.1.2, 4.1.3, 4.1.4, 4.1.7, 4.1.8, 4.1.9, 4.7.1) Commerical Contracts under Standard Contract Terms and Bilateral Agreements
GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 16 Automatic over-frequency control scheme | 1. The scheme for automatic over-frequency control of the system defence plan shall lead to an automatic decrease of the total active power injected in each LFC area. |  | GC0127 | ECC.6.3.7.1, BC.3.7.2 | [5 empty] | SDP (3.3.3)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 16 Automatic over-frequency control scheme | 2. In consultation with the other TSOs of its synchronous area, each TSO shall set out the following parameters of its scheme for automatic over-frequency control: |  | GC0127 | ECC.6.3.7.1, BC.3.7.2 | [5 empty] | SDP (3.3.3) |  |  | I take it you mean not applicable?
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 16 Automatic over-frequency control scheme | (a) the frequency thresholds for its activation; and |  | GC0127 | ECC.6.3.7.1, BC.3.7.2 | [5 empty] | SDP (3.3.3) |  |  | I take it you mean not applicable? | [7 empty] | set at 50.4Hz
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 16 Automatic over-frequency control scheme | (b) the reduction ratio of injection of active power. |  | GC0127 | ECC.6.3.7.1, BC.3.7.2 | [5 empty] | SDP (3.3.3) |  |  | I take it you mean not applicable? | [8 empty] | Not sure what this means. Under the Grid Code all plant has to automatically deload if the frequency exceeds 50.4Hz. Under LFDD 60% of demand in E&W will be shed and 40% in Scotland once the frequency falls to 47Hz.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 16 Automatic over-frequency control scheme | 3. Each TSO shall design its automatic over-frequency control scheme taking into account the capabilities of the power generating modules concerning the limited frequency sensitive mode – overfrequency and of the energy storage units, in its LFC area. If the limited frequency sensitive mode – overfrequency does not exist or is not sufficient to fulfil the requirements set out in points (a) and (b) of paragraph 2, each TSO shall set up in addition a step-wise linear disconnection of generation in its LFC area. The TSO shall establish the maximum size of the steps for disconnection of power generating modules and/or of HVDC systems in consultation with the other TSOs of its synchronous area. |  | GC0127 | ECC.6.3.7.1, BC3.7.2 | [5 empty] | SDP (3.3.3) | Under GC0096 (Storage), is treated as a subset of Generation and therefore would have to satisfy the requirements of ECC.6.3.7.1 (ie LFSM-O) | GC0096 Proposals have been included in the draft text - highlighted in blue | How do we adjust the grid code for E&R codew if GC0096 has yet to report back yet? | [8 empty] | The Grid Code provides for high frequency management through LFSM-O. Emergency Instructions can be applied if necessary
GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | 1. The automatic scheme against voltage collapse of the system defence plan may include one or more of the following schemes, depending on the results of a TSO's assessment of system security: |  | GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (a) a scheme for low voltage demand disconnection according to Article 19(2) of Regulation (EU) 2016/1388; |  | GC0127 | Not specified in GB | [6 empty] | LVDD is not mandated in GB. This is not a mandatory requirement under E&R Code.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (b) a blocking scheme for on load tap changer according to Article 19(3) of Regulation (EU) 2016/1388 ; and |  | GC0127 | Not specified in GB | [6 empty] | LVDD is not mandated in GB. This is not a mandatory requirement under E&R Code. | [10 empty] | Under DCC LVDD is not specified
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (c) system protection schemes for voltage management. |  | GC0127 | ECC.6.2.3.3 | [6 empty] | Specifed in Appendix F of Bilateral Conneciton Agreement is required.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | 2. Unless the assessment pursuant to paragraph 1 demonstrates that implementing a blocking scheme for on load tap changer is not necessary to prevent a voltage collapse in the TSO control area, the TSO shall establish the conditions under which the on load tap changer shall block according to Article19(3) of Regulation (EU) 2016/1388, including at least: |  | GC0127 | Not specified in GB | [6 empty] | LVDD is not mandated in GB. LVDD was investogated in 2001 but it was agreed that it was not apppropriate at that stage to take it forward.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (a) the blocking method (local or remote from control room); |  | GC0127 | Not specified in GB
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (b) the voltage level threshold at the connection point; |  | GC0127 | Not specified in GB
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (c) the flow direction of reactive power; and |  | GC0127 | Not specified in GB
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 17 Automatic scheme against voltage collapse | (d) the maximum lapse of time between the detection of the threshold and the blocking. |  | GC0127 | Not specified in GB
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | 1. The procedure for the management of frequency deviations of the system defence plan shall contain a set of measures to manage a frequency deviation outside the frequency limits defined for the alert state in Article 18(2) of Regulation (EU) 2017/XXX [SO GLs]. The frequency deviation management procedure shall be in line with the procedures set out for remedial actions which need to be managed in a coordinated way in accordance with Article 78(4) of Regulation (EU) 2017/XXX [SO GLs] and shall fulfil at least the following requirements: |  | GC0127 |  | X |  |  |  | TSOG | SDP (4.1)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | (a) a decrease of generation shall be smaller than the decrease of load during under-frequency events; and |  | GC0127 | BC3, CC/ECC6.3.3, CC/ECC.6.3.7
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | (b) a decrease of generation shall be greater than the decrease of load during over-frequency events. |  | GC0127 | BC3.7.2, ECC.6.3.7.1
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | 2. Each TSO shall adapt the operating mode of its LFC in order to prevent interference with manual activation or deactivation of active power as laid down in paragraphs 3 and 5. |  | GC0127 | BC3 | X
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | 3. Each TSO shall be entitled to establish an active power set-point that each SGU identified pursuant to point (c) of Article 11(4) shall maintain, provided that the set-point fulfils the technical constraints of the SGU. Each TSO shall be entitled to establish an active power set-point that each defence service provider shall maintain provided this measure applies to them pursuant to the terms and conditions referred to in Article 4(4) and the set-point respects the technical constraints of the defence service provider. The SGUs and defence service providers shall execute without undue delay the instructions given by the TSO directly or indirectly through DSOs and shall remain in that state until further instructions are issued. Where the instructions are given directly, the TSO shall inform the relevant DSOs without undue delay. |  | GC0127 | CC.6.3.7(a), ECC.6.3.6.1.1, ECC.6.3.6.1.2, CC/ECC.6.3.9, DRSC 5.1, DRSC 6.1, DRSC 7.1, BC.1.4.2, BC1.A.1.1, BC.2.6.1 | [5 empty] | Commercial Contracts under the Standard Contract Terms | [11 empty] | Generators in the BM must be capable of operating to their defined setpoint
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | 4. Each TSO shall be entitled to disconnect SGUs and defence service providers, directly or indirectly through DSOs. SGUs and defence service providers shall remain disconnected until further instructions are issued. Where SGUs are directly disconnected, the TSO shall inform the relevant DSOs without undue delay. Within 30 days of the incident, the TSO shall prepare a report containing a detailed explanation of the rationale, implementation and impact of this action and submit it to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72 as well as make it available to the significantly affected system users. |  | GC0127 | BC2.9.1.2, BC2.9.2.2, OC7.4.5, OC.6.7, OC.10 | [6 empty] | If a Party is not an SGU it cannot be disconnected. This is now clarified as to what is an SGU in Appendix A and B of the SDP | How are we going to discharge this for DSOs (directly or indirectly) and Defence Service Providers? - As part of the Proposers Solution we are very clear what an SGU is a party with a CUSC Contract or BM Party which would have to comply with the appropriate requirements of the Grid Code and hence instructable. If they are not defined as an SGU then this requirement would not apply.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | 5. Prior to the activation of the automatic low frequency demand disconnection scheme set out in Article 15 and provided that the rate of change of frequency allows it, each TSO shall, directly or indirectly through DSOs, activate demand response from the relevant defence service providers and: |  | GC0127 | OC6.5, BC2.9 | [5 empty] | Commerical Contracts under the Standard Contract Terms
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | (a) switch energy storage units acting as load to generation mode at an active power set-point established by the TSO in the system defence plan; or |  | GC0127 | As per GC0096 | [6 empty] | As per GC0096 | [10 empty] | Point for discussion - it is assumed all mechanisms available will be applied prior to declaring an emergency condition
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 18 Frequency deviation management procedure | (b) when the energy storage unit is not capable of switching fast enough to stabilize frequency, manually disconnect the energy storage unit. |  | GC0127 | As per GC0096 | [6 empty] | As per GC0096
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 19 Voltage deviation management procedure | 1. The procedure for the management of voltage deviations of the system defence plan shall contain a set of measures to manage voltage deviations outside the operational security limits set out in Article 25 of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0127 | BC2 | SQSS Section 6 |  |  |  | TSOG | Commercial Contracts Business Procedures
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 19 Voltage deviation management procedure | 2. Each TSO shall be entitled to establish a reactive power range or voltage range and instruct the DSOs and SGUs identified for this measure pursuant to Article 11(4) to maintain it, in accordance with Articles 28 and 29 of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0127 | CC/ECC.6.1.4 CC/ECC.6.3.2 ECC.6.4.5 CC/ECC.6.3.8, BC2.8, BC2.A.2, DRSC.5, DRSC.6, DRSC.7
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 19 Voltage deviation management procedure | 3. Upon request of neighbouring TSO in emergency state, each TSO shall make available all reactive power capabilities that do not lead its transmission system into emergency state or blackout state. |  | GC0127 | [6 empty] | Interconnectos Agreements? | Not relevant in GB as there are no HVAC interconnectors |  | Unless we have HVAC connections to other EU coutnries this does not apply as HVDC systems will be instructed in the TSO area and should have little to no affect on GB system. Anglo-Scottish interconnectors shouldn't be covered under this as Scottish Tos can't declare an emergency state independtly of NGESO?
GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 20 Power flow management procedure | 1. The procedure for power flow management of the system defence plan shall include a set of measures to manage power flow outside the operational security limits set out in Article 25 of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0127 | ECC.6.3.6.1.2.3 | X |  |  |  | TSOG | SDP (4.5) | Error in E&R Code. Art 25 should be Art13?
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 20 Power flow management procedure | 2. Each TSO shall be entitled to establish an active power set-point that each SGU identified pursuant to point (c) Article 11(4) shall maintain provided that the set-point respects the technical constraints of the SGU. Each TSO shall be entitled to establish an active power set-point that each defence service provider shall maintain provided this measure applies to them pursuant to the terms and conditions referred to in Article 4(4) and the set-point respects the technical constraints of the defence service providers. The SGUs and defence service providers shall execute without undue delay the instructions given by the TSO directly or indirectly through DSOs and shall remain in that state until further instructions are issued. Where the instructions are given directly, the TSO shall inform the relevant DSOs without undue delay. |  | GC0127 | CC.6.3.7(a), ECC.6.3.6.1.1, ECC.6.3.6.1.2, CC/ECC.6.3.9, DRSC 5.1, DRSC 6.1, DRSC 7.1, BC.1.4.2, BC1.A.1.1, BC.2.6.1 | [5 empty] | Commercial Contracts under the Standard Contract Terms | [11 empty] | Point for discussion
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 20 Power flow management procedure | 3. Each TSO shall be entitled to disconnect SGUs and defence service providers, directly or indirectly through DSOs. SGUs and defence service providers shall remain disconnected until further instructions are issued. Where SGU are directly disconnected, the TSO shall inform the relevant DSOs without undue delay. Within 30 days of the incident, the TSO shall prepare a report containing a detailed explanation of the rationale, implementation and impact of this action and submit it to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72. |  | GC0127 | BC2.9.1.2, BC2.9.2.2, OC7.4.5, OC.6.7, OC.10 | [6 empty] | SGU List is now defined in Appenidx A and B of SDP and SRP and hence this is no longer an issue as they can be instructed off under and emergecny instruciton |  | Criteria to be on list has been defined, not a 'list'
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | 1. In case of absence of control area adequacy in the day-ahead or intraday timeframe, identified pursuant to paragraphs 1 and 2 of Article 107 of Regulation (EU) 2017/XXX [SO GLs], and prior to any potential suspension of market activities pursuant to Article 35, a TSO shall be entitled to request assistance for active power from: |  | GC0127 | [5 empty] | TSOG | SDP (4.6) and Interconnector Agreements | Between TSOs. Seek assitance from neighbouring TSOs ahead of demand reduction
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (a) any balancing service provider, which, upon the TSO request, shall change its availability status to make available all its active power, provided it was not already activated through the balancing market, and conforming to its technical constraints; |  | GC0127 | BC2.9.1.2(e)(ii), BC2.9.4, BC2.9.5 | [5 empty] | SDP (4.6.3, 4.7)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (b) any SGU connected in its LFC area, which does not already provide a balancing service to the TSO, and which, upon the TSO request, shall make available all its active power, conforming to its technical constraints; and |  | GC0127 | OC9.4.7.5, OC9.4.7.8, OC9.5.1 |  |  | X |  |  |  | Addressed now SGU definition has been clarified
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (c) other TSOs that are in the normal or alert state. |  | GC0127 | BC.2.9.6 |  | STCP 06-1
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | 2. A TSO may activate the assistance for active power from a balancing service provider or a SGU, under points (a) and (b) of paragraph 1, only if it has activated all balancing energy bids available, taking into account the available cross zonal capacity at the moment of absence of adequacy of the control area. |  | GC0127 | BC2.9.1
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | 3. Each TSO who has been subject to a request for assistance for active power pursuant to paragraph 1(c) shall: |  | GC0127 | BC2.9.6
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (a) make available its unshared bids; |  | GC0127 | OC7.4.8, OC7.4.8.5, BC.2.9.6 | [6 empty] | Internal Procedure | Tony - double check BC2 - OC7.4.8 details the process during System Warnings which includes notifying Users of System Events including Generation Shortages. The warning notification process makes BM parties aware of shortages in an attempt to make more Generation available which is managed through OC7.4.8. Emergency Instructions can be issued including Max Gen instructions (BC2.9.1 refers). BC2.9.6 applies to Interconnectors | To do across interconnectors with EU IMO affects on CUSC ?
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (b) be entitled to activate the available balancing energy, in order to provide the corresponding power to the requesting TSO; and |  | GC0127 | BC.2.9.6 |  | STCP 06-1 | [6 empty] | To do across interconnectors with EU IMO | [8 empty] | Is this relevant in GB bearing in mind there is only one TO
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (c) be entitled to request the assistance for active power from its balancing service providers and from any SGU connected in its LFC area which does not already provide a balancing service to the TSO, in order to provide the corresponding assistance for active power to the requesting TSO. |  | GC0127 | BC.2.9.6 | [8 empty] | To do across interconnectors with EU IMO
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | 4. When activating the active power requested pursuant to paragraph 1(c), the requesting and the requested TSOs shall be entitled to use: |  | GC0127 | BC.2.9.6 | [5 empty] | Interconnector operating protocols | Between TSOs. Cross border arrangements. Interconnector operating protocols.
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (a) available cross-zonal capacity in case the activation is made before the intraday cross-zonal gate closure time and if the provision of concerned cross-zonal capacities has not been suspended pursuant to Article 35; |  | GC0127 | BC2.9.2.1, BC.2.9.6 | [6 empty] | BC2.9 provides for Emergency Instructions. Emergency Instructions may only be rejected on safety grounds (relating to plant or personnel). In GB the terminology is slightly different to that used in Europe but it is believed these provisons reflect the E&R Requirements?
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | (b) additional capacity that may be available due to real-time status of the system in which case the requesting and the requested TSOs shall coordinate with other significantly affected TSOs in accordance with Article 6(5). |  | GC0127 | BC.2.9.2.1, BC.2.9.6 | [6 empty] | BC2.9 provides for Emergency Instructions. Emergency Instructions may only be rejected on safety grounds (relating to plant or personnel). In GB the terminology is slightly different to that used in Europe but it is believed these provisons reflect the E&R Requirements?
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 21 Assistance for active power procedure | 5. Once the requested and requesting TSOs have agreed on the conditions for the provision of assistance for active power, the agreed amount of active power and timeslot for the provision shall be firm, unless the transmission system of the TSO providing the assistance enters into the emergency or blackout state. |  | GC0127 | BC.2.9.2.1, BC.2.9.6 | [6 empty] | BC2.9 provides for Emergency Instructions. Emergency Instructions may only be rejected on safety grounds (relating to plant or personnel). In GB the terminology is slightly different to that used in Europe but it is believed these provisons reflect the E&R Requirements?
GC0127
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 22 Manual demand disconnection procedure | 1. In addition to the measures set out in Articles 18 to 21, each TSO may establish an amount of netted demand to be manually disconnected, directly by the TSO or indirectly through DSOs, when necessary to prevent the propagation or worsening of an emergency state. Where demand is to be directly disconnected, the TSO shall inform the relevant DSOs without delay. |  | GC0127 | OC6.5 |  |  | ? |  | TSOG | SDC (4.8) | [9 empty] | System defence plan
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 22 Manual demand disconnection procedure | 2. The TSO shall activate the manual disconnection of the netted demand referred to in paragraph 1 to: |  | GC0127 | [18 empty] | Low frequency demand disconneciton is automatic
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 22 Manual demand disconnection procedure | (a) resolve overloads or under voltage situations; or |  | GC0127 | BC2, OC7 | X |  |  |  |  | SDC (4.8)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 22 Manual demand disconnection procedure | (b) resolve situations in which assistance for active power pursuant to Article 21 has been requested but is not sufficient to maintain adequacy in day-ahead and intraday timeframes in its control area, pursuant to Article 107 of Regulation (EU) 2017/XXX [SO GLs], leading to a risk of frequency deterioration in the synchronous area. |  | GC0127 | OC6, OC7, BC1
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 22 Manual demand disconnection procedure | 3. The TSO shall notify DSOs of the amount of netted demand established pursuant to paragraph 1 to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of netted demand, without undue delay. |  | GC0127 | OC6.5 | [5 empty] | SDC (4.8.3)
CHAPTER II SYSTEM DEFENCE PLAN SECTION 2 MEASURES OF THE SYSTEM DEFENCE PLAN | Article 22 Manual demand disconnection procedure | 4. Within 30 days of the incident, the TSO shall prepare a report containing a detailed explanation of the rationale, implementation and impact of this action and submit it to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72. |  | GC0127 | OC7.4.6, OC10 | [6 empty] | Covered under ESO Business Procedures | Mark/Tony - Confirm current reporting process
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | 1. By [12 months after the entry into force of this Regulation], each TSO shall design a restoration plan in consultation with relevant DSOs, SGUs, national regulatory authorities or entities referred to in Article 4(3), neighbouring TSOs and the other TSOs in that synchronous area. |  | GC0128 | [6 empty] | System Restoration Plan (SRP) | Specified in System Restoration Plan (SRP) | [8 empty] | EIF+12months
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | 2. When designing its restoration plan, each TSO shall take into account, at least, the following elements: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (a) the behaviour and capabilities of load and generation; |  | GC0128 | [6 empty] | SRP (1) | Covered in section 1 of System Restoration Plan
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (b) the specific needs of the high priority significant grid users listed pursuant to paragraph (4); and |  | GC0128 | [5 empty] | TSOG? | SRP (1) | Covered in section 1 of System Restoration Plan | Will be added to Appendix C - action was taken 2 July 2019 This will be black start providers and generators >=100MW Ofgem have advised that ESEC sites do not need to be included as they are already under National Legislation Action: How are ESO going to take on the needs of specific parties - Mark? The needs of specific parties will be addressed through Black Start Contracts and the provisons under the OC9
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (c) the characteristics of its network and of the underlying DSOs networks. |  | GC0128 | OC9.4.7.2 OC9.4.7.9 | [5 empty] | SRP (1) | Covered in section 1 of System Restoration Plan | How are we taking account of these characteristics in designing our restoration plan. Our intention is to take this forward to the industry but it ouside the scope of GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | 3. The restoration plan shall contain at least the following provisions: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (a) the conditions under which the restoration plan is activated, as provided for in Article 25; |  | GC0128 | [6 empty] | SRP (2.1) | Covered in Section 2.1 of the System Restoration Plan
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (b) restoration plan instructions to be issued by the TSO; and |  | GC0128 | OC9 | [5 empty] | SRP (2.1.2, 2.1.3, 3) | Covered in Section 2.1.2, 2.1.3 and 3 of the System Restoration Plan | Where are these set out? These are set out in the System Restoration Plan, Grid Code / STC and Internal Procedures
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (c) measures subject to real-time consultation or coordination with identified parties. |  | GC0128 | [6 empty] | SRP (2, 3.1.2) | Covered in Section 2 and 3.1.2 of the System Restoration Plan
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | 4. In particular, the restoration plan shall include the following elements: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (a) a list of the measures to be implemented by the TSO on its installations; |  | GC0128 | [6 empty] | SRP (2) | Covered in section 2 of the System Restoration Plan
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (b) a list of the measures to be implemented by DSOs and of the DSOs responsible for implementing those measures on their installations; |  | GC0128 |  |  |  | DOC9 |  |  | SRP (2, 2.1 and 3.2.9) | Covered in section 2, 2.1 and 3.2.9 of the System Restoration Plan
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (c) a list of the SGUs responsible for implementing on their installations the measures that result from mandatory requirements set out in Regulations (EU) 2016/631, (EU) 2016/1388 and (EU) 2016/1447 or from national legislation and a list of the measures to be implemented by those SGUs; |  | GC0128 | [5 empty] | RfG DCC HVDC | SRP (Appendix B) | Covered in Appendix B of the System Restoration Plan | [10 empty] | This needs further consideration. If a list of SGU's are required this could be quite a challenge
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (d) the list of high priority significant grid users and the terms and conditions for their disconnection and re-energisation; |  | GC0128 | [6 empty] | SRP (Appendix C) | This is covered in Appendix C of the System Restoration Plan. The SGU Criteria has now been clarified | Will be added to Appendix C - action was taken 2 July 2019 This will be black start service providers and generators >=100MW - Addressed through updates to Appendix C of the System Restoration Plan ESEC sites are high priority significant grid users - On advice from Ofgem this has been removed as it is covered under National Legislation Terms and Conditions will be consulted on - different for SGUs and high priority significant grid users Action: How are ESO going to take on the needs of specific parties - This will be addressed in the longer term with the industry. Anything over and above the current arrangements are outside the scope of GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (e) a list of substations which are essential for its restoration plan procedures; |  | GC0128 | [6 empty] | SRP (Appendix E) | Covered in Appendix E of the System Restoration Plan.
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (f) the number of power sources in the TSO's control area necessary to re-energize its system with bottom-up re-energisation strategy having black start capability, quick re-synchronisation capability (through houseload operation) and island operation capability; and |  | GC0128 | OC9 | [5 empty] | SRP (Appendix D) | Covered in Appendix D of the System Restoration Plan | Mark - consider changing the title of Appendix D to state "Black Start Restoration Providers" - Appendix D of SRP Updated
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (g) the implementation deadlines for each listed measure. |  | GC0128 | [6 empty] | SRP (5) | Covered in System Restoration Plan Section 5
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | 5. The restoration plan shall include at least the following technical and organisational measures specified in Chapter III: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (a) re-energisation procedure, in accordance with Section 2; |  | GC0128 | [6 empty] | SRP (3.1) | Covered in System Restoration Plan Section 3.1
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (b) frequency management procedure, in accordance with Section 3; and |  | GC0128 | [6 empty] | SRP (3.3) | Covered in System Restoration Plan Section 3.1
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (c) resynchronisation procedure, in accordance with Section 4. |  | GC0128 | [6 empty] | SRP (3.2) | Covered in System Restoration Plan Section 3.2
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | 6. The measures contained in the restoration plan shall comply with the following principles : |  | GC0128 | [6 empty] | ESO Licence Special Condition 4G
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (a) their impact on system users shall be minimal; |  | GC0128 | [6 empty] | ESO Licence Special Condition 4G
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (b) they shall be economically efficient; |  | GC0128 | [6 empty] | ESO Licence Special Condition 4G
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (c) only those measures that are necessary shall be activated; and |  | GC0128 | [6 empty] | ESO Licence Special Condition 4G
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 23 Design of the restoration plan | (d) they shall not lead the interconnected transmission systems into emergency state or blackout state. |  | GC0128 | BC2.9.6(b) | [5 empty] | ESO Licence Special Condition 4G
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | 1. By [24 months after entry into force of Regulation] each TSO shall implement those measures of its restoration plan that are to be implemented on the transmission system. It shall maintain the implemented measures henceforth. |  | GC0128 | [6 empty] | SRP (5) | Covered in Section 5 of the System Restoration Plan (SRP) | [8 empty] | EIF+24months
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | 2. By [12 months after entry into force of Regulation] each TSO shall notify the transmission connected DSOs of the measures, including the deadlines for implementation, which are to be implemented on: |  | GC0128 | [6 empty] | SRP (5.1) | Covered in Section 5.1 of the System Restoration Plan (SRP) | [8 empty] | Eif+12months
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (a) the DSO's installations pursuant to Article 23(4); and |  | GC0128 | [8 empty] | Notification Process Ongoing
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (b) the installations of SGU identified pursuant to Article 23(4) and connected to their distribution systems; and |  | GC0128 | [8 empty] | Notification Process Ongoing
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (c) the installations of restoration service providers connected to their distribution systems; and |  | GC0128 | [8 empty] | Notification Process Ongoing
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (d) the installations of DSOs connected to their distribution systems. |  | GC0128 | [8 empty] | Notification Process Ongoing
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | 3. By [12 months after entry into force of Regulation] each TSO shall notify the SGUs identified pursuant to Article 23(4) and restoration service providers directly connected to its transmission system of the measures that are to be implemented on their installations, including the deadlines for implementation pursuant to point (g) of Article 23(4). |  | GC0128 | [8 empty] | Notification Process Ongoing | [7 empty] | EIF+12months
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | 4. When provided for in national legislation, the TSO shall notify directly the SGUs identified pursuant to Article 23(4) and restoration service providers and DSOs connected to distribution systems and shall inform the concerned DSO of this notification. |  | GC0128 | [8 empty] | Notification Process Ongoing
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | 5. Where a TSO notifies a DSO in accordance with paragraph 2, the DSO shall notify in turn, without delay, the SGUs, restoration service providers and DSOs connected to its distribution system of the measures of the restoration plan which they have to implement on their respective installations, including the deadlines for implementation, pursuant to point (g) of Article 23(4). |  | GC0128 | [8 empty] | Notification Process Ongoing
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | 6. Each notified DSO, SGU and restoration service provider shall: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (a) implement the measures notified no later than 12 months from the date of notification; |  | GC0128 | [16 empty] | notification +12months(24) |  | Is this covered under LJRP
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (b) confirm the implementation of the measures to the notifying system operator, who shall, when different from the TSO, notify the TSO; and |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 24 Implementation of the restoration plan | (c) maintain the measures implemented on its installations. |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | 1. Each TSO shall activate the procedures of its restoration plan in coordination with the DSOs and SGUs identified pursuant to Article 23(4) and with restoration service providers in the following cases : | Ofgem discussion? | GC0128 | OC 9 |  | STCP 06-1 |  |  |  | SRP (2.1) | Covered in section 2.1 of the System Restoration Plan | How will the coordination work in practice? - Covered under OC9
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | (a) when the system is in the emergency state in accordance with the criteria in Article 18(3) of Regulation (EU) 2017/XXX [SO GLs], once the system is stabilised following activation of the measures of the system defence plan; or |  | GC0128 | OC9 |  | STCP 06-1 |  |  | TSOG | SRP (2.1.1)
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | (b) when the system is in the blackout state in accordance with the criteria in Article 18(4) of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0128 | OC9 |  | STCP 06-1 |  |  | TSOG | SRP (2.1.1)
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | 2. During system restoration, each TSO shall identify and monitor: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | (a) the extent and borders of the synchronised region or synchronised regions to which its control area belongs; |  | GC0128 |  |  | STCP 06-1 |  |  |  | SRP
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | (b) the TSOs with which it shares a synchronised region or synchronised regions; and |  | GC0128 | [7 empty] | Not applicable in GB
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | (c) the available active power reserves in its control area. |  | GC0128 | OC.9.4.7.2, BC3
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | 3. Each DSO and SGU identified pursuant to Article 23(4), as well as each restoration service provider shall execute without undue delay the restoration plan instructions issued by the TSO, pursuant to point (b) of Article 23(3) in accordance with the restoration plan procedures. |  | GC0128 | OC9, BC2.9.2.1 | [5 empty] | SRP (2.1.3) |  | Procedure for issuing instructions and acting on such instructions - Covered under OC9 and BC2.9?
CHAPTER III RESTORATION PLAN SECTION 1 GENERAL PROVISIONS | Article 25 Activation of the restoration plan | 4. Each TSO shall activate those procedures of its restoration plan that have a significant cross-border impact in coordination with the impacted TSOs. |  | GC0128 | BC.2.9.6 / General Grid Code Practice
GC0128
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | 1. The re-energisation procedure of the restoration plan shall contain a set of measures allowing the TSO to apply: |  | GC0128 | OC9.2.5, OC.9.3.2, OC9.4.7.2, OC.9.4.7.3 |  | NA |  |  |  | SRP (3)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | (a) a top-down re-energisation strategy; and |  | GC0128 |  |  | Not relevent to TOs | [5 empty] | Believe in GB not appropriate to have a top down - Mark/Tony to discuss Top down and bottom up re-energisation is part of the overall Black Start strategy | [10 empty] | Implementation of E&R Code Article 26 in to STCP 6-3 section 3.4 to include strategy for TSO to TSO, top down energisation | Additional section to be added explaining the process for using a HVDC Interconnection to a neighbouring TSO region to contribute to GB restoration, i.e. a Top Down re-energisation and Synchronisation Strategy. This will cover all GB DSO's. Explore the need to include and document procedures to utilise these systems to aid restoration of a neighbouring TSO.
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | (b) a bottom-up re-energisation strategy. |  | GC0128 | OC9.2.5, OC9.4 |  | SCTP 6-1 Section 3.4 |  |  |  | SRP (3.3, 3.1.6, 3.2.7)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | 2. Regarding the bottom-up re-energisation strategy, the re-energisation procedure shall contain at least measures for: |  | GC0128 | OC9.4 |  | STCP 6-1 Section 3.4
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | (a) managing voltage and frequency deviations due to re-energisation; |  | GC0128 | OC.9.4.3, OC.9.4.7.6€, OC9.5.6, |  | STCP 6-1 Section 3.4.5, 3.4.6 | [17 empty] | ***Note*** we have stated the limits, but unclear on what the measures for Voltage and Frequency are documented as?
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | (b) monitoring and managing island operation; and |  | GC0128 | OC.9.4.3, OC9.4.7.6(e), OC9.5.6, OC9.1.2, OC9.2.5, OC9.4.7.2, OC9.5 |  | STCP 6-1 Section 3.4.5 |  |  |  | SRP (3.1.6, 3.1.8, 3.3)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 26 Re-energisation procedure | (c) resynchronising island operation areas. |  | GC0128 | OC9.4.7.7, OC9.4.7.8, OC9.5 |  | SCTP 6-1 Section 3.4.11 |  |  |  | SRP (3.1, 3.2)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | 1. When activating the re-energisation procedure, each TSO shall set up the strategy to be applied, taking into account: |  | GC0128 | OC9 |  | STCP 6-3 Section 3.1.8
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | (a) the availability of power sources capable of re-energisation in its control area; |  | GC0128 | CC/ECC.6.3.5, OC.9.4.5, OC9.4.7.12 |  | STCP 6-3 Section 3.1.8 and 3.4.3.1 |  |  |  | SRP (1, 3.1.3)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | (b) the expected duration of possible re-energisation strategies; |  | GC0128 | OC9.2.5, OC9.4.7.2, OC.9.2.1, OC9.4.4 |  | STCP 3.1 |  |  |  | SRP (2.4) | [10 empty] | Implementation of E&R Code Article 27 1b | Update OC 9.4.4 | Implementation of E&R Code Article 27 1b | Add extra words in SCTP 6-1 Section 3.1 to introduce responsibility of TOs to provide information to contribute to duration and risk analysis during a restoration.
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | (c) the conditions of the power systems; |  | GC0128 | OC9.2.1, OC9.2.5, OC9.4, OC9.4.7.6, OC9.6.10, OC9.6.11 |  | STCP 6-3 Section 3.1.8 |  |  |  | SRP (2, 3.1.4)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | (d) the conditions of the directly connected systems, including at least the status of interconnectors; |  | GC0128 | OC.9.2.5, OC9.4.7.2, OC9.4.7.6, BC2.9.6 |  | SCTP 6-1 3.1.8 |  |  |  | SRP (2)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | (e) the high priority significant grid users listed pursuant to Article 23(4); and |  | GC0128 | OC.9.3 | [5 empty] | SRP (Appendix B and Appendix C) |  | Add to Appendix C - SRP Plan Updated
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | (f) the possibility to combine top-down and bottom-up re-energisation strategies. |  | GC0128 | OC9.3.2, OC9.4, OC9.4.7.2 | [5 empty] | SRP(3, 3.2) plus Interconnector Agreements |  | Believe in GB not appropriate to have a top down - Mark/Tony to discuss Top down and bottom up re-energisation is part of the overall Black Start strategy
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | 2. When applying a top-down re-energisation strategy, each TSO shall manage the connection of load and generation with the aim to regulate the frequency towards the nominal frequency with a maximum tolerance of the maximum steady-state frequency deviation. Each TSO shall apply the conditions for connection of load and generation defined by the frequency leader, where appointed in accordance with Article 29. |  | GC0128 | OC9.4, OC9.4.3, OC9.4.7.6(e), OC9.4.7.6(f), OC9.5.2.2, OC9.5.6 |  | STCP 6-1 3.4.3.5 |  |  |  | SRP (3.2.1, 3.3.1, 3.3.3) | top-down - neighbouring TSOs | Believe in GB not appropriate to have a top down - Mark/Tony to discuss Top down and bottom up re-energisation is part of the overall Black Start strategy | [8 empty] | Implementation of E&R Code Article 27 to clarify obligations ammended to OC9.4.7.6f to manage frequency within the maximum steady state limits. | Wording to be added regarding the appointement of frequency lead by ESO. | Implementation of E&R Code Article 27 to clarify obligations ammended to OC9.4.7.6f to manage frequency within the maximum steady state limits. | Wording to be added regarding the appointement of frequency lead by ESO.
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | 3. When applying a bottom-up re-energisation strategy, each TSO shall manage the connection of load and generation with the aim to regulate the frequency towards the target frequency established in accordance with point (c) of Article 28(3). |  | GC0128 | OC9.4.7.6 (e), OC9.5.2.1, OC9.5.2.2(a) |  | STCP 6-1 3.4.5 |  |  |  | SRP (2, 3.1.4, 3.1.6, 3.3, 3.3.3) | [10 empty] | OC9.4 (especially 9.4.7.6e) | Change Genset to Type c and d power generating module
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | 4. During re-energisation, the TSO shall, after consultation with DSOs, establish and notify the amount of netted demand to be reconnected on distribution networks. Each DSO shall reconnect the notified amount of netted demand, while respecting the block loading and taking into account the automatic re-connection of load and generation in its network. |  | GC0128 | OC9.4.7.5, OC9.4.7.6(e), OC9.4.7.8, OC9.5.2.1, OC9.5.2.2, OC9.5.3, OC9.5.6 |  | STCP 6-1 Section 3.4.11 | DOC 9 |  |  | SRP (3.1.1, 3.2.2, 3.3.3, 4.2) | [11 empty] | Insert words OC9.4.7.5? | Implementation of E&R Code Article 27 (4) to clarify obligation under STCP 6-1 3.4.11 for the ESO to establish and notify the amount of netted demand to be reconnected on distribution networks. | Additional paragraph in STCP 3.4.11, reflecting Article 27 paragraph 4, or an additional section covering the management of the Skeleton Network.
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | 5. Each TSO shall inform its neighbouring TSOs on its capability to support a top-down re-energisation strategy. |  | GC0128 | OC9.3.2, OC9.4.7.2, BC2.9.6 |  | STCP 06-1 (3.2.1, 3.2.1.4, 3.4.3.7) |  |  |  | SRP (3, 3.1, 3.3) |  | Believe in GB not appropriate to have a top down - Mark/Tony to discuss Top down and bottom up re-energisation is part of the overall Black Start strategy | [10 empty] | Ofgem discussion, relevant to communications section (7 year target)
CHAPTER III RESTORATION PLAN SECTION 2 RE-ENERGISATION | Article 27 Activation of the re-energisation procedure | 6. For the activation of a top-down re-energisation strategy, the TSO shall request neighbouring TSOs to support the re-energisation. This support may consist in assistance for active power, in accordance with paragraphs 3 to 5 of Article 21. The requested TSOs shall provide assistance for the re-energisation, unless it would lead their systems to the emergency or blackout states. In this case, the requesting TSO shall use the bottom-up re-energisation strategy. |  | GC0128 | OC9.3.2, BC2.9.6 |  | TSO to TSO STCP 06-1 |  |  |  | SRP (2.,3) | [12 empty] | Interconnectors mod?
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | 1. The frequency management procedure of the restoration plan shall contain a set of measures aiming at restoring system frequency back to the nominal frequency. |  | GC0128 | OC9.4.7.9 OC9.4.7 |  | STCP 6-1 Section 3.4 |  |  | TSOG? | SRP (3.3) | [10 empty] | Implementation of E&R Code Article 28 & 29 to include the clarification on Frequency Management Procedures and appointment of a frequency leader in Grid Code, by a additional section in OC9.4.7 |  | Implementation of E&R Code Articles 28, 29, 30 and 31, Frequency Management proceedure and appointment of a frequency lead into the STCP 6-1 Section 3.4 Black Start Procedure. | Clarification on the appointment of frequency leaders, and documentation of the management of frequency within the written STCP 6-1 section 3.4. To implement Article 29, the modification will included how the ESO will appoint Frequency Leaders for each emerging Power Island within GB. To implement Article 28, the modification will detail the responsibilities of the frequency leader and the process to manage frequency.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | 2. Each TSO shall activate its frequency management procedure: |  | GC0128 | OC9.4.7 |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (a) in preparation of the resynchronisation procedure, when a synchronous area is split in several synchronised regions; |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.2, 3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (b) in case of frequency deviation in the synchronous area; or |  | GC0128 | BC3 |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (c) in case of re-energisation. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.1)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | 3. The frequency management procedure shall include at least: |  | GC0128 | OC9.4.7 |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (a) a list of actions regarding the setting of the load-frequency controller before the appointment of frequency leaders; |  | GC0128 | OC9.2.5, OC9.4, BC3 |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (b) the appointment of frequency leaders; |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (c) the establishment of target frequency in case of bottom-up re-energisation strategy; |  | GC0128 | OC9.5.2.1(a), OC9.5.2.2(a), BC3, |  | STCP 6-1 Section 3.4, 3.4.5 |  |  |  | SRP (3.3.3, 3.3.4)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (d) frequency management after frequency deviation; and |  | GC0128 | OC9.4.3, OC9.5.2.2, OC9.5.6 |  | STCP 6-1 Section 3.4.5, 3.4.6, 3.4.3.7 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (e) frequency management after synchronous area split. |  | GC0128 | OC9.4.3, OC9.5.2.2, OC9.5.6 |  | STCP 6-1 Section 3.4.5, 3.4.6, 3.4.3.7 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 28 Frequency management procedure | (f) the determination of the amount of load and generation to be reconnected, taking into account the available active power reserves within the synchronised region in order to avoid major frequency deviations. |  | GC0128 | BC3, OC9.2.1, OC9.2.5, OC9.4.5.2, OC9.4.7.2, OC9.4.7.3, OC9.4.7.5, 0C9.4.7.6(e),OC9.5.1, OC9.5.2.2, OC9.5.6 |  | STCP 6-1 Section 3.4.3.5 |  |  |  | SRP (3.3)
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | 1. During system restoration, when a synchronous area is split in several synchronised regions, the TSOs of each synchronised region shall appoint a frequency leader, in accordance with paragraph 3. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1. | [9 empty] | Implementation of E&R Code Article 28 & 29 to include the clarification on Frequency Management Procedures and appointment of a frequency leader in Grid Code, by a additional section in OC9.4.7 |  | Implementation of E&R Code Articles 28, 29, 30 and 31, Frequency Management proceedure and appointment of a frequency lead into the STCP 6-1 Section 3.4 Black Start Procedure. | Clarification on the appointment of frequency leaders, and documentation of the management of frequency within the written STCP 6-1 section 3.4. To implement Article 29, the modification will included how the ESO will appoint Frequency Leaders for each emerging Power Island within GB. To implement Article 28, the modification will detail the responsibilities of the frequency leader and the process to manage frequency.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | 2. During system restoration, when a synchronous area is not split but the system frequency exceeds the frequency limits for the alert state as defined in Article 18(2) of Regulation (EU) 2017/XXX [SO GLs], all TSOs of the synchronous area shall appoint a frequency leader, in accordance with paragraph 3. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | 3. The TSO with the highest real-time estimated K-factor shall be appointed as the frequency leader, unless the TSOs of the synchronised region, or of the synchronous area, agree to appoint another TSO as the frequency leader. In that case, the TSOs of the synchronised region, or of the synchronous area, shall consider the following criteria: |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (a) the amount of available active power reserves and especially frequency restoration reserves; |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (b) the capacities available on interconnectors; |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (c) the availability of frequency measurements of TSOs of the synchronised region or of the synchronous area; and |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (d) the availability of measurements on critical elements within the synchronised region or the synchronous area. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | 4. Notwithstanding paragraph 3, where the size of the synchronous area concerned and the real time situation allow it, the TSOs of the synchronous area may appoint a predetermined frequency leader. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1, 3.3.2, 3.3.3) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | 5. The TSO appointed as frequency leader pursuant to paragraphs 1 and 2 shall inform the other TSOs of the synchronous area of its appointment without delay. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | 6. The appointed frequency leader shall act as such until: |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1. .
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (a) another frequency leader is appointed for its synchronised region; |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (b) a new frequency leader is appointed as the result of resynchronisation of its synchronised region with another synchronised region; or |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 29 Appointment of a frequency leader | (c) the synchronous area has been completely resynchronised, the system frequency is within the standard frequency range and the LFC operated by each TSO of the synchronous area is back to its normal operating mode in accordance with Article 18(1) of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  | SRP (3.3.1) | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 30 Frequency management after frequency deviation | 1. During system restoration, when a frequency leader has been appointed pursuant to Article 29(3), the TSOs of the synchronous area, other than the frequency leader, shall as a first measure suspend the manual activation of frequency restoration reserves and replacement reserves. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  | TSOG TERRE |  | In GB the ESO is considered to be the freqiency lead except in Scotland as provided for in STCP 06-1. | [9 empty] | Implementation of E&R Code Article 28, 29, 30 & 31 to include the clarification on Frequency Management Procedures and appointment of a frequency leader in Grid Code, by a additional section in OC9.4.7 |  | Implementation of E&R Code Articles 28, 29, 30 and 31, Frequency Management proceedure and appointment of a frequency lead into the STCP 6-1 Section 3.4 Black Start Procedure. | Clarification on the appointment of frequency leaders, and documentation of the management of frequency within the written STCP 6-1 section 3.4. To implement Article 29, the modification will included how the ESO will appoint Frequency Leaders for each emerging Power Island within GB. To implement Article 28, the modification will detail the responsibilities of the frequency leader and the process to manage frequency.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 30 Frequency management after frequency deviation | 2. The frequency leader shall establish, after consultation with the other TSOs of the synchronous area, the operating mode to be applied on the LFC operated by each TSO of the synchronous area. |  | GC0128 | BC3 |  | STCP 6-1 Section 3.4 |  |  |  |  | Not applicbale in GB. The ESO is responsible for control of System Frequency
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 30 Frequency management after frequency deviation | 3. The frequency leader shall manage the manual activation of frequency restoration reserves and replacement reserves within the synchronous area, aiming at regulating the frequency of the synchronous area towards the nominal frequency and taking into account the operational security limits defined pursuant to Article 25 of Regulation (EU) 2017/XXX [SO GLs]. Upon request, each TSO of the synchronous area shall support the frequency leader. |  | GC0128 | BC3, OC9.4.3, OC9.4.7.6(e), OC9.5.2.1(a), OC9.5.2.2 (a), OC9.5.6 |  | STCP 6-1 Section 3.4 |  |  | TSOG |  | The ESO is responsible for control of System Frequency in GB other than Scotland under the provisions of STCP 06-1
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 31 Frequency management after synchronous area split | 1. During system restoration, when a frequency leader has been appointed pursuant to Article 29(3), the TSOs of each synchronised region, with the exception of the frequency leader, shall as a first measure suspend the manual activation of frequency restoration reserves and replacement reserves. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  |  | The ESO is responsible for control of System Frequency in GB other than Scotland under the provisions of STCP 06-1 | [9 empty] | Implementation of E&R Code Article 28, 29, 30 & 31 to include the clarification on Frequency Management Procedures and appointment of a frequency leader in Grid Code, by a additional section in OC9.4.7 |  | Implementation of E&R Code Articles 28, 29, 30 and 31, Frequency Management proceedure and appointment of a frequency lead into the STCP 6-1 Section 3.4 Black Start Procedure. | Clarification on the appointment of frequency leaders, and documentation of the management of frequency within the written STCP 6-1 section 3.4. To implement Article 29, the modification will included how the ESO will appoint Frequency Leaders for each emerging Power Island within GB. To implement Article 28, the modification will detail the responsibilities of the frequency leader and the process to manage frequency.
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 31 Frequency management after synchronous area split | 2. The frequency leader shall establish, after consultation with the other TSOs of the synchronised region, the operating mode to be applied on the LFC operated by each TSO of the synchronised region. |  | GC0128 |  |  | STCP 6-1 Section 3.4 |  |  |  |  | The ESO is responsible for control of System Frequency in GB other than Scotland under the provisions of STCP 06-1
CHAPTER III RESTORATION PLAN SECTION 3 FREQUENCY MANAGEMENT | Article 31 Frequency management after synchronous area split | 3. The frequency leader shall manage the manual activation of frequency restoration reserves and replacement reserves within the synchronised region, aiming at regulating the frequency of the synchronised region towards the target frequency established by the resynchronisation leader, if any, pursuant to point (a) of Article 34(1) and taking into account the operational security limits set out pursuant to Article 25 of Regulation (EU) 2017/XXX [SO GLs]. When no resynchronisation leader is appointed for the synchronised region, the frequency leader shall aim at regulating the frequency towards the nominal frequency. Upon request, each TSO of the synchronised region shall support the frequency leader. |  | GC0128 | BC3, OC9.4.3, OC9.4.7.6(e), OC9.5.2.1(a), OC9.5.6 |  | STCP 6-1 Section 3.4 |  |  | TSOG | SRP (3.3) | The ESO is responsible for control of System Frequency in GB other than Scotland under the provisions of STCP 06-1
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 32 Resynchronisation procedure | The resynchronisation procedure of the restoration plan shall include, at least: |  | GC0128 | OC9.5 |  | STCP 6-1 Section 3.4.3.7 |  |  |  | SRP (3.2) | Operating the system | [11 empty] | Implementation of E&R Code Article 32, 33, 34, into STCP 6-1 Section 3.4.11 Interconnection of Power Islands | Modification of STCP 6-1 Section 3.4.11 to clarify the NGESO as Resynchronisation lead and the specific strategy to ensuring success. The maximum limits for phase angle, frequency and voltage differences will be documented.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 32 Resynchronisation procedure | (a) the appointment of a resynchronisation leader; |  | GC0128 | OC 9.5.6 |  | STCP 06-1 Section 3.1.11, 3.4.3.7 |  |  |  | SRP (3.2.1) | Tony add in words provided by Garth | [9 empty] | Implement of this Article 32 (a) will be undertaken via Article 33 (1)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 32 Resynchronisation procedure | (b) the measures allowing the TSO to apply a resynchronisation strategy; and |  | GC0128 | OC 9.4.7, OC9.5, BC2.9.2.2 |  | STCP 06-1 3.4 (3.4 and 3.4.3.7) |  |  |  | SRP (3.2.2) | [10 empty] | Covered in Article 34.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 32 Resynchronisation procedure | (c) the maximum limits for phase angle, frequency and voltage differences for connecting lines. |  | GC0128 | [6 empty] | SRP (3.2.6) | [10 empty] | Implementation of E&R Code Article 32 to include maximum limited for phase angle, frequency and voltage differences for Power System Synchronisation of Power Islands. | Addition of maximum limits to OC9.5
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | 1. During system restoration, when two synchronised regions can be resynchronised without endangering the operational security of the transmission systems, the frequency leaders of these synchronised regions shall appoint a resynchronisation leader in consultation with at least the TSO(s) identified as the potential resynchronisation leader and in accordance with paragraph 2. Each frequency leader shall inform without delay the TSOs from its synchronised region of the appointed resynchronisation leader. |  | GC0128 |  |  | STCP 06-1 |  |  |  | SRP (3.2) | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1. There may be a need to change the System Restoration Plan | [9 empty] | Implementation of E&R Code Articles 32 and 33 require minor clarifications OC9.4.7.7 to include the designation of Frequency Leaders and Resynchronisation Leader | The Company will instruct the relevant Users so as to interconnect Power Islands to achieve larger sub-systems, and subsequently the interconnection of these sub-systems to form an integrated system. This should eventually achieve the re-establishment of the Total System or that part of the Total System subject to the Partial Shutdown, as the case maybe. The interconnection of Power Islands and sub-systems will utilise the provisions of all or part of OC9.5 (Re-Synchronisation of De-synchronised Islands) and in such a situation such provisions will be part of the Black Start. The Company may appoint each Power Island with a Frequency Leader, responsible for managing the Power Island. For Resynchronisation the Company will become the Resynchronisation Leader, liaising with the Frequency Leaders. Where necessary The Compay may instruct another party to fulfil the Resynchronisation Lead role. | Implementation of E&R Code Article 32, 33, 34, into STCP 6-1 Section 3.4.11 Interconnection of Power Islands | Modification of STCP 6-1 Section 3.4.11 to clarify the NGESO as Resynchronisation lead and the specific strategy to ensuring success. The maximum limits for phase angle, frequency and voltage differences will be documented.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | 2. For each pair of synchronised regions to be resynchronised, the resynchronisation leader shall be the TSO that: |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  | SRP (3.2.1) | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1. | [9 empty] | Implementation of E&R Code Articles 32 and 33 require definitions of Frequency Leader and Resyncronisation Leader. | Frequency Leader: A party responsible for managing the frequency and voltage of a Power Island. Resynchronisation Leader: A TSO accountable for resynchronising Power Islands, having at least one substation equippped with a parallel switching device on the boarder between two synchronised regions, has access to and is cable to control the frequency and Voltage measurements from both synchronised regions,
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | (a) has in operation at least one substation equipped with a parallel switching device on the border between the two synchronised regions to be resynchronised; |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  | SRP (3.2.1) | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | (b) has access to the frequency measurements from both synchronised regions; |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  | SRP (3.2.1) | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | (c) has access to the voltage measurements on the substations between which potential resynchronisation points are located; and |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  | SRP (3.2.1) | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | (d) is able to control the voltage of potential resynchronisation points. |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  | SRP (3.2.1) | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | 3. Where more than one TSO fulfils the criteria under paragraph 2, the TSO with the highest number of potential resynchronisation points between the two synchronised regions shall be appointed as the resynchronisation leader, unless the frequency leaders of the two synchronised regions agree to appoint another TSO as resynchronisation leader. |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  |  | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1. | [9 empty] | Implementation of E&R Code Articles 32 and 33 require minor clarifications OC9.4.7.7 to include the designation of Frequency Leaders and Resynchronisation Leader | Covered in Article 33 1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | 4. The appointed resynchronisation leader shall act as such until: |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  |  | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | (a) another resynchronisation leader is appointed for the two synchronised regions; or |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  |  | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 33 Appointment of a resynchronisation leader | (b) the two synchronised regions have been resynchronised, and all the steps in Article 34 have been completed. |  | GC0128 |  |  | STCP 06-1 Section 3.4.3 |  |  |  |  | Not applicbale in GB as the ESO are the frequency lead other than in Scotland which is addressed through the STCP 06-1.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | 1. Prior to the resynchronisation, the resynchronisation leader shall: |  | GC0128 | OC9.5 |  | STCP 06-1 (3.4.11) |  |  |  | SRP (3.2.1) | [10 empty] | Implementation of E&R code Article 34 to OC9.5 to include minor changes capturing the responsibilities for the Resynchronisation leader. | Insert a paragraph detailing the Resynchronisation Leader's responsibilities as laid out in Article 34 1, 2,3,4. | Implementation of E&R Code Article 32, 33, 34, into STCP 6-1 Section 3.4.11 Interconnection of Power Islands | Modification of STCP 6-1 Section 3.4.11 to clarify the NGESO as Resynchronisation lead and the specific strategy to ensuring success. The maximum limits for phase angle, frequency and voltage differences will be documented.
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (a) establish, in accordance with the maximum limits referred to in Article 32: |  | GC0128
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (i) the target value of the frequency for resynchronisation; |  | GC0128 | OC9.4.7.6(e), OC9.5.2.1(a), OC9.5.2.2(a) |  | STCP 06-1 (3.2.1.7, 3.4.5, 3.4.11) |  |  |  | SRP (3.2, 3.3.3)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (ii) the maximum frequency difference between the two synchronised regions; |  | GC0128 | OC9.5.2.1, OC9.5.6, OC.9.5.1 |  | STCP 06-1 (3.4.11) |  |  |  | SRP (3.2.6)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (iii) the maximum active and reactive power exchange; and |  | GC0128 |  |  | STCP 06-1 (3.4.11) |  |  |  | SRP (3.2.3, 3.2.4, 3.2.5, 3.2.6)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (iv) the operating mode to be applied on the LFC; |  | GC0128 |  |  | STCP 06-1 (3.4.11) |  |  |  | SRP (3.3.3)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (b) select the resynchronisation point, taking into account the operational security limits in the synchronised regions; |  | GC0128 | OC9.1.2, OC9.4.7.2, OC9.4.7.7, OC9.5 |  | STCP 06-1 (3.4.11) |  |  |  | SRP (3.2.3, 3.2.4, 3.2.5, 3.2.6)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (c) establish and prepare all necessary actions for the resynchronisation of the two synchronised regions at the resynchronisation point; |  | GC0128 | OC9.1.2, OC9.4.7.2, OC9.4.7.7, OC9.5 |  | STCP 06-1 (3.1.11, 3.2, 3.4.11) |  |  |  | SRP (3.2.3, 3.2.4, 3.2.5)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (d) establish and prepare a subsequent set of actions to create additional connections between the synchronised regions; and |  | GC0128 | OC9.1.2, OC9.1.2, OC9.4.7.2, OC9.4.7.7, OC9.5) |  | STCP 06-1 (3.1.11, 3.2, 3.4.11) |  |  |  | SRP (3.2.3, 3.2.4, 3.2.5)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | (e) assess the readiness of the synchronised regions for resynchronisation, taking into account the conditions set out in point (a). |  | GC0128 | OC9.4.7.2, OC9.4.7.7, OC9.5.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.4.11) |  |  |  | SRP (3)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | 2. When carrying out the tasks enumerated in paragraph 1, the resynchronisation leader shall consult the frequency leaders of the involved synchronised regions and, for the tasks listed in points (b) to (e), it shall also consult the TSOs operating the substations used for resynchronisation. |  | GC0128 |  |  | STCP 06-1 (3.4.11.2) |  |  |  | BPs | Not relevant in GB other than Scotland
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | 3. Each frequency leader shall inform the TSOs within its synchronised region of the planned resynchronisation without undue delay. |  | GC0128 |  |  | STCP 06-1 (3.4.3, 3.4.4, 3.4.5, 3.4.11) |  |  |  | SRP (3.4.3, 3.4.4, 3.4.5)
CHAPTER III RESTORATION PLAN SECTION 4 RESYNCHRONISATION | Article 34 Resynchronisation strategy | 4. When all conditions established in accordance with point (a) of paragraph 1 are fulfilled, the resynchronisation leader shall execute the resynchronisation by activating the actions established in accordance with point (c) and (d) of paragraph 1. |  | GC0128 | OC9.1.2, OC9.4.7.2, OC9.4.7.7, OC9.5 |  | STCP 06-1 (3.1.1.1, 3.2, 3.4.11) |  |  |  | SRP (3.2.3, 3.2.4, 3.2.5)
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | 1. A TSO may temporarily suspend one or more market activities laid down in paragraph 2, where: |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (a) the transmission system of the TSO is in blackout state; or |  | GC0127 / GC0128 | OC9.4.6, OC9.4.2 |  |  |  | Section G3 |  | SRP (2,2.1.7) Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (b) the TSO has exhausted all options provided by the market and the continuation of market activities under the emergency state would deteriorate one or more of the conditions referred to in Article 18(3) of Regulation (EU) 2017/XXX [SO GLs]; or |  | GC0127 / GC0128 | OC9.4.1, OC.9.4.2, OC.9.4.6, |  |  |  | Section G3 | TSOG | SRP (2.1.7) Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (c) the continuation of market activities would decrease significantly the effectiveness of the restoration process to the normal or alert state; or |  | GC0127 / GC0128 | OC9.4.2 | [5 empty] | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (d) tools and communication means necessary for the TSOs to facilitate market activities are not available. |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | 2. The following market activities may be suspended pursuant to paragraph 1: |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (a) the provision of cross zonal capacity for capacity allocation on the corresponding bidding zone borders for each market time unit where it is expected that the transmission system shall not be restored to the normal or alert state; |  | GC0127 / GC0128 | OC9.3.2, OC9.4.6 |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (b) the submission by a balancing service provider of balancing capacity and balancing energy bids; |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (c) the provision by a balance responsible party of a balanced position at the end of the day-ahead timeframe if required by the terms and conditions related to balancing; |  | GC0127 / GC0128 | OC9.4.6 | [5 empty] | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (d) the provision of modifications of the position of balance responsible parties; |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (e) the provision of schedules referred to in Article 111(1) and (2) of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G3 | TSOG | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (f) other relevant market activities the suspension of which is deemed necessary to preserve and/or restore the system. |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G3 | TSOG | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | 3. In case of suspension of market activities pursuant to paragraph 1, upon request of the TSO, each SGU shall operate, where technically possible, at an active power set-point established by the TSO. |  | GC0127 / GC0128 | OC9.4.7.6(e), OC9.5.2.1(a), OC9.5.2.2(a), OC9.4.7.3 | [5 empty] | SRP (3.3.3, 3.3.4, 3.2.4) |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | 4. When suspending market activities pursuant to paragraph 1, the TSO may fully or partially suspend the operation of its processes impacted by such suspension. |  | GC0127 / GC0128 | OC9.4 |  |  |  | X |  | Market Suspension Document | (SW) I note that Article 35(4) allows the TSO to suspend its processes impacted by market suspension. Others would also be impacted, including ELEXON’s credit process – the current BSC caters for this and effectively requires partial suspension. I don’t think the NC ER prevents such suspension but it will need to be noted when proposals are developed. And if some of NGET’s activities which feed into the BSC normal processes are (partially) suspended this will have a direct impact on the BSC processes that would need to be reflected in the BSC. So can we mark the BSC as potentially impacted. | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | 5. When suspending market activities pursuant to paragraph 1, the TSO shall coordinate at least with the following parties: |  | GC0127 / GC0128 |  |  | STCP06-1 (3.1.8) |  | X |  |  | (SW) ELEXON should be included in the coordination. ‘At least’ allows for this, but this also means when developing proposals the BSC is likely to be impacted, e.g. to amend the current rules. So, again, can we mark the BSC as potentially impacted, particularly since the current BSC Section G covers communication issues as well as settlements. | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (a) the TSOs of the capacity calculation regions of which the TSO is a member of; |  | GC0127 / GC0128 | OC9.4.6 | [5 empty] | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (b) the TSOs with which the TSO has arrangements for the coordination of balancing; |  | GC0127 / GC0128 | OC9.4.6 |  | STCP 06-1 (3.4, 3.5, 3.4, 3.7) |  |  |  |  | Ref Art 11.3c 'corrdination'. STCP-06 - 1 Arrangements in Scotland are differnet than in England and Wales | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (c) the ‘NEMO’ and other entities assigned or delegated to execute market functions in accordance with Regulation (EU) 2015/1222 within its control area; |  | GC0127 / GC0128 | OC9.4.6 |  |  |  |  | (EU) 2015/1222 | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (d) the TSOs of a load-frequency control block of which the TSO is a member of; and |  | GC0127 / GC0128 | OC9.4.6 |  | STCP 06-1 (3.4, 3.5, 3.4.3.7) |  |  |  | Market Suspension Document | SCTP-06-1 - Arrangements in Scotland are differnet from Englnad and Wales. | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | (e) the coordinated capacity calculator of the capacity calculation regions of which the TSO is a member of. |  | GC0127 / GC0128 | OC9.4.6 |  |  |  |  | RSCs TSOG | Market Suspension Document | RSCs TSOG timescale? | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 35 Procedure for suspension of market activities | 6. In case of suspension of market activities, each TSO shall launch the communication procedure set out in Article 38. |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 1. By [12 months after entry into force of this Regulation], each TSO shall develop a proposal for rules concerning the suspension and restoration of market activities. |  | GC0127 / GC0128 | OC9.4.6, OC9.4.7.9 |  |  |  | Section G3 |  | SRP (2.1.7, 2.1.8.4) Market Suspension Document | Subject to Ofgem Approval | Article 35-39 Out of Scope Addressed through Market Suspension Document | [7 empty] | EiF+12months
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 2. The TSO shall publish these rules on its website following their approval by the relevant regulatory authority in accordance with Article 37 of Directive 2009/72. |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document | the rules are likely to be, at least partially, in the BSC Article 4 (paragraph 3) requires that the NRA decides within 6 months of receipt of the proposals | Article 35-39 Out of Scope Addressed through Market Suspension Document | [7 empty] | EIF+18months
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 3. The rules for suspension and restoration of market activities shall be compatible to the extent possible with: |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document | covers items that are in the BSC, e.g. ‘modifications of position’ means a change to notified energy contracts to the BSC | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (a) the rules on provision of cross zonal capacity within the concerned capacity calculation regions; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (b) the rules for submission by balancing service providers of balancing capacity and balancing energy bids resulting from arrangements with other TSOs for the coordination of balancing; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (c) the rules for provision by balance responsible party of a balanced position at the end of day-ahead timeframe if required by the terms and conditions related to balancing; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (d) rules for provision of modifications of the position of balance responsible parties; and |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (e) the rules for provision of schedules referred to in Article 111(1) and (2) of Regulation (EU) 2017/000 [SO GLs]. |  | GC0127 / GC0128 |  |  |  |  | Section G3 | SOGL, EBGL | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 4. When developing the rules for suspension and restoration of market activities, each TSO shall convert the situations referred to in Article 35(1) into objectively defined parameters taking into account at least the following factors: |  | GC0127 / GC0128 | OC.9.4.1, OC9.4.6 |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (a) the percentage of load disconnection in the LFC area of the TSO corresponding to: |  | GC0127 / GC0128 | Maket Suspension Threshold as deifned in the Grid Code |  |  |  | Section 3.1.5 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (i) the inability of a significant share of balancing responsible parties to maintain their balance; or |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (ii) the necessity for the TSO not to follow the usual balancing processes to perform an efficient re-energization; |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (b) the percentage of generation disconnection in the LFC area of the TSO corresponding to the inability of a significant share of balancing responsible parties to maintain their balance; |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (c) the share and geographic distribution of unavailable transmission system elements corresponding to: |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (i) the desynchronization of a significant part of the LFC area rendering the usual balancing processes counterproductive; or |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (ii) the reduction to zero of cross zonal capacity on a bidding zone border(s); |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (d) the inability of the following affected entities to execute their market activities for reason(s) outside their control: |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (i) balance responsible parties; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (ii) balancing service providers; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (iii) NEMOs and other entities assigned or delegated to execute market functions pursuant to Regulation (EU) 2015/1222; |  | GC0127 / GC0128 | [5 empty] | ? | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (iv) transmission connected DSOs; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (e) the absence of properly functioning tools and communication means necessary to perform: |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (i) the singleday-ahead or intraday coupling or any explicit capacity allocation mechanism; or |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (ii) the frequency restoration process; or |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (iii) the reserve replacement process; or |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (iv) the provision by balance responsible party of a balanced position in day ahead and the provision of change of its position; or |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | (v) the provision of schedules referred to in Article 111(1) and (2) of Regulation (EU) 2017/XXX [SO GLs]. |  | GC0127 / GC0128 | [5 empty] | SOGL | Market Suspension Document, Updates to SRP | Udates required to System Restoration Plan - Paragraph X | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 5. The rules for suspension and restoration of market activities shall define a time delay to be respected for each parameter defined pursuant to paragraph 4, prior to starting the procedure for suspension of market activities. |  | GC0127 / GC0128 | OC.9.4.6, OC9.4.7.9 |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 6. The concerned TSO shall assess in real-time the parameters defined pursuant to paragraph 4, on the basis of the information at its disposal. |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document | General good practice | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 7. By [3 years after entry into force of this Regulation], ENTSO for Electricity shall submit to the Agency a report assessing the level of harmonization of the rules for suspension and restoration of market activities established by the TSOs and identifying, as appropriate, areas that require harmonisation. |  | GC0127 / GC0128 | [7 empty] | Obligation on ENTSO-E. Not relevant for GB implementation | Article 35-39 Out of Scope Addressed through Market Suspension Document | [7 empty] | EIF+3years
CHAPTER IV MARKET INTERACTIONS | Article 36 Rules for suspension and restoration of market activities | 8. By [30 months after entry into force of this Regulation], each TSO shall submit to ENTSO for Electricity the data required to prepare and submit the report in accordance with paragraph 7. |  | GC0127 / GC0128 | [7 empty] | Start collecting this data? Discuss | Article 35-39 Out of Scope Addressed through Market Suspension Document | [7 empty] | EIF+30months
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 1. The concerned TSO, in coordination with the NEMO(s) active in its control area and with the neighbouring TSOs, shall launch the procedure for the restoration of market activities suspended pursuant to Article 35(1) when: |  | GC0127 / GC0128 | OC9.4.7.9 |  |  |  | Section G3 |  | SRP (4) Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | (a) the situation triggering the suspension has ended and no other situation referred to in Article 35(1) applies; and |  | GC0127 / GC0128 | OC9.4.7.9 |  | STCO 06-1 (3.1.8, 3.4.11) |  | Section G3 |  | SRP (4) Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | (b) the entities referred to in Article 38(2) have been duly informed in advance in accordance with Article 38. |  | GC0127 / GC0128 | OC9.4.7.9 |  | STCO 06-1 (3.1.8, 3.4.11) |  | Section G3 |  | SRP (4) Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 2. The concerned TSO, in coordination with neighbouring TSOs, shall launch the restoration of TSO processes impacted by the suspension of market activities when the conditions of paragraph 1 are fulfilled or before, if necessary to restore market activities. |  | GC0127 / GC0128 | OC9.4.7.9 |  | STCO 06-1 (3.1.8, 3.4.11) |  | Section G3 |  | SRP (4) Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 3. The concerned NEMO, in coordination with TSOs and entities referred to in Article 35(5), shall launch the restoration of the relevant day ahead market coupling process and/or the relevant intraday market coupling process after being informed by its TSO(s) that TSOs' processes have been restored. |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document and Bilateral Agreements |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 4. When the provision of cross zonal capacity has been suspended and subsequently restored, each concerned TSO shall update the cross zonal capacities for capacity allocation by using, from the following, the most feasible and efficient option for each market time unit: |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document and Bilateral Agreements |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | (a) by using the latest available cross zonal capacities calculated by the coordinated capacity calculator; |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document and Bilateral Agreements |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | (b) by launching the regional capacity calculation processes applicable in accordance with Articles 29 and 30 of Regulation (EU) 2015/1222; or, |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document and Bilateral Agreements |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | (c) by determining, in coordination with TSOs of the capacity calculation region, cross zonal capacities based on the actual physical network conditions. |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document and Bilateral Agreements |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 5. When part of the total coupled area where market activities have been suspended is back to the normal state or alert state, the NEMO(s) of this area shall be entitled to execute a market coupling in a part of the total coupled area, in consultation with the TSOs and entities referred to in Article 35(5), provided that the TSO has restored the capacity calculation process. |  | GC0127 / GC0128 | [6 empty] | Market Suspension Document and Bilateral Agreements |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 6. No later than 30 days after the market activities have been restored, the TSO(s) that suspended and restored market activities shall prepare a report at least in English containing a detailed explanation of the rationale, implementation and impact of the market suspension and a reference to the compliance with the rules for suspension and restoration of market activities and shall submit it to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72, and make it available to the entities referred to in Article 38(2). |  | GC0127 / GC0128 | OC10 | [5 empty] | Market Suspension Document | Black Start is considered as a System Incident. It is not clear how this is reported to Ofgem | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 37 Procedure for restoration of market activities | 7. The regulatory authorities of the Member States or the Agency may issue a recommendation to the concerned TSO(s) to promote good practices and prevent similar incidents in the future. |  | GC0127 / GC0128 | [7 empty] | Issue for Ofgem. No change to code required. | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | 1. The rules for suspension and restoration of market activities developed pursuant to Article 36 shall also contain a communication procedure detailing the tasks and actions expected from each party in its different roles during the suspension and restoration of market activities. |  | GC0127 / GC0128 | OC9 |  |  |  | Section G 3.1.2 |  |  | • 38 covers communications in the event of market suspension and restoration, but the current BSC Section G also covers this same area, so there are likely to be impacts on the BSC, depending on what NGET proposes. | Article 35-39 Out of Scope Addressed through Market Suspension Document | [7 empty] | EIF+12months
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | 2. The communication procedure shall provide that information is sent, simultaneously, to the following entities: |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G 3.1.2 |  | Market Suspension Document | It is not clear how commerical providers would be informed | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (a) the parties referred to in Article 35(5); |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G 3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (b) the balance responsible parties; |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G 3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (c) the balancing service providers; |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G 3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (d) the transmission connected DSOs; and |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G 3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (e) the relevant regulatory authority of the concerned Member States in accordance with Article 37 of Directive 2009/72. |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G 3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | 3. The communication procedure shall include at least the following steps : |  | GC0127 / GC0128 | [8 empty] | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (a) the notification by the TSO that market activities have been suspended in accordance with Article 35; |  | GC0127 / GC0128 | OC9.4.6 |  |  |  | Section G.3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (b) the notification by the TSO of best estimate for the time and date for transmission system restoration; |  | GC0127 / GC0128 | OC9.4.7.9 |  |  |  | Section G.3.1.2 |  |  |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (c) the notification by the NEMO and other entities designated to execute market functions according to Regulation (EU) 2015/1222 and to Regulation (EU) 2016/1719 of the suspension of their activities, if any; |  | GC0127 / GC0128 | [7 empty] | Not clear how this is addressed - discuss | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (d) the updates by the TSOs on the process for restoration of the transmission system; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.5.2.1 |  |  |  | Section G.3.1.2 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (e) the notification by the entities referred to in points (a) to (d) of paragraph 2, that their market tools and communication systems are operational; |  | GC0127 / GC0128 |  |  |  |  | Section G.3.1.2 |  |  |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (f) the notification by the TSO(s) that the transmission system has been restored back to normal state or alert state; |  | GC0127 / GC0128 | OC9.4.7.9 |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (g) the notification by the NEMO and other entities assigned or delegated to execute market functions according to Regulation (EU) 2015/1222 of the best estimate for time and date when market activities will be restored; and |  | GC0127 / GC0128 | OC9.4.7.9 |  |  |  | Section G |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | (h) the confirmation by the NEMO and other entities assigned or delegated to execute market functions according to Regulation (EU) 2015/1222 that market activities have been restored. |  | GC0127 / GC0128 | OC9.4.7.9 |  |  |  | BSC Section G |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | 4. All notifications and updates by the TSO(s), the NEMO(s) and other entities assigned or delegated to execute market functions referred to in paragraph 3, shall be published on the websites of those entities. When notification or update on the website is not possible, the entity subject to the obligation to notify, shall inform via e-mail, or via any other available means, at least those parties directly participating in the suspended market activities. |  | GC0127 / GC0128 |  |  |  |  | BSC Section G |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 38 Communication procedure | 5. Notification pursuant to point (e) of paragraph 3 shall be done via email or via any other available means to the concerned TSO. |  | GC0127 / GC0128 |  |  |  |  | BSC Section G |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | 1. By [12 months after entry into force of this Regulation], each TSO shall develop a proposal for rules for imbalance settlement and settlement of balancing capacity and balancing energy which shall be applicable for imbalance settlement periods during which the market activities were suspended. The TSO may propose the same rules it applies for normal operations. |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document | • 39 covers the same scope as Section G of the BSC as it covers settlement of imbalances; and balancing energy and capacity (imbalance settlement is within the BSC; and balancing energy/capacity settlement is partly within the BSC and partly within NGET’s balancing services). Interestingly the task of writing the proposals may also be delegated or assigned under paragraph 1. | Article 35-39 Out of Scope Addressed through Market Suspension Document | [7 empty] | EIF+12
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | The TSO shall publish these rules on its website following their approval by the relevant regulatory authority in accordance with Article 37 of Directive 2009/72. |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | A TSO may delegate the TSO's tasks referred to in this Article to one or more third parties, provided that the third party can carry out the respective function at least as effectively as the TSO(s). A Member State or, where applicable, a regulatory authority, may assign the tasks referred to in this Article to one or more third parties, provided that the third party can carry out the respective function at least as effectively as the TSO(s). |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | 2. The rules referred to in paragraph 1 shall address the settlements of TSO's and third parties, where relevant, with balance responsible parties, and balancing services providers. |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | 3. The rules developed in accordance with paragraph 1 shall: |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | (a) ensure the financial neutrality of each TSO and relevant third party referred to in paragraph 1; |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | (b) avoid distortions of incentives or counterproductive incentives to balance responsible parties, balance service providers and TSOs; |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | (c) incentivise balance responsible parties to strive to be balanced or help the system to restore its balance; |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | (d) avoid any financial penalties imposed on balance responsible parties and balancing service providers due to the execution of the actions requested by the TSO; |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | (e) discourage TSOs from suspending market activities, unless strictly necessary, and incentivise TSOs to restore the market activities as soon as possible; and |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document
CHAPTER IV MARKET INTERACTIONS | Article 39 Settlement principles | (f) incentivise balance service providers to offer services to the connecting TSO that helps restore the system to normal state. |  | GC0127 / GC0128 |  |  |  |  | Section G3 |  | Market Suspension Document |  | Article 35-39 Out of Scope Addressed through Market Suspension Document | [9 empty] | This is probably a commerical markets issue
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | 1. In addition to the provisions of Articles 40 to 53 of Regulation (EU) 2017/XXX [SO GLs], each TSO, when in the emergency, blackout or restoration states, shall be entitled to gather the following information : |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL |  | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (a) from DSOs identified in accordance with Article 23(4), the necessary information about at least: |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL |  | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the part of their network that is in island operation; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL |  | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the ability to synchronise parts of their network that is in island operation; and |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL |  | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iii) the capability to start island operation. |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL |  | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (b) from SGU identified in accordance with Article 23(4) and restoration service providers, information about at least the following conditions: |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL | Black Start Contracts | Part of LJRP | What else are we going to require from SGUs and restoration service providers in b(i) to (iv)? - None - this is already captured under the Grid Code in particular OC9.2.5 which has been updatd. Where is this set out today and where will it be set out (if not already set out today)? - See Grid Code references. This is based on the assumption that a GB SGU is any party with a CUSC Contract and would be required to satisfy the requirements of the Grid Code including OC9 We are not asking for any more data than set out in the Grid Code
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the current status of the installation; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL | Black Start Contracts | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the operational limits; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL | Black Start Contracts | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iii) the full activation time and the time to increase generation; and |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL | Black Start Contracts | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iv) the time critical processes. |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.2.5, OC9.4.7.3, OC9.4.5.2, OC9.4.7.4, OC9.4.7.5, OC9.4.7.6, OC9.4.7.8, OC9.4.7.12, OC9.5.2.1, OC9.5.2.2, OC9.5.1, OC9.5.3, OC9.5.4, OC9.5.4.1, OC9.5.6, OC9.5.7 |  | STCP 06-1 (3.2.3, 3.4.4) | DOC9.4.3.6, DOC 9.4.1.5, DOC9.1.3, DOC 9.4.3.7, DOC9.5, DOC9.6.2, DOC9.6.7 |  | SOGL | Black Start Contracts | Part of LJRP
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | 2. During the emergency, blackout or restoration states, each TSO shall provide in due time and for the purposes of system defence plan procedures and restoration plan procedures, the following information, where available to the TSO: |  | GC0127 / GC0128
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (a) to neighbouring TSOs, information about at least: |  | GC0127 / GC0128
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the extent and borders of the synchronised region or synchronised regions to which its control area belongs; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  |  |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the restrictions to operate the synchronised region; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  |  |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iii) the maximum duration and amount of active and reactive power that can be supplied via interconnectors; and |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  |  |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iv) any other technical or organisational restrictions; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  |  |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (b) to the frequency leader of its synchronised region, information about at least: |  | GC0127 / GC0128 |  |  | STCP 06-1 (3.2, 3.4.3) |  |  |  | SRP (3.3.1, 3.3.2) | [11 empty] | Is this relevant in GB.
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the restrictions to maintain island operation; |  | GC0127 / GC0128 |  |  | STCP 06-1 (3.2, 3.4.3) |  |  |  | SRP (3.3.1, 3.3.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the available additional load and generation; and |  | GC0127 / GC0128 |  |  | STCP 06-1 (3.2, 3.4.3) |  |  |  | SRP (3.3.1, 3.3.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iii) the availability of operational reserves; |  | GC0127 / GC0128 |  |  | STCP 06-1 (3.2, 3.4.3) |  |  |  | SRP (3.3.1, 3.3.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (c) to transmission connected DSOs identified in accordance with Article 11(4) and 23(4), information about at least: |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) | DOC 9 | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the system state of its transmission system; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) | DOC 9 | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the limits of active and reactive power, block loading, tap and circuit breaker position at the connection points; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) | DOC 9 | Section G3 |  | SRP (2. 3.4.1, 4.2) | [11 empty] | Are these not normal Grid Code processes
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iii) the information on the current and planned status of power generating modules connected to the DSO, if not available to the DSO directly; and |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) | DOC 9 | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iv) all necessary information leading to further coordination with distribution connected parties; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) | DOC 9 | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (d) to defence service providers, information about at least: |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2) |  | Mark/Tony to confirm how this will be covered - Updates added to OC9.2.5
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the system state of its transmission system; and |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2) | [11 empty] | Captured under existing STC Processes
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the scheduled measures that require participation of the defence service providers; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (e) to DSOs and SGU identified pursuant to Article 23(4) and to restoration service providers, information about at least: |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2) |  | Mark/Tony to confirm how this will be covered - Covered by existing Grid Code references but also see updates to OC9.2.5
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (i) the system state of its transmission system; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (ii) the ability and plans to re-energise couplings; and |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (iii) the scheduled measures that require their participation. |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.7.6, OC9.4.7.9, OC9.6.7, OC9.6.9, OC9.5.2.1, OC9.5.6, OC9.5.7, OC9.6.2, OC9.6.3, OC9.6.4, BC.2.9.6 |  | STCP -6-1 (3.1.4, 3.2.2.2, 3.2.2.5, 3.2, 3.3.1) |  | Section G3 |  | SRP (2. 3.4.1, 4.2)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | 3. TSOs in emergency, blackout or restoration state shall exchange among themselves information concerning, at least: |  | GC0127 / GC0128 | BC2.9.6 |  | STCP 06-1 (3.1.8) STCP 02-1
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (a) the circumstances that led to the current system state of its transmission system, to the extent that they are known; and |  | GC0127 / GC0128 | BC2.9.6 |  | STCP 06-1 (3.1.8) STCP 02-1
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (b) the potential problems making assistance for active power necessary. |  | GC0127 / GC0128 | BC2.9.6 |  | STCP 06-1 (3.1.8) STCP 02-1
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | 4. A TSO in emergency, blackout or restoration state shall provide, in due time, information about the system state of its transmission system and, where available, additional information explaining the situation on the transmission system: |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.6, OC9.5.2.1, OC9.6.3, OC9.6.4, OC9.6.7, OC10 | [5 empty] | SRP (2.1)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (a) to the NEMO(s), who shall make this information available to their market participants, as provided for in Article 38; |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.6, OC9.5.2.1, OC9.6.3, OC9.6.4, OC9.6.7, OC10 | [5 empty] | SRP (2.1)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (b) to its relevant regulatory authority in accordance with Article 37 of Directive 2009/72, or when explicitly provided for in national law, to the entities referred to in Article 4(3); and |  | GC0127 / GC0128 | [8 empty] | Internal Procedure - reported via the SO incident management procedures
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | (c) to any other relevant party, as appropriate. |  | GC0127 / GC0128 | OC9.1.3, OC9.2.3, OC9.4.6, OC9.5.2.1, OC9.6.3, OC9.6.4, OC9.6.7, OC10 | [5 empty] | SRP (2.1)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 40 Information exchange | 5. TSOs shall inform each affected party about the test plan developed pursuant to Article 43(2) and (3). |  | GC0127 / GC0128 | OC5.7 |  | STCP 06-1 (3.7) |  |  |  | SRP (6)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 41 Communication systems | 1. Each DSO and SGU identified in accordance with points (b) and (c) of Article 23(4), each restoration service provider and each TSO shall have a voice communication system in place with sufficient equipment redundancy and backup power supply sources to allow the exchange of the information needed for the restoration plan for at least 24 hours, in case of total absence of external electrical energy supply or in case of failure of any individual voice communication system equipment. Member States may require a minimum backup power capacity higher than 24 hours. |  | GC0127 / GC0128 | CC/ECC.6.5.2 |  | STCP04-05 |  |  |  |  | Under CC/ECC.6.5.2 the Bilateral Agreement will specifiy the requirement for Control Telephony and System Telephony. Control Telephony is resilent and robust with sufficent redundancy but it is not known if it resilent for 24 hours. The control telephony standard needs to be updated an re-loaded onto the ESO website - Phase 2 | Phase 2 | [7 empty] | EIF+5years |  |  | To review (Mike Kay email)
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 41 Communication systems | 2. Each TSO shall establish, in consultation with the DSOs and SGU identified in accordance with Article 23(4) and with restoration service providers, the technical requirements to be fulfilled by their voice communication systems as well as by the TSO's own voice communication system in order to allow their interoperability and to guarantee that the TSO’s incoming call can be identified by the other party and answered immediately. |  | GC0127 / GC0128 | CC/ECC6.5.5 CC/ECC6.5.5 | [6 empty] | Will be covered under Phase 2 | Phase 2 | [7 empty] | EIF+5years
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 41 Communication systems | 3. Each TSO shall establish, in consultation with its neighbouring TSOs and the other TSOs of its synchronous area, the technical requirements to be fulfilled by their voice communication systems as well as by the TSO's own voice communication system in order to allow their interoperability and to guarantee that the TSO’s incoming call can be identified by the other party and answered immediately. |  | GC0127 / GC0128 | CC.6.5.5/ECC.6.5.5 |  | STCP 04-5 (Operational Telephony) |  |  |  |  | Will be covered under Phase 2 | Phase 2 | [7 empty] | EIF+5years
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 41 Communication systems | 4. Notwithstanding paragraph 1, those SGUs identified in accordance with Article 23(4) that are type B power generating modules and those restoration service providers that are type A or B power generating modules, shall have the possibility to have only a data communication system, instead of a voice communication system, if agreed upon with the TSO. This data communication system shall fulfil the requirements laid down in paragraphs 1 and 2. |  | GC0127 / GC0128 | CC/ECC6.5.2 - 6.5.5 CC/ECC6.5.8 | [6 empty] | For Type A and Type B which are either directly connected or have TEC and and Agreement with the ESO then the requirements of the Grid Code apply including the requirements for telpehony and data exchange. There are slight differences if the Generator is Active in the BM - Phse 2 | Phase 2 | [7 empty] | EIF+5years
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 41 Communication systems | 5. Member States may require that, in addition to the voice communication system, a complementary communication system be used to support the restoration plan; in that case, the complementary communication system shall fulfil the requirements laid down in paragraph 1. |  | GC0127 / GC0128 | CC/ECC.6.5.2 - 6.5.5 |  | STCP 04-5 (Operational Telephony) |  |  |  |  | Not required by in GB there is a requirement for both Control Telephony and System Telephony - Phase 2 | Phase 2 | [7 empty] | EIF+5years |  | Not mandatory - exisiting processes already exist in GB. Alternatives can probably be agreed Bilaterally
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 42 Tools and facilities | 1. Each TSO shall make available critical tools and facilities referred to in Article 24 of Regulation (EU) 2017/XXX [SO GLs] for at least 24 hours in case of loss of primary power supply. |  | GC0127 / GC0128 | CC/ECC 6.5.2 - 6.5.5 CC/ECC 6.5.8 |  | STCP 06-1 (Black Start) STCP 04-3 (Realtime Data Provision) STCP 02-1 (Alarm and Event Management) STCP 04-6 (Offshore Datalink functional Specifiation for Telecontrol Communications Interface) STCP 04-1 (Real Time Datalink Management) STCP 04-2 (Real Time Data link Management) STCP 04-4 (Provision of Asset Operational Information) STCP 04-5 (Opeprational Telephony) STCP 06-4 (Contingency Arrangements) STCP 12-1 (Data Exchange Mechanism) |  |  | TSOG |  | GC and STC change might be needed. Critical tools - Art 24 TSOG - Coveredunder Phase 2 | Phase 2 | [7 empty] | EIF+5years |  |  | To review
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 42 Tools and facilities | 2. Each DSO and SGU identified pursuant to Article 23(4) as well as restoration service provider shall make available critical tools and facilities referred to in Article 24 of Regulation (EU) 2017/XXX [SO GLs] and used in the restoration plan for at least 24 hours in case of loss of primary power supply, as defined by the TSO. |  | GC0127 / GC0128 |  |  |  | Dcode change |  | TSOG |  | Covered under Phase 2 | Phase 2 | [7 empty] | EIF+5years
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 42 Tools and facilities | 3. Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities referred to in Article 24 of Regulation (EU) 2017/XXX [SO GLs]. Each TSO shall arrange a backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. |  | GC0127 / GC0128 | [5 empty] | TSOG | Internal Procedures
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 42 Tools and facilities | 4. Each TSO shall prepare a transfer procedure for moving functions from the main control room to the backup control room as quickly as possible, and in any case in a maximum time of three hours. The procedure shall include the operation of the system during the transfer. |  | GC0127 / GC0128 |  |  | STCP06-4 (Contincency Arrangements) |  |  |  | Business Procedure
CHAPTER V INFORMATION EXCHANGE AND COMMUNICATION, TOOLS AND FACILITIES | Article 42 Tools and facilities | 5. Substations identified as essential for the restoration plan procedures pursuant to Article 23(4) shall be operational in case of loss of primary power supply for at least 24 hours. For substations in the synchronous area Ireland and Latvia, the duration of operation in case of loss of primary power supply may be lower than 24 hours and shall be approved by the regulatory authority or other competent authority of the Member State, on proposal of the TSO. |  | GC0127 / GC0128 |  |  | Check |  |  |  |  | Covered under Phase 2 | Phase 2 | [7 empty] | EIF+5years
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 43 General principles | 1. Each TSO shall periodically assess the proper functioning of all equipment and capabilities considered in the system defence plan and the restoration plan. To this end, each TSO shall periodically verify the compliance of such equipment and capabilities, in accordance with paragraph 2 and with Article 41(2) of Regulation (EU) 2016/631, Article 35(2) of Regulation (EU) 2016/1388/] and Article 69(1) and (2) of Regulation (EU) 2016/1447. |  | GC0127 / GC0128 | OC5.5.1.1 |  | STCP 06-1 Updates may be required |  |  | Muiltply EU Codes | SDP (7), SRP(6) | [10 empty] | Implementation of Article 43 into OC5.7 for Black Start Testing | Addition of Communication test requirement for SRP. | Implementing E&R Code Article 43, there will be a clarification of the need to verify compliance to ESO for Article 48 Testing of communication systems | ***note*** not sure if this is quite right, but we'll need DSO's to verify to TSO that they have tested an have compliance.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 43 General principles | 2. By [24 months after the entry into force of the Regulation] each TSO shall define a test plan in consultation with the DSOs, the SGUs identified pursuant to Articles 11(4) and 23(4), the defence service providers and the restoration service providers. The test plan shall identify the equipment and capabilities relevant for the system defence plan and the restoration plan that have to be tested. |  | GC0127 / GC0128 | [6 empty] | SDP (7), SRP(6) |  | Garth - where is the test plan? Tony/Mark - confirm ESO position on this - The SDP (6) and SRP (7) cover this at a high level. The ESO are currently developing a solution with BEIS and Ofgem including exploring funding. | [7 empty] | EIF+24months | Implementation of Article 43 into OC5.7 for Black Start Testing | Add the requirement for the ESO to create a test plan in consultation with Restoration Service Providers, Transmission Operators and Distribution Network Operators.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 43 General principles | 3. The test plan shall include the periodicity and conditions of the tests, following the minimum requirements outlined in Articles 44 to 47. The test plan shall follow the methodology laid down in Regulation (EU) 2016/631 Regulation (EU) 2016/1388 and Regulation (EU) 2016/1447 for the corresponding tested capability. For SGUs that are not subject to Regulation (EU) 2016/631, Regulation (EU) 2016/1388 and Regulation (EU) 2016/1447, the test plan shall follow the provisions of national law. |  | GC0127 / GC0128 | CP/ECP OC5 |  |  |  |  | Muiltply EU Codes | SDP (7), SRP(6) |  | OC5.5.1.1 covers the ability to under take testing in accordance with the CC's and ECP's which link back to the CC's and ECP's where the ECP's contain the requirements on the EU Connection Network Codes. For the individual requirements in Article 44 - 47 see entries below against each Article | [8 empty] | Implementation of Article 43 into OC5.7 for Black Start Provider Testing | Update of the periodicity of the test
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 43 General principles | 4. Each TSO, DSO, SGU, defence service provider and restoration service provider shall not endanger the operational security of the transmission system and of the interconnected transmission system during the test. The test shall be conducted in a way that minimises the impact on system users. |  | GC0127 / GC0128 | OC5.1, OC5.5.1, OC5.5.3.3 |  | Possible update to STCP 06-1 may be required |  |  |  | SDP (7), SRP(6) |  | Updated - OC5.5.3.3 updated
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 43 General principles | 5. The test is deemed to be successful when it fulfils the conditions established by the relevant system operator pursuant to paragraph 3. As long as a test fails to fulfil these criteria, the TSO, DSO, SGU, defence service provider and restoration service provider shall repeat the test. |  | GC0127 / GC0128 | OC5.5.4, OC5.7.2.4
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 44 Compliance testing of power generating module capabilities | 1. Each restoration service provider which is a power generating module delivering black start service shall execute a black start capability test, at least every three years, following the methodology laid down in Article 45(5) of Regulation (EU) 2016/631. |  | GC0127 / GC0128 | OC5.7.1(b) OC5 GC Change GC108 completed |  |  |  |  | RfG |  |  | The issue is also addressed through the changed being proposed through GC0125 | [8 empty] | Implementation of Article 43, 44, and 46 on frequency of Restoration Service (Black Start) Provider testing. | Change of testing periodicity to at least every three years; change of assets being tested to for each Power Generating Module; adaptation of to make technology neutral and across all Black Start Providers.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 44 Compliance testing of power generating module capabilities | 2. Each restoration service provider which is a power generating module delivering a quick re-synchronisation service shall execute tripping to houseload test after any changes of equipment having an impact on its houseload operation capability, or after two unsuccessful consecutive tripping in real operation, following the methodology laid down in Article 45(6) of Regulation (EU) 2016/631. | SRP | GC0127 / GC0128 | OC5.7.1(a) Updated |  |  |  |  | RfG |  | OC5.7.1(a) Updated | OC5.7.1(a) Updated | [8 empty] | Implementation of Article 43, 44, and 46 on frequency of Restoration Service (Black Start) Provider testing. | Change of testing periodicity to at least every three years for each Power Generating Module and make this technology neutral.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 45 Compliance testing of demand facilities providing demand side response | 1. Each defence service provider delivering demand response shall execute a demand modification test, after two consecutive unsuccessful responses in real operation or at least every year, following the methodology laid down in Article 41(1) of Regulation (EU) 2016/1388. |  | GC0127 / GC0128 | DRSC.11.4.1.1, DRSC.11.7 and ECP.A.8.9 | [5 empty] | SDP (7.2.3) |  | Grid Code updated see DRSC.11.7 and ECP.A.8.9
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 45 Compliance testing of demand facilities providing demand side response | 2. Each defence service provider delivering demand response low frequency demand disconnection shall execute a low frequency demand disconnection test within a period to be defined at national level and following the methodology laid down in Article 37(4) of Regulation (EU) 2016/1388 for transmission connected demand facilities or according to a similar methodology defined by the relevant system operator for other demand facilities. |  | GC0127 / GC0128 | DRSC.11.7.2 and ECP.A.8.9.2 |  |  |  |  | DCC | SDP(7.2.3) |  | Grid Code updated see DRSC.11.7.2 and ECP.A.8.9.2
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 46 Compliance testing of HVDC capabilities | Each restoration service provider which is an HVDC system delivering a black start service shall execute a black start capability test, at least every three years, following the methodology laid down in Article 70(11) of Regulation (EU) 2016/1447. |  | GC0127 / GC0128 | OC5.7.1 |  |  |  |  | HVDC | SDP (7.2.1) | Covered under updates and code changes for GC0125 | [9 empty] | Implementation of Article 43, 44, and 46 on frequency of Restoration Service (Black Start) Provider testing. | Change of testing periodicity to at least every three years for each Power Generating Module and make this technology neutral.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 47 Compliance testing of low frequency demand disconnection relays | Each DSO and TSO shall execute testing on the low frequency demand disconnection relays implemented on its installations, within a period to be defined at national level and following the methodology laid down in Article 37(6) and Article 39(5) of Regulation (EU) 2016/1388. |  | GC0127 / GC0128 | ECP.A.8..9.2 and CC.A.5.4.2 and CC.A.5.4.3 |  |  |  |  | Demand Connection Code | SDP (7.2.4) | CC.A.5.4.2, ECC.A.5.4.3 and ECP.A.8.9.2 of the Grid Code added
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 48 Testing of communication systems | 1. Each DSO and SGU identified pursuant to Article 23(4), each TSO and each restoration service provider shall test the communication systems defined in Article 41, at least every year. |  | GC0127 / GC0128 | CC/ECC.6.5.4.4 | [5 empty] | SDP(7.2.6, 7.2.7), SRP (6) | [10 empty] | Implementation of Article 48 into OC5.7 | Clarification of requirement to communications annually. | Implementing E&R Code Article 43, there will be a clarification of the need to verify compliance to ESO for Article 48 Testing of communication systems | ***note*** not sure if this is quite right, but we'll need DSO's to verify to TSO that they have tested an have compliance.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 48 Testing of communication systems | 2. Each DSO and SGU identified pursuant to Article 23(4), each TSO and each restoration service provider shall test the backup power supply of their communication systems at least every five years. |  | GC0127 / GC0128 | CC Updated | [6 empty] | CC/ECC.6.5.4.4 of the Grid Code Updated | [9 empty] | Implementation of Article 48 into OC5.7 | Clarification of requirement to every 5 years.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 48 Testing of communication systems | 3. [By [7 years after the entry into force of the Regulation] each TSO, in consultation with other TSOs, shall define a test plan for testing the inter-TSO communication.] |  | GC0127 / GC0128 |  |  | STCP 08-3 (Operational Tests / System Tests) |  |  |  | SRP (5,6) | [9 empty] | EIF+7 years
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 49 Testing of tools and facilities | 1. Each TSO shall test the capability of main and backup power sources to supply its main and backup control rooms, provided for in Article 42, at least every year. |  | GC0127 / GC0128 | [6 empty] | SDP (7.2.8) plus Internal Procedures | Internal Procedure | [10 empty] | Diesel Generator checks?
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 49 Testing of tools and facilities | 2. Each TSO shall test the functionality of critical tools and facilities referred to in Article 24 of Regulation (EU) 2017/XXX [SO GLs], at least every three years, covering both main and backup tools and facilities. Where these tools and facilities involve DSOs or SGUs, these parties shall participate in this test. |  | GC0127 / GC0128 | CC/ECC.6.5.4.4 |  |  |  |  | SOGL | SDP (7.2.9) plus internal procedures | Internal Procedure
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 49 Testing of tools and facilities | 3. Each TSO shall test the capability of backup power sources to supply essential services of the substations identified as essential for the restoration plan procedures pursuant to Article 23(4), at least every five years. When these substations are in distribution systems, DSOs shall execute this test. |  | GC0127 / GC0128 | [6 empty] | SDP (7.2.10) | Internal Procedure
CHAPTER VI COMPLIANCE AND REVIEW SECTION 1 COMPLIANCE TESTING OF TSO, DSO AND SGU CAPABILITIES | Article 49 Testing of tools and facilities | 4. Each TSO shall test the transfer procedure for moving from the main control room to the backup control room, provided for in Article 42(4), at least every year. |  | GC0127 / GC0128 | [6 empty] | SDP (7.2.11) plus internal procedures | Internal Procedure
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | 1. Each DSO concerned by the implementation of the low frequency demand disconnection on its installations shall update once a year the communication to the notifying system operator provided for in point (b) of Article 12(6). This communication shall include the frequency settings at which netted demand disconnection is initiated and the percentage of netted demand disconnected at every such setting. |  | GC0127 / GC0128 | CC/ECC.A.5 Week 24 Submission (through Planning Code) OC6.6.2(d) | [6 empty] | Submitted through Week 24 Data required under OC6.6.2(d). An update has been added to OC6.6.2(d) to incldue the requirement for netted demand | [10 empty] | Speak to ENA
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | 2. Each TSO shall monitor the proper implementation of the low frequency demand disconnection on the basis of the yearly written communication referred to in paragraph 1 and on the basis of implementation details of TSOs’ installations where applicable. |  | GC0127 / GC0128 | OC6.6.2(d) Week 24 Submission PC.A.1.2 PC.A.6.3.1(a) | [6 empty] | Submitted through Week 24 Data required under OC6.6.2(d). The requirements for regular LFDD testing are covered in ECP.A.8.9
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | 3. Each TSO shall review, at least every five years, its complete system defence plan to assess its effectiveness. The TSO shall in this review take into account at least: |  | GC0127 / GC0128 | [6 empty] | SRP (9)
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | (a) the development and evolution of its network since the last review or first design; |  | GC0127 / GC0128 | [6 empty] | SRP (9) | Covered through the Operational Planning Process and ETYS from long term to operational timescales and Internal Procedures
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | (b) the capabilities of new equipment installed on the transmission and distribution systems since the last review or first design; |  | GC0127 / GC0128 | [6 empty] | SRP (9) | New Equipment installed on the Transmission System would be covered by National Grid Technical Specifications (E&W) and other TO Technical Appendices and requirments under the STC and STCP's
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | (c) the SGU commissioned since the last review or first design, their capabilities and relevant services offered; |  | GC0127 / GC0128 | CC/ECC and CP/ECP | [5 empty] | SRP (9) | Capabilities of new plant developed through the Grid Code CC's/ECC's and CP's and ECP's with site specific requirements developed through the Bilateral Connection Agreement. Any commerical services prcured would be through the Ancillary Serivces Contract
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | (d) the tests carried out and the analysis of system incidents pursuant to Article 56(5) of Regulation (EU) 2017/XXX [SO GLs] ; and |  | GC0127 / GC0128 | CP/ECP and OC5 / OC7 | [5 empty] | SRP (6) | Tests carried out would be in in accordance with CP / ECP and OC5. System Incidents are maanged under OC7 and reported through OC10
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | (e) the operational data collected during normal operation and after disturbance. |  | GC0127 / GC0128 | CC.6.5.6/ECC.6.5.6 + Monitoring (CC/ECC.6.6) | [5 empty] | SRP (6) | Operational Data comprises two parts - Operational Metering data under CC/ECC6.5.6 and the Bilateral Agreement and Monitoring data such as Dynamic System Montoring and Ancillary Serivces Monitoring data captured under CC6.6, ECC6.6 and OC5.4.2(c) in addtion to the requirements specified in the Bilateral Agreement. | [10 empty] | More detailed requirements for monitoring are covered in the Bilateral Agreement.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | 4. Each TSO shall review the relevant measures of its system defence plan in accordance with paragraph 3 before any substantial change in the configuration of the grid. |  | GC0127 / GC0128 | [6 empty] | SDP (9) | This is covered under SDP(9) but an internal procedure is being developed to cover this in mroe detail
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 50 Compliance testing and periodic review of the system defence plan | 5. When the TSO identifies the need to adapt the system defence plan, it shall amend its system defence plan and implement these amendments in accordance with points (c) and (d) of Article 4(2) and Articles 11 and 12. |  | GC0127 / GC0128 |  |  | STCP 06-1 (3.2.2) |  |  |  | SDP (9) | This is covered under SDP(9) but an internal procedure is being developed to cover this in moe detail
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | 1. Each TSO shall review the measures of its restoration plan using computer simulation tests, using data from the DSOs identified pursuant to Article 23(4) and the restoration service providers, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: |  | GC0127 / GC0128 |  |  | STCP 6-1 Section 3.1 |  |  |  | SRP (6) | Internal Procedure - Further updates will be required including updates to the STCP's, particuallry in realtion to computer simulations | Where is the testing procedure? Tony/Mark - confirm ESO position on this - need to design Strategy - Phase 2 - 5 year compliance period | [8 empty] | Implementation of Article 51 into OC 9.4.7.12 | Clarifications to sections a, or b and c, to ensure that Article 51 1 (Computer simulation tests for Local Joint Restoration Plans) are included
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | (a) the energising restoration path from restoration service providers with black start or island operation capabilities; |  | GC0127 / GC0128 |  |  | STCP 6-1 Section 3.1 |  |  |  | SRP (6) | Internal Procedures | [9 empty] | Implementation of Article 51 into OC 9.4.7.12
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | (b) the supply of power generating modules main auxiliaries; |  | GC0127 / GC0128 |  |  | STCP 6-1 Section 3.1 |  |  |  | SRP (6) | Internal Procedures | [9 empty] | Implementation of Article 51 into OC 9.4.7.12
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | (c) the demand reconnection process; and |  | GC0127 / GC0128 | OC9 |  | STCP 6-1 Section 3.1 |  |  |  | SRP (6) | Internal Procedures | [9 empty] | Implementation of Article 51 into OC 9.4.7.12
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | (d) the process for resynchronisation of networks in island operation. |  | GC0127 / GC0128 | OC9 |  | STCP 6-1 Section 3.1 |  |  |  | SRP (6) | Internal Procedures | [9 empty] | Implementation of Article 51 into OC 9.4.7.12
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | 2. In addition, where deemed necessary by the TSO for the effectiveness of the restoration plan, each TSO shall execute operational testing of parts of the restoration plan, in coordination with the DSOs identified pursuant to Article 23(4) and the restoration service providers. The TSO shall set out, in consultation with the DSOs and restoration service providers, those operational tests in a dedicated testing procedure. |  | GC0127 / GC0128 | OC5 |  | STCP 6-1 Section 3.1 |  |  |  | SRP (6) | Black Start Testing is completed as part of OC5. Internal Procedures also includes requirements for testing although some updates will be required to these internal procedures | [10 empty] | Covered in OC5.7
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | 3. Each TSO shall review its restoration plan to assess its effectiveness, at least every five years. |  | GC0127 / GC0128 | OC9 | [5 empty] | SRP (6) | Black Start Testing is completed as part of OC5. Internal Procedures also includes requirements for testing although some updates will be required to these internal procedures | [11 empty] | Implementation of E&R Code Article 51 into STC 6-1 additional section to cover the need for a skeleton network. | Requirement fr DSO to consider and plan for a skeleton network to aid restoration, within their asset investment strategy.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | 4. Each TSO shall review the relevant measures of its restoration plan in accordance with paragraph 1 and review their effectiveness before any substantial change in the configuration of the grid. |  | GC0127 / GC0128 | OC9 | [5 empty] | SRP (6) | Internal Procedure - Further updates will be required including a review of the STCP's. OC9.5.4 details the arrangements for agreeing procedures as part of the LJRP. STCP06-1 section 3.2.3 also details the mechanism of changing the Local Joint Restoration Plan | [11 empty] | Implementation of E&R Code Article 51 into STC 6-1 additional section to cover the need for a skeleton network. | Requirement fr DSO to consider and plan for a skeleton network to aid restoration, within their asset investment strategy.
CHAPTER VI COMPLIANCE AND REVIEW SECTION 2 COMPLIANCE TESTING AND REVIEW OF SYSTEM DEFENCE PLANS AND RESTORATION PLANS | Article 51 Compliance testing and periodic review of the restoration plan | 5. When the TSO identifies the need to adapt the restoration plan, it shall amend its restoration plan and implement these amendments in accordance with points (c) and (d) of Article 4(2) and Articles 23 and 24. |  | GC0127 / GC0128 | OC9 | [5 empty] | SRP (6) | Internal Procedure - Further updates will be required including a review of the STCP's | [11 empty] | Implementation of E&R Code Article 51 into STC 6-1 additional section to cover the need for a skeleton network. | Requirement fr DSO to consider and plan for a skeleton network to aid restoration, within their asset investment strategy.
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | 1. ENTSO for Electricity shall monitor the implementation of this Regulation in accordance with Article 8(8) of Regulation (EC) No 714/2009. Monitoring shall cover in particular the following matters: |  | GC0127 / GC0128 | N/A
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | (a) identification of any divergences in the national implementation of this Regulation for the items listed in Article 4(2); |  | GC0127 / GC0128
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | (b) consistency assessment of system defence plans and restoration plans carried out by TSOs in accordance with Article 6; |  | GC0127 / GC0128
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | (c) thresholds above which the impact of actions of one or more TSOs in the emergency, blackout or restoration states is considered significant for other TSOs within the capacity calculation region in accordance with Article 6; |  | GC0127 / GC0128
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | (d) the level of harmonisation of the rules for suspension and restoration of market activities established by the TSOs in accordance with Article 36(1) and for the purposes of the report provided for in Article 36(7); |  | GC0127 / GC0128
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | (e) the level of harmonisation of the rules for imbalance settlement and settlement of balancing energy in case of market suspension, referred to in Article 39. |  | GC0127 / GC0128
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | 2. The Agency, in cooperation with ENTSO for Electricity, shall produce by [12 months from the entry into force of this Regulation] a list of the relevant information to be communicated by ENTSO for Electricity to the Agency in accordance with Articles 8(9) and 9(1) of Regulation (EC) No 714/2009. The list of relevant information may be subject to updates. ENTSO for Electricity shall maintain a comprehensive, standardized format, digital data archive of the information required by the Agency. |  | GC0127 / GC0128 | N/A
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | 3. Relevant TSOs shall submit to ENTSO for Electricity the information required to perform the tasks referred to in paragraphs 1 and 2. |  | GC0127 / GC0128 | [17 empty] | Implementation of Article 52 into Grid Code section ???? To submit sufficient information to the ESO to permit reporting of SRP to Ofgem and Entso-E (Article 52 paragraph 1) | Additional paragraph to clarify the accountability to submit relevant data in a timely manner to the ESO, using the process established by the ESO to gain efficiency.
CHAPTER VII IMPLEMENTATION | Article 52 Monitoring | 4. Following a request of the relevant regulatory authority in accordance with Article 37 of Directive 2009/72, DSOs and the entities pursuant to Article 39(1) shall provide TSOs with the information under paragraph 2 unless that information is already available to the regulatory authorities, TSOs, the Agency or ENTSO for Electricity in relation to their respective implementation monitoring tasks, with the objective of avoiding duplication of information. |  | GC0127 / GC0128 | [19 empty] | Implementation of Article 52 into Grid Code section ???? To submit sufficient information to the ESO to permit reporting of SRP to Ofgem and Entso-E (Article 52 paragraph 1) | Additional paragraph to clarify the accountability to submit relevant data in a timely manner to the ESO, using the process established by the ESO to gain efficiency.
CHAPTER VII IMPLEMENTATION | Article 53 Stakeholder involvement | The Agency, in close cooperation with ENTSO for Electricity, shall organise stakeholder involvement regarding the implementation of this Regulation. Such involvement shall include regular meetings with stakeholders to identify problems and propose improvements related to the requirements of this Regulation. |  |  | N/A
CHAPTER VII FINAL PROVISIONS | Article 54 Amendments to contracts and general terms and conditions | All relevant clauses in contracts and general terms and conditions of TSOs, DSOs and SGUs relating to system operation shall comply with the requirements of this Regulation. To that effect, those contracts and general terms and conditions shall be modified accordingly. | [9 empty] | Covered by adherence to the above requirements
CHAPTER VII FINAL PROVISIONS | Article 55 Entry into force | This Regulation shall enter into force on the twentieth day following that of its publication in the Official Journal of the European Union. |  |  | N/A
CHAPTER VII FINAL PROVISIONS | Article 55 Entry into force | Article 15 (5) to (8), Article 41 and Article 42(1), (2) and (5) shall apply [5 years after the entry into force of this Regulation].
CHAPTER VII FINAL PROVISIONS | Article 55 Entry into force | This Regulation shall be binding in its entirety and directly applicable in all Member States.
CHAPTER VII FINAL PROVISIONS | Article 55 Entry into force | Done at Brussels,
CHAPTER VII FINAL PROVISIONS | Article 55 Entry into force | For the Commission
CHAPTER VII FINAL PROVISIONS | Article 55 Entry into force | The President […]