## Notes
Stability Pathfinder Phase Two
Short circuit level effectiveness factors V1
June 2020
Notes:
1 | Effectiveness factors show how effective a solution will be based on its location to provide short circuit current contribution to the ESO locations of need
2 | Short circuit current contribution is based on RMS transient value
3 | Effectiveness values for sites at voltages 132kV and above not covered by this list will be provided on request.
4 | An updated effectiveness list will be published at the Expression of Interest stage.

## Example
Example:
The following is an example of how effectiveness factors should be considered.
A solution at Arecleoch 132kV which provides 100MVA short circuit level (based on minimum short circuit current value between 5ms and 140ms following a fault at Arecleoch 132kV substation).
The corresponding section of the effectiveness factors table is shown below.
Effectiveness Location
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Loangannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 6% | 6% | 19% | 15% | 7% | 1% | 44% | 17%
This solution will contribute towards the requirement at all 8 locations.
The effective contribution at all 8 locations will be:
Effective MVA
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Loangannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 6 | 6 | 19 | 15 | 7 | 1 | 44 | 17
The solution is most effective at "Mark Hill/ Coylton 275kV and nearby area". It is equivalent to a 44MVA solution built at a site that is 100% effective at this location.
The solution is least effective at "Spittal 275kV". It is equivalent to a 1MVA solution built at a site that is 100% effective at this location.
The solution's contribution to all 8 locations will be considered in the assessment.

## Effectiveness Factors
Effectiveness Location
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Loangannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 275kV and nearby area
Arecleoch | AREC1 | 132 | 6% | 6% | 19% | 15% | 7% | 1% | 44% | 17%
Auchencrosh | AUCH2 | 275 | 7% | 14% | 43% | 33% | 9% | 1% | 100% | 39%
Auchenwynd | AUCW1 | 132 | 6% | 6% | 19% | 15% | 7% | 1% | 34% | 16%
Beauly | BEAU1 | 132 | 13% | 2% | 4% | 15% | 14% | 6% | 3% | 4%
Beauly | BEAU2 | 275 | 23% | 5% | 9% | 35% | 24% | 12% | 6% | 9%
Blackhill | BLAH1 | 132 | 6% | 6% | 18% | 15% | 7% | 1% | 43% | 17%
Blackhillock | BLHI4 | 400 | 100% | 8% | 13% | 52% | 71% | 6% | 8% | 13%
Blackhillock | BLHI2 | 275 | 48% | 6% | 10% | 38% | 48% | 5% | 6% | 10%
Blackhillock | BLHI1 | 132 | 25% | 3% | 5% | 19% | 25% | 3% | 3% | 5%
Blacklaw Extension | BLLX1 | 132 | 6% | 5% | 9% | 10% | 6% | 1% | 7% | 22%
Blacklaw Windfarm | BLKL1 | 132 | 6% | 6% | 10% | 16% | 7% | 1% | 7% | 13%
Bonnybridge | BONN1 | 132 | 8% | 6% | 11% | 39% | 10% | 1% | 6% | 10%
Braehead Park | BRAP1 | 132 | 7% | 6% | 20% | 21% | 7% | 1% | 10% | 14%
Branxton | BRNX4 | 400 | 6% | 45% | 12% | 18% | 7% | 1% | 9% | 19%
Busby | BUSB2 | 275 | 8% | 13% | 34% | 47% | 10% | 1% | 20% | 32%
Chapelcross | CHAP1 | 132 | 5% | 3% | 4% | 5% | 6% | 1% | 3% | 15%
Charleston | CHAR1 | 132 | 10% | 4% | 7% | 24% | 14% | 2% | 4% | 6%
Clyde North | CLYN2 | 275 | 6% | 9% | 14% | 16% | 7% | 1% | 11% | 59%
Clyde South | CLYS2 | 275 | 6% | 9% | 14% | 16% | 7% | 1% | 11% | 58%
Clyde's Mill | CLYM2 | 275 | 9% | 13% | 29% | 54% | 11% | 2% | 18% | 32%
Coalburn | COAL4 | 400 | 7% | 17% | 31% | 32% | 9% | 1% | 22% | 100%
Coatbridge | COAT2 | 275 | 8% | 14% | 26% | 47% | 10% | 1% | 17% | 31%
Cockenzie | COCK2 | 275 | 7% | 29% | 12% | 26% | 9% | 1% | 8% | 16%
Coylton | COYL2 | 275 | 7% | 13% | 41% | 32% | 9% | 1% | 100% | 38%
Craigiebuckler | CRAI1 | 132 | 19% | 3% | 5% | 20% | 30% | 2% | 3% | 5%
Crookston | CROO1 | 132 | 6% | 6% | 20% | 20% | 7% | 1% | 10% | 14%
Crystal Rigg | CRYR4 | 400 | 7% | 42% | 13% | 21% | 8% | 1% | 10% | 21%
Currie | CURR2 | 275 | 8% | 24% | 13% | 35% | 10% | 1% | 9% | 17%
Dalmally | DALL2 | 275 | 9% | 10% | 29% | 50% | 11% | 2% | 15% | 22%
Denny North | DENN4 | 400 | 17% | 13% | 26% | 100% | 20% | 5% | 15% | 24%
Denny North | DENN2 | 275 | 12% | 12% | 24% | 100% | 14% | 2% | 14% | 22%
Devol Moor | DEVM4 | 400 | 10% | 17% | 66% | 66% | 13% | 2% | 30% | 42%
Devonside | DEVO1 | 132 | 8% | 5% | 10% | 37% | 10% | 1% | 6% | 10%
Dounreay | DOUN2 | 275 | 16% | 3% | 6% | 23% | 17% | 78% | 4% | 6%
Dounreay | DOUN1 | 132 | 10% | 2% | 3% | 11% | 11% | 34% | 2% | 3%
East Kilbride South | EKIS2 | 275 | 8% | 13% | 32% | 47% | 10% | 1% | 19% | 33%
Easterhouse | EERH2 | 275 | 9% | 14% | 27% | 56% | 11% | 2% | 17% | 31%
Eccles | ECCL4 | 400 | 6% | 100% | 10% | 17% | 7% | 1% | 7% | 16%
Eccles | ECCL1 | 132 | 5% | 18% | 4% | 7% | 6% | 1% | 3% | 6%
Elvanfoot | ELVA4 | 400 | 7% | 14% | 24% | 26% | 8% | 1% | 18% | 100%
Elvanfoot | ELVA2 | 275 | 6% | 9% | 14% | 16% | 7% | 1% | 11% | 58%
Errochty | ERRO1 | 132 | 9% | 4% | 7% | 22% | 11% | 2% | 4% | 6%
Fallago | FALL4 | 400 | 7% | 39% | 15% | 24% | 8% | 1% | 11% | 23%
Fettereso | FETT2 | 275 | 32% | 8% | 12% | 47% | 48% | 3% | 7% | 12%
Fort Augustus | FAUG4 | 400 | 22% | 8% | 15% | 55% | 24% | 10% | 9% | 14%
Fort Augustus | FAUG2 | 275 | 18% | 6% | 11% | 38% | 19% | 8% | 6% | 10%
Fort Augustus | FAUG1 | 132 | 10% | 3% | 5% | 16% | 11% | 4% | 3% | 4%
Foyers | FOYE2 | 275 | 25% | 5% | 9% | 34% | 26% | 10% | 5% | 9%
Galashields | GALA1 | 132 | 6% | 17% | 4% | 8% | 6% | 1% | 3% | 6%
Glenglass | GLGL1 | 132 | 6% | 6% | 18% | 14% | 7% | 1% | 42% | 16%
Glenlee | GLLE1 | 132 | 6% | 5% | 14% | 12% | 6% | 1% | 33% | 13%
Glenrothes | GLRO2 | 275 | 15% | 11% | 19% | 100% | 19% | 2% | 11% | 19%
Grangemouth | GRMO2 | 275 | 11% | 17% | 15% | 53% | 14% | 2% | 10% | 18%
Gretna | GRNA4 | 400 | 6% | 12% | 17% | 19% | 7% | 1% | 13% | 100%
Gretna | GRNA1 | 132 | 5% | 4% | 4% | 6% | 6% | 1% | 4% | 16%
Hunterston | HUER4 | 400 | 9% | 19% | 100% | 54% | 11% | 2% | 40% | 50%
Hunterston | HUER1 | 132 | 6% | 6% | 26% | 17% | 7% | 1% | 19% | 16%
Hunterston East | HUNE4 | 400 | 9% | 19% | 100% | 54% | 11% | 2% | 40% | 50%
Inveraray | INVE1 | 132 | 7% | 5% | 14% | 22% | 8% | 1% | 7% | 10%
Inverarnan | INVR2 | 275 | 9% | 10% | 29% | 50% | 11% | 2% | 15% | 22%
Kaimes | KAIM2 | 275 | 8% | 25% | 13% | 32% | 10% | 1% | 9% | 17%
Keith | KEIT1 | 132 | 20% | 3% | 4% | 17% | 21% | 3% | 3% | 4%
Kendoon | KEOO1 | 132 | 6% | 5% | 14% | 12% | 6% | 1% | 33% | 13%
Kilgalleoch | KILG2 | 275 | 7% | 13% | 42% | 33% | 9% | 1% | 100% | 39%
Killin | KIIN1 | 132 | 7% | 3% | 9% | 17% | 8% | 1% | 5% | 7%
Kilmarnock South | KILS4 | 400 | 9% | 19% | 59% | 47% | 10% | 1% | 53% | 55%
Kilmarnock South | KILS2 | 275 | 7% | 13% | 41% | 32% | 9% | 1% | 73% | 38%
Kilmarnock Town | KILT2 | 275 | 7% | 13% | 41% | 32% | 9% | 1% | 72% | 38%
Kilwinning | KILW1 | 132 | 6% | 6% | 24% | 16% | 7% | 1% | 20% | 16%
Kincardine | KINC2 | 275 | 12% | 15% | 17% | 63% | 15% | 2% | 11% | 19%
Kintore | KINT2 | 275 | 38% | 7% | 11% | 43% | 59% | 4% | 7% | 11%
Knocknagael | KNOC2 | 275 | 25% | 5% | 9% | 35% | 26% | 11% | 6% | 9%
Lambhill | LAMB2 | 275 | 10% | 12% | 29% | 66% | 13% | 2% | 16% | 24%
Loch Buidhe | LOCB2 | 275 | 19% | 4% | 7% | 28% | 20% | 32% | 4% | 7%
Longannet | LOAN2 | 275 | 12% | 13% | 23% | 100% | 15% | 2% | 13% | 23%
Mark Hill | MAHI2 | 275 | 7% | 14% | 43% | 33% | 9% | 1% | 100% | 39%
Maybole | MAYB1 | 132 | 6% | 6% | 19% | 15% | 7% | 1% | 34% | 16%
Moffat | MOFF4 | 400 | 6% | 12% | 18% | 20% | 7% | 1% | 13% | 100%
Moffat | MOFF1 | 132 | 5% | 4% | 6% | 7% | 6% | 1% | 4% | 22%
Mossmorran | MOSM2 | 275 | 13% | 12% | 20% | 100% | 17% | 2% | 12% | 20%
Mybster | MYBS1 | 132 | 10% | 2% | 3% | 10% | 10% | 44% | 2% | 3%
Neilston | NEIL4 | 400 | 9% | 18% | 83% | 56% | 11% | 2% | 36% | 48%
New Cumnock | NECU2 | 275 | 7% | 13% | 41% | 32% | 9% | 1% | 100% | 37%
New Deer | NEDE2 | 275 | 40% | 6% | 10% | 38% | 80% | 3% | 6% | 9%
Newarthill | NEAR2 | 275 | 8% | 14% | 26% | 47% | 10% | 1% | 17% | 32%
Newton Stewart | NETS1 | 132 | 6% | 4% | 13% | 11% | 6% | 1% | 30% | 12%
Partick | PART1 | 132 | 7% | 5% | 14% | 25% | 8% | 1% | 7% | 11%
Peterhead | PEHE2 | 275 | 37% | 6% | 9% | 37% | 100% | 3% | 6% | 9%
Peterhead | PEHE1 | 132 | 17% | 3% | 4% | 15% | 39% | 2% | 3% | 4%
Redhouse | REDH1 | 132 | 9% | 5% | 10% | 38% | 11% | 1% | 6% | 9%
Rothienorman | ROTI2 | 275 | 43% | 6% | 10% | 40% | 66% | 4% | 6% | 10%
Shin | SHIN1 | 132 | 11% | 2% | 3% | 12% | 11% | 13% | 2% | 3%
Sloy | SLOY1 | 132 | 7% | 5% | 13% | 22% | 8% | 1% | 7% | 10%
Smeaton | SMEA2 | 275 | 8% | 27% | 12% | 28% | 9% | 1% | 9% | 17%
Spittal | SPIT2 | 275 | 16% | 3% | 6% | 22% | 16% | 100% | 4% | 5%
Spittal | SPIT1 | 132 | 10% | 2% | 3% | 10% | 10% | 43% | 2% | 3%
Strathaven | STHA4 | 400 | 8% | 20% | 38% | 44% | 10% | 1% | 30% | 59%
Strathaven | STHA2 | 275 | 8% | 13% | 31% | 48% | 10% | 1% | 19% | 33%
Tealing | TEAL2 | 275 | 20% | 10% | 15% | 62% | 28% | 3% | 9% | 16%
Tealing | TEAL1 | 132 | 11% | 4% | 7% | 24% | 14% | 2% | 4% | 6%
Thurso | THSO2 | 275 | 16% | 3% | 6% | 22% | 17% | 89% | 4% | 5%
Tongland | TONG1 | 132 | 6% | 4% | 12% | 10% | 6% | 1% | 28% | 11%
Torness | TORN4 | 400 | 6% | 45% | 12% | 18% | 7% | 1% | 9% | 19%
Tummel | TUMM2 | 275 | 14% | 8% | 15% | 51% | 17% | 4% | 9% | 14%
Westfield | WFIE2 | 275 | 14% | 12% | 20% | 100% | 18% | 2% | 12% | 20%
Westfield | WFIE1 | 132 | 9% | 6% | 10% | 39% | 11% | 1% | 6% | 10%
Whitelee | WLEE2 | 275 | 8% | 13% | 32% | 47% | 10% | 1% | 19% | 33%
Whitelee Extension | WLEX2 | 275 | 8% | 13% | 32% | 46% | 10% | 1% | 19% | 33%
Windyhill | WIYH2 | 275 | 10% | 12% | 33% | 58% | 12% | 2% | 17% | 25%
Windyhill | WIYH1 | 132 | 7% | 5% | 14% | 25% | 8% | 1% | 8% | 11%
Wishaw (Gowkthrapple) | WISH4 | 400 | 8% | 22% | 35% | 44% | 10% | 1% | 26% | 52%