## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | Total loss | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 23042020-1 | Loss of STAY-4 BM Unit |  | 2020-04-23 | 12:35 | N/A | Refer to tab 'Event 23042020-1' | 49.99 | 49.85 | -0.074 | 464 | 464 | N/A | N/A | N/A | 156.7254
Event 25042020-1 | Loss of MEDP-1 BM Unit |  | 2020-04-25 | 20:03 | N/A | Refer to tab 'Event 25042020-1' | 50.154 | 49.839 | -0.058 | 676 | 676 | N/A | N/A | N/A | 292.2768

## Event 23042020-1
In UTC
Date | Time | Freq
2020-04-23 | 11:34 | 50.002
2020-04-23 | 11:34 | 50.002
2020-04-23 | 11:34 | 50.001
2020-04-23 | 11:34 | 49.995
2020-04-23 | 11:34 | 49.99
2020-04-23 | 11:34 | 49.984
2020-04-23 | 11:34 | 49.982
2020-04-23 | 11:34 | 49.982
2020-04-23 | 11:34 | 49.982
2020-04-23 | 11:34 | 49.986
2020-04-23 | 11:34 | 49.986
2020-04-23 | 11:34 | 49.989
2020-04-23 | 11:34 | 49.989
2020-04-23 | 11:34 | 49.987
2020-04-23 | 11:34 | 49.987
2020-04-23 | 11:34 | 49.986
2020-04-23 | 11:34 | 49.988
2020-04-23 | 11:34 | 49.99
2020-04-23 | 11:34 | 49.994
2020-04-23 | 11:34 | 49.996
2020-04-23 | 11:34 | 50
2020-04-23 | 11:34 | 50.001
2020-04-23 | 11:34 | 50.002
2020-04-23 | 11:34 | 49.997
2020-04-23 | 11:34 | 49.991
2020-04-23 | 11:34 | 49.983
2020-04-23 | 11:34 | 49.978
2020-04-23 | 11:34 | 49.974
2020-04-23 | 11:34 | 49.973
2020-04-23 | 11:34 | 49.977
2020-04-23 | 11:34 | 49.98
2020-04-23 | 11:34 | 49.986
2020-04-23 | 11:34 | 49.991
2020-04-23 | 11:35 | 49.995
2020-04-23 | 11:35 | 49.999
2020-04-23 | 11:35 | 50
2020-04-23 | 11:35 | 50.004
2020-04-23 | 11:35 | 50.002
2020-04-23 | 11:35 | 49.998
2020-04-23 | 11:35 | 49.992
2020-04-23 | 11:35 | 49.985
2020-04-23 | 11:35 | 49.978
2020-04-23 | 11:35 | 49.973
2020-04-23 | 11:35 | 49.972
2020-04-23 | 11:35 | 49.974
2020-04-23 | 11:35 | 49.979
2020-04-23 | 11:35 | 49.98
2020-04-23 | 11:35 | 49.984
2020-04-23 | 11:35 | 49.987
2020-04-23 | 11:35 | 49.99
2020-04-23 | 11:35 | 49.995
2020-04-23 | 11:35 | 49.994
2020-04-23 | 11:35 | 49.996
2020-04-23 | 11:35 | 49.994
2020-04-23 | 11:35 | 49.992
2020-04-23 | 11:35 | 49.99
2020-04-23 | 11:35 | 49.987
2020-04-23 | 11:35 | 49.984
2020-04-23 | 11:35 | 49.981
2020-04-23 | 11:35 | 49.984
2020-04-23 | 11:35 | 49.988
2020-04-23 | 11:35 | 49.984
2020-04-23 | 11:35 | 49.939
2020-04-23 | 11:35 | 49.901
2020-04-23 | 11:35 | 49.88
2020-04-23 | 11:35 | 49.86
2020-04-23 | 11:35 | 49.854
2020-04-23 | 11:35 | 49.85
2020-04-23 | 11:35 | 49.851
2020-04-23 | 11:35 | 49.851
2020-04-23 | 11:35 | 49.854
2020-04-23 | 11:35 | 49.853
2020-04-23 | 11:35 | 49.854
2020-04-23 | 11:35 | 49.857
2020-04-23 | 11:35 | 49.859
2020-04-23 | 11:35 | 49.861
2020-04-23 | 11:35 | 49.861
2020-04-23 | 11:35 | 49.864
2020-04-23 | 11:35 | 49.864
2020-04-23 | 11:35 | 49.865
2020-04-23 | 11:35 | 49.863
2020-04-23 | 11:35 | 49.861
2020-04-23 | 11:35 | 49.858
2020-04-23 | 11:35 | 49.857
2020-04-23 | 11:35 | 49.857
2020-04-23 | 11:35 | 49.856
2020-04-23 | 11:35 | 49.856
2020-04-23 | 11:35 | 49.853
2020-04-23 | 11:35 | 49.855
2020-04-23 | 11:35 | 49.853
2020-04-23 | 11:35 | 49.855
2020-04-23 | 11:35 | 49.856
2020-04-23 | 11:36 | 49.856
2020-04-23 | 11:36 | 49.858
2020-04-23 | 11:36 | 49.859
2020-04-23 | 11:36 | 49.86
2020-04-23 | 11:36 | 49.862
2020-04-23 | 11:36 | 49.862
2020-04-23 | 11:36 | 49.863
2020-04-23 | 11:36 | 49.859
2020-04-23 | 11:36 | 49.856
2020-04-23 | 11:36 | 49.853
2020-04-23 | 11:36 | 49.852
2020-04-23 | 11:36 | 49.856
2020-04-23 | 11:36 | 49.859
2020-04-23 | 11:36 | 49.862
2020-04-23 | 11:36 | 49.864
2020-04-23 | 11:36 | 49.866
2020-04-23 | 11:36 | 49.869
2020-04-23 | 11:36 | 49.871
2020-04-23 | 11:36 | 49.873
2020-04-23 | 11:36 | 49.875
2020-04-23 | 11:36 | 49.873
2020-04-23 | 11:36 | 49.87
2020-04-23 | 11:36 | 49.866
2020-04-23 | 11:36 | 49.862
2020-04-23 | 11:36 | 49.859
2020-04-23 | 11:36 | 49.857
2020-04-23 | 11:36 | 49.858
2020-04-23 | 11:36 | 49.86
2020-04-23 | 11:36 | 49.863
2020-04-23 | 11:36 | 49.866
2020-04-23 | 11:36 | 49.871
2020-04-23 | 11:36 | 49.871
2020-04-23 | 11:36 | 49.871
2020-04-23 | 11:36 | 49.869
2020-04-23 | 11:36 | 49.869
2020-04-23 | 11:36 | 49.866
2020-04-23 | 11:36 | 49.865
2020-04-23 | 11:36 | 49.862
2020-04-23 | 11:36 | 49.86
2020-04-23 | 11:36 | 49.859
2020-04-23 | 11:36 | 49.858
2020-04-23 | 11:36 | 49.857
2020-04-23 | 11:36 | 49.858
2020-04-23 | 11:36 | 49.86
2020-04-23 | 11:36 | 49.86
2020-04-23 | 11:36 | 49.863
2020-04-23 | 11:36 | 49.864
2020-04-23 | 11:36 | 49.862
2020-04-23 | 11:36 | 49.861
2020-04-23 | 11:36 | 49.859
2020-04-23 | 11:36 | 49.861
2020-04-23 | 11:36 | 49.861
2020-04-23 | 11:36 | 49.863
2020-04-23 | 11:36 | 49.866
2020-04-23 | 11:36 | 49.868
2020-04-23 | 11:36 | 49.867
2020-04-23 | 11:36 | 49.868
2020-04-23 | 11:36 | 49.867
2020-04-23 | 11:36 | 49.867
2020-04-23 | 11:36 | 49.866
2020-04-23 | 11:36 | 49.867
2020-04-23 | 11:37 | 49.866
2020-04-23 | 11:37 | 49.865
2020-04-23 | 11:37 | 49.864
2020-04-23 | 11:37 | 49.864
2020-04-23 | 11:37 | 49.865
2020-04-23 | 11:37 | 49.865
2020-04-23 | 11:37 | 49.866
2020-04-23 | 11:37 | 49.866
2020-04-23 | 11:37 | 49.865
2020-04-23 | 11:37 | 49.864
2020-04-23 | 11:37 | 49.864
2020-04-23 | 11:37 | 49.861
2020-04-23 | 11:37 | 49.86
2020-04-23 | 11:37 | 49.858
2020-04-23 | 11:37 | 49.858
2020-04-23 | 11:37 | 49.856
2020-04-23 | 11:37 | 49.855
2020-04-23 | 11:37 | 49.856
2020-04-23 | 11:37 | 49.858
2020-04-23 | 11:37 | 49.861
2020-04-23 | 11:37 | 49.861
2020-04-23 | 11:37 | 49.861
2020-04-23 | 11:37 | 49.863
2020-04-23 | 11:37 | 49.865
2020-04-23 | 11:37 | 49.866
2020-04-23 | 11:37 | 49.87
2020-04-23 | 11:37 | 49.873
2020-04-23 | 11:37 | 49.875
2020-04-23 | 11:37 | 49.875
2020-04-23 | 11:37 | 49.875
2020-04-23 | 11:37 | 49.877
2020-04-23 | 11:37 | 49.88
2020-04-23 | 11:37 | 49.885
2020-04-23 | 11:37 | 49.891
2020-04-23 | 11:37 | 49.899
2020-04-23 | 11:37 | 49.904
2020-04-23 | 11:37 | 49.908
2020-04-23 | 11:37 | 49.912
2020-04-23 | 11:37 | 49.915
2020-04-23 | 11:37 | 49.917
2020-04-23 | 11:37 | 49.92
2020-04-23 | 11:37 | 49.924
2020-04-23 | 11:37 | 49.929
2020-04-23 | 11:37 | 49.93
2020-04-23 | 11:37 | 49.932
2020-04-23 | 11:37 | 49.932
2020-04-23 | 11:37 | 49.93
2020-04-23 | 11:37 | 49.93
2020-04-23 | 11:37 | 49.929
2020-04-23 | 11:37 | 49.927
2020-04-23 | 11:37 | 49.925
2020-04-23 | 11:37 | 49.923
2020-04-23 | 11:37 | 49.921
2020-04-23 | 11:37 | 49.92
2020-04-23 | 11:37 | 49.919
2020-04-23 | 11:37 | 49.918
2020-04-23 | 11:37 | 49.918
2020-04-23 | 11:37 | 49.917
2020-04-23 | 11:37 | 49.917
2020-04-23 | 11:38 | 49.919
2020-04-23 | 11:38 | 49.921
2020-04-23 | 11:38 | 49.924
2020-04-23 | 11:38 | 49.927
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.932
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.932
2020-04-23 | 11:38 | 49.934
2020-04-23 | 11:38 | 49.934
2020-04-23 | 11:38 | 49.935
2020-04-23 | 11:38 | 49.933
2020-04-23 | 11:38 | 49.933
2020-04-23 | 11:38 | 49.932
2020-04-23 | 11:38 | 49.932
2020-04-23 | 11:38 | 49.933
2020-04-23 | 11:38 | 49.934
2020-04-23 | 11:38 | 49.937
2020-04-23 | 11:38 | 49.939
2020-04-23 | 11:38 | 49.94
2020-04-23 | 11:38 | 49.941
2020-04-23 | 11:38 | 49.941
2020-04-23 | 11:38 | 49.943
2020-04-23 | 11:38 | 49.944
2020-04-23 | 11:38 | 49.943
2020-04-23 | 11:38 | 49.942
2020-04-23 | 11:38 | 49.939
2020-04-23 | 11:38 | 49.935
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.93
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.932
2020-04-23 | 11:38 | 49.935
2020-04-23 | 11:38 | 49.937
2020-04-23 | 11:38 | 49.939
2020-04-23 | 11:38 | 49.943
2020-04-23 | 11:38 | 49.943
2020-04-23 | 11:38 | 49.944
2020-04-23 | 11:38 | 49.942
2020-04-23 | 11:38 | 49.939
2020-04-23 | 11:38 | 49.935
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.929
2020-04-23 | 11:38 | 49.926
2020-04-23 | 11:38 | 49.926
2020-04-23 | 11:38 | 49.924
2020-04-23 | 11:38 | 49.924
2020-04-23 | 11:38 | 49.928
2020-04-23 | 11:38 | 49.931
2020-04-23 | 11:38 | 49.934
2020-04-23 | 11:39 | 49.939
2020-04-23 | 11:39 | 49.943
2020-04-23 | 11:39 | 49.946
2020-04-23 | 11:39 | 49.947
2020-04-23 | 11:39 | 49.946
2020-04-23 | 11:39 | 49.944
2020-04-23 | 11:39 | 49.942
2020-04-23 | 11:39 | 49.941
2020-04-23 | 11:39 | 49.94
2020-04-23 | 11:39 | 49.944
2020-04-23 | 11:39 | 49.951
2020-04-23 | 11:39 | 49.954
2020-04-23 | 11:39 | 49.957
2020-04-23 | 11:39 | 49.958
2020-04-23 | 11:39 | 49.959
2020-04-23 | 11:39 | 49.96
2020-04-23 | 11:39 | 49.961
2020-04-23 | 11:39 | 49.959
2020-04-23 | 11:39 | 49.956
2020-04-23 | 11:39 | 49.952
2020-04-23 | 11:39 | 49.948
2020-04-23 | 11:39 | 49.945
2020-04-23 | 11:39 | 49.939
2020-04-23 | 11:39 | 49.935
2020-04-23 | 11:39 | 49.935
2020-04-23 | 11:39 | 49.937
2020-04-23 | 11:39 | 49.941
2020-04-23 | 11:39 | 49.943
2020-04-23 | 11:39 | 49.943
2020-04-23 | 11:39 | 49.945
2020-04-23 | 11:39 | 49.943
2020-04-23 | 11:39 | 49.943
2020-04-23 | 11:39 | 49.941
2020-04-23 | 11:39 | 49.941
2020-04-23 | 11:39 | 49.94
2020-04-23 | 11:39 | 49.94
2020-04-23 | 11:39 | 49.936
2020-04-23 | 11:39 | 49.936
2020-04-23 | 11:39 | 49.936
2020-04-23 | 11:39 | 49.936
2020-04-23 | 11:39 | 49.937
2020-04-23 | 11:39 | 49.939
2020-04-23 | 11:39 | 49.939
2020-04-23 | 11:39 | 49.941
2020-04-23 | 11:39 | 49.941
2020-04-23 | 11:39 | 49.942
2020-04-23 | 11:39 | 49.943
2020-04-23 | 11:39 | 49.945
2020-04-23 | 11:39 | 49.948
2020-04-23 | 11:39 | 49.949
2020-04-23 | 11:39 | 49.95
2020-04-23 | 11:39 | 49.95
2020-04-23 | 11:39 | 49.95
2020-04-23 | 11:39 | 49.948
2020-04-23 | 11:39 | 49.948
2020-04-23 | 11:39 | 49.946
2020-04-23 | 11:39 | 49.947
2020-04-23 | 11:39 | 49.946
2020-04-23 | 11:39 | 49.947
2020-04-23 | 11:39 | 49.949
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.948
2020-04-23 | 11:40 | 49.948
2020-04-23 | 11:40 | 49.949
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.948
2020-04-23 | 11:40 | 49.948
2020-04-23 | 11:40 | 49.947
2020-04-23 | 11:40 | 49.945
2020-04-23 | 11:40 | 49.944
2020-04-23 | 11:40 | 49.945
2020-04-23 | 11:40 | 49.943
2020-04-23 | 11:40 | 49.944
2020-04-23 | 11:40 | 49.947
2020-04-23 | 11:40 | 49.949
2020-04-23 | 11:40 | 49.952
2020-04-23 | 11:40 | 49.953
2020-04-23 | 11:40 | 49.955
2020-04-23 | 11:40 | 49.954
2020-04-23 | 11:40 | 49.955
2020-04-23 | 11:40 | 49.956
2020-04-23 | 11:40 | 49.956
2020-04-23 | 11:40 | 49.955
2020-04-23 | 11:40 | 49.954
2020-04-23 | 11:40 | 49.953
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.947
2020-04-23 | 11:40 | 49.946
2020-04-23 | 11:40 | 49.945
2020-04-23 | 11:40 | 49.945
2020-04-23 | 11:40 | 49.944
2020-04-23 | 11:40 | 49.942
2020-04-23 | 11:40 | 49.939
2020-04-23 | 11:40 | 49.941
2020-04-23 | 11:40 | 49.94
2020-04-23 | 11:40 | 49.942
2020-04-23 | 11:40 | 49.943
2020-04-23 | 11:40 | 49.944
2020-04-23 | 11:40 | 49.947
2020-04-23 | 11:40 | 49.95
2020-04-23 | 11:40 | 49.951
2020-04-23 | 11:40 | 49.954
2020-04-23 | 11:40 | 49.957
2020-04-23 | 11:40 | 49.96
2020-04-23 | 11:40 | 49.962
2020-04-23 | 11:40 | 49.964
2020-04-23 | 11:40 | 49.965
2020-04-23 | 11:40 | 49.966
2020-04-23 | 11:40 | 49.966
2020-04-23 | 11:40 | 49.966
2020-04-23 | 11:40 | 49.967
2020-04-23 | 11:40 | 49.967
2020-04-23 | 11:40 | 49.965
2020-04-23 | 11:40 | 49.962
2020-04-23 | 11:40 | 49.959
2020-04-23 | 11:41 | 49.956
2020-04-23 | 11:41 | 49.954
2020-04-23 | 11:41 | 49.953
2020-04-23 | 11:41 | 49.951
2020-04-23 | 11:41 | 49.95
2020-04-23 | 11:41 | 49.951
2020-04-23 | 11:41 | 49.95
2020-04-23 | 11:41 | 49.954
2020-04-23 | 11:41 | 49.955
2020-04-23 | 11:41 | 49.954
2020-04-23 | 11:41 | 49.956
2020-04-23 | 11:41 | 49.959
2020-04-23 | 11:41 | 49.96
2020-04-23 | 11:41 | 49.963
2020-04-23 | 11:41 | 49.964
2020-04-23 | 11:41 | 49.964
2020-04-23 | 11:41 | 49.965
2020-04-23 | 11:41 | 49.966
2020-04-23 | 11:41 | 49.966
2020-04-23 | 11:41 | 49.965
2020-04-23 | 11:41 | 49.963
2020-04-23 | 11:41 | 49.962
2020-04-23 | 11:41 | 49.962
2020-04-23 | 11:41 | 49.962
2020-04-23 | 11:41 | 49.961
2020-04-23 | 11:41 | 49.959
2020-04-23 | 11:41 | 49.96
2020-04-23 | 11:41 | 49.962
2020-04-23 | 11:41 | 49.961
2020-04-23 | 11:41 | 49.959
2020-04-23 | 11:41 | 49.956
2020-04-23 | 11:41 | 49.953
2020-04-23 | 11:41 | 49.952
2020-04-23 | 11:41 | 49.95
2020-04-23 | 11:41 | 49.948
2020-04-23 | 11:41 | 49.946
2020-04-23 | 11:41 | 49.946
2020-04-23 | 11:41 | 49.946
2020-04-23 | 11:41 | 49.943
2020-04-23 | 11:41 | 49.941
2020-04-23 | 11:41 | 49.94
2020-04-23 | 11:41 | 49.942
2020-04-23 | 11:41 | 49.94
2020-04-23 | 11:41 | 49.936
2020-04-23 | 11:41 | 49.934
2020-04-23 | 11:41 | 49.931
2020-04-23 | 11:41 | 49.929
2020-04-23 | 11:41 | 49.929
2020-04-23 | 11:41 | 49.929
2020-04-23 | 11:41 | 49.931
2020-04-23 | 11:41 | 49.935
2020-04-23 | 11:41 | 49.938
2020-04-23 | 11:41 | 49.941
2020-04-23 | 11:41 | 49.943
2020-04-23 | 11:41 | 49.944
2020-04-23 | 11:41 | 49.945
2020-04-23 | 11:41 | 49.946
2020-04-23 | 11:41 | 49.945
2020-04-23 | 11:41 | 49.945
2020-04-23 | 11:41 | 49.944
2020-04-23 | 11:42 | 49.941
2020-04-23 | 11:42 | 49.938
2020-04-23 | 11:42 | 49.935
2020-04-23 | 11:42 | 49.936
2020-04-23 | 11:42 | 49.937
2020-04-23 | 11:42 | 49.938
2020-04-23 | 11:42 | 49.938
2020-04-23 | 11:42 | 49.939
2020-04-23 | 11:42 | 49.941
2020-04-23 | 11:42 | 49.942
2020-04-23 | 11:42 | 49.942
2020-04-23 | 11:42 | 49.941
2020-04-23 | 11:42 | 49.942
2020-04-23 | 11:42 | 49.944
2020-04-23 | 11:42 | 49.946
2020-04-23 | 11:42 | 49.951
2020-04-23 | 11:42 | 49.954
2020-04-23 | 11:42 | 49.956
2020-04-23 | 11:42 | 49.957
2020-04-23 | 11:42 | 49.956
2020-04-23 | 11:42 | 49.956
2020-04-23 | 11:42 | 49.956
2020-04-23 | 11:42 | 49.955
2020-04-23 | 11:42 | 49.954
2020-04-23 | 11:42 | 49.954
2020-04-23 | 11:42 | 49.953
2020-04-23 | 11:42 | 49.951
2020-04-23 | 11:42 | 49.949
2020-04-23 | 11:42 | 49.948
2020-04-23 | 11:42 | 49.948
2020-04-23 | 11:42 | 49.946
2020-04-23 | 11:42 | 49.948
2020-04-23 | 11:42 | 49.95
2020-04-23 | 11:42 | 49.954
2020-04-23 | 11:42 | 49.958
2020-04-23 | 11:42 | 49.96
2020-04-23 | 11:42 | 49.963
2020-04-23 | 11:42 | 49.967
2020-04-23 | 11:42 | 49.969
2020-04-23 | 11:42 | 49.971
2020-04-23 | 11:42 | 49.971
2020-04-23 | 11:42 | 49.969
2020-04-23 | 11:42 | 49.967
2020-04-23 | 11:42 | 49.965
2020-04-23 | 11:42 | 49.962
2020-04-23 | 11:42 | 49.961
2020-04-23 | 11:42 | 49.958
2020-04-23 | 11:42 | 49.956
2020-04-23 | 11:42 | 49.956
2020-04-23 | 11:42 | 49.958
2020-04-23 | 11:42 | 49.958
2020-04-23 | 11:42 | 49.959
2020-04-23 | 11:42 | 49.96
2020-04-23 | 11:42 | 49.963
2020-04-23 | 11:42 | 49.968
2020-04-23 | 11:42 | 49.974
2020-04-23 | 11:42 | 49.978
2020-04-23 | 11:42 | 49.98
2020-04-23 | 11:42 | 49.981
2020-04-23 | 11:42 | 49.981
2020-04-23 | 11:43 | 49.98
2020-04-23 | 11:43 | 49.978
2020-04-23 | 11:43 | 49.976
2020-04-23 | 11:43 | 49.972
2020-04-23 | 11:43 | 49.97
2020-04-23 | 11:43 | 49.968
2020-04-23 | 11:43 | 49.969
2020-04-23 | 11:43 | 49.97
2020-04-23 | 11:43 | 49.969
2020-04-23 | 11:43 | 49.969
2020-04-23 | 11:43 | 49.969
2020-04-23 | 11:43 | 49.968
2020-04-23 | 11:43 | 49.97
2020-04-23 | 11:43 | 49.972
2020-04-23 | 11:43 | 49.976
2020-04-23 | 11:43 | 49.977
2020-04-23 | 11:43 | 49.98
2020-04-23 | 11:43 | 49.979
2020-04-23 | 11:43 | 49.982
2020-04-23 | 11:43 | 49.982
2020-04-23 | 11:43 | 49.982
2020-04-23 | 11:43 | 49.981
2020-04-23 | 11:43 | 49.981
2020-04-23 | 11:43 | 49.981
2020-04-23 | 11:43 | 49.979
2020-04-23 | 11:43 | 49.978
2020-04-23 | 11:43 | 49.976
2020-04-23 | 11:43 | 49.973
2020-04-23 | 11:43 | 49.971
2020-04-23 | 11:43 | 49.97
2020-04-23 | 11:43 | 49.969
2020-04-23 | 11:43 | 49.97
2020-04-23 | 11:43 | 49.972
2020-04-23 | 11:43 | 49.974
2020-04-23 | 11:43 | 49.978
2020-04-23 | 11:43 | 49.983
2020-04-23 | 11:43 | 49.985
2020-04-23 | 11:43 | 49.988
2020-04-23 | 11:43 | 49.99
2020-04-23 | 11:43 | 49.994
2020-04-23 | 11:43 | 49.995
2020-04-23 | 11:43 | 49.998
2020-04-23 | 11:43 | 50.001
2020-04-23 | 11:43 | 50.001

## Event 25042020-1
In UTC
Date | Time | Freq
2020-04-25 | 19:02 | 50.102
2020-04-25 | 19:02 | 50.102
2020-04-25 | 19:02 | 50.103
2020-04-25 | 19:02 | 50.102
2020-04-25 | 19:02 | 50.1
2020-04-25 | 19:02 | 50.099
2020-04-25 | 19:02 | 50.099
2020-04-25 | 19:02 | 50.098
2020-04-25 | 19:02 | 50.099
2020-04-25 | 19:02 | 50.101
2020-04-25 | 19:02 | 50.103
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.107
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.106
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.104
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.105
2020-04-25 | 19:02 | 50.107
2020-04-25 | 19:02 | 50.111
2020-04-25 | 19:02 | 50.112
2020-04-25 | 19:02 | 50.113
2020-04-25 | 19:03 | 50.116
2020-04-25 | 19:03 | 50.117
2020-04-25 | 19:03 | 50.117
2020-04-25 | 19:03 | 50.117
2020-04-25 | 19:03 | 50.116
2020-04-25 | 19:03 | 50.113
2020-04-25 | 19:03 | 50.111
2020-04-25 | 19:03 | 50.109
2020-04-25 | 19:03 | 50.107
2020-04-25 | 19:03 | 50.106
2020-04-25 | 19:03 | 50.106
2020-04-25 | 19:03 | 50.109
2020-04-25 | 19:03 | 50.11
2020-04-25 | 19:03 | 50.111
2020-04-25 | 19:03 | 50.112
2020-04-25 | 19:03 | 50.112
2020-04-25 | 19:03 | 50.113
2020-04-25 | 19:03 | 50.115
2020-04-25 | 19:03 | 50.115
2020-04-25 | 19:03 | 50.115
2020-04-25 | 19:03 | 50.117
2020-04-25 | 19:03 | 50.119
2020-04-25 | 19:03 | 50.116
2020-04-25 | 19:03 | 50.121
2020-04-25 | 19:03 | 50.122
2020-04-25 | 19:03 | 50.123
2020-04-25 | 19:03 | 50.126
2020-04-25 | 19:03 | 50.128
2020-04-25 | 19:03 | 50.133
2020-04-25 | 19:03 | 50.134
2020-04-25 | 19:03 | 50.135
2020-04-25 | 19:03 | 50.137
2020-04-25 | 19:03 | 50.141
2020-04-25 | 19:03 | 50.145
2020-04-25 | 19:03 | 50.145
2020-04-25 | 19:03 | 50.145
2020-04-25 | 19:03 | 50.12
2020-04-25 | 19:03 | 50.084
2020-04-25 | 19:03 | 50.052
2020-04-25 | 19:03 | 50.008
2020-04-25 | 19:03 | 49.965
2020-04-25 | 19:03 | 49.925
2020-04-25 | 19:03 | 49.897
2020-04-25 | 19:03 | 49.874
2020-04-25 | 19:03 | 49.86
2020-04-25 | 19:03 | 49.851
2020-04-25 | 19:03 | 49.845
2020-04-25 | 19:03 | 49.846
2020-04-25 | 19:03 | 49.846
2020-04-25 | 19:03 | 49.849
2020-04-25 | 19:03 | 49.855
2020-04-25 | 19:03 | 49.859
2020-04-25 | 19:03 | 49.866
2020-04-25 | 19:03 | 49.873
2020-04-25 | 19:03 | 49.879
2020-04-25 | 19:03 | 49.885
2020-04-25 | 19:03 | 49.887
2020-04-25 | 19:03 | 49.889
2020-04-25 | 19:03 | 49.89
2020-04-25 | 19:04 | 49.891
2020-04-25 | 19:04 | 49.892
2020-04-25 | 19:04 | 49.892
2020-04-25 | 19:04 | 49.892
2020-04-25 | 19:04 | 49.89
2020-04-25 | 19:04 | 49.887
2020-04-25 | 19:04 | 49.884
2020-04-25 | 19:04 | 49.881
2020-04-25 | 19:04 | 49.88
2020-04-25 | 19:04 | 49.877
2020-04-25 | 19:04 | 49.875
2020-04-25 | 19:04 | 49.876
2020-04-25 | 19:04 | 49.874
2020-04-25 | 19:04 | 49.874
2020-04-25 | 19:04 | 49.873
2020-04-25 | 19:04 | 49.874
2020-04-25 | 19:04 | 49.872
2020-04-25 | 19:04 | 49.871
2020-04-25 | 19:04 | 49.87
2020-04-25 | 19:04 | 49.87
2020-04-25 | 19:04 | 49.869
2020-04-25 | 19:04 | 49.871
2020-04-25 | 19:04 | 49.87
2020-04-25 | 19:04 | 49.87
2020-04-25 | 19:04 | 49.869
2020-04-25 | 19:04 | 49.868
2020-04-25 | 19:04 | 49.865
2020-04-25 | 19:04 | 49.866
2020-04-25 | 19:04 | 49.864
2020-04-25 | 19:04 | 49.863
2020-04-25 | 19:04 | 49.863
2020-04-25 | 19:04 | 49.86
2020-04-25 | 19:04 | 49.86
2020-04-25 | 19:04 | 49.859
2020-04-25 | 19:04 | 49.858
2020-04-25 | 19:04 | 49.854
2020-04-25 | 19:04 | 49.852
2020-04-25 | 19:04 | 49.849
2020-04-25 | 19:04 | 49.845
2020-04-25 | 19:04 | 49.843
2020-04-25 | 19:04 | 49.841
2020-04-25 | 19:04 | 49.841
2020-04-25 | 19:04 | 49.839
2020-04-25 | 19:04 | 49.84
2020-04-25 | 19:04 | 49.839
2020-04-25 | 19:04 | 49.842
2020-04-25 | 19:04 | 49.844
2020-04-25 | 19:04 | 49.846
2020-04-25 | 19:04 | 49.85
2020-04-25 | 19:04 | 49.849
2020-04-25 | 19:04 | 49.85
2020-04-25 | 19:04 | 49.851
2020-04-25 | 19:04 | 49.854
2020-04-25 | 19:04 | 49.856
2020-04-25 | 19:04 | 49.859
2020-04-25 | 19:04 | 49.861
2020-04-25 | 19:04 | 49.863
2020-04-25 | 19:04 | 49.864
2020-04-25 | 19:04 | 49.865
2020-04-25 | 19:04 | 49.868
2020-04-25 | 19:04 | 49.869
2020-04-25 | 19:05 | 49.872
2020-04-25 | 19:05 | 49.874
2020-04-25 | 19:05 | 49.877
2020-04-25 | 19:05 | 49.879
2020-04-25 | 19:05 | 49.883
2020-04-25 | 19:05 | 49.886
2020-04-25 | 19:05 | 49.89
2020-04-25 | 19:05 | 49.89
2020-04-25 | 19:05 | 49.893
2020-04-25 | 19:05 | 49.894
2020-04-25 | 19:05 | 49.898
2020-04-25 | 19:05 | 49.902
2020-04-25 | 19:05 | 49.903
2020-04-25 | 19:05 | 49.904
2020-04-25 | 19:05 | 49.904
2020-04-25 | 19:05 | 49.904
2020-04-25 | 19:05 | 49.903
2020-04-25 | 19:05 | 49.902
2020-04-25 | 19:05 | 49.902
2020-04-25 | 19:05 | 49.903
2020-04-25 | 19:05 | 49.906
2020-04-25 | 19:05 | 49.907
2020-04-25 | 19:05 | 49.909
2020-04-25 | 19:05 | 49.909
2020-04-25 | 19:05 | 49.911
2020-04-25 | 19:05 | 49.911
2020-04-25 | 19:05 | 49.911
2020-04-25 | 19:05 | 49.909
2020-04-25 | 19:05 | 49.908
2020-04-25 | 19:05 | 49.905
2020-04-25 | 19:05 | 49.904
2020-04-25 | 19:05 | 49.904
2020-04-25 | 19:05 | 49.902
2020-04-25 | 19:05 | 49.902
2020-04-25 | 19:05 | 49.902
2020-04-25 | 19:05 | 49.903
2020-04-25 | 19:05 | 49.907
2020-04-25 | 19:05 | 49.912
2020-04-25 | 19:05 | 49.917
2020-04-25 | 19:05 | 49.923
2020-04-25 | 19:05 | 49.928
2020-04-25 | 19:05 | 49.933
2020-04-25 | 19:05 | 49.938
2020-04-25 | 19:05 | 49.941
2020-04-25 | 19:05 | 49.944
2020-04-25 | 19:05 | 49.945
2020-04-25 | 19:05 | 49.947
2020-04-25 | 19:05 | 49.948
2020-04-25 | 19:05 | 49.949
2020-04-25 | 19:05 | 49.954
2020-04-25 | 19:05 | 49.957
2020-04-25 | 19:05 | 49.961
2020-04-25 | 19:05 | 49.964
2020-04-25 | 19:05 | 49.967
2020-04-25 | 19:05 | 49.97
2020-04-25 | 19:05 | 49.974
2020-04-25 | 19:05 | 49.976
2020-04-25 | 19:05 | 49.978
2020-04-25 | 19:05 | 49.98
2020-04-25 | 19:05 | 49.984
2020-04-25 | 19:06 | 49.989
2020-04-25 | 19:06 | 49.993
2020-04-25 | 19:06 | 49.997
2020-04-25 | 19:06 | 50
2020-04-25 | 19:06 | 50.004

## Version Control
Version | Changes
GC0105 System Incidents Report - April 2020 - v1 | First version of April report
GC0105 System Incidents Report - April 2020 - v2 | 1. 'Notes' worksheet updated to include more detail 2. 'Total Loss' field added to 'Report' worksheet 3. Unit for 'System Inertia' field in 'Report' worksheet changed from GVA to GWs, and calculation for each event included in cell.