## Notes
Stability Pathfinder Phase Two
Short circuit level effectiveness factors V2
August 2020
Notes:
1 | Effectiveness factors show how effective a solution will be based on its location to provide short circuit current contribution to the ESO locations of need
2 | Short circuit current contribution is based on RMS transient value
3 | Effectiveness values for sites at voltages 132kV and above not covered by this list will be provided on request
4 | An updated effectiveness list V3 with an updated example of how SCL contribution from remote faults will be considered will be published at the EOI stage
5 | Compared to V1, V2 contains these key changes:
5a | Additional sites added based on RFI requests
5b | Some effectiveness values/sites are updated based on RFI feedback and consideration of network owner developments
Removed ROTI2, NEDE2 and added ROTI4, NEDE4, PEHE4
Updated Longannet and nearby area values
Updated some 132kV nodes near Moffat/ Elvanfoot 400kV
5c | Column L heading updated to 'Moffat/ Elvanfoot 400kV and nearby area' - previoulsy 275kV was stated incorrectly.

## Example
Example:
The following is an example of how effectiveness factors should be considered.
A solution at Arecleoch 132kV which provides 100MVA short circuit level (based on minimum short circuit current value between 5ms and 140ms following a fault at Arecleoch 132kV substation).
The corresponding section of the effectiveness factors table is shown below.
Effectiveness Location
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Loangannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 6% | 6% | 19% | 15% | 7% | 1% | 44% | 17%
This solution will contribute towards the requirement at all 8 locations.
The effective contribution at all 8 locations will be:
Effective MVA
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Loangannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 6 | 6 | 19 | 15 | 7 | 1 | 44 | 17
The solution is most effective at "Mark Hill/ Coylton 275kV and nearby area". It is equivalent to a 44MVA solution built at a site that is 100% effective at this location.
The solution is least effective at "Spittal 275kV". It is equivalent to a 1MVA solution built at a site that is 100% effective at this location.
The solution's contribution to all 8 locations will be considered in the assessment.

## Effectiveness Factors
Effectiveness Location
Substation Location | Substation Code | Voltage Level | Blackhillock 400kV | Eccles 400kV | Hunterston 400kV | Longannet 275kV and nearby area | Peterhead 275kV | Spittal 275kV | Mark Hill/ Coylton 275kV and nearby area | Moffat/ Elvanfoot 400kV and nearby area
Arecleoch | AREC1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 44% | 17%
Auchencrosh | AUCH2 | 275 | 7% | 14% | 43% | 35% | 9% | 1% | 100% | 39%
Auchenwynd | AUCW1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 34% | 16%
Beauly | BEAU1 | 132 | 13% | 2% | 4% | 16% | 14% | 6% | 3% | 4%
Beauly | BEAU2 | 275 | 23% | 5% | 9% | 38% | 24% | 12% | 6% | 9%
Blackhill | BLAH1 | 132 | 6% | 6% | 18% | 16% | 7% | 1% | 43% | 17%
Blackhillock | BLHI1 | 132 | 25% | 3% | 5% | 22% | 25% | 3% | 3% | 5%
Blackhillock | BLHI2 | 275 | 48% | 6% | 10% | 44% | 48% | 5% | 6% | 10%
Blackhillock | BLHI4 | 400 | 100% | 8% | 13% | 60% | 71% | 6% | 8% | 13%
Blacklaw Windfarm | BLKL1 | 132 | 6% | 6% | 10% | 17% | 7% | 1% | 7% | 13%
Blacklaw Extension | BLLX1 | 132 | 6% | 5% | 9% | 11% | 6% | 1% | 7% | 22%
Bonnybridge | BONN1 | 132 | 8% | 6% | 11% | 39% | 10% | 1% | 6% | 10%
Braehead Park | BRAP1 | 132 | 7% | 6% | 20% | 22% | 7% | 1% | 10% | 14%
Branxton | BRNX4 | 400 | 6% | 45% | 12% | 22% | 7% | 1% | 9% | 19%
Busby | BUSB2 | 275 | 8% | 13% | 34% | 48% | 10% | 1% | 20% | 32%
Chapelcross | CHAP1 | 132 | 5% | 3% | 4% | 6% | 6% | 1% | 3% | 15%
Charleston | CHAR1 | 132 | 10% | 4% | 7% | 27% | 14% | 2% | 4% | 6%
Clyde's Mill | CLYM2 | 275 | 9% | 13% | 29% | 55% | 11% | 2% | 18% | 32%
Clyde North | CLYN2 | 275 | 6% | 9% | 14% | 17% | 7% | 1% | 11% | 59%
Clyde South | CLYS2 | 275 | 6% | 9% | 14% | 17% | 7% | 1% | 11% | 58%
Coalburn | COAL1 | 132 | 6% | 6% | 10% | 12% | 6% | 1% | 7% | 31%
Coalburn | COAL4 | 400 | 7% | 17% | 31% | 34% | 9% | 1% | 22% | 100%
Coatbridge | COAT2 | 275 | 8% | 14% | 26% | 49% | 10% | 1% | 17% | 31%
Cockenzie | COCK2 | 275 | 7% | 29% | 12% | 35% | 9% | 1% | 8% | 16%
Coylton | COYL2 | 275 | 7% | 13% | 41% | 34% | 9% | 1% | 100% | 38%
Craigiebuckler | CRAI1 | 132 | 19% | 3% | 5% | 23% | 30% | 2% | 3% | 5%
Crookston | CROO1 | 132 | 6% | 6% | 20% | 21% | 7% | 1% | 10% | 14%
Crystal Rigg | CRYR4 | 400 | 7% | 42% | 13% | 24% | 8% | 1% | 10% | 21%
Currie | CURR2 | 275 | 8% | 24% | 13% | 48% | 10% | 1% | 9% | 17%
Dalmally | DALL2 | 275 | 9% | 10% | 29% | 51% | 11% | 2% | 15% | 22%
Denny North | DENN2 | 275 | 12% | 12% | 24% | 100% | 14% | 2% | 14% | 22%
Denny North | DENN4 | 400 | 17% | 13% | 26% | 100% | 20% | 5% | 15% | 24%
Devol Moor | DEVM4 | 400 | 10% | 17% | 66% | 66% | 13% | 2% | 30% | 42%
Devonside | DEVO1 | 132 | 8% | 5% | 10% | 38% | 10% | 1% | 6% | 10%
Dounreay | DOUN1 | 132 | 10% | 2% | 3% | 12% | 11% | 34% | 2% | 3%
Dounreay | DOUN2 | 275 | 16% | 3% | 6% | 25% | 17% | 78% | 4% | 6%
Eccles | ECCL1 | 132 | 5% | 18% | 4% | 9% | 6% | 1% | 3% | 6%
Eccles | ECCL4 | 400 | 6% | 100% | 10% | 20% | 7% | 1% | 7% | 16%
Easterhouse | EERH2 | 275 | 9% | 14% | 27% | 58% | 11% | 2% | 17% | 31%
East Kilbride South | EKIS2 | 275 | 8% | 13% | 32% | 48% | 10% | 1% | 19% | 33%
Elvanfoot | ELVA2 | 275 | 6% | 9% | 14% | 17% | 7% | 1% | 11% | 58%
Elvanfoot | ELVA4 | 400 | 7% | 14% | 24% | 28% | 8% | 1% | 18% | 100%
Errochty | ERRO1 | 132 | 9% | 4% | 7% | 23% | 11% | 2% | 4% | 6%
Fallago | FALL4 | 400 | 7% | 39% | 15% | 28% | 8% | 1% | 11% | 23%
Fort Augustus | FAUG1 | 132 | 10% | 3% | 5% | 17% | 11% | 4% | 3% | 4%
Fort Augustus | FAUG2 | 275 | 18% | 6% | 11% | 41% | 19% | 8% | 6% | 10%
Fort Augustus | FAUG4 | 400 | 22% | 8% | 15% | 59% | 24% | 10% | 9% | 14%
Fettereso | FETT2 | 275 | 32% | 8% | 12% | 56% | 48% | 3% | 7% | 12%
Foyers | FOYE2 | 275 | 25% | 5% | 9% | 37% | 26% | 10% | 5% | 9%
Fyrish | FYRI1 | 132 | 13% | 2% | 4% | 17% | 13% | 10% | 3% | 4%
Fyrish | FYRI2 | 275 | 21% | 5% | 8% | 33% | 21% | 20% | 5% | 8%
Galashields | GALA1 | 132 | 6% | 17% | 4% | 10% | 6% | 1% | 3% | 6%
Glenglass | GLGL1 | 132 | 6% | 6% | 18% | 15% | 7% | 1% | 42% | 16%
Glenlee | GLLE1 | 132 | 6% | 5% | 14% | 12% | 6% | 1% | 33% | 13%
Glenrothes | GLRO2 | 275 | 15% | 11% | 19% | 82% | 19% | 2% | 11% | 19%
Grangemouth | GRMO2 | 275 | 11% | 17% | 15% | 78% | 14% | 2% | 10% | 18%
Gretna | GRNA1 | 132 | 5% | 4% | 4% | 6% | 6% | 1% | 4% | 22%
Gretna | GRNA4 | 400 | 6% | 12% | 17% | 20% | 7% | 1% | 13% | 100%
Harestanes | HARE1 | 132 | 5% | 4% | 6% | 7% | 6% | 1% | 4% | 21%
Hunterston | HUER1 | 132 | 6% | 6% | 26% | 18% | 7% | 1% | 19% | 16%
Hunterston | HUER4 | 400 | 9% | 19% | 100% | 56% | 11% | 2% | 40% | 50%
Hunterston East | HUNE4 | 400 | 9% | 19% | 100% | 56% | 11% | 2% | 40% | 50%
Inveraray | INVE1 | 132 | 7% | 5% | 14% | 22% | 8% | 1% | 7% | 10%
Inverarnan | INVR2 | 275 | 9% | 10% | 29% | 51% | 11% | 2% | 15% | 22%
Kaimes | KAIM2 | 275 | 8% | 25% | 13% | 43% | 10% | 1% | 9% | 17%
Keith | KEIT1 | 132 | 20% | 3% | 4% | 19% | 21% | 3% | 3% | 4%
Kendoon | KEOO1 | 132 | 6% | 5% | 14% | 13% | 6% | 1% | 33% | 13%
Killin | KIIN1 | 132 | 7% | 3% | 9% | 18% | 8% | 1% | 5% | 7%
Kilgalleoch | KILG2 | 275 | 7% | 13% | 42% | 35% | 9% | 1% | 100% | 39%
Kilmarnock South | KILS2 | 275 | 7% | 13% | 41% | 34% | 9% | 1% | 73% | 38%
Kilmarnock South | KILS4 | 400 | 9% | 19% | 59% | 50% | 10% | 1% | 53% | 55%
Kilmarnock Town | KILT2 | 275 | 7% | 13% | 41% | 34% | 9% | 1% | 72% | 38%
Kilwinning | KILW1 | 132 | 6% | 6% | 24% | 17% | 7% | 1% | 20% | 16%
Kincardine | KINC2 | 275 | 12% | 15% | 17% | 100% | 15% | 2% | 11% | 19%
Kintore | KINT2 | 275 | 38% | 7% | 11% | 50% | 59% | 4% | 7% | 11%
Knocknagael | KNOC2 | 275 | 25% | 5% | 9% | 38% | 26% | 11% | 6% | 9%
Lambhill | LAMB2 | 275 | 10% | 12% | 29% | 68% | 13% | 2% | 16% | 24%
Longannet | LOAN2 | 275 | 12% | 13% | 23% | 100% | 15% | 2% | 13% | 23%
Loch Buidhe | LOCB2 | 275 | 19% | 4% | 7% | 30% | 20% | 32% | 4% | 7%
Mark Hill | MAHI2 | 275 | 7% | 14% | 43% | 35% | 9% | 1% | 100% | 39%
Maybole | MAYB1 | 132 | 6% | 6% | 19% | 16% | 7% | 1% | 34% | 16%
Melgrave | MELG1 | 132 | 11% | 3% | 6% | 22% | 11% | 4% | 4% | 6%
Melgrave | MELG4 | 400 | 21% | 9% | 16% | 63% | 24% | 9% | 9% | 16%
Moffat | MOFF1 | 132 | 5% | 4% | 6% | 8% | 6% | 1% | 4% | 30%
Moffat | MOFF4 | 400 | 6% | 12% | 18% | 21% | 7% | 1% | 13% | 100%
Mossmorran | MOSM2 | 275 | 13% | 12% | 20% | 100% | 17% | 2% | 12% | 20%
Mybster | MYBS1 | 132 | 10% | 2% | 3% | 11% | 10% | 44% | 2% | 3%
Newarthill | NEAR2 | 275 | 8% | 14% | 26% | 49% | 10% | 1% | 17% | 32%
New Cumnock | NECU2 | 275 | 7% | 13% | 41% | 33% | 9% | 1% | 100% | 37%
New Deer | NEDE4 | 400 | 67% | 3% | 6% | 21% | 90% | 1% | 3% | 4%
Neilston | NEIL1 | 132 | 7% | 6% | 21% | 22% | 7% | 1% | 10% | 15%
Neilston | NEIL2 | 275 | 8% | 13% | 41% | 48% | 10% | 1% | 21% | 32%
Neilston | NEIL4 | 400 | 9% | 18% | 83% | 58% | 11% | 2% | 36% | 48%
Newton Stewart | NETS1 | 132 | 6% | 4% | 13% | 12% | 6% | 1% | 30% | 12%
Partick | PART1 | 132 | 7% | 5% | 14% | 25% | 8% | 1% | 7% | 11%
Peterhead | PEHE1 | 132 | 17% | 3% | 4% | 18% | 39% | 2% | 3% | 4%
Peterhead | PEHE2 | 275 | 37% | 6% | 9% | 12% | 100% | 3% | 6% | 9%
Peterhead | PEHE4 | 400 | 61% | 3% | 6% | 20% | 100% | 1% | 3% | 4%
Redhouse | REDH1 | 132 | 9% | 5% | 10% | 39% | 11% | 1% | 6% | 9%
Rothienorman | ROTI4 | 400 | 75% | 3% | 6% | 23% | 79% | 1% | 3% | 5%
Shin | SHIN1 | 132 | 11% | 2% | 3% | 13% | 11% | 13% | 2% | 3%
Sloy | SLOY1 | 132 | 7% | 5% | 13% | 23% | 8% | 1% | 7% | 10%
Smeaton | SMEA2 | 275 | 8% | 27% | 12% | 37% | 9% | 1% | 9% | 17%
Spittal | SPIT1 | 132 | 10% | 2% | 3% | 12% | 10% | 43% | 2% | 3%
Spittal | SPIT2 | 275 | 16% | 3% | 6% | 24% | 16% | 100% | 4% | 5%
Strathaven | STHA2 | 275 | 8% | 13% | 31% | 50% | 10% | 1% | 19% | 33%
Strathaven | STHA4 | 400 | 8% | 20% | 38% | 47% | 10% | 1% | 30% | 59%
Tealing | TEAL1 | 132 | 11% | 4% | 7% | 27% | 14% | 2% | 4% | 6%
Tealing | TEAL2 | 275 | 20% | 10% | 15% | 71% | 28% | 3% | 9% | 16%
Thurso | THSO2 | 275 | 16% | 3% | 6% | 24% | 17% | 89% | 4% | 5%
Tongland | TONG1 | 132 | 6% | 4% | 12% | 11% | 6% | 1% | 28% | 11%
Torness | TORN4 | 400 | 6% | 45% | 12% | 22% | 7% | 1% | 9% | 19%
Tummel | TUMM2 | 275 | 14% | 8% | 15% | 54% | 17% | 4% | 9% | 14%
Westfield | WFIE1 | 132 | 9% | 6% | 10% | 40% | 11% | 1% | 6% | 10%
Westfield | WFIE2 | 275 | 14% | 12% | 20% | 100% | 18% | 2% | 12% | 20%
Wishaw (Gowkthrapple) | WISH4 | 400 | 8% | 22% | 35% | 48% | 10% | 1% | 26% | 52%
Windyhill | WIYH1 | 132 | 7% | 5% | 14% | 26% | 8% | 1% | 8% | 11%
Windyhill | WIYH2 | 275 | 10% | 12% | 33% | 60% | 12% | 2% | 17% | 25%
Whitelee | WLEE2 | 275 | 8% | 13% | 32% | 48% | 10% | 1% | 19% | 33%
Whitelee Extension | WLEX2 | 275 | 8% | 13% | 32% | 48% | 10% | 1% | 19% | 33%