## Version Control
Version | Changes
GC0105 System Incidents Report - May 2020 - v1 | First version of May report

## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | Total loss | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20200501-1 | Loss of Embedded Generation |  | 2020-05-01 | 13:54 | 457 | Refer to tab 'Event 20200501-1' | 50.164 | 49.933 | Awaiting data | 457 | 457 | N/A | Bolney - Ninfield 400kV circuit | 91% 100ms transient | Awaiting data
Event 20200510-1 | Loss of SCCL-1 |  | 2020-05-10 | 15:59 | N/A | Refer to tab 'Event 20200510-1' | 49.912 | 49.725 | -0.073 | 350 | 350 | N/A | N/A | N/A | 119.6521
Event 20200524-1 | Loss of DINO-5 and DINO-6 |  | 2020-05-24 | 22:07 | N/A | Refer to tab 'Event 20200524-1' | 50.03 | 49.73 | -0.054 | DINO-5 300, DINO6 300 | 600 | N/A | N/A | N/A | 277.9444
Event 20200527-1 | Loss of GRAI-8 |  | 2020-05-27 | 14:12 | N/A | Refer to tab 'Event 20200527-1' | 49.94 | 49.75 | -0.06 | 425 | 425 | N/A | N/A | N/A | 176.8708
Event 20200528-1 | Loss of CNQPS-1 |  | 2020-05-28 | 14:11 | N/A | Refer to tab 'Event 20200528-1' | 50.03 | 49.859 | -0.057 | 320 | 320 | N/A | N/A | N/A | 140.4351

## Event 20200501-1
In UTC
Date | Time | Freq
2020-05-01 | 12:54 | 50.19
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.186
2020-05-01 | 12:54 | 50.185
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.188
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.186
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.186
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.187
2020-05-01 | 12:54 | 50.186
2020-05-01 | 12:54 | 50.185
2020-05-01 | 12:54 | 50.183
2020-05-01 | 12:54 | 50.181
2020-05-01 | 12:54 | 50.177
2020-05-01 | 12:54 | 50.171
2020-05-01 | 12:54 | 50.166
2020-05-01 | 12:54 | 50.163
2020-05-01 | 12:54 | 50.162
2020-05-01 | 12:54 | 50.162
2020-05-01 | 12:54 | 50.163
2020-05-01 | 12:54 | 50.166
2020-05-01 | 12:54 | 50.169
2020-05-01 | 12:54 | 50.172
2020-05-01 | 12:54 | 50.175
2020-05-01 | 12:54 | 50.176
2020-05-01 | 12:54 | 50.18
2020-05-01 | 12:55 | 50.178
2020-05-01 | 12:55 | 50.172
2020-05-01 | 12:55 | 50.169
2020-05-01 | 12:55 | 50.165
2020-05-01 | 12:55 | 50.163
2020-05-01 | 12:55 | 50.162
2020-05-01 | 12:55 | 50.162
2020-05-01 | 12:55 | 50.163
2020-05-01 | 12:55 | 50.165
2020-05-01 | 12:55 | 50.165
2020-05-01 | 12:55 | 50.163
2020-05-01 | 12:55 | 50.163
2020-05-01 | 12:55 | 50.164
2020-05-01 | 12:55 | 50.066
2020-05-01 | 12:55 | 49.997
2020-05-01 | 12:55 | 49.958
2020-05-01 | 12:55 | 49.937
2020-05-01 | 12:55 | 49.933
2020-05-01 | 12:55 | 49.936
2020-05-01 | 12:55 | 49.944
2020-05-01 | 12:55 | 49.957
2020-05-01 | 12:55 | 49.969
2020-05-01 | 12:55 | 49.983
2020-05-01 | 12:55 | 49.998
2020-05-01 | 12:55 | 50.011
2020-05-01 | 12:55 | 50.024
2020-05-01 | 12:55 | 50.036
2020-05-01 | 12:55 | 50.043
2020-05-01 | 12:55 | 50.045
2020-05-01 | 12:55 | 50.046
2020-05-01 | 12:55 | 50.046
2020-05-01 | 12:55 | 50.046
2020-05-01 | 12:55 | 50.048
2020-05-01 | 12:55 | 50.05
2020-05-01 | 12:55 | 50.05
2020-05-01 | 12:55 | 50.051
2020-05-01 | 12:55 | 50.054
2020-05-01 | 12:55 | 50.058
2020-05-01 | 12:55 | 50.061
2020-05-01 | 12:55 | 50.064
2020-05-01 | 12:55 | 50.067
2020-05-01 | 12:55 | 50.067
2020-05-01 | 12:55 | 50.067
2020-05-01 | 12:55 | 50.066
2020-05-01 | 12:55 | 50.063
2020-05-01 | 12:55 | 50.062
2020-05-01 | 12:55 | 50.061
2020-05-01 | 12:55 | 50.062
2020-05-01 | 12:55 | 50.062
2020-05-01 | 12:55 | 50.059
2020-05-01 | 12:55 | 50.059
2020-05-01 | 12:55 | 50.059
2020-05-01 | 12:55 | 50.058
2020-05-01 | 12:55 | 50.057
2020-05-01 | 12:55 | 50.059
2020-05-01 | 12:55 | 50.055
2020-05-01 | 12:55 | 50.052
2020-05-01 | 12:55 | 50.052
2020-05-01 | 12:55 | 50.051
2020-05-01 | 12:56 | 50.052
2020-05-01 | 12:56 | 50.054
2020-05-01 | 12:56 | 50.056
2020-05-01 | 12:56 | 50.057
2020-05-01 | 12:56 | 50.056
2020-05-01 | 12:56 | 50.058
2020-05-01 | 12:56 | 50.058
2020-05-01 | 12:56 | 50.058
2020-05-01 | 12:56 | 50.056
2020-05-01 | 12:56 | 50.055
2020-05-01 | 12:56 | 50.057
2020-05-01 | 12:56 | 50.054
2020-05-01 | 12:56 | 50.054
2020-05-01 | 12:56 | 50.054
2020-05-01 | 12:56 | 50.056
2020-05-01 | 12:56 | 50.058
2020-05-01 | 12:56 | 50.059
2020-05-01 | 12:56 | 50.06
2020-05-01 | 12:56 | 50.063
2020-05-01 | 12:56 | 50.067
2020-05-01 | 12:56 | 50.067
2020-05-01 | 12:56 | 50.067
2020-05-01 | 12:56 | 50.068
2020-05-01 | 12:56 | 50.067
2020-05-01 | 12:56 | 50.064
2020-05-01 | 12:56 | 50.058
2020-05-01 | 12:56 | 50.052
2020-05-01 | 12:56 | 50.048
2020-05-01 | 12:56 | 50.044
2020-05-01 | 12:56 | 50.042
2020-05-01 | 12:56 | 50.039
2020-05-01 | 12:56 | 50.038
2020-05-01 | 12:56 | 50.036
2020-05-01 | 12:56 | 50.04
2020-05-01 | 12:56 | 50.038
2020-05-01 | 12:56 | 50.038
2020-05-01 | 12:56 | 50.037
2020-05-01 | 12:56 | 50.034
2020-05-01 | 12:56 | 50.033
2020-05-01 | 12:56 | 50.033
2020-05-01 | 12:56 | 50.033
2020-05-01 | 12:56 | 50.033
2020-05-01 | 12:56 | 50.031
2020-05-01 | 12:56 | 50.031
2020-05-01 | 12:56 | 50.029
2020-05-01 | 12:56 | 50.028
2020-05-01 | 12:56 | 50.026
2020-05-01 | 12:56 | 50.024
2020-05-01 | 12:56 | 50.025
2020-05-01 | 12:56 | 50.023
2020-05-01 | 12:56 | 50.022
2020-05-01 | 12:56 | 50.019
2020-05-01 | 12:56 | 50.015
2020-05-01 | 12:56 | 50.013
2020-05-01 | 12:56 | 50.009
2020-05-01 | 12:56 | 50.008
2020-05-01 | 12:56 | 50.011
2020-05-01 | 12:56 | 50.014
2020-05-01 | 12:56 | 50.017
2020-05-01 | 12:56 | 50.018
2020-05-01 | 12:56 | 50.019
2020-05-01 | 12:57 | 50.018
2020-05-01 | 12:57 | 50.018
2020-05-01 | 12:57 | 50.016
2020-05-01 | 12:57 | 50.014
2020-05-01 | 12:57 | 50.012
2020-05-01 | 12:57 | 50.011
2020-05-01 | 12:57 | 50.011
2020-05-01 | 12:57 | 50.01
2020-05-01 | 12:57 | 50.015
2020-05-01 | 12:57 | 50.02
2020-05-01 | 12:57 | 50.022
2020-05-01 | 12:57 | 50.023
2020-05-01 | 12:57 | 50.024
2020-05-01 | 12:57 | 50.025
2020-05-01 | 12:57 | 50.025
2020-05-01 | 12:57 | 50.025
2020-05-01 | 12:57 | 50.025
2020-05-01 | 12:57 | 50.026
2020-05-01 | 12:57 | 50.027
2020-05-01 | 12:57 | 50.028
2020-05-01 | 12:57 | 50.028
2020-05-01 | 12:57 | 50.027
2020-05-01 | 12:57 | 50.026
2020-05-01 | 12:57 | 50.025
2020-05-01 | 12:57 | 50.024
2020-05-01 | 12:57 | 50.021
2020-05-01 | 12:57 | 50.021
2020-05-01 | 12:57 | 50.021
2020-05-01 | 12:57 | 50.023
2020-05-01 | 12:57 | 50.026
2020-05-01 | 12:57 | 50.028
2020-05-01 | 12:57 | 50.031
2020-05-01 | 12:57 | 50.032
2020-05-01 | 12:57 | 50.034
2020-05-01 | 12:57 | 50.036
2020-05-01 | 12:57 | 50.036
2020-05-01 | 12:57 | 50.036
2020-05-01 | 12:57 | 50.033
2020-05-01 | 12:57 | 50.03
2020-05-01 | 12:57 | 50.026
2020-05-01 | 12:57 | 50.023
2020-05-01 | 12:57 | 50.021
2020-05-01 | 12:57 | 50.02
2020-05-01 | 12:57 | 50.023
2020-05-01 | 12:57 | 50.023
2020-05-01 | 12:57 | 50.025
2020-05-01 | 12:57 | 50.026
2020-05-01 | 12:57 | 50.03
2020-05-01 | 12:57 | 50.034
2020-05-01 | 12:57 | 50.041
2020-05-01 | 12:57 | 50.044
2020-05-01 | 12:57 | 50.052
2020-05-01 | 12:57 | 50.056
2020-05-01 | 12:57 | 50.057
2020-05-01 | 12:57 | 50.058
2020-05-01 | 12:57 | 50.057
2020-05-01 | 12:57 | 50.058
2020-05-01 | 12:57 | 50.057
2020-05-01 | 12:57 | 50.054
2020-05-01 | 12:58 | 50.051
2020-05-01 | 12:58 | 50.046
2020-05-01 | 12:58 | 50.042
2020-05-01 | 12:58 | 50.037
2020-05-01 | 12:58 | 50.032
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.028
2020-05-01 | 12:58 | 50.027
2020-05-01 | 12:58 | 50.026
2020-05-01 | 12:58 | 50.027
2020-05-01 | 12:58 | 50.026
2020-05-01 | 12:58 | 50.027
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.031
2020-05-01 | 12:58 | 50.032
2020-05-01 | 12:58 | 50.032
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.03
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.032
2020-05-01 | 12:58 | 50.033
2020-05-01 | 12:58 | 50.033
2020-05-01 | 12:58 | 50.034
2020-05-01 | 12:58 | 50.034
2020-05-01 | 12:58 | 50.035
2020-05-01 | 12:58 | 50.036
2020-05-01 | 12:58 | 50.037
2020-05-01 | 12:58 | 50.037
2020-05-01 | 12:58 | 50.035
2020-05-01 | 12:58 | 50.033
2020-05-01 | 12:58 | 50.031
2020-05-01 | 12:58 | 50.028
2020-05-01 | 12:58 | 50.027
2020-05-01 | 12:58 | 50.026
2020-05-01 | 12:58 | 50.027
2020-05-01 | 12:58 | 50.024
2020-05-01 | 12:58 | 50.023
2020-05-01 | 12:58 | 50.027
2020-05-01 | 12:58 | 50.029
2020-05-01 | 12:58 | 50.034
2020-05-01 | 12:58 | 50.04
2020-05-01 | 12:58 | 50.042
2020-05-01 | 12:58 | 50.045
2020-05-01 | 12:58 | 50.046
2020-05-01 | 12:58 | 50.046
2020-05-01 | 12:58 | 50.048
2020-05-01 | 12:58 | 50.049
2020-05-01 | 12:58 | 50.049
2020-05-01 | 12:58 | 50.049
2020-05-01 | 12:58 | 50.053
2020-05-01 | 12:58 | 50.054
2020-05-01 | 12:58 | 50.054
2020-05-01 | 12:58 | 50.054
2020-05-01 | 12:58 | 50.052
2020-05-01 | 12:58 | 50.051
2020-05-01 | 12:58 | 50.052
2020-05-01 | 12:58 | 50.053
2020-05-01 | 12:58 | 50.053
2020-05-01 | 12:58 | 50.053
2020-05-01 | 12:59 | 50.052
2020-05-01 | 12:59 | 50.052
2020-05-01 | 12:59 | 50.051
2020-05-01 | 12:59 | 50.05
2020-05-01 | 12:59 | 50.049
2020-05-01 | 12:59 | 50.05
2020-05-01 | 12:59 | 50.05
2020-05-01 | 12:59 | 50.05
2020-05-01 | 12:59 | 50.053
2020-05-01 | 12:59 | 50.057
2020-05-01 | 12:59 | 50.06
2020-05-01 | 12:59 | 50.061
2020-05-01 | 12:59 | 50.06
2020-05-01 | 12:59 | 50.06
2020-05-01 | 12:59 | 50.059
2020-05-01 | 12:59 | 50.058
2020-05-01 | 12:59 | 50.056
2020-05-01 | 12:59 | 50.051
2020-05-01 | 12:59 | 50.046
2020-05-01 | 12:59 | 50.042
2020-05-01 | 12:59 | 50.036
2020-05-01 | 12:59 | 50.036
2020-05-01 | 12:59 | 50.035
2020-05-01 | 12:59 | 50.037
2020-05-01 | 12:59 | 50.038
2020-05-01 | 12:59 | 50.039
2020-05-01 | 12:59 | 50.039
2020-05-01 | 12:59 | 50.04
2020-05-01 | 12:59 | 50.043
2020-05-01 | 12:59 | 50.045
2020-05-01 | 12:59 | 50.043
2020-05-01 | 12:59 | 50.041
2020-05-01 | 12:59 | 50.04
2020-05-01 | 12:59 | 50.041
2020-05-01 | 12:59 | 50.044
2020-05-01 | 12:59 | 50.044
2020-05-01 | 12:59 | 50.044
2020-05-01 | 12:59 | 50.045
2020-05-01 | 12:59 | 50.045
2020-05-01 | 12:59 | 50.046
2020-05-01 | 12:59 | 50.047
2020-05-01 | 12:59 | 50.05
2020-05-01 | 12:59 | 50.052
2020-05-01 | 12:59 | 50.057
2020-05-01 | 12:59 | 50.059
2020-05-01 | 12:59 | 50.059
2020-05-01 | 12:59 | 50.05
2020-05-01 | 12:59 | 50.041
2020-05-01 | 12:59 | 50.033
2020-05-01 | 12:59 | 50.031
2020-05-01 | 12:59 | 50.03
2020-05-01 | 12:59 | 50.03
2020-05-01 | 12:59 | 50.031
2020-05-01 | 12:59 | 50.033
2020-05-01 | 12:59 | 50.035
2020-05-01 | 12:59 | 50.035
2020-05-01 | 12:59 | 50.039
2020-05-01 | 12:59 | 50.04
2020-05-01 | 12:59 | 50.043
2020-05-01 | 13:00 | 50.045
2020-05-01 | 13:00 | 50.046
2020-05-01 | 13:00 | 50.045
2020-05-01 | 13:00 | 50.043
2020-05-01 | 13:00 | 50.042
2020-05-01 | 13:00 | 50.04
2020-05-01 | 13:00 | 50.038
2020-05-01 | 13:00 | 50.039
2020-05-01 | 13:00 | 50.04
2020-05-01 | 13:00 | 50.044
2020-05-01 | 13:00 | 50.046
2020-05-01 | 13:00 | 50.049
2020-05-01 | 13:00 | 50.051
2020-05-01 | 13:00 | 50.051
2020-05-01 | 13:00 | 50.053
2020-05-01 | 13:00 | 50.052
2020-05-01 | 13:00 | 50.052
2020-05-01 | 13:00 | 50.051
2020-05-01 | 13:00 | 50.051
2020-05-01 | 13:00 | 50.049
2020-05-01 | 13:00 | 50.051
2020-05-01 | 13:00 | 50.053
2020-05-01 | 13:00 | 50.053
2020-05-01 | 13:00 | 50.054
2020-05-01 | 13:00 | 50.053
2020-05-01 | 13:00 | 50.053
2020-05-01 | 13:00 | 50.053
2020-05-01 | 13:00 | 50.052
2020-05-01 | 13:00 | 50.05
2020-05-01 | 13:00 | 50.047
2020-05-01 | 13:00 | 50.046
2020-05-01 | 13:00 | 50.038
2020-05-01 | 13:00 | 50.032
2020-05-01 | 13:00 | 50.023
2020-05-01 | 13:00 | 50.02
2020-05-01 | 13:00 | 50.016
2020-05-01 | 13:00 | 50.012
2020-05-01 | 13:00 | 50.01
2020-05-01 | 13:00 | 50.004
2020-05-01 | 13:00 | 49.998
2020-05-01 | 13:00 | 49.995
2020-05-01 | 13:00 | 49.992
2020-05-01 | 13:00 | 49.991
2020-05-01 | 13:00 | 49.992
2020-05-01 | 13:00 | 49.992
2020-05-01 | 13:00 | 49.991

## Event 20200510-1
In UTC
Date | Time | Freq
2020-05-10 | 14:58 | 49.954
2020-05-10 | 14:58 | 49.95
2020-05-10 | 14:58 | 49.946
2020-05-10 | 14:58 | 49.945
2020-05-10 | 14:58 | 49.948
2020-05-10 | 14:58 | 49.951
2020-05-10 | 14:58 | 49.953
2020-05-10 | 14:58 | 49.953
2020-05-10 | 14:58 | 49.953
2020-05-10 | 14:58 | 49.952
2020-05-10 | 14:58 | 49.951
2020-05-10 | 14:58 | 49.948
2020-05-10 | 14:58 | 49.944
2020-05-10 | 14:58 | 49.942
2020-05-10 | 14:58 | 49.941
2020-05-10 | 14:58 | 49.939
2020-05-10 | 14:58 | 49.936
2020-05-10 | 14:58 | 49.934
2020-05-10 | 14:58 | 49.935
2020-05-10 | 14:58 | 49.942
2020-05-10 | 14:58 | 49.947
2020-05-10 | 14:58 | 49.95
2020-05-10 | 14:58 | 49.952
2020-05-10 | 14:58 | 49.955
2020-05-10 | 14:58 | 49.955
2020-05-10 | 14:58 | 49.955
2020-05-10 | 14:58 | 49.955
2020-05-10 | 14:58 | 49.955
2020-05-10 | 14:58 | 49.953
2020-05-10 | 14:58 | 49.951
2020-05-10 | 14:58 | 49.947
2020-05-10 | 14:59 | 49.944
2020-05-10 | 14:59 | 49.941
2020-05-10 | 14:59 | 49.938
2020-05-10 | 14:59 | 49.934
2020-05-10 | 14:59 | 49.931
2020-05-10 | 14:59 | 49.929
2020-05-10 | 14:59 | 49.931
2020-05-10 | 14:59 | 49.935
2020-05-10 | 14:59 | 49.937
2020-05-10 | 14:59 | 49.938
2020-05-10 | 14:59 | 49.937
2020-05-10 | 14:59 | 49.938
2020-05-10 | 14:59 | 49.935
2020-05-10 | 14:59 | 49.935
2020-05-10 | 14:59 | 49.934
2020-05-10 | 14:59 | 49.935
2020-05-10 | 14:59 | 49.934
2020-05-10 | 14:59 | 49.933
2020-05-10 | 14:59 | 49.931
2020-05-10 | 14:59 | 49.931
2020-05-10 | 14:59 | 49.929
2020-05-10 | 14:59 | 49.928
2020-05-10 | 14:59 | 49.925
2020-05-10 | 14:59 | 49.925
2020-05-10 | 14:59 | 49.923
2020-05-10 | 14:59 | 49.921
2020-05-10 | 14:59 | 49.918
2020-05-10 | 14:59 | 49.916
2020-05-10 | 14:59 | 49.913
2020-05-10 | 14:59 | 49.911
2020-05-10 | 14:59 | 49.912
2020-05-10 | 14:59 | 49.86
2020-05-10 | 14:59 | 49.82
2020-05-10 | 14:59 | 49.798
2020-05-10 | 14:59 | 49.789
2020-05-10 | 14:59 | 49.787
2020-05-10 | 14:59 | 49.787
2020-05-10 | 14:59 | 49.791
2020-05-10 | 14:59 | 49.803
2020-05-10 | 14:59 | 49.813
2020-05-10 | 14:59 | 49.818
2020-05-10 | 14:59 | 49.819
2020-05-10 | 14:59 | 49.818
2020-05-10 | 14:59 | 49.817
2020-05-10 | 14:59 | 49.812
2020-05-10 | 14:59 | 49.811
2020-05-10 | 14:59 | 49.813
2020-05-10 | 14:59 | 49.813
2020-05-10 | 14:59 | 49.816
2020-05-10 | 14:59 | 49.816
2020-05-10 | 14:59 | 49.82
2020-05-10 | 14:59 | 49.824
2020-05-10 | 14:59 | 49.823
2020-05-10 | 14:59 | 49.824
2020-05-10 | 14:59 | 49.825
2020-05-10 | 14:59 | 49.827
2020-05-10 | 14:59 | 49.827
2020-05-10 | 14:59 | 49.825
2020-05-10 | 14:59 | 49.822
2020-05-10 | 15:00 | 49.817
2020-05-10 | 15:00 | 49.81
2020-05-10 | 15:00 | 49.804
2020-05-10 | 15:00 | 49.798
2020-05-10 | 15:00 | 49.794
2020-05-10 | 15:00 | 49.79
2020-05-10 | 15:00 | 49.788
2020-05-10 | 15:00 | 49.786
2020-05-10 | 15:00 | 49.784
2020-05-10 | 15:00 | 49.78
2020-05-10 | 15:00 | 49.778
2020-05-10 | 15:00 | 49.776
2020-05-10 | 15:00 | 49.773
2020-05-10 | 15:00 | 49.772
2020-05-10 | 15:00 | 49.772
2020-05-10 | 15:00 | 49.772
2020-05-10 | 15:00 | 49.772
2020-05-10 | 15:00 | 49.772
2020-05-10 | 15:00 | 49.773
2020-05-10 | 15:00 | 49.771
2020-05-10 | 15:00 | 49.765
2020-05-10 | 15:00 | 49.76
2020-05-10 | 15:00 | 49.755
2020-05-10 | 15:00 | 49.752
2020-05-10 | 15:00 | 49.752
2020-05-10 | 15:00 | 49.754
2020-05-10 | 15:00 | 49.754
2020-05-10 | 15:00 | 49.756
2020-05-10 | 15:00 | 49.757
2020-05-10 | 15:00 | 49.758
2020-05-10 | 15:00 | 49.756
2020-05-10 | 15:00 | 49.753
2020-05-10 | 15:00 | 49.749
2020-05-10 | 15:00 | 49.744
2020-05-10 | 15:00 | 49.74
2020-05-10 | 15:00 | 49.734
2020-05-10 | 15:00 | 49.731
2020-05-10 | 15:00 | 49.729
2020-05-10 | 15:00 | 49.726
2020-05-10 | 15:00 | 49.725
2020-05-10 | 15:00 | 49.726
2020-05-10 | 15:00 | 49.726
2020-05-10 | 15:00 | 49.727
2020-05-10 | 15:00 | 49.728
2020-05-10 | 15:00 | 49.729
2020-05-10 | 15:00 | 49.734
2020-05-10 | 15:00 | 49.737
2020-05-10 | 15:00 | 49.736
2020-05-10 | 15:00 | 49.737
2020-05-10 | 15:00 | 49.739
2020-05-10 | 15:00 | 49.741
2020-05-10 | 15:00 | 49.748
2020-05-10 | 15:00 | 49.761
2020-05-10 | 15:00 | 49.769
2020-05-10 | 15:00 | 49.778
2020-05-10 | 15:00 | 49.783
2020-05-10 | 15:00 | 49.786
2020-05-10 | 15:00 | 49.789
2020-05-10 | 15:00 | 49.794
2020-05-10 | 15:00 | 49.798
2020-05-10 | 15:00 | 49.801
2020-05-10 | 15:01 | 49.803
2020-05-10 | 15:01 | 49.808
2020-05-10 | 15:01 | 49.814
2020-05-10 | 15:01 | 49.816
2020-05-10 | 15:01 | 49.818
2020-05-10 | 15:01 | 49.818
2020-05-10 | 15:01 | 49.818
2020-05-10 | 15:01 | 49.819
2020-05-10 | 15:01 | 49.822
2020-05-10 | 15:01 | 49.825
2020-05-10 | 15:01 | 49.825
2020-05-10 | 15:01 | 49.828
2020-05-10 | 15:01 | 49.828
2020-05-10 | 15:01 | 49.828
2020-05-10 | 15:01 | 49.827
2020-05-10 | 15:01 | 49.827
2020-05-10 | 15:01 | 49.827
2020-05-10 | 15:01 | 49.833
2020-05-10 | 15:01 | 49.837
2020-05-10 | 15:01 | 49.843
2020-05-10 | 15:01 | 49.848
2020-05-10 | 15:01 | 49.858
2020-05-10 | 15:01 | 49.867
2020-05-10 | 15:01 | 49.878
2020-05-10 | 15:01 | 49.888
2020-05-10 | 15:01 | 49.898
2020-05-10 | 15:01 | 49.907
2020-05-10 | 15:01 | 49.912
2020-05-10 | 15:01 | 49.916
2020-05-10 | 15:01 | 49.917
2020-05-10 | 15:01 | 49.918
2020-05-10 | 15:01 | 49.92
2020-05-10 | 15:01 | 49.919
2020-05-10 | 15:01 | 49.919
2020-05-10 | 15:01 | 49.919
2020-05-10 | 15:01 | 49.92
2020-05-10 | 15:01 | 49.921
2020-05-10 | 15:01 | 49.924
2020-05-10 | 15:01 | 49.929
2020-05-10 | 15:01 | 49.931
2020-05-10 | 15:01 | 49.935
2020-05-10 | 15:01 | 49.938
2020-05-10 | 15:01 | 49.941
2020-05-10 | 15:01 | 49.941
2020-05-10 | 15:01 | 49.942
2020-05-10 | 15:01 | 49.942
2020-05-10 | 15:01 | 49.943
2020-05-10 | 15:01 | 49.945
2020-05-10 | 15:01 | 49.944
2020-05-10 | 15:01 | 49.943
2020-05-10 | 15:01 | 49.946
2020-05-10 | 15:01 | 49.948
2020-05-10 | 15:01 | 49.951
2020-05-10 | 15:01 | 49.954
2020-05-10 | 15:01 | 49.956
2020-05-10 | 15:01 | 49.957
2020-05-10 | 15:01 | 49.959
2020-05-10 | 15:01 | 49.961
2020-05-10 | 15:01 | 49.965
2020-05-10 | 15:02 | 49.961
2020-05-10 | 15:02 | 49.956
2020-05-10 | 15:02 | 49.952
2020-05-10 | 15:02 | 49.954
2020-05-10 | 15:02 | 49.955
2020-05-10 | 15:02 | 49.955
2020-05-10 | 15:02 | 49.956
2020-05-10 | 15:02 | 49.958
2020-05-10 | 15:02 | 49.962
2020-05-10 | 15:02 | 49.966
2020-05-10 | 15:02 | 49.967
2020-05-10 | 15:02 | 49.968
2020-05-10 | 15:02 | 49.968
2020-05-10 | 15:02 | 49.969
2020-05-10 | 15:02 | 49.969
2020-05-10 | 15:02 | 49.969
2020-05-10 | 15:02 | 49.967
2020-05-10 | 15:02 | 49.963
2020-05-10 | 15:02 | 49.958
2020-05-10 | 15:02 | 49.955
2020-05-10 | 15:02 | 49.947
2020-05-10 | 15:02 | 49.942
2020-05-10 | 15:02 | 49.94
2020-05-10 | 15:02 | 49.938
2020-05-10 | 15:02 | 49.937
2020-05-10 | 15:02 | 49.937
2020-05-10 | 15:02 | 49.942
2020-05-10 | 15:02 | 49.947
2020-05-10 | 15:02 | 49.948
2020-05-10 | 15:02 | 49.95
2020-05-10 | 15:02 | 49.948
2020-05-10 | 15:02 | 49.947
2020-05-10 | 15:02 | 49.945
2020-05-10 | 15:02 | 49.944
2020-05-10 | 15:02 | 49.943
2020-05-10 | 15:02 | 49.944
2020-05-10 | 15:02 | 49.945
2020-05-10 | 15:02 | 49.945
2020-05-10 | 15:02 | 49.946
2020-05-10 | 15:02 | 49.947
2020-05-10 | 15:02 | 49.949
2020-05-10 | 15:02 | 49.948
2020-05-10 | 15:02 | 49.949
2020-05-10 | 15:02 | 49.949
2020-05-10 | 15:02 | 49.949
2020-05-10 | 15:02 | 49.948
2020-05-10 | 15:02 | 49.947
2020-05-10 | 15:02 | 49.948
2020-05-10 | 15:02 | 49.948
2020-05-10 | 15:02 | 49.947
2020-05-10 | 15:02 | 49.946
2020-05-10 | 15:02 | 49.946
2020-05-10 | 15:02 | 49.944
2020-05-10 | 15:02 | 49.942
2020-05-10 | 15:02 | 49.939
2020-05-10 | 15:02 | 49.935
2020-05-10 | 15:02 | 49.933
2020-05-10 | 15:02 | 49.929
2020-05-10 | 15:02 | 49.923
2020-05-10 | 15:02 | 49.92
2020-05-10 | 15:02 | 49.918
2020-05-10 | 15:03 | 49.918
2020-05-10 | 15:03 | 49.92
2020-05-10 | 15:03 | 49.924
2020-05-10 | 15:03 | 49.929
2020-05-10 | 15:03 | 49.929
2020-05-10 | 15:03 | 49.928
2020-05-10 | 15:03 | 49.93
2020-05-10 | 15:03 | 49.93
2020-05-10 | 15:03 | 49.93
2020-05-10 | 15:03 | 49.93
2020-05-10 | 15:03 | 49.931
2020-05-10 | 15:03 | 49.932
2020-05-10 | 15:03 | 49.937
2020-05-10 | 15:03 | 49.942
2020-05-10 | 15:03 | 49.943
2020-05-10 | 15:03 | 49.946
2020-05-10 | 15:03 | 49.95
2020-05-10 | 15:03 | 49.95
2020-05-10 | 15:03 | 49.951
2020-05-10 | 15:03 | 49.952
2020-05-10 | 15:03 | 49.953
2020-05-10 | 15:03 | 49.954
2020-05-10 | 15:03 | 49.955
2020-05-10 | 15:03 | 49.952
2020-05-10 | 15:03 | 49.948
2020-05-10 | 15:03 | 49.941
2020-05-10 | 15:03 | 49.935
2020-05-10 | 15:03 | 49.931
2020-05-10 | 15:03 | 49.931
2020-05-10 | 15:03 | 49.93
2020-05-10 | 15:03 | 49.932
2020-05-10 | 15:03 | 49.933
2020-05-10 | 15:03 | 49.934
2020-05-10 | 15:03 | 49.934
2020-05-10 | 15:03 | 49.935
2020-05-10 | 15:03 | 49.937
2020-05-10 | 15:03 | 49.937
2020-05-10 | 15:03 | 49.936
2020-05-10 | 15:03 | 49.934
2020-05-10 | 15:03 | 49.935
2020-05-10 | 15:03 | 49.935
2020-05-10 | 15:03 | 49.937
2020-05-10 | 15:03 | 49.938
2020-05-10 | 15:03 | 49.941
2020-05-10 | 15:03 | 49.946
2020-05-10 | 15:03 | 49.953
2020-05-10 | 15:03 | 49.957
2020-05-10 | 15:03 | 49.955
2020-05-10 | 15:03 | 49.954
2020-05-10 | 15:03 | 49.953
2020-05-10 | 15:03 | 49.955
2020-05-10 | 15:03 | 49.952
2020-05-10 | 15:03 | 49.951
2020-05-10 | 15:03 | 49.949
2020-05-10 | 15:03 | 49.949
2020-05-10 | 15:03 | 49.947
2020-05-10 | 15:03 | 49.946
2020-05-10 | 15:03 | 49.945
2020-05-10 | 15:03 | 49.943
2020-05-10 | 15:04 | 49.941
2020-05-10 | 15:04 | 49.941
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.947
2020-05-10 | 15:04 | 49.95
2020-05-10 | 15:04 | 49.952
2020-05-10 | 15:04 | 49.951
2020-05-10 | 15:04 | 49.953
2020-05-10 | 15:04 | 49.954
2020-05-10 | 15:04 | 49.953
2020-05-10 | 15:04 | 49.951
2020-05-10 | 15:04 | 49.95
2020-05-10 | 15:04 | 49.949
2020-05-10 | 15:04 | 49.949
2020-05-10 | 15:04 | 49.947
2020-05-10 | 15:04 | 49.945
2020-05-10 | 15:04 | 49.944
2020-05-10 | 15:04 | 49.943
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.943
2020-05-10 | 15:04 | 49.94
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.945
2020-05-10 | 15:04 | 49.95
2020-05-10 | 15:04 | 49.958
2020-05-10 | 15:04 | 49.955
2020-05-10 | 15:04 | 49.952
2020-05-10 | 15:04 | 49.948
2020-05-10 | 15:04 | 49.947
2020-05-10 | 15:04 | 49.946
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.943
2020-05-10 | 15:04 | 49.942
2020-05-10 | 15:04 | 49.943
2020-05-10 | 15:04 | 49.945
2020-05-10 | 15:04 | 49.945
2020-05-10 | 15:04 | 49.949
2020-05-10 | 15:04 | 49.953
2020-05-10 | 15:04 | 49.956
2020-05-10 | 15:04 | 49.957
2020-05-10 | 15:04 | 49.958
2020-05-10 | 15:04 | 49.96
2020-05-10 | 15:04 | 49.96
2020-05-10 | 15:04 | 49.959
2020-05-10 | 15:04 | 49.956
2020-05-10 | 15:04 | 49.953
2020-05-10 | 15:04 | 49.951
2020-05-10 | 15:04 | 49.95
2020-05-10 | 15:04 | 49.949
2020-05-10 | 15:04 | 49.952
2020-05-10 | 15:04 | 49.955
2020-05-10 | 15:04 | 49.958
2020-05-10 | 15:04 | 49.96
2020-05-10 | 15:04 | 49.962
2020-05-10 | 15:04 | 49.961
2020-05-10 | 15:04 | 49.961
2020-05-10 | 15:05 | 49.962
2020-05-10 | 15:05 | 49.964
2020-05-10 | 15:05 | 49.967
2020-05-10 | 15:05 | 49.967
2020-05-10 | 15:05 | 49.968
2020-05-10 | 15:05 | 49.969
2020-05-10 | 15:05 | 49.965
2020-05-10 | 15:05 | 49.962
2020-05-10 | 15:05 | 49.961
2020-05-10 | 15:05 | 49.959
2020-05-10 | 15:05 | 49.961
2020-05-10 | 15:05 | 49.962
2020-05-10 | 15:05 | 49.964
2020-05-10 | 15:05 | 49.965
2020-05-10 | 15:05 | 49.966
2020-05-10 | 15:05 | 49.967
2020-05-10 | 15:05 | 49.966
2020-05-10 | 15:05 | 49.964
2020-05-10 | 15:05 | 49.962
2020-05-10 | 15:05 | 49.96
2020-05-10 | 15:05 | 49.958
2020-05-10 | 15:05 | 49.954
2020-05-10 | 15:05 | 49.949
2020-05-10 | 15:05 | 49.944
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.94
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.944
2020-05-10 | 15:05 | 49.943
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.94
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.938
2020-05-10 | 15:05 | 49.938
2020-05-10 | 15:05 | 49.937
2020-05-10 | 15:05 | 49.936
2020-05-10 | 15:05 | 49.938
2020-05-10 | 15:05 | 49.938
2020-05-10 | 15:05 | 49.937
2020-05-10 | 15:05 | 49.936
2020-05-10 | 15:05 | 49.935
2020-05-10 | 15:05 | 49.938
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.944
2020-05-10 | 15:05 | 49.942
2020-05-10 | 15:05 | 49.942
2020-05-10 | 15:05 | 49.942
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.94
2020-05-10 | 15:05 | 49.936
2020-05-10 | 15:05 | 49.934
2020-05-10 | 15:05 | 49.933
2020-05-10 | 15:05 | 49.934
2020-05-10 | 15:05 | 49.936
2020-05-10 | 15:05 | 49.939
2020-05-10 | 15:05 | 49.938
2020-05-10 | 15:05 | 49.941
2020-05-10 | 15:05 | 49.944
2020-05-10 | 15:06 | 49.945
2020-05-10 | 15:06 | 49.948
2020-05-10 | 15:06 | 49.95
2020-05-10 | 15:06 | 49.949
2020-05-10 | 15:06 | 49.948
2020-05-10 | 15:06 | 49.946
2020-05-10 | 15:06 | 49.946
2020-05-10 | 15:06 | 49.946
2020-05-10 | 15:06 | 49.946
2020-05-10 | 15:06 | 49.946
2020-05-10 | 15:06 | 49.947
2020-05-10 | 15:06 | 49.946
2020-05-10 | 15:06 | 49.948
2020-05-10 | 15:06 | 49.948
2020-05-10 | 15:06 | 49.951
2020-05-10 | 15:06 | 49.953
2020-05-10 | 15:06 | 49.956
2020-05-10 | 15:06 | 49.959
2020-05-10 | 15:06 | 49.963
2020-05-10 | 15:06 | 49.966
2020-05-10 | 15:06 | 49.971
2020-05-10 | 15:06 | 49.972
2020-05-10 | 15:06 | 49.973
2020-05-10 | 15:06 | 49.973
2020-05-10 | 15:06 | 49.971
2020-05-10 | 15:06 | 49.971
2020-05-10 | 15:06 | 49.966
2020-05-10 | 15:06 | 49.962
2020-05-10 | 15:06 | 49.96
2020-05-10 | 15:06 | 49.962
2020-05-10 | 15:06 | 49.962
2020-05-10 | 15:06 | 49.964
2020-05-10 | 15:06 | 49.968
2020-05-10 | 15:06 | 49.97
2020-05-10 | 15:06 | 49.972
2020-05-10 | 15:06 | 49.975
2020-05-10 | 15:06 | 49.976
2020-05-10 | 15:06 | 49.977
2020-05-10 | 15:06 | 49.976
2020-05-10 | 15:06 | 49.975
2020-05-10 | 15:06 | 49.976
2020-05-10 | 15:06 | 49.974
2020-05-10 | 15:06 | 49.972
2020-05-10 | 15:06 | 49.971
2020-05-10 | 15:06 | 49.97
2020-05-10 | 15:06 | 49.972
2020-05-10 | 15:06 | 49.971
2020-05-10 | 15:06 | 49.973
2020-05-10 | 15:06 | 49.975
2020-05-10 | 15:06 | 49.98
2020-05-10 | 15:06 | 49.982
2020-05-10 | 15:06 | 49.985
2020-05-10 | 15:06 | 49.987
2020-05-10 | 15:06 | 49.991
2020-05-10 | 15:06 | 49.991
2020-05-10 | 15:06 | 49.991
2020-05-10 | 15:06 | 49.99
2020-05-10 | 15:06 | 49.989
2020-05-10 | 15:06 | 49.981
2020-05-10 | 15:06 | 49.989
2020-05-10 | 15:06 | 49.983
2020-05-10 | 15:07 | 49.984
2020-05-10 | 15:07 | 49.986
2020-05-10 | 15:07 | 49.99
2020-05-10 | 15:07 | 49.993
2020-05-10 | 15:07 | 49.998
2020-05-10 | 15:07 | 50.001

## Event 20200524-1
In UTC
Date | Time | Freq
2020-05-24 | 21:06 | 49.951
2020-05-24 | 21:06 | 49.952
2020-05-24 | 21:06 | 49.953
2020-05-24 | 21:06 | 49.952
2020-05-24 | 21:06 | 49.951
2020-05-24 | 21:06 | 49.95
2020-05-24 | 21:06 | 49.947
2020-05-24 | 21:06 | 49.946
2020-05-24 | 21:06 | 49.946
2020-05-24 | 21:06 | 49.943
2020-05-24 | 21:06 | 49.944
2020-05-24 | 21:06 | 49.942
2020-05-24 | 21:06 | 49.945
2020-05-24 | 21:06 | 49.947
2020-05-24 | 21:06 | 49.95
2020-05-24 | 21:06 | 49.953
2020-05-24 | 21:06 | 49.957
2020-05-24 | 21:06 | 49.964
2020-05-24 | 21:06 | 49.969
2020-05-24 | 21:06 | 49.976
2020-05-24 | 21:06 | 49.98
2020-05-24 | 21:06 | 49.982
2020-05-24 | 21:06 | 49.986
2020-05-24 | 21:06 | 49.988
2020-05-24 | 21:06 | 49.991
2020-05-24 | 21:06 | 49.997
2020-05-24 | 21:06 | 50
2020-05-24 | 21:06 | 50.005
2020-05-24 | 21:06 | 50.011
2020-05-24 | 21:06 | 50.015
2020-05-24 | 21:06 | 50.019
2020-05-24 | 21:07 | 50.022
2020-05-24 | 21:07 | 50.025
2020-05-24 | 21:07 | 50.028
2020-05-24 | 21:07 | 50.028
2020-05-24 | 21:07 | 50.03
2020-05-24 | 21:07 | 50.031
2020-05-24 | 21:07 | 50.031
2020-05-24 | 21:07 | 50.034
2020-05-24 | 21:07 | 50.036
2020-05-24 | 21:07 | 50.037
2020-05-24 | 21:07 | 50.041
2020-05-24 | 21:07 | 50.044
2020-05-24 | 21:07 | 50.038
2020-05-24 | 21:07 | 50.023
2020-05-24 | 21:07 | 49.998
2020-05-24 | 21:07 | 49.961
2020-05-24 | 21:07 | 49.913
2020-05-24 | 21:07 | 49.87
2020-05-24 | 21:07 | 49.835
2020-05-24 | 21:07 | 49.805
2020-05-24 | 21:07 | 49.785
2020-05-24 | 21:07 | 49.764
2020-05-24 | 21:07 | 49.753
2020-05-24 | 21:07 | 49.745
2020-05-24 | 21:07 | 49.741
2020-05-24 | 21:07 | 49.742
2020-05-24 | 21:07 | 49.742
2020-05-24 | 21:07 | 49.745
2020-05-24 | 21:07 | 49.75
2020-05-24 | 21:07 | 49.752
2020-05-24 | 21:07 | 49.755
2020-05-24 | 21:07 | 49.759
2020-05-24 | 21:07 | 49.762
2020-05-24 | 21:07 | 49.766
2020-05-24 | 21:07 | 49.772
2020-05-24 | 21:07 | 49.776
2020-05-24 | 21:07 | 49.779
2020-05-24 | 21:07 | 49.781
2020-05-24 | 21:07 | 49.783
2020-05-24 | 21:07 | 49.785
2020-05-24 | 21:07 | 49.787
2020-05-24 | 21:07 | 49.787
2020-05-24 | 21:07 | 49.785
2020-05-24 | 21:07 | 49.786
2020-05-24 | 21:07 | 49.787
2020-05-24 | 21:07 | 49.789
2020-05-24 | 21:07 | 49.792
2020-05-24 | 21:07 | 49.792
2020-05-24 | 21:07 | 49.792
2020-05-24 | 21:07 | 49.793
2020-05-24 | 21:07 | 49.793
2020-05-24 | 21:07 | 49.794
2020-05-24 | 21:07 | 49.794
2020-05-24 | 21:07 | 49.797
2020-05-24 | 21:07 | 49.797
2020-05-24 | 21:07 | 49.799
2020-05-24 | 21:07 | 49.801
2020-05-24 | 21:07 | 49.802
2020-05-24 | 21:07 | 49.803
2020-05-24 | 21:08 | 49.803
2020-05-24 | 21:08 | 49.805
2020-05-24 | 21:08 | 49.803
2020-05-24 | 21:08 | 49.802
2020-05-24 | 21:08 | 49.801
2020-05-24 | 21:08 | 49.801
2020-05-24 | 21:08 | 49.8
2020-05-24 | 21:08 | 49.8
2020-05-24 | 21:08 | 49.798
2020-05-24 | 21:08 | 49.796
2020-05-24 | 21:08 | 49.795
2020-05-24 | 21:08 | 49.797
2020-05-24 | 21:08 | 49.798
2020-05-24 | 21:08 | 49.801
2020-05-24 | 21:08 | 49.801
2020-05-24 | 21:08 | 49.802
2020-05-24 | 21:08 | 49.801
2020-05-24 | 21:08 | 49.804
2020-05-24 | 21:08 | 49.807
2020-05-24 | 21:08 | 49.809
2020-05-24 | 21:08 | 49.81
2020-05-24 | 21:08 | 49.812
2020-05-24 | 21:08 | 49.813
2020-05-24 | 21:08 | 49.814
2020-05-24 | 21:08 | 49.814
2020-05-24 | 21:08 | 49.814
2020-05-24 | 21:08 | 49.815
2020-05-24 | 21:08 | 49.816
2020-05-24 | 21:08 | 49.816
2020-05-24 | 21:08 | 49.816
2020-05-24 | 21:08 | 49.815
2020-05-24 | 21:08 | 49.815
2020-05-24 | 21:08 | 49.815
2020-05-24 | 21:08 | 49.816
2020-05-24 | 21:08 | 49.819
2020-05-24 | 21:08 | 49.824
2020-05-24 | 21:08 | 49.827
2020-05-24 | 21:08 | 49.832
2020-05-24 | 21:08 | 49.835
2020-05-24 | 21:08 | 49.836
2020-05-24 | 21:08 | 49.84
2020-05-24 | 21:08 | 49.842
2020-05-24 | 21:08 | 49.844
2020-05-24 | 21:08 | 49.846
2020-05-24 | 21:08 | 49.845
2020-05-24 | 21:08 | 49.846
2020-05-24 | 21:08 | 49.846
2020-05-24 | 21:08 | 49.85
2020-05-24 | 21:08 | 49.856
2020-05-24 | 21:08 | 49.862
2020-05-24 | 21:08 | 49.867
2020-05-24 | 21:08 | 49.87
2020-05-24 | 21:08 | 49.872
2020-05-24 | 21:08 | 49.875
2020-05-24 | 21:08 | 49.878
2020-05-24 | 21:08 | 49.884
2020-05-24 | 21:08 | 49.888
2020-05-24 | 21:08 | 49.892
2020-05-24 | 21:08 | 49.897
2020-05-24 | 21:08 | 49.9
2020-05-24 | 21:08 | 49.904
2020-05-24 | 21:09 | 49.908
2020-05-24 | 21:09 | 49.91
2020-05-24 | 21:09 | 49.913
2020-05-24 | 21:09 | 49.918
2020-05-24 | 21:09 | 49.925
2020-05-24 | 21:09 | 49.93
2020-05-24 | 21:09 | 49.935
2020-05-24 | 21:09 | 49.942
2020-05-24 | 21:09 | 49.948
2020-05-24 | 21:09 | 49.954
2020-05-24 | 21:09 | 49.961
2020-05-24 | 21:09 | 49.968
2020-05-24 | 21:09 | 49.973
2020-05-24 | 21:09 | 49.975
2020-05-24 | 21:09 | 49.979
2020-05-24 | 21:09 | 49.981
2020-05-24 | 21:09 | 49.981
2020-05-24 | 21:09 | 49.981
2020-05-24 | 21:09 | 49.98
2020-05-24 | 21:09 | 49.977
2020-05-24 | 21:09 | 49.974
2020-05-24 | 21:09 | 49.973
2020-05-24 | 21:09 | 49.971
2020-05-24 | 21:09 | 49.971
2020-05-24 | 21:09 | 49.974
2020-05-24 | 21:09 | 49.98
2020-05-24 | 21:09 | 49.987
2020-05-24 | 21:09 | 49.992
2020-05-24 | 21:09 | 49.993
2020-05-24 | 21:09 | 49.995
2020-05-24 | 21:09 | 49.997
2020-05-24 | 21:09 | 49.997
2020-05-24 | 21:09 | 49.998
2020-05-24 | 21:09 | 49.997
2020-05-24 | 21:09 | 49.996
2020-05-24 | 21:09 | 49.996
2020-05-24 | 21:09 | 50.002

## Event 20200527-1
In UTC
Date | Time | Freq
2020-05-27 | 13:11 | 49.91
2020-05-27 | 13:11 | 49.909
2020-05-27 | 13:11 | 49.909
2020-05-27 | 13:11 | 49.91
2020-05-27 | 13:11 | 49.908
2020-05-27 | 13:11 | 49.906
2020-05-27 | 13:11 | 49.906
2020-05-27 | 13:11 | 49.908
2020-05-27 | 13:11 | 49.909
2020-05-27 | 13:11 | 49.911
2020-05-27 | 13:11 | 49.915
2020-05-27 | 13:11 | 49.916
2020-05-27 | 13:11 | 49.918
2020-05-27 | 13:11 | 49.921
2020-05-27 | 13:11 | 49.923
2020-05-27 | 13:11 | 49.925
2020-05-27 | 13:11 | 49.924
2020-05-27 | 13:11 | 49.92
2020-05-27 | 13:11 | 49.918
2020-05-27 | 13:11 | 49.916
2020-05-27 | 13:11 | 49.915
2020-05-27 | 13:11 | 49.916
2020-05-27 | 13:11 | 49.916
2020-05-27 | 13:11 | 49.916
2020-05-27 | 13:11 | 49.917
2020-05-27 | 13:11 | 49.918
2020-05-27 | 13:11 | 49.918
2020-05-27 | 13:11 | 49.918
2020-05-27 | 13:11 | 49.919
2020-05-27 | 13:11 | 49.92
2020-05-27 | 13:12 | 49.921
2020-05-27 | 13:12 | 49.921
2020-05-27 | 13:12 | 49.924
2020-05-27 | 13:12 | 49.925
2020-05-27 | 13:12 | 49.926
2020-05-27 | 13:12 | 49.928
2020-05-27 | 13:12 | 49.928
2020-05-27 | 13:12 | 49.926
2020-05-27 | 13:12 | 49.926
2020-05-27 | 13:12 | 49.928
2020-05-27 | 13:12 | 49.93
2020-05-27 | 13:12 | 49.933
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.938
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.934
2020-05-27 | 13:12 | 49.933
2020-05-27 | 13:12 | 49.929
2020-05-27 | 13:12 | 49.928
2020-05-27 | 13:12 | 49.93
2020-05-27 | 13:12 | 49.93
2020-05-27 | 13:12 | 49.928
2020-05-27 | 13:12 | 49.928
2020-05-27 | 13:12 | 49.926
2020-05-27 | 13:12 | 49.927
2020-05-27 | 13:12 | 49.929
2020-05-27 | 13:12 | 49.93
2020-05-27 | 13:12 | 49.932
2020-05-27 | 13:12 | 49.933
2020-05-27 | 13:12 | 49.934
2020-05-27 | 13:12 | 49.935
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.937
2020-05-27 | 13:12 | 49.937
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.934
2020-05-27 | 13:12 | 49.932
2020-05-27 | 13:12 | 49.932
2020-05-27 | 13:12 | 49.931
2020-05-27 | 13:12 | 49.93
2020-05-27 | 13:12 | 49.929
2020-05-27 | 13:12 | 49.93
2020-05-27 | 13:12 | 49.931
2020-05-27 | 13:12 | 49.933
2020-05-27 | 13:12 | 49.934
2020-05-27 | 13:12 | 49.935
2020-05-27 | 13:12 | 49.936
2020-05-27 | 13:12 | 49.904
2020-05-27 | 13:12 | 49.862
2020-05-27 | 13:12 | 49.833
2020-05-27 | 13:12 | 49.814
2020-05-27 | 13:12 | 49.802
2020-05-27 | 13:12 | 49.795
2020-05-27 | 13:12 | 49.793
2020-05-27 | 13:12 | 49.792
2020-05-27 | 13:12 | 49.791
2020-05-27 | 13:13 | 49.792
2020-05-27 | 13:13 | 49.793
2020-05-27 | 13:13 | 49.793
2020-05-27 | 13:13 | 49.791
2020-05-27 | 13:13 | 49.787
2020-05-27 | 13:13 | 49.785
2020-05-27 | 13:13 | 49.782
2020-05-27 | 13:13 | 49.777
2020-05-27 | 13:13 | 49.776
2020-05-27 | 13:13 | 49.774
2020-05-27 | 13:13 | 49.772
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.771
2020-05-27 | 13:13 | 49.771
2020-05-27 | 13:13 | 49.77
2020-05-27 | 13:13 | 49.769
2020-05-27 | 13:13 | 49.768
2020-05-27 | 13:13 | 49.77
2020-05-27 | 13:13 | 49.771
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.774
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.772
2020-05-27 | 13:13 | 49.771
2020-05-27 | 13:13 | 49.771
2020-05-27 | 13:13 | 49.772
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.773
2020-05-27 | 13:13 | 49.775
2020-05-27 | 13:13 | 49.774
2020-05-27 | 13:13 | 49.772
2020-05-27 | 13:13 | 49.769
2020-05-27 | 13:13 | 49.765
2020-05-27 | 13:13 | 49.761
2020-05-27 | 13:13 | 49.756
2020-05-27 | 13:13 | 49.755
2020-05-27 | 13:13 | 49.756
2020-05-27 | 13:13 | 49.757
2020-05-27 | 13:13 | 49.759
2020-05-27 | 13:13 | 49.762
2020-05-27 | 13:13 | 49.762
2020-05-27 | 13:13 | 49.761
2020-05-27 | 13:13 | 49.761
2020-05-27 | 13:13 | 49.761
2020-05-27 | 13:13 | 49.762
2020-05-27 | 13:13 | 49.761
2020-05-27 | 13:13 | 49.761
2020-05-27 | 13:13 | 49.762
2020-05-27 | 13:13 | 49.764
2020-05-27 | 13:13 | 49.764
2020-05-27 | 13:13 | 49.766
2020-05-27 | 13:13 | 49.765
2020-05-27 | 13:13 | 49.766
2020-05-27 | 13:13 | 49.766
2020-05-27 | 13:13 | 49.767
2020-05-27 | 13:13 | 49.767
2020-05-27 | 13:13 | 49.768
2020-05-27 | 13:14 | 49.768
2020-05-27 | 13:14 | 49.765
2020-05-27 | 13:14 | 49.761
2020-05-27 | 13:14 | 49.76
2020-05-27 | 13:14 | 49.761
2020-05-27 | 13:14 | 49.759
2020-05-27 | 13:14 | 49.762
2020-05-27 | 13:14 | 49.764
2020-05-27 | 13:14 | 49.765
2020-05-27 | 13:14 | 49.765
2020-05-27 | 13:14 | 49.764
2020-05-27 | 13:14 | 49.759
2020-05-27 | 13:14 | 49.756
2020-05-27 | 13:14 | 49.754
2020-05-27 | 13:14 | 49.753
2020-05-27 | 13:14 | 49.752
2020-05-27 | 13:14 | 49.751
2020-05-27 | 13:14 | 49.751
2020-05-27 | 13:14 | 49.748
2020-05-27 | 13:14 | 49.747
2020-05-27 | 13:14 | 49.747
2020-05-27 | 13:14 | 49.746
2020-05-27 | 13:14 | 49.749
2020-05-27 | 13:14 | 49.75
2020-05-27 | 13:14 | 49.751
2020-05-27 | 13:14 | 49.754
2020-05-27 | 13:14 | 49.757
2020-05-27 | 13:14 | 49.76
2020-05-27 | 13:14 | 49.764
2020-05-27 | 13:14 | 49.767
2020-05-27 | 13:14 | 49.772
2020-05-27 | 13:14 | 49.778
2020-05-27 | 13:14 | 49.783
2020-05-27 | 13:14 | 49.79
2020-05-27 | 13:14 | 49.791
2020-05-27 | 13:14 | 49.79
2020-05-27 | 13:14 | 49.793
2020-05-27 | 13:14 | 49.792
2020-05-27 | 13:14 | 49.792
2020-05-27 | 13:14 | 49.789
2020-05-27 | 13:14 | 49.786
2020-05-27 | 13:14 | 49.785
2020-05-27 | 13:14 | 49.781
2020-05-27 | 13:14 | 49.781
2020-05-27 | 13:14 | 49.778
2020-05-27 | 13:14 | 49.775
2020-05-27 | 13:14 | 49.772
2020-05-27 | 13:14 | 49.768
2020-05-27 | 13:14 | 49.764
2020-05-27 | 13:14 | 49.762
2020-05-27 | 13:14 | 49.76
2020-05-27 | 13:14 | 49.759
2020-05-27 | 13:14 | 49.76
2020-05-27 | 13:14 | 49.763
2020-05-27 | 13:14 | 49.768
2020-05-27 | 13:14 | 49.773
2020-05-27 | 13:14 | 49.78
2020-05-27 | 13:14 | 49.782
2020-05-27 | 13:14 | 49.784
2020-05-27 | 13:14 | 49.785
2020-05-27 | 13:14 | 49.788
2020-05-27 | 13:15 | 49.79
2020-05-27 | 13:15 | 49.794
2020-05-27 | 13:15 | 49.795
2020-05-27 | 13:15 | 49.795
2020-05-27 | 13:15 | 49.797
2020-05-27 | 13:15 | 49.798
2020-05-27 | 13:15 | 49.8
2020-05-27 | 13:15 | 49.802
2020-05-27 | 13:15 | 49.802
2020-05-27 | 13:15 | 49.803
2020-05-27 | 13:15 | 49.804
2020-05-27 | 13:15 | 49.803
2020-05-27 | 13:15 | 49.801
2020-05-27 | 13:15 | 49.8
2020-05-27 | 13:15 | 49.799
2020-05-27 | 13:15 | 49.795
2020-05-27 | 13:15 | 49.793
2020-05-27 | 13:15 | 49.79
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.791
2020-05-27 | 13:15 | 49.792
2020-05-27 | 13:15 | 49.792
2020-05-27 | 13:15 | 49.792
2020-05-27 | 13:15 | 49.79
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.788
2020-05-27 | 13:15 | 49.79
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.791
2020-05-27 | 13:15 | 49.794
2020-05-27 | 13:15 | 49.795
2020-05-27 | 13:15 | 49.797
2020-05-27 | 13:15 | 49.799
2020-05-27 | 13:15 | 49.801
2020-05-27 | 13:15 | 49.801
2020-05-27 | 13:15 | 49.8
2020-05-27 | 13:15 | 49.796
2020-05-27 | 13:15 | 49.795
2020-05-27 | 13:15 | 49.791
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.787
2020-05-27 | 13:15 | 49.786
2020-05-27 | 13:15 | 49.785
2020-05-27 | 13:15 | 49.786
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.79
2020-05-27 | 13:15 | 49.793
2020-05-27 | 13:15 | 49.793
2020-05-27 | 13:15 | 49.793
2020-05-27 | 13:15 | 49.793
2020-05-27 | 13:15 | 49.792
2020-05-27 | 13:15 | 49.791
2020-05-27 | 13:15 | 49.79
2020-05-27 | 13:15 | 49.789
2020-05-27 | 13:15 | 49.787
2020-05-27 | 13:16 | 49.786
2020-05-27 | 13:16 | 49.787
2020-05-27 | 13:16 | 49.788
2020-05-27 | 13:16 | 49.791
2020-05-27 | 13:16 | 49.795
2020-05-27 | 13:16 | 49.798
2020-05-27 | 13:16 | 49.802
2020-05-27 | 13:16 | 49.803
2020-05-27 | 13:16 | 49.803
2020-05-27 | 13:16 | 49.801
2020-05-27 | 13:16 | 49.799
2020-05-27 | 13:16 | 49.8
2020-05-27 | 13:16 | 49.802
2020-05-27 | 13:16 | 49.804
2020-05-27 | 13:16 | 49.806
2020-05-27 | 13:16 | 49.808
2020-05-27 | 13:16 | 49.813
2020-05-27 | 13:16 | 49.815
2020-05-27 | 13:16 | 49.815
2020-05-27 | 13:16 | 49.814
2020-05-27 | 13:16 | 49.814
2020-05-27 | 13:16 | 49.816
2020-05-27 | 13:16 | 49.816
2020-05-27 | 13:16 | 49.818
2020-05-27 | 13:16 | 49.819
2020-05-27 | 13:16 | 49.82
2020-05-27 | 13:16 | 49.822
2020-05-27 | 13:16 | 49.824
2020-05-27 | 13:16 | 49.825
2020-05-27 | 13:16 | 49.827
2020-05-27 | 13:16 | 49.825
2020-05-27 | 13:16 | 49.823
2020-05-27 | 13:16 | 49.823
2020-05-27 | 13:16 | 49.823
2020-05-27 | 13:16 | 49.824
2020-05-27 | 13:16 | 49.825
2020-05-27 | 13:16 | 49.827
2020-05-27 | 13:16 | 49.828
2020-05-27 | 13:16 | 49.829
2020-05-27 | 13:16 | 49.829
2020-05-27 | 13:16 | 49.831
2020-05-27 | 13:16 | 49.832
2020-05-27 | 13:16 | 49.833
2020-05-27 | 13:16 | 49.835
2020-05-27 | 13:16 | 49.835
2020-05-27 | 13:16 | 49.835
2020-05-27 | 13:16 | 49.835
2020-05-27 | 13:16 | 49.834
2020-05-27 | 13:16 | 49.833
2020-05-27 | 13:16 | 49.836
2020-05-27 | 13:16 | 49.836
2020-05-27 | 13:16 | 49.837
2020-05-27 | 13:16 | 49.839
2020-05-27 | 13:16 | 49.84
2020-05-27 | 13:16 | 49.838
2020-05-27 | 13:16 | 49.84
2020-05-27 | 13:16 | 49.839
2020-05-27 | 13:16 | 49.839
2020-05-27 | 13:16 | 49.841
2020-05-27 | 13:16 | 49.84
2020-05-27 | 13:16 | 49.841
2020-05-27 | 13:17 | 49.844
2020-05-27 | 13:17 | 49.846
2020-05-27 | 13:17 | 49.849
2020-05-27 | 13:17 | 49.854
2020-05-27 | 13:17 | 49.858
2020-05-27 | 13:17 | 49.864
2020-05-27 | 13:17 | 49.87
2020-05-27 | 13:17 | 49.875
2020-05-27 | 13:17 | 49.879
2020-05-27 | 13:17 | 49.882
2020-05-27 | 13:17 | 49.885
2020-05-27 | 13:17 | 49.887
2020-05-27 | 13:17 | 49.891
2020-05-27 | 13:17 | 49.891
2020-05-27 | 13:17 | 49.891
2020-05-27 | 13:17 | 49.892
2020-05-27 | 13:17 | 49.893
2020-05-27 | 13:17 | 49.896
2020-05-27 | 13:17 | 49.897
2020-05-27 | 13:17 | 49.9
2020-05-27 | 13:17 | 49.904
2020-05-27 | 13:17 | 49.907
2020-05-27 | 13:17 | 49.909
2020-05-27 | 13:17 | 49.906
2020-05-27 | 13:17 | 49.907
2020-05-27 | 13:17 | 49.907
2020-05-27 | 13:17 | 49.909
2020-05-27 | 13:17 | 49.912
2020-05-27 | 13:17 | 49.916
2020-05-27 | 13:17 | 49.918
2020-05-27 | 13:17 | 49.919
2020-05-27 | 13:17 | 49.921
2020-05-27 | 13:17 | 49.923
2020-05-27 | 13:17 | 49.925
2020-05-27 | 13:17 | 49.927
2020-05-27 | 13:17 | 49.926
2020-05-27 | 13:17 | 49.926
2020-05-27 | 13:17 | 49.925
2020-05-27 | 13:17 | 49.924
2020-05-27 | 13:17 | 49.926
2020-05-27 | 13:17 | 49.929
2020-05-27 | 13:17 | 49.932
2020-05-27 | 13:17 | 49.934
2020-05-27 | 13:17 | 49.933
2020-05-27 | 13:17 | 49.934
2020-05-27 | 13:17 | 49.934
2020-05-27 | 13:17 | 49.935
2020-05-27 | 13:17 | 49.936
2020-05-27 | 13:17 | 49.936
2020-05-27 | 13:17 | 49.938
2020-05-27 | 13:17 | 49.938
2020-05-27 | 13:17 | 49.938
2020-05-27 | 13:17 | 49.938
2020-05-27 | 13:17 | 49.936
2020-05-27 | 13:17 | 49.934
2020-05-27 | 13:17 | 49.936
2020-05-27 | 13:17 | 49.938
2020-05-27 | 13:17 | 49.939
2020-05-27 | 13:17 | 49.94
2020-05-27 | 13:18 | 49.944
2020-05-27 | 13:18 | 49.943
2020-05-27 | 13:18 | 49.943
2020-05-27 | 13:18 | 49.943
2020-05-27 | 13:18 | 49.944
2020-05-27 | 13:18 | 49.946
2020-05-27 | 13:18 | 49.947
2020-05-27 | 13:18 | 49.947
2020-05-27 | 13:18 | 49.95
2020-05-27 | 13:18 | 49.951
2020-05-27 | 13:18 | 49.952
2020-05-27 | 13:18 | 49.954
2020-05-27 | 13:18 | 49.954
2020-05-27 | 13:18 | 49.954
2020-05-27 | 13:18 | 49.952
2020-05-27 | 13:18 | 49.952
2020-05-27 | 13:18 | 49.953
2020-05-27 | 13:18 | 49.953
2020-05-27 | 13:18 | 49.956
2020-05-27 | 13:18 | 49.959
2020-05-27 | 13:18 | 49.961
2020-05-27 | 13:18 | 49.963
2020-05-27 | 13:18 | 49.962
2020-05-27 | 13:18 | 49.962
2020-05-27 | 13:18 | 49.961
2020-05-27 | 13:18 | 49.96
2020-05-27 | 13:18 | 49.96
2020-05-27 | 13:18 | 49.962
2020-05-27 | 13:18 | 49.965
2020-05-27 | 13:18 | 49.967
2020-05-27 | 13:18 | 49.968
2020-05-27 | 13:18 | 49.969
2020-05-27 | 13:18 | 49.97
2020-05-27 | 13:18 | 49.972
2020-05-27 | 13:18 | 49.972
2020-05-27 | 13:18 | 49.973
2020-05-27 | 13:18 | 49.973
2020-05-27 | 13:18 | 49.974
2020-05-27 | 13:18 | 49.974
2020-05-27 | 13:18 | 49.974
2020-05-27 | 13:18 | 49.974
2020-05-27 | 13:18 | 49.972
2020-05-27 | 13:18 | 49.971
2020-05-27 | 13:18 | 49.968
2020-05-27 | 13:18 | 49.966
2020-05-27 | 13:18 | 49.965
2020-05-27 | 13:18 | 49.966
2020-05-27 | 13:18 | 49.967
2020-05-27 | 13:18 | 49.967
2020-05-27 | 13:18 | 49.967
2020-05-27 | 13:18 | 49.969
2020-05-27 | 13:18 | 49.969
2020-05-27 | 13:18 | 49.969
2020-05-27 | 13:18 | 49.968
2020-05-27 | 13:18 | 49.969
2020-05-27 | 13:18 | 49.972
2020-05-27 | 13:18 | 49.975
2020-05-27 | 13:18 | 49.977
2020-05-27 | 13:18 | 49.977
2020-05-27 | 13:18 | 49.977
2020-05-27 | 13:18 | 49.978
2020-05-27 | 13:19 | 49.982
2020-05-27 | 13:19 | 49.984
2020-05-27 | 13:19 | 49.987
2020-05-27 | 13:19 | 49.987
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.985
2020-05-27 | 13:19 | 49.984
2020-05-27 | 13:19 | 49.984
2020-05-27 | 13:19 | 49.982
2020-05-27 | 13:19 | 49.981
2020-05-27 | 13:19 | 49.983
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.988
2020-05-27 | 13:19 | 49.988
2020-05-27 | 13:19 | 49.985
2020-05-27 | 13:19 | 49.983
2020-05-27 | 13:19 | 49.982
2020-05-27 | 13:19 | 49.982
2020-05-27 | 13:19 | 49.984
2020-05-27 | 13:19 | 49.985
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.987
2020-05-27 | 13:19 | 49.989
2020-05-27 | 13:19 | 49.99
2020-05-27 | 13:19 | 49.99
2020-05-27 | 13:19 | 49.991
2020-05-27 | 13:19 | 49.992
2020-05-27 | 13:19 | 49.994
2020-05-27 | 13:19 | 49.992
2020-05-27 | 13:19 | 49.989
2020-05-27 | 13:19 | 49.988
2020-05-27 | 13:19 | 49.988
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.985
2020-05-27 | 13:19 | 49.983
2020-05-27 | 13:19 | 49.981
2020-05-27 | 13:19 | 49.981
2020-05-27 | 13:19 | 49.983
2020-05-27 | 13:19 | 49.984
2020-05-27 | 13:19 | 49.983
2020-05-27 | 13:19 | 49.984
2020-05-27 | 13:19 | 49.985
2020-05-27 | 13:19 | 49.987
2020-05-27 | 13:19 | 49.986
2020-05-27 | 13:19 | 49.988
2020-05-27 | 13:19 | 49.988
2020-05-27 | 13:19 | 49.99
2020-05-27 | 13:19 | 49.992
2020-05-27 | 13:19 | 49.994
2020-05-27 | 13:19 | 49.999
2020-05-27 | 13:19 | 50.001

## Event 20200528-1
In UTC
Date | Time | Freq
2020-05-28 | 13:09 | 49.954
2020-05-28 | 13:09 | 49.957
2020-05-28 | 13:09 | 49.961
2020-05-28 | 13:09 | 49.968
2020-05-28 | 13:09 | 49.975
2020-05-28 | 13:09 | 49.982
2020-05-28 | 13:09 | 49.985
2020-05-28 | 13:09 | 49.986
2020-05-28 | 13:09 | 49.988
2020-05-28 | 13:09 | 49.986
2020-05-28 | 13:09 | 49.986
2020-05-28 | 13:09 | 49.984
2020-05-28 | 13:09 | 49.984
2020-05-28 | 13:09 | 49.986
2020-05-28 | 13:09 | 49.99
2020-05-28 | 13:09 | 49.991
2020-05-28 | 13:09 | 49.989
2020-05-28 | 13:09 | 49.988
2020-05-28 | 13:09 | 49.99
2020-05-28 | 13:09 | 49.99
2020-05-28 | 13:09 | 49.989
2020-05-28 | 13:09 | 49.987
2020-05-28 | 13:09 | 49.983
2020-05-28 | 13:09 | 49.98
2020-05-28 | 13:09 | 49.982
2020-05-28 | 13:09 | 49.986
2020-05-28 | 13:09 | 49.991
2020-05-28 | 13:09 | 49.994
2020-05-28 | 13:09 | 49.997
2020-05-28 | 13:09 | 49.999
2020-05-28 | 13:10 | 49.999
2020-05-28 | 13:10 | 49.999
2020-05-28 | 13:10 | 50
2020-05-28 | 13:10 | 50.001
2020-05-28 | 13:10 | 50.004
2020-05-28 | 13:10 | 50.005
2020-05-28 | 13:10 | 50.006
2020-05-28 | 13:10 | 50.006
2020-05-28 | 13:10 | 50.006
2020-05-28 | 13:10 | 50.005
2020-05-28 | 13:10 | 50.004
2020-05-28 | 13:10 | 50.004
2020-05-28 | 13:10 | 50.005
2020-05-28 | 13:10 | 50.003
2020-05-28 | 13:10 | 50.003
2020-05-28 | 13:10 | 50.001
2020-05-28 | 13:10 | 50
2020-05-28 | 13:10 | 49.998
2020-05-28 | 13:10 | 49.998
2020-05-28 | 13:10 | 49.998
2020-05-28 | 13:10 | 49.997
2020-05-28 | 13:10 | 49.996
2020-05-28 | 13:10 | 49.995
2020-05-28 | 13:10 | 49.995
2020-05-28 | 13:10 | 49.998
2020-05-28 | 13:10 | 50
2020-05-28 | 13:10 | 50.001
2020-05-28 | 13:10 | 50.002
2020-05-28 | 13:10 | 50.006
2020-05-28 | 13:10 | 50.005
2020-05-28 | 13:10 | 50.004
2020-05-28 | 13:10 | 50.001
2020-05-28 | 13:10 | 50.002
2020-05-28 | 13:10 | 50.001
2020-05-28 | 13:10 | 50.005
2020-05-28 | 13:10 | 50.007
2020-05-28 | 13:10 | 50.008
2020-05-28 | 13:10 | 50.011
2020-05-28 | 13:10 | 50.012
2020-05-28 | 13:10 | 50.014
2020-05-28 | 13:10 | 50.012
2020-05-28 | 13:10 | 50.013
2020-05-28 | 13:10 | 50.013
2020-05-28 | 13:10 | 50.013
2020-05-28 | 13:10 | 50.014
2020-05-28 | 13:10 | 50.016
2020-05-28 | 13:10 | 50.02
2020-05-28 | 13:10 | 50.021
2020-05-28 | 13:10 | 50.024
2020-05-28 | 13:10 | 50.024
2020-05-28 | 13:10 | 50.027
2020-05-28 | 13:10 | 50.027
2020-05-28 | 13:10 | 50.028
2020-05-28 | 13:10 | 50.026
2020-05-28 | 13:10 | 50.027
2020-05-28 | 13:10 | 50.025
2020-05-28 | 13:10 | 50.026
2020-05-28 | 13:10 | 50.028
2020-05-28 | 13:10 | 50.029
2020-05-28 | 13:10 | 50.03
2020-05-28 | 13:10 | 50.03
2020-05-28 | 13:11 | 50.028
2020-05-28 | 13:11 | 50.026
2020-05-28 | 13:11 | 50.025
2020-05-28 | 13:11 | 50.024
2020-05-28 | 13:11 | 50.023
2020-05-28 | 13:11 | 50.023
2020-05-28 | 13:11 | 50.022
2020-05-28 | 13:11 | 50.022
2020-05-28 | 13:11 | 50.021
2020-05-28 | 13:11 | 50.02
2020-05-28 | 13:11 | 50.02
2020-05-28 | 13:11 | 50.022
2020-05-28 | 13:11 | 50.023
2020-05-28 | 13:11 | 50.027
2020-05-28 | 13:11 | 50.028
2020-05-28 | 13:11 | 50.028
2020-05-28 | 13:11 | 50.027
2020-05-28 | 13:11 | 50.028
2020-05-28 | 13:11 | 50.03
2020-05-28 | 13:11 | 50.031
2020-05-28 | 13:11 | 50.031
2020-05-28 | 13:11 | 50.031
2020-05-28 | 13:11 | 50.03
2020-05-28 | 13:11 | 50.025
2020-05-28 | 13:11 | 50.022
2020-05-28 | 13:11 | 50.019
2020-05-28 | 13:11 | 50.016
2020-05-28 | 13:11 | 50.012
2020-05-28 | 13:11 | 50.01
2020-05-28 | 13:11 | 50.007
2020-05-28 | 13:11 | 50.005
2020-05-28 | 13:11 | 50.003
2020-05-28 | 13:11 | 49.998
2020-05-28 | 13:11 | 49.994
2020-05-28 | 13:11 | 49.991
2020-05-28 | 13:11 | 49.968
2020-05-28 | 13:11 | 49.919
2020-05-28 | 13:11 | 49.891
2020-05-28 | 13:11 | 49.876
2020-05-28 | 13:11 | 49.87
2020-05-28 | 13:11 | 49.872
2020-05-28 | 13:11 | 49.878
2020-05-28 | 13:11 | 49.886
2020-05-28 | 13:11 | 49.892
2020-05-28 | 13:11 | 49.898
2020-05-28 | 13:11 | 49.903
2020-05-28 | 13:11 | 49.905
2020-05-28 | 13:11 | 49.907
2020-05-28 | 13:11 | 49.909
2020-05-28 | 13:11 | 49.911
2020-05-28 | 13:11 | 49.91
2020-05-28 | 13:11 | 49.909
2020-05-28 | 13:11 | 49.907
2020-05-28 | 13:11 | 49.904
2020-05-28 | 13:11 | 49.9
2020-05-28 | 13:11 | 49.9
2020-05-28 | 13:11 | 49.901
2020-05-28 | 13:11 | 49.897
2020-05-28 | 13:11 | 49.894
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.888
2020-05-28 | 13:12 | 49.887
2020-05-28 | 13:12 | 49.889
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.894
2020-05-28 | 13:12 | 49.895
2020-05-28 | 13:12 | 49.896
2020-05-28 | 13:12 | 49.897
2020-05-28 | 13:12 | 49.896
2020-05-28 | 13:12 | 49.893
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.888
2020-05-28 | 13:12 | 49.886
2020-05-28 | 13:12 | 49.884
2020-05-28 | 13:12 | 49.881
2020-05-28 | 13:12 | 49.878
2020-05-28 | 13:12 | 49.877
2020-05-28 | 13:12 | 49.877
2020-05-28 | 13:12 | 49.881
2020-05-28 | 13:12 | 49.883
2020-05-28 | 13:12 | 49.885
2020-05-28 | 13:12 | 49.886
2020-05-28 | 13:12 | 49.885
2020-05-28 | 13:12 | 49.884
2020-05-28 | 13:12 | 49.884
2020-05-28 | 13:12 | 49.885
2020-05-28 | 13:12 | 49.887
2020-05-28 | 13:12 | 49.889
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.889
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.892
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.893
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.886
2020-05-28 | 13:12 | 49.886
2020-05-28 | 13:12 | 49.888
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.891
2020-05-28 | 13:12 | 49.89
2020-05-28 | 13:12 | 49.888
2020-05-28 | 13:12 | 49.886
2020-05-28 | 13:12 | 49.886
2020-05-28 | 13:12 | 49.885
2020-05-28 | 13:12 | 49.888
2020-05-28 | 13:12 | 49.889
2020-05-28 | 13:12 | 49.892
2020-05-28 | 13:12 | 49.894
2020-05-28 | 13:12 | 49.894
2020-05-28 | 13:12 | 49.893
2020-05-28 | 13:12 | 49.894
2020-05-28 | 13:12 | 49.895
2020-05-28 | 13:12 | 49.896
2020-05-28 | 13:13 | 49.894
2020-05-28 | 13:13 | 49.891
2020-05-28 | 13:13 | 49.887
2020-05-28 | 13:13 | 49.884
2020-05-28 | 13:13 | 49.886
2020-05-28 | 13:13 | 49.888
2020-05-28 | 13:13 | 49.889
2020-05-28 | 13:13 | 49.889
2020-05-28 | 13:13 | 49.889
2020-05-28 | 13:13 | 49.889
2020-05-28 | 13:13 | 49.888
2020-05-28 | 13:13 | 49.885
2020-05-28 | 13:13 | 49.881
2020-05-28 | 13:13 | 49.877
2020-05-28 | 13:13 | 49.874
2020-05-28 | 13:13 | 49.877
2020-05-28 | 13:13 | 49.881
2020-05-28 | 13:13 | 49.883
2020-05-28 | 13:13 | 49.883
2020-05-28 | 13:13 | 49.881
2020-05-28 | 13:13 | 49.878
2020-05-28 | 13:13 | 49.877
2020-05-28 | 13:13 | 49.879
2020-05-28 | 13:13 | 49.876
2020-05-28 | 13:13 | 49.875
2020-05-28 | 13:13 | 49.87
2020-05-28 | 13:13 | 49.867
2020-05-28 | 13:13 | 49.866
2020-05-28 | 13:13 | 49.865
2020-05-28 | 13:13 | 49.863
2020-05-28 | 13:13 | 49.862
2020-05-28 | 13:13 | 49.863
2020-05-28 | 13:13 | 49.865
2020-05-28 | 13:13 | 49.864
2020-05-28 | 13:13 | 49.863
2020-05-28 | 13:13 | 49.862
2020-05-28 | 13:13 | 49.864
2020-05-28 | 13:13 | 49.863
2020-05-28 | 13:13 | 49.863
2020-05-28 | 13:13 | 49.86
2020-05-28 | 13:13 | 49.857
2020-05-28 | 13:13 | 49.854
2020-05-28 | 13:13 | 49.853
2020-05-28 | 13:13 | 49.852
2020-05-28 | 13:13 | 49.85
2020-05-28 | 13:13 | 49.849
2020-05-28 | 13:13 | 49.851
2020-05-28 | 13:13 | 49.852
2020-05-28 | 13:13 | 49.854
2020-05-28 | 13:13 | 49.855
2020-05-28 | 13:13 | 49.857
2020-05-28 | 13:13 | 49.86
2020-05-28 | 13:13 | 49.863
2020-05-28 | 13:13 | 49.865
2020-05-28 | 13:13 | 49.868
2020-05-28 | 13:13 | 49.871
2020-05-28 | 13:13 | 49.872
2020-05-28 | 13:13 | 49.873
2020-05-28 | 13:13 | 49.875
2020-05-28 | 13:14 | 49.876
2020-05-28 | 13:14 | 49.879
2020-05-28 | 13:14 | 49.881
2020-05-28 | 13:14 | 49.883
2020-05-28 | 13:14 | 49.885
2020-05-28 | 13:14 | 49.888
2020-05-28 | 13:14 | 49.89
2020-05-28 | 13:14 | 49.891
2020-05-28 | 13:14 | 49.889
2020-05-28 | 13:14 | 49.885
2020-05-28 | 13:14 | 49.883
2020-05-28 | 13:14 | 49.878
2020-05-28 | 13:14 | 49.877
2020-05-28 | 13:14 | 49.877
2020-05-28 | 13:14 | 49.876
2020-05-28 | 13:14 | 49.874
2020-05-28 | 13:14 | 49.875
2020-05-28 | 13:14 | 49.879
2020-05-28 | 13:14 | 49.88
2020-05-28 | 13:14 | 49.879
2020-05-28 | 13:14 | 49.878
2020-05-28 | 13:14 | 49.877
2020-05-28 | 13:14 | 49.874
2020-05-28 | 13:14 | 49.874
2020-05-28 | 13:14 | 49.873
2020-05-28 | 13:14 | 49.872
2020-05-28 | 13:14 | 49.873
2020-05-28 | 13:14 | 49.871
2020-05-28 | 13:14 | 49.87
2020-05-28 | 13:14 | 49.869
2020-05-28 | 13:14 | 49.868
2020-05-28 | 13:14 | 49.87
2020-05-28 | 13:14 | 49.872
2020-05-28 | 13:14 | 49.874
2020-05-28 | 13:14 | 49.877
2020-05-28 | 13:14 | 49.88
2020-05-28 | 13:14 | 49.882
2020-05-28 | 13:14 | 49.887
2020-05-28 | 13:14 | 49.889
2020-05-28 | 13:14 | 49.891
2020-05-28 | 13:14 | 49.892
2020-05-28 | 13:14 | 49.892
2020-05-28 | 13:14 | 49.891
2020-05-28 | 13:14 | 49.894
2020-05-28 | 13:14 | 49.897
2020-05-28 | 13:14 | 49.899
2020-05-28 | 13:14 | 49.903
2020-05-28 | 13:14 | 49.903
2020-05-28 | 13:14 | 49.904
2020-05-28 | 13:14 | 49.903
2020-05-28 | 13:14 | 49.898
2020-05-28 | 13:14 | 49.895
2020-05-28 | 13:14 | 49.89
2020-05-28 | 13:14 | 49.885
2020-05-28 | 13:14 | 49.882
2020-05-28 | 13:14 | 49.881
2020-05-28 | 13:14 | 49.878
2020-05-28 | 13:14 | 49.877
2020-05-28 | 13:14 | 49.876
2020-05-28 | 13:14 | 49.878
2020-05-28 | 13:14 | 49.879
2020-05-28 | 13:15 | 49.879
2020-05-28 | 13:15 | 49.878
2020-05-28 | 13:15 | 49.877
2020-05-28 | 13:15 | 49.874
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.868
2020-05-28 | 13:15 | 49.869
2020-05-28 | 13:15 | 49.871
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.871
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.871
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.869
2020-05-28 | 13:15 | 49.868
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.871
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.874
2020-05-28 | 13:15 | 49.873
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.871
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.87
2020-05-28 | 13:15 | 49.872
2020-05-28 | 13:15 | 49.874
2020-05-28 | 13:15 | 49.877
2020-05-28 | 13:15 | 49.88
2020-05-28 | 13:15 | 49.883
2020-05-28 | 13:15 | 49.885
2020-05-28 | 13:15 | 49.89
2020-05-28 | 13:15 | 49.893
2020-05-28 | 13:15 | 49.897
2020-05-28 | 13:15 | 49.899
2020-05-28 | 13:15 | 49.903
2020-05-28 | 13:15 | 49.903
2020-05-28 | 13:15 | 49.906
2020-05-28 | 13:15 | 49.907
2020-05-28 | 13:15 | 49.908
2020-05-28 | 13:15 | 49.908
2020-05-28 | 13:15 | 49.909
2020-05-28 | 13:15 | 49.912
2020-05-28 | 13:15 | 49.914
2020-05-28 | 13:15 | 49.914
2020-05-28 | 13:15 | 49.914
2020-05-28 | 13:15 | 49.915
2020-05-28 | 13:15 | 49.918
2020-05-28 | 13:15 | 49.921
2020-05-28 | 13:15 | 49.924
2020-05-28 | 13:15 | 49.927
2020-05-28 | 13:15 | 49.927
2020-05-28 | 13:15 | 49.929
2020-05-28 | 13:15 | 49.93
2020-05-28 | 13:16 | 49.929
2020-05-28 | 13:16 | 49.928
2020-05-28 | 13:16 | 49.929
2020-05-28 | 13:16 | 49.932
2020-05-28 | 13:16 | 49.936
2020-05-28 | 13:16 | 49.939
2020-05-28 | 13:16 | 49.941
2020-05-28 | 13:16 | 49.941
2020-05-28 | 13:16 | 49.94
2020-05-28 | 13:16 | 49.938
2020-05-28 | 13:16 | 49.939
2020-05-28 | 13:16 | 49.943
2020-05-28 | 13:16 | 49.946
2020-05-28 | 13:16 | 49.949
2020-05-28 | 13:16 | 49.951
2020-05-28 | 13:16 | 49.953
2020-05-28 | 13:16 | 49.954
2020-05-28 | 13:16 | 49.957
2020-05-28 | 13:16 | 49.959
2020-05-28 | 13:16 | 49.96
2020-05-28 | 13:16 | 49.961
2020-05-28 | 13:16 | 49.963
2020-05-28 | 13:16 | 49.964
2020-05-28 | 13:16 | 49.965
2020-05-28 | 13:16 | 49.965
2020-05-28 | 13:16 | 49.964
2020-05-28 | 13:16 | 49.963
2020-05-28 | 13:16 | 49.961
2020-05-28 | 13:16 | 49.959
2020-05-28 | 13:16 | 49.96
2020-05-28 | 13:16 | 49.959
2020-05-28 | 13:16 | 49.959
2020-05-28 | 13:16 | 49.959
2020-05-28 | 13:16 | 49.96
2020-05-28 | 13:16 | 49.96
2020-05-28 | 13:16 | 49.958
2020-05-28 | 13:16 | 49.958
2020-05-28 | 13:16 | 49.958
2020-05-28 | 13:16 | 49.954
2020-05-28 | 13:16 | 49.952
2020-05-28 | 13:16 | 49.951
2020-05-28 | 13:16 | 49.954
2020-05-28 | 13:16 | 49.959
2020-05-28 | 13:16 | 49.961
2020-05-28 | 13:16 | 49.961
2020-05-28 | 13:16 | 49.962
2020-05-28 | 13:16 | 49.964
2020-05-28 | 13:16 | 49.963
2020-05-28 | 13:16 | 49.964
2020-05-28 | 13:16 | 49.967
2020-05-28 | 13:16 | 49.969
2020-05-28 | 13:16 | 49.974
2020-05-28 | 13:16 | 49.975
2020-05-28 | 13:16 | 49.974
2020-05-28 | 13:16 | 49.974
2020-05-28 | 13:16 | 49.974
2020-05-28 | 13:16 | 49.973
2020-05-28 | 13:16 | 49.975
2020-05-28 | 13:16 | 49.972
2020-05-28 | 13:16 | 49.969
2020-05-28 | 13:16 | 49.967
2020-05-28 | 13:17 | 49.966
2020-05-28 | 13:17 | 49.963
2020-05-28 | 13:17 | 49.963
2020-05-28 | 13:17 | 49.964
2020-05-28 | 13:17 | 49.964
2020-05-28 | 13:17 | 49.965
2020-05-28 | 13:17 | 49.964
2020-05-28 | 13:17 | 49.964
2020-05-28 | 13:17 | 49.964
2020-05-28 | 13:17 | 49.963
2020-05-28 | 13:17 | 49.962
2020-05-28 | 13:17 | 49.96
2020-05-28 | 13:17 | 49.958
2020-05-28 | 13:17 | 49.961
2020-05-28 | 13:17 | 49.966
2020-05-28 | 13:17 | 49.97
2020-05-28 | 13:17 | 49.972
2020-05-28 | 13:17 | 49.975
2020-05-28 | 13:17 | 49.978
2020-05-28 | 13:17 | 49.98
2020-05-28 | 13:17 | 49.981
2020-05-28 | 13:17 | 49.983
2020-05-28 | 13:17 | 49.982
2020-05-28 | 13:17 | 49.979
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.975
2020-05-28 | 13:17 | 49.972
2020-05-28 | 13:17 | 49.97
2020-05-28 | 13:17 | 49.969
2020-05-28 | 13:17 | 49.97
2020-05-28 | 13:17 | 49.975
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.978
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.975
2020-05-28 | 13:17 | 49.973
2020-05-28 | 13:17 | 49.973
2020-05-28 | 13:17 | 49.973
2020-05-28 | 13:17 | 49.975
2020-05-28 | 13:17 | 49.974
2020-05-28 | 13:17 | 49.974
2020-05-28 | 13:17 | 49.974
2020-05-28 | 13:17 | 49.976
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.978
2020-05-28 | 13:17 | 49.979
2020-05-28 | 13:17 | 49.979
2020-05-28 | 13:17 | 49.978
2020-05-28 | 13:17 | 49.978
2020-05-28 | 13:17 | 49.979
2020-05-28 | 13:17 | 49.98
2020-05-28 | 13:17 | 49.977
2020-05-28 | 13:17 | 49.975
2020-05-28 | 13:17 | 49.969
2020-05-28 | 13:17 | 49.965
2020-05-28 | 13:18 | 49.964
2020-05-28 | 13:18 | 49.964
2020-05-28 | 13:18 | 49.963
2020-05-28 | 13:18 | 49.964
2020-05-28 | 13:18 | 49.965
2020-05-28 | 13:18 | 49.966
2020-05-28 | 13:18 | 49.967
2020-05-28 | 13:18 | 49.968
2020-05-28 | 13:18 | 49.968
2020-05-28 | 13:18 | 49.968
2020-05-28 | 13:18 | 49.965
2020-05-28 | 13:18 | 49.964
2020-05-28 | 13:18 | 49.961
2020-05-28 | 13:18 | 49.958
2020-05-28 | 13:18 | 49.958
2020-05-28 | 13:18 | 49.961
2020-05-28 | 13:18 | 49.964
2020-05-28 | 13:18 | 49.968
2020-05-28 | 13:18 | 49.974
2020-05-28 | 13:18 | 49.977
2020-05-28 | 13:18 | 49.98
2020-05-28 | 13:18 | 49.983
2020-05-28 | 13:18 | 49.986
2020-05-28 | 13:18 | 49.985
2020-05-28 | 13:18 | 49.983
2020-05-28 | 13:18 | 49.983
2020-05-28 | 13:18 | 49.983
2020-05-28 | 13:18 | 49.982
2020-05-28 | 13:18 | 49.981
2020-05-28 | 13:18 | 49.983
2020-05-28 | 13:18 | 49.983
2020-05-28 | 13:18 | 49.981
2020-05-28 | 13:18 | 49.978
2020-05-28 | 13:18 | 49.975
2020-05-28 | 13:18 | 49.975
2020-05-28 | 13:18 | 49.977
2020-05-28 | 13:18 | 49.98
2020-05-28 | 13:18 | 49.981
2020-05-28 | 13:18 | 49.981
2020-05-28 | 13:18 | 49.98
2020-05-28 | 13:18 | 49.978
2020-05-28 | 13:18 | 49.975
2020-05-28 | 13:18 | 49.972
2020-05-28 | 13:18 | 49.972
2020-05-28 | 13:18 | 49.97
2020-05-28 | 13:18 | 49.97
2020-05-28 | 13:18 | 49.969
2020-05-28 | 13:18 | 49.97
2020-05-28 | 13:18 | 49.967
2020-05-28 | 13:18 | 49.965
2020-05-28 | 13:18 | 49.964
2020-05-28 | 13:18 | 49.963
2020-05-28 | 13:18 | 49.962
2020-05-28 | 13:18 | 49.963
2020-05-28 | 13:18 | 49.966
2020-05-28 | 13:18 | 49.969
2020-05-28 | 13:18 | 49.971
2020-05-28 | 13:18 | 49.974
2020-05-28 | 13:18 | 49.976
2020-05-28 | 13:18 | 49.979
2020-05-28 | 13:18 | 49.98
2020-05-28 | 13:19 | 49.981
2020-05-28 | 13:19 | 49.981
2020-05-28 | 13:19 | 49.982
2020-05-28 | 13:19 | 49.985
2020-05-28 | 13:19 | 49.985
2020-05-28 | 13:19 | 49.986
2020-05-28 | 13:19 | 49.987
2020-05-28 | 13:19 | 49.989
2020-05-28 | 13:19 | 49.991
2020-05-28 | 13:19 | 49.992
2020-05-28 | 13:19 | 49.993
2020-05-28 | 13:19 | 49.995
2020-05-28 | 13:19 | 49.997
2020-05-28 | 13:19 | 50.001
2020-05-28 | 13:19 | 50.003
2020-05-28 | 13:19 | 50.005
2020-05-28 | 13:19 | 50.008
2020-05-28 | 13:19 | 50.012
2020-05-28 | 13:19 | 50.013
2020-05-28 | 13:19 | 50.014
2020-05-28 | 13:19 | 50.014
2020-05-28 | 13:19 | 50.013
2020-05-28 | 13:19 | 50.014
2020-05-28 | 13:19 | 50.013
2020-05-28 | 13:19 | 50.014
2020-05-28 | 13:19 | 50.015
2020-05-28 | 13:19 | 50.014
2020-05-28 | 13:19 | 50.012
2020-05-28 | 13:19 | 50.012