## Sheet 1
Publication date | Question source | Topic | Question number | Question | Answer
2020-08-21 | Questions from the soft launch webinar | Day ahead procurement | 1 | How are the ESO able to do Day Ahead procurement for DC in a relatively short timescale when it takes longer with the existing reserve products? | Our plans to move our markets closer to real time are part of our overall frequency reform activity which also includes the introduction of new products. In determining our plans, it is critical we ensure we meet the operability needs of the system. For reserve, we are developing a fully automated daily procurement approach which needs to be supported by systems and are focused on doing this to enable procurement for April next year when our current STOR contracts cease. We see value to the system and GB consumers in launching Dynamic Containment this autumn and want to launch this new market, so it is as close to the end state as we desire. As set out in our various roadmaps, we intend to move our procurement closer to real time so are taking the opportunity to commence day ahead procurement with the introduction of this new product.
2020-08-21 | Questions from the soft launch webinar | Real time metering and baselines | 2 | Real-time metering and Baselining for non—BM units will be retrospective – how is this helpful and compliant? | Retrospective is obviously not as helpful or useful – but we are aware that we need to strike a balance between participation (and growing a market) and visibility for our control room. This is why we have a 6-month period for the developments to take place – ultimately, we will need ALL providers to give us real time data and visible baselines.
2020-08-21 | Questions from the soft launch webinar | Stacking | 3 | Can you stack DC with other BM instructions? | Providers can be available in the BM for bids/offers but must submit parameters that if accepted would allow the delivery of the BOA and the contracted quantity of DC. It is the responsibility of the provider to ensure that it can deliver the full quantity of DC throughout the contract – we will not prohibit providers who can manage this and BOAs at the same time.
2020-08-21 | Questions from the soft launch webinar | Unit cap | 4 | What is the unit cap per BMU? | 50MW per unit.
2020-08-21 | Questions from the soft launch webinar | Volume | 5 | Do you have an indication of size for the markets aside from the 1GW for DC (for Dynamic Regulation etc?). | This is still under development – our intention is to replace all current response products with the new product suite.
2020-08-21 | Questions from the soft launch webinar | Baselines | 6 | Can the asset decide not to follow their submitted baseline if for example between the SP and the SP+3, an event has occurred, and the asset has rebalanced its SoE from providing service? | This would be captured in the performance monitoring process and would likely entail a reduction in the availability payment. We will measure response delivery from the submitted baseline, so if a provider is not willing/able to follow its baseline its performance will appear poor. Also, deviation from baselines to manage SoE is not allowed.
2020-08-21 | Questions from the soft launch webinar | Contract length | 7 | How long will the contract period be? | 24 hours.
2020-08-21 | Questions from the soft launch webinar | Head/foot room | 8 | If the asset accounts for extra head/foot-room in the SoE can they use it in case of emergency i.e. extended event? | Yes, for MWh and no for MW. Over delivery of MW is treated the same as under delivery of MW. (e.g. delivering 12MW when the contracted quantity is 10MW is not desired by NGESO). Over delivery of MWh is allowed and would be helpful to NGESO in the event of a long duration of low/high frequency. (e.g. sustaining delivery for 20 minutes at full output when the requirement is 15 minutes – for energy limited providers – would be beneficial to NGESO’s ability to contain the frequency. Such an event is extremely rare.)
2020-08-21 | Questions from the soft launch webinar | Delivery | 9 | If you need to deliver between 0.5-1s full power, then how long should you keep this full delivery? And what happens next, is there a 15 min period off where you recharge your capabilities to be ready again? | Continuous service. Continually responding to frequency within 1 second at most. That’s why we have the SEM rules to allow Providers time to recover energy position following event.
2020-08-21 | Questions from the soft launch webinar | Stacking | 10 | Will this service be stackable with Bid/Offer actions in the BM? | Yes, you must be able to accept BOA’s. The provider must maintain ability to deliver service at all times.
2020-08-21 | Questions from the soft launch webinar | Volume | 11 | Is the 500 MW for low frequency in DC in addition to current FFR monthly? | Yes
2020-08-21 | Questions from the soft launch webinar | Renewable generation | 12 | Can renewable generators participate? | Yes, this service is open to all.
2020-08-21 | Questions from the soft launch webinar | Baselines | 13 | Will providers have to provide baselines 1 hour ahead of time? Are you concerned that this will stop potential providers from participating (e.g. DSR (domestic and I&C), renewables) in DC? | Baseline requirements are the same for all providers irrespective of if in the BM or not. Baselines are key, so we understand what assets intent to do. We consider it appropriate to have continued engagement on this.
2020-09-04 | Questions from the soft launch webinar | Procurement | 14 | Because DC won't replace FFR, does that mean it reduces mandatory FR? And if it doesn't, are you not over procuring contrary to SQSS? | DC is a tool to help the ESO manage the risks posed by largest losses, which are changing as we decarbonise the system. Response is a part of that, but we also currently take actions to maintain minimum inertia levels as well as restricting the output from largest losses. There are a range of actions we take to manage our largest losses on the system at the moment, particularly as we manage the interaction within a system that has reducing levels of inertia and whilst we complete the Accelerated Loss of Mains Change Programme to de-sensitise RoCoF relays. There are periods whereby we must reduce losses due to ROCOF and the introduction of DC will in the long term allow us to no longer take such actions? Update (4/9/20) - We view that ultimately our new frequency products will replace the old legacy frequency products. Until the new products are established and we have confidence in their delivery and impact on the system they will be procured in addition to our other services. As and when we have confidence the service can start to replace the current suite of products we will communicate to industry in a timely manner how this transition will work. As a prudent system operator, it is important we have the right level of confidence in making this transition.
2020-08-21 | Questions from the soft launch webinar | Volume | 15 | Where does the 1000MW end goal come from? | Largest losses and lower system inertia are the key reasons for this volume. The Requirements are set as a result of simulations run to forecast the need for our system stability in near future.
2020-08-21 | Questions from the soft launch webinar | Delivery | 16 | If baselined at +1MW, can a unit deliver fixed 1MW while frequency is in the deadband? | Yes – follow baseline. Only deviate in order to deliver response.
2020-08-21 | Questions from the soft launch webinar | Price cap | 17 | Will there be a price cap (or total payment cap) for this service above which National Grid ESO do not think it is financially viable to procure this service (as we see in monthly FFR)? | Yes.
2020-08-21 | Questions from the soft launch webinar | Interconnectors | 18 | Are interconnectors able to participate in DC? If so, is there a risk that smaller market participants could be displaced in the future? | This service is open to all. The geographical diversity of smaller providers is of value to us plus it would not be sensible for us to hold all our response on any single asset or indeed any group of assets in one location (the South East for example). We need liquid and competitive markets for our services.
2020-08-21 | Questions from the soft launch webinar | Baselines | 19 | What happens if I don't follow my baseline? | Your performance will appear poor and this will impact your payment. Response delivery is measured against the baseline. Example: unit is contracted to deliver 10MW of negative response: If your baseline is 0MW but you chose to operate at +5MW during a period where frequency unexpectedly moves to 50.5Hz we would expect to see an output of -10MW. Even if the asset responded proportionally and moved to -5MW this would appear to NGESO as only half the contracted quantity. This would be treated as under delivery and impact your payment.
2020-08-21 | Questions from the soft launch webinar | HF/LF | 20 | When high response is eventually procured, will there be a requirement to provide both (low and high) or they will be procured separately? | The intention is that they will be procured separately ideally with the option for providers to link bids by product (a high bid linked to a low bid).
2020-08-21 | Questions from the soft launch webinar | Baselines | 21 | Do you prefer that providers change their baselines continuously, or in <5% steps on the half hour? | However, you wish provided that the full contracted quantity of DC can be delivered at all times – even during ramping. If the unit is ‘energy limited’ it will have to abide by ramp-rate limits on all baselines submitted for the contract period. A maximum ramp rate of 5% per minute is allowed (as a % of the contacted quantity).
2020-08-21 | Questions from the soft launch webinar | Interconnectors | 22 | As an interconnector, will this be procured via the tendered market or bilaterally? | The procurement mechanisms will be the same for all providers.
2020-08-21 | Questions from the soft launch webinar | Product spec | 23 | When will the ESO publish a formal product spec for the initial phase and enduring phase to allow providers to develop their in-house hardware/software appropriately? | This is included in the consultation documents.
2020-08-21 | Questions from the soft launch webinar | State of Energy | 24 | If a duration asset is in the BM, but follows the SoE guidelines set by NG, will any issues with SoE as a result of BM instructions remain unpenalized? | No. If a unit wishes to be available for and accept BOAs at the same time as holding a DC obligation it must ensure its SoE remains in an acceptable range. This might be achieved by limiting the offer volume in the BM or adjusting some other BM parameters.
2020-08-21 | Questions from the soft launch webinar | Timeline of new products | 25 | Can ESO provide a timeline for specs being shared for the wider suite of new frequency products - Dynamic Reg / Moderation? | Our focus is on launching DC – timelines and details for subsequent services will follow.
2020-08-21 | Questions from the soft launch webinar | GSP | 26 | Will this service be eventually procured on a locational basis? | That is one of the options we are exploring. We require a geographically diverse supply of response and reserve – locational markets are one way to achieve this.
2020-08-21 | Questions from the soft launch webinar | Impact of new products | 27 | What impact will the procurement of DC will have on the volumes of Response that we currently procure through monthly FFR & the weekly auction trial? (I.e. will we be removing volume out of those markets to enable the procurement of DC). | These volumes are in addition to our current response requirements and not yet result in a reduction in procurement in our existing response markets. In the long term our intention is to replace our current products with the three new enduring response products, DC, DR and DM. The soft launch of DC is the first step towards this goal.
2020-08-21 | Questions from the soft launch webinar | Volume cap | 28 | What are the volume caps and size limits? | Up to 500MW of LF for Autumn and up to 1GW for 2021. There is a 50MW cap per unit.
2020-08-21 | Questions from the soft launch webinar | Service design | 29 | Timescales for go-live at end of September are tight. Is the service design locked down now & it’s just the procurement methodologies etc that we are consulting on? Providers will be keen to change their Control System algorithms asap so they can get their assets tested & validated by an ITE, in order to participate in DC from Day 1. Can we be clear that DC design is locked down so that Providers can go ahead with algorithm changes & testing? | The consultation comprises our proposal for the service design. It will be the final version of the service design barring any changes required or arising from the consultation. The point of the consultation is to seek a range of views and make sure the service is fit for purpose. However, we hope that any changes would be minor & not material following our (unofficial) consultation and engagement since early 2020.
2020-08-21 | Questions from the soft launch webinar | Delivery | 30 | The initial version of the service is one way only. There is only a very narrow deadband before we have to start delivering the first volumes (albeit small volumes). Would it be possible to deliver symmetrically in the first band to help with SoC management even if it is a one-way product? Alternatively, have you thought of getting rid of this first slope on the one-way product? We are only going to start the modelling of the one-way product now, so it may not be a huge issue. However, we have seen a lot of issues with SoC management on FFR because the frequency stays a little low for periods of time. I wouldn’t want the post fault product being drained due to narrow frequency deviation? | Providers should deliver the service to the specification detailed in the upcoming contract/consultation. If providing only low response, then there should be no deviation from the baseline when frequency is above 49.985Hz. State of energy management to be met via the submission of and following of baselines. NGESO is aware that frequency quality (or long periods of low/high frequency) is important to frequency response assets that need to manage their SoE.
2020-08-21 | Questions from the soft launch webinar | BM services | 31 | In the Dynamic Containment webinar, it was said that an asset could provide BM services alongside Dynamic Containment. Will this be allowed from the soft launch date of October? | We are aiming to publish the contracts as part of the consultation on Friday 21st August 2020, so information can be there on what is acceptable and required in the soft launch contract. Providers can be available in the BM for bids/offers but must submit parameters that if accepted would allow the delivery of the BOA and the contracted quantity of DC. It is the responsibility of the provider to ensure that it can deliver the full quantity of DC throughout the contract – we will not prohibit providers who can manage this and BOAs at the same time.
2020-08-21 | Questions from the soft launch webinar | Timeline of new products | 32 | Can you advise on dates we could expect existing FFR services to be displaced by new services - is this still Q4 2021 (March 2022) or does the ESO expect this to slip because of COVID-19 delays? | In the Response and Reserve Roadmap, we are signalling Q4 2021/22. We’re still exploring the impacts of COVID and if there are changes to dates, we will ensure these are communicated via the forward plan updates, and in our roadmap.
2020-09-04 | Questions from providers | State of Energy | 33 | For the State of Energy, you are required to declare that you’re unavailable if you run out of energy (or presumably are full and can take no more energy?). | Correct, there is a section in the service terms and guidance document on state of energy.
2020-09-04 | Questions from providers | Delivery | 34 | I also wasn’t clear how you make the declaration that you’re not available or you’re back on service (we want to specify our software to do this automatically)? | This is something we will need to finalise. It may be at the start of the service we only procure LF service but again this has not been finalised yet. For soft launch, it may be that the unit has to totally undeclare if it cannot meet its contracted requirement, again this will need further insight. I would encourage you to flag this through the consultation process please.
2020-09-04 | Questions from providers | Baselines | 35 | If we have a contact for service starting at 2300 tomorrow, are you expecting us to start submitting baselines at 2200 tomorrow? | Baselines should be submitted in line with Physical Notification timescales.
2020-09-04 | Questions from providers | Baselines | 36 | And finally, to what resolution do you want us to specify the baseline. If we specify a PN, its to the nearest integer MW. I infer from the document that you want better resolution than this? | Baselines should be submitted in line with rules and precedents for Physical Notifications, in this case an integer resolution is required.
2020-09-04 | Questions from providers | Unavailability | 37 | What is wasn’t clear on was if you are delivering both a LF and a HF service if you declare the unit unavailable or just the service that you cant deliver unavailable. For example, if your storage is empty, you can still make a HF service available. | This is a good point and one we need to consider. I suspect that initially there will only be a binary choice of "available or unavailable" regardless of if the unit is doing LF or LF+HF. In the future we should allow for one/either service to be notified independently of the other (e.g. a unit may be unavailable for LF but available for HF).
2020-09-04 | Questions from providers | Unavailability | 38 | If both services are unavailable, do you expect us to continue to follow the base line? | It would be helpful, but the service terms do not oblige it during periods of unavailability.
2020-09-04 | Questions from providers | ITE Reports | 39 | I assume NGESO will be accepting output for verification (ITE reports) before end September, to be in a position (barring consultation outcome) to launch 1st October? | As long as the testing doesn't change, we will accept the ITE report.
2020-09-04 | Questions from providers | Stacking | 40 | Are there any limitations on our uncontracted capacity, both MW and MWh. I.e. if we have a +/-50MW 50MWh system, and we tender +20MW into DC-low. Does that mean…? a) We have -50MW/+30MW power and 45MWh energy spare? (reserving 5MWh only for DC-low, i.e. 15mins…) b) We have a -50MW/+30MW and 40MWh energy spare? (reserving 10MWh only for DC-low, i.e. reserving 30mins). We assume the answer is a). ESO is not paying for b) in the current setup. however, b) would apply if tendering for HF and LF together. | Any uncontracted capacity is yours to do with as you wish. Provided, of course, that you can respect the DC service terms. The amount of spare capacity will depend on the asset characteristics and how you choose to model and optimise the asset - we cannot advise you on that.
2020-09-04 | Questions from providers | Re-balancing | 41 | In the draft terms. If we continue the above example, and we need to rebalance at, say, 1MW charge… Can we: a) also charge in the BM at -49MW (50MW minus 1MW charge) b) only charge in the BM at -30MW (50MW minus 20MW contracted capacity [albeit the ESO is contracting the other side of a battery]) c) only charge in the BM at -29MW (50MW minus 20MW contracted capacity, and 1MW rebalancing). We assume a). Again, the ESO isn’t paying for b) in the current setup and therefore should not be able to restrict it. Again, b) would apply if tendering for HF and LF together. | However you choose to charge, you must ensure that the unit can always deliver the full contracted quantity of DC. NGESO will not issue "SoE" BOAs, so you should not rely on using the BM to manage your SoE - this should be done via the submission of baselines.
2020-09-04 | Questions from providers | Transitional arrangements | 42 | Why is the ESO keeping 2/3 of the volume open to participants on the transitional arrangements. For us this is excessive and may decrease the quality. Furthermore, will consideration for full delivery capability be reflected in the service price acceptance? | The transitional arrangements have been designed to balance market accessibility and operational network security. Dynamic containment will be a key and enduring frequency response service for NGESO. We need to stimulate a liquid and competitive market for this service, hence our openness at this early stage. We balance this by time-limiting and volume-limiting the transitional arrangements, giving both the ESO and providers the time and opportunity to make system upgrades.
2020-09-04 | Questions from providers | Volume | 43 | Why is the volume limited to 500MW? | Initially we are only looking to buy up to 500MW of DC. We will give fair notice to the market if/when that limit changes. The initial limit of 500MW at the soft launch has been chosen to give the market an idea of the typical quantities that we will need to procure. Like any new service we will introduce DC in stages, learning as we go.
2020-09-04 | Questions from providers | Onboarding | 44 | For assets joining after the go-live date, what are the onboarding activities and timescales? | Please refer to the service terms and DC guidance document.
2020-09-04 | Questions from providers | Bidding | 45 | Imagine I have a 20MW battery and I’m entering the day ahead tender. As it is a daily product, I need to bid the same volume across the whole day. | This is correct, DC is (initially) a daily service.
2020-09-04 | Questions from providers | Bidding | 46 | How much should I bid? The probability of being called on the service is low so I would probably bid 20MW. However this means that for the entire 24 hour period I cannot charge the battery if I want to make sure I deliver the full 20MW capacity of the contract. If there is an event where I need to deliver energy I then have 2 choices. To stick properly to my 20 MW capacity I can’t adjust the baseline for the remainder of the 24 hour period. I would then have to adjust MW in the next open tender which could be for delivery in more than 24 hours time. This means I’m ensuring I can deliver my capacity but I might run out of energy. Alternatively I could put in a PN to charge at some point, ensuring I have sufficient energy but could be short on capacity if called. | Hopefully the Service Rules will be helpful, particularly section 6. NGESO can not specify how much (MW) any unit can/should bid into the DC tender, we cannot know the asset specifics in enough detail (cycle efficiency being the main one for batteries). However, your example highlights that a 20MW unit cannot bid for 20MW of symmetrical DC unless it has an infinite energy source, or enough energy to deliver 20MW continually for the 24hr contract periods. The actual quantity (MW) of DC that any energy limited unit can bid for will be dependent on its stored energy capacity, whether or not it is doing both LF and HF or just LF/HF. It will also be dependent on how much headroom/footroom the unit needs to maintain to meet the Energy Recovery requirement detailed in the Service Terms. Just one point to clarify: a unit may update its operational baseline at any time but (exactly like PNs) there is a 1hr gate before baselines can be changed. Please see the SoE example in the Guidance Document, and in the Service Terms webinar for a more detailed exploration of this topic.
2020-09-04 | Questions from providers | Bidding | 47 | The alternative is that I always bid 20MW less the volume I would need for charging to restore my battery if I were called. | Yes, this is basically what we want you to do. However, we are only asking that your unit is capable of recovering 20% of the Response Energy Volume in a 30min settlement period. The Service Terms webinar explains this in more detail.
2020-09-04 | Questions from providers | Baselines and State of Energy | 48 | However given the likelihood of being called is relatively low, this is likely to cost more for consumers as I would need to have a higher price per MW to deliver the same return on my battery. I think I would therefore go for the first strategy and cross my fingers that I wasn’t called too often. | You may well be correct on the cost-issue. However, DC is a crucial service for us, we are accepting of the need to pay a premium to guarantee the availability and firmness of the service. We absolutely do not want to 'cross our fingers and hope'!
2020-09-04 | Questions from providers | HF/LF | 49 | Can a unit contracted only for LF also provide HF for £0? This may be beneficial for SoE management for some units. | Initially we will only buy LF, we will inform the market as and when we are ready to accept bids for HF. The service terms require that units may only deliver the service that they have been contracted to deliver. Delivery of HF (in any form) would be viewed by our performance monitoring assessment as under-delivery against the requirement and would negatively impact payment to the provider.
2020-09-04 | Questions from providers | Metering | 50 | Can you confirm if the meter tolerance for measuring frequency is the same as for the FFR product? | Frequency will need to measure to 0.001Hz. Service Terms section 15 has the full details.
2020-09-04 | Questions from providers | Pre-qualification | 51 | Will pre-qualification be required before the soft launch? Given that the 20Hz requirement has been relaxed for delivery will assets that are currently running at 10Hz have to re-qualify at 20Hz? | All units will need to pass pre-qualification before participating in the soft launch. Performance Data can be provided at 10Hz for up to six months after go-live. A pre-qualification of the ability to provide data at 20Hz will be required (for those units that upgrade their capabilities from 10Hz to 20Hz). For the avoidance of doubt, testing must take place at 20Hz granularity.
2020-09-04 | Questions from providers | Testing | 52 | Will the pre-qualification acceptance bands be matched to the service delivery performance bands? For FFR there were substantial differences between the two definitions with the pre-qualification being much tighter. | The prequalification tests are not designed to replicate the service specification. This is deliberate because the tests aim to give NGESO confidence that the asset can deliver the service by testing elements of the delivery curve. Service delivery is fully detailed in the service specification.
2020-09-04 | Questions from providers | Response timings | 53 | Why is a delay in response required at all? The current start and end power, time windows don't overlap which complicates delivery. It would be great to discuss this and point 4 with someone on the design team. | It is key to us that we tightly specify how response is delivered so that we can accurately model how frequency should behave in certain events. Having too wide a range of acceptable delivery means that we would never really know what should be happening in the milliseconds after an event (as providers would respond in different ways). This makes post-event analysis all but impossible. It also potentially means that we can't be certain that our system is secure. 'Too fast' response can be as dangerous as 'too-slow' response, especially when other services that impact frequency (like stability services and protection relays) are considered.
2020-09-08 | Questions from providers | Restrictions on MEL or MIL | 54 | Is there a restriction on the MEL or MIL a BM unit should submit during the DC period? Is unavailability to provide the service declared through MELs and MILs or can these be used solely for indicating stacked BM capability. | There is no restriction other than that the MEL, MIL etc should reflect the units ability to deliver DC. If the contract quantity is 20MW and the baseline is at 0MW then the MEL should be at least 20MW. If there is 'spare' capacity, then this can be offered in the BM in the same way as usual. So, the MEL could be 30MW in the example above - this would indicate 10MW of headroom available to BOAs. Update (8/9/20) - Please be aware that the provider has sole responsibility for ensuring that any BOAs are deliverable in a manner that does not negatively impact the delivery or availability of DC. We will issue guidance on how/when to communicate unavailability, this is likely to be via fax directly to our control room.
2020-09-04 | Questions from providers | EDL Instruction Reason Codes | 55 | Will success of bids be confirmed through use of EDL Instruction Reason Codes to allow automated delivery? | Bids and Offers in the BM will be issued in exactly the same way as normal. The unit should ensure that BOA does not impact its ability to deliver DC - so the provider will need to be very careful with the offered volumes in the BM. If you are referencing to a DC tender, the ESO does not envisage sending mode instructions to BM units for the soft launch. We will communicate further on instructions closer to go-live.
2020-09-04 | Questions from providers | Testing | 56 | Are there any new metrics that need to be reported over the iEMS data concentrator? Specifically, in regards to energy management? | Yes there will be some additional requirements for DC. All required metering and monitoring data submissions are outlined in section 15 of the DC service terms.
2020-09-04 | Questions from providers | Testing | 57 | The pre-qualification does not appear to test delivery with over a PN. Will this be added? | We will not test delivery against a PN. However, as the Service Terms webinar made clear the unit should be capable of accurately following a PN.
2020-09-04 | Questions from providers | Testing | 58 | Will there be any tests to confirm that the values reported over the data concentrator match the values reported in the pre-qualification tests? | There will not be any additional tests to those that are outlined in the document.
2020-09-04 | Questions from providers | Go-live date | 59 | What is the go-live date and when will it be confirmed? | We are aiming for early October. The date is dependent on the responses to the consultation.
2020-10-21 | Questions from providers | Capacity Market | 60 | Is Dynamic Containment a Relevant Balancing Service under the Capacity Market Rules? | No, Dynamic Containment is not currently considered a Relevant Balancing Service under Schedule 4 of the Capacity Market Rules but we are having conversations with the EMR Delivery Body on how (and when) we can include the new suite of frequency response products into the Capacity Market rules. Update (21/10/20) – We have submitted a consultation response to Ofgem asking for the new services (DC, DM & DR) to be added as Relevant Balancing Services under Schedule 4 in the Capacity Market Rules. Whilst at present DC is not a Relevant Balancing Service within the Capacity Market (CM), CM providers do have the option to undertake post stress event Volume Reallocation to reduce or remove any penalty that may be due to non-delivery of CM Obligations. For more information, please see the EMRS guidance on Capacity Provider Payments: https://www.emrsettlement.co.uk/document/guidance/g17-capacity-provider-payments/
2020-09-04 | Questions from providers | Governor control | 61 | Do you expect synchronous generators/CCGTs to be able to offer this service through governor control on the steam turbine? | NGESO is technology neutral and encourages all assets able to meet the technical specification for dynamic containment to participate in this market.
2020-09-04 | Questions from providers | Contingency services | 62 | Are there plans for contingency services slower than 1 second? Faster is not always better. | As soon as possible after the launch of dynamic containment we will begin to consult on subsequent services. Dynamic regulation is a ‘slower’ service. Please refer to the Frequency Response and Reserve Roadmap for more information.
2020-09-04 | Questions from providers | Static | 63 | Why is the procurement level static and independent of the amount of inertia on the system at the time? | A range of factors, including inertia, impact the procurement level.
2020-09-04 | Questions from providers | Baselines | 64 | I understand that the baseline change can't be more that 5% of the amount of service you’re providing. This is clear when the amount of LF and HF is equal. What’s the limit when your service delivery is asymmetric? Suppose that I am delivering 15 MW of Low Frequency and 10 MW of High frequency – what is the maximum rate of change in my base line? | This is explained in the Service Terms and accompanying video. A baseline (for energy limited providers) may change by up to 5% of the contracted quantity per minute. Please see the Service Terms webinar for an explanation of how this applies in the case of asymmetrical quantities.
2020-09-04 | Questions from providers | EFA | 65 | For DC I was under the impression it would be procured by EFA, for each 24hr period; allowing the bidder to offer individual blocks, if that is all they are available for. The video released on the ESO Website suggests its 24hr or nothing? Can you please confirm? | For soft launch we will only be procuring a full EFA day. We will be transitioning to EFA blocks as time progresses but no firm timeline on that as of yet.
2020-09-04 | Questions from providers | Service Terms video | 66 | The Service Terms video states that all performance data has to be submitted within 1 hour, constantly. What is the approved method of doing this for a BMU? Excel? API ? other… ? | Correct, there will be an electronic file transfer every hour, most likely CSV. This will be confirmed in the next week and will be the same mechanism for BM and non-BM.
2020-09-04 | Questions from providers | Service Terms video | 67 | In the (Service Terms) video by Tom Freeman (very good vid) – I think this is incorrect:? - Surely for 6.9, 10% of 50MW of LF means that 2.5MW is required to increase active power ( not decrease as the slide states? ) - I think the slides has the words increase and decrease the wrong way around, | Thanks. A unit delivering LF will be increasing active power in response to low frequency. If that unit is energy limited it may need to submit a baseline that decreases active power to recover SoE. Using a battery as an example the LF delivery will discharge energy and therefore a baseline to charge will need to be submitted. It is for this reason that the ramp-rate limit would be calculated from the LF quantity and applied to baselines that decrease active power. In an extreme example where a unit provides 100MW LF and 2MW HF it would have ramp-rate limits for decreasing/charging and increasing/discharging baselines of 5MW/min and 0.1MW/min respectively.
2020-09-04 | Questions from the Procurement webinar | Volume | 68 | Is the 1GW of procurement for the enduring procurement 1GW of high and 1 GW of low or 1GW total of both? | Both. We expect to have an enduring ~1GW requirement for both low and high frequency dynamic containment. The actual requirement at any given time is highly dependent on the scale of the largest loss (demand and generation) but also dependent on the level of system inertia and the other frequency response services available to us.
2020-09-04 | Questions from the Procurement webinar | Pay as Bid | 69 | Am I correct in think Pay as Bid is temporary for the soft launch and NG ESO may use another method of bidding (Pay as Clear or other) in the future? | Yes, that’s correct. We are currently using pay as bid with the soft launch, and we will evaluate the methods in our preparation for the full delivery of DC. The learnings from the weekly auction will feed into this development.
2020-09-04 | Questions from the Procurement webinar | Volume | 70 | What's the minimum MW procurement you envisage daily? | Our requirement is for (up to) 500MW for the soft launch. There is no daily minimum “must buy” - we will assess our quantity requirement based on cost and risk as we do for all our balancing services.
2020-09-04 | Questions from the Procurement webinar | Bidding | 71 | Could you further clarify the rejection code 1? What are the "alternative costs" that can cause the DC bid to be rejected? Is it an FFR bid for ex? Can you give some more details on the calculation of the maximum economic price? | Dynamic containment will allow NGESO to take fewer actions in constraining largest losses or increasing inertia or use other services. The cap price will reflect our alternative cost.
2020-09-04 | Questions from the Procurement webinar | Bidding | 72 | Could you explain why not implementing divisible bids rather than rejecting bids leading to overholding? Dividing such bids would seems more efficient no? | We are taking a simple approach to begin with and will take the learning from the auction trial with respect to use of curtailable bids in developments for DC in the future.
2020-09-04 | Questions from the Procurement webinar | RTM | 73 | Will the RTM capable and non-RTM capable assets be assessed on equal economic footing? There should be a premium if you can deliver the full service. | All bids will be assessed in one assessment but we will not procure above 300MW of bids that fall into the transitional arrangements.
2020-09-04 | Questions from the Procurement webinar | Procurement | 74 | According to the participation document, the submission window for the weekly tender is 0700-1000 on Tuesday, please can you clarify further on timings? | Correct – weekly submission window is open 07:00-10:00 each Tuesday. It closes for Tuesday’s assessment at 10:00 on Tuesday, and then each subsequent weekday there is a 10:00 cut off should you wish to amend your price or withdraw your submission. 30/9/20 - Following engagement with Ofgem we will be running daily tenders, 7 days a week, procuring in 24 hour blocks 23:00-23:00.
2020-09-04 | Questions from the Procurement webinar | Price | 75 | For tendering, the provider submits a weeks worth of prices on the Tuesday. Can they amend those prices DA (and on Friday for Sat-Mon) or can they just withdraw? | Parties have the opportunity to both update their pricing or withdraw a bid at the day ahead stage. For weekends/bank holidays and Mondays, this would need to submitted by the close of the Friday window as we run the assessment on a Friday for Saturday, Sunday and Monday award.
2020-09-04 | Questions from the Procurement webinar | Procurement | 76 | Is the DC service been procured for delivery over EFA days or midnight to midnight? There have been some conflicting comments in the webinars vs the docs? | 23:00 – 23:00 so in line with EFA day.
2020-09-04 | Questions from the Procurement webinar | Price cap | 77 | Will there be a price cap? | Yes, we will have a price cap and it reflects our alternative cost.
2020-09-04 | Questions from the Procurement webinar | Bidding | 78 | The "random" method for identical bids seems odd; surely previous performance is taken into account and could be the defining factor? | We envisage this scenario to be extremely rare and is a method we have set out prior to tender so all parties are aware. Previous performance for a new service could possibly be a mechanism once the service has been established for a period of time. Thank you for this suggestion.
2020-09-04 | Questions from the Procurement webinar | Bidding | 79 | In Scenario 6, do you ever envisage a scenario when it is more cost effective to accept a larger unit which takes you over the 500MW cap? vs small expensive one | The reasons we set the 50MW unit cap are to increase the diversity of units (like location/ technology type) and reduce the impact of one single large unit failure. The order exceeds the 50MW unit cap will be rejected with code 4: Non-complaint submission.
2020-09-04 | Questions from the Procurement webinar | EFA | 80 | During Soft launch, do you intend to move to EFA block rather than 24h at any point? | At this stage we will be procuring for 24/7. Any changes to this will be communicated with appropriate notice to industry. You are encouraged to respond to the consultation with views on contract/block lengths.
2020-09-04 | Questions from the Procurement webinar | Bidding | 81 | Scenario 5: Could you clarify please why you would exclude one of the two bids with same offers, but accept a more expensive one with a different price? | Since the no-RTM cap is only 300 MW of procurement. Visibility is key for our Control Room and with this soft launch, only 300 MW of no-RTM is allowed so one is rejected and one accepted in this example although price is cheaper than the next options.
2020-09-04 | Questions from the Procurement webinar | Volume | 82 | Will the requirement for 450MW of FFR will change once 1GW is procured from Dynamic Containment? | Highly unlikely however the initial soft launch would allow us to assess the requirement volume for other services.
2020-09-04 | Questions from the Procurement webinar | State of Energy | 83 | The recommended SoE terms provided by the ESO; if a provider has a better alternative approach, will the ESO be amendable to a conversation on this? | We welcome feedback on the consultation documents through the pro forma response. If parties are able to submit any consultation responses sooner rather than later that would be much appreciated so we have as much time as possible to review.
2020-09-04 | Questions from the Procurement webinar | GSP | 84 | Aggregation to GSP group means that assets providing FFR will not be able to provide DC in the future. This create more barriers for small innovative projects. | At soft launch we are allowing aggregation at GSP group. We know there is a lot of interest in aggregation and we have committed to more engagement on this over the next twelve months. Please make use of the consultation period to share your views on this topic.
2020-09-04 | Questions from the Procurement webinar | Volume | 85 | How will the DC volume you intend to procure impact the dynamic FFR volumes you need from the market? When you expect the FFR volumes to be reduced by procurement of DC? Is that likely to remain unchanged throughout the soft launch? | Our requirement for DC is currently in addition to our dynamic containment volumes. Our enduring response product suite is made up of three products. DC is the first, DR and DM will follow and only when we’ve established those services will we look to review our FFR dynamic volumes
2020-09-04 | Questions from the Procurement webinar | Price | 86 | Will the max economic price be published with results? How often do you calculate the max economical price? Weekly or on a daily basis? The upper limit of the economic range NG are willing to accept? Could you share a range for the price cap as this it is a crucial element for participants (for example 50% to 100% higher that DLH)? Do you have an indication on what the cost of more economic alternative solutions are? So what sort of price levels you will be looking to optimise the programme prices against? | TBC in the following weeks.
2020-09-04 | Questions from the Procurement webinar | Price cap | 87 | Could you share a range for the price cap as this it is a crucial element for participants (for example 50% to 100% higher that DLH) | TBC in the following weeks.
2020-09-04 | Questions from the Procurement webinar | Economic alternatives | 88 | Do you have an indication on what the cost of more economic alternative solutions are? | Not at this time but this is likely to be a real-time (the assessment window) calculation of £/MW/h with multiple costs taken into account at the time of the assessment.
2020-09-04 | Questions from the Procurement webinar | Static FFR | 89 | With the launch of DC (LF only); will the traditional Static FFR be suspended for this period? | Static FFR will continue to be procured.
2020-09-04 | Questions from the Procurement webinar | EDL Instruction Reason Codes | 90 | Will success of bids be confirmed through use of EDL Instruction Reason Codes to allow automated delivery? | All results for soft launch will be published on the ESO website. We do not envisage EDL instruction for soft launch but will clarify this further in the published FAQ.
2020-09-04 | Questions from the Procurement webinar | Price | 91 | In the tendering document I read that prices will be limited to integer submission. Are you saying submissions can only be in whole pounds? | I believe this may be for MW submissions that have been read. We will double check that but please email in if you have seen otherwise. Price can be 2 decimals.
2020-09-04 | Questions from the Procurement webinar | Procurement | 92 | Is procurement via COUPA or EPEX? | Tender submissions are via an excel template to a dedicated email account for soft launch. Please reference the guidance document and tender rules for further information.
2020-09-04 | Questions from the Procurement webinar | Economic alternatives | 93 | Where is the information mentioned around economic alternatives for DC? | Slide 6 (in the Procurement Rules webinar slide pack).
2020-09-04 | Questions from the Procurement webinar | EPEX | 94 | Is there a reason the weekly EPEX dispatch platform is not being used for DC? Is this an indication that NGESO will not be continuing with EPEX in the future? | EPEX’s development for day ahead function will take a few months, therefore it cannot meet our soft launch timeline.
2020-09-04 | Questions from the Procurement webinar | Carbon intensity | 95 | Is there a carbon intensity calculation/consideration along with the economic calculation? | No
2020-09-04 | Questions from the Procurement webinar | Delivery | 96 | An asset on DC for the day "X", can do trading or BM in those hours when is not actively "delivering" DC, or shall not be used for other Route to Market? | With adherence to all service rules (Baseline submission, Realtime Monitoring and State of Energy / Charge management) it is possible for the asset to deliver active / reactive power to other markets, only as long as it can deliver the required DC volume to specification and while adhering to all other service rules.
2020-09-04 | Questions from the Onboarding webinar | Registration process | 97 | Please clarify further on allocation 13 calendar days timeframe? If assets are in FFR in September can they begin the registration process in September? | Yes, you can begin registration in parallel.
2020-09-04 | Questions from the Onboarding webinar | Submission timings | 98 | Why do you require weekly submission for a daily process? Why can I only withdraw volume rather than add it when I update on a day? | For the soft launch, several manual processes are in place. Therefore, we will collate the data on a weekly basis but there is the opportunity to update it daily. In the future, when we move to more sophisticated auction platforms and algorithms, the ambition is to move in that direction.
2020-09-04 | Questions from the Onboarding webinar | Submission timings | 99 | Why is the first day a Tuesday - I am more likely to change volumes on Friday once I know results of weekly FFR auction | For the soft launch, we wanted to ensure we had a week to run these processes and be able to learn as we go along. We felt if we left it to a Friday it would give us minimal opportunity during office hours to resolve any issues and work through other processes as we do this for the first time. For the enduring product, we are open to other suggestions and proposals through the consultation.
2020-09-04 | Questions from the Onboarding webinar | DM/DR | 100 | When will we hear more about Dynamic Moderation (DM) and Dynamic Regulation (DR)? | The soft launch of DC paves the way on how we implement and deal with our future suite of response products. We want to see how we interact with the control rooms tool kit, ensure we have the right processes in place and see how the market reacts. We would like to deliver DC first before bringing in DM and DR.
2020-09-04 | Questions from the Onboarding webinar | EFA | 101 | Is the aim to bring DC to EFA / hourly procurement, as daily procurement will clash with DFFR / LFS / DLH? | Yes, we are aiming to move to EFA procurement in the future.
2020-09-04 | Questions from the Testing webinar | 20Hz | 102 | Taken in account the short deadlines, can test be done with 10Hz frequency and interpolated to 20Hz similar to the performance reporting? | No. Testing must occur at 20Hz or better.
2020-09-04 | Questions from the Testing webinar | Delivery | 103 | Are you wanting linear delivery from +/-0.015 to +/-0.2 be linear (up to 5% at 0.2)? | Yes, delivery should be linear between those two points.
2020-09-04 | Questions from the Testing webinar | Response timings | 104 | Why do NG ESO not want any response prior to 0.5s - this could be quite difficult to get from an asset? | There should be no response delivery before 0.25s (not 0.5s). This is to allow us to maintain frequency stability.
2020-09-04 | Questions from the Testing webinar | 20Hz | 105 | Is testing the same for visible/non-visible DC units? Can you confirm performance and operational metering for non-visible is 10Hz but testing is at 20Hz? | All testing must occur at 20Hz.
2020-09-04 | Questions from the Testing webinar | Testing document | 106 | The testing guidelines are draft, are you expecting to change this and when will it be a full release | The testing guidance is referenced as draft for the consultation period. After the consultation period is concluded, the final version will be released. We are not anticipating any significant changes to the testing guidance.
2020-09-04 | Questions from the Testing webinar | GSP | 107 | For an aggregated unit can a group of assets can be submitted together and assessed at the aggregated unit level? | Yes, please be aware of the limited period of GSP group aggregation for GSP group under the transitional arrangements. ESO may still seek the individual asset metering details if requested.
2020-09-04 | Questions from the Testing webinar | Testing - DM/DR | 108 | Is it likely that if an asset passes the test for DC that it will qualify automatically for the other 2 products? | No, as the delivery profile of other frequency product is different from DC. To enter other frequency services, you will need to complete testing for these products.
2020-09-04 | Questions from the Testing webinar | ITE | 109 | How are ITE's updated about the new DC service; will this be new to them or have several already been contacted about the expectations of the new DC service? | ESO do not currently select or have recommended ITE’s. We would strongly encourage ITE’s to follow our webinars and published documents to familiarise themselves with the new service. It is worth mentioning that ITEs have been used by providers for 12 months now for FFR and weekly auctions.
2020-09-04 | Questions from the Testing webinar | Baselines | 110 | What will be the baseline used to perform the tests and assess the response delivered? | The provider can choose the baseline used during testing.
2020-09-04 | Questions from the Testing webinar | ITE | 111 | Is there a list of accepted Independent Technical Experts who can sign off the Test Certificate? | No, ESO do not provide recommendations for ITE’s. This is down to the party to select an appropriate ITE. It is worth noting that ITE’s have been used for the last 12 months.
2020-09-04 | Questions from the Testing webinar | Testing - support | 112 | For any internal DC testing; will the ESO guarantee 'support' to run these tests; assuming a check in with the Grid CCR is done first? - for BMU anyway. | ESO will seek to support all providers where appropriate in their journey for onboarding to the new service.
2020-09-04 | Questions from the Testing webinar | Testing - DM/DR | 113 | Is more testing required for dynamic regulation/moderation? Or does the DC testing cover participation in the new suite? | These services will have their own tests.
2020-09-04 | Questions from the Testing webinar | GSP | 114 | Aggregation to GSP group means that small innovative assets providing FFR toady won't be able to provide services in the future. will NG remove this barrier? | ESO will review the GSP group transitional arrangements and see how it progresses.
2020-09-04 | Questions from the Testing webinar | Grid Code | 115 | Will DC be defined in the Grid Code eventually? | That is not our intention, no. The Grid Code contains technical obligations on users who are CUSC parties i.e. have a bilateral connection agreement with ESO. Commercial Balancing Service providers are not necessarily CUSC parties. Any technical requirements specific to such a service will be defined in contractual documentation. In some cases this may refer to Grid Code obligations.
2020-09-08 | Questions from the Testing webinar | Testing | 116 | The frequency specification accuracy is 0.01Hz (2 DP), but the first knee joint is at 0.015Hz (3 DP), should the accuracy not be 0.001Hz (3DP)? | The accuracy threshold in table 8 (p16 of Testing Guidance) is a proofing error. The correct value, as identified by the questioner is 0.001Hz (3DP). We will rectify this error in a re-issued version of the testing guidance.
2020-09-08 | Questions from the Testing webinar | Metering | 117 | Will the correlation between the live operational metering (1Hz) and the performance metering (20Hz) be tested during the pre-qualification test? | There will be no specific test for this. However, we would expect providers to apply this kind of due diligence and calibration as per normal best practice.
2020-09-08 | Questions from the Testing webinar | Testing | 118 | Test 1 tolerance are expressed as % of expected response. This means low kW tolerance for small frequency deviation. Is this reasonable / intended? | Following review we have removed the % "allowable power tolerance" requirement from tests 1.3 and 1.4. For test 1.3 and 1.4 a noticeable change in power in the correct direction is required. These tests (1.3,1.4) ensure that the unit will start respond to small frequency deviations outside the deadband.
2020-09-08 | Questions from the Testing webinar | Deadband | 119 | If we had a known error of +0.005, then the deadband we would operate with would be -0.01/+0.02. Would this still be allowed as per the 0.01 accuracy for freq? | The question is unclear, can a specific example or more detail be provided?
2020-09-08 | Questions from the Testing webinar | Power Resolution | 120 | What power resolution is required for the test results? (how many decimal places do you want?) | The required resolution (number of decimal places) is dependent on the contracted quantity and required quantity and the delivery tolerances for each test. As a guide a 1MW contracted quantity would require 5DP to show compliance with some of the tests (e.g. 1.5) (assuming measurement in MW as requested).
2020-09-08 | Questions from the Testing webinar | Commercial impact | 121 | What is the commercial impact of an asset responding too quickly? Is the expectation that delivery speed is measured and slowed if too fast? | Delivery outside of the specification would be considered over/under performance and would result in a performance penalty and reduction in the availability fee paid to the provider.
2020-09-08 | Questions from the Testing webinar | Grid Code | 122 | Can you expand on the what is meant by the general Grid Code compliance? Which parts exactly does this refer to? | The GC is the technical requirements for parties that have a CUSC agreement with NGESO, not all providers of DC will be covered by this code. It is not our intention to codify the requirements for DC within the Grid Code.
2020-09-23 | Questions from providers | Ramp rates | 123 | I’m just working through the questions. I think that Q64 was the one I asked below, and if I understand the answer correctly, its referring me to page 16 of the service terms where it states: “Maximum ramp rate for Baselines The maximum ramp rate permitted at any point within a baseline submitted by an energy-limited provider as a % of contracted quantity Contract(h,l) RRbp(h.l) 5% The ramp rate limit can be calculated from the contracted quantity. There will be a different maximum ramp rate if the volumes of high/low response are different.” So if I am delivering 15 MW of low frequency, this means that I can ramp at a maximum of 0.75 MW/minute And if I am delivering 0 MW of high frequency, this means that I can ramp at a maximum of 0 MW/minute (in effect, I cant change load) When do these two different ramp rates apply? My first assumption was that when I was ramping up the LF limit would apply and when I was ramping down the HF limit would apply. But this doesn’t work, in the above example I would be delivering a 15 MW LF service, and delivering the service would cause me to discharge energy hence I would need to ramp up to recharge, which is fine. But when I’ve finished charging, I need to ramp down again, but I cant because my maximum ramp rate is 0 MW. | The ramp rate limits apply to baselines submitted by energy limited providers (updated 23/9/20). In the case of a provider that only provides LF, there will be one ramp rate limit that applies only to baselines that decrease the active power. If no HF is provided (as will be the case for all participants in the soft launch) then there is no ramp rate limit for baselines that increase the active power. In the specific example, the provision is 15MW of LF only. If the initial baseline is 0MW and subsequent to a low-frequency event, the unit needs to re-charge the stored energy then the baseline may move downwards (decrease of active power) at a maximum rate of 0.75mw/min. There is no restriction on baselines that move upwards (increase active power) in this particular case. For example, the baseline could move from 0MW to 10MW instantaneously.
2020-09-08 | Questions from providers | Performance metering | 124 | For a BMU battery, which has operational metering in place; all we need to do is record all performance metering at 10hz? There is no requirement to send in this data to the ESO, apart from on-request as specified in the documents? We just have to store and hold this data for assessment if needed – is this correct? Is there a requirement for BMU asset to submit performance data every hour under contract ( within one hour of delivery ) or did I dream this?! | In your specific situation the performance metering can be recorded at 10Hz (for the transitional period of 6 months, after which it must be at 20Hz). There is an additional requirement, on all providers, to submit that 10Hz/20Hz data to us as part of Performance Monitoring. The exact method is to be confirmed (but indication is that it will be by electronic file transfer) each hour, so you did not dream that!
2020-09-08 | Questions from providers | Grid Testing | 125 | Can this be performed at 10Hz to allow participating in the Soft Launch period? FAQ 51's answer was confusing, but the final sentence suggests 20Hz is needed for testing even if the unit will only be doing 10Hz in the Soft launch period? | Testing must occur at 20Hz.
2020-09-08 | Questions from providers | Operational Metering Fields | 126 | Is there a detailed spec of the fields needed (the field names, data types, examples etc) other than the high level description in section 15 of the DC Service Terms? | We need to produce this.
2020-09-08 | Questions from providers | Performance Metering Fields | 127 | Is there a detailed spec of the fields needed (the field names, data types, examples etc) other than the high level description in section 15 of the DC Service Terms? | We need to produce this.
2020-09-08 | Questions from providers | Performance Metering Submission | 128 | FAQ 66 states a CSV file sent every hour is a likely requirement. Is this required for the soft launch or is the minimum solution required to simply store 10Hz data for 3 months, and make it available on request? | This (hourly submission of performance metering) is a requirement for the soft launch. We will soon share more details on exactly how the file transfer will occur.
2020-09-08 | Questions from providers | Baselines | 129 | For soft launch the current real time baseline should be submitted via the existing operational metering route? Is there any requirement for the Soft Launch to retrospectively submit any additional baseline data if we have been submitting the current baseline real time? | If you already have a Data Concentrator connection then we will require your unit's baseline 1hr in advance (just like a PN). If there is no connection then we can accept the baseline as part of the Performance Metering submission each hour, in this case the baselines may be retrospective. It appears that you are already submitting baselines in real time, this is our preferred (and enduring) solution so there will be no further requirement.
2020-09-08 | Questions from providers | Tenders daily or weekly | 130 | There is some confusion as to whether the tenders will take place daily or weekly? The documentation seems conflicted here. Please can you confirm: a) Daily tenders for Day-ahead DC contracts for 24h (i.e. a tender every single day) b) Weekly tenders for 7xDC contracts for 24h (i.e. only one tender per week) | For the soft launch of Dynamic Containment, participants are required to submit their tender submission during the Tuesday market window outlining the days in which they seek to participate in the DC service for that service week. If no submission is made or days are excluded from this submission, they cannot participate until the following week. Parties then have the ability to send in an updated tender submission (with the exception of weekends and bank holidays) to amend their price or withdraw a bid. This re-submission must also take place in the market windows subsequent to any delivery day. In our first step of launching DC, we envisage that as we develop the service and we introduce further automation this process will likely evolve and develop. ESO have had feedback from our weekly auction that moving to forced daily submission will be a strain on providers resource. Therefore for the soft launch, we have opted to enable submission on a weekly basis allowing those parties who do not want to submit every day the opportunity to do so. The daily re-submission mechanism still allows parties to update on a daily basis or withdraw should their commercial position change with the exclusion of weekends and bank holidays. For clarity, the assessment for tender award is made on a daily basis with the exception of weekends and Mondays when this is conducted on a Friday. For further information on the tendering rules and submissions please refer to the Tender Rules document section 5 DC Tender Submissions, our Guidance document and the Procurement/Onboarding webinars that are published on our webpages. An example: Tuesday 1st 07-10: submit tender for Wed 2nd to Tue 8th, a quantity (MW) and a price (£/MW/hr) Tue 1st to Thur 3rd: • option to withdraw bid or change price for Wed, Thur, Fri • Daily results (at 14:00?) for Wed, Thur, Fri Fri 4th: • option to withdraw bid or change price for Sat, Sun, Mon • Daily results (all on Friday at 14:00?) for Sat, Sun, Mon Mon 7th: • option to withdraw bid or change price for Tue 8th • Daily result (at 14:00?) for Tue Thus if the Tuesday weekly submission tender does not include a bid for any particular day there will not be an opportunity to re-submit.
2020-09-08 | Questions from providers | Response Energy Payments | 131 | Will DC participants will be getting Response Energy Payments? | No. There will be no response energy payment. Availability only.
2020-09-08 | Questions from providers | Penalties | 132 | Penalties. The formulas seem to suggest that if delivery is greater than 7% out in a single settlement period in a week, then payment for that week could be £0? In a similar vein, there doesn’t appear to be any information on declaring out for maintenance / an outage. | On the unavailability point, unavailability will most likely be declared through the data concentrator. If a planned outage is known, parties should not be bidding for that particular period. You have interpreted the penalty formulas correctly.
2020-09-10 | Questions from providers | Bidding | 133 | If participant bids in high for free, what will happen? | In our soft launch, we will be procuring low frequency DC only. Submissions for high will be deemed non-compliant. To be clear, the service terms require that units may only deliver the service that they have been contracted to deliver. Delivery of HF (in any form) would be viewed by our performance monitoring assessment as under-delivery against the requirement and would negatively impact payment to the provider.
2020-09-10 | Questions from providers | Definition of response times | 134 | We are struggling with the current definition of response times. These only seem to make sense for a step based response and not a continuous service as DC is. The graphs used for illustration use 'required delivery quantity' on the y-axis, this does not appear to make sense, as the required quantity is constantly changing. It would be clearer if the timing criteria were described in terms of a time and power window, relative to contracted power not required power. Or further simplified as just a maximum/minimum ramp rate relative to contracted power. | We are minded to stick with our current definition of response times. Specifically, that response should be delivered within the time-limits and as defined against the 'required' quantity and not the 'contracted' quantity.
2020-09-10 | Questions from providers | Data concentrator | 135 | If sites don’t have the data concentrator connection, is it post event spot-check reporting (as we currently do in FFR) or something different? | If there is no connection to data concentrator or BM then Op Metering will also need to be submitted hourly via 'electronic file transfer' with all the Performance Metering. There is no spot-checking like in FFR. All providers submit their performance metering data hourly and we do full performance monitoring on all of them.
2020-09-10 | Questions from the Procurement webinar | Soft launch | 136 | How long is the soft launch expected to last? | We are currently exploring the longer term solution and how we can future-proof our operational needs and system development. We will procure low and high frequency separately for the full delivery of DC, and the period of time will be EFA blocks, potentially settlement periods. With full delivery of the service, and having reviewed how DC interacts with the control room’s toolkit, we will be looking to procure more volume than with the soft launch. We are aiming to deliver DC in full next year.
2020-09-10 | Questions from providers | Pricing | 137 | Will we publish all prices for both BMUs and non-BMUs? | Yes we will publish all prices and volumes.
2020-09-10 | Questions from providers | Grace period | 138 | Can you confirm that the grace period for operational metering, baselines etc. is 6 months? | The grace period is 6 months for Op metering, 10hz and baselines.
2020-09-11 | Questions from providers | ABSVD | 139 | It appears BM units have to select ABSVD? If so, am I correct that the LF only service means that we'll have to buy energy ourselves at market prices, and then give it away for free? Unless, could you confirm BM units get Response Energy Payments for DC? | There will be no response energy payments for DC. Any energy costs incurred by providers should be reflected in the availability price submitted by the unit. We appreciate that the exposure to energy volume and cost is unknown at the point of procurement but the DC service is expected to have low utilisation and small energy volumes. We will monitor the impact of ABSVD during the soft launch of the service and will change it if required later.
2020-09-11 | Questions from providers | ABSVD | 140 | Due to the soft launch LF only; BMUs being automatically ‘ABSVD=YES’ will penalise participants. Given they will have to pay for the charge power that doesn’t get ABSVD treatment. By applying ABSVD to the delivery means a provider won’t get a spill payment to compensate their charge power cost. If the service was symmetrical then it makes no issue; the prob is only caused by this being LF only. | We will monitor the impact of ABSVD during the soft launch of the service and will change it if required later.
2020-09-11 | Questions from providers | ABSVD | 141 | Clarification on how ABSVD will be applied: the current ABSVD clause is written to suit a bidirectional service and that, as low only for now, will BM units be at a disadvantage vs non-BM units (which will not have ABSVD applied for response energy volumes). | We will monitor the impact of ABSVD during the soft launch of the service and will change it if required later.
2020-09-11 | Questions from providers | Ramp rates | 142 | Service Terms 6.8 refers to ‘Maximum ramp rate’ but there is no definition of that within the glossary. For completeness please can you define what this actually means. | The definition can be found in the Service Terms on page 16.
2020-09-11 | Questions from providers | Unit cap | 143 | Is the 50MW unit cap related to the total response providers can offer or that the units registered capacity/TEC has to be no greater than 50MW? I assume a larger unit can participate but only being able to provide response up to 50MW. Is that correct? | The cap is on the volume of response we would accept. So a unit larger than 50MW would be able to register, but only able to register as a DC Response Unit with 50MW of capacity.
2020-09-11 | Questions from providers | SOGL | 144 | Will DC meet the pre-qualification standards for SOGL FCR products? | We believe we are compliant with SOGL Article 155.
2020-09-15 | Questions from providers | Real time metering | 145 | By RTM (Real Time metering) you are referring to BMU operational metering – is that correct? How was the 300/200MW split arrived at? | BMU operational metering is an acceptable method of providing RTM. Our transitional arrangements have been agreed after an internal risk review, balancing the relevant risks against our desire to stimulate a healthy market with as must participation as possible.
2020-09-15 | Questions from providers | Operation issues | 146 | Is there to be any dispensation for the early days of participation in DC (from penalties) if there are small operation issues – given provider naturally will not all be perfect first time in this new service? | We can not commit to doing this in every case but we are willing to learn alongside our providers throughout the soft launch. It would be best to highlight any operational challenges as soon as possible rather than disputing any performance penalty after the fact.
2020-09-15 | Questions from providers | Forced outage | 147 | In the event of any Forced outage on a unit delivering DC, a BMU would use MEL/MIL to signify as such; and performance data would reflect any cessation of operation. Is there any further communication needed , via fax for example? | (Un)availability should be communicated by fax into our control room.
2020-09-15 | Questions from providers | Pricing | 148 | Pricing will be done for the 24hr period a single price; how will the ESO really be able to compare to the alternative when a single rate doesn’t show the natural dip in price overnight or the natural elevated rate over an EFA 5 TRIAD period? A single rate artificially distorts the price and this the comparison? | More granular pricing is a development we may introduce in the future, there are possible benefits as the question describes. For the soft launch and foreseeable future, we believe our pricing structure gives us the flexibility and detail to secure the system in a cost-efficient manner.
2020-09-15 | Questions from providers | Bidding | 149 | During soft launch, can a BMU battery use Bids to manage SoE without compromise of DC performance rules? | Providers are allowed to participate in the BM at the same time as DC for any reason. However, the requirement to maintain/manage SoE is the sole responsibility of the provider and the ESO has no obligation to send BOAs to assist in this. The provider must be certain that their BM activity does not harm their ability to deliver the DC service. For this reason we advise that providers take great care when actively participating in the BM at the same time as DC.
2020-09-15 | Questions from providers | Pricing | 150 | How should a BMU manage Bid/offer prices during a DC commitment? Priced to £9999 to show inflexibility? | Yes.
2020-09-15 | Questions from providers | HF/LF | 151 | As the soft launch is for LF only, the contract must relate only to LF commitment; hence an asset is free to use HF periods to their commercial advantage – is this correct? | No. Please review Service Terms 6.6, 6.7.iv, 6.7.v, 6.11.vi and 6.13.
2020-09-15 | Questions from providers | Response Energy Payments | 152 | In relation to question 131, you state that no response energy will be paid; but in relation to a BMU delivering FFR , via CUSC 4.1.3.9A, response energy is paid; can you please confirm? | There will be no response energy payments for DC. Any energy costs incurred (or anticipated to be incurred) by providers should be reflected in the availability price submitted by the unit.
2020-09-16 | Questions from providers | International standards | 153 | How does our performance monitoring comply with international standards? | Performance metering and operational metering have different purposes, hence the different requirements. Our requirements for operational metering do align with the relevant sections of the Grid Code. Dynamic containment is a novel service therefore it is to be expected that the requirements for performance monitoring will also be novel. We have specified 20Hz metering as this gives the required granularity to adequately assess performance without imposing onerous costs on providers.
2020-09-16 | Questions from providers | Ramp rates | 154 | Page 16 of the Service Terms document defines the minimum ramp rate for response delivery as RRmin = Rx / (TdMax - TiMax), where TdMax is 1.0s and TiMax is 0.5s. The description states that RRmin is "the slowest ramp rate acceptable between change in response delivery and reaching the required delivery quantity". This description makes it very clear that a response rate slower than this is considered unacceptable, but can you confirm that the formula wasn't intended to be RRmin = Rx / (TdMax - TiMin)? This would result in the minimum ramp rate possible within the area highlighted green in the response figure below. | It is understandable that the questioner seeks clarification on this topic as the image and formulas do seem to contradict. For the avoidance of doubt the formulas defining min and max ramp rate are correct and will not be changed.
2020-09-23 | Questions from providers | Mock Tender | 155 | We are looking to enter the DC market early next year - are we able to join in on the DC mock tender that you scheduled for next week? | Yes, the mock tender is open to everyone who is interested to participate.
2020-09-23 | Questions from providers | Mock Tender | 156 | In order to participate in the Dynamic Containment mock auction trial, do the registered assets have to be genuine assets? | No, you can use a dummy asset to take part in the mock tender.
2020-09-23 | Questions from providers | Performance data | 157 | Could you please confirm how frequently performance data is expected to be sent to NG? | As per clause 15.3 in the Service Terms, performance data shall be submitted to NGESO on an hourly basis throughout the DC Service Day. Each csv file should contain a maximum of 1hrs worth of data sent as soon as possible after completion of the hour, but no later than 2hrs after completion of the hour in question.
2020-09-23 | Questions from providers | Data concentrator | 158 | For a BMU, is it expected that we connect to the data concentrator for this? Or is this still to be determined? | Yes as per clause 15.3 in the Service Terms, BMUs should also use the data concentrator connection for submission of performance data.
2020-09-23 | Questions from providers | Delivery | 159 | The Dynamic Containment soft launch tender due to start on 1st Oct. – I understand this is for low frequency Day-ahead pay as bid tender but when is delivery for again (the next day on a daily basis?) | Delivery is from 23:00-23:00 daily e.g. submit before 10am on Tuesday, deliver 23:00 Tuesday to 23:00 Wednesday.
2020-09-23 | Questions from providers | Mock Tender | 160 | Can I check with you whether there will be an element of price discovery to Thursday's mock DC tender? i.e. will you be treating it as if it were a live tender and publish results with National Grid's respective bid ladder as you do in the Phase 2 trial? | No, the main purpose of the mock tender is to test the E2E process, price discovery is out of scope. We will use a dummy price, so please do not treat the mock clearing price as the indicative price. However, we will publish the tender results to help participants understand how the assessment rules work.
2020-09-23 | Questions from providers | Rebalancing | 161 | During FFR delivery we performed rebalancing analysis and scheduling towards the end of the settlement period, performing the analysis then immediately submitting a PN before gate closure. This gives the minimum delay between responding to an event and recovering the energy. In the dynamic containment Service Terms (6.11.i) it states that assessment must be performed at the start of the settlement period, this leads to an additional settlement period before the energy is recovered. In practice, would we be penalised for performing the rebalancing earlier? | Asking providers to assess their rebalancing at the start of a settlement period allows them to use a whole SP for calculation and submission of a new baseline. We think some providers might need this time but we will not penalise providers that chose to assess and action rebalancing at the end of a SP - provided that they remain capable of delivering the required energy volume.
2020-09-23 | Questions from providers | Mock Tender | 162 | Could you confirm if an asset will need a completed ITE Report to take part in the DC mock tender? | An asset doesn’t need to complete an ITE Report to take part in the DC mock tender.
2020-09-30 | Questions from the Mock Tender review webinar | Price cap | 163 | Is £10/MW/h an indicative value for the price cap? | No. Price discovery is out of the scope of this testing, thus dummy prices were used. Please do not take the mock clearing price as the indicative price
2020-09-30 | Questions from the Mock Tender review webinar | Tender submission | 164 | If the first tender submission (on the Tuesday for the week) is rejected because it is not compliant, can the provider update in the daily submissions? | No, any submission needs to be submitted fully compliant.
2020-09-30 | Questions from the Mock Tender review webinar | Tender results | 165 | So from next week onwards, tender results will be published on Tuesday's? | No, results are published on a daily basis. The requirements for data submissions have a number of deadlines. These are outlined in the Participation Guidance Document.
2020-09-30 | Questions from the Mock Tender review webinar | Confirmation receipt | 166 | Once a TT has been submitted will we get a confirmation back to confirm receipt? | No, due to the short timeline, we won't be able to send out the confirmation in the soft launch phase.
2020-09-30 | Questions from the Mock Tender review webinar | Tender templates | 167 | Are there plans to mitigate the issues experienced with tender templates (such as case sensitivity / file type ) by automating through an online portal? | Yes. We are looking forward to enhancing automation as we move through the development lifecycle of DC. And soft launch is a learning by doing launch. Please engage with us and share with us the improvements you would like to see.
2020-09-30 | Questions from the Mock Tender review webinar | Unit technology | 168 | Like the monthly FFR auction results, will unit technology be published as well? | Yes, we can do.
2020-09-30 | Questions from the Mock Tender review webinar | Performance and payment reduction | 169 | When will performance and payment reduction be shared with providers? Will this be daily? | On a monthly basis, in line with payment runs.
2020-09-30 | Questions from the Mock Tender review webinar | Metering | 170 | Can the meter point be confirmed? Is it ok to meter at the asset (LV side) or must this be done at the site boundary meter? Guidance not clear under FFR currently | Metering must show the performance of the eligible asset. The location of the metering will therefore be site specific.
2020-09-30 | Questions from providers | Baselines | 171 | Should the baseline bring us back to 50% SoC or just into the acceptable SoC range, and are we right in thinking that we define that range ourselves based on being able to deliver the product? | The baseline should aim to return the SoE to the acceptable range. The unit should always aim to have sufficient stored energy to deliver at least the minimum energy requirement.
2020-09-30 | Questions from providers | Baselines | 172 | If DC delivery is measured on top of the baseline does this effectively mean the baseline needs to be as accurate as DC, and so during the ramps on the baseline do the ramps also have to be accurate when measured at 20Hz frequency? | Every unit will need to be able to follow its baseline with a high degree of precision. DC delivery is measured against the baseline, so if the unit is not able to follow the baseline it will appear that DC delivery is poor.
2020-09-30 | Questions from providers | Performance data | 173 | Within the docs it states that performance data is to be "sent after the SP in question to verify accuracy of performance; sent hourly at a 20Hz granularity." Can we confirm exactly what window of performance data we are sending each hour? Is it the previous hour's, the previous SP, the last 24 hours, etc. And how long do we have to send it. I.e. at 13:00 do we need to send you the data from 12:00-13:00, or 11:30-12:30 (giving us 30 minutes processing time) | You should send the previous hour's performance data. You should aim to send the data to us no more than a few hours after the completion of the hour, so 30 minutes for processing is entirely acceptable.
2020-09-30 | Questions from providers | Ramp rates | 174 | Is the 5% ramp rate a maximum, or a target rate (explicit or preferred) or are we able to ramp at anything up to 5% as long as we recover the required energy? and on the commercials | The ramp rate for baselines is a maximum. You may choose to ramp slower but may not ramp any faster.
2020-09-30 | Questions from providers | Unavailability | 175 | With the current wording it looks like if we were to declare unavailable during the contracted day (due to a fault for example), or for some reason had another issue that could cause a performance penalty, the week's payment would be lost. So there is no incentive for us to either continue that day or participate for the rest of the week, is this correct? | The consequence you highlight is not the kind of behaviour we want to encourage. We are looking again at our performance penalties to make them less onerous.
2020-10-14 | Questions from providers | Weekly Auction | 176 | The alignment of the DC and Weekly DFFR should be made. There will be conflict over a Saturday bid for both; given the market window for DC is 07:00 – 10:00 and the results for weekly DFFR are not known until around lunchtime Friday. Can the results for Weekly DFFR be made available earlier to allow more time to make an effective DC changes if needed? | We are currently exploring the interactions between the daily and weekly auctions. We will provide an update once a decision has been made.
2020-10-14 | Questions from providers | Performance data | 177 | I understand the need to submit hourly, with regards to avoid huge amounts of data to be submitted in one go for each day. Would it be ok, to still deliver data each hour, but for that data to be for the previous day i.e. it be 24 hours old? This would make our lives easier from a dev perspective. | We require the performance data that is no more than a few hours old. A delay of 24 hours is not acceptable. We would be interested to know what drives your reason for requesting a 24 hour delay.
2020-10-14 | Questions from providers | Tender results | 178 | I saw the results published from the first day of the tender but I can’t find any more since the 1st Oct. Can I just check if there are any more tender results and where they are kept on the website? | The master file named ‘DC Masterdata’ on the ESO Data Portal contains the results from the previous tenders.
2020-10-14 | Questions from providers | Alternative cost | 179 | Will there be a comprehensive list of all available alternative economic actions that NGESO will be considering? | Slide 6 in the Mock Tender review webinar slides (https://www.nationalgrideso.com/document/177191/download) sets out alternative actions NGESO may take, such as: • Frequency Response services • Increase inertia • Reduce Loss of Mains loss size (ALOMCP) • Avoiding unintended tripping of distributed resources The latest market information report for Dynamic Containment can be found here: https://data.nationalgrideso.com/ancillary-services/dynamic-containment-data and contains all tenders submitted to date, their prices and whether they were accepted and rejected (as well as reasons codes for rejection).