## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20200702-1 | Loss of SPLN-1 | Trip of GT | 2020-07-02 | 15:53 | N/A | Refer to tab 'Event 20200702-1' | 49.947 | 49.724 | -0.029 | 385 | -385 | N/A | N/A | N/A | 331.5447
Event 20200703-1 | Trip of WBURB-2 |  | 2020-07-03 | 15:59 | N/A | Refer to tab 'Event 20200703-1' | 49.931 | 49.879 | -0.016 | 252 | -252 | N/A | N/A | N/A | 393.2066
Event 20200703-2 | Trip of GRAI-8 | Output reduced gradually | 2020-07-03 | 18:30 | N/A | Refer to tab 'Event 20200703-2' | 50.02 | 49.878 | N/A | 377 | -377 | N/A | N/A | N/A | N/A
Event 20200706-1 | Trip of HOWAO-2 & HOWAO-3 |  | 2020-07-06 | 13:33 | N/A | Refer to tab 'Event 20200706-1' | 49.95 | 49.685 | -0.076 | HOWAO2 200, HOWAO3 344 | -544 | N/A | N/A | N/A | Under Investigation
Event 20200708-1 | Trip of IFA Bipole 1 |  | 2020-07-08 | 6:21 | N/A | Refer to tab 'Event 20200708-1' | 49.95 | 50.327 | 0.09 | 1000 | 1000 | N/A | N/A | N/A | 277.5
Event 20200708-2 | Trip of IFA Bipole 2 |  | 2020-07-08 | 10:47 | N/A | Refer to tab 'Event 20200708-2' | 49.926 | 50.321 | 0.078 | 1030 | 1030 | N/A | N/A | N/A | 329.6396
Event 20200713-1 | Trip of STAY-1 |  | 2020-07-13 | 10:13 | N/A | Refer to tab 'Event 20200713-1' | 49.984 | 49.794 | -0.023 | 404 | -404 | N/A | N/A | N/A | 438.9899

## Event 20200702-1
In UTC
Date | Time | Freq
2020-07-02 | 14:52 | 49.92
2020-07-02 | 14:52 | 49.919
2020-07-02 | 14:52 | 49.918
2020-07-02 | 14:52 | 49.918
2020-07-02 | 14:52 | 49.918
2020-07-02 | 14:52 | 49.916
2020-07-02 | 14:52 | 49.915
2020-07-02 | 14:52 | 49.916
2020-07-02 | 14:52 | 49.914
2020-07-02 | 14:52 | 49.914
2020-07-02 | 14:52 | 49.913
2020-07-02 | 14:52 | 49.912
2020-07-02 | 14:52 | 49.913
2020-07-02 | 14:52 | 49.912
2020-07-02 | 14:52 | 49.91
2020-07-02 | 14:52 | 49.911
2020-07-02 | 14:52 | 49.911
2020-07-02 | 14:52 | 49.91
2020-07-02 | 14:52 | 49.909
2020-07-02 | 14:52 | 49.908
2020-07-02 | 14:52 | 49.908
2020-07-02 | 14:52 | 49.908
2020-07-02 | 14:52 | 49.908
2020-07-02 | 14:52 | 49.91
2020-07-02 | 14:52 | 49.911
2020-07-02 | 14:52 | 49.913
2020-07-02 | 14:52 | 49.915
2020-07-02 | 14:52 | 49.917
2020-07-02 | 14:52 | 49.918
2020-07-02 | 14:52 | 49.919
2020-07-02 | 14:52 | 49.921
2020-07-02 | 14:53 | 49.924
2020-07-02 | 14:53 | 49.926
2020-07-02 | 14:53 | 49.927
2020-07-02 | 14:53 | 49.928
2020-07-02 | 14:53 | 49.931
2020-07-02 | 14:53 | 49.933
2020-07-02 | 14:53 | 49.936
2020-07-02 | 14:53 | 49.938
2020-07-02 | 14:53 | 49.941
2020-07-02 | 14:53 | 49.942
2020-07-02 | 14:53 | 49.943
2020-07-02 | 14:53 | 49.943
2020-07-02 | 14:53 | 49.944
2020-07-02 | 14:53 | 49.943
2020-07-02 | 14:53 | 49.942
2020-07-02 | 14:53 | 49.941
2020-07-02 | 14:53 | 49.94
2020-07-02 | 14:53 | 49.94
2020-07-02 | 14:53 | 49.942
2020-07-02 | 14:53 | 49.943
2020-07-02 | 14:53 | 49.945
2020-07-02 | 14:53 | 49.945
2020-07-02 | 14:53 | 49.946
2020-07-02 | 14:53 | 49.946
2020-07-02 | 14:53 | 49.948
2020-07-02 | 14:53 | 49.95
2020-07-02 | 14:53 | 49.951
2020-07-02 | 14:53 | 49.953
2020-07-02 | 14:53 | 49.951
2020-07-02 | 14:53 | 49.949
2020-07-02 | 14:53 | 49.95
2020-07-02 | 14:53 | 49.948
2020-07-02 | 14:53 | 49.946
2020-07-02 | 14:53 | 49.947
2020-07-02 | 14:53 | 49.946
2020-07-02 | 14:53 | 49.941
2020-07-02 | 14:53 | 49.921
2020-07-02 | 14:53 | 49.903
2020-07-02 | 14:53 | 49.881
2020-07-02 | 14:53 | 49.857
2020-07-02 | 14:53 | 49.837
2020-07-02 | 14:53 | 49.82
2020-07-02 | 14:53 | 49.808
2020-07-02 | 14:53 | 49.799
2020-07-02 | 14:53 | 49.79
2020-07-02 | 14:53 | 49.783
2020-07-02 | 14:53 | 49.779
2020-07-02 | 14:53 | 49.776
2020-07-02 | 14:53 | 49.774
2020-07-02 | 14:53 | 49.772
2020-07-02 | 14:53 | 49.772
2020-07-02 | 14:53 | 49.771
2020-07-02 | 14:53 | 49.77
2020-07-02 | 14:53 | 49.768
2020-07-02 | 14:53 | 49.766
2020-07-02 | 14:53 | 49.764
2020-07-02 | 14:53 | 49.76
2020-07-02 | 14:53 | 49.756
2020-07-02 | 14:53 | 49.752
2020-07-02 | 14:54 | 49.747
2020-07-02 | 14:54 | 49.744
2020-07-02 | 14:54 | 49.742
2020-07-02 | 14:54 | 49.741
2020-07-02 | 14:54 | 49.738
2020-07-02 | 14:54 | 49.742
2020-07-02 | 14:54 | 49.739
2020-07-02 | 14:54 | 49.738
2020-07-02 | 14:54 | 49.733
2020-07-02 | 14:54 | 49.729
2020-07-02 | 14:54 | 49.727
2020-07-02 | 14:54 | 49.725
2020-07-02 | 14:54 | 49.725
2020-07-02 | 14:54 | 49.724
2020-07-02 | 14:54 | 49.724
2020-07-02 | 14:54 | 49.725
2020-07-02 | 14:54 | 49.726
2020-07-02 | 14:54 | 49.727
2020-07-02 | 14:54 | 49.728
2020-07-02 | 14:54 | 49.73
2020-07-02 | 14:54 | 49.731
2020-07-02 | 14:54 | 49.731
2020-07-02 | 14:54 | 49.731
2020-07-02 | 14:54 | 49.729
2020-07-02 | 14:54 | 49.73
2020-07-02 | 14:54 | 49.729
2020-07-02 | 14:54 | 49.727
2020-07-02 | 14:54 | 49.725
2020-07-02 | 14:54 | 49.726
2020-07-02 | 14:54 | 49.728
2020-07-02 | 14:54 | 49.73
2020-07-02 | 14:54 | 49.732
2020-07-02 | 14:54 | 49.734
2020-07-02 | 14:54 | 49.736
2020-07-02 | 14:54 | 49.738
2020-07-02 | 14:54 | 49.741
2020-07-02 | 14:54 | 49.747
2020-07-02 | 14:54 | 49.751
2020-07-02 | 14:54 | 49.755
2020-07-02 | 14:54 | 49.758
2020-07-02 | 14:54 | 49.761
2020-07-02 | 14:54 | 49.762
2020-07-02 | 14:54 | 49.764
2020-07-02 | 14:54 | 49.765
2020-07-02 | 14:54 | 49.767
2020-07-02 | 14:54 | 49.767
2020-07-02 | 14:54 | 49.77
2020-07-02 | 14:54 | 49.772
2020-07-02 | 14:54 | 49.773
2020-07-02 | 14:54 | 49.774
2020-07-02 | 14:54 | 49.774
2020-07-02 | 14:54 | 49.775
2020-07-02 | 14:54 | 49.775
2020-07-02 | 14:54 | 49.774
2020-07-02 | 14:54 | 49.775
2020-07-02 | 14:54 | 49.775
2020-07-02 | 14:54 | 49.775
2020-07-02 | 14:54 | 49.775
2020-07-02 | 14:54 | 49.778
2020-07-02 | 14:54 | 49.778
2020-07-02 | 14:54 | 49.779
2020-07-02 | 14:55 | 49.78
2020-07-02 | 14:55 | 49.78
2020-07-02 | 14:55 | 49.781
2020-07-02 | 14:55 | 49.784
2020-07-02 | 14:55 | 49.787
2020-07-02 | 14:55 | 49.791
2020-07-02 | 14:55 | 49.795
2020-07-02 | 14:55 | 49.799
2020-07-02 | 14:55 | 49.802
2020-07-02 | 14:55 | 49.803
2020-07-02 | 14:55 | 49.805
2020-07-02 | 14:55 | 49.807
2020-07-02 | 14:55 | 49.809
2020-07-02 | 14:55 | 49.814
2020-07-02 | 14:55 | 49.816
2020-07-02 | 14:55 | 49.818
2020-07-02 | 14:55 | 49.822
2020-07-02 | 14:55 | 49.823
2020-07-02 | 14:55 | 49.824
2020-07-02 | 14:55 | 49.824
2020-07-02 | 14:55 | 49.822
2020-07-02 | 14:55 | 49.821
2020-07-02 | 14:55 | 49.817
2020-07-02 | 14:55 | 49.813
2020-07-02 | 14:55 | 49.81
2020-07-02 | 14:55 | 49.807
2020-07-02 | 14:55 | 49.806
2020-07-02 | 14:55 | 49.805
2020-07-02 | 14:55 | 49.804
2020-07-02 | 14:55 | 49.802
2020-07-02 | 14:55 | 49.799
2020-07-02 | 14:55 | 49.798
2020-07-02 | 14:55 | 49.795
2020-07-02 | 14:55 | 49.794
2020-07-02 | 14:55 | 49.794
2020-07-02 | 14:55 | 49.794
2020-07-02 | 14:55 | 49.795
2020-07-02 | 14:55 | 49.796
2020-07-02 | 14:55 | 49.799
2020-07-02 | 14:55 | 49.799
2020-07-02 | 14:55 | 49.801
2020-07-02 | 14:55 | 49.8
2020-07-02 | 14:55 | 49.8
2020-07-02 | 14:55 | 49.8
2020-07-02 | 14:55 | 49.802
2020-07-02 | 14:55 | 49.802
2020-07-02 | 14:55 | 49.801
2020-07-02 | 14:55 | 49.801
2020-07-02 | 14:55 | 49.798
2020-07-02 | 14:55 | 49.798
2020-07-02 | 14:55 | 49.8
2020-07-02 | 14:55 | 49.799
2020-07-02 | 14:55 | 49.8
2020-07-02 | 14:55 | 49.799
2020-07-02 | 14:55 | 49.8
2020-07-02 | 14:55 | 49.802
2020-07-02 | 14:55 | 49.805
2020-07-02 | 14:55 | 49.809
2020-07-02 | 14:55 | 49.811
2020-07-02 | 14:56 | 49.814
2020-07-02 | 14:56 | 49.815
2020-07-02 | 14:56 | 49.818
2020-07-02 | 14:56 | 49.819
2020-07-02 | 14:56 | 49.818
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.817
2020-07-02 | 14:56 | 49.818
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.817
2020-07-02 | 14:56 | 49.817
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.814
2020-07-02 | 14:56 | 49.814
2020-07-02 | 14:56 | 49.815
2020-07-02 | 14:56 | 49.815
2020-07-02 | 14:56 | 49.816
2020-07-02 | 14:56 | 49.815
2020-07-02 | 14:56 | 49.817
2020-07-02 | 14:56 | 49.817
2020-07-02 | 14:56 | 49.819
2020-07-02 | 14:56 | 49.82
2020-07-02 | 14:56 | 49.819
2020-07-02 | 14:56 | 49.82
2020-07-02 | 14:56 | 49.823
2020-07-02 | 14:56 | 49.828
2020-07-02 | 14:56 | 49.831
2020-07-02 | 14:56 | 49.833
2020-07-02 | 14:56 | 49.837
2020-07-02 | 14:56 | 49.84
2020-07-02 | 14:56 | 49.846
2020-07-02 | 14:56 | 49.85
2020-07-02 | 14:56 | 49.85
2020-07-02 | 14:56 | 49.853
2020-07-02 | 14:56 | 49.855
2020-07-02 | 14:56 | 49.859
2020-07-02 | 14:56 | 49.864
2020-07-02 | 14:56 | 49.868
2020-07-02 | 14:56 | 49.876
2020-07-02 | 14:56 | 49.882
2020-07-02 | 14:56 | 49.887
2020-07-02 | 14:56 | 49.891
2020-07-02 | 14:56 | 49.895
2020-07-02 | 14:56 | 49.897
2020-07-02 | 14:56 | 49.9
2020-07-02 | 14:56 | 49.906
2020-07-02 | 14:56 | 49.913
2020-07-02 | 14:56 | 49.921
2020-07-02 | 14:56 | 49.928
2020-07-02 | 14:56 | 49.935
2020-07-02 | 14:56 | 49.938
2020-07-02 | 14:56 | 49.944
2020-07-02 | 14:56 | 49.947
2020-07-02 | 14:56 | 49.95
2020-07-02 | 14:56 | 49.953
2020-07-02 | 14:56 | 49.955
2020-07-02 | 14:56 | 49.958
2020-07-02 | 14:56 | 49.959
2020-07-02 | 14:57 | 49.96
2020-07-02 | 14:57 | 49.962
2020-07-02 | 14:57 | 49.963
2020-07-02 | 14:57 | 49.964
2020-07-02 | 14:57 | 49.964
2020-07-02 | 14:57 | 49.963
2020-07-02 | 14:57 | 49.961
2020-07-02 | 14:57 | 49.96
2020-07-02 | 14:57 | 49.959
2020-07-02 | 14:57 | 49.96
2020-07-02 | 14:57 | 49.964
2020-07-02 | 14:57 | 49.967
2020-07-02 | 14:57 | 49.971
2020-07-02 | 14:57 | 49.974
2020-07-02 | 14:57 | 49.977
2020-07-02 | 14:57 | 49.979
2020-07-02 | 14:57 | 49.981
2020-07-02 | 14:57 | 49.982
2020-07-02 | 14:57 | 49.981
2020-07-02 | 14:57 | 49.981
2020-07-02 | 14:57 | 49.98
2020-07-02 | 14:57 | 49.98
2020-07-02 | 14:57 | 49.977
2020-07-02 | 14:57 | 49.976
2020-07-02 | 14:57 | 49.976
2020-07-02 | 14:57 | 49.977
2020-07-02 | 14:57 | 49.98
2020-07-02 | 14:57 | 49.98
2020-07-02 | 14:57 | 49.981
2020-07-02 | 14:57 | 49.981
2020-07-02 | 14:57 | 49.98
2020-07-02 | 14:57 | 49.978
2020-07-02 | 14:57 | 49.978
2020-07-02 | 14:57 | 49.976
2020-07-02 | 14:57 | 49.975
2020-07-02 | 14:57 | 49.971
2020-07-02 | 14:57 | 49.971
2020-07-02 | 14:57 | 49.97
2020-07-02 | 14:57 | 49.968
2020-07-02 | 14:57 | 49.967
2020-07-02 | 14:57 | 49.968
2020-07-02 | 14:57 | 49.968
2020-07-02 | 14:57 | 49.968
2020-07-02 | 14:57 | 49.97
2020-07-02 | 14:57 | 49.972
2020-07-02 | 14:57 | 49.973
2020-07-02 | 14:57 | 49.974
2020-07-02 | 14:57 | 49.976
2020-07-02 | 14:57 | 49.977
2020-07-02 | 14:57 | 49.979
2020-07-02 | 14:57 | 49.982
2020-07-02 | 14:57 | 49.984
2020-07-02 | 14:57 | 49.987
2020-07-02 | 14:57 | 49.987
2020-07-02 | 14:57 | 49.987
2020-07-02 | 14:57 | 49.986
2020-07-02 | 14:57 | 49.987
2020-07-02 | 14:57 | 49.989
2020-07-02 | 14:57 | 49.989
2020-07-02 | 14:58 | 49.992
2020-07-02 | 14:58 | 49.994
2020-07-02 | 14:58 | 49.998
2020-07-02 | 14:58 | 50.003
2020-07-02 | 14:58 | 50.01
2020-07-02 | 14:58 | 50.017
2020-07-02 | 14:58 | 50.023
2020-07-02 | 14:58 | 50.031
2020-07-02 | 14:58 | 50.036
2020-07-02 | 14:58 | 50.043
2020-07-02 | 14:58 | 50.048
2020-07-02 | 14:58 | 50.053
2020-07-02 | 14:58 | 50.057
2020-07-02 | 14:58 | 50.059
2020-07-02 | 14:58 | 50.059
2020-07-02 | 14:58 | 50.061
2020-07-02 | 14:58 | 50.06
2020-07-02 | 14:58 | 50.058
2020-07-02 | 14:58 | 50.058
2020-07-02 | 14:58 | 50.056
2020-07-02 | 14:58 | 50.055
2020-07-02 | 14:58 | 50.054
2020-07-02 | 14:58 | 50.054
2020-07-02 | 14:58 | 50.054
2020-07-02 | 14:58 | 50.054
2020-07-02 | 14:58 | 50.054
2020-07-02 | 14:58 | 50.054
2020-07-02 | 14:58 | 50.053
2020-07-02 | 14:58 | 50.053
2020-07-02 | 14:58 | 50.054

## Event 20200703-1
In UTC
Date | Time | Freq
2020-07-03 | 14:58 | 49.91
2020-07-03 | 14:58 | 49.91
2020-07-03 | 14:58 | 49.909
2020-07-03 | 14:58 | 49.912
2020-07-03 | 14:58 | 49.913
2020-07-03 | 14:58 | 49.913
2020-07-03 | 14:58 | 49.911
2020-07-03 | 14:58 | 49.909
2020-07-03 | 14:58 | 49.908
2020-07-03 | 14:58 | 49.908
2020-07-03 | 14:58 | 49.909
2020-07-03 | 14:58 | 49.909
2020-07-03 | 14:58 | 49.912
2020-07-03 | 14:58 | 49.915
2020-07-03 | 14:58 | 49.919
2020-07-03 | 14:58 | 49.923
2020-07-03 | 14:58 | 49.923
2020-07-03 | 14:58 | 49.926
2020-07-03 | 14:58 | 49.928
2020-07-03 | 14:58 | 49.931
2020-07-03 | 14:58 | 49.934
2020-07-03 | 14:58 | 49.934
2020-07-03 | 14:58 | 49.928
2020-07-03 | 14:58 | 49.926
2020-07-03 | 14:58 | 49.923
2020-07-03 | 14:58 | 49.921
2020-07-03 | 14:58 | 49.92
2020-07-03 | 14:58 | 49.921
2020-07-03 | 14:58 | 49.923
2020-07-03 | 14:58 | 49.924
2020-07-03 | 14:58 | 49.925
2020-07-03 | 14:59 | 49.925
2020-07-03 | 14:59 | 49.925
2020-07-03 | 14:59 | 49.927
2020-07-03 | 14:59 | 49.928
2020-07-03 | 14:59 | 49.926
2020-07-03 | 14:59 | 49.923
2020-07-03 | 14:59 | 49.918
2020-07-03 | 14:59 | 49.915
2020-07-03 | 14:59 | 49.913
2020-07-03 | 14:59 | 49.909
2020-07-03 | 14:59 | 49.906
2020-07-03 | 14:59 | 49.905
2020-07-03 | 14:59 | 49.907
2020-07-03 | 14:59 | 49.908
2020-07-03 | 14:59 | 49.909
2020-07-03 | 14:59 | 49.91
2020-07-03 | 14:59 | 49.913
2020-07-03 | 14:59 | 49.916
2020-07-03 | 14:59 | 49.918
2020-07-03 | 14:59 | 49.918
2020-07-03 | 14:59 | 49.919
2020-07-03 | 14:59 | 49.922
2020-07-03 | 14:59 | 49.924
2020-07-03 | 14:59 | 49.928
2020-07-03 | 14:59 | 49.931
2020-07-03 | 14:59 | 49.931
2020-07-03 | 14:59 | 49.931
2020-07-03 | 14:59 | 49.93
2020-07-03 | 14:59 | 49.927
2020-07-03 | 14:59 | 49.923
2020-07-03 | 14:59 | 49.911
2020-07-03 | 14:59 | 49.9
2020-07-03 | 14:59 | 49.892
2020-07-03 | 14:59 | 49.886
2020-07-03 | 14:59 | 49.883
2020-07-03 | 14:59 | 49.88
2020-07-03 | 14:59 | 49.88
2020-07-03 | 14:59 | 49.879
2020-07-03 | 14:59 | 49.88
2020-07-03 | 14:59 | 49.881
2020-07-03 | 14:59 | 49.881
2020-07-03 | 14:59 | 49.883
2020-07-03 | 14:59 | 49.891
2020-07-03 | 14:59 | 49.901
2020-07-03 | 14:59 | 49.909
2020-07-03 | 14:59 | 49.916
2020-07-03 | 14:59 | 49.921
2020-07-03 | 14:59 | 49.922
2020-07-03 | 14:59 | 49.921
2020-07-03 | 14:59 | 49.921
2020-07-03 | 14:59 | 49.919
2020-07-03 | 14:59 | 49.918
2020-07-03 | 14:59 | 49.917
2020-07-03 | 14:59 | 49.916
2020-07-03 | 14:59 | 49.918
2020-07-03 | 14:59 | 49.918
2020-07-03 | 14:59 | 49.92
2020-07-03 | 14:59 | 49.922
2020-07-03 | 14:59 | 49.924
2020-07-03 | 15:00 | 49.929
2020-07-03 | 15:00 | 49.933
2020-07-03 | 15:00 | 49.937
2020-07-03 | 15:00 | 49.937
2020-07-03 | 15:00 | 49.939
2020-07-03 | 15:00 | 49.937
2020-07-03 | 15:00 | 49.934
2020-07-03 | 15:00 | 49.93
2020-07-03 | 15:00 | 49.929
2020-07-03 | 15:00 | 49.928
2020-07-03 | 15:00 | 49.931
2020-07-03 | 15:00 | 49.937
2020-07-03 | 15:00 | 49.943
2020-07-03 | 15:00 | 49.946
2020-07-03 | 15:00 | 49.949
2020-07-03 | 15:00 | 49.949
2020-07-03 | 15:00 | 49.95
2020-07-03 | 15:00 | 49.951
2020-07-03 | 15:00 | 49.952
2020-07-03 | 15:00 | 49.949
2020-07-03 | 15:00 | 49.946
2020-07-03 | 15:00 | 49.94
2020-07-03 | 15:00 | 49.936
2020-07-03 | 15:00 | 49.933
2020-07-03 | 15:00 | 49.932
2020-07-03 | 15:00 | 49.932
2020-07-03 | 15:00 | 49.934
2020-07-03 | 15:00 | 49.936
2020-07-03 | 15:00 | 49.938
2020-07-03 | 15:00 | 49.94
2020-07-03 | 15:00 | 49.942
2020-07-03 | 15:00 | 49.944
2020-07-03 | 15:00 | 49.943
2020-07-03 | 15:00 | 49.943
2020-07-03 | 15:00 | 49.948
2020-07-03 | 15:00 | 49.953
2020-07-03 | 15:00 | 49.959
2020-07-03 | 15:00 | 49.967
2020-07-03 | 15:00 | 49.972
2020-07-03 | 15:00 | 49.979
2020-07-03 | 15:00 | 49.982
2020-07-03 | 15:00 | 49.986
2020-07-03 | 15:00 | 49.986
2020-07-03 | 15:00 | 49.989
2020-07-03 | 15:00 | 49.99
2020-07-03 | 15:00 | 49.993
2020-07-03 | 15:00 | 49.993
2020-07-03 | 15:00 | 49.996
2020-07-03 | 15:00 | 50
2020-07-03 | 15:00 | 50.005
2020-07-03 | 15:00 | 50.011
2020-07-03 | 15:00 | 50.016
2020-07-03 | 15:00 | 50.021
2020-07-03 | 15:00 | 50.022
2020-07-03 | 15:00 | 50.026
2020-07-03 | 15:00 | 50.03
2020-07-03 | 15:00 | 50.035
2020-07-03 | 15:00 | 50.037
2020-07-03 | 15:00 | 50.039
2020-07-03 | 15:00 | 50.04
2020-07-03 | 15:00 | 50.04
2020-07-03 | 15:01 | 50.039
2020-07-03 | 15:01 | 50.039
2020-07-03 | 15:01 | 50.038
2020-07-03 | 15:01 | 50.039
2020-07-03 | 15:01 | 50.041
2020-07-03 | 15:01 | 50.042
2020-07-03 | 15:01 | 50.044
2020-07-03 | 15:01 | 50.049
2020-07-03 | 15:01 | 50.053
2020-07-03 | 15:01 | 50.055
2020-07-03 | 15:01 | 50.056
2020-07-03 | 15:01 | 50.06
2020-07-03 | 15:01 | 50.065
2020-07-03 | 15:01 | 50.068
2020-07-03 | 15:01 | 50.072
2020-07-03 | 15:01 | 50.074
2020-07-03 | 15:01 | 50.072
2020-07-03 | 15:01 | 50.071
2020-07-03 | 15:01 | 50.069
2020-07-03 | 15:01 | 50.065
2020-07-03 | 15:01 | 50.065
2020-07-03 | 15:01 | 50.063
2020-07-03 | 15:01 | 50.063
2020-07-03 | 15:01 | 50.065
2020-07-03 | 15:01 | 50.067
2020-07-03 | 15:01 | 50.067
2020-07-03 | 15:01 | 50.066
2020-07-03 | 15:01 | 50.068
2020-07-03 | 15:01 | 50.072

## Event 20200703-2
In UTC
Date | Time | Freq
2020-07-03 | 17:29 | 50.078 | 49.878
2020-07-03 | 17:29 | 50.078
2020-07-03 | 17:29 | 50.067
2020-07-03 | 17:29 | 50.051
2020-07-03 | 17:29 | 50.041
2020-07-03 | 17:29 | 50.032
2020-07-03 | 17:29 | 50.029
2020-07-03 | 17:29 | 50.027
2020-07-03 | 17:29 | 50.025
2020-07-03 | 17:29 | 50.023
2020-07-03 | 17:29 | 50.022
2020-07-03 | 17:29 | 50.022
2020-07-03 | 17:29 | 50.022
2020-07-03 | 17:29 | 50.021
2020-07-03 | 17:29 | 50.023
2020-07-03 | 17:29 | 50.024
2020-07-03 | 17:29 | 50.023
2020-07-03 | 17:29 | 50.016
2020-07-03 | 17:29 | 50.009
2020-07-03 | 17:29 | 50.005
2020-07-03 | 17:29 | 49.999
2020-07-03 | 17:29 | 49.996
2020-07-03 | 17:29 | 49.995
2020-07-03 | 17:29 | 49.995
2020-07-03 | 17:29 | 49.995
2020-07-03 | 17:29 | 49.998
2020-07-03 | 17:29 | 49.998
2020-07-03 | 17:29 | 49.998
2020-07-03 | 17:29 | 49.998
2020-07-03 | 17:29 | 49.999
2020-07-03 | 17:30 | 49.998
2020-07-03 | 17:30 | 49.996
2020-07-03 | 17:30 | 50
2020-07-03 | 17:30 | 50.004
2020-07-03 | 17:30 | 50.007
2020-07-03 | 17:30 | 50.01
2020-07-03 | 17:30 | 50.01
2020-07-03 | 17:30 | 50.012
2020-07-03 | 17:30 | 50.014
2020-07-03 | 17:30 | 50.015
2020-07-03 | 17:30 | 50.013
2020-07-03 | 17:30 | 50.012
2020-07-03 | 17:30 | 50.012
2020-07-03 | 17:30 | 50.011
2020-07-03 | 17:30 | 50.009
2020-07-03 | 17:30 | 50.007
2020-07-03 | 17:30 | 50.004
2020-07-03 | 17:30 | 50.003
2020-07-03 | 17:30 | 50
2020-07-03 | 17:30 | 49.998
2020-07-03 | 17:30 | 49.995
2020-07-03 | 17:30 | 49.994
2020-07-03 | 17:30 | 49.992
2020-07-03 | 17:30 | 49.99
2020-07-03 | 17:30 | 49.986
2020-07-03 | 17:30 | 49.984
2020-07-03 | 17:30 | 49.979
2020-07-03 | 17:30 | 49.974
2020-07-03 | 17:30 | 49.969
2020-07-03 | 17:30 | 49.963
2020-07-03 | 17:30 | 49.955
2020-07-03 | 17:30 | 49.949
2020-07-03 | 17:30 | 49.941
2020-07-03 | 17:30 | 49.937
2020-07-03 | 17:30 | 49.933
2020-07-03 | 17:30 | 49.929
2020-07-03 | 17:30 | 49.928
2020-07-03 | 17:30 | 49.929
2020-07-03 | 17:30 | 49.932
2020-07-03 | 17:30 | 49.936
2020-07-03 | 17:30 | 49.937
2020-07-03 | 17:30 | 49.938
2020-07-03 | 17:30 | 49.937
2020-07-03 | 17:30 | 49.933
2020-07-03 | 17:30 | 49.93
2020-07-03 | 17:30 | 49.927
2020-07-03 | 17:30 | 49.925
2020-07-03 | 17:30 | 49.924
2020-07-03 | 17:30 | 49.925
2020-07-03 | 17:30 | 49.924
2020-07-03 | 17:30 | 49.925
2020-07-03 | 17:30 | 49.923
2020-07-03 | 17:30 | 49.921
2020-07-03 | 17:30 | 49.92
2020-07-03 | 17:30 | 49.918
2020-07-03 | 17:30 | 49.915
2020-07-03 | 17:30 | 49.913
2020-07-03 | 17:30 | 49.911
2020-07-03 | 17:30 | 49.909
2020-07-03 | 17:30 | 49.909
2020-07-03 | 17:30 | 49.91
2020-07-03 | 17:31 | 49.909
2020-07-03 | 17:31 | 49.906
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.906
2020-07-03 | 17:31 | 49.906
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.906
2020-07-03 | 17:31 | 49.908
2020-07-03 | 17:31 | 49.911
2020-07-03 | 17:31 | 49.914
2020-07-03 | 17:31 | 49.917
2020-07-03 | 17:31 | 49.918
2020-07-03 | 17:31 | 49.921
2020-07-03 | 17:31 | 49.923
2020-07-03 | 17:31 | 49.924
2020-07-03 | 17:31 | 49.923
2020-07-03 | 17:31 | 49.92
2020-07-03 | 17:31 | 49.915
2020-07-03 | 17:31 | 49.91
2020-07-03 | 17:31 | 49.904
2020-07-03 | 17:31 | 49.9
2020-07-03 | 17:31 | 49.897
2020-07-03 | 17:31 | 49.897
2020-07-03 | 17:31 | 49.897
2020-07-03 | 17:31 | 49.898
2020-07-03 | 17:31 | 49.897
2020-07-03 | 17:31 | 49.898
2020-07-03 | 17:31 | 49.899
2020-07-03 | 17:31 | 49.898
2020-07-03 | 17:31 | 49.902
2020-07-03 | 17:31 | 49.904
2020-07-03 | 17:31 | 49.904
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.906
2020-07-03 | 17:31 | 49.908
2020-07-03 | 17:31 | 49.909
2020-07-03 | 17:31 | 49.908
2020-07-03 | 17:31 | 49.908
2020-07-03 | 17:31 | 49.907
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.9
2020-07-03 | 17:31 | 49.898
2020-07-03 | 17:31 | 49.894
2020-07-03 | 17:31 | 49.891
2020-07-03 | 17:31 | 49.89
2020-07-03 | 17:31 | 49.891
2020-07-03 | 17:31 | 49.894
2020-07-03 | 17:31 | 49.897
2020-07-03 | 17:31 | 49.901
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:31 | 49.909
2020-07-03 | 17:31 | 49.914
2020-07-03 | 17:31 | 49.917
2020-07-03 | 17:31 | 49.917
2020-07-03 | 17:31 | 49.915
2020-07-03 | 17:31 | 49.913
2020-07-03 | 17:31 | 49.909
2020-07-03 | 17:31 | 49.905
2020-07-03 | 17:32 | 49.908
2020-07-03 | 17:32 | 49.911
2020-07-03 | 17:32 | 49.914
2020-07-03 | 17:32 | 49.914
2020-07-03 | 17:32 | 49.913
2020-07-03 | 17:32 | 49.912
2020-07-03 | 17:32 | 49.91
2020-07-03 | 17:32 | 49.907
2020-07-03 | 17:32 | 49.902
2020-07-03 | 17:32 | 49.899
2020-07-03 | 17:32 | 49.898
2020-07-03 | 17:32 | 49.899
2020-07-03 | 17:32 | 49.904
2020-07-03 | 17:32 | 49.91
2020-07-03 | 17:32 | 49.91
2020-07-03 | 17:32 | 49.91
2020-07-03 | 17:32 | 49.911
2020-07-03 | 17:32 | 49.911
2020-07-03 | 17:32 | 49.914
2020-07-03 | 17:32 | 49.916
2020-07-03 | 17:32 | 49.916
2020-07-03 | 17:32 | 49.915
2020-07-03 | 17:32 | 49.911
2020-07-03 | 17:32 | 49.91
2020-07-03 | 17:32 | 49.907
2020-07-03 | 17:32 | 49.905
2020-07-03 | 17:32 | 49.904
2020-07-03 | 17:32 | 49.904
2020-07-03 | 17:32 | 49.907
2020-07-03 | 17:32 | 49.909
2020-07-03 | 17:32 | 49.91
2020-07-03 | 17:32 | 49.909
2020-07-03 | 17:32 | 49.906
2020-07-03 | 17:32 | 49.901
2020-07-03 | 17:32 | 49.897
2020-07-03 | 17:32 | 49.892
2020-07-03 | 17:32 | 49.887
2020-07-03 | 17:32 | 49.887
2020-07-03 | 17:32 | 49.883
2020-07-03 | 17:32 | 49.882
2020-07-03 | 17:32 | 49.883
2020-07-03 | 17:32 | 49.883
2020-07-03 | 17:32 | 49.883
2020-07-03 | 17:32 | 49.883
2020-07-03 | 17:32 | 49.881
2020-07-03 | 17:32 | 49.879
2020-07-03 | 17:32 | 49.878
2020-07-03 | 17:32 | 49.878
2020-07-03 | 17:32 | 49.879
2020-07-03 | 17:32 | 49.88
2020-07-03 | 17:32 | 49.881
2020-07-03 | 17:32 | 49.883
2020-07-03 | 17:32 | 49.886
2020-07-03 | 17:32 | 49.891
2020-07-03 | 17:32 | 49.895
2020-07-03 | 17:32 | 49.896
2020-07-03 | 17:32 | 49.898
2020-07-03 | 17:32 | 49.897
2020-07-03 | 17:32 | 49.896
2020-07-03 | 17:32 | 49.896
2020-07-03 | 17:33 | 49.897
2020-07-03 | 17:33 | 49.901
2020-07-03 | 17:33 | 49.904
2020-07-03 | 17:33 | 49.905
2020-07-03 | 17:33 | 49.907
2020-07-03 | 17:33 | 49.906
2020-07-03 | 17:33 | 49.905
2020-07-03 | 17:33 | 49.905
2020-07-03 | 17:33 | 49.902
2020-07-03 | 17:33 | 49.899
2020-07-03 | 17:33 | 49.896
2020-07-03 | 17:33 | 49.896
2020-07-03 | 17:33 | 49.898
2020-07-03 | 17:33 | 49.9
2020-07-03 | 17:33 | 49.901
2020-07-03 | 17:33 | 49.902
2020-07-03 | 17:33 | 49.904
2020-07-03 | 17:33 | 49.907
2020-07-03 | 17:33 | 49.91
2020-07-03 | 17:33 | 49.914
2020-07-03 | 17:33 | 49.918
2020-07-03 | 17:33 | 49.918
2020-07-03 | 17:33 | 49.917
2020-07-03 | 17:33 | 49.914
2020-07-03 | 17:33 | 49.913
2020-07-03 | 17:33 | 49.912
2020-07-03 | 17:33 | 49.911
2020-07-03 | 17:33 | 49.909
2020-07-03 | 17:33 | 49.907
2020-07-03 | 17:33 | 49.904
2020-07-03 | 17:33 | 49.9
2020-07-03 | 17:33 | 49.898
2020-07-03 | 17:33 | 49.896
2020-07-03 | 17:33 | 49.894
2020-07-03 | 17:33 | 49.894
2020-07-03 | 17:33 | 49.898
2020-07-03 | 17:33 | 49.903
2020-07-03 | 17:33 | 49.91
2020-07-03 | 17:33 | 49.915
2020-07-03 | 17:33 | 49.92
2020-07-03 | 17:33 | 49.923
2020-07-03 | 17:33 | 49.929
2020-07-03 | 17:33 | 49.935
2020-07-03 | 17:33 | 49.94
2020-07-03 | 17:33 | 49.945
2020-07-03 | 17:33 | 49.946
2020-07-03 | 17:33 | 49.946
2020-07-03 | 17:33 | 49.945
2020-07-03 | 17:33 | 49.943
2020-07-03 | 17:33 | 49.939
2020-07-03 | 17:33 | 49.938
2020-07-03 | 17:33 | 49.934
2020-07-03 | 17:33 | 49.933
2020-07-03 | 17:33 | 49.936
2020-07-03 | 17:33 | 49.939
2020-07-03 | 17:33 | 49.941
2020-07-03 | 17:33 | 49.943
2020-07-03 | 17:33 | 49.949
2020-07-03 | 17:33 | 49.953
2020-07-03 | 17:34 | 49.956
2020-07-03 | 17:34 | 49.96
2020-07-03 | 17:34 | 49.964
2020-07-03 | 17:34 | 49.966
2020-07-03 | 17:34 | 49.969
2020-07-03 | 17:34 | 49.97
2020-07-03 | 17:34 | 49.971
2020-07-03 | 17:34 | 49.973
2020-07-03 | 17:34 | 49.972
2020-07-03 | 17:34 | 49.973
2020-07-03 | 17:34 | 49.969
2020-07-03 | 17:34 | 49.968
2020-07-03 | 17:34 | 49.967
2020-07-03 | 17:34 | 49.968
2020-07-03 | 17:34 | 49.969
2020-07-03 | 17:34 | 49.972
2020-07-03 | 17:34 | 49.975
2020-07-03 | 17:34 | 49.977
2020-07-03 | 17:34 | 49.979
2020-07-03 | 17:34 | 49.982
2020-07-03 | 17:34 | 49.987
2020-07-03 | 17:34 | 49.992
2020-07-03 | 17:34 | 49.995
2020-07-03 | 17:34 | 49.998
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:34 | 49.998
2020-07-03 | 17:34 | 49.996
2020-07-03 | 17:34 | 49.998
2020-07-03 | 17:34 | 49.995
2020-07-03 | 17:34 | 49.991
2020-07-03 | 17:34 | 49.986
2020-07-03 | 17:34 | 49.983
2020-07-03 | 17:34 | 49.982
2020-07-03 | 17:34 | 49.984
2020-07-03 | 17:34 | 49.986
2020-07-03 | 17:34 | 49.987
2020-07-03 | 17:34 | 49.988
2020-07-03 | 17:34 | 49.988
2020-07-03 | 17:34 | 49.987
2020-07-03 | 17:34 | 49.986
2020-07-03 | 17:34 | 49.986
2020-07-03 | 17:34 | 49.987
2020-07-03 | 17:34 | 49.988
2020-07-03 | 17:34 | 49.991
2020-07-03 | 17:34 | 49.993
2020-07-03 | 17:34 | 49.996
2020-07-03 | 17:34 | 49.995
2020-07-03 | 17:34 | 49.995
2020-07-03 | 17:34 | 49.997
2020-07-03 | 17:34 | 49.996
2020-07-03 | 17:34 | 49.995
2020-07-03 | 17:34 | 49.997
2020-07-03 | 17:34 | 49.998
2020-07-03 | 17:34 | 49.998
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:34 | 49.998
2020-07-03 | 17:34 | 49.999
2020-07-03 | 17:35 | 50.001
2020-07-03 | 17:35 | 50.005
2020-07-03 | 17:35 | 50.009
2020-07-03 | 17:35 | 50.012
2020-07-03 | 17:35 | 50.017
2020-07-03 | 17:35 | 50.023
2020-07-03 | 17:35 | 50.028
2020-07-03 | 17:35 | 50.031
2020-07-03 | 17:35 | 50.03
2020-07-03 | 17:35 | 50.029
2020-07-03 | 17:35 | 50.03
2020-07-03 | 17:35 | 50.033
2020-07-03 | 17:35 | 50.037
2020-07-03 | 17:35 | 50.037
2020-07-03 | 17:35 | 50.037
2020-07-03 | 17:35 | 50.039
2020-07-03 | 17:35 | 50.039
2020-07-03 | 17:35 | 50.039
2020-07-03 | 17:35 | 50.037
2020-07-03 | 17:35 | 50.033
2020-07-03 | 17:35 | 50.028
2020-07-03 | 17:35 | 50.024
2020-07-03 | 17:35 | 50.022
2020-07-03 | 17:35 | 50.02
2020-07-03 | 17:35 | 50.016
2020-07-03 | 17:35 | 50.014
2020-07-03 | 17:35 | 50.013
2020-07-03 | 17:35 | 50.012
2020-07-03 | 17:35 | 50.01

## Event 20200706-1
In UTC
Date | Time | Freq
2020-07-06 | 12:32 | 49.935
2020-07-06 | 12:32 | 49.934
2020-07-06 | 12:32 | 49.935
2020-07-06 | 12:32 | 49.937
2020-07-06 | 12:32 | 49.938
2020-07-06 | 12:32 | 49.939
2020-07-06 | 12:32 | 49.938
2020-07-06 | 12:32 | 49.938
2020-07-06 | 12:32 | 49.937
2020-07-06 | 12:32 | 49.937
2020-07-06 | 12:32 | 49.939
2020-07-06 | 12:32 | 49.939
2020-07-06 | 12:32 | 49.94
2020-07-06 | 12:32 | 49.939
2020-07-06 | 12:32 | 49.939
2020-07-06 | 12:32 | 49.94
2020-07-06 | 12:32 | 49.94
2020-07-06 | 12:32 | 49.94
2020-07-06 | 12:32 | 49.94
2020-07-06 | 12:32 | 49.94
2020-07-06 | 12:32 | 49.942
2020-07-06 | 12:32 | 49.944
2020-07-06 | 12:32 | 49.945
2020-07-06 | 12:32 | 49.946
2020-07-06 | 12:32 | 49.948
2020-07-06 | 12:32 | 49.949
2020-07-06 | 12:32 | 49.95
2020-07-06 | 12:32 | 49.953
2020-07-06 | 12:32 | 49.951
2020-07-06 | 12:32 | 49.949
2020-07-06 | 12:32 | 49.943
2020-07-06 | 12:33 | 49.937
2020-07-06 | 12:33 | 49.931
2020-07-06 | 12:33 | 49.924
2020-07-06 | 12:33 | 49.921
2020-07-06 | 12:33 | 49.917
2020-07-06 | 12:33 | 49.919
2020-07-06 | 12:33 | 49.922
2020-07-06 | 12:33 | 49.927
2020-07-06 | 12:33 | 49.93
2020-07-06 | 12:33 | 49.932
2020-07-06 | 12:33 | 49.938
2020-07-06 | 12:33 | 49.943
2020-07-06 | 12:33 | 49.946
2020-07-06 | 12:33 | 49.947
2020-07-06 | 12:33 | 49.946
2020-07-06 | 12:33 | 49.943
2020-07-06 | 12:33 | 49.938
2020-07-06 | 12:33 | 49.932
2020-07-06 | 12:33 | 49.925
2020-07-06 | 12:33 | 49.92
2020-07-06 | 12:33 | 49.915
2020-07-06 | 12:33 | 49.913
2020-07-06 | 12:33 | 49.911
2020-07-06 | 12:33 | 49.914
2020-07-06 | 12:33 | 49.915
2020-07-06 | 12:33 | 49.915
2020-07-06 | 12:33 | 49.916
2020-07-06 | 12:33 | 49.917
2020-07-06 | 12:33 | 49.916
2020-07-06 | 12:33 | 49.911
2020-07-06 | 12:33 | 49.905
2020-07-06 | 12:33 | 49.9
2020-07-06 | 12:33 | 49.896
2020-07-06 | 12:33 | 49.89
2020-07-06 | 12:33 | 49.881
2020-07-06 | 12:33 | 49.877
2020-07-06 | 12:33 | 49.875
2020-07-06 | 12:33 | 49.873
2020-07-06 | 12:33 | 49.874
2020-07-06 | 12:33 | 49.875
2020-07-06 | 12:33 | 49.878
2020-07-06 | 12:33 | 49.884
2020-07-06 | 12:33 | 49.887
2020-07-06 | 12:33 | 49.891
2020-07-06 | 12:33 | 49.893
2020-07-06 | 12:33 | 49.899
2020-07-06 | 12:33 | 49.899
2020-07-06 | 12:33 | 49.902
2020-07-06 | 12:33 | 49.9
2020-07-06 | 12:33 | 49.9
2020-07-06 | 12:33 | 49.903
2020-07-06 | 12:33 | 49.902
2020-07-06 | 12:33 | 49.902
2020-07-06 | 12:33 | 49.903
2020-07-06 | 12:33 | 49.877
2020-07-06 | 12:33 | 49.815
2020-07-06 | 12:33 | 49.77
2020-07-06 | 12:33 | 49.743
2020-07-06 | 12:33 | 49.726
2020-07-06 | 12:34 | 49.714
2020-07-06 | 12:34 | 49.711
2020-07-06 | 12:34 | 49.71
2020-07-06 | 12:34 | 49.711
2020-07-06 | 12:34 | 49.711
2020-07-06 | 12:34 | 49.713
2020-07-06 | 12:34 | 49.712
2020-07-06 | 12:34 | 49.71
2020-07-06 | 12:34 | 49.708
2020-07-06 | 12:34 | 49.705
2020-07-06 | 12:34 | 49.706
2020-07-06 | 12:34 | 49.705
2020-07-06 | 12:34 | 49.702
2020-07-06 | 12:34 | 49.698
2020-07-06 | 12:34 | 49.696
2020-07-06 | 12:34 | 49.692
2020-07-06 | 12:34 | 49.688
2020-07-06 | 12:34 | 49.686
2020-07-06 | 12:34 | 49.685
2020-07-06 | 12:34 | 49.686
2020-07-06 | 12:34 | 49.689
2020-07-06 | 12:34 | 49.694
2020-07-06 | 12:34 | 49.698
2020-07-06 | 12:34 | 49.699
2020-07-06 | 12:34 | 49.7
2020-07-06 | 12:34 | 49.7
2020-07-06 | 12:34 | 49.699
2020-07-06 | 12:34 | 49.695
2020-07-06 | 12:34 | 49.694
2020-07-06 | 12:34 | 49.69
2020-07-06 | 12:34 | 49.689
2020-07-06 | 12:34 | 49.692
2020-07-06 | 12:34 | 49.693
2020-07-06 | 12:34 | 49.695
2020-07-06 | 12:34 | 49.697
2020-07-06 | 12:34 | 49.702
2020-07-06 | 12:34 | 49.707
2020-07-06 | 12:34 | 49.713
2020-07-06 | 12:34 | 49.721
2020-07-06 | 12:34 | 49.728
2020-07-06 | 12:34 | 49.739
2020-07-06 | 12:34 | 49.749
2020-07-06 | 12:34 | 49.755
2020-07-06 | 12:34 | 49.761
2020-07-06 | 12:34 | 49.767
2020-07-06 | 12:34 | 49.776
2020-07-06 | 12:34 | 49.784
2020-07-06 | 12:34 | 49.79
2020-07-06 | 12:34 | 49.797
2020-07-06 | 12:34 | 49.806
2020-07-06 | 12:34 | 49.813
2020-07-06 | 12:34 | 49.818
2020-07-06 | 12:34 | 49.823
2020-07-06 | 12:34 | 49.826
2020-07-06 | 12:34 | 49.826
2020-07-06 | 12:34 | 49.824
2020-07-06 | 12:34 | 49.823
2020-07-06 | 12:34 | 49.82
2020-07-06 | 12:34 | 49.819
2020-07-06 | 12:34 | 49.819
2020-07-06 | 12:34 | 49.821
2020-07-06 | 12:35 | 49.827
2020-07-06 | 12:35 | 49.835
2020-07-06 | 12:35 | 49.842
2020-07-06 | 12:35 | 49.848
2020-07-06 | 12:35 | 49.852
2020-07-06 | 12:35 | 49.854
2020-07-06 | 12:35 | 49.856
2020-07-06 | 12:35 | 49.861
2020-07-06 | 12:35 | 49.865
2020-07-06 | 12:35 | 49.869
2020-07-06 | 12:35 | 49.871
2020-07-06 | 12:35 | 49.87
2020-07-06 | 12:35 | 49.872
2020-07-06 | 12:35 | 49.875
2020-07-06 | 12:35 | 49.879
2020-07-06 | 12:35 | 49.881
2020-07-06 | 12:35 | 49.887
2020-07-06 | 12:35 | 49.893
2020-07-06 | 12:35 | 49.901
2020-07-06 | 12:35 | 49.908
2020-07-06 | 12:35 | 49.91
2020-07-06 | 12:35 | 49.912
2020-07-06 | 12:35 | 49.913
2020-07-06 | 12:35 | 49.914
2020-07-06 | 12:35 | 49.919
2020-07-06 | 12:35 | 49.921
2020-07-06 | 12:35 | 49.924
2020-07-06 | 12:35 | 49.926
2020-07-06 | 12:35 | 49.928
2020-07-06 | 12:35 | 49.931
2020-07-06 | 12:35 | 49.931
2020-07-06 | 12:35 | 49.935
2020-07-06 | 12:35 | 49.937
2020-07-06 | 12:35 | 49.938
2020-07-06 | 12:35 | 49.939
2020-07-06 | 12:35 | 49.938
2020-07-06 | 12:35 | 49.937
2020-07-06 | 12:35 | 49.938
2020-07-06 | 12:35 | 49.936
2020-07-06 | 12:35 | 49.935
2020-07-06 | 12:35 | 49.933
2020-07-06 | 12:35 | 49.927
2020-07-06 | 12:35 | 49.923
2020-07-06 | 12:35 | 49.923
2020-07-06 | 12:35 | 49.924
2020-07-06 | 12:35 | 49.925
2020-07-06 | 12:35 | 49.926
2020-07-06 | 12:35 | 49.926
2020-07-06 | 12:35 | 49.926
2020-07-06 | 12:35 | 49.926
2020-07-06 | 12:35 | 49.929
2020-07-06 | 12:35 | 49.932
2020-07-06 | 12:35 | 49.934
2020-07-06 | 12:35 | 49.932
2020-07-06 | 12:35 | 49.933
2020-07-06 | 12:35 | 49.932
2020-07-06 | 12:35 | 49.934
2020-07-06 | 12:35 | 49.935
2020-07-06 | 12:35 | 49.937
2020-07-06 | 12:36 | 49.942
2020-07-06 | 12:36 | 49.946
2020-07-06 | 12:36 | 49.949
2020-07-06 | 12:36 | 49.95
2020-07-06 | 12:36 | 49.954
2020-07-06 | 12:36 | 49.957
2020-07-06 | 12:36 | 49.961
2020-07-06 | 12:36 | 49.964
2020-07-06 | 12:36 | 49.965
2020-07-06 | 12:36 | 49.962
2020-07-06 | 12:36 | 49.958
2020-07-06 | 12:36 | 49.952
2020-07-06 | 12:36 | 49.953
2020-07-06 | 12:36 | 49.954
2020-07-06 | 12:36 | 49.957
2020-07-06 | 12:36 | 49.961
2020-07-06 | 12:36 | 49.964
2020-07-06 | 12:36 | 49.967
2020-07-06 | 12:36 | 49.969
2020-07-06 | 12:36 | 49.971
2020-07-06 | 12:36 | 49.974
2020-07-06 | 12:36 | 49.977
2020-07-06 | 12:36 | 49.978
2020-07-06 | 12:36 | 49.977
2020-07-06 | 12:36 | 49.974
2020-07-06 | 12:36 | 49.973
2020-07-06 | 12:36 | 49.974
2020-07-06 | 12:36 | 49.975
2020-07-06 | 12:36 | 49.975
2020-07-06 | 12:36 | 49.976
2020-07-06 | 12:36 | 49.976
2020-07-06 | 12:36 | 49.978
2020-07-06 | 12:36 | 49.978
2020-07-06 | 12:36 | 49.985
2020-07-06 | 12:36 | 49.986
2020-07-06 | 12:36 | 49.985
2020-07-06 | 12:36 | 49.987
2020-07-06 | 12:36 | 49.984
2020-07-06 | 12:36 | 49.981
2020-07-06 | 12:36 | 49.98
2020-07-06 | 12:36 | 49.98
2020-07-06 | 12:36 | 49.983
2020-07-06 | 12:36 | 49.984
2020-07-06 | 12:36 | 49.984
2020-07-06 | 12:36 | 49.982
2020-07-06 | 12:36 | 49.981
2020-07-06 | 12:36 | 49.98
2020-07-06 | 12:36 | 49.981
2020-07-06 | 12:36 | 49.98
2020-07-06 | 12:36 | 49.977
2020-07-06 | 12:36 | 49.974
2020-07-06 | 12:36 | 49.968
2020-07-06 | 12:36 | 49.966
2020-07-06 | 12:36 | 49.966
2020-07-06 | 12:36 | 49.966
2020-07-06 | 12:36 | 49.968
2020-07-06 | 12:36 | 49.97
2020-07-06 | 12:36 | 49.972
2020-07-06 | 12:36 | 49.975
2020-07-06 | 12:36 | 49.977
2020-07-06 | 12:36 | 49.977
2020-07-06 | 12:37 | 49.978
2020-07-06 | 12:37 | 49.984
2020-07-06 | 12:37 | 49.984
2020-07-06 | 12:37 | 49.984
2020-07-06 | 12:37 | 49.983
2020-07-06 | 12:37 | 49.981
2020-07-06 | 12:37 | 49.98
2020-07-06 | 12:37 | 49.98
2020-07-06 | 12:37 | 49.977
2020-07-06 | 12:37 | 49.976
2020-07-06 | 12:37 | 49.974
2020-07-06 | 12:37 | 49.971
2020-07-06 | 12:37 | 49.966
2020-07-06 | 12:37 | 49.965
2020-07-06 | 12:37 | 49.965
2020-07-06 | 12:37 | 49.966
2020-07-06 | 12:37 | 49.966
2020-07-06 | 12:37 | 49.964
2020-07-06 | 12:37 | 49.964
2020-07-06 | 12:37 | 49.964
2020-07-06 | 12:37 | 49.964
2020-07-06 | 12:37 | 49.961
2020-07-06 | 12:37 | 49.957
2020-07-06 | 12:37 | 49.957
2020-07-06 | 12:37 | 49.955
2020-07-06 | 12:37 | 49.955
2020-07-06 | 12:37 | 49.952
2020-07-06 | 12:37 | 49.952
2020-07-06 | 12:37 | 49.95
2020-07-06 | 12:37 | 49.946
2020-07-06 | 12:37 | 49.942
2020-07-06 | 12:37 | 49.94
2020-07-06 | 12:37 | 49.939
2020-07-06 | 12:37 | 49.938
2020-07-06 | 12:37 | 49.938
2020-07-06 | 12:37 | 49.937
2020-07-06 | 12:37 | 49.936
2020-07-06 | 12:37 | 49.933
2020-07-06 | 12:37 | 49.934
2020-07-06 | 12:37 | 49.936
2020-07-06 | 12:37 | 49.941
2020-07-06 | 12:37 | 49.944
2020-07-06 | 12:37 | 49.948
2020-07-06 | 12:37 | 49.951
2020-07-06 | 12:37 | 49.952
2020-07-06 | 12:37 | 49.952
2020-07-06 | 12:37 | 49.951
2020-07-06 | 12:37 | 49.954
2020-07-06 | 12:37 | 49.951
2020-07-06 | 12:37 | 49.949
2020-07-06 | 12:37 | 49.946
2020-07-06 | 12:37 | 49.942
2020-07-06 | 12:37 | 49.94
2020-07-06 | 12:37 | 49.939
2020-07-06 | 12:37 | 49.94
2020-07-06 | 12:37 | 49.941
2020-07-06 | 12:37 | 49.939
2020-07-06 | 12:37 | 49.938
2020-07-06 | 12:37 | 49.94
2020-07-06 | 12:38 | 49.945
2020-07-06 | 12:38 | 49.952
2020-07-06 | 12:38 | 49.957
2020-07-06 | 12:38 | 49.96
2020-07-06 | 12:38 | 49.962
2020-07-06 | 12:38 | 49.96
2020-07-06 | 12:38 | 49.959
2020-07-06 | 12:38 | 49.958
2020-07-06 | 12:38 | 49.961
2020-07-06 | 12:38 | 49.961
2020-07-06 | 12:38 | 49.963
2020-07-06 | 12:38 | 49.969
2020-07-06 | 12:38 | 49.977
2020-07-06 | 12:38 | 49.979
2020-07-06 | 12:38 | 49.979
2020-07-06 | 12:38 | 49.981
2020-07-06 | 12:38 | 49.981
2020-07-06 | 12:38 | 49.983
2020-07-06 | 12:38 | 49.985
2020-07-06 | 12:38 | 49.984
2020-07-06 | 12:38 | 49.983
2020-07-06 | 12:38 | 49.982
2020-07-06 | 12:38 | 49.98
2020-07-06 | 12:38 | 49.98
2020-07-06 | 12:38 | 49.981
2020-07-06 | 12:38 | 49.979
2020-07-06 | 12:38 | 49.977
2020-07-06 | 12:38 | 49.976
2020-07-06 | 12:38 | 49.975
2020-07-06 | 12:38 | 49.977
2020-07-06 | 12:38 | 49.977
2020-07-06 | 12:38 | 49.982
2020-07-06 | 12:38 | 49.987
2020-07-06 | 12:38 | 49.99
2020-07-06 | 12:38 | 49.991
2020-07-06 | 12:38 | 49.992
2020-07-06 | 12:38 | 49.996
2020-07-06 | 12:38 | 49.998
2020-07-06 | 12:38 | 49.999
2020-07-06 | 12:38 | 50.002
2020-07-06 | 12:38 | 50.003
2020-07-06 | 12:38 | 50.002
2020-07-06 | 12:38 | 50.002
2020-07-06 | 12:38 | 50.001
2020-07-06 | 12:38 | 50.004
2020-07-06 | 12:38 | 50.005
2020-07-06 | 12:38 | 50.005
2020-07-06 | 12:38 | 50.006
2020-07-06 | 12:38 | 50.003
2020-07-06 | 12:38 | 50.002
2020-07-06 | 12:38 | 50.001
2020-07-06 | 12:38 | 50.004
2020-07-06 | 12:38 | 50.006
2020-07-06 | 12:38 | 50.008
2020-07-06 | 12:38 | 50.011
2020-07-06 | 12:38 | 50.014
2020-07-06 | 12:38 | 50.018
2020-07-06 | 12:38 | 50.021
2020-07-06 | 12:38 | 50.023
2020-07-06 | 12:38 | 50.025
2020-07-06 | 12:39 | 50.027
2020-07-06 | 12:39 | 50.03
2020-07-06 | 12:39 | 50.033
2020-07-06 | 12:39 | 50.035
2020-07-06 | 12:39 | 50.035
2020-07-06 | 12:39 | 50.034
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.034
2020-07-06 | 12:39 | 50.034
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.031
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.031
2020-07-06 | 12:39 | 50.031
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.035
2020-07-06 | 12:39 | 50.033
2020-07-06 | 12:39 | 50.031
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.032
2020-07-06 | 12:39 | 50.028
2020-07-06 | 12:39 | 50.026
2020-07-06 | 12:39 | 50.023
2020-07-06 | 12:39 | 50.02
2020-07-06 | 12:39 | 50.016
2020-07-06 | 12:39 | 50.013
2020-07-06 | 12:39 | 50.008
2020-07-06 | 12:39 | 50.005

## Event 20200708-1
In UTC
Date | Time | Freq
2020-07-08 | 5:19 | 49.972
2020-07-08 | 5:19 | 49.968
2020-07-08 | 5:19 | 49.963
2020-07-08 | 5:19 | 49.96
2020-07-08 | 5:19 | 49.958
2020-07-08 | 5:19 | 49.959
2020-07-08 | 5:19 | 49.96
2020-07-08 | 5:19 | 49.963
2020-07-08 | 5:19 | 49.966
2020-07-08 | 5:19 | 49.967
2020-07-08 | 5:19 | 49.971
2020-07-08 | 5:19 | 49.972
2020-07-08 | 5:19 | 49.973
2020-07-08 | 5:19 | 49.974
2020-07-08 | 5:19 | 49.975
2020-07-08 | 5:19 | 49.974
2020-07-08 | 5:19 | 49.973
2020-07-08 | 5:19 | 49.97
2020-07-08 | 5:19 | 49.966
2020-07-08 | 5:19 | 49.964
2020-07-08 | 5:19 | 49.963
2020-07-08 | 5:19 | 49.961
2020-07-08 | 5:19 | 49.962
2020-07-08 | 5:19 | 49.963
2020-07-08 | 5:19 | 49.962
2020-07-08 | 5:19 | 49.965
2020-07-08 | 5:19 | 49.965
2020-07-08 | 5:19 | 49.966
2020-07-08 | 5:19 | 49.966
2020-07-08 | 5:19 | 49.967
2020-07-08 | 5:20 | 49.966
2020-07-08 | 5:20 | 49.964
2020-07-08 | 5:20 | 49.963
2020-07-08 | 5:20 | 49.963
2020-07-08 | 5:20 | 49.965
2020-07-08 | 5:20 | 49.967
2020-07-08 | 5:20 | 49.968
2020-07-08 | 5:20 | 49.969
2020-07-08 | 5:20 | 49.972
2020-07-08 | 5:20 | 49.973
2020-07-08 | 5:20 | 49.975
2020-07-08 | 5:20 | 49.976
2020-07-08 | 5:20 | 49.978
2020-07-08 | 5:20 | 49.981
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.985
2020-07-08 | 5:20 | 49.987
2020-07-08 | 5:20 | 49.989
2020-07-08 | 5:20 | 49.991
2020-07-08 | 5:20 | 49.991
2020-07-08 | 5:20 | 49.991
2020-07-08 | 5:20 | 49.989
2020-07-08 | 5:20 | 49.986
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.985
2020-07-08 | 5:20 | 49.986
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.986
2020-07-08 | 5:20 | 49.987
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.982
2020-07-08 | 5:20 | 49.979
2020-07-08 | 5:20 | 49.98
2020-07-08 | 5:20 | 49.98
2020-07-08 | 5:20 | 49.979
2020-07-08 | 5:20 | 49.977
2020-07-08 | 5:20 | 49.978
2020-07-08 | 5:20 | 49.977
2020-07-08 | 5:20 | 49.978
2020-07-08 | 5:20 | 49.978
2020-07-08 | 5:20 | 49.977
2020-07-08 | 5:20 | 49.979
2020-07-08 | 5:20 | 49.98
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.985
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.986
2020-07-08 | 5:20 | 49.986
2020-07-08 | 5:20 | 49.987
2020-07-08 | 5:20 | 49.987
2020-07-08 | 5:20 | 49.986
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.983
2020-07-08 | 5:20 | 49.984
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.987
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.985
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.986
2020-07-08 | 5:21 | 49.985
2020-07-08 | 5:21 | 49.985
2020-07-08 | 5:21 | 49.987
2020-07-08 | 5:21 | 49.987
2020-07-08 | 5:21 | 49.989
2020-07-08 | 5:21 | 49.993
2020-07-08 | 5:21 | 49.997
2020-07-08 | 5:21 | 50.002
2020-07-08 | 5:21 | 50.006
2020-07-08 | 5:21 | 50.009
2020-07-08 | 5:21 | 50.013
2020-07-08 | 5:21 | 50.081
2020-07-08 | 5:21 | 50.166
2020-07-08 | 5:21 | 50.223
2020-07-08 | 5:21 | 50.27
2020-07-08 | 5:21 | 50.301
2020-07-08 | 5:21 | 50.317
2020-07-08 | 5:21 | 50.326
2020-07-08 | 5:21 | 50.326
2020-07-08 | 5:21 | 50.317
2020-07-08 | 5:21 | 50.307
2020-07-08 | 5:21 | 50.298
2020-07-08 | 5:21 | 50.29
2020-07-08 | 5:21 | 50.281
2020-07-08 | 5:21 | 50.276
2020-07-08 | 5:21 | 50.27
2020-07-08 | 5:21 | 50.268
2020-07-08 | 5:21 | 50.268
2020-07-08 | 5:21 | 50.269
2020-07-08 | 5:21 | 50.271
2020-07-08 | 5:21 | 50.272
2020-07-08 | 5:21 | 50.272
2020-07-08 | 5:21 | 50.272
2020-07-08 | 5:21 | 50.271
2020-07-08 | 5:21 | 50.27
2020-07-08 | 5:21 | 50.271
2020-07-08 | 5:21 | 50.269
2020-07-08 | 5:21 | 50.27
2020-07-08 | 5:21 | 50.272
2020-07-08 | 5:21 | 50.274
2020-07-08 | 5:21 | 50.276
2020-07-08 | 5:21 | 50.277
2020-07-08 | 5:21 | 50.279
2020-07-08 | 5:21 | 50.281
2020-07-08 | 5:21 | 50.282
2020-07-08 | 5:21 | 50.283
2020-07-08 | 5:21 | 50.284
2020-07-08 | 5:21 | 50.285
2020-07-08 | 5:21 | 50.286
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.283
2020-07-08 | 5:22 | 50.282
2020-07-08 | 5:22 | 50.278
2020-07-08 | 5:22 | 50.279
2020-07-08 | 5:22 | 50.278
2020-07-08 | 5:22 | 50.279
2020-07-08 | 5:22 | 50.28
2020-07-08 | 5:22 | 50.28
2020-07-08 | 5:22 | 50.28
2020-07-08 | 5:22 | 50.281
2020-07-08 | 5:22 | 50.282
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.285
2020-07-08 | 5:22 | 50.285
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.285
2020-07-08 | 5:22 | 50.289
2020-07-08 | 5:22 | 50.289
2020-07-08 | 5:22 | 50.29
2020-07-08 | 5:22 | 50.291
2020-07-08 | 5:22 | 50.29
2020-07-08 | 5:22 | 50.293
2020-07-08 | 5:22 | 50.292
2020-07-08 | 5:22 | 50.292
2020-07-08 | 5:22 | 50.291
2020-07-08 | 5:22 | 50.29
2020-07-08 | 5:22 | 50.287
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.285
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.287
2020-07-08 | 5:22 | 50.288
2020-07-08 | 5:22 | 50.292
2020-07-08 | 5:22 | 50.296
2020-07-08 | 5:22 | 50.299
2020-07-08 | 5:22 | 50.3
2020-07-08 | 5:22 | 50.301
2020-07-08 | 5:22 | 50.302
2020-07-08 | 5:22 | 50.299
2020-07-08 | 5:22 | 50.299
2020-07-08 | 5:22 | 50.297
2020-07-08 | 5:22 | 50.295
2020-07-08 | 5:22 | 50.294
2020-07-08 | 5:22 | 50.291
2020-07-08 | 5:22 | 50.289
2020-07-08 | 5:22 | 50.287
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.284
2020-07-08 | 5:22 | 50.286
2020-07-08 | 5:22 | 50.289
2020-07-08 | 5:22 | 50.291
2020-07-08 | 5:22 | 50.295
2020-07-08 | 5:22 | 50.296
2020-07-08 | 5:22 | 50.298
2020-07-08 | 5:23 | 50.298
2020-07-08 | 5:23 | 50.299
2020-07-08 | 5:23 | 50.3
2020-07-08 | 5:23 | 50.301
2020-07-08 | 5:23 | 50.299
2020-07-08 | 5:23 | 50.3
2020-07-08 | 5:23 | 50.298
2020-07-08 | 5:23 | 50.299
2020-07-08 | 5:23 | 50.299
2020-07-08 | 5:23 | 50.299
2020-07-08 | 5:23 | 50.298
2020-07-08 | 5:23 | 50.298
2020-07-08 | 5:23 | 50.295
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.292
2020-07-08 | 5:23 | 50.293
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.297
2020-07-08 | 5:23 | 50.299
2020-07-08 | 5:23 | 50.298
2020-07-08 | 5:23 | 50.297
2020-07-08 | 5:23 | 50.297
2020-07-08 | 5:23 | 50.296
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.294
2020-07-08 | 5:23 | 50.292
2020-07-08 | 5:23 | 50.291
2020-07-08 | 5:23 | 50.288
2020-07-08 | 5:23 | 50.286
2020-07-08 | 5:23 | 50.285
2020-07-08 | 5:23 | 50.286
2020-07-08 | 5:23 | 50.286
2020-07-08 | 5:23 | 50.287
2020-07-08 | 5:23 | 50.287
2020-07-08 | 5:23 | 50.289
2020-07-08 | 5:23 | 50.289
2020-07-08 | 5:23 | 50.286
2020-07-08 | 5:23 | 50.286
2020-07-08 | 5:23 | 50.286
2020-07-08 | 5:23 | 50.284
2020-07-08 | 5:23 | 50.285
2020-07-08 | 5:23 | 50.284
2020-07-08 | 5:23 | 50.283
2020-07-08 | 5:23 | 50.283
2020-07-08 | 5:23 | 50.28
2020-07-08 | 5:23 | 50.28
2020-07-08 | 5:23 | 50.28
2020-07-08 | 5:23 | 50.28
2020-07-08 | 5:23 | 50.278
2020-07-08 | 5:23 | 50.278
2020-07-08 | 5:23 | 50.279
2020-07-08 | 5:23 | 50.28
2020-07-08 | 5:23 | 50.281
2020-07-08 | 5:23 | 50.281
2020-07-08 | 5:23 | 50.282
2020-07-08 | 5:23 | 50.283
2020-07-08 | 5:24 | 50.284
2020-07-08 | 5:24 | 50.285
2020-07-08 | 5:24 | 50.286
2020-07-08 | 5:24 | 50.285
2020-07-08 | 5:24 | 50.285
2020-07-08 | 5:24 | 50.285
2020-07-08 | 5:24 | 50.285
2020-07-08 | 5:24 | 50.284
2020-07-08 | 5:24 | 50.281
2020-07-08 | 5:24 | 50.279
2020-07-08 | 5:24 | 50.277
2020-07-08 | 5:24 | 50.274
2020-07-08 | 5:24 | 50.272
2020-07-08 | 5:24 | 50.271
2020-07-08 | 5:24 | 50.268
2020-07-08 | 5:24 | 50.267
2020-07-08 | 5:24 | 50.265
2020-07-08 | 5:24 | 50.264
2020-07-08 | 5:24 | 50.263
2020-07-08 | 5:24 | 50.261
2020-07-08 | 5:24 | 50.259
2020-07-08 | 5:24 | 50.257
2020-07-08 | 5:24 | 50.254
2020-07-08 | 5:24 | 50.252
2020-07-08 | 5:24 | 50.25
2020-07-08 | 5:24 | 50.248
2020-07-08 | 5:24 | 50.25
2020-07-08 | 5:24 | 50.251
2020-07-08 | 5:24 | 50.251
2020-07-08 | 5:24 | 50.252
2020-07-08 | 5:24 | 50.25
2020-07-08 | 5:24 | 50.249
2020-07-08 | 5:24 | 50.247
2020-07-08 | 5:24 | 50.244
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.244
2020-07-08 | 5:24 | 50.245
2020-07-08 | 5:24 | 50.247
2020-07-08 | 5:24 | 50.247
2020-07-08 | 5:24 | 50.249
2020-07-08 | 5:24 | 50.249
2020-07-08 | 5:24 | 50.25
2020-07-08 | 5:24 | 50.25
2020-07-08 | 5:24 | 50.248
2020-07-08 | 5:24 | 50.246
2020-07-08 | 5:24 | 50.243
2020-07-08 | 5:24 | 50.24
2020-07-08 | 5:24 | 50.239
2020-07-08 | 5:24 | 50.236
2020-07-08 | 5:24 | 50.233
2020-07-08 | 5:24 | 50.229
2020-07-08 | 5:24 | 50.23
2020-07-08 | 5:24 | 50.23
2020-07-08 | 5:24 | 50.228
2020-07-08 | 5:24 | 50.225
2020-07-08 | 5:25 | 50.221
2020-07-08 | 5:25 | 50.219
2020-07-08 | 5:25 | 50.218
2020-07-08 | 5:25 | 50.22
2020-07-08 | 5:25 | 50.22
2020-07-08 | 5:25 | 50.22
2020-07-08 | 5:25 | 50.221
2020-07-08 | 5:25 | 50.221
2020-07-08 | 5:25 | 50.22
2020-07-08 | 5:25 | 50.222
2020-07-08 | 5:25 | 50.223
2020-07-08 | 5:25 | 50.224
2020-07-08 | 5:25 | 50.223
2020-07-08 | 5:25 | 50.221
2020-07-08 | 5:25 | 50.219
2020-07-08 | 5:25 | 50.215
2020-07-08 | 5:25 | 50.212
2020-07-08 | 5:25 | 50.21
2020-07-08 | 5:25 | 50.208
2020-07-08 | 5:25 | 50.206
2020-07-08 | 5:25 | 50.205
2020-07-08 | 5:25 | 50.207
2020-07-08 | 5:25 | 50.207
2020-07-08 | 5:25 | 50.211
2020-07-08 | 5:25 | 50.213
2020-07-08 | 5:25 | 50.215
2020-07-08 | 5:25 | 50.215
2020-07-08 | 5:25 | 50.215
2020-07-08 | 5:25 | 50.214
2020-07-08 | 5:25 | 50.212
2020-07-08 | 5:25 | 50.211
2020-07-08 | 5:25 | 50.208
2020-07-08 | 5:25 | 50.205
2020-07-08 | 5:25 | 50.202
2020-07-08 | 5:25 | 50.2
2020-07-08 | 5:25 | 50.202
2020-07-08 | 5:25 | 50.202
2020-07-08 | 5:25 | 50.203
2020-07-08 | 5:25 | 50.204
2020-07-08 | 5:25 | 50.204
2020-07-08 | 5:25 | 50.205
2020-07-08 | 5:25 | 50.205
2020-07-08 | 5:25 | 50.203
2020-07-08 | 5:25 | 50.202
2020-07-08 | 5:25 | 50.202
2020-07-08 | 5:25 | 50.203
2020-07-08 | 5:25 | 50.204
2020-07-08 | 5:25 | 50.205
2020-07-08 | 5:25 | 50.206
2020-07-08 | 5:25 | 50.204
2020-07-08 | 5:25 | 50.2
2020-07-08 | 5:25 | 50.196
2020-07-08 | 5:25 | 50.193
2020-07-08 | 5:25 | 50.191
2020-07-08 | 5:25 | 50.189
2020-07-08 | 5:25 | 50.188
2020-07-08 | 5:25 | 50.186
2020-07-08 | 5:25 | 50.182
2020-07-08 | 5:25 | 50.18
2020-07-08 | 5:26 | 50.179
2020-07-08 | 5:26 | 50.176
2020-07-08 | 5:26 | 50.174
2020-07-08 | 5:26 | 50.175
2020-07-08 | 5:26 | 50.176
2020-07-08 | 5:26 | 50.175
2020-07-08 | 5:26 | 50.174
2020-07-08 | 5:26 | 50.173
2020-07-08 | 5:26 | 50.171
2020-07-08 | 5:26 | 50.169
2020-07-08 | 5:26 | 50.167
2020-07-08 | 5:26 | 50.166
2020-07-08 | 5:26 | 50.164
2020-07-08 | 5:26 | 50.162
2020-07-08 | 5:26 | 50.161
2020-07-08 | 5:26 | 50.16
2020-07-08 | 5:26 | 50.157
2020-07-08 | 5:26 | 50.155
2020-07-08 | 5:26 | 50.155
2020-07-08 | 5:26 | 50.155
2020-07-08 | 5:26 | 50.156
2020-07-08 | 5:26 | 50.158
2020-07-08 | 5:26 | 50.158
2020-07-08 | 5:26 | 50.157
2020-07-08 | 5:26 | 50.155
2020-07-08 | 5:26 | 50.152
2020-07-08 | 5:26 | 50.149
2020-07-08 | 5:26 | 50.145
2020-07-08 | 5:26 | 50.144
2020-07-08 | 5:26 | 50.142
2020-07-08 | 5:26 | 50.141
2020-07-08 | 5:26 | 50.14
2020-07-08 | 5:26 | 50.137
2020-07-08 | 5:26 | 50.135
2020-07-08 | 5:26 | 50.135
2020-07-08 | 5:26 | 50.133
2020-07-08 | 5:26 | 50.133
2020-07-08 | 5:26 | 50.131
2020-07-08 | 5:26 | 50.129
2020-07-08 | 5:26 | 50.127
2020-07-08 | 5:26 | 50.124
2020-07-08 | 5:26 | 50.122
2020-07-08 | 5:26 | 50.121
2020-07-08 | 5:26 | 50.118
2020-07-08 | 5:26 | 50.116
2020-07-08 | 5:26 | 50.113
2020-07-08 | 5:26 | 50.11
2020-07-08 | 5:26 | 50.108
2020-07-08 | 5:26 | 50.105
2020-07-08 | 5:26 | 50.106
2020-07-08 | 5:26 | 50.106
2020-07-08 | 5:26 | 50.109
2020-07-08 | 5:26 | 50.11
2020-07-08 | 5:26 | 50.111
2020-07-08 | 5:26 | 50.113
2020-07-08 | 5:26 | 50.113
2020-07-08 | 5:26 | 50.114
2020-07-08 | 5:26 | 50.114
2020-07-08 | 5:26 | 50.114
2020-07-08 | 5:26 | 50.114
2020-07-08 | 5:26 | 50.113
2020-07-08 | 5:27 | 50.111
2020-07-08 | 5:27 | 50.109
2020-07-08 | 5:27 | 50.107
2020-07-08 | 5:27 | 50.105
2020-07-08 | 5:27 | 50.104
2020-07-08 | 5:27 | 50.103
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.103
2020-07-08 | 5:27 | 50.103
2020-07-08 | 5:27 | 50.104
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.101
2020-07-08 | 5:27 | 50.097
2020-07-08 | 5:27 | 50.095
2020-07-08 | 5:27 | 50.093
2020-07-08 | 5:27 | 50.091
2020-07-08 | 5:27 | 50.091
2020-07-08 | 5:27 | 50.091
2020-07-08 | 5:27 | 50.093
2020-07-08 | 5:27 | 50.092
2020-07-08 | 5:27 | 50.092
2020-07-08 | 5:27 | 50.093
2020-07-08 | 5:27 | 50.092
2020-07-08 | 5:27 | 50.091
2020-07-08 | 5:27 | 50.088
2020-07-08 | 5:27 | 50.088
2020-07-08 | 5:27 | 50.086
2020-07-08 | 5:27 | 50.087
2020-07-08 | 5:27 | 50.087
2020-07-08 | 5:27 | 50.089
2020-07-08 | 5:27 | 50.09
2020-07-08 | 5:27 | 50.091
2020-07-08 | 5:27 | 50.096
2020-07-08 | 5:27 | 50.098
2020-07-08 | 5:27 | 50.099
2020-07-08 | 5:27 | 50.097
2020-07-08 | 5:27 | 50.096
2020-07-08 | 5:27 | 50.095
2020-07-08 | 5:27 | 50.094
2020-07-08 | 5:27 | 50.094
2020-07-08 | 5:27 | 50.095
2020-07-08 | 5:27 | 50.096
2020-07-08 | 5:27 | 50.098
2020-07-08 | 5:27 | 50.101
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.103
2020-07-08 | 5:27 | 50.103
2020-07-08 | 5:27 | 50.103
2020-07-08 | 5:27 | 50.102
2020-07-08 | 5:27 | 50.1
2020-07-08 | 5:27 | 50.098
2020-07-08 | 5:27 | 50.098
2020-07-08 | 5:27 | 50.097
2020-07-08 | 5:27 | 50.097
2020-07-08 | 5:27 | 50.097
2020-07-08 | 5:28 | 50.096
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.1
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.097
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.096
2020-07-08 | 5:28 | 50.093
2020-07-08 | 5:28 | 50.093
2020-07-08 | 5:28 | 50.089
2020-07-08 | 5:28 | 50.087
2020-07-08 | 5:28 | 50.087
2020-07-08 | 5:28 | 50.086
2020-07-08 | 5:28 | 50.088
2020-07-08 | 5:28 | 50.09
2020-07-08 | 5:28 | 50.092
2020-07-08 | 5:28 | 50.095
2020-07-08 | 5:28 | 50.096
2020-07-08 | 5:28 | 50.097
2020-07-08 | 5:28 | 50.097
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.097
2020-07-08 | 5:28 | 50.096
2020-07-08 | 5:28 | 50.093
2020-07-08 | 5:28 | 50.092
2020-07-08 | 5:28 | 50.09
2020-07-08 | 5:28 | 50.089
2020-07-08 | 5:28 | 50.089
2020-07-08 | 5:28 | 50.087
2020-07-08 | 5:28 | 50.088
2020-07-08 | 5:28 | 50.09
2020-07-08 | 5:28 | 50.089
2020-07-08 | 5:28 | 50.091
2020-07-08 | 5:28 | 50.093
2020-07-08 | 5:28 | 50.094
2020-07-08 | 5:28 | 50.095
2020-07-08 | 5:28 | 50.094
2020-07-08 | 5:28 | 50.094
2020-07-08 | 5:28 | 50.096
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.101
2020-07-08 | 5:28 | 50.099
2020-07-08 | 5:28 | 50.098
2020-07-08 | 5:28 | 50.097
2020-07-08 | 5:28 | 50.095
2020-07-08 | 5:28 | 50.094
2020-07-08 | 5:28 | 50.094
2020-07-08 | 5:28 | 50.093
2020-07-08 | 5:28 | 50.092
2020-07-08 | 5:28 | 50.091
2020-07-08 | 5:28 | 50.092
2020-07-08 | 5:28 | 50.094
2020-07-08 | 5:29 | 50.094
2020-07-08 | 5:29 | 50.094
2020-07-08 | 5:29 | 50.094
2020-07-08 | 5:29 | 50.093
2020-07-08 | 5:29 | 50.092
2020-07-08 | 5:29 | 50.091
2020-07-08 | 5:29 | 50.091
2020-07-08 | 5:29 | 50.09
2020-07-08 | 5:29 | 50.088
2020-07-08 | 5:29 | 50.087
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.084
2020-07-08 | 5:29 | 50.084
2020-07-08 | 5:29 | 50.088
2020-07-08 | 5:29 | 50.09
2020-07-08 | 5:29 | 50.091
2020-07-08 | 5:29 | 50.093
2020-07-08 | 5:29 | 50.093
2020-07-08 | 5:29 | 50.094
2020-07-08 | 5:29 | 50.094
2020-07-08 | 5:29 | 50.093
2020-07-08 | 5:29 | 50.091
2020-07-08 | 5:29 | 50.09
2020-07-08 | 5:29 | 50.089
2020-07-08 | 5:29 | 50.084
2020-07-08 | 5:29 | 50.08
2020-07-08 | 5:29 | 50.078
2020-07-08 | 5:29 | 50.075
2020-07-08 | 5:29 | 50.072
2020-07-08 | 5:29 | 50.069
2020-07-08 | 5:29 | 50.068
2020-07-08 | 5:29 | 50.066
2020-07-08 | 5:29 | 50.065
2020-07-08 | 5:29 | 50.065
2020-07-08 | 5:29 | 50.065
2020-07-08 | 5:29 | 50.066
2020-07-08 | 5:29 | 50.066
2020-07-08 | 5:29 | 50.068
2020-07-08 | 5:29 | 50.071
2020-07-08 | 5:29 | 50.075
2020-07-08 | 5:29 | 50.078
2020-07-08 | 5:29 | 50.081
2020-07-08 | 5:29 | 50.083
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.087
2020-07-08 | 5:29 | 50.087
2020-07-08 | 5:29 | 50.087
2020-07-08 | 5:29 | 50.086
2020-07-08 | 5:29 | 50.086
2020-07-08 | 5:29 | 50.085
2020-07-08 | 5:29 | 50.086
2020-07-08 | 5:29 | 50.086
2020-07-08 | 5:29 | 50.087
2020-07-08 | 5:29 | 50.087
2020-07-08 | 5:29 | 50.089
2020-07-08 | 5:30 | 50.091
2020-07-08 | 5:30 | 50.094
2020-07-08 | 5:30 | 50.097
2020-07-08 | 5:30 | 50.099
2020-07-08 | 5:30 | 50.102
2020-07-08 | 5:30 | 50.102
2020-07-08 | 5:30 | 50.102
2020-07-08 | 5:30 | 50.102
2020-07-08 | 5:30 | 50.102
2020-07-08 | 5:30 | 50.102
2020-07-08 | 5:30 | 50.099
2020-07-08 | 5:30 | 50.097
2020-07-08 | 5:30 | 50.094
2020-07-08 | 5:30 | 50.091
2020-07-08 | 5:30 | 50.088
2020-07-08 | 5:30 | 50.086
2020-07-08 | 5:30 | 50.087
2020-07-08 | 5:30 | 50.085
2020-07-08 | 5:30 | 50.084
2020-07-08 | 5:30 | 50.084
2020-07-08 | 5:30 | 50.086
2020-07-08 | 5:30 | 50.087
2020-07-08 | 5:30 | 50.089
2020-07-08 | 5:30 | 50.091
2020-07-08 | 5:30 | 50.093
2020-07-08 | 5:30 | 50.097
2020-07-08 | 5:30 | 50.098
2020-07-08 | 5:30 | 50.099
2020-07-08 | 5:30 | 50.1
2020-07-08 | 5:30 | 50.098
2020-07-08 | 5:30 | 50.095
2020-07-08 | 5:30 | 50.092
2020-07-08 | 5:30 | 50.089
2020-07-08 | 5:30 | 50.085
2020-07-08 | 5:30 | 50.081
2020-07-08 | 5:30 | 50.078
2020-07-08 | 5:30 | 50.074
2020-07-08 | 5:30 | 50.07
2020-07-08 | 5:30 | 50.068
2020-07-08 | 5:30 | 50.066
2020-07-08 | 5:30 | 50.064
2020-07-08 | 5:30 | 50.064
2020-07-08 | 5:30 | 50.065
2020-07-08 | 5:30 | 50.066
2020-07-08 | 5:30 | 50.068
2020-07-08 | 5:30 | 50.069
2020-07-08 | 5:30 | 50.07
2020-07-08 | 5:30 | 50.074
2020-07-08 | 5:30 | 50.078
2020-07-08 | 5:30 | 50.079
2020-07-08 | 5:30 | 50.083
2020-07-08 | 5:30 | 50.084
2020-07-08 | 5:30 | 50.086
2020-07-08 | 5:30 | 50.086
2020-07-08 | 5:30 | 50.086
2020-07-08 | 5:30 | 50.085
2020-07-08 | 5:30 | 50.084
2020-07-08 | 5:30 | 50.083
2020-07-08 | 5:30 | 50.081
2020-07-08 | 5:30 | 50.08
2020-07-08 | 5:30 | 50.081
2020-07-08 | 5:31 | 50.083
2020-07-08 | 5:31 | 50.083
2020-07-08 | 5:31 | 50.084
2020-07-08 | 5:31 | 50.082
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.082
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.078
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.082
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.083
2020-07-08 | 5:31 | 50.083
2020-07-08 | 5:31 | 50.084
2020-07-08 | 5:31 | 50.082
2020-07-08 | 5:31 | 50.082
2020-07-08 | 5:31 | 50.083
2020-07-08 | 5:31 | 50.084
2020-07-08 | 5:31 | 50.083
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.078
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.079
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.081
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.08
2020-07-08 | 5:31 | 50.078
2020-07-08 | 5:31 | 50.078
2020-07-08 | 5:31 | 50.077
2020-07-08 | 5:31 | 50.077
2020-07-08 | 5:32 | 50.076
2020-07-08 | 5:32 | 50.075
2020-07-08 | 5:32 | 50.074
2020-07-08 | 5:32 | 50.075
2020-07-08 | 5:32 | 50.076
2020-07-08 | 5:32 | 50.076
2020-07-08 | 5:32 | 50.076
2020-07-08 | 5:32 | 50.075
2020-07-08 | 5:32 | 50.077
2020-07-08 | 5:32 | 50.079
2020-07-08 | 5:32 | 50.08
2020-07-08 | 5:32 | 50.081
2020-07-08 | 5:32 | 50.085
2020-07-08 | 5:32 | 50.086
2020-07-08 | 5:32 | 50.087
2020-07-08 | 5:32 | 50.087
2020-07-08 | 5:32 | 50.086
2020-07-08 | 5:32 | 50.086
2020-07-08 | 5:32 | 50.085
2020-07-08 | 5:32 | 50.082
2020-07-08 | 5:32 | 50.08
2020-07-08 | 5:32 | 50.077
2020-07-08 | 5:32 | 50.075
2020-07-08 | 5:32 | 50.071
2020-07-08 | 5:32 | 50.071
2020-07-08 | 5:32 | 50.073
2020-07-08 | 5:32 | 50.073
2020-07-08 | 5:32 | 50.074
2020-07-08 | 5:32 | 50.075
2020-07-08 | 5:32 | 50.072
2020-07-08 | 5:32 | 50.072
2020-07-08 | 5:32 | 50.072
2020-07-08 | 5:32 | 50.069
2020-07-08 | 5:32 | 50.069
2020-07-08 | 5:32 | 50.066
2020-07-08 | 5:32 | 50.064
2020-07-08 | 5:32 | 50.063
2020-07-08 | 5:32 | 50.062
2020-07-08 | 5:32 | 50.059
2020-07-08 | 5:32 | 50.057
2020-07-08 | 5:32 | 50.056
2020-07-08 | 5:32 | 50.055
2020-07-08 | 5:32 | 50.055
2020-07-08 | 5:32 | 50.058
2020-07-08 | 5:32 | 50.063
2020-07-08 | 5:32 | 50.065
2020-07-08 | 5:32 | 50.067
2020-07-08 | 5:32 | 50.069
2020-07-08 | 5:32 | 50.073
2020-07-08 | 5:32 | 50.073
2020-07-08 | 5:32 | 50.073
2020-07-08 | 5:32 | 50.073
2020-07-08 | 5:32 | 50.072
2020-07-08 | 5:32 | 50.071
2020-07-08 | 5:32 | 50.07
2020-07-08 | 5:32 | 50.069
2020-07-08 | 5:32 | 50.068
2020-07-08 | 5:32 | 50.065
2020-07-08 | 5:32 | 50.064
2020-07-08 | 5:32 | 50.062
2020-07-08 | 5:32 | 50.061
2020-07-08 | 5:33 | 50.06
2020-07-08 | 5:33 | 50.058
2020-07-08 | 5:33 | 50.057
2020-07-08 | 5:33 | 50.057
2020-07-08 | 5:33 | 50.057
2020-07-08 | 5:33 | 50.057
2020-07-08 | 5:33 | 50.058
2020-07-08 | 5:33 | 50.059
2020-07-08 | 5:33 | 50.06
2020-07-08 | 5:33 | 50.061
2020-07-08 | 5:33 | 50.062
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.062
2020-07-08 | 5:33 | 50.061
2020-07-08 | 5:33 | 50.06
2020-07-08 | 5:33 | 50.059
2020-07-08 | 5:33 | 50.058
2020-07-08 | 5:33 | 50.057
2020-07-08 | 5:33 | 50.056
2020-07-08 | 5:33 | 50.058
2020-07-08 | 5:33 | 50.06
2020-07-08 | 5:33 | 50.062
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.063
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.063
2020-07-08 | 5:33 | 50.063
2020-07-08 | 5:33 | 50.062
2020-07-08 | 5:33 | 50.063
2020-07-08 | 5:33 | 50.064
2020-07-08 | 5:33 | 50.065
2020-07-08 | 5:33 | 50.067
2020-07-08 | 5:33 | 50.069
2020-07-08 | 5:33 | 50.07
2020-07-08 | 5:33 | 50.07
2020-07-08 | 5:33 | 50.07
2020-07-08 | 5:33 | 50.071
2020-07-08 | 5:33 | 50.069
2020-07-08 | 5:33 | 50.067
2020-07-08 | 5:33 | 50.062
2020-07-08 | 5:33 | 50.059
2020-07-08 | 5:33 | 50.057
2020-07-08 | 5:33 | 50.051
2020-07-08 | 5:33 | 50.052
2020-07-08 | 5:33 | 50.05
2020-07-08 | 5:33 | 50.051
2020-07-08 | 5:33 | 50.051
2020-07-08 | 5:33 | 50.05
2020-07-08 | 5:33 | 50.05
2020-07-08 | 5:33 | 50.049
2020-07-08 | 5:33 | 50.05
2020-07-08 | 5:33 | 50.05
2020-07-08 | 5:33 | 50.051
2020-07-08 | 5:33 | 50.052
2020-07-08 | 5:33 | 50.053
2020-07-08 | 5:33 | 50.053
2020-07-08 | 5:34 | 50.056
2020-07-08 | 5:34 | 50.057
2020-07-08 | 5:34 | 50.059
2020-07-08 | 5:34 | 50.06
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.063
2020-07-08 | 5:34 | 50.065
2020-07-08 | 5:34 | 50.064
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.057
2020-07-08 | 5:34 | 50.053
2020-07-08 | 5:34 | 50.051
2020-07-08 | 5:34 | 50.049
2020-07-08 | 5:34 | 50.05
2020-07-08 | 5:34 | 50.049
2020-07-08 | 5:34 | 50.05
2020-07-08 | 5:34 | 50.051
2020-07-08 | 5:34 | 50.051
2020-07-08 | 5:34 | 50.052
2020-07-08 | 5:34 | 50.057
2020-07-08 | 5:34 | 50.059
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.064
2020-07-08 | 5:34 | 50.063
2020-07-08 | 5:34 | 50.063
2020-07-08 | 5:34 | 50.063
2020-07-08 | 5:34 | 50.064
2020-07-08 | 5:34 | 50.064
2020-07-08 | 5:34 | 50.064
2020-07-08 | 5:34 | 50.065
2020-07-08 | 5:34 | 50.064
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.069
2020-07-08 | 5:34 | 50.069
2020-07-08 | 5:34 | 50.069
2020-07-08 | 5:34 | 50.069
2020-07-08 | 5:34 | 50.068
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.065
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.063
2020-07-08 | 5:34 | 50.063
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.062
2020-07-08 | 5:34 | 50.065
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.066
2020-07-08 | 5:34 | 50.067
2020-07-08 | 5:34 | 50.068
2020-07-08 | 5:34 | 50.071
2020-07-08 | 5:34 | 50.073
2020-07-08 | 5:34 | 50.075
2020-07-08 | 5:34 | 50.076
2020-07-08 | 5:34 | 50.078
2020-07-08 | 5:34 | 50.081
2020-07-08 | 5:34 | 50.081
2020-07-08 | 5:35 | 50.081
2020-07-08 | 5:35 | 50.08
2020-07-08 | 5:35 | 50.081
2020-07-08 | 5:35 | 50.083
2020-07-08 | 5:35 | 50.085
2020-07-08 | 5:35 | 50.084
2020-07-08 | 5:35 | 50.083
2020-07-08 | 5:35 | 50.083
2020-07-08 | 5:35 | 50.085
2020-07-08 | 5:35 | 50.084
2020-07-08 | 5:35 | 50.085
2020-07-08 | 5:35 | 50.084
2020-07-08 | 5:35 | 50.083
2020-07-08 | 5:35 | 50.081
2020-07-08 | 5:35 | 50.079
2020-07-08 | 5:35 | 50.078
2020-07-08 | 5:35 | 50.075
2020-07-08 | 5:35 | 50.074
2020-07-08 | 5:35 | 50.073
2020-07-08 | 5:35 | 50.074
2020-07-08 | 5:35 | 50.071
2020-07-08 | 5:35 | 50.071
2020-07-08 | 5:35 | 50.07
2020-07-08 | 5:35 | 50.068
2020-07-08 | 5:35 | 50.066
2020-07-08 | 5:35 | 50.066
2020-07-08 | 5:35 | 50.064
2020-07-08 | 5:35 | 50.062
2020-07-08 | 5:35 | 50.06
2020-07-08 | 5:35 | 50.057
2020-07-08 | 5:35 | 50.055
2020-07-08 | 5:35 | 50.055
2020-07-08 | 5:35 | 50.056
2020-07-08 | 5:35 | 50.058
2020-07-08 | 5:35 | 50.062
2020-07-08 | 5:35 | 50.065
2020-07-08 | 5:35 | 50.07
2020-07-08 | 5:35 | 50.074
2020-07-08 | 5:35 | 50.078
2020-07-08 | 5:35 | 50.08
2020-07-08 | 5:35 | 50.079
2020-07-08 | 5:35 | 50.076
2020-07-08 | 5:35 | 50.075
2020-07-08 | 5:35 | 50.07
2020-07-08 | 5:35 | 50.068
2020-07-08 | 5:35 | 50.065
2020-07-08 | 5:35 | 50.062
2020-07-08 | 5:35 | 50.059
2020-07-08 | 5:35 | 50.058
2020-07-08 | 5:35 | 50.058
2020-07-08 | 5:35 | 50.059
2020-07-08 | 5:35 | 50.06
2020-07-08 | 5:35 | 50.061
2020-07-08 | 5:35 | 50.062
2020-07-08 | 5:35 | 50.063
2020-07-08 | 5:35 | 50.065
2020-07-08 | 5:35 | 50.066
2020-07-08 | 5:35 | 50.066
2020-07-08 | 5:35 | 50.066
2020-07-08 | 5:36 | 50.066
2020-07-08 | 5:36 | 50.063
2020-07-08 | 5:36 | 50.065
2020-07-08 | 5:36 | 50.064
2020-07-08 | 5:36 | 50.064
2020-07-08 | 5:36 | 50.063
2020-07-08 | 5:36 | 50.062
2020-07-08 | 5:36 | 50.06
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.058
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.057
2020-07-08 | 5:36 | 50.055
2020-07-08 | 5:36 | 50.053
2020-07-08 | 5:36 | 50.05
2020-07-08 | 5:36 | 50.049
2020-07-08 | 5:36 | 50.047
2020-07-08 | 5:36 | 50.047
2020-07-08 | 5:36 | 50.047
2020-07-08 | 5:36 | 50.045
2020-07-08 | 5:36 | 50.046
2020-07-08 | 5:36 | 50.047
2020-07-08 | 5:36 | 50.048
2020-07-08 | 5:36 | 50.047
2020-07-08 | 5:36 | 50.047
2020-07-08 | 5:36 | 50.049
2020-07-08 | 5:36 | 50.051
2020-07-08 | 5:36 | 50.055
2020-07-08 | 5:36 | 50.057
2020-07-08 | 5:36 | 50.058
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.058
2020-07-08 | 5:36 | 50.056
2020-07-08 | 5:36 | 50.056
2020-07-08 | 5:36 | 50.056
2020-07-08 | 5:36 | 50.057
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.06
2020-07-08 | 5:36 | 50.06
2020-07-08 | 5:36 | 50.062
2020-07-08 | 5:36 | 50.062
2020-07-08 | 5:36 | 50.063
2020-07-08 | 5:36 | 50.063
2020-07-08 | 5:36 | 50.063
2020-07-08 | 5:36 | 50.064
2020-07-08 | 5:36 | 50.061
2020-07-08 | 5:36 | 50.059
2020-07-08 | 5:36 | 50.058
2020-07-08 | 5:36 | 50.057
2020-07-08 | 5:36 | 50.055
2020-07-08 | 5:36 | 50.053
2020-07-08 | 5:36 | 50.052
2020-07-08 | 5:36 | 50.052
2020-07-08 | 5:36 | 50.052
2020-07-08 | 5:36 | 50.051
2020-07-08 | 5:36 | 50.05
2020-07-08 | 5:36 | 50.05
2020-07-08 | 5:36 | 50.051
2020-07-08 | 5:36 | 50.053
2020-07-08 | 5:37 | 50.052
2020-07-08 | 5:37 | 50.055
2020-07-08 | 5:37 | 50.056
2020-07-08 | 5:37 | 50.059
2020-07-08 | 5:37 | 50.061
2020-07-08 | 5:37 | 50.065
2020-07-08 | 5:37 | 50.068
2020-07-08 | 5:37 | 50.073
2020-07-08 | 5:37 | 50.074
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.076
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.075
2020-07-08 | 5:37 | 50.074
2020-07-08 | 5:37 | 50.074
2020-07-08 | 5:37 | 50.074
2020-07-08 | 5:37 | 50.076
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.076
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.08
2020-07-08 | 5:37 | 50.083
2020-07-08 | 5:37 | 50.081
2020-07-08 | 5:37 | 50.082
2020-07-08 | 5:37 | 50.08
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.079
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.078
2020-07-08 | 5:37 | 50.076
2020-07-08 | 5:37 | 50.075
2020-07-08 | 5:37 | 50.073
2020-07-08 | 5:37 | 50.072
2020-07-08 | 5:37 | 50.071
2020-07-08 | 5:37 | 50.07
2020-07-08 | 5:37 | 50.07
2020-07-08 | 5:37 | 50.069
2020-07-08 | 5:37 | 50.07
2020-07-08 | 5:37 | 50.071
2020-07-08 | 5:37 | 50.071
2020-07-08 | 5:37 | 50.072
2020-07-08 | 5:37 | 50.072
2020-07-08 | 5:37 | 50.071
2020-07-08 | 5:37 | 50.072
2020-07-08 | 5:37 | 50.072
2020-07-08 | 5:37 | 50.074
2020-07-08 | 5:37 | 50.075
2020-07-08 | 5:37 | 50.076
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:37 | 50.077
2020-07-08 | 5:38 | 50.075
2020-07-08 | 5:38 | 50.075
2020-07-08 | 5:38 | 50.076
2020-07-08 | 5:38 | 50.077
2020-07-08 | 5:38 | 50.079
2020-07-08 | 5:38 | 50.081
2020-07-08 | 5:38 | 50.083
2020-07-08 | 5:38 | 50.083
2020-07-08 | 5:38 | 50.083
2020-07-08 | 5:38 | 50.083
2020-07-08 | 5:38 | 50.083
2020-07-08 | 5:38 | 50.082
2020-07-08 | 5:38 | 50.08
2020-07-08 | 5:38 | 50.078
2020-07-08 | 5:38 | 50.076
2020-07-08 | 5:38 | 50.075
2020-07-08 | 5:38 | 50.073
2020-07-08 | 5:38 | 50.072
2020-07-08 | 5:38 | 50.07
2020-07-08 | 5:38 | 50.068
2020-07-08 | 5:38 | 50.068
2020-07-08 | 5:38 | 50.069
2020-07-08 | 5:38 | 50.068
2020-07-08 | 5:38 | 50.067
2020-07-08 | 5:38 | 50.066
2020-07-08 | 5:38 | 50.067
2020-07-08 | 5:38 | 50.067
2020-07-08 | 5:38 | 50.064
2020-07-08 | 5:38 | 50.061
2020-07-08 | 5:38 | 50.058
2020-07-08 | 5:38 | 50.055
2020-07-08 | 5:38 | 50.052
2020-07-08 | 5:38 | 50.05
2020-07-08 | 5:38 | 50.052
2020-07-08 | 5:38 | 50.053
2020-07-08 | 5:38 | 50.054
2020-07-08 | 5:38 | 50.057
2020-07-08 | 5:38 | 50.06
2020-07-08 | 5:38 | 50.061
2020-07-08 | 5:38 | 50.063
2020-07-08 | 5:38 | 50.066
2020-07-08 | 5:38 | 50.067
2020-07-08 | 5:38 | 50.066
2020-07-08 | 5:38 | 50.067
2020-07-08 | 5:38 | 50.069
2020-07-08 | 5:38 | 50.07
2020-07-08 | 5:38 | 50.07
2020-07-08 | 5:38 | 50.07
2020-07-08 | 5:38 | 50.071
2020-07-08 | 5:38 | 50.071
2020-07-08 | 5:38 | 50.071
2020-07-08 | 5:38 | 50.069
2020-07-08 | 5:38 | 50.068
2020-07-08 | 5:38 | 50.066
2020-07-08 | 5:38 | 50.063
2020-07-08 | 5:38 | 50.059
2020-07-08 | 5:38 | 50.058
2020-07-08 | 5:38 | 50.058
2020-07-08 | 5:38 | 50.056
2020-07-08 | 5:38 | 50.055
2020-07-08 | 5:38 | 50.054
2020-07-08 | 5:39 | 50.053
2020-07-08 | 5:39 | 50.052
2020-07-08 | 5:39 | 50.053
2020-07-08 | 5:39 | 50.052
2020-07-08 | 5:39 | 50.054
2020-07-08 | 5:39 | 50.054
2020-07-08 | 5:39 | 50.054
2020-07-08 | 5:39 | 50.055
2020-07-08 | 5:39 | 50.053
2020-07-08 | 5:39 | 50.051
2020-07-08 | 5:39 | 50.049
2020-07-08 | 5:39 | 50.047
2020-07-08 | 5:39 | 50.045
2020-07-08 | 5:39 | 50.043
2020-07-08 | 5:39 | 50.042
2020-07-08 | 5:39 | 50.041
2020-07-08 | 5:39 | 50.041
2020-07-08 | 5:39 | 50.043
2020-07-08 | 5:39 | 50.042
2020-07-08 | 5:39 | 50.044
2020-07-08 | 5:39 | 50.045
2020-07-08 | 5:39 | 50.047
2020-07-08 | 5:39 | 50.051
2020-07-08 | 5:39 | 50.054
2020-07-08 | 5:39 | 50.055
2020-07-08 | 5:39 | 50.057
2020-07-08 | 5:39 | 50.058
2020-07-08 | 5:39 | 50.057
2020-07-08 | 5:39 | 50.056
2020-07-08 | 5:39 | 50.053
2020-07-08 | 5:39 | 50.05
2020-07-08 | 5:39 | 50.049
2020-07-08 | 5:39 | 50.049
2020-07-08 | 5:39 | 50.048
2020-07-08 | 5:39 | 50.048
2020-07-08 | 5:39 | 50.049
2020-07-08 | 5:39 | 50.048
2020-07-08 | 5:39 | 50.05
2020-07-08 | 5:39 | 50.05
2020-07-08 | 5:39 | 50.047
2020-07-08 | 5:39 | 50.047
2020-07-08 | 5:39 | 50.043
2020-07-08 | 5:39 | 50.04
2020-07-08 | 5:39 | 50.038
2020-07-08 | 5:39 | 50.039
2020-07-08 | 5:39 | 50.039
2020-07-08 | 5:39 | 50.04
2020-07-08 | 5:39 | 50.041
2020-07-08 | 5:39 | 50.041
2020-07-08 | 5:39 | 50.04
2020-07-08 | 5:39 | 50.04
2020-07-08 | 5:39 | 50.039
2020-07-08 | 5:39 | 50.036
2020-07-08 | 5:39 | 50.035
2020-07-08 | 5:39 | 50.032
2020-07-08 | 5:39 | 50.031
2020-07-08 | 5:39 | 50.031
2020-07-08 | 5:39 | 50.03
2020-07-08 | 5:39 | 50.027
2020-07-08 | 5:40 | 50.025
2020-07-08 | 5:40 | 50.027
2020-07-08 | 5:40 | 50.026
2020-07-08 | 5:40 | 50.026
2020-07-08 | 5:40 | 50.028
2020-07-08 | 5:40 | 50.029
2020-07-08 | 5:40 | 50.031
2020-07-08 | 5:40 | 50.031
2020-07-08 | 5:40 | 50.033
2020-07-08 | 5:40 | 50.034
2020-07-08 | 5:40 | 50.035
2020-07-08 | 5:40 | 50.036
2020-07-08 | 5:40 | 50.035
2020-07-08 | 5:40 | 50.035
2020-07-08 | 5:40 | 50.035
2020-07-08 | 5:40 | 50.035
2020-07-08 | 5:40 | 50.036
2020-07-08 | 5:40 | 50.036
2020-07-08 | 5:40 | 50.037
2020-07-08 | 5:40 | 50.039
2020-07-08 | 5:40 | 50.039
2020-07-08 | 5:40 | 50.039
2020-07-08 | 5:40 | 50.037
2020-07-08 | 5:40 | 50.035
2020-07-08 | 5:40 | 50.033
2020-07-08 | 5:40 | 50.03
2020-07-08 | 5:40 | 50.028
2020-07-08 | 5:40 | 50.025
2020-07-08 | 5:40 | 50.025
2020-07-08 | 5:40 | 50.024
2020-07-08 | 5:40 | 50.022
2020-07-08 | 5:40 | 50.019
2020-07-08 | 5:40 | 50.017
2020-07-08 | 5:40 | 50.016
2020-07-08 | 5:40 | 50.014
2020-07-08 | 5:40 | 50.013
2020-07-08 | 5:40 | 50.012
2020-07-08 | 5:40 | 50.015
2020-07-08 | 5:40 | 50.017
2020-07-08 | 5:40 | 50.02
2020-07-08 | 5:40 | 50.023
2020-07-08 | 5:40 | 50.025
2020-07-08 | 5:40 | 50.028
2020-07-08 | 5:40 | 50.029
2020-07-08 | 5:40 | 50.032
2020-07-08 | 5:40 | 50.033
2020-07-08 | 5:40 | 50.033
2020-07-08 | 5:40 | 50.033
2020-07-08 | 5:40 | 50.034
2020-07-08 | 5:40 | 50.031
2020-07-08 | 5:40 | 50.032
2020-07-08 | 5:40 | 50.031
2020-07-08 | 5:40 | 50.03
2020-07-08 | 5:40 | 50.031
2020-07-08 | 5:40 | 50.03
2020-07-08 | 5:40 | 50.027
2020-07-08 | 5:40 | 50.025
2020-07-08 | 5:40 | 50.023
2020-07-08 | 5:40 | 50.02
2020-07-08 | 5:40 | 50.02
2020-07-08 | 5:40 | 50.019
2020-07-08 | 5:41 | 50.02
2020-07-08 | 5:41 | 50.019
2020-07-08 | 5:41 | 50.019
2020-07-08 | 5:41 | 50.022
2020-07-08 | 5:41 | 50.019
2020-07-08 | 5:41 | 50.018
2020-07-08 | 5:41 | 50.018
2020-07-08 | 5:41 | 50.019
2020-07-08 | 5:41 | 50.019
2020-07-08 | 5:41 | 50.02
2020-07-08 | 5:41 | 50.021
2020-07-08 | 5:41 | 50.022
2020-07-08 | 5:41 | 50.022
2020-07-08 | 5:41 | 50.023
2020-07-08 | 5:41 | 50.02
2020-07-08 | 5:41 | 50.021
2020-07-08 | 5:41 | 50.019
2020-07-08 | 5:41 | 50.016
2020-07-08 | 5:41 | 50.013
2020-07-08 | 5:41 | 50.012
2020-07-08 | 5:41 | 50.011
2020-07-08 | 5:41 | 50.012
2020-07-08 | 5:41 | 50.011
2020-07-08 | 5:41 | 50.011
2020-07-08 | 5:41 | 50.011
2020-07-08 | 5:41 | 50.009
2020-07-08 | 5:41 | 50.009
2020-07-08 | 5:41 | 50.007
2020-07-08 | 5:41 | 50.005
2020-07-08 | 5:41 | 50.002
2020-07-08 | 5:41 | 49.998
2020-07-08 | 5:41 | 49.996
2020-07-08 | 5:41 | 49.991
2020-07-08 | 5:41 | 49.99
2020-07-08 | 5:41 | 49.992
2020-07-08 | 5:41 | 49.993
2020-07-08 | 5:41 | 49.993
2020-07-08 | 5:41 | 49.993
2020-07-08 | 5:41 | 49.993
2020-07-08 | 5:41 | 49.993
2020-07-08 | 5:41 | 49.99
2020-07-08 | 5:41 | 49.99
2020-07-08 | 5:41 | 49.988
2020-07-08 | 5:41 | 49.985
2020-07-08 | 5:41 | 49.984
2020-07-08 | 5:41 | 49.983
2020-07-08 | 5:41 | 49.982
2020-07-08 | 5:41 | 49.98
2020-07-08 | 5:41 | 49.981
2020-07-08 | 5:41 | 49.981
2020-07-08 | 5:41 | 49.982
2020-07-08 | 5:41 | 49.982
2020-07-08 | 5:41 | 49.984
2020-07-08 | 5:41 | 49.986
2020-07-08 | 5:41 | 49.988
2020-07-08 | 5:41 | 49.988
2020-07-08 | 5:41 | 49.99
2020-07-08 | 5:41 | 49.993
2020-07-08 | 5:41 | 49.995
2020-07-08 | 5:42 | 49.997
2020-07-08 | 5:42 | 50.002
2020-07-08 | 5:42 | 50.008
2020-07-08 | 5:42 | 50.014
2020-07-08 | 5:42 | 50.019
2020-07-08 | 5:42 | 50.02
2020-07-08 | 5:42 | 50.021
2020-07-08 | 5:42 | 50.02
2020-07-08 | 5:42 | 50.017
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.013
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.016
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.015
2020-07-08 | 5:42 | 50.014
2020-07-08 | 5:42 | 50.014
2020-07-08 | 5:42 | 50.014
2020-07-08 | 5:42 | 50.014
2020-07-08 | 5:42 | 50.012
2020-07-08 | 5:42 | 50.012
2020-07-08 | 5:42 | 50.013
2020-07-08 | 5:42 | 50.014
2020-07-08 | 5:42 | 50.017
2020-07-08 | 5:42 | 50.018
2020-07-08 | 5:42 | 50.018

## Event 20200708-2
In UTC
Date | Time | Freq
2020-07-08 | 9:45 | 50.069
2020-07-08 | 9:45 | 50.063
2020-07-08 | 9:45 | 50.056
2020-07-08 | 9:45 | 50.047
2020-07-08 | 9:45 | 50.039
2020-07-08 | 9:45 | 50.032
2020-07-08 | 9:45 | 50.026
2020-07-08 | 9:45 | 50.017
2020-07-08 | 9:45 | 50.007
2020-07-08 | 9:45 | 49.997
2020-07-08 | 9:45 | 49.986
2020-07-08 | 9:45 | 49.973
2020-07-08 | 9:45 | 49.961
2020-07-08 | 9:45 | 49.95
2020-07-08 | 9:45 | 49.943
2020-07-08 | 9:45 | 49.937
2020-07-08 | 9:45 | 49.932
2020-07-08 | 9:45 | 49.931
2020-07-08 | 9:45 | 49.93
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.928
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.927
2020-07-08 | 9:45 | 49.929
2020-07-08 | 9:45 | 49.931
2020-07-08 | 9:45 | 49.932
2020-07-08 | 9:46 | 49.932
2020-07-08 | 9:46 | 49.936
2020-07-08 | 9:46 | 49.938
2020-07-08 | 9:46 | 49.94
2020-07-08 | 9:46 | 49.945
2020-07-08 | 9:46 | 49.949
2020-07-08 | 9:46 | 49.951
2020-07-08 | 9:46 | 49.955
2020-07-08 | 9:46 | 49.957
2020-07-08 | 9:46 | 49.957
2020-07-08 | 9:46 | 49.956
2020-07-08 | 9:46 | 49.956
2020-07-08 | 9:46 | 49.957
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.959
2020-07-08 | 9:46 | 49.957
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.959
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.958
2020-07-08 | 9:46 | 49.955
2020-07-08 | 9:46 | 49.956
2020-07-08 | 9:46 | 49.957
2020-07-08 | 9:46 | 49.959
2020-07-08 | 9:46 | 49.96
2020-07-08 | 9:46 | 49.962
2020-07-08 | 9:46 | 49.964
2020-07-08 | 9:46 | 49.965
2020-07-08 | 9:46 | 49.964
2020-07-08 | 9:46 | 49.964
2020-07-08 | 9:46 | 49.964
2020-07-08 | 9:46 | 49.964
2020-07-08 | 9:46 | 49.962
2020-07-08 | 9:46 | 49.963
2020-07-08 | 9:46 | 49.962
2020-07-08 | 9:46 | 49.961
2020-07-08 | 9:46 | 49.962
2020-07-08 | 9:46 | 49.962
2020-07-08 | 9:46 | 49.962
2020-07-08 | 9:46 | 49.964
2020-07-08 | 9:46 | 49.966
2020-07-08 | 9:46 | 49.965
2020-07-08 | 9:46 | 49.967
2020-07-08 | 9:46 | 49.97
2020-07-08 | 9:46 | 49.971
2020-07-08 | 9:46 | 49.975
2020-07-08 | 9:46 | 49.981
2020-07-08 | 9:46 | 49.983
2020-07-08 | 9:46 | 49.984
2020-07-08 | 9:46 | 49.988
2020-07-08 | 9:46 | 49.99
2020-07-08 | 9:46 | 49.992
2020-07-08 | 9:46 | 49.997
2020-07-08 | 9:46 | 50
2020-07-08 | 9:46 | 50.001
2020-07-08 | 9:46 | 50.002
2020-07-08 | 9:47 | 50.003
2020-07-08 | 9:47 | 50.005
2020-07-08 | 9:47 | 50.007
2020-07-08 | 9:47 | 50.008
2020-07-08 | 9:47 | 50.012
2020-07-08 | 9:47 | 50.015
2020-07-08 | 9:47 | 50.017
2020-07-08 | 9:47 | 50.019
2020-07-08 | 9:47 | 50.021
2020-07-08 | 9:47 | 50.021
2020-07-08 | 9:47 | 50.022
2020-07-08 | 9:47 | 50.023
2020-07-08 | 9:47 | 50.025
2020-07-08 | 9:47 | 50.024
2020-07-08 | 9:47 | 50.025
2020-07-08 | 9:47 | 50.026
2020-07-08 | 9:47 | 50.027
2020-07-08 | 9:47 | 50.029
2020-07-08 | 9:47 | 50.031
2020-07-08 | 9:47 | 50.038
2020-07-08 | 9:47 | 50.082
2020-07-08 | 9:47 | 50.14
2020-07-08 | 9:47 | 50.195
2020-07-08 | 9:47 | 50.237
2020-07-08 | 9:47 | 50.267
2020-07-08 | 9:47 | 50.286
2020-07-08 | 9:47 | 50.299
2020-07-08 | 9:47 | 50.305
2020-07-08 | 9:47 | 50.306
2020-07-08 | 9:47 | 50.305
2020-07-08 | 9:47 | 50.302
2020-07-08 | 9:47 | 50.301
2020-07-08 | 9:47 | 50.299
2020-07-08 | 9:47 | 50.296
2020-07-08 | 9:47 | 50.294
2020-07-08 | 9:47 | 50.294
2020-07-08 | 9:47 | 50.293
2020-07-08 | 9:47 | 50.291
2020-07-08 | 9:47 | 50.29
2020-07-08 | 9:47 | 50.289
2020-07-08 | 9:47 | 50.287
2020-07-08 | 9:47 | 50.287
2020-07-08 | 9:47 | 50.288
2020-07-08 | 9:47 | 50.287
2020-07-08 | 9:47 | 50.286
2020-07-08 | 9:47 | 50.285
2020-07-08 | 9:47 | 50.285
2020-07-08 | 9:47 | 50.284
2020-07-08 | 9:47 | 50.283
2020-07-08 | 9:47 | 50.281
2020-07-08 | 9:47 | 50.278
2020-07-08 | 9:47 | 50.276
2020-07-08 | 9:47 | 50.277
2020-07-08 | 9:47 | 50.277
2020-07-08 | 9:47 | 50.281
2020-07-08 | 9:47 | 50.284
2020-07-08 | 9:47 | 50.288
2020-07-08 | 9:47 | 50.289
2020-07-08 | 9:47 | 50.29
2020-07-08 | 9:48 | 50.291
2020-07-08 | 9:48 | 50.292
2020-07-08 | 9:48 | 50.294
2020-07-08 | 9:48 | 50.298
2020-07-08 | 9:48 | 50.301
2020-07-08 | 9:48 | 50.303
2020-07-08 | 9:48 | 50.305
2020-07-08 | 9:48 | 50.307
2020-07-08 | 9:48 | 50.309
2020-07-08 | 9:48 | 50.312
2020-07-08 | 9:48 | 50.315
2020-07-08 | 9:48 | 50.318
2020-07-08 | 9:48 | 50.318
2020-07-08 | 9:48 | 50.32
2020-07-08 | 9:48 | 50.32
2020-07-08 | 9:48 | 50.32
2020-07-08 | 9:48 | 50.318
2020-07-08 | 9:48 | 50.314
2020-07-08 | 9:48 | 50.311
2020-07-08 | 9:48 | 50.307
2020-07-08 | 9:48 | 50.304
2020-07-08 | 9:48 | 50.307
2020-07-08 | 9:48 | 50.309
2020-07-08 | 9:48 | 50.311
2020-07-08 | 9:48 | 50.312
2020-07-08 | 9:48 | 50.312
2020-07-08 | 9:48 | 50.311
2020-07-08 | 9:48 | 50.31
2020-07-08 | 9:48 | 50.308
2020-07-08 | 9:48 | 50.306
2020-07-08 | 9:48 | 50.3
2020-07-08 | 9:48 | 50.296
2020-07-08 | 9:48 | 50.293
2020-07-08 | 9:48 | 50.29
2020-07-08 | 9:48 | 50.287
2020-07-08 | 9:48 | 50.286
2020-07-08 | 9:48 | 50.287
2020-07-08 | 9:48 | 50.29
2020-07-08 | 9:48 | 50.293
2020-07-08 | 9:48 | 50.295
2020-07-08 | 9:48 | 50.295
2020-07-08 | 9:48 | 50.296
2020-07-08 | 9:48 | 50.296
2020-07-08 | 9:48 | 50.295
2020-07-08 | 9:48 | 50.292
2020-07-08 | 9:48 | 50.289
2020-07-08 | 9:48 | 50.285
2020-07-08 | 9:48 | 50.282
2020-07-08 | 9:48 | 50.278
2020-07-08 | 9:48 | 50.278
2020-07-08 | 9:48 | 50.274
2020-07-08 | 9:48 | 50.275
2020-07-08 | 9:48 | 50.273
2020-07-08 | 9:48 | 50.274
2020-07-08 | 9:48 | 50.278
2020-07-08 | 9:48 | 50.279
2020-07-08 | 9:48 | 50.279
2020-07-08 | 9:48 | 50.28
2020-07-08 | 9:48 | 50.283
2020-07-08 | 9:48 | 50.286
2020-07-08 | 9:48 | 50.286
2020-07-08 | 9:49 | 50.289
2020-07-08 | 9:49 | 50.288
2020-07-08 | 9:49 | 50.285
2020-07-08 | 9:49 | 50.278
2020-07-08 | 9:49 | 50.271
2020-07-08 | 9:49 | 50.259
2020-07-08 | 9:49 | 50.248
2020-07-08 | 9:49 | 50.239
2020-07-08 | 9:49 | 50.232
2020-07-08 | 9:49 | 50.228
2020-07-08 | 9:49 | 50.227
2020-07-08 | 9:49 | 50.226
2020-07-08 | 9:49 | 50.224
2020-07-08 | 9:49 | 50.223
2020-07-08 | 9:49 | 50.22
2020-07-08 | 9:49 | 50.219
2020-07-08 | 9:49 | 50.218
2020-07-08 | 9:49 | 50.216
2020-07-08 | 9:49 | 50.212
2020-07-08 | 9:49 | 50.207
2020-07-08 | 9:49 | 50.203
2020-07-08 | 9:49 | 50.198
2020-07-08 | 9:49 | 50.195
2020-07-08 | 9:49 | 50.195
2020-07-08 | 9:49 | 50.196
2020-07-08 | 9:49 | 50.198
2020-07-08 | 9:49 | 50.2
2020-07-08 | 9:49 | 50.202
2020-07-08 | 9:49 | 50.205
2020-07-08 | 9:49 | 50.213
2020-07-08 | 9:49 | 50.222
2020-07-08 | 9:49 | 50.228
2020-07-08 | 9:49 | 50.23
2020-07-08 | 9:49 | 50.235
2020-07-08 | 9:49 | 50.235
2020-07-08 | 9:49 | 50.236
2020-07-08 | 9:49 | 50.235
2020-07-08 | 9:49 | 50.235
2020-07-08 | 9:49 | 50.235
2020-07-08 | 9:49 | 50.234
2020-07-08 | 9:49 | 50.234
2020-07-08 | 9:49 | 50.233
2020-07-08 | 9:49 | 50.231
2020-07-08 | 9:49 | 50.228
2020-07-08 | 9:49 | 50.225
2020-07-08 | 9:49 | 50.221
2020-07-08 | 9:49 | 50.22
2020-07-08 | 9:49 | 50.221
2020-07-08 | 9:49 | 50.22
2020-07-08 | 9:49 | 50.221
2020-07-08 | 9:49 | 50.221
2020-07-08 | 9:49 | 50.224
2020-07-08 | 9:49 | 50.225
2020-07-08 | 9:49 | 50.227
2020-07-08 | 9:49 | 50.229
2020-07-08 | 9:49 | 50.23
2020-07-08 | 9:49 | 50.23
2020-07-08 | 9:49 | 50.232
2020-07-08 | 9:49 | 50.232
2020-07-08 | 9:50 | 50.231
2020-07-08 | 9:50 | 50.229
2020-07-08 | 9:50 | 50.23
2020-07-08 | 9:50 | 50.23
2020-07-08 | 9:50 | 50.23
2020-07-08 | 9:50 | 50.233
2020-07-08 | 9:50 | 50.232
2020-07-08 | 9:50 | 50.234
2020-07-08 | 9:50 | 50.233
2020-07-08 | 9:50 | 50.234
2020-07-08 | 9:50 | 50.232
2020-07-08 | 9:50 | 50.232
2020-07-08 | 9:50 | 50.227
2020-07-08 | 9:50 | 50.227
2020-07-08 | 9:50 | 50.225
2020-07-08 | 9:50 | 50.226
2020-07-08 | 9:50 | 50.225
2020-07-08 | 9:50 | 50.226
2020-07-08 | 9:50 | 50.227
2020-07-08 | 9:50 | 50.228
2020-07-08 | 9:50 | 50.228
2020-07-08 | 9:50 | 50.229
2020-07-08 | 9:50 | 50.231
2020-07-08 | 9:50 | 50.233
2020-07-08 | 9:50 | 50.232
2020-07-08 | 9:50 | 50.232
2020-07-08 | 9:50 | 50.233
2020-07-08 | 9:50 | 50.231
2020-07-08 | 9:50 | 50.228
2020-07-08 | 9:50 | 50.228
2020-07-08 | 9:50 | 50.224
2020-07-08 | 9:50 | 50.218
2020-07-08 | 9:50 | 50.213
2020-07-08 | 9:50 | 50.213
2020-07-08 | 9:50 | 50.208
2020-07-08 | 9:50 | 50.207
2020-07-08 | 9:50 | 50.207
2020-07-08 | 9:50 | 50.205
2020-07-08 | 9:50 | 50.205
2020-07-08 | 9:50 | 50.203
2020-07-08 | 9:50 | 50.202
2020-07-08 | 9:50 | 50.202
2020-07-08 | 9:50 | 50.199
2020-07-08 | 9:50 | 50.199
2020-07-08 | 9:50 | 50.201
2020-07-08 | 9:50 | 50.202
2020-07-08 | 9:50 | 50.204
2020-07-08 | 9:50 | 50.208
2020-07-08 | 9:50 | 50.209
2020-07-08 | 9:50 | 50.215
2020-07-08 | 9:50 | 50.216
2020-07-08 | 9:50 | 50.22
2020-07-08 | 9:50 | 50.22
2020-07-08 | 9:50 | 50.223
2020-07-08 | 9:50 | 50.224
2020-07-08 | 9:50 | 50.224
2020-07-08 | 9:50 | 50.224
2020-07-08 | 9:50 | 50.222
2020-07-08 | 9:50 | 50.221
2020-07-08 | 9:50 | 50.22
2020-07-08 | 9:50 | 50.217
2020-07-08 | 9:51 | 50.216
2020-07-08 | 9:51 | 50.214
2020-07-08 | 9:51 | 50.212
2020-07-08 | 9:51 | 50.209
2020-07-08 | 9:51 | 50.204
2020-07-08 | 9:51 | 50.198
2020-07-08 | 9:51 | 50.195
2020-07-08 | 9:51 | 50.191
2020-07-08 | 9:51 | 50.188
2020-07-08 | 9:51 | 50.186
2020-07-08 | 9:51 | 50.185
2020-07-08 | 9:51 | 50.184
2020-07-08 | 9:51 | 50.183
2020-07-08 | 9:51 | 50.184
2020-07-08 | 9:51 | 50.183
2020-07-08 | 9:51 | 50.184
2020-07-08 | 9:51 | 50.185
2020-07-08 | 9:51 | 50.184
2020-07-08 | 9:51 | 50.185
2020-07-08 | 9:51 | 50.182
2020-07-08 | 9:51 | 50.182
2020-07-08 | 9:51 | 50.183
2020-07-08 | 9:51 | 50.183
2020-07-08 | 9:51 | 50.182
2020-07-08 | 9:51 | 50.181
2020-07-08 | 9:51 | 50.179
2020-07-08 | 9:51 | 50.178
2020-07-08 | 9:51 | 50.177
2020-07-08 | 9:51 | 50.175
2020-07-08 | 9:51 | 50.174
2020-07-08 | 9:51 | 50.173
2020-07-08 | 9:51 | 50.171
2020-07-08 | 9:51 | 50.17
2020-07-08 | 9:51 | 50.169
2020-07-08 | 9:51 | 50.168
2020-07-08 | 9:51 | 50.168
2020-07-08 | 9:51 | 50.165
2020-07-08 | 9:51 | 50.164
2020-07-08 | 9:51 | 50.16
2020-07-08 | 9:51 | 50.155
2020-07-08 | 9:51 | 50.153
2020-07-08 | 9:51 | 50.147
2020-07-08 | 9:51 | 50.145
2020-07-08 | 9:51 | 50.144
2020-07-08 | 9:51 | 50.142
2020-07-08 | 9:51 | 50.144
2020-07-08 | 9:51 | 50.142
2020-07-08 | 9:51 | 50.142
2020-07-08 | 9:51 | 50.143
2020-07-08 | 9:51 | 50.144
2020-07-08 | 9:51 | 50.144
2020-07-08 | 9:51 | 50.143
2020-07-08 | 9:51 | 50.142
2020-07-08 | 9:51 | 50.139
2020-07-08 | 9:51 | 50.138
2020-07-08 | 9:51 | 50.133
2020-07-08 | 9:51 | 50.13
2020-07-08 | 9:51 | 50.128
2020-07-08 | 9:51 | 50.13
2020-07-08 | 9:52 | 50.13
2020-07-08 | 9:52 | 50.132
2020-07-08 | 9:52 | 50.132
2020-07-08 | 9:52 | 50.133
2020-07-08 | 9:52 | 50.133
2020-07-08 | 9:52 | 50.133
2020-07-08 | 9:52 | 50.133
2020-07-08 | 9:52 | 50.13
2020-07-08 | 9:52 | 50.131
2020-07-08 | 9:52 | 50.132
2020-07-08 | 9:52 | 50.132
2020-07-08 | 9:52 | 50.132
2020-07-08 | 9:52 | 50.132
2020-07-08 | 9:52 | 50.13
2020-07-08 | 9:52 | 50.129
2020-07-08 | 9:52 | 50.126
2020-07-08 | 9:52 | 50.123
2020-07-08 | 9:52 | 50.124
2020-07-08 | 9:52 | 50.124
2020-07-08 | 9:52 | 50.126
2020-07-08 | 9:52 | 50.127
2020-07-08 | 9:52 | 50.126
2020-07-08 | 9:52 | 50.126
2020-07-08 | 9:52 | 50.124
2020-07-08 | 9:52 | 50.125
2020-07-08 | 9:52 | 50.125
2020-07-08 | 9:52 | 50.124
2020-07-08 | 9:52 | 50.125
2020-07-08 | 9:52 | 50.124
2020-07-08 | 9:52 | 50.123
2020-07-08 | 9:52 | 50.121
2020-07-08 | 9:52 | 50.121
2020-07-08 | 9:52 | 50.12
2020-07-08 | 9:52 | 50.119
2020-07-08 | 9:52 | 50.116
2020-07-08 | 9:52 | 50.112
2020-07-08 | 9:52 | 50.109
2020-07-08 | 9:52 | 50.103
2020-07-08 | 9:52 | 50.099
2020-07-08 | 9:52 | 50.094
2020-07-08 | 9:52 | 50.094
2020-07-08 | 9:52 | 50.094
2020-07-08 | 9:52 | 50.094
2020-07-08 | 9:52 | 50.097
2020-07-08 | 9:52 | 50.1
2020-07-08 | 9:52 | 50.1
2020-07-08 | 9:52 | 50.1
2020-07-08 | 9:52 | 50.1
2020-07-08 | 9:52 | 50.099
2020-07-08 | 9:52 | 50.101
2020-07-08 | 9:52 | 50.1
2020-07-08 | 9:52 | 50.098
2020-07-08 | 9:52 | 50.096
2020-07-08 | 9:52 | 50.096
2020-07-08 | 9:52 | 50.095
2020-07-08 | 9:52 | 50.092
2020-07-08 | 9:52 | 50.091
2020-07-08 | 9:52 | 50.092
2020-07-08 | 9:52 | 50.093
2020-07-08 | 9:52 | 50.093
2020-07-08 | 9:52 | 50.095
2020-07-08 | 9:53 | 50.098
2020-07-08 | 9:53 | 50.099
2020-07-08 | 9:53 | 50.104
2020-07-08 | 9:53 | 50.105
2020-07-08 | 9:53 | 50.107
2020-07-08 | 9:53 | 50.107
2020-07-08 | 9:53 | 50.108
2020-07-08 | 9:53 | 50.107
2020-07-08 | 9:53 | 50.105
2020-07-08 | 9:53 | 50.104
2020-07-08 | 9:53 | 50.103
2020-07-08 | 9:53 | 50.104
2020-07-08 | 9:53 | 50.104
2020-07-08 | 9:53 | 50.104
2020-07-08 | 9:53 | 50.106
2020-07-08 | 9:53 | 50.105
2020-07-08 | 9:53 | 50.105
2020-07-08 | 9:53 | 50.103
2020-07-08 | 9:53 | 50.105
2020-07-08 | 9:53 | 50.104
2020-07-08 | 9:53 | 50.102
2020-07-08 | 9:53 | 50.101
2020-07-08 | 9:53 | 50.1
2020-07-08 | 9:53 | 50.096
2020-07-08 | 9:53 | 50.094
2020-07-08 | 9:53 | 50.093
2020-07-08 | 9:53 | 50.094
2020-07-08 | 9:53 | 50.094
2020-07-08 | 9:53 | 50.094
2020-07-08 | 9:53 | 50.092
2020-07-08 | 9:53 | 50.09
2020-07-08 | 9:53 | 50.09
2020-07-08 | 9:53 | 50.089
2020-07-08 | 9:53 | 50.088
2020-07-08 | 9:53 | 50.088
2020-07-08 | 9:53 | 50.086
2020-07-08 | 9:53 | 50.085
2020-07-08 | 9:53 | 50.087
2020-07-08 | 9:53 | 50.089
2020-07-08 | 9:53 | 50.089
2020-07-08 | 9:53 | 50.089
2020-07-08 | 9:53 | 50.088
2020-07-08 | 9:53 | 50.087
2020-07-08 | 9:53 | 50.086
2020-07-08 | 9:53 | 50.082
2020-07-08 | 9:53 | 50.081
2020-07-08 | 9:53 | 50.079
2020-07-08 | 9:53 | 50.08
2020-07-08 | 9:53 | 50.08
2020-07-08 | 9:53 | 50.079
2020-07-08 | 9:53 | 50.079
2020-07-08 | 9:53 | 50.079
2020-07-08 | 9:53 | 50.077
2020-07-08 | 9:53 | 50.076
2020-07-08 | 9:53 | 50.074
2020-07-08 | 9:53 | 50.074
2020-07-08 | 9:53 | 50.069
2020-07-08 | 9:53 | 50.07
2020-07-08 | 9:53 | 50.07
2020-07-08 | 9:54 | 50.07
2020-07-08 | 9:54 | 50.069
2020-07-08 | 9:54 | 50.068
2020-07-08 | 9:54 | 50.066
2020-07-08 | 9:54 | 50.065
2020-07-08 | 9:54 | 50.065
2020-07-08 | 9:54 | 50.063
2020-07-08 | 9:54 | 50.062
2020-07-08 | 9:54 | 50.063
2020-07-08 | 9:54 | 50.065
2020-07-08 | 9:54 | 50.064
2020-07-08 | 9:54 | 50.068
2020-07-08 | 9:54 | 50.073
2020-07-08 | 9:54 | 50.075
2020-07-08 | 9:54 | 50.077
2020-07-08 | 9:54 | 50.078
2020-07-08 | 9:54 | 50.078
2020-07-08 | 9:54 | 50.077
2020-07-08 | 9:54 | 50.079
2020-07-08 | 9:54 | 50.079
2020-07-08 | 9:54 | 50.079
2020-07-08 | 9:54 | 50.077
2020-07-08 | 9:54 | 50.074
2020-07-08 | 9:54 | 50.072
2020-07-08 | 9:54 | 50.069
2020-07-08 | 9:54 | 50.069
2020-07-08 | 9:54 | 50.068
2020-07-08 | 9:54 | 50.068
2020-07-08 | 9:54 | 50.069
2020-07-08 | 9:54 | 50.071
2020-07-08 | 9:54 | 50.074
2020-07-08 | 9:54 | 50.076
2020-07-08 | 9:54 | 50.079
2020-07-08 | 9:54 | 50.082
2020-07-08 | 9:54 | 50.083
2020-07-08 | 9:54 | 50.084
2020-07-08 | 9:54 | 50.084
2020-07-08 | 9:54 | 50.084
2020-07-08 | 9:54 | 50.084
2020-07-08 | 9:54 | 50.086
2020-07-08 | 9:54 | 50.086
2020-07-08 | 9:54 | 50.088
2020-07-08 | 9:54 | 50.089
2020-07-08 | 9:54 | 50.091
2020-07-08 | 9:54 | 50.092
2020-07-08 | 9:54 | 50.09
2020-07-08 | 9:54 | 50.088
2020-07-08 | 9:54 | 50.083
2020-07-08 | 9:54 | 50.083
2020-07-08 | 9:54 | 50.081
2020-07-08 | 9:54 | 50.077
2020-07-08 | 9:54 | 50.074
2020-07-08 | 9:54 | 50.073
2020-07-08 | 9:54 | 50.072
2020-07-08 | 9:54 | 50.074
2020-07-08 | 9:54 | 50.073
2020-07-08 | 9:54 | 50.075
2020-07-08 | 9:54 | 50.076
2020-07-08 | 9:54 | 50.075
2020-07-08 | 9:54 | 50.075
2020-07-08 | 9:54 | 50.076
2020-07-08 | 9:55 | 50.078
2020-07-08 | 9:55 | 50.078
2020-07-08 | 9:55 | 50.077
2020-07-08 | 9:55 | 50.078
2020-07-08 | 9:55 | 50.077
2020-07-08 | 9:55 | 50.074
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.071
2020-07-08 | 9:55 | 50.07
2020-07-08 | 9:55 | 50.068
2020-07-08 | 9:55 | 50.067
2020-07-08 | 9:55 | 50.065
2020-07-08 | 9:55 | 50.066
2020-07-08 | 9:55 | 50.066
2020-07-08 | 9:55 | 50.067
2020-07-08 | 9:55 | 50.069
2020-07-08 | 9:55 | 50.07
2020-07-08 | 9:55 | 50.071
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.073
2020-07-08 | 9:55 | 50.073
2020-07-08 | 9:55 | 50.074
2020-07-08 | 9:55 | 50.077
2020-07-08 | 9:55 | 50.081
2020-07-08 | 9:55 | 50.083
2020-07-08 | 9:55 | 50.083
2020-07-08 | 9:55 | 50.08
2020-07-08 | 9:55 | 50.078
2020-07-08 | 9:55 | 50.076
2020-07-08 | 9:55 | 50.076
2020-07-08 | 9:55 | 50.072
2020-07-08 | 9:55 | 50.07
2020-07-08 | 9:55 | 50.068
2020-07-08 | 9:55 | 50.064
2020-07-08 | 9:55 | 50.061
2020-07-08 | 9:55 | 50.058
2020-07-08 | 9:55 | 50.059
2020-07-08 | 9:55 | 50.059
2020-07-08 | 9:55 | 50.061
2020-07-08 | 9:55 | 50.062
2020-07-08 | 9:55 | 50.064
2020-07-08 | 9:55 | 50.065
2020-07-08 | 9:55 | 50.067
2020-07-08 | 9:55 | 50.068
2020-07-08 | 9:55 | 50.068
2020-07-08 | 9:55 | 50.067
2020-07-08 | 9:55 | 50.064
2020-07-08 | 9:55 | 50.063
2020-07-08 | 9:55 | 50.064
2020-07-08 | 9:55 | 50.065
2020-07-08 | 9:55 | 50.066
2020-07-08 | 9:55 | 50.068
2020-07-08 | 9:55 | 50.069
2020-07-08 | 9:55 | 50.07
2020-07-08 | 9:55 | 50.071
2020-07-08 | 9:56 | 50.073
2020-07-08 | 9:56 | 50.074
2020-07-08 | 9:56 | 50.073
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.069
2020-07-08 | 9:56 | 50.068
2020-07-08 | 9:56 | 50.068
2020-07-08 | 9:56 | 50.069
2020-07-08 | 9:56 | 50.069
2020-07-08 | 9:56 | 50.067
2020-07-08 | 9:56 | 50.07
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.073
2020-07-08 | 9:56 | 50.074
2020-07-08 | 9:56 | 50.072
2020-07-08 | 9:56 | 50.07
2020-07-08 | 9:56 | 50.067
2020-07-08 | 9:56 | 50.065
2020-07-08 | 9:56 | 50.062
2020-07-08 | 9:56 | 50.064
2020-07-08 | 9:56 | 50.065
2020-07-08 | 9:56 | 50.064
2020-07-08 | 9:56 | 50.066
2020-07-08 | 9:56 | 50.067
2020-07-08 | 9:56 | 50.066
2020-07-08 | 9:56 | 50.068
2020-07-08 | 9:56 | 50.069
2020-07-08 | 9:56 | 50.069
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.072
2020-07-08 | 9:56 | 50.072
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.07
2020-07-08 | 9:56 | 50.067
2020-07-08 | 9:56 | 50.066
2020-07-08 | 9:56 | 50.065
2020-07-08 | 9:56 | 50.064
2020-07-08 | 9:56 | 50.064
2020-07-08 | 9:56 | 50.065
2020-07-08 | 9:56 | 50.065
2020-07-08 | 9:56 | 50.066
2020-07-08 | 9:56 | 50.068
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.072
2020-07-08 | 9:56 | 50.072
2020-07-08 | 9:56 | 50.074
2020-07-08 | 9:56 | 50.073
2020-07-08 | 9:56 | 50.073
2020-07-08 | 9:56 | 50.073
2020-07-08 | 9:56 | 50.071
2020-07-08 | 9:56 | 50.07
2020-07-08 | 9:56 | 50.067
2020-07-08 | 9:56 | 50.066
2020-07-08 | 9:56 | 50.064
2020-07-08 | 9:56 | 50.061
2020-07-08 | 9:57 | 50.06
2020-07-08 | 9:57 | 50.059
2020-07-08 | 9:57 | 50.056
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.054
2020-07-08 | 9:57 | 50.053
2020-07-08 | 9:57 | 50.053
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.052
2020-07-08 | 9:57 | 50.051
2020-07-08 | 9:57 | 50.051
2020-07-08 | 9:57 | 50.052
2020-07-08 | 9:57 | 50.054
2020-07-08 | 9:57 | 50.056
2020-07-08 | 9:57 | 50.058
2020-07-08 | 9:57 | 50.062
2020-07-08 | 9:57 | 50.063
2020-07-08 | 9:57 | 50.063
2020-07-08 | 9:57 | 50.063
2020-07-08 | 9:57 | 50.063
2020-07-08 | 9:57 | 50.062
2020-07-08 | 9:57 | 50.061
2020-07-08 | 9:57 | 50.059
2020-07-08 | 9:57 | 50.056
2020-07-08 | 9:57 | 50.052
2020-07-08 | 9:57 | 50.05
2020-07-08 | 9:57 | 50.047
2020-07-08 | 9:57 | 50.047
2020-07-08 | 9:57 | 50.043
2020-07-08 | 9:57 | 50.044
2020-07-08 | 9:57 | 50.044
2020-07-08 | 9:57 | 50.043
2020-07-08 | 9:57 | 50.043
2020-07-08 | 9:57 | 50.042
2020-07-08 | 9:57 | 50.041
2020-07-08 | 9:57 | 50.041
2020-07-08 | 9:57 | 50.041
2020-07-08 | 9:57 | 50.042
2020-07-08 | 9:57 | 50.045
2020-07-08 | 9:57 | 50.049
2020-07-08 | 9:57 | 50.052
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.056
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.055
2020-07-08 | 9:57 | 50.057
2020-07-08 | 9:57 | 50.058
2020-07-08 | 9:57 | 50.06
2020-07-08 | 9:57 | 50.061
2020-07-08 | 9:57 | 50.063
2020-07-08 | 9:57 | 50.065
2020-07-08 | 9:57 | 50.066
2020-07-08 | 9:57 | 50.068
2020-07-08 | 9:57 | 50.068
2020-07-08 | 9:57 | 50.07
2020-07-08 | 9:57 | 50.07
2020-07-08 | 9:57 | 50.069
2020-07-08 | 9:58 | 50.07
2020-07-08 | 9:58 | 50.068
2020-07-08 | 9:58 | 50.068
2020-07-08 | 9:58 | 50.067
2020-07-08 | 9:58 | 50.066
2020-07-08 | 9:58 | 50.064
2020-07-08 | 9:58 | 50.059
2020-07-08 | 9:58 | 50.056
2020-07-08 | 9:58 | 50.052
2020-07-08 | 9:58 | 50.051
2020-07-08 | 9:58 | 50.051
2020-07-08 | 9:58 | 50.054
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.059
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.065
2020-07-08 | 9:58 | 50.069
2020-07-08 | 9:58 | 50.071
2020-07-08 | 9:58 | 50.073
2020-07-08 | 9:58 | 50.074
2020-07-08 | 9:58 | 50.074
2020-07-08 | 9:58 | 50.074
2020-07-08 | 9:58 | 50.073
2020-07-08 | 9:58 | 50.074
2020-07-08 | 9:58 | 50.075
2020-07-08 | 9:58 | 50.077
2020-07-08 | 9:58 | 50.079
2020-07-08 | 9:58 | 50.078
2020-07-08 | 9:58 | 50.078
2020-07-08 | 9:58 | 50.075
2020-07-08 | 9:58 | 50.071
2020-07-08 | 9:58 | 50.069
2020-07-08 | 9:58 | 50.067
2020-07-08 | 9:58 | 50.065
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.061
2020-07-08 | 9:58 | 50.059
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.058
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.058
2020-07-08 | 9:58 | 50.058
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.058
2020-07-08 | 9:58 | 50.059
2020-07-08 | 9:58 | 50.061
2020-07-08 | 9:58 | 50.061
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.062
2020-07-08 | 9:58 | 50.059
2020-07-08 | 9:58 | 50.057
2020-07-08 | 9:58 | 50.056
2020-07-08 | 9:58 | 50.056
2020-07-08 | 9:58 | 50.054
2020-07-08 | 9:58 | 50.053
2020-07-08 | 9:58 | 50.051
2020-07-08 | 9:59 | 50.051
2020-07-08 | 9:59 | 50.051
2020-07-08 | 9:59 | 50.051
2020-07-08 | 9:59 | 50.048
2020-07-08 | 9:59 | 50.05
2020-07-08 | 9:59 | 50.047
2020-07-08 | 9:59 | 50.046
2020-07-08 | 9:59 | 50.042
2020-07-08 | 9:59 | 50.041
2020-07-08 | 9:59 | 50.039
2020-07-08 | 9:59 | 50.039
2020-07-08 | 9:59 | 50.037
2020-07-08 | 9:59 | 50.037
2020-07-08 | 9:59 | 50.037
2020-07-08 | 9:59 | 50.039
2020-07-08 | 9:59 | 50.04
2020-07-08 | 9:59 | 50.041
2020-07-08 | 9:59 | 50.042
2020-07-08 | 9:59 | 50.041
2020-07-08 | 9:59 | 50.041
2020-07-08 | 9:59 | 50.038
2020-07-08 | 9:59 | 50.036
2020-07-08 | 9:59 | 50.035
2020-07-08 | 9:59 | 50.034
2020-07-08 | 9:59 | 50.036
2020-07-08 | 9:59 | 50.039
2020-07-08 | 9:59 | 50.041
2020-07-08 | 9:59 | 50.045
2020-07-08 | 9:59 | 50.047
2020-07-08 | 9:59 | 50.048
2020-07-08 | 9:59 | 50.051
2020-07-08 | 9:59 | 50.05
2020-07-08 | 9:59 | 50.052
2020-07-08 | 9:59 | 50.053
2020-07-08 | 9:59 | 50.05
2020-07-08 | 9:59 | 50.051
2020-07-08 | 9:59 | 50.05
2020-07-08 | 9:59 | 50.049
2020-07-08 | 9:59 | 50.047
2020-07-08 | 9:59 | 50.045
2020-07-08 | 9:59 | 50.042
2020-07-08 | 9:59 | 50.037
2020-07-08 | 9:59 | 50.032
2020-07-08 | 9:59 | 50.028
2020-07-08 | 9:59 | 50.023
2020-07-08 | 9:59 | 50.018
2020-07-08 | 9:59 | 50.015
2020-07-08 | 9:59 | 50.012
2020-07-08 | 9:59 | 50.011
2020-07-08 | 9:59 | 50.012
2020-07-08 | 9:59 | 50.015
2020-07-08 | 9:59 | 50.017
2020-07-08 | 9:59 | 50.017
2020-07-08 | 9:59 | 50.017
2020-07-08 | 9:59 | 50.02
2020-07-08 | 9:59 | 50.022
2020-07-08 | 9:59 | 50.024
2020-07-08 | 9:59 | 50.025
2020-07-08 | 9:59 | 50.025
2020-07-08 | 10:00 | 50.025
2020-07-08 | 10:00 | 50.023
2020-07-08 | 10:00 | 50.022
2020-07-08 | 10:00 | 50.02
2020-07-08 | 10:00 | 50.019
2020-07-08 | 10:00 | 50.017
2020-07-08 | 10:00 | 50.015
2020-07-08 | 10:00 | 50.014
2020-07-08 | 10:00 | 50.016
2020-07-08 | 10:00 | 50.018
2020-07-08 | 10:00 | 50.02
2020-07-08 | 10:00 | 50.022
2020-07-08 | 10:00 | 50.024
2020-07-08 | 10:00 | 50.026
2020-07-08 | 10:00 | 50.029
2020-07-08 | 10:00 | 50.031
2020-07-08 | 10:00 | 50.032
2020-07-08 | 10:00 | 50.035
2020-07-08 | 10:00 | 50.036
2020-07-08 | 10:00 | 50.035
2020-07-08 | 10:00 | 50.033
2020-07-08 | 10:00 | 50.031
2020-07-08 | 10:00 | 50.027
2020-07-08 | 10:00 | 50.025
2020-07-08 | 10:00 | 50.025
2020-07-08 | 10:00 | 50.024
2020-07-08 | 10:00 | 50.024
2020-07-08 | 10:00 | 50.021
2020-07-08 | 10:00 | 50.02
2020-07-08 | 10:00 | 50.019
2020-07-08 | 10:00 | 50.018
2020-07-08 | 10:00 | 50.015
2020-07-08 | 10:00 | 50.014
2020-07-08 | 10:00 | 50.013
2020-07-08 | 10:00 | 50.011
2020-07-08 | 10:00 | 50.012
2020-07-08 | 10:00 | 50.009
2020-07-08 | 10:00 | 50.009
2020-07-08 | 10:00 | 50.008
2020-07-08 | 10:00 | 50.008
2020-07-08 | 10:00 | 50.007
2020-07-08 | 10:00 | 50.005
2020-07-08 | 10:00 | 50
2020-07-08 | 10:00 | 49.99
2020-07-08 | 10:00 | 49.974
2020-07-08 | 10:00 | 49.968
2020-07-08 | 10:00 | 49.961
2020-07-08 | 10:00 | 49.955
2020-07-08 | 10:00 | 49.95
2020-07-08 | 10:00 | 49.945
2020-07-08 | 10:00 | 49.94
2020-07-08 | 10:00 | 49.937
2020-07-08 | 10:00 | 49.935
2020-07-08 | 10:00 | 49.933
2020-07-08 | 10:00 | 49.931
2020-07-08 | 10:00 | 49.931
2020-07-08 | 10:00 | 49.931
2020-07-08 | 10:00 | 49.932
2020-07-08 | 10:00 | 49.934
2020-07-08 | 10:00 | 49.934
2020-07-08 | 10:00 | 49.936
2020-07-08 | 10:01 | 49.937
2020-07-08 | 10:01 | 49.938
2020-07-08 | 10:01 | 49.936
2020-07-08 | 10:01 | 49.934
2020-07-08 | 10:01 | 49.932
2020-07-08 | 10:01 | 49.932
2020-07-08 | 10:01 | 49.931
2020-07-08 | 10:01 | 49.93
2020-07-08 | 10:01 | 49.93
2020-07-08 | 10:01 | 49.932
2020-07-08 | 10:01 | 49.931
2020-07-08 | 10:01 | 49.934
2020-07-08 | 10:01 | 49.936
2020-07-08 | 10:01 | 49.937
2020-07-08 | 10:01 | 49.938
2020-07-08 | 10:01 | 49.94
2020-07-08 | 10:01 | 49.94
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.94
2020-07-08 | 10:01 | 49.938
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.939
2020-07-08 | 10:01 | 49.94
2020-07-08 | 10:01 | 49.943
2020-07-08 | 10:01 | 49.942

## Event 20200713-1
In UTC
Date | Time | Freq
2020-07-13 | 9:12 | 50.001
2020-07-13 | 9:12 | 50.001
2020-07-13 | 9:12 | 50
2020-07-13 | 9:12 | 49.998
2020-07-13 | 9:12 | 49.995
2020-07-13 | 9:12 | 49.994
2020-07-13 | 9:12 | 49.992
2020-07-13 | 9:12 | 49.991
2020-07-13 | 9:12 | 49.99
2020-07-13 | 9:12 | 49.989
2020-07-13 | 9:12 | 49.988
2020-07-13 | 9:12 | 49.984
2020-07-13 | 9:12 | 49.982
2020-07-13 | 9:12 | 49.98
2020-07-13 | 9:12 | 49.98
2020-07-13 | 9:12 | 49.981
2020-07-13 | 9:12 | 49.98
2020-07-13 | 9:12 | 49.98
2020-07-13 | 9:12 | 49.979
2020-07-13 | 9:12 | 49.979
2020-07-13 | 9:12 | 49.978
2020-07-13 | 9:12 | 49.978
2020-07-13 | 9:12 | 49.974
2020-07-13 | 9:12 | 49.972
2020-07-13 | 9:12 | 49.971
2020-07-13 | 9:12 | 49.973
2020-07-13 | 9:12 | 49.975
2020-07-13 | 9:12 | 49.977
2020-07-13 | 9:12 | 49.981
2020-07-13 | 9:12 | 49.983
2020-07-13 | 9:12 | 49.984
2020-07-13 | 9:13 | 49.985
2020-07-13 | 9:13 | 49.982
2020-07-13 | 9:13 | 49.978
2020-07-13 | 9:13 | 49.975
2020-07-13 | 9:13 | 49.972
2020-07-13 | 9:13 | 49.97
2020-07-13 | 9:13 | 49.969
2020-07-13 | 9:13 | 49.966
2020-07-13 | 9:13 | 49.964
2020-07-13 | 9:13 | 49.961
2020-07-13 | 9:13 | 49.96
2020-07-13 | 9:13 | 49.958
2020-07-13 | 9:13 | 49.96
2020-07-13 | 9:13 | 49.96
2020-07-13 | 9:13 | 49.961
2020-07-13 | 9:13 | 49.964
2020-07-13 | 9:13 | 49.966
2020-07-13 | 9:13 | 49.966
2020-07-13 | 9:13 | 49.97
2020-07-13 | 9:13 | 49.974
2020-07-13 | 9:13 | 49.975
2020-07-13 | 9:13 | 49.978
2020-07-13 | 9:13 | 49.98
2020-07-13 | 9:13 | 49.983
2020-07-13 | 9:13 | 49.984
2020-07-13 | 9:13 | 49.985
2020-07-13 | 9:13 | 49.984
2020-07-13 | 9:13 | 49.978
2020-07-13 | 9:13 | 49.961
2020-07-13 | 9:13 | 49.944
2020-07-13 | 9:13 | 49.931
2020-07-13 | 9:13 | 49.922
2020-07-13 | 9:13 | 49.919
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.915
2020-07-13 | 9:13 | 49.913
2020-07-13 | 9:13 | 49.912
2020-07-13 | 9:13 | 49.912
2020-07-13 | 9:13 | 49.914
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.918
2020-07-13 | 9:13 | 49.919
2020-07-13 | 9:13 | 49.92
2020-07-13 | 9:13 | 49.917
2020-07-13 | 9:13 | 49.915
2020-07-13 | 9:13 | 49.911
2020-07-13 | 9:13 | 49.907
2020-07-13 | 9:13 | 49.905
2020-07-13 | 9:13 | 49.902
2020-07-13 | 9:13 | 49.899
2020-07-13 | 9:13 | 49.897
2020-07-13 | 9:13 | 49.893
2020-07-13 | 9:13 | 49.891
2020-07-13 | 9:13 | 49.889
2020-07-13 | 9:13 | 49.886
2020-07-13 | 9:14 | 49.882
2020-07-13 | 9:14 | 49.876
2020-07-13 | 9:14 | 49.873
2020-07-13 | 9:14 | 49.869
2020-07-13 | 9:14 | 49.872
2020-07-13 | 9:14 | 49.874
2020-07-13 | 9:14 | 49.877
2020-07-13 | 9:14 | 49.878
2020-07-13 | 9:14 | 49.877
2020-07-13 | 9:14 | 49.876
2020-07-13 | 9:14 | 49.875
2020-07-13 | 9:14 | 49.872
2020-07-13 | 9:14 | 49.871
2020-07-13 | 9:14 | 49.865
2020-07-13 | 9:14 | 49.863
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.861
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.859
2020-07-13 | 9:14 | 49.861
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.859
2020-07-13 | 9:14 | 49.859
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.864
2020-07-13 | 9:14 | 49.866
2020-07-13 | 9:14 | 49.867
2020-07-13 | 9:14 | 49.869
2020-07-13 | 9:14 | 49.869
2020-07-13 | 9:14 | 49.869
2020-07-13 | 9:14 | 49.871
2020-07-13 | 9:14 | 49.868
2020-07-13 | 9:14 | 49.865
2020-07-13 | 9:14 | 49.863
2020-07-13 | 9:14 | 49.86
2020-07-13 | 9:14 | 49.861
2020-07-13 | 9:14 | 49.861
2020-07-13 | 9:14 | 49.858
2020-07-13 | 9:14 | 49.859
2020-07-13 | 9:14 | 49.858
2020-07-13 | 9:14 | 49.857
2020-07-13 | 9:14 | 49.853
2020-07-13 | 9:14 | 49.85
2020-07-13 | 9:14 | 49.845
2020-07-13 | 9:14 | 49.844
2020-07-13 | 9:14 | 49.842
2020-07-13 | 9:14 | 49.839
2020-07-13 | 9:14 | 49.834
2020-07-13 | 9:14 | 49.832
2020-07-13 | 9:14 | 49.828
2020-07-13 | 9:14 | 49.824
2020-07-13 | 9:14 | 49.821
2020-07-13 | 9:14 | 49.816
2020-07-13 | 9:14 | 49.814
2020-07-13 | 9:14 | 49.814
2020-07-13 | 9:14 | 49.81
2020-07-13 | 9:14 | 49.808
2020-07-13 | 9:14 | 49.809
2020-07-13 | 9:14 | 49.806
2020-07-13 | 9:15 | 49.804
2020-07-13 | 9:15 | 49.802
2020-07-13 | 9:15 | 49.802
2020-07-13 | 9:15 | 49.805
2020-07-13 | 9:15 | 49.81
2020-07-13 | 9:15 | 49.81
2020-07-13 | 9:15 | 49.816
2020-07-13 | 9:15 | 49.82
2020-07-13 | 9:15 | 49.821
2020-07-13 | 9:15 | 49.826
2020-07-13 | 9:15 | 49.83
2020-07-13 | 9:15 | 49.832
2020-07-13 | 9:15 | 49.833
2020-07-13 | 9:15 | 49.83
2020-07-13 | 9:15 | 49.827
2020-07-13 | 9:15 | 49.828
2020-07-13 | 9:15 | 49.824
2020-07-13 | 9:15 | 49.821
2020-07-13 | 9:15 | 49.819
2020-07-13 | 9:15 | 49.818
2020-07-13 | 9:15 | 49.817
2020-07-13 | 9:15 | 49.817
2020-07-13 | 9:15 | 49.815
2020-07-13 | 9:15 | 49.815
2020-07-13 | 9:15 | 49.812
2020-07-13 | 9:15 | 49.805
2020-07-13 | 9:15 | 49.804
2020-07-13 | 9:15 | 49.804
2020-07-13 | 9:15 | 49.803
2020-07-13 | 9:15 | 49.799
2020-07-13 | 9:15 | 49.797
2020-07-13 | 9:15 | 49.794
2020-07-13 | 9:15 | 49.795
2020-07-13 | 9:15 | 49.801
2020-07-13 | 9:15 | 49.806
2020-07-13 | 9:15 | 49.811
2020-07-13 | 9:15 | 49.822
2020-07-13 | 9:15 | 49.831
2020-07-13 | 9:15 | 49.842
2020-07-13 | 9:15 | 49.853
2020-07-13 | 9:15 | 49.861
2020-07-13 | 9:15 | 49.869
2020-07-13 | 9:15 | 49.875
2020-07-13 | 9:15 | 49.881
2020-07-13 | 9:15 | 49.885
2020-07-13 | 9:15 | 49.888
2020-07-13 | 9:15 | 49.891
2020-07-13 | 9:15 | 49.893
2020-07-13 | 9:15 | 49.895
2020-07-13 | 9:15 | 49.896
2020-07-13 | 9:15 | 49.899
2020-07-13 | 9:15 | 49.897
2020-07-13 | 9:15 | 49.897
2020-07-13 | 9:15 | 49.901
2020-07-13 | 9:15 | 49.901
2020-07-13 | 9:15 | 49.902
2020-07-13 | 9:15 | 49.901
2020-07-13 | 9:15 | 49.901
2020-07-13 | 9:15 | 49.9
2020-07-13 | 9:16 | 49.9
2020-07-13 | 9:16 | 49.9
2020-07-13 | 9:16 | 49.9
2020-07-13 | 9:16 | 49.901
2020-07-13 | 9:16 | 49.904
2020-07-13 | 9:16 | 49.904
2020-07-13 | 9:16 | 49.904
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.9
2020-07-13 | 9:16 | 49.899
2020-07-13 | 9:16 | 49.901
2020-07-13 | 9:16 | 49.906
2020-07-13 | 9:16 | 49.91
2020-07-13 | 9:16 | 49.912
2020-07-13 | 9:16 | 49.912
2020-07-13 | 9:16 | 49.915
2020-07-13 | 9:16 | 49.916
2020-07-13 | 9:16 | 49.915
2020-07-13 | 9:16 | 49.915
2020-07-13 | 9:16 | 49.914
2020-07-13 | 9:16 | 49.912
2020-07-13 | 9:16 | 49.911
2020-07-13 | 9:16 | 49.909
2020-07-13 | 9:16 | 49.907
2020-07-13 | 9:16 | 49.907
2020-07-13 | 9:16 | 49.906
2020-07-13 | 9:16 | 49.904
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.904
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.903
2020-07-13 | 9:16 | 49.904
2020-07-13 | 9:16 | 49.906
2020-07-13 | 9:16 | 49.905
2020-07-13 | 9:16 | 49.907
2020-07-13 | 9:16 | 49.909
2020-07-13 | 9:16 | 49.913
2020-07-13 | 9:16 | 49.916
2020-07-13 | 9:16 | 49.918
2020-07-13 | 9:16 | 49.923
2020-07-13 | 9:16 | 49.923
2020-07-13 | 9:16 | 49.925
2020-07-13 | 9:16 | 49.927
2020-07-13 | 9:16 | 49.929
2020-07-13 | 9:16 | 49.93
2020-07-13 | 9:16 | 49.93
2020-07-13 | 9:16 | 49.93
2020-07-13 | 9:16 | 49.929
2020-07-13 | 9:16 | 49.926
2020-07-13 | 9:16 | 49.926
2020-07-13 | 9:16 | 49.924
2020-07-13 | 9:16 | 49.927
2020-07-13 | 9:16 | 49.929
2020-07-13 | 9:16 | 49.931
2020-07-13 | 9:16 | 49.933
2020-07-13 | 9:17 | 49.934
2020-07-13 | 9:17 | 49.936
2020-07-13 | 9:17 | 49.935
2020-07-13 | 9:17 | 49.935
2020-07-13 | 9:17 | 49.934
2020-07-13 | 9:17 | 49.93
2020-07-13 | 9:17 | 49.927
2020-07-13 | 9:17 | 49.924
2020-07-13 | 9:17 | 49.922
2020-07-13 | 9:17 | 49.922
2020-07-13 | 9:17 | 49.922
2020-07-13 | 9:17 | 49.919
2020-07-13 | 9:17 | 49.92
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:17 | 49.915
2020-07-13 | 9:17 | 49.915
2020-07-13 | 9:17 | 49.914
2020-07-13 | 9:17 | 49.913
2020-07-13 | 9:17 | 49.913
2020-07-13 | 9:17 | 49.914
2020-07-13 | 9:17 | 49.912
2020-07-13 | 9:17 | 49.914
2020-07-13 | 9:17 | 49.912
2020-07-13 | 9:17 | 49.912
2020-07-13 | 9:17 | 49.911
2020-07-13 | 9:17 | 49.909
2020-07-13 | 9:17 | 49.909
2020-07-13 | 9:17 | 49.908
2020-07-13 | 9:17 | 49.908
2020-07-13 | 9:17 | 49.908
2020-07-13 | 9:17 | 49.91
2020-07-13 | 9:17 | 49.91
2020-07-13 | 9:17 | 49.912
2020-07-13 | 9:17 | 49.913
2020-07-13 | 9:17 | 49.914
2020-07-13 | 9:17 | 49.915
2020-07-13 | 9:17 | 49.915
2020-07-13 | 9:17 | 49.917
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:17 | 49.915
2020-07-13 | 9:17 | 49.913
2020-07-13 | 9:17 | 49.912
2020-07-13 | 9:17 | 49.911
2020-07-13 | 9:17 | 49.91
2020-07-13 | 9:17 | 49.909
2020-07-13 | 9:17 | 49.907
2020-07-13 | 9:17 | 49.91
2020-07-13 | 9:17 | 49.911
2020-07-13 | 9:17 | 49.912
2020-07-13 | 9:17 | 49.914
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:17 | 49.919
2020-07-13 | 9:17 | 49.919
2020-07-13 | 9:17 | 49.92
2020-07-13 | 9:17 | 49.919
2020-07-13 | 9:17 | 49.917
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:17 | 49.916
2020-07-13 | 9:18 | 49.916
2020-07-13 | 9:18 | 49.917
2020-07-13 | 9:18 | 49.917
2020-07-13 | 9:18 | 49.917
2020-07-13 | 9:18 | 49.917
2020-07-13 | 9:18 | 49.915
2020-07-13 | 9:18 | 49.914
2020-07-13 | 9:18 | 49.912
2020-07-13 | 9:18 | 49.91
2020-07-13 | 9:18 | 49.909
2020-07-13 | 9:18 | 49.906
2020-07-13 | 9:18 | 49.904
2020-07-13 | 9:18 | 49.902
2020-07-13 | 9:18 | 49.903
2020-07-13 | 9:18 | 49.904
2020-07-13 | 9:18 | 49.905
2020-07-13 | 9:18 | 49.907
2020-07-13 | 9:18 | 49.91
2020-07-13 | 9:18 | 49.911
2020-07-13 | 9:18 | 49.911
2020-07-13 | 9:18 | 49.909
2020-07-13 | 9:18 | 49.907
2020-07-13 | 9:18 | 49.904
2020-07-13 | 9:18 | 49.903
2020-07-13 | 9:18 | 49.9
2020-07-13 | 9:18 | 49.901
2020-07-13 | 9:18 | 49.902
2020-07-13 | 9:18 | 49.904
2020-07-13 | 9:18 | 49.904
2020-07-13 | 9:18 | 49.905
2020-07-13 | 9:18 | 49.905
2020-07-13 | 9:18 | 49.906
2020-07-13 | 9:18 | 49.906
2020-07-13 | 9:18 | 49.906
2020-07-13 | 9:18 | 49.905
2020-07-13 | 9:18 | 49.905
2020-07-13 | 9:18 | 49.904
2020-07-13 | 9:18 | 49.906
2020-07-13 | 9:18 | 49.909
2020-07-13 | 9:18 | 49.912
2020-07-13 | 9:18 | 49.912
2020-07-13 | 9:18 | 49.914
2020-07-13 | 9:18 | 49.915
2020-07-13 | 9:18 | 49.916
2020-07-13 | 9:18 | 49.918
2020-07-13 | 9:18 | 49.92
2020-07-13 | 9:18 | 49.921
2020-07-13 | 9:18 | 49.922
2020-07-13 | 9:18 | 49.923
2020-07-13 | 9:18 | 49.925
2020-07-13 | 9:18 | 49.927
2020-07-13 | 9:18 | 49.93
2020-07-13 | 9:18 | 49.934
2020-07-13 | 9:18 | 49.938
2020-07-13 | 9:18 | 49.942
2020-07-13 | 9:18 | 49.945
2020-07-13 | 9:18 | 49.946
2020-07-13 | 9:18 | 49.948
2020-07-13 | 9:18 | 49.947
2020-07-13 | 9:18 | 49.947
2020-07-13 | 9:19 | 49.945
2020-07-13 | 9:19 | 49.943
2020-07-13 | 9:19 | 49.938
2020-07-13 | 9:19 | 49.935
2020-07-13 | 9:19 | 49.931
2020-07-13 | 9:19 | 49.931
2020-07-13 | 9:19 | 49.933
2020-07-13 | 9:19 | 49.934
2020-07-13 | 9:19 | 49.937
2020-07-13 | 9:19 | 49.941
2020-07-13 | 9:19 | 49.945
2020-07-13 | 9:19 | 49.945
2020-07-13 | 9:19 | 49.945
2020-07-13 | 9:19 | 49.947
2020-07-13 | 9:19 | 49.948
2020-07-13 | 9:19 | 49.948
2020-07-13 | 9:19 | 49.95
2020-07-13 | 9:19 | 49.949
2020-07-13 | 9:19 | 49.948
2020-07-13 | 9:19 | 49.946
2020-07-13 | 9:19 | 49.946
2020-07-13 | 9:19 | 49.944
2020-07-13 | 9:19 | 49.942
2020-07-13 | 9:19 | 49.942
2020-07-13 | 9:19 | 49.942
2020-07-13 | 9:19 | 49.943
2020-07-13 | 9:19 | 49.942
2020-07-13 | 9:19 | 49.942
2020-07-13 | 9:19 | 49.941
2020-07-13 | 9:19 | 49.939
2020-07-13 | 9:19 | 49.937
2020-07-13 | 9:19 | 49.934
2020-07-13 | 9:19 | 49.929
2020-07-13 | 9:19 | 49.926
2020-07-13 | 9:19 | 49.927
2020-07-13 | 9:19 | 49.929
2020-07-13 | 9:19 | 49.934
2020-07-13 | 9:19 | 49.938
2020-07-13 | 9:19 | 49.94
2020-07-13 | 9:19 | 49.942
2020-07-13 | 9:19 | 49.946
2020-07-13 | 9:19 | 49.949
2020-07-13 | 9:19 | 49.952
2020-07-13 | 9:19 | 49.955
2020-07-13 | 9:19 | 49.956
2020-07-13 | 9:19 | 49.958
2020-07-13 | 9:19 | 49.96
2020-07-13 | 9:19 | 49.962
2020-07-13 | 9:19 | 49.962
2020-07-13 | 9:19 | 49.96
2020-07-13 | 9:19 | 49.96
2020-07-13 | 9:19 | 49.96
2020-07-13 | 9:19 | 49.96
2020-07-13 | 9:19 | 49.959
2020-07-13 | 9:19 | 49.962
2020-07-13 | 9:19 | 49.963
2020-07-13 | 9:19 | 49.964
2020-07-13 | 9:19 | 49.964
2020-07-13 | 9:19 | 49.961
2020-07-13 | 9:19 | 49.957
2020-07-13 | 9:20 | 49.956
2020-07-13 | 9:20 | 49.954
2020-07-13 | 9:20 | 49.952
2020-07-13 | 9:20 | 49.951
2020-07-13 | 9:20 | 49.947
2020-07-13 | 9:20 | 49.945
2020-07-13 | 9:20 | 49.944
2020-07-13 | 9:20 | 49.943
2020-07-13 | 9:20 | 49.942
2020-07-13 | 9:20 | 49.943
2020-07-13 | 9:20 | 49.942
2020-07-13 | 9:20 | 49.943
2020-07-13 | 9:20 | 49.942
2020-07-13 | 9:20 | 49.944
2020-07-13 | 9:20 | 49.944
2020-07-13 | 9:20 | 49.944
2020-07-13 | 9:20 | 49.947
2020-07-13 | 9:20 | 49.948
2020-07-13 | 9:20 | 49.95
2020-07-13 | 9:20 | 49.948
2020-07-13 | 9:20 | 49.947
2020-07-13 | 9:20 | 49.945
2020-07-13 | 9:20 | 49.943
2020-07-13 | 9:20 | 49.94
2020-07-13 | 9:20 | 49.938
2020-07-13 | 9:20 | 49.936
2020-07-13 | 9:20 | 49.936
2020-07-13 | 9:20 | 49.936
2020-07-13 | 9:20 | 49.935
2020-07-13 | 9:20 | 49.934
2020-07-13 | 9:20 | 49.932
2020-07-13 | 9:20 | 49.929
2020-07-13 | 9:20 | 49.927
2020-07-13 | 9:20 | 49.925
2020-07-13 | 9:20 | 49.923
2020-07-13 | 9:20 | 49.921
2020-07-13 | 9:20 | 49.921
2020-07-13 | 9:20 | 49.923
2020-07-13 | 9:20 | 49.924
2020-07-13 | 9:20 | 49.928
2020-07-13 | 9:20 | 49.931
2020-07-13 | 9:20 | 49.934
2020-07-13 | 9:20 | 49.937
2020-07-13 | 9:20 | 49.937
2020-07-13 | 9:20 | 49.94
2020-07-13 | 9:20 | 49.94
2020-07-13 | 9:20 | 49.942
2020-07-13 | 9:20 | 49.945
2020-07-13 | 9:20 | 49.945
2020-07-13 | 9:20 | 49.944
2020-07-13 | 9:20 | 49.942
2020-07-13 | 9:20 | 49.94
2020-07-13 | 9:20 | 49.939
2020-07-13 | 9:20 | 49.939
2020-07-13 | 9:20 | 49.938
2020-07-13 | 9:20 | 49.937
2020-07-13 | 9:20 | 49.937
2020-07-13 | 9:20 | 49.938
2020-07-13 | 9:20 | 49.938
2020-07-13 | 9:20 | 49.936
2020-07-13 | 9:21 | 49.937
2020-07-13 | 9:21 | 49.938
2020-07-13 | 9:21 | 49.939
2020-07-13 | 9:21 | 49.94
2020-07-13 | 9:21 | 49.941
2020-07-13 | 9:21 | 49.944
2020-07-13 | 9:21 | 49.944
2020-07-13 | 9:21 | 49.945
2020-07-13 | 9:21 | 49.945
2020-07-13 | 9:21 | 49.946
2020-07-13 | 9:21 | 49.948
2020-07-13 | 9:21 | 49.947
2020-07-13 | 9:21 | 49.946
2020-07-13 | 9:21 | 49.944
2020-07-13 | 9:21 | 49.944
2020-07-13 | 9:21 | 49.945
2020-07-13 | 9:21 | 49.949
2020-07-13 | 9:21 | 49.952
2020-07-13 | 9:21 | 49.958
2020-07-13 | 9:21 | 49.965
2020-07-13 | 9:21 | 49.975
2020-07-13 | 9:21 | 49.981
2020-07-13 | 9:21 | 49.986
2020-07-13 | 9:21 | 49.989
2020-07-13 | 9:21 | 49.994
2020-07-13 | 9:21 | 49.995
2020-07-13 | 9:21 | 49.996
2020-07-13 | 9:21 | 49.997
2020-07-13 | 9:21 | 49.999
2020-07-13 | 9:21 | 49.998
2020-07-13 | 9:21 | 49.995
2020-07-13 | 9:21 | 49.993
2020-07-13 | 9:21 | 49.994
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.994
2020-07-13 | 9:21 | 49.997
2020-07-13 | 9:21 | 49.997
2020-07-13 | 9:21 | 49.999
2020-07-13 | 9:21 | 50.001
2020-07-13 | 9:21 | 50.004
2020-07-13 | 9:21 | 50.005
2020-07-13 | 9:21 | 50.005
2020-07-13 | 9:21 | 50.004
2020-07-13 | 9:21 | 50.002
2020-07-13 | 9:21 | 49.999
2020-07-13 | 9:21 | 49.998
2020-07-13 | 9:21 | 49.995
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.994
2020-07-13 | 9:21 | 49.994
2020-07-13 | 9:21 | 49.994
2020-07-13 | 9:21 | 49.992
2020-07-13 | 9:21 | 49.99
2020-07-13 | 9:21 | 49.987
2020-07-13 | 9:21 | 49.985
2020-07-13 | 9:21 | 49.98
2020-07-13 | 9:22 | 49.978
2020-07-13 | 9:22 | 49.974
2020-07-13 | 9:22 | 49.973
2020-07-13 | 9:22 | 49.972
2020-07-13 | 9:22 | 49.973
2020-07-13 | 9:22 | 49.975
2020-07-13 | 9:22 | 49.975
2020-07-13 | 9:22 | 49.975
2020-07-13 | 9:22 | 49.972
2020-07-13 | 9:22 | 49.969
2020-07-13 | 9:22 | 49.969
2020-07-13 | 9:22 | 49.967
2020-07-13 | 9:22 | 49.965
2020-07-13 | 9:22 | 49.961
2020-07-13 | 9:22 | 49.96
2020-07-13 | 9:22 | 49.958
2020-07-13 | 9:22 | 49.958
2020-07-13 | 9:22 | 49.962
2020-07-13 | 9:22 | 49.965
2020-07-13 | 9:22 | 49.969
2020-07-13 | 9:22 | 49.969
2020-07-13 | 9:22 | 49.968
2020-07-13 | 9:22 | 49.968
2020-07-13 | 9:22 | 49.967
2020-07-13 | 9:22 | 49.964
2020-07-13 | 9:22 | 49.963
2020-07-13 | 9:22 | 49.96
2020-07-13 | 9:22 | 49.96
2020-07-13 | 9:22 | 49.96