## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20200107-1 | Trip of IFA Bipole 1 |  | 2020-01-07 | 14:02 | N/A | Refer to tab 'Event 20200107-1' | 50.037 | 50.212 | 0.034 | 800 | 800 | N/A | N/A | N/A | 588.6706
Event 20200108-1 | Trip of GYAR |  | 2020-01-08 | 14:16 | N/A | Refer to tab 'Event 20200108-1' | 49.921 | 49.755 | -0.02 | 409 | -409 | N/A | N/A | N/A | 510.4422
Event 20200117-1 | Trip of HEYS12 |  | 2020-01-17 | 2:07 | N/A | Refer to tab 'Event 20200117-1' | 50.18 | 50.066 | -0.043 | 300 | -300 | N/A | N/A | N/A | 175.0465
Event 20200122-1 | Loss of PEHE-1 | GT tripped | 2020-01-22 | 15:23 | N/A | Refer to tab 'Event 20200122-1' | 49.988 | 49.89 | -0.028 | 373 | -373 | N/A | N/A | N/A | 332.9558
Event 20200122-2 | Trip of GRAI-8 |  | 2020-01-22 | 20:15 | N/A | Refer to tab 'Event 20200122-2' | 50.038 | 49.916 | -0.02 | 364 | -364 | N/A | N/A | N/A | 455.3458
Event 20200123-1 | Trip of GRAI-8 |  | 2020-01-23 | 21:00 | N/A | Refer to tab 'Event 20200123-1' | 49.982 | 49.827 | -0.023 | 280 | -280 | N/A | N/A | N/A | 304.2383
Event 20200126-1 | Trip of LAGA-1 | Output reduced gradually from 399MW at 21:14 to 0Mw at 21:43 | 2020-01-26 | 21:15 | N/A | Refer to tab 'Event 20200126-1' | 50.021 | 49.943 | N/A | 399 | -399 | N/A | N/A | N/A | N/A
Event 20200127-1 | Trip of HUMR-1 |  | 2020-01-27 | 11:29 | N/A | Refer to tab 'Event 20200127-1' | 49.947 | 49.795 | -0.034 | 348 | -348 | N/A | N/A | N/A | 255.6111
Event 20200128-1 | Trip of KLYN-A-1 |  | 2020-01-28 | 7:37 | N/A | Refer to tab 'Event 20200128-1' | 50.051 | 49.866 | -0.034 | 376 | -376 | N/A | N/A | N/A | 276.7526

## Event 20200107-1
In UTC
Date | Time | Freq
2020-01-07 | 14:00 | 50.098
2020-01-07 | 14:00 | 50.098
2020-01-07 | 14:00 | 50.093
2020-01-07 | 14:00 | 50.09
2020-01-07 | 14:00 | 50.087
2020-01-07 | 14:00 | 50.082
2020-01-07 | 14:00 | 50.078
2020-01-07 | 14:00 | 50.077
2020-01-07 | 14:00 | 50.074
2020-01-07 | 14:00 | 50.072
2020-01-07 | 14:00 | 50.068
2020-01-07 | 14:00 | 50.067
2020-01-07 | 14:00 | 50.065
2020-01-07 | 14:00 | 50.064
2020-01-07 | 14:00 | 50.063
2020-01-07 | 14:00 | 50.062
2020-01-07 | 14:00 | 50.062
2020-01-07 | 14:00 | 50.062
2020-01-07 | 14:00 | 50.065
2020-01-07 | 14:00 | 50.07
2020-01-07 | 14:00 | 50.071
2020-01-07 | 14:00 | 50.077
2020-01-07 | 14:00 | 50.078
2020-01-07 | 14:00 | 50.079
2020-01-07 | 14:00 | 50.08
2020-01-07 | 14:00 | 50.08
2020-01-07 | 14:00 | 50.081
2020-01-07 | 14:00 | 50.079
2020-01-07 | 14:00 | 50.077
2020-01-07 | 14:00 | 50.074
2020-01-07 | 14:00 | 50.073
2020-01-07 | 14:01 | 50.073
2020-01-07 | 14:01 | 50.073
2020-01-07 | 14:01 | 50.071
2020-01-07 | 14:01 | 50.067
2020-01-07 | 14:01 | 50.066
2020-01-07 | 14:01 | 50.064
2020-01-07 | 14:01 | 50.074
2020-01-07 | 14:01 | 50.075
2020-01-07 | 14:01 | 50.075
2020-01-07 | 14:01 | 50.08
2020-01-07 | 14:01 | 50.074
2020-01-07 | 14:01 | 50.073
2020-01-07 | 14:01 | 50.072
2020-01-07 | 14:01 | 50.074
2020-01-07 | 14:01 | 50.073
2020-01-07 | 14:01 | 50.074
2020-01-07 | 14:01 | 50.07
2020-01-07 | 14:01 | 50.071
2020-01-07 | 14:01 | 50.072
2020-01-07 | 14:01 | 50.071
2020-01-07 | 14:01 | 50.063
2020-01-07 | 14:01 | 50.06
2020-01-07 | 14:01 | 50.059
2020-01-07 | 14:01 | 50.057
2020-01-07 | 14:01 | 50.051
2020-01-07 | 14:01 | 50.046
2020-01-07 | 14:01 | 50.048
2020-01-07 | 14:01 | 50.046
2020-01-07 | 14:01 | 50.045
2020-01-07 | 14:01 | 50.044
2020-01-07 | 14:01 | 50.043
2020-01-07 | 14:01 | 50.046
2020-01-07 | 14:01 | 50.053
2020-01-07 | 14:01 | 50.05
2020-01-07 | 14:01 | 50.049
2020-01-07 | 14:01 | 50.047
2020-01-07 | 14:01 | 50.05
2020-01-07 | 14:01 | 50.053
2020-01-07 | 14:01 | 50.047
2020-01-07 | 14:01 | 50.044
2020-01-07 | 14:01 | 50.046
2020-01-07 | 14:01 | 50.046
2020-01-07 | 14:01 | 50.047
2020-01-07 | 14:01 | 50.049
2020-01-07 | 14:01 | 50.038
2020-01-07 | 14:01 | 50.04
2020-01-07 | 14:01 | 50.033
2020-01-07 | 14:01 | 50.032
2020-01-07 | 14:01 | 50.031
2020-01-07 | 14:01 | 50.036
2020-01-07 | 14:01 | 50.03
2020-01-07 | 14:01 | 50.028
2020-01-07 | 14:01 | 50.03
2020-01-07 | 14:01 | 50.039
2020-01-07 | 14:01 | 50.044
2020-01-07 | 14:01 | 50.038
2020-01-07 | 14:01 | 50.045
2020-01-07 | 14:01 | 50.051
2020-01-07 | 14:01 | 50.053
2020-01-07 | 14:02 | 50.047
2020-01-07 | 14:02 | 50.037
2020-01-07 | 14:02 | 50.041
2020-01-07 | 14:02 | 50.068
2020-01-07 | 14:02 | 50.097
2020-01-07 | 14:02 | 50.118
2020-01-07 | 14:02 | 50.134
2020-01-07 | 14:02 | 50.143
2020-01-07 | 14:02 | 50.149
2020-01-07 | 14:02 | 50.152
2020-01-07 | 14:02 | 50.152
2020-01-07 | 14:02 | 50.151
2020-01-07 | 14:02 | 50.151
2020-01-07 | 14:02 | 50.151
2020-01-07 | 14:02 | 50.153
2020-01-07 | 14:02 | 50.154
2020-01-07 | 14:02 | 50.156
2020-01-07 | 14:02 | 50.159
2020-01-07 | 14:02 | 50.159
2020-01-07 | 14:02 | 50.16
2020-01-07 | 14:02 | 50.162
2020-01-07 | 14:02 | 50.163
2020-01-07 | 14:02 | 50.164
2020-01-07 | 14:02 | 50.165
2020-01-07 | 14:02 | 50.167
2020-01-07 | 14:02 | 50.166
2020-01-07 | 14:02 | 50.168
2020-01-07 | 14:02 | 50.17
2020-01-07 | 14:02 | 50.171
2020-01-07 | 14:02 | 50.173
2020-01-07 | 14:02 | 50.172
2020-01-07 | 14:02 | 50.173
2020-01-07 | 14:02 | 50.174
2020-01-07 | 14:02 | 50.174
2020-01-07 | 14:02 | 50.174
2020-01-07 | 14:02 | 50.173
2020-01-07 | 14:02 | 50.171
2020-01-07 | 14:02 | 50.169
2020-01-07 | 14:02 | 50.167
2020-01-07 | 14:02 | 50.164
2020-01-07 | 14:02 | 50.163
2020-01-07 | 14:02 | 50.162
2020-01-07 | 14:02 | 50.162
2020-01-07 | 14:02 | 50.163
2020-01-07 | 14:02 | 50.162
2020-01-07 | 14:02 | 50.163
2020-01-07 | 14:02 | 50.166
2020-01-07 | 14:02 | 50.168
2020-01-07 | 14:02 | 50.17
2020-01-07 | 14:02 | 50.173
2020-01-07 | 14:02 | 50.175
2020-01-07 | 14:02 | 50.177
2020-01-07 | 14:02 | 50.178
2020-01-07 | 14:02 | 50.177
2020-01-07 | 14:02 | 50.178
2020-01-07 | 14:02 | 50.178
2020-01-07 | 14:02 | 50.177
2020-01-07 | 14:02 | 50.178
2020-01-07 | 14:02 | 50.178
2020-01-07 | 14:02 | 50.179
2020-01-07 | 14:02 | 50.176
2020-01-07 | 14:03 | 50.175
2020-01-07 | 14:03 | 50.176
2020-01-07 | 14:03 | 50.175
2020-01-07 | 14:03 | 50.175
2020-01-07 | 14:03 | 50.178
2020-01-07 | 14:03 | 50.181
2020-01-07 | 14:03 | 50.186
2020-01-07 | 14:03 | 50.187
2020-01-07 | 14:03 | 50.19
2020-01-07 | 14:03 | 50.189
2020-01-07 | 14:03 | 50.189
2020-01-07 | 14:03 | 50.191
2020-01-07 | 14:03 | 50.192
2020-01-07 | 14:03 | 50.194
2020-01-07 | 14:03 | 50.197
2020-01-07 | 14:03 | 50.199
2020-01-07 | 14:03 | 50.198
2020-01-07 | 14:03 | 50.197
2020-01-07 | 14:03 | 50.197
2020-01-07 | 14:03 | 50.197
2020-01-07 | 14:03 | 50.199
2020-01-07 | 14:03 | 50.202
2020-01-07 | 14:03 | 50.203
2020-01-07 | 14:03 | 50.203
2020-01-07 | 14:03 | 50.204
2020-01-07 | 14:03 | 50.204
2020-01-07 | 14:03 | 50.205
2020-01-07 | 14:03 | 50.207
2020-01-07 | 14:03 | 50.209
2020-01-07 | 14:03 | 50.209
2020-01-07 | 14:03 | 50.209
2020-01-07 | 14:03 | 50.21
2020-01-07 | 14:03 | 50.212
2020-01-07 | 14:03 | 50.214
2020-01-07 | 14:03 | 50.212
2020-01-07 | 14:03 | 50.211
2020-01-07 | 14:03 | 50.21
2020-01-07 | 14:03 | 50.207
2020-01-07 | 14:03 | 50.203
2020-01-07 | 14:03 | 50.198
2020-01-07 | 14:03 | 50.193
2020-01-07 | 14:03 | 50.191
2020-01-07 | 14:03 | 50.19
2020-01-07 | 14:03 | 50.192
2020-01-07 | 14:03 | 50.191
2020-01-07 | 14:03 | 50.191
2020-01-07 | 14:03 | 50.187
2020-01-07 | 14:03 | 50.185
2020-01-07 | 14:03 | 50.185
2020-01-07 | 14:03 | 50.183
2020-01-07 | 14:03 | 50.184
2020-01-07 | 14:03 | 50.183
2020-01-07 | 14:03 | 50.182
2020-01-07 | 14:03 | 50.183
2020-01-07 | 14:03 | 50.182
2020-01-07 | 14:03 | 50.186
2020-01-07 | 14:03 | 50.188
2020-01-07 | 14:03 | 50.192
2020-01-07 | 14:03 | 50.194
2020-01-07 | 14:04 | 50.194
2020-01-07 | 14:04 | 50.193
2020-01-07 | 14:04 | 50.194
2020-01-07 | 14:04 | 50.193
2020-01-07 | 14:04 | 50.192
2020-01-07 | 14:04 | 50.188
2020-01-07 | 14:04 | 50.186
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.184
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.186
2020-01-07 | 14:04 | 50.189
2020-01-07 | 14:04 | 50.191
2020-01-07 | 14:04 | 50.192
2020-01-07 | 14:04 | 50.194
2020-01-07 | 14:04 | 50.192
2020-01-07 | 14:04 | 50.191
2020-01-07 | 14:04 | 50.19
2020-01-07 | 14:04 | 50.189
2020-01-07 | 14:04 | 50.187
2020-01-07 | 14:04 | 50.186
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.186
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.185
2020-01-07 | 14:04 | 50.186
2020-01-07 | 14:04 | 50.184
2020-01-07 | 14:04 | 50.183
2020-01-07 | 14:04 | 50.182
2020-01-07 | 14:04 | 50.18
2020-01-07 | 14:04 | 50.18
2020-01-07 | 14:04 | 50.179
2020-01-07 | 14:04 | 50.18
2020-01-07 | 14:04 | 50.18
2020-01-07 | 14:04 | 50.178
2020-01-07 | 14:04 | 50.18
2020-01-07 | 14:04 | 50.178
2020-01-07 | 14:04 | 50.176
2020-01-07 | 14:04 | 50.176
2020-01-07 | 14:04 | 50.176
2020-01-07 | 14:04 | 50.176
2020-01-07 | 14:04 | 50.175
2020-01-07 | 14:04 | 50.175
2020-01-07 | 14:04 | 50.173
2020-01-07 | 14:04 | 50.171
2020-01-07 | 14:04 | 50.172
2020-01-07 | 14:04 | 50.173
2020-01-07 | 14:04 | 50.173
2020-01-07 | 14:04 | 50.172
2020-01-07 | 14:04 | 50.172
2020-01-07 | 14:04 | 50.173
2020-01-07 | 14:04 | 50.175
2020-01-07 | 14:04 | 50.174
2020-01-07 | 14:04 | 50.174
2020-01-07 | 14:04 | 50.174
2020-01-07 | 14:04 | 50.175
2020-01-07 | 14:04 | 50.175
2020-01-07 | 14:04 | 50.174
2020-01-07 | 14:04 | 50.176
2020-01-07 | 14:05 | 50.178
2020-01-07 | 14:05 | 50.178
2020-01-07 | 14:05 | 50.18
2020-01-07 | 14:05 | 50.182
2020-01-07 | 14:05 | 50.185
2020-01-07 | 14:05 | 50.187
2020-01-07 | 14:05 | 50.187
2020-01-07 | 14:05 | 50.187
2020-01-07 | 14:05 | 50.189
2020-01-07 | 14:05 | 50.189
2020-01-07 | 14:05 | 50.189
2020-01-07 | 14:05 | 50.19
2020-01-07 | 14:05 | 50.193
2020-01-07 | 14:05 | 50.193
2020-01-07 | 14:05 | 50.193
2020-01-07 | 14:05 | 50.192
2020-01-07 | 14:05 | 50.191
2020-01-07 | 14:05 | 50.191
2020-01-07 | 14:05 | 50.188
2020-01-07 | 14:05 | 50.187
2020-01-07 | 14:05 | 50.185
2020-01-07 | 14:05 | 50.184
2020-01-07 | 14:05 | 50.182
2020-01-07 | 14:05 | 50.18
2020-01-07 | 14:05 | 50.177
2020-01-07 | 14:05 | 50.174
2020-01-07 | 14:05 | 50.17
2020-01-07 | 14:05 | 50.166
2020-01-07 | 14:05 | 50.161
2020-01-07 | 14:05 | 50.159
2020-01-07 | 14:05 | 50.155
2020-01-07 | 14:05 | 50.153
2020-01-07 | 14:05 | 50.148
2020-01-07 | 14:05 | 50.148
2020-01-07 | 14:05 | 50.147
2020-01-07 | 14:05 | 50.146
2020-01-07 | 14:05 | 50.145
2020-01-07 | 14:05 | 50.141
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.138
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.142
2020-01-07 | 14:05 | 50.144
2020-01-07 | 14:05 | 50.144
2020-01-07 | 14:05 | 50.143
2020-01-07 | 14:05 | 50.143
2020-01-07 | 14:05 | 50.144
2020-01-07 | 14:05 | 50.143
2020-01-07 | 14:05 | 50.141
2020-01-07 | 14:05 | 50.14
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.138
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.139
2020-01-07 | 14:05 | 50.14
2020-01-07 | 14:05 | 50.137
2020-01-07 | 14:06 | 50.136
2020-01-07 | 14:06 | 50.137
2020-01-07 | 14:06 | 50.135
2020-01-07 | 14:06 | 50.133
2020-01-07 | 14:06 | 50.131
2020-01-07 | 14:06 | 50.128
2020-01-07 | 14:06 | 50.128
2020-01-07 | 14:06 | 50.126
2020-01-07 | 14:06 | 50.125
2020-01-07 | 14:06 | 50.121
2020-01-07 | 14:06 | 50.121
2020-01-07 | 14:06 | 50.121
2020-01-07 | 14:06 | 50.119
2020-01-07 | 14:06 | 50.119
2020-01-07 | 14:06 | 50.119
2020-01-07 | 14:06 | 50.119
2020-01-07 | 14:06 | 50.118
2020-01-07 | 14:06 | 50.119
2020-01-07 | 14:06 | 50.115
2020-01-07 | 14:06 | 50.115
2020-01-07 | 14:06 | 50.113
2020-01-07 | 14:06 | 50.112
2020-01-07 | 14:06 | 50.111
2020-01-07 | 14:06 | 50.109
2020-01-07 | 14:06 | 50.109
2020-01-07 | 14:06 | 50.108
2020-01-07 | 14:06 | 50.108
2020-01-07 | 14:06 | 50.107
2020-01-07 | 14:06 | 50.105
2020-01-07 | 14:06 | 50.104
2020-01-07 | 14:06 | 50.102
2020-01-07 | 14:06 | 50.098
2020-01-07 | 14:06 | 50.097
2020-01-07 | 14:06 | 50.097
2020-01-07 | 14:06 | 50.094
2020-01-07 | 14:06 | 50.094
2020-01-07 | 14:06 | 50.094
2020-01-07 | 14:06 | 50.094
2020-01-07 | 14:06 | 50.094
2020-01-07 | 14:06 | 50.094
2020-01-07 | 14:06 | 50.093
2020-01-07 | 14:06 | 50.091
2020-01-07 | 14:06 | 50.091
2020-01-07 | 14:06 | 50.089
2020-01-07 | 14:06 | 50.087
2020-01-07 | 14:06 | 50.086
2020-01-07 | 14:06 | 50.085
2020-01-07 | 14:06 | 50.086
2020-01-07 | 14:06 | 50.087
2020-01-07 | 14:06 | 50.085
2020-01-07 | 14:06 | 50.084
2020-01-07 | 14:06 | 50.083
2020-01-07 | 14:06 | 50.082
2020-01-07 | 14:06 | 50.08
2020-01-07 | 14:06 | 50.079
2020-01-07 | 14:06 | 50.077
2020-01-07 | 14:06 | 50.076
2020-01-07 | 14:06 | 50.075
2020-01-07 | 14:06 | 50.073
2020-01-07 | 14:06 | 50.071
2020-01-07 | 14:06 | 50.07
2020-01-07 | 14:07 | 50.071
2020-01-07 | 14:07 | 50.071
2020-01-07 | 14:07 | 50.071
2020-01-07 | 14:07 | 50.071
2020-01-07 | 14:07 | 50.072
2020-01-07 | 14:07 | 50.073
2020-01-07 | 14:07 | 50.073
2020-01-07 | 14:07 | 50.074
2020-01-07 | 14:07 | 50.075
2020-01-07 | 14:07 | 50.076
2020-01-07 | 14:07 | 50.076
2020-01-07 | 14:07 | 50.077
2020-01-07 | 14:07 | 50.077
2020-01-07 | 14:07 | 50.077
2020-01-07 | 14:07 | 50.078
2020-01-07 | 14:07 | 50.078
2020-01-07 | 14:07 | 50.073
2020-01-07 | 14:07 | 50.07
2020-01-07 | 14:07 | 50.069
2020-01-07 | 14:07 | 50.069
2020-01-07 | 14:07 | 50.069
2020-01-07 | 14:07 | 50.07
2020-01-07 | 14:07 | 50.071
2020-01-07 | 14:07 | 50.07
2020-01-07 | 14:07 | 50.068
2020-01-07 | 14:07 | 50.066
2020-01-07 | 14:07 | 50.064
2020-01-07 | 14:07 | 50.064
2020-01-07 | 14:07 | 50.06
2020-01-07 | 14:07 | 50.056
2020-01-07 | 14:07 | 50.054
2020-01-07 | 14:07 | 50.052
2020-01-07 | 14:07 | 50.053
2020-01-07 | 14:07 | 50.052
2020-01-07 | 14:07 | 50.053
2020-01-07 | 14:07 | 50.054
2020-01-07 | 14:07 | 50.057
2020-01-07 | 14:07 | 50.06
2020-01-07 | 14:07 | 50.065
2020-01-07 | 14:07 | 50.067
2020-01-07 | 14:07 | 50.067
2020-01-07 | 14:07 | 50.067
2020-01-07 | 14:07 | 50.066
2020-01-07 | 14:07 | 50.065
2020-01-07 | 14:07 | 50.063
2020-01-07 | 14:07 | 50.064
2020-01-07 | 14:07 | 50.065
2020-01-07 | 14:07 | 50.066
2020-01-07 | 14:07 | 50.065
2020-01-07 | 14:07 | 50.065
2020-01-07 | 14:07 | 50.064
2020-01-07 | 14:07 | 50.061
2020-01-07 | 14:07 | 50.058
2020-01-07 | 14:07 | 50.059
2020-01-07 | 14:07 | 50.056
2020-01-07 | 14:07 | 50.052
2020-01-07 | 14:07 | 50.051
2020-01-07 | 14:07 | 50.048
2020-01-07 | 14:07 | 50.048
2020-01-07 | 14:08 | 50.048
2020-01-07 | 14:08 | 50.048
2020-01-07 | 14:08 | 50.048
2020-01-07 | 14:08 | 50.047
2020-01-07 | 14:08 | 50.046
2020-01-07 | 14:08 | 50.047
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.043
2020-01-07 | 14:08 | 50.042
2020-01-07 | 14:08 | 50.042
2020-01-07 | 14:08 | 50.043
2020-01-07 | 14:08 | 50.044
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.046
2020-01-07 | 14:08 | 50.046
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.045
2020-01-07 | 14:08 | 50.043
2020-01-07 | 14:08 | 50.041
2020-01-07 | 14:08 | 50.039
2020-01-07 | 14:08 | 50.037
2020-01-07 | 14:08 | 50.037
2020-01-07 | 14:08 | 50.037
2020-01-07 | 14:08 | 50.039
2020-01-07 | 14:08 | 50.039
2020-01-07 | 14:08 | 50.039
2020-01-07 | 14:08 | 50.039
2020-01-07 | 14:08 | 50.04
2020-01-07 | 14:08 | 50.042
2020-01-07 | 14:08 | 50.042
2020-01-07 | 14:08 | 50.043
2020-01-07 | 14:08 | 50.041
2020-01-07 | 14:08 | 50.039
2020-01-07 | 14:08 | 50.037
2020-01-07 | 14:08 | 50.034
2020-01-07 | 14:08 | 50.031
2020-01-07 | 14:08 | 50.026
2020-01-07 | 14:08 | 50.021
2020-01-07 | 14:08 | 50.014
2020-01-07 | 14:08 | 50.009
2020-01-07 | 14:08 | 50.007
2020-01-07 | 14:08 | 50.005
2020-01-07 | 14:08 | 50.003
2020-01-07 | 14:08 | 50.003
2020-01-07 | 14:08 | 50.002
2020-01-07 | 14:08 | 49.999
2020-01-07 | 14:08 | 49.999
2020-01-07 | 14:08 | 49.996
2020-01-07 | 14:08 | 49.995
2020-01-07 | 14:08 | 49.994
2020-01-07 | 14:08 | 49.992
2020-01-07 | 14:08 | 49.988
2020-01-07 | 14:08 | 49.984
2020-01-07 | 14:08 | 49.979
2020-01-07 | 14:08 | 49.976
2020-01-07 | 14:08 | 49.976
2020-01-07 | 14:08 | 49.974
2020-01-07 | 14:09 | 49.974
2020-01-07 | 14:09 | 49.974
2020-01-07 | 14:09 | 49.971
2020-01-07 | 14:09 | 49.972
2020-01-07 | 14:09 | 49.973
2020-01-07 | 14:09 | 49.975
2020-01-07 | 14:09 | 49.975
2020-01-07 | 14:09 | 49.974
2020-01-07 | 14:09 | 49.973
2020-01-07 | 14:09 | 49.972
2020-01-07 | 14:09 | 49.973
2020-01-07 | 14:09 | 49.972
2020-01-07 | 14:09 | 49.974
2020-01-07 | 14:09 | 49.976
2020-01-07 | 14:09 | 49.979
2020-01-07 | 14:09 | 49.979
2020-01-07 | 14:09 | 49.981
2020-01-07 | 14:09 | 49.983
2020-01-07 | 14:09 | 49.982
2020-01-07 | 14:09 | 49.982
2020-01-07 | 14:09 | 49.982
2020-01-07 | 14:09 | 49.981
2020-01-07 | 14:09 | 49.98
2020-01-07 | 14:09 | 49.978
2020-01-07 | 14:09 | 49.975
2020-01-07 | 14:09 | 49.973
2020-01-07 | 14:09 | 49.973
2020-01-07 | 14:09 | 49.973
2020-01-07 | 14:09 | 49.972
2020-01-07 | 14:09 | 49.971

## Event 20200108-1
In UTC
Date | Time | Freq
2020-01-08 | 14:15 | 49.973
2020-01-08 | 14:15 | 49.971
2020-01-08 | 14:15 | 49.969
2020-01-08 | 14:15 | 49.969
2020-01-08 | 14:15 | 49.969
2020-01-08 | 14:15 | 49.972
2020-01-08 | 14:15 | 49.971
2020-01-08 | 14:15 | 49.972
2020-01-08 | 14:15 | 49.97
2020-01-08 | 14:15 | 49.972
2020-01-08 | 14:15 | 49.972
2020-01-08 | 14:15 | 49.972
2020-01-08 | 14:15 | 49.97
2020-01-08 | 14:15 | 49.968
2020-01-08 | 14:15 | 49.962
2020-01-08 | 14:15 | 49.955
2020-01-08 | 14:15 | 49.95
2020-01-08 | 14:15 | 49.945
2020-01-08 | 14:15 | 49.941
2020-01-08 | 14:15 | 49.937
2020-01-08 | 14:15 | 49.936
2020-01-08 | 14:15 | 49.934
2020-01-08 | 14:15 | 49.933
2020-01-08 | 14:15 | 49.934
2020-01-08 | 14:15 | 49.937
2020-01-08 | 14:15 | 49.939
2020-01-08 | 14:15 | 49.942
2020-01-08 | 14:15 | 49.941
2020-01-08 | 14:15 | 49.939
2020-01-08 | 14:15 | 49.936
2020-01-08 | 14:15 | 49.933
2020-01-08 | 14:16 | 49.933
2020-01-08 | 14:16 | 49.932
2020-01-08 | 14:16 | 49.929
2020-01-08 | 14:16 | 49.928
2020-01-08 | 14:16 | 49.927
2020-01-08 | 14:16 | 49.929
2020-01-08 | 14:16 | 49.931
2020-01-08 | 14:16 | 49.931
2020-01-08 | 14:16 | 49.933
2020-01-08 | 14:16 | 49.934
2020-01-08 | 14:16 | 49.934
2020-01-08 | 14:16 | 49.936
2020-01-08 | 14:16 | 49.934
2020-01-08 | 14:16 | 49.936
2020-01-08 | 14:16 | 49.936
2020-01-08 | 14:16 | 49.937
2020-01-08 | 14:16 | 49.939
2020-01-08 | 14:16 | 49.938
2020-01-08 | 14:16 | 49.938
2020-01-08 | 14:16 | 49.939
2020-01-08 | 14:16 | 49.941
2020-01-08 | 14:16 | 49.941
2020-01-08 | 14:16 | 49.94
2020-01-08 | 14:16 | 49.939
2020-01-08 | 14:16 | 49.937
2020-01-08 | 14:16 | 49.937
2020-01-08 | 14:16 | 49.936
2020-01-08 | 14:16 | 49.935
2020-01-08 | 14:16 | 49.935
2020-01-08 | 14:16 | 49.934
2020-01-08 | 14:16 | 49.932
2020-01-08 | 14:16 | 49.93
2020-01-08 | 14:16 | 49.929
2020-01-08 | 14:16 | 49.926
2020-01-08 | 14:16 | 49.924
2020-01-08 | 14:16 | 49.922
2020-01-08 | 14:16 | 49.921
2020-01-08 | 14:16 | 49.92
2020-01-08 | 14:16 | 49.92
2020-01-08 | 14:16 | 49.919
2020-01-08 | 14:16 | 49.92
2020-01-08 | 14:16 | 49.92
2020-01-08 | 14:16 | 49.922
2020-01-08 | 14:16 | 49.923
2020-01-08 | 14:16 | 49.924
2020-01-08 | 14:16 | 49.927
2020-01-08 | 14:16 | 49.927
2020-01-08 | 14:16 | 49.927
2020-01-08 | 14:16 | 49.926
2020-01-08 | 14:16 | 49.923
2020-01-08 | 14:16 | 49.92
2020-01-08 | 14:16 | 49.919
2020-01-08 | 14:16 | 49.918
2020-01-08 | 14:16 | 49.917
2020-01-08 | 14:16 | 49.916
2020-01-08 | 14:16 | 49.917
2020-01-08 | 14:16 | 49.919
2020-01-08 | 14:16 | 49.921
2020-01-08 | 14:16 | 49.921
2020-01-08 | 14:17 | 49.911
2020-01-08 | 14:17 | 49.9
2020-01-08 | 14:17 | 49.89
2020-01-08 | 14:17 | 49.882
2020-01-08 | 14:17 | 49.875
2020-01-08 | 14:17 | 49.867
2020-01-08 | 14:17 | 49.861
2020-01-08 | 14:17 | 49.853
2020-01-08 | 14:17 | 49.846
2020-01-08 | 14:17 | 49.841
2020-01-08 | 14:17 | 49.837
2020-01-08 | 14:17 | 49.833
2020-01-08 | 14:17 | 49.83
2020-01-08 | 14:17 | 49.83
2020-01-08 | 14:17 | 49.829
2020-01-08 | 14:17 | 49.829
2020-01-08 | 14:17 | 49.828
2020-01-08 | 14:17 | 49.827
2020-01-08 | 14:17 | 49.825
2020-01-08 | 14:17 | 49.821
2020-01-08 | 14:17 | 49.819
2020-01-08 | 14:17 | 49.818
2020-01-08 | 14:17 | 49.817
2020-01-08 | 14:17 | 49.817
2020-01-08 | 14:17 | 49.816
2020-01-08 | 14:17 | 49.815
2020-01-08 | 14:17 | 49.814
2020-01-08 | 14:17 | 49.814
2020-01-08 | 14:17 | 49.811
2020-01-08 | 14:17 | 49.807
2020-01-08 | 14:17 | 49.8
2020-01-08 | 14:17 | 49.796
2020-01-08 | 14:17 | 49.792
2020-01-08 | 14:17 | 49.788
2020-01-08 | 14:17 | 49.787
2020-01-08 | 14:17 | 49.787
2020-01-08 | 14:17 | 49.789
2020-01-08 | 14:17 | 49.79
2020-01-08 | 14:17 | 49.79
2020-01-08 | 14:17 | 49.789
2020-01-08 | 14:17 | 49.792
2020-01-08 | 14:17 | 49.791
2020-01-08 | 14:17 | 49.792
2020-01-08 | 14:17 | 49.793
2020-01-08 | 14:17 | 49.794
2020-01-08 | 14:17 | 49.795
2020-01-08 | 14:17 | 49.796
2020-01-08 | 14:17 | 49.798
2020-01-08 | 14:17 | 49.801
2020-01-08 | 14:17 | 49.805
2020-01-08 | 14:17 | 49.806
2020-01-08 | 14:17 | 49.806
2020-01-08 | 14:17 | 49.805
2020-01-08 | 14:17 | 49.801
2020-01-08 | 14:17 | 49.798
2020-01-08 | 14:17 | 49.794
2020-01-08 | 14:17 | 49.792
2020-01-08 | 14:17 | 49.786
2020-01-08 | 14:17 | 49.781
2020-01-08 | 14:17 | 49.776
2020-01-08 | 14:17 | 49.772
2020-01-08 | 14:18 | 49.77
2020-01-08 | 14:18 | 49.769
2020-01-08 | 14:18 | 49.768
2020-01-08 | 14:18 | 49.766
2020-01-08 | 14:18 | 49.765
2020-01-08 | 14:18 | 49.764
2020-01-08 | 14:18 | 49.763
2020-01-08 | 14:18 | 49.761
2020-01-08 | 14:18 | 49.759
2020-01-08 | 14:18 | 49.755
2020-01-08 | 14:18 | 49.757
2020-01-08 | 14:18 | 49.758
2020-01-08 | 14:18 | 49.76
2020-01-08 | 14:18 | 49.763
2020-01-08 | 14:18 | 49.765
2020-01-08 | 14:18 | 49.768
2020-01-08 | 14:18 | 49.771
2020-01-08 | 14:18 | 49.772
2020-01-08 | 14:18 | 49.774
2020-01-08 | 14:18 | 49.775
2020-01-08 | 14:18 | 49.777
2020-01-08 | 14:18 | 49.778
2020-01-08 | 14:18 | 49.778
2020-01-08 | 14:18 | 49.777
2020-01-08 | 14:18 | 49.775
2020-01-08 | 14:18 | 49.776
2020-01-08 | 14:18 | 49.775
2020-01-08 | 14:18 | 49.777
2020-01-08 | 14:18 | 49.778
2020-01-08 | 14:18 | 49.777
2020-01-08 | 14:18 | 49.777
2020-01-08 | 14:18 | 49.776
2020-01-08 | 14:18 | 49.777
2020-01-08 | 14:18 | 49.778
2020-01-08 | 14:18 | 49.778
2020-01-08 | 14:18 | 49.78
2020-01-08 | 14:18 | 49.78
2020-01-08 | 14:18 | 49.782
2020-01-08 | 14:18 | 49.785
2020-01-08 | 14:18 | 49.788
2020-01-08 | 14:18 | 49.79
2020-01-08 | 14:18 | 49.792
2020-01-08 | 14:18 | 49.794
2020-01-08 | 14:18 | 49.797
2020-01-08 | 14:18 | 49.801
2020-01-08 | 14:18 | 49.804
2020-01-08 | 14:18 | 49.808
2020-01-08 | 14:18 | 49.812
2020-01-08 | 14:18 | 49.817
2020-01-08 | 14:18 | 49.819
2020-01-08 | 14:18 | 49.821
2020-01-08 | 14:18 | 49.824
2020-01-08 | 14:18 | 49.825
2020-01-08 | 14:18 | 49.826
2020-01-08 | 14:18 | 49.827
2020-01-08 | 14:18 | 49.828
2020-01-08 | 14:18 | 49.826
2020-01-08 | 14:18 | 49.827
2020-01-08 | 14:18 | 49.826
2020-01-08 | 14:19 | 49.823
2020-01-08 | 14:19 | 49.823
2020-01-08 | 14:19 | 49.821
2020-01-08 | 14:19 | 49.823
2020-01-08 | 14:19 | 49.824
2020-01-08 | 14:19 | 49.827
2020-01-08 | 14:19 | 49.828
2020-01-08 | 14:19 | 49.826
2020-01-08 | 14:19 | 49.825
2020-01-08 | 14:19 | 49.824
2020-01-08 | 14:19 | 49.824
2020-01-08 | 14:19 | 49.825
2020-01-08 | 14:19 | 49.825
2020-01-08 | 14:19 | 49.826
2020-01-08 | 14:19 | 49.826
2020-01-08 | 14:19 | 49.829
2020-01-08 | 14:19 | 49.83
2020-01-08 | 14:19 | 49.831
2020-01-08 | 14:19 | 49.832
2020-01-08 | 14:19 | 49.834
2020-01-08 | 14:19 | 49.836
2020-01-08 | 14:19 | 49.837
2020-01-08 | 14:19 | 49.841
2020-01-08 | 14:19 | 49.845
2020-01-08 | 14:19 | 49.85
2020-01-08 | 14:19 | 49.853
2020-01-08 | 14:19 | 49.856
2020-01-08 | 14:19 | 49.857
2020-01-08 | 14:19 | 49.859
2020-01-08 | 14:19 | 49.859
2020-01-08 | 14:19 | 49.857
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.854
2020-01-08 | 14:19 | 49.854
2020-01-08 | 14:19 | 49.853
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.856
2020-01-08 | 14:19 | 49.857
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.854
2020-01-08 | 14:19 | 49.854
2020-01-08 | 14:19 | 49.852
2020-01-08 | 14:19 | 49.851
2020-01-08 | 14:19 | 49.851
2020-01-08 | 14:19 | 49.851
2020-01-08 | 14:19 | 49.851
2020-01-08 | 14:19 | 49.851
2020-01-08 | 14:19 | 49.851
2020-01-08 | 14:19 | 49.852
2020-01-08 | 14:19 | 49.852
2020-01-08 | 14:19 | 49.855
2020-01-08 | 14:19 | 49.858
2020-01-08 | 14:19 | 49.862
2020-01-08 | 14:19 | 49.868
2020-01-08 | 14:19 | 49.874
2020-01-08 | 14:19 | 49.88
2020-01-08 | 14:19 | 49.881
2020-01-08 | 14:19 | 49.882
2020-01-08 | 14:20 | 49.886
2020-01-08 | 14:20 | 49.889
2020-01-08 | 14:20 | 49.895
2020-01-08 | 14:20 | 49.902
2020-01-08 | 14:20 | 49.908
2020-01-08 | 14:20 | 49.91
2020-01-08 | 14:20 | 49.913
2020-01-08 | 14:20 | 49.917
2020-01-08 | 14:20 | 49.918
2020-01-08 | 14:20 | 49.917
2020-01-08 | 14:20 | 49.917
2020-01-08 | 14:20 | 49.918
2020-01-08 | 14:20 | 49.919
2020-01-08 | 14:20 | 49.917
2020-01-08 | 14:20 | 49.915
2020-01-08 | 14:20 | 49.914
2020-01-08 | 14:20 | 49.912
2020-01-08 | 14:20 | 49.911
2020-01-08 | 14:20 | 49.912
2020-01-08 | 14:20 | 49.909
2020-01-08 | 14:20 | 49.907
2020-01-08 | 14:20 | 49.903
2020-01-08 | 14:20 | 49.902
2020-01-08 | 14:20 | 49.903
2020-01-08 | 14:20 | 49.905
2020-01-08 | 14:20 | 49.911
2020-01-08 | 14:20 | 49.917
2020-01-08 | 14:20 | 49.924
2020-01-08 | 14:20 | 49.93
2020-01-08 | 14:20 | 49.935
2020-01-08 | 14:20 | 49.937
2020-01-08 | 14:20 | 49.937
2020-01-08 | 14:20 | 49.937
2020-01-08 | 14:20 | 49.939
2020-01-08 | 14:20 | 49.939
2020-01-08 | 14:20 | 49.937
2020-01-08 | 14:20 | 49.936
2020-01-08 | 14:20 | 49.933
2020-01-08 | 14:20 | 49.934
2020-01-08 | 14:20 | 49.935
2020-01-08 | 14:20 | 49.936
2020-01-08 | 14:20 | 49.936
2020-01-08 | 14:20 | 49.937
2020-01-08 | 14:20 | 49.939
2020-01-08 | 14:20 | 49.937
2020-01-08 | 14:20 | 49.939
2020-01-08 | 14:20 | 49.936
2020-01-08 | 14:20 | 49.936
2020-01-08 | 14:20 | 49.932
2020-01-08 | 14:20 | 49.93
2020-01-08 | 14:20 | 49.929
2020-01-08 | 14:20 | 49.929
2020-01-08 | 14:20 | 49.928
2020-01-08 | 14:20 | 49.927
2020-01-08 | 14:20 | 49.926
2020-01-08 | 14:20 | 49.924
2020-01-08 | 14:20 | 49.923
2020-01-08 | 14:20 | 49.922
2020-01-08 | 14:20 | 49.92
2020-01-08 | 14:21 | 49.917
2020-01-08 | 14:21 | 49.913
2020-01-08 | 14:21 | 49.909
2020-01-08 | 14:21 | 49.908
2020-01-08 | 14:21 | 49.906
2020-01-08 | 14:21 | 49.903
2020-01-08 | 14:21 | 49.901
2020-01-08 | 14:21 | 49.902
2020-01-08 | 14:21 | 49.9
2020-01-08 | 14:21 | 49.9
2020-01-08 | 14:21 | 49.902
2020-01-08 | 14:21 | 49.904
2020-01-08 | 14:21 | 49.906
2020-01-08 | 14:21 | 49.907
2020-01-08 | 14:21 | 49.908
2020-01-08 | 14:21 | 49.907
2020-01-08 | 14:21 | 49.906
2020-01-08 | 14:21 | 49.905
2020-01-08 | 14:21 | 49.903
2020-01-08 | 14:21 | 49.903
2020-01-08 | 14:21 | 49.902
2020-01-08 | 14:21 | 49.901
2020-01-08 | 14:21 | 49.899
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.896
2020-01-08 | 14:21 | 49.896
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.898
2020-01-08 | 14:21 | 49.898
2020-01-08 | 14:21 | 49.901
2020-01-08 | 14:21 | 49.902
2020-01-08 | 14:21 | 49.905
2020-01-08 | 14:21 | 49.906
2020-01-08 | 14:21 | 49.908
2020-01-08 | 14:21 | 49.91
2020-01-08 | 14:21 | 49.913
2020-01-08 | 14:21 | 49.914
2020-01-08 | 14:21 | 49.915
2020-01-08 | 14:21 | 49.914
2020-01-08 | 14:21 | 49.912
2020-01-08 | 14:21 | 49.911
2020-01-08 | 14:21 | 49.908
2020-01-08 | 14:21 | 49.906
2020-01-08 | 14:21 | 49.904
2020-01-08 | 14:21 | 49.897
2020-01-08 | 14:21 | 49.895
2020-01-08 | 14:21 | 49.894
2020-01-08 | 14:21 | 49.894
2020-01-08 | 14:21 | 49.895
2020-01-08 | 14:21 | 49.896
2020-01-08 | 14:21 | 49.898
2020-01-08 | 14:21 | 49.899
2020-01-08 | 14:21 | 49.9
2020-01-08 | 14:21 | 49.903
2020-01-08 | 14:21 | 49.905
2020-01-08 | 14:21 | 49.908
2020-01-08 | 14:22 | 49.911
2020-01-08 | 14:22 | 49.916
2020-01-08 | 14:22 | 49.919
2020-01-08 | 14:22 | 49.92
2020-01-08 | 14:22 | 49.919
2020-01-08 | 14:22 | 49.92
2020-01-08 | 14:22 | 49.92
2020-01-08 | 14:22 | 49.919
2020-01-08 | 14:22 | 49.917
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.913
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.913
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.913
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.916
2020-01-08 | 14:22 | 49.918
2020-01-08 | 14:22 | 49.918
2020-01-08 | 14:22 | 49.918
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.913
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.916
2020-01-08 | 14:22 | 49.916
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.911
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.912
2020-01-08 | 14:22 | 49.911
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.914
2020-01-08 | 14:22 | 49.915
2020-01-08 | 14:22 | 49.918
2020-01-08 | 14:22 | 49.919
2020-01-08 | 14:22 | 49.921
2020-01-08 | 14:22 | 49.923
2020-01-08 | 14:22 | 49.922
2020-01-08 | 14:22 | 49.923
2020-01-08 | 14:22 | 49.925
2020-01-08 | 14:22 | 49.929
2020-01-08 | 14:22 | 49.931
2020-01-08 | 14:22 | 49.933
2020-01-08 | 14:22 | 49.935
2020-01-08 | 14:23 | 49.936
2020-01-08 | 14:23 | 49.939
2020-01-08 | 14:23 | 49.942
2020-01-08 | 14:23 | 49.946
2020-01-08 | 14:23 | 49.949
2020-01-08 | 14:23 | 49.95
2020-01-08 | 14:23 | 49.952
2020-01-08 | 14:23 | 49.95
2020-01-08 | 14:23 | 49.951
2020-01-08 | 14:23 | 49.951
2020-01-08 | 14:23 | 49.953
2020-01-08 | 14:23 | 49.952
2020-01-08 | 14:23 | 49.952
2020-01-08 | 14:23 | 49.951
2020-01-08 | 14:23 | 49.95
2020-01-08 | 14:23 | 49.95
2020-01-08 | 14:23 | 49.95
2020-01-08 | 14:23 | 49.95
2020-01-08 | 14:23 | 49.948
2020-01-08 | 14:23 | 49.946
2020-01-08 | 14:23 | 49.943
2020-01-08 | 14:23 | 49.941
2020-01-08 | 14:23 | 49.94
2020-01-08 | 14:23 | 49.941
2020-01-08 | 14:23 | 49.942
2020-01-08 | 14:23 | 49.943
2020-01-08 | 14:23 | 49.946
2020-01-08 | 14:23 | 49.949
2020-01-08 | 14:23 | 49.953
2020-01-08 | 14:23 | 49.956
2020-01-08 | 14:23 | 49.958
2020-01-08 | 14:23 | 49.96
2020-01-08 | 14:23 | 49.962
2020-01-08 | 14:23 | 49.966
2020-01-08 | 14:23 | 49.968
2020-01-08 | 14:23 | 49.971
2020-01-08 | 14:23 | 49.972
2020-01-08 | 14:23 | 49.974
2020-01-08 | 14:23 | 49.975
2020-01-08 | 14:23 | 49.977
2020-01-08 | 14:23 | 49.977
2020-01-08 | 14:23 | 49.975
2020-01-08 | 14:23 | 49.974
2020-01-08 | 14:23 | 49.978
2020-01-08 | 14:23 | 49.978
2020-01-08 | 14:23 | 49.978
2020-01-08 | 14:23 | 49.979
2020-01-08 | 14:23 | 49.979
2020-01-08 | 14:23 | 49.982
2020-01-08 | 14:23 | 49.982
2020-01-08 | 14:23 | 49.983
2020-01-08 | 14:23 | 49.984
2020-01-08 | 14:23 | 49.986
2020-01-08 | 14:23 | 49.987
2020-01-08 | 14:23 | 49.988
2020-01-08 | 14:23 | 49.987
2020-01-08 | 14:23 | 49.987
2020-01-08 | 14:23 | 49.988
2020-01-08 | 14:23 | 49.99
2020-01-08 | 14:24 | 49.992
2020-01-08 | 14:24 | 49.994
2020-01-08 | 14:24 | 49.996
2020-01-08 | 14:24 | 49.999
2020-01-08 | 14:24 | 50
2020-01-08 | 14:24 | 49.999
2020-01-08 | 14:24 | 49.998
2020-01-08 | 14:24 | 49.994
2020-01-08 | 14:24 | 49.988
2020-01-08 | 14:24 | 49.982
2020-01-08 | 14:24 | 49.977
2020-01-08 | 14:24 | 49.975
2020-01-08 | 14:24 | 49.974
2020-01-08 | 14:24 | 49.976
2020-01-08 | 14:24 | 49.978
2020-01-08 | 14:24 | 49.981
2020-01-08 | 14:24 | 49.983
2020-01-08 | 14:24 | 49.983
2020-01-08 | 14:24 | 49.986
2020-01-08 | 14:24 | 49.987
2020-01-08 | 14:24 | 49.986
2020-01-08 | 14:24 | 49.985
2020-01-08 | 14:24 | 49.983
2020-01-08 | 14:24 | 49.98
2020-01-08 | 14:24 | 49.98
2020-01-08 | 14:24 | 49.981
2020-01-08 | 14:24 | 49.985
2020-01-08 | 14:24 | 49.988
2020-01-08 | 14:24 | 49.995
2020-01-08 | 14:24 | 50.001

## Event 20200117-1
In UTC
Date | Time | Freq
2020-01-17 | 2:06 | 50.19
2020-01-17 | 2:06 | 50.189
2020-01-17 | 2:06 | 50.187
2020-01-17 | 2:06 | 50.189
2020-01-17 | 2:06 | 50.19
2020-01-17 | 2:06 | 50.189
2020-01-17 | 2:06 | 50.187
2020-01-17 | 2:06 | 50.189
2020-01-17 | 2:06 | 50.191
2020-01-17 | 2:06 | 50.192
2020-01-17 | 2:06 | 50.193
2020-01-17 | 2:06 | 50.194
2020-01-17 | 2:06 | 50.191
2020-01-17 | 2:06 | 50.189
2020-01-17 | 2:06 | 50.186
2020-01-17 | 2:06 | 50.183
2020-01-17 | 2:06 | 50.18
2020-01-17 | 2:06 | 50.18
2020-01-17 | 2:06 | 50.177
2020-01-17 | 2:06 | 50.177
2020-01-17 | 2:06 | 50.175
2020-01-17 | 2:06 | 50.175
2020-01-17 | 2:06 | 50.177
2020-01-17 | 2:06 | 50.177
2020-01-17 | 2:06 | 50.176
2020-01-17 | 2:06 | 50.175
2020-01-17 | 2:06 | 50.174
2020-01-17 | 2:06 | 50.176
2020-01-17 | 2:06 | 50.177
2020-01-17 | 2:06 | 50.177
2020-01-17 | 2:07 | 50.179
2020-01-17 | 2:07 | 50.184
2020-01-17 | 2:07 | 50.185
2020-01-17 | 2:07 | 50.184
2020-01-17 | 2:07 | 50.185
2020-01-17 | 2:07 | 50.184
2020-01-17 | 2:07 | 50.185
2020-01-17 | 2:07 | 50.185
2020-01-17 | 2:07 | 50.181
2020-01-17 | 2:07 | 50.178
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.172
2020-01-17 | 2:07 | 50.174
2020-01-17 | 2:07 | 50.179
2020-01-17 | 2:07 | 50.18
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.176
2020-01-17 | 2:07 | 50.176
2020-01-17 | 2:07 | 50.175
2020-01-17 | 2:07 | 50.175
2020-01-17 | 2:07 | 50.174
2020-01-17 | 2:07 | 50.172
2020-01-17 | 2:07 | 50.174
2020-01-17 | 2:07 | 50.172
2020-01-17 | 2:07 | 50.171
2020-01-17 | 2:07 | 50.171
2020-01-17 | 2:07 | 50.172
2020-01-17 | 2:07 | 50.172
2020-01-17 | 2:07 | 50.172
2020-01-17 | 2:07 | 50.173
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.177
2020-01-17 | 2:07 | 50.18
2020-01-17 | 2:07 | 50.18
2020-01-17 | 2:07 | 50.164
2020-01-17 | 2:07 | 50.125
2020-01-17 | 2:07 | 50.096
2020-01-17 | 2:07 | 50.078
2020-01-17 | 2:07 | 50.068
2020-01-17 | 2:07 | 50.066
2020-01-17 | 2:07 | 50.068
2020-01-17 | 2:07 | 50.07
2020-01-17 | 2:07 | 50.073
2020-01-17 | 2:07 | 50.076
2020-01-17 | 2:07 | 50.077
2020-01-17 | 2:07 | 50.078
2020-01-17 | 2:07 | 50.078
2020-01-17 | 2:07 | 50.081
2020-01-17 | 2:07 | 50.082
2020-01-17 | 2:07 | 50.082
2020-01-17 | 2:07 | 50.08
2020-01-17 | 2:07 | 50.081
2020-01-17 | 2:07 | 50.082
2020-01-17 | 2:07 | 50.084
2020-01-17 | 2:07 | 50.084
2020-01-17 | 2:07 | 50.08
2020-01-17 | 2:07 | 50.079
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.074
2020-01-17 | 2:08 | 50.073
2020-01-17 | 2:08 | 50.074
2020-01-17 | 2:08 | 50.074
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.076
2020-01-17 | 2:08 | 50.075
2020-01-17 | 2:08 | 50.075
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.079
2020-01-17 | 2:08 | 50.082
2020-01-17 | 2:08 | 50.082
2020-01-17 | 2:08 | 50.083
2020-01-17 | 2:08 | 50.083
2020-01-17 | 2:08 | 50.082
2020-01-17 | 2:08 | 50.083
2020-01-17 | 2:08 | 50.083
2020-01-17 | 2:08 | 50.083
2020-01-17 | 2:08 | 50.081
2020-01-17 | 2:08 | 50.079
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.076
2020-01-17 | 2:08 | 50.073
2020-01-17 | 2:08 | 50.074
2020-01-17 | 2:08 | 50.075
2020-01-17 | 2:08 | 50.076
2020-01-17 | 2:08 | 50.075
2020-01-17 | 2:08 | 50.073
2020-01-17 | 2:08 | 50.074
2020-01-17 | 2:08 | 50.076
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.08
2020-01-17 | 2:08 | 50.08
2020-01-17 | 2:08 | 50.08
2020-01-17 | 2:08 | 50.083
2020-01-17 | 2:08 | 50.081
2020-01-17 | 2:08 | 50.078
2020-01-17 | 2:08 | 50.077
2020-01-17 | 2:08 | 50.079
2020-01-17 | 2:08 | 50.081
2020-01-17 | 2:08 | 50.08
2020-01-17 | 2:08 | 50.08
2020-01-17 | 2:08 | 50.081
2020-01-17 | 2:08 | 50.08
2020-01-17 | 2:08 | 50.085
2020-01-17 | 2:08 | 50.087
2020-01-17 | 2:08 | 50.086
2020-01-17 | 2:09 | 50.081
2020-01-17 | 2:09 | 50.076
2020-01-17 | 2:09 | 50.071
2020-01-17 | 2:09 | 50.066
2020-01-17 | 2:09 | 50.062
2020-01-17 | 2:09 | 50.059
2020-01-17 | 2:09 | 50.057
2020-01-17 | 2:09 | 50.057
2020-01-17 | 2:09 | 50.057
2020-01-17 | 2:09 | 50.056
2020-01-17 | 2:09 | 50.055
2020-01-17 | 2:09 | 50.054
2020-01-17 | 2:09 | 50.056
2020-01-17 | 2:09 | 50.056
2020-01-17 | 2:09 | 50.057
2020-01-17 | 2:09 | 50.057
2020-01-17 | 2:09 | 50.056
2020-01-17 | 2:09 | 50.056
2020-01-17 | 2:09 | 50.056
2020-01-17 | 2:09 | 50.057
2020-01-17 | 2:09 | 50.058
2020-01-17 | 2:09 | 50.059
2020-01-17 | 2:09 | 50.062
2020-01-17 | 2:09 | 50.065
2020-01-17 | 2:09 | 50.065
2020-01-17 | 2:09 | 50.064
2020-01-17 | 2:09 | 50.066
2020-01-17 | 2:09 | 50.066
2020-01-17 | 2:09 | 50.065
2020-01-17 | 2:09 | 50.063
2020-01-17 | 2:09 | 50.063
2020-01-17 | 2:09 | 50.064
2020-01-17 | 2:09 | 50.065
2020-01-17 | 2:09 | 50.064
2020-01-17 | 2:09 | 50.063
2020-01-17 | 2:09 | 50.062
2020-01-17 | 2:09 | 50.064
2020-01-17 | 2:09 | 50.065
2020-01-17 | 2:09 | 50.067
2020-01-17 | 2:09 | 50.068
2020-01-17 | 2:09 | 50.071
2020-01-17 | 2:09 | 50.07
2020-01-17 | 2:09 | 50.072
2020-01-17 | 2:09 | 50.069
2020-01-17 | 2:09 | 50.074
2020-01-17 | 2:09 | 50.078
2020-01-17 | 2:09 | 50.084
2020-01-17 | 2:09 | 50.085
2020-01-17 | 2:09 | 50.083
2020-01-17 | 2:09 | 50.078
2020-01-17 | 2:09 | 50.073
2020-01-17 | 2:09 | 50.068
2020-01-17 | 2:09 | 50.066
2020-01-17 | 2:09 | 50.062
2020-01-17 | 2:09 | 50.059
2020-01-17 | 2:09 | 50.059
2020-01-17 | 2:09 | 50.059
2020-01-17 | 2:09 | 50.06
2020-01-17 | 2:09 | 50.06
2020-01-17 | 2:10 | 50.064
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.068
2020-01-17 | 2:10 | 50.071
2020-01-17 | 2:10 | 50.071
2020-01-17 | 2:10 | 50.069
2020-01-17 | 2:10 | 50.071
2020-01-17 | 2:10 | 50.074
2020-01-17 | 2:10 | 50.076
2020-01-17 | 2:10 | 50.077
2020-01-17 | 2:10 | 50.079
2020-01-17 | 2:10 | 50.08
2020-01-17 | 2:10 | 50.078
2020-01-17 | 2:10 | 50.074
2020-01-17 | 2:10 | 50.072
2020-01-17 | 2:10 | 50.07
2020-01-17 | 2:10 | 50.067
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.067
2020-01-17 | 2:10 | 50.069
2020-01-17 | 2:10 | 50.069
2020-01-17 | 2:10 | 50.069
2020-01-17 | 2:10 | 50.071
2020-01-17 | 2:10 | 50.071
2020-01-17 | 2:10 | 50.068
2020-01-17 | 2:10 | 50.068
2020-01-17 | 2:10 | 50.068
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.063
2020-01-17 | 2:10 | 50.065
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.062
2020-01-17 | 2:10 | 50.06
2020-01-17 | 2:10 | 50.061
2020-01-17 | 2:10 | 50.06
2020-01-17 | 2:10 | 50.058
2020-01-17 | 2:10 | 50.054
2020-01-17 | 2:10 | 50.055
2020-01-17 | 2:10 | 50.056
2020-01-17 | 2:10 | 50.056
2020-01-17 | 2:10 | 50.056
2020-01-17 | 2:10 | 50.06
2020-01-17 | 2:10 | 50.06
2020-01-17 | 2:10 | 50.06
2020-01-17 | 2:10 | 50.059
2020-01-17 | 2:10 | 50.06
2020-01-17 | 2:10 | 50.061
2020-01-17 | 2:10 | 50.061
2020-01-17 | 2:10 | 50.062
2020-01-17 | 2:10 | 50.065
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.067
2020-01-17 | 2:10 | 50.068
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.066
2020-01-17 | 2:10 | 50.069
2020-01-17 | 2:10 | 50.067
2020-01-17 | 2:10 | 50.068
2020-01-17 | 2:10 | 50.071
2020-01-17 | 2:11 | 50.071
2020-01-17 | 2:11 | 50.071
2020-01-17 | 2:11 | 50.072
2020-01-17 | 2:11 | 50.072
2020-01-17 | 2:11 | 50.071
2020-01-17 | 2:11 | 50.073
2020-01-17 | 2:11 | 50.075
2020-01-17 | 2:11 | 50.075
2020-01-17 | 2:11 | 50.079
2020-01-17 | 2:11 | 50.083
2020-01-17 | 2:11 | 50.083
2020-01-17 | 2:11 | 50.085
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.089
2020-01-17 | 2:11 | 50.089
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.09
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.085
2020-01-17 | 2:11 | 50.084
2020-01-17 | 2:11 | 50.081
2020-01-17 | 2:11 | 50.08
2020-01-17 | 2:11 | 50.078
2020-01-17 | 2:11 | 50.077
2020-01-17 | 2:11 | 50.077
2020-01-17 | 2:11 | 50.081
2020-01-17 | 2:11 | 50.081
2020-01-17 | 2:11 | 50.082
2020-01-17 | 2:11 | 50.081
2020-01-17 | 2:11 | 50.081
2020-01-17 | 2:11 | 50.081
2020-01-17 | 2:11 | 50.083
2020-01-17 | 2:11 | 50.084
2020-01-17 | 2:11 | 50.084
2020-01-17 | 2:11 | 50.084
2020-01-17 | 2:11 | 50.086
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.091
2020-01-17 | 2:11 | 50.091
2020-01-17 | 2:11 | 50.089
2020-01-17 | 2:11 | 50.092
2020-01-17 | 2:11 | 50.092
2020-01-17 | 2:11 | 50.091
2020-01-17 | 2:11 | 50.09
2020-01-17 | 2:11 | 50.09
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.086
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.088
2020-01-17 | 2:11 | 50.087
2020-01-17 | 2:11 | 50.089
2020-01-17 | 2:11 | 50.09
2020-01-17 | 2:11 | 50.089
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.089
2020-01-17 | 2:12 | 50.09
2020-01-17 | 2:12 | 50.092
2020-01-17 | 2:12 | 50.093
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.09
2020-01-17 | 2:12 | 50.092
2020-01-17 | 2:12 | 50.09
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.092
2020-01-17 | 2:12 | 50.094
2020-01-17 | 2:12 | 50.096
2020-01-17 | 2:12 | 50.095
2020-01-17 | 2:12 | 50.096
2020-01-17 | 2:12 | 50.095
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.096
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.101
2020-01-17 | 2:12 | 50.101
2020-01-17 | 2:12 | 50.101
2020-01-17 | 2:12 | 50.099
2020-01-17 | 2:12 | 50.099
2020-01-17 | 2:12 | 50.099
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.094
2020-01-17 | 2:12 | 50.093
2020-01-17 | 2:12 | 50.092
2020-01-17 | 2:12 | 50.09
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.091
2020-01-17 | 2:12 | 50.093
2020-01-17 | 2:12 | 50.094
2020-01-17 | 2:12 | 50.096
2020-01-17 | 2:12 | 50.095
2020-01-17 | 2:12 | 50.096
2020-01-17 | 2:12 | 50.098
2020-01-17 | 2:12 | 50.099
2020-01-17 | 2:12 | 50.098
2020-01-17 | 2:12 | 50.1
2020-01-17 | 2:12 | 50.103
2020-01-17 | 2:12 | 50.103
2020-01-17 | 2:12 | 50.101
2020-01-17 | 2:12 | 50.102
2020-01-17 | 2:12 | 50.1
2020-01-17 | 2:12 | 50.099
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:12 | 50.098
2020-01-17 | 2:12 | 50.097
2020-01-17 | 2:13 | 50.097
2020-01-17 | 2:13 | 50.097
2020-01-17 | 2:13 | 50.097
2020-01-17 | 2:13 | 50.097
2020-01-17 | 2:13 | 50.096
2020-01-17 | 2:13 | 50.097
2020-01-17 | 2:13 | 50.098
2020-01-17 | 2:13 | 50.1
2020-01-17 | 2:13 | 50.098
2020-01-17 | 2:13 | 50.101
2020-01-17 | 2:13 | 50.1
2020-01-17 | 2:13 | 50.1
2020-01-17 | 2:13 | 50.101
2020-01-17 | 2:13 | 50.103
2020-01-17 | 2:13 | 50.103
2020-01-17 | 2:13 | 50.104
2020-01-17 | 2:13 | 50.106
2020-01-17 | 2:13 | 50.107
2020-01-17 | 2:13 | 50.104
2020-01-17 | 2:13 | 50.103
2020-01-17 | 2:13 | 50.104
2020-01-17 | 2:13 | 50.102
2020-01-17 | 2:13 | 50.1
2020-01-17 | 2:13 | 50.099
2020-01-17 | 2:13 | 50.097
2020-01-17 | 2:13 | 50.094
2020-01-17 | 2:13 | 50.091
2020-01-17 | 2:13 | 50.089
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.078
2020-01-17 | 2:13 | 50.077
2020-01-17 | 2:13 | 50.076
2020-01-17 | 2:13 | 50.075
2020-01-17 | 2:13 | 50.075
2020-01-17 | 2:13 | 50.079
2020-01-17 | 2:13 | 50.081
2020-01-17 | 2:13 | 50.081
2020-01-17 | 2:13 | 50.082
2020-01-17 | 2:13 | 50.084
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.084
2020-01-17 | 2:13 | 50.081
2020-01-17 | 2:13 | 50.079
2020-01-17 | 2:13 | 50.079
2020-01-17 | 2:13 | 50.08
2020-01-17 | 2:13 | 50.078
2020-01-17 | 2:13 | 50.078
2020-01-17 | 2:13 | 50.078
2020-01-17 | 2:13 | 50.08
2020-01-17 | 2:13 | 50.08
2020-01-17 | 2:13 | 50.081
2020-01-17 | 2:13 | 50.084
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.084
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.085
2020-01-17 | 2:13 | 50.084
2020-01-17 | 2:14 | 50.083
2020-01-17 | 2:14 | 50.086
2020-01-17 | 2:14 | 50.084
2020-01-17 | 2:14 | 50.082
2020-01-17 | 2:14 | 50.081
2020-01-17 | 2:14 | 50.083
2020-01-17 | 2:14 | 50.081
2020-01-17 | 2:14 | 50.083
2020-01-17 | 2:14 | 50.085
2020-01-17 | 2:14 | 50.087
2020-01-17 | 2:14 | 50.087
2020-01-17 | 2:14 | 50.088
2020-01-17 | 2:14 | 50.09
2020-01-17 | 2:14 | 50.091
2020-01-17 | 2:14 | 50.092
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.097
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.097
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.096
2020-01-17 | 2:14 | 50.094
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.096
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.099
2020-01-17 | 2:14 | 50.101
2020-01-17 | 2:14 | 50.101
2020-01-17 | 2:14 | 50.1
2020-01-17 | 2:14 | 50.099
2020-01-17 | 2:14 | 50.1
2020-01-17 | 2:14 | 50.099
2020-01-17 | 2:14 | 50.097
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.097
2020-01-17 | 2:14 | 50.096
2020-01-17 | 2:14 | 50.092
2020-01-17 | 2:14 | 50.092
2020-01-17 | 2:14 | 50.092
2020-01-17 | 2:14 | 50.091
2020-01-17 | 2:14 | 50.089
2020-01-17 | 2:14 | 50.089
2020-01-17 | 2:14 | 50.091
2020-01-17 | 2:14 | 50.091
2020-01-17 | 2:14 | 50.091
2020-01-17 | 2:14 | 50.093
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.095
2020-01-17 | 2:14 | 50.097
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.098
2020-01-17 | 2:14 | 50.1
2020-01-17 | 2:14 | 50.102
2020-01-17 | 2:14 | 50.104
2020-01-17 | 2:14 | 50.101
2020-01-17 | 2:14 | 50.1
2020-01-17 | 2:15 | 50.1
2020-01-17 | 2:15 | 50.099
2020-01-17 | 2:15 | 50.097
2020-01-17 | 2:15 | 50.097
2020-01-17 | 2:15 | 50.098
2020-01-17 | 2:15 | 50.1
2020-01-17 | 2:15 | 50.1
2020-01-17 | 2:15 | 50.103
2020-01-17 | 2:15 | 50.104
2020-01-17 | 2:15 | 50.103
2020-01-17 | 2:15 | 50.107
2020-01-17 | 2:15 | 50.109
2020-01-17 | 2:15 | 50.108
2020-01-17 | 2:15 | 50.111
2020-01-17 | 2:15 | 50.111
2020-01-17 | 2:15 | 50.112
2020-01-17 | 2:15 | 50.11
2020-01-17 | 2:15 | 50.106
2020-01-17 | 2:15 | 50.101
2020-01-17 | 2:15 | 50.09
2020-01-17 | 2:15 | 50.077
2020-01-17 | 2:15 | 50.069
2020-01-17 | 2:15 | 50.059
2020-01-17 | 2:15 | 50.052
2020-01-17 | 2:15 | 50.049
2020-01-17 | 2:15 | 50.044
2020-01-17 | 2:15 | 50.041
2020-01-17 | 2:15 | 50.04
2020-01-17 | 2:15 | 50.038
2020-01-17 | 2:15 | 50.039
2020-01-17 | 2:15 | 50.038
2020-01-17 | 2:15 | 50.036
2020-01-17 | 2:15 | 50.042
2020-01-17 | 2:15 | 50.043
2020-01-17 | 2:15 | 50.045
2020-01-17 | 2:15 | 50.05
2020-01-17 | 2:15 | 50.051
2020-01-17 | 2:15 | 50.053
2020-01-17 | 2:15 | 50.054
2020-01-17 | 2:15 | 50.052
2020-01-17 | 2:15 | 50.053
2020-01-17 | 2:15 | 50.053
2020-01-17 | 2:15 | 50.05
2020-01-17 | 2:15 | 50.049
2020-01-17 | 2:15 | 50.049
2020-01-17 | 2:15 | 50.047
2020-01-17 | 2:15 | 50.049
2020-01-17 | 2:15 | 50.047
2020-01-17 | 2:15 | 50.045
2020-01-17 | 2:15 | 50.046
2020-01-17 | 2:15 | 50.044
2020-01-17 | 2:15 | 50.04
2020-01-17 | 2:15 | 50.04
2020-01-17 | 2:15 | 50.043
2020-01-17 | 2:15 | 50.041
2020-01-17 | 2:15 | 50.037
2020-01-17 | 2:15 | 50.035
2020-01-17 | 2:15 | 50.031
2020-01-17 | 2:15 | 50.027
2020-01-17 | 2:16 | 50.025
2020-01-17 | 2:16 | 50.025
2020-01-17 | 2:16 | 50.025
2020-01-17 | 2:16 | 50.027
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.027
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.038
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.039
2020-01-17 | 2:16 | 50.038
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.025
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.027
2020-01-17 | 2:16 | 50.028
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.033
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.035
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.038
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.03
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.027
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.022
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.026
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.027
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.02
2020-01-17 | 2:17 | 50.019
2020-01-17 | 2:17 | 50.018
2020-01-17 | 2:17 | 50.019
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.03
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.033
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.026
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.022
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.02
2020-01-17 | 2:17 | 50.017
2020-01-17 | 2:18 | 50.015
2020-01-17 | 2:18 | 50.014
2020-01-17 | 2:18 | 50.011
2020-01-17 | 2:18 | 50.01
2020-01-17 | 2:18 | 50.007
2020-01-17 | 2:18 | 50.002
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.992
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.988
2020-01-17 | 2:18 | 49.987
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.987
2020-01-17 | 2:18 | 49.988
2020-01-17 | 2:18 | 49.991
2020-01-17 | 2:18 | 49.99
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.99
2020-01-17 | 2:18 | 49.991
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.995
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.995
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.998
2020-01-17 | 2:18 | 49.997
2020-01-17 | 2:18 | 49.999

## Event 20200122-1
In UTC
Date | Time | Freq
2020-01-22 | 15:21 | 49.969
2020-01-22 | 15:21 | 49.968
2020-01-22 | 15:21 | 49.966
2020-01-22 | 15:21 | 49.967
2020-01-22 | 15:21 | 49.968
2020-01-22 | 15:21 | 49.968
2020-01-22 | 15:21 | 49.967
2020-01-22 | 15:21 | 49.964
2020-01-22 | 15:21 | 49.961
2020-01-22 | 15:21 | 49.96
2020-01-22 | 15:21 | 49.96
2020-01-22 | 15:21 | 49.958
2020-01-22 | 15:21 | 49.957
2020-01-22 | 15:21 | 49.956
2020-01-22 | 15:21 | 49.955
2020-01-22 | 15:21 | 49.957
2020-01-22 | 15:21 | 49.959
2020-01-22 | 15:21 | 49.96
2020-01-22 | 15:21 | 49.961
2020-01-22 | 15:21 | 49.962
2020-01-22 | 15:21 | 49.963
2020-01-22 | 15:21 | 49.965
2020-01-22 | 15:21 | 49.966
2020-01-22 | 15:21 | 49.967
2020-01-22 | 15:21 | 49.968
2020-01-22 | 15:21 | 49.966
2020-01-22 | 15:21 | 49.966
2020-01-22 | 15:21 | 49.967
2020-01-22 | 15:21 | 49.967
2020-01-22 | 15:21 | 49.967
2020-01-22 | 15:22 | 49.966
2020-01-22 | 15:22 | 49.964
2020-01-22 | 15:22 | 49.962
2020-01-22 | 15:22 | 49.964
2020-01-22 | 15:22 | 49.964
2020-01-22 | 15:22 | 49.963
2020-01-22 | 15:22 | 49.963
2020-01-22 | 15:22 | 49.963
2020-01-22 | 15:22 | 49.963
2020-01-22 | 15:22 | 49.965
2020-01-22 | 15:22 | 49.966
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.968
2020-01-22 | 15:22 | 49.968
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.965
2020-01-22 | 15:22 | 49.964
2020-01-22 | 15:22 | 49.964
2020-01-22 | 15:22 | 49.966
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.968
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.968
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.969
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.971
2020-01-22 | 15:22 | 49.969
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.965
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.971
2020-01-22 | 15:22 | 49.969
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.971
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.97
2020-01-22 | 15:22 | 49.966
2020-01-22 | 15:22 | 49.965
2020-01-22 | 15:22 | 49.967
2020-01-22 | 15:22 | 49.969
2020-01-22 | 15:22 | 49.971
2020-01-22 | 15:22 | 49.974
2020-01-22 | 15:22 | 49.974
2020-01-22 | 15:22 | 49.978
2020-01-22 | 15:22 | 49.982
2020-01-22 | 15:22 | 49.982
2020-01-22 | 15:22 | 49.979
2020-01-22 | 15:22 | 49.978
2020-01-22 | 15:22 | 49.976
2020-01-22 | 15:23 | 49.972
2020-01-22 | 15:23 | 49.969
2020-01-22 | 15:23 | 49.968
2020-01-22 | 15:23 | 49.966
2020-01-22 | 15:23 | 49.962
2020-01-22 | 15:23 | 49.961
2020-01-22 | 15:23 | 49.965
2020-01-22 | 15:23 | 49.97
2020-01-22 | 15:23 | 49.97
2020-01-22 | 15:23 | 49.975
2020-01-22 | 15:23 | 49.979
2020-01-22 | 15:23 | 49.982
2020-01-22 | 15:23 | 49.984
2020-01-22 | 15:23 | 49.987
2020-01-22 | 15:23 | 49.988
2020-01-22 | 15:23 | 49.988
2020-01-22 | 15:23 | 49.97
2020-01-22 | 15:23 | 49.957
2020-01-22 | 15:23 | 49.943
2020-01-22 | 15:23 | 49.935
2020-01-22 | 15:23 | 49.925
2020-01-22 | 15:23 | 49.916
2020-01-22 | 15:23 | 49.907
2020-01-22 | 15:23 | 49.902
2020-01-22 | 15:23 | 49.897
2020-01-22 | 15:23 | 49.894
2020-01-22 | 15:23 | 49.891
2020-01-22 | 15:23 | 49.89
2020-01-22 | 15:23 | 49.891
2020-01-22 | 15:23 | 49.891
2020-01-22 | 15:23 | 49.892
2020-01-22 | 15:23 | 49.894
2020-01-22 | 15:23 | 49.896
2020-01-22 | 15:23 | 49.898
2020-01-22 | 15:23 | 49.898
2020-01-22 | 15:23 | 49.899
2020-01-22 | 15:23 | 49.901
2020-01-22 | 15:23 | 49.902
2020-01-22 | 15:23 | 49.905
2020-01-22 | 15:23 | 49.905
2020-01-22 | 15:23 | 49.906
2020-01-22 | 15:23 | 49.904
2020-01-22 | 15:23 | 49.904
2020-01-22 | 15:23 | 49.903
2020-01-22 | 15:23 | 49.906
2020-01-22 | 15:23 | 49.907
2020-01-22 | 15:23 | 49.908
2020-01-22 | 15:23 | 49.908
2020-01-22 | 15:23 | 49.906
2020-01-22 | 15:23 | 49.906
2020-01-22 | 15:23 | 49.906
2020-01-22 | 15:23 | 49.908
2020-01-22 | 15:23 | 49.908
2020-01-22 | 15:23 | 49.908
2020-01-22 | 15:23 | 49.908
2020-01-22 | 15:23 | 49.907
2020-01-22 | 15:23 | 49.906
2020-01-22 | 15:23 | 49.903
2020-01-22 | 15:23 | 49.903
2020-01-22 | 15:24 | 49.902
2020-01-22 | 15:24 | 49.9
2020-01-22 | 15:24 | 49.9
2020-01-22 | 15:24 | 49.899
2020-01-22 | 15:24 | 49.898
2020-01-22 | 15:24 | 49.899
2020-01-22 | 15:24 | 49.901
2020-01-22 | 15:24 | 49.903
2020-01-22 | 15:24 | 49.905
2020-01-22 | 15:24 | 49.906
2020-01-22 | 15:24 | 49.909
2020-01-22 | 15:24 | 49.912
2020-01-22 | 15:24 | 49.915
2020-01-22 | 15:24 | 49.917
2020-01-22 | 15:24 | 49.923
2020-01-22 | 15:24 | 49.924
2020-01-22 | 15:24 | 49.93
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.94
2020-01-22 | 15:24 | 49.942
2020-01-22 | 15:24 | 49.945
2020-01-22 | 15:24 | 49.945
2020-01-22 | 15:24 | 49.949
2020-01-22 | 15:24 | 49.951
2020-01-22 | 15:24 | 49.952
2020-01-22 | 15:24 | 49.953
2020-01-22 | 15:24 | 49.953
2020-01-22 | 15:24 | 49.952
2020-01-22 | 15:24 | 49.952
2020-01-22 | 15:24 | 49.95
2020-01-22 | 15:24 | 49.947
2020-01-22 | 15:24 | 49.944
2020-01-22 | 15:24 | 49.942
2020-01-22 | 15:24 | 49.94
2020-01-22 | 15:24 | 49.94
2020-01-22 | 15:24 | 49.938
2020-01-22 | 15:24 | 49.937
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.933
2020-01-22 | 15:24 | 49.933
2020-01-22 | 15:24 | 49.933
2020-01-22 | 15:24 | 49.933
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.934
2020-01-22 | 15:24 | 49.933
2020-01-22 | 15:24 | 49.932
2020-01-22 | 15:24 | 49.93
2020-01-22 | 15:24 | 49.929
2020-01-22 | 15:24 | 49.93
2020-01-22 | 15:24 | 49.93
2020-01-22 | 15:24 | 49.929
2020-01-22 | 15:24 | 49.927
2020-01-22 | 15:24 | 49.926
2020-01-22 | 15:24 | 49.924
2020-01-22 | 15:24 | 49.921
2020-01-22 | 15:24 | 49.918
2020-01-22 | 15:25 | 49.917
2020-01-22 | 15:25 | 49.917
2020-01-22 | 15:25 | 49.917
2020-01-22 | 15:25 | 49.919
2020-01-22 | 15:25 | 49.92
2020-01-22 | 15:25 | 49.92
2020-01-22 | 15:25 | 49.919
2020-01-22 | 15:25 | 49.918
2020-01-22 | 15:25 | 49.92
2020-01-22 | 15:25 | 49.918
2020-01-22 | 15:25 | 49.918
2020-01-22 | 15:25 | 49.916
2020-01-22 | 15:25 | 49.915
2020-01-22 | 15:25 | 49.916
2020-01-22 | 15:25 | 49.919
2020-01-22 | 15:25 | 49.925
2020-01-22 | 15:25 | 49.929
2020-01-22 | 15:25 | 49.93
2020-01-22 | 15:25 | 49.933
2020-01-22 | 15:25 | 49.937
2020-01-22 | 15:25 | 49.94
2020-01-22 | 15:25 | 49.943
2020-01-22 | 15:25 | 49.944
2020-01-22 | 15:25 | 49.944
2020-01-22 | 15:25 | 49.941
2020-01-22 | 15:25 | 49.942
2020-01-22 | 15:25 | 49.941
2020-01-22 | 15:25 | 49.939
2020-01-22 | 15:25 | 49.937
2020-01-22 | 15:25 | 49.935
2020-01-22 | 15:25 | 49.933
2020-01-22 | 15:25 | 49.932
2020-01-22 | 15:25 | 49.932
2020-01-22 | 15:25 | 49.931
2020-01-22 | 15:25 | 49.932
2020-01-22 | 15:25 | 49.932
2020-01-22 | 15:25 | 49.933
2020-01-22 | 15:25 | 49.931
2020-01-22 | 15:25 | 49.933
2020-01-22 | 15:25 | 49.935
2020-01-22 | 15:25 | 49.938
2020-01-22 | 15:25 | 49.937
2020-01-22 | 15:25 | 49.933
2020-01-22 | 15:25 | 49.932
2020-01-22 | 15:25 | 49.93
2020-01-22 | 15:25 | 49.928
2020-01-22 | 15:25 | 49.928
2020-01-22 | 15:25 | 49.927
2020-01-22 | 15:25 | 49.927
2020-01-22 | 15:25 | 49.929
2020-01-22 | 15:25 | 49.929
2020-01-22 | 15:25 | 49.925
2020-01-22 | 15:25 | 49.923
2020-01-22 | 15:25 | 49.922
2020-01-22 | 15:25 | 49.921
2020-01-22 | 15:25 | 49.92
2020-01-22 | 15:25 | 49.917
2020-01-22 | 15:25 | 49.914
2020-01-22 | 15:25 | 49.914
2020-01-22 | 15:26 | 49.915
2020-01-22 | 15:26 | 49.915
2020-01-22 | 15:26 | 49.914
2020-01-22 | 15:26 | 49.913
2020-01-22 | 15:26 | 49.912
2020-01-22 | 15:26 | 49.912
2020-01-22 | 15:26 | 49.909
2020-01-22 | 15:26 | 49.907
2020-01-22 | 15:26 | 49.907
2020-01-22 | 15:26 | 49.908
2020-01-22 | 15:26 | 49.91
2020-01-22 | 15:26 | 49.912
2020-01-22 | 15:26 | 49.913
2020-01-22 | 15:26 | 49.916
2020-01-22 | 15:26 | 49.917
2020-01-22 | 15:26 | 49.92
2020-01-22 | 15:26 | 49.921
2020-01-22 | 15:26 | 49.921
2020-01-22 | 15:26 | 49.921
2020-01-22 | 15:26 | 49.923
2020-01-22 | 15:26 | 49.924
2020-01-22 | 15:26 | 49.924
2020-01-22 | 15:26 | 49.924
2020-01-22 | 15:26 | 49.923
2020-01-22 | 15:26 | 49.923
2020-01-22 | 15:26 | 49.925
2020-01-22 | 15:26 | 49.927
2020-01-22 | 15:26 | 49.928
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.928
2020-01-22 | 15:26 | 49.928
2020-01-22 | 15:26 | 49.928
2020-01-22 | 15:26 | 49.929
2020-01-22 | 15:26 | 49.928
2020-01-22 | 15:26 | 49.927
2020-01-22 | 15:26 | 49.925
2020-01-22 | 15:26 | 49.923
2020-01-22 | 15:26 | 49.921
2020-01-22 | 15:26 | 49.919
2020-01-22 | 15:26 | 49.915
2020-01-22 | 15:26 | 49.911
2020-01-22 | 15:26 | 49.907
2020-01-22 | 15:26 | 49.904
2020-01-22 | 15:26 | 49.902
2020-01-22 | 15:26 | 49.9
2020-01-22 | 15:26 | 49.899
2020-01-22 | 15:26 | 49.897
2020-01-22 | 15:26 | 49.897
2020-01-22 | 15:26 | 49.896
2020-01-22 | 15:26 | 49.897
2020-01-22 | 15:26 | 49.896
2020-01-22 | 15:26 | 49.897
2020-01-22 | 15:26 | 49.899
2020-01-22 | 15:26 | 49.899
2020-01-22 | 15:26 | 49.901
2020-01-22 | 15:26 | 49.902
2020-01-22 | 15:27 | 49.904
2020-01-22 | 15:27 | 49.905
2020-01-22 | 15:27 | 49.905
2020-01-22 | 15:27 | 49.904
2020-01-22 | 15:27 | 49.903
2020-01-22 | 15:27 | 49.902
2020-01-22 | 15:27 | 49.902
2020-01-22 | 15:27 | 49.902
2020-01-22 | 15:27 | 49.905
2020-01-22 | 15:27 | 49.909
2020-01-22 | 15:27 | 49.911
2020-01-22 | 15:27 | 49.915
2020-01-22 | 15:27 | 49.916
2020-01-22 | 15:27 | 49.918
2020-01-22 | 15:27 | 49.922
2020-01-22 | 15:27 | 49.921
2020-01-22 | 15:27 | 49.922
2020-01-22 | 15:27 | 49.923
2020-01-22 | 15:27 | 49.925
2020-01-22 | 15:27 | 49.927
2020-01-22 | 15:27 | 49.931
2020-01-22 | 15:27 | 49.934
2020-01-22 | 15:27 | 49.935
2020-01-22 | 15:27 | 49.937
2020-01-22 | 15:27 | 49.937
2020-01-22 | 15:27 | 49.939
2020-01-22 | 15:27 | 49.937
2020-01-22 | 15:27 | 49.936
2020-01-22 | 15:27 | 49.935
2020-01-22 | 15:27 | 49.934
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.932
2020-01-22 | 15:27 | 49.931
2020-01-22 | 15:27 | 49.932
2020-01-22 | 15:27 | 49.932
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.934
2020-01-22 | 15:27 | 49.935
2020-01-22 | 15:27 | 49.937
2020-01-22 | 15:27 | 49.937
2020-01-22 | 15:27 | 49.937
2020-01-22 | 15:27 | 49.939
2020-01-22 | 15:27 | 49.94
2020-01-22 | 15:27 | 49.938
2020-01-22 | 15:27 | 49.935
2020-01-22 | 15:27 | 49.934
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.931
2020-01-22 | 15:27 | 49.931
2020-01-22 | 15:27 | 49.931
2020-01-22 | 15:27 | 49.93
2020-01-22 | 15:27 | 49.931
2020-01-22 | 15:27 | 49.932
2020-01-22 | 15:27 | 49.933
2020-01-22 | 15:27 | 49.934
2020-01-22 | 15:28 | 49.935
2020-01-22 | 15:28 | 49.937
2020-01-22 | 15:28 | 49.94
2020-01-22 | 15:28 | 49.942
2020-01-22 | 15:28 | 49.941
2020-01-22 | 15:28 | 49.941
2020-01-22 | 15:28 | 49.941
2020-01-22 | 15:28 | 49.941
2020-01-22 | 15:28 | 49.941
2020-01-22 | 15:28 | 49.939
2020-01-22 | 15:28 | 49.936
2020-01-22 | 15:28 | 49.933
2020-01-22 | 15:28 | 49.932
2020-01-22 | 15:28 | 49.93
2020-01-22 | 15:28 | 49.929
2020-01-22 | 15:28 | 49.928
2020-01-22 | 15:28 | 49.927
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.924
2020-01-22 | 15:28 | 49.923
2020-01-22 | 15:28 | 49.923
2020-01-22 | 15:28 | 49.923
2020-01-22 | 15:28 | 49.924
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.926
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.924
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.927
2020-01-22 | 15:28 | 49.928
2020-01-22 | 15:28 | 49.929
2020-01-22 | 15:28 | 49.93
2020-01-22 | 15:28 | 49.932
2020-01-22 | 15:28 | 49.933
2020-01-22 | 15:28 | 49.933
2020-01-22 | 15:28 | 49.933
2020-01-22 | 15:28 | 49.933
2020-01-22 | 15:28 | 49.93
2020-01-22 | 15:28 | 49.929
2020-01-22 | 15:28 | 49.929
2020-01-22 | 15:28 | 49.93
2020-01-22 | 15:28 | 49.929
2020-01-22 | 15:28 | 49.927
2020-01-22 | 15:28 | 49.926
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.923
2020-01-22 | 15:28 | 49.923
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.925
2020-01-22 | 15:28 | 49.923
2020-01-22 | 15:28 | 49.922
2020-01-22 | 15:28 | 49.922
2020-01-22 | 15:28 | 49.922
2020-01-22 | 15:28 | 49.922
2020-01-22 | 15:28 | 49.922
2020-01-22 | 15:28 | 49.922
2020-01-22 | 15:28 | 49.919
2020-01-22 | 15:28 | 49.916
2020-01-22 | 15:28 | 49.914
2020-01-22 | 15:29 | 49.913
2020-01-22 | 15:29 | 49.914
2020-01-22 | 15:29 | 49.912
2020-01-22 | 15:29 | 49.91
2020-01-22 | 15:29 | 49.911
2020-01-22 | 15:29 | 49.91
2020-01-22 | 15:29 | 49.908
2020-01-22 | 15:29 | 49.907
2020-01-22 | 15:29 | 49.905
2020-01-22 | 15:29 | 49.904
2020-01-22 | 15:29 | 49.904
2020-01-22 | 15:29 | 49.903
2020-01-22 | 15:29 | 49.9
2020-01-22 | 15:29 | 49.898
2020-01-22 | 15:29 | 49.896
2020-01-22 | 15:29 | 49.894
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.892
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.894
2020-01-22 | 15:29 | 49.894
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.894
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.894
2020-01-22 | 15:29 | 49.895
2020-01-22 | 15:29 | 49.897
2020-01-22 | 15:29 | 49.898
2020-01-22 | 15:29 | 49.898
2020-01-22 | 15:29 | 49.901
2020-01-22 | 15:29 | 49.903
2020-01-22 | 15:29 | 49.906
2020-01-22 | 15:29 | 49.907
2020-01-22 | 15:29 | 49.908
2020-01-22 | 15:29 | 49.908
2020-01-22 | 15:29 | 49.904
2020-01-22 | 15:29 | 49.902
2020-01-22 | 15:29 | 49.899
2020-01-22 | 15:29 | 49.898
2020-01-22 | 15:29 | 49.896
2020-01-22 | 15:29 | 49.895
2020-01-22 | 15:29 | 49.893
2020-01-22 | 15:29 | 49.896
2020-01-22 | 15:29 | 49.901
2020-01-22 | 15:29 | 49.908
2020-01-22 | 15:29 | 49.914
2020-01-22 | 15:29 | 49.92
2020-01-22 | 15:29 | 49.924
2020-01-22 | 15:29 | 49.928
2020-01-22 | 15:29 | 49.934
2020-01-22 | 15:29 | 49.937
2020-01-22 | 15:29 | 49.94
2020-01-22 | 15:29 | 49.94
2020-01-22 | 15:29 | 49.94
2020-01-22 | 15:29 | 49.94
2020-01-22 | 15:30 | 49.941
2020-01-22 | 15:30 | 49.943
2020-01-22 | 15:30 | 49.943
2020-01-22 | 15:30 | 49.943
2020-01-22 | 15:30 | 49.945
2020-01-22 | 15:30 | 49.947
2020-01-22 | 15:30 | 49.948
2020-01-22 | 15:30 | 49.951
2020-01-22 | 15:30 | 49.953
2020-01-22 | 15:30 | 49.954
2020-01-22 | 15:30 | 49.955
2020-01-22 | 15:30 | 49.955
2020-01-22 | 15:30 | 49.957
2020-01-22 | 15:30 | 49.959
2020-01-22 | 15:30 | 49.961
2020-01-22 | 15:30 | 49.96
2020-01-22 | 15:30 | 49.959
2020-01-22 | 15:30 | 49.959
2020-01-22 | 15:30 | 49.96
2020-01-22 | 15:30 | 49.96
2020-01-22 | 15:30 | 49.961
2020-01-22 | 15:30 | 49.961
2020-01-22 | 15:30 | 49.96
2020-01-22 | 15:30 | 49.957
2020-01-22 | 15:30 | 49.957
2020-01-22 | 15:30 | 49.958
2020-01-22 | 15:30 | 49.96
2020-01-22 | 15:30 | 49.962
2020-01-22 | 15:30 | 49.965
2020-01-22 | 15:30 | 49.965
2020-01-22 | 15:30 | 49.962
2020-01-22 | 15:30 | 49.959
2020-01-22 | 15:30 | 49.957
2020-01-22 | 15:30 | 49.953
2020-01-22 | 15:30 | 49.952
2020-01-22 | 15:30 | 49.95
2020-01-22 | 15:30 | 49.95
2020-01-22 | 15:30 | 49.949
2020-01-22 | 15:30 | 49.949
2020-01-22 | 15:30 | 49.948
2020-01-22 | 15:30 | 49.949
2020-01-22 | 15:30 | 49.949
2020-01-22 | 15:30 | 49.952
2020-01-22 | 15:30 | 49.955
2020-01-22 | 15:30 | 49.96
2020-01-22 | 15:30 | 49.964
2020-01-22 | 15:30 | 49.967
2020-01-22 | 15:30 | 49.97
2020-01-22 | 15:30 | 49.973
2020-01-22 | 15:30 | 49.974
2020-01-22 | 15:30 | 49.978
2020-01-22 | 15:30 | 49.982
2020-01-22 | 15:30 | 49.985
2020-01-22 | 15:30 | 49.988
2020-01-22 | 15:30 | 49.991
2020-01-22 | 15:30 | 49.995
2020-01-22 | 15:30 | 50
2020-01-22 | 15:30 | 50.005
2020-01-22 | 15:30 | 50.01
2020-01-22 | 15:30 | 50.016
2020-01-22 | 15:30 | 50.02
2020-01-22 | 15:31 | 50.024
2020-01-22 | 15:31 | 50.028
2020-01-22 | 15:31 | 50.033
2020-01-22 | 15:31 | 50.037
2020-01-22 | 15:31 | 50.039
2020-01-22 | 15:31 | 50.04
2020-01-22 | 15:31 | 50.041
2020-01-22 | 15:31 | 50.041
2020-01-22 | 15:31 | 50.04
2020-01-22 | 15:31 | 50.039
2020-01-22 | 15:31 | 50.039
2020-01-22 | 15:31 | 50.039
2020-01-22 | 15:31 | 50.039
2020-01-22 | 15:31 | 50.038
2020-01-22 | 15:31 | 50.037
2020-01-22 | 15:31 | 50.037
2020-01-22 | 15:31 | 50.036
2020-01-22 | 15:31 | 50.037
2020-01-22 | 15:31 | 50.035
2020-01-22 | 15:31 | 50.032
2020-01-22 | 15:31 | 50.031
2020-01-22 | 15:31 | 50.029
2020-01-22 | 15:31 | 50.03
2020-01-22 | 15:31 | 50.028
2020-01-22 | 15:31 | 50.027
2020-01-22 | 15:31 | 50.026
2020-01-22 | 15:31 | 50.022
2020-01-22 | 15:31 | 50.02
2020-01-22 | 15:31 | 50.018
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.038
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.039
2020-01-17 | 2:16 | 50.038
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.025
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.027
2020-01-17 | 2:16 | 50.028
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.033
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.035
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.038
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.03
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.027
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.022
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.026
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.027
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.02
2020-01-17 | 2:17 | 50.019
2020-01-17 | 2:17 | 50.018
2020-01-17 | 2:17 | 50.019
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.03
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.033
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.026
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.022
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.02
2020-01-17 | 2:17 | 50.017
2020-01-17 | 2:18 | 50.015
2020-01-17 | 2:18 | 50.014
2020-01-17 | 2:18 | 50.011
2020-01-17 | 2:18 | 50.01
2020-01-17 | 2:18 | 50.007
2020-01-17 | 2:18 | 50.002
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.992
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.988
2020-01-17 | 2:18 | 49.987
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.987
2020-01-17 | 2:18 | 49.988
2020-01-17 | 2:18 | 49.991
2020-01-17 | 2:18 | 49.99
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.99
2020-01-17 | 2:18 | 49.991
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.995
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.995
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.998
2020-01-17 | 2:18 | 49.997
2020-01-17 | 2:18 | 49.999

## Event 20200122-2
In UTC
Date | Time | Freq
2020-01-22 | 20:14 | 50.066
2020-01-22 | 20:14 | 50.067
2020-01-22 | 20:14 | 50.066
2020-01-22 | 20:14 | 50.069
2020-01-22 | 20:14 | 50.071
2020-01-22 | 20:14 | 50.071
2020-01-22 | 20:14 | 50.075
2020-01-22 | 20:14 | 50.081
2020-01-22 | 20:14 | 50.084
2020-01-22 | 20:14 | 50.086
2020-01-22 | 20:14 | 50.089
2020-01-22 | 20:14 | 50.09
2020-01-22 | 20:14 | 50.089
2020-01-22 | 20:14 | 50.087
2020-01-22 | 20:14 | 50.087
2020-01-22 | 20:14 | 50.084
2020-01-22 | 20:14 | 50.081
2020-01-22 | 20:14 | 50.079
2020-01-22 | 20:14 | 50.078
2020-01-22 | 20:14 | 50.076
2020-01-22 | 20:14 | 50.074
2020-01-22 | 20:14 | 50.074
2020-01-22 | 20:14 | 50.075
2020-01-22 | 20:14 | 50.075
2020-01-22 | 20:14 | 50.074
2020-01-22 | 20:14 | 50.072
2020-01-22 | 20:14 | 50.071
2020-01-22 | 20:14 | 50.069
2020-01-22 | 20:14 | 50.064
2020-01-22 | 20:14 | 50.06
2020-01-22 | 20:14 | 50.058
2020-01-22 | 20:15 | 50.054
2020-01-22 | 20:15 | 50.05
2020-01-22 | 20:15 | 50.05
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.046
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.049
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.049
2020-01-22 | 20:15 | 50.049
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.049
2020-01-22 | 20:15 | 50.051
2020-01-22 | 20:15 | 50.052
2020-01-22 | 20:15 | 50.052
2020-01-22 | 20:15 | 50.051
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.044
2020-01-22 | 20:15 | 50.043
2020-01-22 | 20:15 | 50.043
2020-01-22 | 20:15 | 50.043
2020-01-22 | 20:15 | 50.045
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.048
2020-01-22 | 20:15 | 50.049
2020-01-22 | 20:15 | 50.053
2020-01-22 | 20:15 | 50.056
2020-01-22 | 20:15 | 50.057
2020-01-22 | 20:15 | 50.06
2020-01-22 | 20:15 | 50.061
2020-01-22 | 20:15 | 50.059
2020-01-22 | 20:15 | 50.059
2020-01-22 | 20:15 | 50.057
2020-01-22 | 20:15 | 50.053
2020-01-22 | 20:15 | 50.05
2020-01-22 | 20:15 | 50.05
2020-01-22 | 20:15 | 50.046
2020-01-22 | 20:15 | 50.046
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.045
2020-01-22 | 20:15 | 50.047
2020-01-22 | 20:15 | 50.046
2020-01-22 | 20:15 | 50.043
2020-01-22 | 20:15 | 50.041
2020-01-22 | 20:15 | 50.041
2020-01-22 | 20:15 | 50.039
2020-01-22 | 20:15 | 50.041
2020-01-22 | 20:15 | 50.04
2020-01-22 | 20:15 | 50.039
2020-01-22 | 20:15 | 50.039
2020-01-22 | 20:15 | 50.037
2020-01-22 | 20:15 | 50.038
2020-01-22 | 20:16 | 50.034
2020-01-22 | 20:16 | 50.031
2020-01-22 | 20:16 | 50.029
2020-01-22 | 20:16 | 50.026
2020-01-22 | 20:16 | 50.022
2020-01-22 | 20:16 | 50.021
2020-01-22 | 20:16 | 50.011
2020-01-22 | 20:16 | 50.001
2020-01-22 | 20:16 | 49.992
2020-01-22 | 20:16 | 49.982
2020-01-22 | 20:16 | 49.975
2020-01-22 | 20:16 | 49.968
2020-01-22 | 20:16 | 49.958
2020-01-22 | 20:16 | 49.952
2020-01-22 | 20:16 | 49.943
2020-01-22 | 20:16 | 49.936
2020-01-22 | 20:16 | 49.933
2020-01-22 | 20:16 | 49.927
2020-01-22 | 20:16 | 49.925
2020-01-22 | 20:16 | 49.923
2020-01-22 | 20:16 | 49.92
2020-01-22 | 20:16 | 49.921
2020-01-22 | 20:16 | 49.923
2020-01-22 | 20:16 | 49.925
2020-01-22 | 20:16 | 49.927
2020-01-22 | 20:16 | 49.927
2020-01-22 | 20:16 | 49.928
2020-01-22 | 20:16 | 49.926
2020-01-22 | 20:16 | 49.926
2020-01-22 | 20:16 | 49.926
2020-01-22 | 20:16 | 49.923
2020-01-22 | 20:16 | 49.921
2020-01-22 | 20:16 | 49.919
2020-01-22 | 20:16 | 49.918
2020-01-22 | 20:16 | 49.917
2020-01-22 | 20:16 | 49.916
2020-01-22 | 20:16 | 49.916
2020-01-22 | 20:16 | 49.918
2020-01-22 | 20:16 | 49.918
2020-01-22 | 20:16 | 49.924
2020-01-22 | 20:16 | 49.93
2020-01-22 | 20:16 | 49.935
2020-01-22 | 20:16 | 49.942
2020-01-22 | 20:16 | 49.944
2020-01-22 | 20:16 | 49.95
2020-01-22 | 20:16 | 49.952
2020-01-22 | 20:16 | 49.953
2020-01-22 | 20:16 | 49.956
2020-01-22 | 20:16 | 49.955
2020-01-22 | 20:16 | 49.957
2020-01-22 | 20:16 | 49.958
2020-01-22 | 20:16 | 49.956
2020-01-22 | 20:16 | 49.958
2020-01-22 | 20:16 | 49.956
2020-01-22 | 20:16 | 49.953
2020-01-22 | 20:16 | 49.955
2020-01-22 | 20:16 | 49.954
2020-01-22 | 20:16 | 49.953
2020-01-22 | 20:16 | 49.952
2020-01-22 | 20:16 | 49.95
2020-01-22 | 20:16 | 49.947
2020-01-22 | 20:17 | 49.948
2020-01-22 | 20:17 | 49.946
2020-01-22 | 20:17 | 49.945
2020-01-22 | 20:17 | 49.943
2020-01-22 | 20:17 | 49.938
2020-01-22 | 20:17 | 49.936
2020-01-22 | 20:17 | 49.936
2020-01-22 | 20:17 | 49.932
2020-01-22 | 20:17 | 49.931
2020-01-22 | 20:17 | 49.932
2020-01-22 | 20:17 | 49.932
2020-01-22 | 20:17 | 49.932
2020-01-22 | 20:17 | 49.936
2020-01-22 | 20:17 | 49.933
2020-01-22 | 20:17 | 49.933
2020-01-22 | 20:17 | 49.931
2020-01-22 | 20:17 | 49.926
2020-01-22 | 20:17 | 49.924
2020-01-22 | 20:17 | 49.922
2020-01-22 | 20:17 | 49.92
2020-01-22 | 20:17 | 49.921
2020-01-22 | 20:17 | 49.921
2020-01-22 | 20:17 | 49.921
2020-01-22 | 20:17 | 49.923
2020-01-22 | 20:17 | 49.925
2020-01-22 | 20:17 | 49.93
2020-01-22 | 20:17 | 49.931
2020-01-22 | 20:17 | 49.934
2020-01-22 | 20:17 | 49.935
2020-01-22 | 20:17 | 49.933
2020-01-22 | 20:17 | 49.935
2020-01-22 | 20:17 | 49.936
2020-01-22 | 20:17 | 49.937
2020-01-22 | 20:17 | 49.938
2020-01-22 | 20:17 | 49.937
2020-01-22 | 20:17 | 49.94
2020-01-22 | 20:17 | 49.939
2020-01-22 | 20:17 | 49.941
2020-01-22 | 20:17 | 49.944
2020-01-22 | 20:17 | 49.939
2020-01-22 | 20:17 | 49.938
2020-01-22 | 20:17 | 49.932
2020-01-22 | 20:17 | 49.93
2020-01-22 | 20:17 | 49.929
2020-01-22 | 20:17 | 49.927
2020-01-22 | 20:17 | 49.925
2020-01-22 | 20:17 | 49.925
2020-01-22 | 20:17 | 49.922
2020-01-22 | 20:17 | 49.922
2020-01-22 | 20:17 | 49.919
2020-01-22 | 20:17 | 49.921
2020-01-22 | 20:17 | 49.919
2020-01-22 | 20:17 | 49.917
2020-01-22 | 20:17 | 49.917
2020-01-22 | 20:17 | 49.915
2020-01-22 | 20:17 | 49.914
2020-01-22 | 20:17 | 49.914
2020-01-22 | 20:17 | 49.912
2020-01-22 | 20:17 | 49.909
2020-01-22 | 20:18 | 49.91
2020-01-22 | 20:18 | 49.908
2020-01-22 | 20:18 | 49.905
2020-01-22 | 20:18 | 49.907
2020-01-22 | 20:18 | 49.905
2020-01-22 | 20:18 | 49.906
2020-01-22 | 20:18 | 49.908
2020-01-22 | 20:18 | 49.908
2020-01-22 | 20:18 | 49.911
2020-01-22 | 20:18 | 49.917
2020-01-22 | 20:18 | 49.916
2020-01-22 | 20:18 | 49.92
2020-01-22 | 20:18 | 49.923
2020-01-22 | 20:18 | 49.924
2020-01-22 | 20:18 | 49.925
2020-01-22 | 20:18 | 49.93
2020-01-22 | 20:18 | 49.931
2020-01-22 | 20:18 | 49.936
2020-01-22 | 20:18 | 49.936
2020-01-22 | 20:18 | 49.936
2020-01-22 | 20:18 | 49.937
2020-01-22 | 20:18 | 49.935
2020-01-22 | 20:18 | 49.935
2020-01-22 | 20:18 | 49.936
2020-01-22 | 20:18 | 49.933
2020-01-22 | 20:18 | 49.931
2020-01-22 | 20:18 | 49.929
2020-01-22 | 20:18 | 49.93
2020-01-22 | 20:18 | 49.93
2020-01-22 | 20:18 | 49.926
2020-01-22 | 20:18 | 49.926
2020-01-22 | 20:18 | 49.927
2020-01-22 | 20:18 | 49.926
2020-01-22 | 20:18 | 49.926
2020-01-22 | 20:18 | 49.928
2020-01-22 | 20:18 | 49.929
2020-01-22 | 20:18 | 49.93
2020-01-22 | 20:18 | 49.933
2020-01-22 | 20:18 | 49.935
2020-01-22 | 20:18 | 49.935
2020-01-22 | 20:18 | 49.936
2020-01-22 | 20:18 | 49.938
2020-01-22 | 20:18 | 49.938
2020-01-22 | 20:18 | 49.94
2020-01-22 | 20:18 | 49.939
2020-01-22 | 20:18 | 49.938
2020-01-22 | 20:18 | 49.937
2020-01-22 | 20:18 | 49.939
2020-01-22 | 20:18 | 49.936
2020-01-22 | 20:18 | 49.934
2020-01-22 | 20:18 | 49.934
2020-01-22 | 20:18 | 49.932
2020-01-22 | 20:18 | 49.933
2020-01-22 | 20:18 | 49.931
2020-01-22 | 20:18 | 49.93
2020-01-22 | 20:18 | 49.931
2020-01-22 | 20:18 | 49.928
2020-01-22 | 20:18 | 49.929
2020-01-22 | 20:18 | 49.931
2020-01-22 | 20:18 | 49.929
2020-01-22 | 20:18 | 49.934
2020-01-22 | 20:19 | 49.936
2020-01-22 | 20:19 | 49.937
2020-01-22 | 20:19 | 49.94
2020-01-22 | 20:19 | 49.942
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.947
2020-01-22 | 20:19 | 49.949
2020-01-22 | 20:19 | 49.949
2020-01-22 | 20:19 | 49.948
2020-01-22 | 20:19 | 49.949
2020-01-22 | 20:19 | 49.95
2020-01-22 | 20:19 | 49.947
2020-01-22 | 20:19 | 49.948
2020-01-22 | 20:19 | 49.947
2020-01-22 | 20:19 | 49.947
2020-01-22 | 20:19 | 49.947
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.943
2020-01-22 | 20:19 | 49.941
2020-01-22 | 20:19 | 49.94
2020-01-22 | 20:19 | 49.939
2020-01-22 | 20:19 | 49.938
2020-01-22 | 20:19 | 49.939
2020-01-22 | 20:19 | 49.937
2020-01-22 | 20:19 | 49.934
2020-01-22 | 20:19 | 49.936
2020-01-22 | 20:19 | 49.936
2020-01-22 | 20:19 | 49.937
2020-01-22 | 20:19 | 49.938
2020-01-22 | 20:19 | 49.94
2020-01-22 | 20:19 | 49.942
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.947
2020-01-22 | 20:19 | 49.948
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.944
2020-01-22 | 20:19 | 49.948
2020-01-22 | 20:19 | 49.95
2020-01-22 | 20:19 | 49.949
2020-01-22 | 20:19 | 49.951
2020-01-22 | 20:19 | 49.951
2020-01-22 | 20:19 | 49.949
2020-01-22 | 20:19 | 49.951
2020-01-22 | 20:19 | 49.949
2020-01-22 | 20:19 | 49.946
2020-01-22 | 20:19 | 49.945
2020-01-22 | 20:19 | 49.942
2020-01-22 | 20:19 | 49.939
2020-01-22 | 20:19 | 49.939
2020-01-22 | 20:19 | 49.936
2020-01-22 | 20:19 | 49.935
2020-01-22 | 20:20 | 49.937
2020-01-22 | 20:20 | 49.936
2020-01-22 | 20:20 | 49.937
2020-01-22 | 20:20 | 49.939
2020-01-22 | 20:20 | 49.937
2020-01-22 | 20:20 | 49.938
2020-01-22 | 20:20 | 49.939
2020-01-22 | 20:20 | 49.94
2020-01-22 | 20:20 | 49.944
2020-01-22 | 20:20 | 49.95
2020-01-22 | 20:20 | 49.953
2020-01-22 | 20:20 | 49.96
2020-01-22 | 20:20 | 49.964
2020-01-22 | 20:20 | 49.967
2020-01-22 | 20:20 | 49.971
2020-01-22 | 20:20 | 49.972
2020-01-22 | 20:20 | 49.975
2020-01-22 | 20:20 | 49.979
2020-01-22 | 20:20 | 49.978
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.979
2020-01-22 | 20:20 | 49.976
2020-01-22 | 20:20 | 49.976
2020-01-22 | 20:20 | 49.971
2020-01-22 | 20:20 | 49.971
2020-01-22 | 20:20 | 49.968
2020-01-22 | 20:20 | 49.966
2020-01-22 | 20:20 | 49.967
2020-01-22 | 20:20 | 49.965
2020-01-22 | 20:20 | 49.968
2020-01-22 | 20:20 | 49.968
2020-01-22 | 20:20 | 49.97
2020-01-22 | 20:20 | 49.972
2020-01-22 | 20:20 | 49.971
2020-01-22 | 20:20 | 49.975
2020-01-22 | 20:20 | 49.976
2020-01-22 | 20:20 | 49.977
2020-01-22 | 20:20 | 49.979
2020-01-22 | 20:20 | 49.978
2020-01-22 | 20:20 | 49.981
2020-01-22 | 20:20 | 49.981
2020-01-22 | 20:20 | 49.981
2020-01-22 | 20:20 | 49.982
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.983
2020-01-22 | 20:20 | 49.982
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.982
2020-01-22 | 20:20 | 49.979
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.977
2020-01-22 | 20:20 | 49.976
2020-01-22 | 20:20 | 49.978
2020-01-22 | 20:20 | 49.979
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.981
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.98
2020-01-22 | 20:20 | 49.978
2020-01-22 | 20:20 | 49.976
2020-01-22 | 20:20 | 49.975
2020-01-22 | 20:21 | 49.973
2020-01-22 | 20:21 | 49.973
2020-01-22 | 20:21 | 49.971
2020-01-22 | 20:21 | 49.974
2020-01-22 | 20:21 | 49.974
2020-01-22 | 20:21 | 49.972
2020-01-22 | 20:21 | 49.975
2020-01-22 | 20:21 | 49.972
2020-01-22 | 20:21 | 49.972
2020-01-22 | 20:21 | 49.972
2020-01-22 | 20:21 | 49.969
2020-01-22 | 20:21 | 49.969
2020-01-22 | 20:21 | 49.965
2020-01-22 | 20:21 | 49.964
2020-01-22 | 20:21 | 49.961
2020-01-22 | 20:21 | 49.956
2020-01-22 | 20:21 | 49.954
2020-01-22 | 20:21 | 49.949
2020-01-22 | 20:21 | 49.947
2020-01-22 | 20:21 | 49.944
2020-01-22 | 20:21 | 49.941
2020-01-22 | 20:21 | 49.938
2020-01-22 | 20:21 | 49.935
2020-01-22 | 20:21 | 49.937
2020-01-22 | 20:21 | 49.935
2020-01-22 | 20:21 | 49.936
2020-01-22 | 20:21 | 49.938
2020-01-22 | 20:21 | 49.939
2020-01-22 | 20:21 | 49.941
2020-01-22 | 20:21 | 49.941
2020-01-22 | 20:21 | 49.941
2020-01-22 | 20:21 | 49.943
2020-01-22 | 20:21 | 49.941
2020-01-22 | 20:21 | 49.944
2020-01-22 | 20:21 | 49.944
2020-01-22 | 20:21 | 49.946
2020-01-22 | 20:21 | 49.948
2020-01-22 | 20:21 | 49.947
2020-01-22 | 20:21 | 49.95
2020-01-22 | 20:21 | 49.954
2020-01-22 | 20:21 | 49.957
2020-01-22 | 20:21 | 49.96
2020-01-22 | 20:21 | 49.962
2020-01-22 | 20:21 | 49.965
2020-01-22 | 20:21 | 49.964
2020-01-22 | 20:21 | 49.965
2020-01-22 | 20:21 | 49.964
2020-01-22 | 20:21 | 49.964
2020-01-22 | 20:21 | 49.963
2020-01-22 | 20:21 | 49.961
2020-01-22 | 20:21 | 49.964
2020-01-22 | 20:21 | 49.963
2020-01-22 | 20:21 | 49.964
2020-01-22 | 20:21 | 49.965
2020-01-22 | 20:21 | 49.966
2020-01-22 | 20:21 | 49.97
2020-01-22 | 20:21 | 49.97
2020-01-22 | 20:21 | 49.974
2020-01-22 | 20:21 | 49.974
2020-01-22 | 20:22 | 49.974
2020-01-22 | 20:22 | 49.976
2020-01-22 | 20:22 | 49.976
2020-01-22 | 20:22 | 49.977
2020-01-22 | 20:22 | 49.978
2020-01-22 | 20:22 | 49.978
2020-01-22 | 20:22 | 49.978
2020-01-22 | 20:22 | 49.981
2020-01-22 | 20:22 | 49.979
2020-01-22 | 20:22 | 49.981
2020-01-22 | 20:22 | 49.98
2020-01-22 | 20:22 | 49.98
2020-01-22 | 20:22 | 49.981
2020-01-22 | 20:22 | 49.978
2020-01-22 | 20:22 | 49.978
2020-01-22 | 20:22 | 49.977
2020-01-22 | 20:22 | 49.977
2020-01-22 | 20:22 | 49.973
2020-01-22 | 20:22 | 49.973
2020-01-22 | 20:22 | 49.97
2020-01-22 | 20:22 | 49.966
2020-01-22 | 20:22 | 49.964
2020-01-22 | 20:22 | 49.96
2020-01-22 | 20:22 | 49.96
2020-01-22 | 20:22 | 49.957
2020-01-22 | 20:22 | 49.954
2020-01-22 | 20:22 | 49.955
2020-01-22 | 20:22 | 49.951
2020-01-22 | 20:22 | 49.954
2020-01-22 | 20:22 | 49.953
2020-01-22 | 20:22 | 49.952
2020-01-22 | 20:22 | 49.951
2020-01-22 | 20:22 | 49.951
2020-01-22 | 20:22 | 49.951
2020-01-22 | 20:22 | 49.95
2020-01-22 | 20:22 | 49.95
2020-01-22 | 20:22 | 49.949
2020-01-22 | 20:22 | 49.948
2020-01-22 | 20:22 | 49.95
2020-01-22 | 20:22 | 49.949
2020-01-22 | 20:22 | 49.951
2020-01-22 | 20:22 | 49.949
2020-01-22 | 20:22 | 49.951
2020-01-22 | 20:22 | 49.952
2020-01-22 | 20:22 | 49.952
2020-01-22 | 20:22 | 49.957
2020-01-22 | 20:22 | 49.957
2020-01-22 | 20:22 | 49.96
2020-01-22 | 20:22 | 49.961
2020-01-22 | 20:22 | 49.961
2020-01-22 | 20:22 | 49.963
2020-01-22 | 20:22 | 49.964
2020-01-22 | 20:22 | 49.965
2020-01-22 | 20:22 | 49.968
2020-01-22 | 20:22 | 49.968
2020-01-22 | 20:22 | 49.968
2020-01-22 | 20:22 | 49.97
2020-01-22 | 20:22 | 49.968
2020-01-22 | 20:22 | 49.968
2020-01-22 | 20:22 | 49.968
2020-01-22 | 20:22 | 49.966
2020-01-22 | 20:23 | 49.967
2020-01-22 | 20:23 | 49.966
2020-01-22 | 20:23 | 49.963
2020-01-22 | 20:23 | 49.965
2020-01-22 | 20:23 | 49.962
2020-01-22 | 20:23 | 49.961
2020-01-22 | 20:23 | 49.961
2020-01-22 | 20:23 | 49.959
2020-01-22 | 20:23 | 49.96
2020-01-22 | 20:23 | 49.961
2020-01-22 | 20:23 | 49.961
2020-01-22 | 20:23 | 49.96
2020-01-22 | 20:23 | 49.963
2020-01-22 | 20:23 | 49.962
2020-01-22 | 20:23 | 49.965
2020-01-22 | 20:23 | 49.967
2020-01-22 | 20:23 | 49.967
2020-01-22 | 20:23 | 49.968
2020-01-22 | 20:23 | 49.967
2020-01-22 | 20:23 | 49.968
2020-01-22 | 20:23 | 49.967
2020-01-22 | 20:23 | 49.969
2020-01-22 | 20:23 | 49.971
2020-01-22 | 20:23 | 49.969
2020-01-22 | 20:23 | 49.971
2020-01-22 | 20:23 | 49.972
2020-01-22 | 20:23 | 49.974
2020-01-22 | 20:23 | 49.973
2020-01-22 | 20:23 | 49.976
2020-01-22 | 20:23 | 49.975
2020-01-22 | 20:23 | 49.976
2020-01-22 | 20:23 | 49.975
2020-01-22 | 20:23 | 49.98
2020-01-22 | 20:23 | 49.984
2020-01-22 | 20:23 | 49.985
2020-01-22 | 20:23 | 49.989
2020-01-22 | 20:23 | 49.99
2020-01-22 | 20:23 | 49.993
2020-01-22 | 20:23 | 49.993
2020-01-22 | 20:23 | 49.996
2020-01-22 | 20:23 | 49.998
2020-01-22 | 20:23 | 50.002
2020-01-22 | 20:23 | 50.002
2020-01-22 | 20:23 | 50.004
2020-01-22 | 20:23 | 50.006
2020-01-22 | 20:23 | 50.008
2020-01-22 | 20:23 | 50.01
2020-01-22 | 20:23 | 50.009
2020-01-22 | 20:23 | 50.012
2020-01-22 | 20:23 | 50.011
2020-01-22 | 20:23 | 50.015
2020-01-22 | 20:23 | 50.014
2020-01-22 | 20:23 | 50.017
2020-01-22 | 20:23 | 50.016
2020-01-22 | 20:23 | 50.02
2020-01-22 | 20:23 | 50.019
2020-01-22 | 20:23 | 50.022
2020-01-22 | 20:23 | 50.021
2020-01-22 | 20:23 | 50.025
2020-01-22 | 20:24 | 50.024
2020-01-22 | 20:24 | 50.026
2020-01-22 | 20:24 | 50.026
2020-01-22 | 20:24 | 50.027
2020-01-22 | 20:24 | 50.03
2020-01-22 | 20:24 | 50.03
2020-01-22 | 20:24 | 50.034
2020-01-22 | 20:24 | 50.034
2020-01-22 | 20:24 | 50.036
2020-01-22 | 20:24 | 50.035
2020-01-22 | 20:24 | 50.036
2020-01-22 | 20:24 | 50.037
2020-01-22 | 20:24 | 50.039
2020-01-22 | 20:24 | 50.042
2020-01-22 | 20:24 | 50.043
2020-01-22 | 20:24 | 50.045
2020-01-22 | 20:24 | 50.044
2020-01-22 | 20:24 | 50.047
2020-01-22 | 20:24 | 50.047
2020-01-22 | 20:24 | 50.046
2020-01-22 | 20:24 | 50.051
2020-01-22 | 20:24 | 50.048
2020-01-22 | 20:24 | 50.045
2020-01-22 | 20:24 | 50.041
2020-01-22 | 20:24 | 50.033
2020-01-22 | 20:24 | 50.029
2020-01-22 | 20:24 | 50.023
2020-01-22 | 20:24 | 50.02
2020-01-22 | 20:24 | 50.017
2020-01-22 | 20:24 | 50.012
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.038
2020-01-17 | 2:16 | 50.037
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.029
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.03
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.035
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.039
2020-01-17 | 2:16 | 50.038
2020-01-17 | 2:16 | 50.036
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.025
2020-01-17 | 2:16 | 50.026
2020-01-17 | 2:16 | 50.027
2020-01-17 | 2:16 | 50.028
2020-01-17 | 2:16 | 50.031
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.032
2020-01-17 | 2:16 | 50.033
2020-01-17 | 2:16 | 50.034
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.033
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.035
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.038
2020-01-17 | 2:17 | 50.036
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.034
2020-01-17 | 2:17 | 50.03
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.027
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.022
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.026
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.027
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.023
2020-01-17 | 2:17 | 50.02
2020-01-17 | 2:17 | 50.019
2020-01-17 | 2:17 | 50.018
2020-01-17 | 2:17 | 50.019
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.028
2020-01-17 | 2:17 | 50.03
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.033
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.032
2020-01-17 | 2:17 | 50.031
2020-01-17 | 2:17 | 50.029
2020-01-17 | 2:17 | 50.026
2020-01-17 | 2:17 | 50.025
2020-01-17 | 2:17 | 50.024
2020-01-17 | 2:17 | 50.022
2020-01-17 | 2:17 | 50.021
2020-01-17 | 2:17 | 50.02
2020-01-17 | 2:17 | 50.017
2020-01-17 | 2:18 | 50.015
2020-01-17 | 2:18 | 50.014
2020-01-17 | 2:18 | 50.011
2020-01-17 | 2:18 | 50.01
2020-01-17 | 2:18 | 50.007
2020-01-17 | 2:18 | 50.002
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.992
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.988
2020-01-17 | 2:18 | 49.987
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.987
2020-01-17 | 2:18 | 49.988
2020-01-17 | 2:18 | 49.991
2020-01-17 | 2:18 | 49.99
2020-01-17 | 2:18 | 49.989
2020-01-17 | 2:18 | 49.99
2020-01-17 | 2:18 | 49.991
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.995
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.995
2020-01-17 | 2:18 | 49.994
2020-01-17 | 2:18 | 49.996
2020-01-17 | 2:18 | 49.998
2020-01-17 | 2:18 | 49.997
2020-01-17 | 2:18 | 49.999

## Event 20200123-1
In UTC
Date | Time | Freq
2020-01-23 | 20:59 | 50.066
2020-01-23 | 20:59 | 50.061
2020-01-23 | 20:59 | 50.057
2020-01-23 | 20:59 | 50.056
2020-01-23 | 20:59 | 50.053
2020-01-23 | 20:59 | 50.051
2020-01-23 | 20:59 | 50.051
2020-01-23 | 20:59 | 50.049
2020-01-23 | 20:59 | 50.048
2020-01-23 | 20:59 | 50.046
2020-01-23 | 20:59 | 50.043
2020-01-23 | 20:59 | 50.04
2020-01-23 | 20:59 | 50.039
2020-01-23 | 20:59 | 50.043
2020-01-23 | 20:59 | 50.047
2020-01-23 | 20:59 | 50.049
2020-01-23 | 20:59 | 50.048
2020-01-23 | 20:59 | 50.047
2020-01-23 | 20:59 | 50.049
2020-01-23 | 20:59 | 50.047
2020-01-23 | 20:59 | 50.045
2020-01-23 | 20:59 | 50.045
2020-01-23 | 20:59 | 50.043
2020-01-23 | 20:59 | 50.041
2020-01-23 | 20:59 | 50.042
2020-01-23 | 20:59 | 50.039
2020-01-23 | 20:59 | 50.037
2020-01-23 | 20:59 | 50.036
2020-01-23 | 20:59 | 50.038
2020-01-23 | 20:59 | 50.036
2020-01-23 | 21:00 | 50.037
2020-01-23 | 21:00 | 50.035
2020-01-23 | 21:00 | 50.033
2020-01-23 | 21:00 | 50.033
2020-01-23 | 21:00 | 50.031
2020-01-23 | 21:00 | 50.03
2020-01-23 | 21:00 | 50.031
2020-01-23 | 21:00 | 50.028
2020-01-23 | 21:00 | 50.029
2020-01-23 | 21:00 | 50.028
2020-01-23 | 21:00 | 50.029
2020-01-23 | 21:00 | 50.032
2020-01-23 | 21:00 | 50.03
2020-01-23 | 21:00 | 50.031
2020-01-23 | 21:00 | 50.032
2020-01-23 | 21:00 | 50.03
2020-01-23 | 21:00 | 50.031
2020-01-23 | 21:00 | 50.032
2020-01-23 | 21:00 | 50.034
2020-01-23 | 21:00 | 50.032
2020-01-23 | 21:00 | 50.032
2020-01-23 | 21:00 | 50.03
2020-01-23 | 21:00 | 50.028
2020-01-23 | 21:00 | 50.028
2020-01-23 | 21:00 | 50.026
2020-01-23 | 21:00 | 50.029
2020-01-23 | 21:00 | 50.029
2020-01-23 | 21:00 | 50.031
2020-01-23 | 21:00 | 50.03
2020-01-23 | 21:00 | 50.028
2020-01-23 | 21:00 | 50.025
2020-01-23 | 21:00 | 50.023
2020-01-23 | 21:00 | 50.019
2020-01-23 | 21:00 | 50.015
2020-01-23 | 21:00 | 50.012
2020-01-23 | 21:00 | 50.008
2020-01-23 | 21:00 | 50.007
2020-01-23 | 21:00 | 50.006
2020-01-23 | 21:00 | 50.004
2020-01-23 | 21:00 | 50
2020-01-23 | 21:00 | 49.999
2020-01-23 | 21:00 | 49.993
2020-01-23 | 21:00 | 49.997
2020-01-23 | 21:00 | 49.987
2020-01-23 | 21:00 | 49.983
2020-01-23 | 21:00 | 49.983
2020-01-23 | 21:00 | 49.981
2020-01-23 | 21:00 | 49.981
2020-01-23 | 21:00 | 49.982
2020-01-23 | 21:00 | 49.98
2020-01-23 | 21:00 | 49.97
2020-01-23 | 21:00 | 49.959
2020-01-23 | 21:00 | 49.942
2020-01-23 | 21:00 | 49.93
2020-01-23 | 21:00 | 49.922
2020-01-23 | 21:00 | 49.913
2020-01-23 | 21:00 | 49.905
2020-01-23 | 21:00 | 49.901
2020-01-23 | 21:00 | 49.897
2020-01-23 | 21:00 | 49.893
2020-01-23 | 21:00 | 49.893
2020-01-23 | 21:01 | 49.892
2020-01-23 | 21:01 | 49.892
2020-01-23 | 21:01 | 49.893
2020-01-23 | 21:01 | 49.892
2020-01-23 | 21:01 | 49.889
2020-01-23 | 21:01 | 49.89
2020-01-23 | 21:01 | 49.889
2020-01-23 | 21:01 | 49.886
2020-01-23 | 21:01 | 49.883
2020-01-23 | 21:01 | 49.883
2020-01-23 | 21:01 | 49.881
2020-01-23 | 21:01 | 49.876
2020-01-23 | 21:01 | 49.876
2020-01-23 | 21:01 | 49.872
2020-01-23 | 21:01 | 49.871
2020-01-23 | 21:01 | 49.869
2020-01-23 | 21:01 | 49.866
2020-01-23 | 21:01 | 49.863
2020-01-23 | 21:01 | 49.861
2020-01-23 | 21:01 | 49.858
2020-01-23 | 21:01 | 49.855
2020-01-23 | 21:01 | 49.853
2020-01-23 | 21:01 | 49.852
2020-01-23 | 21:01 | 49.851
2020-01-23 | 21:01 | 49.851
2020-01-23 | 21:01 | 49.852
2020-01-23 | 21:01 | 49.855
2020-01-23 | 21:01 | 49.856
2020-01-23 | 21:01 | 49.859
2020-01-23 | 21:01 | 49.856
2020-01-23 | 21:01 | 49.854
2020-01-23 | 21:01 | 49.852
2020-01-23 | 21:01 | 49.848
2020-01-23 | 21:01 | 49.848
2020-01-23 | 21:01 | 49.843
2020-01-23 | 21:01 | 49.842
2020-01-23 | 21:01 | 49.841
2020-01-23 | 21:01 | 49.838
2020-01-23 | 21:01 | 49.838
2020-01-23 | 21:01 | 49.836
2020-01-23 | 21:01 | 49.834
2020-01-23 | 21:01 | 49.834
2020-01-23 | 21:01 | 49.831
2020-01-23 | 21:01 | 49.831
2020-01-23 | 21:01 | 49.83
2020-01-23 | 21:01 | 49.828
2020-01-23 | 21:01 | 49.829
2020-01-23 | 21:01 | 49.828
2020-01-23 | 21:01 | 49.828
2020-01-23 | 21:01 | 49.831
2020-01-23 | 21:01 | 49.827
2020-01-23 | 21:01 | 49.828
2020-01-23 | 21:01 | 49.83
2020-01-23 | 21:01 | 49.831
2020-01-23 | 21:01 | 49.834
2020-01-23 | 21:01 | 49.837
2020-01-23 | 21:01 | 49.839
2020-01-23 | 21:01 | 49.843
2020-01-23 | 21:01 | 49.849
2020-01-23 | 21:02 | 49.849
2020-01-23 | 21:02 | 49.853
2020-01-23 | 21:02 | 49.857
2020-01-23 | 21:02 | 49.858
2020-01-23 | 21:02 | 49.862
2020-01-23 | 21:02 | 49.865
2020-01-23 | 21:02 | 49.87
2020-01-23 | 21:02 | 49.877
2020-01-23 | 21:02 | 49.882
2020-01-23 | 21:02 | 49.89
2020-01-23 | 21:02 | 49.893
2020-01-23 | 21:02 | 49.894
2020-01-23 | 21:02 | 49.898
2020-01-23 | 21:02 | 49.898
2020-01-23 | 21:02 | 49.9
2020-01-23 | 21:02 | 49.899
2020-01-23 | 21:02 | 49.898
2020-01-23 | 21:02 | 49.898
2020-01-23 | 21:02 | 49.895
2020-01-23 | 21:02 | 49.892
2020-01-23 | 21:02 | 49.892
2020-01-23 | 21:02 | 49.889
2020-01-23 | 21:02 | 49.891
2020-01-23 | 21:02 | 49.889
2020-01-23 | 21:02 | 49.891
2020-01-23 | 21:02 | 49.891
2020-01-23 | 21:02 | 49.889
2020-01-23 | 21:02 | 49.89
2020-01-23 | 21:02 | 49.89
2020-01-23 | 21:02 | 49.889
2020-01-23 | 21:02 | 49.893
2020-01-23 | 21:02 | 49.895
2020-01-23 | 21:02 | 49.896
2020-01-23 | 21:02 | 49.901
2020-01-23 | 21:02 | 49.902
2020-01-23 | 21:02 | 49.905
2020-01-23 | 21:02 | 49.908
2020-01-23 | 21:02 | 49.908
2020-01-23 | 21:02 | 49.912
2020-01-23 | 21:02 | 49.915
2020-01-23 | 21:02 | 49.919
2020-01-23 | 21:02 | 49.921
2020-01-23 | 21:02 | 49.925
2020-01-23 | 21:02 | 49.927
2020-01-23 | 21:02 | 49.931
2020-01-23 | 21:02 | 49.933
2020-01-23 | 21:02 | 49.934
2020-01-23 | 21:02 | 49.936
2020-01-23 | 21:02 | 49.938
2020-01-23 | 21:02 | 49.938
2020-01-23 | 21:02 | 49.94
2020-01-23 | 21:02 | 49.94
2020-01-23 | 21:02 | 49.941
2020-01-23 | 21:02 | 49.941
2020-01-23 | 21:02 | 49.937
2020-01-23 | 21:02 | 49.936
2020-01-23 | 21:02 | 49.934
2020-01-23 | 21:02 | 49.934
2020-01-23 | 21:02 | 49.935
2020-01-23 | 21:02 | 49.935
2020-01-23 | 21:02 | 49.935
2020-01-23 | 21:03 | 49.936
2020-01-23 | 21:03 | 49.934
2020-01-23 | 21:03 | 49.935
2020-01-23 | 21:03 | 49.934
2020-01-23 | 21:03 | 49.934
2020-01-23 | 21:03 | 49.935
2020-01-23 | 21:03 | 49.935
2020-01-23 | 21:03 | 49.937
2020-01-23 | 21:03 | 49.938
2020-01-23 | 21:03 | 49.94
2020-01-23 | 21:03 | 49.945
2020-01-23 | 21:03 | 49.947
2020-01-23 | 21:03 | 49.95
2020-01-23 | 21:03 | 49.954
2020-01-23 | 21:03 | 49.955
2020-01-23 | 21:03 | 49.959
2020-01-23 | 21:03 | 49.963
2020-01-23 | 21:03 | 49.964
2020-01-23 | 21:03 | 49.967
2020-01-23 | 21:03 | 49.971
2020-01-23 | 21:03 | 49.974
2020-01-23 | 21:03 | 49.978
2020-01-23 | 21:03 | 49.98
2020-01-23 | 21:03 | 49.977
2020-01-23 | 21:03 | 49.981
2020-01-23 | 21:03 | 49.978
2020-01-23 | 21:03 | 49.977
2020-01-23 | 21:03 | 49.977
2020-01-23 | 21:03 | 49.975
2020-01-23 | 21:03 | 49.976
2020-01-23 | 21:03 | 49.974
2020-01-23 | 21:03 | 49.973
2020-01-23 | 21:03 | 49.975
2020-01-23 | 21:03 | 49.975
2020-01-23 | 21:03 | 49.974
2020-01-23 | 21:03 | 49.976
2020-01-23 | 21:03 | 49.976
2020-01-23 | 21:03 | 49.976
2020-01-23 | 21:03 | 49.979
2020-01-23 | 21:03 | 49.981
2020-01-23 | 21:03 | 49.982
2020-01-23 | 21:03 | 49.985
2020-01-23 | 21:03 | 49.985
2020-01-23 | 21:03 | 49.986
2020-01-23 | 21:03 | 49.986
2020-01-23 | 21:03 | 49.984
2020-01-23 | 21:03 | 49.983
2020-01-23 | 21:03 | 49.982
2020-01-23 | 21:03 | 49.977
2020-01-23 | 21:03 | 49.976
2020-01-23 | 21:03 | 49.973
2020-01-23 | 21:03 | 49.975
2020-01-23 | 21:03 | 49.975
2020-01-23 | 21:03 | 49.974
2020-01-23 | 21:03 | 49.977
2020-01-23 | 21:03 | 49.977
2020-01-23 | 21:03 | 49.979
2020-01-23 | 21:03 | 49.983
2020-01-23 | 21:03 | 49.986
2020-01-23 | 21:04 | 49.993
2020-01-23 | 21:04 | 49.996
2020-01-23 | 21:04 | 49.997
2020-01-23 | 21:04 | 49.999
2020-01-23 | 21:04 | 49.997
2020-01-23 | 21:04 | 49.997
2020-01-23 | 21:04 | 49.996
2020-01-23 | 21:04 | 49.994
2020-01-23 | 21:04 | 49.993
2020-01-23 | 21:04 | 49.99
2020-01-23 | 21:04 | 49.99
2020-01-23 | 21:04 | 49.989
2020-01-23 | 21:04 | 49.987
2020-01-23 | 21:04 | 49.988
2020-01-23 | 21:04 | 49.987
2020-01-23 | 21:04 | 49.987
2020-01-23 | 21:04 | 49.989
2020-01-23 | 21:04 | 49.989
2020-01-23 | 21:04 | 49.993
2020-01-23 | 21:04 | 49.994
2020-01-23 | 21:04 | 49.998
2020-01-23 | 21:04 | 50.002
2020-01-23 | 21:04 | 50.006
2020-01-23 | 21:04 | 50.01
2020-01-23 | 21:04 | 50.012
2020-01-23 | 21:04 | 50.016
2020-01-23 | 21:04 | 50.018
2020-01-23 | 21:04 | 50.018
2020-01-23 | 21:04 | 50.017
2020-01-23 | 21:04 | 50.013

## Event 20200126-1
In UTC
Date | Time | Freq
2020-01-26 | 21:13 | 50.003
2020-01-26 | 21:13 | 49.999
2020-01-26 | 21:13 | 49.995
2020-01-26 | 21:13 | 49.993
2020-01-26 | 21:13 | 49.99
2020-01-26 | 21:13 | 49.988
2020-01-26 | 21:13 | 49.986
2020-01-26 | 21:13 | 49.987
2020-01-26 | 21:13 | 49.99
2020-01-26 | 21:13 | 49.992
2020-01-26 | 21:13 | 49.994
2020-01-26 | 21:13 | 49.997
2020-01-26 | 21:13 | 49.998
2020-01-26 | 21:13 | 50
2020-01-26 | 21:13 | 50.001
2020-01-26 | 21:13 | 50.003
2020-01-26 | 21:13 | 50.005
2020-01-26 | 21:13 | 50.005
2020-01-26 | 21:13 | 50.003
2020-01-26 | 21:13 | 50.004
2020-01-26 | 21:13 | 50.004
2020-01-26 | 21:13 | 50.004
2020-01-26 | 21:13 | 50.005
2020-01-26 | 21:13 | 50.007
2020-01-26 | 21:13 | 50.01
2020-01-26 | 21:13 | 50.014
2020-01-26 | 21:13 | 50.017
2020-01-26 | 21:13 | 50.018
2020-01-26 | 21:13 | 50.018
2020-01-26 | 21:13 | 50.017
2020-01-26 | 21:14 | 50.016
2020-01-26 | 21:14 | 50.014
2020-01-26 | 21:14 | 50.01
2020-01-26 | 21:14 | 50.008
2020-01-26 | 21:14 | 50.006
2020-01-26 | 21:14 | 50.004
2020-01-26 | 21:14 | 50.003
2020-01-26 | 21:14 | 50.002
2020-01-26 | 21:14 | 50.004
2020-01-26 | 21:14 | 50.005
2020-01-26 | 21:14 | 50.008
2020-01-26 | 21:14 | 50.01
2020-01-26 | 21:14 | 50.012
2020-01-26 | 21:14 | 50.014
2020-01-26 | 21:14 | 50.017
2020-01-26 | 21:14 | 50.02
2020-01-26 | 21:14 | 50.021
2020-01-26 | 21:14 | 50.022
2020-01-26 | 21:14 | 50.021
2020-01-26 | 21:14 | 50.02
2020-01-26 | 21:14 | 50.018
2020-01-26 | 21:14 | 50.017
2020-01-26 | 21:14 | 50.016
2020-01-26 | 21:14 | 50.014
2020-01-26 | 21:14 | 50.011
2020-01-26 | 21:14 | 50.008
2020-01-26 | 21:14 | 50.005
2020-01-26 | 21:14 | 50.002
2020-01-26 | 21:14 | 50.001
2020-01-26 | 21:14 | 50.001
2020-01-26 | 21:14 | 50.001
2020-01-26 | 21:14 | 50.001
2020-01-26 | 21:14 | 49.999
2020-01-26 | 21:14 | 49.998
2020-01-26 | 21:14 | 49.997
2020-01-26 | 21:14 | 49.997
2020-01-26 | 21:14 | 50
2020-01-26 | 21:14 | 50.001
2020-01-26 | 21:14 | 50.005
2020-01-26 | 21:14 | 50.009
2020-01-26 | 21:14 | 50.012
2020-01-26 | 21:14 | 50.015
2020-01-26 | 21:14 | 50.018
2020-01-26 | 21:14 | 50.02
2020-01-26 | 21:14 | 50.02
2020-01-26 | 21:14 | 50.021
2020-01-26 | 21:14 | 50.021
2020-01-26 | 21:14 | 50.019
2020-01-26 | 21:14 | 50.016
2020-01-26 | 21:14 | 50.015
2020-01-26 | 21:14 | 50.014
2020-01-26 | 21:14 | 50.014
2020-01-26 | 21:14 | 50.012
2020-01-26 | 21:14 | 50.011
2020-01-26 | 21:14 | 50.01
2020-01-26 | 21:14 | 50.008
2020-01-26 | 21:14 | 50.008
2020-01-26 | 21:14 | 50.006
2020-01-26 | 21:14 | 50.005
2020-01-26 | 21:14 | 50.002
2020-01-26 | 21:14 | 49.999
2020-01-26 | 21:15 | 49.999
2020-01-26 | 21:15 | 49.999
2020-01-26 | 21:15 | 49.997
2020-01-26 | 21:15 | 49.996
2020-01-26 | 21:15 | 49.995
2020-01-26 | 21:15 | 49.995
2020-01-26 | 21:15 | 49.996
2020-01-26 | 21:15 | 50
2020-01-26 | 21:15 | 50.004
2020-01-26 | 21:15 | 50.007
2020-01-26 | 21:15 | 50.01
2020-01-26 | 21:15 | 50.013
2020-01-26 | 21:15 | 50.017
2020-01-26 | 21:15 | 50.019
2020-01-26 | 21:15 | 50.02
2020-01-26 | 21:15 | 50.019
2020-01-26 | 21:15 | 50.019
2020-01-26 | 21:15 | 50.019
2020-01-26 | 21:15 | 50.019
2020-01-26 | 21:15 | 50.022
2020-01-26 | 21:15 | 50.022
2020-01-26 | 21:15 | 50.021
2020-01-26 | 21:15 | 50.022
2020-01-26 | 21:15 | 50.024
2020-01-26 | 21:15 | 50.024
2020-01-26 | 21:15 | 50.024
2020-01-26 | 21:15 | 50.023
2020-01-26 | 21:15 | 50.023
2020-01-26 | 21:15 | 50.021
2020-01-26 | 21:15 | 50.017
2020-01-26 | 21:15 | 50.014
2020-01-26 | 21:15 | 50.011
2020-01-26 | 21:15 | 50.008
2020-01-26 | 21:15 | 50.006
2020-01-26 | 21:15 | 50.006
2020-01-26 | 21:15 | 50.008
2020-01-26 | 21:15 | 50.01
2020-01-26 | 21:15 | 50.01
2020-01-26 | 21:15 | 50.009
2020-01-26 | 21:15 | 50.011
2020-01-26 | 21:15 | 50.011
2020-01-26 | 21:15 | 50.011
2020-01-26 | 21:15 | 50.008
2020-01-26 | 21:15 | 50.006
2020-01-26 | 21:15 | 50.004
2020-01-26 | 21:15 | 50.003
2020-01-26 | 21:15 | 50.003
2020-01-26 | 21:15 | 50.003
2020-01-26 | 21:15 | 50.003
2020-01-26 | 21:15 | 50.003
2020-01-26 | 21:15 | 50.005
2020-01-26 | 21:15 | 50.006
2020-01-26 | 21:15 | 50.005
2020-01-26 | 21:15 | 50.005
2020-01-26 | 21:15 | 50.005
2020-01-26 | 21:15 | 50.005
2020-01-26 | 21:15 | 50.004
2020-01-26 | 21:15 | 50.004
2020-01-26 | 21:15 | 50.004
2020-01-26 | 21:16 | 50.004
2020-01-26 | 21:16 | 50.004
2020-01-26 | 21:16 | 50.005
2020-01-26 | 21:16 | 50.007
2020-01-26 | 21:16 | 50.009
2020-01-26 | 21:16 | 50.011
2020-01-26 | 21:16 | 50.013
2020-01-26 | 21:16 | 50.014
2020-01-26 | 21:16 | 50.016
2020-01-26 | 21:16 | 50.016
2020-01-26 | 21:16 | 50.016
2020-01-26 | 21:16 | 50.018
2020-01-26 | 21:16 | 50.018
2020-01-26 | 21:16 | 50.018
2020-01-26 | 21:16 | 50.019
2020-01-26 | 21:16 | 50.021
2020-01-26 | 21:16 | 50.023
2020-01-26 | 21:16 | 50.023
2020-01-26 | 21:16 | 50.022
2020-01-26 | 21:16 | 50.022
2020-01-26 | 21:16 | 50.023
2020-01-26 | 21:16 | 50.026
2020-01-26 | 21:16 | 50.029
2020-01-26 | 21:16 | 50.035
2020-01-26 | 21:16 | 50.04
2020-01-26 | 21:16 | 50.045
2020-01-26 | 21:16 | 50.047
2020-01-26 | 21:16 | 50.05
2020-01-26 | 21:16 | 50.053
2020-01-26 | 21:16 | 50.054
2020-01-26 | 21:16 | 50.053
2020-01-26 | 21:16 | 50.053
2020-01-26 | 21:16 | 50.053
2020-01-26 | 21:16 | 50.053
2020-01-26 | 21:16 | 50.054
2020-01-26 | 21:16 | 50.054
2020-01-26 | 21:16 | 50.051
2020-01-26 | 21:16 | 50.051
2020-01-26 | 21:16 | 50.052
2020-01-26 | 21:16 | 50.051
2020-01-26 | 21:16 | 50.051
2020-01-26 | 21:16 | 50.051
2020-01-26 | 21:16 | 50.052
2020-01-26 | 21:16 | 50.051
2020-01-26 | 21:16 | 50.049
2020-01-26 | 21:16 | 50.047
2020-01-26 | 21:16 | 50.045
2020-01-26 | 21:16 | 50.044
2020-01-26 | 21:16 | 50.045
2020-01-26 | 21:16 | 50.044
2020-01-26 | 21:16 | 50.043
2020-01-26 | 21:16 | 50.041
2020-01-26 | 21:16 | 50.038
2020-01-26 | 21:16 | 50.036
2020-01-26 | 21:16 | 50.033
2020-01-26 | 21:16 | 50.029
2020-01-26 | 21:16 | 50.029
2020-01-26 | 21:16 | 50.03
2020-01-26 | 21:16 | 50.032
2020-01-26 | 21:16 | 50.036
2020-01-26 | 21:16 | 50.04
2020-01-26 | 21:17 | 50.043
2020-01-26 | 21:17 | 50.047
2020-01-26 | 21:17 | 50.049
2020-01-26 | 21:17 | 50.049
2020-01-26 | 21:17 | 50.048
2020-01-26 | 21:17 | 50.045
2020-01-26 | 21:17 | 50.042
2020-01-26 | 21:17 | 50.039
2020-01-26 | 21:17 | 50.036
2020-01-26 | 21:17 | 50.032
2020-01-26 | 21:17 | 50.029
2020-01-26 | 21:17 | 50.029
2020-01-26 | 21:17 | 50.029
2020-01-26 | 21:17 | 50.03
2020-01-26 | 21:17 | 50.033
2020-01-26 | 21:17 | 50.037
2020-01-26 | 21:17 | 50.043
2020-01-26 | 21:17 | 50.048
2020-01-26 | 21:17 | 50.052
2020-01-26 | 21:17 | 50.057
2020-01-26 | 21:17 | 50.06
2020-01-26 | 21:17 | 50.062
2020-01-26 | 21:17 | 50.063
2020-01-26 | 21:17 | 50.063
2020-01-26 | 21:17 | 50.062
2020-01-26 | 21:17 | 50.06
2020-01-26 | 21:17 | 50.058
2020-01-26 | 21:17 | 50.056
2020-01-26 | 21:17 | 50.054
2020-01-26 | 21:17 | 50.054
2020-01-26 | 21:17 | 50.055
2020-01-26 | 21:17 | 50.052
2020-01-26 | 21:17 | 50.05
2020-01-26 | 21:17 | 50.05
2020-01-26 | 21:17 | 50.051
2020-01-26 | 21:17 | 50.051
2020-01-26 | 21:17 | 50.053
2020-01-26 | 21:17 | 50.057
2020-01-26 | 21:17 | 50.059
2020-01-26 | 21:17 | 50.061
2020-01-26 | 21:17 | 50.06
2020-01-26 | 21:17 | 50.058
2020-01-26 | 21:17 | 50.056
2020-01-26 | 21:17 | 50.055
2020-01-26 | 21:17 | 50.053
2020-01-26 | 21:17 | 50.052
2020-01-26 | 21:17 | 50.051
2020-01-26 | 21:17 | 50.05
2020-01-26 | 21:17 | 50.048
2020-01-26 | 21:17 | 50.048
2020-01-26 | 21:17 | 50.047
2020-01-26 | 21:17 | 50.046
2020-01-26 | 21:17 | 50.046
2020-01-26 | 21:17 | 50.044
2020-01-26 | 21:17 | 50.043
2020-01-26 | 21:17 | 50.043
2020-01-26 | 21:17 | 50.042
2020-01-26 | 21:17 | 50.043
2020-01-26 | 21:17 | 50.044
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.045
2020-01-26 | 21:18 | 50.045
2020-01-26 | 21:18 | 50.045
2020-01-26 | 21:18 | 50.046
2020-01-26 | 21:18 | 50.045
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.041
2020-01-26 | 21:18 | 50.041
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.042
2020-01-26 | 21:18 | 50.041
2020-01-26 | 21:18 | 50.042
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.043
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.044
2020-01-26 | 21:18 | 50.042
2020-01-26 | 21:18 | 50.04
2020-01-26 | 21:18 | 50.038
2020-01-26 | 21:18 | 50.039
2020-01-26 | 21:18 | 50.04
2020-01-26 | 21:18 | 50.04
2020-01-26 | 21:18 | 50.038
2020-01-26 | 21:18 | 50.035
2020-01-26 | 21:18 | 50.032
2020-01-26 | 21:18 | 50.03
2020-01-26 | 21:18 | 50.027
2020-01-26 | 21:18 | 50.023
2020-01-26 | 21:18 | 50.019
2020-01-26 | 21:18 | 50.017
2020-01-26 | 21:18 | 50.016
2020-01-26 | 21:18 | 50.019
2020-01-26 | 21:18 | 50.021
2020-01-26 | 21:18 | 50.024
2020-01-26 | 21:18 | 50.027
2020-01-26 | 21:18 | 50.029
2020-01-26 | 21:18 | 50.031
2020-01-26 | 21:18 | 50.032
2020-01-26 | 21:18 | 50.033
2020-01-26 | 21:18 | 50.033
2020-01-26 | 21:18 | 50.033
2020-01-26 | 21:18 | 50.032
2020-01-26 | 21:18 | 50.03
2020-01-26 | 21:18 | 50.029
2020-01-26 | 21:18 | 50.026
2020-01-26 | 21:18 | 50.025
2020-01-26 | 21:18 | 50.025
2020-01-26 | 21:18 | 50.027
2020-01-26 | 21:18 | 50.028
2020-01-26 | 21:18 | 50.031
2020-01-26 | 21:18 | 50.033
2020-01-26 | 21:18 | 50.034
2020-01-26 | 21:18 | 50.034
2020-01-26 | 21:19 | 50.032
2020-01-26 | 21:19 | 50.028
2020-01-26 | 21:19 | 50.024
2020-01-26 | 21:19 | 50.021
2020-01-26 | 21:19 | 50.019
2020-01-26 | 21:19 | 50.016
2020-01-26 | 21:19 | 50.012
2020-01-26 | 21:19 | 50.01
2020-01-26 | 21:19 | 50.009
2020-01-26 | 21:19 | 50.008
2020-01-26 | 21:19 | 50.009
2020-01-26 | 21:19 | 50.009
2020-01-26 | 21:19 | 50.01
2020-01-26 | 21:19 | 50.013
2020-01-26 | 21:19 | 50.013
2020-01-26 | 21:19 | 50.015
2020-01-26 | 21:19 | 50.016
2020-01-26 | 21:19 | 50.017
2020-01-26 | 21:19 | 50.019
2020-01-26 | 21:19 | 50.02
2020-01-26 | 21:19 | 50.022
2020-01-26 | 21:19 | 50.022
2020-01-26 | 21:19 | 50.025
2020-01-26 | 21:19 | 50.029
2020-01-26 | 21:19 | 50.032
2020-01-26 | 21:19 | 50.034
2020-01-26 | 21:19 | 50.036
2020-01-26 | 21:19 | 50.037
2020-01-26 | 21:19 | 50.038
2020-01-26 | 21:19 | 50.037
2020-01-26 | 21:19 | 50.039
2020-01-26 | 21:19 | 50.039
2020-01-26 | 21:19 | 50.038
2020-01-26 | 21:19 | 50.041
2020-01-26 | 21:19 | 50.044
2020-01-26 | 21:19 | 50.046
2020-01-26 | 21:19 | 50.049
2020-01-26 | 21:19 | 50.053
2020-01-26 | 21:19 | 50.057
2020-01-26 | 21:19 | 50.061
2020-01-26 | 21:19 | 50.066
2020-01-26 | 21:19 | 50.07
2020-01-26 | 21:19 | 50.07
2020-01-26 | 21:19 | 50.069
2020-01-26 | 21:19 | 50.068
2020-01-26 | 21:19 | 50.066
2020-01-26 | 21:19 | 50.065
2020-01-26 | 21:19 | 50.067
2020-01-26 | 21:19 | 50.066
2020-01-26 | 21:19 | 50.064
2020-01-26 | 21:19 | 50.063
2020-01-26 | 21:19 | 50.06
2020-01-26 | 21:19 | 50.058
2020-01-26 | 21:19 | 50.055
2020-01-26 | 21:19 | 50.054
2020-01-26 | 21:19 | 50.054
2020-01-26 | 21:19 | 50.053
2020-01-26 | 21:19 | 50.052
2020-01-26 | 21:19 | 50.051
2020-01-26 | 21:20 | 50.052
2020-01-26 | 21:20 | 50.052
2020-01-26 | 21:20 | 50.049
2020-01-26 | 21:20 | 50.047
2020-01-26 | 21:20 | 50.044
2020-01-26 | 21:20 | 50.043
2020-01-26 | 21:20 | 50.042
2020-01-26 | 21:20 | 50.041
2020-01-26 | 21:20 | 50.039
2020-01-26 | 21:20 | 50.036
2020-01-26 | 21:20 | 50.033
2020-01-26 | 21:20 | 50.03
2020-01-26 | 21:20 | 50.027
2020-01-26 | 21:20 | 50.025
2020-01-26 | 21:20 | 50.023
2020-01-26 | 21:20 | 50.02
2020-01-26 | 21:20 | 50.018
2020-01-26 | 21:20 | 50.017
2020-01-26 | 21:20 | 50.016
2020-01-26 | 21:20 | 50.018
2020-01-26 | 21:20 | 50.019
2020-01-26 | 21:20 | 50.021
2020-01-26 | 21:20 | 50.021
2020-01-26 | 21:20 | 50.022
2020-01-26 | 21:20 | 50.022
2020-01-26 | 21:20 | 50.021
2020-01-26 | 21:20 | 50.018
2020-01-26 | 21:20 | 50.016
2020-01-26 | 21:20 | 50.013
2020-01-26 | 21:20 | 50.01
2020-01-26 | 21:20 | 50.007
2020-01-26 | 21:20 | 50.003
2020-01-26 | 21:20 | 49.997
2020-01-26 | 21:20 | 49.994
2020-01-26 | 21:20 | 49.99
2020-01-26 | 21:20 | 49.988
2020-01-26 | 21:20 | 49.986
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.983
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.983
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.981
2020-01-26 | 21:20 | 49.981
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.981
2020-01-26 | 21:20 | 49.982
2020-01-26 | 21:20 | 49.983
2020-01-26 | 21:20 | 49.985
2020-01-26 | 21:20 | 49.986
2020-01-26 | 21:20 | 49.987
2020-01-26 | 21:20 | 49.99
2020-01-26 | 21:20 | 49.992
2020-01-26 | 21:20 | 49.994
2020-01-26 | 21:20 | 49.996
2020-01-26 | 21:20 | 49.998
2020-01-26 | 21:20 | 50
2020-01-26 | 21:20 | 50.002
2020-01-26 | 21:20 | 50.004
2020-01-26 | 21:21 | 50.007
2020-01-26 | 21:21 | 50.007
2020-01-26 | 21:21 | 50.008
2020-01-26 | 21:21 | 50.009
2020-01-26 | 21:21 | 50.008
2020-01-26 | 21:21 | 50.007
2020-01-26 | 21:21 | 50.006
2020-01-26 | 21:21 | 50.005
2020-01-26 | 21:21 | 50.004
2020-01-26 | 21:21 | 50.002
2020-01-26 | 21:21 | 50
2020-01-26 | 21:21 | 49.997
2020-01-26 | 21:21 | 49.991
2020-01-26 | 21:21 | 49.987
2020-01-26 | 21:21 | 49.982
2020-01-26 | 21:21 | 49.977
2020-01-26 | 21:21 | 49.974
2020-01-26 | 21:21 | 49.972
2020-01-26 | 21:21 | 49.972
2020-01-26 | 21:21 | 49.972
2020-01-26 | 21:21 | 49.973
2020-01-26 | 21:21 | 49.972
2020-01-26 | 21:21 | 49.973
2020-01-26 | 21:21 | 49.974
2020-01-26 | 21:21 | 49.976
2020-01-26 | 21:21 | 49.978
2020-01-26 | 21:21 | 49.98
2020-01-26 | 21:21 | 49.983
2020-01-26 | 21:21 | 49.984
2020-01-26 | 21:21 | 49.984
2020-01-26 | 21:21 | 49.985
2020-01-26 | 21:21 | 49.983
2020-01-26 | 21:21 | 49.981
2020-01-26 | 21:21 | 49.977
2020-01-26 | 21:21 | 49.975
2020-01-26 | 21:21 | 49.971
2020-01-26 | 21:21 | 49.967
2020-01-26 | 21:21 | 49.965
2020-01-26 | 21:21 | 49.965
2020-01-26 | 21:21 | 49.967
2020-01-26 | 21:21 | 49.966
2020-01-26 | 21:21 | 49.969
2020-01-26 | 21:21 | 49.973
2020-01-26 | 21:21 | 49.978
2020-01-26 | 21:21 | 49.981
2020-01-26 | 21:21 | 49.983
2020-01-26 | 21:21 | 49.986
2020-01-26 | 21:21 | 49.987
2020-01-26 | 21:21 | 49.988
2020-01-26 | 21:21 | 49.988
2020-01-26 | 21:21 | 49.988
2020-01-26 | 21:21 | 49.988
2020-01-26 | 21:21 | 49.99
2020-01-26 | 21:21 | 49.991
2020-01-26 | 21:21 | 49.99
2020-01-26 | 21:21 | 49.99
2020-01-26 | 21:21 | 49.989
2020-01-26 | 21:21 | 49.988
2020-01-26 | 21:21 | 49.986
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.982
2020-01-26 | 21:22 | 49.983
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.985
2020-01-26 | 21:22 | 49.985
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.983
2020-01-26 | 21:22 | 49.982
2020-01-26 | 21:22 | 49.98
2020-01-26 | 21:22 | 49.978
2020-01-26 | 21:22 | 49.977
2020-01-26 | 21:22 | 49.976
2020-01-26 | 21:22 | 49.974
2020-01-26 | 21:22 | 49.974
2020-01-26 | 21:22 | 49.974
2020-01-26 | 21:22 | 49.977
2020-01-26 | 21:22 | 49.981
2020-01-26 | 21:22 | 49.983
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.987
2020-01-26 | 21:22 | 49.988
2020-01-26 | 21:22 | 49.991
2020-01-26 | 21:22 | 49.994
2020-01-26 | 21:22 | 49.996
2020-01-26 | 21:22 | 49.994
2020-01-26 | 21:22 | 49.993
2020-01-26 | 21:22 | 49.995
2020-01-26 | 21:22 | 49.995
2020-01-26 | 21:22 | 49.997
2020-01-26 | 21:22 | 49.998
2020-01-26 | 21:22 | 49.997
2020-01-26 | 21:22 | 49.993
2020-01-26 | 21:22 | 49.991
2020-01-26 | 21:22 | 49.987
2020-01-26 | 21:22 | 49.984
2020-01-26 | 21:22 | 49.982
2020-01-26 | 21:22 | 49.981
2020-01-26 | 21:22 | 49.981
2020-01-26 | 21:22 | 49.98
2020-01-26 | 21:22 | 49.98
2020-01-26 | 21:22 | 49.98
2020-01-26 | 21:22 | 49.979
2020-01-26 | 21:22 | 49.976
2020-01-26 | 21:22 | 49.975
2020-01-26 | 21:22 | 49.973
2020-01-26 | 21:22 | 49.973
2020-01-26 | 21:22 | 49.97
2020-01-26 | 21:22 | 49.97
2020-01-26 | 21:22 | 49.969
2020-01-26 | 21:22 | 49.968
2020-01-26 | 21:22 | 49.968
2020-01-26 | 21:22 | 49.967
2020-01-26 | 21:22 | 49.966
2020-01-26 | 21:22 | 49.968
2020-01-26 | 21:22 | 49.971
2020-01-26 | 21:22 | 49.973
2020-01-26 | 21:22 | 49.975
2020-01-26 | 21:22 | 49.977
2020-01-26 | 21:23 | 49.979
2020-01-26 | 21:23 | 49.981
2020-01-26 | 21:23 | 49.985
2020-01-26 | 21:23 | 49.988
2020-01-26 | 21:23 | 49.988
2020-01-26 | 21:23 | 49.988
2020-01-26 | 21:23 | 49.988
2020-01-26 | 21:23 | 49.987
2020-01-26 | 21:23 | 49.986
2020-01-26 | 21:23 | 49.988
2020-01-26 | 21:23 | 49.991
2020-01-26 | 21:23 | 49.994
2020-01-26 | 21:23 | 49.996
2020-01-26 | 21:23 | 50.001
2020-01-26 | 21:23 | 50.006
2020-01-26 | 21:23 | 50.011
2020-01-26 | 21:23 | 50.014
2020-01-26 | 21:23 | 50.017
2020-01-26 | 21:23 | 50.017
2020-01-26 | 21:23 | 50.019
2020-01-26 | 21:23 | 50.019
2020-01-26 | 21:23 | 50.02
2020-01-26 | 21:23 | 50.02
2020-01-26 | 21:23 | 50.02
2020-01-26 | 21:23 | 50.018
2020-01-26 | 21:23 | 50.017
2020-01-26 | 21:23 | 50.014
2020-01-26 | 21:23 | 50.011
2020-01-26 | 21:23 | 50.009
2020-01-26 | 21:23 | 50.007
2020-01-26 | 21:23 | 50.006
2020-01-26 | 21:23 | 50.008
2020-01-26 | 21:23 | 50.009
2020-01-26 | 21:23 | 50.009
2020-01-26 | 21:23 | 50.01
2020-01-26 | 21:23 | 50.011
2020-01-26 | 21:23 | 50.013
2020-01-26 | 21:23 | 50.013
2020-01-26 | 21:23 | 50.013
2020-01-26 | 21:23 | 50.011
2020-01-26 | 21:23 | 50.01
2020-01-26 | 21:23 | 50.01
2020-01-26 | 21:23 | 50.012
2020-01-26 | 21:23 | 50.014
2020-01-26 | 21:23 | 50.018
2020-01-26 | 21:23 | 50.02
2020-01-26 | 21:23 | 50.022
2020-01-26 | 21:23 | 50.023
2020-01-26 | 21:23 | 50.023
2020-01-26 | 21:23 | 50.021
2020-01-26 | 21:23 | 50.018
2020-01-26 | 21:23 | 50.014
2020-01-26 | 21:23 | 50.011
2020-01-26 | 21:23 | 50.008
2020-01-26 | 21:23 | 50.006
2020-01-26 | 21:23 | 50.005
2020-01-26 | 21:23 | 50.005
2020-01-26 | 21:23 | 50.007
2020-01-26 | 21:23 | 50.009
2020-01-26 | 21:24 | 50.01
2020-01-26 | 21:24 | 50.011
2020-01-26 | 21:24 | 50.011
2020-01-26 | 21:24 | 50.012
2020-01-26 | 21:24 | 50.015
2020-01-26 | 21:24 | 50.016
2020-01-26 | 21:24 | 50.016
2020-01-26 | 21:24 | 50.015
2020-01-26 | 21:24 | 50.015
2020-01-26 | 21:24 | 50.014
2020-01-26 | 21:24 | 50.015
2020-01-26 | 21:24 | 50.014
2020-01-26 | 21:24 | 50.013
2020-01-26 | 21:24 | 50.014
2020-01-26 | 21:24 | 50.018
2020-01-26 | 21:24 | 50.022
2020-01-26 | 21:24 | 50.026
2020-01-26 | 21:24 | 50.031
2020-01-26 | 21:24 | 50.038
2020-01-26 | 21:24 | 50.041
2020-01-26 | 21:24 | 50.041
2020-01-26 | 21:24 | 50.039
2020-01-26 | 21:24 | 50.037
2020-01-26 | 21:24 | 50.035
2020-01-26 | 21:24 | 50.033
2020-01-26 | 21:24 | 50.032
2020-01-26 | 21:24 | 50.029
2020-01-26 | 21:24 | 50.028
2020-01-26 | 21:24 | 50.027
2020-01-26 | 21:24 | 50.027
2020-01-26 | 21:24 | 50.025
2020-01-26 | 21:24 | 50.022
2020-01-26 | 21:24 | 50.02
2020-01-26 | 21:24 | 50.02
2020-01-26 | 21:24 | 50.021
2020-01-26 | 21:24 | 50.023
2020-01-26 | 21:24 | 50.022
2020-01-26 | 21:24 | 50.022
2020-01-26 | 21:24 | 50.023
2020-01-26 | 21:24 | 50.025
2020-01-26 | 21:24 | 50.026
2020-01-26 | 21:24 | 50.028
2020-01-26 | 21:24 | 50.031
2020-01-26 | 21:24 | 50.034
2020-01-26 | 21:24 | 50.038
2020-01-26 | 21:24 | 50.041
2020-01-26 | 21:24 | 50.045
2020-01-26 | 21:24 | 50.047
2020-01-26 | 21:24 | 50.05
2020-01-26 | 21:24 | 50.053
2020-01-26 | 21:24 | 50.053
2020-01-26 | 21:24 | 50.055
2020-01-26 | 21:24 | 50.056
2020-01-26 | 21:24 | 50.056
2020-01-26 | 21:24 | 50.057
2020-01-26 | 21:24 | 50.056
2020-01-26 | 21:24 | 50.057
2020-01-26 | 21:24 | 50.057
2020-01-26 | 21:24 | 50.057
2020-01-26 | 21:24 | 50.058
2020-01-26 | 21:25 | 50.059
2020-01-26 | 21:25 | 50.062
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.063
2020-01-26 | 21:25 | 50.062
2020-01-26 | 21:25 | 50.061
2020-01-26 | 21:25 | 50.06
2020-01-26 | 21:25 | 50.061
2020-01-26 | 21:25 | 50.062
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.065
2020-01-26 | 21:25 | 50.068
2020-01-26 | 21:25 | 50.07
2020-01-26 | 21:25 | 50.07
2020-01-26 | 21:25 | 50.071
2020-01-26 | 21:25 | 50.071
2020-01-26 | 21:25 | 50.07
2020-01-26 | 21:25 | 50.07
2020-01-26 | 21:25 | 50.069
2020-01-26 | 21:25 | 50.067
2020-01-26 | 21:25 | 50.063
2020-01-26 | 21:25 | 50.065
2020-01-26 | 21:25 | 50.065
2020-01-26 | 21:25 | 50.067
2020-01-26 | 21:25 | 50.068
2020-01-26 | 21:25 | 50.067
2020-01-26 | 21:25 | 50.069
2020-01-26 | 21:25 | 50.069
2020-01-26 | 21:25 | 50.068
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.06
2020-01-26 | 21:25 | 50.056
2020-01-26 | 21:25 | 50.051
2020-01-26 | 21:25 | 50.048
2020-01-26 | 21:25 | 50.045
2020-01-26 | 21:25 | 50.042
2020-01-26 | 21:25 | 50.04
2020-01-26 | 21:25 | 50.042
2020-01-26 | 21:25 | 50.043
2020-01-26 | 21:25 | 50.044
2020-01-26 | 21:25 | 50.044
2020-01-26 | 21:25 | 50.046
2020-01-26 | 21:25 | 50.048
2020-01-26 | 21:25 | 50.05
2020-01-26 | 21:25 | 50.053
2020-01-26 | 21:25 | 50.055
2020-01-26 | 21:25 | 50.057
2020-01-26 | 21:25 | 50.058
2020-01-26 | 21:25 | 50.061
2020-01-26 | 21:25 | 50.062
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.064
2020-01-26 | 21:25 | 50.065
2020-01-26 | 21:25 | 50.065
2020-01-26 | 21:25 | 50.067
2020-01-26 | 21:25 | 50.069
2020-01-26 | 21:26 | 50.07
2020-01-26 | 21:26 | 50.071
2020-01-26 | 21:26 | 50.07
2020-01-26 | 21:26 | 50.069
2020-01-26 | 21:26 | 50.068
2020-01-26 | 21:26 | 50.069
2020-01-26 | 21:26 | 50.068
2020-01-26 | 21:26 | 50.069
2020-01-26 | 21:26 | 50.068
2020-01-26 | 21:26 | 50.068
2020-01-26 | 21:26 | 50.066
2020-01-26 | 21:26 | 50.066
2020-01-26 | 21:26 | 50.066
2020-01-26 | 21:26 | 50.065
2020-01-26 | 21:26 | 50.066
2020-01-26 | 21:26 | 50.067
2020-01-26 | 21:26 | 50.068
2020-01-26 | 21:26 | 50.069
2020-01-26 | 21:26 | 50.071
2020-01-26 | 21:26 | 50.073
2020-01-26 | 21:26 | 50.074
2020-01-26 | 21:26 | 50.076
2020-01-26 | 21:26 | 50.077
2020-01-26 | 21:26 | 50.077
2020-01-26 | 21:26 | 50.078
2020-01-26 | 21:26 | 50.078
2020-01-26 | 21:26 | 50.079
2020-01-26 | 21:26 | 50.081
2020-01-26 | 21:26 | 50.082
2020-01-26 | 21:26 | 50.083
2020-01-26 | 21:26 | 50.082
2020-01-26 | 21:26 | 50.081
2020-01-26 | 21:26 | 50.08
2020-01-26 | 21:26 | 50.08
2020-01-26 | 21:26 | 50.079
2020-01-26 | 21:26 | 50.081
2020-01-26 | 21:26 | 50.082
2020-01-26 | 21:26 | 50.084
2020-01-26 | 21:26 | 50.085
2020-01-26 | 21:26 | 50.084
2020-01-26 | 21:26 | 50.085
2020-01-26 | 21:26 | 50.084
2020-01-26 | 21:26 | 50.083
2020-01-26 | 21:26 | 50.083
2020-01-26 | 21:26 | 50.083
2020-01-26 | 21:26 | 50.081
2020-01-26 | 21:26 | 50.08
2020-01-26 | 21:26 | 50.081
2020-01-26 | 21:26 | 50.081
2020-01-26 | 21:26 | 50.083
2020-01-26 | 21:26 | 50.085
2020-01-26 | 21:26 | 50.087
2020-01-26 | 21:26 | 50.086
2020-01-26 | 21:26 | 50.085
2020-01-26 | 21:26 | 50.087
2020-01-26 | 21:26 | 50.09
2020-01-26 | 21:26 | 50.091
2020-01-26 | 21:26 | 50.09
2020-01-26 | 21:26 | 50.092
2020-01-26 | 21:26 | 50.096
2020-01-26 | 21:26 | 50.098
2020-01-26 | 21:27 | 50.102
2020-01-26 | 21:27 | 50.107
2020-01-26 | 21:27 | 50.11
2020-01-26 | 21:27 | 50.115
2020-01-26 | 21:27 | 50.12
2020-01-26 | 21:27 | 50.125
2020-01-26 | 21:27 | 50.128
2020-01-26 | 21:27 | 50.129
2020-01-26 | 21:27 | 50.13
2020-01-26 | 21:27 | 50.129
2020-01-26 | 21:27 | 50.126
2020-01-26 | 21:27 | 50.126
2020-01-26 | 21:27 | 50.127
2020-01-26 | 21:27 | 50.127
2020-01-26 | 21:27 | 50.131
2020-01-26 | 21:27 | 50.133
2020-01-26 | 21:27 | 50.134
2020-01-26 | 21:27 | 50.136
2020-01-26 | 21:27 | 50.14
2020-01-26 | 21:27 | 50.141
2020-01-26 | 21:27 | 50.145
2020-01-26 | 21:27 | 50.147
2020-01-26 | 21:27 | 50.147
2020-01-26 | 21:27 | 50.148
2020-01-26 | 21:27 | 50.148
2020-01-26 | 21:27 | 50.148
2020-01-26 | 21:27 | 50.148
2020-01-26 | 21:27 | 50.148
2020-01-26 | 21:27 | 50.147
2020-01-26 | 21:27 | 50.146
2020-01-26 | 21:27 | 50.144
2020-01-26 | 21:27 | 50.143
2020-01-26 | 21:27 | 50.142
2020-01-26 | 21:27 | 50.143
2020-01-26 | 21:27 | 50.141
2020-01-26 | 21:27 | 50.14
2020-01-26 | 21:27 | 50.14
2020-01-26 | 21:27 | 50.138
2020-01-26 | 21:27 | 50.136
2020-01-26 | 21:27 | 50.134
2020-01-26 | 21:27 | 50.133
2020-01-26 | 21:27 | 50.134
2020-01-26 | 21:27 | 50.136
2020-01-26 | 21:27 | 50.137
2020-01-26 | 21:27 | 50.137
2020-01-26 | 21:27 | 50.137
2020-01-26 | 21:27 | 50.135
2020-01-26 | 21:27 | 50.134
2020-01-26 | 21:27 | 50.132
2020-01-26 | 21:27 | 50.131
2020-01-26 | 21:27 | 50.13
2020-01-26 | 21:27 | 50.129
2020-01-26 | 21:27 | 50.128
2020-01-26 | 21:27 | 50.129
2020-01-26 | 21:27 | 50.129
2020-01-26 | 21:27 | 50.13
2020-01-26 | 21:27 | 50.132
2020-01-26 | 21:27 | 50.134
2020-01-26 | 21:27 | 50.136
2020-01-26 | 21:28 | 50.137
2020-01-26 | 21:28 | 50.137
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.137
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.135
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.131
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.134
2020-01-26 | 21:28 | 50.134
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.132
2020-01-26 | 21:28 | 50.13
2020-01-26 | 21:28 | 50.129
2020-01-26 | 21:28 | 50.13
2020-01-26 | 21:28 | 50.13
2020-01-26 | 21:28 | 50.131
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.132
2020-01-26 | 21:28 | 50.131
2020-01-26 | 21:28 | 50.131
2020-01-26 | 21:28 | 50.132
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.135
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.139
2020-01-26 | 21:28 | 50.138
2020-01-26 | 21:28 | 50.137
2020-01-26 | 21:28 | 50.137
2020-01-26 | 21:28 | 50.136
2020-01-26 | 21:28 | 50.136
2020-01-26 | 21:28 | 50.134
2020-01-26 | 21:28 | 50.133
2020-01-26 | 21:28 | 50.13
2020-01-26 | 21:28 | 50.128
2020-01-26 | 21:28 | 50.126
2020-01-26 | 21:28 | 50.126
2020-01-26 | 21:28 | 50.126
2020-01-26 | 21:28 | 50.124
2020-01-26 | 21:28 | 50.124
2020-01-26 | 21:28 | 50.124
2020-01-26 | 21:28 | 50.125
2020-01-26 | 21:28 | 50.127
2020-01-26 | 21:28 | 50.127
2020-01-26 | 21:28 | 50.129
2020-01-26 | 21:28 | 50.129
2020-01-26 | 21:28 | 50.128
2020-01-26 | 21:28 | 50.127
2020-01-26 | 21:28 | 50.126
2020-01-26 | 21:28 | 50.126
2020-01-26 | 21:28 | 50.127
2020-01-26 | 21:28 | 50.129
2020-01-26 | 21:28 | 50.132
2020-01-26 | 21:29 | 50.13
2020-01-26 | 21:29 | 50.13
2020-01-26 | 21:29 | 50.13
2020-01-26 | 21:29 | 50.133
2020-01-26 | 21:29 | 50.135
2020-01-26 | 21:29 | 50.137
2020-01-26 | 21:29 | 50.138
2020-01-26 | 21:29 | 50.137
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.138
2020-01-26 | 21:29 | 50.137
2020-01-26 | 21:29 | 50.138
2020-01-26 | 21:29 | 50.136
2020-01-26 | 21:29 | 50.134
2020-01-26 | 21:29 | 50.133
2020-01-26 | 21:29 | 50.133
2020-01-26 | 21:29 | 50.134
2020-01-26 | 21:29 | 50.136
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.141
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.141
2020-01-26 | 21:29 | 50.142
2020-01-26 | 21:29 | 50.141
2020-01-26 | 21:29 | 50.141
2020-01-26 | 21:29 | 50.141
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.14
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.137
2020-01-26 | 21:29 | 50.135
2020-01-26 | 21:29 | 50.134
2020-01-26 | 21:29 | 50.134
2020-01-26 | 21:29 | 50.135
2020-01-26 | 21:29 | 50.134
2020-01-26 | 21:29 | 50.13
2020-01-26 | 21:29 | 50.127
2020-01-26 | 21:29 | 50.127
2020-01-26 | 21:29 | 50.127
2020-01-26 | 21:29 | 50.127
2020-01-26 | 21:29 | 50.129
2020-01-26 | 21:29 | 50.129
2020-01-26 | 21:29 | 50.131
2020-01-26 | 21:29 | 50.132
2020-01-26 | 21:29 | 50.134
2020-01-26 | 21:29 | 50.138
2020-01-26 | 21:29 | 50.139
2020-01-26 | 21:29 | 50.142
2020-01-26 | 21:29 | 50.142
2020-01-26 | 21:29 | 50.144
2020-01-26 | 21:29 | 50.144
2020-01-26 | 21:29 | 50.145
2020-01-26 | 21:29 | 50.145
2020-01-26 | 21:30 | 50.146
2020-01-26 | 21:30 | 50.147
2020-01-26 | 21:30 | 50.147
2020-01-26 | 21:30 | 50.145
2020-01-26 | 21:30 | 50.143
2020-01-26 | 21:30 | 50.141
2020-01-26 | 21:30 | 50.139
2020-01-26 | 21:30 | 50.141
2020-01-26 | 21:30 | 50.14
2020-01-26 | 21:30 | 50.142
2020-01-26 | 21:30 | 50.141
2020-01-26 | 21:30 | 50.139
2020-01-26 | 21:30 | 50.136
2020-01-26 | 21:30 | 50.132
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.128
2020-01-26 | 21:30 | 50.128
2020-01-26 | 21:30 | 50.129
2020-01-26 | 21:30 | 50.129
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.131
2020-01-26 | 21:30 | 50.131
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.13
2020-01-26 | 21:30 | 50.129
2020-01-26 | 21:30 | 50.128
2020-01-26 | 21:30 | 50.128
2020-01-26 | 21:30 | 50.128
2020-01-26 | 21:30 | 50.127
2020-01-26 | 21:30 | 50.126
2020-01-26 | 21:30 | 50.127
2020-01-26 | 21:30 | 50.127
2020-01-26 | 21:30 | 50.127
2020-01-26 | 21:30 | 50.123
2020-01-26 | 21:30 | 50.121
2020-01-26 | 21:30 | 50.118
2020-01-26 | 21:30 | 50.116
2020-01-26 | 21:30 | 50.113
2020-01-26 | 21:30 | 50.111
2020-01-26 | 21:30 | 50.108
2020-01-26 | 21:30 | 50.106
2020-01-26 | 21:30 | 50.102
2020-01-26 | 21:30 | 50.102
2020-01-26 | 21:30 | 50.101
2020-01-26 | 21:30 | 50.102
2020-01-26 | 21:30 | 50.103
2020-01-26 | 21:30 | 50.106
2020-01-26 | 21:30 | 50.109
2020-01-26 | 21:30 | 50.112
2020-01-26 | 21:30 | 50.114
2020-01-26 | 21:30 | 50.117
2020-01-26 | 21:30 | 50.119
2020-01-26 | 21:30 | 50.12
2020-01-26 | 21:30 | 50.121
2020-01-26 | 21:30 | 50.121
2020-01-26 | 21:30 | 50.123
2020-01-26 | 21:30 | 50.125
2020-01-26 | 21:30 | 50.126
2020-01-26 | 21:31 | 50.126
2020-01-26 | 21:31 | 50.126
2020-01-26 | 21:31 | 50.125
2020-01-26 | 21:31 | 50.123
2020-01-26 | 21:31 | 50.123
2020-01-26 | 21:31 | 50.123
2020-01-26 | 21:31 | 50.121
2020-01-26 | 21:31 | 50.12
2020-01-26 | 21:31 | 50.119
2020-01-26 | 21:31 | 50.12
2020-01-26 | 21:31 | 50.12
2020-01-26 | 21:31 | 50.118
2020-01-26 | 21:31 | 50.118
2020-01-26 | 21:31 | 50.118
2020-01-26 | 21:31 | 50.118
2020-01-26 | 21:31 | 50.118
2020-01-26 | 21:31 | 50.117
2020-01-26 | 21:31 | 50.117
2020-01-26 | 21:31 | 50.116
2020-01-26 | 21:31 | 50.114
2020-01-26 | 21:31 | 50.113
2020-01-26 | 21:31 | 50.11
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.103
2020-01-26 | 21:31 | 50.101
2020-01-26 | 21:31 | 50.102
2020-01-26 | 21:31 | 50.103
2020-01-26 | 21:31 | 50.103
2020-01-26 | 21:31 | 50.105
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.107
2020-01-26 | 21:31 | 50.108
2020-01-26 | 21:31 | 50.108
2020-01-26 | 21:31 | 50.105
2020-01-26 | 21:31 | 50.101
2020-01-26 | 21:31 | 50.099
2020-01-26 | 21:31 | 50.098
2020-01-26 | 21:31 | 50.098
2020-01-26 | 21:31 | 50.099
2020-01-26 | 21:31 | 50.099
2020-01-26 | 21:31 | 50.1
2020-01-26 | 21:31 | 50.099
2020-01-26 | 21:31 | 50.1
2020-01-26 | 21:31 | 50.101
2020-01-26 | 21:31 | 50.101
2020-01-26 | 21:31 | 50.103
2020-01-26 | 21:31 | 50.104
2020-01-26 | 21:31 | 50.104
2020-01-26 | 21:31 | 50.104
2020-01-26 | 21:31 | 50.104
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.107
2020-01-26 | 21:31 | 50.107
2020-01-26 | 21:31 | 50.106
2020-01-26 | 21:31 | 50.105
2020-01-26 | 21:32 | 50.105
2020-01-26 | 21:32 | 50.105
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.105
2020-01-26 | 21:32 | 50.105
2020-01-26 | 21:32 | 50.107
2020-01-26 | 21:32 | 50.107
2020-01-26 | 21:32 | 50.107
2020-01-26 | 21:32 | 50.106
2020-01-26 | 21:32 | 50.106
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.101
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.105
2020-01-26 | 21:32 | 50.106
2020-01-26 | 21:32 | 50.109
2020-01-26 | 21:32 | 50.113
2020-01-26 | 21:32 | 50.117
2020-01-26 | 21:32 | 50.119
2020-01-26 | 21:32 | 50.12
2020-01-26 | 21:32 | 50.118
2020-01-26 | 21:32 | 50.118
2020-01-26 | 21:32 | 50.117
2020-01-26 | 21:32 | 50.116
2020-01-26 | 21:32 | 50.117
2020-01-26 | 21:32 | 50.118
2020-01-26 | 21:32 | 50.119
2020-01-26 | 21:32 | 50.119
2020-01-26 | 21:32 | 50.118
2020-01-26 | 21:32 | 50.118
2020-01-26 | 21:32 | 50.116
2020-01-26 | 21:32 | 50.113
2020-01-26 | 21:32 | 50.113
2020-01-26 | 21:32 | 50.112
2020-01-26 | 21:32 | 50.112
2020-01-26 | 21:32 | 50.113
2020-01-26 | 21:32 | 50.113
2020-01-26 | 21:32 | 50.114
2020-01-26 | 21:32 | 50.115
2020-01-26 | 21:32 | 50.115
2020-01-26 | 21:32 | 50.114
2020-01-26 | 21:32 | 50.114
2020-01-26 | 21:32 | 50.112
2020-01-26 | 21:32 | 50.111
2020-01-26 | 21:32 | 50.108
2020-01-26 | 21:32 | 50.104
2020-01-26 | 21:32 | 50.101
2020-01-26 | 21:32 | 50.099
2020-01-26 | 21:32 | 50.099
2020-01-26 | 21:32 | 50.097
2020-01-26 | 21:32 | 50.097
2020-01-26 | 21:32 | 50.099
2020-01-26 | 21:32 | 50.102
2020-01-26 | 21:33 | 50.103
2020-01-26 | 21:33 | 50.104
2020-01-26 | 21:33 | 50.103
2020-01-26 | 21:33 | 50.103
2020-01-26 | 21:33 | 50.104
2020-01-26 | 21:33 | 50.105
2020-01-26 | 21:33 | 50.105
2020-01-26 | 21:33 | 50.106
2020-01-26 | 21:33 | 50.108
2020-01-26 | 21:33 | 50.11
2020-01-26 | 21:33 | 50.11
2020-01-26 | 21:33 | 50.114
2020-01-26 | 21:33 | 50.116
2020-01-26 | 21:33 | 50.12
2020-01-26 | 21:33 | 50.123
2020-01-26 | 21:33 | 50.127
2020-01-26 | 21:33 | 50.13
2020-01-26 | 21:33 | 50.13
2020-01-26 | 21:33 | 50.131
2020-01-26 | 21:33 | 50.129
2020-01-26 | 21:33 | 50.128
2020-01-26 | 21:33 | 50.125
2020-01-26 | 21:33 | 50.124
2020-01-26 | 21:33 | 50.125
2020-01-26 | 21:33 | 50.124
2020-01-26 | 21:33 | 50.125
2020-01-26 | 21:33 | 50.124
2020-01-26 | 21:33 | 50.124
2020-01-26 | 21:33 | 50.124
2020-01-26 | 21:33 | 50.124
2020-01-26 | 21:33 | 50.122
2020-01-26 | 21:33 | 50.12
2020-01-26 | 21:33 | 50.118
2020-01-26 | 21:33 | 50.117
2020-01-26 | 21:33 | 50.116
2020-01-26 | 21:33 | 50.114
2020-01-26 | 21:33 | 50.114
2020-01-26 | 21:33 | 50.113
2020-01-26 | 21:33 | 50.113
2020-01-26 | 21:33 | 50.113
2020-01-26 | 21:33 | 50.115
2020-01-26 | 21:33 | 50.117
2020-01-26 | 21:33 | 50.121
2020-01-26 | 21:33 | 50.121
2020-01-26 | 21:33 | 50.125
2020-01-26 | 21:33 | 50.127
2020-01-26 | 21:33 | 50.13
2020-01-26 | 21:33 | 50.132
2020-01-26 | 21:33 | 50.134
2020-01-26 | 21:33 | 50.133
2020-01-26 | 21:33 | 50.132
2020-01-26 | 21:33 | 50.132
2020-01-26 | 21:33 | 50.132
2020-01-26 | 21:33 | 50.133
2020-01-26 | 21:33 | 50.134
2020-01-26 | 21:33 | 50.133
2020-01-26 | 21:33 | 50.135
2020-01-26 | 21:33 | 50.136
2020-01-26 | 21:33 | 50.138
2020-01-26 | 21:33 | 50.138
2020-01-26 | 21:34 | 50.136
2020-01-26 | 21:34 | 50.135
2020-01-26 | 21:34 | 50.134
2020-01-26 | 21:34 | 50.132
2020-01-26 | 21:34 | 50.131
2020-01-26 | 21:34 | 50.13
2020-01-26 | 21:34 | 50.13
2020-01-26 | 21:34 | 50.129
2020-01-26 | 21:34 | 50.127
2020-01-26 | 21:34 | 50.126
2020-01-26 | 21:34 | 50.124
2020-01-26 | 21:34 | 50.122
2020-01-26 | 21:34 | 50.119
2020-01-26 | 21:34 | 50.117
2020-01-26 | 21:34 | 50.113
2020-01-26 | 21:34 | 50.11
2020-01-26 | 21:34 | 50.109
2020-01-26 | 21:34 | 50.106
2020-01-26 | 21:34 | 50.101
2020-01-26 | 21:34 | 50.102
2020-01-26 | 21:34 | 50.102
2020-01-26 | 21:34 | 50.103
2020-01-26 | 21:34 | 50.105
2020-01-26 | 21:34 | 50.106
2020-01-26 | 21:34 | 50.106
2020-01-26 | 21:34 | 50.106
2020-01-26 | 21:34 | 50.108
2020-01-26 | 21:34 | 50.109
2020-01-26 | 21:34 | 50.111
2020-01-26 | 21:34 | 50.114
2020-01-26 | 21:34 | 50.117
2020-01-26 | 21:34 | 50.118
2020-01-26 | 21:34 | 50.117
2020-01-26 | 21:34 | 50.118
2020-01-26 | 21:34 | 50.117
2020-01-26 | 21:34 | 50.116
2020-01-26 | 21:34 | 50.116
2020-01-26 | 21:34 | 50.115
2020-01-26 | 21:34 | 50.117
2020-01-26 | 21:34 | 50.119
2020-01-26 | 21:34 | 50.12
2020-01-26 | 21:34 | 50.122
2020-01-26 | 21:34 | 50.123
2020-01-26 | 21:34 | 50.126
2020-01-26 | 21:34 | 50.129
2020-01-26 | 21:34 | 50.132
2020-01-26 | 21:34 | 50.134
2020-01-26 | 21:34 | 50.134
2020-01-26 | 21:34 | 50.133
2020-01-26 | 21:34 | 50.133
2020-01-26 | 21:34 | 50.131
2020-01-26 | 21:34 | 50.128
2020-01-26 | 21:34 | 50.126
2020-01-26 | 21:34 | 50.125
2020-01-26 | 21:34 | 50.124
2020-01-26 | 21:34 | 50.121
2020-01-26 | 21:34 | 50.119
2020-01-26 | 21:34 | 50.121
2020-01-26 | 21:34 | 50.123
2020-01-26 | 21:34 | 50.125
2020-01-26 | 21:34 | 50.127
2020-01-26 | 21:35 | 50.134
2020-01-26 | 21:35 | 50.138
2020-01-26 | 21:35 | 50.141
2020-01-26 | 21:35 | 50.144
2020-01-26 | 21:35 | 50.144
2020-01-26 | 21:35 | 50.144
2020-01-26 | 21:35 | 50.143
2020-01-26 | 21:35 | 50.142
2020-01-26 | 21:35 | 50.141
2020-01-26 | 21:35 | 50.143
2020-01-26 | 21:35 | 50.145
2020-01-26 | 21:35 | 50.147
2020-01-26 | 21:35 | 50.149
2020-01-26 | 21:35 | 50.151
2020-01-26 | 21:35 | 50.153
2020-01-26 | 21:35 | 50.154
2020-01-26 | 21:35 | 50.154
2020-01-26 | 21:35 | 50.155
2020-01-26 | 21:35 | 50.156
2020-01-26 | 21:35 | 50.157
2020-01-26 | 21:35 | 50.157
2020-01-26 | 21:35 | 50.157
2020-01-26 | 21:35 | 50.159
2020-01-26 | 21:35 | 50.161
2020-01-26 | 21:35 | 50.162
2020-01-26 | 21:35 | 50.164
2020-01-26 | 21:35 | 50.162
2020-01-26 | 21:35 | 50.162
2020-01-26 | 21:35 | 50.165
2020-01-26 | 21:35 | 50.165
2020-01-26 | 21:35 | 50.165
2020-01-26 | 21:35 | 50.163
2020-01-26 | 21:35 | 50.163
2020-01-26 | 21:35 | 50.163
2020-01-26 | 21:35 | 50.163
2020-01-26 | 21:35 | 50.164
2020-01-26 | 21:35 | 50.163
2020-01-26 | 21:35 | 50.162
2020-01-26 | 21:35 | 50.162
2020-01-26 | 21:35 | 50.163
2020-01-26 | 21:35 | 50.165
2020-01-26 | 21:35 | 50.167
2020-01-26 | 21:35 | 50.17
2020-01-26 | 21:35 | 50.172
2020-01-26 | 21:35 | 50.174
2020-01-26 | 21:35 | 50.175
2020-01-26 | 21:35 | 50.176
2020-01-26 | 21:35 | 50.178
2020-01-26 | 21:35 | 50.18
2020-01-26 | 21:35 | 50.182
2020-01-26 | 21:35 | 50.183
2020-01-26 | 21:35 | 50.185
2020-01-26 | 21:35 | 50.185
2020-01-26 | 21:35 | 50.183
2020-01-26 | 21:35 | 50.183
2020-01-26 | 21:35 | 50.179
2020-01-26 | 21:35 | 50.175
2020-01-26 | 21:35 | 50.171
2020-01-26 | 21:35 | 50.167
2020-01-26 | 21:36 | 50.164
2020-01-26 | 21:36 | 50.161
2020-01-26 | 21:36 | 50.16
2020-01-26 | 21:36 | 50.158
2020-01-26 | 21:36 | 50.158
2020-01-26 | 21:36 | 50.16
2020-01-26 | 21:36 | 50.161
2020-01-26 | 21:36 | 50.159
2020-01-26 | 21:36 | 50.158
2020-01-26 | 21:36 | 50.159
2020-01-26 | 21:36 | 50.16
2020-01-26 | 21:36 | 50.161
2020-01-26 | 21:36 | 50.161
2020-01-26 | 21:36 | 50.161
2020-01-26 | 21:36 | 50.163
2020-01-26 | 21:36 | 50.163
2020-01-26 | 21:36 | 50.164
2020-01-26 | 21:36 | 50.165
2020-01-26 | 21:36 | 50.167
2020-01-26 | 21:36 | 50.168
2020-01-26 | 21:36 | 50.169
2020-01-26 | 21:36 | 50.169
2020-01-26 | 21:36 | 50.166
2020-01-26 | 21:36 | 50.165
2020-01-26 | 21:36 | 50.163
2020-01-26 | 21:36 | 50.162
2020-01-26 | 21:36 | 50.161
2020-01-26 | 21:36 | 50.159
2020-01-26 | 21:36 | 50.157
2020-01-26 | 21:36 | 50.156
2020-01-26 | 21:36 | 50.156
2020-01-26 | 21:36 | 50.157
2020-01-26 | 21:36 | 50.157
2020-01-26 | 21:36 | 50.157
2020-01-26 | 21:36 | 50.157
2020-01-26 | 21:36 | 50.158
2020-01-26 | 21:36 | 50.16
2020-01-26 | 21:36 | 50.162
2020-01-26 | 21:36 | 50.16
2020-01-26 | 21:36 | 50.158
2020-01-26 | 21:36 | 50.154
2020-01-26 | 21:36 | 50.151
2020-01-26 | 21:36 | 50.147
2020-01-26 | 21:36 | 50.145
2020-01-26 | 21:36 | 50.142
2020-01-26 | 21:36 | 50.139
2020-01-26 | 21:36 | 50.136
2020-01-26 | 21:36 | 50.132
2020-01-26 | 21:36 | 50.131
2020-01-26 | 21:36 | 50.129
2020-01-26 | 21:36 | 50.126
2020-01-26 | 21:36 | 50.123
2020-01-26 | 21:36 | 50.121
2020-01-26 | 21:36 | 50.119
2020-01-26 | 21:36 | 50.116
2020-01-26 | 21:36 | 50.115
2020-01-26 | 21:36 | 50.113
2020-01-26 | 21:36 | 50.112
2020-01-26 | 21:36 | 50.112
2020-01-26 | 21:36 | 50.113
2020-01-26 | 21:36 | 50.113
2020-01-26 | 21:37 | 50.114
2020-01-26 | 21:37 | 50.115
2020-01-26 | 21:37 | 50.116
2020-01-26 | 21:37 | 50.118
2020-01-26 | 21:37 | 50.119
2020-01-26 | 21:37 | 50.119
2020-01-26 | 21:37 | 50.119
2020-01-26 | 21:37 | 50.119
2020-01-26 | 21:37 | 50.12
2020-01-26 | 21:37 | 50.124
2020-01-26 | 21:37 | 50.126
2020-01-26 | 21:37 | 50.127
2020-01-26 | 21:37 | 50.129
2020-01-26 | 21:37 | 50.128
2020-01-26 | 21:37 | 50.127
2020-01-26 | 21:37 | 50.126
2020-01-26 | 21:37 | 50.125
2020-01-26 | 21:37 | 50.123
2020-01-26 | 21:37 | 50.122
2020-01-26 | 21:37 | 50.119
2020-01-26 | 21:37 | 50.118
2020-01-26 | 21:37 | 50.117
2020-01-26 | 21:37 | 50.118
2020-01-26 | 21:37 | 50.12
2020-01-26 | 21:37 | 50.121
2020-01-26 | 21:37 | 50.123
2020-01-26 | 21:37 | 50.123
2020-01-26 | 21:37 | 50.124
2020-01-26 | 21:37 | 50.124
2020-01-26 | 21:37 | 50.123
2020-01-26 | 21:37 | 50.122
2020-01-26 | 21:37 | 50.121
2020-01-26 | 21:37 | 50.12
2020-01-26 | 21:37 | 50.121
2020-01-26 | 21:37 | 50.119
2020-01-26 | 21:37 | 50.12
2020-01-26 | 21:37 | 50.12
2020-01-26 | 21:37 | 50.121
2020-01-26 | 21:37 | 50.121
2020-01-26 | 21:37 | 50.122
2020-01-26 | 21:37 | 50.123
2020-01-26 | 21:37 | 50.125
2020-01-26 | 21:37 | 50.126
2020-01-26 | 21:37 | 50.127
2020-01-26 | 21:37 | 50.125
2020-01-26 | 21:37 | 50.124
2020-01-26 | 21:37 | 50.125
2020-01-26 | 21:37 | 50.126
2020-01-26 | 21:37 | 50.127
2020-01-26 | 21:37 | 50.127
2020-01-26 | 21:37 | 50.126
2020-01-26 | 21:37 | 50.127
2020-01-26 | 21:37 | 50.128
2020-01-26 | 21:37 | 50.129
2020-01-26 | 21:37 | 50.129
2020-01-26 | 21:37 | 50.129
2020-01-26 | 21:37 | 50.13
2020-01-26 | 21:37 | 50.13
2020-01-26 | 21:37 | 50.128
2020-01-26 | 21:38 | 50.128
2020-01-26 | 21:38 | 50.126
2020-01-26 | 21:38 | 50.126
2020-01-26 | 21:38 | 50.124
2020-01-26 | 21:38 | 50.121
2020-01-26 | 21:38 | 50.117
2020-01-26 | 21:38 | 50.113
2020-01-26 | 21:38 | 50.108
2020-01-26 | 21:38 | 50.107
2020-01-26 | 21:38 | 50.106
2020-01-26 | 21:38 | 50.105
2020-01-26 | 21:38 | 50.102
2020-01-26 | 21:38 | 50.098
2020-01-26 | 21:38 | 50.096
2020-01-26 | 21:38 | 50.095
2020-01-26 | 21:38 | 50.097
2020-01-26 | 21:38 | 50.097
2020-01-26 | 21:38 | 50.097
2020-01-26 | 21:38 | 50.098
2020-01-26 | 21:38 | 50.098
2020-01-26 | 21:38 | 50.097
2020-01-26 | 21:38 | 50.095
2020-01-26 | 21:38 | 50.092
2020-01-26 | 21:38 | 50.091
2020-01-26 | 21:38 | 50.091
2020-01-26 | 21:38 | 50.092
2020-01-26 | 21:38 | 50.091
2020-01-26 | 21:38 | 50.092
2020-01-26 | 21:38 | 50.091
2020-01-26 | 21:38 | 50.091
2020-01-26 | 21:38 | 50.091
2020-01-26 | 21:38 | 50.092
2020-01-26 | 21:38 | 50.09
2020-01-26 | 21:38 | 50.089
2020-01-26 | 21:38 | 50.088
2020-01-26 | 21:38 | 50.087
2020-01-26 | 21:38 | 50.084
2020-01-26 | 21:38 | 50.081
2020-01-26 | 21:38 | 50.08
2020-01-26 | 21:38 | 50.08
2020-01-26 | 21:38 | 50.08
2020-01-26 | 21:38 | 50.078
2020-01-26 | 21:38 | 50.076
2020-01-26 | 21:38 | 50.072
2020-01-26 | 21:38 | 50.07
2020-01-26 | 21:38 | 50.069
2020-01-26 | 21:38 | 50.069
2020-01-26 | 21:38 | 50.069
2020-01-26 | 21:38 | 50.072
2020-01-26 | 21:38 | 50.075
2020-01-26 | 21:38 | 50.077
2020-01-26 | 21:38 | 50.078
2020-01-26 | 21:38 | 50.077
2020-01-26 | 21:38 | 50.076
2020-01-26 | 21:38 | 50.076
2020-01-26 | 21:38 | 50.076
2020-01-26 | 21:38 | 50.074
2020-01-26 | 21:38 | 50.071
2020-01-26 | 21:38 | 50.068
2020-01-26 | 21:38 | 50.067
2020-01-26 | 21:38 | 50.067
2020-01-26 | 21:39 | 50.066
2020-01-26 | 21:39 | 50.065
2020-01-26 | 21:39 | 50.064
2020-01-26 | 21:39 | 50.064
2020-01-26 | 21:39 | 50.064
2020-01-26 | 21:39 | 50.064
2020-01-26 | 21:39 | 50.06
2020-01-26 | 21:39 | 50.057
2020-01-26 | 21:39 | 50.053
2020-01-26 | 21:39 | 50.05
2020-01-26 | 21:39 | 50.044
2020-01-26 | 21:39 | 50.04
2020-01-26 | 21:39 | 50.036
2020-01-26 | 21:39 | 50.032
2020-01-26 | 21:39 | 50.03
2020-01-26 | 21:39 | 50.027
2020-01-26 | 21:39 | 50.026
2020-01-26 | 21:39 | 50.026
2020-01-26 | 21:39 | 50.026
2020-01-26 | 21:39 | 50.025
2020-01-26 | 21:39 | 50.024
2020-01-26 | 21:39 | 50.024
2020-01-26 | 21:39 | 50.024
2020-01-26 | 21:39 | 50.022
2020-01-26 | 21:39 | 50.02
2020-01-26 | 21:39 | 50.02
2020-01-26 | 21:39 | 50.018
2020-01-26 | 21:39 | 50.015
2020-01-26 | 21:39 | 50.014
2020-01-26 | 21:39 | 50.012
2020-01-26 | 21:39 | 50.011
2020-01-26 | 21:39 | 50.01
2020-01-26 | 21:39 | 50.009
2020-01-26 | 21:39 | 50.01
2020-01-26 | 21:39 | 50.011
2020-01-26 | 21:39 | 50.013
2020-01-26 | 21:39 | 50.016
2020-01-26 | 21:39 | 50.017
2020-01-26 | 21:39 | 50.016
2020-01-26 | 21:39 | 50.016
2020-01-26 | 21:39 | 50.013
2020-01-26 | 21:39 | 50.011
2020-01-26 | 21:39 | 50.008
2020-01-26 | 21:39 | 50.006
2020-01-26 | 21:39 | 50.004
2020-01-26 | 21:39 | 50.002
2020-01-26 | 21:39 | 49.999
2020-01-26 | 21:39 | 49.998
2020-01-26 | 21:39 | 49.997
2020-01-26 | 21:39 | 49.995
2020-01-26 | 21:39 | 49.993
2020-01-26 | 21:39 | 49.992
2020-01-26 | 21:39 | 49.989
2020-01-26 | 21:39 | 49.986
2020-01-26 | 21:39 | 49.982
2020-01-26 | 21:39 | 49.979
2020-01-26 | 21:39 | 49.976
2020-01-26 | 21:39 | 49.974
2020-01-26 | 21:39 | 49.974
2020-01-26 | 21:40 | 49.973
2020-01-26 | 21:40 | 49.974
2020-01-26 | 21:40 | 49.977
2020-01-26 | 21:40 | 49.977
2020-01-26 | 21:40 | 49.976
2020-01-26 | 21:40 | 49.975
2020-01-26 | 21:40 | 49.972
2020-01-26 | 21:40 | 49.969
2020-01-26 | 21:40 | 49.965
2020-01-26 | 21:40 | 49.962
2020-01-26 | 21:40 | 49.962
2020-01-26 | 21:40 | 49.96
2020-01-26 | 21:40 | 49.959
2020-01-26 | 21:40 | 49.958
2020-01-26 | 21:40 | 49.957
2020-01-26 | 21:40 | 49.955
2020-01-26 | 21:40 | 49.955
2020-01-26 | 21:40 | 49.956
2020-01-26 | 21:40 | 49.957
2020-01-26 | 21:40 | 49.958
2020-01-26 | 21:40 | 49.96
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.962
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.962
2020-01-26 | 21:40 | 49.962
2020-01-26 | 21:40 | 49.963
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.961
2020-01-26 | 21:40 | 49.959
2020-01-26 | 21:40 | 49.957
2020-01-26 | 21:40 | 49.956
2020-01-26 | 21:40 | 49.954
2020-01-26 | 21:40 | 49.952
2020-01-26 | 21:40 | 49.951
2020-01-26 | 21:40 | 49.952
2020-01-26 | 21:40 | 49.954
2020-01-26 | 21:40 | 49.956
2020-01-26 | 21:40 | 49.959
2020-01-26 | 21:40 | 49.96
2020-01-26 | 21:40 | 49.962
2020-01-26 | 21:40 | 49.964
2020-01-26 | 21:40 | 49.964
2020-01-26 | 21:40 | 49.963
2020-01-26 | 21:40 | 49.964
2020-01-26 | 21:40 | 49.965
2020-01-26 | 21:40 | 49.967
2020-01-26 | 21:40 | 49.967
2020-01-26 | 21:40 | 49.969
2020-01-26 | 21:40 | 49.971
2020-01-26 | 21:40 | 49.972
2020-01-26 | 21:40 | 49.973
2020-01-26 | 21:40 | 49.972
2020-01-26 | 21:40 | 49.973
2020-01-26 | 21:40 | 49.973
2020-01-26 | 21:40 | 49.972
2020-01-26 | 21:40 | 49.972
2020-01-26 | 21:41 | 49.97
2020-01-26 | 21:41 | 49.968
2020-01-26 | 21:41 | 49.967
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.965
2020-01-26 | 21:41 | 49.965
2020-01-26 | 21:41 | 49.965
2020-01-26 | 21:41 | 49.962
2020-01-26 | 21:41 | 49.961
2020-01-26 | 21:41 | 49.959
2020-01-26 | 21:41 | 49.957
2020-01-26 | 21:41 | 49.955
2020-01-26 | 21:41 | 49.953
2020-01-26 | 21:41 | 49.952
2020-01-26 | 21:41 | 49.952
2020-01-26 | 21:41 | 49.953
2020-01-26 | 21:41 | 49.952
2020-01-26 | 21:41 | 49.95
2020-01-26 | 21:41 | 49.949
2020-01-26 | 21:41 | 49.945
2020-01-26 | 21:41 | 49.943
2020-01-26 | 21:41 | 49.944
2020-01-26 | 21:41 | 49.944
2020-01-26 | 21:41 | 49.945
2020-01-26 | 21:41 | 49.946
2020-01-26 | 21:41 | 49.948
2020-01-26 | 21:41 | 49.95
2020-01-26 | 21:41 | 49.953
2020-01-26 | 21:41 | 49.956
2020-01-26 | 21:41 | 49.958
2020-01-26 | 21:41 | 49.959
2020-01-26 | 21:41 | 49.96
2020-01-26 | 21:41 | 49.961
2020-01-26 | 21:41 | 49.962
2020-01-26 | 21:41 | 49.961
2020-01-26 | 21:41 | 49.963
2020-01-26 | 21:41 | 49.964
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.965
2020-01-26 | 21:41 | 49.964
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.966
2020-01-26 | 21:41 | 49.968
2020-01-26 | 21:41 | 49.969
2020-01-26 | 21:41 | 49.973
2020-01-26 | 21:41 | 49.976
2020-01-26 | 21:41 | 49.978
2020-01-26 | 21:41 | 49.981
2020-01-26 | 21:41 | 49.981
2020-01-26 | 21:41 | 49.982
2020-01-26 | 21:41 | 49.983
2020-01-26 | 21:41 | 49.982
2020-01-26 | 21:41 | 49.981
2020-01-26 | 21:41 | 49.981
2020-01-26 | 21:41 | 49.982
2020-01-26 | 21:41 | 49.98
2020-01-26 | 21:42 | 49.982
2020-01-26 | 21:42 | 49.984
2020-01-26 | 21:42 | 49.986
2020-01-26 | 21:42 | 49.988
2020-01-26 | 21:42 | 49.989
2020-01-26 | 21:42 | 49.99
2020-01-26 | 21:42 | 49.992
2020-01-26 | 21:42 | 49.993
2020-01-26 | 21:42 | 49.994
2020-01-26 | 21:42 | 49.996
2020-01-26 | 21:42 | 49.998
2020-01-26 | 21:42 | 50.001
2020-01-26 | 21:42 | 50.003
2020-01-26 | 21:42 | 50.004
2020-01-26 | 21:42 | 50.003
2020-01-26 | 21:42 | 50.004
2020-01-26 | 21:42 | 50.003
2020-01-26 | 21:42 | 50
2020-01-26 | 21:42 | 49.999
2020-01-26 | 21:42 | 49.999
2020-01-26 | 21:42 | 50
2020-01-26 | 21:42 | 49.999
2020-01-26 | 21:42 | 49.998
2020-01-26 | 21:42 | 49.997
2020-01-26 | 21:42 | 49.998
2020-01-26 | 21:42 | 50
2020-01-26 | 21:42 | 50.003
2020-01-26 | 21:42 | 50.003
2020-01-26 | 21:42 | 50.005
2020-01-26 | 21:42 | 50.006
2020-01-26 | 21:42 | 50.009
2020-01-26 | 21:42 | 50.011
2020-01-26 | 21:42 | 50.012
2020-01-26 | 21:42 | 50.014
2020-01-26 | 21:42 | 50.016
2020-01-26 | 21:42 | 50.017
2020-01-26 | 21:42 | 50.02
2020-01-26 | 21:42 | 50.022
2020-01-26 | 21:42 | 50.024
2020-01-26 | 21:42 | 50.025
2020-01-26 | 21:42 | 50.025
2020-01-26 | 21:42 | 50.024
2020-01-26 | 21:42 | 50.021
2020-01-26 | 21:42 | 50.018
2020-01-26 | 21:42 | 50.014
2020-01-26 | 21:42 | 50.013
2020-01-26 | 21:42 | 50.013
2020-01-26 | 21:42 | 50.015
2020-01-26 | 21:42 | 50.018
2020-01-26 | 21:42 | 50.02
2020-01-26 | 21:42 | 50.024
2020-01-26 | 21:42 | 50.026
2020-01-26 | 21:42 | 50.029
2020-01-26 | 21:42 | 50.032
2020-01-26 | 21:42 | 50.034
2020-01-26 | 21:42 | 50.036
2020-01-26 | 21:42 | 50.036
2020-01-26 | 21:42 | 50.037
2020-01-26 | 21:42 | 50.038
2020-01-26 | 21:42 | 50.036
2020-01-26 | 21:42 | 50.037
2020-01-26 | 21:43 | 50.036
2020-01-26 | 21:43 | 50.034
2020-01-26 | 21:43 | 50.034
2020-01-26 | 21:43 | 50.032
2020-01-26 | 21:43 | 50.032
2020-01-26 | 21:43 | 50.03
2020-01-26 | 21:43 | 50.03
2020-01-26 | 21:43 | 50.03
2020-01-26 | 21:43 | 50.029
2020-01-26 | 21:43 | 50.029
2020-01-26 | 21:43 | 50.03
2020-01-26 | 21:43 | 50.031
2020-01-26 | 21:43 | 50.033
2020-01-26 | 21:43 | 50.034
2020-01-26 | 21:43 | 50.035
2020-01-26 | 21:43 | 50.035
2020-01-26 | 21:43 | 50.035
2020-01-26 | 21:43 | 50.036
2020-01-26 | 21:43 | 50.039
2020-01-26 | 21:43 | 50.039
2020-01-26 | 21:43 | 50.04
2020-01-26 | 21:43 | 50.041
2020-01-26 | 21:43 | 50.043
2020-01-26 | 21:43 | 50.045
2020-01-26 | 21:43 | 50.047
2020-01-26 | 21:43 | 50.047
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:43 | 50.049
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:43 | 50.047
2020-01-26 | 21:43 | 50.044
2020-01-26 | 21:43 | 50.041
2020-01-26 | 21:43 | 50.04
2020-01-26 | 21:43 | 50.038
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.036
2020-01-26 | 21:43 | 50.036
2020-01-26 | 21:43 | 50.036
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.038
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.037
2020-01-26 | 21:43 | 50.038
2020-01-26 | 21:43 | 50.041
2020-01-26 | 21:43 | 50.042
2020-01-26 | 21:43 | 50.046
2020-01-26 | 21:43 | 50.046
2020-01-26 | 21:43 | 50.046
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:43 | 50.049
2020-01-26 | 21:43 | 50.049
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:43 | 50.047
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:43 | 50.048
2020-01-26 | 21:44 | 50.048
2020-01-26 | 21:44 | 50.05
2020-01-26 | 21:44 | 50.052
2020-01-26 | 21:44 | 50.054
2020-01-26 | 21:44 | 50.056
2020-01-26 | 21:44 | 50.056
2020-01-26 | 21:44 | 50.055
2020-01-26 | 21:44 | 50.054
2020-01-26 | 21:44 | 50.055
2020-01-26 | 21:44 | 50.054
2020-01-26 | 21:44 | 50.053
2020-01-26 | 21:44 | 50.05
2020-01-26 | 21:44 | 50.047
2020-01-26 | 21:44 | 50.045
2020-01-26 | 21:44 | 50.043
2020-01-26 | 21:44 | 50.043
2020-01-26 | 21:44 | 50.045
2020-01-26 | 21:44 | 50.045
2020-01-26 | 21:44 | 50.046
2020-01-26 | 21:44 | 50.047
2020-01-26 | 21:44 | 50.047
2020-01-26 | 21:44 | 50.049
2020-01-26 | 21:44 | 50.05
2020-01-26 | 21:44 | 50.053
2020-01-26 | 21:44 | 50.053
2020-01-26 | 21:44 | 50.055
2020-01-26 | 21:44 | 50.056
2020-01-26 | 21:44 | 50.057
2020-01-26 | 21:44 | 50.057
2020-01-26 | 21:44 | 50.057
2020-01-26 | 21:44 | 50.054
2020-01-26 | 21:44 | 50.054
2020-01-26 | 21:44 | 50.055
2020-01-26 | 21:44 | 50.057
2020-01-26 | 21:44 | 50.058
2020-01-26 | 21:44 | 50.061
2020-01-26 | 21:44 | 50.064
2020-01-26 | 21:44 | 50.063
2020-01-26 | 21:44 | 50.064
2020-01-26 | 21:44 | 50.064
2020-01-26 | 21:44 | 50.062
2020-01-26 | 21:44 | 50.06
2020-01-26 | 21:44 | 50.059
2020-01-26 | 21:44 | 50.058
2020-01-26 | 21:44 | 50.055
2020-01-26 | 21:44 | 50.051
2020-01-26 | 21:44 | 50.047
2020-01-26 | 21:44 | 50.043
2020-01-26 | 21:44 | 50.041
2020-01-26 | 21:44 | 50.039
2020-01-26 | 21:44 | 50.036
2020-01-26 | 21:44 | 50.036
2020-01-26 | 21:44 | 50.035
2020-01-26 | 21:44 | 50.034
2020-01-26 | 21:44 | 50.034
2020-01-26 | 21:44 | 50.034
2020-01-26 | 21:44 | 50.034
2020-01-26 | 21:44 | 50.035
2020-01-26 | 21:44 | 50.035
2020-01-26 | 21:44 | 50.034
2020-01-26 | 21:44 | 50.033
2020-01-26 | 21:45 | 50.032
2020-01-26 | 21:45 | 50.03
2020-01-26 | 21:45 | 50.03
2020-01-26 | 21:45 | 50.029
2020-01-26 | 21:45 | 50.029
2020-01-26 | 21:45 | 50.03
2020-01-26 | 21:45 | 50.032
2020-01-26 | 21:45 | 50.033
2020-01-26 | 21:45 | 50.035
2020-01-26 | 21:45 | 50.037
2020-01-26 | 21:45 | 50.036
2020-01-26 | 21:45 | 50.036
2020-01-26 | 21:45 | 50.034
2020-01-26 | 21:45 | 50.032
2020-01-26 | 21:45 | 50.031
2020-01-26 | 21:45 | 50.028
2020-01-26 | 21:45 | 50.027
2020-01-26 | 21:45 | 50.029
2020-01-26 | 21:45 | 50.029
2020-01-26 | 21:45 | 50.03
2020-01-26 | 21:45 | 50.029
2020-01-26 | 21:45 | 50.028
2020-01-26 | 21:45 | 50.026
2020-01-26 | 21:45 | 50.025
2020-01-26 | 21:45 | 50.025
2020-01-26 | 21:45 | 50.023
2020-01-26 | 21:45 | 50.022
2020-01-26 | 21:45 | 50.022
2020-01-26 | 21:45 | 50.021

## Event 20200127-1
In UTC
Date | Time | Freq
2020-01-27 | 11:28 | 49.943
2020-01-27 | 11:28 | 49.941
2020-01-27 | 11:28 | 49.94
2020-01-27 | 11:28 | 49.937
2020-01-27 | 11:28 | 49.938
2020-01-27 | 11:28 | 49.938
2020-01-27 | 11:28 | 49.937
2020-01-27 | 11:28 | 49.937
2020-01-27 | 11:28 | 49.939
2020-01-27 | 11:28 | 49.942
2020-01-27 | 11:28 | 49.942
2020-01-27 | 11:28 | 49.945
2020-01-27 | 11:28 | 49.945
2020-01-27 | 11:28 | 49.946
2020-01-27 | 11:28 | 49.948
2020-01-27 | 11:28 | 49.947
2020-01-27 | 11:28 | 49.946
2020-01-27 | 11:28 | 49.946
2020-01-27 | 11:28 | 49.944
2020-01-27 | 11:28 | 49.944
2020-01-27 | 11:28 | 49.943
2020-01-27 | 11:28 | 49.941
2020-01-27 | 11:28 | 49.939
2020-01-27 | 11:28 | 49.937
2020-01-27 | 11:28 | 49.932
2020-01-27 | 11:28 | 49.932
2020-01-27 | 11:28 | 49.931
2020-01-27 | 11:28 | 49.93
2020-01-27 | 11:28 | 49.929
2020-01-27 | 11:28 | 49.932
2020-01-27 | 11:28 | 49.934
2020-01-27 | 11:29 | 49.936
2020-01-27 | 11:29 | 49.939
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.941
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.94
2020-01-27 | 11:29 | 49.94
2020-01-27 | 11:29 | 49.942
2020-01-27 | 11:29 | 49.944
2020-01-27 | 11:29 | 49.947
2020-01-27 | 11:29 | 49.947
2020-01-27 | 11:29 | 49.948
2020-01-27 | 11:29 | 49.948
2020-01-27 | 11:29 | 49.947
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.943
2020-01-27 | 11:29 | 49.936
2020-01-27 | 11:29 | 49.908
2020-01-27 | 11:29 | 49.887
2020-01-27 | 11:29 | 49.873
2020-01-27 | 11:29 | 49.859
2020-01-27 | 11:29 | 49.851
2020-01-27 | 11:29 | 49.845
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.84
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.843
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.843
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.84
2020-01-27 | 11:29 | 49.84
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.844
2020-01-27 | 11:29 | 49.843
2020-01-27 | 11:29 | 49.841
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:29 | 49.844
2020-01-27 | 11:29 | 49.844
2020-01-27 | 11:29 | 49.845
2020-01-27 | 11:29 | 49.842
2020-01-27 | 11:30 | 49.84
2020-01-27 | 11:30 | 49.839
2020-01-27 | 11:30 | 49.839
2020-01-27 | 11:30 | 49.837
2020-01-27 | 11:30 | 49.838
2020-01-27 | 11:30 | 49.838
2020-01-27 | 11:30 | 49.836
2020-01-27 | 11:30 | 49.835
2020-01-27 | 11:30 | 49.833
2020-01-27 | 11:30 | 49.834
2020-01-27 | 11:30 | 49.836
2020-01-27 | 11:30 | 49.836
2020-01-27 | 11:30 | 49.838
2020-01-27 | 11:30 | 49.84
2020-01-27 | 11:30 | 49.842
2020-01-27 | 11:30 | 49.843
2020-01-27 | 11:30 | 49.844
2020-01-27 | 11:30 | 49.845
2020-01-27 | 11:30 | 49.846
2020-01-27 | 11:30 | 49.847
2020-01-27 | 11:30 | 49.848
2020-01-27 | 11:30 | 49.848
2020-01-27 | 11:30 | 49.848
2020-01-27 | 11:30 | 49.848
2020-01-27 | 11:30 | 49.849
2020-01-27 | 11:30 | 49.849
2020-01-27 | 11:30 | 49.848
2020-01-27 | 11:30 | 49.848
2020-01-27 | 11:30 | 49.85
2020-01-27 | 11:30 | 49.853
2020-01-27 | 11:30 | 49.853
2020-01-27 | 11:30 | 49.853
2020-01-27 | 11:30 | 49.852
2020-01-27 | 11:30 | 49.85
2020-01-27 | 11:30 | 49.85
2020-01-27 | 11:30 | 49.851
2020-01-27 | 11:30 | 49.855
2020-01-27 | 11:30 | 49.858
2020-01-27 | 11:30 | 49.864
2020-01-27 | 11:30 | 49.869
2020-01-27 | 11:30 | 49.873
2020-01-27 | 11:30 | 49.881
2020-01-27 | 11:30 | 49.886
2020-01-27 | 11:30 | 49.89
2020-01-27 | 11:30 | 49.892
2020-01-27 | 11:30 | 49.894
2020-01-27 | 11:30 | 49.896
2020-01-27 | 11:30 | 49.895
2020-01-27 | 11:30 | 49.894
2020-01-27 | 11:30 | 49.892
2020-01-27 | 11:30 | 49.892
2020-01-27 | 11:30 | 49.89
2020-01-27 | 11:30 | 49.889
2020-01-27 | 11:30 | 49.887
2020-01-27 | 11:30 | 49.886
2020-01-27 | 11:30 | 49.887
2020-01-27 | 11:30 | 49.886
2020-01-27 | 11:30 | 49.886
2020-01-27 | 11:30 | 49.884
2020-01-27 | 11:30 | 49.882
2020-01-27 | 11:30 | 49.883
2020-01-27 | 11:31 | 49.882
2020-01-27 | 11:31 | 49.882
2020-01-27 | 11:31 | 49.884
2020-01-27 | 11:31 | 49.885
2020-01-27 | 11:31 | 49.888
2020-01-27 | 11:31 | 49.887
2020-01-27 | 11:31 | 49.888
2020-01-27 | 11:31 | 49.888
2020-01-27 | 11:31 | 49.888
2020-01-27 | 11:31 | 49.89
2020-01-27 | 11:31 | 49.89
2020-01-27 | 11:31 | 49.891
2020-01-27 | 11:31 | 49.889
2020-01-27 | 11:31 | 49.886
2020-01-27 | 11:31 | 49.884
2020-01-27 | 11:31 | 49.881
2020-01-27 | 11:31 | 49.881
2020-01-27 | 11:31 | 49.878
2020-01-27 | 11:31 | 49.874
2020-01-27 | 11:31 | 49.871
2020-01-27 | 11:31 | 49.867
2020-01-27 | 11:31 | 49.862
2020-01-27 | 11:31 | 49.856
2020-01-27 | 11:31 | 49.854
2020-01-27 | 11:31 | 49.851
2020-01-27 | 11:31 | 49.848
2020-01-27 | 11:31 | 49.847
2020-01-27 | 11:31 | 49.846
2020-01-27 | 11:31 | 49.843
2020-01-27 | 11:31 | 49.843
2020-01-27 | 11:31 | 49.841
2020-01-27 | 11:31 | 49.842
2020-01-27 | 11:31 | 49.841
2020-01-27 | 11:31 | 49.839
2020-01-27 | 11:31 | 49.838
2020-01-27 | 11:31 | 49.838
2020-01-27 | 11:31 | 49.837
2020-01-27 | 11:31 | 49.836
2020-01-27 | 11:31 | 49.836
2020-01-27 | 11:31 | 49.835
2020-01-27 | 11:31 | 49.836
2020-01-27 | 11:31 | 49.835
2020-01-27 | 11:31 | 49.834
2020-01-27 | 11:31 | 49.836
2020-01-27 | 11:31 | 49.834
2020-01-27 | 11:31 | 49.833
2020-01-27 | 11:31 | 49.83
2020-01-27 | 11:31 | 49.829
2020-01-27 | 11:31 | 49.825
2020-01-27 | 11:31 | 49.823
2020-01-27 | 11:31 | 49.822
2020-01-27 | 11:31 | 49.821
2020-01-27 | 11:31 | 49.821
2020-01-27 | 11:31 | 49.821
2020-01-27 | 11:31 | 49.819
2020-01-27 | 11:31 | 49.819
2020-01-27 | 11:31 | 49.818
2020-01-27 | 11:31 | 49.819
2020-01-27 | 11:31 | 49.817
2020-01-27 | 11:32 | 49.818
2020-01-27 | 11:32 | 49.815
2020-01-27 | 11:32 | 49.813
2020-01-27 | 11:32 | 49.811
2020-01-27 | 11:32 | 49.811
2020-01-27 | 11:32 | 49.811
2020-01-27 | 11:32 | 49.815
2020-01-27 | 11:32 | 49.816
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.82
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.818
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.82
2020-01-27 | 11:32 | 49.821
2020-01-27 | 11:32 | 49.824
2020-01-27 | 11:32 | 49.829
2020-01-27 | 11:32 | 49.833
2020-01-27 | 11:32 | 49.835
2020-01-27 | 11:32 | 49.834
2020-01-27 | 11:32 | 49.83
2020-01-27 | 11:32 | 49.828
2020-01-27 | 11:32 | 49.824
2020-01-27 | 11:32 | 49.821
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.817
2020-01-27 | 11:32 | 49.815
2020-01-27 | 11:32 | 49.813
2020-01-27 | 11:32 | 49.811
2020-01-27 | 11:32 | 49.811
2020-01-27 | 11:32 | 49.809
2020-01-27 | 11:32 | 49.809
2020-01-27 | 11:32 | 49.81
2020-01-27 | 11:32 | 49.813
2020-01-27 | 11:32 | 49.814
2020-01-27 | 11:32 | 49.817
2020-01-27 | 11:32 | 49.82
2020-01-27 | 11:32 | 49.824
2020-01-27 | 11:32 | 49.825
2020-01-27 | 11:32 | 49.828
2020-01-27 | 11:32 | 49.829
2020-01-27 | 11:32 | 49.83
2020-01-27 | 11:32 | 49.83
2020-01-27 | 11:32 | 49.832
2020-01-27 | 11:32 | 49.831
2020-01-27 | 11:32 | 49.83
2020-01-27 | 11:32 | 49.829
2020-01-27 | 11:32 | 49.826
2020-01-27 | 11:32 | 49.826
2020-01-27 | 11:32 | 49.824
2020-01-27 | 11:32 | 49.822
2020-01-27 | 11:32 | 49.822
2020-01-27 | 11:32 | 49.82
2020-01-27 | 11:32 | 49.819
2020-01-27 | 11:32 | 49.817
2020-01-27 | 11:32 | 49.818
2020-01-27 | 11:32 | 49.82
2020-01-27 | 11:32 | 49.822
2020-01-27 | 11:33 | 49.826
2020-01-27 | 11:33 | 49.833
2020-01-27 | 11:33 | 49.839
2020-01-27 | 11:33 | 49.846
2020-01-27 | 11:33 | 49.854
2020-01-27 | 11:33 | 49.862
2020-01-27 | 11:33 | 49.87
2020-01-27 | 11:33 | 49.877
2020-01-27 | 11:33 | 49.884
2020-01-27 | 11:33 | 49.888
2020-01-27 | 11:33 | 49.89
2020-01-27 | 11:33 | 49.892
2020-01-27 | 11:33 | 49.894
2020-01-27 | 11:33 | 49.895
2020-01-27 | 11:33 | 49.896
2020-01-27 | 11:33 | 49.898
2020-01-27 | 11:33 | 49.901
2020-01-27 | 11:33 | 49.902
2020-01-27 | 11:33 | 49.907
2020-01-27 | 11:33 | 49.908
2020-01-27 | 11:33 | 49.912
2020-01-27 | 11:33 | 49.915
2020-01-27 | 11:33 | 49.919
2020-01-27 | 11:33 | 49.919
2020-01-27 | 11:33 | 49.921
2020-01-27 | 11:33 | 49.921
2020-01-27 | 11:33 | 49.922
2020-01-27 | 11:33 | 49.922
2020-01-27 | 11:33 | 49.92
2020-01-27 | 11:33 | 49.917
2020-01-27 | 11:33 | 49.914
2020-01-27 | 11:33 | 49.911
2020-01-27 | 11:33 | 49.909
2020-01-27 | 11:33 | 49.909
2020-01-27 | 11:33 | 49.906
2020-01-27 | 11:33 | 49.907
2020-01-27 | 11:33 | 49.907
2020-01-27 | 11:33 | 49.909
2020-01-27 | 11:33 | 49.909
2020-01-27 | 11:33 | 49.909
2020-01-27 | 11:33 | 49.912
2020-01-27 | 11:33 | 49.914
2020-01-27 | 11:33 | 49.918
2020-01-27 | 11:33 | 49.921
2020-01-27 | 11:33 | 49.922
2020-01-27 | 11:33 | 49.919
2020-01-27 | 11:33 | 49.915
2020-01-27 | 11:33 | 49.914
2020-01-27 | 11:33 | 49.914
2020-01-27 | 11:33 | 49.914
2020-01-27 | 11:33 | 49.913
2020-01-27 | 11:33 | 49.913
2020-01-27 | 11:33 | 49.914
2020-01-27 | 11:33 | 49.915
2020-01-27 | 11:33 | 49.917
2020-01-27 | 11:33 | 49.919
2020-01-27 | 11:33 | 49.92
2020-01-27 | 11:33 | 49.923
2020-01-27 | 11:33 | 49.922
2020-01-27 | 11:34 | 49.919
2020-01-27 | 11:34 | 49.919
2020-01-27 | 11:34 | 49.918
2020-01-27 | 11:34 | 49.919
2020-01-27 | 11:34 | 49.923
2020-01-27 | 11:34 | 49.929
2020-01-27 | 11:34 | 49.93
2020-01-27 | 11:34 | 49.932
2020-01-27 | 11:34 | 49.935
2020-01-27 | 11:34 | 49.937
2020-01-27 | 11:34 | 49.937
2020-01-27 | 11:34 | 49.939
2020-01-27 | 11:34 | 49.939
2020-01-27 | 11:34 | 49.94
2020-01-27 | 11:34 | 49.938
2020-01-27 | 11:34 | 49.94
2020-01-27 | 11:34 | 49.942
2020-01-27 | 11:34 | 49.945
2020-01-27 | 11:34 | 49.949
2020-01-27 | 11:34 | 49.95
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.954
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.951
2020-01-27 | 11:34 | 49.951
2020-01-27 | 11:34 | 49.95
2020-01-27 | 11:34 | 49.948
2020-01-27 | 11:34 | 49.949
2020-01-27 | 11:34 | 49.949
2020-01-27 | 11:34 | 49.944
2020-01-27 | 11:34 | 49.943
2020-01-27 | 11:34 | 49.943
2020-01-27 | 11:34 | 49.943
2020-01-27 | 11:34 | 49.944
2020-01-27 | 11:34 | 49.948
2020-01-27 | 11:34 | 49.949
2020-01-27 | 11:34 | 49.952
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.952
2020-01-27 | 11:34 | 49.954
2020-01-27 | 11:34 | 49.959
2020-01-27 | 11:34 | 49.959
2020-01-27 | 11:34 | 49.959
2020-01-27 | 11:34 | 49.959
2020-01-27 | 11:34 | 49.959
2020-01-27 | 11:34 | 49.955
2020-01-27 | 11:34 | 49.955
2020-01-27 | 11:34 | 49.954
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.95
2020-01-27 | 11:34 | 49.952
2020-01-27 | 11:34 | 49.951
2020-01-27 | 11:34 | 49.952
2020-01-27 | 11:34 | 49.953
2020-01-27 | 11:34 | 49.954
2020-01-27 | 11:34 | 49.955
2020-01-27 | 11:34 | 49.956
2020-01-27 | 11:34 | 49.957
2020-01-27 | 11:35 | 49.958
2020-01-27 | 11:35 | 49.96
2020-01-27 | 11:35 | 49.963
2020-01-27 | 11:35 | 49.966
2020-01-27 | 11:35 | 49.971
2020-01-27 | 11:35 | 49.973
2020-01-27 | 11:35 | 49.975
2020-01-27 | 11:35 | 49.975
2020-01-27 | 11:35 | 49.975
2020-01-27 | 11:35 | 49.975
2020-01-27 | 11:35 | 49.976
2020-01-27 | 11:35 | 49.976
2020-01-27 | 11:35 | 49.976
2020-01-27 | 11:35 | 49.978
2020-01-27 | 11:35 | 49.977
2020-01-27 | 11:35 | 49.979
2020-01-27 | 11:35 | 49.979
2020-01-27 | 11:35 | 49.978
2020-01-27 | 11:35 | 49.979
2020-01-27 | 11:35 | 49.978
2020-01-27 | 11:35 | 49.975
2020-01-27 | 11:35 | 49.972
2020-01-27 | 11:35 | 49.971
2020-01-27 | 11:35 | 49.969
2020-01-27 | 11:35 | 49.969
2020-01-27 | 11:35 | 49.97
2020-01-27 | 11:35 | 49.966
2020-01-27 | 11:35 | 49.964
2020-01-27 | 11:35 | 49.964
2020-01-27 | 11:35 | 49.964
2020-01-27 | 11:35 | 49.966
2020-01-27 | 11:35 | 49.967
2020-01-27 | 11:35 | 49.973
2020-01-27 | 11:35 | 49.977
2020-01-27 | 11:35 | 49.979
2020-01-27 | 11:35 | 49.98
2020-01-27 | 11:35 | 49.98
2020-01-27 | 11:35 | 49.978
2020-01-27 | 11:35 | 49.976
2020-01-27 | 11:35 | 49.972
2020-01-27 | 11:35 | 49.971
2020-01-27 | 11:35 | 49.967
2020-01-27 | 11:35 | 49.968
2020-01-27 | 11:35 | 49.965
2020-01-27 | 11:35 | 49.966
2020-01-27 | 11:35 | 49.966
2020-01-27 | 11:35 | 49.964
2020-01-27 | 11:35 | 49.963
2020-01-27 | 11:35 | 49.96
2020-01-27 | 11:35 | 49.958
2020-01-27 | 11:35 | 49.954
2020-01-27 | 11:35 | 49.953
2020-01-27 | 11:35 | 49.95
2020-01-27 | 11:35 | 49.947
2020-01-27 | 11:35 | 49.945
2020-01-27 | 11:35 | 49.943
2020-01-27 | 11:35 | 49.944
2020-01-27 | 11:35 | 49.945
2020-01-27 | 11:35 | 49.948
2020-01-27 | 11:36 | 49.948
2020-01-27 | 11:36 | 49.951
2020-01-27 | 11:36 | 49.953
2020-01-27 | 11:36 | 49.957
2020-01-27 | 11:36 | 49.961
2020-01-27 | 11:36 | 49.966
2020-01-27 | 11:36 | 49.967
2020-01-27 | 11:36 | 49.969
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.97
2020-01-27 | 11:36 | 49.969
2020-01-27 | 11:36 | 49.966
2020-01-27 | 11:36 | 49.967
2020-01-27 | 11:36 | 49.965
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.969
2020-01-27 | 11:36 | 49.969
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.967
2020-01-27 | 11:36 | 49.969
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.97
2020-01-27 | 11:36 | 49.97
2020-01-27 | 11:36 | 49.971
2020-01-27 | 11:36 | 49.97
2020-01-27 | 11:36 | 49.972
2020-01-27 | 11:36 | 49.972
2020-01-27 | 11:36 | 49.971
2020-01-27 | 11:36 | 49.971
2020-01-27 | 11:36 | 49.973
2020-01-27 | 11:36 | 49.973
2020-01-27 | 11:36 | 49.976
2020-01-27 | 11:36 | 49.98
2020-01-27 | 11:36 | 49.984
2020-01-27 | 11:36 | 49.985
2020-01-27 | 11:36 | 49.986
2020-01-27 | 11:36 | 49.988
2020-01-27 | 11:36 | 49.987
2020-01-27 | 11:36 | 49.991
2020-01-27 | 11:36 | 49.989
2020-01-27 | 11:36 | 49.991
2020-01-27 | 11:36 | 49.99
2020-01-27 | 11:36 | 49.989
2020-01-27 | 11:36 | 49.988
2020-01-27 | 11:36 | 49.987
2020-01-27 | 11:36 | 49.986
2020-01-27 | 11:36 | 49.984
2020-01-27 | 11:36 | 49.979
2020-01-27 | 11:36 | 49.976
2020-01-27 | 11:36 | 49.976
2020-01-27 | 11:36 | 49.973
2020-01-27 | 11:36 | 49.971
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.967
2020-01-27 | 11:36 | 49.969
2020-01-27 | 11:36 | 49.968
2020-01-27 | 11:36 | 49.967
2020-01-27 | 11:36 | 49.967
2020-01-27 | 11:36 | 49.966
2020-01-27 | 11:37 | 49.968
2020-01-27 | 11:37 | 49.972
2020-01-27 | 11:37 | 49.975
2020-01-27 | 11:37 | 49.978
2020-01-27 | 11:37 | 49.98
2020-01-27 | 11:37 | 49.983
2020-01-27 | 11:37 | 49.985
2020-01-27 | 11:37 | 49.986
2020-01-27 | 11:37 | 49.987
2020-01-27 | 11:37 | 49.988
2020-01-27 | 11:37 | 49.991
2020-01-27 | 11:37 | 49.987
2020-01-27 | 11:37 | 49.985
2020-01-27 | 11:37 | 49.982
2020-01-27 | 11:37 | 49.981
2020-01-27 | 11:37 | 49.978
2020-01-27 | 11:37 | 49.977
2020-01-27 | 11:37 | 49.974
2020-01-27 | 11:37 | 49.97
2020-01-27 | 11:37 | 49.968
2020-01-27 | 11:37 | 49.967
2020-01-27 | 11:37 | 49.964
2020-01-27 | 11:37 | 49.964
2020-01-27 | 11:37 | 49.962
2020-01-27 | 11:37 | 49.961
2020-01-27 | 11:37 | 49.96
2020-01-27 | 11:37 | 49.962
2020-01-27 | 11:37 | 49.961
2020-01-27 | 11:37 | 49.963
2020-01-27 | 11:37 | 49.962
2020-01-27 | 11:37 | 49.963
2020-01-27 | 11:37 | 49.965
2020-01-27 | 11:37 | 49.966
2020-01-27 | 11:37 | 49.968
2020-01-27 | 11:37 | 49.967
2020-01-27 | 11:37 | 49.969
2020-01-27 | 11:37 | 49.97
2020-01-27 | 11:37 | 49.969
2020-01-27 | 11:37 | 49.971
2020-01-27 | 11:37 | 49.971
2020-01-27 | 11:37 | 49.972
2020-01-27 | 11:37 | 49.971
2020-01-27 | 11:37 | 49.972
2020-01-27 | 11:37 | 49.973
2020-01-27 | 11:37 | 49.973
2020-01-27 | 11:37 | 49.973
2020-01-27 | 11:37 | 49.975
2020-01-27 | 11:37 | 49.977
2020-01-27 | 11:37 | 49.977
2020-01-27 | 11:37 | 49.977
2020-01-27 | 11:37 | 49.977
2020-01-27 | 11:37 | 49.978
2020-01-27 | 11:37 | 49.978
2020-01-27 | 11:37 | 49.978
2020-01-27 | 11:37 | 49.977
2020-01-27 | 11:37 | 49.975
2020-01-27 | 11:37 | 49.974
2020-01-27 | 11:37 | 49.972
2020-01-27 | 11:37 | 49.971
2020-01-27 | 11:38 | 49.971
2020-01-27 | 11:38 | 49.972
2020-01-27 | 11:38 | 49.972
2020-01-27 | 11:38 | 49.971
2020-01-27 | 11:38 | 49.97
2020-01-27 | 11:38 | 49.97
2020-01-27 | 11:38 | 49.969
2020-01-27 | 11:38 | 49.966
2020-01-27 | 11:38 | 49.964
2020-01-27 | 11:38 | 49.961
2020-01-27 | 11:38 | 49.961
2020-01-27 | 11:38 | 49.958
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.956
2020-01-27 | 11:38 | 49.954
2020-01-27 | 11:38 | 49.956
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.956
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.956
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.956
2020-01-27 | 11:38 | 49.954
2020-01-27 | 11:38 | 49.953
2020-01-27 | 11:38 | 49.952
2020-01-27 | 11:38 | 49.951
2020-01-27 | 11:38 | 49.951
2020-01-27 | 11:38 | 49.95
2020-01-27 | 11:38 | 49.948
2020-01-27 | 11:38 | 49.948
2020-01-27 | 11:38 | 49.95
2020-01-27 | 11:38 | 49.952
2020-01-27 | 11:38 | 49.954
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.958
2020-01-27 | 11:38 | 49.959
2020-01-27 | 11:38 | 49.961
2020-01-27 | 11:38 | 49.962
2020-01-27 | 11:38 | 49.963
2020-01-27 | 11:38 | 49.962
2020-01-27 | 11:38 | 49.964
2020-01-27 | 11:38 | 49.961
2020-01-27 | 11:38 | 49.958
2020-01-27 | 11:38 | 49.957
2020-01-27 | 11:38 | 49.956
2020-01-27 | 11:38 | 49.953
2020-01-27 | 11:38 | 49.951
2020-01-27 | 11:38 | 49.95
2020-01-27 | 11:38 | 49.949
2020-01-27 | 11:38 | 49.948
2020-01-27 | 11:38 | 49.946
2020-01-27 | 11:38 | 49.945
2020-01-27 | 11:38 | 49.942
2020-01-27 | 11:38 | 49.941
2020-01-27 | 11:38 | 49.938
2020-01-27 | 11:38 | 49.936
2020-01-27 | 11:38 | 49.934
2020-01-27 | 11:38 | 49.929
2020-01-27 | 11:39 | 49.925
2020-01-27 | 11:39 | 49.919
2020-01-27 | 11:39 | 49.915
2020-01-27 | 11:39 | 49.91
2020-01-27 | 11:39 | 49.906
2020-01-27 | 11:39 | 49.901
2020-01-27 | 11:39 | 49.897
2020-01-27 | 11:39 | 49.892
2020-01-27 | 11:39 | 49.885
2020-01-27 | 11:39 | 49.881
2020-01-27 | 11:39 | 49.879
2020-01-27 | 11:39 | 49.878
2020-01-27 | 11:39 | 49.876
2020-01-27 | 11:39 | 49.878
2020-01-27 | 11:39 | 49.881
2020-01-27 | 11:39 | 49.881
2020-01-27 | 11:39 | 49.883
2020-01-27 | 11:39 | 49.885
2020-01-27 | 11:39 | 49.886
2020-01-27 | 11:39 | 49.887
2020-01-27 | 11:39 | 49.887
2020-01-27 | 11:39 | 49.888
2020-01-27 | 11:39 | 49.888
2020-01-27 | 11:39 | 49.887
2020-01-27 | 11:39 | 49.887
2020-01-27 | 11:39 | 49.886
2020-01-27 | 11:39 | 49.886
2020-01-27 | 11:39 | 49.886
2020-01-27 | 11:39 | 49.886
2020-01-27 | 11:39 | 49.886
2020-01-27 | 11:39 | 49.884
2020-01-27 | 11:39 | 49.882
2020-01-27 | 11:39 | 49.881
2020-01-27 | 11:39 | 49.879
2020-01-27 | 11:39 | 49.878
2020-01-27 | 11:39 | 49.877
2020-01-27 | 11:39 | 49.878
2020-01-27 | 11:39 | 49.876
2020-01-27 | 11:39 | 49.875
2020-01-27 | 11:39 | 49.873
2020-01-27 | 11:39 | 49.872
2020-01-27 | 11:39 | 49.874
2020-01-27 | 11:39 | 49.873
2020-01-27 | 11:39 | 49.875
2020-01-27 | 11:39 | 49.875
2020-01-27 | 11:39 | 49.873
2020-01-27 | 11:39 | 49.873
2020-01-27 | 11:39 | 49.871
2020-01-27 | 11:39 | 49.87
2020-01-27 | 11:39 | 49.866
2020-01-27 | 11:39 | 49.863
2020-01-27 | 11:39 | 49.861
2020-01-27 | 11:39 | 49.857
2020-01-27 | 11:39 | 49.856
2020-01-27 | 11:39 | 49.854
2020-01-27 | 11:39 | 49.854
2020-01-27 | 11:39 | 49.852
2020-01-27 | 11:39 | 49.851
2020-01-27 | 11:39 | 49.852
2020-01-27 | 11:39 | 49.851
2020-01-27 | 11:40 | 49.852
2020-01-27 | 11:40 | 49.851
2020-01-27 | 11:40 | 49.849
2020-01-27 | 11:40 | 49.848
2020-01-27 | 11:40 | 49.847
2020-01-27 | 11:40 | 49.845
2020-01-27 | 11:40 | 49.844
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.842
2020-01-27 | 11:40 | 49.845
2020-01-27 | 11:40 | 49.849
2020-01-27 | 11:40 | 49.851
2020-01-27 | 11:40 | 49.854
2020-01-27 | 11:40 | 49.854
2020-01-27 | 11:40 | 49.855
2020-01-27 | 11:40 | 49.855
2020-01-27 | 11:40 | 49.85
2020-01-27 | 11:40 | 49.846
2020-01-27 | 11:40 | 49.843
2020-01-27 | 11:40 | 49.838
2020-01-27 | 11:40 | 49.835
2020-01-27 | 11:40 | 49.834
2020-01-27 | 11:40 | 49.834
2020-01-27 | 11:40 | 49.834
2020-01-27 | 11:40 | 49.834
2020-01-27 | 11:40 | 49.834
2020-01-27 | 11:40 | 49.835
2020-01-27 | 11:40 | 49.836
2020-01-27 | 11:40 | 49.833
2020-01-27 | 11:40 | 49.836
2020-01-27 | 11:40 | 49.834
2020-01-27 | 11:40 | 49.831
2020-01-27 | 11:40 | 49.829
2020-01-27 | 11:40 | 49.827
2020-01-27 | 11:40 | 49.824
2020-01-27 | 11:40 | 49.823
2020-01-27 | 11:40 | 49.823
2020-01-27 | 11:40 | 49.824
2020-01-27 | 11:40 | 49.825
2020-01-27 | 11:40 | 49.828
2020-01-27 | 11:40 | 49.831
2020-01-27 | 11:40 | 49.833
2020-01-27 | 11:40 | 49.835
2020-01-27 | 11:40 | 49.838
2020-01-27 | 11:40 | 49.839
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.839
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.839
2020-01-27 | 11:40 | 49.838
2020-01-27 | 11:40 | 49.838
2020-01-27 | 11:40 | 49.84
2020-01-27 | 11:40 | 49.841
2020-01-27 | 11:40 | 49.843
2020-01-27 | 11:40 | 49.846
2020-01-27 | 11:40 | 49.849
2020-01-27 | 11:40 | 49.851
2020-01-27 | 11:41 | 49.853
2020-01-27 | 11:41 | 49.854
2020-01-27 | 11:41 | 49.854
2020-01-27 | 11:41 | 49.854
2020-01-27 | 11:41 | 49.855
2020-01-27 | 11:41 | 49.857
2020-01-27 | 11:41 | 49.858
2020-01-27 | 11:41 | 49.86
2020-01-27 | 11:41 | 49.864
2020-01-27 | 11:41 | 49.87
2020-01-27 | 11:41 | 49.875
2020-01-27 | 11:41 | 49.882
2020-01-27 | 11:41 | 49.887
2020-01-27 | 11:41 | 49.893
2020-01-27 | 11:41 | 49.898
2020-01-27 | 11:41 | 49.904
2020-01-27 | 11:41 | 49.909
2020-01-27 | 11:41 | 49.915
2020-01-27 | 11:41 | 49.922
2020-01-27 | 11:41 | 49.927
2020-01-27 | 11:41 | 49.931
2020-01-27 | 11:41 | 49.934
2020-01-27 | 11:41 | 49.937
2020-01-27 | 11:41 | 49.939
2020-01-27 | 11:41 | 49.941
2020-01-27 | 11:41 | 49.943
2020-01-27 | 11:41 | 49.947
2020-01-27 | 11:41 | 49.948
2020-01-27 | 11:41 | 49.949
2020-01-27 | 11:41 | 49.951
2020-01-27 | 11:41 | 49.951
2020-01-27 | 11:41 | 49.95
2020-01-27 | 11:41 | 49.95
2020-01-27 | 11:41 | 49.95
2020-01-27 | 11:41 | 49.95
2020-01-27 | 11:41 | 49.949
2020-01-27 | 11:41 | 49.949
2020-01-27 | 11:41 | 49.948
2020-01-27 | 11:41 | 49.949
2020-01-27 | 11:41 | 49.95
2020-01-27 | 11:41 | 49.951
2020-01-27 | 11:41 | 49.952
2020-01-27 | 11:41 | 49.952
2020-01-27 | 11:41 | 49.952
2020-01-27 | 11:41 | 49.95
2020-01-27 | 11:41 | 49.948
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.944
2020-01-27 | 11:41 | 49.945
2020-01-27 | 11:41 | 49.944
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.946
2020-01-27 | 11:41 | 49.944
2020-01-27 | 11:41 | 49.943
2020-01-27 | 11:41 | 49.944
2020-01-27 | 11:41 | 49.944
2020-01-27 | 11:42 | 49.944
2020-01-27 | 11:42 | 49.945
2020-01-27 | 11:42 | 49.948
2020-01-27 | 11:42 | 49.95
2020-01-27 | 11:42 | 49.951
2020-01-27 | 11:42 | 49.952
2020-01-27 | 11:42 | 49.952
2020-01-27 | 11:42 | 49.95
2020-01-27 | 11:42 | 49.949
2020-01-27 | 11:42 | 49.946
2020-01-27 | 11:42 | 49.943
2020-01-27 | 11:42 | 49.939
2020-01-27 | 11:42 | 49.935
2020-01-27 | 11:42 | 49.933
2020-01-27 | 11:42 | 49.931
2020-01-27 | 11:42 | 49.932
2020-01-27 | 11:42 | 49.934
2020-01-27 | 11:42 | 49.935
2020-01-27 | 11:42 | 49.934
2020-01-27 | 11:42 | 49.934
2020-01-27 | 11:42 | 49.934
2020-01-27 | 11:42 | 49.934
2020-01-27 | 11:42 | 49.932
2020-01-27 | 11:42 | 49.93
2020-01-27 | 11:42 | 49.929
2020-01-27 | 11:42 | 49.928
2020-01-27 | 11:42 | 49.926
2020-01-27 | 11:42 | 49.927
2020-01-27 | 11:42 | 49.926
2020-01-27 | 11:42 | 49.925
2020-01-27 | 11:42 | 49.923
2020-01-27 | 11:42 | 49.922
2020-01-27 | 11:42 | 49.922
2020-01-27 | 11:42 | 49.922
2020-01-27 | 11:42 | 49.924
2020-01-27 | 11:42 | 49.923
2020-01-27 | 11:42 | 49.922
2020-01-27 | 11:42 | 49.921
2020-01-27 | 11:42 | 49.92
2020-01-27 | 11:42 | 49.92
2020-01-27 | 11:42 | 49.918
2020-01-27 | 11:42 | 49.919
2020-01-27 | 11:42 | 49.919
2020-01-27 | 11:42 | 49.918
2020-01-27 | 11:42 | 49.92
2020-01-27 | 11:42 | 49.921
2020-01-27 | 11:42 | 49.921
2020-01-27 | 11:42 | 49.922
2020-01-27 | 11:42 | 49.924
2020-01-27 | 11:42 | 49.922
2020-01-27 | 11:42 | 49.921
2020-01-27 | 11:42 | 49.918
2020-01-27 | 11:42 | 49.917
2020-01-27 | 11:42 | 49.916
2020-01-27 | 11:42 | 49.915
2020-01-27 | 11:42 | 49.914
2020-01-27 | 11:42 | 49.915
2020-01-27 | 11:42 | 49.915
2020-01-27 | 11:42 | 49.915
2020-01-27 | 11:42 | 49.916
2020-01-27 | 11:43 | 49.915
2020-01-27 | 11:43 | 49.917
2020-01-27 | 11:43 | 49.918
2020-01-27 | 11:43 | 49.92
2020-01-27 | 11:43 | 49.921
2020-01-27 | 11:43 | 49.922
2020-01-27 | 11:43 | 49.921
2020-01-27 | 11:43 | 49.921
2020-01-27 | 11:43 | 49.92
2020-01-27 | 11:43 | 49.922
2020-01-27 | 11:43 | 49.922
2020-01-27 | 11:43 | 49.922
2020-01-27 | 11:43 | 49.922
2020-01-27 | 11:43 | 49.919
2020-01-27 | 11:43 | 49.917
2020-01-27 | 11:43 | 49.916
2020-01-27 | 11:43 | 49.916
2020-01-27 | 11:43 | 49.916
2020-01-27 | 11:43 | 49.916
2020-01-27 | 11:43 | 49.918
2020-01-27 | 11:43 | 49.92
2020-01-27 | 11:43 | 49.923
2020-01-27 | 11:43 | 49.925
2020-01-27 | 11:43 | 49.928
2020-01-27 | 11:43 | 49.928
2020-01-27 | 11:43 | 49.93
2020-01-27 | 11:43 | 49.931
2020-01-27 | 11:43 | 49.932
2020-01-27 | 11:43 | 49.932
2020-01-27 | 11:43 | 49.931
2020-01-27 | 11:43 | 49.932
2020-01-27 | 11:43 | 49.93
2020-01-27 | 11:43 | 49.929
2020-01-27 | 11:43 | 49.927
2020-01-27 | 11:43 | 49.926
2020-01-27 | 11:43 | 49.924
2020-01-27 | 11:43 | 49.923
2020-01-27 | 11:43 | 49.923
2020-01-27 | 11:43 | 49.923
2020-01-27 | 11:43 | 49.924
2020-01-27 | 11:43 | 49.926
2020-01-27 | 11:43 | 49.927
2020-01-27 | 11:43 | 49.927
2020-01-27 | 11:43 | 49.926
2020-01-27 | 11:43 | 49.925
2020-01-27 | 11:43 | 49.924
2020-01-27 | 11:43 | 49.923
2020-01-27 | 11:43 | 49.919
2020-01-27 | 11:43 | 49.918
2020-01-27 | 11:43 | 49.915
2020-01-27 | 11:43 | 49.915
2020-01-27 | 11:43 | 49.912
2020-01-27 | 11:43 | 49.91
2020-01-27 | 11:43 | 49.908
2020-01-27 | 11:43 | 49.908
2020-01-27 | 11:43 | 49.908
2020-01-27 | 11:43 | 49.907
2020-01-27 | 11:43 | 49.905
2020-01-27 | 11:43 | 49.901
2020-01-27 | 11:43 | 49.898
2020-01-27 | 11:44 | 49.894
2020-01-27 | 11:44 | 49.889
2020-01-27 | 11:44 | 49.886
2020-01-27 | 11:44 | 49.881
2020-01-27 | 11:44 | 49.879
2020-01-27 | 11:44 | 49.874
2020-01-27 | 11:44 | 49.873
2020-01-27 | 11:44 | 49.871
2020-01-27 | 11:44 | 49.867
2020-01-27 | 11:44 | 49.864
2020-01-27 | 11:44 | 49.862
2020-01-27 | 11:44 | 49.86
2020-01-27 | 11:44 | 49.86
2020-01-27 | 11:44 | 49.859
2020-01-27 | 11:44 | 49.858
2020-01-27 | 11:44 | 49.855
2020-01-27 | 11:44 | 49.854
2020-01-27 | 11:44 | 49.85
2020-01-27 | 11:44 | 49.847
2020-01-27 | 11:44 | 49.845
2020-01-27 | 11:44 | 49.846
2020-01-27 | 11:44 | 49.845
2020-01-27 | 11:44 | 49.845
2020-01-27 | 11:44 | 49.845
2020-01-27 | 11:44 | 49.846
2020-01-27 | 11:44 | 49.847
2020-01-27 | 11:44 | 49.846
2020-01-27 | 11:44 | 49.844
2020-01-27 | 11:44 | 49.842
2020-01-27 | 11:44 | 49.842
2020-01-27 | 11:44 | 49.841
2020-01-27 | 11:44 | 49.841
2020-01-27 | 11:44 | 49.842
2020-01-27 | 11:44 | 49.841
2020-01-27 | 11:44 | 49.841
2020-01-27 | 11:44 | 49.84
2020-01-27 | 11:44 | 49.84
2020-01-27 | 11:44 | 49.838
2020-01-27 | 11:44 | 49.839
2020-01-27 | 11:44 | 49.836
2020-01-27 | 11:44 | 49.831
2020-01-27 | 11:44 | 49.828
2020-01-27 | 11:44 | 49.824
2020-01-27 | 11:44 | 49.823
2020-01-27 | 11:44 | 49.821
2020-01-27 | 11:44 | 49.819
2020-01-27 | 11:44 | 49.817
2020-01-27 | 11:44 | 49.818
2020-01-27 | 11:44 | 49.82
2020-01-27 | 11:44 | 49.822
2020-01-27 | 11:44 | 49.82
2020-01-27 | 11:44 | 49.82
2020-01-27 | 11:44 | 49.82
2020-01-27 | 11:44 | 49.821
2020-01-27 | 11:44 | 49.82
2020-01-27 | 11:44 | 49.818
2020-01-27 | 11:44 | 49.817
2020-01-27 | 11:44 | 49.816
2020-01-27 | 11:44 | 49.818
2020-01-27 | 11:44 | 49.816
2020-01-27 | 11:44 | 49.815
2020-01-27 | 11:45 | 49.82
2020-01-27 | 11:45 | 49.823
2020-01-27 | 11:45 | 49.829
2020-01-27 | 11:45 | 49.835
2020-01-27 | 11:45 | 49.838
2020-01-27 | 11:45 | 49.843
2020-01-27 | 11:45 | 49.847
2020-01-27 | 11:45 | 49.851
2020-01-27 | 11:45 | 49.853
2020-01-27 | 11:45 | 49.852
2020-01-27 | 11:45 | 49.852
2020-01-27 | 11:45 | 49.851
2020-01-27 | 11:45 | 49.851
2020-01-27 | 11:45 | 49.85
2020-01-27 | 11:45 | 49.849
2020-01-27 | 11:45 | 49.846
2020-01-27 | 11:45 | 49.846
2020-01-27 | 11:45 | 49.844
2020-01-27 | 11:45 | 49.842
2020-01-27 | 11:45 | 49.84
2020-01-27 | 11:45 | 49.835
2020-01-27 | 11:45 | 49.832
2020-01-27 | 11:45 | 49.83
2020-01-27 | 11:45 | 49.831
2020-01-27 | 11:45 | 49.834
2020-01-27 | 11:45 | 49.837
2020-01-27 | 11:45 | 49.837
2020-01-27 | 11:45 | 49.837
2020-01-27 | 11:45 | 49.836
2020-01-27 | 11:45 | 49.835
2020-01-27 | 11:45 | 49.834
2020-01-27 | 11:45 | 49.832
2020-01-27 | 11:45 | 49.829
2020-01-27 | 11:45 | 49.828
2020-01-27 | 11:45 | 49.827
2020-01-27 | 11:45 | 49.829
2020-01-27 | 11:45 | 49.829
2020-01-27 | 11:45 | 49.832
2020-01-27 | 11:45 | 49.833
2020-01-27 | 11:45 | 49.835
2020-01-27 | 11:45 | 49.837
2020-01-27 | 11:45 | 49.84
2020-01-27 | 11:45 | 49.843
2020-01-27 | 11:45 | 49.845
2020-01-27 | 11:45 | 49.847
2020-01-27 | 11:45 | 49.847
2020-01-27 | 11:45 | 49.846
2020-01-27 | 11:45 | 49.849
2020-01-27 | 11:45 | 49.851
2020-01-27 | 11:45 | 49.853
2020-01-27 | 11:45 | 49.854
2020-01-27 | 11:45 | 49.857
2020-01-27 | 11:45 | 49.859
2020-01-27 | 11:45 | 49.861
2020-01-27 | 11:45 | 49.862
2020-01-27 | 11:45 | 49.863
2020-01-27 | 11:45 | 49.866
2020-01-27 | 11:45 | 49.869
2020-01-27 | 11:45 | 49.872
2020-01-27 | 11:46 | 49.875
2020-01-27 | 11:46 | 49.876
2020-01-27 | 11:46 | 49.877
2020-01-27 | 11:46 | 49.879
2020-01-27 | 11:46 | 49.883
2020-01-27 | 11:46 | 49.889
2020-01-27 | 11:46 | 49.893
2020-01-27 | 11:46 | 49.896
2020-01-27 | 11:46 | 49.902
2020-01-27 | 11:46 | 49.907
2020-01-27 | 11:46 | 49.908
2020-01-27 | 11:46 | 49.909
2020-01-27 | 11:46 | 49.91
2020-01-27 | 11:46 | 49.911
2020-01-27 | 11:46 | 49.912
2020-01-27 | 11:46 | 49.911
2020-01-27 | 11:46 | 49.909
2020-01-27 | 11:46 | 49.91
2020-01-27 | 11:46 | 49.911
2020-01-27 | 11:46 | 49.91
2020-01-27 | 11:46 | 49.909
2020-01-27 | 11:46 | 49.908
2020-01-27 | 11:46 | 49.907
2020-01-27 | 11:46 | 49.906
2020-01-27 | 11:46 | 49.903
2020-01-27 | 11:46 | 49.901
2020-01-27 | 11:46 | 49.899
2020-01-27 | 11:46 | 49.897
2020-01-27 | 11:46 | 49.899
2020-01-27 | 11:46 | 49.899
2020-01-27 | 11:46 | 49.899
2020-01-27 | 11:46 | 49.903
2020-01-27 | 11:46 | 49.903
2020-01-27 | 11:46 | 49.904
2020-01-27 | 11:46 | 49.903
2020-01-27 | 11:46 | 49.9
2020-01-27 | 11:46 | 49.901
2020-01-27 | 11:46 | 49.898
2020-01-27 | 11:46 | 49.895
2020-01-27 | 11:46 | 49.891
2020-01-27 | 11:46 | 49.889
2020-01-27 | 11:46 | 49.888
2020-01-27 | 11:46 | 49.887
2020-01-27 | 11:46 | 49.887
2020-01-27 | 11:46 | 49.884
2020-01-27 | 11:46 | 49.884
2020-01-27 | 11:46 | 49.886
2020-01-27 | 11:46 | 49.886
2020-01-27 | 11:46 | 49.888
2020-01-27 | 11:46 | 49.89
2020-01-27 | 11:46 | 49.89
2020-01-27 | 11:46 | 49.891
2020-01-27 | 11:46 | 49.89
2020-01-27 | 11:46 | 49.891
2020-01-27 | 11:46 | 49.892
2020-01-27 | 11:46 | 49.893
2020-01-27 | 11:46 | 49.895
2020-01-27 | 11:46 | 49.898
2020-01-27 | 11:46 | 49.899
2020-01-27 | 11:46 | 49.902
2020-01-27 | 11:46 | 49.903
2020-01-27 | 11:47 | 49.906
2020-01-27 | 11:47 | 49.908
2020-01-27 | 11:47 | 49.908
2020-01-27 | 11:47 | 49.909
2020-01-27 | 11:47 | 49.907
2020-01-27 | 11:47 | 49.905
2020-01-27 | 11:47 | 49.903
2020-01-27 | 11:47 | 49.899
2020-01-27 | 11:47 | 49.897
2020-01-27 | 11:47 | 49.896
2020-01-27 | 11:47 | 49.895
2020-01-27 | 11:47 | 49.894
2020-01-27 | 11:47 | 49.893
2020-01-27 | 11:47 | 49.894
2020-01-27 | 11:47 | 49.896
2020-01-27 | 11:47 | 49.897
2020-01-27 | 11:47 | 49.9
2020-01-27 | 11:47 | 49.904
2020-01-27 | 11:47 | 49.909
2020-01-27 | 11:47 | 49.914
2020-01-27 | 11:47 | 49.917
2020-01-27 | 11:47 | 49.919
2020-01-27 | 11:47 | 49.922
2020-01-27 | 11:47 | 49.924
2020-01-27 | 11:47 | 49.924
2020-01-27 | 11:47 | 49.926
2020-01-27 | 11:47 | 49.926
2020-01-27 | 11:47 | 49.926
2020-01-27 | 11:47 | 49.926
2020-01-27 | 11:47 | 49.925
2020-01-27 | 11:47 | 49.924
2020-01-27 | 11:47 | 49.922
2020-01-27 | 11:47 | 49.92
2020-01-27 | 11:47 | 49.921
2020-01-27 | 11:47 | 49.921
2020-01-27 | 11:47 | 49.92
2020-01-27 | 11:47 | 49.92
2020-01-27 | 11:47 | 49.922
2020-01-27 | 11:47 | 49.923
2020-01-27 | 11:47 | 49.923
2020-01-27 | 11:47 | 49.923
2020-01-27 | 11:47 | 49.921
2020-01-27 | 11:47 | 49.921
2020-01-27 | 11:47 | 49.923
2020-01-27 | 11:47 | 49.924
2020-01-27 | 11:47 | 49.925
2020-01-27 | 11:47 | 49.923
2020-01-27 | 11:47 | 49.921
2020-01-27 | 11:47 | 49.92
2020-01-27 | 11:47 | 49.919
2020-01-27 | 11:47 | 49.918
2020-01-27 | 11:47 | 49.918
2020-01-27 | 11:47 | 49.918
2020-01-27 | 11:47 | 49.916
2020-01-27 | 11:47 | 49.915
2020-01-27 | 11:47 | 49.915
2020-01-27 | 11:47 | 49.915
2020-01-27 | 11:47 | 49.916
2020-01-27 | 11:47 | 49.916
2020-01-27 | 11:48 | 49.915
2020-01-27 | 11:48 | 49.914
2020-01-27 | 11:48 | 49.918
2020-01-27 | 11:48 | 49.918
2020-01-27 | 11:48 | 49.918
2020-01-27 | 11:48 | 49.917
2020-01-27 | 11:48 | 49.917
2020-01-27 | 11:48 | 49.914
2020-01-27 | 11:48 | 49.911
2020-01-27 | 11:48 | 49.908
2020-01-27 | 11:48 | 49.907
2020-01-27 | 11:48 | 49.909
2020-01-27 | 11:48 | 49.91
2020-01-27 | 11:48 | 49.911
2020-01-27 | 11:48 | 49.913
2020-01-27 | 11:48 | 49.918
2020-01-27 | 11:48 | 49.92
2020-01-27 | 11:48 | 49.923
2020-01-27 | 11:48 | 49.923
2020-01-27 | 11:48 | 49.923
2020-01-27 | 11:48 | 49.925
2020-01-27 | 11:48 | 49.928
2020-01-27 | 11:48 | 49.932
2020-01-27 | 11:48 | 49.936
2020-01-27 | 11:48 | 49.938
2020-01-27 | 11:48 | 49.939
2020-01-27 | 11:48 | 49.938
2020-01-27 | 11:48 | 49.937
2020-01-27 | 11:48 | 49.94
2020-01-27 | 11:48 | 49.941
2020-01-27 | 11:48 | 49.938
2020-01-27 | 11:48 | 49.935
2020-01-27 | 11:48 | 49.932
2020-01-27 | 11:48 | 49.932
2020-01-27 | 11:48 | 49.932
2020-01-27 | 11:48 | 49.93
2020-01-27 | 11:48 | 49.928
2020-01-27 | 11:48 | 49.926
2020-01-27 | 11:48 | 49.923
2020-01-27 | 11:48 | 49.922
2020-01-27 | 11:48 | 49.919
2020-01-27 | 11:48 | 49.915
2020-01-27 | 11:48 | 49.91
2020-01-27 | 11:48 | 49.906
2020-01-27 | 11:48 | 49.903
2020-01-27 | 11:48 | 49.902
2020-01-27 | 11:48 | 49.902
2020-01-27 | 11:48 | 49.903
2020-01-27 | 11:48 | 49.903
2020-01-27 | 11:48 | 49.907
2020-01-27 | 11:48 | 49.907
2020-01-27 | 11:48 | 49.908
2020-01-27 | 11:48 | 49.909
2020-01-27 | 11:48 | 49.911
2020-01-27 | 11:48 | 49.914
2020-01-27 | 11:48 | 49.915
2020-01-27 | 11:48 | 49.913
2020-01-27 | 11:48 | 49.913
2020-01-27 | 11:48 | 49.911
2020-01-27 | 11:48 | 49.912
2020-01-27 | 11:48 | 49.911
2020-01-27 | 11:49 | 49.913
2020-01-27 | 11:49 | 49.912
2020-01-27 | 11:49 | 49.912
2020-01-27 | 11:49 | 49.913
2020-01-27 | 11:49 | 49.914
2020-01-27 | 11:49 | 49.915
2020-01-27 | 11:49 | 49.914
2020-01-27 | 11:49 | 49.915
2020-01-27 | 11:49 | 49.917
2020-01-27 | 11:49 | 49.92
2020-01-27 | 11:49 | 49.925
2020-01-27 | 11:49 | 49.929
2020-01-27 | 11:49 | 49.932
2020-01-27 | 11:49 | 49.938
2020-01-27 | 11:49 | 49.942
2020-01-27 | 11:49 | 49.947
2020-01-27 | 11:49 | 49.949
2020-01-27 | 11:49 | 49.951
2020-01-27 | 11:49 | 49.952
2020-01-27 | 11:49 | 49.953
2020-01-27 | 11:49 | 49.957
2020-01-27 | 11:49 | 49.959
2020-01-27 | 11:49 | 49.961
2020-01-27 | 11:49 | 49.964
2020-01-27 | 11:49 | 49.965
2020-01-27 | 11:49 | 49.967
2020-01-27 | 11:49 | 49.967
2020-01-27 | 11:49 | 49.969
2020-01-27 | 11:49 | 49.971
2020-01-27 | 11:49 | 49.974
2020-01-27 | 11:49 | 49.976
2020-01-27 | 11:49 | 49.976
2020-01-27 | 11:49 | 49.976
2020-01-27 | 11:49 | 49.976
2020-01-27 | 11:49 | 49.975
2020-01-27 | 11:49 | 49.975
2020-01-27 | 11:49 | 49.974
2020-01-27 | 11:49 | 49.975
2020-01-27 | 11:49 | 49.975
2020-01-27 | 11:49 | 49.976
2020-01-27 | 11:49 | 49.976
2020-01-27 | 11:49 | 49.978
2020-01-27 | 11:49 | 49.979
2020-01-27 | 11:49 | 49.981
2020-01-27 | 11:49 | 49.982
2020-01-27 | 11:49 | 49.984
2020-01-27 | 11:49 | 49.986
2020-01-27 | 11:49 | 49.987
2020-01-27 | 11:49 | 49.986
2020-01-27 | 11:49 | 49.986
2020-01-27 | 11:49 | 49.985
2020-01-27 | 11:49 | 49.984
2020-01-27 | 11:49 | 49.985
2020-01-27 | 11:49 | 49.985
2020-01-27 | 11:49 | 49.986
2020-01-27 | 11:49 | 49.986
2020-01-27 | 11:49 | 49.986
2020-01-27 | 11:49 | 49.984
2020-01-27 | 11:49 | 49.983
2020-01-27 | 11:50 | 49.98
2020-01-27 | 11:50 | 49.979
2020-01-27 | 11:50 | 49.978
2020-01-27 | 11:50 | 49.976
2020-01-27 | 11:50 | 49.976
2020-01-27 | 11:50 | 49.978
2020-01-27 | 11:50 | 49.978
2020-01-27 | 11:50 | 49.979
2020-01-27 | 11:50 | 49.983
2020-01-27 | 11:50 | 49.985
2020-01-27 | 11:50 | 49.986
2020-01-27 | 11:50 | 49.987
2020-01-27 | 11:50 | 49.987
2020-01-27 | 11:50 | 49.987
2020-01-27 | 11:50 | 49.99
2020-01-27 | 11:50 | 49.99
2020-01-27 | 11:50 | 49.988
2020-01-27 | 11:50 | 49.987
2020-01-27 | 11:50 | 49.984
2020-01-27 | 11:50 | 49.983
2020-01-27 | 11:50 | 49.982
2020-01-27 | 11:50 | 49.979
2020-01-27 | 11:50 | 49.976
2020-01-27 | 11:50 | 49.972
2020-01-27 | 11:50 | 49.971
2020-01-27 | 11:50 | 49.973
2020-01-27 | 11:50 | 49.975
2020-01-27 | 11:50 | 49.977
2020-01-27 | 11:50 | 49.976
2020-01-27 | 11:50 | 49.977
2020-01-27 | 11:50 | 49.975
2020-01-27 | 11:50 | 49.975
2020-01-27 | 11:50 | 49.973
2020-01-27 | 11:50 | 49.971
2020-01-27 | 11:50 | 49.97
2020-01-27 | 11:50 | 49.968
2020-01-27 | 11:50 | 49.964
2020-01-27 | 11:50 | 49.964
2020-01-27 | 11:50 | 49.963
2020-01-27 | 11:50 | 49.964
2020-01-27 | 11:50 | 49.965
2020-01-27 | 11:50 | 49.961
2020-01-27 | 11:50 | 49.96
2020-01-27 | 11:50 | 49.96
2020-01-27 | 11:50 | 49.956
2020-01-27 | 11:50 | 49.954
2020-01-27 | 11:50 | 49.951
2020-01-27 | 11:50 | 49.947
2020-01-27 | 11:50 | 49.944
2020-01-27 | 11:50 | 49.943
2020-01-27 | 11:50 | 49.943
2020-01-27 | 11:50 | 49.945
2020-01-27 | 11:50 | 49.947
2020-01-27 | 11:50 | 49.949
2020-01-27 | 11:50 | 49.953
2020-01-27 | 11:50 | 49.957
2020-01-27 | 11:50 | 49.961
2020-01-27 | 11:50 | 49.964
2020-01-27 | 11:50 | 49.965
2020-01-27 | 11:50 | 49.967
2020-01-27 | 11:50 | 49.968
2020-01-27 | 11:51 | 49.968
2020-01-27 | 11:51 | 49.967
2020-01-27 | 11:51 | 49.966
2020-01-27 | 11:51 | 49.966
2020-01-27 | 11:51 | 49.966
2020-01-27 | 11:51 | 49.965
2020-01-27 | 11:51 | 49.963
2020-01-27 | 11:51 | 49.962
2020-01-27 | 11:51 | 49.961
2020-01-27 | 11:51 | 49.958
2020-01-27 | 11:51 | 49.956
2020-01-27 | 11:51 | 49.955
2020-01-27 | 11:51 | 49.953
2020-01-27 | 11:51 | 49.952
2020-01-27 | 11:51 | 49.951
2020-01-27 | 11:51 | 49.95
2020-01-27 | 11:51 | 49.948
2020-01-27 | 11:51 | 49.947
2020-01-27 | 11:51 | 49.946
2020-01-27 | 11:51 | 49.946
2020-01-27 | 11:51 | 49.946
2020-01-27 | 11:51 | 49.943
2020-01-27 | 11:51 | 49.944
2020-01-27 | 11:51 | 49.943
2020-01-27 | 11:51 | 49.944
2020-01-27 | 11:51 | 49.947
2020-01-27 | 11:51 | 49.952
2020-01-27 | 11:51 | 49.953
2020-01-27 | 11:51 | 49.956
2020-01-27 | 11:51 | 49.955
2020-01-27 | 11:51 | 49.956
2020-01-27 | 11:51 | 49.954
2020-01-27 | 11:51 | 49.954
2020-01-27 | 11:51 | 49.953
2020-01-27 | 11:51 | 49.952
2020-01-27 | 11:51 | 49.953
2020-01-27 | 11:51 | 49.956
2020-01-27 | 11:51 | 49.958
2020-01-27 | 11:51 | 49.96
2020-01-27 | 11:51 | 49.962
2020-01-27 | 11:51 | 49.964
2020-01-27 | 11:51 | 49.966
2020-01-27 | 11:51 | 49.967
2020-01-27 | 11:51 | 49.968
2020-01-27 | 11:51 | 49.97
2020-01-27 | 11:51 | 49.972
2020-01-27 | 11:51 | 49.975
2020-01-27 | 11:51 | 49.976
2020-01-27 | 11:51 | 49.976
2020-01-27 | 11:51 | 49.974
2020-01-27 | 11:51 | 49.975
2020-01-27 | 11:51 | 49.976
2020-01-27 | 11:51 | 49.978
2020-01-27 | 11:51 | 49.98
2020-01-27 | 11:51 | 49.982
2020-01-27 | 11:51 | 49.98
2020-01-27 | 11:51 | 49.982
2020-01-27 | 11:51 | 49.982
2020-01-27 | 11:51 | 49.98
2020-01-27 | 11:52 | 49.978
2020-01-27 | 11:52 | 49.977
2020-01-27 | 11:52 | 49.976
2020-01-27 | 11:52 | 49.975
2020-01-27 | 11:52 | 49.973
2020-01-27 | 11:52 | 49.972
2020-01-27 | 11:52 | 49.97
2020-01-27 | 11:52 | 49.972
2020-01-27 | 11:52 | 49.975
2020-01-27 | 11:52 | 49.976
2020-01-27 | 11:52 | 49.973
2020-01-27 | 11:52 | 49.974
2020-01-27 | 11:52 | 49.973
2020-01-27 | 11:52 | 49.971
2020-01-27 | 11:52 | 49.968
2020-01-27 | 11:52 | 49.965
2020-01-27 | 11:52 | 49.962
2020-01-27 | 11:52 | 49.961
2020-01-27 | 11:52 | 49.961
2020-01-27 | 11:52 | 49.962
2020-01-27 | 11:52 | 49.961
2020-01-27 | 11:52 | 49.961
2020-01-27 | 11:52 | 49.962
2020-01-27 | 11:52 | 49.96
2020-01-27 | 11:52 | 49.958
2020-01-27 | 11:52 | 49.955
2020-01-27 | 11:52 | 49.952
2020-01-27 | 11:52 | 49.948
2020-01-27 | 11:52 | 49.945
2020-01-27 | 11:52 | 49.942
2020-01-27 | 11:52 | 49.939
2020-01-27 | 11:52 | 49.94
2020-01-27 | 11:52 | 49.942
2020-01-27 | 11:52 | 49.943
2020-01-27 | 11:52 | 49.943
2020-01-27 | 11:52 | 49.943
2020-01-27 | 11:52 | 49.943
2020-01-27 | 11:52 | 49.941
2020-01-27 | 11:52 | 49.939
2020-01-27 | 11:52 | 49.937
2020-01-27 | 11:52 | 49.934
2020-01-27 | 11:52 | 49.935
2020-01-27 | 11:52 | 49.936
2020-01-27 | 11:52 | 49.935
2020-01-27 | 11:52 | 49.935
2020-01-27 | 11:52 | 49.937
2020-01-27 | 11:52 | 49.936
2020-01-27 | 11:52 | 49.939
2020-01-27 | 11:52 | 49.942
2020-01-27 | 11:52 | 49.946
2020-01-27 | 11:52 | 49.95
2020-01-27 | 11:52 | 49.953
2020-01-27 | 11:52 | 49.955
2020-01-27 | 11:52 | 49.956
2020-01-27 | 11:52 | 49.956
2020-01-27 | 11:52 | 49.956
2020-01-27 | 11:52 | 49.958
2020-01-27 | 11:52 | 49.958
2020-01-27 | 11:52 | 49.955
2020-01-27 | 11:52 | 49.955
2020-01-27 | 11:52 | 49.953
2020-01-27 | 11:53 | 49.949
2020-01-27 | 11:53 | 49.946
2020-01-27 | 11:53 | 49.941
2020-01-27 | 11:53 | 49.937
2020-01-27 | 11:53 | 49.932
2020-01-27 | 11:53 | 49.932
2020-01-27 | 11:53 | 49.928
2020-01-27 | 11:53 | 49.927
2020-01-27 | 11:53 | 49.927
2020-01-27 | 11:53 | 49.927
2020-01-27 | 11:53 | 49.927
2020-01-27 | 11:53 | 49.929
2020-01-27 | 11:53 | 49.932
2020-01-27 | 11:53 | 49.936
2020-01-27 | 11:53 | 49.94
2020-01-27 | 11:53 | 49.943
2020-01-27 | 11:53 | 49.947
2020-01-27 | 11:53 | 49.949
2020-01-27 | 11:53 | 49.95
2020-01-27 | 11:53 | 49.951
2020-01-27 | 11:53 | 49.952
2020-01-27 | 11:53 | 49.953
2020-01-27 | 11:53 | 49.953
2020-01-27 | 11:53 | 49.955
2020-01-27 | 11:53 | 49.959
2020-01-27 | 11:53 | 49.961
2020-01-27 | 11:53 | 49.962
2020-01-27 | 11:53 | 49.961
2020-01-27 | 11:53 | 49.961
2020-01-27 | 11:53 | 49.96
2020-01-27 | 11:53 | 49.959
2020-01-27 | 11:53 | 49.959
2020-01-27 | 11:53 | 49.96
2020-01-27 | 11:53 | 49.96
2020-01-27 | 11:53 | 49.957
2020-01-27 | 11:53 | 49.959
2020-01-27 | 11:53 | 49.957
2020-01-27 | 11:53 | 49.955
2020-01-27 | 11:53 | 49.952
2020-01-27 | 11:53 | 49.951
2020-01-27 | 11:53 | 49.95
2020-01-27 | 11:53 | 49.946
2020-01-27 | 11:53 | 49.944
2020-01-27 | 11:53 | 49.943
2020-01-27 | 11:53 | 49.943
2020-01-27 | 11:53 | 49.943
2020-01-27 | 11:53 | 49.941
2020-01-27 | 11:53 | 49.938
2020-01-27 | 11:53 | 49.932
2020-01-27 | 11:53 | 49.929
2020-01-27 | 11:53 | 49.927
2020-01-27 | 11:53 | 49.922
2020-01-27 | 11:53 | 49.919
2020-01-27 | 11:53 | 49.913
2020-01-27 | 11:53 | 49.909
2020-01-27 | 11:53 | 49.908
2020-01-27 | 11:53 | 49.908
2020-01-27 | 11:53 | 49.907
2020-01-27 | 11:53 | 49.905
2020-01-27 | 11:54 | 49.904
2020-01-27 | 11:54 | 49.903
2020-01-27 | 11:54 | 49.903
2020-01-27 | 11:54 | 49.902
2020-01-27 | 11:54 | 49.902
2020-01-27 | 11:54 | 49.904
2020-01-27 | 11:54 | 49.904
2020-01-27 | 11:54 | 49.904
2020-01-27 | 11:54 | 49.906
2020-01-27 | 11:54 | 49.91
2020-01-27 | 11:54 | 49.912
2020-01-27 | 11:54 | 49.915
2020-01-27 | 11:54 | 49.913
2020-01-27 | 11:54 | 49.914
2020-01-27 | 11:54 | 49.914
2020-01-27 | 11:54 | 49.914
2020-01-27 | 11:54 | 49.912
2020-01-27 | 11:54 | 49.909
2020-01-27 | 11:54 | 49.906
2020-01-27 | 11:54 | 49.903
2020-01-27 | 11:54 | 49.901
2020-01-27 | 11:54 | 49.899
2020-01-27 | 11:54 | 49.899
2020-01-27 | 11:54 | 49.901
2020-01-27 | 11:54 | 49.904
2020-01-27 | 11:54 | 49.908
2020-01-27 | 11:54 | 49.91
2020-01-27 | 11:54 | 49.911
2020-01-27 | 11:54 | 49.913
2020-01-27 | 11:54 | 49.916
2020-01-27 | 11:54 | 49.918
2020-01-27 | 11:54 | 49.917
2020-01-27 | 11:54 | 49.915
2020-01-27 | 11:54 | 49.913
2020-01-27 | 11:54 | 49.91
2020-01-27 | 11:54 | 49.912
2020-01-27 | 11:54 | 49.911
2020-01-27 | 11:54 | 49.911
2020-01-27 | 11:54 | 49.911
2020-01-27 | 11:54 | 49.913
2020-01-27 | 11:54 | 49.917
2020-01-27 | 11:54 | 49.924
2020-01-27 | 11:54 | 49.927
2020-01-27 | 11:54 | 49.933
2020-01-27 | 11:54 | 49.936
2020-01-27 | 11:54 | 49.94
2020-01-27 | 11:54 | 49.945
2020-01-27 | 11:54 | 49.949
2020-01-27 | 11:54 | 49.951
2020-01-27 | 11:54 | 49.953
2020-01-27 | 11:54 | 49.956
2020-01-27 | 11:54 | 49.957
2020-01-27 | 11:54 | 49.958
2020-01-27 | 11:54 | 49.96
2020-01-27 | 11:54 | 49.961
2020-01-27 | 11:54 | 49.962
2020-01-27 | 11:54 | 49.961
2020-01-27 | 11:54 | 49.96
2020-01-27 | 11:54 | 49.958
2020-01-27 | 11:54 | 49.957
2020-01-27 | 11:54 | 49.955
2020-01-27 | 11:55 | 49.951
2020-01-27 | 11:55 | 49.948
2020-01-27 | 11:55 | 49.945
2020-01-27 | 11:55 | 49.942
2020-01-27 | 11:55 | 49.94
2020-01-27 | 11:55 | 49.94
2020-01-27 | 11:55 | 49.938
2020-01-27 | 11:55 | 49.939
2020-01-27 | 11:55 | 49.94
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.945
2020-01-27 | 11:55 | 49.947
2020-01-27 | 11:55 | 49.947
2020-01-27 | 11:55 | 49.945
2020-01-27 | 11:55 | 49.946
2020-01-27 | 11:55 | 49.945
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.942
2020-01-27 | 11:55 | 49.942
2020-01-27 | 11:55 | 49.942
2020-01-27 | 11:55 | 49.944
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.943
2020-01-27 | 11:55 | 49.941
2020-01-27 | 11:55 | 49.939
2020-01-27 | 11:55 | 49.938
2020-01-27 | 11:55 | 49.936
2020-01-27 | 11:55 | 49.934
2020-01-27 | 11:55 | 49.93
2020-01-27 | 11:55 | 49.928
2020-01-27 | 11:55 | 49.924
2020-01-27 | 11:55 | 49.92
2020-01-27 | 11:55 | 49.919
2020-01-27 | 11:55 | 49.916
2020-01-27 | 11:55 | 49.916
2020-01-27 | 11:55 | 49.919
2020-01-27 | 11:55 | 49.919
2020-01-27 | 11:55 | 49.922
2020-01-27 | 11:55 | 49.923
2020-01-27 | 11:55 | 49.926
2020-01-27 | 11:55 | 49.929
2020-01-27 | 11:55 | 49.932
2020-01-27 | 11:55 | 49.932
2020-01-27 | 11:55 | 49.932
2020-01-27 | 11:55 | 49.931
2020-01-27 | 11:55 | 49.93
2020-01-27 | 11:55 | 49.932
2020-01-27 | 11:55 | 49.932
2020-01-27 | 11:55 | 49.934
2020-01-27 | 11:55 | 49.934
2020-01-27 | 11:55 | 49.933
2020-01-27 | 11:55 | 49.934
2020-01-27 | 11:55 | 49.934
2020-01-27 | 11:55 | 49.933
2020-01-27 | 11:55 | 49.932
2020-01-27 | 11:56 | 49.931
2020-01-27 | 11:56 | 49.928
2020-01-27 | 11:56 | 49.923
2020-01-27 | 11:56 | 49.92
2020-01-27 | 11:56 | 49.916
2020-01-27 | 11:56 | 49.914
2020-01-27 | 11:56 | 49.912
2020-01-27 | 11:56 | 49.911
2020-01-27 | 11:56 | 49.912
2020-01-27 | 11:56 | 49.911
2020-01-27 | 11:56 | 49.911
2020-01-27 | 11:56 | 49.912
2020-01-27 | 11:56 | 49.909
2020-01-27 | 11:56 | 49.909
2020-01-27 | 11:56 | 49.91
2020-01-27 | 11:56 | 49.91
2020-01-27 | 11:56 | 49.911
2020-01-27 | 11:56 | 49.913
2020-01-27 | 11:56 | 49.919
2020-01-27 | 11:56 | 49.919
2020-01-27 | 11:56 | 49.921
2020-01-27 | 11:56 | 49.923
2020-01-27 | 11:56 | 49.924
2020-01-27 | 11:56 | 49.926
2020-01-27 | 11:56 | 49.928
2020-01-27 | 11:56 | 49.932
2020-01-27 | 11:56 | 49.934
2020-01-27 | 11:56 | 49.933
2020-01-27 | 11:56 | 49.932
2020-01-27 | 11:56 | 49.93
2020-01-27 | 11:56 | 49.928
2020-01-27 | 11:56 | 49.927
2020-01-27 | 11:56 | 49.926
2020-01-27 | 11:56 | 49.928
2020-01-27 | 11:56 | 49.93
2020-01-27 | 11:56 | 49.93
2020-01-27 | 11:56 | 49.934
2020-01-27 | 11:56 | 49.935
2020-01-27 | 11:56 | 49.938
2020-01-27 | 11:56 | 49.937
2020-01-27 | 11:56 | 49.938
2020-01-27 | 11:56 | 49.938
2020-01-27 | 11:56 | 49.936
2020-01-27 | 11:56 | 49.934
2020-01-27 | 11:56 | 49.934
2020-01-27 | 11:56 | 49.934
2020-01-27 | 11:56 | 49.933
2020-01-27 | 11:56 | 49.935
2020-01-27 | 11:56 | 49.933
2020-01-27 | 11:56 | 49.934
2020-01-27 | 11:56 | 49.936
2020-01-27 | 11:56 | 49.936
2020-01-27 | 11:56 | 49.939
2020-01-27 | 11:56 | 49.942
2020-01-27 | 11:56 | 49.944
2020-01-27 | 11:56 | 49.946
2020-01-27 | 11:56 | 49.95
2020-01-27 | 11:56 | 49.951
2020-01-27 | 11:56 | 49.951
2020-01-27 | 11:56 | 49.949
2020-01-27 | 11:56 | 49.948
2020-01-27 | 11:57 | 49.949
2020-01-27 | 11:57 | 49.95
2020-01-27 | 11:57 | 49.954
2020-01-27 | 11:57 | 49.959
2020-01-27 | 11:57 | 49.961
2020-01-27 | 11:57 | 49.964
2020-01-27 | 11:57 | 49.969
2020-01-27 | 11:57 | 49.97
2020-01-27 | 11:57 | 49.975
2020-01-27 | 11:57 | 49.976
2020-01-27 | 11:57 | 49.977
2020-01-27 | 11:57 | 49.978
2020-01-27 | 11:57 | 49.978
2020-01-27 | 11:57 | 49.978
2020-01-27 | 11:57 | 49.98
2020-01-27 | 11:57 | 49.981
2020-01-27 | 11:57 | 49.981
2020-01-27 | 11:57 | 49.98
2020-01-27 | 11:57 | 49.98
2020-01-27 | 11:57 | 49.978
2020-01-27 | 11:57 | 49.976
2020-01-27 | 11:57 | 49.974
2020-01-27 | 11:57 | 49.972
2020-01-27 | 11:57 | 49.972
2020-01-27 | 11:57 | 49.97
2020-01-27 | 11:57 | 49.97
2020-01-27 | 11:57 | 49.97
2020-01-27 | 11:57 | 49.969
2020-01-27 | 11:57 | 49.968
2020-01-27 | 11:57 | 49.966
2020-01-27 | 11:57 | 49.964
2020-01-27 | 11:57 | 49.965
2020-01-27 | 11:57 | 49.963
2020-01-27 | 11:57 | 49.962
2020-01-27 | 11:57 | 49.963
2020-01-27 | 11:57 | 49.965
2020-01-27 | 11:57 | 49.963
2020-01-27 | 11:57 | 49.963
2020-01-27 | 11:57 | 49.962
2020-01-27 | 11:57 | 49.961
2020-01-27 | 11:57 | 49.961
2020-01-27 | 11:57 | 49.962
2020-01-27 | 11:57 | 49.965
2020-01-27 | 11:57 | 49.967
2020-01-27 | 11:57 | 49.969
2020-01-27 | 11:57 | 49.97
2020-01-27 | 11:57 | 49.97
2020-01-27 | 11:57 | 49.968
2020-01-27 | 11:57 | 49.966
2020-01-27 | 11:57 | 49.963
2020-01-27 | 11:57 | 49.96
2020-01-27 | 11:57 | 49.959
2020-01-27 | 11:57 | 49.953
2020-01-27 | 11:57 | 49.95
2020-01-27 | 11:57 | 49.946
2020-01-27 | 11:57 | 49.942
2020-01-27 | 11:57 | 49.939
2020-01-27 | 11:57 | 49.935
2020-01-27 | 11:57 | 49.932
2020-01-27 | 11:58 | 49.931
2020-01-27 | 11:58 | 49.93
2020-01-27 | 11:58 | 49.929
2020-01-27 | 11:58 | 49.926
2020-01-27 | 11:58 | 49.924
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.92
2020-01-27 | 11:58 | 49.92
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.922
2020-01-27 | 11:58 | 49.922
2020-01-27 | 11:58 | 49.922
2020-01-27 | 11:58 | 49.922
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.919
2020-01-27 | 11:58 | 49.916
2020-01-27 | 11:58 | 49.915
2020-01-27 | 11:58 | 49.914
2020-01-27 | 11:58 | 49.913
2020-01-27 | 11:58 | 49.912
2020-01-27 | 11:58 | 49.915
2020-01-27 | 11:58 | 49.916
2020-01-27 | 11:58 | 49.919
2020-01-27 | 11:58 | 49.92
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.921
2020-01-27 | 11:58 | 49.922
2020-01-27 | 11:58 | 49.917
2020-01-27 | 11:58 | 49.914
2020-01-27 | 11:58 | 49.911
2020-01-27 | 11:58 | 49.907
2020-01-27 | 11:58 | 49.904
2020-01-27 | 11:58 | 49.902
2020-01-27 | 11:58 | 49.899
2020-01-27 | 11:58 | 49.898
2020-01-27 | 11:58 | 49.895
2020-01-27 | 11:58 | 49.892
2020-01-27 | 11:58 | 49.889
2020-01-27 | 11:58 | 49.889
2020-01-27 | 11:58 | 49.888
2020-01-27 | 11:58 | 49.885
2020-01-27 | 11:58 | 49.884
2020-01-27 | 11:58 | 49.885
2020-01-27 | 11:58 | 49.888
2020-01-27 | 11:58 | 49.891
2020-01-27 | 11:58 | 49.893
2020-01-27 | 11:58 | 49.898
2020-01-27 | 11:58 | 49.901
2020-01-27 | 11:58 | 49.902
2020-01-27 | 11:58 | 49.902
2020-01-27 | 11:58 | 49.903
2020-01-27 | 11:58 | 49.903
2020-01-27 | 11:58 | 49.903
2020-01-27 | 11:58 | 49.905
2020-01-27 | 11:58 | 49.905
2020-01-27 | 11:58 | 49.906
2020-01-27 | 11:58 | 49.906
2020-01-27 | 11:58 | 49.911
2020-01-27 | 11:59 | 49.914
2020-01-27 | 11:59 | 49.917
2020-01-27 | 11:59 | 49.919
2020-01-27 | 11:59 | 49.921
2020-01-27 | 11:59 | 49.918
2020-01-27 | 11:59 | 49.914
2020-01-27 | 11:59 | 49.912
2020-01-27 | 11:59 | 49.908
2020-01-27 | 11:59 | 49.906
2020-01-27 | 11:59 | 49.907
2020-01-27 | 11:59 | 49.909
2020-01-27 | 11:59 | 49.91
2020-01-27 | 11:59 | 49.911
2020-01-27 | 11:59 | 49.911
2020-01-27 | 11:59 | 49.912
2020-01-27 | 11:59 | 49.912
2020-01-27 | 11:59 | 49.912
2020-01-27 | 11:59 | 49.912
2020-01-27 | 11:59 | 49.915
2020-01-27 | 11:59 | 49.92
2020-01-27 | 11:59 | 49.923
2020-01-27 | 11:59 | 49.926
2020-01-27 | 11:59 | 49.929
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.932
2020-01-27 | 11:59 | 49.933
2020-01-27 | 11:59 | 49.936
2020-01-27 | 11:59 | 49.937
2020-01-27 | 11:59 | 49.938
2020-01-27 | 11:59 | 49.937
2020-01-27 | 11:59 | 49.938
2020-01-27 | 11:59 | 49.936
2020-01-27 | 11:59 | 49.937
2020-01-27 | 11:59 | 49.94
2020-01-27 | 11:59 | 49.94
2020-01-27 | 11:59 | 49.941
2020-01-27 | 11:59 | 49.94
2020-01-27 | 11:59 | 49.938
2020-01-27 | 11:59 | 49.934
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.929
2020-01-27 | 11:59 | 49.928
2020-01-27 | 11:59 | 49.928
2020-01-27 | 11:59 | 49.928
2020-01-27 | 11:59 | 49.928
2020-01-27 | 11:59 | 49.929
2020-01-27 | 11:59 | 49.93
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.932
2020-01-27 | 11:59 | 49.932
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.93
2020-01-27 | 11:59 | 49.929
2020-01-27 | 11:59 | 49.929
2020-01-27 | 11:59 | 49.93
2020-01-27 | 11:59 | 49.931
2020-01-27 | 11:59 | 49.93
2020-01-27 | 12:00 | 49.931
2020-01-27 | 12:00 | 49.932
2020-01-27 | 12:00 | 49.933
2020-01-27 | 12:00 | 49.936
2020-01-27 | 12:00 | 49.938
2020-01-27 | 12:00 | 49.942
2020-01-27 | 12:00 | 49.944
2020-01-27 | 12:00 | 49.945
2020-01-27 | 12:00 | 49.945
2020-01-27 | 12:00 | 49.944
2020-01-27 | 12:00 | 49.943
2020-01-27 | 12:00 | 49.943
2020-01-27 | 12:00 | 49.941
2020-01-27 | 12:00 | 49.94
2020-01-27 | 12:00 | 49.94
2020-01-27 | 12:00 | 49.942
2020-01-27 | 12:00 | 49.942
2020-01-27 | 12:00 | 49.941
2020-01-27 | 12:00 | 49.942
2020-01-27 | 12:00 | 49.944
2020-01-27 | 12:00 | 49.945
2020-01-27 | 12:00 | 49.947
2020-01-27 | 12:00 | 49.946
2020-01-27 | 12:00 | 49.945
2020-01-27 | 12:00 | 49.943
2020-01-27 | 12:00 | 49.941
2020-01-27 | 12:00 | 49.938
2020-01-27 | 12:00 | 49.935
2020-01-27 | 12:00 | 49.933
2020-01-27 | 12:00 | 49.929
2020-01-27 | 12:00 | 49.925
2020-01-27 | 12:00 | 49.922
2020-01-27 | 12:00 | 49.92
2020-01-27 | 12:00 | 49.918
2020-01-27 | 12:00 | 49.921
2020-01-27 | 12:00 | 49.925
2020-01-27 | 12:00 | 49.929
2020-01-27 | 12:00 | 49.934
2020-01-27 | 12:00 | 49.938
2020-01-27 | 12:00 | 49.939
2020-01-27 | 12:00 | 49.94
2020-01-27 | 12:00 | 49.944
2020-01-27 | 12:00 | 49.947
2020-01-27 | 12:00 | 49.951
2020-01-27 | 12:00 | 49.956
2020-01-27 | 12:00 | 49.959
2020-01-27 | 12:00 | 49.96
2020-01-27 | 12:00 | 49.962
2020-01-27 | 12:00 | 49.963
2020-01-27 | 12:00 | 49.961
2020-01-27 | 12:00 | 49.96
2020-01-27 | 12:00 | 49.957
2020-01-27 | 12:00 | 49.955
2020-01-27 | 12:00 | 49.95
2020-01-27 | 12:00 | 49.948
2020-01-27 | 12:00 | 49.943
2020-01-27 | 12:00 | 49.943
2020-01-27 | 12:00 | 49.943
2020-01-27 | 12:00 | 49.945
2020-01-27 | 12:00 | 49.946
2020-01-27 | 12:00 | 49.947
2020-01-27 | 12:01 | 49.947
2020-01-27 | 12:01 | 49.946
2020-01-27 | 12:01 | 49.944
2020-01-27 | 12:01 | 49.941
2020-01-27 | 12:01 | 49.937
2020-01-27 | 12:01 | 49.935
2020-01-27 | 12:01 | 49.935
2020-01-27 | 12:01 | 49.936
2020-01-27 | 12:01 | 49.937
2020-01-27 | 12:01 | 49.937
2020-01-27 | 12:01 | 49.939
2020-01-27 | 12:01 | 49.941
2020-01-27 | 12:01 | 49.942
2020-01-27 | 12:01 | 49.944
2020-01-27 | 12:01 | 49.945
2020-01-27 | 12:01 | 49.947
2020-01-27 | 12:01 | 49.948
2020-01-27 | 12:01 | 49.949
2020-01-27 | 12:01 | 49.95
2020-01-27 | 12:01 | 49.952
2020-01-27 | 12:01 | 49.953
2020-01-27 | 12:01 | 49.954
2020-01-27 | 12:01 | 49.957
2020-01-27 | 12:01 | 49.959
2020-01-27 | 12:01 | 49.96
2020-01-27 | 12:01 | 49.962
2020-01-27 | 12:01 | 49.961
2020-01-27 | 12:01 | 49.957
2020-01-27 | 12:01 | 49.957
2020-01-27 | 12:01 | 49.956
2020-01-27 | 12:01 | 49.955
2020-01-27 | 12:01 | 49.956
2020-01-27 | 12:01 | 49.956
2020-01-27 | 12:01 | 49.957
2020-01-27 | 12:01 | 49.96
2020-01-27 | 12:01 | 49.961
2020-01-27 | 12:01 | 49.964
2020-01-27 | 12:01 | 49.963
2020-01-27 | 12:01 | 49.962
2020-01-27 | 12:01 | 49.962
2020-01-27 | 12:01 | 49.96
2020-01-27 | 12:01 | 49.959
2020-01-27 | 12:01 | 49.96
2020-01-27 | 12:01 | 49.958
2020-01-27 | 12:01 | 49.956
2020-01-27 | 12:01 | 49.954
2020-01-27 | 12:01 | 49.952
2020-01-27 | 12:01 | 49.95
2020-01-27 | 12:01 | 49.948
2020-01-27 | 12:01 | 49.946
2020-01-27 | 12:01 | 49.943
2020-01-27 | 12:01 | 49.941
2020-01-27 | 12:01 | 49.939
2020-01-27 | 12:01 | 49.939
2020-01-27 | 12:01 | 49.937
2020-01-27 | 12:01 | 49.938
2020-01-27 | 12:01 | 49.939
2020-01-27 | 12:01 | 49.939
2020-01-27 | 12:01 | 49.938
2020-01-27 | 12:02 | 49.937
2020-01-27 | 12:02 | 49.935
2020-01-27 | 12:02 | 49.934
2020-01-27 | 12:02 | 49.933
2020-01-27 | 12:02 | 49.933
2020-01-27 | 12:02 | 49.931
2020-01-27 | 12:02 | 49.93
2020-01-27 | 12:02 | 49.931
2020-01-27 | 12:02 | 49.929
2020-01-27 | 12:02 | 49.927
2020-01-27 | 12:02 | 49.923
2020-01-27 | 12:02 | 49.92
2020-01-27 | 12:02 | 49.919
2020-01-27 | 12:02 | 49.917
2020-01-27 | 12:02 | 49.916
2020-01-27 | 12:02 | 49.914
2020-01-27 | 12:02 | 49.915
2020-01-27 | 12:02 | 49.916
2020-01-27 | 12:02 | 49.917
2020-01-27 | 12:02 | 49.918
2020-01-27 | 12:02 | 49.918
2020-01-27 | 12:02 | 49.918
2020-01-27 | 12:02 | 49.918
2020-01-27 | 12:02 | 49.916
2020-01-27 | 12:02 | 49.915
2020-01-27 | 12:02 | 49.913
2020-01-27 | 12:02 | 49.91
2020-01-27 | 12:02 | 49.908
2020-01-27 | 12:02 | 49.906
2020-01-27 | 12:02 | 49.902
2020-01-27 | 12:02 | 49.898
2020-01-27 | 12:02 | 49.896
2020-01-27 | 12:02 | 49.893
2020-01-27 | 12:02 | 49.893
2020-01-27 | 12:02 | 49.892
2020-01-27 | 12:02 | 49.891
2020-01-27 | 12:02 | 49.891
2020-01-27 | 12:02 | 49.889
2020-01-27 | 12:02 | 49.887
2020-01-27 | 12:02 | 49.885
2020-01-27 | 12:02 | 49.882
2020-01-27 | 12:02 | 49.882
2020-01-27 | 12:02 | 49.881
2020-01-27 | 12:02 | 49.88
2020-01-27 | 12:02 | 49.881
2020-01-27 | 12:02 | 49.883
2020-01-27 | 12:02 | 49.882
2020-01-27 | 12:02 | 49.882
2020-01-27 | 12:02 | 49.882
2020-01-27 | 12:02 | 49.883
2020-01-27 | 12:02 | 49.886
2020-01-27 | 12:02 | 49.887
2020-01-27 | 12:02 | 49.888
2020-01-27 | 12:02 | 49.888
2020-01-27 | 12:02 | 49.89
2020-01-27 | 12:02 | 49.89
2020-01-27 | 12:02 | 49.892
2020-01-27 | 12:02 | 49.895
2020-01-27 | 12:02 | 49.896
2020-01-27 | 12:02 | 49.897
2020-01-27 | 12:02 | 49.896
2020-01-27 | 12:03 | 49.895
2020-01-27 | 12:03 | 49.893
2020-01-27 | 12:03 | 49.891
2020-01-27 | 12:03 | 49.888
2020-01-27 | 12:03 | 49.885
2020-01-27 | 12:03 | 49.881
2020-01-27 | 12:03 | 49.877
2020-01-27 | 12:03 | 49.874
2020-01-27 | 12:03 | 49.872
2020-01-27 | 12:03 | 49.871
2020-01-27 | 12:03 | 49.872
2020-01-27 | 12:03 | 49.872
2020-01-27 | 12:03 | 49.873
2020-01-27 | 12:03 | 49.873
2020-01-27 | 12:03 | 49.875
2020-01-27 | 12:03 | 49.874
2020-01-27 | 12:03 | 49.876
2020-01-27 | 12:03 | 49.877
2020-01-27 | 12:03 | 49.877
2020-01-27 | 12:03 | 49.875
2020-01-27 | 12:03 | 49.874
2020-01-27 | 12:03 | 49.873
2020-01-27 | 12:03 | 49.875
2020-01-27 | 12:03 | 49.877
2020-01-27 | 12:03 | 49.879
2020-01-27 | 12:03 | 49.882
2020-01-27 | 12:03 | 49.884
2020-01-27 | 12:03 | 49.889
2020-01-27 | 12:03 | 49.893
2020-01-27 | 12:03 | 49.895
2020-01-27 | 12:03 | 49.896
2020-01-27 | 12:03 | 49.896
2020-01-27 | 12:03 | 49.895
2020-01-27 | 12:03 | 49.895
2020-01-27 | 12:03 | 49.894
2020-01-27 | 12:03 | 49.895
2020-01-27 | 12:03 | 49.894
2020-01-27 | 12:03 | 49.894
2020-01-27 | 12:03 | 49.893
2020-01-27 | 12:03 | 49.893
2020-01-27 | 12:03 | 49.891
2020-01-27 | 12:03 | 49.89
2020-01-27 | 12:03 | 49.889
2020-01-27 | 12:03 | 49.889
2020-01-27 | 12:03 | 49.889
2020-01-27 | 12:03 | 49.888
2020-01-27 | 12:03 | 49.885
2020-01-27 | 12:03 | 49.882
2020-01-27 | 12:03 | 49.878
2020-01-27 | 12:03 | 49.874
2020-01-27 | 12:03 | 49.871
2020-01-27 | 12:03 | 49.867
2020-01-27 | 12:03 | 49.865
2020-01-27 | 12:03 | 49.865
2020-01-27 | 12:03 | 49.863
2020-01-27 | 12:03 | 49.862
2020-01-27 | 12:03 | 49.862
2020-01-27 | 12:03 | 49.862
2020-01-27 | 12:03 | 49.863
2020-01-27 | 12:04 | 49.863
2020-01-27 | 12:04 | 49.865
2020-01-27 | 12:04 | 49.865
2020-01-27 | 12:04 | 49.866
2020-01-27 | 12:04 | 49.867
2020-01-27 | 12:04 | 49.867
2020-01-27 | 12:04 | 49.866
2020-01-27 | 12:04 | 49.864
2020-01-27 | 12:04 | 49.867
2020-01-27 | 12:04 | 49.869
2020-01-27 | 12:04 | 49.87
2020-01-27 | 12:04 | 49.872
2020-01-27 | 12:04 | 49.87
2020-01-27 | 12:04 | 49.869
2020-01-27 | 12:04 | 49.868
2020-01-27 | 12:04 | 49.866
2020-01-27 | 12:04 | 49.865
2020-01-27 | 12:04 | 49.863
2020-01-27 | 12:04 | 49.861
2020-01-27 | 12:04 | 49.859
2020-01-27 | 12:04 | 49.857
2020-01-27 | 12:04 | 49.852
2020-01-27 | 12:04 | 49.851
2020-01-27 | 12:04 | 49.848
2020-01-27 | 12:04 | 49.846
2020-01-27 | 12:04 | 49.844
2020-01-27 | 12:04 | 49.841
2020-01-27 | 12:04 | 49.84
2020-01-27 | 12:04 | 49.837
2020-01-27 | 12:04 | 49.833
2020-01-27 | 12:04 | 49.829
2020-01-27 | 12:04 | 49.826
2020-01-27 | 12:04 | 49.822
2020-01-27 | 12:04 | 49.822
2020-01-27 | 12:04 | 49.821
2020-01-27 | 12:04 | 49.822
2020-01-27 | 12:04 | 49.821
2020-01-27 | 12:04 | 49.821
2020-01-27 | 12:04 | 49.821
2020-01-27 | 12:04 | 49.82
2020-01-27 | 12:04 | 49.817
2020-01-27 | 12:04 | 49.814
2020-01-27 | 12:04 | 49.811
2020-01-27 | 12:04 | 49.81
2020-01-27 | 12:04 | 49.81
2020-01-27 | 12:04 | 49.81
2020-01-27 | 12:04 | 49.812
2020-01-27 | 12:04 | 49.812
2020-01-27 | 12:04 | 49.812
2020-01-27 | 12:04 | 49.814
2020-01-27 | 12:04 | 49.814
2020-01-27 | 12:04 | 49.817
2020-01-27 | 12:04 | 49.818
2020-01-27 | 12:04 | 49.819
2020-01-27 | 12:04 | 49.819
2020-01-27 | 12:04 | 49.817
2020-01-27 | 12:04 | 49.816
2020-01-27 | 12:04 | 49.813
2020-01-27 | 12:04 | 49.81
2020-01-27 | 12:04 | 49.805
2020-01-27 | 12:04 | 49.802
2020-01-27 | 12:05 | 49.799
2020-01-27 | 12:05 | 49.797
2020-01-27 | 12:05 | 49.795
2020-01-27 | 12:05 | 49.795
2020-01-27 | 12:05 | 49.796
2020-01-27 | 12:05 | 49.797
2020-01-27 | 12:05 | 49.797
2020-01-27 | 12:05 | 49.799
2020-01-27 | 12:05 | 49.801
2020-01-27 | 12:05 | 49.803
2020-01-27 | 12:05 | 49.804
2020-01-27 | 12:05 | 49.806
2020-01-27 | 12:05 | 49.805
2020-01-27 | 12:05 | 49.804
2020-01-27 | 12:05 | 49.806
2020-01-27 | 12:05 | 49.807
2020-01-27 | 12:05 | 49.808
2020-01-27 | 12:05 | 49.809
2020-01-27 | 12:05 | 49.81
2020-01-27 | 12:05 | 49.814
2020-01-27 | 12:05 | 49.818
2020-01-27 | 12:05 | 49.818
2020-01-27 | 12:05 | 49.819
2020-01-27 | 12:05 | 49.819
2020-01-27 | 12:05 | 49.818
2020-01-27 | 12:05 | 49.819
2020-01-27 | 12:05 | 49.819
2020-01-27 | 12:05 | 49.821
2020-01-27 | 12:05 | 49.821
2020-01-27 | 12:05 | 49.822
2020-01-27 | 12:05 | 49.822
2020-01-27 | 12:05 | 49.822
2020-01-27 | 12:05 | 49.822
2020-01-27 | 12:05 | 49.822
2020-01-27 | 12:05 | 49.823
2020-01-27 | 12:05 | 49.824
2020-01-27 | 12:05 | 49.824
2020-01-27 | 12:05 | 49.823
2020-01-27 | 12:05 | 49.822
2020-01-27 | 12:05 | 49.823
2020-01-27 | 12:05 | 49.825
2020-01-27 | 12:05 | 49.827
2020-01-27 | 12:05 | 49.83
2020-01-27 | 12:05 | 49.832
2020-01-27 | 12:05 | 49.834
2020-01-27 | 12:05 | 49.836
2020-01-27 | 12:05 | 49.838
2020-01-27 | 12:05 | 49.838
2020-01-27 | 12:05 | 49.839
2020-01-27 | 12:05 | 49.838
2020-01-27 | 12:05 | 49.838
2020-01-27 | 12:05 | 49.839
2020-01-27 | 12:05 | 49.835
2020-01-27 | 12:05 | 49.833
2020-01-27 | 12:05 | 49.83
2020-01-27 | 12:05 | 49.826
2020-01-27 | 12:05 | 49.827
2020-01-27 | 12:05 | 49.829
2020-01-27 | 12:05 | 49.834
2020-01-27 | 12:06 | 49.839
2020-01-27 | 12:06 | 49.843
2020-01-27 | 12:06 | 49.849
2020-01-27 | 12:06 | 49.856
2020-01-27 | 12:06 | 49.863
2020-01-27 | 12:06 | 49.868
2020-01-27 | 12:06 | 49.877
2020-01-27 | 12:06 | 49.884
2020-01-27 | 12:06 | 49.892
2020-01-27 | 12:06 | 49.897
2020-01-27 | 12:06 | 49.901
2020-01-27 | 12:06 | 49.903
2020-01-27 | 12:06 | 49.903
2020-01-27 | 12:06 | 49.903
2020-01-27 | 12:06 | 49.903
2020-01-27 | 12:06 | 49.9
2020-01-27 | 12:06 | 49.897
2020-01-27 | 12:06 | 49.896
2020-01-27 | 12:06 | 49.894
2020-01-27 | 12:06 | 49.892
2020-01-27 | 12:06 | 49.89
2020-01-27 | 12:06 | 49.887
2020-01-27 | 12:06 | 49.885
2020-01-27 | 12:06 | 49.884
2020-01-27 | 12:06 | 49.884
2020-01-27 | 12:06 | 49.884
2020-01-27 | 12:06 | 49.883
2020-01-27 | 12:06 | 49.881
2020-01-27 | 12:06 | 49.879
2020-01-27 | 12:06 | 49.877
2020-01-27 | 12:06 | 49.875
2020-01-27 | 12:06 | 49.871
2020-01-27 | 12:06 | 49.868
2020-01-27 | 12:06 | 49.865
2020-01-27 | 12:06 | 49.861
2020-01-27 | 12:06 | 49.856
2020-01-27 | 12:06 | 49.853
2020-01-27 | 12:06 | 49.849
2020-01-27 | 12:06 | 49.846
2020-01-27 | 12:06 | 49.843
2020-01-27 | 12:06 | 49.84
2020-01-27 | 12:06 | 49.838
2020-01-27 | 12:06 | 49.839
2020-01-27 | 12:06 | 49.838
2020-01-27 | 12:06 | 49.837
2020-01-27 | 12:06 | 49.837
2020-01-27 | 12:06 | 49.837
2020-01-27 | 12:06 | 49.838
2020-01-27 | 12:06 | 49.84
2020-01-27 | 12:06 | 49.841
2020-01-27 | 12:06 | 49.842
2020-01-27 | 12:06 | 49.842
2020-01-27 | 12:06 | 49.842
2020-01-27 | 12:06 | 49.843
2020-01-27 | 12:06 | 49.845
2020-01-27 | 12:06 | 49.846
2020-01-27 | 12:06 | 49.845
2020-01-27 | 12:06 | 49.846
2020-01-27 | 12:06 | 49.846
2020-01-27 | 12:06 | 49.846
2020-01-27 | 12:06 | 49.846
2020-01-27 | 12:07 | 49.843
2020-01-27 | 12:07 | 49.842
2020-01-27 | 12:07 | 49.84
2020-01-27 | 12:07 | 49.841
2020-01-27 | 12:07 | 49.842
2020-01-27 | 12:07 | 49.843
2020-01-27 | 12:07 | 49.844
2020-01-27 | 12:07 | 49.847
2020-01-27 | 12:07 | 49.851
2020-01-27 | 12:07 | 49.852
2020-01-27 | 12:07 | 49.855
2020-01-27 | 12:07 | 49.858
2020-01-27 | 12:07 | 49.86
2020-01-27 | 12:07 | 49.861
2020-01-27 | 12:07 | 49.859
2020-01-27 | 12:07 | 49.857
2020-01-27 | 12:07 | 49.858
2020-01-27 | 12:07 | 49.858
2020-01-27 | 12:07 | 49.856
2020-01-27 | 12:07 | 49.856
2020-01-27 | 12:07 | 49.856
2020-01-27 | 12:07 | 49.856
2020-01-27 | 12:07 | 49.858
2020-01-27 | 12:07 | 49.857
2020-01-27 | 12:07 | 49.86
2020-01-27 | 12:07 | 49.861
2020-01-27 | 12:07 | 49.859
2020-01-27 | 12:07 | 49.859
2020-01-27 | 12:07 | 49.857
2020-01-27 | 12:07 | 49.854
2020-01-27 | 12:07 | 49.849
2020-01-27 | 12:07 | 49.846
2020-01-27 | 12:07 | 49.843
2020-01-27 | 12:07 | 49.844
2020-01-27 | 12:07 | 49.846
2020-01-27 | 12:07 | 49.846
2020-01-27 | 12:07 | 49.845
2020-01-27 | 12:07 | 49.845
2020-01-27 | 12:07 | 49.843
2020-01-27 | 12:07 | 49.843
2020-01-27 | 12:07 | 49.842
2020-01-27 | 12:07 | 49.841
2020-01-27 | 12:07 | 49.839
2020-01-27 | 12:07 | 49.838
2020-01-27 | 12:07 | 49.835
2020-01-27 | 12:07 | 49.835
2020-01-27 | 12:07 | 49.835
2020-01-27 | 12:07 | 49.837
2020-01-27 | 12:07 | 49.838
2020-01-27 | 12:07 | 49.838
2020-01-27 | 12:07 | 49.844
2020-01-27 | 12:07 | 49.847
2020-01-27 | 12:07 | 49.855
2020-01-27 | 12:07 | 49.858
2020-01-27 | 12:07 | 49.864
2020-01-27 | 12:07 | 49.869
2020-01-27 | 12:07 | 49.874
2020-01-27 | 12:07 | 49.879
2020-01-27 | 12:07 | 49.882
2020-01-27 | 12:08 | 49.885
2020-01-27 | 12:08 | 49.887
2020-01-27 | 12:08 | 49.889
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.894
2020-01-27 | 12:08 | 49.897
2020-01-27 | 12:08 | 49.898
2020-01-27 | 12:08 | 49.897
2020-01-27 | 12:08 | 49.897
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.891
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.897
2020-01-27 | 12:08 | 49.9
2020-01-27 | 12:08 | 49.904
2020-01-27 | 12:08 | 49.905
2020-01-27 | 12:08 | 49.908
2020-01-27 | 12:08 | 49.909
2020-01-27 | 12:08 | 49.912
2020-01-27 | 12:08 | 49.914
2020-01-27 | 12:08 | 49.916
2020-01-27 | 12:08 | 49.916
2020-01-27 | 12:08 | 49.918
2020-01-27 | 12:08 | 49.915
2020-01-27 | 12:08 | 49.912
2020-01-27 | 12:08 | 49.909
2020-01-27 | 12:08 | 49.905
2020-01-27 | 12:08 | 49.9
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.894
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.894
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.894
2020-01-27 | 12:08 | 49.894
2020-01-27 | 12:08 | 49.896
2020-01-27 | 12:08 | 49.896
2020-01-27 | 12:08 | 49.897
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.894
2020-01-27 | 12:08 | 49.895
2020-01-27 | 12:08 | 49.893
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.892
2020-01-27 | 12:08 | 49.89
2020-01-27 | 12:08 | 49.89
2020-01-27 | 12:08 | 49.89
2020-01-27 | 12:09 | 49.891
2020-01-27 | 12:09 | 49.891
2020-01-27 | 12:09 | 49.889
2020-01-27 | 12:09 | 49.89
2020-01-27 | 12:09 | 49.889
2020-01-27 | 12:09 | 49.888
2020-01-27 | 12:09 | 49.884
2020-01-27 | 12:09 | 49.883
2020-01-27 | 12:09 | 49.881
2020-01-27 | 12:09 | 49.876
2020-01-27 | 12:09 | 49.874
2020-01-27 | 12:09 | 49.874
2020-01-27 | 12:09 | 49.873
2020-01-27 | 12:09 | 49.876
2020-01-27 | 12:09 | 49.877
2020-01-27 | 12:09 | 49.877
2020-01-27 | 12:09 | 49.877
2020-01-27 | 12:09 | 49.877
2020-01-27 | 12:09 | 49.878
2020-01-27 | 12:09 | 49.881
2020-01-27 | 12:09 | 49.88
2020-01-27 | 12:09 | 49.878
2020-01-27 | 12:09 | 49.876
2020-01-27 | 12:09 | 49.876
2020-01-27 | 12:09 | 49.878
2020-01-27 | 12:09 | 49.88
2020-01-27 | 12:09 | 49.884
2020-01-27 | 12:09 | 49.888
2020-01-27 | 12:09 | 49.891
2020-01-27 | 12:09 | 49.891
2020-01-27 | 12:09 | 49.892
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.897
2020-01-27 | 12:09 | 49.898
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.897
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.895
2020-01-27 | 12:09 | 49.895
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.897
2020-01-27 | 12:09 | 49.896
2020-01-27 | 12:09 | 49.899
2020-01-27 | 12:09 | 49.901
2020-01-27 | 12:09 | 49.905
2020-01-27 | 12:09 | 49.906
2020-01-27 | 12:09 | 49.907
2020-01-27 | 12:09 | 49.908
2020-01-27 | 12:09 | 49.907
2020-01-27 | 12:09 | 49.906
2020-01-27 | 12:09 | 49.904
2020-01-27 | 12:09 | 49.903
2020-01-27 | 12:09 | 49.902
2020-01-27 | 12:09 | 49.904
2020-01-27 | 12:09 | 49.9
2020-01-27 | 12:09 | 49.899
2020-01-27 | 12:09 | 49.903
2020-01-27 | 12:10 | 49.907
2020-01-27 | 12:10 | 49.909
2020-01-27 | 12:10 | 49.91
2020-01-27 | 12:10 | 49.912
2020-01-27 | 12:10 | 49.914
2020-01-27 | 12:10 | 49.917
2020-01-27 | 12:10 | 49.919
2020-01-27 | 12:10 | 49.922
2020-01-27 | 12:10 | 49.925
2020-01-27 | 12:10 | 49.927
2020-01-27 | 12:10 | 49.926
2020-01-27 | 12:10 | 49.926
2020-01-27 | 12:10 | 49.927
2020-01-27 | 12:10 | 49.93
2020-01-27 | 12:10 | 49.931
2020-01-27 | 12:10 | 49.934
2020-01-27 | 12:10 | 49.933
2020-01-27 | 12:10 | 49.933
2020-01-27 | 12:10 | 49.932
2020-01-27 | 12:10 | 49.929
2020-01-27 | 12:10 | 49.927
2020-01-27 | 12:10 | 49.928
2020-01-27 | 12:10 | 49.925
2020-01-27 | 12:10 | 49.925
2020-01-27 | 12:10 | 49.925
2020-01-27 | 12:10 | 49.926
2020-01-27 | 12:10 | 49.926
2020-01-27 | 12:10 | 49.928
2020-01-27 | 12:10 | 49.93
2020-01-27 | 12:10 | 49.931
2020-01-27 | 12:10 | 49.933
2020-01-27 | 12:10 | 49.933
2020-01-27 | 12:10 | 49.934
2020-01-27 | 12:10 | 49.935
2020-01-27 | 12:10 | 49.936
2020-01-27 | 12:10 | 49.938
2020-01-27 | 12:10 | 49.943
2020-01-27 | 12:10 | 49.946
2020-01-27 | 12:10 | 49.949
2020-01-27 | 12:10 | 49.951
2020-01-27 | 12:10 | 49.953
2020-01-27 | 12:10 | 49.953
2020-01-27 | 12:10 | 49.954
2020-01-27 | 12:10 | 49.957
2020-01-27 | 12:10 | 49.958
2020-01-27 | 12:10 | 49.957
2020-01-27 | 12:10 | 49.957
2020-01-27 | 12:10 | 49.957
2020-01-27 | 12:10 | 49.956
2020-01-27 | 12:10 | 49.953
2020-01-27 | 12:10 | 49.954
2020-01-27 | 12:10 | 49.957
2020-01-27 | 12:10 | 49.956
2020-01-27 | 12:10 | 49.956
2020-01-27 | 12:10 | 49.958
2020-01-27 | 12:10 | 49.958
2020-01-27 | 12:10 | 49.957
2020-01-27 | 12:10 | 49.956
2020-01-27 | 12:10 | 49.954
2020-01-27 | 12:10 | 49.952
2020-01-27 | 12:10 | 49.951
2020-01-27 | 12:11 | 49.95
2020-01-27 | 12:11 | 49.95
2020-01-27 | 12:11 | 49.949
2020-01-27 | 12:11 | 49.946
2020-01-27 | 12:11 | 49.947
2020-01-27 | 12:11 | 49.946
2020-01-27 | 12:11 | 49.942
2020-01-27 | 12:11 | 49.941
2020-01-27 | 12:11 | 49.94
2020-01-27 | 12:11 | 49.936
2020-01-27 | 12:11 | 49.935
2020-01-27 | 12:11 | 49.932
2020-01-27 | 12:11 | 49.93
2020-01-27 | 12:11 | 49.931
2020-01-27 | 12:11 | 49.933
2020-01-27 | 12:11 | 49.932
2020-01-27 | 12:11 | 49.932
2020-01-27 | 12:11 | 49.932
2020-01-27 | 12:11 | 49.931
2020-01-27 | 12:11 | 49.933
2020-01-27 | 12:11 | 49.931
2020-01-27 | 12:11 | 49.93
2020-01-27 | 12:11 | 49.927
2020-01-27 | 12:11 | 49.926
2020-01-27 | 12:11 | 49.925
2020-01-27 | 12:11 | 49.93
2020-01-27 | 12:11 | 49.934
2020-01-27 | 12:11 | 49.935
2020-01-27 | 12:11 | 49.935
2020-01-27 | 12:11 | 49.936
2020-01-27 | 12:11 | 49.936
2020-01-27 | 12:11 | 49.934
2020-01-27 | 12:11 | 49.933
2020-01-27 | 12:11 | 49.929
2020-01-27 | 12:11 | 49.924
2020-01-27 | 12:11 | 49.92
2020-01-27 | 12:11 | 49.916
2020-01-27 | 12:11 | 49.915
2020-01-27 | 12:11 | 49.916
2020-01-27 | 12:11 | 49.914
2020-01-27 | 12:11 | 49.914
2020-01-27 | 12:11 | 49.913
2020-01-27 | 12:11 | 49.911
2020-01-27 | 12:11 | 49.909
2020-01-27 | 12:11 | 49.908
2020-01-27 | 12:11 | 49.905
2020-01-27 | 12:11 | 49.902
2020-01-27 | 12:11 | 49.9
2020-01-27 | 12:11 | 49.899
2020-01-27 | 12:11 | 49.898
2020-01-27 | 12:11 | 49.897
2020-01-27 | 12:11 | 49.897
2020-01-27 | 12:11 | 49.899
2020-01-27 | 12:11 | 49.901
2020-01-27 | 12:11 | 49.902
2020-01-27 | 12:11 | 49.902
2020-01-27 | 12:11 | 49.906
2020-01-27 | 12:11 | 49.908
2020-01-27 | 12:11 | 49.91
2020-01-27 | 12:12 | 49.912
2020-01-27 | 12:12 | 49.918
2020-01-27 | 12:12 | 49.918
2020-01-27 | 12:12 | 49.919
2020-01-27 | 12:12 | 49.922
2020-01-27 | 12:12 | 49.921
2020-01-27 | 12:12 | 49.924
2020-01-27 | 12:12 | 49.93
2020-01-27 | 12:12 | 49.934
2020-01-27 | 12:12 | 49.936
2020-01-27 | 12:12 | 49.938
2020-01-27 | 12:12 | 49.94
2020-01-27 | 12:12 | 49.943
2020-01-27 | 12:12 | 49.946
2020-01-27 | 12:12 | 49.947
2020-01-27 | 12:12 | 49.951
2020-01-27 | 12:12 | 49.954
2020-01-27 | 12:12 | 49.955
2020-01-27 | 12:12 | 49.954
2020-01-27 | 12:12 | 49.953
2020-01-27 | 12:12 | 49.952
2020-01-27 | 12:12 | 49.952
2020-01-27 | 12:12 | 49.952
2020-01-27 | 12:12 | 49.95
2020-01-27 | 12:12 | 49.946
2020-01-27 | 12:12 | 49.944
2020-01-27 | 12:12 | 49.943
2020-01-27 | 12:12 | 49.941
2020-01-27 | 12:12 | 49.938
2020-01-27 | 12:12 | 49.934
2020-01-27 | 12:12 | 49.932
2020-01-27 | 12:12 | 49.931
2020-01-27 | 12:12 | 49.93
2020-01-27 | 12:12 | 49.928
2020-01-27 | 12:12 | 49.928
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.932
2020-01-27 | 12:12 | 49.932
2020-01-27 | 12:12 | 49.933
2020-01-27 | 12:12 | 49.932
2020-01-27 | 12:12 | 49.931
2020-01-27 | 12:12 | 49.93
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.931
2020-01-27 | 12:12 | 49.928
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.928
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.929
2020-01-27 | 12:12 | 49.931
2020-01-27 | 12:12 | 49.933
2020-01-27 | 12:12 | 49.935
2020-01-27 | 12:12 | 49.935
2020-01-27 | 12:12 | 49.937
2020-01-27 | 12:12 | 49.937
2020-01-27 | 12:12 | 49.94
2020-01-27 | 12:12 | 49.943
2020-01-27 | 12:12 | 49.944
2020-01-27 | 12:12 | 49.945
2020-01-27 | 12:13 | 49.945
2020-01-27 | 12:13 | 49.947
2020-01-27 | 12:13 | 49.948
2020-01-27 | 12:13 | 49.947
2020-01-27 | 12:13 | 49.945
2020-01-27 | 12:13 | 49.944
2020-01-27 | 12:13 | 49.943
2020-01-27 | 12:13 | 49.939
2020-01-27 | 12:13 | 49.939
2020-01-27 | 12:13 | 49.936
2020-01-27 | 12:13 | 49.932
2020-01-27 | 12:13 | 49.929
2020-01-27 | 12:13 | 49.928
2020-01-27 | 12:13 | 49.925
2020-01-27 | 12:13 | 49.923
2020-01-27 | 12:13 | 49.924
2020-01-27 | 12:13 | 49.923
2020-01-27 | 12:13 | 49.922
2020-01-27 | 12:13 | 49.921
2020-01-27 | 12:13 | 49.922
2020-01-27 | 12:13 | 49.922
2020-01-27 | 12:13 | 49.921
2020-01-27 | 12:13 | 49.92
2020-01-27 | 12:13 | 49.92
2020-01-27 | 12:13 | 49.919
2020-01-27 | 12:13 | 49.916
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.913
2020-01-27 | 12:13 | 49.911
2020-01-27 | 12:13 | 49.911
2020-01-27 | 12:13 | 49.908
2020-01-27 | 12:13 | 49.908
2020-01-27 | 12:13 | 49.909
2020-01-27 | 12:13 | 49.911
2020-01-27 | 12:13 | 49.912
2020-01-27 | 12:13 | 49.913
2020-01-27 | 12:13 | 49.913
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.914
2020-01-27 | 12:13 | 49.912
2020-01-27 | 12:13 | 49.912
2020-01-27 | 12:13 | 49.909
2020-01-27 | 12:13 | 49.909
2020-01-27 | 12:13 | 49.908
2020-01-27 | 12:13 | 49.907
2020-01-27 | 12:13 | 49.906
2020-01-27 | 12:13 | 49.91
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.916
2020-01-27 | 12:13 | 49.916
2020-01-27 | 12:13 | 49.916
2020-01-27 | 12:13 | 49.915
2020-01-27 | 12:13 | 49.914
2020-01-27 | 12:13 | 49.91
2020-01-27 | 12:13 | 49.904
2020-01-27 | 12:13 | 49.897
2020-01-27 | 12:14 | 49.89
2020-01-27 | 12:14 | 49.885
2020-01-27 | 12:14 | 49.881
2020-01-27 | 12:14 | 49.878
2020-01-27 | 12:14 | 49.874
2020-01-27 | 12:14 | 49.871
2020-01-27 | 12:14 | 49.869
2020-01-27 | 12:14 | 49.867
2020-01-27 | 12:14 | 49.865
2020-01-27 | 12:14 | 49.865
2020-01-27 | 12:14 | 49.862
2020-01-27 | 12:14 | 49.861
2020-01-27 | 12:14 | 49.86
2020-01-27 | 12:14 | 49.863
2020-01-27 | 12:14 | 49.865
2020-01-27 | 12:14 | 49.868
2020-01-27 | 12:14 | 49.87
2020-01-27 | 12:14 | 49.873
2020-01-27 | 12:14 | 49.878
2020-01-27 | 12:14 | 49.881
2020-01-27 | 12:14 | 49.884
2020-01-27 | 12:14 | 49.888
2020-01-27 | 12:14 | 49.888
2020-01-27 | 12:14 | 49.89
2020-01-27 | 12:14 | 49.889
2020-01-27 | 12:14 | 49.89
2020-01-27 | 12:14 | 49.891
2020-01-27 | 12:14 | 49.895
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.9
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.9
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:14 | 49.898
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.9
2020-01-27 | 12:14 | 49.898
2020-01-27 | 12:14 | 49.898
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.898
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.901
2020-01-27 | 12:14 | 49.902
2020-01-27 | 12:14 | 49.902
2020-01-27 | 12:14 | 49.902
2020-01-27 | 12:14 | 49.9
2020-01-27 | 12:14 | 49.898
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:14 | 49.896
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:14 | 49.898
2020-01-27 | 12:14 | 49.899
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:14 | 49.897
2020-01-27 | 12:15 | 49.896
2020-01-27 | 12:15 | 49.891
2020-01-27 | 12:15 | 49.89
2020-01-27 | 12:15 | 49.891
2020-01-27 | 12:15 | 49.891
2020-01-27 | 12:15 | 49.891
2020-01-27 | 12:15 | 49.892
2020-01-27 | 12:15 | 49.895
2020-01-27 | 12:15 | 49.896
2020-01-27 | 12:15 | 49.899
2020-01-27 | 12:15 | 49.9
2020-01-27 | 12:15 | 49.901
2020-01-27 | 12:15 | 49.903
2020-01-27 | 12:15 | 49.904
2020-01-27 | 12:15 | 49.906
2020-01-27 | 12:15 | 49.904
2020-01-27 | 12:15 | 49.904
2020-01-27 | 12:15 | 49.902
2020-01-27 | 12:15 | 49.902
2020-01-27 | 12:15 | 49.9
2020-01-27 | 12:15 | 49.898
2020-01-27 | 12:15 | 49.896
2020-01-27 | 12:15 | 49.895
2020-01-27 | 12:15 | 49.895
2020-01-27 | 12:15 | 49.893
2020-01-27 | 12:15 | 49.894
2020-01-27 | 12:15 | 49.892
2020-01-27 | 12:15 | 49.889
2020-01-27 | 12:15 | 49.887
2020-01-27 | 12:15 | 49.883
2020-01-27 | 12:15 | 49.879
2020-01-27 | 12:15 | 49.875
2020-01-27 | 12:15 | 49.873
2020-01-27 | 12:15 | 49.872
2020-01-27 | 12:15 | 49.873
2020-01-27 | 12:15 | 49.875
2020-01-27 | 12:15 | 49.878
2020-01-27 | 12:15 | 49.877
2020-01-27 | 12:15 | 49.876
2020-01-27 | 12:15 | 49.875
2020-01-27 | 12:15 | 49.873
2020-01-27 | 12:15 | 49.873
2020-01-27 | 12:15 | 49.87
2020-01-27 | 12:15 | 49.868
2020-01-27 | 12:15 | 49.866
2020-01-27 | 12:15 | 49.865
2020-01-27 | 12:15 | 49.865
2020-01-27 | 12:15 | 49.866
2020-01-27 | 12:15 | 49.868
2020-01-27 | 12:15 | 49.871
2020-01-27 | 12:15 | 49.872
2020-01-27 | 12:15 | 49.871
2020-01-27 | 12:15 | 49.871
2020-01-27 | 12:15 | 49.872
2020-01-27 | 12:15 | 49.872
2020-01-27 | 12:15 | 49.872
2020-01-27 | 12:15 | 49.871
2020-01-27 | 12:15 | 49.869
2020-01-27 | 12:15 | 49.868
2020-01-27 | 12:16 | 49.867
2020-01-27 | 12:16 | 49.867
2020-01-27 | 12:16 | 49.866
2020-01-27 | 12:16 | 49.867
2020-01-27 | 12:16 | 49.868
2020-01-27 | 12:16 | 49.87
2020-01-27 | 12:16 | 49.869
2020-01-27 | 12:16 | 49.869
2020-01-27 | 12:16 | 49.869
2020-01-27 | 12:16 | 49.869
2020-01-27 | 12:16 | 49.867
2020-01-27 | 12:16 | 49.866
2020-01-27 | 12:16 | 49.864
2020-01-27 | 12:16 | 49.861
2020-01-27 | 12:16 | 49.861
2020-01-27 | 12:16 | 49.859
2020-01-27 | 12:16 | 49.86
2020-01-27 | 12:16 | 49.862
2020-01-27 | 12:16 | 49.864
2020-01-27 | 12:16 | 49.867
2020-01-27 | 12:16 | 49.869
2020-01-27 | 12:16 | 49.873
2020-01-27 | 12:16 | 49.878
2020-01-27 | 12:16 | 49.881
2020-01-27 | 12:16 | 49.885
2020-01-27 | 12:16 | 49.887
2020-01-27 | 12:16 | 49.892
2020-01-27 | 12:16 | 49.897
2020-01-27 | 12:16 | 49.901
2020-01-27 | 12:16 | 49.903
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.906
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.904
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.906
2020-01-27 | 12:16 | 49.904
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.905
2020-01-27 | 12:16 | 49.904
2020-01-27 | 12:16 | 49.901
2020-01-27 | 12:16 | 49.901
2020-01-27 | 12:16 | 49.9
2020-01-27 | 12:16 | 49.898
2020-01-27 | 12:16 | 49.899
2020-01-27 | 12:16 | 49.899
2020-01-27 | 12:16 | 49.899
2020-01-27 | 12:16 | 49.901
2020-01-27 | 12:16 | 49.9
2020-01-27 | 12:16 | 49.902
2020-01-27 | 12:16 | 49.901
2020-01-27 | 12:16 | 49.901
2020-01-27 | 12:16 | 49.898
2020-01-27 | 12:16 | 49.896
2020-01-27 | 12:16 | 49.894
2020-01-27 | 12:16 | 49.892
2020-01-27 | 12:16 | 49.889
2020-01-27 | 12:16 | 49.888
2020-01-27 | 12:16 | 49.885
2020-01-27 | 12:17 | 49.884
2020-01-27 | 12:17 | 49.882
2020-01-27 | 12:17 | 49.883
2020-01-27 | 12:17 | 49.883
2020-01-27 | 12:17 | 49.885
2020-01-27 | 12:17 | 49.885
2020-01-27 | 12:17 | 49.888
2020-01-27 | 12:17 | 49.888
2020-01-27 | 12:17 | 49.888
2020-01-27 | 12:17 | 49.888
2020-01-27 | 12:17 | 49.888
2020-01-27 | 12:17 | 49.889
2020-01-27 | 12:17 | 49.889
2020-01-27 | 12:17 | 49.89
2020-01-27 | 12:17 | 49.891
2020-01-27 | 12:17 | 49.891
2020-01-27 | 12:17 | 49.891
2020-01-27 | 12:17 | 49.89
2020-01-27 | 12:17 | 49.89
2020-01-27 | 12:17 | 49.888
2020-01-27 | 12:17 | 49.887
2020-01-27 | 12:17 | 49.885
2020-01-27 | 12:17 | 49.883
2020-01-27 | 12:17 | 49.879
2020-01-27 | 12:17 | 49.878
2020-01-27 | 12:17 | 49.876
2020-01-27 | 12:17 | 49.874
2020-01-27 | 12:17 | 49.874
2020-01-27 | 12:17 | 49.873
2020-01-27 | 12:17 | 49.872
2020-01-27 | 12:17 | 49.873
2020-01-27 | 12:17 | 49.873
2020-01-27 | 12:17 | 49.873
2020-01-27 | 12:17 | 49.873
2020-01-27 | 12:17 | 49.869
2020-01-27 | 12:17 | 49.867
2020-01-27 | 12:17 | 49.862
2020-01-27 | 12:17 | 49.858
2020-01-27 | 12:17 | 49.854
2020-01-27 | 12:17 | 49.852
2020-01-27 | 12:17 | 49.851
2020-01-27 | 12:17 | 49.851
2020-01-27 | 12:17 | 49.851
2020-01-27 | 12:17 | 49.851
2020-01-27 | 12:17 | 49.853
2020-01-27 | 12:17 | 49.856
2020-01-27 | 12:17 | 49.857
2020-01-27 | 12:17 | 49.856
2020-01-27 | 12:17 | 49.856
2020-01-27 | 12:17 | 49.854
2020-01-27 | 12:17 | 49.853
2020-01-27 | 12:17 | 49.852
2020-01-27 | 12:17 | 49.851
2020-01-27 | 12:17 | 49.853
2020-01-27 | 12:17 | 49.855
2020-01-27 | 12:17 | 49.859
2020-01-27 | 12:17 | 49.862
2020-01-27 | 12:17 | 49.867
2020-01-27 | 12:17 | 49.87
2020-01-27 | 12:18 | 49.872
2020-01-27 | 12:18 | 49.873
2020-01-27 | 12:18 | 49.872
2020-01-27 | 12:18 | 49.872
2020-01-27 | 12:18 | 49.872
2020-01-27 | 12:18 | 49.87
2020-01-27 | 12:18 | 49.874
2020-01-27 | 12:18 | 49.875
2020-01-27 | 12:18 | 49.875
2020-01-27 | 12:18 | 49.875
2020-01-27 | 12:18 | 49.877
2020-01-27 | 12:18 | 49.879
2020-01-27 | 12:18 | 49.882
2020-01-27 | 12:18 | 49.886
2020-01-27 | 12:18 | 49.889
2020-01-27 | 12:18 | 49.892
2020-01-27 | 12:18 | 49.894
2020-01-27 | 12:18 | 49.898
2020-01-27 | 12:18 | 49.899
2020-01-27 | 12:18 | 49.899
2020-01-27 | 12:18 | 49.897
2020-01-27 | 12:18 | 49.894
2020-01-27 | 12:18 | 49.891
2020-01-27 | 12:18 | 49.889
2020-01-27 | 12:18 | 49.887
2020-01-27 | 12:18 | 49.884
2020-01-27 | 12:18 | 49.884
2020-01-27 | 12:18 | 49.885
2020-01-27 | 12:18 | 49.887
2020-01-27 | 12:18 | 49.89
2020-01-27 | 12:18 | 49.894
2020-01-27 | 12:18 | 49.897
2020-01-27 | 12:18 | 49.899
2020-01-27 | 12:18 | 49.902
2020-01-27 | 12:18 | 49.907
2020-01-27 | 12:18 | 49.912
2020-01-27 | 12:18 | 49.917
2020-01-27 | 12:18 | 49.922
2020-01-27 | 12:18 | 49.928
2020-01-27 | 12:18 | 49.934
2020-01-27 | 12:18 | 49.938
2020-01-27 | 12:18 | 49.942
2020-01-27 | 12:18 | 49.944
2020-01-27 | 12:18 | 49.946
2020-01-27 | 12:18 | 49.948
2020-01-27 | 12:18 | 49.95
2020-01-27 | 12:18 | 49.949
2020-01-27 | 12:18 | 49.949
2020-01-27 | 12:18 | 49.948
2020-01-27 | 12:18 | 49.947
2020-01-27 | 12:18 | 49.947
2020-01-27 | 12:18 | 49.947
2020-01-27 | 12:18 | 49.947
2020-01-27 | 12:18 | 49.947
2020-01-27 | 12:18 | 49.946
2020-01-27 | 12:18 | 49.947
2020-01-27 | 12:18 | 49.948
2020-01-27 | 12:18 | 49.95
2020-01-27 | 12:18 | 49.951
2020-01-27 | 12:18 | 49.951
2020-01-27 | 12:18 | 49.949
2020-01-27 | 12:19 | 49.949
2020-01-27 | 12:19 | 49.949
2020-01-27 | 12:19 | 49.947
2020-01-27 | 12:19 | 49.945
2020-01-27 | 12:19 | 49.945
2020-01-27 | 12:19 | 49.943
2020-01-27 | 12:19 | 49.941
2020-01-27 | 12:19 | 49.94
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.94
2020-01-27 | 12:19 | 49.938
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.942
2020-01-27 | 12:19 | 49.943
2020-01-27 | 12:19 | 49.944
2020-01-27 | 12:19 | 49.945
2020-01-27 | 12:19 | 49.945
2020-01-27 | 12:19 | 49.945
2020-01-27 | 12:19 | 49.944
2020-01-27 | 12:19 | 49.943
2020-01-27 | 12:19 | 49.943
2020-01-27 | 12:19 | 49.942
2020-01-27 | 12:19 | 49.941
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.937
2020-01-27 | 12:19 | 49.937
2020-01-27 | 12:19 | 49.935
2020-01-27 | 12:19 | 49.934
2020-01-27 | 12:19 | 49.931
2020-01-27 | 12:19 | 49.931
2020-01-27 | 12:19 | 49.929
2020-01-27 | 12:19 | 49.927
2020-01-27 | 12:19 | 49.925
2020-01-27 | 12:19 | 49.925
2020-01-27 | 12:19 | 49.923
2020-01-27 | 12:19 | 49.922
2020-01-27 | 12:19 | 49.923
2020-01-27 | 12:19 | 49.924
2020-01-27 | 12:19 | 49.926
2020-01-27 | 12:19 | 49.93
2020-01-27 | 12:19 | 49.934
2020-01-27 | 12:19 | 49.938
2020-01-27 | 12:19 | 49.941
2020-01-27 | 12:19 | 49.942
2020-01-27 | 12:19 | 49.942
2020-01-27 | 12:19 | 49.942
2020-01-27 | 12:19 | 49.939
2020-01-27 | 12:19 | 49.937
2020-01-27 | 12:19 | 49.937
2020-01-27 | 12:19 | 49.937
2020-01-27 | 12:19 | 49.937
2020-01-27 | 12:19 | 49.94
2020-01-27 | 12:19 | 49.941
2020-01-27 | 12:19 | 49.944
2020-01-27 | 12:19 | 49.946
2020-01-27 | 12:19 | 49.95
2020-01-27 | 12:20 | 49.954
2020-01-27 | 12:20 | 49.958
2020-01-27 | 12:20 | 49.963
2020-01-27 | 12:20 | 49.968
2020-01-27 | 12:20 | 49.968
2020-01-27 | 12:20 | 49.97
2020-01-27 | 12:20 | 49.972
2020-01-27 | 12:20 | 49.976
2020-01-27 | 12:20 | 49.981
2020-01-27 | 12:20 | 49.985
2020-01-27 | 12:20 | 49.99
2020-01-27 | 12:20 | 49.992
2020-01-27 | 12:20 | 49.997
2020-01-27 | 12:20 | 50.001
2020-01-27 | 12:20 | 50.004
2020-01-27 | 12:20 | 50.007
2020-01-27 | 12:20 | 50.008
2020-01-27 | 12:20 | 50.007
2020-01-27 | 12:20 | 50.007
2020-01-27 | 12:20 | 50.007
2020-01-27 | 12:20 | 50.005
2020-01-27 | 12:20 | 50.004
2020-01-27 | 12:20 | 50.003
2020-01-27 | 12:20 | 50.004
2020-01-27 | 12:20 | 50.004
2020-01-27 | 12:20 | 50.004
2020-01-27 | 12:20 | 50.003
2020-01-27 | 12:20 | 50.002
2020-01-27 | 12:20 | 50.001
2020-01-27 | 12:20 | 50.002
2020-01-27 | 12:20 | 50.001
2020-01-27 | 12:20 | 50.001
2020-01-27 | 12:20 | 49.996
2020-01-27 | 12:20 | 49.991
2020-01-27 | 12:20 | 49.985
2020-01-27 | 12:20 | 49.98
2020-01-27 | 12:20 | 49.974
2020-01-27 | 12:20 | 49.975
2020-01-27 | 12:20 | 49.974
2020-01-27 | 12:20 | 49.973
2020-01-27 | 12:20 | 49.973
2020-01-27 | 12:20 | 49.977
2020-01-27 | 12:20 | 49.98
2020-01-27 | 12:20 | 49.983
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.984
2020-01-27 | 12:20 | 49.986
2020-01-27 | 12:20 | 49.988
2020-01-27 | 12:20 | 49.99
2020-01-27 | 12:20 | 49.991
2020-01-27 | 12:20 | 49.994
2020-01-27 | 12:20 | 49.994
2020-01-27 | 12:20 | 49.995
2020-01-27 | 12:20 | 49.995
2020-01-27 | 12:20 | 49.995
2020-01-27 | 12:20 | 49.991
2020-01-27 | 12:21 | 49.988
2020-01-27 | 12:21 | 49.985
2020-01-27 | 12:21 | 49.985
2020-01-27 | 12:21 | 49.985
2020-01-27 | 12:21 | 49.985
2020-01-27 | 12:21 | 49.985
2020-01-27 | 12:21 | 49.985
2020-01-27 | 12:21 | 49.984
2020-01-27 | 12:21 | 49.982
2020-01-27 | 12:21 | 49.981
2020-01-27 | 12:21 | 49.98
2020-01-27 | 12:21 | 49.977
2020-01-27 | 12:21 | 49.977
2020-01-27 | 12:21 | 49.977
2020-01-27 | 12:21 | 49.977
2020-01-27 | 12:21 | 49.977
2020-01-27 | 12:21 | 49.977
2020-01-27 | 12:21 | 49.976
2020-01-27 | 12:21 | 49.975
2020-01-27 | 12:21 | 49.973
2020-01-27 | 12:21 | 49.97
2020-01-27 | 12:21 | 49.967
2020-01-27 | 12:21 | 49.967
2020-01-27 | 12:21 | 49.966
2020-01-27 | 12:21 | 49.964
2020-01-27 | 12:21 | 49.964
2020-01-27 | 12:21 | 49.963
2020-01-27 | 12:21 | 49.96
2020-01-27 | 12:21 | 49.958

## Event 20200128-1
In UTC
Date | Time | Freq
2020-01-28 | 7:36 | 50.013
2020-01-28 | 7:36 | 50.014
2020-01-28 | 7:36 | 50.014
2020-01-28 | 7:36 | 50.016
2020-01-28 | 7:36 | 50.018
2020-01-28 | 7:36 | 50.018
2020-01-28 | 7:36 | 50.018
2020-01-28 | 7:36 | 50.019
2020-01-28 | 7:36 | 50.02
2020-01-28 | 7:36 | 50.021
2020-01-28 | 7:36 | 50.021
2020-01-28 | 7:36 | 50.023
2020-01-28 | 7:36 | 50.023
2020-01-28 | 7:36 | 50.023
2020-01-28 | 7:36 | 50.023
2020-01-28 | 7:36 | 50.024
2020-01-28 | 7:36 | 50.025
2020-01-28 | 7:36 | 50.027
2020-01-28 | 7:36 | 50.029
2020-01-28 | 7:36 | 50.033
2020-01-28 | 7:36 | 50.035
2020-01-28 | 7:36 | 50.038
2020-01-28 | 7:36 | 50.04
2020-01-28 | 7:36 | 50.041
2020-01-28 | 7:36 | 50.042
2020-01-28 | 7:36 | 50.042
2020-01-28 | 7:36 | 50.043
2020-01-28 | 7:36 | 50.044
2020-01-28 | 7:36 | 50.044
2020-01-28 | 7:36 | 50.044
2020-01-28 | 7:36 | 50.046
2020-01-28 | 7:37 | 50.047
2020-01-28 | 7:37 | 50.049
2020-01-28 | 7:37 | 50.05
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.053
2020-01-28 | 7:37 | 50.052
2020-01-28 | 7:37 | 50.053
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.05
2020-01-28 | 7:37 | 50.047
2020-01-28 | 7:37 | 50.048
2020-01-28 | 7:37 | 50.047
2020-01-28 | 7:37 | 50.05
2020-01-28 | 7:37 | 50.052
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.05
2020-01-28 | 7:37 | 50.049
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.05
2020-01-28 | 7:37 | 50.052
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.053
2020-01-28 | 7:37 | 50.054
2020-01-28 | 7:37 | 50.057
2020-01-28 | 7:37 | 50.06
2020-01-28 | 7:37 | 50.064
2020-01-28 | 7:37 | 50.068
2020-01-28 | 7:37 | 50.072
2020-01-28 | 7:37 | 50.075
2020-01-28 | 7:37 | 50.076
2020-01-28 | 7:37 | 50.076
2020-01-28 | 7:37 | 50.076
2020-01-28 | 7:37 | 50.076
2020-01-28 | 7:37 | 50.076
2020-01-28 | 7:37 | 50.076
2020-01-28 | 7:37 | 50.073
2020-01-28 | 7:37 | 50.071
2020-01-28 | 7:37 | 50.068
2020-01-28 | 7:37 | 50.067
2020-01-28 | 7:37 | 50.064
2020-01-28 | 7:37 | 50.062
2020-01-28 | 7:37 | 50.057
2020-01-28 | 7:37 | 50.054
2020-01-28 | 7:37 | 50.054
2020-01-28 | 7:37 | 50.053
2020-01-28 | 7:37 | 50.052
2020-01-28 | 7:37 | 50.052
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.049
2020-01-28 | 7:37 | 50.048
2020-01-28 | 7:37 | 50.048
2020-01-28 | 7:37 | 50.05
2020-01-28 | 7:37 | 50.051
2020-01-28 | 7:37 | 50.029
2020-01-28 | 7:37 | 50.001
2020-01-28 | 7:37 | 49.976
2020-01-28 | 7:37 | 49.955
2020-01-28 | 7:38 | 49.938
2020-01-28 | 7:38 | 49.924
2020-01-28 | 7:38 | 49.914
2020-01-28 | 7:38 | 49.904
2020-01-28 | 7:38 | 49.899
2020-01-28 | 7:38 | 49.892
2020-01-28 | 7:38 | 49.889
2020-01-28 | 7:38 | 49.886
2020-01-28 | 7:38 | 49.887
2020-01-28 | 7:38 | 49.887
2020-01-28 | 7:38 | 49.889
2020-01-28 | 7:38 | 49.892
2020-01-28 | 7:38 | 49.894
2020-01-28 | 7:38 | 49.896
2020-01-28 | 7:38 | 49.897
2020-01-28 | 7:38 | 49.898
2020-01-28 | 7:38 | 49.897
2020-01-28 | 7:38 | 49.899
2020-01-28 | 7:38 | 49.899
2020-01-28 | 7:38 | 49.902
2020-01-28 | 7:38 | 49.902
2020-01-28 | 7:38 | 49.903
2020-01-28 | 7:38 | 49.903
2020-01-28 | 7:38 | 49.905
2020-01-28 | 7:38 | 49.905
2020-01-28 | 7:38 | 49.906
2020-01-28 | 7:38 | 49.907
2020-01-28 | 7:38 | 49.909
2020-01-28 | 7:38 | 49.91
2020-01-28 | 7:38 | 49.909
2020-01-28 | 7:38 | 49.909
2020-01-28 | 7:38 | 49.909
2020-01-28 | 7:38 | 49.908
2020-01-28 | 7:38 | 49.907
2020-01-28 | 7:38 | 49.905
2020-01-28 | 7:38 | 49.904
2020-01-28 | 7:38 | 49.903
2020-01-28 | 7:38 | 49.905
2020-01-28 | 7:38 | 49.907
2020-01-28 | 7:38 | 49.909
2020-01-28 | 7:38 | 49.909
2020-01-28 | 7:38 | 49.91
2020-01-28 | 7:38 | 49.91
2020-01-28 | 7:38 | 49.908
2020-01-28 | 7:38 | 49.908
2020-01-28 | 7:38 | 49.907
2020-01-28 | 7:38 | 49.905
2020-01-28 | 7:38 | 49.902
2020-01-28 | 7:38 | 49.898
2020-01-28 | 7:38 | 49.894
2020-01-28 | 7:38 | 49.891
2020-01-28 | 7:38 | 49.89
2020-01-28 | 7:38 | 49.888
2020-01-28 | 7:38 | 49.887
2020-01-28 | 7:38 | 49.886
2020-01-28 | 7:38 | 49.883
2020-01-28 | 7:38 | 49.881
2020-01-28 | 7:38 | 49.878
2020-01-28 | 7:38 | 49.877
2020-01-28 | 7:38 | 49.876
2020-01-28 | 7:38 | 49.874
2020-01-28 | 7:39 | 49.875
2020-01-28 | 7:39 | 49.879
2020-01-28 | 7:39 | 49.881
2020-01-28 | 7:39 | 49.882
2020-01-28 | 7:39 | 49.883
2020-01-28 | 7:39 | 49.883
2020-01-28 | 7:39 | 49.884
2020-01-28 | 7:39 | 49.884
2020-01-28 | 7:39 | 49.883
2020-01-28 | 7:39 | 49.882
2020-01-28 | 7:39 | 49.88
2020-01-28 | 7:39 | 49.88
2020-01-28 | 7:39 | 49.879
2020-01-28 | 7:39 | 49.879
2020-01-28 | 7:39 | 49.878
2020-01-28 | 7:39 | 49.879
2020-01-28 | 7:39 | 49.879
2020-01-28 | 7:39 | 49.881
2020-01-28 | 7:39 | 49.88
2020-01-28 | 7:39 | 49.881
2020-01-28 | 7:39 | 49.881
2020-01-28 | 7:39 | 49.883
2020-01-28 | 7:39 | 49.882
2020-01-28 | 7:39 | 49.882
2020-01-28 | 7:39 | 49.88
2020-01-28 | 7:39 | 49.878
2020-01-28 | 7:39 | 49.879
2020-01-28 | 7:39 | 49.881
2020-01-28 | 7:39 | 49.883
2020-01-28 | 7:39 | 49.885
2020-01-28 | 7:39 | 49.888
2020-01-28 | 7:39 | 49.892
2020-01-28 | 7:39 | 49.898
2020-01-28 | 7:39 | 49.9
2020-01-28 | 7:39 | 49.906
2020-01-28 | 7:39 | 49.911
2020-01-28 | 7:39 | 49.912
2020-01-28 | 7:39 | 49.913
2020-01-28 | 7:39 | 49.914
2020-01-28 | 7:39 | 49.915
2020-01-28 | 7:39 | 49.917
2020-01-28 | 7:39 | 49.918
2020-01-28 | 7:39 | 49.918
2020-01-28 | 7:39 | 49.918
2020-01-28 | 7:39 | 49.916
2020-01-28 | 7:39 | 49.916
2020-01-28 | 7:39 | 49.913
2020-01-28 | 7:39 | 49.914
2020-01-28 | 7:39 | 49.912
2020-01-28 | 7:39 | 49.912
2020-01-28 | 7:39 | 49.911
2020-01-28 | 7:39 | 49.912
2020-01-28 | 7:39 | 49.911
2020-01-28 | 7:39 | 49.91
2020-01-28 | 7:39 | 49.907
2020-01-28 | 7:39 | 49.905
2020-01-28 | 7:39 | 49.902
2020-01-28 | 7:39 | 49.898
2020-01-28 | 7:39 | 49.894
2020-01-28 | 7:39 | 49.893
2020-01-28 | 7:40 | 49.894
2020-01-28 | 7:40 | 49.895
2020-01-28 | 7:40 | 49.897
2020-01-28 | 7:40 | 49.898
2020-01-28 | 7:40 | 49.899
2020-01-28 | 7:40 | 49.901
2020-01-28 | 7:40 | 49.904
2020-01-28 | 7:40 | 49.905
2020-01-28 | 7:40 | 49.906
2020-01-28 | 7:40 | 49.906
2020-01-28 | 7:40 | 49.906
2020-01-28 | 7:40 | 49.905
2020-01-28 | 7:40 | 49.905
2020-01-28 | 7:40 | 49.905
2020-01-28 | 7:40 | 49.903
2020-01-28 | 7:40 | 49.9
2020-01-28 | 7:40 | 49.896
2020-01-28 | 7:40 | 49.893
2020-01-28 | 7:40 | 49.887
2020-01-28 | 7:40 | 49.881
2020-01-28 | 7:40 | 49.876
2020-01-28 | 7:40 | 49.871
2020-01-28 | 7:40 | 49.867
2020-01-28 | 7:40 | 49.865
2020-01-28 | 7:40 | 49.863
2020-01-28 | 7:40 | 49.861
2020-01-28 | 7:40 | 49.863
2020-01-28 | 7:40 | 49.867
2020-01-28 | 7:40 | 49.869
2020-01-28 | 7:40 | 49.871
2020-01-28 | 7:40 | 49.871
2020-01-28 | 7:40 | 49.873
2020-01-28 | 7:40 | 49.874
2020-01-28 | 7:40 | 49.873
2020-01-28 | 7:40 | 49.874
2020-01-28 | 7:40 | 49.875
2020-01-28 | 7:40 | 49.875
2020-01-28 | 7:40 | 49.876
2020-01-28 | 7:40 | 49.877
2020-01-28 | 7:40 | 49.877
2020-01-28 | 7:40 | 49.876
2020-01-28 | 7:40 | 49.874
2020-01-28 | 7:40 | 49.873
2020-01-28 | 7:40 | 49.872
2020-01-28 | 7:40 | 49.871
2020-01-28 | 7:40 | 49.869
2020-01-28 | 7:40 | 49.868
2020-01-28 | 7:40 | 49.867
2020-01-28 | 7:40 | 49.867
2020-01-28 | 7:40 | 49.872
2020-01-28 | 7:40 | 49.875
2020-01-28 | 7:40 | 49.878
2020-01-28 | 7:40 | 49.879
2020-01-28 | 7:40 | 49.88
2020-01-28 | 7:40 | 49.878
2020-01-28 | 7:40 | 49.877
2020-01-28 | 7:40 | 49.875
2020-01-28 | 7:40 | 49.872
2020-01-28 | 7:40 | 49.869
2020-01-28 | 7:40 | 49.865
2020-01-28 | 7:41 | 49.862
2020-01-28 | 7:41 | 49.859
2020-01-28 | 7:41 | 49.86
2020-01-28 | 7:41 | 49.859
2020-01-28 | 7:41 | 49.859
2020-01-28 | 7:41 | 49.858
2020-01-28 | 7:41 | 49.858
2020-01-28 | 7:41 | 49.857
2020-01-28 | 7:41 | 49.856
2020-01-28 | 7:41 | 49.855
2020-01-28 | 7:41 | 49.854
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.85
2020-01-28 | 7:41 | 49.848
2020-01-28 | 7:41 | 49.848
2020-01-28 | 7:41 | 49.849
2020-01-28 | 7:41 | 49.85
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.85
2020-01-28 | 7:41 | 49.85
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.85
2020-01-28 | 7:41 | 49.85
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.855
2020-01-28 | 7:41 | 49.855
2020-01-28 | 7:41 | 49.857
2020-01-28 | 7:41 | 49.855
2020-01-28 | 7:41 | 49.856
2020-01-28 | 7:41 | 49.854
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.852
2020-01-28 | 7:41 | 49.851
2020-01-28 | 7:41 | 49.853
2020-01-28 | 7:41 | 49.856
2020-01-28 | 7:41 | 49.86
2020-01-28 | 7:41 | 49.862
2020-01-28 | 7:41 | 49.867
2020-01-28 | 7:41 | 49.87
2020-01-28 | 7:41 | 49.875
2020-01-28 | 7:41 | 49.878
2020-01-28 | 7:41 | 49.881
2020-01-28 | 7:41 | 49.882
2020-01-28 | 7:41 | 49.883
2020-01-28 | 7:42 | 49.887
2020-01-28 | 7:42 | 49.892
2020-01-28 | 7:42 | 49.898
2020-01-28 | 7:42 | 49.902
2020-01-28 | 7:42 | 49.906
2020-01-28 | 7:42 | 49.911
2020-01-28 | 7:42 | 49.912
2020-01-28 | 7:42 | 49.911
2020-01-28 | 7:42 | 49.91
2020-01-28 | 7:42 | 49.909
2020-01-28 | 7:42 | 49.906
2020-01-28 | 7:42 | 49.904
2020-01-28 | 7:42 | 49.902
2020-01-28 | 7:42 | 49.898
2020-01-28 | 7:42 | 49.897
2020-01-28 | 7:42 | 49.895
2020-01-28 | 7:42 | 49.892
2020-01-28 | 7:42 | 49.888
2020-01-28 | 7:42 | 49.887
2020-01-28 | 7:42 | 49.885
2020-01-28 | 7:42 | 49.885
2020-01-28 | 7:42 | 49.886
2020-01-28 | 7:42 | 49.885
2020-01-28 | 7:42 | 49.886
2020-01-28 | 7:42 | 49.886
2020-01-28 | 7:42 | 49.886
2020-01-28 | 7:42 | 49.886
2020-01-28 | 7:42 | 49.887
2020-01-28 | 7:42 | 49.887
2020-01-28 | 7:42 | 49.885
2020-01-28 | 7:42 | 49.887
2020-01-28 | 7:42 | 49.889
2020-01-28 | 7:42 | 49.888
2020-01-28 | 7:42 | 49.888
2020-01-28 | 7:42 | 49.889
2020-01-28 | 7:42 | 49.888
2020-01-28 | 7:42 | 49.89
2020-01-28 | 7:42 | 49.891
2020-01-28 | 7:42 | 49.891
2020-01-28 | 7:42 | 49.893
2020-01-28 | 7:42 | 49.895
2020-01-28 | 7:42 | 49.899
2020-01-28 | 7:42 | 49.904
2020-01-28 | 7:42 | 49.906
2020-01-28 | 7:42 | 49.911
2020-01-28 | 7:42 | 49.912
2020-01-28 | 7:42 | 49.916
2020-01-28 | 7:42 | 49.919
2020-01-28 | 7:42 | 49.922
2020-01-28 | 7:42 | 49.92
2020-01-28 | 7:42 | 49.918
2020-01-28 | 7:42 | 49.918
2020-01-28 | 7:42 | 49.919
2020-01-28 | 7:42 | 49.923
2020-01-28 | 7:42 | 49.926
2020-01-28 | 7:42 | 49.929
2020-01-28 | 7:42 | 49.932
2020-01-28 | 7:42 | 49.935
2020-01-28 | 7:42 | 49.937
2020-01-28 | 7:42 | 49.94
2020-01-28 | 7:43 | 49.945
2020-01-28 | 7:43 | 49.95
2020-01-28 | 7:43 | 49.955
2020-01-28 | 7:43 | 49.958
2020-01-28 | 7:43 | 49.959
2020-01-28 | 7:43 | 49.96
2020-01-28 | 7:43 | 49.961
2020-01-28 | 7:43 | 49.961
2020-01-28 | 7:43 | 49.963
2020-01-28 | 7:43 | 49.962
2020-01-28 | 7:43 | 49.962
2020-01-28 | 7:43 | 49.963
2020-01-28 | 7:43 | 49.965
2020-01-28 | 7:43 | 49.969
2020-01-28 | 7:43 | 49.973
2020-01-28 | 7:43 | 49.975
2020-01-28 | 7:43 | 49.976
2020-01-28 | 7:43 | 49.978
2020-01-28 | 7:43 | 49.979
2020-01-28 | 7:43 | 49.98
2020-01-28 | 7:43 | 49.979
2020-01-28 | 7:43 | 49.978
2020-01-28 | 7:43 | 49.978
2020-01-28 | 7:43 | 49.977
2020-01-28 | 7:43 | 49.976
2020-01-28 | 7:43 | 49.976
2020-01-28 | 7:43 | 49.976
2020-01-28 | 7:43 | 49.976
2020-01-28 | 7:43 | 49.973
2020-01-28 | 7:43 | 49.969
2020-01-28 | 7:43 | 49.968
2020-01-28 | 7:43 | 49.966
2020-01-28 | 7:43 | 49.965
2020-01-28 | 7:43 | 49.963
2020-01-28 | 7:43 | 49.962
2020-01-28 | 7:43 | 49.961
2020-01-28 | 7:43 | 49.962
2020-01-28 | 7:43 | 49.963
2020-01-28 | 7:43 | 49.964
2020-01-28 | 7:43 | 49.966
2020-01-28 | 7:43 | 49.97
2020-01-28 | 7:43 | 49.973
2020-01-28 | 7:43 | 49.975
2020-01-28 | 7:43 | 49.977
2020-01-28 | 7:43 | 49.982
2020-01-28 | 7:43 | 49.986
2020-01-28 | 7:43 | 49.988
2020-01-28 | 7:43 | 49.991
2020-01-28 | 7:43 | 49.995
2020-01-28 | 7:43 | 50
2020-01-28 | 7:43 | 50.006
2020-01-28 | 7:43 | 50.01
2020-01-28 | 7:43 | 50.014
2020-01-28 | 7:43 | 50.014
2020-01-28 | 7:43 | 50.015
2020-01-28 | 7:43 | 50.017
2020-01-28 | 7:43 | 50.018
2020-01-28 | 7:43 | 50.016
2020-01-28 | 7:43 | 50.014
2020-01-28 | 7:43 | 50.014
2020-01-28 | 7:44 | 50.014
2020-01-28 | 7:44 | 50.014
2020-01-28 | 7:44 | 50.015
2020-01-28 | 7:44 | 50.015
2020-01-28 | 7:44 | 50.016
2020-01-28 | 7:44 | 50.016
2020-01-28 | 7:44 | 50.017
2020-01-28 | 7:44 | 50.014
2020-01-28 | 7:44 | 50.013
2020-01-28 | 7:44 | 50.012
2020-01-28 | 7:44 | 50.011
2020-01-28 | 7:44 | 50.009
2020-01-28 | 7:44 | 50.009
2020-01-28 | 7:44 | 50.01
2020-01-28 | 7:44 | 50.012
2020-01-28 | 7:44 | 50.013
2020-01-28 | 7:44 | 50.014
2020-01-28 | 7:44 | 50.016
2020-01-28 | 7:44 | 50.016
2020-01-28 | 7:44 | 50.015
2020-01-28 | 7:44 | 50.013
2020-01-28 | 7:44 | 50.012
2020-01-28 | 7:44 | 50.014
2020-01-28 | 7:44 | 50.017
2020-01-28 | 7:44 | 50.019
2020-01-28 | 7:44 | 50.02
2020-01-28 | 7:44 | 50.024
2020-01-28 | 7:44 | 50.027
2020-01-28 | 7:44 | 50.029