## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20200202-1 | Trip of WBURB-3 |  | 2020-02-02 | 2:59 | N/A | Refer to tab 'Event 20200202-1' | 50.04 | 49.891 | -0.008 | 350 | -350 | N/A | N/A | N/A | N/A
Event 20200209-1 | Pelham – Sundon 400kV circuit trip caused embedded generation loss | Coincident with off-shore wind decreased rapidly | 2020-02-09 | 8:58 | N/A | Refer to tab 'Event 20200209-1' | 50.06 | 49.569 | N/A | 100 | -100 | N/A | Pelham-Sundon 400kV circuit | N/A | N/A
Event 20200209-2 | Wind decreased rapidly and coincident with sudden demand pick up | The wind dropped approximately 1.2GW and the demand picked up approximately 1GW | 2020-02-09 | 9:39 | N/A | Refer to tab 'Event 20200209-2' | 49.95 | 49.592 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Event 20200213-1 | Trip of Moyle HVDC | Output changed gradually from +81MW at 14:23 to -454MW at 16:55 | 2020-02-13 | 15:24 | N/A | Refer to tab 'Event 20200213-1' | 50.05 | 49.76 | N/A | 535 | -535 | N/A | N/A | N/A | N/A
Event 20200217-1 | Trip of Coalburn SGT3 | Embbedded Generation loss | 2020-02-17 | 0:49 | N/A | Refer to tab 'Event 20200217-1' | 50.098 | 49.879 | N/A | 260 | -260 | N/A | Coalburn 400/132kv SGT3 | N/A | N/A
Event 20200219-1 | Trip Axminster SGT1 | Loss of Demand | 2020-02-19 | 4:42 | N/A | Refer to tab 'Event 20200219-1' | 49.974 | 50.023 | N/A | N/A | N/A | 102 | Axminster SGT1 | N/A | N/A
Event 20200224-1 | Trip of NEMO |  | 2020-02-24 | 13:32 | N/A | Refer to tab 'Event 20200224-1' | 49.99 | 49.584 | N/A | 1000 | -1000 | N/A | N/A | N/A | N/A
Event 20200224-2 | Trip of HUMB-1 | GT 15 tripped | 2020-02-24 | 18:49 | N/A | Refer to tab 'Event 20200224-2' | 49.968 | 49.83 | -0.033 | 346 | -346 | N/A | N/A | N/A | 261.9535
Event 20200224-3 | Trip of FIDF-4 | Output reduced gradually from 250MW at 19:42 to 0MW at 19:51 | 2020-02-24 | 19:42 | N/A | Refer to tab 'Event 20200224-3' | 50.098 | 49.867 | N/A | 250 | -250 | N/A | N/A | N/A | N/A
Event 20200227-1 | Trip of HINB-7 |  | 2020-02-27 | 9:02 | N/A | Refer to tab 'Event 20200227-1' | 50.03 | 49.875 | -0.024 | 275 | -275 | N/A | N/A | N/A | 286.6302

## Event 20200202-1
In UTC
Date | Time | Freq
2020-02-02 | 2:58 | 50.018
2020-02-02 | 2:58 | 50.016
2020-02-02 | 2:58 | 50.015
2020-02-02 | 2:58 | 50.016
2020-02-02 | 2:58 | 50.018
2020-02-02 | 2:58 | 50.021
2020-02-02 | 2:58 | 50.024
2020-02-02 | 2:58 | 50.025
2020-02-02 | 2:58 | 50.026
2020-02-02 | 2:58 | 50.027
2020-02-02 | 2:58 | 50.029
2020-02-02 | 2:58 | 50.029
2020-02-02 | 2:58 | 50.028
2020-02-02 | 2:58 | 50.027
2020-02-02 | 2:58 | 50.026
2020-02-02 | 2:58 | 50.025
2020-02-02 | 2:58 | 50.026
2020-02-02 | 2:58 | 50.027
2020-02-02 | 2:58 | 50.029
2020-02-02 | 2:58 | 50.031
2020-02-02 | 2:58 | 50.033
2020-02-02 | 2:58 | 50.037
2020-02-02 | 2:58 | 50.038
2020-02-02 | 2:58 | 50.041
2020-02-02 | 2:58 | 50.04
2020-02-02 | 2:58 | 50.039
2020-02-02 | 2:58 | 50.039
2020-02-02 | 2:58 | 50.038
2020-02-02 | 2:58 | 50.038
2020-02-02 | 2:58 | 50.037
2020-02-02 | 2:58 | 50.038
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.037
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.036
2020-02-02 | 2:59 | 50.037
2020-02-02 | 2:59 | 50.036
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.039
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.038
2020-02-02 | 2:59 | 50.037
2020-02-02 | 2:59 | 50.037
2020-02-02 | 2:59 | 50.035
2020-02-02 | 2:59 | 50.036
2020-02-02 | 2:59 | 50.036
2020-02-02 | 2:59 | 50.036
2020-02-02 | 2:59 | 50.035
2020-02-02 | 2:59 | 50.036
2020-02-02 | 2:59 | 50.035
2020-02-02 | 2:59 | 50.033
2020-02-02 | 2:59 | 50.033
2020-02-02 | 2:59 | 50.031
2020-02-02 | 2:59 | 50.032
2020-02-02 | 2:59 | 50.032
2020-02-02 | 2:59 | 50.031
2020-02-02 | 2:59 | 50.031
2020-02-02 | 2:59 | 50.03
2020-02-02 | 2:59 | 50.03
2020-02-02 | 2:59 | 50.029
2020-02-02 | 2:59 | 50.028
2020-02-02 | 2:59 | 50.028
2020-02-02 | 2:59 | 50.028
2020-02-02 | 2:59 | 50.03
2020-02-02 | 2:59 | 50.028
2020-02-02 | 2:59 | 50.029
2020-02-02 | 2:59 | 50.029
2020-02-02 | 2:59 | 50.028
2020-02-02 | 2:59 | 50.027
2020-02-02 | 2:59 | 50.026
2020-02-02 | 2:59 | 50.026
2020-02-02 | 2:59 | 50.023
2020-02-02 | 2:59 | 50.023
2020-02-02 | 2:59 | 50.023
2020-02-02 | 2:59 | 50.022
2020-02-02 | 2:59 | 50.023
2020-02-02 | 2:59 | 50.021
2020-02-02 | 2:59 | 50.022
2020-02-02 | 2:59 | 50.02
2020-02-02 | 2:59 | 50.019
2020-02-02 | 2:59 | 50.018
2020-02-02 | 2:59 | 50.017
2020-02-02 | 2:59 | 50.017
2020-02-02 | 2:59 | 50.015
2020-02-02 | 2:59 | 50.015
2020-02-02 | 2:59 | 50.013
2020-02-02 | 2:59 | 50.012
2020-02-02 | 2:59 | 50.01
2020-02-02 | 3:00 | 50.008
2020-02-02 | 3:00 | 50.006
2020-02-02 | 3:00 | 50.002
2020-02-02 | 3:00 | 50
2020-02-02 | 3:00 | 49.995
2020-02-02 | 3:00 | 49.991
2020-02-02 | 3:00 | 49.985
2020-02-02 | 3:00 | 49.979
2020-02-02 | 3:00 | 49.977
2020-02-02 | 3:00 | 49.975
2020-02-02 | 3:00 | 49.976
2020-02-02 | 3:00 | 49.976
2020-02-02 | 3:00 | 49.976
2020-02-02 | 3:00 | 49.975
2020-02-02 | 3:00 | 49.975
2020-02-02 | 3:00 | 49.976
2020-02-02 | 3:00 | 49.976
2020-02-02 | 3:00 | 49.976
2020-02-02 | 3:00 | 49.975
2020-02-02 | 3:00 | 49.975
2020-02-02 | 3:00 | 49.973
2020-02-02 | 3:00 | 49.97
2020-02-02 | 3:00 | 49.969
2020-02-02 | 3:00 | 49.966
2020-02-02 | 3:00 | 49.966
2020-02-02 | 3:00 | 49.964
2020-02-02 | 3:00 | 49.964
2020-02-02 | 3:00 | 49.963
2020-02-02 | 3:00 | 49.961
2020-02-02 | 3:00 | 49.96
2020-02-02 | 3:00 | 49.956
2020-02-02 | 3:00 | 49.952
2020-02-02 | 3:00 | 49.944
2020-02-02 | 3:00 | 49.939
2020-02-02 | 3:00 | 49.936
2020-02-02 | 3:00 | 49.934
2020-02-02 | 3:00 | 49.934
2020-02-02 | 3:00 | 49.932
2020-02-02 | 3:00 | 49.934
2020-02-02 | 3:00 | 49.932
2020-02-02 | 3:00 | 49.932
2020-02-02 | 3:00 | 49.93
2020-02-02 | 3:00 | 49.929
2020-02-02 | 3:00 | 49.928
2020-02-02 | 3:00 | 49.926
2020-02-02 | 3:00 | 49.927
2020-02-02 | 3:00 | 49.924
2020-02-02 | 3:00 | 49.921
2020-02-02 | 3:00 | 49.918
2020-02-02 | 3:00 | 49.915
2020-02-02 | 3:00 | 49.914
2020-02-02 | 3:00 | 49.916
2020-02-02 | 3:00 | 49.919
2020-02-02 | 3:00 | 49.92
2020-02-02 | 3:00 | 49.922
2020-02-02 | 3:00 | 49.92
2020-02-02 | 3:00 | 49.919
2020-02-02 | 3:00 | 49.918
2020-02-02 | 3:00 | 49.916
2020-02-02 | 3:00 | 49.914
2020-02-02 | 3:00 | 49.909
2020-02-02 | 3:01 | 49.904
2020-02-02 | 3:01 | 49.901
2020-02-02 | 3:01 | 49.901
2020-02-02 | 3:01 | 49.902
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.906
2020-02-02 | 3:01 | 49.906
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.904
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.904
2020-02-02 | 3:01 | 49.904
2020-02-02 | 3:01 | 49.903
2020-02-02 | 3:01 | 49.901
2020-02-02 | 3:01 | 49.897
2020-02-02 | 3:01 | 49.895
2020-02-02 | 3:01 | 49.893
2020-02-02 | 3:01 | 49.893
2020-02-02 | 3:01 | 49.894
2020-02-02 | 3:01 | 49.896
2020-02-02 | 3:01 | 49.9
2020-02-02 | 3:01 | 49.902
2020-02-02 | 3:01 | 49.903
2020-02-02 | 3:01 | 49.903
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.902
2020-02-02 | 3:01 | 49.9
2020-02-02 | 3:01 | 49.897
2020-02-02 | 3:01 | 49.895
2020-02-02 | 3:01 | 49.892
2020-02-02 | 3:01 | 49.892
2020-02-02 | 3:01 | 49.892
2020-02-02 | 3:01 | 49.891
2020-02-02 | 3:01 | 49.892
2020-02-02 | 3:01 | 49.895
2020-02-02 | 3:01 | 49.898
2020-02-02 | 3:01 | 49.9
2020-02-02 | 3:01 | 49.901
2020-02-02 | 3:01 | 49.902
2020-02-02 | 3:01 | 49.902
2020-02-02 | 3:01 | 49.902
2020-02-02 | 3:01 | 49.903
2020-02-02 | 3:01 | 49.905
2020-02-02 | 3:01 | 49.906
2020-02-02 | 3:01 | 49.906
2020-02-02 | 3:01 | 49.907
2020-02-02 | 3:01 | 49.907
2020-02-02 | 3:01 | 49.908
2020-02-02 | 3:01 | 49.911
2020-02-02 | 3:01 | 49.911
2020-02-02 | 3:01 | 49.912
2020-02-02 | 3:01 | 49.914
2020-02-02 | 3:01 | 49.913
2020-02-02 | 3:01 | 49.914
2020-02-02 | 3:01 | 49.916
2020-02-02 | 3:01 | 49.916
2020-02-02 | 3:01 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.914
2020-02-02 | 3:02 | 49.913
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.915
2020-02-02 | 3:02 | 49.914
2020-02-02 | 3:02 | 49.914
2020-02-02 | 3:02 | 49.913
2020-02-02 | 3:02 | 49.912
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.912
2020-02-02 | 3:02 | 49.912
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.909
2020-02-02 | 3:02 | 49.906
2020-02-02 | 3:02 | 49.905
2020-02-02 | 3:02 | 49.906
2020-02-02 | 3:02 | 49.907
2020-02-02 | 3:02 | 49.907
2020-02-02 | 3:02 | 49.908
2020-02-02 | 3:02 | 49.908
2020-02-02 | 3:02 | 49.909
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.909
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.909
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.91
2020-02-02 | 3:02 | 49.911
2020-02-02 | 3:02 | 49.912
2020-02-02 | 3:02 | 49.914
2020-02-02 | 3:02 | 49.913
2020-02-02 | 3:02 | 49.914
2020-02-02 | 3:02 | 49.916
2020-02-02 | 3:02 | 49.917
2020-02-02 | 3:02 | 49.917
2020-02-02 | 3:03 | 49.916
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.917
2020-02-02 | 3:03 | 49.919
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.919
2020-02-02 | 3:03 | 49.917
2020-02-02 | 3:03 | 49.917
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.919
2020-02-02 | 3:03 | 49.92
2020-02-02 | 3:03 | 49.919
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.918
2020-02-02 | 3:03 | 49.919
2020-02-02 | 3:03 | 49.922
2020-02-02 | 3:03 | 49.923
2020-02-02 | 3:03 | 49.926
2020-02-02 | 3:03 | 49.926
2020-02-02 | 3:03 | 49.927
2020-02-02 | 3:03 | 49.929
2020-02-02 | 3:03 | 49.929
2020-02-02 | 3:03 | 49.929
2020-02-02 | 3:03 | 49.929
2020-02-02 | 3:03 | 49.929
2020-02-02 | 3:03 | 49.928
2020-02-02 | 3:03 | 49.926
2020-02-02 | 3:03 | 49.924
2020-02-02 | 3:03 | 49.922
2020-02-02 | 3:03 | 49.924
2020-02-02 | 3:03 | 49.926
2020-02-02 | 3:03 | 49.93
2020-02-02 | 3:03 | 49.933
2020-02-02 | 3:03 | 49.936
2020-02-02 | 3:03 | 49.938
2020-02-02 | 3:03 | 49.94
2020-02-02 | 3:03 | 49.941
2020-02-02 | 3:03 | 49.941
2020-02-02 | 3:03 | 49.941
2020-02-02 | 3:03 | 49.939
2020-02-02 | 3:03 | 49.937
2020-02-02 | 3:03 | 49.936
2020-02-02 | 3:03 | 49.935
2020-02-02 | 3:03 | 49.938
2020-02-02 | 3:03 | 49.94
2020-02-02 | 3:03 | 49.943
2020-02-02 | 3:03 | 49.945
2020-02-02 | 3:03 | 49.946
2020-02-02 | 3:03 | 49.946
2020-02-02 | 3:03 | 49.947
2020-02-02 | 3:03 | 49.947
2020-02-02 | 3:03 | 49.945
2020-02-02 | 3:03 | 49.942
2020-02-02 | 3:03 | 49.938
2020-02-02 | 3:03 | 49.935
2020-02-02 | 3:04 | 49.932
2020-02-02 | 3:04 | 49.931
2020-02-02 | 3:04 | 49.93
2020-02-02 | 3:04 | 49.932
2020-02-02 | 3:04 | 49.935
2020-02-02 | 3:04 | 49.939
2020-02-02 | 3:04 | 49.942
2020-02-02 | 3:04 | 49.943
2020-02-02 | 3:04 | 49.943
2020-02-02 | 3:04 | 49.943
2020-02-02 | 3:04 | 49.944
2020-02-02 | 3:04 | 49.945
2020-02-02 | 3:04 | 49.944
2020-02-02 | 3:04 | 49.942
2020-02-02 | 3:04 | 49.941
2020-02-02 | 3:04 | 49.94
2020-02-02 | 3:04 | 49.941
2020-02-02 | 3:04 | 49.941
2020-02-02 | 3:04 | 49.943
2020-02-02 | 3:04 | 49.944
2020-02-02 | 3:04 | 49.945
2020-02-02 | 3:04 | 49.95
2020-02-02 | 3:04 | 49.954
2020-02-02 | 3:04 | 49.958
2020-02-02 | 3:04 | 49.959
2020-02-02 | 3:04 | 49.959
2020-02-02 | 3:04 | 49.959
2020-02-02 | 3:04 | 49.959
2020-02-02 | 3:04 | 49.959
2020-02-02 | 3:04 | 49.962
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.965
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.967
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.965
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.967
2020-02-02 | 3:04 | 49.967
2020-02-02 | 3:04 | 49.967
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.966
2020-02-02 | 3:04 | 49.965
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.964
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:04 | 49.963
2020-02-02 | 3:05 | 49.961
2020-02-02 | 3:05 | 49.96
2020-02-02 | 3:05 | 49.959
2020-02-02 | 3:05 | 49.958
2020-02-02 | 3:05 | 49.958
2020-02-02 | 3:05 | 49.956
2020-02-02 | 3:05 | 49.955
2020-02-02 | 3:05 | 49.952
2020-02-02 | 3:05 | 49.95
2020-02-02 | 3:05 | 49.95
2020-02-02 | 3:05 | 49.947
2020-02-02 | 3:05 | 49.948
2020-02-02 | 3:05 | 49.947
2020-02-02 | 3:05 | 49.947
2020-02-02 | 3:05 | 49.949
2020-02-02 | 3:05 | 49.951
2020-02-02 | 3:05 | 49.951
2020-02-02 | 3:05 | 49.95
2020-02-02 | 3:05 | 49.949
2020-02-02 | 3:05 | 49.947
2020-02-02 | 3:05 | 49.947
2020-02-02 | 3:05 | 49.945
2020-02-02 | 3:05 | 49.944
2020-02-02 | 3:05 | 49.943
2020-02-02 | 3:05 | 49.943
2020-02-02 | 3:05 | 49.943
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.94
2020-02-02 | 3:05 | 49.939
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.936
2020-02-02 | 3:05 | 49.937
2020-02-02 | 3:05 | 49.939
2020-02-02 | 3:05 | 49.939
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.942
2020-02-02 | 3:05 | 49.942
2020-02-02 | 3:05 | 49.942
2020-02-02 | 3:05 | 49.942
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.941
2020-02-02 | 3:05 | 49.939
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.937
2020-02-02 | 3:05 | 49.936
2020-02-02 | 3:05 | 49.936
2020-02-02 | 3:05 | 49.936
2020-02-02 | 3:05 | 49.936
2020-02-02 | 3:05 | 49.936
2020-02-02 | 3:05 | 49.937
2020-02-02 | 3:05 | 49.937
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:05 | 49.938
2020-02-02 | 3:06 | 49.938
2020-02-02 | 3:06 | 49.936
2020-02-02 | 3:06 | 49.938
2020-02-02 | 3:06 | 49.938
2020-02-02 | 3:06 | 49.94
2020-02-02 | 3:06 | 49.94
2020-02-02 | 3:06 | 49.941
2020-02-02 | 3:06 | 49.941
2020-02-02 | 3:06 | 49.942
2020-02-02 | 3:06 | 49.942
2020-02-02 | 3:06 | 49.942
2020-02-02 | 3:06 | 49.94
2020-02-02 | 3:06 | 49.938
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.933
2020-02-02 | 3:06 | 49.931
2020-02-02 | 3:06 | 49.93
2020-02-02 | 3:06 | 49.929
2020-02-02 | 3:06 | 49.931
2020-02-02 | 3:06 | 49.932
2020-02-02 | 3:06 | 49.933
2020-02-02 | 3:06 | 49.933
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.934
2020-02-02 | 3:06 | 49.932
2020-02-02 | 3:06 | 49.93
2020-02-02 | 3:06 | 49.928
2020-02-02 | 3:06 | 49.929
2020-02-02 | 3:06 | 49.931
2020-02-02 | 3:06 | 49.933
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.937
2020-02-02 | 3:06 | 49.938
2020-02-02 | 3:06 | 49.94
2020-02-02 | 3:06 | 49.939
2020-02-02 | 3:06 | 49.94
2020-02-02 | 3:06 | 49.939
2020-02-02 | 3:06 | 49.938
2020-02-02 | 3:06 | 49.937
2020-02-02 | 3:06 | 49.934
2020-02-02 | 3:06 | 49.933
2020-02-02 | 3:06 | 49.932
2020-02-02 | 3:06 | 49.93
2020-02-02 | 3:06 | 49.931
2020-02-02 | 3:06 | 49.932
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.936
2020-02-02 | 3:06 | 49.936
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.935
2020-02-02 | 3:06 | 49.934
2020-02-02 | 3:06 | 49.933
2020-02-02 | 3:06 | 49.931
2020-02-02 | 3:06 | 49.929
2020-02-02 | 3:06 | 49.926
2020-02-02 | 3:06 | 49.925
2020-02-02 | 3:06 | 49.926
2020-02-02 | 3:06 | 49.926
2020-02-02 | 3:07 | 49.926
2020-02-02 | 3:07 | 49.927
2020-02-02 | 3:07 | 49.929
2020-02-02 | 3:07 | 49.931
2020-02-02 | 3:07 | 49.933
2020-02-02 | 3:07 | 49.935
2020-02-02 | 3:07 | 49.937
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.941
2020-02-02 | 3:07 | 49.942
2020-02-02 | 3:07 | 49.944
2020-02-02 | 3:07 | 49.943
2020-02-02 | 3:07 | 49.943
2020-02-02 | 3:07 | 49.942
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.936
2020-02-02 | 3:07 | 49.937
2020-02-02 | 3:07 | 49.937
2020-02-02 | 3:07 | 49.937
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.937
2020-02-02 | 3:07 | 49.938
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.939
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.94
2020-02-02 | 3:07 | 49.941
2020-02-02 | 3:07 | 49.942
2020-02-02 | 3:07 | 49.942
2020-02-02 | 3:07 | 49.944
2020-02-02 | 3:07 | 49.945
2020-02-02 | 3:07 | 49.947
2020-02-02 | 3:07 | 49.947
2020-02-02 | 3:07 | 49.946
2020-02-02 | 3:07 | 49.945
2020-02-02 | 3:07 | 49.944
2020-02-02 | 3:07 | 49.944
2020-02-02 | 3:07 | 49.943
2020-02-02 | 3:08 | 49.943
2020-02-02 | 3:08 | 49.942
2020-02-02 | 3:08 | 49.941
2020-02-02 | 3:08 | 49.941
2020-02-02 | 3:08 | 49.941
2020-02-02 | 3:08 | 49.94
2020-02-02 | 3:08 | 49.941
2020-02-02 | 3:08 | 49.941
2020-02-02 | 3:08 | 49.941
2020-02-02 | 3:08 | 49.94
2020-02-02 | 3:08 | 49.94
2020-02-02 | 3:08 | 49.939
2020-02-02 | 3:08 | 49.939
2020-02-02 | 3:08 | 49.939
2020-02-02 | 3:08 | 49.939
2020-02-02 | 3:08 | 49.938
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.936
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.936
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.936
2020-02-02 | 3:08 | 49.936
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.932
2020-02-02 | 3:08 | 49.933
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.933
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.938
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.938
2020-02-02 | 3:08 | 49.937
2020-02-02 | 3:08 | 49.936
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.933
2020-02-02 | 3:08 | 49.93
2020-02-02 | 3:08 | 49.927
2020-02-02 | 3:08 | 49.926
2020-02-02 | 3:08 | 49.927
2020-02-02 | 3:08 | 49.931
2020-02-02 | 3:08 | 49.933
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.935
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.934
2020-02-02 | 3:08 | 49.932
2020-02-02 | 3:08 | 49.928
2020-02-02 | 3:09 | 49.927
2020-02-02 | 3:09 | 49.927
2020-02-02 | 3:09 | 49.929
2020-02-02 | 3:09 | 49.933
2020-02-02 | 3:09 | 49.936
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.939
2020-02-02 | 3:09 | 49.943
2020-02-02 | 3:09 | 49.943
2020-02-02 | 3:09 | 49.94
2020-02-02 | 3:09 | 49.936
2020-02-02 | 3:09 | 49.934
2020-02-02 | 3:09 | 49.933
2020-02-02 | 3:09 | 49.932
2020-02-02 | 3:09 | 49.931
2020-02-02 | 3:09 | 49.931
2020-02-02 | 3:09 | 49.934
2020-02-02 | 3:09 | 49.937
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.939
2020-02-02 | 3:09 | 49.94
2020-02-02 | 3:09 | 49.94
2020-02-02 | 3:09 | 49.94
2020-02-02 | 3:09 | 49.939
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.936
2020-02-02 | 3:09 | 49.934
2020-02-02 | 3:09 | 49.932
2020-02-02 | 3:09 | 49.932
2020-02-02 | 3:09 | 49.932
2020-02-02 | 3:09 | 49.931
2020-02-02 | 3:09 | 49.932
2020-02-02 | 3:09 | 49.932
2020-02-02 | 3:09 | 49.935
2020-02-02 | 3:09 | 49.936
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.94
2020-02-02 | 3:09 | 49.941
2020-02-02 | 3:09 | 49.942
2020-02-02 | 3:09 | 49.944
2020-02-02 | 3:09 | 49.947
2020-02-02 | 3:09 | 49.947
2020-02-02 | 3:09 | 49.948
2020-02-02 | 3:09 | 49.947
2020-02-02 | 3:09 | 49.947
2020-02-02 | 3:09 | 49.945
2020-02-02 | 3:09 | 49.944
2020-02-02 | 3:09 | 49.94
2020-02-02 | 3:09 | 49.939
2020-02-02 | 3:09 | 49.937
2020-02-02 | 3:09 | 49.937
2020-02-02 | 3:09 | 49.937
2020-02-02 | 3:09 | 49.938
2020-02-02 | 3:09 | 49.939
2020-02-02 | 3:09 | 49.941
2020-02-02 | 3:09 | 49.941
2020-02-02 | 3:09 | 49.941
2020-02-02 | 3:10 | 49.942
2020-02-02 | 3:10 | 49.942
2020-02-02 | 3:10 | 49.943
2020-02-02 | 3:10 | 49.942
2020-02-02 | 3:10 | 49.942
2020-02-02 | 3:10 | 49.942
2020-02-02 | 3:10 | 49.941
2020-02-02 | 3:10 | 49.94
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.938
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.939
2020-02-02 | 3:10 | 49.938
2020-02-02 | 3:10 | 49.937
2020-02-02 | 3:10 | 49.937
2020-02-02 | 3:10 | 49.938
2020-02-02 | 3:10 | 49.937
2020-02-02 | 3:10 | 49.938
2020-02-02 | 3:10 | 49.937
2020-02-02 | 3:10 | 49.937
2020-02-02 | 3:10 | 49.935
2020-02-02 | 3:10 | 49.935
2020-02-02 | 3:10 | 49.934
2020-02-02 | 3:10 | 49.933
2020-02-02 | 3:10 | 49.931
2020-02-02 | 3:10 | 49.93
2020-02-02 | 3:10 | 49.929
2020-02-02 | 3:10 | 49.926
2020-02-02 | 3:10 | 49.925
2020-02-02 | 3:10 | 49.923
2020-02-02 | 3:10 | 49.922
2020-02-02 | 3:10 | 49.921
2020-02-02 | 3:10 | 49.92
2020-02-02 | 3:10 | 49.918
2020-02-02 | 3:10 | 49.917
2020-02-02 | 3:10 | 49.917
2020-02-02 | 3:10 | 49.917
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.913
2020-02-02 | 3:10 | 49.912
2020-02-02 | 3:10 | 49.911
2020-02-02 | 3:10 | 49.912
2020-02-02 | 3:10 | 49.913
2020-02-02 | 3:10 | 49.913
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.916
2020-02-02 | 3:10 | 49.916
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.914
2020-02-02 | 3:10 | 49.915
2020-02-02 | 3:10 | 49.914
2020-02-02 | 3:10 | 49.913
2020-02-02 | 3:10 | 49.911
2020-02-02 | 3:11 | 49.911
2020-02-02 | 3:11 | 49.909
2020-02-02 | 3:11 | 49.91
2020-02-02 | 3:11 | 49.91
2020-02-02 | 3:11 | 49.91
2020-02-02 | 3:11 | 49.911
2020-02-02 | 3:11 | 49.911
2020-02-02 | 3:11 | 49.912
2020-02-02 | 3:11 | 49.913
2020-02-02 | 3:11 | 49.913
2020-02-02 | 3:11 | 49.914
2020-02-02 | 3:11 | 49.915
2020-02-02 | 3:11 | 49.915
2020-02-02 | 3:11 | 49.914
2020-02-02 | 3:11 | 49.913
2020-02-02 | 3:11 | 49.911
2020-02-02 | 3:11 | 49.911
2020-02-02 | 3:11 | 49.91
2020-02-02 | 3:11 | 49.913
2020-02-02 | 3:11 | 49.916
2020-02-02 | 3:11 | 49.919
2020-02-02 | 3:11 | 49.921
2020-02-02 | 3:11 | 49.921
2020-02-02 | 3:11 | 49.923
2020-02-02 | 3:11 | 49.923
2020-02-02 | 3:11 | 49.922
2020-02-02 | 3:11 | 49.922
2020-02-02 | 3:11 | 49.919
2020-02-02 | 3:11 | 49.916
2020-02-02 | 3:11 | 49.916
2020-02-02 | 3:11 | 49.914
2020-02-02 | 3:11 | 49.916
2020-02-02 | 3:11 | 49.918
2020-02-02 | 3:11 | 49.919
2020-02-02 | 3:11 | 49.92
2020-02-02 | 3:11 | 49.921
2020-02-02 | 3:11 | 49.919
2020-02-02 | 3:11 | 49.919
2020-02-02 | 3:11 | 49.918
2020-02-02 | 3:11 | 49.917
2020-02-02 | 3:11 | 49.916
2020-02-02 | 3:11 | 49.913
2020-02-02 | 3:11 | 49.912
2020-02-02 | 3:11 | 49.912
2020-02-02 | 3:11 | 49.914
2020-02-02 | 3:11 | 49.915
2020-02-02 | 3:11 | 49.917
2020-02-02 | 3:11 | 49.921
2020-02-02 | 3:11 | 49.926
2020-02-02 | 3:11 | 49.929
2020-02-02 | 3:11 | 49.93
2020-02-02 | 3:11 | 49.931
2020-02-02 | 3:11 | 49.932
2020-02-02 | 3:11 | 49.931
2020-02-02 | 3:11 | 49.929
2020-02-02 | 3:11 | 49.927
2020-02-02 | 3:11 | 49.925
2020-02-02 | 3:11 | 49.923
2020-02-02 | 3:11 | 49.922
2020-02-02 | 3:12 | 49.923
2020-02-02 | 3:12 | 49.923
2020-02-02 | 3:12 | 49.924
2020-02-02 | 3:12 | 49.923
2020-02-02 | 3:12 | 49.924
2020-02-02 | 3:12 | 49.926
2020-02-02 | 3:12 | 49.928
2020-02-02 | 3:12 | 49.927
2020-02-02 | 3:12 | 49.927
2020-02-02 | 3:12 | 49.927
2020-02-02 | 3:12 | 49.925
2020-02-02 | 3:12 | 49.925
2020-02-02 | 3:12 | 49.927
2020-02-02 | 3:12 | 49.929
2020-02-02 | 3:12 | 49.93
2020-02-02 | 3:12 | 49.93
2020-02-02 | 3:12 | 49.93
2020-02-02 | 3:12 | 49.929
2020-02-02 | 3:12 | 49.93
2020-02-02 | 3:12 | 49.93
2020-02-02 | 3:12 | 49.931
2020-02-02 | 3:12 | 49.932
2020-02-02 | 3:12 | 49.933
2020-02-02 | 3:12 | 49.933
2020-02-02 | 3:12 | 49.933
2020-02-02 | 3:12 | 49.933
2020-02-02 | 3:12 | 49.933
2020-02-02 | 3:12 | 49.935
2020-02-02 | 3:12 | 49.935
2020-02-02 | 3:12 | 49.934
2020-02-02 | 3:12 | 49.934
2020-02-02 | 3:12 | 49.934
2020-02-02 | 3:12 | 49.934
2020-02-02 | 3:12 | 49.935
2020-02-02 | 3:12 | 49.934
2020-02-02 | 3:12 | 49.935
2020-02-02 | 3:12 | 49.936
2020-02-02 | 3:12 | 49.936
2020-02-02 | 3:12 | 49.936
2020-02-02 | 3:12 | 49.936
2020-02-02 | 3:12 | 49.936
2020-02-02 | 3:12 | 49.937
2020-02-02 | 3:12 | 49.938
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.938
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.94
2020-02-02 | 3:12 | 49.94
2020-02-02 | 3:12 | 49.942
2020-02-02 | 3:12 | 49.941
2020-02-02 | 3:12 | 49.94
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.939
2020-02-02 | 3:12 | 49.94
2020-02-02 | 3:12 | 49.94
2020-02-02 | 3:12 | 49.941
2020-02-02 | 3:12 | 49.942
2020-02-02 | 3:12 | 49.942
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.942
2020-02-02 | 3:13 | 49.943
2020-02-02 | 3:13 | 49.944
2020-02-02 | 3:13 | 49.943
2020-02-02 | 3:13 | 49.943
2020-02-02 | 3:13 | 49.943
2020-02-02 | 3:13 | 49.942
2020-02-02 | 3:13 | 49.94
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.937
2020-02-02 | 3:13 | 49.937
2020-02-02 | 3:13 | 49.936
2020-02-02 | 3:13 | 49.937
2020-02-02 | 3:13 | 49.937
2020-02-02 | 3:13 | 49.937
2020-02-02 | 3:13 | 49.938
2020-02-02 | 3:13 | 49.938
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.94
2020-02-02 | 3:13 | 49.94
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.941
2020-02-02 | 3:13 | 49.94
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.939
2020-02-02 | 3:13 | 49.94
2020-02-02 | 3:13 | 49.942
2020-02-02 | 3:13 | 49.943
2020-02-02 | 3:13 | 49.946
2020-02-02 | 3:13 | 49.95
2020-02-02 | 3:13 | 49.951
2020-02-02 | 3:13 | 49.953
2020-02-02 | 3:13 | 49.955
2020-02-02 | 3:13 | 49.955
2020-02-02 | 3:13 | 49.954
2020-02-02 | 3:13 | 49.953
2020-02-02 | 3:13 | 49.951
2020-02-02 | 3:13 | 49.949
2020-02-02 | 3:13 | 49.947
2020-02-02 | 3:13 | 49.946
2020-02-02 | 3:13 | 49.949
2020-02-02 | 3:13 | 49.95
2020-02-02 | 3:13 | 49.951
2020-02-02 | 3:13 | 49.952
2020-02-02 | 3:13 | 49.953
2020-02-02 | 3:13 | 49.954
2020-02-02 | 3:13 | 49.955
2020-02-02 | 3:13 | 49.954
2020-02-02 | 3:14 | 49.952
2020-02-02 | 3:14 | 49.949
2020-02-02 | 3:14 | 49.946
2020-02-02 | 3:14 | 49.945
2020-02-02 | 3:14 | 49.948
2020-02-02 | 3:14 | 49.949
2020-02-02 | 3:14 | 49.948
2020-02-02 | 3:14 | 49.945
2020-02-02 | 3:14 | 49.941
2020-02-02 | 3:14 | 49.938
2020-02-02 | 3:14 | 49.936
2020-02-02 | 3:14 | 49.936
2020-02-02 | 3:14 | 49.935
2020-02-02 | 3:14 | 49.933
2020-02-02 | 3:14 | 49.932
2020-02-02 | 3:14 | 49.93
2020-02-02 | 3:14 | 49.931
2020-02-02 | 3:14 | 49.934
2020-02-02 | 3:14 | 49.934
2020-02-02 | 3:14 | 49.937
2020-02-02 | 3:14 | 49.939
2020-02-02 | 3:14 | 49.941
2020-02-02 | 3:14 | 49.941
2020-02-02 | 3:14 | 49.941
2020-02-02 | 3:14 | 49.941
2020-02-02 | 3:14 | 49.943
2020-02-02 | 3:14 | 49.943
2020-02-02 | 3:14 | 49.94
2020-02-02 | 3:14 | 49.937
2020-02-02 | 3:14 | 49.934
2020-02-02 | 3:14 | 49.934
2020-02-02 | 3:14 | 49.934
2020-02-02 | 3:14 | 49.934
2020-02-02 | 3:14 | 49.933
2020-02-02 | 3:14 | 49.935
2020-02-02 | 3:14 | 49.938
2020-02-02 | 3:14 | 49.941
2020-02-02 | 3:14 | 49.944
2020-02-02 | 3:14 | 49.946
2020-02-02 | 3:14 | 49.947
2020-02-02 | 3:14 | 49.949
2020-02-02 | 3:14 | 49.951
2020-02-02 | 3:14 | 49.953
2020-02-02 | 3:14 | 49.955
2020-02-02 | 3:14 | 49.956
2020-02-02 | 3:14 | 49.956
2020-02-02 | 3:14 | 49.955
2020-02-02 | 3:14 | 49.956
2020-02-02 | 3:14 | 49.956
2020-02-02 | 3:14 | 49.956
2020-02-02 | 3:14 | 49.955
2020-02-02 | 3:14 | 49.957
2020-02-02 | 3:14 | 49.959
2020-02-02 | 3:14 | 49.961
2020-02-02 | 3:14 | 49.961
2020-02-02 | 3:14 | 49.962
2020-02-02 | 3:14 | 49.963
2020-02-02 | 3:14 | 49.963
2020-02-02 | 3:14 | 49.963
2020-02-02 | 3:14 | 49.963
2020-02-02 | 3:14 | 49.962
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.964
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.959
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.957
2020-02-02 | 3:15 | 49.958
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.958
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.962
2020-02-02 | 3:15 | 49.963
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.959
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.96
2020-02-02 | 3:15 | 49.961
2020-02-02 | 3:15 | 49.959
2020-02-02 | 3:15 | 49.958
2020-02-02 | 3:15 | 49.957
2020-02-02 | 3:15 | 49.957
2020-02-02 | 3:15 | 49.957
2020-02-02 | 3:15 | 49.957
2020-02-02 | 3:15 | 49.956
2020-02-02 | 3:15 | 49.956
2020-02-02 | 3:15 | 49.955
2020-02-02 | 3:15 | 49.955
2020-02-02 | 3:15 | 49.955
2020-02-02 | 3:15 | 49.956
2020-02-02 | 3:15 | 49.955
2020-02-02 | 3:15 | 49.956
2020-02-02 | 3:15 | 49.955
2020-02-02 | 3:15 | 49.954
2020-02-02 | 3:15 | 49.952
2020-02-02 | 3:15 | 49.952
2020-02-02 | 3:15 | 49.95
2020-02-02 | 3:15 | 49.95
2020-02-02 | 3:15 | 49.951
2020-02-02 | 3:15 | 49.949
2020-02-02 | 3:16 | 49.949
2020-02-02 | 3:16 | 49.949
2020-02-02 | 3:16 | 49.948
2020-02-02 | 3:16 | 49.945
2020-02-02 | 3:16 | 49.945
2020-02-02 | 3:16 | 49.944
2020-02-02 | 3:16 | 49.944
2020-02-02 | 3:16 | 49.945
2020-02-02 | 3:16 | 49.947
2020-02-02 | 3:16 | 49.95
2020-02-02 | 3:16 | 49.951
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.955
2020-02-02 | 3:16 | 49.954
2020-02-02 | 3:16 | 49.954
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.951
2020-02-02 | 3:16 | 49.949
2020-02-02 | 3:16 | 49.947
2020-02-02 | 3:16 | 49.946
2020-02-02 | 3:16 | 49.95
2020-02-02 | 3:16 | 49.96
2020-02-02 | 3:16 | 49.965
2020-02-02 | 3:16 | 49.963
2020-02-02 | 3:16 | 49.959
2020-02-02 | 3:16 | 49.959
2020-02-02 | 3:16 | 49.957
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.951
2020-02-02 | 3:16 | 49.952
2020-02-02 | 3:16 | 49.954
2020-02-02 | 3:16 | 49.956
2020-02-02 | 3:16 | 49.955
2020-02-02 | 3:16 | 49.956
2020-02-02 | 3:16 | 49.955
2020-02-02 | 3:16 | 49.955
2020-02-02 | 3:16 | 49.954
2020-02-02 | 3:16 | 49.954
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.953
2020-02-02 | 3:16 | 49.951
2020-02-02 | 3:16 | 49.949
2020-02-02 | 3:16 | 49.947
2020-02-02 | 3:16 | 49.944
2020-02-02 | 3:16 | 49.944
2020-02-02 | 3:16 | 49.943
2020-02-02 | 3:16 | 49.946
2020-02-02 | 3:16 | 49.946
2020-02-02 | 3:16 | 49.947
2020-02-02 | 3:16 | 49.946
2020-02-02 | 3:16 | 49.948
2020-02-02 | 3:16 | 49.948
2020-02-02 | 3:16 | 49.951
2020-02-02 | 3:16 | 49.951
2020-02-02 | 3:16 | 49.95
2020-02-02 | 3:16 | 49.948
2020-02-02 | 3:16 | 49.947
2020-02-02 | 3:17 | 49.946
2020-02-02 | 3:17 | 49.947
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.949
2020-02-02 | 3:17 | 49.951
2020-02-02 | 3:17 | 49.954
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.96
2020-02-02 | 3:17 | 49.96
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.961
2020-02-02 | 3:17 | 49.96
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.96
2020-02-02 | 3:17 | 49.96
2020-02-02 | 3:17 | 49.958
2020-02-02 | 3:17 | 49.957
2020-02-02 | 3:17 | 49.958
2020-02-02 | 3:17 | 49.958
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.958
2020-02-02 | 3:17 | 49.962
2020-02-02 | 3:17 | 49.961
2020-02-02 | 3:17 | 49.96
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.957
2020-02-02 | 3:17 | 49.955
2020-02-02 | 3:17 | 49.955
2020-02-02 | 3:17 | 49.956
2020-02-02 | 3:17 | 49.959
2020-02-02 | 3:17 | 49.957
2020-02-02 | 3:17 | 49.956
2020-02-02 | 3:17 | 49.957
2020-02-02 | 3:17 | 49.958
2020-02-02 | 3:17 | 49.956
2020-02-02 | 3:17 | 49.955
2020-02-02 | 3:17 | 49.955
2020-02-02 | 3:17 | 49.954
2020-02-02 | 3:17 | 49.955
2020-02-02 | 3:17 | 49.955
2020-02-02 | 3:17 | 49.952
2020-02-02 | 3:17 | 49.949
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.949
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.947
2020-02-02 | 3:17 | 49.95
2020-02-02 | 3:17 | 49.95
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.949
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.947
2020-02-02 | 3:17 | 49.946
2020-02-02 | 3:17 | 49.948
2020-02-02 | 3:17 | 49.945
2020-02-02 | 3:17 | 49.944
2020-02-02 | 3:17 | 49.941
2020-02-02 | 3:17 | 49.94
2020-02-02 | 3:18 | 49.938
2020-02-02 | 3:18 | 49.938
2020-02-02 | 3:18 | 49.937
2020-02-02 | 3:18 | 49.934
2020-02-02 | 3:18 | 49.934
2020-02-02 | 3:18 | 49.93
2020-02-02 | 3:18 | 49.931
2020-02-02 | 3:18 | 49.928
2020-02-02 | 3:18 | 49.927
2020-02-02 | 3:18 | 49.926
2020-02-02 | 3:18 | 49.925
2020-02-02 | 3:18 | 49.926
2020-02-02 | 3:18 | 49.925
2020-02-02 | 3:18 | 49.925
2020-02-02 | 3:18 | 49.924
2020-02-02 | 3:18 | 49.923
2020-02-02 | 3:18 | 49.925
2020-02-02 | 3:18 | 49.923
2020-02-02 | 3:18 | 49.925
2020-02-02 | 3:18 | 49.924
2020-02-02 | 3:18 | 49.924
2020-02-02 | 3:18 | 49.924
2020-02-02 | 3:18 | 49.921
2020-02-02 | 3:18 | 49.919
2020-02-02 | 3:18 | 49.918
2020-02-02 | 3:18 | 49.916
2020-02-02 | 3:18 | 49.914
2020-02-02 | 3:18 | 49.914
2020-02-02 | 3:18 | 49.911
2020-02-02 | 3:18 | 49.912
2020-02-02 | 3:18 | 49.91
2020-02-02 | 3:18 | 49.91
2020-02-02 | 3:18 | 49.908
2020-02-02 | 3:18 | 49.908
2020-02-02 | 3:18 | 49.91
2020-02-02 | 3:18 | 49.908
2020-02-02 | 3:18 | 49.91
2020-02-02 | 3:18 | 49.909
2020-02-02 | 3:18 | 49.911
2020-02-02 | 3:18 | 49.909
2020-02-02 | 3:18 | 49.911
2020-02-02 | 3:18 | 49.91
2020-02-02 | 3:18 | 49.909
2020-02-02 | 3:18 | 49.907
2020-02-02 | 3:18 | 49.907
2020-02-02 | 3:18 | 49.906
2020-02-02 | 3:18 | 49.904
2020-02-02 | 3:18 | 49.903
2020-02-02 | 3:18 | 49.903
2020-02-02 | 3:18 | 49.904
2020-02-02 | 3:18 | 49.906
2020-02-02 | 3:18 | 49.91
2020-02-02 | 3:18 | 49.911
2020-02-02 | 3:18 | 49.912
2020-02-02 | 3:18 | 49.912
2020-02-02 | 3:18 | 49.913
2020-02-02 | 3:18 | 49.911
2020-02-02 | 3:18 | 49.911
2020-02-02 | 3:18 | 49.909
2020-02-02 | 3:18 | 49.907
2020-02-02 | 3:19 | 49.905
2020-02-02 | 3:19 | 49.909
2020-02-02 | 3:19 | 49.91
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.915
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.912
2020-02-02 | 3:19 | 49.909
2020-02-02 | 3:19 | 49.908
2020-02-02 | 3:19 | 49.905
2020-02-02 | 3:19 | 49.905
2020-02-02 | 3:19 | 49.906
2020-02-02 | 3:19 | 49.906
2020-02-02 | 3:19 | 49.908
2020-02-02 | 3:19 | 49.91
2020-02-02 | 3:19 | 49.913
2020-02-02 | 3:19 | 49.913
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.913
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.913
2020-02-02 | 3:19 | 49.911
2020-02-02 | 3:19 | 49.912
2020-02-02 | 3:19 | 49.91
2020-02-02 | 3:19 | 49.909
2020-02-02 | 3:19 | 49.908
2020-02-02 | 3:19 | 49.908
2020-02-02 | 3:19 | 49.908
2020-02-02 | 3:19 | 49.909
2020-02-02 | 3:19 | 49.909
2020-02-02 | 3:19 | 49.911
2020-02-02 | 3:19 | 49.911
2020-02-02 | 3:19 | 49.912
2020-02-02 | 3:19 | 49.913
2020-02-02 | 3:19 | 49.912
2020-02-02 | 3:19 | 49.913
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.915
2020-02-02 | 3:19 | 49.915
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.915
2020-02-02 | 3:19 | 49.915
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.914
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.917
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:19 | 49.915
2020-02-02 | 3:19 | 49.917
2020-02-02 | 3:19 | 49.916
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.914
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.914
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.914
2020-02-02 | 3:20 | 49.913
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.912
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.913
2020-02-02 | 3:20 | 49.912
2020-02-02 | 3:20 | 49.913
2020-02-02 | 3:20 | 49.913
2020-02-02 | 3:20 | 49.914
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.919
2020-02-02 | 3:20 | 49.918
2020-02-02 | 3:20 | 49.92
2020-02-02 | 3:20 | 49.919
2020-02-02 | 3:20 | 49.919
2020-02-02 | 3:20 | 49.92
2020-02-02 | 3:20 | 49.919
2020-02-02 | 3:20 | 49.917
2020-02-02 | 3:20 | 49.916
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.915
2020-02-02 | 3:20 | 49.914
2020-02-02 | 3:20 | 49.913
2020-02-02 | 3:20 | 49.912
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.912
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.912
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.909
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.911
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.91
2020-02-02 | 3:20 | 49.908
2020-02-02 | 3:20 | 49.908
2020-02-02 | 3:20 | 49.905
2020-02-02 | 3:20 | 49.904
2020-02-02 | 3:20 | 49.902
2020-02-02 | 3:20 | 49.901
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.902
2020-02-02 | 3:21 | 49.905
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.904
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.902
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.899
2020-02-02 | 3:21 | 49.897
2020-02-02 | 3:21 | 49.897
2020-02-02 | 3:21 | 49.898
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.904
2020-02-02 | 3:21 | 49.902
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.899
2020-02-02 | 3:21 | 49.894
2020-02-02 | 3:21 | 49.892
2020-02-02 | 3:21 | 49.89
2020-02-02 | 3:21 | 49.888
2020-02-02 | 3:21 | 49.895
2020-02-02 | 3:21 | 49.897
2020-02-02 | 3:21 | 49.899
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.904
2020-02-02 | 3:21 | 49.905
2020-02-02 | 3:21 | 49.906
2020-02-02 | 3:21 | 49.905
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.898
2020-02-02 | 3:21 | 49.899
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.904
2020-02-02 | 3:21 | 49.906
2020-02-02 | 3:21 | 49.907
2020-02-02 | 3:21 | 49.908
2020-02-02 | 3:21 | 49.909
2020-02-02 | 3:21 | 49.909
2020-02-02 | 3:21 | 49.906
2020-02-02 | 3:21 | 49.907
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.902
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.9
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.901
2020-02-02 | 3:21 | 49.903
2020-02-02 | 3:21 | 49.904
2020-02-02 | 3:22 | 49.904
2020-02-02 | 3:22 | 49.905
2020-02-02 | 3:22 | 49.906
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.911
2020-02-02 | 3:22 | 49.915
2020-02-02 | 3:22 | 49.917
2020-02-02 | 3:22 | 49.92
2020-02-02 | 3:22 | 49.92
2020-02-02 | 3:22 | 49.92
2020-02-02 | 3:22 | 49.922
2020-02-02 | 3:22 | 49.921
2020-02-02 | 3:22 | 49.925
2020-02-02 | 3:22 | 49.926
2020-02-02 | 3:22 | 49.928
2020-02-02 | 3:22 | 49.928
2020-02-02 | 3:22 | 49.926
2020-02-02 | 3:22 | 49.932
2020-02-02 | 3:22 | 49.933
2020-02-02 | 3:22 | 49.935
2020-02-02 | 3:22 | 49.932
2020-02-02 | 3:22 | 49.929
2020-02-02 | 3:22 | 49.928
2020-02-02 | 3:22 | 49.923
2020-02-02 | 3:22 | 49.921
2020-02-02 | 3:22 | 49.919
2020-02-02 | 3:22 | 49.916
2020-02-02 | 3:22 | 49.915
2020-02-02 | 3:22 | 49.913
2020-02-02 | 3:22 | 49.914
2020-02-02 | 3:22 | 49.913
2020-02-02 | 3:22 | 49.911
2020-02-02 | 3:22 | 49.912
2020-02-02 | 3:22 | 49.913
2020-02-02 | 3:22 | 49.913
2020-02-02 | 3:22 | 49.913
2020-02-02 | 3:22 | 49.913
2020-02-02 | 3:22 | 49.912
2020-02-02 | 3:22 | 49.912
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.908
2020-02-02 | 3:22 | 49.907
2020-02-02 | 3:22 | 49.908
2020-02-02 | 3:22 | 49.907
2020-02-02 | 3:22 | 49.908
2020-02-02 | 3:22 | 49.908
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.908
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.909
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:22 | 49.91
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.908
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.908
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.907
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.907
2020-02-02 | 3:23 | 49.907
2020-02-02 | 3:23 | 49.908
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.91
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.907
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.903
2020-02-02 | 3:23 | 49.903
2020-02-02 | 3:23 | 49.9
2020-02-02 | 3:23 | 49.898
2020-02-02 | 3:23 | 49.899
2020-02-02 | 3:23 | 49.9
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.905
2020-02-02 | 3:23 | 49.903
2020-02-02 | 3:23 | 49.901
2020-02-02 | 3:23 | 49.899
2020-02-02 | 3:23 | 49.901
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.904
2020-02-02 | 3:23 | 49.906
2020-02-02 | 3:23 | 49.907
2020-02-02 | 3:23 | 49.907
2020-02-02 | 3:23 | 49.909
2020-02-02 | 3:23 | 49.908
2020-02-02 | 3:23 | 49.911
2020-02-02 | 3:23 | 49.91
2020-02-02 | 3:24 | 49.908
2020-02-02 | 3:24 | 49.904
2020-02-02 | 3:24 | 49.904
2020-02-02 | 3:24 | 49.903
2020-02-02 | 3:24 | 49.903
2020-02-02 | 3:24 | 49.903
2020-02-02 | 3:24 | 49.905
2020-02-02 | 3:24 | 49.907
2020-02-02 | 3:24 | 49.908
2020-02-02 | 3:24 | 49.911
2020-02-02 | 3:24 | 49.912
2020-02-02 | 3:24 | 49.914
2020-02-02 | 3:24 | 49.915
2020-02-02 | 3:24 | 49.914
2020-02-02 | 3:24 | 49.914
2020-02-02 | 3:24 | 49.913
2020-02-02 | 3:24 | 49.913
2020-02-02 | 3:24 | 49.913
2020-02-02 | 3:24 | 49.913
2020-02-02 | 3:24 | 49.912
2020-02-02 | 3:24 | 49.911
2020-02-02 | 3:24 | 49.913
2020-02-02 | 3:24 | 49.914
2020-02-02 | 3:24 | 49.916
2020-02-02 | 3:24 | 49.918
2020-02-02 | 3:24 | 49.92
2020-02-02 | 3:24 | 49.925
2020-02-02 | 3:24 | 49.928
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.932
2020-02-02 | 3:24 | 49.931
2020-02-02 | 3:24 | 49.93
2020-02-02 | 3:24 | 49.928
2020-02-02 | 3:24 | 49.927
2020-02-02 | 3:24 | 49.925
2020-02-02 | 3:24 | 49.926
2020-02-02 | 3:24 | 49.925
2020-02-02 | 3:24 | 49.925
2020-02-02 | 3:24 | 49.925
2020-02-02 | 3:24 | 49.926
2020-02-02 | 3:24 | 49.926
2020-02-02 | 3:24 | 49.927
2020-02-02 | 3:24 | 49.927
2020-02-02 | 3:24 | 49.925
2020-02-02 | 3:24 | 49.923
2020-02-02 | 3:24 | 49.922
2020-02-02 | 3:24 | 49.921
2020-02-02 | 3:24 | 49.921
2020-02-02 | 3:24 | 49.921
2020-02-02 | 3:24 | 49.921
2020-02-02 | 3:24 | 49.92
2020-02-02 | 3:24 | 49.919
2020-02-02 | 3:24 | 49.917
2020-02-02 | 3:24 | 49.916
2020-02-02 | 3:24 | 49.916
2020-02-02 | 3:24 | 49.915
2020-02-02 | 3:25 | 49.915
2020-02-02 | 3:25 | 49.916
2020-02-02 | 3:25 | 49.917
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.922
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.924
2020-02-02 | 3:25 | 49.924
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.927
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.926
2020-02-02 | 3:25 | 49.925
2020-02-02 | 3:25 | 49.925
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.924
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.924
2020-02-02 | 3:25 | 49.923
2020-02-02 | 3:25 | 49.922
2020-02-02 | 3:25 | 49.921
2020-02-02 | 3:25 | 49.921
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.92
2020-02-02 | 3:25 | 49.92
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.917
2020-02-02 | 3:25 | 49.915
2020-02-02 | 3:25 | 49.913
2020-02-02 | 3:25 | 49.911
2020-02-02 | 3:25 | 49.911
2020-02-02 | 3:25 | 49.912
2020-02-02 | 3:25 | 49.914
2020-02-02 | 3:25 | 49.915
2020-02-02 | 3:25 | 49.916
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.919
2020-02-02 | 3:25 | 49.918
2020-02-02 | 3:25 | 49.917
2020-02-02 | 3:25 | 49.914
2020-02-02 | 3:26 | 49.913
2020-02-02 | 3:26 | 49.913
2020-02-02 | 3:26 | 49.912
2020-02-02 | 3:26 | 49.913
2020-02-02 | 3:26 | 49.916
2020-02-02 | 3:26 | 49.917
2020-02-02 | 3:26 | 49.919
2020-02-02 | 3:26 | 49.921
2020-02-02 | 3:26 | 49.922
2020-02-02 | 3:26 | 49.921
2020-02-02 | 3:26 | 49.921
2020-02-02 | 3:26 | 49.92
2020-02-02 | 3:26 | 49.919
2020-02-02 | 3:26 | 49.918
2020-02-02 | 3:26 | 49.92
2020-02-02 | 3:26 | 49.922
2020-02-02 | 3:26 | 49.923
2020-02-02 | 3:26 | 49.924
2020-02-02 | 3:26 | 49.923
2020-02-02 | 3:26 | 49.922
2020-02-02 | 3:26 | 49.92
2020-02-02 | 3:26 | 49.919
2020-02-02 | 3:26 | 49.917
2020-02-02 | 3:26 | 49.915
2020-02-02 | 3:26 | 49.91
2020-02-02 | 3:26 | 49.907
2020-02-02 | 3:26 | 49.904
2020-02-02 | 3:26 | 49.903
2020-02-02 | 3:26 | 49.903
2020-02-02 | 3:26 | 49.906
2020-02-02 | 3:26 | 49.912
2020-02-02 | 3:26 | 49.916
2020-02-02 | 3:26 | 49.919
2020-02-02 | 3:26 | 49.921
2020-02-02 | 3:26 | 49.924
2020-02-02 | 3:26 | 49.924
2020-02-02 | 3:26 | 49.922
2020-02-02 | 3:26 | 49.922
2020-02-02 | 3:26 | 49.919
2020-02-02 | 3:26 | 49.915
2020-02-02 | 3:26 | 49.914
2020-02-02 | 3:26 | 49.912
2020-02-02 | 3:26 | 49.912
2020-02-02 | 3:26 | 49.913
2020-02-02 | 3:26 | 49.914
2020-02-02 | 3:26 | 49.915
2020-02-02 | 3:26 | 49.918
2020-02-02 | 3:26 | 49.919
2020-02-02 | 3:26 | 49.921
2020-02-02 | 3:26 | 49.923
2020-02-02 | 3:26 | 49.924
2020-02-02 | 3:26 | 49.926
2020-02-02 | 3:26 | 49.928
2020-02-02 | 3:26 | 49.93
2020-02-02 | 3:26 | 49.932
2020-02-02 | 3:26 | 49.933
2020-02-02 | 3:26 | 49.934
2020-02-02 | 3:26 | 49.935
2020-02-02 | 3:26 | 49.936
2020-02-02 | 3:26 | 49.937
2020-02-02 | 3:26 | 49.937
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.938
2020-02-02 | 3:27 | 49.938
2020-02-02 | 3:27 | 49.937
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.937
2020-02-02 | 3:27 | 49.937
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.939
2020-02-02 | 3:27 | 49.938
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.937
2020-02-02 | 3:27 | 49.938
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.936
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.935
2020-02-02 | 3:27 | 49.934
2020-02-02 | 3:27 | 49.932
2020-02-02 | 3:27 | 49.931
2020-02-02 | 3:27 | 49.93
2020-02-02 | 3:27 | 49.928
2020-02-02 | 3:27 | 49.928
2020-02-02 | 3:27 | 49.926
2020-02-02 | 3:27 | 49.925
2020-02-02 | 3:27 | 49.923
2020-02-02 | 3:27 | 49.923
2020-02-02 | 3:27 | 49.922
2020-02-02 | 3:27 | 49.924
2020-02-02 | 3:27 | 49.924
2020-02-02 | 3:27 | 49.924
2020-02-02 | 3:27 | 49.925
2020-02-02 | 3:27 | 49.925
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.927
2020-02-02 | 3:28 | 49.928
2020-02-02 | 3:28 | 49.928
2020-02-02 | 3:28 | 49.929
2020-02-02 | 3:28 | 49.929
2020-02-02 | 3:28 | 49.929
2020-02-02 | 3:28 | 49.928
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.924
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.924
2020-02-02 | 3:28 | 49.925
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.927
2020-02-02 | 3:28 | 49.927
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.925
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.924
2020-02-02 | 3:28 | 49.925
2020-02-02 | 3:28 | 49.925
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.927
2020-02-02 | 3:28 | 49.926
2020-02-02 | 3:28 | 49.924
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.92
2020-02-02 | 3:28 | 49.92
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.923
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.922
2020-02-02 | 3:28 | 49.921
2020-02-02 | 3:28 | 49.92
2020-02-02 | 3:28 | 49.919
2020-02-02 | 3:28 | 49.916
2020-02-02 | 3:28 | 49.916
2020-02-02 | 3:28 | 49.914
2020-02-02 | 3:28 | 49.914
2020-02-02 | 3:28 | 49.915
2020-02-02 | 3:28 | 49.916
2020-02-02 | 3:28 | 49.919
2020-02-02 | 3:28 | 49.919
2020-02-02 | 3:29 | 49.919
2020-02-02 | 3:29 | 49.918
2020-02-02 | 3:29 | 49.919
2020-02-02 | 3:29 | 49.919
2020-02-02 | 3:29 | 49.918
2020-02-02 | 3:29 | 49.916
2020-02-02 | 3:29 | 49.916
2020-02-02 | 3:29 | 49.914
2020-02-02 | 3:29 | 49.914
2020-02-02 | 3:29 | 49.914
2020-02-02 | 3:29 | 49.914
2020-02-02 | 3:29 | 49.914
2020-02-02 | 3:29 | 49.913
2020-02-02 | 3:29 | 49.914
2020-02-02 | 3:29 | 49.916
2020-02-02 | 3:29 | 49.919
2020-02-02 | 3:29 | 49.92
2020-02-02 | 3:29 | 49.921
2020-02-02 | 3:29 | 49.923
2020-02-02 | 3:29 | 49.925
2020-02-02 | 3:29 | 49.927
2020-02-02 | 3:29 | 49.928
2020-02-02 | 3:29 | 49.929
2020-02-02 | 3:29 | 49.928
2020-02-02 | 3:29 | 49.929
2020-02-02 | 3:29 | 49.927
2020-02-02 | 3:29 | 49.926
2020-02-02 | 3:29 | 49.925
2020-02-02 | 3:29 | 49.925
2020-02-02 | 3:29 | 49.924
2020-02-02 | 3:29 | 49.924
2020-02-02 | 3:29 | 49.923
2020-02-02 | 3:29 | 49.923
2020-02-02 | 3:29 | 49.923
2020-02-02 | 3:29 | 49.924
2020-02-02 | 3:29 | 49.925
2020-02-02 | 3:29 | 49.927
2020-02-02 | 3:29 | 49.929
2020-02-02 | 3:29 | 49.931
2020-02-02 | 3:29 | 49.935
2020-02-02 | 3:29 | 49.939
2020-02-02 | 3:29 | 49.943
2020-02-02 | 3:29 | 49.947
2020-02-02 | 3:29 | 49.948
2020-02-02 | 3:29 | 49.949
2020-02-02 | 3:29 | 49.95
2020-02-02 | 3:29 | 49.949
2020-02-02 | 3:29 | 49.948
2020-02-02 | 3:29 | 49.947
2020-02-02 | 3:29 | 49.947
2020-02-02 | 3:29 | 49.948
2020-02-02 | 3:29 | 49.948
2020-02-02 | 3:29 | 49.947
2020-02-02 | 3:29 | 49.946
2020-02-02 | 3:29 | 49.947
2020-02-02 | 3:29 | 49.946
2020-02-02 | 3:29 | 49.946
2020-02-02 | 3:29 | 49.946
2020-02-02 | 3:29 | 49.946
2020-02-02 | 3:29 | 49.948
2020-02-02 | 3:30 | 49.95
2020-02-02 | 3:30 | 49.95
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.946
2020-02-02 | 3:30 | 49.946
2020-02-02 | 3:30 | 49.946
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.95
2020-02-02 | 3:30 | 49.95
2020-02-02 | 3:30 | 49.95
2020-02-02 | 3:30 | 49.951
2020-02-02 | 3:30 | 49.951
2020-02-02 | 3:30 | 49.951
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.946
2020-02-02 | 3:30 | 49.946
2020-02-02 | 3:30 | 49.942
2020-02-02 | 3:30 | 49.941
2020-02-02 | 3:30 | 49.943
2020-02-02 | 3:30 | 49.944
2020-02-02 | 3:30 | 49.944
2020-02-02 | 3:30 | 49.946
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.949
2020-02-02 | 3:30 | 49.948
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.947
2020-02-02 | 3:30 | 49.945
2020-02-02 | 3:30 | 49.942
2020-02-02 | 3:30 | 49.939
2020-02-02 | 3:30 | 49.938
2020-02-02 | 3:30 | 49.939
2020-02-02 | 3:30 | 49.941
2020-02-02 | 3:30 | 49.942
2020-02-02 | 3:30 | 49.943
2020-02-02 | 3:30 | 49.942
2020-02-02 | 3:30 | 49.942
2020-02-02 | 3:31 | 49.94
2020-02-02 | 3:31 | 49.939
2020-02-02 | 3:31 | 49.938
2020-02-02 | 3:31 | 49.935
2020-02-02 | 3:31 | 49.934
2020-02-02 | 3:31 | 49.933
2020-02-02 | 3:31 | 49.935
2020-02-02 | 3:31 | 49.937
2020-02-02 | 3:31 | 49.94
2020-02-02 | 3:31 | 49.942
2020-02-02 | 3:31 | 49.944
2020-02-02 | 3:31 | 49.945
2020-02-02 | 3:31 | 49.946
2020-02-02 | 3:31 | 49.946
2020-02-02 | 3:31 | 49.945
2020-02-02 | 3:31 | 49.942
2020-02-02 | 3:31 | 49.94
2020-02-02 | 3:31 | 49.936
2020-02-02 | 3:31 | 49.933
2020-02-02 | 3:31 | 49.933
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.933
2020-02-02 | 3:31 | 49.931
2020-02-02 | 3:31 | 49.93
2020-02-02 | 3:31 | 49.929
2020-02-02 | 3:31 | 49.927
2020-02-02 | 3:31 | 49.926
2020-02-02 | 3:31 | 49.922
2020-02-02 | 3:31 | 49.92
2020-02-02 | 3:31 | 49.916
2020-02-02 | 3:31 | 49.913
2020-02-02 | 3:31 | 49.909
2020-02-02 | 3:31 | 49.908
2020-02-02 | 3:31 | 49.908
2020-02-02 | 3:31 | 49.908
2020-02-02 | 3:31 | 49.908
2020-02-02 | 3:31 | 49.91
2020-02-02 | 3:31 | 49.913
2020-02-02 | 3:31 | 49.915
2020-02-02 | 3:31 | 49.918
2020-02-02 | 3:31 | 49.918
2020-02-02 | 3:31 | 49.92
2020-02-02 | 3:31 | 49.922
2020-02-02 | 3:31 | 49.925
2020-02-02 | 3:31 | 49.927
2020-02-02 | 3:31 | 49.929
2020-02-02 | 3:31 | 49.929
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.934
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.932
2020-02-02 | 3:31 | 49.93
2020-02-02 | 3:31 | 49.93
2020-02-02 | 3:31 | 49.928
2020-02-02 | 3:32 | 49.928
2020-02-02 | 3:32 | 49.927
2020-02-02 | 3:32 | 49.926
2020-02-02 | 3:32 | 49.928
2020-02-02 | 3:32 | 49.927
2020-02-02 | 3:32 | 49.927
2020-02-02 | 3:32 | 49.927
2020-02-02 | 3:32 | 49.928
2020-02-02 | 3:32 | 49.929
2020-02-02 | 3:32 | 49.93
2020-02-02 | 3:32 | 49.93
2020-02-02 | 3:32 | 49.928
2020-02-02 | 3:32 | 49.929
2020-02-02 | 3:32 | 49.931
2020-02-02 | 3:32 | 49.932
2020-02-02 | 3:32 | 49.934
2020-02-02 | 3:32 | 49.933
2020-02-02 | 3:32 | 49.934
2020-02-02 | 3:32 | 49.933
2020-02-02 | 3:32 | 49.933
2020-02-02 | 3:32 | 49.931
2020-02-02 | 3:32 | 49.93
2020-02-02 | 3:32 | 49.929
2020-02-02 | 3:32 | 49.927
2020-02-02 | 3:32 | 49.926
2020-02-02 | 3:32 | 49.925
2020-02-02 | 3:32 | 49.922
2020-02-02 | 3:32 | 49.921
2020-02-02 | 3:32 | 49.921
2020-02-02 | 3:32 | 49.922
2020-02-02 | 3:32 | 49.921
2020-02-02 | 3:32 | 49.919
2020-02-02 | 3:32 | 49.917
2020-02-02 | 3:32 | 49.917
2020-02-02 | 3:32 | 49.916
2020-02-02 | 3:32 | 49.915
2020-02-02 | 3:32 | 49.914
2020-02-02 | 3:32 | 49.914
2020-02-02 | 3:32 | 49.913
2020-02-02 | 3:32 | 49.913
2020-02-02 | 3:32 | 49.911
2020-02-02 | 3:32 | 49.912
2020-02-02 | 3:32 | 49.909
2020-02-02 | 3:32 | 49.907
2020-02-02 | 3:32 | 49.905
2020-02-02 | 3:32 | 49.905
2020-02-02 | 3:32 | 49.904
2020-02-02 | 3:32 | 49.902
2020-02-02 | 3:32 | 49.902
2020-02-02 | 3:32 | 49.903
2020-02-02 | 3:32 | 49.904
2020-02-02 | 3:32 | 49.905
2020-02-02 | 3:32 | 49.906
2020-02-02 | 3:32 | 49.906
2020-02-02 | 3:32 | 49.908
2020-02-02 | 3:32 | 49.908
2020-02-02 | 3:32 | 49.908
2020-02-02 | 3:32 | 49.907
2020-02-02 | 3:32 | 49.907
2020-02-02 | 3:32 | 49.906
2020-02-02 | 3:32 | 49.906
2020-02-02 | 3:33 | 49.903
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.901
2020-02-02 | 3:33 | 49.901
2020-02-02 | 3:33 | 49.9
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.905
2020-02-02 | 3:33 | 49.905
2020-02-02 | 3:33 | 49.905
2020-02-02 | 3:33 | 49.907
2020-02-02 | 3:33 | 49.906
2020-02-02 | 3:33 | 49.905
2020-02-02 | 3:33 | 49.907
2020-02-02 | 3:33 | 49.907
2020-02-02 | 3:33 | 49.906
2020-02-02 | 3:33 | 49.905
2020-02-02 | 3:33 | 49.903
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.904
2020-02-02 | 3:33 | 49.907
2020-02-02 | 3:33 | 49.907
2020-02-02 | 3:33 | 49.906
2020-02-02 | 3:33 | 49.906
2020-02-02 | 3:33 | 49.906
2020-02-02 | 3:33 | 49.905
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.898
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.897
2020-02-02 | 3:33 | 49.898
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.9
2020-02-02 | 3:33 | 49.901
2020-02-02 | 3:33 | 49.901
2020-02-02 | 3:33 | 49.9
2020-02-02 | 3:33 | 49.899
2020-02-02 | 3:33 | 49.895
2020-02-02 | 3:33 | 49.896
2020-02-02 | 3:33 | 49.895
2020-02-02 | 3:33 | 49.896
2020-02-02 | 3:33 | 49.898
2020-02-02 | 3:33 | 49.9
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.904
2020-02-02 | 3:33 | 49.903
2020-02-02 | 3:33 | 49.903
2020-02-02 | 3:33 | 49.903
2020-02-02 | 3:33 | 49.902
2020-02-02 | 3:33 | 49.9
2020-02-02 | 3:33 | 49.898
2020-02-02 | 3:33 | 49.895
2020-02-02 | 3:33 | 49.896
2020-02-02 | 3:33 | 49.898
2020-02-02 | 3:34 | 49.897
2020-02-02 | 3:34 | 49.896
2020-02-02 | 3:34 | 49.897
2020-02-02 | 3:34 | 49.899
2020-02-02 | 3:34 | 49.902
2020-02-02 | 3:34 | 49.906
2020-02-02 | 3:34 | 49.909
2020-02-02 | 3:34 | 49.909
2020-02-02 | 3:34 | 49.91
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.913
2020-02-02 | 3:34 | 49.913
2020-02-02 | 3:34 | 49.915
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.913
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.917
2020-02-02 | 3:34 | 49.917
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.917
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.917
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.917
2020-02-02 | 3:34 | 49.917
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.915
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.915
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.914
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.915
2020-02-02 | 3:34 | 49.916
2020-02-02 | 3:34 | 49.918
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.919
2020-02-02 | 3:34 | 49.92
2020-02-02 | 3:34 | 49.921
2020-02-02 | 3:34 | 49.923
2020-02-02 | 3:34 | 49.924
2020-02-02 | 3:35 | 49.924
2020-02-02 | 3:35 | 49.922
2020-02-02 | 3:35 | 49.921
2020-02-02 | 3:35 | 49.919
2020-02-02 | 3:35 | 49.917
2020-02-02 | 3:35 | 49.916
2020-02-02 | 3:35 | 49.913
2020-02-02 | 3:35 | 49.912
2020-02-02 | 3:35 | 49.912
2020-02-02 | 3:35 | 49.91
2020-02-02 | 3:35 | 49.911
2020-02-02 | 3:35 | 49.91
2020-02-02 | 3:35 | 49.912
2020-02-02 | 3:35 | 49.911
2020-02-02 | 3:35 | 49.912
2020-02-02 | 3:35 | 49.911
2020-02-02 | 3:35 | 49.911
2020-02-02 | 3:35 | 49.91
2020-02-02 | 3:35 | 49.911
2020-02-02 | 3:35 | 49.91
2020-02-02 | 3:35 | 49.908
2020-02-02 | 3:35 | 49.907
2020-02-02 | 3:35 | 49.908
2020-02-02 | 3:35 | 49.907
2020-02-02 | 3:35 | 49.907
2020-02-02 | 3:35 | 49.906
2020-02-02 | 3:35 | 49.907
2020-02-02 | 3:35 | 49.906
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.902
2020-02-02 | 3:35 | 49.901
2020-02-02 | 3:35 | 49.901
2020-02-02 | 3:35 | 49.903
2020-02-02 | 3:35 | 49.902
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.904
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.906
2020-02-02 | 3:35 | 49.904
2020-02-02 | 3:35 | 49.904
2020-02-02 | 3:35 | 49.904
2020-02-02 | 3:35 | 49.903
2020-02-02 | 3:35 | 49.902
2020-02-02 | 3:35 | 49.9
2020-02-02 | 3:35 | 49.899
2020-02-02 | 3:35 | 49.899
2020-02-02 | 3:35 | 49.902
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.907
2020-02-02 | 3:35 | 49.908
2020-02-02 | 3:35 | 49.908
2020-02-02 | 3:35 | 49.907
2020-02-02 | 3:35 | 49.905
2020-02-02 | 3:35 | 49.902
2020-02-02 | 3:35 | 49.901
2020-02-02 | 3:36 | 49.9
2020-02-02 | 3:36 | 49.902
2020-02-02 | 3:36 | 49.906
2020-02-02 | 3:36 | 49.907
2020-02-02 | 3:36 | 49.908
2020-02-02 | 3:36 | 49.908
2020-02-02 | 3:36 | 49.907
2020-02-02 | 3:36 | 49.909
2020-02-02 | 3:36 | 49.907
2020-02-02 | 3:36 | 49.907
2020-02-02 | 3:36 | 49.905
2020-02-02 | 3:36 | 49.902
2020-02-02 | 3:36 | 49.899
2020-02-02 | 3:36 | 49.897
2020-02-02 | 3:36 | 49.895
2020-02-02 | 3:36 | 49.893
2020-02-02 | 3:36 | 49.894
2020-02-02 | 3:36 | 49.898
2020-02-02 | 3:36 | 49.9
2020-02-02 | 3:36 | 49.903
2020-02-02 | 3:36 | 49.902
2020-02-02 | 3:36 | 49.903
2020-02-02 | 3:36 | 49.904
2020-02-02 | 3:36 | 49.904
2020-02-02 | 3:36 | 49.905
2020-02-02 | 3:36 | 49.901
2020-02-02 | 3:36 | 49.901
2020-02-02 | 3:36 | 49.898
2020-02-02 | 3:36 | 49.901
2020-02-02 | 3:36 | 49.904
2020-02-02 | 3:36 | 49.906
2020-02-02 | 3:36 | 49.91
2020-02-02 | 3:36 | 49.912
2020-02-02 | 3:36 | 49.913
2020-02-02 | 3:36 | 49.917
2020-02-02 | 3:36 | 49.919
2020-02-02 | 3:36 | 49.92
2020-02-02 | 3:36 | 49.923
2020-02-02 | 3:36 | 49.924
2020-02-02 | 3:36 | 49.927
2020-02-02 | 3:36 | 49.927
2020-02-02 | 3:36 | 49.927
2020-02-02 | 3:36 | 49.926
2020-02-02 | 3:36 | 49.924
2020-02-02 | 3:36 | 49.921
2020-02-02 | 3:36 | 49.92
2020-02-02 | 3:36 | 49.917
2020-02-02 | 3:36 | 49.913
2020-02-02 | 3:36 | 49.914
2020-02-02 | 3:36 | 49.914
2020-02-02 | 3:36 | 49.915
2020-02-02 | 3:36 | 49.915
2020-02-02 | 3:36 | 49.916
2020-02-02 | 3:36 | 49.916
2020-02-02 | 3:36 | 49.918
2020-02-02 | 3:36 | 49.918
2020-02-02 | 3:36 | 49.918
2020-02-02 | 3:36 | 49.918
2020-02-02 | 3:36 | 49.918
2020-02-02 | 3:36 | 49.918
2020-02-02 | 3:36 | 49.92
2020-02-02 | 3:37 | 49.923
2020-02-02 | 3:37 | 49.923
2020-02-02 | 3:37 | 49.924
2020-02-02 | 3:37 | 49.924
2020-02-02 | 3:37 | 49.926
2020-02-02 | 3:37 | 49.926
2020-02-02 | 3:37 | 49.928
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.93
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.93
2020-02-02 | 3:37 | 49.93
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.929
2020-02-02 | 3:37 | 49.928
2020-02-02 | 3:37 | 49.928
2020-02-02 | 3:37 | 49.928
2020-02-02 | 3:37 | 49.927
2020-02-02 | 3:37 | 49.927
2020-02-02 | 3:37 | 49.927
2020-02-02 | 3:37 | 49.925
2020-02-02 | 3:37 | 49.923
2020-02-02 | 3:37 | 49.921
2020-02-02 | 3:37 | 49.919
2020-02-02 | 3:37 | 49.92
2020-02-02 | 3:37 | 49.919
2020-02-02 | 3:37 | 49.919
2020-02-02 | 3:37 | 49.92
2020-02-02 | 3:37 | 49.919
2020-02-02 | 3:37 | 49.921
2020-02-02 | 3:37 | 49.92
2020-02-02 | 3:37 | 49.921
2020-02-02 | 3:37 | 49.92
2020-02-02 | 3:37 | 49.921
2020-02-02 | 3:37 | 49.921
2020-02-02 | 3:37 | 49.919
2020-02-02 | 3:37 | 49.916
2020-02-02 | 3:37 | 49.913
2020-02-02 | 3:37 | 49.913
2020-02-02 | 3:37 | 49.912
2020-02-02 | 3:37 | 49.916
2020-02-02 | 3:37 | 49.916
2020-02-02 | 3:37 | 49.918
2020-02-02 | 3:37 | 49.918
2020-02-02 | 3:37 | 49.917
2020-02-02 | 3:37 | 49.916
2020-02-02 | 3:37 | 49.915
2020-02-02 | 3:37 | 49.915
2020-02-02 | 3:37 | 49.911
2020-02-02 | 3:37 | 49.908
2020-02-02 | 3:38 | 49.905
2020-02-02 | 3:38 | 49.903
2020-02-02 | 3:38 | 49.902
2020-02-02 | 3:38 | 49.904
2020-02-02 | 3:38 | 49.906
2020-02-02 | 3:38 | 49.908
2020-02-02 | 3:38 | 49.909
2020-02-02 | 3:38 | 49.91
2020-02-02 | 3:38 | 49.911
2020-02-02 | 3:38 | 49.911
2020-02-02 | 3:38 | 49.912
2020-02-02 | 3:38 | 49.912
2020-02-02 | 3:38 | 49.909
2020-02-02 | 3:38 | 49.906
2020-02-02 | 3:38 | 49.904
2020-02-02 | 3:38 | 49.902
2020-02-02 | 3:38 | 49.902
2020-02-02 | 3:38 | 49.903
2020-02-02 | 3:38 | 49.904
2020-02-02 | 3:38 | 49.907
2020-02-02 | 3:38 | 49.911
2020-02-02 | 3:38 | 49.912
2020-02-02 | 3:38 | 49.913
2020-02-02 | 3:38 | 49.913
2020-02-02 | 3:38 | 49.914
2020-02-02 | 3:38 | 49.915
2020-02-02 | 3:38 | 49.915
2020-02-02 | 3:38 | 49.915
2020-02-02 | 3:38 | 49.912
2020-02-02 | 3:38 | 49.91
2020-02-02 | 3:38 | 49.909
2020-02-02 | 3:38 | 49.908
2020-02-02 | 3:38 | 49.907
2020-02-02 | 3:38 | 49.908
2020-02-02 | 3:38 | 49.909
2020-02-02 | 3:38 | 49.912
2020-02-02 | 3:38 | 49.916
2020-02-02 | 3:38 | 49.916
2020-02-02 | 3:38 | 49.914
2020-02-02 | 3:38 | 49.917
2020-02-02 | 3:38 | 49.917
2020-02-02 | 3:38 | 49.918
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.92
2020-02-02 | 3:38 | 49.92
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.918
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.92
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.918
2020-02-02 | 3:38 | 49.919
2020-02-02 | 3:38 | 49.92
2020-02-02 | 3:38 | 49.921
2020-02-02 | 3:38 | 49.921
2020-02-02 | 3:38 | 49.921
2020-02-02 | 3:38 | 49.921
2020-02-02 | 3:38 | 49.922
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.925
2020-02-02 | 3:39 | 49.924
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.924
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.923
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.921
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.922
2020-02-02 | 3:39 | 49.92
2020-02-02 | 3:39 | 49.919
2020-02-02 | 3:39 | 49.917
2020-02-02 | 3:39 | 49.914
2020-02-02 | 3:39 | 49.914
2020-02-02 | 3:39 | 49.913
2020-02-02 | 3:39 | 49.912
2020-02-02 | 3:39 | 49.912
2020-02-02 | 3:39 | 49.912
2020-02-02 | 3:39 | 49.912
2020-02-02 | 3:39 | 49.913
2020-02-02 | 3:39 | 49.914
2020-02-02 | 3:39 | 49.913
2020-02-02 | 3:39 | 49.913
2020-02-02 | 3:39 | 49.913
2020-02-02 | 3:39 | 49.912
2020-02-02 | 3:39 | 49.913
2020-02-02 | 3:39 | 49.911
2020-02-02 | 3:39 | 49.91
2020-02-02 | 3:39 | 49.908
2020-02-02 | 3:39 | 49.907
2020-02-02 | 3:39 | 49.906
2020-02-02 | 3:39 | 49.906
2020-02-02 | 3:39 | 49.908
2020-02-02 | 3:39 | 49.91
2020-02-02 | 3:39 | 49.91
2020-02-02 | 3:39 | 49.911
2020-02-02 | 3:39 | 49.911
2020-02-02 | 3:39 | 49.911
2020-02-02 | 3:39 | 49.909
2020-02-02 | 3:39 | 49.905
2020-02-02 | 3:39 | 49.902
2020-02-02 | 3:39 | 49.897
2020-02-02 | 3:39 | 49.895
2020-02-02 | 3:40 | 49.895
2020-02-02 | 3:40 | 49.897
2020-02-02 | 3:40 | 49.899
2020-02-02 | 3:40 | 49.901
2020-02-02 | 3:40 | 49.903
2020-02-02 | 3:40 | 49.905
2020-02-02 | 3:40 | 49.904
2020-02-02 | 3:40 | 49.906
2020-02-02 | 3:40 | 49.906
2020-02-02 | 3:40 | 49.906
2020-02-02 | 3:40 | 49.904
2020-02-02 | 3:40 | 49.902
2020-02-02 | 3:40 | 49.9
2020-02-02 | 3:40 | 49.901
2020-02-02 | 3:40 | 49.898
2020-02-02 | 3:40 | 49.898
2020-02-02 | 3:40 | 49.9
2020-02-02 | 3:40 | 49.903
2020-02-02 | 3:40 | 49.907
2020-02-02 | 3:40 | 49.908
2020-02-02 | 3:40 | 49.909
2020-02-02 | 3:40 | 49.91
2020-02-02 | 3:40 | 49.91
2020-02-02 | 3:40 | 49.911
2020-02-02 | 3:40 | 49.909
2020-02-02 | 3:40 | 49.906
2020-02-02 | 3:40 | 49.903
2020-02-02 | 3:40 | 49.901
2020-02-02 | 3:40 | 49.901
2020-02-02 | 3:40 | 49.906
2020-02-02 | 3:40 | 49.912
2020-02-02 | 3:40 | 49.916
2020-02-02 | 3:40 | 49.921
2020-02-02 | 3:40 | 49.926
2020-02-02 | 3:40 | 49.928
2020-02-02 | 3:40 | 49.927
2020-02-02 | 3:40 | 49.928
2020-02-02 | 3:40 | 49.928
2020-02-02 | 3:40 | 49.927
2020-02-02 | 3:40 | 49.927
2020-02-02 | 3:40 | 49.927
2020-02-02 | 3:40 | 49.925
2020-02-02 | 3:40 | 49.923
2020-02-02 | 3:40 | 49.921
2020-02-02 | 3:40 | 49.921
2020-02-02 | 3:40 | 49.922
2020-02-02 | 3:40 | 49.923
2020-02-02 | 3:40 | 49.923
2020-02-02 | 3:40 | 49.923
2020-02-02 | 3:40 | 49.923
2020-02-02 | 3:40 | 49.924
2020-02-02 | 3:40 | 49.924
2020-02-02 | 3:40 | 49.926
2020-02-02 | 3:40 | 49.926
2020-02-02 | 3:40 | 49.925
2020-02-02 | 3:40 | 49.925
2020-02-02 | 3:40 | 49.926
2020-02-02 | 3:40 | 49.925
2020-02-02 | 3:40 | 49.926
2020-02-02 | 3:40 | 49.927
2020-02-02 | 3:41 | 49.928
2020-02-02 | 3:41 | 49.928
2020-02-02 | 3:41 | 49.928
2020-02-02 | 3:41 | 49.928
2020-02-02 | 3:41 | 49.926
2020-02-02 | 3:41 | 49.926
2020-02-02 | 3:41 | 49.923
2020-02-02 | 3:41 | 49.922
2020-02-02 | 3:41 | 49.921
2020-02-02 | 3:41 | 49.919
2020-02-02 | 3:41 | 49.92
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.917
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.917
2020-02-02 | 3:41 | 49.919
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.919
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.919
2020-02-02 | 3:41 | 49.92
2020-02-02 | 3:41 | 49.921
2020-02-02 | 3:41 | 49.923
2020-02-02 | 3:41 | 49.923
2020-02-02 | 3:41 | 49.923
2020-02-02 | 3:41 | 49.923
2020-02-02 | 3:41 | 49.922
2020-02-02 | 3:41 | 49.921
2020-02-02 | 3:41 | 49.921
2020-02-02 | 3:41 | 49.919
2020-02-02 | 3:41 | 49.917
2020-02-02 | 3:41 | 49.914
2020-02-02 | 3:41 | 49.916
2020-02-02 | 3:41 | 49.915
2020-02-02 | 3:41 | 49.916
2020-02-02 | 3:41 | 49.916
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.921
2020-02-02 | 3:41 | 49.92
2020-02-02 | 3:41 | 49.921
2020-02-02 | 3:41 | 49.922
2020-02-02 | 3:41 | 49.922
2020-02-02 | 3:41 | 49.92
2020-02-02 | 3:41 | 49.92
2020-02-02 | 3:41 | 49.918
2020-02-02 | 3:41 | 49.916
2020-02-02 | 3:41 | 49.913
2020-02-02 | 3:41 | 49.911
2020-02-02 | 3:41 | 49.911
2020-02-02 | 3:41 | 49.91
2020-02-02 | 3:41 | 49.913
2020-02-02 | 3:41 | 49.914
2020-02-02 | 3:41 | 49.917
2020-02-02 | 3:41 | 49.915
2020-02-02 | 3:41 | 49.915
2020-02-02 | 3:41 | 49.914
2020-02-02 | 3:41 | 49.914
2020-02-02 | 3:41 | 49.911
2020-02-02 | 3:42 | 49.91
2020-02-02 | 3:42 | 49.905
2020-02-02 | 3:42 | 49.903
2020-02-02 | 3:42 | 49.902
2020-02-02 | 3:42 | 49.903
2020-02-02 | 3:42 | 49.906
2020-02-02 | 3:42 | 49.908
2020-02-02 | 3:42 | 49.91
2020-02-02 | 3:42 | 49.908
2020-02-02 | 3:42 | 49.904
2020-02-02 | 3:42 | 49.902
2020-02-02 | 3:42 | 49.899
2020-02-02 | 3:42 | 49.895
2020-02-02 | 3:42 | 49.893
2020-02-02 | 3:42 | 49.89
2020-02-02 | 3:42 | 49.889
2020-02-02 | 3:42 | 49.884
2020-02-02 | 3:42 | 49.886
2020-02-02 | 3:42 | 49.884
2020-02-02 | 3:42 | 49.886
2020-02-02 | 3:42 | 49.888
2020-02-02 | 3:42 | 49.892
2020-02-02 | 3:42 | 49.895
2020-02-02 | 3:42 | 49.896
2020-02-02 | 3:42 | 49.9
2020-02-02 | 3:42 | 49.901
2020-02-02 | 3:42 | 49.903
2020-02-02 | 3:42 | 49.905
2020-02-02 | 3:42 | 49.905
2020-02-02 | 3:42 | 49.903
2020-02-02 | 3:42 | 49.902
2020-02-02 | 3:42 | 49.9
2020-02-02 | 3:42 | 49.898
2020-02-02 | 3:42 | 49.898
2020-02-02 | 3:42 | 49.897
2020-02-02 | 3:42 | 49.895
2020-02-02 | 3:42 | 49.894
2020-02-02 | 3:42 | 49.896
2020-02-02 | 3:42 | 49.895
2020-02-02 | 3:42 | 49.896
2020-02-02 | 3:42 | 49.895
2020-02-02 | 3:42 | 49.896
2020-02-02 | 3:42 | 49.899
2020-02-02 | 3:42 | 49.9
2020-02-02 | 3:42 | 49.904
2020-02-02 | 3:42 | 49.904
2020-02-02 | 3:42 | 49.907
2020-02-02 | 3:42 | 49.906
2020-02-02 | 3:42 | 49.906
2020-02-02 | 3:42 | 49.904
2020-02-02 | 3:42 | 49.904
2020-02-02 | 3:42 | 49.903
2020-02-02 | 3:42 | 49.902
2020-02-02 | 3:42 | 49.9
2020-02-02 | 3:42 | 49.897
2020-02-02 | 3:42 | 49.897
2020-02-02 | 3:42 | 49.896
2020-02-02 | 3:42 | 49.895
2020-02-02 | 3:42 | 49.894
2020-02-02 | 3:42 | 49.894
2020-02-02 | 3:43 | 49.895
2020-02-02 | 3:43 | 49.893
2020-02-02 | 3:43 | 49.895
2020-02-02 | 3:43 | 49.894
2020-02-02 | 3:43 | 49.895
2020-02-02 | 3:43 | 49.896
2020-02-02 | 3:43 | 49.896
2020-02-02 | 3:43 | 49.896
2020-02-02 | 3:43 | 49.897
2020-02-02 | 3:43 | 49.898
2020-02-02 | 3:43 | 49.899
2020-02-02 | 3:43 | 49.902
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:43 | 49.907
2020-02-02 | 3:43 | 49.907
2020-02-02 | 3:43 | 49.909
2020-02-02 | 3:43 | 49.908
2020-02-02 | 3:43 | 49.91
2020-02-02 | 3:43 | 49.909
2020-02-02 | 3:43 | 49.909
2020-02-02 | 3:43 | 49.91
2020-02-02 | 3:43 | 49.91
2020-02-02 | 3:43 | 49.907
2020-02-02 | 3:43 | 49.906
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.902
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.901
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.903
2020-02-02 | 3:43 | 49.902
2020-02-02 | 3:43 | 49.902
2020-02-02 | 3:43 | 49.901
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.901
2020-02-02 | 3:43 | 49.901
2020-02-02 | 3:43 | 49.901
2020-02-02 | 3:43 | 49.899
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.899
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.901
2020-02-02 | 3:43 | 49.9
2020-02-02 | 3:43 | 49.899
2020-02-02 | 3:43 | 49.896
2020-02-02 | 3:43 | 49.899
2020-02-02 | 3:43 | 49.902
2020-02-02 | 3:43 | 49.904
2020-02-02 | 3:44 | 49.904
2020-02-02 | 3:44 | 49.905
2020-02-02 | 3:44 | 49.906
2020-02-02 | 3:44 | 49.904
2020-02-02 | 3:44 | 49.904
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.897
2020-02-02 | 3:44 | 49.897
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.901
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.898
2020-02-02 | 3:44 | 49.898
2020-02-02 | 3:44 | 49.894
2020-02-02 | 3:44 | 49.892
2020-02-02 | 3:44 | 49.892
2020-02-02 | 3:44 | 49.892
2020-02-02 | 3:44 | 49.892
2020-02-02 | 3:44 | 49.896
2020-02-02 | 3:44 | 49.898
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.901
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.899
2020-02-02 | 3:44 | 49.897
2020-02-02 | 3:44 | 49.895
2020-02-02 | 3:44 | 49.892
2020-02-02 | 3:44 | 49.891
2020-02-02 | 3:44 | 49.89
2020-02-02 | 3:44 | 49.892
2020-02-02 | 3:44 | 49.894
2020-02-02 | 3:44 | 49.894
2020-02-02 | 3:44 | 49.896
2020-02-02 | 3:44 | 49.894
2020-02-02 | 3:44 | 49.897
2020-02-02 | 3:44 | 49.896
2020-02-02 | 3:44 | 49.897
2020-02-02 | 3:44 | 49.898
2020-02-02 | 3:44 | 49.902
2020-02-02 | 3:44 | 49.901
2020-02-02 | 3:44 | 49.902
2020-02-02 | 3:44 | 49.901
2020-02-02 | 3:44 | 49.901
2020-02-02 | 3:44 | 49.902
2020-02-02 | 3:44 | 49.903
2020-02-02 | 3:44 | 49.905
2020-02-02 | 3:44 | 49.905
2020-02-02 | 3:44 | 49.907
2020-02-02 | 3:44 | 49.906
2020-02-02 | 3:44 | 49.905
2020-02-02 | 3:44 | 49.903
2020-02-02 | 3:44 | 49.9
2020-02-02 | 3:45 | 49.898
2020-02-02 | 3:45 | 49.898
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.9
2020-02-02 | 3:45 | 49.902
2020-02-02 | 3:45 | 49.903
2020-02-02 | 3:45 | 49.902
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.902
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.898
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.9
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.9
2020-02-02 | 3:45 | 49.9
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.897
2020-02-02 | 3:45 | 49.898
2020-02-02 | 3:45 | 49.9
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.9
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.903
2020-02-02 | 3:45 | 49.903
2020-02-02 | 3:45 | 49.904
2020-02-02 | 3:45 | 49.906
2020-02-02 | 3:45 | 49.906
2020-02-02 | 3:45 | 49.907
2020-02-02 | 3:45 | 49.908
2020-02-02 | 3:45 | 49.909
2020-02-02 | 3:45 | 49.909
2020-02-02 | 3:45 | 49.91
2020-02-02 | 3:45 | 49.912
2020-02-02 | 3:45 | 49.913
2020-02-02 | 3:45 | 49.911
2020-02-02 | 3:45 | 49.913
2020-02-02 | 3:45 | 49.912
2020-02-02 | 3:45 | 49.912
2020-02-02 | 3:45 | 49.909
2020-02-02 | 3:45 | 49.909
2020-02-02 | 3:45 | 49.905
2020-02-02 | 3:45 | 49.903
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.898
2020-02-02 | 3:45 | 49.896
2020-02-02 | 3:45 | 49.896
2020-02-02 | 3:45 | 49.898
2020-02-02 | 3:45 | 49.899
2020-02-02 | 3:45 | 49.901
2020-02-02 | 3:45 | 49.903
2020-02-02 | 3:45 | 49.904
2020-02-02 | 3:46 | 49.904
2020-02-02 | 3:46 | 49.903
2020-02-02 | 3:46 | 49.903
2020-02-02 | 3:46 | 49.899
2020-02-02 | 3:46 | 49.898
2020-02-02 | 3:46 | 49.896
2020-02-02 | 3:46 | 49.9
2020-02-02 | 3:46 | 49.9
2020-02-02 | 3:46 | 49.902
2020-02-02 | 3:46 | 49.904
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.905
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.907
2020-02-02 | 3:46 | 49.905
2020-02-02 | 3:46 | 49.902
2020-02-02 | 3:46 | 49.899
2020-02-02 | 3:46 | 49.897
2020-02-02 | 3:46 | 49.896
2020-02-02 | 3:46 | 49.894
2020-02-02 | 3:46 | 49.894
2020-02-02 | 3:46 | 49.896
2020-02-02 | 3:46 | 49.898
2020-02-02 | 3:46 | 49.903
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.907
2020-02-02 | 3:46 | 49.907
2020-02-02 | 3:46 | 49.907
2020-02-02 | 3:46 | 49.909
2020-02-02 | 3:46 | 49.908
2020-02-02 | 3:46 | 49.905
2020-02-02 | 3:46 | 49.9
2020-02-02 | 3:46 | 49.898
2020-02-02 | 3:46 | 49.897
2020-02-02 | 3:46 | 49.894
2020-02-02 | 3:46 | 49.892
2020-02-02 | 3:46 | 49.893
2020-02-02 | 3:46 | 49.892
2020-02-02 | 3:46 | 49.893
2020-02-02 | 3:46 | 49.895
2020-02-02 | 3:46 | 49.896
2020-02-02 | 3:46 | 49.899
2020-02-02 | 3:46 | 49.901
2020-02-02 | 3:46 | 49.9
2020-02-02 | 3:46 | 49.899
2020-02-02 | 3:46 | 49.902
2020-02-02 | 3:46 | 49.901
2020-02-02 | 3:46 | 49.901
2020-02-02 | 3:46 | 49.902
2020-02-02 | 3:46 | 49.903
2020-02-02 | 3:46 | 49.904
2020-02-02 | 3:46 | 49.905
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.905
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.905
2020-02-02 | 3:46 | 49.906
2020-02-02 | 3:46 | 49.907
2020-02-02 | 3:46 | 49.907
2020-02-02 | 3:47 | 49.907
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.906
2020-02-02 | 3:47 | 49.906
2020-02-02 | 3:47 | 49.907
2020-02-02 | 3:47 | 49.904
2020-02-02 | 3:47 | 49.904
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.906
2020-02-02 | 3:47 | 49.906
2020-02-02 | 3:47 | 49.903
2020-02-02 | 3:47 | 49.904
2020-02-02 | 3:47 | 49.904
2020-02-02 | 3:47 | 49.903
2020-02-02 | 3:47 | 49.903
2020-02-02 | 3:47 | 49.904
2020-02-02 | 3:47 | 49.904
2020-02-02 | 3:47 | 49.905
2020-02-02 | 3:47 | 49.906
2020-02-02 | 3:47 | 49.907
2020-02-02 | 3:47 | 49.908
2020-02-02 | 3:47 | 49.909
2020-02-02 | 3:47 | 49.909
2020-02-02 | 3:47 | 49.908
2020-02-02 | 3:47 | 49.908
2020-02-02 | 3:47 | 49.909
2020-02-02 | 3:47 | 49.91
2020-02-02 | 3:47 | 49.91
2020-02-02 | 3:47 | 49.909
2020-02-02 | 3:47 | 49.908
2020-02-02 | 3:47 | 49.909
2020-02-02 | 3:47 | 49.908
2020-02-02 | 3:47 | 49.908
2020-02-02 | 3:47 | 49.909
2020-02-02 | 3:47 | 49.91
2020-02-02 | 3:47 | 49.912
2020-02-02 | 3:47 | 49.913
2020-02-02 | 3:47 | 49.914
2020-02-02 | 3:47 | 49.916
2020-02-02 | 3:47 | 49.917
2020-02-02 | 3:47 | 49.917
2020-02-02 | 3:47 | 49.918
2020-02-02 | 3:47 | 49.916
2020-02-02 | 3:47 | 49.915
2020-02-02 | 3:47 | 49.914
2020-02-02 | 3:47 | 49.912
2020-02-02 | 3:47 | 49.912
2020-02-02 | 3:47 | 49.912
2020-02-02 | 3:47 | 49.913
2020-02-02 | 3:47 | 49.914
2020-02-02 | 3:47 | 49.917
2020-02-02 | 3:47 | 49.917
2020-02-02 | 3:47 | 49.918
2020-02-02 | 3:47 | 49.919
2020-02-02 | 3:48 | 49.919
2020-02-02 | 3:48 | 49.918
2020-02-02 | 3:48 | 49.915
2020-02-02 | 3:48 | 49.912
2020-02-02 | 3:48 | 49.912
2020-02-02 | 3:48 | 49.912
2020-02-02 | 3:48 | 49.915
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.92
2020-02-02 | 3:48 | 49.92
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.922
2020-02-02 | 3:48 | 49.922
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.918
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.916
2020-02-02 | 3:48 | 49.915
2020-02-02 | 3:48 | 49.914
2020-02-02 | 3:48 | 49.916
2020-02-02 | 3:48 | 49.92
2020-02-02 | 3:48 | 49.922
2020-02-02 | 3:48 | 49.925
2020-02-02 | 3:48 | 49.925
2020-02-02 | 3:48 | 49.925
2020-02-02 | 3:48 | 49.925
2020-02-02 | 3:48 | 49.924
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.914
2020-02-02 | 3:48 | 49.912
2020-02-02 | 3:48 | 49.911
2020-02-02 | 3:48 | 49.912
2020-02-02 | 3:48 | 49.912
2020-02-02 | 3:48 | 49.91
2020-02-02 | 3:48 | 49.909
2020-02-02 | 3:48 | 49.91
2020-02-02 | 3:48 | 49.911
2020-02-02 | 3:48 | 49.913
2020-02-02 | 3:48 | 49.913
2020-02-02 | 3:48 | 49.916
2020-02-02 | 3:48 | 49.918
2020-02-02 | 3:48 | 49.918
2020-02-02 | 3:48 | 49.92
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.922
2020-02-02 | 3:48 | 49.921
2020-02-02 | 3:48 | 49.919
2020-02-02 | 3:48 | 49.918
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.916
2020-02-02 | 3:48 | 49.916
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.917
2020-02-02 | 3:48 | 49.918
2020-02-02 | 3:48 | 49.92
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.923
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.923
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.923
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.92
2020-02-02 | 3:49 | 49.92
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.925
2020-02-02 | 3:49 | 49.926
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.93
2020-02-02 | 3:49 | 49.931
2020-02-02 | 3:49 | 49.93
2020-02-02 | 3:49 | 49.931
2020-02-02 | 3:49 | 49.93
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.923
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.92
2020-02-02 | 3:49 | 49.92
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.921
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:49 | 49.923
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.926
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.927
2020-02-02 | 3:49 | 49.926
2020-02-02 | 3:49 | 49.926
2020-02-02 | 3:49 | 49.925
2020-02-02 | 3:49 | 49.925
2020-02-02 | 3:49 | 49.926
2020-02-02 | 3:49 | 49.929
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.928
2020-02-02 | 3:49 | 49.927
2020-02-02 | 3:49 | 49.926
2020-02-02 | 3:49 | 49.925
2020-02-02 | 3:49 | 49.924
2020-02-02 | 3:49 | 49.922
2020-02-02 | 3:50 | 49.921
2020-02-02 | 3:50 | 49.92
2020-02-02 | 3:50 | 49.922
2020-02-02 | 3:50 | 49.924
2020-02-02 | 3:50 | 49.924
2020-02-02 | 3:50 | 49.923
2020-02-02 | 3:50 | 49.922
2020-02-02 | 3:50 | 49.923
2020-02-02 | 3:50 | 49.925
2020-02-02 | 3:50 | 49.926
2020-02-02 | 3:50 | 49.925
2020-02-02 | 3:50 | 49.926
2020-02-02 | 3:50 | 49.924
2020-02-02 | 3:50 | 49.924
2020-02-02 | 3:50 | 49.926
2020-02-02 | 3:50 | 49.927
2020-02-02 | 3:50 | 49.928
2020-02-02 | 3:50 | 49.931
2020-02-02 | 3:50 | 49.936
2020-02-02 | 3:50 | 49.939
2020-02-02 | 3:50 | 49.941
2020-02-02 | 3:50 | 49.943
2020-02-02 | 3:50 | 49.945
2020-02-02 | 3:50 | 49.945
2020-02-02 | 3:50 | 49.945
2020-02-02 | 3:50 | 49.943
2020-02-02 | 3:50 | 49.942
2020-02-02 | 3:50 | 49.941
2020-02-02 | 3:50 | 49.942
2020-02-02 | 3:50 | 49.942
2020-02-02 | 3:50 | 49.942
2020-02-02 | 3:50 | 49.943
2020-02-02 | 3:50 | 49.941
2020-02-02 | 3:50 | 49.942
2020-02-02 | 3:50 | 49.942
2020-02-02 | 3:50 | 49.944
2020-02-02 | 3:50 | 49.944
2020-02-02 | 3:50 | 49.945
2020-02-02 | 3:50 | 49.947
2020-02-02 | 3:50 | 49.949
2020-02-02 | 3:50 | 49.95
2020-02-02 | 3:50 | 49.95
2020-02-02 | 3:50 | 49.951
2020-02-02 | 3:50 | 49.951
2020-02-02 | 3:50 | 49.952
2020-02-02 | 3:50 | 49.951
2020-02-02 | 3:50 | 49.951
2020-02-02 | 3:50 | 49.95
2020-02-02 | 3:50 | 49.95
2020-02-02 | 3:50 | 49.951
2020-02-02 | 3:50 | 49.952
2020-02-02 | 3:50 | 49.953
2020-02-02 | 3:50 | 49.956
2020-02-02 | 3:50 | 49.956
2020-02-02 | 3:50 | 49.957
2020-02-02 | 3:50 | 49.958
2020-02-02 | 3:50 | 49.96
2020-02-02 | 3:50 | 49.959
2020-02-02 | 3:50 | 49.959
2020-02-02 | 3:50 | 49.96
2020-02-02 | 3:51 | 49.959
2020-02-02 | 3:51 | 49.959
2020-02-02 | 3:51 | 49.959
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.957
2020-02-02 | 3:51 | 49.956
2020-02-02 | 3:51 | 49.956
2020-02-02 | 3:51 | 49.956
2020-02-02 | 3:51 | 49.955
2020-02-02 | 3:51 | 49.955
2020-02-02 | 3:51 | 49.956
2020-02-02 | 3:51 | 49.957
2020-02-02 | 3:51 | 49.957
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.957
2020-02-02 | 3:51 | 49.957
2020-02-02 | 3:51 | 49.956
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.959
2020-02-02 | 3:51 | 49.959
2020-02-02 | 3:51 | 49.961
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.961
2020-02-02 | 3:51 | 49.96
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.957
2020-02-02 | 3:51 | 49.956
2020-02-02 | 3:51 | 49.958
2020-02-02 | 3:51 | 49.959
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.963
2020-02-02 | 3:51 | 49.964
2020-02-02 | 3:51 | 49.965
2020-02-02 | 3:51 | 49.967
2020-02-02 | 3:51 | 49.967
2020-02-02 | 3:51 | 49.965
2020-02-02 | 3:51 | 49.962
2020-02-02 | 3:51 | 49.963
2020-02-02 | 3:51 | 49.964
2020-02-02 | 3:51 | 49.968
2020-02-02 | 3:51 | 49.971
2020-02-02 | 3:51 | 49.972
2020-02-02 | 3:51 | 49.974
2020-02-02 | 3:51 | 49.975
2020-02-02 | 3:51 | 49.975
2020-02-02 | 3:51 | 49.975
2020-02-02 | 3:51 | 49.975
2020-02-02 | 3:51 | 49.972
2020-02-02 | 3:51 | 49.967
2020-02-02 | 3:51 | 49.963
2020-02-02 | 3:52 | 49.961
2020-02-02 | 3:52 | 49.959
2020-02-02 | 3:52 | 49.96
2020-02-02 | 3:52 | 49.962
2020-02-02 | 3:52 | 49.965
2020-02-02 | 3:52 | 49.969
2020-02-02 | 3:52 | 49.971
2020-02-02 | 3:52 | 49.972
2020-02-02 | 3:52 | 49.973
2020-02-02 | 3:52 | 49.974
2020-02-02 | 3:52 | 49.973
2020-02-02 | 3:52 | 49.972
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.969
2020-02-02 | 3:52 | 49.967
2020-02-02 | 3:52 | 49.966
2020-02-02 | 3:52 | 49.964
2020-02-02 | 3:52 | 49.964
2020-02-02 | 3:52 | 49.962
2020-02-02 | 3:52 | 49.961
2020-02-02 | 3:52 | 49.962
2020-02-02 | 3:52 | 49.963
2020-02-02 | 3:52 | 49.966
2020-02-02 | 3:52 | 49.967
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.972
2020-02-02 | 3:52 | 49.973
2020-02-02 | 3:52 | 49.974
2020-02-02 | 3:52 | 49.975
2020-02-02 | 3:52 | 49.975
2020-02-02 | 3:52 | 49.974
2020-02-02 | 3:52 | 49.972
2020-02-02 | 3:52 | 49.967
2020-02-02 | 3:52 | 49.963
2020-02-02 | 3:52 | 49.961
2020-02-02 | 3:52 | 49.96
2020-02-02 | 3:52 | 49.959
2020-02-02 | 3:52 | 49.959
2020-02-02 | 3:52 | 49.959
2020-02-02 | 3:52 | 49.961
2020-02-02 | 3:52 | 49.963
2020-02-02 | 3:52 | 49.964
2020-02-02 | 3:52 | 49.967
2020-02-02 | 3:52 | 49.968
2020-02-02 | 3:52 | 49.969
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.969
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.97
2020-02-02 | 3:52 | 49.971
2020-02-02 | 3:52 | 49.971
2020-02-02 | 3:52 | 49.971
2020-02-02 | 3:52 | 49.973
2020-02-02 | 3:52 | 49.974
2020-02-02 | 3:52 | 49.974
2020-02-02 | 3:53 | 49.973
2020-02-02 | 3:53 | 49.972
2020-02-02 | 3:53 | 49.972
2020-02-02 | 3:53 | 49.969
2020-02-02 | 3:53 | 49.967
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.967
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.967
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.967
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.964
2020-02-02 | 3:53 | 49.964
2020-02-02 | 3:53 | 49.964
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.962
2020-02-02 | 3:53 | 49.957
2020-02-02 | 3:53 | 49.956
2020-02-02 | 3:53 | 49.956
2020-02-02 | 3:53 | 49.958
2020-02-02 | 3:53 | 49.963
2020-02-02 | 3:53 | 49.964
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.969
2020-02-02 | 3:53 | 49.969
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.964
2020-02-02 | 3:53 | 49.963
2020-02-02 | 3:53 | 49.96
2020-02-02 | 3:53 | 49.957
2020-02-02 | 3:53 | 49.957
2020-02-02 | 3:53 | 49.958
2020-02-02 | 3:53 | 49.96
2020-02-02 | 3:53 | 49.963
2020-02-02 | 3:53 | 49.965
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.969
2020-02-02 | 3:53 | 49.971
2020-02-02 | 3:53 | 49.968
2020-02-02 | 3:53 | 49.966
2020-02-02 | 3:54 | 49.963
2020-02-02 | 3:54 | 49.961
2020-02-02 | 3:54 | 49.96
2020-02-02 | 3:54 | 49.958
2020-02-02 | 3:54 | 49.958
2020-02-02 | 3:54 | 49.957
2020-02-02 | 3:54 | 49.957
2020-02-02 | 3:54 | 49.958
2020-02-02 | 3:54 | 49.959
2020-02-02 | 3:54 | 49.959
2020-02-02 | 3:54 | 49.96
2020-02-02 | 3:54 | 49.962
2020-02-02 | 3:54 | 49.965
2020-02-02 | 3:54 | 49.966
2020-02-02 | 3:54 | 49.967
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.969
2020-02-02 | 3:54 | 49.97
2020-02-02 | 3:54 | 49.97
2020-02-02 | 3:54 | 49.969
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.969
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.967
2020-02-02 | 3:54 | 49.966
2020-02-02 | 3:54 | 49.964
2020-02-02 | 3:54 | 49.964
2020-02-02 | 3:54 | 49.963
2020-02-02 | 3:54 | 49.963
2020-02-02 | 3:54 | 49.962
2020-02-02 | 3:54 | 49.962
2020-02-02 | 3:54 | 49.962
2020-02-02 | 3:54 | 49.963
2020-02-02 | 3:54 | 49.965
2020-02-02 | 3:54 | 49.966
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.968
2020-02-02 | 3:54 | 49.969
2020-02-02 | 3:54 | 49.97
2020-02-02 | 3:54 | 49.972
2020-02-02 | 3:54 | 49.974
2020-02-02 | 3:54 | 49.975
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.977
2020-02-02 | 3:54 | 49.978
2020-02-02 | 3:54 | 49.977
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.977
2020-02-02 | 3:54 | 49.976
2020-02-02 | 3:54 | 49.977
2020-02-02 | 3:54 | 49.978
2020-02-02 | 3:54 | 49.98
2020-02-02 | 3:54 | 49.982
2020-02-02 | 3:54 | 49.984
2020-02-02 | 3:54 | 49.986
2020-02-02 | 3:55 | 49.984
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.984
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.982
2020-02-02 | 3:55 | 49.98
2020-02-02 | 3:55 | 49.979
2020-02-02 | 3:55 | 49.978
2020-02-02 | 3:55 | 49.978
2020-02-02 | 3:55 | 49.981
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.984
2020-02-02 | 3:55 | 49.981
2020-02-02 | 3:55 | 49.979
2020-02-02 | 3:55 | 49.977
2020-02-02 | 3:55 | 49.978
2020-02-02 | 3:55 | 49.981
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.985
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.987
2020-02-02 | 3:55 | 49.987
2020-02-02 | 3:55 | 49.984
2020-02-02 | 3:55 | 49.98
2020-02-02 | 3:55 | 49.977
2020-02-02 | 3:55 | 49.974
2020-02-02 | 3:55 | 49.973
2020-02-02 | 3:55 | 49.971
2020-02-02 | 3:55 | 49.971
2020-02-02 | 3:55 | 49.972
2020-02-02 | 3:55 | 49.977
2020-02-02 | 3:55 | 49.978
2020-02-02 | 3:55 | 49.981
2020-02-02 | 3:55 | 49.984
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.988
2020-02-02 | 3:55 | 49.991
2020-02-02 | 3:55 | 49.991
2020-02-02 | 3:55 | 49.99
2020-02-02 | 3:55 | 49.988
2020-02-02 | 3:55 | 49.985
2020-02-02 | 3:55 | 49.985
2020-02-02 | 3:55 | 49.982
2020-02-02 | 3:55 | 49.983
2020-02-02 | 3:55 | 49.982
2020-02-02 | 3:55 | 49.982
2020-02-02 | 3:55 | 49.985
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.986
2020-02-02 | 3:55 | 49.989
2020-02-02 | 3:55 | 49.99
2020-02-02 | 3:56 | 49.993
2020-02-02 | 3:56 | 49.994
2020-02-02 | 3:56 | 49.994
2020-02-02 | 3:56 | 49.994
2020-02-02 | 3:56 | 49.993
2020-02-02 | 3:56 | 49.991
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.986
2020-02-02 | 3:56 | 49.984
2020-02-02 | 3:56 | 49.983
2020-02-02 | 3:56 | 49.983
2020-02-02 | 3:56 | 49.985
2020-02-02 | 3:56 | 49.987
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.99
2020-02-02 | 3:56 | 49.992
2020-02-02 | 3:56 | 49.993
2020-02-02 | 3:56 | 49.996
2020-02-02 | 3:56 | 49.996
2020-02-02 | 3:56 | 49.996
2020-02-02 | 3:56 | 49.995
2020-02-02 | 3:56 | 49.992
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.985
2020-02-02 | 3:56 | 49.984
2020-02-02 | 3:56 | 49.985
2020-02-02 | 3:56 | 49.984
2020-02-02 | 3:56 | 49.986
2020-02-02 | 3:56 | 49.987
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.987
2020-02-02 | 3:56 | 49.99
2020-02-02 | 3:56 | 49.992
2020-02-02 | 3:56 | 49.993
2020-02-02 | 3:56 | 49.994
2020-02-02 | 3:56 | 49.992
2020-02-02 | 3:56 | 49.991
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.99
2020-02-02 | 3:56 | 49.992
2020-02-02 | 3:56 | 49.993
2020-02-02 | 3:56 | 49.994
2020-02-02 | 3:56 | 49.993
2020-02-02 | 3:56 | 49.992
2020-02-02 | 3:56 | 49.991
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.988
2020-02-02 | 3:56 | 49.986
2020-02-02 | 3:56 | 49.984
2020-02-02 | 3:56 | 49.984
2020-02-02 | 3:56 | 49.984
2020-02-02 | 3:56 | 49.985
2020-02-02 | 3:56 | 49.987
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.989
2020-02-02 | 3:56 | 49.987
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.986
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.983
2020-02-02 | 3:57 | 49.98
2020-02-02 | 3:57 | 49.978
2020-02-02 | 3:57 | 49.977
2020-02-02 | 3:57 | 49.979
2020-02-02 | 3:57 | 49.981
2020-02-02 | 3:57 | 49.982
2020-02-02 | 3:57 | 49.984
2020-02-02 | 3:57 | 49.986
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.988
2020-02-02 | 3:57 | 49.988
2020-02-02 | 3:57 | 49.988
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.986
2020-02-02 | 3:57 | 49.984
2020-02-02 | 3:57 | 49.982
2020-02-02 | 3:57 | 49.982
2020-02-02 | 3:57 | 49.982
2020-02-02 | 3:57 | 49.983
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.986
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.982
2020-02-02 | 3:57 | 49.98
2020-02-02 | 3:57 | 49.978
2020-02-02 | 3:57 | 49.978
2020-02-02 | 3:57 | 49.978
2020-02-02 | 3:57 | 49.978
2020-02-02 | 3:57 | 49.978
2020-02-02 | 3:57 | 49.98
2020-02-02 | 3:57 | 49.981
2020-02-02 | 3:57 | 49.983
2020-02-02 | 3:57 | 49.985
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.988
2020-02-02 | 3:57 | 49.991
2020-02-02 | 3:57 | 49.992
2020-02-02 | 3:57 | 49.994
2020-02-02 | 3:57 | 49.995
2020-02-02 | 3:57 | 49.996
2020-02-02 | 3:57 | 49.995
2020-02-02 | 3:57 | 49.992
2020-02-02 | 3:57 | 49.99
2020-02-02 | 3:57 | 49.988
2020-02-02 | 3:57 | 49.986
2020-02-02 | 3:57 | 49.986
2020-02-02 | 3:57 | 49.987
2020-02-02 | 3:57 | 49.989
2020-02-02 | 3:57 | 49.989
2020-02-02 | 3:57 | 49.992
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.99
2020-02-02 | 3:58 | 49.99
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.99
2020-02-02 | 3:58 | 49.988
2020-02-02 | 3:58 | 49.987
2020-02-02 | 3:58 | 49.987
2020-02-02 | 3:58 | 49.987
2020-02-02 | 3:58 | 49.988
2020-02-02 | 3:58 | 49.989
2020-02-02 | 3:58 | 49.99
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.994
2020-02-02 | 3:58 | 49.994
2020-02-02 | 3:58 | 49.994
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.994
2020-02-02 | 3:58 | 49.995
2020-02-02 | 3:58 | 49.995
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.995
2020-02-02 | 3:58 | 49.995
2020-02-02 | 3:58 | 49.995
2020-02-02 | 3:58 | 49.993
2020-02-02 | 3:58 | 49.99
2020-02-02 | 3:58 | 49.987
2020-02-02 | 3:58 | 49.984
2020-02-02 | 3:58 | 49.981
2020-02-02 | 3:58 | 49.979
2020-02-02 | 3:58 | 49.982
2020-02-02 | 3:58 | 49.986
2020-02-02 | 3:58 | 49.988
2020-02-02 | 3:58 | 49.99
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.991
2020-02-02 | 3:58 | 49.992
2020-02-02 | 3:58 | 49.994
2020-02-02 | 3:58 | 49.994
2020-02-02 | 3:59 | 49.992
2020-02-02 | 3:59 | 49.989
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.986
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.989
2020-02-02 | 3:59 | 49.991
2020-02-02 | 3:59 | 49.995
2020-02-02 | 3:59 | 49.998
2020-02-02 | 3:59 | 49.999
2020-02-02 | 3:59 | 50
2020-02-02 | 3:59 | 50
2020-02-02 | 3:59 | 49.997
2020-02-02 | 3:59 | 49.994
2020-02-02 | 3:59 | 49.99
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.984
2020-02-02 | 3:59 | 49.983
2020-02-02 | 3:59 | 49.986
2020-02-02 | 3:59 | 49.989
2020-02-02 | 3:59 | 49.99
2020-02-02 | 3:59 | 49.991
2020-02-02 | 3:59 | 49.991
2020-02-02 | 3:59 | 49.993
2020-02-02 | 3:59 | 49.993
2020-02-02 | 3:59 | 49.994
2020-02-02 | 3:59 | 49.994
2020-02-02 | 3:59 | 49.994
2020-02-02 | 3:59 | 49.993
2020-02-02 | 3:59 | 49.992
2020-02-02 | 3:59 | 49.991
2020-02-02 | 3:59 | 49.988
2020-02-02 | 3:59 | 49.985
2020-02-02 | 3:59 | 49.983
2020-02-02 | 3:59 | 49.984
2020-02-02 | 3:59 | 49.985
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.987
2020-02-02 | 3:59 | 49.989
2020-02-02 | 3:59 | 49.99
2020-02-02 | 3:59 | 49.992
2020-02-02 | 3:59 | 49.994
2020-02-02 | 3:59 | 49.995
2020-02-02 | 3:59 | 49.996
2020-02-02 | 3:59 | 49.999
2020-02-02 | 3:59 | 50.006
2020-02-02 | 3:59 | 50.012
2020-02-02 | 3:59 | 50.016
2020-02-02 | 3:59 | 50.018
2020-02-02 | 3:59 | 50.018
2020-02-02 | 3:59 | 50.021
2020-02-02 | 3:59 | 50.023
2020-02-02 | 3:59 | 50.024
2020-02-02 | 3:59 | 50.024
2020-02-02 | 3:59 | 50.024
2020-02-02 | 3:59 | 50.024
2020-02-02 | 3:59 | 50.026
2020-02-02 | 4:00 | 50.026
2020-02-02 | 4:00 | 50.027
2020-02-02 | 4:00 | 50.026
2020-02-02 | 4:00 | 50.026
2020-02-02 | 4:00 | 50.025
2020-02-02 | 4:00 | 50.024
2020-02-02 | 4:00 | 50.022
2020-02-02 | 4:00 | 50.021
2020-02-02 | 4:00 | 50.018
2020-02-02 | 4:00 | 50.014
2020-02-02 | 4:00 | 50.01
2020-02-02 | 4:00 | 50.005
2020-02-02 | 4:00 | 49.999
2020-02-02 | 4:00 | 49.994
2020-02-02 | 4:00 | 49.99
2020-02-02 | 4:00 | 49.984
2020-02-02 | 4:00 | 49.981
2020-02-02 | 4:00 | 49.98
2020-02-02 | 4:00 | 49.982
2020-02-02 | 4:00 | 49.985
2020-02-02 | 4:00 | 49.987
2020-02-02 | 4:00 | 49.988
2020-02-02 | 4:00 | 49.989
2020-02-02 | 4:00 | 49.991
2020-02-02 | 4:00 | 49.991
2020-02-02 | 4:00 | 49.992
2020-02-02 | 4:00 | 49.993
2020-02-02 | 4:00 | 49.994
2020-02-02 | 4:00 | 49.994
2020-02-02 | 4:00 | 49.995

## Event 20200209-1
In UTC
Date | Time | Freq
2020-02-09 | 8:56 | 50.035
2020-02-09 | 8:56 | 50.032
2020-02-09 | 8:56 | 50.035
2020-02-09 | 8:56 | 50.035
2020-02-09 | 8:56 | 50.038
2020-02-09 | 8:56 | 50.043
2020-02-09 | 8:56 | 50.044
2020-02-09 | 8:56 | 50.047
2020-02-09 | 8:56 | 50.048
2020-02-09 | 8:56 | 50.052
2020-02-09 | 8:56 | 50.049
2020-02-09 | 8:56 | 50.05
2020-02-09 | 8:56 | 50.049
2020-02-09 | 8:56 | 50.048
2020-02-09 | 8:56 | 50.046
2020-02-09 | 8:56 | 50.042
2020-02-09 | 8:56 | 50.04
2020-02-09 | 8:56 | 50.044
2020-02-09 | 8:56 | 50.043
2020-02-09 | 8:56 | 50.044
2020-02-09 | 8:56 | 50.046
2020-02-09 | 8:56 | 50.051
2020-02-09 | 8:56 | 50.054
2020-02-09 | 8:56 | 50.058
2020-02-09 | 8:56 | 50.055
2020-02-09 | 8:56 | 50.055
2020-02-09 | 8:56 | 50.054
2020-02-09 | 8:56 | 50.05
2020-02-09 | 8:56 | 50.05
2020-02-09 | 8:56 | 50.042
2020-02-09 | 8:56 | 50.04
2020-02-09 | 8:57 | 50.043
2020-02-09 | 8:57 | 50.047
2020-02-09 | 8:57 | 50.048
2020-02-09 | 8:57 | 50.049
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.05
2020-02-09 | 8:57 | 50.052
2020-02-09 | 8:57 | 50.053
2020-02-09 | 8:57 | 50.054
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.052
2020-02-09 | 8:57 | 50.05
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.055
2020-02-09 | 8:57 | 50.057
2020-02-09 | 8:57 | 50.055
2020-02-09 | 8:57 | 50.049
2020-02-09 | 8:57 | 50.056
2020-02-09 | 8:57 | 50.062
2020-02-09 | 8:57 | 50.064
2020-02-09 | 8:57 | 50.067
2020-02-09 | 8:57 | 50.061
2020-02-09 | 8:57 | 50.062
2020-02-09 | 8:57 | 50.062
2020-02-09 | 8:57 | 50.06
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.06
2020-02-09 | 8:57 | 50.059
2020-02-09 | 8:57 | 50.059
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.059
2020-02-09 | 8:57 | 50.059
2020-02-09 | 8:57 | 50.059
2020-02-09 | 8:57 | 50.058
2020-02-09 | 8:57 | 50.059
2020-02-09 | 8:57 | 50.057
2020-02-09 | 8:57 | 50.058
2020-02-09 | 8:57 | 50.057
2020-02-09 | 8:57 | 50.054
2020-02-09 | 8:57 | 50.055
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.054
2020-02-09 | 8:57 | 50.054
2020-02-09 | 8:57 | 50.054
2020-02-09 | 8:57 | 50.055
2020-02-09 | 8:57 | 50.052
2020-02-09 | 8:57 | 50.051
2020-02-09 | 8:57 | 50.05
2020-02-09 | 8:57 | 50.047
2020-02-09 | 8:57 | 50.044
2020-02-09 | 8:57 | 50.042
2020-02-09 | 8:57 | 50.038
2020-02-09 | 8:57 | 50.035
2020-02-09 | 8:57 | 50.037
2020-02-09 | 8:57 | 50.038
2020-02-09 | 8:57 | 50.036
2020-02-09 | 8:57 | 50.038
2020-02-09 | 8:57 | 50.038
2020-02-09 | 8:57 | 50.035
2020-02-09 | 8:58 | 50.031
2020-02-09 | 8:58 | 50.028
2020-02-09 | 8:58 | 50.027
2020-02-09 | 8:58 | 50.025
2020-02-09 | 8:58 | 49.979
2020-02-09 | 8:58 | 49.905
2020-02-09 | 8:58 | 49.871
2020-02-09 | 8:58 | 49.853
2020-02-09 | 8:58 | 49.833
2020-02-09 | 8:58 | 49.83
2020-02-09 | 8:58 | 49.799
2020-02-09 | 8:58 | 49.804
2020-02-09 | 8:58 | 49.801
2020-02-09 | 8:58 | 49.786
2020-02-09 | 8:58 | 49.784
2020-02-09 | 8:58 | 49.775
2020-02-09 | 8:58 | 49.78
2020-02-09 | 8:58 | 49.778
2020-02-09 | 8:58 | 49.773
2020-02-09 | 8:58 | 49.769
2020-02-09 | 8:58 | 49.76
2020-02-09 | 8:58 | 49.762
2020-02-09 | 8:58 | 49.756
2020-02-09 | 8:58 | 49.748
2020-02-09 | 8:58 | 49.754
2020-02-09 | 8:58 | 49.748
2020-02-09 | 8:58 | 49.752
2020-02-09 | 8:58 | 49.744
2020-02-09 | 8:58 | 49.744
2020-02-09 | 8:58 | 49.733
2020-02-09 | 8:58 | 49.747
2020-02-09 | 8:58 | 49.744
2020-02-09 | 8:58 | 49.733
2020-02-09 | 8:58 | 49.748
2020-02-09 | 8:58 | 49.735
2020-02-09 | 8:58 | 49.72
2020-02-09 | 8:58 | 49.704
2020-02-09 | 8:58 | 49.707
2020-02-09 | 8:58 | 49.696
2020-02-09 | 8:58 | 49.681
2020-02-09 | 8:58 | 49.659
2020-02-09 | 8:58 | 49.645
2020-02-09 | 8:58 | 49.631
2020-02-09 | 8:58 | 49.615
2020-02-09 | 8:58 | 49.601
2020-02-09 | 8:58 | 49.594
2020-02-09 | 8:58 | 49.594
2020-02-09 | 8:58 | 49.583
2020-02-09 | 8:58 | 49.581
2020-02-09 | 8:58 | 49.583
2020-02-09 | 8:58 | 49.574
2020-02-09 | 8:58 | 49.578
2020-02-09 | 8:58 | 49.578
2020-02-09 | 8:58 | 49.578
2020-02-09 | 8:58 | 49.581
2020-02-09 | 8:58 | 49.585
2020-02-09 | 8:58 | 49.578
2020-02-09 | 8:58 | 49.581
2020-02-09 | 8:58 | 49.589
2020-02-09 | 8:58 | 49.58
2020-02-09 | 8:58 | 49.584
2020-02-09 | 8:59 | 49.596
2020-02-09 | 8:59 | 49.594
2020-02-09 | 8:59 | 49.61
2020-02-09 | 8:59 | 49.611
2020-02-09 | 8:59 | 49.633
2020-02-09 | 8:59 | 49.625
2020-02-09 | 8:59 | 49.628
2020-02-09 | 8:59 | 49.627
2020-02-09 | 8:59 | 49.623
2020-02-09 | 8:59 | 49.639
2020-02-09 | 8:59 | 49.632
2020-02-09 | 8:59 | 49.634
2020-02-09 | 8:59 | 49.641
2020-02-09 | 8:59 | 49.638
2020-02-09 | 8:59 | 49.639
2020-02-09 | 8:59 | 49.649
2020-02-09 | 8:59 | 49.648
2020-02-09 | 8:59 | 49.65
2020-02-09 | 8:59 | 49.647
2020-02-09 | 8:59 | 49.644
2020-02-09 | 8:59 | 49.65
2020-02-09 | 8:59 | 49.651
2020-02-09 | 8:59 | 49.637
2020-02-09 | 8:59 | 49.646
2020-02-09 | 8:59 | 49.646
2020-02-09 | 8:59 | 49.647
2020-02-09 | 8:59 | 49.639
2020-02-09 | 8:59 | 49.645
2020-02-09 | 8:59 | 49.647
2020-02-09 | 8:59 | 49.631
2020-02-09 | 8:59 | 49.637
2020-02-09 | 8:59 | 49.642
2020-02-09 | 8:59 | 49.622
2020-02-09 | 8:59 | 49.633
2020-02-09 | 8:59 | 49.637
2020-02-09 | 8:59 | 49.625
2020-02-09 | 8:59 | 49.64
2020-02-09 | 8:59 | 49.646
2020-02-09 | 8:59 | 49.643
2020-02-09 | 8:59 | 49.642
2020-02-09 | 8:59 | 49.651
2020-02-09 | 8:59 | 49.648
2020-02-09 | 8:59 | 49.643
2020-02-09 | 8:59 | 49.656
2020-02-09 | 8:59 | 49.673
2020-02-09 | 8:59 | 49.67
2020-02-09 | 8:59 | 49.678
2020-02-09 | 8:59 | 49.687
2020-02-09 | 8:59 | 49.696
2020-02-09 | 8:59 | 49.709
2020-02-09 | 8:59 | 49.723
2020-02-09 | 8:59 | 49.727
2020-02-09 | 8:59 | 49.747
2020-02-09 | 8:59 | 49.757
2020-02-09 | 8:59 | 49.754
2020-02-09 | 8:59 | 49.776
2020-02-09 | 8:59 | 49.776
2020-02-09 | 8:59 | 49.795
2020-02-09 | 8:59 | 49.807
2020-02-09 | 9:00 | 49.803
2020-02-09 | 9:00 | 49.821
2020-02-09 | 9:00 | 49.827
2020-02-09 | 9:00 | 49.839
2020-02-09 | 9:00 | 49.856
2020-02-09 | 9:00 | 49.857
2020-02-09 | 9:00 | 49.862
2020-02-09 | 9:00 | 49.866
2020-02-09 | 9:00 | 49.874
2020-02-09 | 9:00 | 49.863
2020-02-09 | 9:00 | 49.864
2020-02-09 | 9:00 | 49.865
2020-02-09 | 9:00 | 49.867
2020-02-09 | 9:00 | 49.869
2020-02-09 | 9:00 | 49.872
2020-02-09 | 9:00 | 49.872
2020-02-09 | 9:00 | 49.87
2020-02-09 | 9:00 | 49.871
2020-02-09 | 9:00 | 49.873
2020-02-09 | 9:00 | 49.88
2020-02-09 | 9:00 | 49.89
2020-02-09 | 9:00 | 49.876
2020-02-09 | 9:00 | 49.883
2020-02-09 | 9:00 | 49.885
2020-02-09 | 9:00 | 49.88
2020-02-09 | 9:00 | 49.885
2020-02-09 | 9:00 | 49.896
2020-02-09 | 9:00 | 49.887
2020-02-09 | 9:00 | 49.893
2020-02-09 | 9:00 | 49.892
2020-02-09 | 9:00 | 49.885
2020-02-09 | 9:00 | 49.896
2020-02-09 | 9:00 | 49.884
2020-02-09 | 9:00 | 49.89
2020-02-09 | 9:00 | 49.894
2020-02-09 | 9:00 | 49.891
2020-02-09 | 9:00 | 49.906
2020-02-09 | 9:00 | 49.893
2020-02-09 | 9:00 | 49.901
2020-02-09 | 9:00 | 49.895
2020-02-09 | 9:00 | 49.912
2020-02-09 | 9:00 | 49.904
2020-02-09 | 9:00 | 49.906
2020-02-09 | 9:00 | 49.905
2020-02-09 | 9:00 | 49.906
2020-02-09 | 9:00 | 49.911
2020-02-09 | 9:00 | 49.903
2020-02-09 | 9:00 | 49.907
2020-02-09 | 9:00 | 49.914
2020-02-09 | 9:00 | 49.91
2020-02-09 | 9:00 | 49.912
2020-02-09 | 9:00 | 49.92
2020-02-09 | 9:00 | 49.913
2020-02-09 | 9:00 | 49.92
2020-02-09 | 9:00 | 49.922
2020-02-09 | 9:00 | 49.924
2020-02-09 | 9:00 | 49.933
2020-02-09 | 9:00 | 49.946
2020-02-09 | 9:00 | 49.938
2020-02-09 | 9:00 | 49.942
2020-02-09 | 9:00 | 49.942
2020-02-09 | 9:01 | 49.952
2020-02-09 | 9:01 | 49.943
2020-02-09 | 9:01 | 49.955
2020-02-09 | 9:01 | 49.945
2020-02-09 | 9:01 | 49.943
2020-02-09 | 9:01 | 49.944
2020-02-09 | 9:01 | 49.945
2020-02-09 | 9:01 | 49.948
2020-02-09 | 9:01 | 49.948
2020-02-09 | 9:01 | 49.955
2020-02-09 | 9:01 | 49.959
2020-02-09 | 9:01 | 49.968
2020-02-09 | 9:01 | 49.966
2020-02-09 | 9:01 | 49.97
2020-02-09 | 9:01 | 49.97
2020-02-09 | 9:01 | 49.975
2020-02-09 | 9:01 | 49.978
2020-02-09 | 9:01 | 49.974
2020-02-09 | 9:01 | 49.97
2020-02-09 | 9:01 | 49.976
2020-02-09 | 9:01 | 49.975
2020-02-09 | 9:01 | 49.973
2020-02-09 | 9:01 | 49.974
2020-02-09 | 9:01 | 49.978
2020-02-09 | 9:01 | 49.975
2020-02-09 | 9:01 | 49.974
2020-02-09 | 9:01 | 49.981
2020-02-09 | 9:01 | 49.981
2020-02-09 | 9:01 | 49.979
2020-02-09 | 9:01 | 49.98
2020-02-09 | 9:01 | 49.982
2020-02-09 | 9:01 | 49.982
2020-02-09 | 9:01 | 49.981
2020-02-09 | 9:01 | 49.979
2020-02-09 | 9:01 | 49.982
2020-02-09 | 9:01 | 49.982
2020-02-09 | 9:01 | 49.983
2020-02-09 | 9:01 | 49.992
2020-02-09 | 9:01 | 49.98
2020-02-09 | 9:01 | 49.981
2020-02-09 | 9:01 | 49.979
2020-02-09 | 9:01 | 49.978
2020-02-09 | 9:01 | 49.98
2020-02-09 | 9:01 | 49.98
2020-02-09 | 9:01 | 49.98
2020-02-09 | 9:01 | 49.991
2020-02-09 | 9:01 | 49.983
2020-02-09 | 9:01 | 49.987
2020-02-09 | 9:01 | 49.985
2020-02-09 | 9:01 | 49.985
2020-02-09 | 9:01 | 49.987
2020-02-09 | 9:01 | 49.992
2020-02-09 | 9:01 | 49.996
2020-02-09 | 9:01 | 50
2020-02-09 | 9:01 | 50.004
2020-02-09 | 9:01 | 50.008
2020-02-09 | 9:01 | 50.01
2020-02-09 | 9:01 | 50.01
2020-02-09 | 9:01 | 50.008
2020-02-09 | 9:02 | 50.008
2020-02-09 | 9:02 | 50.011
2020-02-09 | 9:02 | 50.012
2020-02-09 | 9:02 | 50.015
2020-02-09 | 9:02 | 50.016
2020-02-09 | 9:02 | 50.017
2020-02-09 | 9:02 | 50.017
2020-02-09 | 9:02 | 50.019
2020-02-09 | 9:02 | 50.02
2020-02-09 | 9:02 | 50.023
2020-02-09 | 9:02 | 50.027
2020-02-09 | 9:02 | 50.028
2020-02-09 | 9:02 | 50.032
2020-02-09 | 9:02 | 50.035
2020-02-09 | 9:02 | 50.039
2020-02-09 | 9:02 | 50.044
2020-02-09 | 9:02 | 50.044
2020-02-09 | 9:02 | 50.052
2020-02-09 | 9:02 | 50.05
2020-02-09 | 9:02 | 50.054
2020-02-09 | 9:02 | 50.058
2020-02-09 | 9:02 | 50.058
2020-02-09 | 9:02 | 50.057
2020-02-09 | 9:02 | 50.064
2020-02-09 | 9:02 | 50.066
2020-02-09 | 9:02 | 50.067
2020-02-09 | 9:02 | 50.061
2020-02-09 | 9:02 | 50.067
2020-02-09 | 9:02 | 50.069
2020-02-09 | 9:02 | 50.077

## Event 20200209-2
In UTC
Date | Time | Freq
2020-02-09 | 9:31 | 49.831
2020-02-09 | 9:31 | 49.836
2020-02-09 | 9:31 | 49.844
2020-02-09 | 9:31 | 49.848
2020-02-09 | 9:31 | 49.848
2020-02-09 | 9:31 | 49.853
2020-02-09 | 9:31 | 49.855
2020-02-09 | 9:31 | 49.858
2020-02-09 | 9:31 | 49.857
2020-02-09 | 9:31 | 49.858
2020-02-09 | 9:31 | 49.858
2020-02-09 | 9:31 | 49.857
2020-02-09 | 9:31 | 49.854
2020-02-09 | 9:31 | 49.853
2020-02-09 | 9:31 | 49.847
2020-02-09 | 9:31 | 49.845
2020-02-09 | 9:31 | 49.845
2020-02-09 | 9:31 | 49.844
2020-02-09 | 9:31 | 49.847
2020-02-09 | 9:31 | 49.846
2020-02-09 | 9:31 | 49.847
2020-02-09 | 9:31 | 49.846
2020-02-09 | 9:31 | 49.845
2020-02-09 | 9:31 | 49.844
2020-02-09 | 9:31 | 49.846
2020-02-09 | 9:31 | 49.844
2020-02-09 | 9:31 | 49.842
2020-02-09 | 9:31 | 49.847
2020-02-09 | 9:31 | 49.843
2020-02-09 | 9:31 | 49.851
2020-02-09 | 9:32 | 49.837
2020-02-09 | 9:32 | 49.835
2020-02-09 | 9:32 | 49.834
2020-02-09 | 9:32 | 49.836
2020-02-09 | 9:32 | 49.841
2020-02-09 | 9:32 | 49.842
2020-02-09 | 9:32 | 49.839
2020-02-09 | 9:32 | 49.835
2020-02-09 | 9:32 | 49.846
2020-02-09 | 9:32 | 49.838
2020-02-09 | 9:32 | 49.822
2020-02-09 | 9:32 | 49.825
2020-02-09 | 9:32 | 49.832
2020-02-09 | 9:32 | 49.829
2020-02-09 | 9:32 | 49.839
2020-02-09 | 9:32 | 49.832
2020-02-09 | 9:32 | 49.825
2020-02-09 | 9:32 | 49.827
2020-02-09 | 9:32 | 49.836
2020-02-09 | 9:32 | 49.841
2020-02-09 | 9:32 | 49.84
2020-02-09 | 9:32 | 49.841
2020-02-09 | 9:32 | 49.85
2020-02-09 | 9:32 | 49.844
2020-02-09 | 9:32 | 49.829
2020-02-09 | 9:32 | 49.826
2020-02-09 | 9:32 | 49.832
2020-02-09 | 9:32 | 49.835
2020-02-09 | 9:32 | 49.83
2020-02-09 | 9:32 | 49.839
2020-02-09 | 9:32 | 49.835
2020-02-09 | 9:32 | 49.821
2020-02-09 | 9:32 | 49.824
2020-02-09 | 9:32 | 49.83
2020-02-09 | 9:32 | 49.826
2020-02-09 | 9:32 | 49.836
2020-02-09 | 9:32 | 49.815
2020-02-09 | 9:32 | 49.818
2020-02-09 | 9:32 | 49.821
2020-02-09 | 9:32 | 49.822
2020-02-09 | 9:32 | 49.829
2020-02-09 | 9:32 | 49.809
2020-02-09 | 9:32 | 49.816
2020-02-09 | 9:32 | 49.818
2020-02-09 | 9:32 | 49.824
2020-02-09 | 9:32 | 49.818
2020-02-09 | 9:32 | 49.811
2020-02-09 | 9:32 | 49.816
2020-02-09 | 9:32 | 49.823
2020-02-09 | 9:32 | 49.801
2020-02-09 | 9:32 | 49.803
2020-02-09 | 9:32 | 49.798
2020-02-09 | 9:32 | 49.802
2020-02-09 | 9:32 | 49.783
2020-02-09 | 9:32 | 49.796
2020-02-09 | 9:32 | 49.787
2020-02-09 | 9:32 | 49.778
2020-02-09 | 9:32 | 49.781
2020-02-09 | 9:32 | 49.771
2020-02-09 | 9:32 | 49.779
2020-02-09 | 9:32 | 49.772
2020-02-09 | 9:33 | 49.78
2020-02-09 | 9:33 | 49.775
2020-02-09 | 9:33 | 49.779
2020-02-09 | 9:33 | 49.774
2020-02-09 | 9:33 | 49.781
2020-02-09 | 9:33 | 49.771
2020-02-09 | 9:33 | 49.776
2020-02-09 | 9:33 | 49.768
2020-02-09 | 9:33 | 49.763
2020-02-09 | 9:33 | 49.768
2020-02-09 | 9:33 | 49.757
2020-02-09 | 9:33 | 49.768
2020-02-09 | 9:33 | 49.763
2020-02-09 | 9:33 | 49.782
2020-02-09 | 9:33 | 49.762
2020-02-09 | 9:33 | 49.776
2020-02-09 | 9:33 | 49.759
2020-02-09 | 9:33 | 49.766
2020-02-09 | 9:33 | 49.764
2020-02-09 | 9:33 | 49.752
2020-02-09 | 9:33 | 49.755
2020-02-09 | 9:33 | 49.742
2020-02-09 | 9:33 | 49.745
2020-02-09 | 9:33 | 49.751
2020-02-09 | 9:33 | 49.736
2020-02-09 | 9:33 | 49.725
2020-02-09 | 9:33 | 49.739
2020-02-09 | 9:33 | 49.729
2020-02-09 | 9:33 | 49.725
2020-02-09 | 9:33 | 49.719
2020-02-09 | 9:33 | 49.72
2020-02-09 | 9:33 | 49.735
2020-02-09 | 9:33 | 49.726
2020-02-09 | 9:33 | 49.72
2020-02-09 | 9:33 | 49.731
2020-02-09 | 9:33 | 49.718
2020-02-09 | 9:33 | 49.716
2020-02-09 | 9:33 | 49.714
2020-02-09 | 9:33 | 49.708
2020-02-09 | 9:33 | 49.722
2020-02-09 | 9:33 | 49.73
2020-02-09 | 9:33 | 49.732
2020-02-09 | 9:33 | 49.725
2020-02-09 | 9:33 | 49.716
2020-02-09 | 9:33 | 49.722
2020-02-09 | 9:33 | 49.724
2020-02-09 | 9:33 | 49.729
2020-02-09 | 9:33 | 49.715
2020-02-09 | 9:33 | 49.715
2020-02-09 | 9:33 | 49.71
2020-02-09 | 9:33 | 49.703
2020-02-09 | 9:33 | 49.72
2020-02-09 | 9:33 | 49.724
2020-02-09 | 9:33 | 49.723
2020-02-09 | 9:33 | 49.715
2020-02-09 | 9:33 | 49.715
2020-02-09 | 9:33 | 49.71
2020-02-09 | 9:33 | 49.723
2020-02-09 | 9:33 | 49.728
2020-02-09 | 9:34 | 49.729
2020-02-09 | 9:34 | 49.729
2020-02-09 | 9:34 | 49.727
2020-02-09 | 9:34 | 49.744
2020-02-09 | 9:34 | 49.743
2020-02-09 | 9:34 | 49.744
2020-02-09 | 9:34 | 49.755
2020-02-09 | 9:34 | 49.751
2020-02-09 | 9:34 | 49.744
2020-02-09 | 9:34 | 49.76
2020-02-09 | 9:34 | 49.753
2020-02-09 | 9:34 | 49.765
2020-02-09 | 9:34 | 49.757
2020-02-09 | 9:34 | 49.76
2020-02-09 | 9:34 | 49.766
2020-02-09 | 9:34 | 49.756
2020-02-09 | 9:34 | 49.765
2020-02-09 | 9:34 | 49.756
2020-02-09 | 9:34 | 49.775
2020-02-09 | 9:34 | 49.762
2020-02-09 | 9:34 | 49.768
2020-02-09 | 9:34 | 49.76
2020-02-09 | 9:34 | 49.754
2020-02-09 | 9:34 | 49.758
2020-02-09 | 9:34 | 49.751
2020-02-09 | 9:34 | 49.765
2020-02-09 | 9:34 | 49.76
2020-02-09 | 9:34 | 49.745
2020-02-09 | 9:34 | 49.758
2020-02-09 | 9:34 | 49.75
2020-02-09 | 9:34 | 49.769
2020-02-09 | 9:34 | 49.754
2020-02-09 | 9:34 | 49.746
2020-02-09 | 9:34 | 49.754
2020-02-09 | 9:34 | 49.745
2020-02-09 | 9:34 | 49.759
2020-02-09 | 9:34 | 49.749
2020-02-09 | 9:34 | 49.742
2020-02-09 | 9:34 | 49.754
2020-02-09 | 9:34 | 49.747
2020-02-09 | 9:34 | 49.735
2020-02-09 | 9:34 | 49.748
2020-02-09 | 9:34 | 49.74
2020-02-09 | 9:34 | 49.727
2020-02-09 | 9:34 | 49.739
2020-02-09 | 9:34 | 49.741
2020-02-09 | 9:34 | 49.731
2020-02-09 | 9:34 | 49.726
2020-02-09 | 9:34 | 49.73
2020-02-09 | 9:34 | 49.737
2020-02-09 | 9:34 | 49.729
2020-02-09 | 9:34 | 49.725
2020-02-09 | 9:34 | 49.733
2020-02-09 | 9:34 | 49.728
2020-02-09 | 9:34 | 49.724
2020-02-09 | 9:34 | 49.717
2020-02-09 | 9:34 | 49.733
2020-02-09 | 9:34 | 49.735
2020-02-09 | 9:34 | 49.731
2020-02-09 | 9:34 | 49.725
2020-02-09 | 9:34 | 49.733
2020-02-09 | 9:35 | 49.739
2020-02-09 | 9:35 | 49.728
2020-02-09 | 9:35 | 49.721
2020-02-09 | 9:35 | 49.71
2020-02-09 | 9:35 | 49.725
2020-02-09 | 9:35 | 49.725
2020-02-09 | 9:35 | 49.72
2020-02-09 | 9:35 | 49.723
2020-02-09 | 9:35 | 49.722
2020-02-09 | 9:35 | 49.735
2020-02-09 | 9:35 | 49.748
2020-02-09 | 9:35 | 49.736
2020-02-09 | 9:35 | 49.728
2020-02-09 | 9:35 | 49.735
2020-02-09 | 9:35 | 49.741
2020-02-09 | 9:35 | 49.734
2020-02-09 | 9:35 | 49.726
2020-02-09 | 9:35 | 49.734
2020-02-09 | 9:35 | 49.738
2020-02-09 | 9:35 | 49.725
2020-02-09 | 9:35 | 49.719
2020-02-09 | 9:35 | 49.714
2020-02-09 | 9:35 | 49.722
2020-02-09 | 9:35 | 49.723
2020-02-09 | 9:35 | 49.721
2020-02-09 | 9:35 | 49.715
2020-02-09 | 9:35 | 49.713
2020-02-09 | 9:35 | 49.717
2020-02-09 | 9:35 | 49.72
2020-02-09 | 9:35 | 49.718
2020-02-09 | 9:35 | 49.715
2020-02-09 | 9:35 | 49.709
2020-02-09 | 9:35 | 49.705
2020-02-09 | 9:35 | 49.7
2020-02-09 | 9:35 | 49.704
2020-02-09 | 9:35 | 49.71
2020-02-09 | 9:35 | 49.712
2020-02-09 | 9:35 | 49.72
2020-02-09 | 9:35 | 49.712
2020-02-09 | 9:35 | 49.716
2020-02-09 | 9:35 | 49.717
2020-02-09 | 9:35 | 49.712
2020-02-09 | 9:35 | 49.727
2020-02-09 | 9:35 | 49.732
2020-02-09 | 9:35 | 49.732
2020-02-09 | 9:35 | 49.732
2020-02-09 | 9:35 | 49.739
2020-02-09 | 9:35 | 49.753
2020-02-09 | 9:35 | 49.747
2020-02-09 | 9:35 | 49.741
2020-02-09 | 9:35 | 49.755
2020-02-09 | 9:35 | 49.757
2020-02-09 | 9:35 | 49.763
2020-02-09 | 9:35 | 49.761
2020-02-09 | 9:35 | 49.75
2020-02-09 | 9:35 | 49.761
2020-02-09 | 9:35 | 49.751
2020-02-09 | 9:35 | 49.758
2020-02-09 | 9:35 | 49.757
2020-02-09 | 9:36 | 49.752
2020-02-09 | 9:36 | 49.764
2020-02-09 | 9:36 | 49.758
2020-02-09 | 9:36 | 49.769
2020-02-09 | 9:36 | 49.77
2020-02-09 | 9:36 | 49.771
2020-02-09 | 9:36 | 49.767
2020-02-09 | 9:36 | 49.758
2020-02-09 | 9:36 | 49.763
2020-02-09 | 9:36 | 49.76
2020-02-09 | 9:36 | 49.76
2020-02-09 | 9:36 | 49.757
2020-02-09 | 9:36 | 49.765
2020-02-09 | 9:36 | 49.757
2020-02-09 | 9:36 | 49.762
2020-02-09 | 9:36 | 49.759
2020-02-09 | 9:36 | 49.767
2020-02-09 | 9:36 | 49.762
2020-02-09 | 9:36 | 49.76
2020-02-09 | 9:36 | 49.757
2020-02-09 | 9:36 | 49.746
2020-02-09 | 9:36 | 49.755
2020-02-09 | 9:36 | 49.755
2020-02-09 | 9:36 | 49.745
2020-02-09 | 9:36 | 49.746
2020-02-09 | 9:36 | 49.748
2020-02-09 | 9:36 | 49.736
2020-02-09 | 9:36 | 49.753
2020-02-09 | 9:36 | 49.745
2020-02-09 | 9:36 | 49.732
2020-02-09 | 9:36 | 49.75
2020-02-09 | 9:36 | 49.744
2020-02-09 | 9:36 | 49.734
2020-02-09 | 9:36 | 49.747
2020-02-09 | 9:36 | 49.746
2020-02-09 | 9:36 | 49.737
2020-02-09 | 9:36 | 49.742
2020-02-09 | 9:36 | 49.737
2020-02-09 | 9:36 | 49.731
2020-02-09 | 9:36 | 49.723
2020-02-09 | 9:36 | 49.736
2020-02-09 | 9:36 | 49.739
2020-02-09 | 9:36 | 49.74
2020-02-09 | 9:36 | 49.741
2020-02-09 | 9:36 | 49.742
2020-02-09 | 9:36 | 49.739
2020-02-09 | 9:36 | 49.726
2020-02-09 | 9:36 | 49.738
2020-02-09 | 9:36 | 49.733
2020-02-09 | 9:36 | 49.724
2020-02-09 | 9:36 | 49.733
2020-02-09 | 9:36 | 49.725
2020-02-09 | 9:36 | 49.723
2020-02-09 | 9:36 | 49.715
2020-02-09 | 9:36 | 49.721
2020-02-09 | 9:36 | 49.718
2020-02-09 | 9:36 | 49.721
2020-02-09 | 9:36 | 49.706
2020-02-09 | 9:36 | 49.705
2020-02-09 | 9:36 | 49.703
2020-02-09 | 9:36 | 49.702
2020-02-09 | 9:37 | 49.697
2020-02-09 | 9:37 | 49.695
2020-02-09 | 9:37 | 49.688
2020-02-09 | 9:37 | 49.691
2020-02-09 | 9:37 | 49.686
2020-02-09 | 9:37 | 49.683
2020-02-09 | 9:37 | 49.687
2020-02-09 | 9:37 | 49.685
2020-02-09 | 9:37 | 49.688
2020-02-09 | 9:37 | 49.688
2020-02-09 | 9:37 | 49.689
2020-02-09 | 9:37 | 49.689
2020-02-09 | 9:37 | 49.688
2020-02-09 | 9:37 | 49.688
2020-02-09 | 9:37 | 49.691
2020-02-09 | 9:37 | 49.694
2020-02-09 | 9:37 | 49.699
2020-02-09 | 9:37 | 49.697
2020-02-09 | 9:37 | 49.698
2020-02-09 | 9:37 | 49.698
2020-02-09 | 9:37 | 49.697
2020-02-09 | 9:37 | 49.698
2020-02-09 | 9:37 | 49.692
2020-02-09 | 9:37 | 49.693
2020-02-09 | 9:37 | 49.691
2020-02-09 | 9:37 | 49.687
2020-02-09 | 9:37 | 49.686
2020-02-09 | 9:37 | 49.673
2020-02-09 | 9:37 | 49.678
2020-02-09 | 9:37 | 49.682
2020-02-09 | 9:37 | 49.685
2020-02-09 | 9:37 | 49.687
2020-02-09 | 9:37 | 49.685
2020-02-09 | 9:37 | 49.694
2020-02-09 | 9:37 | 49.683
2020-02-09 | 9:37 | 49.683
2020-02-09 | 9:37 | 49.681
2020-02-09 | 9:37 | 49.685
2020-02-09 | 9:37 | 49.677
2020-02-09 | 9:37 | 49.678
2020-02-09 | 9:37 | 49.673
2020-02-09 | 9:37 | 49.674
2020-02-09 | 9:37 | 49.675
2020-02-09 | 9:37 | 49.677
2020-02-09 | 9:37 | 49.676
2020-02-09 | 9:37 | 49.672
2020-02-09 | 9:37 | 49.679
2020-02-09 | 9:37 | 49.675
2020-02-09 | 9:37 | 49.676
2020-02-09 | 9:37 | 49.667
2020-02-09 | 9:37 | 49.677
2020-02-09 | 9:37 | 49.68
2020-02-09 | 9:37 | 49.691
2020-02-09 | 9:37 | 49.69
2020-02-09 | 9:37 | 49.688
2020-02-09 | 9:37 | 49.683
2020-02-09 | 9:37 | 49.683
2020-02-09 | 9:37 | 49.67
2020-02-09 | 9:37 | 49.667
2020-02-09 | 9:38 | 49.672
2020-02-09 | 9:38 | 49.672
2020-02-09 | 9:38 | 49.675
2020-02-09 | 9:38 | 49.674
2020-02-09 | 9:38 | 49.679
2020-02-09 | 9:38 | 49.67
2020-02-09 | 9:38 | 49.666
2020-02-09 | 9:38 | 49.661
2020-02-09 | 9:38 | 49.663
2020-02-09 | 9:38 | 49.668
2020-02-09 | 9:38 | 49.666
2020-02-09 | 9:38 | 49.676
2020-02-09 | 9:38 | 49.669
2020-02-09 | 9:38 | 49.667
2020-02-09 | 9:38 | 49.656
2020-02-09 | 9:38 | 49.664
2020-02-09 | 9:38 | 49.669
2020-02-09 | 9:38 | 49.668
2020-02-09 | 9:38 | 49.666
2020-02-09 | 9:38 | 49.664
2020-02-09 | 9:38 | 49.655
2020-02-09 | 9:38 | 49.664
2020-02-09 | 9:38 | 49.671
2020-02-09 | 9:38 | 49.67
2020-02-09 | 9:38 | 49.671
2020-02-09 | 9:38 | 49.675
2020-02-09 | 9:38 | 49.673
2020-02-09 | 9:38 | 49.673
2020-02-09 | 9:38 | 49.68
2020-02-09 | 9:38 | 49.671
2020-02-09 | 9:38 | 49.667
2020-02-09 | 9:38 | 49.656
2020-02-09 | 9:38 | 49.662
2020-02-09 | 9:38 | 49.666
2020-02-09 | 9:38 | 49.664
2020-02-09 | 9:38 | 49.662
2020-02-09 | 9:38 | 49.658
2020-02-09 | 9:38 | 49.649
2020-02-09 | 9:38 | 49.654
2020-02-09 | 9:38 | 49.661
2020-02-09 | 9:38 | 49.649
2020-02-09 | 9:38 | 49.645
2020-02-09 | 9:38 | 49.651
2020-02-09 | 9:38 | 49.657
2020-02-09 | 9:38 | 49.654
2020-02-09 | 9:38 | 49.652
2020-02-09 | 9:38 | 49.659
2020-02-09 | 9:38 | 49.662
2020-02-09 | 9:38 | 49.672
2020-02-09 | 9:38 | 49.667
2020-02-09 | 9:38 | 49.655
2020-02-09 | 9:38 | 49.661
2020-02-09 | 9:38 | 49.667
2020-02-09 | 9:38 | 49.666
2020-02-09 | 9:38 | 49.666
2020-02-09 | 9:38 | 49.67
2020-02-09 | 9:38 | 49.671
2020-02-09 | 9:38 | 49.67
2020-02-09 | 9:38 | 49.667
2020-02-09 | 9:38 | 49.66
2020-02-09 | 9:38 | 49.655
2020-02-09 | 9:39 | 49.657
2020-02-09 | 9:39 | 49.658
2020-02-09 | 9:39 | 49.644
2020-02-09 | 9:39 | 49.635
2020-02-09 | 9:39 | 49.629
2020-02-09 | 9:39 | 49.627
2020-02-09 | 9:39 | 49.623
2020-02-09 | 9:39 | 49.62
2020-02-09 | 9:39 | 49.613
2020-02-09 | 9:39 | 49.623
2020-02-09 | 9:39 | 49.603
2020-02-09 | 9:39 | 49.618
2020-02-09 | 9:39 | 49.6
2020-02-09 | 9:39 | 49.609
2020-02-09 | 9:39 | 49.602
2020-02-09 | 9:39 | 49.607
2020-02-09 | 9:39 | 49.603
2020-02-09 | 9:39 | 49.602
2020-02-09 | 9:39 | 49.599
2020-02-09 | 9:39 | 49.599
2020-02-09 | 9:39 | 49.597
2020-02-09 | 9:39 | 49.609
2020-02-09 | 9:39 | 49.594
2020-02-09 | 9:39 | 49.615
2020-02-09 | 9:39 | 49.611
2020-02-09 | 9:39 | 49.633
2020-02-09 | 9:39 | 49.644
2020-02-09 | 9:39 | 49.645
2020-02-09 | 9:39 | 49.658
2020-02-09 | 9:39 | 49.664
2020-02-09 | 9:39 | 49.678
2020-02-09 | 9:39 | 49.679
2020-02-09 | 9:39 | 49.683
2020-02-09 | 9:39 | 49.684
2020-02-09 | 9:39 | 49.692
2020-02-09 | 9:39 | 49.697
2020-02-09 | 9:39 | 49.7
2020-02-09 | 9:39 | 49.705
2020-02-09 | 9:39 | 49.716
2020-02-09 | 9:39 | 49.711
2020-02-09 | 9:39 | 49.716
2020-02-09 | 9:39 | 49.716
2020-02-09 | 9:39 | 49.713
2020-02-09 | 9:39 | 49.715
2020-02-09 | 9:39 | 49.724
2020-02-09 | 9:39 | 49.73
2020-02-09 | 9:39 | 49.731
2020-02-09 | 9:39 | 49.731
2020-02-09 | 9:39 | 49.739
2020-02-09 | 9:39 | 49.736
2020-02-09 | 9:39 | 49.741
2020-02-09 | 9:39 | 49.747
2020-02-09 | 9:39 | 49.744
2020-02-09 | 9:39 | 49.735
2020-02-09 | 9:39 | 49.739
2020-02-09 | 9:39 | 49.734
2020-02-09 | 9:39 | 49.73
2020-02-09 | 9:39 | 49.723
2020-02-09 | 9:39 | 49.727
2020-02-09 | 9:40 | 49.728
2020-02-09 | 9:40 | 49.726
2020-02-09 | 9:40 | 49.725
2020-02-09 | 9:40 | 49.719
2020-02-09 | 9:40 | 49.725
2020-02-09 | 9:40 | 49.728
2020-02-09 | 9:40 | 49.72
2020-02-09 | 9:40 | 49.719
2020-02-09 | 9:40 | 49.712
2020-02-09 | 9:40 | 49.704
2020-02-09 | 9:40 | 49.717
2020-02-09 | 9:40 | 49.716
2020-02-09 | 9:40 | 49.719
2020-02-09 | 9:40 | 49.708
2020-02-09 | 9:40 | 49.709
2020-02-09 | 9:40 | 49.705
2020-02-09 | 9:40 | 49.704
2020-02-09 | 9:40 | 49.699
2020-02-09 | 9:40 | 49.692
2020-02-09 | 9:40 | 49.693
2020-02-09 | 9:40 | 49.689
2020-02-09 | 9:40 | 49.706
2020-02-09 | 9:40 | 49.703
2020-02-09 | 9:40 | 49.706
2020-02-09 | 9:40 | 49.707
2020-02-09 | 9:40 | 49.711
2020-02-09 | 9:40 | 49.71
2020-02-09 | 9:40 | 49.699
2020-02-09 | 9:40 | 49.713
2020-02-09 | 9:40 | 49.715
2020-02-09 | 9:40 | 49.723
2020-02-09 | 9:40 | 49.715
2020-02-09 | 9:40 | 49.72
2020-02-09 | 9:40 | 49.717
2020-02-09 | 9:40 | 49.712
2020-02-09 | 9:40 | 49.724
2020-02-09 | 9:40 | 49.733
2020-02-09 | 9:40 | 49.73
2020-02-09 | 9:40 | 49.729
2020-02-09 | 9:40 | 49.74
2020-02-09 | 9:40 | 49.751
2020-02-09 | 9:40 | 49.749
2020-02-09 | 9:40 | 49.757
2020-02-09 | 9:40 | 49.757
2020-02-09 | 9:40 | 49.762
2020-02-09 | 9:40 | 49.775
2020-02-09 | 9:40 | 49.775
2020-02-09 | 9:40 | 49.782
2020-02-09 | 9:40 | 49.787
2020-02-09 | 9:40 | 49.799
2020-02-09 | 9:40 | 49.808
2020-02-09 | 9:40 | 49.806
2020-02-09 | 9:40 | 49.816
2020-02-09 | 9:40 | 49.821
2020-02-09 | 9:40 | 49.833
2020-02-09 | 9:40 | 49.835
2020-02-09 | 9:40 | 49.825
2020-02-09 | 9:40 | 49.831
2020-02-09 | 9:40 | 49.84
2020-02-09 | 9:40 | 49.839
2020-02-09 | 9:40 | 49.836
2020-02-09 | 9:41 | 49.839
2020-02-09 | 9:41 | 49.842
2020-02-09 | 9:41 | 49.846
2020-02-09 | 9:41 | 49.834
2020-02-09 | 9:41 | 49.841
2020-02-09 | 9:41 | 49.841
2020-02-09 | 9:41 | 49.843
2020-02-09 | 9:41 | 49.843
2020-02-09 | 9:41 | 49.842
2020-02-09 | 9:41 | 49.836
2020-02-09 | 9:41 | 49.831
2020-02-09 | 9:41 | 49.837
2020-02-09 | 9:41 | 49.822
2020-02-09 | 9:41 | 49.824
2020-02-09 | 9:41 | 49.824
2020-02-09 | 9:41 | 49.826
2020-02-09 | 9:41 | 49.825
2020-02-09 | 9:41 | 49.82
2020-02-09 | 9:41 | 49.824
2020-02-09 | 9:41 | 49.808
2020-02-09 | 9:41 | 49.814
2020-02-09 | 9:41 | 49.815
2020-02-09 | 9:41 | 49.8
2020-02-09 | 9:41 | 49.806
2020-02-09 | 9:41 | 49.799
2020-02-09 | 9:41 | 49.795
2020-02-09 | 9:41 | 49.808
2020-02-09 | 9:41 | 49.811
2020-02-09 | 9:41 | 49.82
2020-02-09 | 9:41 | 49.815
2020-02-09 | 9:41 | 49.827
2020-02-09 | 9:41 | 49.828
2020-02-09 | 9:41 | 49.821
2020-02-09 | 9:41 | 49.83
2020-02-09 | 9:41 | 49.823
2020-02-09 | 9:41 | 49.825
2020-02-09 | 9:41 | 49.832
2020-02-09 | 9:41 | 49.823
2020-02-09 | 9:41 | 49.828
2020-02-09 | 9:41 | 49.819
2020-02-09 | 9:41 | 49.814
2020-02-09 | 9:41 | 49.816
2020-02-09 | 9:41 | 49.817
2020-02-09 | 9:41 | 49.805
2020-02-09 | 9:41 | 49.808
2020-02-09 | 9:41 | 49.81
2020-02-09 | 9:41 | 49.812
2020-02-09 | 9:41 | 49.812
2020-02-09 | 9:41 | 49.825
2020-02-09 | 9:41 | 49.825
2020-02-09 | 9:41 | 49.824
2020-02-09 | 9:41 | 49.825
2020-02-09 | 9:41 | 49.814
2020-02-09 | 9:41 | 49.817
2020-02-09 | 9:41 | 49.815
2020-02-09 | 9:41 | 49.819
2020-02-09 | 9:41 | 49.812
2020-02-09 | 9:41 | 49.82
2020-02-09 | 9:41 | 49.816
2020-02-09 | 9:42 | 49.821
2020-02-09 | 9:42 | 49.809
2020-02-09 | 9:42 | 49.815
2020-02-09 | 9:42 | 49.818
2020-02-09 | 9:42 | 49.818
2020-02-09 | 9:42 | 49.806
2020-02-09 | 9:42 | 49.81
2020-02-09 | 9:42 | 49.802
2020-02-09 | 9:42 | 49.804
2020-02-09 | 9:42 | 49.795
2020-02-09 | 9:42 | 49.812
2020-02-09 | 9:42 | 49.817
2020-02-09 | 9:42 | 49.821
2020-02-09 | 9:42 | 49.817
2020-02-09 | 9:42 | 49.829
2020-02-09 | 9:42 | 49.831
2020-02-09 | 9:42 | 49.83
2020-02-09 | 9:42 | 49.843
2020-02-09 | 9:42 | 49.841
2020-02-09 | 9:42 | 49.836
2020-02-09 | 9:42 | 49.837
2020-02-09 | 9:42 | 49.84
2020-02-09 | 9:42 | 49.844
2020-02-09 | 9:42 | 49.842
2020-02-09 | 9:42 | 49.839
2020-02-09 | 9:42 | 49.834
2020-02-09 | 9:42 | 49.829
2020-02-09 | 9:42 | 49.834
2020-02-09 | 9:42 | 49.824
2020-02-09 | 9:42 | 49.824
2020-02-09 | 9:42 | 49.824
2020-02-09 | 9:42 | 49.825
2020-02-09 | 9:42 | 49.822
2020-02-09 | 9:42 | 49.815
2020-02-09 | 9:42 | 49.817
2020-02-09 | 9:42 | 49.821
2020-02-09 | 9:42 | 49.832
2020-02-09 | 9:42 | 49.817
2020-02-09 | 9:42 | 49.827
2020-02-09 | 9:42 | 49.835
2020-02-09 | 9:42 | 49.837
2020-02-09 | 9:42 | 49.839
2020-02-09 | 9:42 | 49.84
2020-02-09 | 9:42 | 49.839
2020-02-09 | 9:42 | 49.853
2020-02-09 | 9:42 | 49.851
2020-02-09 | 9:42 | 49.85
2020-02-09 | 9:42 | 49.843
2020-02-09 | 9:42 | 49.853
2020-02-09 | 9:42 | 49.854
2020-02-09 | 9:42 | 49.861
2020-02-09 | 9:42 | 49.865
2020-02-09 | 9:42 | 49.849
2020-02-09 | 9:42 | 49.852
2020-02-09 | 9:42 | 49.845
2020-02-09 | 9:42 | 49.852
2020-02-09 | 9:42 | 49.854
2020-02-09 | 9:42 | 49.855
2020-02-09 | 9:42 | 49.847
2020-02-09 | 9:42 | 49.841
2020-02-09 | 9:42 | 49.841
2020-02-09 | 9:43 | 49.843
2020-02-09 | 9:43 | 49.841
2020-02-09 | 9:43 | 49.843
2020-02-09 | 9:43 | 49.839
2020-02-09 | 9:43 | 49.836
2020-02-09 | 9:43 | 49.846
2020-02-09 | 9:43 | 49.845
2020-02-09 | 9:43 | 49.835
2020-02-09 | 9:43 | 49.84
2020-02-09 | 9:43 | 49.838
2020-02-09 | 9:43 | 49.838
2020-02-09 | 9:43 | 49.835
2020-02-09 | 9:43 | 49.838
2020-02-09 | 9:43 | 49.834
2020-02-09 | 9:43 | 49.827
2020-02-09 | 9:43 | 49.825
2020-02-09 | 9:43 | 49.826
2020-02-09 | 9:43 | 49.816
2020-02-09 | 9:43 | 49.821
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.819
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.817
2020-02-09 | 9:43 | 49.819
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.825
2020-02-09 | 9:43 | 49.817
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.822
2020-02-09 | 9:43 | 49.826
2020-02-09 | 9:43 | 49.812
2020-02-09 | 9:43 | 49.815
2020-02-09 | 9:43 | 49.814
2020-02-09 | 9:43 | 49.814
2020-02-09 | 9:43 | 49.81
2020-02-09 | 9:43 | 49.811
2020-02-09 | 9:43 | 49.818
2020-02-09 | 9:43 | 49.822
2020-02-09 | 9:43 | 49.813
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.815
2020-02-09 | 9:43 | 49.822
2020-02-09 | 9:43 | 49.819
2020-02-09 | 9:43 | 49.824
2020-02-09 | 9:43 | 49.825
2020-02-09 | 9:43 | 49.829
2020-02-09 | 9:43 | 49.833
2020-02-09 | 9:43 | 49.823
2020-02-09 | 9:43 | 49.824
2020-02-09 | 9:43 | 49.828
2020-02-09 | 9:43 | 49.824
2020-02-09 | 9:43 | 49.828
2020-02-09 | 9:43 | 49.817
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:43 | 49.826
2020-02-09 | 9:43 | 49.824
2020-02-09 | 9:43 | 49.831
2020-02-09 | 9:43 | 49.82
2020-02-09 | 9:44 | 49.821
2020-02-09 | 9:44 | 49.824
2020-02-09 | 9:44 | 49.817
2020-02-09 | 9:44 | 49.819
2020-02-09 | 9:44 | 49.81
2020-02-09 | 9:44 | 49.815
2020-02-09 | 9:44 | 49.808
2020-02-09 | 9:44 | 49.813
2020-02-09 | 9:44 | 49.806
2020-02-09 | 9:44 | 49.799
2020-02-09 | 9:44 | 49.793
2020-02-09 | 9:44 | 49.791
2020-02-09 | 9:44 | 49.796
2020-02-09 | 9:44 | 49.801
2020-02-09 | 9:44 | 49.793
2020-02-09 | 9:44 | 49.795
2020-02-09 | 9:44 | 49.796
2020-02-09 | 9:44 | 49.794
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.789
2020-02-09 | 9:44 | 49.796
2020-02-09 | 9:44 | 49.802
2020-02-09 | 9:44 | 49.791
2020-02-09 | 9:44 | 49.793
2020-02-09 | 9:44 | 49.799
2020-02-09 | 9:44 | 49.794
2020-02-09 | 9:44 | 49.79
2020-02-09 | 9:44 | 49.79
2020-02-09 | 9:44 | 49.796
2020-02-09 | 9:44 | 49.798
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.791
2020-02-09 | 9:44 | 49.796
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.798
2020-02-09 | 9:44 | 49.789
2020-02-09 | 9:44 | 49.791
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.786
2020-02-09 | 9:44 | 49.791
2020-02-09 | 9:44 | 49.782
2020-02-09 | 9:44 | 49.786
2020-02-09 | 9:44 | 49.776
2020-02-09 | 9:44 | 49.779
2020-02-09 | 9:44 | 49.772
2020-02-09 | 9:44 | 49.781
2020-02-09 | 9:44 | 49.787
2020-02-09 | 9:44 | 49.787
2020-02-09 | 9:44 | 49.795
2020-02-09 | 9:44 | 49.784
2020-02-09 | 9:44 | 49.787
2020-02-09 | 9:44 | 49.785
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.794
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.787
2020-02-09 | 9:44 | 49.784
2020-02-09 | 9:44 | 49.785
2020-02-09 | 9:44 | 49.792
2020-02-09 | 9:44 | 49.791
2020-02-09 | 9:44 | 49.795
2020-02-09 | 9:45 | 49.794
2020-02-09 | 9:45 | 49.791
2020-02-09 | 9:45 | 49.795
2020-02-09 | 9:45 | 49.799
2020-02-09 | 9:45 | 49.794
2020-02-09 | 9:45 | 49.797
2020-02-09 | 9:45 | 49.788
2020-02-09 | 9:45 | 49.801
2020-02-09 | 9:45 | 49.808
2020-02-09 | 9:45 | 49.801
2020-02-09 | 9:45 | 49.808
2020-02-09 | 9:45 | 49.804
2020-02-09 | 9:45 | 49.803
2020-02-09 | 9:45 | 49.81
2020-02-09 | 9:45 | 49.809
2020-02-09 | 9:45 | 49.807
2020-02-09 | 9:45 | 49.8
2020-02-09 | 9:45 | 49.802
2020-02-09 | 9:45 | 49.801
2020-02-09 | 9:45 | 49.79
2020-02-09 | 9:45 | 49.79
2020-02-09 | 9:45 | 49.778
2020-02-09 | 9:45 | 49.784
2020-02-09 | 9:45 | 49.779
2020-02-09 | 9:45 | 49.777
2020-02-09 | 9:45 | 49.776
2020-02-09 | 9:45 | 49.775
2020-02-09 | 9:45 | 49.778
2020-02-09 | 9:45 | 49.779
2020-02-09 | 9:45 | 49.778
2020-02-09 | 9:45 | 49.78
2020-02-09 | 9:45 | 49.778
2020-02-09 | 9:45 | 49.779
2020-02-09 | 9:45 | 49.788
2020-02-09 | 9:45 | 49.779
2020-02-09 | 9:45 | 49.781
2020-02-09 | 9:45 | 49.78
2020-02-09 | 9:45 | 49.789
2020-02-09 | 9:45 | 49.789
2020-02-09 | 9:45 | 49.787
2020-02-09 | 9:45 | 49.794
2020-02-09 | 9:45 | 49.784
2020-02-09 | 9:45 | 49.785
2020-02-09 | 9:45 | 49.783
2020-02-09 | 9:45 | 49.782
2020-02-09 | 9:45 | 49.784
2020-02-09 | 9:45 | 49.78
2020-02-09 | 9:45 | 49.794
2020-02-09 | 9:45 | 49.798
2020-02-09 | 9:45 | 49.789
2020-02-09 | 9:45 | 49.794
2020-02-09 | 9:45 | 49.797
2020-02-09 | 9:45 | 49.792
2020-02-09 | 9:45 | 49.797
2020-02-09 | 9:45 | 49.782
2020-02-09 | 9:45 | 49.785
2020-02-09 | 9:45 | 49.785
2020-02-09 | 9:45 | 49.783
2020-02-09 | 9:45 | 49.786
2020-02-09 | 9:46 | 49.787
2020-02-09 | 9:46 | 49.79
2020-02-09 | 9:46 | 49.779
2020-02-09 | 9:46 | 49.778
2020-02-09 | 9:46 | 49.78
2020-02-09 | 9:46 | 49.785
2020-02-09 | 9:46 | 49.779
2020-02-09 | 9:46 | 49.793
2020-02-09 | 9:46 | 49.795
2020-02-09 | 9:46 | 49.786
2020-02-09 | 9:46 | 49.788
2020-02-09 | 9:46 | 49.782
2020-02-09 | 9:46 | 49.792
2020-02-09 | 9:46 | 49.795
2020-02-09 | 9:46 | 49.787
2020-02-09 | 9:46 | 49.786
2020-02-09 | 9:46 | 49.777
2020-02-09 | 9:46 | 49.783
2020-02-09 | 9:46 | 49.781
2020-02-09 | 9:46 | 49.78
2020-02-09 | 9:46 | 49.781
2020-02-09 | 9:46 | 49.776
2020-02-09 | 9:46 | 49.772
2020-02-09 | 9:46 | 49.767
2020-02-09 | 9:46 | 49.757
2020-02-09 | 9:46 | 49.763
2020-02-09 | 9:46 | 49.76
2020-02-09 | 9:46 | 49.76
2020-02-09 | 9:46 | 49.76
2020-02-09 | 9:46 | 49.767
2020-02-09 | 9:46 | 49.766
2020-02-09 | 9:46 | 49.764
2020-02-09 | 9:46 | 49.757
2020-02-09 | 9:46 | 49.769
2020-02-09 | 9:46 | 49.764
2020-02-09 | 9:46 | 49.764
2020-02-09 | 9:46 | 49.765
2020-02-09 | 9:46 | 49.754
2020-02-09 | 9:46 | 49.763
2020-02-09 | 9:46 | 49.762
2020-02-09 | 9:46 | 49.772
2020-02-09 | 9:46 | 49.765
2020-02-09 | 9:46 | 49.765
2020-02-09 | 9:46 | 49.764
2020-02-09 | 9:46 | 49.766
2020-02-09 | 9:46 | 49.767
2020-02-09 | 9:46 | 49.767
2020-02-09 | 9:46 | 49.773
2020-02-09 | 9:46 | 49.775
2020-02-09 | 9:46 | 49.784
2020-02-09 | 9:46 | 49.788
2020-02-09 | 9:46 | 49.787
2020-02-09 | 9:46 | 49.787
2020-02-09 | 9:46 | 49.785
2020-02-09 | 9:46 | 49.785
2020-02-09 | 9:46 | 49.779
2020-02-09 | 9:46 | 49.779
2020-02-09 | 9:46 | 49.776
2020-02-09 | 9:46 | 49.783
2020-02-09 | 9:46 | 49.787
2020-02-09 | 9:46 | 49.787
2020-02-09 | 9:47 | 49.791
2020-02-09 | 9:47 | 49.788
2020-02-09 | 9:47 | 49.786
2020-02-09 | 9:47 | 49.787
2020-02-09 | 9:47 | 49.799
2020-02-09 | 9:47 | 49.804
2020-02-09 | 9:47 | 49.8
2020-02-09 | 9:47 | 49.799
2020-02-09 | 9:47 | 49.794
2020-02-09 | 9:47 | 49.786
2020-02-09 | 9:47 | 49.793
2020-02-09 | 9:47 | 49.791
2020-02-09 | 9:47 | 49.784
2020-02-09 | 9:47 | 49.793
2020-02-09 | 9:47 | 49.791
2020-02-09 | 9:47 | 49.788
2020-02-09 | 9:47 | 49.787
2020-02-09 | 9:47 | 49.78
2020-02-09 | 9:47 | 49.774
2020-02-09 | 9:47 | 49.774
2020-02-09 | 9:47 | 49.776
2020-02-09 | 9:47 | 49.769
2020-02-09 | 9:47 | 49.771
2020-02-09 | 9:47 | 49.771
2020-02-09 | 9:47 | 49.769
2020-02-09 | 9:47 | 49.772
2020-02-09 | 9:47 | 49.775
2020-02-09 | 9:47 | 49.765
2020-02-09 | 9:47 | 49.774
2020-02-09 | 9:47 | 49.765
2020-02-09 | 9:47 | 49.77
2020-02-09 | 9:47 | 49.77
2020-02-09 | 9:47 | 49.77
2020-02-09 | 9:47 | 49.77
2020-02-09 | 9:47 | 49.77
2020-02-09 | 9:47 | 49.764
2020-02-09 | 9:47 | 49.763
2020-02-09 | 9:47 | 49.76
2020-02-09 | 9:47 | 49.761
2020-02-09 | 9:47 | 49.761
2020-02-09 | 9:47 | 49.75
2020-02-09 | 9:47 | 49.758
2020-02-09 | 9:47 | 49.76
2020-02-09 | 9:47 | 49.768
2020-02-09 | 9:47 | 49.763
2020-02-09 | 9:47 | 49.768
2020-02-09 | 9:47 | 49.769
2020-02-09 | 9:47 | 49.772
2020-02-09 | 9:47 | 49.77
2020-02-09 | 9:47 | 49.759
2020-02-09 | 9:47 | 49.769
2020-02-09 | 9:47 | 49.758
2020-02-09 | 9:47 | 49.768
2020-02-09 | 9:47 | 49.763
2020-02-09 | 9:47 | 49.769
2020-02-09 | 9:47 | 49.773
2020-02-09 | 9:47 | 49.776
2020-02-09 | 9:47 | 49.779
2020-02-09 | 9:47 | 49.794
2020-02-09 | 9:48 | 49.799
2020-02-09 | 9:48 | 49.798
2020-02-09 | 9:48 | 49.807
2020-02-09 | 9:48 | 49.805
2020-02-09 | 9:48 | 49.815
2020-02-09 | 9:48 | 49.811
2020-02-09 | 9:48 | 49.819
2020-02-09 | 9:48 | 49.815
2020-02-09 | 9:48 | 49.815
2020-02-09 | 9:48 | 49.807
2020-02-09 | 9:48 | 49.812
2020-02-09 | 9:48 | 49.807
2020-02-09 | 9:48 | 49.815
2020-02-09 | 9:48 | 49.808
2020-02-09 | 9:48 | 49.812
2020-02-09 | 9:48 | 49.811
2020-02-09 | 9:48 | 49.803
2020-02-09 | 9:48 | 49.81
2020-02-09 | 9:48 | 49.816
2020-02-09 | 9:48 | 49.823
2020-02-09 | 9:48 | 49.813
2020-02-09 | 9:48 | 49.818
2020-02-09 | 9:48 | 49.817
2020-02-09 | 9:48 | 49.813
2020-02-09 | 9:48 | 49.82
2020-02-09 | 9:48 | 49.809
2020-02-09 | 9:48 | 49.818
2020-02-09 | 9:48 | 49.822
2020-02-09 | 9:48 | 49.807
2020-02-09 | 9:48 | 49.816
2020-02-09 | 9:48 | 49.812
2020-02-09 | 9:48 | 49.815
2020-02-09 | 9:48 | 49.802
2020-02-09 | 9:48 | 49.809
2020-02-09 | 9:48 | 49.808
2020-02-09 | 9:48 | 49.813
2020-02-09 | 9:48 | 49.803
2020-02-09 | 9:48 | 49.801
2020-02-09 | 9:48 | 49.806
2020-02-09 | 9:48 | 49.798
2020-02-09 | 9:48 | 49.803
2020-02-09 | 9:48 | 49.806
2020-02-09 | 9:48 | 49.798
2020-02-09 | 9:48 | 49.805
2020-02-09 | 9:48 | 49.809
2020-02-09 | 9:48 | 49.804
2020-02-09 | 9:48 | 49.812
2020-02-09 | 9:48 | 49.81
2020-02-09 | 9:48 | 49.818
2020-02-09 | 9:48 | 49.816
2020-02-09 | 9:48 | 49.825
2020-02-09 | 9:48 | 49.824
2020-02-09 | 9:48 | 49.83
2020-02-09 | 9:48 | 49.832
2020-02-09 | 9:48 | 49.825
2020-02-09 | 9:48 | 49.82
2020-02-09 | 9:48 | 49.831
2020-02-09 | 9:48 | 49.827
2020-02-09 | 9:48 | 49.82
2020-02-09 | 9:48 | 49.828
2020-02-09 | 9:48 | 49.814
2020-02-09 | 9:49 | 49.819
2020-02-09 | 9:49 | 49.828
2020-02-09 | 9:49 | 49.825
2020-02-09 | 9:49 | 49.833
2020-02-09 | 9:49 | 49.821
2020-02-09 | 9:49 | 49.827
2020-02-09 | 9:49 | 49.83
2020-02-09 | 9:49 | 49.837
2020-02-09 | 9:49 | 49.836
2020-02-09 | 9:49 | 49.831
2020-02-09 | 9:49 | 49.842
2020-02-09 | 9:49 | 49.841
2020-02-09 | 9:49 | 49.844
2020-02-09 | 9:49 | 49.837
2020-02-09 | 9:49 | 49.842
2020-02-09 | 9:49 | 49.845
2020-02-09 | 9:49 | 49.848
2020-02-09 | 9:49 | 49.85
2020-02-09 | 9:49 | 49.852
2020-02-09 | 9:49 | 49.853
2020-02-09 | 9:49 | 49.85
2020-02-09 | 9:49 | 49.851
2020-02-09 | 9:49 | 49.851
2020-02-09 | 9:49 | 49.854
2020-02-09 | 9:49 | 49.854
2020-02-09 | 9:49 | 49.854
2020-02-09 | 9:49 | 49.853
2020-02-09 | 9:49 | 49.855
2020-02-09 | 9:49 | 49.858
2020-02-09 | 9:49 | 49.858
2020-02-09 | 9:49 | 49.859
2020-02-09 | 9:49 | 49.856
2020-02-09 | 9:49 | 49.854
2020-02-09 | 9:49 | 49.854
2020-02-09 | 9:49 | 49.855
2020-02-09 | 9:49 | 49.852
2020-02-09 | 9:49 | 49.851
2020-02-09 | 9:49 | 49.848
2020-02-09 | 9:49 | 49.847
2020-02-09 | 9:49 | 49.852
2020-02-09 | 9:49 | 49.848
2020-02-09 | 9:49 | 49.853
2020-02-09 | 9:49 | 49.854
2020-02-09 | 9:49 | 49.855
2020-02-09 | 9:49 | 49.841
2020-02-09 | 9:49 | 49.84
2020-02-09 | 9:49 | 49.844
2020-02-09 | 9:49 | 49.843
2020-02-09 | 9:49 | 49.847
2020-02-09 | 9:49 | 49.846
2020-02-09 | 9:49 | 49.847
2020-02-09 | 9:49 | 49.838
2020-02-09 | 9:49 | 49.841
2020-02-09 | 9:49 | 49.843
2020-02-09 | 9:49 | 49.843
2020-02-09 | 9:49 | 49.841
2020-02-09 | 9:49 | 49.84
2020-02-09 | 9:49 | 49.844
2020-02-09 | 9:49 | 49.848
2020-02-09 | 9:50 | 49.847
2020-02-09 | 9:50 | 49.834
2020-02-09 | 9:50 | 49.84
2020-02-09 | 9:50 | 49.839
2020-02-09 | 9:50 | 49.841
2020-02-09 | 9:50 | 49.845
2020-02-09 | 9:50 | 49.837
2020-02-09 | 9:50 | 49.831
2020-02-09 | 9:50 | 49.835
2020-02-09 | 9:50 | 49.83
2020-02-09 | 9:50 | 49.827
2020-02-09 | 9:50 | 49.834
2020-02-09 | 9:50 | 49.842
2020-02-09 | 9:50 | 49.846
2020-02-09 | 9:50 | 49.846
2020-02-09 | 9:50 | 49.848
2020-02-09 | 9:50 | 49.848
2020-02-09 | 9:50 | 49.845
2020-02-09 | 9:50 | 49.845
2020-02-09 | 9:50 | 49.849
2020-02-09 | 9:50 | 49.851
2020-02-09 | 9:50 | 49.848
2020-02-09 | 9:50 | 49.834
2020-02-09 | 9:50 | 49.833
2020-02-09 | 9:50 | 49.83
2020-02-09 | 9:50 | 49.834
2020-02-09 | 9:50 | 49.832
2020-02-09 | 9:50 | 49.827
2020-02-09 | 9:50 | 49.84
2020-02-09 | 9:50 | 49.841
2020-02-09 | 9:50 | 49.833
2020-02-09 | 9:50 | 49.837
2020-02-09 | 9:50 | 49.842
2020-02-09 | 9:50 | 49.846
2020-02-09 | 9:50 | 49.852
2020-02-09 | 9:50 | 49.854
2020-02-09 | 9:50 | 49.851
2020-02-09 | 9:50 | 49.853
2020-02-09 | 9:50 | 49.852
2020-02-09 | 9:50 | 49.855
2020-02-09 | 9:50 | 49.854
2020-02-09 | 9:50 | 49.855
2020-02-09 | 9:50 | 49.857
2020-02-09 | 9:50 | 49.856
2020-02-09 | 9:50 | 49.855
2020-02-09 | 9:50 | 49.85
2020-02-09 | 9:50 | 49.85
2020-02-09 | 9:50 | 49.851
2020-02-09 | 9:50 | 49.849
2020-02-09 | 9:50 | 49.849
2020-02-09 | 9:50 | 49.847
2020-02-09 | 9:50 | 49.846
2020-02-09 | 9:50 | 49.858
2020-02-09 | 9:50 | 49.856
2020-02-09 | 9:50 | 49.851
2020-02-09 | 9:50 | 49.864
2020-02-09 | 9:50 | 49.859
2020-02-09 | 9:50 | 49.86
2020-02-09 | 9:50 | 49.86
2020-02-09 | 9:50 | 49.86
2020-02-09 | 9:50 | 49.861
2020-02-09 | 9:51 | 49.863
2020-02-09 | 9:51 | 49.869
2020-02-09 | 9:51 | 49.875
2020-02-09 | 9:51 | 49.87
2020-02-09 | 9:51 | 49.87
2020-02-09 | 9:51 | 49.87
2020-02-09 | 9:51 | 49.865
2020-02-09 | 9:51 | 49.878
2020-02-09 | 9:51 | 49.88
2020-02-09 | 9:51 | 49.873
2020-02-09 | 9:51 | 49.874
2020-02-09 | 9:51 | 49.876
2020-02-09 | 9:51 | 49.877
2020-02-09 | 9:51 | 49.871
2020-02-09 | 9:51 | 49.867
2020-02-09 | 9:51 | 49.869
2020-02-09 | 9:51 | 49.865
2020-02-09 | 9:51 | 49.876
2020-02-09 | 9:51 | 49.88
2020-02-09 | 9:51 | 49.87
2020-02-09 | 9:51 | 49.875
2020-02-09 | 9:51 | 49.878
2020-02-09 | 9:51 | 49.882
2020-02-09 | 9:51 | 49.878
2020-02-09 | 9:51 | 49.88
2020-02-09 | 9:51 | 49.889
2020-02-09 | 9:51 | 49.88
2020-02-09 | 9:51 | 49.886
2020-02-09 | 9:51 | 49.892
2020-02-09 | 9:51 | 49.887
2020-02-09 | 9:51 | 49.89
2020-02-09 | 9:51 | 49.893
2020-02-09 | 9:51 | 49.887
2020-02-09 | 9:51 | 49.893
2020-02-09 | 9:51 | 49.884
2020-02-09 | 9:51 | 49.881
2020-02-09 | 9:51 | 49.895
2020-02-09 | 9:51 | 49.885
2020-02-09 | 9:51 | 49.89
2020-02-09 | 9:51 | 49.887
2020-02-09 | 9:51 | 49.888
2020-02-09 | 9:51 | 49.901
2020-02-09 | 9:51 | 49.892
2020-02-09 | 9:51 | 49.9
2020-02-09 | 9:51 | 49.89
2020-02-09 | 9:51 | 49.895
2020-02-09 | 9:51 | 49.893
2020-02-09 | 9:51 | 49.902
2020-02-09 | 9:51 | 49.901
2020-02-09 | 9:51 | 49.915
2020-02-09 | 9:51 | 49.903
2020-02-09 | 9:51 | 49.905
2020-02-09 | 9:51 | 49.9
2020-02-09 | 9:51 | 49.899
2020-02-09 | 9:51 | 49.902
2020-02-09 | 9:51 | 49.899
2020-02-09 | 9:51 | 49.907
2020-02-09 | 9:51 | 49.903
2020-02-09 | 9:51 | 49.909
2020-02-09 | 9:52 | 49.907
2020-02-09 | 9:52 | 49.91
2020-02-09 | 9:52 | 49.916
2020-02-09 | 9:52 | 49.908
2020-02-09 | 9:52 | 49.912
2020-02-09 | 9:52 | 49.917
2020-02-09 | 9:52 | 49.908
2020-02-09 | 9:52 | 49.913
2020-02-09 | 9:52 | 49.913
2020-02-09 | 9:52 | 49.913
2020-02-09 | 9:52 | 49.914
2020-02-09 | 9:52 | 49.912
2020-02-09 | 9:52 | 49.915
2020-02-09 | 9:52 | 49.922
2020-02-09 | 9:52 | 49.919
2020-02-09 | 9:52 | 49.919
2020-02-09 | 9:52 | 49.93
2020-02-09 | 9:52 | 49.939
2020-02-09 | 9:52 | 49.932
2020-02-09 | 9:52 | 49.936
2020-02-09 | 9:52 | 49.941
2020-02-09 | 9:52 | 49.946
2020-02-09 | 9:52 | 49.946
2020-02-09 | 9:52 | 49.933
2020-02-09 | 9:52 | 49.939
2020-02-09 | 9:52 | 49.935
2020-02-09 | 9:52 | 49.938
2020-02-09 | 9:52 | 49.929
2020-02-09 | 9:52 | 49.934
2020-02-09 | 9:52 | 49.932
2020-02-09 | 9:52 | 49.935
2020-02-09 | 9:52 | 49.937
2020-02-09 | 9:52 | 49.942
2020-02-09 | 9:52 | 49.945
2020-02-09 | 9:52 | 49.951
2020-02-09 | 9:52 | 49.959
2020-02-09 | 9:52 | 49.958
2020-02-09 | 9:52 | 49.957
2020-02-09 | 9:52 | 49.96
2020-02-09 | 9:52 | 49.967
2020-02-09 | 9:52 | 49.961
2020-02-09 | 9:52 | 49.96
2020-02-09 | 9:52 | 49.96
2020-02-09 | 9:52 | 49.963
2020-02-09 | 9:52 | 49.962
2020-02-09 | 9:52 | 49.964
2020-02-09 | 9:52 | 49.977
2020-02-09 | 9:52 | 49.964
2020-02-09 | 9:52 | 49.964
2020-02-09 | 9:52 | 49.972
2020-02-09 | 9:52 | 49.968
2020-02-09 | 9:52 | 49.969
2020-02-09 | 9:52 | 49.971
2020-02-09 | 9:52 | 49.97
2020-02-09 | 9:52 | 49.972
2020-02-09 | 9:52 | 49.971
2020-02-09 | 9:52 | 49.975
2020-02-09 | 9:52 | 49.978
2020-02-09 | 9:52 | 49.978
2020-02-09 | 9:52 | 49.975
2020-02-09 | 9:52 | 49.981
2020-02-09 | 9:53 | 49.983
2020-02-09 | 9:53 | 49.984
2020-02-09 | 9:53 | 49.988
2020-02-09 | 9:53 | 49.986
2020-02-09 | 9:53 | 49.991
2020-02-09 | 9:53 | 49.991
2020-02-09 | 9:53 | 49.992
2020-02-09 | 9:53 | 50.001
2020-02-09 | 9:53 | 49.999
2020-02-09 | 9:53 | 50.001
2020-02-09 | 9:53 | 50.003
2020-02-09 | 9:53 | 50.003
2020-02-09 | 9:53 | 50.002
2020-02-09 | 9:53 | 50.001
2020-02-09 | 9:53 | 50.001
2020-02-09 | 9:53 | 50.009
2020-02-09 | 9:53 | 50.016
2020-02-09 | 9:53 | 50.014
2020-02-09 | 9:53 | 50.02
2020-02-09 | 9:53 | 50.022
2020-02-09 | 9:53 | 50.026
2020-02-09 | 9:53 | 50.028
2020-02-09 | 9:53 | 50.029
2020-02-09 | 9:53 | 50.033
2020-02-09 | 9:53 | 50.029
2020-02-09 | 9:53 | 50.032
2020-02-09 | 9:53 | 50.033
2020-02-09 | 9:53 | 50.033
2020-02-09 | 9:53 | 50.035

## Event 20200213-1
In UTC
Date | Time | Freq
2020-02-13 | 14:22 | 50.059
2020-02-13 | 14:22 | 50.056
2020-02-13 | 14:22 | 50.056
2020-02-13 | 14:22 | 50.055
2020-02-13 | 14:22 | 50.054
2020-02-13 | 14:22 | 50.053
2020-02-13 | 14:22 | 50.051
2020-02-13 | 14:22 | 50.049
2020-02-13 | 14:22 | 50.047
2020-02-13 | 14:22 | 50.045
2020-02-13 | 14:22 | 50.041
2020-02-13 | 14:22 | 50.038
2020-02-13 | 14:22 | 50.033
2020-02-13 | 14:22 | 50.032
2020-02-13 | 14:22 | 50.031
2020-02-13 | 14:22 | 50.028
2020-02-13 | 14:22 | 50.026
2020-02-13 | 14:22 | 50.024
2020-02-13 | 14:22 | 50.022
2020-02-13 | 14:22 | 50.022
2020-02-13 | 14:22 | 50.023
2020-02-13 | 14:22 | 50.021
2020-02-13 | 14:22 | 50.019
2020-02-13 | 14:22 | 50.017
2020-02-13 | 14:22 | 50.017
2020-02-13 | 14:22 | 50.017
2020-02-13 | 14:22 | 50.018
2020-02-13 | 14:22 | 50.018
2020-02-13 | 14:22 | 50.016
2020-02-13 | 14:22 | 50.013
2020-02-13 | 14:22 | 50.014
2020-02-13 | 14:23 | 50.015
2020-02-13 | 14:23 | 50.017
2020-02-13 | 14:23 | 50.02
2020-02-13 | 14:23 | 50.023
2020-02-13 | 14:23 | 50.029
2020-02-13 | 14:23 | 50.032
2020-02-13 | 14:23 | 50.037
2020-02-13 | 14:23 | 50.04
2020-02-13 | 14:23 | 50.044
2020-02-13 | 14:23 | 50.047
2020-02-13 | 14:23 | 50.048
2020-02-13 | 14:23 | 50.05
2020-02-13 | 14:23 | 50.051
2020-02-13 | 14:23 | 50.05
2020-02-13 | 14:23 | 50.052
2020-02-13 | 14:23 | 50.052
2020-02-13 | 14:23 | 50.054
2020-02-13 | 14:23 | 50.055
2020-02-13 | 14:23 | 50.055
2020-02-13 | 14:23 | 50.054
2020-02-13 | 14:23 | 50.053
2020-02-13 | 14:23 | 50.051
2020-02-13 | 14:23 | 50.05
2020-02-13 | 14:23 | 50.05
2020-02-13 | 14:23 | 50.047
2020-02-13 | 14:23 | 50.044
2020-02-13 | 14:23 | 50.042
2020-02-13 | 14:23 | 50.041
2020-02-13 | 14:23 | 50.039
2020-02-13 | 14:23 | 50.036
2020-02-13 | 14:23 | 50.036
2020-02-13 | 14:23 | 50.037
2020-02-13 | 14:23 | 50.037
2020-02-13 | 14:23 | 50.038
2020-02-13 | 14:23 | 50.04
2020-02-13 | 14:23 | 50.041
2020-02-13 | 14:23 | 50.041
2020-02-13 | 14:23 | 50.042
2020-02-13 | 14:23 | 50.043
2020-02-13 | 14:23 | 50.045
2020-02-13 | 14:23 | 50.046
2020-02-13 | 14:23 | 50.046
2020-02-13 | 14:23 | 50.046
2020-02-13 | 14:23 | 50.048
2020-02-13 | 14:23 | 50.05
2020-02-13 | 14:23 | 50.055
2020-02-13 | 14:23 | 50.057
2020-02-13 | 14:23 | 50.057
2020-02-13 | 14:23 | 50.058
2020-02-13 | 14:23 | 50.057
2020-02-13 | 14:23 | 50.057
2020-02-13 | 14:23 | 50.056
2020-02-13 | 14:23 | 50.054
2020-02-13 | 14:23 | 50.053
2020-02-13 | 14:23 | 50.052
2020-02-13 | 14:23 | 50.052
2020-02-13 | 14:23 | 50.052
2020-02-13 | 14:23 | 50.051
2020-02-13 | 14:23 | 50.052
2020-02-13 | 14:24 | 50.051
2020-02-13 | 14:24 | 50.051
2020-02-13 | 14:24 | 50.052
2020-02-13 | 14:24 | 50.053
2020-02-13 | 14:24 | 50.053
2020-02-13 | 14:24 | 50.053
2020-02-13 | 14:24 | 50.055
2020-02-13 | 14:24 | 50.056
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.06
2020-02-13 | 14:24 | 50.06
2020-02-13 | 14:24 | 50.059
2020-02-13 | 14:24 | 50.059
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.057
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.057
2020-02-13 | 14:24 | 50.056
2020-02-13 | 14:24 | 50.059
2020-02-13 | 14:24 | 50.062
2020-02-13 | 14:24 | 50.064
2020-02-13 | 14:24 | 50.065
2020-02-13 | 14:24 | 50.066
2020-02-13 | 14:24 | 50.067
2020-02-13 | 14:24 | 50.069
2020-02-13 | 14:24 | 50.068
2020-02-13 | 14:24 | 50.069
2020-02-13 | 14:24 | 50.069
2020-02-13 | 14:24 | 50.068
2020-02-13 | 14:24 | 50.069
2020-02-13 | 14:24 | 50.07
2020-02-13 | 14:24 | 50.071
2020-02-13 | 14:24 | 50.072
2020-02-13 | 14:24 | 50.074
2020-02-13 | 14:24 | 50.075
2020-02-13 | 14:24 | 50.078
2020-02-13 | 14:24 | 50.079
2020-02-13 | 14:24 | 50.081
2020-02-13 | 14:24 | 50.08
2020-02-13 | 14:24 | 50.078
2020-02-13 | 14:24 | 50.078
2020-02-13 | 14:24 | 50.077
2020-02-13 | 14:24 | 50.076
2020-02-13 | 14:24 | 50.077
2020-02-13 | 14:24 | 50.075
2020-02-13 | 14:24 | 50.076
2020-02-13 | 14:24 | 50.075
2020-02-13 | 14:24 | 50.073
2020-02-13 | 14:24 | 50.07
2020-02-13 | 14:24 | 50.07
2020-02-13 | 14:24 | 50.068
2020-02-13 | 14:24 | 50.065
2020-02-13 | 14:24 | 50.063
2020-02-13 | 14:24 | 50.061
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:24 | 50.056
2020-02-13 | 14:24 | 50.057
2020-02-13 | 14:24 | 50.058
2020-02-13 | 14:25 | 50.059
2020-02-13 | 14:25 | 50.061
2020-02-13 | 14:25 | 50.062
2020-02-13 | 14:25 | 50.063
2020-02-13 | 14:25 | 50.066
2020-02-13 | 14:25 | 50.068
2020-02-13 | 14:25 | 50.071
2020-02-13 | 14:25 | 50.076
2020-02-13 | 14:25 | 50.082
2020-02-13 | 14:25 | 50.089
2020-02-13 | 14:25 | 50.095
2020-02-13 | 14:25 | 50.099
2020-02-13 | 14:25 | 50.103
2020-02-13 | 14:25 | 50.104
2020-02-13 | 14:25 | 50.104
2020-02-13 | 14:25 | 50.101
2020-02-13 | 14:25 | 50.097
2020-02-13 | 14:25 | 50.093
2020-02-13 | 14:25 | 50.087
2020-02-13 | 14:25 | 50.084
2020-02-13 | 14:25 | 50.079
2020-02-13 | 14:25 | 50.077
2020-02-13 | 14:25 | 50.075
2020-02-13 | 14:25 | 50.077
2020-02-13 | 14:25 | 50.077
2020-02-13 | 14:25 | 50.078
2020-02-13 | 14:25 | 50.08
2020-02-13 | 14:25 | 50.081
2020-02-13 | 14:25 | 50.084
2020-02-13 | 14:25 | 50.087
2020-02-13 | 14:25 | 50.089
2020-02-13 | 14:25 | 50.091
2020-02-13 | 14:25 | 50.09
2020-02-13 | 14:25 | 50.089
2020-02-13 | 14:25 | 50.085
2020-02-13 | 14:25 | 50.079
2020-02-13 | 14:25 | 50.076
2020-02-13 | 14:25 | 50.073
2020-02-13 | 14:25 | 50.072
2020-02-13 | 14:25 | 50.071
2020-02-13 | 14:25 | 50.07
2020-02-13 | 14:25 | 50.07
2020-02-13 | 14:25 | 50.068
2020-02-13 | 14:25 | 50.066
2020-02-13 | 14:25 | 50.064
2020-02-13 | 14:25 | 50.066
2020-02-13 | 14:25 | 50.065
2020-02-13 | 14:25 | 50.067
2020-02-13 | 14:25 | 50.067
2020-02-13 | 14:25 | 50.068
2020-02-13 | 14:25 | 50.07
2020-02-13 | 14:25 | 50.068
2020-02-13 | 14:25 | 50.07
2020-02-13 | 14:25 | 50.07
2020-02-13 | 14:25 | 50.07
2020-02-13 | 14:25 | 50.069
2020-02-13 | 14:25 | 50.071
2020-02-13 | 14:25 | 50.072
2020-02-13 | 14:25 | 50.073
2020-02-13 | 14:26 | 50.074
2020-02-13 | 14:26 | 50.073
2020-02-13 | 14:26 | 50.074
2020-02-13 | 14:26 | 50.074
2020-02-13 | 14:26 | 50.074
2020-02-13 | 14:26 | 50.074
2020-02-13 | 14:26 | 50.075
2020-02-13 | 14:26 | 50.076
2020-02-13 | 14:26 | 50.076
2020-02-13 | 14:26 | 50.077
2020-02-13 | 14:26 | 50.079
2020-02-13 | 14:26 | 50.079
2020-02-13 | 14:26 | 50.081
2020-02-13 | 14:26 | 50.084
2020-02-13 | 14:26 | 50.087
2020-02-13 | 14:26 | 50.086
2020-02-13 | 14:26 | 50.085
2020-02-13 | 14:26 | 50.084
2020-02-13 | 14:26 | 50.082
2020-02-13 | 14:26 | 50.081
2020-02-13 | 14:26 | 50.081
2020-02-13 | 14:26 | 50.084
2020-02-13 | 14:26 | 50.084
2020-02-13 | 14:26 | 50.086
2020-02-13 | 14:26 | 50.087
2020-02-13 | 14:26 | 50.091
2020-02-13 | 14:26 | 50.093
2020-02-13 | 14:26 | 50.096
2020-02-13 | 14:26 | 50.095
2020-02-13 | 14:26 | 50.096
2020-02-13 | 14:26 | 50.094
2020-02-13 | 14:26 | 50.096
2020-02-13 | 14:26 | 50.095
2020-02-13 | 14:26 | 50.094
2020-02-13 | 14:26 | 50.092
2020-02-13 | 14:26 | 50.089
2020-02-13 | 14:26 | 50.088
2020-02-13 | 14:26 | 50.087
2020-02-13 | 14:26 | 50.085
2020-02-13 | 14:26 | 50.085
2020-02-13 | 14:26 | 50.083
2020-02-13 | 14:26 | 50.082
2020-02-13 | 14:26 | 50.081
2020-02-13 | 14:26 | 50.081
2020-02-13 | 14:26 | 50.08
2020-02-13 | 14:26 | 50.079
2020-02-13 | 14:26 | 50.078
2020-02-13 | 14:26 | 50.077
2020-02-13 | 14:26 | 50.075
2020-02-13 | 14:26 | 50.077
2020-02-13 | 14:26 | 50.076
2020-02-13 | 14:26 | 50.076
2020-02-13 | 14:26 | 50.077
2020-02-13 | 14:26 | 50.078
2020-02-13 | 14:26 | 50.079
2020-02-13 | 14:26 | 50.08
2020-02-13 | 14:26 | 50.079
2020-02-13 | 14:26 | 50.08
2020-02-13 | 14:26 | 50.08
2020-02-13 | 14:26 | 50.08
2020-02-13 | 14:26 | 50.081
2020-02-13 | 14:27 | 50.079
2020-02-13 | 14:27 | 50.079
2020-02-13 | 14:27 | 50.078
2020-02-13 | 14:27 | 50.08
2020-02-13 | 14:27 | 50.081
2020-02-13 | 14:27 | 50.083
2020-02-13 | 14:27 | 50.085
2020-02-13 | 14:27 | 50.087
2020-02-13 | 14:27 | 50.091
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.103
2020-02-13 | 14:27 | 50.107
2020-02-13 | 14:27 | 50.108
2020-02-13 | 14:27 | 50.11
2020-02-13 | 14:27 | 50.113
2020-02-13 | 14:27 | 50.113
2020-02-13 | 14:27 | 50.111
2020-02-13 | 14:27 | 50.109
2020-02-13 | 14:27 | 50.106
2020-02-13 | 14:27 | 50.105
2020-02-13 | 14:27 | 50.103
2020-02-13 | 14:27 | 50.101
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.099
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.096
2020-02-13 | 14:27 | 50.097
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:27 | 50.097
2020-02-13 | 14:27 | 50.095
2020-02-13 | 14:27 | 50.093
2020-02-13 | 14:27 | 50.093
2020-02-13 | 14:27 | 50.092
2020-02-13 | 14:27 | 50.091
2020-02-13 | 14:27 | 50.087
2020-02-13 | 14:27 | 50.086
2020-02-13 | 14:27 | 50.087
2020-02-13 | 14:27 | 50.087
2020-02-13 | 14:27 | 50.088
2020-02-13 | 14:27 | 50.089
2020-02-13 | 14:27 | 50.09
2020-02-13 | 14:27 | 50.094
2020-02-13 | 14:27 | 50.099
2020-02-13 | 14:27 | 50.101
2020-02-13 | 14:27 | 50.102
2020-02-13 | 14:27 | 50.105
2020-02-13 | 14:27 | 50.107
2020-02-13 | 14:27 | 50.107
2020-02-13 | 14:27 | 50.107
2020-02-13 | 14:27 | 50.106
2020-02-13 | 14:27 | 50.102
2020-02-13 | 14:27 | 50.099
2020-02-13 | 14:27 | 50.097
2020-02-13 | 14:27 | 50.096
2020-02-13 | 14:27 | 50.096
2020-02-13 | 14:27 | 50.098
2020-02-13 | 14:28 | 50.101
2020-02-13 | 14:28 | 50.103
2020-02-13 | 14:28 | 50.103
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.108
2020-02-13 | 14:28 | 50.106
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.108
2020-02-13 | 14:28 | 50.108
2020-02-13 | 14:28 | 50.11
2020-02-13 | 14:28 | 50.112
2020-02-13 | 14:28 | 50.11
2020-02-13 | 14:28 | 50.111
2020-02-13 | 14:28 | 50.108
2020-02-13 | 14:28 | 50.107
2020-02-13 | 14:28 | 50.103
2020-02-13 | 14:28 | 50.103
2020-02-13 | 14:28 | 50.101
2020-02-13 | 14:28 | 50.1
2020-02-13 | 14:28 | 50.1
2020-02-13 | 14:28 | 50.098
2020-02-13 | 14:28 | 50.099
2020-02-13 | 14:28 | 50.097
2020-02-13 | 14:28 | 50.096
2020-02-13 | 14:28 | 50.097
2020-02-13 | 14:28 | 50.097
2020-02-13 | 14:28 | 50.096
2020-02-13 | 14:28 | 50.095
2020-02-13 | 14:28 | 50.093
2020-02-13 | 14:28 | 50.092
2020-02-13 | 14:28 | 50.092
2020-02-13 | 14:28 | 50.093
2020-02-13 | 14:28 | 50.094
2020-02-13 | 14:28 | 50.092
2020-02-13 | 14:28 | 50.091
2020-02-13 | 14:28 | 50.09
2020-02-13 | 14:28 | 50.09
2020-02-13 | 14:28 | 50.09
2020-02-13 | 14:28 | 50.089
2020-02-13 | 14:28 | 50.088
2020-02-13 | 14:28 | 50.089
2020-02-13 | 14:28 | 50.088
2020-02-13 | 14:28 | 50.089
2020-02-13 | 14:28 | 50.086
2020-02-13 | 14:28 | 50.086
2020-02-13 | 14:28 | 50.085
2020-02-13 | 14:28 | 50.084
2020-02-13 | 14:28 | 50.085
2020-02-13 | 14:28 | 50.084
2020-02-13 | 14:28 | 50.084
2020-02-13 | 14:28 | 50.083
2020-02-13 | 14:28 | 50.081
2020-02-13 | 14:28 | 50.081
2020-02-13 | 14:28 | 50.081
2020-02-13 | 14:28 | 50.08
2020-02-13 | 14:28 | 50.081
2020-02-13 | 14:28 | 50.08
2020-02-13 | 14:29 | 50.081
2020-02-13 | 14:29 | 50.081
2020-02-13 | 14:29 | 50.081
2020-02-13 | 14:29 | 50.081
2020-02-13 | 14:29 | 50.08
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.08
2020-02-13 | 14:29 | 50.08
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.08
2020-02-13 | 14:29 | 50.081
2020-02-13 | 14:29 | 50.083
2020-02-13 | 14:29 | 50.083
2020-02-13 | 14:29 | 50.083
2020-02-13 | 14:29 | 50.085
2020-02-13 | 14:29 | 50.086
2020-02-13 | 14:29 | 50.087
2020-02-13 | 14:29 | 50.09
2020-02-13 | 14:29 | 50.094
2020-02-13 | 14:29 | 50.098
2020-02-13 | 14:29 | 50.1
2020-02-13 | 14:29 | 50.101
2020-02-13 | 14:29 | 50.103
2020-02-13 | 14:29 | 50.103
2020-02-13 | 14:29 | 50.105
2020-02-13 | 14:29 | 50.102
2020-02-13 | 14:29 | 50.097
2020-02-13 | 14:29 | 50.093
2020-02-13 | 14:29 | 50.087
2020-02-13 | 14:29 | 50.083
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.075
2020-02-13 | 14:29 | 50.071
2020-02-13 | 14:29 | 50.068
2020-02-13 | 14:29 | 50.065
2020-02-13 | 14:29 | 50.065
2020-02-13 | 14:29 | 50.065
2020-02-13 | 14:29 | 50.065
2020-02-13 | 14:29 | 50.067
2020-02-13 | 14:29 | 50.07
2020-02-13 | 14:29 | 50.074
2020-02-13 | 14:29 | 50.077
2020-02-13 | 14:29 | 50.076
2020-02-13 | 14:29 | 50.076
2020-02-13 | 14:29 | 50.076
2020-02-13 | 14:29 | 50.076
2020-02-13 | 14:29 | 50.078
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.08
2020-02-13 | 14:29 | 50.08
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.079
2020-02-13 | 14:29 | 50.078
2020-02-13 | 14:29 | 50.076
2020-02-13 | 14:29 | 50.077
2020-02-13 | 14:29 | 50.078
2020-02-13 | 14:29 | 50.081
2020-02-13 | 14:29 | 50.084
2020-02-13 | 14:30 | 50.087
2020-02-13 | 14:30 | 50.09
2020-02-13 | 14:30 | 50.091
2020-02-13 | 14:30 | 50.093
2020-02-13 | 14:30 | 50.095
2020-02-13 | 14:30 | 50.096
2020-02-13 | 14:30 | 50.096
2020-02-13 | 14:30 | 50.098
2020-02-13 | 14:30 | 50.098
2020-02-13 | 14:30 | 50.099
2020-02-13 | 14:30 | 50.101
2020-02-13 | 14:30 | 50.099
2020-02-13 | 14:30 | 50.097
2020-02-13 | 14:30 | 50.095
2020-02-13 | 14:30 | 50.094
2020-02-13 | 14:30 | 50.091
2020-02-13 | 14:30 | 50.09
2020-02-13 | 14:30 | 50.091
2020-02-13 | 14:30 | 50.09
2020-02-13 | 14:30 | 50.088
2020-02-13 | 14:30 | 50.086
2020-02-13 | 14:30 | 50.083
2020-02-13 | 14:30 | 50.081
2020-02-13 | 14:30 | 50.078
2020-02-13 | 14:30 | 50.074
2020-02-13 | 14:30 | 50.072
2020-02-13 | 14:30 | 50.072
2020-02-13 | 14:30 | 50.072
2020-02-13 | 14:30 | 50.073
2020-02-13 | 14:30 | 50.074
2020-02-13 | 14:30 | 50.074
2020-02-13 | 14:30 | 50.075
2020-02-13 | 14:30 | 50.078
2020-02-13 | 14:30 | 50.081
2020-02-13 | 14:30 | 50.082
2020-02-13 | 14:30 | 50.086
2020-02-13 | 14:30 | 50.088
2020-02-13 | 14:30 | 50.091
2020-02-13 | 14:30 | 50.091
2020-02-13 | 14:30 | 50.089
2020-02-13 | 14:30 | 50.085
2020-02-13 | 14:30 | 50.082
2020-02-13 | 14:30 | 50.079
2020-02-13 | 14:30 | 50.077
2020-02-13 | 14:30 | 50.074
2020-02-13 | 14:30 | 50.074
2020-02-13 | 14:30 | 50.071
2020-02-13 | 14:30 | 50.071
2020-02-13 | 14:30 | 50.07
2020-02-13 | 14:30 | 50.067
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.064
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.063
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.065
2020-02-13 | 14:30 | 50.067
2020-02-13 | 14:31 | 50.068
2020-02-13 | 14:31 | 50.067
2020-02-13 | 14:31 | 50.068
2020-02-13 | 14:31 | 50.068
2020-02-13 | 14:31 | 50.065
2020-02-13 | 14:31 | 50.065
2020-02-13 | 14:31 | 50.065
2020-02-13 | 14:31 | 50.067
2020-02-13 | 14:31 | 50.066
2020-02-13 | 14:31 | 50.067
2020-02-13 | 14:31 | 50.066
2020-02-13 | 14:31 | 50.067
2020-02-13 | 14:31 | 50.068
2020-02-13 | 14:31 | 50.07
2020-02-13 | 14:31 | 50.072
2020-02-13 | 14:31 | 50.074
2020-02-13 | 14:31 | 50.077
2020-02-13 | 14:31 | 50.076
2020-02-13 | 14:31 | 50.079
2020-02-13 | 14:31 | 50.079
2020-02-13 | 14:31 | 50.077
2020-02-13 | 14:31 | 50.077
2020-02-13 | 14:31 | 50.078
2020-02-13 | 14:31 | 50.078
2020-02-13 | 14:31 | 50.08
2020-02-13 | 14:31 | 50.082
2020-02-13 | 14:31 | 50.083
2020-02-13 | 14:31 | 50.085
2020-02-13 | 14:31 | 50.088
2020-02-13 | 14:31 | 50.09
2020-02-13 | 14:31 | 50.094
2020-02-13 | 14:31 | 50.095
2020-02-13 | 14:31 | 50.094
2020-02-13 | 14:31 | 50.094
2020-02-13 | 14:31 | 50.094
2020-02-13 | 14:31 | 50.093
2020-02-13 | 14:31 | 50.094
2020-02-13 | 14:31 | 50.094
2020-02-13 | 14:31 | 50.093
2020-02-13 | 14:31 | 50.092
2020-02-13 | 14:31 | 50.091
2020-02-13 | 14:31 | 50.089
2020-02-13 | 14:31 | 50.088
2020-02-13 | 14:31 | 50.088
2020-02-13 | 14:31 | 50.086
2020-02-13 | 14:31 | 50.084
2020-02-13 | 14:31 | 50.085
2020-02-13 | 14:31 | 50.084
2020-02-13 | 14:31 | 50.085
2020-02-13 | 14:31 | 50.084
2020-02-13 | 14:31 | 50.087
2020-02-13 | 14:31 | 50.089
2020-02-13 | 14:31 | 50.09
2020-02-13 | 14:31 | 50.089
2020-02-13 | 14:31 | 50.087
2020-02-13 | 14:31 | 50.084
2020-02-13 | 14:31 | 50.082
2020-02-13 | 14:31 | 50.079
2020-02-13 | 14:31 | 50.078
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.075
2020-02-13 | 14:32 | 50.074
2020-02-13 | 14:32 | 50.075
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.077
2020-02-13 | 14:32 | 50.078
2020-02-13 | 14:32 | 50.08
2020-02-13 | 14:32 | 50.082
2020-02-13 | 14:32 | 50.083
2020-02-13 | 14:32 | 50.083
2020-02-13 | 14:32 | 50.084
2020-02-13 | 14:32 | 50.083
2020-02-13 | 14:32 | 50.085
2020-02-13 | 14:32 | 50.084
2020-02-13 | 14:32 | 50.086
2020-02-13 | 14:32 | 50.088
2020-02-13 | 14:32 | 50.089
2020-02-13 | 14:32 | 50.092
2020-02-13 | 14:32 | 50.091
2020-02-13 | 14:32 | 50.091
2020-02-13 | 14:32 | 50.092
2020-02-13 | 14:32 | 50.093
2020-02-13 | 14:32 | 50.094
2020-02-13 | 14:32 | 50.092
2020-02-13 | 14:32 | 50.093
2020-02-13 | 14:32 | 50.093
2020-02-13 | 14:32 | 50.095
2020-02-13 | 14:32 | 50.095
2020-02-13 | 14:32 | 50.095
2020-02-13 | 14:32 | 50.094
2020-02-13 | 14:32 | 50.093
2020-02-13 | 14:32 | 50.09
2020-02-13 | 14:32 | 50.088
2020-02-13 | 14:32 | 50.086
2020-02-13 | 14:32 | 50.085
2020-02-13 | 14:32 | 50.085
2020-02-13 | 14:32 | 50.084
2020-02-13 | 14:32 | 50.082
2020-02-13 | 14:32 | 50.08
2020-02-13 | 14:32 | 50.078
2020-02-13 | 14:32 | 50.077
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.077
2020-02-13 | 14:32 | 50.077
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.075
2020-02-13 | 14:32 | 50.074
2020-02-13 | 14:32 | 50.073
2020-02-13 | 14:32 | 50.074
2020-02-13 | 14:32 | 50.073
2020-02-13 | 14:32 | 50.075
2020-02-13 | 14:32 | 50.075
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.076
2020-02-13 | 14:32 | 50.075
2020-02-13 | 14:32 | 50.071
2020-02-13 | 14:32 | 50.068
2020-02-13 | 14:32 | 50.065
2020-02-13 | 14:33 | 50.062
2020-02-13 | 14:33 | 50.059
2020-02-13 | 14:33 | 50.057
2020-02-13 | 14:33 | 50.056
2020-02-13 | 14:33 | 50.058
2020-02-13 | 14:33 | 50.059
2020-02-13 | 14:33 | 50.06
2020-02-13 | 14:33 | 50.062
2020-02-13 | 14:33 | 50.063
2020-02-13 | 14:33 | 50.063
2020-02-13 | 14:33 | 50.066
2020-02-13 | 14:33 | 50.067
2020-02-13 | 14:33 | 50.069
2020-02-13 | 14:33 | 50.07
2020-02-13 | 14:33 | 50.069
2020-02-13 | 14:33 | 50.068
2020-02-13 | 14:33 | 50.068
2020-02-13 | 14:33 | 50.068
2020-02-13 | 14:33 | 50.067
2020-02-13 | 14:33 | 50.065
2020-02-13 | 14:33 | 50.06
2020-02-13 | 14:33 | 50.056
2020-02-13 | 14:33 | 50.053
2020-02-13 | 14:33 | 50.049
2020-02-13 | 14:33 | 50.044
2020-02-13 | 14:33 | 50.04
2020-02-13 | 14:33 | 50.039
2020-02-13 | 14:33 | 50.038
2020-02-13 | 14:33 | 50.042
2020-02-13 | 14:33 | 50.044
2020-02-13 | 14:33 | 50.048
2020-02-13 | 14:33 | 50.05
2020-02-13 | 14:33 | 50.053
2020-02-13 | 14:33 | 50.054
2020-02-13 | 14:33 | 50.054
2020-02-13 | 14:33 | 50.055
2020-02-13 | 14:33 | 50.054
2020-02-13 | 14:33 | 50.053
2020-02-13 | 14:33 | 50.051
2020-02-13 | 14:33 | 50.052
2020-02-13 | 14:33 | 50.052
2020-02-13 | 14:33 | 50.055
2020-02-13 | 14:33 | 50.055
2020-02-13 | 14:33 | 50.06
2020-02-13 | 14:33 | 50.06
2020-02-13 | 14:33 | 50.062
2020-02-13 | 14:33 | 50.063
2020-02-13 | 14:33 | 50.066
2020-02-13 | 14:33 | 50.069
2020-02-13 | 14:33 | 50.072
2020-02-13 | 14:33 | 50.074
2020-02-13 | 14:33 | 50.077
2020-02-13 | 14:33 | 50.078
2020-02-13 | 14:33 | 50.076
2020-02-13 | 14:33 | 50.073
2020-02-13 | 14:33 | 50.07
2020-02-13 | 14:33 | 50.068
2020-02-13 | 14:33 | 50.066
2020-02-13 | 14:33 | 50.063
2020-02-13 | 14:34 | 50.059
2020-02-13 | 14:34 | 50.055
2020-02-13 | 14:34 | 50.054
2020-02-13 | 14:34 | 50.049
2020-02-13 | 14:34 | 50.048
2020-02-13 | 14:34 | 50.045
2020-02-13 | 14:34 | 50.044
2020-02-13 | 14:34 | 50.042
2020-02-13 | 14:34 | 50.043
2020-02-13 | 14:34 | 50.042
2020-02-13 | 14:34 | 50.043
2020-02-13 | 14:34 | 50.044
2020-02-13 | 14:34 | 50.043
2020-02-13 | 14:34 | 50.045
2020-02-13 | 14:34 | 50.045
2020-02-13 | 14:34 | 50.047
2020-02-13 | 14:34 | 50.048
2020-02-13 | 14:34 | 50.049
2020-02-13 | 14:34 | 50.05
2020-02-13 | 14:34 | 50.049
2020-02-13 | 14:34 | 50.049
2020-02-13 | 14:34 | 50.049
2020-02-13 | 14:34 | 50.048
2020-02-13 | 14:34 | 50.047
2020-02-13 | 14:34 | 50.046
2020-02-13 | 14:34 | 50.045
2020-02-13 | 14:34 | 50.043
2020-02-13 | 14:34 | 50.04
2020-02-13 | 14:34 | 50.038
2020-02-13 | 14:34 | 50.036
2020-02-13 | 14:34 | 50.033
2020-02-13 | 14:34 | 50.03
2020-02-13 | 14:34 | 50.028
2020-02-13 | 14:34 | 50.027
2020-02-13 | 14:34 | 50.025
2020-02-13 | 14:34 | 50.023
2020-02-13 | 14:34 | 50.019
2020-02-13 | 14:34 | 50.018
2020-02-13 | 14:34 | 50.017
2020-02-13 | 14:34 | 50.016
2020-02-13 | 14:34 | 50.019
2020-02-13 | 14:34 | 50.019
2020-02-13 | 14:34 | 50.018
2020-02-13 | 14:34 | 50.018
2020-02-13 | 14:34 | 50.019
2020-02-13 | 14:34 | 50.019
2020-02-13 | 14:34 | 50.02
2020-02-13 | 14:34 | 50.022
2020-02-13 | 14:34 | 50.023
2020-02-13 | 14:34 | 50.023
2020-02-13 | 14:34 | 50.022
2020-02-13 | 14:34 | 50.022
2020-02-13 | 14:34 | 50.022
2020-02-13 | 14:34 | 50.024
2020-02-13 | 14:34 | 50.027
2020-02-13 | 14:34 | 50.03
2020-02-13 | 14:34 | 50.033
2020-02-13 | 14:34 | 50.035
2020-02-13 | 14:34 | 50.039
2020-02-13 | 14:34 | 50.041
2020-02-13 | 14:34 | 50.043
2020-02-13 | 14:35 | 50.044
2020-02-13 | 14:35 | 50.044
2020-02-13 | 14:35 | 50.046
2020-02-13 | 14:35 | 50.047
2020-02-13 | 14:35 | 50.048
2020-02-13 | 14:35 | 50.05
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.053
2020-02-13 | 14:35 | 50.054
2020-02-13 | 14:35 | 50.055
2020-02-13 | 14:35 | 50.055
2020-02-13 | 14:35 | 50.057
2020-02-13 | 14:35 | 50.056
2020-02-13 | 14:35 | 50.057
2020-02-13 | 14:35 | 50.057
2020-02-13 | 14:35 | 50.055
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.055
2020-02-13 | 14:35 | 50.054
2020-02-13 | 14:35 | 50.055
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.052
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.049
2020-02-13 | 14:35 | 50.048
2020-02-13 | 14:35 | 50.043
2020-02-13 | 14:35 | 50.043
2020-02-13 | 14:35 | 50.04
2020-02-13 | 14:35 | 50.037
2020-02-13 | 14:35 | 50.034
2020-02-13 | 14:35 | 50.032
2020-02-13 | 14:35 | 50.03
2020-02-13 | 14:35 | 50.029
2020-02-13 | 14:35 | 50.028
2020-02-13 | 14:35 | 50.029
2020-02-13 | 14:35 | 50.032
2020-02-13 | 14:35 | 50.033
2020-02-13 | 14:35 | 50.033
2020-02-13 | 14:35 | 50.032
2020-02-13 | 14:35 | 50.031
2020-02-13 | 14:35 | 50.031
2020-02-13 | 14:35 | 50.035
2020-02-13 | 14:35 | 50.037
2020-02-13 | 14:35 | 50.037
2020-02-13 | 14:35 | 50.041
2020-02-13 | 14:35 | 50.043
2020-02-13 | 14:35 | 50.046
2020-02-13 | 14:35 | 50.047
2020-02-13 | 14:35 | 50.049
2020-02-13 | 14:35 | 50.051
2020-02-13 | 14:35 | 50.054
2020-02-13 | 14:36 | 50.053
2020-02-13 | 14:36 | 50.056
2020-02-13 | 14:36 | 50.058
2020-02-13 | 14:36 | 50.06
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.064
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.06
2020-02-13 | 14:36 | 50.06
2020-02-13 | 14:36 | 50.059
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.063
2020-02-13 | 14:36 | 50.062
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.058
2020-02-13 | 14:36 | 50.055
2020-02-13 | 14:36 | 50.052
2020-02-13 | 14:36 | 50.053
2020-02-13 | 14:36 | 50.052
2020-02-13 | 14:36 | 50.054
2020-02-13 | 14:36 | 50.058
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.065
2020-02-13 | 14:36 | 50.066
2020-02-13 | 14:36 | 50.068
2020-02-13 | 14:36 | 50.067
2020-02-13 | 14:36 | 50.065
2020-02-13 | 14:36 | 50.066
2020-02-13 | 14:36 | 50.064
2020-02-13 | 14:36 | 50.061
2020-02-13 | 14:36 | 50.057
2020-02-13 | 14:36 | 50.054
2020-02-13 | 14:36 | 50.053
2020-02-13 | 14:36 | 50.051
2020-02-13 | 14:36 | 50.05
2020-02-13 | 14:36 | 50.053
2020-02-13 | 14:36 | 50.057
2020-02-13 | 14:36 | 50.058
2020-02-13 | 14:36 | 50.064
2020-02-13 | 14:36 | 50.067
2020-02-13 | 14:36 | 50.07
2020-02-13 | 14:36 | 50.072
2020-02-13 | 14:36 | 50.073
2020-02-13 | 14:36 | 50.074
2020-02-13 | 14:36 | 50.075
2020-02-13 | 14:36 | 50.076
2020-02-13 | 14:36 | 50.076
2020-02-13 | 14:36 | 50.073
2020-02-13 | 14:36 | 50.074
2020-02-13 | 14:36 | 50.072
2020-02-13 | 14:36 | 50.073
2020-02-13 | 14:36 | 50.074
2020-02-13 | 14:36 | 50.074
2020-02-13 | 14:36 | 50.073
2020-02-13 | 14:37 | 50.073
2020-02-13 | 14:37 | 50.075
2020-02-13 | 14:37 | 50.076
2020-02-13 | 14:37 | 50.076
2020-02-13 | 14:37 | 50.077
2020-02-13 | 14:37 | 50.079
2020-02-13 | 14:37 | 50.084
2020-02-13 | 14:37 | 50.085
2020-02-13 | 14:37 | 50.088
2020-02-13 | 14:37 | 50.089
2020-02-13 | 14:37 | 50.09
2020-02-13 | 14:37 | 50.087
2020-02-13 | 14:37 | 50.088
2020-02-13 | 14:37 | 50.087
2020-02-13 | 14:37 | 50.086
2020-02-13 | 14:37 | 50.085
2020-02-13 | 14:37 | 50.086
2020-02-13 | 14:37 | 50.085
2020-02-13 | 14:37 | 50.085
2020-02-13 | 14:37 | 50.085
2020-02-13 | 14:37 | 50.086
2020-02-13 | 14:37 | 50.085
2020-02-13 | 14:37 | 50.083
2020-02-13 | 14:37 | 50.084
2020-02-13 | 14:37 | 50.084
2020-02-13 | 14:37 | 50.084
2020-02-13 | 14:37 | 50.084
2020-02-13 | 14:37 | 50.082
2020-02-13 | 14:37 | 50.08
2020-02-13 | 14:37 | 50.08
2020-02-13 | 14:37 | 50.077
2020-02-13 | 14:37 | 50.076
2020-02-13 | 14:37 | 50.075
2020-02-13 | 14:37 | 50.073
2020-02-13 | 14:37 | 50.072
2020-02-13 | 14:37 | 50.072
2020-02-13 | 14:37 | 50.071
2020-02-13 | 14:37 | 50.072
2020-02-13 | 14:37 | 50.071
2020-02-13 | 14:37 | 50.071
2020-02-13 | 14:37 | 50.071
2020-02-13 | 14:37 | 50.07
2020-02-13 | 14:37 | 50.069
2020-02-13 | 14:37 | 50.07
2020-02-13 | 14:37 | 50.07
2020-02-13 | 14:37 | 50.07
2020-02-13 | 14:37 | 50.067
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.066
2020-02-13 | 14:37 | 50.067
2020-02-13 | 14:37 | 50.064
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.065
2020-02-13 | 14:37 | 50.068
2020-02-13 | 14:37 | 50.072
2020-02-13 | 14:38 | 50.076
2020-02-13 | 14:38 | 50.081
2020-02-13 | 14:38 | 50.084
2020-02-13 | 14:38 | 50.087
2020-02-13 | 14:38 | 50.088
2020-02-13 | 14:38 | 50.088
2020-02-13 | 14:38 | 50.089
2020-02-13 | 14:38 | 50.089
2020-02-13 | 14:38 | 50.087
2020-02-13 | 14:38 | 50.087
2020-02-13 | 14:38 | 50.089
2020-02-13 | 14:38 | 50.09
2020-02-13 | 14:38 | 50.091
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.09
2020-02-13 | 14:38 | 50.089
2020-02-13 | 14:38 | 50.087
2020-02-13 | 14:38 | 50.085
2020-02-13 | 14:38 | 50.087
2020-02-13 | 14:38 | 50.088
2020-02-13 | 14:38 | 50.09
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.095
2020-02-13 | 14:38 | 50.095
2020-02-13 | 14:38 | 50.092
2020-02-13 | 14:38 | 50.091
2020-02-13 | 14:38 | 50.089
2020-02-13 | 14:38 | 50.086
2020-02-13 | 14:38 | 50.083
2020-02-13 | 14:38 | 50.082
2020-02-13 | 14:38 | 50.08
2020-02-13 | 14:38 | 50.08
2020-02-13 | 14:38 | 50.079
2020-02-13 | 14:38 | 50.08
2020-02-13 | 14:38 | 50.08
2020-02-13 | 14:38 | 50.08
2020-02-13 | 14:38 | 50.08
2020-02-13 | 14:38 | 50.082
2020-02-13 | 14:38 | 50.083
2020-02-13 | 14:38 | 50.085
2020-02-13 | 14:38 | 50.086
2020-02-13 | 14:38 | 50.088
2020-02-13 | 14:38 | 50.089
2020-02-13 | 14:38 | 50.091
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.093
2020-02-13 | 14:38 | 50.095
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.094
2020-02-13 | 14:38 | 50.095
2020-02-13 | 14:38 | 50.095
2020-02-13 | 14:38 | 50.096
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.099
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.096
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.095
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.096
2020-02-13 | 14:39 | 50.095
2020-02-13 | 14:39 | 50.093
2020-02-13 | 14:39 | 50.091
2020-02-13 | 14:39 | 50.088
2020-02-13 | 14:39 | 50.085
2020-02-13 | 14:39 | 50.084
2020-02-13 | 14:39 | 50.083
2020-02-13 | 14:39 | 50.082
2020-02-13 | 14:39 | 50.084
2020-02-13 | 14:39 | 50.085
2020-02-13 | 14:39 | 50.087
2020-02-13 | 14:39 | 50.087
2020-02-13 | 14:39 | 50.089
2020-02-13 | 14:39 | 50.088
2020-02-13 | 14:39 | 50.09
2020-02-13 | 14:39 | 50.091
2020-02-13 | 14:39 | 50.09
2020-02-13 | 14:39 | 50.089
2020-02-13 | 14:39 | 50.088
2020-02-13 | 14:39 | 50.087
2020-02-13 | 14:39 | 50.087
2020-02-13 | 14:39 | 50.088
2020-02-13 | 14:39 | 50.089
2020-02-13 | 14:39 | 50.093
2020-02-13 | 14:39 | 50.096
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.101
2020-02-13 | 14:39 | 50.105
2020-02-13 | 14:39 | 50.103
2020-02-13 | 14:39 | 50.103
2020-02-13 | 14:39 | 50.1
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.094
2020-02-13 | 14:39 | 50.095
2020-02-13 | 14:39 | 50.096
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.096
2020-02-13 | 14:39 | 50.097
2020-02-13 | 14:39 | 50.098
2020-02-13 | 14:39 | 50.1
2020-02-13 | 14:40 | 50.101
2020-02-13 | 14:40 | 50.098
2020-02-13 | 14:40 | 50.098
2020-02-13 | 14:40 | 50.097
2020-02-13 | 14:40 | 50.096
2020-02-13 | 14:40 | 50.095
2020-02-13 | 14:40 | 50.095
2020-02-13 | 14:40 | 50.097
2020-02-13 | 14:40 | 50.097
2020-02-13 | 14:40 | 50.103
2020-02-13 | 14:40 | 50.107
2020-02-13 | 14:40 | 50.111
2020-02-13 | 14:40 | 50.115
2020-02-13 | 14:40 | 50.119
2020-02-13 | 14:40 | 50.123
2020-02-13 | 14:40 | 50.125
2020-02-13 | 14:40 | 50.128
2020-02-13 | 14:40 | 50.127
2020-02-13 | 14:40 | 50.129
2020-02-13 | 14:40 | 50.128
2020-02-13 | 14:40 | 50.128
2020-02-13 | 14:40 | 50.127
2020-02-13 | 14:40 | 50.126
2020-02-13 | 14:40 | 50.126
2020-02-13 | 14:40 | 50.127
2020-02-13 | 14:40 | 50.126
2020-02-13 | 14:40 | 50.126
2020-02-13 | 14:40 | 50.123
2020-02-13 | 14:40 | 50.12
2020-02-13 | 14:40 | 50.119
2020-02-13 | 14:40 | 50.115
2020-02-13 | 14:40 | 50.119
2020-02-13 | 14:40 | 50.118
2020-02-13 | 14:40 | 50.119
2020-02-13 | 14:40 | 50.121
2020-02-13 | 14:40 | 50.123
2020-02-13 | 14:40 | 50.125
2020-02-13 | 14:40 | 50.127
2020-02-13 | 14:40 | 50.128
2020-02-13 | 14:40 | 50.13
2020-02-13 | 14:40 | 50.132
2020-02-13 | 14:40 | 50.134
2020-02-13 | 14:40 | 50.136
2020-02-13 | 14:40 | 50.139
2020-02-13 | 14:40 | 50.141
2020-02-13 | 14:40 | 50.14
2020-02-13 | 14:40 | 50.141
2020-02-13 | 14:40 | 50.141
2020-02-13 | 14:40 | 50.142
2020-02-13 | 14:40 | 50.145
2020-02-13 | 14:40 | 50.143
2020-02-13 | 14:40 | 50.145
2020-02-13 | 14:40 | 50.147
2020-02-13 | 14:40 | 50.15
2020-02-13 | 14:40 | 50.152
2020-02-13 | 14:40 | 50.153
2020-02-13 | 14:40 | 50.155
2020-02-13 | 14:40 | 50.156
2020-02-13 | 14:40 | 50.157
2020-02-13 | 14:40 | 50.159
2020-02-13 | 14:40 | 50.16
2020-02-13 | 14:41 | 50.16
2020-02-13 | 14:41 | 50.16
2020-02-13 | 14:41 | 50.159
2020-02-13 | 14:41 | 50.16
2020-02-13 | 14:41 | 50.161
2020-02-13 | 14:41 | 50.162
2020-02-13 | 14:41 | 50.163
2020-02-13 | 14:41 | 50.167
2020-02-13 | 14:41 | 50.169
2020-02-13 | 14:41 | 50.17
2020-02-13 | 14:41 | 50.171
2020-02-13 | 14:41 | 50.17
2020-02-13 | 14:41 | 50.17
2020-02-13 | 14:41 | 50.171
2020-02-13 | 14:41 | 50.17
2020-02-13 | 14:41 | 50.17
2020-02-13 | 14:41 | 50.17
2020-02-13 | 14:41 | 50.169
2020-02-13 | 14:41 | 50.171
2020-02-13 | 14:41 | 50.172
2020-02-13 | 14:41 | 50.173
2020-02-13 | 14:41 | 50.173
2020-02-13 | 14:41 | 50.175
2020-02-13 | 14:41 | 50.177
2020-02-13 | 14:41 | 50.177
2020-02-13 | 14:41 | 50.176
2020-02-13 | 14:41 | 50.175
2020-02-13 | 14:41 | 50.172
2020-02-13 | 14:41 | 50.168
2020-02-13 | 14:41 | 50.163
2020-02-13 | 14:41 | 50.158
2020-02-13 | 14:41 | 50.155
2020-02-13 | 14:41 | 50.153
2020-02-13 | 14:41 | 50.152
2020-02-13 | 14:41 | 50.149
2020-02-13 | 14:41 | 50.147
2020-02-13 | 14:41 | 50.144
2020-02-13 | 14:41 | 50.14
2020-02-13 | 14:41 | 50.14
2020-02-13 | 14:41 | 50.139
2020-02-13 | 14:41 | 50.141
2020-02-13 | 14:41 | 50.145
2020-02-13 | 14:41 | 50.148
2020-02-13 | 14:41 | 50.147
2020-02-13 | 14:41 | 50.149
2020-02-13 | 14:41 | 50.15
2020-02-13 | 14:41 | 50.149
2020-02-13 | 14:41 | 50.149
2020-02-13 | 14:41 | 50.15
2020-02-13 | 14:41 | 50.149
2020-02-13 | 14:41 | 50.148
2020-02-13 | 14:41 | 50.146
2020-02-13 | 14:41 | 50.145
2020-02-13 | 14:41 | 50.142
2020-02-13 | 14:41 | 50.143
2020-02-13 | 14:41 | 50.144
2020-02-13 | 14:41 | 50.145
2020-02-13 | 14:41 | 50.147
2020-02-13 | 14:41 | 50.148
2020-02-13 | 14:42 | 50.148
2020-02-13 | 14:42 | 50.147
2020-02-13 | 14:42 | 50.146
2020-02-13 | 14:42 | 50.145
2020-02-13 | 14:42 | 50.146
2020-02-13 | 14:42 | 50.146
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.148
2020-02-13 | 14:42 | 50.145
2020-02-13 | 14:42 | 50.143
2020-02-13 | 14:42 | 50.145
2020-02-13 | 14:42 | 50.146
2020-02-13 | 14:42 | 50.148
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.147
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.151
2020-02-13 | 14:42 | 50.151
2020-02-13 | 14:42 | 50.152
2020-02-13 | 14:42 | 50.152
2020-02-13 | 14:42 | 50.149
2020-02-13 | 14:42 | 50.148
2020-02-13 | 14:42 | 50.144
2020-02-13 | 14:42 | 50.14
2020-02-13 | 14:42 | 50.14
2020-02-13 | 14:42 | 50.138
2020-02-13 | 14:42 | 50.136
2020-02-13 | 14:42 | 50.133
2020-02-13 | 14:42 | 50.129
2020-02-13 | 14:42 | 50.126
2020-02-13 | 14:42 | 50.124
2020-02-13 | 14:42 | 50.125
2020-02-13 | 14:42 | 50.126
2020-02-13 | 14:42 | 50.127
2020-02-13 | 14:42 | 50.127
2020-02-13 | 14:42 | 50.125
2020-02-13 | 14:42 | 50.125
2020-02-13 | 14:42 | 50.123
2020-02-13 | 14:42 | 50.122
2020-02-13 | 14:42 | 50.124
2020-02-13 | 14:42 | 50.124
2020-02-13 | 14:42 | 50.125
2020-02-13 | 14:42 | 50.125
2020-02-13 | 14:42 | 50.126
2020-02-13 | 14:42 | 50.129
2020-02-13 | 14:42 | 50.127
2020-02-13 | 14:42 | 50.128
2020-02-13 | 14:42 | 50.129
2020-02-13 | 14:42 | 50.129
2020-02-13 | 14:42 | 50.131
2020-02-13 | 14:42 | 50.134
2020-02-13 | 14:42 | 50.136
2020-02-13 | 14:42 | 50.137
2020-02-13 | 14:42 | 50.14
2020-02-13 | 14:42 | 50.14
2020-02-13 | 14:42 | 50.14
2020-02-13 | 14:42 | 50.143
2020-02-13 | 14:42 | 50.145
2020-02-13 | 14:43 | 50.146
2020-02-13 | 14:43 | 50.146
2020-02-13 | 14:43 | 50.147
2020-02-13 | 14:43 | 50.146
2020-02-13 | 14:43 | 50.144
2020-02-13 | 14:43 | 50.141
2020-02-13 | 14:43 | 50.137
2020-02-13 | 14:43 | 50.136
2020-02-13 | 14:43 | 50.134
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.133
2020-02-13 | 14:43 | 50.134
2020-02-13 | 14:43 | 50.134
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.134
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.134
2020-02-13 | 14:43 | 50.133
2020-02-13 | 14:43 | 50.132
2020-02-13 | 14:43 | 50.13
2020-02-13 | 14:43 | 50.13
2020-02-13 | 14:43 | 50.13
2020-02-13 | 14:43 | 50.131
2020-02-13 | 14:43 | 50.133
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.137
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.135
2020-02-13 | 14:43 | 50.131
2020-02-13 | 14:43 | 50.128
2020-02-13 | 14:43 | 50.125
2020-02-13 | 14:43 | 50.123
2020-02-13 | 14:43 | 50.12
2020-02-13 | 14:43 | 50.12
2020-02-13 | 14:43 | 50.119
2020-02-13 | 14:43 | 50.116
2020-02-13 | 14:43 | 50.114
2020-02-13 | 14:43 | 50.113
2020-02-13 | 14:43 | 50.113
2020-02-13 | 14:43 | 50.112
2020-02-13 | 14:43 | 50.111
2020-02-13 | 14:43 | 50.11
2020-02-13 | 14:43 | 50.111
2020-02-13 | 14:43 | 50.109
2020-02-13 | 14:43 | 50.108
2020-02-13 | 14:43 | 50.108
2020-02-13 | 14:43 | 50.106
2020-02-13 | 14:43 | 50.104
2020-02-13 | 14:43 | 50.102
2020-02-13 | 14:43 | 50.1
2020-02-13 | 14:43 | 50.098
2020-02-13 | 14:43 | 50.098
2020-02-13 | 14:43 | 50.1
2020-02-13 | 14:43 | 50.101
2020-02-13 | 14:43 | 50.101
2020-02-13 | 14:43 | 50.1
2020-02-13 | 14:43 | 50.1
2020-02-13 | 14:43 | 50.102
2020-02-13 | 14:44 | 50.102
2020-02-13 | 14:44 | 50.103
2020-02-13 | 14:44 | 50.103
2020-02-13 | 14:44 | 50.104
2020-02-13 | 14:44 | 50.102
2020-02-13 | 14:44 | 50.099
2020-02-13 | 14:44 | 50.095
2020-02-13 | 14:44 | 50.091
2020-02-13 | 14:44 | 50.089
2020-02-13 | 14:44 | 50.088
2020-02-13 | 14:44 | 50.087
2020-02-13 | 14:44 | 50.089
2020-02-13 | 14:44 | 50.09
2020-02-13 | 14:44 | 50.094
2020-02-13 | 14:44 | 50.095
2020-02-13 | 14:44 | 50.097
2020-02-13 | 14:44 | 50.1
2020-02-13 | 14:44 | 50.1
2020-02-13 | 14:44 | 50.101
2020-02-13 | 14:44 | 50.101
2020-02-13 | 14:44 | 50.1
2020-02-13 | 14:44 | 50.098
2020-02-13 | 14:44 | 50.098
2020-02-13 | 14:44 | 50.096
2020-02-13 | 14:44 | 50.096
2020-02-13 | 14:44 | 50.097
2020-02-13 | 14:44 | 50.098
2020-02-13 | 14:44 | 50.099
2020-02-13 | 14:44 | 50.099
2020-02-13 | 14:44 | 50.1
2020-02-13 | 14:44 | 50.1
2020-02-13 | 14:44 | 50.1
2020-02-13 | 14:44 | 50.098
2020-02-13 | 14:44 | 50.097
2020-02-13 | 14:44 | 50.096
2020-02-13 | 14:44 | 50.094
2020-02-13 | 14:44 | 50.093
2020-02-13 | 14:44 | 50.092
2020-02-13 | 14:44 | 50.091
2020-02-13 | 14:44 | 50.088
2020-02-13 | 14:44 | 50.084
2020-02-13 | 14:44 | 50.082
2020-02-13 | 14:44 | 50.079
2020-02-13 | 14:44 | 50.076
2020-02-13 | 14:44 | 50.074
2020-02-13 | 14:44 | 50.07
2020-02-13 | 14:44 | 50.066
2020-02-13 | 14:44 | 50.063
2020-02-13 | 14:44 | 50.06
2020-02-13 | 14:44 | 50.058
2020-02-13 | 14:44 | 50.056
2020-02-13 | 14:44 | 50.056
2020-02-13 | 14:44 | 50.055
2020-02-13 | 14:44 | 50.055
2020-02-13 | 14:44 | 50.055
2020-02-13 | 14:44 | 50.054
2020-02-13 | 14:44 | 50.053
2020-02-13 | 14:44 | 50.054
2020-02-13 | 14:44 | 50.055
2020-02-13 | 14:44 | 50.055
2020-02-13 | 14:44 | 50.057
2020-02-13 | 14:45 | 50.056
2020-02-13 | 14:45 | 50.057
2020-02-13 | 14:45 | 50.057
2020-02-13 | 14:45 | 50.057
2020-02-13 | 14:45 | 50.058
2020-02-13 | 14:45 | 50.059
2020-02-13 | 14:45 | 50.059
2020-02-13 | 14:45 | 50.06
2020-02-13 | 14:45 | 50.061
2020-02-13 | 14:45 | 50.064
2020-02-13 | 14:45 | 50.067
2020-02-13 | 14:45 | 50.071
2020-02-13 | 14:45 | 50.073
2020-02-13 | 14:45 | 50.076
2020-02-13 | 14:45 | 50.076
2020-02-13 | 14:45 | 50.077
2020-02-13 | 14:45 | 50.076
2020-02-13 | 14:45 | 50.073
2020-02-13 | 14:45 | 50.073
2020-02-13 | 14:45 | 50.071
2020-02-13 | 14:45 | 50.07
2020-02-13 | 14:45 | 50.068
2020-02-13 | 14:45 | 50.068
2020-02-13 | 14:45 | 50.068
2020-02-13 | 14:45 | 50.069
2020-02-13 | 14:45 | 50.07
2020-02-13 | 14:45 | 50.069
2020-02-13 | 14:45 | 50.069
2020-02-13 | 14:45 | 50.069
2020-02-13 | 14:45 | 50.069
2020-02-13 | 14:45 | 50.068
2020-02-13 | 14:45 | 50.067
2020-02-13 | 14:45 | 50.065
2020-02-13 | 14:45 | 50.064
2020-02-13 | 14:45 | 50.064
2020-02-13 | 14:45 | 50.063
2020-02-13 | 14:45 | 50.062
2020-02-13 | 14:45 | 50.06
2020-02-13 | 14:45 | 50.059
2020-02-13 | 14:45 | 50.058
2020-02-13 | 14:45 | 50.059
2020-02-13 | 14:45 | 50.059
2020-02-13 | 14:45 | 50.058
2020-02-13 | 14:45 | 50.055
2020-02-13 | 14:45 | 50.052
2020-02-13 | 14:45 | 50.05
2020-02-13 | 14:45 | 50.049
2020-02-13 | 14:45 | 50.05
2020-02-13 | 14:45 | 50.052
2020-02-13 | 14:45 | 50.054
2020-02-13 | 14:45 | 50.055
2020-02-13 | 14:45 | 50.057
2020-02-13 | 14:45 | 50.058
2020-02-13 | 14:45 | 50.06
2020-02-13 | 14:45 | 50.058
2020-02-13 | 14:45 | 50.056
2020-02-13 | 14:45 | 50.054
2020-02-13 | 14:45 | 50.052
2020-02-13 | 14:45 | 50.047
2020-02-13 | 14:46 | 50.043
2020-02-13 | 14:46 | 50.038
2020-02-13 | 14:46 | 50.034
2020-02-13 | 14:46 | 50.03
2020-02-13 | 14:46 | 50.026
2020-02-13 | 14:46 | 50.025
2020-02-13 | 14:46 | 50.025
2020-02-13 | 14:46 | 50.025
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:46 | 50.022
2020-02-13 | 14:46 | 50.02
2020-02-13 | 14:46 | 50.02
2020-02-13 | 14:46 | 50.018
2020-02-13 | 14:46 | 50.016
2020-02-13 | 14:46 | 50.014
2020-02-13 | 14:46 | 50.011
2020-02-13 | 14:46 | 50.008
2020-02-13 | 14:46 | 50.005
2020-02-13 | 14:46 | 50
2020-02-13 | 14:46 | 49.997
2020-02-13 | 14:46 | 49.996
2020-02-13 | 14:46 | 49.998
2020-02-13 | 14:46 | 49.998
2020-02-13 | 14:46 | 49.999
2020-02-13 | 14:46 | 49.999
2020-02-13 | 14:46 | 50
2020-02-13 | 14:46 | 50.002
2020-02-13 | 14:46 | 50.003
2020-02-13 | 14:46 | 50.008
2020-02-13 | 14:46 | 50.011
2020-02-13 | 14:46 | 50.014
2020-02-13 | 14:46 | 50.017
2020-02-13 | 14:46 | 50.019
2020-02-13 | 14:46 | 50.018
2020-02-13 | 14:46 | 50.017
2020-02-13 | 14:46 | 50.016
2020-02-13 | 14:46 | 50.015
2020-02-13 | 14:46 | 50.015
2020-02-13 | 14:46 | 50.014
2020-02-13 | 14:46 | 50.014
2020-02-13 | 14:46 | 50.013
2020-02-13 | 14:46 | 50.014
2020-02-13 | 14:46 | 50.012
2020-02-13 | 14:46 | 50.012
2020-02-13 | 14:46 | 50.01
2020-02-13 | 14:46 | 50.01
2020-02-13 | 14:46 | 50.009
2020-02-13 | 14:46 | 50.01
2020-02-13 | 14:46 | 50.009
2020-02-13 | 14:46 | 50.01
2020-02-13 | 14:46 | 50.01
2020-02-13 | 14:46 | 50.013
2020-02-13 | 14:46 | 50.017
2020-02-13 | 14:46 | 50.02
2020-02-13 | 14:46 | 50.022
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:46 | 50.024
2020-02-13 | 14:47 | 50.023
2020-02-13 | 14:47 | 50.02
2020-02-13 | 14:47 | 50.019
2020-02-13 | 14:47 | 50.017
2020-02-13 | 14:47 | 50.02
2020-02-13 | 14:47 | 50.02
2020-02-13 | 14:47 | 50.019
2020-02-13 | 14:47 | 50.016
2020-02-13 | 14:47 | 50.016
2020-02-13 | 14:47 | 50.014
2020-02-13 | 14:47 | 50.012
2020-02-13 | 14:47 | 50.009
2020-02-13 | 14:47 | 50.008
2020-02-13 | 14:47 | 50.008
2020-02-13 | 14:47 | 50.007
2020-02-13 | 14:47 | 50.008
2020-02-13 | 14:47 | 50.008
2020-02-13 | 14:47 | 50.009
2020-02-13 | 14:47 | 50.01
2020-02-13 | 14:47 | 50.012
2020-02-13 | 14:47 | 50.012
2020-02-13 | 14:47 | 50.011
2020-02-13 | 14:47 | 50.008
2020-02-13 | 14:47 | 50.006
2020-02-13 | 14:47 | 50.003
2020-02-13 | 14:47 | 50
2020-02-13 | 14:47 | 49.998
2020-02-13 | 14:47 | 49.996
2020-02-13 | 14:47 | 49.993
2020-02-13 | 14:47 | 49.987
2020-02-13 | 14:47 | 49.985
2020-02-13 | 14:47 | 49.981
2020-02-13 | 14:47 | 49.977
2020-02-13 | 14:47 | 49.973
2020-02-13 | 14:47 | 49.971
2020-02-13 | 14:47 | 49.968
2020-02-13 | 14:47 | 49.964
2020-02-13 | 14:47 | 49.96
2020-02-13 | 14:47 | 49.956
2020-02-13 | 14:47 | 49.955
2020-02-13 | 14:47 | 49.953
2020-02-13 | 14:47 | 49.953
2020-02-13 | 14:47 | 49.953
2020-02-13 | 14:47 | 49.954
2020-02-13 | 14:47 | 49.956
2020-02-13 | 14:47 | 49.958
2020-02-13 | 14:47 | 49.96
2020-02-13 | 14:47 | 49.964
2020-02-13 | 14:47 | 49.967
2020-02-13 | 14:47 | 49.973
2020-02-13 | 14:47 | 49.974
2020-02-13 | 14:47 | 49.976
2020-02-13 | 14:47 | 49.977
2020-02-13 | 14:47 | 49.977
2020-02-13 | 14:47 | 49.975
2020-02-13 | 14:47 | 49.974
2020-02-13 | 14:47 | 49.973
2020-02-13 | 14:47 | 49.974
2020-02-13 | 14:47 | 49.976
2020-02-13 | 14:48 | 49.979
2020-02-13 | 14:48 | 49.98
2020-02-13 | 14:48 | 49.981
2020-02-13 | 14:48 | 49.982
2020-02-13 | 14:48 | 49.984
2020-02-13 | 14:48 | 49.987
2020-02-13 | 14:48 | 49.989
2020-02-13 | 14:48 | 49.992
2020-02-13 | 14:48 | 49.994
2020-02-13 | 14:48 | 49.996
2020-02-13 | 14:48 | 49.998
2020-02-13 | 14:48 | 50
2020-02-13 | 14:48 | 50
2020-02-13 | 14:48 | 50.002
2020-02-13 | 14:48 | 50.004
2020-02-13 | 14:48 | 50.008
2020-02-13 | 14:48 | 50.012
2020-02-13 | 14:48 | 50.017
2020-02-13 | 14:48 | 50.022
2020-02-13 | 14:48 | 50.024
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.027
2020-02-13 | 14:48 | 50.027
2020-02-13 | 14:48 | 50.029
2020-02-13 | 14:48 | 50.031
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.032
2020-02-13 | 14:48 | 50.032
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.034
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.035
2020-02-13 | 14:48 | 50.034
2020-02-13 | 14:48 | 50.034
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:48 | 50.031
2020-02-13 | 14:48 | 50.03
2020-02-13 | 14:48 | 50.028
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.024
2020-02-13 | 14:48 | 50.025
2020-02-13 | 14:48 | 50.021
2020-02-13 | 14:48 | 50.021
2020-02-13 | 14:48 | 50.023
2020-02-13 | 14:48 | 50.024
2020-02-13 | 14:48 | 50.026
2020-02-13 | 14:48 | 50.027
2020-02-13 | 14:48 | 50.029
2020-02-13 | 14:48 | 50.03
2020-02-13 | 14:48 | 50.032
2020-02-13 | 14:48 | 50.032
2020-02-13 | 14:48 | 50.032
2020-02-13 | 14:48 | 50.033
2020-02-13 | 14:49 | 50.034
2020-02-13 | 14:49 | 50.035
2020-02-13 | 14:49 | 50.037
2020-02-13 | 14:49 | 50.038
2020-02-13 | 14:49 | 50.038
2020-02-13 | 14:49 | 50.042
2020-02-13 | 14:49 | 50.042
2020-02-13 | 14:49 | 50.044
2020-02-13 | 14:49 | 50.046
2020-02-13 | 14:49 | 50.048
2020-02-13 | 14:49 | 50.05
2020-02-13 | 14:49 | 50.053
2020-02-13 | 14:49 | 50.054
2020-02-13 | 14:49 | 50.056
2020-02-13 | 14:49 | 50.057
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.062
2020-02-13 | 14:49 | 50.063
2020-02-13 | 14:49 | 50.065
2020-02-13 | 14:49 | 50.065
2020-02-13 | 14:49 | 50.066
2020-02-13 | 14:49 | 50.066
2020-02-13 | 14:49 | 50.065
2020-02-13 | 14:49 | 50.064
2020-02-13 | 14:49 | 50.064
2020-02-13 | 14:49 | 50.063
2020-02-13 | 14:49 | 50.063
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.058
2020-02-13 | 14:49 | 50.059
2020-02-13 | 14:49 | 50.059
2020-02-13 | 14:49 | 50.058
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.061
2020-02-13 | 14:49 | 50.062
2020-02-13 | 14:49 | 50.062
2020-02-13 | 14:49 | 50.061
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.059
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.062
2020-02-13 | 14:49 | 50.063
2020-02-13 | 14:49 | 50.062
2020-02-13 | 14:49 | 50.064
2020-02-13 | 14:49 | 50.064
2020-02-13 | 14:49 | 50.065
2020-02-13 | 14:49 | 50.064
2020-02-13 | 14:49 | 50.061
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.06
2020-02-13 | 14:49 | 50.059
2020-02-13 | 14:49 | 50.057
2020-02-13 | 14:49 | 50.056
2020-02-13 | 14:49 | 50.054
2020-02-13 | 14:49 | 50.053
2020-02-13 | 14:49 | 50.051
2020-02-13 | 14:49 | 50.05
2020-02-13 | 14:50 | 50.049
2020-02-13 | 14:50 | 50.047
2020-02-13 | 14:50 | 50.047
2020-02-13 | 14:50 | 50.046
2020-02-13 | 14:50 | 50.047
2020-02-13 | 14:50 | 50.047
2020-02-13 | 14:50 | 50.049
2020-02-13 | 14:50 | 50.052
2020-02-13 | 14:50 | 50.056
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.057
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.06
2020-02-13 | 14:50 | 50.06
2020-02-13 | 14:50 | 50.063
2020-02-13 | 14:50 | 50.064
2020-02-13 | 14:50 | 50.062
2020-02-13 | 14:50 | 50.064
2020-02-13 | 14:50 | 50.063
2020-02-13 | 14:50 | 50.063
2020-02-13 | 14:50 | 50.062
2020-02-13 | 14:50 | 50.06
2020-02-13 | 14:50 | 50.057
2020-02-13 | 14:50 | 50.054
2020-02-13 | 14:50 | 50.052
2020-02-13 | 14:50 | 50.051
2020-02-13 | 14:50 | 50.05
2020-02-13 | 14:50 | 50.049
2020-02-13 | 14:50 | 50.05
2020-02-13 | 14:50 | 50.048
2020-02-13 | 14:50 | 50.048
2020-02-13 | 14:50 | 50.048
2020-02-13 | 14:50 | 50.051
2020-02-13 | 14:50 | 50.053
2020-02-13 | 14:50 | 50.054
2020-02-13 | 14:50 | 50.055
2020-02-13 | 14:50 | 50.057
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.06
2020-02-13 | 14:50 | 50.06
2020-02-13 | 14:50 | 50.061
2020-02-13 | 14:50 | 50.06
2020-02-13 | 14:50 | 50.061
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.057
2020-02-13 | 14:50 | 50.058
2020-02-13 | 14:50 | 50.059
2020-02-13 | 14:50 | 50.061
2020-02-13 | 14:50 | 50.063
2020-02-13 | 14:51 | 50.065
2020-02-13 | 14:51 | 50.067
2020-02-13 | 14:51 | 50.069
2020-02-13 | 14:51 | 50.071
2020-02-13 | 14:51 | 50.071
2020-02-13 | 14:51 | 50.07
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.071
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.073
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.071
2020-02-13 | 14:51 | 50.072
2020-02-13 | 14:51 | 50.073
2020-02-13 | 14:51 | 50.074
2020-02-13 | 14:51 | 50.076
2020-02-13 | 14:51 | 50.076
2020-02-13 | 14:51 | 50.075
2020-02-13 | 14:51 | 50.074
2020-02-13 | 14:51 | 50.074
2020-02-13 | 14:51 | 50.074
2020-02-13 | 14:51 | 50.076
2020-02-13 | 14:51 | 50.077
2020-02-13 | 14:51 | 50.077
2020-02-13 | 14:51 | 50.079
2020-02-13 | 14:51 | 50.079
2020-02-13 | 14:51 | 50.08
2020-02-13 | 14:51 | 50.078
2020-02-13 | 14:51 | 50.08
2020-02-13 | 14:51 | 50.08
2020-02-13 | 14:51 | 50.079
2020-02-13 | 14:51 | 50.081
2020-02-13 | 14:51 | 50.081
2020-02-13 | 14:51 | 50.082
2020-02-13 | 14:51 | 50.088
2020-02-13 | 14:51 | 50.092
2020-02-13 | 14:51 | 50.094
2020-02-13 | 14:51 | 50.096
2020-02-13 | 14:51 | 50.096
2020-02-13 | 14:51 | 50.097
2020-02-13 | 14:51 | 50.098
2020-02-13 | 14:51 | 50.098
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.098
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.098
2020-02-13 | 14:51 | 50.1
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.099
2020-02-13 | 14:51 | 50.098
2020-02-13 | 14:51 | 50.097
2020-02-13 | 14:51 | 50.096
2020-02-13 | 14:51 | 50.095
2020-02-13 | 14:52 | 50.094
2020-02-13 | 14:52 | 50.095
2020-02-13 | 14:52 | 50.095
2020-02-13 | 14:52 | 50.094
2020-02-13 | 14:52 | 50.094
2020-02-13 | 14:52 | 50.094
2020-02-13 | 14:52 | 50.095
2020-02-13 | 14:52 | 50.095
2020-02-13 | 14:52 | 50.096
2020-02-13 | 14:52 | 50.098
2020-02-13 | 14:52 | 50.098
2020-02-13 | 14:52 | 50.1
2020-02-13 | 14:52 | 50.104
2020-02-13 | 14:52 | 50.108
2020-02-13 | 14:52 | 50.11
2020-02-13 | 14:52 | 50.114
2020-02-13 | 14:52 | 50.117
2020-02-13 | 14:52 | 50.12
2020-02-13 | 14:52 | 50.122
2020-02-13 | 14:52 | 50.121
2020-02-13 | 14:52 | 50.123
2020-02-13 | 14:52 | 50.121
2020-02-13 | 14:52 | 50.121
2020-02-13 | 14:52 | 50.118
2020-02-13 | 14:52 | 50.116
2020-02-13 | 14:52 | 50.115
2020-02-13 | 14:52 | 50.114
2020-02-13 | 14:52 | 50.114
2020-02-13 | 14:52 | 50.113
2020-02-13 | 14:52 | 50.113
2020-02-13 | 14:52 | 50.112
2020-02-13 | 14:52 | 50.114
2020-02-13 | 14:52 | 50.113
2020-02-13 | 14:52 | 50.114
2020-02-13 | 14:52 | 50.115
2020-02-13 | 14:52 | 50.117
2020-02-13 | 14:52 | 50.117
2020-02-13 | 14:52 | 50.119
2020-02-13 | 14:52 | 50.12
2020-02-13 | 14:52 | 50.122
2020-02-13 | 14:52 | 50.123
2020-02-13 | 14:52 | 50.125
2020-02-13 | 14:52 | 50.124
2020-02-13 | 14:52 | 50.123
2020-02-13 | 14:52 | 50.123
2020-02-13 | 14:52 | 50.123
2020-02-13 | 14:52 | 50.122
2020-02-13 | 14:52 | 50.119
2020-02-13 | 14:52 | 50.117
2020-02-13 | 14:52 | 50.119
2020-02-13 | 14:52 | 50.119
2020-02-13 | 14:52 | 50.119
2020-02-13 | 14:52 | 50.118
2020-02-13 | 14:52 | 50.121
2020-02-13 | 14:52 | 50.123
2020-02-13 | 14:52 | 50.125
2020-02-13 | 14:52 | 50.126
2020-02-13 | 14:52 | 50.127
2020-02-13 | 14:52 | 50.127
2020-02-13 | 14:52 | 50.128
2020-02-13 | 14:52 | 50.125
2020-02-13 | 14:53 | 50.124
2020-02-13 | 14:53 | 50.125
2020-02-13 | 14:53 | 50.124
2020-02-13 | 14:53 | 50.125
2020-02-13 | 14:53 | 50.125
2020-02-13 | 14:53 | 50.126
2020-02-13 | 14:53 | 50.128
2020-02-13 | 14:53 | 50.129
2020-02-13 | 14:53 | 50.13
2020-02-13 | 14:53 | 50.13
2020-02-13 | 14:53 | 50.13
2020-02-13 | 14:53 | 50.131
2020-02-13 | 14:53 | 50.13
2020-02-13 | 14:53 | 50.132
2020-02-13 | 14:53 | 50.133
2020-02-13 | 14:53 | 50.133
2020-02-13 | 14:53 | 50.135
2020-02-13 | 14:53 | 50.133
2020-02-13 | 14:53 | 50.131
2020-02-13 | 14:53 | 50.129
2020-02-13 | 14:53 | 50.126
2020-02-13 | 14:53 | 50.124
2020-02-13 | 14:53 | 50.122
2020-02-13 | 14:53 | 50.123
2020-02-13 | 14:53 | 50.12
2020-02-13 | 14:53 | 50.118
2020-02-13 | 14:53 | 50.116
2020-02-13 | 14:53 | 50.115
2020-02-13 | 14:53 | 50.113
2020-02-13 | 14:53 | 50.111
2020-02-13 | 14:53 | 50.11
2020-02-13 | 14:53 | 50.108
2020-02-13 | 14:53 | 50.108
2020-02-13 | 14:53 | 50.108
2020-02-13 | 14:53 | 50.105
2020-02-13 | 14:53 | 50.103
2020-02-13 | 14:53 | 50.1
2020-02-13 | 14:53 | 50.098
2020-02-13 | 14:53 | 50.096
2020-02-13 | 14:53 | 50.096
2020-02-13 | 14:53 | 50.094
2020-02-13 | 14:53 | 50.094
2020-02-13 | 14:53 | 50.092
2020-02-13 | 14:53 | 50.089
2020-02-13 | 14:53 | 50.087
2020-02-13 | 14:53 | 50.086
2020-02-13 | 14:53 | 50.088
2020-02-13 | 14:53 | 50.088
2020-02-13 | 14:53 | 50.091
2020-02-13 | 14:53 | 50.093
2020-02-13 | 14:53 | 50.098
2020-02-13 | 14:53 | 50.099
2020-02-13 | 14:53 | 50.102
2020-02-13 | 14:53 | 50.105
2020-02-13 | 14:53 | 50.106
2020-02-13 | 14:53 | 50.105
2020-02-13 | 14:53 | 50.106
2020-02-13 | 14:53 | 50.105
2020-02-13 | 14:53 | 50.103
2020-02-13 | 14:54 | 50.101
2020-02-13 | 14:54 | 50.099
2020-02-13 | 14:54 | 50.097
2020-02-13 | 14:54 | 50.095
2020-02-13 | 14:54 | 50.093
2020-02-13 | 14:54 | 50.089
2020-02-13 | 14:54 | 50.089
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.082
2020-02-13 | 14:54 | 50.084
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.085
2020-02-13 | 14:54 | 50.084
2020-02-13 | 14:54 | 50.083
2020-02-13 | 14:54 | 50.082
2020-02-13 | 14:54 | 50.084
2020-02-13 | 14:54 | 50.084
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.087
2020-02-13 | 14:54 | 50.087
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.087
2020-02-13 | 14:54 | 50.083
2020-02-13 | 14:54 | 50.081
2020-02-13 | 14:54 | 50.08
2020-02-13 | 14:54 | 50.078
2020-02-13 | 14:54 | 50.076
2020-02-13 | 14:54 | 50.076
2020-02-13 | 14:54 | 50.077
2020-02-13 | 14:54 | 50.078
2020-02-13 | 14:54 | 50.079
2020-02-13 | 14:54 | 50.079
2020-02-13 | 14:54 | 50.081
2020-02-13 | 14:54 | 50.082
2020-02-13 | 14:54 | 50.082
2020-02-13 | 14:54 | 50.084
2020-02-13 | 14:54 | 50.088
2020-02-13 | 14:54 | 50.089
2020-02-13 | 14:54 | 50.091
2020-02-13 | 14:54 | 50.092
2020-02-13 | 14:54 | 50.091
2020-02-13 | 14:54 | 50.09
2020-02-13 | 14:54 | 50.087
2020-02-13 | 14:54 | 50.087
2020-02-13 | 14:54 | 50.088
2020-02-13 | 14:54 | 50.089
2020-02-13 | 14:54 | 50.09
2020-02-13 | 14:54 | 50.087
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.085
2020-02-13 | 14:54 | 50.083
2020-02-13 | 14:54 | 50.084
2020-02-13 | 14:54 | 50.086
2020-02-13 | 14:54 | 50.088
2020-02-13 | 14:54 | 50.088
2020-02-13 | 14:54 | 50.09
2020-02-13 | 14:54 | 50.092
2020-02-13 | 14:54 | 50.094
2020-02-13 | 14:54 | 50.098
2020-02-13 | 14:54 | 50.099
2020-02-13 | 14:55 | 50.1
2020-02-13 | 14:55 | 50.101
2020-02-13 | 14:55 | 50.101
2020-02-13 | 14:55 | 50.103
2020-02-13 | 14:55 | 50.101
2020-02-13 | 14:55 | 50.1
2020-02-13 | 14:55 | 50.099
2020-02-13 | 14:55 | 50.097
2020-02-13 | 14:55 | 50.097
2020-02-13 | 14:55 | 50.096
2020-02-13 | 14:55 | 50.096
2020-02-13 | 14:55 | 50.093
2020-02-13 | 14:55 | 50.091
2020-02-13 | 14:55 | 50.089
2020-02-13 | 14:55 | 50.086
2020-02-13 | 14:55 | 50.084
2020-02-13 | 14:55 | 50.083
2020-02-13 | 14:55 | 50.082
2020-02-13 | 14:55 | 50.081
2020-02-13 | 14:55 | 50.08
2020-02-13 | 14:55 | 50.079
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.076
2020-02-13 | 14:55 | 50.075
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.077
2020-02-13 | 14:55 | 50.076
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.08
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.076
2020-02-13 | 14:55 | 50.074
2020-02-13 | 14:55 | 50.072
2020-02-13 | 14:55 | 50.071
2020-02-13 | 14:55 | 50.07
2020-02-13 | 14:55 | 50.07
2020-02-13 | 14:55 | 50.069
2020-02-13 | 14:55 | 50.07
2020-02-13 | 14:55 | 50.07
2020-02-13 | 14:55 | 50.072
2020-02-13 | 14:55 | 50.073
2020-02-13 | 14:55 | 50.077
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.076
2020-02-13 | 14:55 | 50.076
2020-02-13 | 14:55 | 50.074
2020-02-13 | 14:55 | 50.075
2020-02-13 | 14:55 | 50.076
2020-02-13 | 14:55 | 50.077
2020-02-13 | 14:55 | 50.078
2020-02-13 | 14:55 | 50.08
2020-02-13 | 14:55 | 50.079
2020-02-13 | 14:56 | 50.079
2020-02-13 | 14:56 | 50.08
2020-02-13 | 14:56 | 50.079
2020-02-13 | 14:56 | 50.078
2020-02-13 | 14:56 | 50.077
2020-02-13 | 14:56 | 50.074
2020-02-13 | 14:56 | 50.073
2020-02-13 | 14:56 | 50.071
2020-02-13 | 14:56 | 50.07
2020-02-13 | 14:56 | 50.07
2020-02-13 | 14:56 | 50.069
2020-02-13 | 14:56 | 50.07
2020-02-13 | 14:56 | 50.07
2020-02-13 | 14:56 | 50.067
2020-02-13 | 14:56 | 50.07
2020-02-13 | 14:56 | 50.071
2020-02-13 | 14:56 | 50.072
2020-02-13 | 14:56 | 50.072
2020-02-13 | 14:56 | 50.074
2020-02-13 | 14:56 | 50.077
2020-02-13 | 14:56 | 50.079
2020-02-13 | 14:56 | 50.077
2020-02-13 | 14:56 | 50.078
2020-02-13 | 14:56 | 50.077
2020-02-13 | 14:56 | 50.077
2020-02-13 | 14:56 | 50.075
2020-02-13 | 14:56 | 50.076
2020-02-13 | 14:56 | 50.076
2020-02-13 | 14:56 | 50.076
2020-02-13 | 14:56 | 50.075
2020-02-13 | 14:56 | 50.075
2020-02-13 | 14:56 | 50.076
2020-02-13 | 14:56 | 50.075
2020-02-13 | 14:56 | 50.074
2020-02-13 | 14:56 | 50.072
2020-02-13 | 14:56 | 50.07
2020-02-13 | 14:56 | 50.068
2020-02-13 | 14:56 | 50.066
2020-02-13 | 14:56 | 50.063
2020-02-13 | 14:56 | 50.061
2020-02-13 | 14:56 | 50.06
2020-02-13 | 14:56 | 50.058
2020-02-13 | 14:56 | 50.055
2020-02-13 | 14:56 | 50.055
2020-02-13 | 14:56 | 50.054
2020-02-13 | 14:56 | 50.053
2020-02-13 | 14:56 | 50.053
2020-02-13 | 14:56 | 50.053
2020-02-13 | 14:56 | 50.055
2020-02-13 | 14:56 | 50.056
2020-02-13 | 14:56 | 50.057
2020-02-13 | 14:56 | 50.058
2020-02-13 | 14:56 | 50.06
2020-02-13 | 14:56 | 50.059
2020-02-13 | 14:56 | 50.058
2020-02-13 | 14:56 | 50.058
2020-02-13 | 14:56 | 50.055
2020-02-13 | 14:56 | 50.052
2020-02-13 | 14:56 | 50.049
2020-02-13 | 14:56 | 50.045
2020-02-13 | 14:56 | 50.043
2020-02-13 | 14:57 | 50.041
2020-02-13 | 14:57 | 50.041
2020-02-13 | 14:57 | 50.042
2020-02-13 | 14:57 | 50.041
2020-02-13 | 14:57 | 50.041
2020-02-13 | 14:57 | 50.042
2020-02-13 | 14:57 | 50.042
2020-02-13 | 14:57 | 50.042
2020-02-13 | 14:57 | 50.041
2020-02-13 | 14:57 | 50.043
2020-02-13 | 14:57 | 50.044
2020-02-13 | 14:57 | 50.044
2020-02-13 | 14:57 | 50.046
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.051
2020-02-13 | 14:57 | 50.053
2020-02-13 | 14:57 | 50.056
2020-02-13 | 14:57 | 50.057
2020-02-13 | 14:57 | 50.058
2020-02-13 | 14:57 | 50.056
2020-02-13 | 14:57 | 50.055
2020-02-13 | 14:57 | 50.055
2020-02-13 | 14:57 | 50.053
2020-02-13 | 14:57 | 50.051
2020-02-13 | 14:57 | 50.05
2020-02-13 | 14:57 | 50.05
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.047
2020-02-13 | 14:57 | 50.047
2020-02-13 | 14:57 | 50.046
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.049
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.049
2020-02-13 | 14:57 | 50.051
2020-02-13 | 14:57 | 50.052
2020-02-13 | 14:57 | 50.054
2020-02-13 | 14:57 | 50.058
2020-02-13 | 14:57 | 50.061
2020-02-13 | 14:57 | 50.062
2020-02-13 | 14:57 | 50.061
2020-02-13 | 14:57 | 50.061
2020-02-13 | 14:57 | 50.061
2020-02-13 | 14:57 | 50.058
2020-02-13 | 14:57 | 50.054
2020-02-13 | 14:57 | 50.053
2020-02-13 | 14:57 | 50.051
2020-02-13 | 14:57 | 50.05
2020-02-13 | 14:57 | 50.049
2020-02-13 | 14:57 | 50.048
2020-02-13 | 14:57 | 50.046
2020-02-13 | 14:57 | 50.041
2020-02-13 | 14:57 | 50.035
2020-02-13 | 14:57 | 50.028
2020-02-13 | 14:57 | 50.021
2020-02-13 | 14:57 | 50.012
2020-02-13 | 14:58 | 50.006
2020-02-13 | 14:58 | 49.999
2020-02-13 | 14:58 | 49.996
2020-02-13 | 14:58 | 49.992
2020-02-13 | 14:58 | 49.987
2020-02-13 | 14:58 | 49.981
2020-02-13 | 14:58 | 49.977
2020-02-13 | 14:58 | 49.975
2020-02-13 | 14:58 | 49.975
2020-02-13 | 14:58 | 49.974
2020-02-13 | 14:58 | 49.972
2020-02-13 | 14:58 | 49.971
2020-02-13 | 14:58 | 49.97
2020-02-13 | 14:58 | 49.97
2020-02-13 | 14:58 | 49.97
2020-02-13 | 14:58 | 49.968
2020-02-13 | 14:58 | 49.966
2020-02-13 | 14:58 | 49.97
2020-02-13 | 14:58 | 49.973
2020-02-13 | 14:58 | 49.98
2020-02-13 | 14:58 | 49.992
2020-02-13 | 14:58 | 50.002
2020-02-13 | 14:58 | 50.011
2020-02-13 | 14:58 | 50.018
2020-02-13 | 14:58 | 50.025
2020-02-13 | 14:58 | 50.031
2020-02-13 | 14:58 | 50.038
2020-02-13 | 14:58 | 50.044
2020-02-13 | 14:58 | 50.05
2020-02-13 | 14:58 | 50.054
2020-02-13 | 14:58 | 50.058
2020-02-13 | 14:58 | 50.06
2020-02-13 | 14:58 | 50.06
2020-02-13 | 14:58 | 50.059
2020-02-13 | 14:58 | 50.058
2020-02-13 | 14:58 | 50.055
2020-02-13 | 14:58 | 50.051
2020-02-13 | 14:58 | 50.046
2020-02-13 | 14:58 | 50.041
2020-02-13 | 14:58 | 50.035
2020-02-13 | 14:58 | 50.029
2020-02-13 | 14:58 | 50.02
2020-02-13 | 14:58 | 50.014
2020-02-13 | 14:58 | 50.007
2020-02-13 | 14:58 | 50.002
2020-02-13 | 14:58 | 49.996
2020-02-13 | 14:58 | 49.993
2020-02-13 | 14:58 | 49.989
2020-02-13 | 14:58 | 49.985
2020-02-13 | 14:58 | 49.981
2020-02-13 | 14:58 | 49.978
2020-02-13 | 14:58 | 49.977
2020-02-13 | 14:58 | 49.977
2020-02-13 | 14:58 | 49.976
2020-02-13 | 14:58 | 49.976
2020-02-13 | 14:58 | 49.977
2020-02-13 | 14:58 | 49.977
2020-02-13 | 14:58 | 49.977
2020-02-13 | 14:58 | 49.98
2020-02-13 | 14:58 | 49.98
2020-02-13 | 14:58 | 49.984
2020-02-13 | 14:59 | 49.984
2020-02-13 | 14:59 | 49.987
2020-02-13 | 14:59 | 49.988
2020-02-13 | 14:59 | 49.99
2020-02-13 | 14:59 | 49.992
2020-02-13 | 14:59 | 49.992
2020-02-13 | 14:59 | 49.992
2020-02-13 | 14:59 | 49.99
2020-02-13 | 14:59 | 49.992
2020-02-13 | 14:59 | 49.992
2020-02-13 | 14:59 | 49.99
2020-02-13 | 14:59 | 49.987
2020-02-13 | 14:59 | 49.987
2020-02-13 | 14:59 | 49.982
2020-02-13 | 14:59 | 49.98
2020-02-13 | 14:59 | 49.977
2020-02-13 | 14:59 | 49.974
2020-02-13 | 14:59 | 49.97
2020-02-13 | 14:59 | 49.966
2020-02-13 | 14:59 | 49.965
2020-02-13 | 14:59 | 49.96
2020-02-13 | 14:59 | 49.957
2020-02-13 | 14:59 | 49.955
2020-02-13 | 14:59 | 49.952
2020-02-13 | 14:59 | 49.949
2020-02-13 | 14:59 | 49.948
2020-02-13 | 14:59 | 49.946
2020-02-13 | 14:59 | 49.945
2020-02-13 | 14:59 | 49.942
2020-02-13 | 14:59 | 49.94
2020-02-13 | 14:59 | 49.938
2020-02-13 | 14:59 | 49.937
2020-02-13 | 14:59 | 49.937
2020-02-13 | 14:59 | 49.939
2020-02-13 | 14:59 | 49.938
2020-02-13 | 14:59 | 49.937
2020-02-13 | 14:59 | 49.936
2020-02-13 | 14:59 | 49.937
2020-02-13 | 14:59 | 49.934
2020-02-13 | 14:59 | 49.933
2020-02-13 | 14:59 | 49.929
2020-02-13 | 14:59 | 49.935
2020-02-13 | 14:59 | 49.937
2020-02-13 | 14:59 | 49.938
2020-02-13 | 14:59 | 49.939
2020-02-13 | 14:59 | 49.942
2020-02-13 | 14:59 | 49.945
2020-02-13 | 14:59 | 49.949
2020-02-13 | 14:59 | 49.954
2020-02-13 | 14:59 | 49.957
2020-02-13 | 14:59 | 49.961
2020-02-13 | 14:59 | 49.966
2020-02-13 | 14:59 | 49.972
2020-02-13 | 14:59 | 49.979
2020-02-13 | 14:59 | 49.984
2020-02-13 | 14:59 | 49.988
2020-02-13 | 14:59 | 49.989
2020-02-13 | 14:59 | 49.991
2020-02-13 | 14:59 | 49.992
2020-02-13 | 15:00 | 49.993
2020-02-13 | 15:00 | 49.994
2020-02-13 | 15:00 | 49.994
2020-02-13 | 15:00 | 49.996
2020-02-13 | 15:00 | 49.996
2020-02-13 | 15:00 | 49.997
2020-02-13 | 15:00 | 49.997
2020-02-13 | 15:00 | 49.996
2020-02-13 | 15:00 | 49.996
2020-02-13 | 15:00 | 49.996
2020-02-13 | 15:00 | 49.994
2020-02-13 | 15:00 | 49.993
2020-02-13 | 15:00 | 49.991
2020-02-13 | 15:00 | 49.989
2020-02-13 | 15:00 | 49.987
2020-02-13 | 15:00 | 49.984
2020-02-13 | 15:00 | 49.983
2020-02-13 | 15:00 | 49.983
2020-02-13 | 15:00 | 49.985
2020-02-13 | 15:00 | 49.987
2020-02-13 | 15:00 | 49.988
2020-02-13 | 15:00 | 49.99
2020-02-13 | 15:00 | 49.992
2020-02-13 | 15:00 | 49.993
2020-02-13 | 15:00 | 49.994
2020-02-13 | 15:00 | 49.995
2020-02-13 | 15:00 | 49.993
2020-02-13 | 15:00 | 49.992
2020-02-13 | 15:00 | 49.991
2020-02-13 | 15:00 | 49.989
2020-02-13 | 15:00 | 49.989
2020-02-13 | 15:00 | 49.987
2020-02-13 | 15:00 | 49.983
2020-02-13 | 15:00 | 49.979
2020-02-13 | 15:00 | 49.976
2020-02-13 | 15:00 | 49.973
2020-02-13 | 15:00 | 49.968
2020-02-13 | 15:00 | 49.963
2020-02-13 | 15:00 | 49.959
2020-02-13 | 15:00 | 49.955
2020-02-13 | 15:00 | 49.951
2020-02-13 | 15:00 | 49.948
2020-02-13 | 15:00 | 49.946
2020-02-13 | 15:00 | 49.945
2020-02-13 | 15:00 | 49.943
2020-02-13 | 15:00 | 49.941
2020-02-13 | 15:00 | 49.938
2020-02-13 | 15:00 | 49.935
2020-02-13 | 15:00 | 49.933
2020-02-13 | 15:00 | 49.929
2020-02-13 | 15:00 | 49.925
2020-02-13 | 15:00 | 49.919
2020-02-13 | 15:00 | 49.914
2020-02-13 | 15:00 | 49.908
2020-02-13 | 15:00 | 49.903
2020-02-13 | 15:00 | 49.897
2020-02-13 | 15:00 | 49.891
2020-02-13 | 15:00 | 49.887
2020-02-13 | 15:00 | 49.882
2020-02-13 | 15:00 | 49.878
2020-02-13 | 15:00 | 49.874
2020-02-13 | 15:01 | 49.868
2020-02-13 | 15:01 | 49.867
2020-02-13 | 15:01 | 49.864
2020-02-13 | 15:01 | 49.863
2020-02-13 | 15:01 | 49.864
2020-02-13 | 15:01 | 49.864
2020-02-13 | 15:01 | 49.864
2020-02-13 | 15:01 | 49.865
2020-02-13 | 15:01 | 49.867
2020-02-13 | 15:01 | 49.87
2020-02-13 | 15:01 | 49.87
2020-02-13 | 15:01 | 49.871
2020-02-13 | 15:01 | 49.871
2020-02-13 | 15:01 | 49.869
2020-02-13 | 15:01 | 49.869
2020-02-13 | 15:01 | 49.868
2020-02-13 | 15:01 | 49.867
2020-02-13 | 15:01 | 49.867
2020-02-13 | 15:01 | 49.867
2020-02-13 | 15:01 | 49.868
2020-02-13 | 15:01 | 49.866
2020-02-13 | 15:01 | 49.865
2020-02-13 | 15:01 | 49.865
2020-02-13 | 15:01 | 49.865
2020-02-13 | 15:01 | 49.863
2020-02-13 | 15:01 | 49.862
2020-02-13 | 15:01 | 49.861
2020-02-13 | 15:01 | 49.862
2020-02-13 | 15:01 | 49.861
2020-02-13 | 15:01 | 49.857
2020-02-13 | 15:01 | 49.853
2020-02-13 | 15:01 | 49.846
2020-02-13 | 15:01 | 49.842
2020-02-13 | 15:01 | 49.837
2020-02-13 | 15:01 | 49.833
2020-02-13 | 15:01 | 49.831
2020-02-13 | 15:01 | 49.826
2020-02-13 | 15:01 | 49.823
2020-02-13 | 15:01 | 49.821
2020-02-13 | 15:01 | 49.82
2020-02-13 | 15:01 | 49.818
2020-02-13 | 15:01 | 49.816
2020-02-13 | 15:01 | 49.813
2020-02-13 | 15:01 | 49.814
2020-02-13 | 15:01 | 49.812
2020-02-13 | 15:01 | 49.81
2020-02-13 | 15:01 | 49.809
2020-02-13 | 15:01 | 49.808
2020-02-13 | 15:01 | 49.808
2020-02-13 | 15:01 | 49.807
2020-02-13 | 15:01 | 49.805
2020-02-13 | 15:01 | 49.803
2020-02-13 | 15:01 | 49.801
2020-02-13 | 15:01 | 49.803
2020-02-13 | 15:01 | 49.802
2020-02-13 | 15:01 | 49.8
2020-02-13 | 15:01 | 49.799
2020-02-13 | 15:01 | 49.796
2020-02-13 | 15:01 | 49.798
2020-02-13 | 15:02 | 49.796
2020-02-13 | 15:02 | 49.797
2020-02-13 | 15:02 | 49.795
2020-02-13 | 15:02 | 49.798
2020-02-13 | 15:02 | 49.799
2020-02-13 | 15:02 | 49.798
2020-02-13 | 15:02 | 49.796
2020-02-13 | 15:02 | 49.794
2020-02-13 | 15:02 | 49.792
2020-02-13 | 15:02 | 49.79
2020-02-13 | 15:02 | 49.787
2020-02-13 | 15:02 | 49.787
2020-02-13 | 15:02 | 49.787
2020-02-13 | 15:02 | 49.788
2020-02-13 | 15:02 | 49.788
2020-02-13 | 15:02 | 49.79
2020-02-13 | 15:02 | 49.788
2020-02-13 | 15:02 | 49.787
2020-02-13 | 15:02 | 49.79
2020-02-13 | 15:02 | 49.791
2020-02-13 | 15:02 | 49.792
2020-02-13 | 15:02 | 49.792
2020-02-13 | 15:02 | 49.793
2020-02-13 | 15:02 | 49.79
2020-02-13 | 15:02 | 49.788
2020-02-13 | 15:02 | 49.783
2020-02-13 | 15:02 | 49.781
2020-02-13 | 15:02 | 49.779
2020-02-13 | 15:02 | 49.777
2020-02-13 | 15:02 | 49.775
2020-02-13 | 15:02 | 49.773
2020-02-13 | 15:02 | 49.769
2020-02-13 | 15:02 | 49.766
2020-02-13 | 15:02 | 49.763
2020-02-13 | 15:02 | 49.761
2020-02-13 | 15:02 | 49.76
2020-02-13 | 15:02 | 49.76
2020-02-13 | 15:02 | 49.761
2020-02-13 | 15:02 | 49.763
2020-02-13 | 15:02 | 49.768
2020-02-13 | 15:02 | 49.772
2020-02-13 | 15:02 | 49.782
2020-02-13 | 15:02 | 49.793
2020-02-13 | 15:02 | 49.807
2020-02-13 | 15:02 | 49.824
2020-02-13 | 15:02 | 49.843
2020-02-13 | 15:02 | 49.861
2020-02-13 | 15:02 | 49.878
2020-02-13 | 15:02 | 49.893
2020-02-13 | 15:02 | 49.907
2020-02-13 | 15:02 | 49.918
2020-02-13 | 15:02 | 49.928
2020-02-13 | 15:02 | 49.935
2020-02-13 | 15:02 | 49.94
2020-02-13 | 15:02 | 49.944
2020-02-13 | 15:02 | 49.948
2020-02-13 | 15:02 | 49.95
2020-02-13 | 15:02 | 49.95
2020-02-13 | 15:02 | 49.949
2020-02-13 | 15:02 | 49.95
2020-02-13 | 15:02 | 49.95
2020-02-13 | 15:03 | 49.949
2020-02-13 | 15:03 | 49.948
2020-02-13 | 15:03 | 49.948
2020-02-13 | 15:03 | 49.946
2020-02-13 | 15:03 | 49.944
2020-02-13 | 15:03 | 49.944
2020-02-13 | 15:03 | 49.945
2020-02-13 | 15:03 | 49.945
2020-02-13 | 15:03 | 49.944
2020-02-13 | 15:03 | 49.946
2020-02-13 | 15:03 | 49.948
2020-02-13 | 15:03 | 49.949
2020-02-13 | 15:03 | 49.951
2020-02-13 | 15:03 | 49.952
2020-02-13 | 15:03 | 49.955
2020-02-13 | 15:03 | 49.956
2020-02-13 | 15:03 | 49.955
2020-02-13 | 15:03 | 49.956
2020-02-13 | 15:03 | 49.958
2020-02-13 | 15:03 | 49.958
2020-02-13 | 15:03 | 49.958
2020-02-13 | 15:03 | 49.957
2020-02-13 | 15:03 | 49.958
2020-02-13 | 15:03 | 49.961
2020-02-13 | 15:03 | 49.96
2020-02-13 | 15:03 | 49.961
2020-02-13 | 15:03 | 49.962
2020-02-13 | 15:03 | 49.965
2020-02-13 | 15:03 | 49.97
2020-02-13 | 15:03 | 49.971
2020-02-13 | 15:03 | 49.974
2020-02-13 | 15:03 | 49.976
2020-02-13 | 15:03 | 49.975
2020-02-13 | 15:03 | 49.974
2020-02-13 | 15:03 | 49.972
2020-02-13 | 15:03 | 49.969
2020-02-13 | 15:03 | 49.966
2020-02-13 | 15:03 | 49.962
2020-02-13 | 15:03 | 49.96
2020-02-13 | 15:03 | 49.958
2020-02-13 | 15:03 | 49.956
2020-02-13 | 15:03 | 49.956
2020-02-13 | 15:03 | 49.955
2020-02-13 | 15:03 | 49.957
2020-02-13 | 15:03 | 49.957
2020-02-13 | 15:03 | 49.96
2020-02-13 | 15:03 | 49.96
2020-02-13 | 15:03 | 49.96
2020-02-13 | 15:03 | 49.96
2020-02-13 | 15:03 | 49.962
2020-02-13 | 15:03 | 49.965
2020-02-13 | 15:03 | 49.969
2020-02-13 | 15:03 | 49.972
2020-02-13 | 15:03 | 49.974
2020-02-13 | 15:03 | 49.98
2020-02-13 | 15:03 | 49.982
2020-02-13 | 15:03 | 49.985
2020-02-13 | 15:03 | 49.986
2020-02-13 | 15:03 | 49.988
2020-02-13 | 15:04 | 49.991
2020-02-13 | 15:04 | 49.992
2020-02-13 | 15:04 | 49.992
2020-02-13 | 15:04 | 49.992
2020-02-13 | 15:04 | 49.99
2020-02-13 | 15:04 | 49.992
2020-02-13 | 15:04 | 49.992
2020-02-13 | 15:04 | 49.993
2020-02-13 | 15:04 | 49.99
2020-02-13 | 15:04 | 49.988
2020-02-13 | 15:04 | 49.986
2020-02-13 | 15:04 | 49.982
2020-02-13 | 15:04 | 49.978
2020-02-13 | 15:04 | 49.974
2020-02-13 | 15:04 | 49.971
2020-02-13 | 15:04 | 49.968
2020-02-13 | 15:04 | 49.966
2020-02-13 | 15:04 | 49.966
2020-02-13 | 15:04 | 49.966
2020-02-13 | 15:04 | 49.967
2020-02-13 | 15:04 | 49.967
2020-02-13 | 15:04 | 49.969
2020-02-13 | 15:04 | 49.969
2020-02-13 | 15:04 | 49.969
2020-02-13 | 15:04 | 49.971
2020-02-13 | 15:04 | 49.971
2020-02-13 | 15:04 | 49.974
2020-02-13 | 15:04 | 49.975
2020-02-13 | 15:04 | 49.974
2020-02-13 | 15:04 | 49.976
2020-02-13 | 15:04 | 49.978
2020-02-13 | 15:04 | 49.98
2020-02-13 | 15:04 | 49.98
2020-02-13 | 15:04 | 49.98
2020-02-13 | 15:04 | 49.978
2020-02-13 | 15:04 | 49.978
2020-02-13 | 15:04 | 49.979
2020-02-13 | 15:04 | 49.979
2020-02-13 | 15:04 | 49.979
2020-02-13 | 15:04 | 49.976
2020-02-13 | 15:04 | 49.975
2020-02-13 | 15:04 | 49.975
2020-02-13 | 15:04 | 49.974
2020-02-13 | 15:04 | 49.973
2020-02-13 | 15:04 | 49.974
2020-02-13 | 15:04 | 49.977
2020-02-13 | 15:04 | 49.979
2020-02-13 | 15:04 | 49.981
2020-02-13 | 15:04 | 49.982
2020-02-13 | 15:04 | 49.985
2020-02-13 | 15:04 | 49.988
2020-02-13 | 15:04 | 49.991
2020-02-13 | 15:04 | 49.993
2020-02-13 | 15:04 | 49.996
2020-02-13 | 15:04 | 50.002
2020-02-13 | 15:04 | 50.006
2020-02-13 | 15:04 | 50.007
2020-02-13 | 15:04 | 50.009
2020-02-13 | 15:04 | 50.011
2020-02-13 | 15:04 | 50.012
2020-02-13 | 15:04 | 50.01
2020-02-13 | 15:05 | 50.01
2020-02-13 | 15:05 | 50.007
2020-02-13 | 15:05 | 50.002
2020-02-13 | 15:05 | 49.998
2020-02-13 | 15:05 | 49.995
2020-02-13 | 15:05 | 49.992
2020-02-13 | 15:05 | 49.987
2020-02-13 | 15:05 | 49.983
2020-02-13 | 15:05 | 49.982
2020-02-13 | 15:05 | 49.98
2020-02-13 | 15:05 | 49.979
2020-02-13 | 15:05 | 49.977
2020-02-13 | 15:05 | 49.977
2020-02-13 | 15:05 | 49.977
2020-02-13 | 15:05 | 49.978
2020-02-13 | 15:05 | 49.979
2020-02-13 | 15:05 | 49.979
2020-02-13 | 15:05 | 49.978
2020-02-13 | 15:05 | 49.981
2020-02-13 | 15:05 | 49.982
2020-02-13 | 15:05 | 49.983
2020-02-13 | 15:05 | 49.984
2020-02-13 | 15:05 | 49.985
2020-02-13 | 15:05 | 49.987
2020-02-13 | 15:05 | 49.986
2020-02-13 | 15:05 | 49.985
2020-02-13 | 15:05 | 49.986
2020-02-13 | 15:05 | 49.986
2020-02-13 | 15:05 | 49.985
2020-02-13 | 15:05 | 49.983
2020-02-13 | 15:05 | 49.982
2020-02-13 | 15:05 | 49.981
2020-02-13 | 15:05 | 49.981
2020-02-13 | 15:05 | 49.979
2020-02-13 | 15:05 | 49.975
2020-02-13 | 15:05 | 49.973
2020-02-13 | 15:05 | 49.969
2020-02-13 | 15:05 | 49.966
2020-02-13 | 15:05 | 49.961
2020-02-13 | 15:05 | 49.96
2020-02-13 | 15:05 | 49.959
2020-02-13 | 15:05 | 49.957
2020-02-13 | 15:05 | 49.957
2020-02-13 | 15:05 | 49.959
2020-02-13 | 15:05 | 49.962
2020-02-13 | 15:05 | 49.963
2020-02-13 | 15:05 | 49.964
2020-02-13 | 15:05 | 49.966
2020-02-13 | 15:05 | 49.968
2020-02-13 | 15:05 | 49.969
2020-02-13 | 15:05 | 49.969
2020-02-13 | 15:05 | 49.968
2020-02-13 | 15:05 | 49.969
2020-02-13 | 15:05 | 49.97
2020-02-13 | 15:05 | 49.971
2020-02-13 | 15:05 | 49.972
2020-02-13 | 15:05 | 49.974
2020-02-13 | 15:05 | 49.977
2020-02-13 | 15:05 | 49.982
2020-02-13 | 15:06 | 49.983
2020-02-13 | 15:06 | 49.983
2020-02-13 | 15:06 | 49.984
2020-02-13 | 15:06 | 49.985
2020-02-13 | 15:06 | 49.986
2020-02-13 | 15:06 | 49.986
2020-02-13 | 15:06 | 49.987
2020-02-13 | 15:06 | 49.989
2020-02-13 | 15:06 | 49.993
2020-02-13 | 15:06 | 49.995
2020-02-13 | 15:06 | 49.996
2020-02-13 | 15:06 | 49.999
2020-02-13 | 15:06 | 49.999
2020-02-13 | 15:06 | 49.998
2020-02-13 | 15:06 | 49.998
2020-02-13 | 15:06 | 49.998
2020-02-13 | 15:06 | 49.999
2020-02-13 | 15:06 | 49.998
2020-02-13 | 15:06 | 49.997
2020-02-13 | 15:06 | 49.995
2020-02-13 | 15:06 | 49.995
2020-02-13 | 15:06 | 49.995
2020-02-13 | 15:06 | 49.995
2020-02-13 | 15:06 | 49.996
2020-02-13 | 15:06 | 49.997
2020-02-13 | 15:06 | 49.997
2020-02-13 | 15:06 | 49.997
2020-02-13 | 15:06 | 49.997
2020-02-13 | 15:06 | 49.998
2020-02-13 | 15:06 | 49.999
2020-02-13 | 15:06 | 50
2020-02-13 | 15:06 | 49.999
2020-02-13 | 15:06 | 50.002
2020-02-13 | 15:06 | 50.003
2020-02-13 | 15:06 | 50.004
2020-02-13 | 15:06 | 50.004
2020-02-13 | 15:06 | 50.006
2020-02-13 | 15:06 | 50.006
2020-02-13 | 15:06 | 50.005
2020-02-13 | 15:06 | 50.006
2020-02-13 | 15:06 | 50.008
2020-02-13 | 15:06 | 50.01
2020-02-13 | 15:06 | 50.012
2020-02-13 | 15:06 | 50.014
2020-02-13 | 15:06 | 50.019
2020-02-13 | 15:06 | 50.023
2020-02-13 | 15:06 | 50.025
2020-02-13 | 15:06 | 50.03
2020-02-13 | 15:06 | 50.036
2020-02-13 | 15:06 | 50.039
2020-02-13 | 15:06 | 50.042
2020-02-13 | 15:06 | 50.046
2020-02-13 | 15:06 | 50.047
2020-02-13 | 15:06 | 50.046
2020-02-13 | 15:06 | 50.049
2020-02-13 | 15:06 | 50.05
2020-02-13 | 15:06 | 50.049
2020-02-13 | 15:06 | 50.05
2020-02-13 | 15:06 | 50.049
2020-02-13 | 15:06 | 50.049
2020-02-13 | 15:06 | 50.049
2020-02-13 | 15:07 | 50.047
2020-02-13 | 15:07 | 50.049
2020-02-13 | 15:07 | 50.052
2020-02-13 | 15:07 | 50.051
2020-02-13 | 15:07 | 50.052
2020-02-13 | 15:07 | 50.054
2020-02-13 | 15:07 | 50.055
2020-02-13 | 15:07 | 50.055
2020-02-13 | 15:07 | 50.055
2020-02-13 | 15:07 | 50.056
2020-02-13 | 15:07 | 50.056
2020-02-13 | 15:07 | 50.055
2020-02-13 | 15:07 | 50.055
2020-02-13 | 15:07 | 50.057
2020-02-13 | 15:07 | 50.054
2020-02-13 | 15:07 | 50.053
2020-02-13 | 15:07 | 50.053
2020-02-13 | 15:07 | 50.05
2020-02-13 | 15:07 | 50.05
2020-02-13 | 15:07 | 50.051
2020-02-13 | 15:07 | 50.054
2020-02-13 | 15:07 | 50.054
2020-02-13 | 15:07 | 50.054
2020-02-13 | 15:07 | 50.059
2020-02-13 | 15:07 | 50.061
2020-02-13 | 15:07 | 50.064
2020-02-13 | 15:07 | 50.064
2020-02-13 | 15:07 | 50.066
2020-02-13 | 15:07 | 50.069
2020-02-13 | 15:07 | 50.07
2020-02-13 | 15:07 | 50.072
2020-02-13 | 15:07 | 50.073
2020-02-13 | 15:07 | 50.076
2020-02-13 | 15:07 | 50.075
2020-02-13 | 15:07 | 50.075
2020-02-13 | 15:07 | 50.076
2020-02-13 | 15:07 | 50.076
2020-02-13 | 15:07 | 50.074
2020-02-13 | 15:07 | 50.073
2020-02-13 | 15:07 | 50.074
2020-02-13 | 15:07 | 50.074
2020-02-13 | 15:07 | 50.075
2020-02-13 | 15:07 | 50.075
2020-02-13 | 15:07 | 50.075
2020-02-13 | 15:07 | 50.074
2020-02-13 | 15:07 | 50.073
2020-02-13 | 15:07 | 50.068
2020-02-13 | 15:07 | 50.065
2020-02-13 | 15:07 | 50.059
2020-02-13 | 15:07 | 50.055
2020-02-13 | 15:07 | 50.046
2020-02-13 | 15:07 | 50.042
2020-02-13 | 15:07 | 50.04
2020-02-13 | 15:07 | 50.035
2020-02-13 | 15:07 | 50.034
2020-02-13 | 15:07 | 50.031
2020-02-13 | 15:07 | 50.029
2020-02-13 | 15:07 | 50.029
2020-02-13 | 15:07 | 50.029
2020-02-13 | 15:08 | 50.029
2020-02-13 | 15:08 | 50.033
2020-02-13 | 15:08 | 50.037
2020-02-13 | 15:08 | 50.04
2020-02-13 | 15:08 | 50.045
2020-02-13 | 15:08 | 50.049
2020-02-13 | 15:08 | 50.053
2020-02-13 | 15:08 | 50.058
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.065
2020-02-13 | 15:08 | 50.065
2020-02-13 | 15:08 | 50.064
2020-02-13 | 15:08 | 50.062
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.062
2020-02-13 | 15:08 | 50.059
2020-02-13 | 15:08 | 50.06
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.06
2020-02-13 | 15:08 | 50.06
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.062
2020-02-13 | 15:08 | 50.062
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.061
2020-02-13 | 15:08 | 50.059
2020-02-13 | 15:08 | 50.055
2020-02-13 | 15:08 | 50.052
2020-02-13 | 15:08 | 50.049
2020-02-13 | 15:08 | 50.047
2020-02-13 | 15:08 | 50.044
2020-02-13 | 15:08 | 50.041
2020-02-13 | 15:08 | 50.038
2020-02-13 | 15:08 | 50.034
2020-02-13 | 15:08 | 50.032
2020-02-13 | 15:08 | 50.03
2020-02-13 | 15:08 | 50.028
2020-02-13 | 15:08 | 50.027
2020-02-13 | 15:08 | 50.024
2020-02-13 | 15:08 | 50.023
2020-02-13 | 15:08 | 50.019
2020-02-13 | 15:08 | 50.016
2020-02-13 | 15:08 | 50.012
2020-02-13 | 15:08 | 50.005
2020-02-13 | 15:08 | 49.995
2020-02-13 | 15:08 | 49.987
2020-02-13 | 15:08 | 49.982
2020-02-13 | 15:08 | 49.978
2020-02-13 | 15:08 | 49.975
2020-02-13 | 15:08 | 49.972
2020-02-13 | 15:08 | 49.973
2020-02-13 | 15:08 | 49.974
2020-02-13 | 15:08 | 49.977
2020-02-13 | 15:08 | 49.979
2020-02-13 | 15:08 | 49.985
2020-02-13 | 15:08 | 49.989
2020-02-13 | 15:08 | 49.991
2020-02-13 | 15:08 | 49.993
2020-02-13 | 15:08 | 49.997
2020-02-13 | 15:08 | 49.999
2020-02-13 | 15:09 | 49.999
2020-02-13 | 15:09 | 50.001
2020-02-13 | 15:09 | 50.003
2020-02-13 | 15:09 | 50.004
2020-02-13 | 15:09 | 50.005
2020-02-13 | 15:09 | 50.004
2020-02-13 | 15:09 | 50.007
2020-02-13 | 15:09 | 50.009
2020-02-13 | 15:09 | 50.011
2020-02-13 | 15:09 | 50.012
2020-02-13 | 15:09 | 50.016
2020-02-13 | 15:09 | 50.019
2020-02-13 | 15:09 | 50.021
2020-02-13 | 15:09 | 50.02
2020-02-13 | 15:09 | 50.023
2020-02-13 | 15:09 | 50.022
2020-02-13 | 15:09 | 50.021
2020-02-13 | 15:09 | 50.019
2020-02-13 | 15:09 | 50.016
2020-02-13 | 15:09 | 50.012
2020-02-13 | 15:09 | 50.008
2020-02-13 | 15:09 | 50.005
2020-02-13 | 15:09 | 49.999
2020-02-13 | 15:09 | 49.993
2020-02-13 | 15:09 | 49.99
2020-02-13 | 15:09 | 49.986
2020-02-13 | 15:09 | 49.981
2020-02-13 | 15:09 | 49.979
2020-02-13 | 15:09 | 49.979
2020-02-13 | 15:09 | 49.979
2020-02-13 | 15:09 | 49.98
2020-02-13 | 15:09 | 49.98
2020-02-13 | 15:09 | 49.98
2020-02-13 | 15:09 | 49.981
2020-02-13 | 15:09 | 49.983
2020-02-13 | 15:09 | 49.985
2020-02-13 | 15:09 | 49.985
2020-02-13 | 15:09 | 49.985
2020-02-13 | 15:09 | 49.982
2020-02-13 | 15:09 | 49.98
2020-02-13 | 15:09 | 49.976
2020-02-13 | 15:09 | 49.972
2020-02-13 | 15:09 | 49.97
2020-02-13 | 15:09 | 49.966
2020-02-13 | 15:09 | 49.965
2020-02-13 | 15:09 | 49.96
2020-02-13 | 15:09 | 49.959
2020-02-13 | 15:09 | 49.958
2020-02-13 | 15:09 | 49.958
2020-02-13 | 15:09 | 49.958
2020-02-13 | 15:09 | 49.958
2020-02-13 | 15:09 | 49.961
2020-02-13 | 15:09 | 49.962
2020-02-13 | 15:09 | 49.963
2020-02-13 | 15:09 | 49.964
2020-02-13 | 15:09 | 49.966
2020-02-13 | 15:09 | 49.969
2020-02-13 | 15:09 | 49.972
2020-02-13 | 15:09 | 49.974
2020-02-13 | 15:10 | 49.975
2020-02-13 | 15:10 | 49.974
2020-02-13 | 15:10 | 49.976
2020-02-13 | 15:10 | 49.979
2020-02-13 | 15:10 | 49.98
2020-02-13 | 15:10 | 49.982
2020-02-13 | 15:10 | 49.981
2020-02-13 | 15:10 | 49.98
2020-02-13 | 15:10 | 49.976
2020-02-13 | 15:10 | 49.974
2020-02-13 | 15:10 | 49.972
2020-02-13 | 15:10 | 49.971
2020-02-13 | 15:10 | 49.97
2020-02-13 | 15:10 | 49.972
2020-02-13 | 15:10 | 49.974
2020-02-13 | 15:10 | 49.977
2020-02-13 | 15:10 | 49.979
2020-02-13 | 15:10 | 49.981
2020-02-13 | 15:10 | 49.982
2020-02-13 | 15:10 | 49.984
2020-02-13 | 15:10 | 49.986
2020-02-13 | 15:10 | 49.99
2020-02-13 | 15:10 | 49.993
2020-02-13 | 15:10 | 49.998
2020-02-13 | 15:10 | 50.002
2020-02-13 | 15:10 | 50.004
2020-02-13 | 15:10 | 50.005
2020-02-13 | 15:10 | 50.006
2020-02-13 | 15:10 | 50.004
2020-02-13 | 15:10 | 50.004
2020-02-13 | 15:10 | 50.003
2020-02-13 | 15:10 | 50.002
2020-02-13 | 15:10 | 50
2020-02-13 | 15:10 | 49.997
2020-02-13 | 15:10 | 49.995
2020-02-13 | 15:10 | 49.992
2020-02-13 | 15:10 | 49.99
2020-02-13 | 15:10 | 49.988
2020-02-13 | 15:10 | 49.984
2020-02-13 | 15:10 | 49.982
2020-02-13 | 15:10 | 49.979
2020-02-13 | 15:10 | 49.976
2020-02-13 | 15:10 | 49.975
2020-02-13 | 15:10 | 49.974
2020-02-13 | 15:10 | 49.974
2020-02-13 | 15:10 | 49.973
2020-02-13 | 15:10 | 49.975
2020-02-13 | 15:10 | 49.975
2020-02-13 | 15:10 | 49.977
2020-02-13 | 15:10 | 49.977
2020-02-13 | 15:10 | 49.979
2020-02-13 | 15:10 | 49.98
2020-02-13 | 15:10 | 49.982
2020-02-13 | 15:10 | 49.985
2020-02-13 | 15:10 | 49.988
2020-02-13 | 15:10 | 49.991
2020-02-13 | 15:10 | 49.992
2020-02-13 | 15:10 | 49.994
2020-02-13 | 15:10 | 49.994
2020-02-13 | 15:10 | 49.996
2020-02-13 | 15:10 | 49.996
2020-02-13 | 15:11 | 49.998
2020-02-13 | 15:11 | 49.998
2020-02-13 | 15:11 | 50.001
2020-02-13 | 15:11 | 50.003
2020-02-13 | 15:11 | 50.008
2020-02-13 | 15:11 | 50.012
2020-02-13 | 15:11 | 50.016
2020-02-13 | 15:11 | 50.018
2020-02-13 | 15:11 | 50.017
2020-02-13 | 15:11 | 50.018
2020-02-13 | 15:11 | 50.016
2020-02-13 | 15:11 | 50.016
2020-02-13 | 15:11 | 50.013
2020-02-13 | 15:11 | 50.011
2020-02-13 | 15:11 | 50.013
2020-02-13 | 15:11 | 50.013
2020-02-13 | 15:11 | 50.014
2020-02-13 | 15:11 | 50.012
2020-02-13 | 15:11 | 50.011
2020-02-13 | 15:11 | 50.01
2020-02-13 | 15:11 | 50.01
2020-02-13 | 15:11 | 50.012
2020-02-13 | 15:11 | 50.012
2020-02-13 | 15:11 | 50.012
2020-02-13 | 15:11 | 50.011
2020-02-13 | 15:11 | 50.007
2020-02-13 | 15:11 | 50.005
2020-02-13 | 15:11 | 50.001
2020-02-13 | 15:11 | 49.995
2020-02-13 | 15:11 | 49.99
2020-02-13 | 15:11 | 49.981
2020-02-13 | 15:11 | 49.973
2020-02-13 | 15:11 | 49.963
2020-02-13 | 15:11 | 49.954
2020-02-13 | 15:11 | 49.947
2020-02-13 | 15:11 | 49.943
2020-02-13 | 15:11 | 49.938
2020-02-13 | 15:11 | 49.936
2020-02-13 | 15:11 | 49.934
2020-02-13 | 15:11 | 49.935
2020-02-13 | 15:11 | 49.937
2020-02-13 | 15:11 | 49.94
2020-02-13 | 15:11 | 49.941
2020-02-13 | 15:11 | 49.944
2020-02-13 | 15:11 | 49.947
2020-02-13 | 15:11 | 49.945
2020-02-13 | 15:11 | 49.948
2020-02-13 | 15:11 | 49.949
2020-02-13 | 15:11 | 49.95
2020-02-13 | 15:11 | 49.951
2020-02-13 | 15:11 | 49.95
2020-02-13 | 15:11 | 49.949
2020-02-13 | 15:11 | 49.949
2020-02-13 | 15:11 | 49.949
2020-02-13 | 15:11 | 49.952
2020-02-13 | 15:11 | 49.954
2020-02-13 | 15:11 | 49.957
2020-02-13 | 15:11 | 49.961
2020-02-13 | 15:11 | 49.964
2020-02-13 | 15:12 | 49.965
2020-02-13 | 15:12 | 49.967
2020-02-13 | 15:12 | 49.967
2020-02-13 | 15:12 | 49.966
2020-02-13 | 15:12 | 49.966
2020-02-13 | 15:12 | 49.966
2020-02-13 | 15:12 | 49.966
2020-02-13 | 15:12 | 49.965
2020-02-13 | 15:12 | 49.965
2020-02-13 | 15:12 | 49.964
2020-02-13 | 15:12 | 49.962
2020-02-13 | 15:12 | 49.963
2020-02-13 | 15:12 | 49.964
2020-02-13 | 15:12 | 49.964
2020-02-13 | 15:12 | 49.964
2020-02-13 | 15:12 | 49.964
2020-02-13 | 15:12 | 49.964
2020-02-13 | 15:12 | 49.962
2020-02-13 | 15:12 | 49.962
2020-02-13 | 15:12 | 49.96
2020-02-13 | 15:12 | 49.961
2020-02-13 | 15:12 | 49.961
2020-02-13 | 15:12 | 49.96
2020-02-13 | 15:12 | 49.96
2020-02-13 | 15:12 | 49.961
2020-02-13 | 15:12 | 49.958
2020-02-13 | 15:12 | 49.955
2020-02-13 | 15:12 | 49.953
2020-02-13 | 15:12 | 49.95
2020-02-13 | 15:12 | 49.948
2020-02-13 | 15:12 | 49.945
2020-02-13 | 15:12 | 49.943
2020-02-13 | 15:12 | 49.94
2020-02-13 | 15:12 | 49.939
2020-02-13 | 15:12 | 49.937
2020-02-13 | 15:12 | 49.937
2020-02-13 | 15:12 | 49.937
2020-02-13 | 15:12 | 49.934
2020-02-13 | 15:12 | 49.934
2020-02-13 | 15:12 | 49.935
2020-02-13 | 15:12 | 49.936
2020-02-13 | 15:12 | 49.935
2020-02-13 | 15:12 | 49.934
2020-02-13 | 15:12 | 49.934
2020-02-13 | 15:12 | 49.932
2020-02-13 | 15:12 | 49.93
2020-02-13 | 15:12 | 49.927
2020-02-13 | 15:12 | 49.925
2020-02-13 | 15:12 | 49.925
2020-02-13 | 15:12 | 49.925
2020-02-13 | 15:12 | 49.926
2020-02-13 | 15:12 | 49.927
2020-02-13 | 15:12 | 49.926
2020-02-13 | 15:12 | 49.926
2020-02-13 | 15:12 | 49.925
2020-02-13 | 15:12 | 49.927
2020-02-13 | 15:12 | 49.928
2020-02-13 | 15:12 | 49.929
2020-02-13 | 15:12 | 49.929
2020-02-13 | 15:12 | 49.929
2020-02-13 | 15:12 | 49.929
2020-02-13 | 15:13 | 49.931
2020-02-13 | 15:13 | 49.932
2020-02-13 | 15:13 | 49.937
2020-02-13 | 15:13 | 49.94
2020-02-13 | 15:13 | 49.945
2020-02-13 | 15:13 | 49.949
2020-02-13 | 15:13 | 49.949
2020-02-13 | 15:13 | 49.95
2020-02-13 | 15:13 | 49.952
2020-02-13 | 15:13 | 49.95
2020-02-13 | 15:13 | 49.949
2020-02-13 | 15:13 | 49.947
2020-02-13 | 15:13 | 49.945
2020-02-13 | 15:13 | 49.947
2020-02-13 | 15:13 | 49.946
2020-02-13 | 15:13 | 49.947
2020-02-13 | 15:13 | 49.948
2020-02-13 | 15:13 | 49.948
2020-02-13 | 15:13 | 49.949
2020-02-13 | 15:13 | 49.949
2020-02-13 | 15:13 | 49.95
2020-02-13 | 15:13 | 49.95
2020-02-13 | 15:13 | 49.951
2020-02-13 | 15:13 | 49.951
2020-02-13 | 15:13 | 49.951
2020-02-13 | 15:13 | 49.951
2020-02-13 | 15:13 | 49.954
2020-02-13 | 15:13 | 49.954
2020-02-13 | 15:13 | 49.956
2020-02-13 | 15:13 | 49.957
2020-02-13 | 15:13 | 49.959
2020-02-13 | 15:13 | 49.96
2020-02-13 | 15:13 | 49.962
2020-02-13 | 15:13 | 49.963
2020-02-13 | 15:13 | 49.963
2020-02-13 | 15:13 | 49.964
2020-02-13 | 15:13 | 49.962
2020-02-13 | 15:13 | 49.961
2020-02-13 | 15:13 | 49.962
2020-02-13 | 15:13 | 49.963
2020-02-13 | 15:13 | 49.963
2020-02-13 | 15:13 | 49.962
2020-02-13 | 15:13 | 49.964
2020-02-13 | 15:13 | 49.966
2020-02-13 | 15:13 | 49.968
2020-02-13 | 15:13 | 49.97
2020-02-13 | 15:13 | 49.968
2020-02-13 | 15:13 | 49.97
2020-02-13 | 15:13 | 49.971
2020-02-13 | 15:13 | 49.975
2020-02-13 | 15:13 | 49.978
2020-02-13 | 15:13 | 49.981
2020-02-13 | 15:13 | 49.984
2020-02-13 | 15:13 | 49.985
2020-02-13 | 15:13 | 49.987
2020-02-13 | 15:13 | 49.987
2020-02-13 | 15:13 | 49.986
2020-02-13 | 15:13 | 49.987
2020-02-13 | 15:13 | 49.987
2020-02-13 | 15:14 | 49.985
2020-02-13 | 15:14 | 49.985
2020-02-13 | 15:14 | 49.984
2020-02-13 | 15:14 | 49.985
2020-02-13 | 15:14 | 49.987
2020-02-13 | 15:14 | 49.989
2020-02-13 | 15:14 | 49.99
2020-02-13 | 15:14 | 49.993
2020-02-13 | 15:14 | 49.996
2020-02-13 | 15:14 | 49.996
2020-02-13 | 15:14 | 49.995
2020-02-13 | 15:14 | 49.993
2020-02-13 | 15:14 | 49.991
2020-02-13 | 15:14 | 49.99
2020-02-13 | 15:14 | 49.99
2020-02-13 | 15:14 | 49.99
2020-02-13 | 15:14 | 49.989
2020-02-13 | 15:14 | 49.987
2020-02-13 | 15:14 | 49.986
2020-02-13 | 15:14 | 49.987
2020-02-13 | 15:14 | 49.986
2020-02-13 | 15:14 | 49.984
2020-02-13 | 15:14 | 49.981
2020-02-13 | 15:14 | 49.982
2020-02-13 | 15:14 | 49.981
2020-02-13 | 15:14 | 49.983
2020-02-13 | 15:14 | 49.983
2020-02-13 | 15:14 | 49.985
2020-02-13 | 15:14 | 49.985
2020-02-13 | 15:14 | 49.986
2020-02-13 | 15:14 | 49.987
2020-02-13 | 15:14 | 49.983
2020-02-13 | 15:14 | 49.984
2020-02-13 | 15:14 | 49.982
2020-02-13 | 15:14 | 49.982
2020-02-13 | 15:14 | 49.981
2020-02-13 | 15:14 | 49.98
2020-02-13 | 15:14 | 49.977
2020-02-13 | 15:14 | 49.972
2020-02-13 | 15:14 | 49.97
2020-02-13 | 15:14 | 49.969
2020-02-13 | 15:14 | 49.965
2020-02-13 | 15:14 | 49.963
2020-02-13 | 15:14 | 49.963
2020-02-13 | 15:14 | 49.962
2020-02-13 | 15:14 | 49.961
2020-02-13 | 15:14 | 49.959
2020-02-13 | 15:14 | 49.959
2020-02-13 | 15:14 | 49.959
2020-02-13 | 15:14 | 49.959
2020-02-13 | 15:14 | 49.961
2020-02-13 | 15:14 | 49.96
2020-02-13 | 15:14 | 49.962
2020-02-13 | 15:14 | 49.965
2020-02-13 | 15:14 | 49.965
2020-02-13 | 15:14 | 49.967
2020-02-13 | 15:14 | 49.967
2020-02-13 | 15:14 | 49.964
2020-02-13 | 15:14 | 49.964
2020-02-13 | 15:14 | 49.963
2020-02-13 | 15:14 | 49.965
2020-02-13 | 15:15 | 49.969
2020-02-13 | 15:15 | 49.97
2020-02-13 | 15:15 | 49.973
2020-02-13 | 15:15 | 49.976
2020-02-13 | 15:15 | 49.983
2020-02-13 | 15:15 | 49.984
2020-02-13 | 15:15 | 49.987
2020-02-13 | 15:15 | 49.987
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.991
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.988
2020-02-13 | 15:15 | 49.989
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.989
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.99
2020-02-13 | 15:15 | 49.988
2020-02-13 | 15:15 | 49.987
2020-02-13 | 15:15 | 49.985
2020-02-13 | 15:15 | 49.983
2020-02-13 | 15:15 | 49.983
2020-02-13 | 15:15 | 49.982
2020-02-13 | 15:15 | 49.98
2020-02-13 | 15:15 | 49.979
2020-02-13 | 15:15 | 49.977
2020-02-13 | 15:15 | 49.975
2020-02-13 | 15:15 | 49.974
2020-02-13 | 15:15 | 49.973
2020-02-13 | 15:15 | 49.972
2020-02-13 | 15:15 | 49.971
2020-02-13 | 15:15 | 49.969
2020-02-13 | 15:15 | 49.968
2020-02-13 | 15:15 | 49.968
2020-02-13 | 15:15 | 49.968
2020-02-13 | 15:15 | 49.969
2020-02-13 | 15:15 | 49.969
2020-02-13 | 15:15 | 49.97
2020-02-13 | 15:15 | 49.97
2020-02-13 | 15:15 | 49.968
2020-02-13 | 15:15 | 49.971
2020-02-13 | 15:15 | 49.974
2020-02-13 | 15:15 | 49.974
2020-02-13 | 15:15 | 49.975
2020-02-13 | 15:15 | 49.976
2020-02-13 | 15:15 | 49.978
2020-02-13 | 15:15 | 49.98
2020-02-13 | 15:15 | 49.98
2020-02-13 | 15:15 | 49.98
2020-02-13 | 15:15 | 49.982
2020-02-13 | 15:15 | 49.981
2020-02-13 | 15:15 | 49.98
2020-02-13 | 15:15 | 49.979
2020-02-13 | 15:15 | 49.976
2020-02-13 | 15:15 | 49.976
2020-02-13 | 15:15 | 49.975
2020-02-13 | 15:15 | 49.976
2020-02-13 | 15:16 | 49.977
2020-02-13 | 15:16 | 49.975
2020-02-13 | 15:16 | 49.975
2020-02-13 | 15:16 | 49.975
2020-02-13 | 15:16 | 49.977
2020-02-13 | 15:16 | 49.977
2020-02-13 | 15:16 | 49.977
2020-02-13 | 15:16 | 49.979
2020-02-13 | 15:16 | 49.98
2020-02-13 | 15:16 | 49.982
2020-02-13 | 15:16 | 49.985
2020-02-13 | 15:16 | 49.988
2020-02-13 | 15:16 | 49.992
2020-02-13 | 15:16 | 49.993
2020-02-13 | 15:16 | 49.996
2020-02-13 | 15:16 | 49.999
2020-02-13 | 15:16 | 50
2020-02-13 | 15:16 | 50
2020-02-13 | 15:16 | 50
2020-02-13 | 15:16 | 49.999
2020-02-13 | 15:16 | 49.999
2020-02-13 | 15:16 | 50
2020-02-13 | 15:16 | 50
2020-02-13 | 15:16 | 49.999
2020-02-13 | 15:16 | 49.998
2020-02-13 | 15:16 | 49.996
2020-02-13 | 15:16 | 49.996
2020-02-13 | 15:16 | 49.995
2020-02-13 | 15:16 | 49.994
2020-02-13 | 15:16 | 49.993
2020-02-13 | 15:16 | 49.991
2020-02-13 | 15:16 | 49.991
2020-02-13 | 15:16 | 49.992
2020-02-13 | 15:16 | 49.991
2020-02-13 | 15:16 | 49.989
2020-02-13 | 15:16 | 49.987
2020-02-13 | 15:16 | 49.983
2020-02-13 | 15:16 | 49.98
2020-02-13 | 15:16 | 49.978
2020-02-13 | 15:16 | 49.974
2020-02-13 | 15:16 | 49.971
2020-02-13 | 15:16 | 49.966
2020-02-13 | 15:16 | 49.963
2020-02-13 | 15:16 | 49.962
2020-02-13 | 15:16 | 49.96
2020-02-13 | 15:16 | 49.959
2020-02-13 | 15:16 | 49.959
2020-02-13 | 15:16 | 49.957
2020-02-13 | 15:16 | 49.96
2020-02-13 | 15:16 | 49.961
2020-02-13 | 15:16 | 49.962
2020-02-13 | 15:16 | 49.966
2020-02-13 | 15:16 | 49.968
2020-02-13 | 15:16 | 49.966
2020-02-13 | 15:16 | 49.967
2020-02-13 | 15:16 | 49.966
2020-02-13 | 15:16 | 49.965
2020-02-13 | 15:16 | 49.963
2020-02-13 | 15:16 | 49.963
2020-02-13 | 15:16 | 49.964
2020-02-13 | 15:16 | 49.965
2020-02-13 | 15:17 | 49.966
2020-02-13 | 15:17 | 49.966
2020-02-13 | 15:17 | 49.969
2020-02-13 | 15:17 | 49.971
2020-02-13 | 15:17 | 49.974
2020-02-13 | 15:17 | 49.976
2020-02-13 | 15:17 | 49.978
2020-02-13 | 15:17 | 49.98
2020-02-13 | 15:17 | 49.98
2020-02-13 | 15:17 | 49.978
2020-02-13 | 15:17 | 49.975
2020-02-13 | 15:17 | 49.973
2020-02-13 | 15:17 | 49.97
2020-02-13 | 15:17 | 49.967
2020-02-13 | 15:17 | 49.965
2020-02-13 | 15:17 | 49.964
2020-02-13 | 15:17 | 49.963
2020-02-13 | 15:17 | 49.961
2020-02-13 | 15:17 | 49.961
2020-02-13 | 15:17 | 49.961
2020-02-13 | 15:17 | 49.96
2020-02-13 | 15:17 | 49.961
2020-02-13 | 15:17 | 49.957
2020-02-13 | 15:17 | 49.953
2020-02-13 | 15:17 | 49.95
2020-02-13 | 15:17 | 49.949
2020-02-13 | 15:17 | 49.946
2020-02-13 | 15:17 | 49.945
2020-02-13 | 15:17 | 49.942
2020-02-13 | 15:17 | 49.939
2020-02-13 | 15:17 | 49.937
2020-02-13 | 15:17 | 49.936
2020-02-13 | 15:17 | 49.934
2020-02-13 | 15:17 | 49.932
2020-02-13 | 15:17 | 49.933
2020-02-13 | 15:17 | 49.934
2020-02-13 | 15:17 | 49.936
2020-02-13 | 15:17 | 49.937
2020-02-13 | 15:17 | 49.937
2020-02-13 | 15:17 | 49.935
2020-02-13 | 15:17 | 49.937
2020-02-13 | 15:17 | 49.937
2020-02-13 | 15:17 | 49.939
2020-02-13 | 15:17 | 49.941
2020-02-13 | 15:17 | 49.945
2020-02-13 | 15:17 | 49.948
2020-02-13 | 15:17 | 49.95
2020-02-13 | 15:17 | 49.953
2020-02-13 | 15:17 | 49.956
2020-02-13 | 15:17 | 49.957
2020-02-13 | 15:17 | 49.958
2020-02-13 | 15:17 | 49.96
2020-02-13 | 15:17 | 49.962
2020-02-13 | 15:17 | 49.963
2020-02-13 | 15:17 | 49.965
2020-02-13 | 15:17 | 49.966
2020-02-13 | 15:17 | 49.967
2020-02-13 | 15:17 | 49.967
2020-02-13 | 15:17 | 49.963
2020-02-13 | 15:18 | 49.961
2020-02-13 | 15:18 | 49.958
2020-02-13 | 15:18 | 49.958
2020-02-13 | 15:18 | 49.957
2020-02-13 | 15:18 | 49.958
2020-02-13 | 15:18 | 49.96
2020-02-13 | 15:18 | 49.959
2020-02-13 | 15:18 | 49.961
2020-02-13 | 15:18 | 49.962
2020-02-13 | 15:18 | 49.962
2020-02-13 | 15:18 | 49.959
2020-02-13 | 15:18 | 49.959
2020-02-13 | 15:18 | 49.959
2020-02-13 | 15:18 | 49.959
2020-02-13 | 15:18 | 49.96
2020-02-13 | 15:18 | 49.962
2020-02-13 | 15:18 | 49.962
2020-02-13 | 15:18 | 49.962
2020-02-13 | 15:18 | 49.962
2020-02-13 | 15:18 | 49.959
2020-02-13 | 15:18 | 49.956
2020-02-13 | 15:18 | 49.953
2020-02-13 | 15:18 | 49.949
2020-02-13 | 15:18 | 49.949
2020-02-13 | 15:18 | 49.949
2020-02-13 | 15:18 | 49.948
2020-02-13 | 15:18 | 49.948
2020-02-13 | 15:18 | 49.948
2020-02-13 | 15:18 | 49.95
2020-02-13 | 15:18 | 49.95
2020-02-13 | 15:18 | 49.951
2020-02-13 | 15:18 | 49.954
2020-02-13 | 15:18 | 49.957
2020-02-13 | 15:18 | 49.963
2020-02-13 | 15:18 | 49.97
2020-02-13 | 15:18 | 49.976
2020-02-13 | 15:18 | 49.98
2020-02-13 | 15:18 | 49.983
2020-02-13 | 15:18 | 49.985
2020-02-13 | 15:18 | 49.987
2020-02-13 | 15:18 | 49.986
2020-02-13 | 15:18 | 49.985
2020-02-13 | 15:18 | 49.985
2020-02-13 | 15:18 | 49.983
2020-02-13 | 15:18 | 49.983
2020-02-13 | 15:18 | 49.985
2020-02-13 | 15:18 | 49.983
2020-02-13 | 15:18 | 49.982
2020-02-13 | 15:18 | 49.981
2020-02-13 | 15:18 | 49.977
2020-02-13 | 15:18 | 49.972
2020-02-13 | 15:18 | 49.967
2020-02-13 | 15:18 | 49.961
2020-02-13 | 15:18 | 49.957
2020-02-13 | 15:18 | 49.955
2020-02-13 | 15:18 | 49.953
2020-02-13 | 15:18 | 49.952
2020-02-13 | 15:18 | 49.95
2020-02-13 | 15:18 | 49.949
2020-02-13 | 15:18 | 49.947
2020-02-13 | 15:18 | 49.948
2020-02-13 | 15:19 | 49.95
2020-02-13 | 15:19 | 49.952
2020-02-13 | 15:19 | 49.953
2020-02-13 | 15:19 | 49.953
2020-02-13 | 15:19 | 49.956
2020-02-13 | 15:19 | 49.957
2020-02-13 | 15:19 | 49.957
2020-02-13 | 15:19 | 49.959
2020-02-13 | 15:19 | 49.962
2020-02-13 | 15:19 | 49.962
2020-02-13 | 15:19 | 49.962
2020-02-13 | 15:19 | 49.959
2020-02-13 | 15:19 | 49.959
2020-02-13 | 15:19 | 49.957
2020-02-13 | 15:19 | 49.956
2020-02-13 | 15:19 | 49.953
2020-02-13 | 15:19 | 49.948
2020-02-13 | 15:19 | 49.943
2020-02-13 | 15:19 | 49.937
2020-02-13 | 15:19 | 49.933
2020-02-13 | 15:19 | 49.929
2020-02-13 | 15:19 | 49.925
2020-02-13 | 15:19 | 49.92
2020-02-13 | 15:19 | 49.916
2020-02-13 | 15:19 | 49.913
2020-02-13 | 15:19 | 49.911
2020-02-13 | 15:19 | 49.911
2020-02-13 | 15:19 | 49.908
2020-02-13 | 15:19 | 49.905
2020-02-13 | 15:19 | 49.903
2020-02-13 | 15:19 | 49.904
2020-02-13 | 15:19 | 49.904
2020-02-13 | 15:19 | 49.902
2020-02-13 | 15:19 | 49.901
2020-02-13 | 15:19 | 49.9
2020-02-13 | 15:19 | 49.901
2020-02-13 | 15:19 | 49.903
2020-02-13 | 15:19 | 49.905
2020-02-13 | 15:19 | 49.907
2020-02-13 | 15:19 | 49.909
2020-02-13 | 15:19 | 49.911
2020-02-13 | 15:19 | 49.914
2020-02-13 | 15:19 | 49.917
2020-02-13 | 15:19 | 49.92
2020-02-13 | 15:19 | 49.923
2020-02-13 | 15:19 | 49.923
2020-02-13 | 15:19 | 49.925
2020-02-13 | 15:19 | 49.927
2020-02-13 | 15:19 | 49.929
2020-02-13 | 15:19 | 49.93
2020-02-13 | 15:19 | 49.93
2020-02-13 | 15:19 | 49.935
2020-02-13 | 15:19 | 49.937
2020-02-13 | 15:19 | 49.938
2020-02-13 | 15:19 | 49.939
2020-02-13 | 15:19 | 49.937
2020-02-13 | 15:19 | 49.934
2020-02-13 | 15:19 | 49.932
2020-02-13 | 15:19 | 49.929
2020-02-13 | 15:20 | 49.93
2020-02-13 | 15:20 | 49.932
2020-02-13 | 15:20 | 49.932
2020-02-13 | 15:20 | 49.932
2020-02-13 | 15:20 | 49.933
2020-02-13 | 15:20 | 49.934
2020-02-13 | 15:20 | 49.937
2020-02-13 | 15:20 | 49.938
2020-02-13 | 15:20 | 49.94
2020-02-13 | 15:20 | 49.943
2020-02-13 | 15:20 | 49.945
2020-02-13 | 15:20 | 49.947
2020-02-13 | 15:20 | 49.947
2020-02-13 | 15:20 | 49.947
2020-02-13 | 15:20 | 49.947
2020-02-13 | 15:20 | 49.948
2020-02-13 | 15:20 | 49.947
2020-02-13 | 15:20 | 49.949
2020-02-13 | 15:20 | 49.951
2020-02-13 | 15:20 | 49.951
2020-02-13 | 15:20 | 49.956
2020-02-13 | 15:20 | 49.957
2020-02-13 | 15:20 | 49.961
2020-02-13 | 15:20 | 49.965
2020-02-13 | 15:20 | 49.966
2020-02-13 | 15:20 | 49.966
2020-02-13 | 15:20 | 49.965
2020-02-13 | 15:20 | 49.963
2020-02-13 | 15:20 | 49.961
2020-02-13 | 15:20 | 49.959
2020-02-13 | 15:20 | 49.957
2020-02-13 | 15:20 | 49.957
2020-02-13 | 15:20 | 49.958
2020-02-13 | 15:20 | 49.958
2020-02-13 | 15:20 | 49.958
2020-02-13 | 15:20 | 49.959
2020-02-13 | 15:20 | 49.959
2020-02-13 | 15:20 | 49.958
2020-02-13 | 15:20 | 49.959
2020-02-13 | 15:20 | 49.962
2020-02-13 | 15:20 | 49.965
2020-02-13 | 15:20 | 49.967
2020-02-13 | 15:20 | 49.966
2020-02-13 | 15:20 | 49.967
2020-02-13 | 15:20 | 49.966
2020-02-13 | 15:20 | 49.966
2020-02-13 | 15:20 | 49.968
2020-02-13 | 15:20 | 49.972
2020-02-13 | 15:20 | 49.973
2020-02-13 | 15:20 | 49.975
2020-02-13 | 15:20 | 49.975
2020-02-13 | 15:20 | 49.975
2020-02-13 | 15:20 | 49.976
2020-02-13 | 15:20 | 49.979
2020-02-13 | 15:20 | 49.981
2020-02-13 | 15:20 | 49.985
2020-02-13 | 15:20 | 49.987
2020-02-13 | 15:20 | 49.99
2020-02-13 | 15:20 | 49.988
2020-02-13 | 15:20 | 49.987
2020-02-13 | 15:20 | 49.986
2020-02-13 | 15:21 | 49.985
2020-02-13 | 15:21 | 49.982
2020-02-13 | 15:21 | 49.981
2020-02-13 | 15:21 | 49.979
2020-02-13 | 15:21 | 49.976
2020-02-13 | 15:21 | 49.974
2020-02-13 | 15:21 | 49.971
2020-02-13 | 15:21 | 49.97
2020-02-13 | 15:21 | 49.97
2020-02-13 | 15:21 | 49.969
2020-02-13 | 15:21 | 49.967
2020-02-13 | 15:21 | 49.966
2020-02-13 | 15:21 | 49.965
2020-02-13 | 15:21 | 49.967
2020-02-13 | 15:21 | 49.97
2020-02-13 | 15:21 | 49.971
2020-02-13 | 15:21 | 49.973
2020-02-13 | 15:21 | 49.976
2020-02-13 | 15:21 | 49.977
2020-02-13 | 15:21 | 49.978
2020-02-13 | 15:21 | 49.98
2020-02-13 | 15:21 | 49.981
2020-02-13 | 15:21 | 49.984
2020-02-13 | 15:21 | 49.984
2020-02-13 | 15:21 | 49.985
2020-02-13 | 15:21 | 49.985
2020-02-13 | 15:21 | 49.984
2020-02-13 | 15:21 | 49.984
2020-02-13 | 15:21 | 49.984
2020-02-13 | 15:21 | 49.98
2020-02-13 | 15:21 | 49.978
2020-02-13 | 15:21 | 49.976
2020-02-13 | 15:21 | 49.976
2020-02-13 | 15:21 | 49.976
2020-02-13 | 15:21 | 49.977
2020-02-13 | 15:21 | 49.976
2020-02-13 | 15:21 | 49.977
2020-02-13 | 15:21 | 49.978
2020-02-13 | 15:21 | 49.979
2020-02-13 | 15:21 | 49.982
2020-02-13 | 15:21 | 49.982
2020-02-13 | 15:21 | 49.981
2020-02-13 | 15:21 | 49.98
2020-02-13 | 15:21 | 49.978
2020-02-13 | 15:21 | 49.977
2020-02-13 | 15:21 | 49.975
2020-02-13 | 15:21 | 49.974
2020-02-13 | 15:21 | 49.972
2020-02-13 | 15:21 | 49.971
2020-02-13 | 15:21 | 49.97
2020-02-13 | 15:21 | 49.969
2020-02-13 | 15:21 | 49.967
2020-02-13 | 15:21 | 49.965
2020-02-13 | 15:21 | 49.963
2020-02-13 | 15:21 | 49.963
2020-02-13 | 15:21 | 49.962
2020-02-13 | 15:21 | 49.961
2020-02-13 | 15:21 | 49.958
2020-02-13 | 15:21 | 49.957
2020-02-13 | 15:22 | 49.956
2020-02-13 | 15:22 | 49.955
2020-02-13 | 15:22 | 49.955
2020-02-13 | 15:22 | 49.956
2020-02-13 | 15:22 | 49.957
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.962
2020-02-13 | 15:22 | 49.962
2020-02-13 | 15:22 | 49.964
2020-02-13 | 15:22 | 49.965
2020-02-13 | 15:22 | 49.968
2020-02-13 | 15:22 | 49.968
2020-02-13 | 15:22 | 49.973
2020-02-13 | 15:22 | 49.974
2020-02-13 | 15:22 | 49.976
2020-02-13 | 15:22 | 49.976
2020-02-13 | 15:22 | 49.977
2020-02-13 | 15:22 | 49.978
2020-02-13 | 15:22 | 49.979
2020-02-13 | 15:22 | 49.978
2020-02-13 | 15:22 | 49.978
2020-02-13 | 15:22 | 49.976
2020-02-13 | 15:22 | 49.974
2020-02-13 | 15:22 | 49.973
2020-02-13 | 15:22 | 49.972
2020-02-13 | 15:22 | 49.973
2020-02-13 | 15:22 | 49.972
2020-02-13 | 15:22 | 49.971
2020-02-13 | 15:22 | 49.971
2020-02-13 | 15:22 | 49.97
2020-02-13 | 15:22 | 49.969
2020-02-13 | 15:22 | 49.97
2020-02-13 | 15:22 | 49.968
2020-02-13 | 15:22 | 49.967
2020-02-13 | 15:22 | 49.965
2020-02-13 | 15:22 | 49.964
2020-02-13 | 15:22 | 49.963
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.962
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.961
2020-02-13 | 15:22 | 49.96
2020-02-13 | 15:22 | 49.959
2020-02-13 | 15:22 | 49.96
2020-02-13 | 15:22 | 49.956
2020-02-13 | 15:22 | 49.955
2020-02-13 | 15:22 | 49.953
2020-02-13 | 15:22 | 49.95
2020-02-13 | 15:22 | 49.951
2020-02-13 | 15:22 | 49.95
2020-02-13 | 15:22 | 49.949
2020-02-13 | 15:22 | 49.947
2020-02-13 | 15:22 | 49.946
2020-02-13 | 15:22 | 49.946
2020-02-13 | 15:22 | 49.947
2020-02-13 | 15:22 | 49.95
2020-02-13 | 15:22 | 49.953
2020-02-13 | 15:22 | 49.956
2020-02-13 | 15:23 | 49.958
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.961
2020-02-13 | 15:23 | 49.962
2020-02-13 | 15:23 | 49.965
2020-02-13 | 15:23 | 49.964
2020-02-13 | 15:23 | 49.963
2020-02-13 | 15:23 | 49.963
2020-02-13 | 15:23 | 49.962
2020-02-13 | 15:23 | 49.958
2020-02-13 | 15:23 | 49.958
2020-02-13 | 15:23 | 49.962
2020-02-13 | 15:23 | 49.962
2020-02-13 | 15:23 | 49.961
2020-02-13 | 15:23 | 49.961
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.962
2020-02-13 | 15:23 | 49.961
2020-02-13 | 15:23 | 49.961
2020-02-13 | 15:23 | 49.96
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.957
2020-02-13 | 15:23 | 49.956
2020-02-13 | 15:23 | 49.956
2020-02-13 | 15:23 | 49.953
2020-02-13 | 15:23 | 49.952
2020-02-13 | 15:23 | 49.951
2020-02-13 | 15:23 | 49.95
2020-02-13 | 15:23 | 49.948
2020-02-13 | 15:23 | 49.946
2020-02-13 | 15:23 | 49.946
2020-02-13 | 15:23 | 49.947
2020-02-13 | 15:23 | 49.946
2020-02-13 | 15:23 | 49.947
2020-02-13 | 15:23 | 49.947
2020-02-13 | 15:23 | 49.948
2020-02-13 | 15:23 | 49.948
2020-02-13 | 15:23 | 49.951
2020-02-13 | 15:23 | 49.953
2020-02-13 | 15:23 | 49.953
2020-02-13 | 15:23 | 49.955
2020-02-13 | 15:23 | 49.959
2020-02-13 | 15:23 | 49.961
2020-02-13 | 15:23 | 49.963
2020-02-13 | 15:23 | 49.963
2020-02-13 | 15:23 | 49.964
2020-02-13 | 15:23 | 49.966
2020-02-13 | 15:23 | 49.969
2020-02-13 | 15:23 | 49.972
2020-02-13 | 15:23 | 49.972
2020-02-13 | 15:23 | 49.974
2020-02-13 | 15:23 | 49.974
2020-02-13 | 15:23 | 49.974
2020-02-13 | 15:23 | 49.976
2020-02-13 | 15:23 | 49.976
2020-02-13 | 15:23 | 49.976
2020-02-13 | 15:24 | 49.974
2020-02-13 | 15:24 | 49.973
2020-02-13 | 15:24 | 49.969
2020-02-13 | 15:24 | 49.968
2020-02-13 | 15:24 | 49.965
2020-02-13 | 15:24 | 49.961
2020-02-13 | 15:24 | 49.958
2020-02-13 | 15:24 | 49.954
2020-02-13 | 15:24 | 49.952
2020-02-13 | 15:24 | 49.95
2020-02-13 | 15:24 | 49.949
2020-02-13 | 15:24 | 49.948
2020-02-13 | 15:24 | 49.944
2020-02-13 | 15:24 | 49.944
2020-02-13 | 15:24 | 49.944
2020-02-13 | 15:24 | 49.944
2020-02-13 | 15:24 | 49.945
2020-02-13 | 15:24 | 49.945
2020-02-13 | 15:24 | 49.948
2020-02-13 | 15:24 | 49.951
2020-02-13 | 15:24 | 49.954
2020-02-13 | 15:24 | 49.954
2020-02-13 | 15:24 | 49.955
2020-02-13 | 15:24 | 49.954
2020-02-13 | 15:24 | 49.956
2020-02-13 | 15:24 | 49.956
2020-02-13 | 15:24 | 49.959
2020-02-13 | 15:24 | 49.956
2020-02-13 | 15:24 | 49.955
2020-02-13 | 15:24 | 49.957
2020-02-13 | 15:24 | 49.959
2020-02-13 | 15:24 | 49.961
2020-02-13 | 15:24 | 49.964
2020-02-13 | 15:24 | 49.967
2020-02-13 | 15:24 | 49.967
2020-02-13 | 15:24 | 49.97
2020-02-13 | 15:24 | 49.972
2020-02-13 | 15:24 | 49.978
2020-02-13 | 15:24 | 49.98
2020-02-13 | 15:24 | 49.983
2020-02-13 | 15:24 | 49.983
2020-02-13 | 15:24 | 49.983
2020-02-13 | 15:24 | 49.983
2020-02-13 | 15:24 | 49.982
2020-02-13 | 15:24 | 49.981
2020-02-13 | 15:24 | 49.98
2020-02-13 | 15:24 | 49.98
2020-02-13 | 15:24 | 49.982
2020-02-13 | 15:24 | 49.982
2020-02-13 | 15:24 | 49.982
2020-02-13 | 15:24 | 49.983
2020-02-13 | 15:24 | 49.985
2020-02-13 | 15:24 | 49.985
2020-02-13 | 15:24 | 49.988
2020-02-13 | 15:24 | 49.989
2020-02-13 | 15:24 | 49.989
2020-02-13 | 15:24 | 49.989
2020-02-13 | 15:24 | 49.99
2020-02-13 | 15:24 | 49.992
2020-02-13 | 15:24 | 49.996
2020-02-13 | 15:24 | 50
2020-02-13 | 15:25 | 50.004
2020-02-13 | 15:25 | 50.005
2020-02-13 | 15:25 | 50.005
2020-02-13 | 15:25 | 50.004
2020-02-13 | 15:25 | 50.004
2020-02-13 | 15:25 | 50.005
2020-02-13 | 15:25 | 50.005
2020-02-13 | 15:25 | 50.007
2020-02-13 | 15:25 | 50.009
2020-02-13 | 15:25 | 50.008
2020-02-13 | 15:25 | 50.007
2020-02-13 | 15:25 | 50.007
2020-02-13 | 15:25 | 50.008
2020-02-13 | 15:25 | 50.007
2020-02-13 | 15:25 | 50.007
2020-02-13 | 15:25 | 50.008
2020-02-13 | 15:25 | 50.009
2020-02-13 | 15:25 | 50.011
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.013
2020-02-13 | 15:25 | 50.015
2020-02-13 | 15:25 | 50.016
2020-02-13 | 15:25 | 50.019
2020-02-13 | 15:25 | 50.021
2020-02-13 | 15:25 | 50.023
2020-02-13 | 15:25 | 50.023
2020-02-13 | 15:25 | 50.025
2020-02-13 | 15:25 | 50.027
2020-02-13 | 15:25 | 50.03
2020-02-13 | 15:25 | 50.03
2020-02-13 | 15:25 | 50.033
2020-02-13 | 15:25 | 50.033
2020-02-13 | 15:25 | 50.035
2020-02-13 | 15:25 | 50.035
2020-02-13 | 15:25 | 50.036
2020-02-13 | 15:25 | 50.037
2020-02-13 | 15:25 | 50.037
2020-02-13 | 15:25 | 50.036
2020-02-13 | 15:25 | 50.037
2020-02-13 | 15:25 | 50.037
2020-02-13 | 15:25 | 50.035
2020-02-13 | 15:25 | 50.032
2020-02-13 | 15:25 | 50.029
2020-02-13 | 15:25 | 50.026
2020-02-13 | 15:25 | 50.023
2020-02-13 | 15:25 | 50.022
2020-02-13 | 15:25 | 50.017
2020-02-13 | 15:25 | 50.015
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.013
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.013
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:25 | 50.012
2020-02-13 | 15:26 | 50.013
2020-02-13 | 15:26 | 50.014
2020-02-13 | 15:26 | 50.016
2020-02-13 | 15:26 | 50.019
2020-02-13 | 15:26 | 50.022
2020-02-13 | 15:26 | 50.024
2020-02-13 | 15:26 | 50.027
2020-02-13 | 15:26 | 50.029
2020-02-13 | 15:26 | 50.033
2020-02-13 | 15:26 | 50.036
2020-02-13 | 15:26 | 50.04
2020-02-13 | 15:26 | 50.045
2020-02-13 | 15:26 | 50.049
2020-02-13 | 15:26 | 50.05
2020-02-13 | 15:26 | 50.053
2020-02-13 | 15:26 | 50.056
2020-02-13 | 15:26 | 50.055
2020-02-13 | 15:26 | 50.056
2020-02-13 | 15:26 | 50.058
2020-02-13 | 15:26 | 50.061
2020-02-13 | 15:26 | 50.061
2020-02-13 | 15:26 | 50.064
2020-02-13 | 15:26 | 50.065
2020-02-13 | 15:26 | 50.064
2020-02-13 | 15:26 | 50.063
2020-02-13 | 15:26 | 50.063
2020-02-13 | 15:26 | 50.062
2020-02-13 | 15:26 | 50.061
2020-02-13 | 15:26 | 50.062
2020-02-13 | 15:26 | 50.061
2020-02-13 | 15:26 | 50.06
2020-02-13 | 15:26 | 50.06
2020-02-13 | 15:26 | 50.059
2020-02-13 | 15:26 | 50.057
2020-02-13 | 15:26 | 50.055
2020-02-13 | 15:26 | 50.054
2020-02-13 | 15:26 | 50.051
2020-02-13 | 15:26 | 50.051
2020-02-13 | 15:26 | 50.049
2020-02-13 | 15:26 | 50.049
2020-02-13 | 15:26 | 50.05
2020-02-13 | 15:26 | 50.05
2020-02-13 | 15:26 | 50.052
2020-02-13 | 15:26 | 50.051
2020-02-13 | 15:26 | 50.054
2020-02-13 | 15:26 | 50.056
2020-02-13 | 15:26 | 50.059
2020-02-13 | 15:26 | 50.061
2020-02-13 | 15:26 | 50.066
2020-02-13 | 15:26 | 50.069
2020-02-13 | 15:26 | 50.07
2020-02-13 | 15:26 | 50.073
2020-02-13 | 15:26 | 50.077
2020-02-13 | 15:26 | 50.079
2020-02-13 | 15:26 | 50.082
2020-02-13 | 15:26 | 50.084
2020-02-13 | 15:26 | 50.086
2020-02-13 | 15:26 | 50.087
2020-02-13 | 15:26 | 50.087
2020-02-13 | 15:26 | 50.089
2020-02-13 | 15:26 | 50.089
2020-02-13 | 15:27 | 50.089
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.089
2020-02-13 | 15:27 | 50.089
2020-02-13 | 15:27 | 50.09
2020-02-13 | 15:27 | 50.089
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.087
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.088
2020-02-13 | 15:27 | 50.089
2020-02-13 | 15:27 | 50.09
2020-02-13 | 15:27 | 50.092
2020-02-13 | 15:27 | 50.092
2020-02-13 | 15:27 | 50.089
2020-02-13 | 15:27 | 50.087
2020-02-13 | 15:27 | 50.085
2020-02-13 | 15:27 | 50.08
2020-02-13 | 15:27 | 50.077
2020-02-13 | 15:27 | 50.074
2020-02-13 | 15:27 | 50.073
2020-02-13 | 15:27 | 50.071
2020-02-13 | 15:27 | 50.07
2020-02-13 | 15:27 | 50.069
2020-02-13 | 15:27 | 50.068
2020-02-13 | 15:27 | 50.066
2020-02-13 | 15:27 | 50.064
2020-02-13 | 15:27 | 50.064
2020-02-13 | 15:27 | 50.065
2020-02-13 | 15:27 | 50.063
2020-02-13 | 15:27 | 50.061
2020-02-13 | 15:27 | 50.057
2020-02-13 | 15:27 | 50.052
2020-02-13 | 15:27 | 50.047
2020-02-13 | 15:27 | 50.042
2020-02-13 | 15:27 | 50.038
2020-02-13 | 15:27 | 50.035
2020-02-13 | 15:27 | 50.034
2020-02-13 | 15:27 | 50.038
2020-02-13 | 15:27 | 50.04
2020-02-13 | 15:27 | 50.039
2020-02-13 | 15:27 | 50.041
2020-02-13 | 15:27 | 50.042
2020-02-13 | 15:27 | 50.044
2020-02-13 | 15:27 | 50.044
2020-02-13 | 15:27 | 50.045
2020-02-13 | 15:27 | 50.045
2020-02-13 | 15:27 | 50.047
2020-02-13 | 15:27 | 50.047
2020-02-13 | 15:27 | 50.049
2020-02-13 | 15:27 | 50.048
2020-02-13 | 15:27 | 50.048
2020-02-13 | 15:27 | 50.051
2020-02-13 | 15:27 | 50.056
2020-02-13 | 15:27 | 50.066
2020-02-13 | 15:27 | 50.078
2020-02-13 | 15:28 | 50.089
2020-02-13 | 15:28 | 50.098
2020-02-13 | 15:28 | 50.106
2020-02-13 | 15:28 | 50.111
2020-02-13 | 15:28 | 50.112
2020-02-13 | 15:28 | 50.115
2020-02-13 | 15:28 | 50.118
2020-02-13 | 15:28 | 50.119
2020-02-13 | 15:28 | 50.12
2020-02-13 | 15:28 | 50.12
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.125
2020-02-13 | 15:28 | 50.125
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.123
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.123
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.124
2020-02-13 | 15:28 | 50.125
2020-02-13 | 15:28 | 50.123
2020-02-13 | 15:28 | 50.12
2020-02-13 | 15:28 | 50.118
2020-02-13 | 15:28 | 50.116
2020-02-13 | 15:28 | 50.115
2020-02-13 | 15:28 | 50.114
2020-02-13 | 15:28 | 50.113
2020-02-13 | 15:28 | 50.114
2020-02-13 | 15:28 | 50.111
2020-02-13 | 15:28 | 50.109
2020-02-13 | 15:28 | 50.108
2020-02-13 | 15:28 | 50.105
2020-02-13 | 15:28 | 50.104
2020-02-13 | 15:28 | 50.101
2020-02-13 | 15:28 | 50.098
2020-02-13 | 15:28 | 50.097
2020-02-13 | 15:28 | 50.096
2020-02-13 | 15:28 | 50.094
2020-02-13 | 15:28 | 50.094
2020-02-13 | 15:28 | 50.095
2020-02-13 | 15:28 | 50.095
2020-02-13 | 15:28 | 50.097
2020-02-13 | 15:28 | 50.097
2020-02-13 | 15:28 | 50.095
2020-02-13 | 15:28 | 50.096
2020-02-13 | 15:28 | 50.095
2020-02-13 | 15:28 | 50.096
2020-02-13 | 15:28 | 50.098
2020-02-13 | 15:28 | 50.099
2020-02-13 | 15:28 | 50.1
2020-02-13 | 15:28 | 50.102
2020-02-13 | 15:28 | 50.103
2020-02-13 | 15:28 | 50.104
2020-02-13 | 15:28 | 50.107
2020-02-13 | 15:28 | 50.107
2020-02-13 | 15:28 | 50.107
2020-02-13 | 15:28 | 50.108
2020-02-13 | 15:28 | 50.106
2020-02-13 | 15:28 | 50.102
2020-02-13 | 15:29 | 50.1
2020-02-13 | 15:29 | 50.099
2020-02-13 | 15:29 | 50.103
2020-02-13 | 15:29 | 50.104
2020-02-13 | 15:29 | 50.106
2020-02-13 | 15:29 | 50.106
2020-02-13 | 15:29 | 50.106
2020-02-13 | 15:29 | 50.106
2020-02-13 | 15:29 | 50.106
2020-02-13 | 15:29 | 50.105
2020-02-13 | 15:29 | 50.103
2020-02-13 | 15:29 | 50.104
2020-02-13 | 15:29 | 50.103
2020-02-13 | 15:29 | 50.104
2020-02-13 | 15:29 | 50.104
2020-02-13 | 15:29 | 50.105
2020-02-13 | 15:29 | 50.106
2020-02-13 | 15:29 | 50.108
2020-02-13 | 15:29 | 50.112
2020-02-13 | 15:29 | 50.115
2020-02-13 | 15:29 | 50.119
2020-02-13 | 15:29 | 50.122
2020-02-13 | 15:29 | 50.124
2020-02-13 | 15:29 | 50.125
2020-02-13 | 15:29 | 50.126
2020-02-13 | 15:29 | 50.125
2020-02-13 | 15:29 | 50.125
2020-02-13 | 15:29 | 50.124
2020-02-13 | 15:29 | 50.122
2020-02-13 | 15:29 | 50.121
2020-02-13 | 15:29 | 50.121
2020-02-13 | 15:29 | 50.123
2020-02-13 | 15:29 | 50.125
2020-02-13 | 15:29 | 50.126
2020-02-13 | 15:29 | 50.126
2020-02-13 | 15:29 | 50.127
2020-02-13 | 15:29 | 50.129
2020-02-13 | 15:29 | 50.13
2020-02-13 | 15:29 | 50.132
2020-02-13 | 15:29 | 50.132
2020-02-13 | 15:29 | 50.136
2020-02-13 | 15:29 | 50.137
2020-02-13 | 15:29 | 50.14
2020-02-13 | 15:29 | 50.139
2020-02-13 | 15:29 | 50.139
2020-02-13 | 15:29 | 50.138
2020-02-13 | 15:29 | 50.136
2020-02-13 | 15:29 | 50.132
2020-02-13 | 15:29 | 50.13
2020-02-13 | 15:29 | 50.127
2020-02-13 | 15:29 | 50.127
2020-02-13 | 15:29 | 50.13
2020-02-13 | 15:29 | 50.13
2020-02-13 | 15:29 | 50.132
2020-02-13 | 15:29 | 50.133
2020-02-13 | 15:29 | 50.131
2020-02-13 | 15:29 | 50.131
2020-02-13 | 15:29 | 50.129
2020-02-13 | 15:29 | 50.129
2020-02-13 | 15:30 | 50.13
2020-02-13 | 15:30 | 50.13
2020-02-13 | 15:30 | 50.131
2020-02-13 | 15:30 | 50.132
2020-02-13 | 15:30 | 50.133
2020-02-13 | 15:30 | 50.137
2020-02-13 | 15:30 | 50.14
2020-02-13 | 15:30 | 50.141
2020-02-13 | 15:30 | 50.144
2020-02-13 | 15:30 | 50.146
2020-02-13 | 15:30 | 50.147
2020-02-13 | 15:30 | 50.149
2020-02-13 | 15:30 | 50.153
2020-02-13 | 15:30 | 50.153
2020-02-13 | 15:30 | 50.154
2020-02-13 | 15:30 | 50.156
2020-02-13 | 15:30 | 50.156
2020-02-13 | 15:30 | 50.158
2020-02-13 | 15:30 | 50.161
2020-02-13 | 15:30 | 50.16
2020-02-13 | 15:30 | 50.162
2020-02-13 | 15:30 | 50.164
2020-02-13 | 15:30 | 50.166
2020-02-13 | 15:30 | 50.165
2020-02-13 | 15:30 | 50.163
2020-02-13 | 15:30 | 50.161
2020-02-13 | 15:30 | 50.161
2020-02-13 | 15:30 | 50.16
2020-02-13 | 15:30 | 50.157
2020-02-13 | 15:30 | 50.155
2020-02-13 | 15:30 | 50.151
2020-02-13 | 15:30 | 50.151
2020-02-13 | 15:30 | 50.152
2020-02-13 | 15:30 | 50.155
2020-02-13 | 15:30 | 50.157
2020-02-13 | 15:30 | 50.162
2020-02-13 | 15:30 | 50.168
2020-02-13 | 15:30 | 50.172
2020-02-13 | 15:30 | 50.174
2020-02-13 | 15:30 | 50.175
2020-02-13 | 15:30 | 50.175
2020-02-13 | 15:30 | 50.175
2020-02-13 | 15:30 | 50.178
2020-02-13 | 15:30 | 50.178
2020-02-13 | 15:30 | 50.176
2020-02-13 | 15:30 | 50.173
2020-02-13 | 15:30 | 50.171
2020-02-13 | 15:30 | 50.169
2020-02-13 | 15:30 | 50.169
2020-02-13 | 15:30 | 50.168
2020-02-13 | 15:30 | 50.165
2020-02-13 | 15:30 | 50.165
2020-02-13 | 15:30 | 50.166
2020-02-13 | 15:30 | 50.167
2020-02-13 | 15:30 | 50.168
2020-02-13 | 15:30 | 50.17
2020-02-13 | 15:30 | 50.172
2020-02-13 | 15:30 | 50.176
2020-02-13 | 15:30 | 50.179
2020-02-13 | 15:30 | 50.182
2020-02-13 | 15:30 | 50.183
2020-02-13 | 15:31 | 50.183
2020-02-13 | 15:31 | 50.183
2020-02-13 | 15:31 | 50.183
2020-02-13 | 15:31 | 50.182
2020-02-13 | 15:31 | 50.179
2020-02-13 | 15:31 | 50.176
2020-02-13 | 15:31 | 50.171
2020-02-13 | 15:31 | 50.167
2020-02-13 | 15:31 | 50.165
2020-02-13 | 15:31 | 50.164
2020-02-13 | 15:31 | 50.163
2020-02-13 | 15:31 | 50.163
2020-02-13 | 15:31 | 50.162
2020-02-13 | 15:31 | 50.162
2020-02-13 | 15:31 | 50.163
2020-02-13 | 15:31 | 50.163
2020-02-13 | 15:31 | 50.162
2020-02-13 | 15:31 | 50.16
2020-02-13 | 15:31 | 50.16
2020-02-13 | 15:31 | 50.159
2020-02-13 | 15:31 | 50.16
2020-02-13 | 15:31 | 50.159
2020-02-13 | 15:31 | 50.159
2020-02-13 | 15:31 | 50.158
2020-02-13 | 15:31 | 50.158
2020-02-13 | 15:31 | 50.157
2020-02-13 | 15:31 | 50.156
2020-02-13 | 15:31 | 50.156
2020-02-13 | 15:31 | 50.153
2020-02-13 | 15:31 | 50.151
2020-02-13 | 15:31 | 50.154
2020-02-13 | 15:31 | 50.151
2020-02-13 | 15:31 | 50.149
2020-02-13 | 15:31 | 50.147
2020-02-13 | 15:31 | 50.147
2020-02-13 | 15:31 | 50.146
2020-02-13 | 15:31 | 50.146
2020-02-13 | 15:31 | 50.142
2020-02-13 | 15:31 | 50.142
2020-02-13 | 15:31 | 50.139
2020-02-13 | 15:31 | 50.138
2020-02-13 | 15:31 | 50.136
2020-02-13 | 15:31 | 50.134
2020-02-13 | 15:31 | 50.133
2020-02-13 | 15:31 | 50.132
2020-02-13 | 15:31 | 50.131
2020-02-13 | 15:31 | 50.13
2020-02-13 | 15:31 | 50.129
2020-02-13 | 15:31 | 50.128
2020-02-13 | 15:31 | 50.126
2020-02-13 | 15:31 | 50.128
2020-02-13 | 15:31 | 50.129
2020-02-13 | 15:31 | 50.131
2020-02-13 | 15:31 | 50.133
2020-02-13 | 15:31 | 50.134
2020-02-13 | 15:31 | 50.134
2020-02-13 | 15:31 | 50.133
2020-02-13 | 15:31 | 50.135
2020-02-13 | 15:31 | 50.138
2020-02-13 | 15:32 | 50.139
2020-02-13 | 15:32 | 50.14
2020-02-13 | 15:32 | 50.142
2020-02-13 | 15:32 | 50.147
2020-02-13 | 15:32 | 50.148
2020-02-13 | 15:32 | 50.148
2020-02-13 | 15:32 | 50.147
2020-02-13 | 15:32 | 50.144
2020-02-13 | 15:32 | 50.14
2020-02-13 | 15:32 | 50.14
2020-02-13 | 15:32 | 50.139
2020-02-13 | 15:32 | 50.137
2020-02-13 | 15:32 | 50.139
2020-02-13 | 15:32 | 50.141
2020-02-13 | 15:32 | 50.141
2020-02-13 | 15:32 | 50.141
2020-02-13 | 15:32 | 50.14
2020-02-13 | 15:32 | 50.136
2020-02-13 | 15:32 | 50.134
2020-02-13 | 15:32 | 50.13
2020-02-13 | 15:32 | 50.124
2020-02-13 | 15:32 | 50.119
2020-02-13 | 15:32 | 50.112
2020-02-13 | 15:32 | 50.105
2020-02-13 | 15:32 | 50.1
2020-02-13 | 15:32 | 50.094
2020-02-13 | 15:32 | 50.089
2020-02-13 | 15:32 | 50.085
2020-02-13 | 15:32 | 50.086
2020-02-13 | 15:32 | 50.087
2020-02-13 | 15:32 | 50.087
2020-02-13 | 15:32 | 50.088
2020-02-13 | 15:32 | 50.091
2020-02-13 | 15:32 | 50.094
2020-02-13 | 15:32 | 50.096
2020-02-13 | 15:32 | 50.095
2020-02-13 | 15:32 | 50.096
2020-02-13 | 15:32 | 50.096
2020-02-13 | 15:32 | 50.094
2020-02-13 | 15:32 | 50.092
2020-02-13 | 15:32 | 50.094
2020-02-13 | 15:32 | 50.093
2020-02-13 | 15:32 | 50.09
2020-02-13 | 15:32 | 50.089
2020-02-13 | 15:32 | 50.089
2020-02-13 | 15:32 | 50.086
2020-02-13 | 15:32 | 50.084
2020-02-13 | 15:32 | 50.084
2020-02-13 | 15:32 | 50.083
2020-02-13 | 15:32 | 50.082
2020-02-13 | 15:32 | 50.083
2020-02-13 | 15:32 | 50.085
2020-02-13 | 15:32 | 50.085
2020-02-13 | 15:32 | 50.086
2020-02-13 | 15:32 | 50.089
2020-02-13 | 15:32 | 50.089
2020-02-13 | 15:32 | 50.088
2020-02-13 | 15:32 | 50.087
2020-02-13 | 15:32 | 50.087
2020-02-13 | 15:32 | 50.084
2020-02-13 | 15:32 | 50.082
2020-02-13 | 15:33 | 50.08
2020-02-13 | 15:33 | 50.083
2020-02-13 | 15:33 | 50.087
2020-02-13 | 15:33 | 50.091
2020-02-13 | 15:33 | 50.097
2020-02-13 | 15:33 | 50.101
2020-02-13 | 15:33 | 50.103
2020-02-13 | 15:33 | 50.106
2020-02-13 | 15:33 | 50.109
2020-02-13 | 15:33 | 50.111
2020-02-13 | 15:33 | 50.112
2020-02-13 | 15:33 | 50.112
2020-02-13 | 15:33 | 50.112
2020-02-13 | 15:33 | 50.109
2020-02-13 | 15:33 | 50.11
2020-02-13 | 15:33 | 50.108
2020-02-13 | 15:33 | 50.103
2020-02-13 | 15:33 | 50.102
2020-02-13 | 15:33 | 50.098
2020-02-13 | 15:33 | 50.095
2020-02-13 | 15:33 | 50.092
2020-02-13 | 15:33 | 50.087
2020-02-13 | 15:33 | 50.082
2020-02-13 | 15:33 | 50.078
2020-02-13 | 15:33 | 50.076
2020-02-13 | 15:33 | 50.075
2020-02-13 | 15:33 | 50.071
2020-02-13 | 15:33 | 50.071
2020-02-13 | 15:33 | 50.07
2020-02-13 | 15:33 | 50.066
2020-02-13 | 15:33 | 50.062
2020-02-13 | 15:33 | 50.063
2020-02-13 | 15:33 | 50.061
2020-02-13 | 15:33 | 50.06
2020-02-13 | 15:33 | 50.062
2020-02-13 | 15:33 | 50.062
2020-02-13 | 15:33 | 50.062
2020-02-13 | 15:33 | 50.061
2020-02-13 | 15:33 | 50.059
2020-02-13 | 15:33 | 50.055
2020-02-13 | 15:33 | 50.051
2020-02-13 | 15:33 | 50.048
2020-02-13 | 15:33 | 50.046
2020-02-13 | 15:33 | 50.041
2020-02-13 | 15:33 | 50.034
2020-02-13 | 15:33 | 50.03
2020-02-13 | 15:33 | 50.024
2020-02-13 | 15:33 | 50.017
2020-02-13 | 15:33 | 50.014
2020-02-13 | 15:33 | 50.011
2020-02-13 | 15:33 | 50.006
2020-02-13 | 15:33 | 50.001
2020-02-13 | 15:33 | 50
2020-02-13 | 15:33 | 49.999
2020-02-13 | 15:33 | 49.997
2020-02-13 | 15:33 | 49.997
2020-02-13 | 15:33 | 49.998
2020-02-13 | 15:33 | 49.997
2020-02-13 | 15:33 | 50
2020-02-13 | 15:34 | 50
2020-02-13 | 15:34 | 49.999
2020-02-13 | 15:34 | 50
2020-02-13 | 15:34 | 50.001
2020-02-13 | 15:34 | 50
2020-02-13 | 15:34 | 50.002
2020-02-13 | 15:34 | 50.004
2020-02-13 | 15:34 | 50
2020-02-13 | 15:34 | 49.998
2020-02-13 | 15:34 | 49.998
2020-02-13 | 15:34 | 49.995
2020-02-13 | 15:34 | 49.992
2020-02-13 | 15:34 | 49.994
2020-02-13 | 15:34 | 49.992
2020-02-13 | 15:34 | 49.992
2020-02-13 | 15:34 | 49.991
2020-02-13 | 15:34 | 49.989
2020-02-13 | 15:34 | 49.988
2020-02-13 | 15:34 | 49.986
2020-02-13 | 15:34 | 49.984
2020-02-13 | 15:34 | 49.982
2020-02-13 | 15:34 | 49.98
2020-02-13 | 15:34 | 49.981
2020-02-13 | 15:34 | 49.979
2020-02-13 | 15:34 | 49.979
2020-02-13 | 15:34 | 49.98
2020-02-13 | 15:34 | 49.98
2020-02-13 | 15:34 | 49.979
2020-02-13 | 15:34 | 49.98
2020-02-13 | 15:34 | 49.98
2020-02-13 | 15:34 | 49.977
2020-02-13 | 15:34 | 49.976
2020-02-13 | 15:34 | 49.977
2020-02-13 | 15:34 | 49.974
2020-02-13 | 15:34 | 49.975
2020-02-13 | 15:34 | 49.973
2020-02-13 | 15:34 | 49.969
2020-02-13 | 15:34 | 49.969
2020-02-13 | 15:34 | 49.967
2020-02-13 | 15:34 | 49.962
2020-02-13 | 15:34 | 49.961
2020-02-13 | 15:34 | 49.96
2020-02-13 | 15:34 | 49.957
2020-02-13 | 15:34 | 49.959
2020-02-13 | 15:34 | 49.962
2020-02-13 | 15:34 | 49.961
2020-02-13 | 15:34 | 49.966
2020-02-13 | 15:34 | 49.967
2020-02-13 | 15:34 | 49.969
2020-02-13 | 15:34 | 49.972
2020-02-13 | 15:34 | 49.974
2020-02-13 | 15:34 | 49.976
2020-02-13 | 15:34 | 49.976
2020-02-13 | 15:34 | 49.977
2020-02-13 | 15:34 | 49.976
2020-02-13 | 15:34 | 49.976
2020-02-13 | 15:34 | 49.98
2020-02-13 | 15:34 | 49.981
2020-02-13 | 15:34 | 49.981
2020-02-13 | 15:34 | 49.983
2020-02-13 | 15:34 | 49.984
2020-02-13 | 15:35 | 49.982
2020-02-13 | 15:35 | 49.98
2020-02-13 | 15:35 | 49.977
2020-02-13 | 15:35 | 49.975
2020-02-13 | 15:35 | 49.972
2020-02-13 | 15:35 | 49.969
2020-02-13 | 15:35 | 49.964
2020-02-13 | 15:35 | 49.963
2020-02-13 | 15:35 | 49.959
2020-02-13 | 15:35 | 49.957
2020-02-13 | 15:35 | 49.953
2020-02-13 | 15:35 | 49.953
2020-02-13 | 15:35 | 49.952
2020-02-13 | 15:35 | 49.951
2020-02-13 | 15:35 | 49.95
2020-02-13 | 15:35 | 49.951
2020-02-13 | 15:35 | 49.949
2020-02-13 | 15:35 | 49.946
2020-02-13 | 15:35 | 49.948
2020-02-13 | 15:35 | 49.95
2020-02-13 | 15:35 | 49.947
2020-02-13 | 15:35 | 49.947
2020-02-13 | 15:35 | 49.947
2020-02-13 | 15:35 | 49.946
2020-02-13 | 15:35 | 49.943
2020-02-13 | 15:35 | 49.943
2020-02-13 | 15:35 | 49.942
2020-02-13 | 15:35 | 49.94
2020-02-13 | 15:35 | 49.939
2020-02-13 | 15:35 | 49.938
2020-02-13 | 15:35 | 49.936
2020-02-13 | 15:35 | 49.935
2020-02-13 | 15:35 | 49.937
2020-02-13 | 15:35 | 49.937
2020-02-13 | 15:35 | 49.938
2020-02-13 | 15:35 | 49.942
2020-02-13 | 15:35 | 49.942
2020-02-13 | 15:35 | 49.943
2020-02-13 | 15:35 | 49.947
2020-02-13 | 15:35 | 49.947
2020-02-13 | 15:35 | 49.949
2020-02-13 | 15:35 | 49.95
2020-02-13 | 15:35 | 49.951
2020-02-13 | 15:35 | 49.949
2020-02-13 | 15:35 | 49.948
2020-02-13 | 15:35 | 49.945
2020-02-13 | 15:35 | 49.943
2020-02-13 | 15:35 | 49.94
2020-02-13 | 15:35 | 49.938
2020-02-13 | 15:35 | 49.935
2020-02-13 | 15:35 | 49.933
2020-02-13 | 15:35 | 49.93
2020-02-13 | 15:35 | 49.93
2020-02-13 | 15:35 | 49.93
2020-02-13 | 15:35 | 49.929
2020-02-13 | 15:35 | 49.931
2020-02-13 | 15:35 | 49.93
2020-02-13 | 15:35 | 49.929
2020-02-13 | 15:35 | 49.929
2020-02-13 | 15:36 | 49.93
2020-02-13 | 15:36 | 49.927
2020-02-13 | 15:36 | 49.928
2020-02-13 | 15:36 | 49.93
2020-02-13 | 15:36 | 49.929
2020-02-13 | 15:36 | 49.928
2020-02-13 | 15:36 | 49.929
2020-02-13 | 15:36 | 49.928
2020-02-13 | 15:36 | 49.925
2020-02-13 | 15:36 | 49.925
2020-02-13 | 15:36 | 49.921
2020-02-13 | 15:36 | 49.918
2020-02-13 | 15:36 | 49.915
2020-02-13 | 15:36 | 49.914
2020-02-13 | 15:36 | 49.912
2020-02-13 | 15:36 | 49.912
2020-02-13 | 15:36 | 49.913
2020-02-13 | 15:36 | 49.91
2020-02-13 | 15:36 | 49.909
2020-02-13 | 15:36 | 49.911
2020-02-13 | 15:36 | 49.908
2020-02-13 | 15:36 | 49.908
2020-02-13 | 15:36 | 49.91
2020-02-13 | 15:36 | 49.909
2020-02-13 | 15:36 | 49.907
2020-02-13 | 15:36 | 49.906
2020-02-13 | 15:36 | 49.909
2020-02-13 | 15:36 | 49.91
2020-02-13 | 15:36 | 49.912
2020-02-13 | 15:36 | 49.913
2020-02-13 | 15:36 | 49.917
2020-02-13 | 15:36 | 49.917
2020-02-13 | 15:36 | 49.917
2020-02-13 | 15:36 | 49.916
2020-02-13 | 15:36 | 49.915
2020-02-13 | 15:36 | 49.913
2020-02-13 | 15:36 | 49.911
2020-02-13 | 15:36 | 49.911
2020-02-13 | 15:36 | 49.913
2020-02-13 | 15:36 | 49.91
2020-02-13 | 15:36 | 49.908
2020-02-13 | 15:36 | 49.908
2020-02-13 | 15:36 | 49.906
2020-02-13 | 15:36 | 49.906
2020-02-13 | 15:36 | 49.906
2020-02-13 | 15:36 | 49.903
2020-02-13 | 15:36 | 49.906
2020-02-13 | 15:36 | 49.905
2020-02-13 | 15:36 | 49.908
2020-02-13 | 15:36 | 49.911
2020-02-13 | 15:36 | 49.912
2020-02-13 | 15:36 | 49.914
2020-02-13 | 15:36 | 49.915
2020-02-13 | 15:36 | 49.917
2020-02-13 | 15:36 | 49.916
2020-02-13 | 15:36 | 49.917
2020-02-13 | 15:36 | 49.919
2020-02-13 | 15:36 | 49.918
2020-02-13 | 15:36 | 49.916
2020-02-13 | 15:36 | 49.913
2020-02-13 | 15:36 | 49.916
2020-02-13 | 15:37 | 49.913
2020-02-13 | 15:37 | 49.912
2020-02-13 | 15:37 | 49.909
2020-02-13 | 15:37 | 49.906
2020-02-13 | 15:37 | 49.906
2020-02-13 | 15:37 | 49.902
2020-02-13 | 15:37 | 49.898
2020-02-13 | 15:37 | 49.895
2020-02-13 | 15:37 | 49.895
2020-02-13 | 15:37 | 49.894
2020-02-13 | 15:37 | 49.893
2020-02-13 | 15:37 | 49.893
2020-02-13 | 15:37 | 49.896
2020-02-13 | 15:37 | 49.895
2020-02-13 | 15:37 | 49.895
2020-02-13 | 15:37 | 49.897
2020-02-13 | 15:37 | 49.9
2020-02-13 | 15:37 | 49.9
2020-02-13 | 15:37 | 49.9
2020-02-13 | 15:37 | 49.9
2020-02-13 | 15:37 | 49.901
2020-02-13 | 15:37 | 49.901
2020-02-13 | 15:37 | 49.902
2020-02-13 | 15:37 | 49.905
2020-02-13 | 15:37 | 49.903
2020-02-13 | 15:37 | 49.903
2020-02-13 | 15:37 | 49.903
2020-02-13 | 15:37 | 49.903
2020-02-13 | 15:37 | 49.904
2020-02-13 | 15:37 | 49.902
2020-02-13 | 15:37 | 49.902
2020-02-13 | 15:37 | 49.903
2020-02-13 | 15:37 | 49.903
2020-02-13 | 15:37 | 49.902
2020-02-13 | 15:37 | 49.902
2020-02-13 | 15:37 | 49.905
2020-02-13 | 15:37 | 49.907
2020-02-13 | 15:37 | 49.907
2020-02-13 | 15:37 | 49.911
2020-02-13 | 15:37 | 49.911
2020-02-13 | 15:37 | 49.913
2020-02-13 | 15:37 | 49.916
2020-02-13 | 15:37 | 49.919
2020-02-13 | 15:37 | 49.92
2020-02-13 | 15:37 | 49.921
2020-02-13 | 15:37 | 49.919
2020-02-13 | 15:37 | 49.918
2020-02-13 | 15:37 | 49.917
2020-02-13 | 15:37 | 49.915
2020-02-13 | 15:37 | 49.913
2020-02-13 | 15:37 | 49.915
2020-02-13 | 15:37 | 49.916
2020-02-13 | 15:37 | 49.915
2020-02-13 | 15:37 | 49.916
2020-02-13 | 15:37 | 49.918
2020-02-13 | 15:37 | 49.916
2020-02-13 | 15:37 | 49.914
2020-02-13 | 15:37 | 49.913
2020-02-13 | 15:37 | 49.913
2020-02-13 | 15:38 | 49.912
2020-02-13 | 15:38 | 49.91
2020-02-13 | 15:38 | 49.911
2020-02-13 | 15:38 | 49.907
2020-02-13 | 15:38 | 49.905
2020-02-13 | 15:38 | 49.902
2020-02-13 | 15:38 | 49.902
2020-02-13 | 15:38 | 49.902
2020-02-13 | 15:38 | 49.898
2020-02-13 | 15:38 | 49.896
2020-02-13 | 15:38 | 49.898
2020-02-13 | 15:38 | 49.899
2020-02-13 | 15:38 | 49.899
2020-02-13 | 15:38 | 49.897
2020-02-13 | 15:38 | 49.899
2020-02-13 | 15:38 | 49.899
2020-02-13 | 15:38 | 49.898
2020-02-13 | 15:38 | 49.899
2020-02-13 | 15:38 | 49.904
2020-02-13 | 15:38 | 49.906
2020-02-13 | 15:38 | 49.91
2020-02-13 | 15:38 | 49.913
2020-02-13 | 15:38 | 49.915
2020-02-13 | 15:38 | 49.918
2020-02-13 | 15:38 | 49.92
2020-02-13 | 15:38 | 49.92
2020-02-13 | 15:38 | 49.921
2020-02-13 | 15:38 | 49.922
2020-02-13 | 15:38 | 49.92
2020-02-13 | 15:38 | 49.918
2020-02-13 | 15:38 | 49.916
2020-02-13 | 15:38 | 49.913
2020-02-13 | 15:38 | 49.911
2020-02-13 | 15:38 | 49.907
2020-02-13 | 15:38 | 49.903
2020-02-13 | 15:38 | 49.9
2020-02-13 | 15:38 | 49.896
2020-02-13 | 15:38 | 49.889
2020-02-13 | 15:38 | 49.886
2020-02-13 | 15:38 | 49.885
2020-02-13 | 15:38 | 49.883
2020-02-13 | 15:38 | 49.884
2020-02-13 | 15:38 | 49.887
2020-02-13 | 15:38 | 49.89
2020-02-13 | 15:38 | 49.891
2020-02-13 | 15:38 | 49.894
2020-02-13 | 15:38 | 49.895
2020-02-13 | 15:38 | 49.896
2020-02-13 | 15:38 | 49.898
2020-02-13 | 15:38 | 49.899
2020-02-13 | 15:38 | 49.9
2020-02-13 | 15:38 | 49.9
2020-02-13 | 15:38 | 49.898
2020-02-13 | 15:38 | 49.894
2020-02-13 | 15:38 | 49.892
2020-02-13 | 15:38 | 49.89
2020-02-13 | 15:38 | 49.89
2020-02-13 | 15:38 | 49.89
2020-02-13 | 15:38 | 49.892
2020-02-13 | 15:38 | 49.892
2020-02-13 | 15:39 | 49.895
2020-02-13 | 15:39 | 49.897
2020-02-13 | 15:39 | 49.897
2020-02-13 | 15:39 | 49.899
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.898
2020-02-13 | 15:39 | 49.899
2020-02-13 | 15:39 | 49.898
2020-02-13 | 15:39 | 49.898
2020-02-13 | 15:39 | 49.897
2020-02-13 | 15:39 | 49.899
2020-02-13 | 15:39 | 49.899
2020-02-13 | 15:39 | 49.901
2020-02-13 | 15:39 | 49.902
2020-02-13 | 15:39 | 49.903
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.901
2020-02-13 | 15:39 | 49.901
2020-02-13 | 15:39 | 49.902
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.902
2020-02-13 | 15:39 | 49.899
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.897
2020-02-13 | 15:39 | 49.895
2020-02-13 | 15:39 | 49.895
2020-02-13 | 15:39 | 49.892
2020-02-13 | 15:39 | 49.889
2020-02-13 | 15:39 | 49.885
2020-02-13 | 15:39 | 49.884
2020-02-13 | 15:39 | 49.881
2020-02-13 | 15:39 | 49.88
2020-02-13 | 15:39 | 49.882
2020-02-13 | 15:39 | 49.88
2020-02-13 | 15:39 | 49.879
2020-02-13 | 15:39 | 49.882
2020-02-13 | 15:39 | 49.884
2020-02-13 | 15:39 | 49.884
2020-02-13 | 15:39 | 49.887
2020-02-13 | 15:39 | 49.889
2020-02-13 | 15:39 | 49.892
2020-02-13 | 15:39 | 49.893
2020-02-13 | 15:39 | 49.897
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.899
2020-02-13 | 15:39 | 49.902
2020-02-13 | 15:39 | 49.904
2020-02-13 | 15:39 | 49.903
2020-02-13 | 15:39 | 49.903
2020-02-13 | 15:39 | 49.903
2020-02-13 | 15:39 | 49.9
2020-02-13 | 15:39 | 49.895
2020-02-13 | 15:39 | 49.893
2020-02-13 | 15:39 | 49.891
2020-02-13 | 15:39 | 49.89
2020-02-13 | 15:39 | 49.892
2020-02-13 | 15:39 | 49.891
2020-02-13 | 15:39 | 49.891
2020-02-13 | 15:39 | 49.892
2020-02-13 | 15:39 | 49.893
2020-02-13 | 15:40 | 49.894
2020-02-13 | 15:40 | 49.894
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.894
2020-02-13 | 15:40 | 49.89
2020-02-13 | 15:40 | 49.892
2020-02-13 | 15:40 | 49.894
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.893
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.896
2020-02-13 | 15:40 | 49.897
2020-02-13 | 15:40 | 49.894
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.896
2020-02-13 | 15:40 | 49.896
2020-02-13 | 15:40 | 49.894
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.898
2020-02-13 | 15:40 | 49.898
2020-02-13 | 15:40 | 49.898
2020-02-13 | 15:40 | 49.899
2020-02-13 | 15:40 | 49.898
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.895
2020-02-13 | 15:40 | 49.893
2020-02-13 | 15:40 | 49.892
2020-02-13 | 15:40 | 49.89
2020-02-13 | 15:40 | 49.888
2020-02-13 | 15:40 | 49.886
2020-02-13 | 15:40 | 49.885
2020-02-13 | 15:40 | 49.883
2020-02-13 | 15:40 | 49.884
2020-02-13 | 15:40 | 49.882
2020-02-13 | 15:40 | 49.878
2020-02-13 | 15:40 | 49.877
2020-02-13 | 15:40 | 49.875
2020-02-13 | 15:40 | 49.872
2020-02-13 | 15:40 | 49.87
2020-02-13 | 15:40 | 49.869
2020-02-13 | 15:40 | 49.867
2020-02-13 | 15:40 | 49.866
2020-02-13 | 15:40 | 49.866
2020-02-13 | 15:40 | 49.866
2020-02-13 | 15:40 | 49.866
2020-02-13 | 15:40 | 49.865
2020-02-13 | 15:40 | 49.863
2020-02-13 | 15:40 | 49.862
2020-02-13 | 15:40 | 49.863
2020-02-13 | 15:40 | 49.862
2020-02-13 | 15:40 | 49.861
2020-02-13 | 15:40 | 49.86
2020-02-13 | 15:40 | 49.86
2020-02-13 | 15:40 | 49.858
2020-02-13 | 15:40 | 49.855
2020-02-13 | 15:40 | 49.854
2020-02-13 | 15:40 | 49.853
2020-02-13 | 15:40 | 49.849
2020-02-13 | 15:40 | 49.848
2020-02-13 | 15:41 | 49.846
2020-02-13 | 15:41 | 49.845
2020-02-13 | 15:41 | 49.844
2020-02-13 | 15:41 | 49.844
2020-02-13 | 15:41 | 49.842
2020-02-13 | 15:41 | 49.843
2020-02-13 | 15:41 | 49.843
2020-02-13 | 15:41 | 49.845
2020-02-13 | 15:41 | 49.843
2020-02-13 | 15:41 | 49.847
2020-02-13 | 15:41 | 49.849
2020-02-13 | 15:41 | 49.85
2020-02-13 | 15:41 | 49.848
2020-02-13 | 15:41 | 49.851
2020-02-13 | 15:41 | 49.85
2020-02-13 | 15:41 | 49.851
2020-02-13 | 15:41 | 49.852
2020-02-13 | 15:41 | 49.852
2020-02-13 | 15:41 | 49.853
2020-02-13 | 15:41 | 49.855
2020-02-13 | 15:41 | 49.856
2020-02-13 | 15:41 | 49.858
2020-02-13 | 15:41 | 49.86
2020-02-13 | 15:41 | 49.862
2020-02-13 | 15:41 | 49.861
2020-02-13 | 15:41 | 49.864
2020-02-13 | 15:41 | 49.865
2020-02-13 | 15:41 | 49.865
2020-02-13 | 15:41 | 49.864
2020-02-13 | 15:41 | 49.866
2020-02-13 | 15:41 | 49.866
2020-02-13 | 15:41 | 49.866
2020-02-13 | 15:41 | 49.867
2020-02-13 | 15:41 | 49.865
2020-02-13 | 15:41 | 49.863
2020-02-13 | 15:41 | 49.861
2020-02-13 | 15:41 | 49.859
2020-02-13 | 15:41 | 49.854
2020-02-13 | 15:41 | 49.85
2020-02-13 | 15:41 | 49.848
2020-02-13 | 15:41 | 49.846
2020-02-13 | 15:41 | 49.841
2020-02-13 | 15:41 | 49.84
2020-02-13 | 15:41 | 49.836
2020-02-13 | 15:41 | 49.834
2020-02-13 | 15:41 | 49.834
2020-02-13 | 15:41 | 49.834
2020-02-13 | 15:41 | 49.833
2020-02-13 | 15:41 | 49.838
2020-02-13 | 15:41 | 49.841
2020-02-13 | 15:41 | 49.845
2020-02-13 | 15:41 | 49.85
2020-02-13 | 15:41 | 49.855
2020-02-13 | 15:41 | 49.857
2020-02-13 | 15:41 | 49.864
2020-02-13 | 15:41 | 49.867
2020-02-13 | 15:41 | 49.868
2020-02-13 | 15:41 | 49.873
2020-02-13 | 15:41 | 49.878
2020-02-13 | 15:41 | 49.881
2020-02-13 | 15:41 | 49.885
2020-02-13 | 15:42 | 49.889
2020-02-13 | 15:42 | 49.89
2020-02-13 | 15:42 | 49.888
2020-02-13 | 15:42 | 49.892
2020-02-13 | 15:42 | 49.892
2020-02-13 | 15:42 | 49.891
2020-02-13 | 15:42 | 49.891
2020-02-13 | 15:42 | 49.894
2020-02-13 | 15:42 | 49.894
2020-02-13 | 15:42 | 49.896
2020-02-13 | 15:42 | 49.9
2020-02-13 | 15:42 | 49.903
2020-02-13 | 15:42 | 49.904
2020-02-13 | 15:42 | 49.908
2020-02-13 | 15:42 | 49.909
2020-02-13 | 15:42 | 49.908
2020-02-13 | 15:42 | 49.91
2020-02-13 | 15:42 | 49.913
2020-02-13 | 15:42 | 49.912
2020-02-13 | 15:42 | 49.914
2020-02-13 | 15:42 | 49.914
2020-02-13 | 15:42 | 49.911
2020-02-13 | 15:42 | 49.911
2020-02-13 | 15:42 | 49.912
2020-02-13 | 15:42 | 49.91
2020-02-13 | 15:42 | 49.907
2020-02-13 | 15:42 | 49.907
2020-02-13 | 15:42 | 49.904
2020-02-13 | 15:42 | 49.904
2020-02-13 | 15:42 | 49.904
2020-02-13 | 15:42 | 49.902
2020-02-13 | 15:42 | 49.902
2020-02-13 | 15:42 | 49.904
2020-02-13 | 15:42 | 49.905
2020-02-13 | 15:42 | 49.903
2020-02-13 | 15:42 | 49.905
2020-02-13 | 15:42 | 49.91
2020-02-13 | 15:42 | 49.913
2020-02-13 | 15:42 | 49.918
2020-02-13 | 15:42 | 49.926
2020-02-13 | 15:42 | 49.934
2020-02-13 | 15:42 | 49.943
2020-02-13 | 15:42 | 49.953
2020-02-13 | 15:42 | 49.962
2020-02-13 | 15:42 | 49.972
2020-02-13 | 15:42 | 49.979
2020-02-13 | 15:42 | 49.981
2020-02-13 | 15:42 | 49.983
2020-02-13 | 15:42 | 49.985
2020-02-13 | 15:42 | 49.985
2020-02-13 | 15:42 | 49.986
2020-02-13 | 15:42 | 49.987
2020-02-13 | 15:42 | 49.987
2020-02-13 | 15:42 | 49.985
2020-02-13 | 15:42 | 49.984
2020-02-13 | 15:42 | 49.983
2020-02-13 | 15:42 | 49.982
2020-02-13 | 15:42 | 49.982
2020-02-13 | 15:42 | 49.982
2020-02-13 | 15:43 | 49.979
2020-02-13 | 15:43 | 49.978
2020-02-13 | 15:43 | 49.977
2020-02-13 | 15:43 | 49.976
2020-02-13 | 15:43 | 49.976
2020-02-13 | 15:43 | 49.974
2020-02-13 | 15:43 | 49.974
2020-02-13 | 15:43 | 49.972
2020-02-13 | 15:43 | 49.971
2020-02-13 | 15:43 | 49.97
2020-02-13 | 15:43 | 49.973
2020-02-13 | 15:43 | 49.976
2020-02-13 | 15:43 | 49.978
2020-02-13 | 15:43 | 49.981
2020-02-13 | 15:43 | 49.981
2020-02-13 | 15:43 | 49.985
2020-02-13 | 15:43 | 49.986
2020-02-13 | 15:43 | 49.987
2020-02-13 | 15:43 | 49.987
2020-02-13 | 15:43 | 49.989
2020-02-13 | 15:43 | 49.992
2020-02-13 | 15:43 | 49.995
2020-02-13 | 15:43 | 49.998
2020-02-13 | 15:43 | 50
2020-02-13 | 15:43 | 50.002
2020-02-13 | 15:43 | 50.003
2020-02-13 | 15:43 | 50.001
2020-02-13 | 15:43 | 49.999
2020-02-13 | 15:43 | 49.998
2020-02-13 | 15:43 | 49.995
2020-02-13 | 15:43 | 49.996
2020-02-13 | 15:43 | 49.994
2020-02-13 | 15:43 | 49.991
2020-02-13 | 15:43 | 49.989
2020-02-13 | 15:43 | 49.989
2020-02-13 | 15:43 | 49.988
2020-02-13 | 15:43 | 49.985
2020-02-13 | 15:43 | 49.983
2020-02-13 | 15:43 | 49.986
2020-02-13 | 15:43 | 49.979
2020-02-13 | 15:43 | 49.976
2020-02-13 | 15:43 | 49.975
2020-02-13 | 15:43 | 49.975
2020-02-13 | 15:43 | 49.974
2020-02-13 | 15:43 | 49.973
2020-02-13 | 15:43 | 49.975
2020-02-13 | 15:43 | 49.975
2020-02-13 | 15:43 | 49.977
2020-02-13 | 15:43 | 49.98
2020-02-13 | 15:43 | 49.984
2020-02-13 | 15:43 | 49.985
2020-02-13 | 15:43 | 49.987
2020-02-13 | 15:43 | 49.99
2020-02-13 | 15:43 | 49.994
2020-02-13 | 15:43 | 49.997
2020-02-13 | 15:43 | 50.002
2020-02-13 | 15:43 | 50.005
2020-02-13 | 15:43 | 50.008
2020-02-13 | 15:43 | 50.013
2020-02-13 | 15:43 | 50.014
2020-02-13 | 15:43 | 50.014
2020-02-13 | 15:44 | 50.015
2020-02-13 | 15:44 | 50.011
2020-02-13 | 15:44 | 50.01
2020-02-13 | 15:44 | 50.01
2020-02-13 | 15:44 | 50.006
2020-02-13 | 15:44 | 50.005
2020-02-13 | 15:44 | 50.002
2020-02-13 | 15:44 | 49.999
2020-02-13 | 15:44 | 49.998
2020-02-13 | 15:44 | 49.995
2020-02-13 | 15:44 | 49.994
2020-02-13 | 15:44 | 49.994
2020-02-13 | 15:44 | 49.992
2020-02-13 | 15:44 | 49.994
2020-02-13 | 15:44 | 49.995
2020-02-13 | 15:44 | 49.995
2020-02-13 | 15:44 | 49.995
2020-02-13 | 15:44 | 49.997
2020-02-13 | 15:44 | 49.999
2020-02-13 | 15:44 | 49.999
2020-02-13 | 15:44 | 50
2020-02-13 | 15:44 | 50
2020-02-13 | 15:44 | 50.003
2020-02-13 | 15:44 | 50.003
2020-02-13 | 15:44 | 50.004
2020-02-13 | 15:44 | 50.007
2020-02-13 | 15:44 | 50.009
2020-02-13 | 15:44 | 50.011
2020-02-13 | 15:44 | 50.012
2020-02-13 | 15:44 | 50.013
2020-02-13 | 15:44 | 50.015
2020-02-13 | 15:44 | 50.017
2020-02-13 | 15:44 | 50.019
2020-02-13 | 15:44 | 50.021
2020-02-13 | 15:44 | 50.023
2020-02-13 | 15:44 | 50.025
2020-02-13 | 15:44 | 50.024
2020-02-13 | 15:44 | 50.023
2020-02-13 | 15:44 | 50.021
2020-02-13 | 15:44 | 50.018
2020-02-13 | 15:44 | 50.018
2020-02-13 | 15:44 | 50.018
2020-02-13 | 15:44 | 50.017
2020-02-13 | 15:44 | 50.016
2020-02-13 | 15:44 | 50.015
2020-02-13 | 15:44 | 50.016
2020-02-13 | 15:44 | 50.014
2020-02-13 | 15:44 | 50.014
2020-02-13 | 15:44 | 50.013
2020-02-13 | 15:44 | 50.011
2020-02-13 | 15:44 | 50.011
2020-02-13 | 15:44 | 50.01
2020-02-13 | 15:44 | 50.011
2020-02-13 | 15:44 | 50.011
2020-02-13 | 15:44 | 50.013
2020-02-13 | 15:44 | 50.014
2020-02-13 | 15:44 | 50.012
2020-02-13 | 15:44 | 50.015
2020-02-13 | 15:44 | 50.015
2020-02-13 | 15:45 | 50.017
2020-02-13 | 15:45 | 50.02
2020-02-13 | 15:45 | 50.019
2020-02-13 | 15:45 | 50.019
2020-02-13 | 15:45 | 50.015
2020-02-13 | 15:45 | 50.014
2020-02-13 | 15:45 | 50.013
2020-02-13 | 15:45 | 50.013
2020-02-13 | 15:45 | 50.015
2020-02-13 | 15:45 | 50.018
2020-02-13 | 15:45 | 50.02
2020-02-13 | 15:45 | 50.026
2020-02-13 | 15:45 | 50.027
2020-02-13 | 15:45 | 50.03
2020-02-13 | 15:45 | 50.03
2020-02-13 | 15:45 | 50.031
2020-02-13 | 15:45 | 50.032
2020-02-13 | 15:45 | 50.032
2020-02-13 | 15:45 | 50.032
2020-02-13 | 15:45 | 50.033
2020-02-13 | 15:45 | 50.032
2020-02-13 | 15:45 | 50.033
2020-02-13 | 15:45 | 50.035
2020-02-13 | 15:45 | 50.034
2020-02-13 | 15:45 | 50.036
2020-02-13 | 15:45 | 50.035
2020-02-13 | 15:45 | 50.035
2020-02-13 | 15:45 | 50.035
2020-02-13 | 15:45 | 50.033
2020-02-13 | 15:45 | 50.031
2020-02-13 | 15:45 | 50.03
2020-02-13 | 15:45 | 50.029
2020-02-13 | 15:45 | 50.031
2020-02-13 | 15:45 | 50.031
2020-02-13 | 15:45 | 50.03
2020-02-13 | 15:45 | 50.029
2020-02-13 | 15:45 | 50.027
2020-02-13 | 15:45 | 50.024
2020-02-13 | 15:45 | 50.023
2020-02-13 | 15:45 | 50.019
2020-02-13 | 15:45 | 50.015
2020-02-13 | 15:45 | 50.009
2020-02-13 | 15:45 | 50.004
2020-02-13 | 15:45 | 50.003
2020-02-13 | 15:45 | 50
2020-02-13 | 15:45 | 50
2020-02-13 | 15:45 | 49.997
2020-02-13 | 15:45 | 49.998
2020-02-13 | 15:45 | 49.999
2020-02-13 | 15:45 | 50.003
2020-02-13 | 15:45 | 50.004
2020-02-13 | 15:45 | 50.005
2020-02-13 | 15:45 | 50.005
2020-02-13 | 15:45 | 50.007
2020-02-13 | 15:45 | 50.008
2020-02-13 | 15:45 | 50.013
2020-02-13 | 15:45 | 50.016
2020-02-13 | 15:45 | 50.02
2020-02-13 | 15:45 | 50.023
2020-02-13 | 15:45 | 50.024
2020-02-13 | 15:45 | 50.026
2020-02-13 | 15:46 | 50.03
2020-02-13 | 15:46 | 50.032
2020-02-13 | 15:46 | 50.035
2020-02-13 | 15:46 | 50.034
2020-02-13 | 15:46 | 50.037
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.041
2020-02-13 | 15:46 | 50.045
2020-02-13 | 15:46 | 50.044
2020-02-13 | 15:46 | 50.046
2020-02-13 | 15:46 | 50.045
2020-02-13 | 15:46 | 50.044
2020-02-13 | 15:46 | 50.043
2020-02-13 | 15:46 | 50.042
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.04
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.038
2020-02-13 | 15:46 | 50.04
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.04
2020-02-13 | 15:46 | 50.041
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.042
2020-02-13 | 15:46 | 50.043
2020-02-13 | 15:46 | 50.046
2020-02-13 | 15:46 | 50.049
2020-02-13 | 15:46 | 50.049
2020-02-13 | 15:46 | 50.049
2020-02-13 | 15:46 | 50.05
2020-02-13 | 15:46 | 50.049
2020-02-13 | 15:46 | 50.047
2020-02-13 | 15:46 | 50.043
2020-02-13 | 15:46 | 50.041
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.038
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.039
2020-02-13 | 15:46 | 50.037
2020-02-13 | 15:46 | 50.035
2020-02-13 | 15:46 | 50.034
2020-02-13 | 15:46 | 50.033
2020-02-13 | 15:46 | 50.029
2020-02-13 | 15:46 | 50.026
2020-02-13 | 15:46 | 50.022
2020-02-13 | 15:46 | 50.02
2020-02-13 | 15:46 | 50.017
2020-02-13 | 15:46 | 50.016
2020-02-13 | 15:46 | 50.016
2020-02-13 | 15:46 | 50.018
2020-02-13 | 15:46 | 50.02
2020-02-13 | 15:46 | 50.023
2020-02-13 | 15:46 | 50.026
2020-02-13 | 15:46 | 50.027
2020-02-13 | 15:46 | 50.029
2020-02-13 | 15:46 | 50.03
2020-02-13 | 15:47 | 50.031
2020-02-13 | 15:47 | 50.03
2020-02-13 | 15:47 | 50.029
2020-02-13 | 15:47 | 50.025
2020-02-13 | 15:47 | 50.023
2020-02-13 | 15:47 | 50.024
2020-02-13 | 15:47 | 50.025
2020-02-13 | 15:47 | 50.025
2020-02-13 | 15:47 | 50.027
2020-02-13 | 15:47 | 50.029
2020-02-13 | 15:47 | 50.032
2020-02-13 | 15:47 | 50.036
2020-02-13 | 15:47 | 50.039
2020-02-13 | 15:47 | 50.042
2020-02-13 | 15:47 | 50.044
2020-02-13 | 15:47 | 50.045
2020-02-13 | 15:47 | 50.048
2020-02-13 | 15:47 | 50.048
2020-02-13 | 15:47 | 50.047
2020-02-13 | 15:47 | 50.046
2020-02-13 | 15:47 | 50.044
2020-02-13 | 15:47 | 50.04
2020-02-13 | 15:47 | 50.04
2020-02-13 | 15:47 | 50.04
2020-02-13 | 15:47 | 50.038
2020-02-13 | 15:47 | 50.035
2020-02-13 | 15:47 | 50.035
2020-02-13 | 15:47 | 50.032
2020-02-13 | 15:47 | 50.027
2020-02-13 | 15:47 | 50.022
2020-02-13 | 15:47 | 50.016
2020-02-13 | 15:47 | 50.012
2020-02-13 | 15:47 | 50.009
2020-02-13 | 15:47 | 50.006
2020-02-13 | 15:47 | 50.004
2020-02-13 | 15:47 | 50.002
2020-02-13 | 15:47 | 50
2020-02-13 | 15:47 | 49.997
2020-02-13 | 15:47 | 49.995
2020-02-13 | 15:47 | 49.99
2020-02-13 | 15:47 | 49.983
2020-02-13 | 15:47 | 49.979
2020-02-13 | 15:47 | 49.973
2020-02-13 | 15:47 | 49.967
2020-02-13 | 15:47 | 49.962
2020-02-13 | 15:47 | 49.96
2020-02-13 | 15:47 | 49.958
2020-02-13 | 15:47 | 49.957
2020-02-13 | 15:47 | 49.955
2020-02-13 | 15:47 | 49.956
2020-02-13 | 15:47 | 49.956
2020-02-13 | 15:47 | 49.958
2020-02-13 | 15:47 | 49.959
2020-02-13 | 15:47 | 49.959
2020-02-13 | 15:47 | 49.958
2020-02-13 | 15:47 | 49.959
2020-02-13 | 15:47 | 49.957
2020-02-13 | 15:47 | 49.956
2020-02-13 | 15:47 | 49.956
2020-02-13 | 15:47 | 49.958
2020-02-13 | 15:47 | 49.959
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.963
2020-02-13 | 15:48 | 49.965
2020-02-13 | 15:48 | 49.967
2020-02-13 | 15:48 | 49.968
2020-02-13 | 15:48 | 49.968
2020-02-13 | 15:48 | 49.971
2020-02-13 | 15:48 | 49.973
2020-02-13 | 15:48 | 49.975
2020-02-13 | 15:48 | 49.975
2020-02-13 | 15:48 | 49.975
2020-02-13 | 15:48 | 49.973
2020-02-13 | 15:48 | 49.971
2020-02-13 | 15:48 | 49.969
2020-02-13 | 15:48 | 49.967
2020-02-13 | 15:48 | 49.966
2020-02-13 | 15:48 | 49.964
2020-02-13 | 15:48 | 49.962
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.962
2020-02-13 | 15:48 | 49.963
2020-02-13 | 15:48 | 49.963
2020-02-13 | 15:48 | 49.963
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.96
2020-02-13 | 15:48 | 49.961
2020-02-13 | 15:48 | 49.958
2020-02-13 | 15:48 | 49.958
2020-02-13 | 15:48 | 49.957
2020-02-13 | 15:48 | 49.957
2020-02-13 | 15:48 | 49.954
2020-02-13 | 15:48 | 49.952
2020-02-13 | 15:48 | 49.949
2020-02-13 | 15:48 | 49.947
2020-02-13 | 15:48 | 49.944
2020-02-13 | 15:48 | 49.94
2020-02-13 | 15:48 | 49.937
2020-02-13 | 15:48 | 49.934
2020-02-13 | 15:48 | 49.932
2020-02-13 | 15:48 | 49.929
2020-02-13 | 15:48 | 49.932
2020-02-13 | 15:48 | 49.933
2020-02-13 | 15:48 | 49.936
2020-02-13 | 15:48 | 49.936
2020-02-13 | 15:48 | 49.936
2020-02-13 | 15:48 | 49.938
2020-02-13 | 15:48 | 49.939
2020-02-13 | 15:48 | 49.939
2020-02-13 | 15:48 | 49.94
2020-02-13 | 15:48 | 49.94
2020-02-13 | 15:48 | 49.94
2020-02-13 | 15:48 | 49.94
2020-02-13 | 15:48 | 49.94
2020-02-13 | 15:48 | 49.942
2020-02-13 | 15:48 | 49.943
2020-02-13 | 15:48 | 49.943
2020-02-13 | 15:49 | 49.942
2020-02-13 | 15:49 | 49.941
2020-02-13 | 15:49 | 49.941
2020-02-13 | 15:49 | 49.943
2020-02-13 | 15:49 | 49.942
2020-02-13 | 15:49 | 49.942
2020-02-13 | 15:49 | 49.939
2020-02-13 | 15:49 | 49.937
2020-02-13 | 15:49 | 49.935
2020-02-13 | 15:49 | 49.934
2020-02-13 | 15:49 | 49.934
2020-02-13 | 15:49 | 49.932
2020-02-13 | 15:49 | 49.93
2020-02-13 | 15:49 | 49.931
2020-02-13 | 15:49 | 49.933
2020-02-13 | 15:49 | 49.934
2020-02-13 | 15:49 | 49.936
2020-02-13 | 15:49 | 49.939
2020-02-13 | 15:49 | 49.944
2020-02-13 | 15:49 | 49.948
2020-02-13 | 15:49 | 49.95
2020-02-13 | 15:49 | 49.953
2020-02-13 | 15:49 | 49.956
2020-02-13 | 15:49 | 49.957
2020-02-13 | 15:49 | 49.958
2020-02-13 | 15:49 | 49.959
2020-02-13 | 15:49 | 49.96
2020-02-13 | 15:49 | 49.958
2020-02-13 | 15:49 | 49.955
2020-02-13 | 15:49 | 49.952
2020-02-13 | 15:49 | 49.944
2020-02-13 | 15:49 | 49.932
2020-02-13 | 15:49 | 49.92
2020-02-13 | 15:49 | 49.911
2020-02-13 | 15:49 | 49.898
2020-02-13 | 15:49 | 49.89
2020-02-13 | 15:49 | 49.885
2020-02-13 | 15:49 | 49.88
2020-02-13 | 15:49 | 49.88
2020-02-13 | 15:49 | 49.883
2020-02-13 | 15:49 | 49.885
2020-02-13 | 15:49 | 49.888
2020-02-13 | 15:49 | 49.892
2020-02-13 | 15:49 | 49.894
2020-02-13 | 15:49 | 49.9
2020-02-13 | 15:49 | 49.904
2020-02-13 | 15:49 | 49.906
2020-02-13 | 15:49 | 49.911
2020-02-13 | 15:49 | 49.915
2020-02-13 | 15:49 | 49.915
2020-02-13 | 15:49 | 49.918
2020-02-13 | 15:49 | 49.92
2020-02-13 | 15:49 | 49.917
2020-02-13 | 15:49 | 49.917
2020-02-13 | 15:49 | 49.917
2020-02-13 | 15:49 | 49.914
2020-02-13 | 15:49 | 49.912
2020-02-13 | 15:49 | 49.91
2020-02-13 | 15:49 | 49.907
2020-02-13 | 15:49 | 49.907
2020-02-13 | 15:49 | 49.905
2020-02-13 | 15:50 | 49.906
2020-02-13 | 15:50 | 49.906
2020-02-13 | 15:50 | 49.905
2020-02-13 | 15:50 | 49.904
2020-02-13 | 15:50 | 49.904
2020-02-13 | 15:50 | 49.908
2020-02-13 | 15:50 | 49.91
2020-02-13 | 15:50 | 49.911
2020-02-13 | 15:50 | 49.913
2020-02-13 | 15:50 | 49.915
2020-02-13 | 15:50 | 49.917
2020-02-13 | 15:50 | 49.921
2020-02-13 | 15:50 | 49.92
2020-02-13 | 15:50 | 49.923
2020-02-13 | 15:50 | 49.92
2020-02-13 | 15:50 | 49.914
2020-02-13 | 15:50 | 49.912
2020-02-13 | 15:50 | 49.901
2020-02-13 | 15:50 | 49.894
2020-02-13 | 15:50 | 49.88
2020-02-13 | 15:50 | 49.869
2020-02-13 | 15:50 | 49.857
2020-02-13 | 15:50 | 49.845
2020-02-13 | 15:50 | 49.839
2020-02-13 | 15:50 | 49.834
2020-02-13 | 15:50 | 49.831
2020-02-13 | 15:50 | 49.837
2020-02-13 | 15:50 | 49.841
2020-02-13 | 15:50 | 49.847
2020-02-13 | 15:50 | 49.849
2020-02-13 | 15:50 | 49.856
2020-02-13 | 15:50 | 49.866
2020-02-13 | 15:50 | 49.88
2020-02-13 | 15:50 | 49.891
2020-02-13 | 15:50 | 49.9
2020-02-13 | 15:50 | 49.905
2020-02-13 | 15:50 | 49.908
2020-02-13 | 15:50 | 49.909
2020-02-13 | 15:50 | 49.91
2020-02-13 | 15:50 | 49.908
2020-02-13 | 15:50 | 49.911
2020-02-13 | 15:50 | 49.91
2020-02-13 | 15:50 | 49.911
2020-02-13 | 15:50 | 49.91
2020-02-13 | 15:50 | 49.91
2020-02-13 | 15:50 | 49.909
2020-02-13 | 15:50 | 49.907
2020-02-13 | 15:50 | 49.909
2020-02-13 | 15:50 | 49.909
2020-02-13 | 15:50 | 49.91
2020-02-13 | 15:50 | 49.911
2020-02-13 | 15:50 | 49.913
2020-02-13 | 15:50 | 49.915
2020-02-13 | 15:50 | 49.92
2020-02-13 | 15:50 | 49.92
2020-02-13 | 15:50 | 49.924
2020-02-13 | 15:50 | 49.925
2020-02-13 | 15:50 | 49.925
2020-02-13 | 15:50 | 49.926
2020-02-13 | 15:51 | 49.924
2020-02-13 | 15:51 | 49.923
2020-02-13 | 15:51 | 49.924
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.923
2020-02-13 | 15:51 | 49.923
2020-02-13 | 15:51 | 49.922
2020-02-13 | 15:51 | 49.923
2020-02-13 | 15:51 | 49.92
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.919
2020-02-13 | 15:51 | 49.922
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.92
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.924
2020-02-13 | 15:51 | 49.924
2020-02-13 | 15:51 | 49.928
2020-02-13 | 15:51 | 49.928
2020-02-13 | 15:51 | 49.93
2020-02-13 | 15:51 | 49.932
2020-02-13 | 15:51 | 49.932
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.93
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.93
2020-02-13 | 15:51 | 49.929
2020-02-13 | 15:51 | 49.928
2020-02-13 | 15:51 | 49.926
2020-02-13 | 15:51 | 49.925
2020-02-13 | 15:51 | 49.921
2020-02-13 | 15:51 | 49.919
2020-02-13 | 15:51 | 49.916
2020-02-13 | 15:51 | 49.912
2020-02-13 | 15:51 | 49.91
2020-02-13 | 15:51 | 49.908
2020-02-13 | 15:51 | 49.906
2020-02-13 | 15:51 | 49.907
2020-02-13 | 15:51 | 49.904
2020-02-13 | 15:51 | 49.904
2020-02-13 | 15:51 | 49.902
2020-02-13 | 15:51 | 49.9
2020-02-13 | 15:51 | 49.901
2020-02-13 | 15:51 | 49.899
2020-02-13 | 15:51 | 49.901
2020-02-13 | 15:51 | 49.899
2020-02-13 | 15:51 | 49.898
2020-02-13 | 15:51 | 49.895
2020-02-13 | 15:51 | 49.893
2020-02-13 | 15:51 | 49.891
2020-02-13 | 15:51 | 49.889
2020-02-13 | 15:51 | 49.889
2020-02-13 | 15:52 | 49.889
2020-02-13 | 15:52 | 49.89
2020-02-13 | 15:52 | 49.89
2020-02-13 | 15:52 | 49.893
2020-02-13 | 15:52 | 49.895
2020-02-13 | 15:52 | 49.895
2020-02-13 | 15:52 | 49.9
2020-02-13 | 15:52 | 49.902
2020-02-13 | 15:52 | 49.908
2020-02-13 | 15:52 | 49.912
2020-02-13 | 15:52 | 49.916
2020-02-13 | 15:52 | 49.918
2020-02-13 | 15:52 | 49.921
2020-02-13 | 15:52 | 49.924
2020-02-13 | 15:52 | 49.926
2020-02-13 | 15:52 | 49.925
2020-02-13 | 15:52 | 49.927
2020-02-13 | 15:52 | 49.928
2020-02-13 | 15:52 | 49.927
2020-02-13 | 15:52 | 49.93
2020-02-13 | 15:52 | 49.931
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.936
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.937
2020-02-13 | 15:52 | 49.937
2020-02-13 | 15:52 | 49.937
2020-02-13 | 15:52 | 49.938
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.932
2020-02-13 | 15:52 | 49.933
2020-02-13 | 15:52 | 49.929
2020-02-13 | 15:52 | 49.932
2020-02-13 | 15:52 | 49.931
2020-02-13 | 15:52 | 49.932
2020-02-13 | 15:52 | 49.934
2020-02-13 | 15:52 | 49.934
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.934
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.934
2020-02-13 | 15:52 | 49.937
2020-02-13 | 15:52 | 49.939
2020-02-13 | 15:52 | 49.939
2020-02-13 | 15:52 | 49.943
2020-02-13 | 15:52 | 49.942
2020-02-13 | 15:52 | 49.945
2020-02-13 | 15:52 | 49.943
2020-02-13 | 15:52 | 49.945
2020-02-13 | 15:52 | 49.943
2020-02-13 | 15:52 | 49.944
2020-02-13 | 15:52 | 49.942
2020-02-13 | 15:52 | 49.941
2020-02-13 | 15:52 | 49.939
2020-02-13 | 15:52 | 49.939
2020-02-13 | 15:52 | 49.936
2020-02-13 | 15:52 | 49.936
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.935
2020-02-13 | 15:52 | 49.934
2020-02-13 | 15:53 | 49.935
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.934
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.932
2020-02-13 | 15:53 | 49.93
2020-02-13 | 15:53 | 49.929
2020-02-13 | 15:53 | 49.928
2020-02-13 | 15:53 | 49.927
2020-02-13 | 15:53 | 49.925
2020-02-13 | 15:53 | 49.926
2020-02-13 | 15:53 | 49.926
2020-02-13 | 15:53 | 49.93
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.94
2020-02-13 | 15:53 | 49.943
2020-02-13 | 15:53 | 49.95
2020-02-13 | 15:53 | 49.952
2020-02-13 | 15:53 | 49.957
2020-02-13 | 15:53 | 49.956
2020-02-13 | 15:53 | 49.956
2020-02-13 | 15:53 | 49.952
2020-02-13 | 15:53 | 49.952
2020-02-13 | 15:53 | 49.946
2020-02-13 | 15:53 | 49.945
2020-02-13 | 15:53 | 49.938
2020-02-13 | 15:53 | 49.936
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.931
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.932
2020-02-13 | 15:53 | 49.933
2020-02-13 | 15:53 | 49.931
2020-02-13 | 15:53 | 49.929
2020-02-13 | 15:53 | 49.929
2020-02-13 | 15:53 | 49.926
2020-02-13 | 15:53 | 49.925
2020-02-13 | 15:53 | 49.92
2020-02-13 | 15:53 | 49.92
2020-02-13 | 15:53 | 49.917
2020-02-13 | 15:53 | 49.916
2020-02-13 | 15:53 | 49.916
2020-02-13 | 15:53 | 49.917
2020-02-13 | 15:53 | 49.915
2020-02-13 | 15:53 | 49.915
2020-02-13 | 15:53 | 49.914
2020-02-13 | 15:53 | 49.914
2020-02-13 | 15:53 | 49.914
2020-02-13 | 15:53 | 49.911
2020-02-13 | 15:53 | 49.91
2020-02-13 | 15:53 | 49.909
2020-02-13 | 15:53 | 49.91
2020-02-13 | 15:53 | 49.91
2020-02-13 | 15:53 | 49.908
2020-02-13 | 15:53 | 49.911
2020-02-13 | 15:53 | 49.911
2020-02-13 | 15:53 | 49.915
2020-02-13 | 15:54 | 49.919
2020-02-13 | 15:54 | 49.921
2020-02-13 | 15:54 | 49.923
2020-02-13 | 15:54 | 49.923
2020-02-13 | 15:54 | 49.925
2020-02-13 | 15:54 | 49.923
2020-02-13 | 15:54 | 49.925
2020-02-13 | 15:54 | 49.923
2020-02-13 | 15:54 | 49.922
2020-02-13 | 15:54 | 49.924
2020-02-13 | 15:54 | 49.922
2020-02-13 | 15:54 | 49.926
2020-02-13 | 15:54 | 49.926
2020-02-13 | 15:54 | 49.928
2020-02-13 | 15:54 | 49.928
2020-02-13 | 15:54 | 49.926
2020-02-13 | 15:54 | 49.929
2020-02-13 | 15:54 | 49.926
2020-02-13 | 15:54 | 49.925
2020-02-13 | 15:54 | 49.927
2020-02-13 | 15:54 | 49.927
2020-02-13 | 15:54 | 49.929
2020-02-13 | 15:54 | 49.928
2020-02-13 | 15:54 | 49.929
2020-02-13 | 15:54 | 49.929
2020-02-13 | 15:54 | 49.928
2020-02-13 | 15:54 | 49.927
2020-02-13 | 15:54 | 49.925
2020-02-13 | 15:54 | 49.924
2020-02-13 | 15:54 | 49.921
2020-02-13 | 15:54 | 49.92
2020-02-13 | 15:54 | 49.919
2020-02-13 | 15:54 | 49.918
2020-02-13 | 15:54 | 49.916
2020-02-13 | 15:54 | 49.914
2020-02-13 | 15:54 | 49.914
2020-02-13 | 15:54 | 49.914
2020-02-13 | 15:54 | 49.915
2020-02-13 | 15:54 | 49.916
2020-02-13 | 15:54 | 49.916
2020-02-13 | 15:54 | 49.917
2020-02-13 | 15:54 | 49.916
2020-02-13 | 15:54 | 49.919
2020-02-13 | 15:54 | 49.92
2020-02-13 | 15:54 | 49.921
2020-02-13 | 15:54 | 49.923
2020-02-13 | 15:54 | 49.921
2020-02-13 | 15:54 | 49.923
2020-02-13 | 15:54 | 49.924
2020-02-13 | 15:54 | 49.925
2020-02-13 | 15:54 | 49.928
2020-02-13 | 15:54 | 49.928
2020-02-13 | 15:54 | 49.929
2020-02-13 | 15:54 | 49.93
2020-02-13 | 15:54 | 49.93
2020-02-13 | 15:54 | 49.933
2020-02-13 | 15:54 | 49.934
2020-02-13 | 15:54 | 49.935
2020-02-13 | 15:54 | 49.936
2020-02-13 | 15:54 | 49.935
2020-02-13 | 15:54 | 49.934
2020-02-13 | 15:55 | 49.934
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.928
2020-02-13 | 15:55 | 49.924
2020-02-13 | 15:55 | 49.924
2020-02-13 | 15:55 | 49.922
2020-02-13 | 15:55 | 49.922
2020-02-13 | 15:55 | 49.921
2020-02-13 | 15:55 | 49.92
2020-02-13 | 15:55 | 49.922
2020-02-13 | 15:55 | 49.923
2020-02-13 | 15:55 | 49.922
2020-02-13 | 15:55 | 49.924
2020-02-13 | 15:55 | 49.924
2020-02-13 | 15:55 | 49.927
2020-02-13 | 15:55 | 49.931
2020-02-13 | 15:55 | 49.934
2020-02-13 | 15:55 | 49.939
2020-02-13 | 15:55 | 49.944
2020-02-13 | 15:55 | 49.948
2020-02-13 | 15:55 | 49.956
2020-02-13 | 15:55 | 49.958
2020-02-13 | 15:55 | 49.96
2020-02-13 | 15:55 | 49.962
2020-02-13 | 15:55 | 49.961
2020-02-13 | 15:55 | 49.962
2020-02-13 | 15:55 | 49.961
2020-02-13 | 15:55 | 49.959
2020-02-13 | 15:55 | 49.96
2020-02-13 | 15:55 | 49.958
2020-02-13 | 15:55 | 49.957
2020-02-13 | 15:55 | 49.955
2020-02-13 | 15:55 | 49.952
2020-02-13 | 15:55 | 49.951
2020-02-13 | 15:55 | 49.947
2020-02-13 | 15:55 | 49.942
2020-02-13 | 15:55 | 49.939
2020-02-13 | 15:55 | 49.935
2020-02-13 | 15:55 | 49.932
2020-02-13 | 15:55 | 49.929
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.931
2020-02-13 | 15:55 | 49.931
2020-02-13 | 15:55 | 49.931
2020-02-13 | 15:55 | 49.931
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.928
2020-02-13 | 15:55 | 49.927
2020-02-13 | 15:55 | 49.928
2020-02-13 | 15:55 | 49.928
2020-02-13 | 15:55 | 49.929
2020-02-13 | 15:55 | 49.931
2020-02-13 | 15:55 | 49.929
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.93
2020-02-13 | 15:55 | 49.932
2020-02-13 | 15:55 | 49.934
2020-02-13 | 15:56 | 49.937
2020-02-13 | 15:56 | 49.941
2020-02-13 | 15:56 | 49.945
2020-02-13 | 15:56 | 49.949
2020-02-13 | 15:56 | 49.953
2020-02-13 | 15:56 | 49.953
2020-02-13 | 15:56 | 49.955
2020-02-13 | 15:56 | 49.954
2020-02-13 | 15:56 | 49.952
2020-02-13 | 15:56 | 49.955
2020-02-13 | 15:56 | 49.955
2020-02-13 | 15:56 | 49.958
2020-02-13 | 15:56 | 49.959
2020-02-13 | 15:56 | 49.957
2020-02-13 | 15:56 | 49.956
2020-02-13 | 15:56 | 49.957
2020-02-13 | 15:56 | 49.954
2020-02-13 | 15:56 | 49.95
2020-02-13 | 15:56 | 49.949
2020-02-13 | 15:56 | 49.948
2020-02-13 | 15:56 | 49.947
2020-02-13 | 15:56 | 49.945
2020-02-13 | 15:56 | 49.943
2020-02-13 | 15:56 | 49.939
2020-02-13 | 15:56 | 49.939
2020-02-13 | 15:56 | 49.939
2020-02-13 | 15:56 | 49.938
2020-02-13 | 15:56 | 49.939
2020-02-13 | 15:56 | 49.94
2020-02-13 | 15:56 | 49.941
2020-02-13 | 15:56 | 49.941
2020-02-13 | 15:56 | 49.942
2020-02-13 | 15:56 | 49.944
2020-02-13 | 15:56 | 49.946
2020-02-13 | 15:56 | 49.949
2020-02-13 | 15:56 | 49.954
2020-02-13 | 15:56 | 49.954
2020-02-13 | 15:56 | 49.956
2020-02-13 | 15:56 | 49.958
2020-02-13 | 15:56 | 49.961
2020-02-13 | 15:56 | 49.96
2020-02-13 | 15:56 | 49.963
2020-02-13 | 15:56 | 49.964
2020-02-13 | 15:56 | 49.964
2020-02-13 | 15:56 | 49.964
2020-02-13 | 15:56 | 49.964
2020-02-13 | 15:56 | 49.963
2020-02-13 | 15:56 | 49.963
2020-02-13 | 15:56 | 49.963
2020-02-13 | 15:56 | 49.965
2020-02-13 | 15:56 | 49.967
2020-02-13 | 15:56 | 49.966
2020-02-13 | 15:56 | 49.967
2020-02-13 | 15:56 | 49.968
2020-02-13 | 15:56 | 49.97
2020-02-13 | 15:56 | 49.972
2020-02-13 | 15:56 | 49.972
2020-02-13 | 15:56 | 49.972
2020-02-13 | 15:56 | 49.972
2020-02-13 | 15:56 | 49.973
2020-02-13 | 15:56 | 49.971
2020-02-13 | 15:57 | 49.971
2020-02-13 | 15:57 | 49.971
2020-02-13 | 15:57 | 49.97
2020-02-13 | 15:57 | 49.971
2020-02-13 | 15:57 | 49.972
2020-02-13 | 15:57 | 49.973
2020-02-13 | 15:57 | 49.974
2020-02-13 | 15:57 | 49.974
2020-02-13 | 15:57 | 49.973
2020-02-13 | 15:57 | 49.974
2020-02-13 | 15:57 | 49.973
2020-02-13 | 15:57 | 49.974
2020-02-13 | 15:57 | 49.974
2020-02-13 | 15:57 | 49.976
2020-02-13 | 15:57 | 49.975
2020-02-13 | 15:57 | 49.976
2020-02-13 | 15:57 | 49.977
2020-02-13 | 15:57 | 49.977
2020-02-13 | 15:57 | 49.979
2020-02-13 | 15:57 | 49.981
2020-02-13 | 15:57 | 49.983
2020-02-13 | 15:57 | 49.987
2020-02-13 | 15:57 | 49.992
2020-02-13 | 15:57 | 49.994
2020-02-13 | 15:57 | 49.997
2020-02-13 | 15:57 | 49.998
2020-02-13 | 15:57 | 49.998
2020-02-13 | 15:57 | 49.998
2020-02-13 | 15:57 | 49.999
2020-02-13 | 15:57 | 49.997
2020-02-13 | 15:57 | 49.996
2020-02-13 | 15:57 | 49.997
2020-02-13 | 15:57 | 49.997
2020-02-13 | 15:57 | 49.996
2020-02-13 | 15:57 | 49.993
2020-02-13 | 15:57 | 49.991
2020-02-13 | 15:57 | 49.989
2020-02-13 | 15:57 | 49.986
2020-02-13 | 15:57 | 49.982
2020-02-13 | 15:57 | 49.98
2020-02-13 | 15:57 | 49.976
2020-02-13 | 15:57 | 49.977
2020-02-13 | 15:57 | 49.976
2020-02-13 | 15:57 | 49.977
2020-02-13 | 15:57 | 49.979
2020-02-13 | 15:57 | 49.982
2020-02-13 | 15:57 | 49.986
2020-02-13 | 15:57 | 49.988
2020-02-13 | 15:57 | 49.99
2020-02-13 | 15:57 | 49.993
2020-02-13 | 15:57 | 49.994
2020-02-13 | 15:57 | 49.997
2020-02-13 | 15:57 | 50
2020-02-13 | 15:57 | 50.002
2020-02-13 | 15:57 | 50.006
2020-02-13 | 15:57 | 50.011
2020-02-13 | 15:57 | 50.015
2020-02-13 | 15:57 | 50.017
2020-02-13 | 15:57 | 50.016
2020-02-13 | 15:58 | 50.016
2020-02-13 | 15:58 | 50.014
2020-02-13 | 15:58 | 50.014
2020-02-13 | 15:58 | 50.012
2020-02-13 | 15:58 | 50.013
2020-02-13 | 15:58 | 50.012
2020-02-13 | 15:58 | 50.012
2020-02-13 | 15:58 | 50.011
2020-02-13 | 15:58 | 50.012
2020-02-13 | 15:58 | 50.011
2020-02-13 | 15:58 | 50.012
2020-02-13 | 15:58 | 50.014
2020-02-13 | 15:58 | 50.017
2020-02-13 | 15:58 | 50.017
2020-02-13 | 15:58 | 50.017
2020-02-13 | 15:58 | 50.018
2020-02-13 | 15:58 | 50.018
2020-02-13 | 15:58 | 50.021
2020-02-13 | 15:58 | 50.023
2020-02-13 | 15:58 | 50.027
2020-02-13 | 15:58 | 50.03
2020-02-13 | 15:58 | 50.031
2020-02-13 | 15:58 | 50.03
2020-02-13 | 15:58 | 50.028
2020-02-13 | 15:58 | 50.025
2020-02-13 | 15:58 | 50.019
2020-02-13 | 15:58 | 50.015
2020-02-13 | 15:58 | 50.01
2020-02-13 | 15:58 | 50.009
2020-02-13 | 15:58 | 50.007
2020-02-13 | 15:58 | 50.004
2020-02-13 | 15:58 | 50.004
2020-02-13 | 15:58 | 50.001
2020-02-13 | 15:58 | 50
2020-02-13 | 15:58 | 49.997
2020-02-13 | 15:58 | 49.997
2020-02-13 | 15:58 | 49.996
2020-02-13 | 15:58 | 49.995
2020-02-13 | 15:58 | 49.995
2020-02-13 | 15:58 | 49.999
2020-02-13 | 15:58 | 50.004
2020-02-13 | 15:58 | 50.008
2020-02-13 | 15:58 | 50.014
2020-02-13 | 15:58 | 50.022
2020-02-13 | 15:58 | 50.026
2020-02-13 | 15:58 | 50.03
2020-02-13 | 15:58 | 50.031
2020-02-13 | 15:58 | 50.034
2020-02-13 | 15:58 | 50.033
2020-02-13 | 15:58 | 50.031
2020-02-13 | 15:58 | 50.03
2020-02-13 | 15:58 | 50.028
2020-02-13 | 15:58 | 50.024
2020-02-13 | 15:58 | 50.021
2020-02-13 | 15:58 | 50.016
2020-02-13 | 15:58 | 50.012
2020-02-13 | 15:58 | 50.009
2020-02-13 | 15:58 | 50.004
2020-02-13 | 15:58 | 50.001
2020-02-13 | 15:58 | 49.996
2020-02-13 | 15:58 | 49.992
2020-02-13 | 15:59 | 49.988
2020-02-13 | 15:59 | 49.982
2020-02-13 | 15:59 | 49.977
2020-02-13 | 15:59 | 49.974
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.971
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.971
2020-02-13 | 15:59 | 49.972
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.967
2020-02-13 | 15:59 | 49.968
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.968
2020-02-13 | 15:59 | 49.967
2020-02-13 | 15:59 | 49.966
2020-02-13 | 15:59 | 49.965
2020-02-13 | 15:59 | 49.965
2020-02-13 | 15:59 | 49.965
2020-02-13 | 15:59 | 49.966
2020-02-13 | 15:59 | 49.965
2020-02-13 | 15:59 | 49.966
2020-02-13 | 15:59 | 49.967
2020-02-13 | 15:59 | 49.967
2020-02-13 | 15:59 | 49.967
2020-02-13 | 15:59 | 49.966
2020-02-13 | 15:59 | 49.966
2020-02-13 | 15:59 | 49.966
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.972
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.969
2020-02-13 | 15:59 | 49.968
2020-02-13 | 15:59 | 49.968
2020-02-13 | 15:59 | 49.967
2020-02-13 | 15:59 | 49.968
2020-02-13 | 15:59 | 49.97
2020-02-13 | 15:59 | 49.972
2020-02-13 | 15:59 | 49.975
2020-02-13 | 15:59 | 49.976
2020-02-13 | 15:59 | 49.977
2020-02-13 | 15:59 | 49.977
2020-02-13 | 15:59 | 49.978
2020-02-13 | 15:59 | 49.978
2020-02-13 | 15:59 | 49.979
2020-02-13 | 16:00 | 49.978
2020-02-13 | 16:00 | 49.978
2020-02-13 | 16:00 | 49.977
2020-02-13 | 16:00 | 49.975
2020-02-13 | 16:00 | 49.977
2020-02-13 | 16:00 | 49.979
2020-02-13 | 16:00 | 49.98
2020-02-13 | 16:00 | 49.984
2020-02-13 | 16:00 | 49.987
2020-02-13 | 16:00 | 49.991
2020-02-13 | 16:00 | 49.993
2020-02-13 | 16:00 | 49.995
2020-02-13 | 16:00 | 49.996
2020-02-13 | 16:00 | 49.997
2020-02-13 | 16:00 | 50
2020-02-13 | 16:00 | 50.003
2020-02-13 | 16:00 | 50.005
2020-02-13 | 16:00 | 50.007
2020-02-13 | 16:00 | 50.011
2020-02-13 | 16:00 | 50.012
2020-02-13 | 16:00 | 50.013
2020-02-13 | 16:00 | 50.016
2020-02-13 | 16:00 | 50.018
2020-02-13 | 16:00 | 50.02
2020-02-13 | 16:00 | 50.021
2020-02-13 | 16:00 | 50.02
2020-02-13 | 16:00 | 50.02
2020-02-13 | 16:00 | 50.017
2020-02-13 | 16:00 | 50.017
2020-02-13 | 16:00 | 50.015
2020-02-13 | 16:00 | 50.012
2020-02-13 | 16:00 | 50.008
2020-02-13 | 16:00 | 50.005
2020-02-13 | 16:00 | 50.004
2020-02-13 | 16:00 | 50.003
2020-02-13 | 16:00 | 50
2020-02-13 | 16:00 | 49.998
2020-02-13 | 16:00 | 49.997
2020-02-13 | 16:00 | 49.996
2020-02-13 | 16:00 | 49.996
2020-02-13 | 16:00 | 49.997
2020-02-13 | 16:00 | 49.998
2020-02-13 | 16:00 | 49.997
2020-02-13 | 16:00 | 49.998
2020-02-13 | 16:00 | 49.999
2020-02-13 | 16:00 | 49.999
2020-02-13 | 16:00 | 50
2020-02-13 | 16:00 | 50.001
2020-02-13 | 16:00 | 50.001
2020-02-13 | 16:00 | 50.004
2020-02-13 | 16:00 | 50.004
2020-02-13 | 16:00 | 50.004
2020-02-13 | 16:00 | 50.005
2020-02-13 | 16:00 | 50.005
2020-02-13 | 16:00 | 50.003
2020-02-13 | 16:00 | 50
2020-02-13 | 16:00 | 49.997
2020-02-13 | 16:00 | 49.993
2020-02-13 | 16:00 | 49.99
2020-02-13 | 16:00 | 49.986
2020-02-13 | 16:00 | 49.983
2020-02-13 | 16:01 | 49.983
2020-02-13 | 16:01 | 49.984
2020-02-13 | 16:01 | 49.982
2020-02-13 | 16:01 | 49.983
2020-02-13 | 16:01 | 49.98
2020-02-13 | 16:01 | 49.978
2020-02-13 | 16:01 | 49.976
2020-02-13 | 16:01 | 49.975
2020-02-13 | 16:01 | 49.973
2020-02-13 | 16:01 | 49.971
2020-02-13 | 16:01 | 49.971
2020-02-13 | 16:01 | 49.969
2020-02-13 | 16:01 | 49.97
2020-02-13 | 16:01 | 49.97
2020-02-13 | 16:01 | 49.971
2020-02-13 | 16:01 | 49.971
2020-02-13 | 16:01 | 49.974
2020-02-13 | 16:01 | 49.978
2020-02-13 | 16:01 | 49.979
2020-02-13 | 16:01 | 49.982
2020-02-13 | 16:01 | 49.986
2020-02-13 | 16:01 | 49.987
2020-02-13 | 16:01 | 49.992
2020-02-13 | 16:01 | 49.998
2020-02-13 | 16:01 | 50.003
2020-02-13 | 16:01 | 50.009
2020-02-13 | 16:01 | 50.012
2020-02-13 | 16:01 | 50.016
2020-02-13 | 16:01 | 50.018
2020-02-13 | 16:01 | 50.02
2020-02-13 | 16:01 | 50.021
2020-02-13 | 16:01 | 50.021
2020-02-13 | 16:01 | 50.021
2020-02-13 | 16:01 | 50.021
2020-02-13 | 16:01 | 50.021
2020-02-13 | 16:01 | 50.02
2020-02-13 | 16:01 | 50.02
2020-02-13 | 16:01 | 50.02
2020-02-13 | 16:01 | 50.019
2020-02-13 | 16:01 | 50.019
2020-02-13 | 16:01 | 50.018
2020-02-13 | 16:01 | 50.018
2020-02-13 | 16:01 | 50.019
2020-02-13 | 16:01 | 50.018
2020-02-13 | 16:01 | 50.017
2020-02-13 | 16:01 | 50.016
2020-02-13 | 16:01 | 50.015
2020-02-13 | 16:01 | 50.015
2020-02-13 | 16:01 | 50.012
2020-02-13 | 16:01 | 50.012
2020-02-13 | 16:01 | 50.011
2020-02-13 | 16:01 | 50.011
2020-02-13 | 16:01 | 50.009
2020-02-13 | 16:01 | 50.009
2020-02-13 | 16:01 | 50.01
2020-02-13 | 16:01 | 50.009
2020-02-13 | 16:01 | 50.011
2020-02-13 | 16:01 | 50.011
2020-02-13 | 16:01 | 50.01
2020-02-13 | 16:01 | 50.008
2020-02-13 | 16:02 | 50.007
2020-02-13 | 16:02 | 50.003
2020-02-13 | 16:02 | 49.999
2020-02-13 | 16:02 | 49.994
2020-02-13 | 16:02 | 49.99
2020-02-13 | 16:02 | 49.986
2020-02-13 | 16:02 | 49.981
2020-02-13 | 16:02 | 49.978
2020-02-13 | 16:02 | 49.974
2020-02-13 | 16:02 | 49.973
2020-02-13 | 16:02 | 49.972
2020-02-13 | 16:02 | 49.971
2020-02-13 | 16:02 | 49.972
2020-02-13 | 16:02 | 49.972
2020-02-13 | 16:02 | 49.973
2020-02-13 | 16:02 | 49.975
2020-02-13 | 16:02 | 49.974
2020-02-13 | 16:02 | 49.977
2020-02-13 | 16:02 | 49.976
2020-02-13 | 16:02 | 49.976
2020-02-13 | 16:02 | 49.976
2020-02-13 | 16:02 | 49.977
2020-02-13 | 16:02 | 49.975
2020-02-13 | 16:02 | 49.973
2020-02-13 | 16:02 | 49.971
2020-02-13 | 16:02 | 49.969
2020-02-13 | 16:02 | 49.967
2020-02-13 | 16:02 | 49.965
2020-02-13 | 16:02 | 49.962
2020-02-13 | 16:02 | 49.958
2020-02-13 | 16:02 | 49.953
2020-02-13 | 16:02 | 49.951
2020-02-13 | 16:02 | 49.948
2020-02-13 | 16:02 | 49.944
2020-02-13 | 16:02 | 49.942
2020-02-13 | 16:02 | 49.941
2020-02-13 | 16:02 | 49.941
2020-02-13 | 16:02 | 49.941
2020-02-13 | 16:02 | 49.94
2020-02-13 | 16:02 | 49.939
2020-02-13 | 16:02 | 49.939
2020-02-13 | 16:02 | 49.939
2020-02-13 | 16:02 | 49.939
2020-02-13 | 16:02 | 49.94
2020-02-13 | 16:02 | 49.941
2020-02-13 | 16:02 | 49.942
2020-02-13 | 16:02 | 49.942
2020-02-13 | 16:02 | 49.942
2020-02-13 | 16:02 | 49.942
2020-02-13 | 16:02 | 49.942
2020-02-13 | 16:02 | 49.944
2020-02-13 | 16:02 | 49.947
2020-02-13 | 16:02 | 49.949
2020-02-13 | 16:02 | 49.953
2020-02-13 | 16:02 | 49.959
2020-02-13 | 16:02 | 49.965
2020-02-13 | 16:02 | 49.97
2020-02-13 | 16:02 | 49.976
2020-02-13 | 16:02 | 49.976
2020-02-13 | 16:02 | 49.98
2020-02-13 | 16:03 | 49.983
2020-02-13 | 16:03 | 49.985
2020-02-13 | 16:03 | 49.985
2020-02-13 | 16:03 | 49.984
2020-02-13 | 16:03 | 49.985
2020-02-13 | 16:03 | 49.985
2020-02-13 | 16:03 | 49.987
2020-02-13 | 16:03 | 49.988
2020-02-13 | 16:03 | 49.989
2020-02-13 | 16:03 | 49.99
2020-02-13 | 16:03 | 49.991
2020-02-13 | 16:03 | 49.993
2020-02-13 | 16:03 | 49.99
2020-02-13 | 16:03 | 49.989
2020-02-13 | 16:03 | 49.987
2020-02-13 | 16:03 | 49.986
2020-02-13 | 16:03 | 49.984
2020-02-13 | 16:03 | 49.983
2020-02-13 | 16:03 | 49.981
2020-02-13 | 16:03 | 49.979
2020-02-13 | 16:03 | 49.976
2020-02-13 | 16:03 | 49.974
2020-02-13 | 16:03 | 49.973
2020-02-13 | 16:03 | 49.972
2020-02-13 | 16:03 | 49.969
2020-02-13 | 16:03 | 49.967
2020-02-13 | 16:03 | 49.966
2020-02-13 | 16:03 | 49.964
2020-02-13 | 16:03 | 49.964
2020-02-13 | 16:03 | 49.96
2020-02-13 | 16:03 | 49.961
2020-02-13 | 16:03 | 49.962
2020-02-13 | 16:03 | 49.962
2020-02-13 | 16:03 | 49.963
2020-02-13 | 16:03 | 49.963
2020-02-13 | 16:03 | 49.964
2020-02-13 | 16:03 | 49.965
2020-02-13 | 16:03 | 49.964
2020-02-13 | 16:03 | 49.963
2020-02-13 | 16:03 | 49.964
2020-02-13 | 16:03 | 49.964
2020-02-13 | 16:03 | 49.962
2020-02-13 | 16:03 | 49.961
2020-02-13 | 16:03 | 49.96
2020-02-13 | 16:03 | 49.959
2020-02-13 | 16:03 | 49.956
2020-02-13 | 16:03 | 49.955
2020-02-13 | 16:03 | 49.953
2020-02-13 | 16:03 | 49.953
2020-02-13 | 16:03 | 49.951
2020-02-13 | 16:03 | 49.95
2020-02-13 | 16:03 | 49.95
2020-02-13 | 16:03 | 49.949
2020-02-13 | 16:03 | 49.948
2020-02-13 | 16:03 | 49.947
2020-02-13 | 16:03 | 49.946
2020-02-13 | 16:03 | 49.945
2020-02-13 | 16:03 | 49.946
2020-02-13 | 16:03 | 49.945
2020-02-13 | 16:04 | 49.947
2020-02-13 | 16:04 | 49.946
2020-02-13 | 16:04 | 49.946
2020-02-13 | 16:04 | 49.944
2020-02-13 | 16:04 | 49.945
2020-02-13 | 16:04 | 49.943
2020-02-13 | 16:04 | 49.943
2020-02-13 | 16:04 | 49.943
2020-02-13 | 16:04 | 49.944
2020-02-13 | 16:04 | 49.947
2020-02-13 | 16:04 | 49.949
2020-02-13 | 16:04 | 49.951
2020-02-13 | 16:04 | 49.954
2020-02-13 | 16:04 | 49.954
2020-02-13 | 16:04 | 49.955
2020-02-13 | 16:04 | 49.958
2020-02-13 | 16:04 | 49.96
2020-02-13 | 16:04 | 49.965
2020-02-13 | 16:04 | 49.969
2020-02-13 | 16:04 | 49.972
2020-02-13 | 16:04 | 49.978
2020-02-13 | 16:04 | 49.981
2020-02-13 | 16:04 | 49.98
2020-02-13 | 16:04 | 49.979
2020-02-13 | 16:04 | 49.977
2020-02-13 | 16:04 | 49.974
2020-02-13 | 16:04 | 49.973
2020-02-13 | 16:04 | 49.969
2020-02-13 | 16:04 | 49.969
2020-02-13 | 16:04 | 49.968
2020-02-13 | 16:04 | 49.97
2020-02-13 | 16:04 | 49.969
2020-02-13 | 16:04 | 49.971
2020-02-13 | 16:04 | 49.971
2020-02-13 | 16:04 | 49.972
2020-02-13 | 16:04 | 49.973
2020-02-13 | 16:04 | 49.973
2020-02-13 | 16:04 | 49.971
2020-02-13 | 16:04 | 49.969
2020-02-13 | 16:04 | 49.966
2020-02-13 | 16:04 | 49.964
2020-02-13 | 16:04 | 49.962
2020-02-13 | 16:04 | 49.962
2020-02-13 | 16:04 | 49.961
2020-02-13 | 16:04 | 49.961
2020-02-13 | 16:04 | 49.96
2020-02-13 | 16:04 | 49.958
2020-02-13 | 16:04 | 49.956
2020-02-13 | 16:04 | 49.955
2020-02-13 | 16:04 | 49.953
2020-02-13 | 16:04 | 49.949
2020-02-13 | 16:04 | 49.946
2020-02-13 | 16:04 | 49.942
2020-02-13 | 16:04 | 49.937
2020-02-13 | 16:04 | 49.935
2020-02-13 | 16:04 | 49.932
2020-02-13 | 16:04 | 49.932
2020-02-13 | 16:04 | 49.932
2020-02-13 | 16:04 | 49.934
2020-02-13 | 16:04 | 49.936
2020-02-13 | 16:04 | 49.938
2020-02-13 | 16:05 | 49.94
2020-02-13 | 16:05 | 49.943
2020-02-13 | 16:05 | 49.946
2020-02-13 | 16:05 | 49.947
2020-02-13 | 16:05 | 49.951
2020-02-13 | 16:05 | 49.951
2020-02-13 | 16:05 | 49.954
2020-02-13 | 16:05 | 49.958
2020-02-13 | 16:05 | 49.959
2020-02-13 | 16:05 | 49.963
2020-02-13 | 16:05 | 49.965
2020-02-13 | 16:05 | 49.972
2020-02-13 | 16:05 | 49.977
2020-02-13 | 16:05 | 49.983
2020-02-13 | 16:05 | 49.984
2020-02-13 | 16:05 | 49.989
2020-02-13 | 16:05 | 49.99
2020-02-13 | 16:05 | 49.991
2020-02-13 | 16:05 | 49.991
2020-02-13 | 16:05 | 49.992
2020-02-13 | 16:05 | 49.992
2020-02-13 | 16:05 | 49.992
2020-02-13 | 16:05 | 49.992
2020-02-13 | 16:05 | 49.994
2020-02-13 | 16:05 | 49.995
2020-02-13 | 16:05 | 49.994
2020-02-13 | 16:05 | 49.994
2020-02-13 | 16:05 | 49.995
2020-02-13 | 16:05 | 49.994
2020-02-13 | 16:05 | 49.992
2020-02-13 | 16:05 | 49.991
2020-02-13 | 16:05 | 49.989
2020-02-13 | 16:05 | 49.987
2020-02-13 | 16:05 | 49.987
2020-02-13 | 16:05 | 49.985
2020-02-13 | 16:05 | 49.983
2020-02-13 | 16:05 | 49.981
2020-02-13 | 16:05 | 49.98
2020-02-13 | 16:05 | 49.977
2020-02-13 | 16:05 | 49.973
2020-02-13 | 16:05 | 49.97
2020-02-13 | 16:05 | 49.967
2020-02-13 | 16:05 | 49.963
2020-02-13 | 16:05 | 49.962
2020-02-13 | 16:05 | 49.961
2020-02-13 | 16:05 | 49.963
2020-02-13 | 16:05 | 49.965
2020-02-13 | 16:05 | 49.966
2020-02-13 | 16:05 | 49.967
2020-02-13 | 16:05 | 49.967
2020-02-13 | 16:05 | 49.965
2020-02-13 | 16:05 | 49.963
2020-02-13 | 16:05 | 49.961
2020-02-13 | 16:05 | 49.96
2020-02-13 | 16:05 | 49.958
2020-02-13 | 16:05 | 49.96
2020-02-13 | 16:05 | 49.959
2020-02-13 | 16:05 | 49.96
2020-02-13 | 16:05 | 49.959
2020-02-13 | 16:05 | 49.961
2020-02-13 | 16:06 | 49.958
2020-02-13 | 16:06 | 49.96
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.96
2020-02-13 | 16:06 | 49.962
2020-02-13 | 16:06 | 49.964
2020-02-13 | 16:06 | 49.962
2020-02-13 | 16:06 | 49.96
2020-02-13 | 16:06 | 49.96
2020-02-13 | 16:06 | 49.961
2020-02-13 | 16:06 | 49.961
2020-02-13 | 16:06 | 49.961
2020-02-13 | 16:06 | 49.962
2020-02-13 | 16:06 | 49.962
2020-02-13 | 16:06 | 49.961
2020-02-13 | 16:06 | 49.961
2020-02-13 | 16:06 | 49.958
2020-02-13 | 16:06 | 49.957
2020-02-13 | 16:06 | 49.957
2020-02-13 | 16:06 | 49.957
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.958
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.96
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.961
2020-02-13 | 16:06 | 49.963
2020-02-13 | 16:06 | 49.963
2020-02-13 | 16:06 | 49.964
2020-02-13 | 16:06 | 49.965
2020-02-13 | 16:06 | 49.963
2020-02-13 | 16:06 | 49.964
2020-02-13 | 16:06 | 49.966
2020-02-13 | 16:06 | 49.964
2020-02-13 | 16:06 | 49.966
2020-02-13 | 16:06 | 49.967
2020-02-13 | 16:06 | 49.971
2020-02-13 | 16:06 | 49.971
2020-02-13 | 16:06 | 49.972
2020-02-13 | 16:06 | 49.971
2020-02-13 | 16:06 | 49.971
2020-02-13 | 16:06 | 49.97
2020-02-13 | 16:06 | 49.967
2020-02-13 | 16:06 | 49.966
2020-02-13 | 16:06 | 49.965
2020-02-13 | 16:06 | 49.963
2020-02-13 | 16:06 | 49.96
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.959
2020-02-13 | 16:06 | 49.958
2020-02-13 | 16:06 | 49.957
2020-02-13 | 16:06 | 49.956
2020-02-13 | 16:06 | 49.955
2020-02-13 | 16:06 | 49.955
2020-02-13 | 16:06 | 49.953
2020-02-13 | 16:06 | 49.952
2020-02-13 | 16:06 | 49.949
2020-02-13 | 16:06 | 49.95
2020-02-13 | 16:06 | 49.95
2020-02-13 | 16:07 | 49.949
2020-02-13 | 16:07 | 49.95
2020-02-13 | 16:07 | 49.951
2020-02-13 | 16:07 | 49.952
2020-02-13 | 16:07 | 49.953
2020-02-13 | 16:07 | 49.955
2020-02-13 | 16:07 | 49.959
2020-02-13 | 16:07 | 49.96
2020-02-13 | 16:07 | 49.961
2020-02-13 | 16:07 | 49.961
2020-02-13 | 16:07 | 49.958
2020-02-13 | 16:07 | 49.956
2020-02-13 | 16:07 | 49.953
2020-02-13 | 16:07 | 49.951
2020-02-13 | 16:07 | 49.95
2020-02-13 | 16:07 | 49.95
2020-02-13 | 16:07 | 49.948
2020-02-13 | 16:07 | 49.946
2020-02-13 | 16:07 | 49.945
2020-02-13 | 16:07 | 49.944
2020-02-13 | 16:07 | 49.94
2020-02-13 | 16:07 | 49.938
2020-02-13 | 16:07 | 49.936
2020-02-13 | 16:07 | 49.931
2020-02-13 | 16:07 | 49.927
2020-02-13 | 16:07 | 49.925
2020-02-13 | 16:07 | 49.92
2020-02-13 | 16:07 | 49.918
2020-02-13 | 16:07 | 49.914
2020-02-13 | 16:07 | 49.913
2020-02-13 | 16:07 | 49.912
2020-02-13 | 16:07 | 49.909
2020-02-13 | 16:07 | 49.909
2020-02-13 | 16:07 | 49.907
2020-02-13 | 16:07 | 49.906
2020-02-13 | 16:07 | 49.906
2020-02-13 | 16:07 | 49.908
2020-02-13 | 16:07 | 49.907
2020-02-13 | 16:07 | 49.906
2020-02-13 | 16:07 | 49.906
2020-02-13 | 16:07 | 49.907
2020-02-13 | 16:07 | 49.911
2020-02-13 | 16:07 | 49.912
2020-02-13 | 16:07 | 49.913
2020-02-13 | 16:07 | 49.916
2020-02-13 | 16:07 | 49.917
2020-02-13 | 16:07 | 49.919
2020-02-13 | 16:07 | 49.922
2020-02-13 | 16:07 | 49.924
2020-02-13 | 16:07 | 49.925
2020-02-13 | 16:07 | 49.928
2020-02-13 | 16:07 | 49.931
2020-02-13 | 16:07 | 49.935
2020-02-13 | 16:07 | 49.939
2020-02-13 | 16:07 | 49.942
2020-02-13 | 16:07 | 49.942
2020-02-13 | 16:07 | 49.944
2020-02-13 | 16:07 | 49.943
2020-02-13 | 16:07 | 49.945
2020-02-13 | 16:08 | 49.945
2020-02-13 | 16:08 | 49.944
2020-02-13 | 16:08 | 49.945
2020-02-13 | 16:08 | 49.943
2020-02-13 | 16:08 | 49.942
2020-02-13 | 16:08 | 49.942
2020-02-13 | 16:08 | 49.942
2020-02-13 | 16:08 | 49.94
2020-02-13 | 16:08 | 49.939
2020-02-13 | 16:08 | 49.938
2020-02-13 | 16:08 | 49.936
2020-02-13 | 16:08 | 49.937
2020-02-13 | 16:08 | 49.938
2020-02-13 | 16:08 | 49.94
2020-02-13 | 16:08 | 49.942
2020-02-13 | 16:08 | 49.943
2020-02-13 | 16:08 | 49.946
2020-02-13 | 16:08 | 49.946
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.95
2020-02-13 | 16:08 | 49.951
2020-02-13 | 16:08 | 49.95
2020-02-13 | 16:08 | 49.948
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.948
2020-02-13 | 16:08 | 49.95
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.95
2020-02-13 | 16:08 | 49.951
2020-02-13 | 16:08 | 49.952
2020-02-13 | 16:08 | 49.952
2020-02-13 | 16:08 | 49.953
2020-02-13 | 16:08 | 49.954
2020-02-13 | 16:08 | 49.953
2020-02-13 | 16:08 | 49.955
2020-02-13 | 16:08 | 49.958
2020-02-13 | 16:08 | 49.96
2020-02-13 | 16:08 | 49.962
2020-02-13 | 16:08 | 49.963
2020-02-13 | 16:08 | 49.963
2020-02-13 | 16:08 | 49.962
2020-02-13 | 16:08 | 49.96
2020-02-13 | 16:08 | 49.958
2020-02-13 | 16:08 | 49.955
2020-02-13 | 16:08 | 49.952
2020-02-13 | 16:08 | 49.951
2020-02-13 | 16:08 | 49.949
2020-02-13 | 16:08 | 49.947
2020-02-13 | 16:08 | 49.947
2020-02-13 | 16:08 | 49.947
2020-02-13 | 16:08 | 49.946
2020-02-13 | 16:08 | 49.944
2020-02-13 | 16:08 | 49.941
2020-02-13 | 16:08 | 49.941
2020-02-13 | 16:08 | 49.94
2020-02-13 | 16:08 | 49.94
2020-02-13 | 16:08 | 49.939
2020-02-13 | 16:08 | 49.939
2020-02-13 | 16:09 | 49.938
2020-02-13 | 16:09 | 49.936
2020-02-13 | 16:09 | 49.934
2020-02-13 | 16:09 | 49.935
2020-02-13 | 16:09 | 49.936
2020-02-13 | 16:09 | 49.937
2020-02-13 | 16:09 | 49.941
2020-02-13 | 16:09 | 49.943
2020-02-13 | 16:09 | 49.944
2020-02-13 | 16:09 | 49.948
2020-02-13 | 16:09 | 49.95
2020-02-13 | 16:09 | 49.953
2020-02-13 | 16:09 | 49.955
2020-02-13 | 16:09 | 49.955
2020-02-13 | 16:09 | 49.955
2020-02-13 | 16:09 | 49.957
2020-02-13 | 16:09 | 49.956
2020-02-13 | 16:09 | 49.955
2020-02-13 | 16:09 | 49.954
2020-02-13 | 16:09 | 49.954
2020-02-13 | 16:09 | 49.952
2020-02-13 | 16:09 | 49.95
2020-02-13 | 16:09 | 49.945
2020-02-13 | 16:09 | 49.942
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:09 | 49.938
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:09 | 49.939
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:09 | 49.938
2020-02-13 | 16:09 | 49.936
2020-02-13 | 16:09 | 49.933
2020-02-13 | 16:09 | 49.93
2020-02-13 | 16:09 | 49.928
2020-02-13 | 16:09 | 49.926
2020-02-13 | 16:09 | 49.924
2020-02-13 | 16:09 | 49.924
2020-02-13 | 16:09 | 49.924
2020-02-13 | 16:09 | 49.923
2020-02-13 | 16:09 | 49.923
2020-02-13 | 16:09 | 49.922
2020-02-13 | 16:09 | 49.921
2020-02-13 | 16:09 | 49.921
2020-02-13 | 16:09 | 49.923
2020-02-13 | 16:09 | 49.922
2020-02-13 | 16:09 | 49.923
2020-02-13 | 16:09 | 49.922
2020-02-13 | 16:09 | 49.922
2020-02-13 | 16:09 | 49.923
2020-02-13 | 16:09 | 49.926
2020-02-13 | 16:09 | 49.928
2020-02-13 | 16:09 | 49.931
2020-02-13 | 16:09 | 49.933
2020-02-13 | 16:09 | 49.935
2020-02-13 | 16:09 | 49.938
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:09 | 49.94
2020-02-13 | 16:10 | 49.938
2020-02-13 | 16:10 | 49.941
2020-02-13 | 16:10 | 49.941
2020-02-13 | 16:10 | 49.942
2020-02-13 | 16:10 | 49.943
2020-02-13 | 16:10 | 49.943
2020-02-13 | 16:10 | 49.943
2020-02-13 | 16:10 | 49.941
2020-02-13 | 16:10 | 49.94
2020-02-13 | 16:10 | 49.943
2020-02-13 | 16:10 | 49.944
2020-02-13 | 16:10 | 49.943
2020-02-13 | 16:10 | 49.941
2020-02-13 | 16:10 | 49.94
2020-02-13 | 16:10 | 49.938
2020-02-13 | 16:10 | 49.937
2020-02-13 | 16:10 | 49.936
2020-02-13 | 16:10 | 49.935
2020-02-13 | 16:10 | 49.935
2020-02-13 | 16:10 | 49.934
2020-02-13 | 16:10 | 49.934
2020-02-13 | 16:10 | 49.934
2020-02-13 | 16:10 | 49.933
2020-02-13 | 16:10 | 49.935
2020-02-13 | 16:10 | 49.935
2020-02-13 | 16:10 | 49.934
2020-02-13 | 16:10 | 49.931
2020-02-13 | 16:10 | 49.929
2020-02-13 | 16:10 | 49.928
2020-02-13 | 16:10 | 49.928
2020-02-13 | 16:10 | 49.927
2020-02-13 | 16:10 | 49.927
2020-02-13 | 16:10 | 49.928
2020-02-13 | 16:10 | 49.929
2020-02-13 | 16:10 | 49.932
2020-02-13 | 16:10 | 49.934
2020-02-13 | 16:10 | 49.938
2020-02-13 | 16:10 | 49.942
2020-02-13 | 16:10 | 49.945
2020-02-13 | 16:10 | 49.945
2020-02-13 | 16:10 | 49.948
2020-02-13 | 16:10 | 49.95
2020-02-13 | 16:10 | 49.954
2020-02-13 | 16:10 | 49.954
2020-02-13 | 16:10 | 49.956
2020-02-13 | 16:10 | 49.956
2020-02-13 | 16:10 | 49.957
2020-02-13 | 16:10 | 49.956
2020-02-13 | 16:10 | 49.955
2020-02-13 | 16:10 | 49.955
2020-02-13 | 16:10 | 49.956
2020-02-13 | 16:10 | 49.955
2020-02-13 | 16:10 | 49.954
2020-02-13 | 16:10 | 49.954
2020-02-13 | 16:10 | 49.951
2020-02-13 | 16:10 | 49.951
2020-02-13 | 16:10 | 49.951
2020-02-13 | 16:10 | 49.952
2020-02-13 | 16:10 | 49.95
2020-02-13 | 16:10 | 49.952
2020-02-13 | 16:10 | 49.952
2020-02-13 | 16:11 | 49.951
2020-02-13 | 16:11 | 49.949
2020-02-13 | 16:11 | 49.95
2020-02-13 | 16:11 | 49.949
2020-02-13 | 16:11 | 49.951
2020-02-13 | 16:11 | 49.953
2020-02-13 | 16:11 | 49.955
2020-02-13 | 16:11 | 49.955
2020-02-13 | 16:11 | 49.958
2020-02-13 | 16:11 | 49.958
2020-02-13 | 16:11 | 49.96
2020-02-13 | 16:11 | 49.963
2020-02-13 | 16:11 | 49.965
2020-02-13 | 16:11 | 49.967
2020-02-13 | 16:11 | 49.969
2020-02-13 | 16:11 | 49.97
2020-02-13 | 16:11 | 49.969
2020-02-13 | 16:11 | 49.971
2020-02-13 | 16:11 | 49.971
2020-02-13 | 16:11 | 49.971
2020-02-13 | 16:11 | 49.971
2020-02-13 | 16:11 | 49.971
2020-02-13 | 16:11 | 49.972
2020-02-13 | 16:11 | 49.971
2020-02-13 | 16:11 | 49.97
2020-02-13 | 16:11 | 49.967
2020-02-13 | 16:11 | 49.965
2020-02-13 | 16:11 | 49.965
2020-02-13 | 16:11 | 49.962
2020-02-13 | 16:11 | 49.961
2020-02-13 | 16:11 | 49.96
2020-02-13 | 16:11 | 49.959
2020-02-13 | 16:11 | 49.96
2020-02-13 | 16:11 | 49.958
2020-02-13 | 16:11 | 49.957
2020-02-13 | 16:11 | 49.958
2020-02-13 | 16:11 | 49.959
2020-02-13 | 16:11 | 49.959
2020-02-13 | 16:11 | 49.957
2020-02-13 | 16:11 | 49.959
2020-02-13 | 16:11 | 49.959
2020-02-13 | 16:11 | 49.958
2020-02-13 | 16:11 | 49.959
2020-02-13 | 16:11 | 49.957
2020-02-13 | 16:11 | 49.957
2020-02-13 | 16:11 | 49.957
2020-02-13 | 16:11 | 49.956
2020-02-13 | 16:11 | 49.955
2020-02-13 | 16:11 | 49.955
2020-02-13 | 16:11 | 49.954
2020-02-13 | 16:11 | 49.951
2020-02-13 | 16:11 | 49.95
2020-02-13 | 16:11 | 49.949
2020-02-13 | 16:11 | 49.949
2020-02-13 | 16:11 | 49.948
2020-02-13 | 16:11 | 49.949
2020-02-13 | 16:11 | 49.948
2020-02-13 | 16:11 | 49.948
2020-02-13 | 16:11 | 49.95
2020-02-13 | 16:12 | 49.951
2020-02-13 | 16:12 | 49.948
2020-02-13 | 16:12 | 49.946
2020-02-13 | 16:12 | 49.946
2020-02-13 | 16:12 | 49.947
2020-02-13 | 16:12 | 49.946
2020-02-13 | 16:12 | 49.945
2020-02-13 | 16:12 | 49.943
2020-02-13 | 16:12 | 49.94
2020-02-13 | 16:12 | 49.938
2020-02-13 | 16:12 | 49.934
2020-02-13 | 16:12 | 49.929
2020-02-13 | 16:12 | 49.926
2020-02-13 | 16:12 | 49.925
2020-02-13 | 16:12 | 49.925
2020-02-13 | 16:12 | 49.926
2020-02-13 | 16:12 | 49.926
2020-02-13 | 16:12 | 49.926
2020-02-13 | 16:12 | 49.925
2020-02-13 | 16:12 | 49.929
2020-02-13 | 16:12 | 49.93
2020-02-13 | 16:12 | 49.932
2020-02-13 | 16:12 | 49.933
2020-02-13 | 16:12 | 49.935
2020-02-13 | 16:12 | 49.936
2020-02-13 | 16:12 | 49.935
2020-02-13 | 16:12 | 49.935
2020-02-13 | 16:12 | 49.936
2020-02-13 | 16:12 | 49.936
2020-02-13 | 16:12 | 49.937
2020-02-13 | 16:12 | 49.934
2020-02-13 | 16:12 | 49.933
2020-02-13 | 16:12 | 49.932
2020-02-13 | 16:12 | 49.93
2020-02-13 | 16:12 | 49.928
2020-02-13 | 16:12 | 49.925
2020-02-13 | 16:12 | 49.922
2020-02-13 | 16:12 | 49.921
2020-02-13 | 16:12 | 49.92
2020-02-13 | 16:12 | 49.918
2020-02-13 | 16:12 | 49.914
2020-02-13 | 16:12 | 49.912
2020-02-13 | 16:12 | 49.91
2020-02-13 | 16:12 | 49.91
2020-02-13 | 16:12 | 49.908
2020-02-13 | 16:12 | 49.906
2020-02-13 | 16:12 | 49.906
2020-02-13 | 16:12 | 49.908
2020-02-13 | 16:12 | 49.91
2020-02-13 | 16:12 | 49.911
2020-02-13 | 16:12 | 49.911
2020-02-13 | 16:12 | 49.913
2020-02-13 | 16:12 | 49.916
2020-02-13 | 16:12 | 49.919
2020-02-13 | 16:12 | 49.92
2020-02-13 | 16:12 | 49.921
2020-02-13 | 16:12 | 49.922
2020-02-13 | 16:12 | 49.921
2020-02-13 | 16:12 | 49.921
2020-02-13 | 16:12 | 49.919
2020-02-13 | 16:12 | 49.918
2020-02-13 | 16:13 | 49.918
2020-02-13 | 16:13 | 49.92
2020-02-13 | 16:13 | 49.923
2020-02-13 | 16:13 | 49.924
2020-02-13 | 16:13 | 49.925
2020-02-13 | 16:13 | 49.928
2020-02-13 | 16:13 | 49.93
2020-02-13 | 16:13 | 49.933
2020-02-13 | 16:13 | 49.934
2020-02-13 | 16:13 | 49.935
2020-02-13 | 16:13 | 49.933
2020-02-13 | 16:13 | 49.933
2020-02-13 | 16:13 | 49.933
2020-02-13 | 16:13 | 49.933
2020-02-13 | 16:13 | 49.933
2020-02-13 | 16:13 | 49.93
2020-02-13 | 16:13 | 49.929
2020-02-13 | 16:13 | 49.926
2020-02-13 | 16:13 | 49.926
2020-02-13 | 16:13 | 49.927
2020-02-13 | 16:13 | 49.927
2020-02-13 | 16:13 | 49.927
2020-02-13 | 16:13 | 49.923
2020-02-13 | 16:13 | 49.92
2020-02-13 | 16:13 | 49.919
2020-02-13 | 16:13 | 49.917
2020-02-13 | 16:13 | 49.916
2020-02-13 | 16:13 | 49.914
2020-02-13 | 16:13 | 49.913
2020-02-13 | 16:13 | 49.912
2020-02-13 | 16:13 | 49.911
2020-02-13 | 16:13 | 49.912
2020-02-13 | 16:13 | 49.913
2020-02-13 | 16:13 | 49.913
2020-02-13 | 16:13 | 49.913
2020-02-13 | 16:13 | 49.912
2020-02-13 | 16:13 | 49.912
2020-02-13 | 16:13 | 49.909
2020-02-13 | 16:13 | 49.908
2020-02-13 | 16:13 | 49.904
2020-02-13 | 16:13 | 49.902
2020-02-13 | 16:13 | 49.901
2020-02-13 | 16:13 | 49.901
2020-02-13 | 16:13 | 49.902
2020-02-13 | 16:13 | 49.904
2020-02-13 | 16:13 | 49.905
2020-02-13 | 16:13 | 49.906
2020-02-13 | 16:13 | 49.906
2020-02-13 | 16:13 | 49.907
2020-02-13 | 16:13 | 49.905
2020-02-13 | 16:13 | 49.905
2020-02-13 | 16:13 | 49.903
2020-02-13 | 16:13 | 49.903
2020-02-13 | 16:13 | 49.903
2020-02-13 | 16:13 | 49.903
2020-02-13 | 16:13 | 49.903
2020-02-13 | 16:13 | 49.902
2020-02-13 | 16:13 | 49.9
2020-02-13 | 16:13 | 49.901
2020-02-13 | 16:14 | 49.9
2020-02-13 | 16:14 | 49.901
2020-02-13 | 16:14 | 49.901
2020-02-13 | 16:14 | 49.902
2020-02-13 | 16:14 | 49.904
2020-02-13 | 16:14 | 49.904
2020-02-13 | 16:14 | 49.903
2020-02-13 | 16:14 | 49.904
2020-02-13 | 16:14 | 49.905
2020-02-13 | 16:14 | 49.907
2020-02-13 | 16:14 | 49.908
2020-02-13 | 16:14 | 49.909
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.91
2020-02-13 | 16:14 | 49.91
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.912
2020-02-13 | 16:14 | 49.913
2020-02-13 | 16:14 | 49.913
2020-02-13 | 16:14 | 49.914
2020-02-13 | 16:14 | 49.913
2020-02-13 | 16:14 | 49.913
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.909
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.912
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.909
2020-02-13 | 16:14 | 49.908
2020-02-13 | 16:14 | 49.907
2020-02-13 | 16:14 | 49.908
2020-02-13 | 16:14 | 49.908
2020-02-13 | 16:14 | 49.907
2020-02-13 | 16:14 | 49.908
2020-02-13 | 16:14 | 49.909
2020-02-13 | 16:14 | 49.909
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.911
2020-02-13 | 16:14 | 49.913
2020-02-13 | 16:14 | 49.913
2020-02-13 | 16:14 | 49.914
2020-02-13 | 16:14 | 49.916
2020-02-13 | 16:14 | 49.917
2020-02-13 | 16:14 | 49.919
2020-02-13 | 16:14 | 49.92
2020-02-13 | 16:14 | 49.919
2020-02-13 | 16:14 | 49.918
2020-02-13 | 16:14 | 49.918
2020-02-13 | 16:14 | 49.917
2020-02-13 | 16:14 | 49.915
2020-02-13 | 16:14 | 49.914
2020-02-13 | 16:14 | 49.912
2020-02-13 | 16:14 | 49.91
2020-02-13 | 16:14 | 49.908
2020-02-13 | 16:14 | 49.907
2020-02-13 | 16:14 | 49.907
2020-02-13 | 16:14 | 49.905
2020-02-13 | 16:14 | 49.902
2020-02-13 | 16:14 | 49.899
2020-02-13 | 16:14 | 49.896
2020-02-13 | 16:15 | 49.892
2020-02-13 | 16:15 | 49.889
2020-02-13 | 16:15 | 49.887
2020-02-13 | 16:15 | 49.886
2020-02-13 | 16:15 | 49.885
2020-02-13 | 16:15 | 49.885
2020-02-13 | 16:15 | 49.882
2020-02-13 | 16:15 | 49.879
2020-02-13 | 16:15 | 49.877
2020-02-13 | 16:15 | 49.877
2020-02-13 | 16:15 | 49.875
2020-02-13 | 16:15 | 49.876
2020-02-13 | 16:15 | 49.876
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.879
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.879
2020-02-13 | 16:15 | 49.881
2020-02-13 | 16:15 | 49.883
2020-02-13 | 16:15 | 49.884
2020-02-13 | 16:15 | 49.886
2020-02-13 | 16:15 | 49.888
2020-02-13 | 16:15 | 49.89
2020-02-13 | 16:15 | 49.889
2020-02-13 | 16:15 | 49.891
2020-02-13 | 16:15 | 49.891
2020-02-13 | 16:15 | 49.891
2020-02-13 | 16:15 | 49.889
2020-02-13 | 16:15 | 49.889
2020-02-13 | 16:15 | 49.888
2020-02-13 | 16:15 | 49.887
2020-02-13 | 16:15 | 49.886
2020-02-13 | 16:15 | 49.885
2020-02-13 | 16:15 | 49.883
2020-02-13 | 16:15 | 49.881
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.878
2020-02-13 | 16:15 | 49.88
2020-02-13 | 16:15 | 49.88
2020-02-13 | 16:15 | 49.88
2020-02-13 | 16:15 | 49.877
2020-02-13 | 16:15 | 49.879
2020-02-13 | 16:15 | 49.88
2020-02-13 | 16:15 | 49.88
2020-02-13 | 16:15 | 49.885
2020-02-13 | 16:15 | 49.888
2020-02-13 | 16:15 | 49.891
2020-02-13 | 16:15 | 49.894
2020-02-13 | 16:15 | 49.899
2020-02-13 | 16:15 | 49.904
2020-02-13 | 16:15 | 49.907
2020-02-13 | 16:15 | 49.912
2020-02-13 | 16:15 | 49.913
2020-02-13 | 16:15 | 49.916
2020-02-13 | 16:15 | 49.918
2020-02-13 | 16:16 | 49.919
2020-02-13 | 16:16 | 49.918
2020-02-13 | 16:16 | 49.918
2020-02-13 | 16:16 | 49.915
2020-02-13 | 16:16 | 49.915
2020-02-13 | 16:16 | 49.914
2020-02-13 | 16:16 | 49.913
2020-02-13 | 16:16 | 49.91
2020-02-13 | 16:16 | 49.906
2020-02-13 | 16:16 | 49.904
2020-02-13 | 16:16 | 49.902
2020-02-13 | 16:16 | 49.902
2020-02-13 | 16:16 | 49.901
2020-02-13 | 16:16 | 49.902
2020-02-13 | 16:16 | 49.902
2020-02-13 | 16:16 | 49.901
2020-02-13 | 16:16 | 49.902
2020-02-13 | 16:16 | 49.904
2020-02-13 | 16:16 | 49.904
2020-02-13 | 16:16 | 49.907
2020-02-13 | 16:16 | 49.909
2020-02-13 | 16:16 | 49.911
2020-02-13 | 16:16 | 49.912
2020-02-13 | 16:16 | 49.91
2020-02-13 | 16:16 | 49.907
2020-02-13 | 16:16 | 49.903
2020-02-13 | 16:16 | 49.901
2020-02-13 | 16:16 | 49.901
2020-02-13 | 16:16 | 49.898
2020-02-13 | 16:16 | 49.895
2020-02-13 | 16:16 | 49.89
2020-02-13 | 16:16 | 49.888
2020-02-13 | 16:16 | 49.884
2020-02-13 | 16:16 | 49.881
2020-02-13 | 16:16 | 49.88
2020-02-13 | 16:16 | 49.879
2020-02-13 | 16:16 | 49.878
2020-02-13 | 16:16 | 49.878
2020-02-13 | 16:16 | 49.877
2020-02-13 | 16:16 | 49.875
2020-02-13 | 16:16 | 49.875
2020-02-13 | 16:16 | 49.877
2020-02-13 | 16:16 | 49.878
2020-02-13 | 16:16 | 49.881
2020-02-13 | 16:16 | 49.884
2020-02-13 | 16:16 | 49.886
2020-02-13 | 16:16 | 49.882
2020-02-13 | 16:16 | 49.888
2020-02-13 | 16:16 | 49.891
2020-02-13 | 16:16 | 49.894
2020-02-13 | 16:16 | 49.898
2020-02-13 | 16:16 | 49.899
2020-02-13 | 16:16 | 49.898
2020-02-13 | 16:16 | 49.897
2020-02-13 | 16:16 | 49.897
2020-02-13 | 16:16 | 49.896
2020-02-13 | 16:16 | 49.895
2020-02-13 | 16:16 | 49.895
2020-02-13 | 16:16 | 49.892
2020-02-13 | 16:16 | 49.893
2020-02-13 | 16:16 | 49.894
2020-02-13 | 16:17 | 49.896
2020-02-13 | 16:17 | 49.897
2020-02-13 | 16:17 | 49.9
2020-02-13 | 16:17 | 49.902
2020-02-13 | 16:17 | 49.902
2020-02-13 | 16:17 | 49.904
2020-02-13 | 16:17 | 49.906
2020-02-13 | 16:17 | 49.905
2020-02-13 | 16:17 | 49.906
2020-02-13 | 16:17 | 49.907
2020-02-13 | 16:17 | 49.905
2020-02-13 | 16:17 | 49.904
2020-02-13 | 16:17 | 49.905
2020-02-13 | 16:17 | 49.902
2020-02-13 | 16:17 | 49.902
2020-02-13 | 16:17 | 49.901
2020-02-13 | 16:17 | 49.901
2020-02-13 | 16:17 | 49.901
2020-02-13 | 16:17 | 49.899
2020-02-13 | 16:17 | 49.899
2020-02-13 | 16:17 | 49.898
2020-02-13 | 16:17 | 49.897
2020-02-13 | 16:17 | 49.894
2020-02-13 | 16:17 | 49.887
2020-02-13 | 16:17 | 49.878
2020-02-13 | 16:17 | 49.869
2020-02-13 | 16:17 | 49.861
2020-02-13 | 16:17 | 49.849
2020-02-13 | 16:17 | 49.842
2020-02-13 | 16:17 | 49.834
2020-02-13 | 16:17 | 49.831
2020-02-13 | 16:17 | 49.831
2020-02-13 | 16:17 | 49.834
2020-02-13 | 16:17 | 49.841
2020-02-13 | 16:17 | 49.851
2020-02-13 | 16:17 | 49.858
2020-02-13 | 16:17 | 49.864
2020-02-13 | 16:17 | 49.864
2020-02-13 | 16:17 | 49.863
2020-02-13 | 16:17 | 49.863
2020-02-13 | 16:17 | 49.862
2020-02-13 | 16:17 | 49.861
2020-02-13 | 16:17 | 49.859
2020-02-13 | 16:17 | 49.858
2020-02-13 | 16:17 | 49.858
2020-02-13 | 16:17 | 49.858
2020-02-13 | 16:17 | 49.859
2020-02-13 | 16:17 | 49.86
2020-02-13 | 16:17 | 49.862
2020-02-13 | 16:17 | 49.862
2020-02-13 | 16:17 | 49.863
2020-02-13 | 16:17 | 49.862
2020-02-13 | 16:17 | 49.861
2020-02-13 | 16:17 | 49.862
2020-02-13 | 16:17 | 49.863
2020-02-13 | 16:17 | 49.865
2020-02-13 | 16:17 | 49.87
2020-02-13 | 16:17 | 49.877
2020-02-13 | 16:17 | 49.885
2020-02-13 | 16:18 | 49.89
2020-02-13 | 16:18 | 49.896
2020-02-13 | 16:18 | 49.9
2020-02-13 | 16:18 | 49.904
2020-02-13 | 16:18 | 49.906
2020-02-13 | 16:18 | 49.906
2020-02-13 | 16:18 | 49.906
2020-02-13 | 16:18 | 49.908
2020-02-13 | 16:18 | 49.909
2020-02-13 | 16:18 | 49.911
2020-02-13 | 16:18 | 49.911
2020-02-13 | 16:18 | 49.912
2020-02-13 | 16:18 | 49.912
2020-02-13 | 16:18 | 49.911
2020-02-13 | 16:18 | 49.914
2020-02-13 | 16:18 | 49.914
2020-02-13 | 16:18 | 49.915
2020-02-13 | 16:18 | 49.915
2020-02-13 | 16:18 | 49.914
2020-02-13 | 16:18 | 49.913
2020-02-13 | 16:18 | 49.909
2020-02-13 | 16:18 | 49.905
2020-02-13 | 16:18 | 49.901
2020-02-13 | 16:18 | 49.897
2020-02-13 | 16:18 | 49.893
2020-02-13 | 16:18 | 49.89
2020-02-13 | 16:18 | 49.886
2020-02-13 | 16:18 | 49.883
2020-02-13 | 16:18 | 49.884
2020-02-13 | 16:18 | 49.883
2020-02-13 | 16:18 | 49.883
2020-02-13 | 16:18 | 49.884
2020-02-13 | 16:18 | 49.885
2020-02-13 | 16:18 | 49.887
2020-02-13 | 16:18 | 49.889
2020-02-13 | 16:18 | 49.892
2020-02-13 | 16:18 | 49.895
2020-02-13 | 16:18 | 49.899
2020-02-13 | 16:18 | 49.908
2020-02-13 | 16:18 | 49.914
2020-02-13 | 16:18 | 49.921
2020-02-13 | 16:18 | 49.929
2020-02-13 | 16:18 | 49.936
2020-02-13 | 16:18 | 49.946
2020-02-13 | 16:18 | 49.953
2020-02-13 | 16:18 | 49.957
2020-02-13 | 16:18 | 49.96
2020-02-13 | 16:18 | 49.96
2020-02-13 | 16:18 | 49.959
2020-02-13 | 16:18 | 49.957
2020-02-13 | 16:18 | 49.955
2020-02-13 | 16:18 | 49.952
2020-02-13 | 16:18 | 49.951
2020-02-13 | 16:18 | 49.949
2020-02-13 | 16:18 | 49.947
2020-02-13 | 16:18 | 49.946
2020-02-13 | 16:18 | 49.943
2020-02-13 | 16:18 | 49.939
2020-02-13 | 16:18 | 49.936
2020-02-13 | 16:18 | 49.933
2020-02-13 | 16:18 | 49.932
2020-02-13 | 16:19 | 49.928
2020-02-13 | 16:19 | 49.925
2020-02-13 | 16:19 | 49.921
2020-02-13 | 16:19 | 49.919
2020-02-13 | 16:19 | 49.917
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.915
2020-02-13 | 16:19 | 49.917
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.917
2020-02-13 | 16:19 | 49.917
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.916
2020-02-13 | 16:19 | 49.915
2020-02-13 | 16:19 | 49.915
2020-02-13 | 16:19 | 49.917
2020-02-13 | 16:19 | 49.92
2020-02-13 | 16:19 | 49.922
2020-02-13 | 16:19 | 49.923
2020-02-13 | 16:19 | 49.927
2020-02-13 | 16:19 | 49.931
2020-02-13 | 16:19 | 49.933
2020-02-13 | 16:19 | 49.934
2020-02-13 | 16:19 | 49.935
2020-02-13 | 16:19 | 49.936
2020-02-13 | 16:19 | 49.937
2020-02-13 | 16:19 | 49.937
2020-02-13 | 16:19 | 49.939
2020-02-13 | 16:19 | 49.94
2020-02-13 | 16:19 | 49.943
2020-02-13 | 16:19 | 49.943
2020-02-13 | 16:19 | 49.942
2020-02-13 | 16:19 | 49.939
2020-02-13 | 16:19 | 49.938
2020-02-13 | 16:19 | 49.933
2020-02-13 | 16:19 | 49.931
2020-02-13 | 16:19 | 49.931
2020-02-13 | 16:19 | 49.93
2020-02-13 | 16:19 | 49.929
2020-02-13 | 16:19 | 49.928
2020-02-13 | 16:19 | 49.927
2020-02-13 | 16:19 | 49.929
2020-02-13 | 16:19 | 49.926
2020-02-13 | 16:19 | 49.927
2020-02-13 | 16:19 | 49.928
2020-02-13 | 16:19 | 49.927
2020-02-13 | 16:19 | 49.926
2020-02-13 | 16:19 | 49.927
2020-02-13 | 16:19 | 49.929
2020-02-13 | 16:19 | 49.932
2020-02-13 | 16:19 | 49.933
2020-02-13 | 16:19 | 49.936
2020-02-13 | 16:19 | 49.942
2020-02-13 | 16:19 | 49.945
2020-02-13 | 16:19 | 49.95
2020-02-13 | 16:19 | 49.951
2020-02-13 | 16:20 | 49.952
2020-02-13 | 16:20 | 49.953
2020-02-13 | 16:20 | 49.952
2020-02-13 | 16:20 | 49.952
2020-02-13 | 16:20 | 49.95
2020-02-13 | 16:20 | 49.947
2020-02-13 | 16:20 | 49.946
2020-02-13 | 16:20 | 49.944
2020-02-13 | 16:20 | 49.943
2020-02-13 | 16:20 | 49.946
2020-02-13 | 16:20 | 49.947
2020-02-13 | 16:20 | 49.948
2020-02-13 | 16:20 | 49.949
2020-02-13 | 16:20 | 49.952
2020-02-13 | 16:20 | 49.951
2020-02-13 | 16:20 | 49.951
2020-02-13 | 16:20 | 49.951
2020-02-13 | 16:20 | 49.948
2020-02-13 | 16:20 | 49.947
2020-02-13 | 16:20 | 49.943
2020-02-13 | 16:20 | 49.94
2020-02-13 | 16:20 | 49.939
2020-02-13 | 16:20 | 49.94
2020-02-13 | 16:20 | 49.941
2020-02-13 | 16:20 | 49.942
2020-02-13 | 16:20 | 49.943
2020-02-13 | 16:20 | 49.944
2020-02-13 | 16:20 | 49.945
2020-02-13 | 16:20 | 49.944
2020-02-13 | 16:20 | 49.945
2020-02-13 | 16:20 | 49.941
2020-02-13 | 16:20 | 49.936
2020-02-13 | 16:20 | 49.932
2020-02-13 | 16:20 | 49.928
2020-02-13 | 16:20 | 49.924
2020-02-13 | 16:20 | 49.92
2020-02-13 | 16:20 | 49.917
2020-02-13 | 16:20 | 49.914
2020-02-13 | 16:20 | 49.911
2020-02-13 | 16:20 | 49.912
2020-02-13 | 16:20 | 49.913
2020-02-13 | 16:20 | 49.915
2020-02-13 | 16:20 | 49.916
2020-02-13 | 16:20 | 49.919
2020-02-13 | 16:20 | 49.919
2020-02-13 | 16:20 | 49.92
2020-02-13 | 16:20 | 49.92
2020-02-13 | 16:20 | 49.923
2020-02-13 | 16:20 | 49.926
2020-02-13 | 16:20 | 49.929
2020-02-13 | 16:20 | 49.93
2020-02-13 | 16:20 | 49.933
2020-02-13 | 16:20 | 49.936
2020-02-13 | 16:20 | 49.936
2020-02-13 | 16:20 | 49.936
2020-02-13 | 16:20 | 49.938
2020-02-13 | 16:20 | 49.939
2020-02-13 | 16:20 | 49.939
2020-02-13 | 16:20 | 49.94
2020-02-13 | 16:20 | 49.938
2020-02-13 | 16:20 | 49.937
2020-02-13 | 16:21 | 49.936
2020-02-13 | 16:21 | 49.937
2020-02-13 | 16:21 | 49.94
2020-02-13 | 16:21 | 49.941
2020-02-13 | 16:21 | 49.942
2020-02-13 | 16:21 | 49.944
2020-02-13 | 16:21 | 49.945
2020-02-13 | 16:21 | 49.945
2020-02-13 | 16:21 | 49.946
2020-02-13 | 16:21 | 49.946
2020-02-13 | 16:21 | 49.95
2020-02-13 | 16:21 | 49.952
2020-02-13 | 16:21 | 49.955
2020-02-13 | 16:21 | 49.959
2020-02-13 | 16:21 | 49.961
2020-02-13 | 16:21 | 49.964
2020-02-13 | 16:21 | 49.966
2020-02-13 | 16:21 | 49.966
2020-02-13 | 16:21 | 49.966
2020-02-13 | 16:21 | 49.967
2020-02-13 | 16:21 | 49.965
2020-02-13 | 16:21 | 49.963
2020-02-13 | 16:21 | 49.959
2020-02-13 | 16:21 | 49.956
2020-02-13 | 16:21 | 49.954
2020-02-13 | 16:21 | 49.951
2020-02-13 | 16:21 | 49.948
2020-02-13 | 16:21 | 49.945
2020-02-13 | 16:21 | 49.943
2020-02-13 | 16:21 | 49.939
2020-02-13 | 16:21 | 49.936
2020-02-13 | 16:21 | 49.934
2020-02-13 | 16:21 | 49.93
2020-02-13 | 16:21 | 49.929
2020-02-13 | 16:21 | 49.928
2020-02-13 | 16:21 | 49.926
2020-02-13 | 16:21 | 49.927
2020-02-13 | 16:21 | 49.926
2020-02-13 | 16:21 | 49.927
2020-02-13 | 16:21 | 49.926
2020-02-13 | 16:21 | 49.928
2020-02-13 | 16:21 | 49.931
2020-02-13 | 16:21 | 49.933
2020-02-13 | 16:21 | 49.934
2020-02-13 | 16:21 | 49.936
2020-02-13 | 16:21 | 49.938
2020-02-13 | 16:21 | 49.939
2020-02-13 | 16:21 | 49.94
2020-02-13 | 16:21 | 49.941
2020-02-13 | 16:21 | 49.941
2020-02-13 | 16:21 | 49.942
2020-02-13 | 16:21 | 49.943
2020-02-13 | 16:21 | 49.942
2020-02-13 | 16:21 | 49.945
2020-02-13 | 16:21 | 49.945
2020-02-13 | 16:21 | 49.943
2020-02-13 | 16:21 | 49.941
2020-02-13 | 16:21 | 49.941
2020-02-13 | 16:21 | 49.939
2020-02-13 | 16:22 | 49.937
2020-02-13 | 16:22 | 49.937
2020-02-13 | 16:22 | 49.937
2020-02-13 | 16:22 | 49.936
2020-02-13 | 16:22 | 49.939
2020-02-13 | 16:22 | 49.941
2020-02-13 | 16:22 | 49.945
2020-02-13 | 16:22 | 49.949
2020-02-13 | 16:22 | 49.953
2020-02-13 | 16:22 | 49.957
2020-02-13 | 16:22 | 49.96
2020-02-13 | 16:22 | 49.962
2020-02-13 | 16:22 | 49.965
2020-02-13 | 16:22 | 49.965
2020-02-13 | 16:22 | 49.965
2020-02-13 | 16:22 | 49.966
2020-02-13 | 16:22 | 49.965
2020-02-13 | 16:22 | 49.964
2020-02-13 | 16:22 | 49.96
2020-02-13 | 16:22 | 49.959
2020-02-13 | 16:22 | 49.956
2020-02-13 | 16:22 | 49.955
2020-02-13 | 16:22 | 49.952
2020-02-13 | 16:22 | 49.952
2020-02-13 | 16:22 | 49.953
2020-02-13 | 16:22 | 49.953
2020-02-13 | 16:22 | 49.954
2020-02-13 | 16:22 | 49.955
2020-02-13 | 16:22 | 49.956
2020-02-13 | 16:22 | 49.956
2020-02-13 | 16:22 | 49.957
2020-02-13 | 16:22 | 49.957
2020-02-13 | 16:22 | 49.956
2020-02-13 | 16:22 | 49.957
2020-02-13 | 16:22 | 49.954
2020-02-13 | 16:22 | 49.951
2020-02-13 | 16:22 | 49.948
2020-02-13 | 16:22 | 49.943
2020-02-13 | 16:22 | 49.938
2020-02-13 | 16:22 | 49.933
2020-02-13 | 16:22 | 49.93
2020-02-13 | 16:22 | 49.928
2020-02-13 | 16:22 | 49.927
2020-02-13 | 16:22 | 49.927
2020-02-13 | 16:22 | 49.926
2020-02-13 | 16:22 | 49.927
2020-02-13 | 16:22 | 49.929
2020-02-13 | 16:22 | 49.927
2020-02-13 | 16:22 | 49.93
2020-02-13 | 16:22 | 49.933
2020-02-13 | 16:22 | 49.935
2020-02-13 | 16:22 | 49.939
2020-02-13 | 16:22 | 49.941
2020-02-13 | 16:22 | 49.942
2020-02-13 | 16:22 | 49.944
2020-02-13 | 16:22 | 49.944
2020-02-13 | 16:22 | 49.945
2020-02-13 | 16:22 | 49.947
2020-02-13 | 16:22 | 49.947
2020-02-13 | 16:22 | 49.947
2020-02-13 | 16:22 | 49.946
2020-02-13 | 16:23 | 49.948
2020-02-13 | 16:23 | 49.948
2020-02-13 | 16:23 | 49.951
2020-02-13 | 16:23 | 49.952
2020-02-13 | 16:23 | 49.955
2020-02-13 | 16:23 | 49.959
2020-02-13 | 16:23 | 49.962
2020-02-13 | 16:23 | 49.964
2020-02-13 | 16:23 | 49.969
2020-02-13 | 16:23 | 49.97
2020-02-13 | 16:23 | 49.973
2020-02-13 | 16:23 | 49.975
2020-02-13 | 16:23 | 49.978
2020-02-13 | 16:23 | 49.98
2020-02-13 | 16:23 | 49.983
2020-02-13 | 16:23 | 49.987
2020-02-13 | 16:23 | 49.99
2020-02-13 | 16:23 | 49.99
2020-02-13 | 16:23 | 49.992
2020-02-13 | 16:23 | 49.993
2020-02-13 | 16:23 | 49.995
2020-02-13 | 16:23 | 49.998
2020-02-13 | 16:23 | 50.001
2020-02-13 | 16:23 | 50.004
2020-02-13 | 16:23 | 50.005
2020-02-13 | 16:23 | 50.007
2020-02-13 | 16:23 | 50.008
2020-02-13 | 16:23 | 50.008
2020-02-13 | 16:23 | 50.007
2020-02-13 | 16:23 | 50.004
2020-02-13 | 16:23 | 50.001
2020-02-13 | 16:23 | 49.997
2020-02-13 | 16:23 | 49.993
2020-02-13 | 16:23 | 49.989
2020-02-13 | 16:23 | 49.986
2020-02-13 | 16:23 | 49.983
2020-02-13 | 16:23 | 49.978
2020-02-13 | 16:23 | 49.977
2020-02-13 | 16:23 | 49.975
2020-02-13 | 16:23 | 49.975
2020-02-13 | 16:23 | 49.971
2020-02-13 | 16:23 | 49.972
2020-02-13 | 16:23 | 49.971
2020-02-13 | 16:23 | 49.97
2020-02-13 | 16:23 | 49.97
2020-02-13 | 16:23 | 49.972
2020-02-13 | 16:23 | 49.971
2020-02-13 | 16:23 | 49.971
2020-02-13 | 16:23 | 49.971
2020-02-13 | 16:23 | 49.973
2020-02-13 | 16:23 | 49.973
2020-02-13 | 16:23 | 49.973
2020-02-13 | 16:23 | 49.973
2020-02-13 | 16:23 | 49.972
2020-02-13 | 16:23 | 49.972
2020-02-13 | 16:23 | 49.97
2020-02-13 | 16:23 | 49.969
2020-02-13 | 16:23 | 49.969
2020-02-13 | 16:23 | 49.969
2020-02-13 | 16:24 | 49.971
2020-02-13 | 16:24 | 49.972
2020-02-13 | 16:24 | 49.973
2020-02-13 | 16:24 | 49.976
2020-02-13 | 16:24 | 49.977
2020-02-13 | 16:24 | 49.978
2020-02-13 | 16:24 | 49.978
2020-02-13 | 16:24 | 49.98
2020-02-13 | 16:24 | 49.982
2020-02-13 | 16:24 | 49.986
2020-02-13 | 16:24 | 49.985
2020-02-13 | 16:24 | 49.989
2020-02-13 | 16:24 | 49.99
2020-02-13 | 16:24 | 49.989
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.988
2020-02-13 | 16:24 | 49.987
2020-02-13 | 16:24 | 49.989
2020-02-13 | 16:24 | 49.989
2020-02-13 | 16:24 | 49.99
2020-02-13 | 16:24 | 49.988
2020-02-13 | 16:24 | 49.988
2020-02-13 | 16:24 | 49.99
2020-02-13 | 16:24 | 49.988
2020-02-13 | 16:24 | 49.989
2020-02-13 | 16:24 | 49.989
2020-02-13 | 16:24 | 49.99
2020-02-13 | 16:24 | 49.992
2020-02-13 | 16:24 | 49.993
2020-02-13 | 16:24 | 49.996
2020-02-13 | 16:24 | 49.998
2020-02-13 | 16:24 | 50
2020-02-13 | 16:24 | 50.002
2020-02-13 | 16:24 | 50.003
2020-02-13 | 16:24 | 50.006
2020-02-13 | 16:24 | 50.008
2020-02-13 | 16:24 | 50.011
2020-02-13 | 16:24 | 50.012
2020-02-13 | 16:24 | 50.013
2020-02-13 | 16:24 | 50.015
2020-02-13 | 16:24 | 50.017
2020-02-13 | 16:24 | 50.018
2020-02-13 | 16:24 | 50.018
2020-02-13 | 16:24 | 50.02
2020-02-13 | 16:24 | 50.023
2020-02-13 | 16:24 | 50.023
2020-02-13 | 16:24 | 50.024
2020-02-13 | 16:24 | 50.025
2020-02-13 | 16:24 | 50.028
2020-02-13 | 16:24 | 50.027
2020-02-13 | 16:24 | 50.029
2020-02-13 | 16:24 | 50.029
2020-02-13 | 16:24 | 50.028
2020-02-13 | 16:24 | 50.03
2020-02-13 | 16:24 | 50.03
2020-02-13 | 16:25 | 50.03
2020-02-13 | 16:25 | 50.029
2020-02-13 | 16:25 | 50.03
2020-02-13 | 16:25 | 50.028
2020-02-13 | 16:25 | 50.028
2020-02-13 | 16:25 | 50.025
2020-02-13 | 16:25 | 50.025
2020-02-13 | 16:25 | 50.023
2020-02-13 | 16:25 | 50.023
2020-02-13 | 16:25 | 50.023
2020-02-13 | 16:25 | 50.025
2020-02-13 | 16:25 | 50.027
2020-02-13 | 16:25 | 50.029
2020-02-13 | 16:25 | 50.028
2020-02-13 | 16:25 | 50.031
2020-02-13 | 16:25 | 50.033
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.035
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.035
2020-02-13 | 16:25 | 50.035
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.036
2020-02-13 | 16:25 | 50.035
2020-02-13 | 16:25 | 50.034
2020-02-13 | 16:25 | 50.032
2020-02-13 | 16:25 | 50.027
2020-02-13 | 16:25 | 50.021
2020-02-13 | 16:25 | 50.013
2020-02-13 | 16:25 | 50.004
2020-02-13 | 16:25 | 49.993
2020-02-13 | 16:25 | 49.98
2020-02-13 | 16:25 | 49.97
2020-02-13 | 16:25 | 49.96
2020-02-13 | 16:25 | 49.951
2020-02-13 | 16:25 | 49.944
2020-02-13 | 16:25 | 49.94
2020-02-13 | 16:25 | 49.936
2020-02-13 | 16:25 | 49.936
2020-02-13 | 16:25 | 49.937
2020-02-13 | 16:25 | 49.939
2020-02-13 | 16:25 | 49.94
2020-02-13 | 16:25 | 49.943
2020-02-13 | 16:25 | 49.946
2020-02-13 | 16:25 | 49.946
2020-02-13 | 16:25 | 49.946
2020-02-13 | 16:25 | 49.947
2020-02-13 | 16:25 | 49.946
2020-02-13 | 16:25 | 49.947
2020-02-13 | 16:25 | 49.947
2020-02-13 | 16:25 | 49.946
2020-02-13 | 16:25 | 49.944
2020-02-13 | 16:25 | 49.942
2020-02-13 | 16:25 | 49.939
2020-02-13 | 16:25 | 49.939
2020-02-13 | 16:25 | 49.938
2020-02-13 | 16:26 | 49.936
2020-02-13 | 16:26 | 49.933
2020-02-13 | 16:26 | 49.934
2020-02-13 | 16:26 | 49.934
2020-02-13 | 16:26 | 49.936
2020-02-13 | 16:26 | 49.936
2020-02-13 | 16:26 | 49.938
2020-02-13 | 16:26 | 49.941
2020-02-13 | 16:26 | 49.945
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.95
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.951
2020-02-13 | 16:26 | 49.95
2020-02-13 | 16:26 | 49.951
2020-02-13 | 16:26 | 49.951
2020-02-13 | 16:26 | 49.95
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.949
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.947
2020-02-13 | 16:26 | 49.948
2020-02-13 | 16:26 | 49.946
2020-02-13 | 16:26 | 49.944
2020-02-13 | 16:26 | 49.943
2020-02-13 | 16:26 | 49.941
2020-02-13 | 16:26 | 49.938
2020-02-13 | 16:26 | 49.935
2020-02-13 | 16:26 | 49.933
2020-02-13 | 16:26 | 49.931
2020-02-13 | 16:26 | 49.93
2020-02-13 | 16:26 | 49.929
2020-02-13 | 16:26 | 49.928
2020-02-13 | 16:26 | 49.928
2020-02-13 | 16:26 | 49.926
2020-02-13 | 16:26 | 49.923
2020-02-13 | 16:26 | 49.921
2020-02-13 | 16:27 | 49.918
2020-02-13 | 16:27 | 49.917
2020-02-13 | 16:27 | 49.913
2020-02-13 | 16:27 | 49.911
2020-02-13 | 16:27 | 49.911
2020-02-13 | 16:27 | 49.911
2020-02-13 | 16:27 | 49.91
2020-02-13 | 16:27 | 49.91
2020-02-13 | 16:27 | 49.911
2020-02-13 | 16:27 | 49.911
2020-02-13 | 16:27 | 49.912
2020-02-13 | 16:27 | 49.914
2020-02-13 | 16:27 | 49.914
2020-02-13 | 16:27 | 49.917
2020-02-13 | 16:27 | 49.918
2020-02-13 | 16:27 | 49.918
2020-02-13 | 16:27 | 49.921
2020-02-13 | 16:27 | 49.923
2020-02-13 | 16:27 | 49.925
2020-02-13 | 16:27 | 49.927
2020-02-13 | 16:27 | 49.927
2020-02-13 | 16:27 | 49.928
2020-02-13 | 16:27 | 49.929
2020-02-13 | 16:27 | 49.929
2020-02-13 | 16:27 | 49.931
2020-02-13 | 16:27 | 49.93
2020-02-13 | 16:27 | 49.932
2020-02-13 | 16:27 | 49.929
2020-02-13 | 16:27 | 49.929
2020-02-13 | 16:27 | 49.925
2020-02-13 | 16:27 | 49.922
2020-02-13 | 16:27 | 49.919
2020-02-13 | 16:27 | 49.914
2020-02-13 | 16:27 | 49.911
2020-02-13 | 16:27 | 49.908
2020-02-13 | 16:27 | 49.906
2020-02-13 | 16:27 | 49.905
2020-02-13 | 16:27 | 49.907
2020-02-13 | 16:27 | 49.908
2020-02-13 | 16:27 | 49.91
2020-02-13 | 16:27 | 49.914
2020-02-13 | 16:27 | 49.916
2020-02-13 | 16:27 | 49.918
2020-02-13 | 16:27 | 49.919
2020-02-13 | 16:27 | 49.921
2020-02-13 | 16:27 | 49.922
2020-02-13 | 16:27 | 49.922
2020-02-13 | 16:27 | 49.924
2020-02-13 | 16:27 | 49.921
2020-02-13 | 16:27 | 49.921
2020-02-13 | 16:27 | 49.92
2020-02-13 | 16:27 | 49.92
2020-02-13 | 16:27 | 49.919
2020-02-13 | 16:27 | 49.918
2020-02-13 | 16:27 | 49.92
2020-02-13 | 16:27 | 49.923
2020-02-13 | 16:27 | 49.927
2020-02-13 | 16:27 | 49.931
2020-02-13 | 16:27 | 49.934
2020-02-13 | 16:27 | 49.937
2020-02-13 | 16:28 | 49.941
2020-02-13 | 16:28 | 49.943
2020-02-13 | 16:28 | 49.947
2020-02-13 | 16:28 | 49.947
2020-02-13 | 16:28 | 49.947
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.948
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.95
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.95
2020-02-13 | 16:28 | 49.95
2020-02-13 | 16:28 | 49.95
2020-02-13 | 16:28 | 49.952
2020-02-13 | 16:28 | 49.951
2020-02-13 | 16:28 | 49.952
2020-02-13 | 16:28 | 49.954
2020-02-13 | 16:28 | 49.956
2020-02-13 | 16:28 | 49.957
2020-02-13 | 16:28 | 49.956
2020-02-13 | 16:28 | 49.956
2020-02-13 | 16:28 | 49.954
2020-02-13 | 16:28 | 49.953
2020-02-13 | 16:28 | 49.95
2020-02-13 | 16:28 | 49.949
2020-02-13 | 16:28 | 49.947
2020-02-13 | 16:28 | 49.948
2020-02-13 | 16:28 | 49.947
2020-02-13 | 16:28 | 49.95
2020-02-13 | 16:28 | 49.951
2020-02-13 | 16:28 | 49.953
2020-02-13 | 16:28 | 49.955
2020-02-13 | 16:28 | 49.957
2020-02-13 | 16:28 | 49.957
2020-02-13 | 16:28 | 49.956
2020-02-13 | 16:28 | 49.953
2020-02-13 | 16:28 | 49.952
2020-02-13 | 16:28 | 49.947
2020-02-13 | 16:28 | 49.943
2020-02-13 | 16:28 | 49.941
2020-02-13 | 16:28 | 49.94
2020-02-13 | 16:28 | 49.94
2020-02-13 | 16:28 | 49.941
2020-02-13 | 16:28 | 49.939
2020-02-13 | 16:28 | 49.938
2020-02-13 | 16:28 | 49.936
2020-02-13 | 16:28 | 49.934
2020-02-13 | 16:28 | 49.933
2020-02-13 | 16:28 | 49.931
2020-02-13 | 16:28 | 49.933
2020-02-13 | 16:28 | 49.93
2020-02-13 | 16:28 | 49.93
2020-02-13 | 16:28 | 49.93
2020-02-13 | 16:28 | 49.93
2020-02-13 | 16:28 | 49.93
2020-02-13 | 16:29 | 49.933
2020-02-13 | 16:29 | 49.936
2020-02-13 | 16:29 | 49.938
2020-02-13 | 16:29 | 49.936
2020-02-13 | 16:29 | 49.939
2020-02-13 | 16:29 | 49.94
2020-02-13 | 16:29 | 49.941
2020-02-13 | 16:29 | 49.942
2020-02-13 | 16:29 | 49.942
2020-02-13 | 16:29 | 49.944
2020-02-13 | 16:29 | 49.944
2020-02-13 | 16:29 | 49.946
2020-02-13 | 16:29 | 49.948
2020-02-13 | 16:29 | 49.948
2020-02-13 | 16:29 | 49.95
2020-02-13 | 16:29 | 49.951
2020-02-13 | 16:29 | 49.951
2020-02-13 | 16:29 | 49.954
2020-02-13 | 16:29 | 49.952
2020-02-13 | 16:29 | 49.951
2020-02-13 | 16:29 | 49.949
2020-02-13 | 16:29 | 49.948
2020-02-13 | 16:29 | 49.946
2020-02-13 | 16:29 | 49.945
2020-02-13 | 16:29 | 49.944
2020-02-13 | 16:29 | 49.942
2020-02-13 | 16:29 | 49.941
2020-02-13 | 16:29 | 49.943
2020-02-13 | 16:29 | 49.944
2020-02-13 | 16:29 | 49.944
2020-02-13 | 16:29 | 49.946
2020-02-13 | 16:29 | 49.946
2020-02-13 | 16:29 | 49.948
2020-02-13 | 16:29 | 49.952
2020-02-13 | 16:29 | 49.955
2020-02-13 | 16:29 | 49.96
2020-02-13 | 16:29 | 49.962
2020-02-13 | 16:29 | 49.962
2020-02-13 | 16:29 | 49.963
2020-02-13 | 16:29 | 49.963
2020-02-13 | 16:29 | 49.964
2020-02-13 | 16:29 | 49.965
2020-02-13 | 16:29 | 49.966
2020-02-13 | 16:29 | 49.967
2020-02-13 | 16:29 | 49.966
2020-02-13 | 16:29 | 49.964
2020-02-13 | 16:29 | 49.963
2020-02-13 | 16:29 | 49.962
2020-02-13 | 16:29 | 49.959
2020-02-13 | 16:29 | 49.955
2020-02-13 | 16:29 | 49.953
2020-02-13 | 16:29 | 49.95
2020-02-13 | 16:29 | 49.948
2020-02-13 | 16:29 | 49.945
2020-02-13 | 16:29 | 49.943
2020-02-13 | 16:29 | 49.941
2020-02-13 | 16:29 | 49.939
2020-02-13 | 16:29 | 49.938
2020-02-13 | 16:29 | 49.936
2020-02-13 | 16:29 | 49.933
2020-02-13 | 16:30 | 49.933
2020-02-13 | 16:30 | 49.932
2020-02-13 | 16:30 | 49.931
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.93
2020-02-13 | 16:30 | 49.931
2020-02-13 | 16:30 | 49.93
2020-02-13 | 16:30 | 49.93
2020-02-13 | 16:30 | 49.928
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.931
2020-02-13 | 16:30 | 49.933
2020-02-13 | 16:30 | 49.934
2020-02-13 | 16:30 | 49.935
2020-02-13 | 16:30 | 49.935
2020-02-13 | 16:30 | 49.937
2020-02-13 | 16:30 | 49.938
2020-02-13 | 16:30 | 49.939
2020-02-13 | 16:30 | 49.939
2020-02-13 | 16:30 | 49.94
2020-02-13 | 16:30 | 49.941
2020-02-13 | 16:30 | 49.941
2020-02-13 | 16:30 | 49.942
2020-02-13 | 16:30 | 49.94
2020-02-13 | 16:30 | 49.94
2020-02-13 | 16:30 | 49.938
2020-02-13 | 16:30 | 49.936
2020-02-13 | 16:30 | 49.935
2020-02-13 | 16:30 | 49.935
2020-02-13 | 16:30 | 49.934
2020-02-13 | 16:30 | 49.931
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.925
2020-02-13 | 16:30 | 49.924
2020-02-13 | 16:30 | 49.925
2020-02-13 | 16:30 | 49.925
2020-02-13 | 16:30 | 49.927
2020-02-13 | 16:30 | 49.929
2020-02-13 | 16:30 | 49.928
2020-02-13 | 16:30 | 49.928
2020-02-13 | 16:30 | 49.926
2020-02-13 | 16:30 | 49.927
2020-02-13 | 16:30 | 49.927
2020-02-13 | 16:30 | 49.93
2020-02-13 | 16:30 | 49.934
2020-02-13 | 16:30 | 49.939
2020-02-13 | 16:30 | 49.944
2020-02-13 | 16:30 | 49.952
2020-02-13 | 16:30 | 49.959
2020-02-13 | 16:30 | 49.966
2020-02-13 | 16:30 | 49.976
2020-02-13 | 16:30 | 49.982
2020-02-13 | 16:30 | 49.99
2020-02-13 | 16:30 | 49.998
2020-02-13 | 16:30 | 50.007
2020-02-13 | 16:31 | 50.015
2020-02-13 | 16:31 | 50.024
2020-02-13 | 16:31 | 50.031
2020-02-13 | 16:31 | 50.036
2020-02-13 | 16:31 | 50.039
2020-02-13 | 16:31 | 50.045
2020-02-13 | 16:31 | 50.049
2020-02-13 | 16:31 | 50.053
2020-02-13 | 16:31 | 50.058
2020-02-13 | 16:31 | 50.06
2020-02-13 | 16:31 | 50.061
2020-02-13 | 16:31 | 50.06
2020-02-13 | 16:31 | 50.058
2020-02-13 | 16:31 | 50.056
2020-02-13 | 16:31 | 50.057
2020-02-13 | 16:31 | 50.058
2020-02-13 | 16:31 | 50.058
2020-02-13 | 16:31 | 50.06
2020-02-13 | 16:31 | 50.06
2020-02-13 | 16:31 | 50.06
2020-02-13 | 16:31 | 50.061
2020-02-13 | 16:31 | 50.06
2020-02-13 | 16:31 | 50.062
2020-02-13 | 16:31 | 50.064
2020-02-13 | 16:31 | 50.065
2020-02-13 | 16:31 | 50.069
2020-02-13 | 16:31 | 50.07
2020-02-13 | 16:31 | 50.072
2020-02-13 | 16:31 | 50.073
2020-02-13 | 16:31 | 50.075
2020-02-13 | 16:31 | 50.075
2020-02-13 | 16:31 | 50.077
2020-02-13 | 16:31 | 50.076
2020-02-13 | 16:31 | 50.076
2020-02-13 | 16:31 | 50.077
2020-02-13 | 16:31 | 50.077
2020-02-13 | 16:31 | 50.076
2020-02-13 | 16:31 | 50.076
2020-02-13 | 16:31 | 50.078
2020-02-13 | 16:31 | 50.079
2020-02-13 | 16:31 | 50.08
2020-02-13 | 16:31 | 50.082
2020-02-13 | 16:31 | 50.083
2020-02-13 | 16:31 | 50.085
2020-02-13 | 16:31 | 50.084
2020-02-13 | 16:31 | 50.086
2020-02-13 | 16:31 | 50.085
2020-02-13 | 16:31 | 50.084
2020-02-13 | 16:31 | 50.084
2020-02-13 | 16:31 | 50.086
2020-02-13 | 16:31 | 50.087
2020-02-13 | 16:31 | 50.089
2020-02-13 | 16:31 | 50.09
2020-02-13 | 16:31 | 50.091
2020-02-13 | 16:31 | 50.09
2020-02-13 | 16:31 | 50.089
2020-02-13 | 16:31 | 50.087
2020-02-13 | 16:31 | 50.085
2020-02-13 | 16:31 | 50.085
2020-02-13 | 16:31 | 50.085
2020-02-13 | 16:32 | 50.085
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.085
2020-02-13 | 16:32 | 50.085
2020-02-13 | 16:32 | 50.084
2020-02-13 | 16:32 | 50.084
2020-02-13 | 16:32 | 50.083
2020-02-13 | 16:32 | 50.084
2020-02-13 | 16:32 | 50.083
2020-02-13 | 16:32 | 50.083
2020-02-13 | 16:32 | 50.083
2020-02-13 | 16:32 | 50.085
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.088
2020-02-13 | 16:32 | 50.09
2020-02-13 | 16:32 | 50.09
2020-02-13 | 16:32 | 50.09
2020-02-13 | 16:32 | 50.09
2020-02-13 | 16:32 | 50.089
2020-02-13 | 16:32 | 50.088
2020-02-13 | 16:32 | 50.089
2020-02-13 | 16:32 | 50.087
2020-02-13 | 16:32 | 50.087
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.086
2020-02-13 | 16:32 | 50.085
2020-02-13 | 16:32 | 50.083
2020-02-13 | 16:32 | 50.079
2020-02-13 | 16:32 | 50.076
2020-02-13 | 16:32 | 50.075
2020-02-13 | 16:32 | 50.073
2020-02-13 | 16:32 | 50.071
2020-02-13 | 16:32 | 50.07
2020-02-13 | 16:32 | 50.069
2020-02-13 | 16:32 | 50.068
2020-02-13 | 16:32 | 50.066
2020-02-13 | 16:32 | 50.064
2020-02-13 | 16:32 | 50.061
2020-02-13 | 16:32 | 50.059
2020-02-13 | 16:32 | 50.058
2020-02-13 | 16:32 | 50.056
2020-02-13 | 16:32 | 50.057
2020-02-13 | 16:32 | 50.057
2020-02-13 | 16:32 | 50.057
2020-02-13 | 16:32 | 50.056
2020-02-13 | 16:32 | 50.057
2020-02-13 | 16:32 | 50.059
2020-02-13 | 16:32 | 50.06
2020-02-13 | 16:32 | 50.061
2020-02-13 | 16:32 | 50.064
2020-02-13 | 16:32 | 50.067
2020-02-13 | 16:32 | 50.067
2020-02-13 | 16:32 | 50.068
2020-02-13 | 16:32 | 50.07
2020-02-13 | 16:32 | 50.071
2020-02-13 | 16:32 | 50.072
2020-02-13 | 16:33 | 50.075
2020-02-13 | 16:33 | 50.076
2020-02-13 | 16:33 | 50.078
2020-02-13 | 16:33 | 50.081
2020-02-13 | 16:33 | 50.083
2020-02-13 | 16:33 | 50.085
2020-02-13 | 16:33 | 50.086
2020-02-13 | 16:33 | 50.089
2020-02-13 | 16:33 | 50.091
2020-02-13 | 16:33 | 50.091
2020-02-13 | 16:33 | 50.09
2020-02-13 | 16:33 | 50.09
2020-02-13 | 16:33 | 50.089
2020-02-13 | 16:33 | 50.087
2020-02-13 | 16:33 | 50.084
2020-02-13 | 16:33 | 50.084
2020-02-13 | 16:33 | 50.082
2020-02-13 | 16:33 | 50.081
2020-02-13 | 16:33 | 50.08
2020-02-13 | 16:33 | 50.078
2020-02-13 | 16:33 | 50.077
2020-02-13 | 16:33 | 50.077
2020-02-13 | 16:33 | 50.075
2020-02-13 | 16:33 | 50.074
2020-02-13 | 16:33 | 50.074
2020-02-13 | 16:33 | 50.071
2020-02-13 | 16:33 | 50.07
2020-02-13 | 16:33 | 50.069
2020-02-13 | 16:33 | 50.069
2020-02-13 | 16:33 | 50.07
2020-02-13 | 16:33 | 50.072
2020-02-13 | 16:33 | 50.074
2020-02-13 | 16:33 | 50.074
2020-02-13 | 16:33 | 50.072
2020-02-13 | 16:33 | 50.07
2020-02-13 | 16:33 | 50.067
2020-02-13 | 16:33 | 50.067
2020-02-13 | 16:33 | 50.065
2020-02-13 | 16:33 | 50.062
2020-02-13 | 16:33 | 50.059
2020-02-13 | 16:33 | 50.058
2020-02-13 | 16:33 | 50.056
2020-02-13 | 16:33 | 50.058
2020-02-13 | 16:33 | 50.062
2020-02-13 | 16:33 | 50.064
2020-02-13 | 16:33 | 50.065
2020-02-13 | 16:33 | 50.068
2020-02-13 | 16:33 | 50.072
2020-02-13 | 16:33 | 50.075
2020-02-13 | 16:33 | 50.079
2020-02-13 | 16:33 | 50.08
2020-02-13 | 16:33 | 50.082
2020-02-13 | 16:33 | 50.082
2020-02-13 | 16:33 | 50.08
2020-02-13 | 16:33 | 50.08
2020-02-13 | 16:33 | 50.08
2020-02-13 | 16:33 | 50.081
2020-02-13 | 16:33 | 50.082
2020-02-13 | 16:33 | 50.083
2020-02-13 | 16:33 | 50.087
2020-02-13 | 16:34 | 50.089
2020-02-13 | 16:34 | 50.089
2020-02-13 | 16:34 | 50.09
2020-02-13 | 16:34 | 50.09
2020-02-13 | 16:34 | 50.091
2020-02-13 | 16:34 | 50.09
2020-02-13 | 16:34 | 50.09
2020-02-13 | 16:34 | 50.087
2020-02-13 | 16:34 | 50.084
2020-02-13 | 16:34 | 50.081
2020-02-13 | 16:34 | 50.078
2020-02-13 | 16:34 | 50.074
2020-02-13 | 16:34 | 50.071
2020-02-13 | 16:34 | 50.067
2020-02-13 | 16:34 | 50.064
2020-02-13 | 16:34 | 50.062
2020-02-13 | 16:34 | 50.063
2020-02-13 | 16:34 | 50.062
2020-02-13 | 16:34 | 50.062
2020-02-13 | 16:34 | 50.062
2020-02-13 | 16:34 | 50.061
2020-02-13 | 16:34 | 50.06
2020-02-13 | 16:34 | 50.06
2020-02-13 | 16:34 | 50.06
2020-02-13 | 16:34 | 50.06
2020-02-13 | 16:34 | 50.061
2020-02-13 | 16:34 | 50.06
2020-02-13 | 16:34 | 50.056
2020-02-13 | 16:34 | 50.054
2020-02-13 | 16:34 | 50.051
2020-02-13 | 16:34 | 50.05
2020-02-13 | 16:34 | 50.048
2020-02-13 | 16:34 | 50.047
2020-02-13 | 16:34 | 50.046
2020-02-13 | 16:34 | 50.048
2020-02-13 | 16:34 | 50.047
2020-02-13 | 16:34 | 50.045
2020-02-13 | 16:34 | 50.045
2020-02-13 | 16:34 | 50.044
2020-02-13 | 16:34 | 50.04
2020-02-13 | 16:34 | 50.039
2020-02-13 | 16:34 | 50.038
2020-02-13 | 16:34 | 50.038
2020-02-13 | 16:34 | 50.036
2020-02-13 | 16:34 | 50.036
2020-02-13 | 16:34 | 50.037
2020-02-13 | 16:34 | 50.035
2020-02-13 | 16:34 | 50.033
2020-02-13 | 16:34 | 50.033
2020-02-13 | 16:34 | 50.031
2020-02-13 | 16:34 | 50.032
2020-02-13 | 16:34 | 50.033
2020-02-13 | 16:34 | 50.031
2020-02-13 | 16:34 | 50.03
2020-02-13 | 16:34 | 50.027
2020-02-13 | 16:34 | 50.027
2020-02-13 | 16:34 | 50.026
2020-02-13 | 16:34 | 50.025
2020-02-13 | 16:34 | 50.024
2020-02-13 | 16:34 | 50.024
2020-02-13 | 16:34 | 50.025
2020-02-13 | 16:35 | 50.024
2020-02-13 | 16:35 | 50.026
2020-02-13 | 16:35 | 50.025
2020-02-13 | 16:35 | 50.024
2020-02-13 | 16:35 | 50.023
2020-02-13 | 16:35 | 50.023
2020-02-13 | 16:35 | 50.023
2020-02-13 | 16:35 | 50.021
2020-02-13 | 16:35 | 50.021
2020-02-13 | 16:35 | 50.019
2020-02-13 | 16:35 | 50.018
2020-02-13 | 16:35 | 50.018
2020-02-13 | 16:35 | 50.016
2020-02-13 | 16:35 | 50.016
2020-02-13 | 16:35 | 50.014
2020-02-13 | 16:35 | 50.014
2020-02-13 | 16:35 | 50.013
2020-02-13 | 16:35 | 50.014
2020-02-13 | 16:35 | 50.017
2020-02-13 | 16:35 | 50.016
2020-02-13 | 16:35 | 50.018
2020-02-13 | 16:35 | 50.02
2020-02-13 | 16:35 | 50.02
2020-02-13 | 16:35 | 50.02
2020-02-13 | 16:35 | 50.02
2020-02-13 | 16:35 | 50.015
2020-02-13 | 16:35 | 50.016
2020-02-13 | 16:35 | 50.014
2020-02-13 | 16:35 | 50.016
2020-02-13 | 16:35 | 50.017
2020-02-13 | 16:35 | 50.017
2020-02-13 | 16:35 | 50.023
2020-02-13 | 16:35 | 50.021
2020-02-13 | 16:35 | 50.022
2020-02-13 | 16:35 | 50.023
2020-02-13 | 16:35 | 50.024
2020-02-13 | 16:35 | 50.024
2020-02-13 | 16:35 | 50.023
2020-02-13 | 16:35 | 50.02
2020-02-13 | 16:35 | 50.017
2020-02-13 | 16:35 | 50.013
2020-02-13 | 16:35 | 50.01
2020-02-13 | 16:35 | 50.009
2020-02-13 | 16:35 | 50.011
2020-02-13 | 16:35 | 50.008
2020-02-13 | 16:35 | 50.009
2020-02-13 | 16:35 | 50.009
2020-02-13 | 16:35 | 50.008
2020-02-13 | 16:35 | 50.006
2020-02-13 | 16:35 | 50.003
2020-02-13 | 16:35 | 49.999
2020-02-13 | 16:35 | 49.994
2020-02-13 | 16:35 | 49.989
2020-02-13 | 16:35 | 49.984
2020-02-13 | 16:35 | 49.981
2020-02-13 | 16:35 | 49.98
2020-02-13 | 16:35 | 49.979
2020-02-13 | 16:35 | 49.98
2020-02-13 | 16:35 | 49.983
2020-02-13 | 16:35 | 49.986
2020-02-13 | 16:36 | 49.989
2020-02-13 | 16:36 | 49.991
2020-02-13 | 16:36 | 49.99
2020-02-13 | 16:36 | 49.989
2020-02-13 | 16:36 | 49.99
2020-02-13 | 16:36 | 49.99
2020-02-13 | 16:36 | 49.99
2020-02-13 | 16:36 | 49.989
2020-02-13 | 16:36 | 49.986
2020-02-13 | 16:36 | 49.983
2020-02-13 | 16:36 | 49.981
2020-02-13 | 16:36 | 49.979
2020-02-13 | 16:36 | 49.977
2020-02-13 | 16:36 | 49.973
2020-02-13 | 16:36 | 49.97
2020-02-13 | 16:36 | 49.968
2020-02-13 | 16:36 | 49.966
2020-02-13 | 16:36 | 49.964
2020-02-13 | 16:36 | 49.962
2020-02-13 | 16:36 | 49.962
2020-02-13 | 16:36 | 49.963
2020-02-13 | 16:36 | 49.962
2020-02-13 | 16:36 | 49.963
2020-02-13 | 16:36 | 49.964
2020-02-13 | 16:36 | 49.961
2020-02-13 | 16:36 | 49.961
2020-02-13 | 16:36 | 49.959
2020-02-13 | 16:36 | 49.955
2020-02-13 | 16:36 | 49.953
2020-02-13 | 16:36 | 49.95
2020-02-13 | 16:36 | 49.948
2020-02-13 | 16:36 | 49.946
2020-02-13 | 16:36 | 49.941
2020-02-13 | 16:36 | 49.94
2020-02-13 | 16:36 | 49.939
2020-02-13 | 16:36 | 49.938
2020-02-13 | 16:36 | 49.937
2020-02-13 | 16:36 | 49.937
2020-02-13 | 16:36 | 49.939
2020-02-13 | 16:36 | 49.942
2020-02-13 | 16:36 | 49.946
2020-02-13 | 16:36 | 49.951
2020-02-13 | 16:36 | 49.956
2020-02-13 | 16:36 | 49.96
2020-02-13 | 16:36 | 49.965
2020-02-13 | 16:36 | 49.968
2020-02-13 | 16:36 | 49.969
2020-02-13 | 16:36 | 49.973
2020-02-13 | 16:36 | 49.975
2020-02-13 | 16:36 | 49.977
2020-02-13 | 16:36 | 49.98
2020-02-13 | 16:36 | 49.98
2020-02-13 | 16:36 | 49.983
2020-02-13 | 16:36 | 49.985
2020-02-13 | 16:36 | 49.986
2020-02-13 | 16:36 | 49.987
2020-02-13 | 16:36 | 49.989
2020-02-13 | 16:36 | 49.991
2020-02-13 | 16:36 | 49.991
2020-02-13 | 16:36 | 49.993
2020-02-13 | 16:37 | 49.994
2020-02-13 | 16:37 | 49.996
2020-02-13 | 16:37 | 49.998
2020-02-13 | 16:37 | 49.999
2020-02-13 | 16:37 | 49.998
2020-02-13 | 16:37 | 49.998
2020-02-13 | 16:37 | 49.998
2020-02-13 | 16:37 | 49.997
2020-02-13 | 16:37 | 49.997
2020-02-13 | 16:37 | 49.997
2020-02-13 | 16:37 | 49.995
2020-02-13 | 16:37 | 49.995
2020-02-13 | 16:37 | 49.994
2020-02-13 | 16:37 | 49.993
2020-02-13 | 16:37 | 49.992
2020-02-13 | 16:37 | 49.993
2020-02-13 | 16:37 | 49.992
2020-02-13 | 16:37 | 49.989
2020-02-13 | 16:37 | 49.986
2020-02-13 | 16:37 | 49.984
2020-02-13 | 16:37 | 49.981
2020-02-13 | 16:37 | 49.978
2020-02-13 | 16:37 | 49.975
2020-02-13 | 16:37 | 49.973
2020-02-13 | 16:37 | 49.969
2020-02-13 | 16:37 | 49.966
2020-02-13 | 16:37 | 49.963
2020-02-13 | 16:37 | 49.963
2020-02-13 | 16:37 | 49.963
2020-02-13 | 16:37 | 49.96
2020-02-13 | 16:37 | 49.959
2020-02-13 | 16:37 | 49.956
2020-02-13 | 16:37 | 49.953
2020-02-13 | 16:37 | 49.952
2020-02-13 | 16:37 | 49.95
2020-02-13 | 16:37 | 49.949
2020-02-13 | 16:37 | 49.947
2020-02-13 | 16:37 | 49.943
2020-02-13 | 16:37 | 49.942
2020-02-13 | 16:37 | 49.941
2020-02-13 | 16:37 | 49.94
2020-02-13 | 16:37 | 49.939
2020-02-13 | 16:37 | 49.94
2020-02-13 | 16:37 | 49.941
2020-02-13 | 16:37 | 49.943
2020-02-13 | 16:37 | 49.944
2020-02-13 | 16:37 | 49.945
2020-02-13 | 16:37 | 49.947
2020-02-13 | 16:37 | 49.947
2020-02-13 | 16:37 | 49.945
2020-02-13 | 16:37 | 49.943
2020-02-13 | 16:37 | 49.938
2020-02-13 | 16:37 | 49.938
2020-02-13 | 16:37 | 49.936
2020-02-13 | 16:37 | 49.936
2020-02-13 | 16:37 | 49.936
2020-02-13 | 16:37 | 49.937
2020-02-13 | 16:37 | 49.94
2020-02-13 | 16:37 | 49.943
2020-02-13 | 16:38 | 49.945
2020-02-13 | 16:38 | 49.948
2020-02-13 | 16:38 | 49.95
2020-02-13 | 16:38 | 49.952
2020-02-13 | 16:38 | 49.953
2020-02-13 | 16:38 | 49.954
2020-02-13 | 16:38 | 49.956
2020-02-13 | 16:38 | 49.953
2020-02-13 | 16:38 | 49.953
2020-02-13 | 16:38 | 49.952
2020-02-13 | 16:38 | 49.952
2020-02-13 | 16:38 | 49.952
2020-02-13 | 16:38 | 49.952
2020-02-13 | 16:38 | 49.954
2020-02-13 | 16:38 | 49.953
2020-02-13 | 16:38 | 49.953
2020-02-13 | 16:38 | 49.95
2020-02-13 | 16:38 | 49.948
2020-02-13 | 16:38 | 49.946
2020-02-13 | 16:38 | 49.944
2020-02-13 | 16:38 | 49.941
2020-02-13 | 16:38 | 49.943
2020-02-13 | 16:38 | 49.944
2020-02-13 | 16:38 | 49.944
2020-02-13 | 16:38 | 49.944
2020-02-13 | 16:38 | 49.945
2020-02-13 | 16:38 | 49.947
2020-02-13 | 16:38 | 49.949
2020-02-13 | 16:38 | 49.95
2020-02-13 | 16:38 | 49.95
2020-02-13 | 16:38 | 49.95
2020-02-13 | 16:38 | 49.95
2020-02-13 | 16:38 | 49.949
2020-02-13 | 16:38 | 49.948
2020-02-13 | 16:38 | 49.947
2020-02-13 | 16:38 | 49.944
2020-02-13 | 16:38 | 49.942
2020-02-13 | 16:38 | 49.941
2020-02-13 | 16:38 | 49.941
2020-02-13 | 16:38 | 49.939
2020-02-13 | 16:38 | 49.939
2020-02-13 | 16:38 | 49.939
2020-02-13 | 16:38 | 49.938
2020-02-13 | 16:38 | 49.938
2020-02-13 | 16:38 | 49.937
2020-02-13 | 16:38 | 49.936
2020-02-13 | 16:38 | 49.935
2020-02-13 | 16:38 | 49.934
2020-02-13 | 16:38 | 49.934
2020-02-13 | 16:38 | 49.932
2020-02-13 | 16:38 | 49.93
2020-02-13 | 16:38 | 49.929
2020-02-13 | 16:38 | 49.929
2020-02-13 | 16:38 | 49.929
2020-02-13 | 16:38 | 49.929
2020-02-13 | 16:38 | 49.93
2020-02-13 | 16:38 | 49.931
2020-02-13 | 16:38 | 49.932
2020-02-13 | 16:38 | 49.931
2020-02-13 | 16:38 | 49.931
2020-02-13 | 16:38 | 49.932
2020-02-13 | 16:39 | 49.934
2020-02-13 | 16:39 | 49.935
2020-02-13 | 16:39 | 49.937
2020-02-13 | 16:39 | 49.937
2020-02-13 | 16:39 | 49.939
2020-02-13 | 16:39 | 49.941
2020-02-13 | 16:39 | 49.944
2020-02-13 | 16:39 | 49.947
2020-02-13 | 16:39 | 49.947
2020-02-13 | 16:39 | 49.947
2020-02-13 | 16:39 | 49.946
2020-02-13 | 16:39 | 49.946
2020-02-13 | 16:39 | 49.945
2020-02-13 | 16:39 | 49.944
2020-02-13 | 16:39 | 49.942
2020-02-13 | 16:39 | 49.94
2020-02-13 | 16:39 | 49.938
2020-02-13 | 16:39 | 49.936
2020-02-13 | 16:39 | 49.933
2020-02-13 | 16:39 | 49.93
2020-02-13 | 16:39 | 49.927
2020-02-13 | 16:39 | 49.924
2020-02-13 | 16:39 | 49.921
2020-02-13 | 16:39 | 49.92
2020-02-13 | 16:39 | 49.918
2020-02-13 | 16:39 | 49.917
2020-02-13 | 16:39 | 49.919
2020-02-13 | 16:39 | 49.921
2020-02-13 | 16:39 | 49.921
2020-02-13 | 16:39 | 49.92
2020-02-13 | 16:39 | 49.919
2020-02-13 | 16:39 | 49.919
2020-02-13 | 16:39 | 49.92
2020-02-13 | 16:39 | 49.921
2020-02-13 | 16:39 | 49.922
2020-02-13 | 16:39 | 49.922
2020-02-13 | 16:39 | 49.922
2020-02-13 | 16:39 | 49.922
2020-02-13 | 16:39 | 49.922
2020-02-13 | 16:39 | 49.92
2020-02-13 | 16:39 | 49.918
2020-02-13 | 16:39 | 49.916
2020-02-13 | 16:39 | 49.915
2020-02-13 | 16:39 | 49.915
2020-02-13 | 16:39 | 49.916
2020-02-13 | 16:39 | 49.915
2020-02-13 | 16:39 | 49.918
2020-02-13 | 16:39 | 49.915
2020-02-13 | 16:39 | 49.914
2020-02-13 | 16:39 | 49.914
2020-02-13 | 16:39 | 49.915
2020-02-13 | 16:39 | 49.916
2020-02-13 | 16:39 | 49.916
2020-02-13 | 16:39 | 49.916
2020-02-13 | 16:39 | 49.916
2020-02-13 | 16:39 | 49.913
2020-02-13 | 16:39 | 49.913
2020-02-13 | 16:39 | 49.914
2020-02-13 | 16:39 | 49.913
2020-02-13 | 16:40 | 49.912
2020-02-13 | 16:40 | 49.915
2020-02-13 | 16:40 | 49.917
2020-02-13 | 16:40 | 49.919
2020-02-13 | 16:40 | 49.92
2020-02-13 | 16:40 | 49.921
2020-02-13 | 16:40 | 49.922
2020-02-13 | 16:40 | 49.924
2020-02-13 | 16:40 | 49.928
2020-02-13 | 16:40 | 49.931
2020-02-13 | 16:40 | 49.931
2020-02-13 | 16:40 | 49.933
2020-02-13 | 16:40 | 49.936
2020-02-13 | 16:40 | 49.94
2020-02-13 | 16:40 | 49.943
2020-02-13 | 16:40 | 49.947
2020-02-13 | 16:40 | 49.949
2020-02-13 | 16:40 | 49.95
2020-02-13 | 16:40 | 49.953
2020-02-13 | 16:40 | 49.953
2020-02-13 | 16:40 | 49.951
2020-02-13 | 16:40 | 49.953
2020-02-13 | 16:40 | 49.952
2020-02-13 | 16:40 | 49.952
2020-02-13 | 16:40 | 49.953
2020-02-13 | 16:40 | 49.953
2020-02-13 | 16:40 | 49.954
2020-02-13 | 16:40 | 49.955
2020-02-13 | 16:40 | 49.954
2020-02-13 | 16:40 | 49.952
2020-02-13 | 16:40 | 49.95
2020-02-13 | 16:40 | 49.95
2020-02-13 | 16:40 | 49.947
2020-02-13 | 16:40 | 49.946
2020-02-13 | 16:40 | 49.945
2020-02-13 | 16:40 | 49.943
2020-02-13 | 16:40 | 49.941
2020-02-13 | 16:40 | 49.94
2020-02-13 | 16:40 | 49.939
2020-02-13 | 16:40 | 49.94
2020-02-13 | 16:40 | 49.939
2020-02-13 | 16:40 | 49.939
2020-02-13 | 16:40 | 49.938
2020-02-13 | 16:40 | 49.938
2020-02-13 | 16:40 | 49.937
2020-02-13 | 16:40 | 49.935
2020-02-13 | 16:40 | 49.934
2020-02-13 | 16:40 | 49.933
2020-02-13 | 16:40 | 49.932
2020-02-13 | 16:40 | 49.929
2020-02-13 | 16:40 | 49.927
2020-02-13 | 16:40 | 49.922
2020-02-13 | 16:40 | 49.921
2020-02-13 | 16:40 | 49.917
2020-02-13 | 16:40 | 49.916
2020-02-13 | 16:40 | 49.915
2020-02-13 | 16:40 | 49.916
2020-02-13 | 16:40 | 49.917
2020-02-13 | 16:40 | 49.918
2020-02-13 | 16:40 | 49.92
2020-02-13 | 16:40 | 49.925
2020-02-13 | 16:41 | 49.929
2020-02-13 | 16:41 | 49.932
2020-02-13 | 16:41 | 49.934
2020-02-13 | 16:41 | 49.939
2020-02-13 | 16:41 | 49.94
2020-02-13 | 16:41 | 49.942
2020-02-13 | 16:41 | 49.941
2020-02-13 | 16:41 | 49.946
2020-02-13 | 16:41 | 49.947
2020-02-13 | 16:41 | 49.948
2020-02-13 | 16:41 | 49.947
2020-02-13 | 16:41 | 49.945
2020-02-13 | 16:41 | 49.943
2020-02-13 | 16:41 | 49.943
2020-02-13 | 16:41 | 49.942
2020-02-13 | 16:41 | 49.941
2020-02-13 | 16:41 | 49.937
2020-02-13 | 16:41 | 49.934
2020-02-13 | 16:41 | 49.933
2020-02-13 | 16:41 | 49.931
2020-02-13 | 16:41 | 49.933
2020-02-13 | 16:41 | 49.934
2020-02-13 | 16:41 | 49.936
2020-02-13 | 16:41 | 49.935
2020-02-13 | 16:41 | 49.933
2020-02-13 | 16:41 | 49.932
2020-02-13 | 16:41 | 49.93
2020-02-13 | 16:41 | 49.928
2020-02-13 | 16:41 | 49.925
2020-02-13 | 16:41 | 49.921
2020-02-13 | 16:41 | 49.919
2020-02-13 | 16:41 | 49.914
2020-02-13 | 16:41 | 49.912
2020-02-13 | 16:41 | 49.915
2020-02-13 | 16:41 | 49.915
2020-02-13 | 16:41 | 49.917
2020-02-13 | 16:41 | 49.918
2020-02-13 | 16:41 | 49.92
2020-02-13 | 16:41 | 49.923
2020-02-13 | 16:41 | 49.927
2020-02-13 | 16:41 | 49.932
2020-02-13 | 16:41 | 49.936
2020-02-13 | 16:41 | 49.939
2020-02-13 | 16:41 | 49.939
2020-02-13 | 16:41 | 49.94
2020-02-13 | 16:41 | 49.938
2020-02-13 | 16:41 | 49.937
2020-02-13 | 16:41 | 49.936
2020-02-13 | 16:41 | 49.933
2020-02-13 | 16:41 | 49.932
2020-02-13 | 16:41 | 49.932
2020-02-13 | 16:41 | 49.932
2020-02-13 | 16:41 | 49.93
2020-02-13 | 16:41 | 49.929
2020-02-13 | 16:41 | 49.928
2020-02-13 | 16:41 | 49.927
2020-02-13 | 16:41 | 49.925
2020-02-13 | 16:41 | 49.923
2020-02-13 | 16:41 | 49.921
2020-02-13 | 16:42 | 49.918
2020-02-13 | 16:42 | 49.915
2020-02-13 | 16:42 | 49.913
2020-02-13 | 16:42 | 49.911
2020-02-13 | 16:42 | 49.91
2020-02-13 | 16:42 | 49.909
2020-02-13 | 16:42 | 49.911
2020-02-13 | 16:42 | 49.911
2020-02-13 | 16:42 | 49.913
2020-02-13 | 16:42 | 49.912
2020-02-13 | 16:42 | 49.915
2020-02-13 | 16:42 | 49.914
2020-02-13 | 16:42 | 49.917
2020-02-13 | 16:42 | 49.916
2020-02-13 | 16:42 | 49.918
2020-02-13 | 16:42 | 49.918
2020-02-13 | 16:42 | 49.92
2020-02-13 | 16:42 | 49.92
2020-02-13 | 16:42 | 49.922
2020-02-13 | 16:42 | 49.924
2020-02-13 | 16:42 | 49.928
2020-02-13 | 16:42 | 49.928
2020-02-13 | 16:42 | 49.932
2020-02-13 | 16:42 | 49.931
2020-02-13 | 16:42 | 49.931
2020-02-13 | 16:42 | 49.932
2020-02-13 | 16:42 | 49.933
2020-02-13 | 16:42 | 49.935
2020-02-13 | 16:42 | 49.938
2020-02-13 | 16:42 | 49.939
2020-02-13 | 16:42 | 49.942
2020-02-13 | 16:42 | 49.944
2020-02-13 | 16:42 | 49.948
2020-02-13 | 16:42 | 49.948
2020-02-13 | 16:42 | 49.95
2020-02-13 | 16:42 | 49.952
2020-02-13 | 16:42 | 49.957
2020-02-13 | 16:42 | 49.96
2020-02-13 | 16:42 | 49.965
2020-02-13 | 16:42 | 49.97
2020-02-13 | 16:42 | 49.976
2020-02-13 | 16:42 | 49.979
2020-02-13 | 16:42 | 49.984
2020-02-13 | 16:42 | 49.99
2020-02-13 | 16:42 | 49.996
2020-02-13 | 16:42 | 50.002
2020-02-13 | 16:42 | 50.007
2020-02-13 | 16:42 | 50.011
2020-02-13 | 16:42 | 50.016
2020-02-13 | 16:42 | 50.02
2020-02-13 | 16:42 | 50.022
2020-02-13 | 16:42 | 50.023
2020-02-13 | 16:42 | 50.027
2020-02-13 | 16:42 | 50.03
2020-02-13 | 16:42 | 50.033
2020-02-13 | 16:42 | 50.036
2020-02-13 | 16:42 | 50.039
2020-02-13 | 16:42 | 50.042
2020-02-13 | 16:42 | 50.045
2020-02-13 | 16:42 | 50.047
2020-02-13 | 16:42 | 50.05
2020-02-13 | 16:43 | 50.052
2020-02-13 | 16:43 | 50.052
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.052
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.051
2020-02-13 | 16:43 | 50.051
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.051
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.048
2020-02-13 | 16:43 | 50.049
2020-02-13 | 16:43 | 50.049
2020-02-13 | 16:43 | 50.046
2020-02-13 | 16:43 | 50.045
2020-02-13 | 16:43 | 50.044
2020-02-13 | 16:43 | 50.042
2020-02-13 | 16:43 | 50.043
2020-02-13 | 16:43 | 50.043
2020-02-13 | 16:43 | 50.045
2020-02-13 | 16:43 | 50.044
2020-02-13 | 16:43 | 50.043
2020-02-13 | 16:43 | 50.045
2020-02-13 | 16:43 | 50.047
2020-02-13 | 16:43 | 50.048
2020-02-13 | 16:43 | 50.049
2020-02-13 | 16:43 | 50.049
2020-02-13 | 16:43 | 50.051
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.053
2020-02-13 | 16:43 | 50.052
2020-02-13 | 16:43 | 50.052
2020-02-13 | 16:43 | 50.052
2020-02-13 | 16:43 | 50.051
2020-02-13 | 16:43 | 50.05
2020-02-13 | 16:43 | 50.049
2020-02-13 | 16:43 | 50.046
2020-02-13 | 16:43 | 50.044
2020-02-13 | 16:43 | 50.043
2020-02-13 | 16:43 | 50.041
2020-02-13 | 16:43 | 50.038
2020-02-13 | 16:43 | 50.037
2020-02-13 | 16:43 | 50.034
2020-02-13 | 16:43 | 50.035
2020-02-13 | 16:43 | 50.035
2020-02-13 | 16:43 | 50.032
2020-02-13 | 16:43 | 50.031
2020-02-13 | 16:43 | 50.033
2020-02-13 | 16:43 | 50.033
2020-02-13 | 16:43 | 50.033
2020-02-13 | 16:43 | 50.031
2020-02-13 | 16:43 | 50.028
2020-02-13 | 16:43 | 50.028
2020-02-13 | 16:43 | 50.027
2020-02-13 | 16:43 | 50.028
2020-02-13 | 16:43 | 50.028
2020-02-13 | 16:43 | 50.029
2020-02-13 | 16:43 | 50.029
2020-02-13 | 16:44 | 50.029
2020-02-13 | 16:44 | 50.027
2020-02-13 | 16:44 | 50.028
2020-02-13 | 16:44 | 50.025
2020-02-13 | 16:44 | 50.025
2020-02-13 | 16:44 | 50.026
2020-02-13 | 16:44 | 50.028
2020-02-13 | 16:44 | 50.031
2020-02-13 | 16:44 | 50.034
2020-02-13 | 16:44 | 50.037
2020-02-13 | 16:44 | 50.043
2020-02-13 | 16:44 | 50.049
2020-02-13 | 16:44 | 50.054
2020-02-13 | 16:44 | 50.06
2020-02-13 | 16:44 | 50.065
2020-02-13 | 16:44 | 50.068
2020-02-13 | 16:44 | 50.073
2020-02-13 | 16:44 | 50.076
2020-02-13 | 16:44 | 50.077
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.082
2020-02-13 | 16:44 | 50.083
2020-02-13 | 16:44 | 50.083
2020-02-13 | 16:44 | 50.083
2020-02-13 | 16:44 | 50.082
2020-02-13 | 16:44 | 50.08
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.077
2020-02-13 | 16:44 | 50.074
2020-02-13 | 16:44 | 50.072
2020-02-13 | 16:44 | 50.071
2020-02-13 | 16:44 | 50.072
2020-02-13 | 16:44 | 50.072
2020-02-13 | 16:44 | 50.075
2020-02-13 | 16:44 | 50.076
2020-02-13 | 16:44 | 50.078
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.083
2020-02-13 | 16:44 | 50.084
2020-02-13 | 16:44 | 50.083
2020-02-13 | 16:44 | 50.082
2020-02-13 | 16:44 | 50.082
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.08
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.08
2020-02-13 | 16:44 | 50.08
2020-02-13 | 16:44 | 50.081
2020-02-13 | 16:44 | 50.08
2020-02-13 | 16:44 | 50.079
2020-02-13 | 16:44 | 50.077
2020-02-13 | 16:45 | 50.077
2020-02-13 | 16:45 | 50.076
2020-02-13 | 16:45 | 50.076
2020-02-13 | 16:45 | 50.075
2020-02-13 | 16:45 | 50.073
2020-02-13 | 16:45 | 50.072
2020-02-13 | 16:45 | 50.068
2020-02-13 | 16:45 | 50.065
2020-02-13 | 16:45 | 50.063
2020-02-13 | 16:45 | 50.062
2020-02-13 | 16:45 | 50.061
2020-02-13 | 16:45 | 50.06
2020-02-13 | 16:45 | 50.059
2020-02-13 | 16:45 | 50.058
2020-02-13 | 16:45 | 50.056
2020-02-13 | 16:45 | 50.056
2020-02-13 | 16:45 | 50.057
2020-02-13 | 16:45 | 50.059
2020-02-13 | 16:45 | 50.062
2020-02-13 | 16:45 | 50.067
2020-02-13 | 16:45 | 50.07
2020-02-13 | 16:45 | 50.074
2020-02-13 | 16:45 | 50.076
2020-02-13 | 16:45 | 50.075
2020-02-13 | 16:45 | 50.075
2020-02-13 | 16:45 | 50.073
2020-02-13 | 16:45 | 50.07
2020-02-13 | 16:45 | 50.065
2020-02-13 | 16:45 | 50.061
2020-02-13 | 16:45 | 50.057
2020-02-13 | 16:45 | 50.05
2020-02-13 | 16:45 | 50.045
2020-02-13 | 16:45 | 50.042
2020-02-13 | 16:45 | 50.039
2020-02-13 | 16:45 | 50.037
2020-02-13 | 16:45 | 50.036
2020-02-13 | 16:45 | 50.034
2020-02-13 | 16:45 | 50.032
2020-02-13 | 16:45 | 50.035
2020-02-13 | 16:45 | 50.037
2020-02-13 | 16:45 | 50.037
2020-02-13 | 16:45 | 50.039
2020-02-13 | 16:45 | 50.042
2020-02-13 | 16:45 | 50.041
2020-02-13 | 16:45 | 50.044
2020-02-13 | 16:45 | 50.045
2020-02-13 | 16:45 | 50.043
2020-02-13 | 16:45 | 50.044
2020-02-13 | 16:45 | 50.042
2020-02-13 | 16:45 | 50.041
2020-02-13 | 16:45 | 50.04
2020-02-13 | 16:45 | 50.038
2020-02-13 | 16:45 | 50.038
2020-02-13 | 16:45 | 50.037
2020-02-13 | 16:45 | 50.036
2020-02-13 | 16:45 | 50.034
2020-02-13 | 16:45 | 50.031
2020-02-13 | 16:45 | 50.03
2020-02-13 | 16:45 | 50.028
2020-02-13 | 16:46 | 50.025
2020-02-13 | 16:46 | 50.026
2020-02-13 | 16:46 | 50.024
2020-02-13 | 16:46 | 50.025
2020-02-13 | 16:46 | 50.027
2020-02-13 | 16:46 | 50.033
2020-02-13 | 16:46 | 50.038
2020-02-13 | 16:46 | 50.043
2020-02-13 | 16:46 | 50.046
2020-02-13 | 16:46 | 50.047
2020-02-13 | 16:46 | 50.051
2020-02-13 | 16:46 | 50.052
2020-02-13 | 16:46 | 50.053
2020-02-13 | 16:46 | 50.055
2020-02-13 | 16:46 | 50.054
2020-02-13 | 16:46 | 50.052
2020-02-13 | 16:46 | 50.05
2020-02-13 | 16:46 | 50.049
2020-02-13 | 16:46 | 50.051
2020-02-13 | 16:46 | 50.053
2020-02-13 | 16:46 | 50.055
2020-02-13 | 16:46 | 50.057
2020-02-13 | 16:46 | 50.058
2020-02-13 | 16:46 | 50.058
2020-02-13 | 16:46 | 50.059
2020-02-13 | 16:46 | 50.057
2020-02-13 | 16:46 | 50.057
2020-02-13 | 16:46 | 50.056
2020-02-13 | 16:46 | 50.054
2020-02-13 | 16:46 | 50.052
2020-02-13 | 16:46 | 50.053
2020-02-13 | 16:46 | 50.054
2020-02-13 | 16:46 | 50.054
2020-02-13 | 16:46 | 50.054
2020-02-13 | 16:46 | 50.055
2020-02-13 | 16:46 | 50.056
2020-02-13 | 16:46 | 50.056
2020-02-13 | 16:46 | 50.058
2020-02-13 | 16:46 | 50.06
2020-02-13 | 16:46 | 50.063
2020-02-13 | 16:46 | 50.064
2020-02-13 | 16:46 | 50.063
2020-02-13 | 16:46 | 50.064
2020-02-13 | 16:46 | 50.065
2020-02-13 | 16:46 | 50.067
2020-02-13 | 16:46 | 50.069
2020-02-13 | 16:46 | 50.072
2020-02-13 | 16:46 | 50.074
2020-02-13 | 16:46 | 50.074
2020-02-13 | 16:46 | 50.076
2020-02-13 | 16:46 | 50.077
2020-02-13 | 16:46 | 50.077
2020-02-13 | 16:46 | 50.078
2020-02-13 | 16:46 | 50.079
2020-02-13 | 16:46 | 50.079
2020-02-13 | 16:46 | 50.079
2020-02-13 | 16:46 | 50.079
2020-02-13 | 16:46 | 50.078
2020-02-13 | 16:46 | 50.076
2020-02-13 | 16:46 | 50.073
2020-02-13 | 16:46 | 50.07
2020-02-13 | 16:47 | 50.067
2020-02-13 | 16:47 | 50.066
2020-02-13 | 16:47 | 50.064
2020-02-13 | 16:47 | 50.063
2020-02-13 | 16:47 | 50.06
2020-02-13 | 16:47 | 50.061
2020-02-13 | 16:47 | 50.062
2020-02-13 | 16:47 | 50.063
2020-02-13 | 16:47 | 50.062
2020-02-13 | 16:47 | 50.061
2020-02-13 | 16:47 | 50.06
2020-02-13 | 16:47 | 50.058
2020-02-13 | 16:47 | 50.056
2020-02-13 | 16:47 | 50.054
2020-02-13 | 16:47 | 50.053
2020-02-13 | 16:47 | 50.05
2020-02-13 | 16:47 | 50.049
2020-02-13 | 16:47 | 50.047
2020-02-13 | 16:47 | 50.048
2020-02-13 | 16:47 | 50.046
2020-02-13 | 16:47 | 50.046
2020-02-13 | 16:47 | 50.043
2020-02-13 | 16:47 | 50.044
2020-02-13 | 16:47 | 50.046
2020-02-13 | 16:47 | 50.044
2020-02-13 | 16:47 | 50.046
2020-02-13 | 16:47 | 50.048
2020-02-13 | 16:47 | 50.049
2020-02-13 | 16:47 | 50.051
2020-02-13 | 16:47 | 50.052
2020-02-13 | 16:47 | 50.057
2020-02-13 | 16:47 | 50.058
2020-02-13 | 16:47 | 50.061
2020-02-13 | 16:47 | 50.063
2020-02-13 | 16:47 | 50.065
2020-02-13 | 16:47 | 50.065
2020-02-13 | 16:47 | 50.065
2020-02-13 | 16:47 | 50.063
2020-02-13 | 16:47 | 50.059
2020-02-13 | 16:47 | 50.06
2020-02-13 | 16:47 | 50.058
2020-02-13 | 16:47 | 50.056
2020-02-13 | 16:47 | 50.054
2020-02-13 | 16:47 | 50.055
2020-02-13 | 16:47 | 50.051
2020-02-13 | 16:47 | 50.05
2020-02-13 | 16:47 | 50.047
2020-02-13 | 16:47 | 50.044
2020-02-13 | 16:47 | 50.043
2020-02-13 | 16:47 | 50.039
2020-02-13 | 16:47 | 50.034
2020-02-13 | 16:47 | 50.031
2020-02-13 | 16:47 | 50.028
2020-02-13 | 16:47 | 50.027
2020-02-13 | 16:47 | 50.025
2020-02-13 | 16:47 | 50.026
2020-02-13 | 16:47 | 50.028
2020-02-13 | 16:47 | 50.031
2020-02-13 | 16:47 | 50.035
2020-02-13 | 16:48 | 50.036
2020-02-13 | 16:48 | 50.038
2020-02-13 | 16:48 | 50.04
2020-02-13 | 16:48 | 50.041
2020-02-13 | 16:48 | 50.042
2020-02-13 | 16:48 | 50.044
2020-02-13 | 16:48 | 50.041
2020-02-13 | 16:48 | 50.043
2020-02-13 | 16:48 | 50.043
2020-02-13 | 16:48 | 50.042
2020-02-13 | 16:48 | 50.043
2020-02-13 | 16:48 | 50.046
2020-02-13 | 16:48 | 50.05
2020-02-13 | 16:48 | 50.056
2020-02-13 | 16:48 | 50.061
2020-02-13 | 16:48 | 50.065
2020-02-13 | 16:48 | 50.066
2020-02-13 | 16:48 | 50.071
2020-02-13 | 16:48 | 50.071
2020-02-13 | 16:48 | 50.073
2020-02-13 | 16:48 | 50.075
2020-02-13 | 16:48 | 50.076
2020-02-13 | 16:48 | 50.077
2020-02-13 | 16:48 | 50.077
2020-02-13 | 16:48 | 50.08
2020-02-13 | 16:48 | 50.079
2020-02-13 | 16:48 | 50.078
2020-02-13 | 16:48 | 50.079
2020-02-13 | 16:48 | 50.077
2020-02-13 | 16:48 | 50.077
2020-02-13 | 16:48 | 50.076
2020-02-13 | 16:48 | 50.073
2020-02-13 | 16:48 | 50.071
2020-02-13 | 16:48 | 50.069
2020-02-13 | 16:48 | 50.069
2020-02-13 | 16:48 | 50.068
2020-02-13 | 16:48 | 50.068
2020-02-13 | 16:48 | 50.066
2020-02-13 | 16:48 | 50.067
2020-02-13 | 16:48 | 50.065
2020-02-13 | 16:48 | 50.064
2020-02-13 | 16:48 | 50.065
2020-02-13 | 16:48 | 50.061
2020-02-13 | 16:48 | 50.061
2020-02-13 | 16:48 | 50.058
2020-02-13 | 16:48 | 50.056
2020-02-13 | 16:48 | 50.055
2020-02-13 | 16:48 | 50.054
2020-02-13 | 16:48 | 50.051
2020-02-13 | 16:48 | 50.049
2020-02-13 | 16:48 | 50.047
2020-02-13 | 16:48 | 50.045
2020-02-13 | 16:48 | 50.043
2020-02-13 | 16:48 | 50.046
2020-02-13 | 16:48 | 50.049
2020-02-13 | 16:48 | 50.051
2020-02-13 | 16:48 | 50.051
2020-02-13 | 16:48 | 50.052
2020-02-13 | 16:48 | 50.052
2020-02-13 | 16:48 | 50.053
2020-02-13 | 16:48 | 50.054
2020-02-13 | 16:49 | 50.056
2020-02-13 | 16:49 | 50.057
2020-02-13 | 16:49 | 50.057
2020-02-13 | 16:49 | 50.058
2020-02-13 | 16:49 | 50.057
2020-02-13 | 16:49 | 50.056
2020-02-13 | 16:49 | 50.054
2020-02-13 | 16:49 | 50.052
2020-02-13 | 16:49 | 50.05
2020-02-13 | 16:49 | 50.051
2020-02-13 | 16:49 | 50.052
2020-02-13 | 16:49 | 50.051
2020-02-13 | 16:49 | 50.055
2020-02-13 | 16:49 | 50.055
2020-02-13 | 16:49 | 50.059
2020-02-13 | 16:49 | 50.058
2020-02-13 | 16:49 | 50.061
2020-02-13 | 16:49 | 50.062
2020-02-13 | 16:49 | 50.064
2020-02-13 | 16:49 | 50.065
2020-02-13 | 16:49 | 50.067
2020-02-13 | 16:49 | 50.069
2020-02-13 | 16:49 | 50.067
2020-02-13 | 16:49 | 50.068
2020-02-13 | 16:49 | 50.065
2020-02-13 | 16:49 | 50.064
2020-02-13 | 16:49 | 50.063
2020-02-13 | 16:49 | 50.06
2020-02-13 | 16:49 | 50.058
2020-02-13 | 16:49 | 50.053
2020-02-13 | 16:49 | 50.05
2020-02-13 | 16:49 | 50.045
2020-02-13 | 16:49 | 50.04
2020-02-13 | 16:49 | 50.034
2020-02-13 | 16:49 | 50.03
2020-02-13 | 16:49 | 50.027
2020-02-13 | 16:49 | 50.023
2020-02-13 | 16:49 | 50.018
2020-02-13 | 16:49 | 50.015
2020-02-13 | 16:49 | 50.011
2020-02-13 | 16:49 | 50.008
2020-02-13 | 16:49 | 50.008
2020-02-13 | 16:49 | 50.007
2020-02-13 | 16:49 | 50.01
2020-02-13 | 16:49 | 50.01
2020-02-13 | 16:49 | 50.011
2020-02-13 | 16:49 | 50.01
2020-02-13 | 16:49 | 50.012
2020-02-13 | 16:49 | 50.011
2020-02-13 | 16:49 | 50.012
2020-02-13 | 16:49 | 50.013
2020-02-13 | 16:49 | 50.013
2020-02-13 | 16:49 | 50.014
2020-02-13 | 16:49 | 50.016
2020-02-13 | 16:49 | 50.019
2020-02-13 | 16:49 | 50.021
2020-02-13 | 16:49 | 50.024
2020-02-13 | 16:49 | 50.024
2020-02-13 | 16:49 | 50.024
2020-02-13 | 16:50 | 50.027
2020-02-13 | 16:50 | 50.026
2020-02-13 | 16:50 | 50.026
2020-02-13 | 16:50 | 50.025
2020-02-13 | 16:50 | 50.024
2020-02-13 | 16:50 | 50.022
2020-02-13 | 16:50 | 50.019
2020-02-13 | 16:50 | 50.02
2020-02-13 | 16:50 | 50.02
2020-02-13 | 16:50 | 50.021
2020-02-13 | 16:50 | 50.021
2020-02-13 | 16:50 | 50.02
2020-02-13 | 16:50 | 50.021
2020-02-13 | 16:50 | 50.025
2020-02-13 | 16:50 | 50.026
2020-02-13 | 16:50 | 50.028
2020-02-13 | 16:50 | 50.03
2020-02-13 | 16:50 | 50.034
2020-02-13 | 16:50 | 50.04
2020-02-13 | 16:50 | 50.041
2020-02-13 | 16:50 | 50.04
2020-02-13 | 16:50 | 50.042
2020-02-13 | 16:50 | 50.045
2020-02-13 | 16:50 | 50.044
2020-02-13 | 16:50 | 50.045
2020-02-13 | 16:50 | 50.045
2020-02-13 | 16:50 | 50.045
2020-02-13 | 16:50 | 50.047
2020-02-13 | 16:50 | 50.046
2020-02-13 | 16:50 | 50.044
2020-02-13 | 16:50 | 50.042
2020-02-13 | 16:50 | 50.041
2020-02-13 | 16:50 | 50.038
2020-02-13 | 16:50 | 50.037
2020-02-13 | 16:50 | 50.035
2020-02-13 | 16:50 | 50.033
2020-02-13 | 16:50 | 50.034
2020-02-13 | 16:50 | 50.033
2020-02-13 | 16:50 | 50.031
2020-02-13 | 16:50 | 50.031
2020-02-13 | 16:50 | 50.03
2020-02-13 | 16:50 | 50.028
2020-02-13 | 16:50 | 50.026
2020-02-13 | 16:50 | 50.025
2020-02-13 | 16:50 | 50.024
2020-02-13 | 16:50 | 50.023
2020-02-13 | 16:50 | 50.021
2020-02-13 | 16:50 | 50.023
2020-02-13 | 16:50 | 50.024
2020-02-13 | 16:50 | 50.025
2020-02-13 | 16:50 | 50.026
2020-02-13 | 16:50 | 50.028
2020-02-13 | 16:50 | 50.029
2020-02-13 | 16:50 | 50.031
2020-02-13 | 16:50 | 50.035
2020-02-13 | 16:50 | 50.035
2020-02-13 | 16:50 | 50.038
2020-02-13 | 16:50 | 50.04
2020-02-13 | 16:50 | 50.04
2020-02-13 | 16:50 | 50.04
2020-02-13 | 16:50 | 50.042
2020-02-13 | 16:51 | 50.043
2020-02-13 | 16:51 | 50.042
2020-02-13 | 16:51 | 50.043
2020-02-13 | 16:51 | 50.045
2020-02-13 | 16:51 | 50.046
2020-02-13 | 16:51 | 50.047
2020-02-13 | 16:51 | 50.046
2020-02-13 | 16:51 | 50.046
2020-02-13 | 16:51 | 50.046
2020-02-13 | 16:51 | 50.045
2020-02-13 | 16:51 | 50.045
2020-02-13 | 16:51 | 50.043
2020-02-13 | 16:51 | 50.043
2020-02-13 | 16:51 | 50.041
2020-02-13 | 16:51 | 50.039
2020-02-13 | 16:51 | 50.038
2020-02-13 | 16:51 | 50.036
2020-02-13 | 16:51 | 50.032
2020-02-13 | 16:51 | 50.028
2020-02-13 | 16:51 | 50.025
2020-02-13 | 16:51 | 50.021
2020-02-13 | 16:51 | 50.016
2020-02-13 | 16:51 | 50.014
2020-02-13 | 16:51 | 50.012
2020-02-13 | 16:51 | 50.012
2020-02-13 | 16:51 | 50.011
2020-02-13 | 16:51 | 50.01
2020-02-13 | 16:51 | 50.011
2020-02-13 | 16:51 | 50.009
2020-02-13 | 16:51 | 50.008
2020-02-13 | 16:51 | 50.009
2020-02-13 | 16:51 | 50.012
2020-02-13 | 16:51 | 50.015
2020-02-13 | 16:51 | 50.016
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.018
2020-02-13 | 16:51 | 50.017
2020-02-13 | 16:51 | 50.015
2020-02-13 | 16:51 | 50.015
2020-02-13 | 16:51 | 50.016
2020-02-13 | 16:51 | 50.019
2020-02-13 | 16:51 | 50.02
2020-02-13 | 16:51 | 50.023
2020-02-13 | 16:51 | 50.025
2020-02-13 | 16:51 | 50.026
2020-02-13 | 16:51 | 50.026
2020-02-13 | 16:51 | 50.025
2020-02-13 | 16:51 | 50.024
2020-02-13 | 16:51 | 50.025
2020-02-13 | 16:51 | 50.023
2020-02-13 | 16:51 | 50.021
2020-02-13 | 16:51 | 50.02
2020-02-13 | 16:51 | 50.02
2020-02-13 | 16:51 | 50.021
2020-02-13 | 16:52 | 50.022
2020-02-13 | 16:52 | 50.021
2020-02-13 | 16:52 | 50.022
2020-02-13 | 16:52 | 50.023
2020-02-13 | 16:52 | 50.022
2020-02-13 | 16:52 | 50.023
2020-02-13 | 16:52 | 50.024
2020-02-13 | 16:52 | 50.024
2020-02-13 | 16:52 | 50.023
2020-02-13 | 16:52 | 50.022
2020-02-13 | 16:52 | 50.022
2020-02-13 | 16:52 | 50.02
2020-02-13 | 16:52 | 50.02
2020-02-13 | 16:52 | 50.022
2020-02-13 | 16:52 | 50.025
2020-02-13 | 16:52 | 50.03
2020-02-13 | 16:52 | 50.035
2020-02-13 | 16:52 | 50.04
2020-02-13 | 16:52 | 50.043
2020-02-13 | 16:52 | 50.049
2020-02-13 | 16:52 | 50.053
2020-02-13 | 16:52 | 50.056
2020-02-13 | 16:52 | 50.059
2020-02-13 | 16:52 | 50.06
2020-02-13 | 16:52 | 50.057
2020-02-13 | 16:52 | 50.055
2020-02-13 | 16:52 | 50.053
2020-02-13 | 16:52 | 50.051
2020-02-13 | 16:52 | 50.049
2020-02-13 | 16:52 | 50.047
2020-02-13 | 16:52 | 50.045
2020-02-13 | 16:52 | 50.044
2020-02-13 | 16:52 | 50.043
2020-02-13 | 16:52 | 50.043
2020-02-13 | 16:52 | 50.042
2020-02-13 | 16:52 | 50.041
2020-02-13 | 16:52 | 50.042
2020-02-13 | 16:52 | 50.043
2020-02-13 | 16:52 | 50.045
2020-02-13 | 16:52 | 50.047
2020-02-13 | 16:52 | 50.049
2020-02-13 | 16:52 | 50.05
2020-02-13 | 16:52 | 50.054
2020-02-13 | 16:52 | 50.057
2020-02-13 | 16:52 | 50.06
2020-02-13 | 16:52 | 50.063
2020-02-13 | 16:52 | 50.065
2020-02-13 | 16:52 | 50.068
2020-02-13 | 16:52 | 50.067
2020-02-13 | 16:52 | 50.067
2020-02-13 | 16:52 | 50.065
2020-02-13 | 16:52 | 50.064
2020-02-13 | 16:52 | 50.063
2020-02-13 | 16:52 | 50.062
2020-02-13 | 16:52 | 50.063
2020-02-13 | 16:52 | 50.06
2020-02-13 | 16:52 | 50.058
2020-02-13 | 16:52 | 50.054
2020-02-13 | 16:52 | 50.051
2020-02-13 | 16:52 | 50.045
2020-02-13 | 16:52 | 50.041
2020-02-13 | 16:53 | 50.037
2020-02-13 | 16:53 | 50.036
2020-02-13 | 16:53 | 50.035
2020-02-13 | 16:53 | 50.037
2020-02-13 | 16:53 | 50.037
2020-02-13 | 16:53 | 50.038
2020-02-13 | 16:53 | 50.038
2020-02-13 | 16:53 | 50.04
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.04
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.04
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.043
2020-02-13 | 16:53 | 50.044
2020-02-13 | 16:53 | 50.046
2020-02-13 | 16:53 | 50.046
2020-02-13 | 16:53 | 50.048
2020-02-13 | 16:53 | 50.047
2020-02-13 | 16:53 | 50.046
2020-02-13 | 16:53 | 50.046
2020-02-13 | 16:53 | 50.045
2020-02-13 | 16:53 | 50.043
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.039
2020-02-13 | 16:53 | 50.039
2020-02-13 | 16:53 | 50.039
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.04
2020-02-13 | 16:53 | 50.042
2020-02-13 | 16:53 | 50.042
2020-02-13 | 16:53 | 50.042
2020-02-13 | 16:53 | 50.041
2020-02-13 | 16:53 | 50.04
2020-02-13 | 16:53 | 50.037
2020-02-13 | 16:53 | 50.035
2020-02-13 | 16:53 | 50.032
2020-02-13 | 16:53 | 50.029
2020-02-13 | 16:53 | 50.026
2020-02-13 | 16:53 | 50.024
2020-02-13 | 16:53 | 50.023
2020-02-13 | 16:53 | 50.022
2020-02-13 | 16:53 | 50.02
2020-02-13 | 16:53 | 50.021
2020-02-13 | 16:53 | 50.017
2020-02-13 | 16:53 | 50.014
2020-02-13 | 16:53 | 50.011
2020-02-13 | 16:53 | 50.008
2020-02-13 | 16:53 | 50.006
2020-02-13 | 16:53 | 50.002
2020-02-13 | 16:53 | 49.998
2020-02-13 | 16:53 | 49.998
2020-02-13 | 16:53 | 49.998
2020-02-13 | 16:53 | 49.999
2020-02-13 | 16:53 | 50.002
2020-02-13 | 16:53 | 50.005
2020-02-13 | 16:53 | 50.007
2020-02-13 | 16:54 | 50.008
2020-02-13 | 16:54 | 50.011
2020-02-13 | 16:54 | 50.014
2020-02-13 | 16:54 | 50.015
2020-02-13 | 16:54 | 50.015
2020-02-13 | 16:54 | 50.012
2020-02-13 | 16:54 | 50.011
2020-02-13 | 16:54 | 50.01
2020-02-13 | 16:54 | 50.007
2020-02-13 | 16:54 | 50.006
2020-02-13 | 16:54 | 50.005
2020-02-13 | 16:54 | 50.004
2020-02-13 | 16:54 | 50.006
2020-02-13 | 16:54 | 50.007
2020-02-13 | 16:54 | 50.009
2020-02-13 | 16:54 | 50.01
2020-02-13 | 16:54 | 50.01
2020-02-13 | 16:54 | 50.011
2020-02-13 | 16:54 | 50.01
2020-02-13 | 16:54 | 50.008
2020-02-13 | 16:54 | 50.006
2020-02-13 | 16:54 | 50.004
2020-02-13 | 16:54 | 50.003
2020-02-13 | 16:54 | 50.002
2020-02-13 | 16:54 | 50.002
2020-02-13 | 16:54 | 50.001
2020-02-13 | 16:54 | 50
2020-02-13 | 16:54 | 49.998
2020-02-13 | 16:54 | 49.997
2020-02-13 | 16:54 | 49.997
2020-02-13 | 16:54 | 50
2020-02-13 | 16:54 | 50.001
2020-02-13 | 16:54 | 50.003
2020-02-13 | 16:54 | 50.005
2020-02-13 | 16:54 | 50.009
2020-02-13 | 16:54 | 50.013
2020-02-13 | 16:54 | 50.02
2020-02-13 | 16:54 | 50.024
2020-02-13 | 16:54 | 50.029
2020-02-13 | 16:54 | 50.033
2020-02-13 | 16:54 | 50.037
2020-02-13 | 16:54 | 50.038
2020-02-13 | 16:54 | 50.039
2020-02-13 | 16:54 | 50.041
2020-02-13 | 16:54 | 50.042
2020-02-13 | 16:54 | 50.044
2020-02-13 | 16:54 | 50.045
2020-02-13 | 16:54 | 50.047
2020-02-13 | 16:54 | 50.049
2020-02-13 | 16:54 | 50.049
2020-02-13 | 16:54 | 50.052
2020-02-13 | 16:54 | 50.052
2020-02-13 | 16:54 | 50.054
2020-02-13 | 16:54 | 50.055
2020-02-13 | 16:54 | 50.058
2020-02-13 | 16:54 | 50.06
2020-02-13 | 16:54 | 50.062
2020-02-13 | 16:54 | 50.064
2020-02-13 | 16:54 | 50.064
2020-02-13 | 16:54 | 50.066
2020-02-13 | 16:55 | 50.067
2020-02-13 | 16:55 | 50.069
2020-02-13 | 16:55 | 50.068
2020-02-13 | 16:55 | 50.067
2020-02-13 | 16:55 | 50.067
2020-02-13 | 16:55 | 50.064
2020-02-13 | 16:55 | 50.063
2020-02-13 | 16:55 | 50.06
2020-02-13 | 16:55 | 50.06
2020-02-13 | 16:55 | 50.058
2020-02-13 | 16:55 | 50.057
2020-02-13 | 16:55 | 50.057
2020-02-13 | 16:55 | 50.057
2020-02-13 | 16:55 | 50.058
2020-02-13 | 16:55 | 50.056
2020-02-13 | 16:55 | 50.056
2020-02-13 | 16:55 | 50.055
2020-02-13 | 16:55 | 50.052
2020-02-13 | 16:55 | 50.047
2020-02-13 | 16:55 | 50.045
2020-02-13 | 16:55 | 50.039
2020-02-13 | 16:55 | 50.035
2020-02-13 | 16:55 | 50.032
2020-02-13 | 16:55 | 50.028
2020-02-13 | 16:55 | 50.025
2020-02-13 | 16:55 | 50.021
2020-02-13 | 16:55 | 50.019
2020-02-13 | 16:55 | 50.018
2020-02-13 | 16:55 | 50.015
2020-02-13 | 16:55 | 50.014
2020-02-13 | 16:55 | 50.01
2020-02-13 | 16:55 | 50.007
2020-02-13 | 16:55 | 50.004
2020-02-13 | 16:55 | 50.001
2020-02-13 | 16:55 | 49.997
2020-02-13 | 16:55 | 49.996
2020-02-13 | 16:55 | 49.995
2020-02-13 | 16:55 | 49.99
2020-02-13 | 16:55 | 49.989
2020-02-13 | 16:55 | 49.987
2020-02-13 | 16:55 | 49.985
2020-02-13 | 16:55 | 49.987
2020-02-13 | 16:55 | 49.985
2020-02-13 | 16:55 | 49.985
2020-02-13 | 16:55 | 49.986
2020-02-13 | 16:55 | 49.989
2020-02-13 | 16:55 | 49.991
2020-02-13 | 16:55 | 49.995
2020-02-13 | 16:55 | 49.998
2020-02-13 | 16:55 | 50.001
2020-02-13 | 16:55 | 50.005
2020-02-13 | 16:55 | 50.008
2020-02-13 | 16:55 | 50.011
2020-02-13 | 16:55 | 50.015
2020-02-13 | 16:55 | 50.017
2020-02-13 | 16:55 | 50.019
2020-02-13 | 16:55 | 50.023
2020-02-13 | 16:55 | 50.024
2020-02-13 | 16:55 | 50.025
2020-02-13 | 16:55 | 50.027
2020-02-13 | 16:56 | 50.027
2020-02-13 | 16:56 | 50.026
2020-02-13 | 16:56 | 50.025
2020-02-13 | 16:56 | 50.025
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.02
2020-02-13 | 16:56 | 50.019
2020-02-13 | 16:56 | 50.02
2020-02-13 | 16:56 | 50.019
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.02
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.023
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.023
2020-02-13 | 16:56 | 50.023
2020-02-13 | 16:56 | 50.024
2020-02-13 | 16:56 | 50.027
2020-02-13 | 16:56 | 50.028
2020-02-13 | 16:56 | 50.027
2020-02-13 | 16:56 | 50.027
2020-02-13 | 16:56 | 50.024
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.023
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.023
2020-02-13 | 16:56 | 50.023
2020-02-13 | 16:56 | 50.024
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.022
2020-02-13 | 16:56 | 50.019
2020-02-13 | 16:56 | 50.015
2020-02-13 | 16:56 | 50.013
2020-02-13 | 16:56 | 50.011
2020-02-13 | 16:56 | 50.007
2020-02-13 | 16:56 | 50.006
2020-02-13 | 16:56 | 50.002
2020-02-13 | 16:56 | 50.001
2020-02-13 | 16:56 | 50.004
2020-02-13 | 16:56 | 50.005
2020-02-13 | 16:56 | 50.009
2020-02-13 | 16:56 | 50.011
2020-02-13 | 16:56 | 50.013
2020-02-13 | 16:56 | 50.015
2020-02-13 | 16:56 | 50.017
2020-02-13 | 16:56 | 50.018
2020-02-13 | 16:56 | 50.019
2020-02-13 | 16:56 | 50.019
2020-02-13 | 16:56 | 50.019
2020-02-13 | 16:56 | 50.02
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:56 | 50.021
2020-02-13 | 16:57 | 50.019
2020-02-13 | 16:57 | 50.016
2020-02-13 | 16:57 | 50.013
2020-02-13 | 16:57 | 50.01
2020-02-13 | 16:57 | 50.006
2020-02-13 | 16:57 | 50.004
2020-02-13 | 16:57 | 49.999
2020-02-13 | 16:57 | 49.996
2020-02-13 | 16:57 | 49.992
2020-02-13 | 16:57 | 49.988
2020-02-13 | 16:57 | 49.986
2020-02-13 | 16:57 | 49.985
2020-02-13 | 16:57 | 49.985
2020-02-13 | 16:57 | 49.986
2020-02-13 | 16:57 | 49.988
2020-02-13 | 16:57 | 49.99
2020-02-13 | 16:57 | 49.993
2020-02-13 | 16:57 | 49.997
2020-02-13 | 16:57 | 49.999
2020-02-13 | 16:57 | 50.002
2020-02-13 | 16:57 | 50.004
2020-02-13 | 16:57 | 50.004
2020-02-13 | 16:57 | 50.007
2020-02-13 | 16:57 | 50.006
2020-02-13 | 16:57 | 50.005
2020-02-13 | 16:57 | 50.003
2020-02-13 | 16:57 | 50.002
2020-02-13 | 16:57 | 50.002
2020-02-13 | 16:57 | 50.003

## Event 20200217-1
In UTC
Date | Time | Freq
2020-02-17 | 0:48 | 50.096
2020-02-17 | 0:48 | 50.097
2020-02-17 | 0:48 | 50.094
2020-02-17 | 0:48 | 50.095
2020-02-17 | 0:48 | 50.094
2020-02-17 | 0:48 | 50.093
2020-02-17 | 0:48 | 50.093
2020-02-17 | 0:48 | 50.094
2020-02-17 | 0:48 | 50.093
2020-02-17 | 0:48 | 50.093
2020-02-17 | 0:48 | 50.092
2020-02-17 | 0:48 | 50.09
2020-02-17 | 0:48 | 50.09
2020-02-17 | 0:48 | 50.091
2020-02-17 | 0:48 | 50.091
2020-02-17 | 0:48 | 50.091
2020-02-17 | 0:48 | 50.088
2020-02-17 | 0:48 | 50.089
2020-02-17 | 0:48 | 50.087
2020-02-17 | 0:48 | 50.088
2020-02-17 | 0:48 | 50.088
2020-02-17 | 0:48 | 50.089
2020-02-17 | 0:48 | 50.091
2020-02-17 | 0:48 | 50.092
2020-02-17 | 0:48 | 50.095
2020-02-17 | 0:48 | 50.098
2020-02-17 | 0:48 | 50.098
2020-02-17 | 0:48 | 50.099
2020-02-17 | 0:48 | 50.098
2020-02-17 | 0:48 | 50.098
2020-02-17 | 0:48 | 50.1
2020-02-17 | 0:49 | 50.099
2020-02-17 | 0:49 | 50.098
2020-02-17 | 0:49 | 50.1
2020-02-17 | 0:49 | 50.098
2020-02-17 | 0:49 | 50.096
2020-02-17 | 0:49 | 50.095
2020-02-17 | 0:49 | 50.094
2020-02-17 | 0:49 | 50.094
2020-02-17 | 0:49 | 50.092
2020-02-17 | 0:49 | 50.092
2020-02-17 | 0:49 | 50.092
2020-02-17 | 0:49 | 50.094
2020-02-17 | 0:49 | 50.093
2020-02-17 | 0:49 | 50.096
2020-02-17 | 0:49 | 50.095
2020-02-17 | 0:49 | 50.096
2020-02-17 | 0:49 | 50.095
2020-02-17 | 0:49 | 50.097
2020-02-17 | 0:49 | 50.095
2020-02-17 | 0:49 | 50.096
2020-02-17 | 0:49 | 50.096
2020-02-17 | 0:49 | 50.097
2020-02-17 | 0:49 | 50.097
2020-02-17 | 0:49 | 50.095
2020-02-17 | 0:49 | 50.094
2020-02-17 | 0:49 | 50.093
2020-02-17 | 0:49 | 50.094
2020-02-17 | 0:49 | 50.095
2020-02-17 | 0:49 | 50.096
2020-02-17 | 0:49 | 50.098
2020-02-17 | 0:49 | 50.021
2020-02-17 | 0:49 | 49.961
2020-02-17 | 0:49 | 49.912
2020-02-17 | 0:49 | 49.889
2020-02-17 | 0:49 | 49.879
2020-02-17 | 0:49 | 49.881
2020-02-17 | 0:49 | 49.888
2020-02-17 | 0:49 | 49.905
2020-02-17 | 0:49 | 49.919
2020-02-17 | 0:49 | 49.925
2020-02-17 | 0:49 | 49.928
2020-02-17 | 0:49 | 49.931
2020-02-17 | 0:49 | 49.93
2020-02-17 | 0:49 | 49.932
2020-02-17 | 0:49 | 49.933
2020-02-17 | 0:49 | 49.932
2020-02-17 | 0:49 | 49.934
2020-02-17 | 0:49 | 49.936
2020-02-17 | 0:49 | 49.935
2020-02-17 | 0:49 | 49.933
2020-02-17 | 0:49 | 49.934
2020-02-17 | 0:49 | 49.933
2020-02-17 | 0:49 | 49.931
2020-02-17 | 0:49 | 49.929
2020-02-17 | 0:49 | 49.928
2020-02-17 | 0:49 | 49.927
2020-02-17 | 0:49 | 49.924
2020-02-17 | 0:49 | 49.924
2020-02-17 | 0:49 | 49.923
2020-02-17 | 0:49 | 49.923
2020-02-17 | 0:50 | 49.922
2020-02-17 | 0:50 | 49.921
2020-02-17 | 0:50 | 49.92
2020-02-17 | 0:50 | 49.918
2020-02-17 | 0:50 | 49.918
2020-02-17 | 0:50 | 49.916
2020-02-17 | 0:50 | 49.916
2020-02-17 | 0:50 | 49.912
2020-02-17 | 0:50 | 49.914
2020-02-17 | 0:50 | 49.914
2020-02-17 | 0:50 | 49.914
2020-02-17 | 0:50 | 49.914
2020-02-17 | 0:50 | 49.915
2020-02-17 | 0:50 | 49.916
2020-02-17 | 0:50 | 49.913
2020-02-17 | 0:50 | 49.912
2020-02-17 | 0:50 | 49.91
2020-02-17 | 0:50 | 49.911
2020-02-17 | 0:50 | 49.913
2020-02-17 | 0:50 | 49.912
2020-02-17 | 0:50 | 49.914
2020-02-17 | 0:50 | 49.913
2020-02-17 | 0:50 | 49.913
2020-02-17 | 0:50 | 49.911
2020-02-17 | 0:50 | 49.909
2020-02-17 | 0:50 | 49.907
2020-02-17 | 0:50 | 49.907
2020-02-17 | 0:50 | 49.907
2020-02-17 | 0:50 | 49.905
2020-02-17 | 0:50 | 49.904
2020-02-17 | 0:50 | 49.902
2020-02-17 | 0:50 | 49.901
2020-02-17 | 0:50 | 49.901
2020-02-17 | 0:50 | 49.901
2020-02-17 | 0:50 | 49.901
2020-02-17 | 0:50 | 49.902
2020-02-17 | 0:50 | 49.9
2020-02-17 | 0:50 | 49.901
2020-02-17 | 0:50 | 49.903
2020-02-17 | 0:50 | 49.904
2020-02-17 | 0:50 | 49.902
2020-02-17 | 0:50 | 49.9
2020-02-17 | 0:50 | 49.897
2020-02-17 | 0:50 | 49.899
2020-02-17 | 0:50 | 49.903
2020-02-17 | 0:50 | 49.905
2020-02-17 | 0:50 | 49.907
2020-02-17 | 0:50 | 49.907
2020-02-17 | 0:50 | 49.908
2020-02-17 | 0:50 | 49.908
2020-02-17 | 0:50 | 49.907
2020-02-17 | 0:50 | 49.908
2020-02-17 | 0:50 | 49.906
2020-02-17 | 0:50 | 49.906
2020-02-17 | 0:50 | 49.902
2020-02-17 | 0:50 | 49.898
2020-02-17 | 0:50 | 49.897
2020-02-17 | 0:50 | 49.898
2020-02-17 | 0:50 | 49.898
2020-02-17 | 0:50 | 49.897
2020-02-17 | 0:51 | 49.896
2020-02-17 | 0:51 | 49.899
2020-02-17 | 0:51 | 49.901
2020-02-17 | 0:51 | 49.902
2020-02-17 | 0:51 | 49.899
2020-02-17 | 0:51 | 49.897
2020-02-17 | 0:51 | 49.895
2020-02-17 | 0:51 | 49.894
2020-02-17 | 0:51 | 49.893
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.887
2020-02-17 | 0:51 | 49.885
2020-02-17 | 0:51 | 49.884
2020-02-17 | 0:51 | 49.887
2020-02-17 | 0:51 | 49.888
2020-02-17 | 0:51 | 49.888
2020-02-17 | 0:51 | 49.889
2020-02-17 | 0:51 | 49.889
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.887
2020-02-17 | 0:51 | 49.884
2020-02-17 | 0:51 | 49.884
2020-02-17 | 0:51 | 49.889
2020-02-17 | 0:51 | 49.889
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.895
2020-02-17 | 0:51 | 49.897
2020-02-17 | 0:51 | 49.9
2020-02-17 | 0:51 | 49.899
2020-02-17 | 0:51 | 49.898
2020-02-17 | 0:51 | 49.897
2020-02-17 | 0:51 | 49.896
2020-02-17 | 0:51 | 49.894
2020-02-17 | 0:51 | 49.892
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.89
2020-02-17 | 0:51 | 49.891
2020-02-17 | 0:51 | 49.893
2020-02-17 | 0:51 | 49.897
2020-02-17 | 0:51 | 49.9
2020-02-17 | 0:51 | 49.902
2020-02-17 | 0:51 | 49.903
2020-02-17 | 0:52 | 49.902
2020-02-17 | 0:52 | 49.9
2020-02-17 | 0:52 | 49.899
2020-02-17 | 0:52 | 49.898
2020-02-17 | 0:52 | 49.896
2020-02-17 | 0:52 | 49.895
2020-02-17 | 0:52 | 49.894
2020-02-17 | 0:52 | 49.893
2020-02-17 | 0:52 | 49.89
2020-02-17 | 0:52 | 49.889
2020-02-17 | 0:52 | 49.89
2020-02-17 | 0:52 | 49.895
2020-02-17 | 0:52 | 49.898
2020-02-17 | 0:52 | 49.899
2020-02-17 | 0:52 | 49.901
2020-02-17 | 0:52 | 49.9
2020-02-17 | 0:52 | 49.902
2020-02-17 | 0:52 | 49.899
2020-02-17 | 0:52 | 49.897
2020-02-17 | 0:52 | 49.89
2020-02-17 | 0:52 | 49.889
2020-02-17 | 0:52 | 49.888
2020-02-17 | 0:52 | 49.89
2020-02-17 | 0:52 | 49.892
2020-02-17 | 0:52 | 49.895
2020-02-17 | 0:52 | 49.897
2020-02-17 | 0:52 | 49.899
2020-02-17 | 0:52 | 49.9
2020-02-17 | 0:52 | 49.897
2020-02-17 | 0:52 | 49.896
2020-02-17 | 0:52 | 49.894
2020-02-17 | 0:52 | 49.892
2020-02-17 | 0:52 | 49.888
2020-02-17 | 0:52 | 49.885
2020-02-17 | 0:52 | 49.883
2020-02-17 | 0:52 | 49.882
2020-02-17 | 0:52 | 49.882
2020-02-17 | 0:52 | 49.878
2020-02-17 | 0:52 | 49.88
2020-02-17 | 0:52 | 49.881
2020-02-17 | 0:52 | 49.884
2020-02-17 | 0:52 | 49.887
2020-02-17 | 0:52 | 49.887
2020-02-17 | 0:52 | 49.887
2020-02-17 | 0:52 | 49.886
2020-02-17 | 0:52 | 49.884
2020-02-17 | 0:52 | 49.885
2020-02-17 | 0:52 | 49.885
2020-02-17 | 0:52 | 49.884
2020-02-17 | 0:52 | 49.882
2020-02-17 | 0:52 | 49.88
2020-02-17 | 0:52 | 49.88
2020-02-17 | 0:52 | 49.879
2020-02-17 | 0:52 | 49.881
2020-02-17 | 0:52 | 49.879
2020-02-17 | 0:52 | 49.878
2020-02-17 | 0:52 | 49.878
2020-02-17 | 0:52 | 49.877
2020-02-17 | 0:52 | 49.877
2020-02-17 | 0:52 | 49.877
2020-02-17 | 0:52 | 49.878
2020-02-17 | 0:53 | 49.88
2020-02-17 | 0:53 | 49.883
2020-02-17 | 0:53 | 49.884
2020-02-17 | 0:53 | 49.884
2020-02-17 | 0:53 | 49.885
2020-02-17 | 0:53 | 49.885
2020-02-17 | 0:53 | 49.887
2020-02-17 | 0:53 | 49.886
2020-02-17 | 0:53 | 49.887
2020-02-17 | 0:53 | 49.887
2020-02-17 | 0:53 | 49.889
2020-02-17 | 0:53 | 49.888
2020-02-17 | 0:53 | 49.888
2020-02-17 | 0:53 | 49.89
2020-02-17 | 0:53 | 49.891
2020-02-17 | 0:53 | 49.891
2020-02-17 | 0:53 | 49.894
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.894
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.897
2020-02-17 | 0:53 | 49.896
2020-02-17 | 0:53 | 49.896
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.896
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.897
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.896
2020-02-17 | 0:53 | 49.895
2020-02-17 | 0:53 | 49.897
2020-02-17 | 0:53 | 49.899
2020-02-17 | 0:53 | 49.901
2020-02-17 | 0:53 | 49.903
2020-02-17 | 0:53 | 49.906
2020-02-17 | 0:53 | 49.905
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.91
2020-02-17 | 0:53 | 49.912
2020-02-17 | 0:53 | 49.914
2020-02-17 | 0:53 | 49.913
2020-02-17 | 0:53 | 49.912
2020-02-17 | 0:53 | 49.91
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.905
2020-02-17 | 0:53 | 49.904
2020-02-17 | 0:53 | 49.906
2020-02-17 | 0:53 | 49.906
2020-02-17 | 0:53 | 49.906
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.906
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.909
2020-02-17 | 0:53 | 49.907
2020-02-17 | 0:53 | 49.908
2020-02-17 | 0:54 | 49.911
2020-02-17 | 0:54 | 49.914
2020-02-17 | 0:54 | 49.917
2020-02-17 | 0:54 | 49.918
2020-02-17 | 0:54 | 49.921
2020-02-17 | 0:54 | 49.92
2020-02-17 | 0:54 | 49.919
2020-02-17 | 0:54 | 49.918
2020-02-17 | 0:54 | 49.917
2020-02-17 | 0:54 | 49.915
2020-02-17 | 0:54 | 49.913
2020-02-17 | 0:54 | 49.912
2020-02-17 | 0:54 | 49.91
2020-02-17 | 0:54 | 49.91
2020-02-17 | 0:54 | 49.911
2020-02-17 | 0:54 | 49.911
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.912
2020-02-17 | 0:54 | 49.918
2020-02-17 | 0:54 | 49.922
2020-02-17 | 0:54 | 49.921
2020-02-17 | 0:54 | 49.923
2020-02-17 | 0:54 | 49.922
2020-02-17 | 0:54 | 49.922
2020-02-17 | 0:54 | 49.923
2020-02-17 | 0:54 | 49.921
2020-02-17 | 0:54 | 49.92
2020-02-17 | 0:54 | 49.917
2020-02-17 | 0:54 | 49.914
2020-02-17 | 0:54 | 49.914
2020-02-17 | 0:54 | 49.912
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.91
2020-02-17 | 0:54 | 49.912
2020-02-17 | 0:54 | 49.914
2020-02-17 | 0:54 | 49.915
2020-02-17 | 0:54 | 49.913
2020-02-17 | 0:54 | 49.91
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.91
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.908
2020-02-17 | 0:54 | 49.909
2020-02-17 | 0:54 | 49.91
2020-02-17 | 0:54 | 49.912
2020-02-17 | 0:54 | 49.916
2020-02-17 | 0:54 | 49.917
2020-02-17 | 0:54 | 49.922
2020-02-17 | 0:54 | 49.921
2020-02-17 | 0:54 | 49.924
2020-02-17 | 0:54 | 49.924
2020-02-17 | 0:54 | 49.923
2020-02-17 | 0:54 | 49.923
2020-02-17 | 0:54 | 49.921
2020-02-17 | 0:54 | 49.919
2020-02-17 | 0:54 | 49.921
2020-02-17 | 0:54 | 49.92
2020-02-17 | 0:54 | 49.922
2020-02-17 | 0:54 | 49.922
2020-02-17 | 0:55 | 49.925
2020-02-17 | 0:55 | 49.926
2020-02-17 | 0:55 | 49.928
2020-02-17 | 0:55 | 49.93
2020-02-17 | 0:55 | 49.931
2020-02-17 | 0:55 | 49.933
2020-02-17 | 0:55 | 49.935
2020-02-17 | 0:55 | 49.934
2020-02-17 | 0:55 | 49.933
2020-02-17 | 0:55 | 49.933
2020-02-17 | 0:55 | 49.933
2020-02-17 | 0:55 | 49.935
2020-02-17 | 0:55 | 49.935
2020-02-17 | 0:55 | 49.937
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.941
2020-02-17 | 0:55 | 49.941
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.938
2020-02-17 | 0:55 | 49.935
2020-02-17 | 0:55 | 49.934
2020-02-17 | 0:55 | 49.933
2020-02-17 | 0:55 | 49.933
2020-02-17 | 0:55 | 49.937
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.938
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.94
2020-02-17 | 0:55 | 49.937
2020-02-17 | 0:55 | 49.935
2020-02-17 | 0:55 | 49.932
2020-02-17 | 0:55 | 49.93
2020-02-17 | 0:55 | 49.93
2020-02-17 | 0:55 | 49.934
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.941
2020-02-17 | 0:55 | 49.944
2020-02-17 | 0:55 | 49.947
2020-02-17 | 0:55 | 49.95
2020-02-17 | 0:55 | 49.95
2020-02-17 | 0:55 | 49.951
2020-02-17 | 0:55 | 49.949
2020-02-17 | 0:55 | 49.946
2020-02-17 | 0:55 | 49.947
2020-02-17 | 0:55 | 49.942
2020-02-17 | 0:55 | 49.938
2020-02-17 | 0:55 | 49.938
2020-02-17 | 0:55 | 49.939
2020-02-17 | 0:55 | 49.94
2020-02-17 | 0:55 | 49.945
2020-02-17 | 0:55 | 49.95
2020-02-17 | 0:55 | 49.953
2020-02-17 | 0:55 | 49.953
2020-02-17 | 0:55 | 49.954
2020-02-17 | 0:55 | 49.955
2020-02-17 | 0:56 | 49.955
2020-02-17 | 0:56 | 49.957
2020-02-17 | 0:56 | 49.958
2020-02-17 | 0:56 | 49.956
2020-02-17 | 0:56 | 49.956
2020-02-17 | 0:56 | 49.956
2020-02-17 | 0:56 | 49.958
2020-02-17 | 0:56 | 49.957
2020-02-17 | 0:56 | 49.957
2020-02-17 | 0:56 | 49.958
2020-02-17 | 0:56 | 49.961
2020-02-17 | 0:56 | 49.963
2020-02-17 | 0:56 | 49.963
2020-02-17 | 0:56 | 49.964
2020-02-17 | 0:56 | 49.966
2020-02-17 | 0:56 | 49.971
2020-02-17 | 0:56 | 49.975
2020-02-17 | 0:56 | 49.978
2020-02-17 | 0:56 | 49.981
2020-02-17 | 0:56 | 49.982
2020-02-17 | 0:56 | 49.985
2020-02-17 | 0:56 | 49.987
2020-02-17 | 0:56 | 49.988
2020-02-17 | 0:56 | 49.988
2020-02-17 | 0:56 | 49.988
2020-02-17 | 0:56 | 49.99
2020-02-17 | 0:56 | 49.993
2020-02-17 | 0:56 | 49.995
2020-02-17 | 0:56 | 49.998
2020-02-17 | 0:56 | 50.002

## Event 20200219-1
In UTC
Date | Time | Freq
2020-02-19 | 4:41 | 49.975
2020-02-19 | 4:41 | 49.976
2020-02-19 | 4:41 | 49.977
2020-02-19 | 4:41 | 49.982
2020-02-19 | 4:41 | 49.986
2020-02-19 | 4:41 | 49.988
2020-02-19 | 4:41 | 49.991
2020-02-19 | 4:41 | 49.993
2020-02-19 | 4:41 | 49.993
2020-02-19 | 4:41 | 49.994
2020-02-19 | 4:41 | 49.996
2020-02-19 | 4:41 | 49.995
2020-02-19 | 4:41 | 49.995
2020-02-19 | 4:41 | 49.995
2020-02-19 | 4:41 | 49.995
2020-02-19 | 4:41 | 49.993
2020-02-19 | 4:41 | 49.991
2020-02-19 | 4:41 | 49.989
2020-02-19 | 4:41 | 49.987
2020-02-19 | 4:41 | 49.986
2020-02-19 | 4:41 | 49.987
2020-02-19 | 4:41 | 49.988
2020-02-19 | 4:41 | 49.988
2020-02-19 | 4:41 | 49.989
2020-02-19 | 4:41 | 49.989
2020-02-19 | 4:41 | 49.991
2020-02-19 | 4:41 | 49.993
2020-02-19 | 4:41 | 49.994
2020-02-19 | 4:41 | 49.996
2020-02-19 | 4:41 | 49.997
2020-02-19 | 4:42 | 49.997
2020-02-19 | 4:42 | 49.997
2020-02-19 | 4:42 | 49.998
2020-02-19 | 4:42 | 49.998
2020-02-19 | 4:42 | 49.996
2020-02-19 | 4:42 | 49.994
2020-02-19 | 4:42 | 49.991
2020-02-19 | 4:42 | 49.988
2020-02-19 | 4:42 | 49.985
2020-02-19 | 4:42 | 49.982
2020-02-19 | 4:42 | 49.98
2020-02-19 | 4:42 | 49.977
2020-02-19 | 4:42 | 49.977
2020-02-19 | 4:42 | 49.976
2020-02-19 | 4:42 | 49.975
2020-02-19 | 4:42 | 49.975
2020-02-19 | 4:42 | 49.974
2020-02-19 | 4:42 | 49.974
2020-02-19 | 4:42 | 49.976
2020-02-19 | 4:42 | 49.976
2020-02-19 | 4:42 | 49.979
2020-02-19 | 4:42 | 49.98
2020-02-19 | 4:42 | 49.983
2020-02-19 | 4:42 | 49.984
2020-02-19 | 4:42 | 49.985
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.987
2020-02-19 | 4:42 | 49.989
2020-02-19 | 4:42 | 49.989
2020-02-19 | 4:42 | 49.99
2020-02-19 | 4:42 | 49.991
2020-02-19 | 4:42 | 49.991
2020-02-19 | 4:42 | 49.989
2020-02-19 | 4:42 | 49.987
2020-02-19 | 4:42 | 49.986
2020-02-19 | 4:42 | 49.985
2020-02-19 | 4:42 | 49.983
2020-02-19 | 4:42 | 49.983
2020-02-19 | 4:42 | 49.982
2020-02-19 | 4:42 | 49.983
2020-02-19 | 4:42 | 49.984
2020-02-19 | 4:42 | 49.984
2020-02-19 | 4:42 | 49.981
2020-02-19 | 4:42 | 49.982
2020-02-19 | 4:42 | 49.981
2020-02-19 | 4:42 | 49.978
2020-02-19 | 4:42 | 49.976
2020-02-19 | 4:42 | 49.975
2020-02-19 | 4:42 | 49.974
2020-02-19 | 4:42 | 49.975
2020-02-19 | 4:42 | 49.976
2020-02-19 | 4:42 | 49.978
2020-02-19 | 4:42 | 49.981
2020-02-19 | 4:42 | 49.985
2020-02-19 | 4:42 | 49.997
2020-02-19 | 4:43 | 50.007
2020-02-19 | 4:43 | 50.016
2020-02-19 | 4:43 | 50.021
2020-02-19 | 4:43 | 50.022
2020-02-19 | 4:43 | 50.022
2020-02-19 | 4:43 | 50.021
2020-02-19 | 4:43 | 50.021
2020-02-19 | 4:43 | 50.023
2020-02-19 | 4:43 | 50.02
2020-02-19 | 4:43 | 50.018
2020-02-19 | 4:43 | 50.015
2020-02-19 | 4:43 | 50.013
2020-02-19 | 4:43 | 50.012
2020-02-19 | 4:43 | 50.01
2020-02-19 | 4:43 | 50.008
2020-02-19 | 4:43 | 50.007
2020-02-19 | 4:43 | 50.008
2020-02-19 | 4:43 | 50.007
2020-02-19 | 4:43 | 50.005
2020-02-19 | 4:43 | 50.004
2020-02-19 | 4:43 | 50.003
2020-02-19 | 4:43 | 50.002
2020-02-19 | 4:43 | 50.001
2020-02-19 | 4:43 | 50
2020-02-19 | 4:43 | 49.997
2020-02-19 | 4:43 | 49.993
2020-02-19 | 4:43 | 49.992
2020-02-19 | 4:43 | 49.99
2020-02-19 | 4:43 | 49.991
2020-02-19 | 4:43 | 49.993
2020-02-19 | 4:43 | 49.995
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.997
2020-02-19 | 4:43 | 49.998
2020-02-19 | 4:43 | 49.999
2020-02-19 | 4:43 | 50
2020-02-19 | 4:43 | 49.998
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.993
2020-02-19 | 4:43 | 49.991
2020-02-19 | 4:43 | 49.989
2020-02-19 | 4:43 | 49.992
2020-02-19 | 4:43 | 49.995
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.996
2020-02-19 | 4:43 | 49.998
2020-02-19 | 4:43 | 49.999
2020-02-19 | 4:43 | 49.999
2020-02-19 | 4:43 | 49.999
2020-02-19 | 4:43 | 49.997
2020-02-19 | 4:43 | 49.994
2020-02-19 | 4:43 | 49.99
2020-02-19 | 4:43 | 49.984
2020-02-19 | 4:43 | 49.979
2020-02-19 | 4:43 | 49.978
2020-02-19 | 4:43 | 49.979
2020-02-19 | 4:44 | 49.981
2020-02-19 | 4:44 | 49.984
2020-02-19 | 4:44 | 49.987
2020-02-19 | 4:44 | 49.989
2020-02-19 | 4:44 | 49.992
2020-02-19 | 4:44 | 49.995
2020-02-19 | 4:44 | 49.997
2020-02-19 | 4:44 | 49.999
2020-02-19 | 4:44 | 50.002
2020-02-19 | 4:44 | 50.002
2020-02-19 | 4:44 | 50.003
2020-02-19 | 4:44 | 50.004
2020-02-19 | 4:44 | 50.005
2020-02-19 | 4:44 | 50.003
2020-02-19 | 4:44 | 50.001
2020-02-19 | 4:44 | 49.999
2020-02-19 | 4:44 | 49.999
2020-02-19 | 4:44 | 49.998
2020-02-19 | 4:44 | 49.997
2020-02-19 | 4:44 | 49.998
2020-02-19 | 4:44 | 49.996
2020-02-19 | 4:44 | 49.995
2020-02-19 | 4:44 | 49.997
2020-02-19 | 4:44 | 50
2020-02-19 | 4:44 | 49.999
2020-02-19 | 4:44 | 49.999
2020-02-19 | 4:44 | 50.002
2020-02-19 | 4:44 | 50.005
2020-02-19 | 4:44 | 50.008
2020-02-19 | 4:44 | 50.012
2020-02-19 | 4:44 | 50.015
2020-02-19 | 4:44 | 50.016
2020-02-19 | 4:44 | 50.017
2020-02-19 | 4:44 | 50.018
2020-02-19 | 4:44 | 50.018
2020-02-19 | 4:44 | 50.018
2020-02-19 | 4:44 | 50.019
2020-02-19 | 4:44 | 50.02
2020-02-19 | 4:44 | 50.022
2020-02-19 | 4:44 | 50.024
2020-02-19 | 4:44 | 50.025
2020-02-19 | 4:44 | 50.024
2020-02-19 | 4:44 | 50.022
2020-02-19 | 4:44 | 50.021
2020-02-19 | 4:44 | 50.021
2020-02-19 | 4:44 | 50.021
2020-02-19 | 4:44 | 50.02
2020-02-19 | 4:44 | 50.02
2020-02-19 | 4:44 | 50.02
2020-02-19 | 4:44 | 50.019
2020-02-19 | 4:44 | 50.019
2020-02-19 | 4:44 | 50.019
2020-02-19 | 4:44 | 50.021
2020-02-19 | 4:44 | 50.021
2020-02-19 | 4:44 | 50.02
2020-02-19 | 4:44 | 50.021
2020-02-19 | 4:44 | 50.023
2020-02-19 | 4:44 | 50.024
2020-02-19 | 4:44 | 50.026
2020-02-19 | 4:44 | 50.028
2020-02-19 | 4:44 | 50.03
2020-02-19 | 4:45 | 50.03
2020-02-19 | 4:45 | 50.032
2020-02-19 | 4:45 | 50.032
2020-02-19 | 4:45 | 50.032
2020-02-19 | 4:45 | 50.031
2020-02-19 | 4:45 | 50.03
2020-02-19 | 4:45 | 50.027
2020-02-19 | 4:45 | 50.025
2020-02-19 | 4:45 | 50.023
2020-02-19 | 4:45 | 50.023
2020-02-19 | 4:45 | 50.022
2020-02-19 | 4:45 | 50.021
2020-02-19 | 4:45 | 50.019
2020-02-19 | 4:45 | 50.018
2020-02-19 | 4:45 | 50.017
2020-02-19 | 4:45 | 50.017
2020-02-19 | 4:45 | 50.017
2020-02-19 | 4:45 | 50.017
2020-02-19 | 4:45 | 50.018
2020-02-19 | 4:45 | 50.02
2020-02-19 | 4:45 | 50.021
2020-02-19 | 4:45 | 50.024
2020-02-19 | 4:45 | 50.026
2020-02-19 | 4:45 | 50.029
2020-02-19 | 4:45 | 50.034
2020-02-19 | 4:45 | 50.04
2020-02-19 | 4:45 | 50.04
2020-02-19 | 4:45 | 50.039
2020-02-19 | 4:45 | 50.037

## Event 20200224-1
In UTC
Date | Time | Freq
2020-02-24 | 13:31 | 49.945
2020-02-24 | 13:31 | 49.946
2020-02-24 | 13:31 | 49.944
2020-02-24 | 13:31 | 49.94
2020-02-24 | 13:31 | 49.938
2020-02-24 | 13:31 | 49.936
2020-02-24 | 13:31 | 49.934
2020-02-24 | 13:31 | 49.933
2020-02-24 | 13:31 | 49.935
2020-02-24 | 13:31 | 49.934
2020-02-24 | 13:31 | 49.935
2020-02-24 | 13:31 | 49.937
2020-02-24 | 13:31 | 49.94
2020-02-24 | 13:31 | 49.94
2020-02-24 | 13:31 | 49.943
2020-02-24 | 13:31 | 49.942
2020-02-24 | 13:31 | 49.941
2020-02-24 | 13:31 | 49.944
2020-02-24 | 13:31 | 49.944
2020-02-24 | 13:31 | 49.947
2020-02-24 | 13:31 | 49.947
2020-02-24 | 13:31 | 49.949
2020-02-24 | 13:31 | 49.95
2020-02-24 | 13:31 | 49.95
2020-02-24 | 13:31 | 49.953
2020-02-24 | 13:31 | 49.952
2020-02-24 | 13:31 | 49.956
2020-02-24 | 13:31 | 49.956
2020-02-24 | 13:31 | 49.959
2020-02-24 | 13:31 | 49.96
2020-02-24 | 13:32 | 49.965
2020-02-24 | 13:32 | 49.968
2020-02-24 | 13:32 | 49.97
2020-02-24 | 13:32 | 49.972
2020-02-24 | 13:32 | 49.971
2020-02-24 | 13:32 | 49.974
2020-02-24 | 13:32 | 49.974
2020-02-24 | 13:32 | 49.974
2020-02-24 | 13:32 | 49.976
2020-02-24 | 13:32 | 49.981
2020-02-24 | 13:32 | 49.981
2020-02-24 | 13:32 | 49.982
2020-02-24 | 13:32 | 49.985
2020-02-24 | 13:32 | 49.988
2020-02-24 | 13:32 | 49.992
2020-02-24 | 13:32 | 49.994
2020-02-24 | 13:32 | 49.991
2020-02-24 | 13:32 | 49.991
2020-02-24 | 13:32 | 49.99
2020-02-24 | 13:32 | 49.989
2020-02-24 | 13:32 | 49.986
2020-02-24 | 13:32 | 49.987
2020-02-24 | 13:32 | 49.984
2020-02-24 | 13:32 | 49.983
2020-02-24 | 13:32 | 49.981
2020-02-24 | 13:32 | 49.981
2020-02-24 | 13:32 | 49.981
2020-02-24 | 13:32 | 49.982
2020-02-24 | 13:32 | 49.983
2020-02-24 | 13:32 | 49.981
2020-02-24 | 13:32 | 49.98
2020-02-24 | 13:32 | 49.98
2020-02-24 | 13:32 | 49.978
2020-02-24 | 13:32 | 49.977
2020-02-24 | 13:32 | 49.976
2020-02-24 | 13:32 | 49.937
2020-02-24 | 13:32 | 49.844
2020-02-24 | 13:32 | 49.793
2020-02-24 | 13:32 | 49.741
2020-02-24 | 13:32 | 49.699
2020-02-24 | 13:32 | 49.673
2020-02-24 | 13:32 | 49.646
2020-02-24 | 13:32 | 49.626
2020-02-24 | 13:32 | 49.61
2020-02-24 | 13:32 | 49.598
2020-02-24 | 13:32 | 49.596
2020-02-24 | 13:32 | 49.596
2020-02-24 | 13:32 | 49.596
2020-02-24 | 13:32 | 49.598
2020-02-24 | 13:32 | 49.598
2020-02-24 | 13:32 | 49.601
2020-02-24 | 13:32 | 49.603
2020-02-24 | 13:32 | 49.604
2020-02-24 | 13:32 | 49.607
2020-02-24 | 13:32 | 49.608
2020-02-24 | 13:32 | 49.613
2020-02-24 | 13:32 | 49.617
2020-02-24 | 13:32 | 49.621
2020-02-24 | 13:32 | 49.626
2020-02-24 | 13:32 | 49.626
2020-02-24 | 13:32 | 49.629
2020-02-24 | 13:33 | 49.63
2020-02-24 | 13:33 | 49.634
2020-02-24 | 13:33 | 49.633
2020-02-24 | 13:33 | 49.635
2020-02-24 | 13:33 | 49.636
2020-02-24 | 13:33 | 49.636
2020-02-24 | 13:33 | 49.635
2020-02-24 | 13:33 | 49.634
2020-02-24 | 13:33 | 49.633
2020-02-24 | 13:33 | 49.633
2020-02-24 | 13:33 | 49.632
2020-02-24 | 13:33 | 49.633
2020-02-24 | 13:33 | 49.635
2020-02-24 | 13:33 | 49.63
2020-02-24 | 13:33 | 49.63
2020-02-24 | 13:33 | 49.626
2020-02-24 | 13:33 | 49.62
2020-02-24 | 13:33 | 49.615
2020-02-24 | 13:33 | 49.61
2020-02-24 | 13:33 | 49.606
2020-02-24 | 13:33 | 49.605
2020-02-24 | 13:33 | 49.603
2020-02-24 | 13:33 | 49.602
2020-02-24 | 13:33 | 49.602
2020-02-24 | 13:33 | 49.6
2020-02-24 | 13:33 | 49.598
2020-02-24 | 13:33 | 49.601
2020-02-24 | 13:33 | 49.601
2020-02-24 | 13:33 | 49.604
2020-02-24 | 13:33 | 49.604
2020-02-24 | 13:33 | 49.606
2020-02-24 | 13:33 | 49.608
2020-02-24 | 13:33 | 49.607
2020-02-24 | 13:33 | 49.605
2020-02-24 | 13:33 | 49.605
2020-02-24 | 13:33 | 49.604
2020-02-24 | 13:33 | 49.604
2020-02-24 | 13:33 | 49.605
2020-02-24 | 13:33 | 49.605
2020-02-24 | 13:33 | 49.607
2020-02-24 | 13:33 | 49.613
2020-02-24 | 13:33 | 49.621
2020-02-24 | 13:33 | 49.629
2020-02-24 | 13:33 | 49.635
2020-02-24 | 13:33 | 49.642
2020-02-24 | 13:33 | 49.648
2020-02-24 | 13:33 | 49.654
2020-02-24 | 13:33 | 49.66
2020-02-24 | 13:33 | 49.667
2020-02-24 | 13:33 | 49.671
2020-02-24 | 13:33 | 49.678
2020-02-24 | 13:33 | 49.685
2020-02-24 | 13:33 | 49.693
2020-02-24 | 13:33 | 49.7
2020-02-24 | 13:33 | 49.709
2020-02-24 | 13:33 | 49.713
2020-02-24 | 13:33 | 49.718
2020-02-24 | 13:33 | 49.725
2020-02-24 | 13:33 | 49.73
2020-02-24 | 13:34 | 49.736
2020-02-24 | 13:34 | 49.74
2020-02-24 | 13:34 | 49.744
2020-02-24 | 13:34 | 49.745
2020-02-24 | 13:34 | 49.751
2020-02-24 | 13:34 | 49.755
2020-02-24 | 13:34 | 49.762
2020-02-24 | 13:34 | 49.765
2020-02-24 | 13:34 | 49.767
2020-02-24 | 13:34 | 49.77
2020-02-24 | 13:34 | 49.771
2020-02-24 | 13:34 | 49.774
2020-02-24 | 13:34 | 49.777
2020-02-24 | 13:34 | 49.782
2020-02-24 | 13:34 | 49.783
2020-02-24 | 13:34 | 49.785
2020-02-24 | 13:34 | 49.787
2020-02-24 | 13:34 | 49.787
2020-02-24 | 13:34 | 49.788
2020-02-24 | 13:34 | 49.79
2020-02-24 | 13:34 | 49.791
2020-02-24 | 13:34 | 49.794
2020-02-24 | 13:34 | 49.793
2020-02-24 | 13:34 | 49.795
2020-02-24 | 13:34 | 49.795
2020-02-24 | 13:34 | 49.797
2020-02-24 | 13:34 | 49.798
2020-02-24 | 13:34 | 49.799
2020-02-24 | 13:34 | 49.796
2020-02-24 | 13:34 | 49.796
2020-02-24 | 13:34 | 49.797
2020-02-24 | 13:34 | 49.798
2020-02-24 | 13:34 | 49.801
2020-02-24 | 13:34 | 49.803
2020-02-24 | 13:34 | 49.806
2020-02-24 | 13:34 | 49.811
2020-02-24 | 13:34 | 49.815
2020-02-24 | 13:34 | 49.82
2020-02-24 | 13:34 | 49.823
2020-02-24 | 13:34 | 49.825
2020-02-24 | 13:34 | 49.828
2020-02-24 | 13:34 | 49.828
2020-02-24 | 13:34 | 49.828
2020-02-24 | 13:34 | 49.832
2020-02-24 | 13:34 | 49.833
2020-02-24 | 13:34 | 49.835
2020-02-24 | 13:34 | 49.836
2020-02-24 | 13:34 | 49.84
2020-02-24 | 13:34 | 49.841
2020-02-24 | 13:34 | 49.842
2020-02-24 | 13:34 | 49.845
2020-02-24 | 13:34 | 49.846
2020-02-24 | 13:34 | 49.844
2020-02-24 | 13:34 | 49.845
2020-02-24 | 13:34 | 49.843
2020-02-24 | 13:34 | 49.846
2020-02-24 | 13:34 | 49.843
2020-02-24 | 13:34 | 49.844
2020-02-24 | 13:34 | 49.844
2020-02-24 | 13:34 | 49.844
2020-02-24 | 13:34 | 49.846
2020-02-24 | 13:35 | 49.845
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.849
2020-02-24 | 13:35 | 49.849
2020-02-24 | 13:35 | 49.848
2020-02-24 | 13:35 | 49.85
2020-02-24 | 13:35 | 49.851
2020-02-24 | 13:35 | 49.851
2020-02-24 | 13:35 | 49.848
2020-02-24 | 13:35 | 49.849
2020-02-24 | 13:35 | 49.851
2020-02-24 | 13:35 | 49.852
2020-02-24 | 13:35 | 49.854
2020-02-24 | 13:35 | 49.853
2020-02-24 | 13:35 | 49.853
2020-02-24 | 13:35 | 49.854
2020-02-24 | 13:35 | 49.853
2020-02-24 | 13:35 | 49.849
2020-02-24 | 13:35 | 49.85
2020-02-24 | 13:35 | 49.849
2020-02-24 | 13:35 | 49.848
2020-02-24 | 13:35 | 49.845
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.844
2020-02-24 | 13:35 | 49.845
2020-02-24 | 13:35 | 49.843
2020-02-24 | 13:35 | 49.845
2020-02-24 | 13:35 | 49.846
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.848
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.848
2020-02-24 | 13:35 | 49.846
2020-02-24 | 13:35 | 49.845
2020-02-24 | 13:35 | 49.843
2020-02-24 | 13:35 | 49.845
2020-02-24 | 13:35 | 49.847
2020-02-24 | 13:35 | 49.849
2020-02-24 | 13:35 | 49.853
2020-02-24 | 13:35 | 49.858
2020-02-24 | 13:35 | 49.858
2020-02-24 | 13:35 | 49.862
2020-02-24 | 13:35 | 49.863
2020-02-24 | 13:35 | 49.863
2020-02-24 | 13:35 | 49.864
2020-02-24 | 13:35 | 49.865
2020-02-24 | 13:35 | 49.864
2020-02-24 | 13:35 | 49.866
2020-02-24 | 13:35 | 49.866
2020-02-24 | 13:35 | 49.868
2020-02-24 | 13:35 | 49.869
2020-02-24 | 13:35 | 49.869
2020-02-24 | 13:35 | 49.87
2020-02-24 | 13:35 | 49.871
2020-02-24 | 13:35 | 49.873
2020-02-24 | 13:35 | 49.871
2020-02-24 | 13:35 | 49.873
2020-02-24 | 13:36 | 49.874
2020-02-24 | 13:36 | 49.876
2020-02-24 | 13:36 | 49.879
2020-02-24 | 13:36 | 49.882
2020-02-24 | 13:36 | 49.881
2020-02-24 | 13:36 | 49.885
2020-02-24 | 13:36 | 49.888
2020-02-24 | 13:36 | 49.896
2020-02-24 | 13:36 | 49.904
2020-02-24 | 13:36 | 49.909
2020-02-24 | 13:36 | 49.915
2020-02-24 | 13:36 | 49.919
2020-02-24 | 13:36 | 49.925
2020-02-24 | 13:36 | 49.932
2020-02-24 | 13:36 | 49.935
2020-02-24 | 13:36 | 49.937
2020-02-24 | 13:36 | 49.938
2020-02-24 | 13:36 | 49.941
2020-02-24 | 13:36 | 49.943
2020-02-24 | 13:36 | 49.945
2020-02-24 | 13:36 | 49.947
2020-02-24 | 13:36 | 49.951
2020-02-24 | 13:36 | 49.952
2020-02-24 | 13:36 | 49.953
2020-02-24 | 13:36 | 49.954
2020-02-24 | 13:36 | 49.954
2020-02-24 | 13:36 | 49.956
2020-02-24 | 13:36 | 49.96
2020-02-24 | 13:36 | 49.96
2020-02-24 | 13:36 | 49.96
2020-02-24 | 13:36 | 49.962
2020-02-24 | 13:36 | 49.965
2020-02-24 | 13:36 | 49.968
2020-02-24 | 13:36 | 49.97
2020-02-24 | 13:36 | 49.972
2020-02-24 | 13:36 | 49.976
2020-02-24 | 13:36 | 49.982
2020-02-24 | 13:36 | 49.986
2020-02-24 | 13:36 | 49.989
2020-02-24 | 13:36 | 49.99
2020-02-24 | 13:36 | 49.989
2020-02-24 | 13:36 | 49.99
2020-02-24 | 13:36 | 49.99
2020-02-24 | 13:36 | 49.991
2020-02-24 | 13:36 | 49.992
2020-02-24 | 13:36 | 49.993
2020-02-24 | 13:36 | 49.994
2020-02-24 | 13:36 | 49.997
2020-02-24 | 13:36 | 49.997
2020-02-24 | 13:36 | 49.994
2020-02-24 | 13:36 | 49.993
2020-02-24 | 13:36 | 49.992
2020-02-24 | 13:36 | 49.989
2020-02-24 | 13:36 | 49.99
2020-02-24 | 13:36 | 49.989
2020-02-24 | 13:36 | 49.991
2020-02-24 | 13:36 | 49.99
2020-02-24 | 13:36 | 49.992
2020-02-24 | 13:36 | 49.993
2020-02-24 | 13:36 | 49.994
2020-02-24 | 13:36 | 49.996
2020-02-24 | 13:37 | 50.003
2020-02-24 | 13:37 | 50.005
2020-02-24 | 13:37 | 50.012
2020-02-24 | 13:37 | 50.014
2020-02-24 | 13:37 | 50.016
2020-02-24 | 13:37 | 50.022
2020-02-24 | 13:37 | 50.026
2020-02-24 | 13:37 | 50.029
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.035
2020-02-24 | 13:37 | 50.035
2020-02-24 | 13:37 | 50.036
2020-02-24 | 13:37 | 50.035
2020-02-24 | 13:37 | 50.034
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.03
2020-02-24 | 13:37 | 50.03
2020-02-24 | 13:37 | 50.03
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.03
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.031
2020-02-24 | 13:37 | 50.029
2020-02-24 | 13:37 | 50.026
2020-02-24 | 13:37 | 50.024
2020-02-24 | 13:37 | 50.02
2020-02-24 | 13:37 | 50.017

## Event 20200224-2
In UTC
Date | Time | Freq
2020-02-24 | 18:47 | 49.967
2020-02-24 | 18:47 | 49.967
2020-02-24 | 18:47 | 49.971
2020-02-24 | 18:47 | 49.97
2020-02-24 | 18:47 | 49.97
2020-02-24 | 18:47 | 49.969
2020-02-24 | 18:47 | 49.969
2020-02-24 | 18:47 | 49.967
2020-02-24 | 18:47 | 49.966
2020-02-24 | 18:47 | 49.965
2020-02-24 | 18:47 | 49.963
2020-02-24 | 18:47 | 49.962
2020-02-24 | 18:47 | 49.961
2020-02-24 | 18:47 | 49.962
2020-02-24 | 18:47 | 49.96
2020-02-24 | 18:47 | 49.958
2020-02-24 | 18:47 | 49.957
2020-02-24 | 18:47 | 49.957
2020-02-24 | 18:47 | 49.957
2020-02-24 | 18:47 | 49.956
2020-02-24 | 18:47 | 49.956
2020-02-24 | 18:47 | 49.955
2020-02-24 | 18:47 | 49.957
2020-02-24 | 18:47 | 49.959
2020-02-24 | 18:47 | 49.959
2020-02-24 | 18:47 | 49.962
2020-02-24 | 18:47 | 49.964
2020-02-24 | 18:47 | 49.968
2020-02-24 | 18:47 | 49.97
2020-02-24 | 18:47 | 49.973
2020-02-24 | 18:48 | 49.976
2020-02-24 | 18:48 | 49.976
2020-02-24 | 18:48 | 49.977
2020-02-24 | 18:48 | 49.979
2020-02-24 | 18:48 | 49.979
2020-02-24 | 18:48 | 49.98
2020-02-24 | 18:48 | 49.979
2020-02-24 | 18:48 | 49.978
2020-02-24 | 18:48 | 49.977
2020-02-24 | 18:48 | 49.976
2020-02-24 | 18:48 | 49.974
2020-02-24 | 18:48 | 49.973
2020-02-24 | 18:48 | 49.971
2020-02-24 | 18:48 | 49.969
2020-02-24 | 18:48 | 49.967
2020-02-24 | 18:48 | 49.965
2020-02-24 | 18:48 | 49.966
2020-02-24 | 18:48 | 49.966
2020-02-24 | 18:48 | 49.97
2020-02-24 | 18:48 | 49.972
2020-02-24 | 18:48 | 49.975
2020-02-24 | 18:48 | 49.979
2020-02-24 | 18:48 | 49.982
2020-02-24 | 18:48 | 49.985
2020-02-24 | 18:48 | 49.987
2020-02-24 | 18:48 | 49.987
2020-02-24 | 18:48 | 49.988
2020-02-24 | 18:48 | 49.987
2020-02-24 | 18:48 | 49.986
2020-02-24 | 18:48 | 49.985
2020-02-24 | 18:48 | 49.982
2020-02-24 | 18:48 | 49.98
2020-02-24 | 18:48 | 49.98
2020-02-24 | 18:48 | 49.979
2020-02-24 | 18:48 | 49.979
2020-02-24 | 18:48 | 49.98
2020-02-24 | 18:48 | 49.981
2020-02-24 | 18:48 | 49.981
2020-02-24 | 18:48 | 49.982
2020-02-24 | 18:48 | 49.984
2020-02-24 | 18:48 | 49.985
2020-02-24 | 18:48 | 49.986
2020-02-24 | 18:48 | 49.985
2020-02-24 | 18:48 | 49.987
2020-02-24 | 18:48 | 49.99
2020-02-24 | 18:48 | 49.993
2020-02-24 | 18:48 | 49.995
2020-02-24 | 18:48 | 49.997
2020-02-24 | 18:48 | 49.995
2020-02-24 | 18:48 | 49.998
2020-02-24 | 18:48 | 49.996
2020-02-24 | 18:48 | 49.997
2020-02-24 | 18:48 | 49.998
2020-02-24 | 18:48 | 49.995
2020-02-24 | 18:48 | 49.993
2020-02-24 | 18:48 | 49.988
2020-02-24 | 18:48 | 49.983
2020-02-24 | 18:48 | 49.977
2020-02-24 | 18:48 | 49.972
2020-02-24 | 18:48 | 49.97
2020-02-24 | 18:48 | 49.969
2020-02-24 | 18:49 | 49.967
2020-02-24 | 18:49 | 49.969
2020-02-24 | 18:49 | 49.968
2020-02-24 | 18:49 | 49.965
2020-02-24 | 18:49 | 49.962
2020-02-24 | 18:49 | 49.95
2020-02-24 | 18:49 | 49.928
2020-02-24 | 18:49 | 49.913
2020-02-24 | 18:49 | 49.898
2020-02-24 | 18:49 | 49.888
2020-02-24 | 18:49 | 49.88
2020-02-24 | 18:49 | 49.876
2020-02-24 | 18:49 | 49.875
2020-02-24 | 18:49 | 49.876
2020-02-24 | 18:49 | 49.877
2020-02-24 | 18:49 | 49.88
2020-02-24 | 18:49 | 49.884
2020-02-24 | 18:49 | 49.888
2020-02-24 | 18:49 | 49.893
2020-02-24 | 18:49 | 49.896
2020-02-24 | 18:49 | 49.899
2020-02-24 | 18:49 | 49.9
2020-02-24 | 18:49 | 49.898
2020-02-24 | 18:49 | 49.896
2020-02-24 | 18:49 | 49.894
2020-02-24 | 18:49 | 49.891
2020-02-24 | 18:49 | 49.89
2020-02-24 | 18:49 | 49.888
2020-02-24 | 18:49 | 49.888
2020-02-24 | 18:49 | 49.887
2020-02-24 | 18:49 | 49.888
2020-02-24 | 18:49 | 49.887
2020-02-24 | 18:49 | 49.885
2020-02-24 | 18:49 | 49.883
2020-02-24 | 18:49 | 49.879
2020-02-24 | 18:49 | 49.876
2020-02-24 | 18:49 | 49.871
2020-02-24 | 18:49 | 49.865
2020-02-24 | 18:49 | 49.86
2020-02-24 | 18:49 | 49.855
2020-02-24 | 18:49 | 49.85
2020-02-24 | 18:49 | 49.846
2020-02-24 | 18:49 | 49.843
2020-02-24 | 18:49 | 49.84
2020-02-24 | 18:49 | 49.838
2020-02-24 | 18:49 | 49.837
2020-02-24 | 18:49 | 49.836
2020-02-24 | 18:49 | 49.834
2020-02-24 | 18:49 | 49.834
2020-02-24 | 18:49 | 49.83
2020-02-24 | 18:49 | 49.83
2020-02-24 | 18:49 | 49.83
2020-02-24 | 18:49 | 49.83
2020-02-24 | 18:49 | 49.833
2020-02-24 | 18:49 | 49.834
2020-02-24 | 18:49 | 49.837
2020-02-24 | 18:49 | 49.836
2020-02-24 | 18:49 | 49.838
2020-02-24 | 18:49 | 49.837
2020-02-24 | 18:50 | 49.839
2020-02-24 | 18:50 | 49.841
2020-02-24 | 18:50 | 49.843
2020-02-24 | 18:50 | 49.844
2020-02-24 | 18:50 | 49.845
2020-02-24 | 18:50 | 49.846
2020-02-24 | 18:50 | 49.85
2020-02-24 | 18:50 | 49.852
2020-02-24 | 18:50 | 49.854
2020-02-24 | 18:50 | 49.855
2020-02-24 | 18:50 | 49.858
2020-02-24 | 18:50 | 49.858
2020-02-24 | 18:50 | 49.859
2020-02-24 | 18:50 | 49.859
2020-02-24 | 18:50 | 49.861
2020-02-24 | 18:50 | 49.859
2020-02-24 | 18:50 | 49.86
2020-02-24 | 18:50 | 49.858
2020-02-24 | 18:50 | 49.857
2020-02-24 | 18:50 | 49.856
2020-02-24 | 18:50 | 49.854
2020-02-24 | 18:50 | 49.853
2020-02-24 | 18:50 | 49.852
2020-02-24 | 18:50 | 49.852
2020-02-24 | 18:50 | 49.851
2020-02-24 | 18:50 | 49.852
2020-02-24 | 18:50 | 49.851
2020-02-24 | 18:50 | 49.855
2020-02-24 | 18:50 | 49.857
2020-02-24 | 18:50 | 49.86
2020-02-24 | 18:50 | 49.861
2020-02-24 | 18:50 | 49.863
2020-02-24 | 18:50 | 49.865
2020-02-24 | 18:50 | 49.866
2020-02-24 | 18:50 | 49.87
2020-02-24 | 18:50 | 49.876
2020-02-24 | 18:50 | 49.884
2020-02-24 | 18:50 | 49.892
2020-02-24 | 18:50 | 49.905
2020-02-24 | 18:50 | 49.914
2020-02-24 | 18:50 | 49.927
2020-02-24 | 18:50 | 49.937
2020-02-24 | 18:50 | 49.948
2020-02-24 | 18:50 | 49.955
2020-02-24 | 18:50 | 49.96
2020-02-24 | 18:50 | 49.961
2020-02-24 | 18:50 | 49.961
2020-02-24 | 18:50 | 49.96
2020-02-24 | 18:50 | 49.96
2020-02-24 | 18:50 | 49.958
2020-02-24 | 18:50 | 49.956
2020-02-24 | 18:50 | 49.955
2020-02-24 | 18:50 | 49.959
2020-02-24 | 18:50 | 49.965
2020-02-24 | 18:50 | 49.967
2020-02-24 | 18:50 | 49.975
2020-02-24 | 18:50 | 49.974
2020-02-24 | 18:50 | 49.974
2020-02-24 | 18:50 | 49.973
2020-02-24 | 18:50 | 49.97
2020-02-24 | 18:50 | 49.969
2020-02-24 | 18:51 | 49.968
2020-02-24 | 18:51 | 49.97
2020-02-24 | 18:51 | 49.969
2020-02-24 | 18:51 | 49.97
2020-02-24 | 18:51 | 49.968
2020-02-24 | 18:51 | 49.97
2020-02-24 | 18:51 | 49.97
2020-02-24 | 18:51 | 49.971
2020-02-24 | 18:51 | 49.97
2020-02-24 | 18:51 | 49.969
2020-02-24 | 18:51 | 49.968
2020-02-24 | 18:51 | 49.967
2020-02-24 | 18:51 | 49.967
2020-02-24 | 18:51 | 49.965
2020-02-24 | 18:51 | 49.964
2020-02-24 | 18:51 | 49.962
2020-02-24 | 18:51 | 49.963
2020-02-24 | 18:51 | 49.962
2020-02-24 | 18:51 | 49.963
2020-02-24 | 18:51 | 49.963
2020-02-24 | 18:51 | 49.964
2020-02-24 | 18:51 | 49.965
2020-02-24 | 18:51 | 49.967
2020-02-24 | 18:51 | 49.967
2020-02-24 | 18:51 | 49.97
2020-02-24 | 18:51 | 49.973
2020-02-24 | 18:51 | 49.978
2020-02-24 | 18:51 | 49.982
2020-02-24 | 18:51 | 49.986
2020-02-24 | 18:51 | 49.988
2020-02-24 | 18:51 | 49.99
2020-02-24 | 18:51 | 49.992
2020-02-24 | 18:51 | 49.995
2020-02-24 | 18:51 | 49.999
2020-02-24 | 18:51 | 50.002
2020-02-24 | 18:51 | 50.006
2020-02-24 | 18:51 | 50.006
2020-02-24 | 18:51 | 50.009
2020-02-24 | 18:51 | 50.011
2020-02-24 | 18:51 | 50.016
2020-02-24 | 18:51 | 50.018
2020-02-24 | 18:51 | 50.018
2020-02-24 | 18:51 | 50.017
2020-02-24 | 18:51 | 50.012
2020-02-24 | 18:51 | 50.011
2020-02-24 | 18:51 | 50.007
2020-02-24 | 18:51 | 50.005
2020-02-24 | 18:51 | 50.002
2020-02-24 | 18:51 | 50.002
2020-02-24 | 18:51 | 50.002
2020-02-24 | 18:51 | 50.002
2020-02-24 | 18:51 | 50.003
2020-02-24 | 18:51 | 50.004
2020-02-24 | 18:51 | 50.005
2020-02-24 | 18:51 | 50.009
2020-02-24 | 18:51 | 50.011
2020-02-24 | 18:51 | 50.013
2020-02-24 | 18:51 | 50.014
2020-02-24 | 18:51 | 50.016
2020-02-24 | 18:52 | 50.019
2020-02-24 | 18:52 | 50.021
2020-02-24 | 18:52 | 50.02
2020-02-24 | 18:52 | 50.021
2020-02-24 | 18:52 | 50.02
2020-02-24 | 18:52 | 50.019
2020-02-24 | 18:52 | 50.017
2020-02-24 | 18:52 | 50.015
2020-02-24 | 18:52 | 50.013
2020-02-24 | 18:52 | 50.012
2020-02-24 | 18:52 | 50.011
2020-02-24 | 18:52 | 50.01
2020-02-24 | 18:52 | 50.007
2020-02-24 | 18:52 | 50.006
2020-02-24 | 18:52 | 50.001
2020-02-24 | 18:52 | 50
2020-02-24 | 18:52 | 49.998
2020-02-24 | 18:52 | 49.995
2020-02-24 | 18:52 | 49.993
2020-02-24 | 18:52 | 49.993
2020-02-24 | 18:52 | 49.995
2020-02-24 | 18:52 | 49.999
2020-02-24 | 18:52 | 50.005
2020-02-24 | 18:52 | 50.011
2020-02-24 | 18:52 | 50.015
2020-02-24 | 18:52 | 50.02
2020-02-24 | 18:52 | 50.021
2020-02-24 | 18:52 | 50.022
2020-02-24 | 18:52 | 50.021
2020-02-24 | 18:52 | 50.019

## Event 20200224-3
In UTC
Date | Time | Freq
2020-02-24 | 19:41 | 50.078
2020-02-24 | 19:41 | 50.075
2020-02-24 | 19:41 | 50.073
2020-02-24 | 19:41 | 50.069
2020-02-24 | 19:41 | 50.067
2020-02-24 | 19:41 | 50.063
2020-02-24 | 19:41 | 50.058
2020-02-24 | 19:41 | 50.054
2020-02-24 | 19:41 | 50.052
2020-02-24 | 19:41 | 50.053
2020-02-24 | 19:41 | 50.053
2020-02-24 | 19:41 | 50.051
2020-02-24 | 19:41 | 50.049
2020-02-24 | 19:41 | 50.046
2020-02-24 | 19:41 | 50.044
2020-02-24 | 19:41 | 50.043
2020-02-24 | 19:41 | 50.042
2020-02-24 | 19:41 | 50.044
2020-02-24 | 19:41 | 50.045
2020-02-24 | 19:41 | 50.048
2020-02-24 | 19:41 | 50.051
2020-02-24 | 19:41 | 50.053
2020-02-24 | 19:41 | 50.054
2020-02-24 | 19:41 | 50.057
2020-02-24 | 19:41 | 50.058
2020-02-24 | 19:41 | 50.06
2020-02-24 | 19:41 | 50.061
2020-02-24 | 19:41 | 50.062
2020-02-24 | 19:41 | 50.062
2020-02-24 | 19:41 | 50.062
2020-02-24 | 19:42 | 50.064
2020-02-24 | 19:42 | 50.065
2020-02-24 | 19:42 | 50.071
2020-02-24 | 19:42 | 50.072
2020-02-24 | 19:42 | 50.071
2020-02-24 | 19:42 | 50.07
2020-02-24 | 19:42 | 50.071
2020-02-24 | 19:42 | 50.068
2020-02-24 | 19:42 | 50.067
2020-02-24 | 19:42 | 50.063
2020-02-24 | 19:42 | 50.061
2020-02-24 | 19:42 | 50.06
2020-02-24 | 19:42 | 50.059
2020-02-24 | 19:42 | 50.058
2020-02-24 | 19:42 | 50.058
2020-02-24 | 19:42 | 50.057
2020-02-24 | 19:42 | 50.055
2020-02-24 | 19:42 | 50.052
2020-02-24 | 19:42 | 50.048
2020-02-24 | 19:42 | 50.045
2020-02-24 | 19:42 | 50.043
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.038
2020-02-24 | 19:42 | 50.039
2020-02-24 | 19:42 | 50.038
2020-02-24 | 19:42 | 50.039
2020-02-24 | 19:42 | 50.04
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.043
2020-02-24 | 19:42 | 50.042
2020-02-24 | 19:42 | 50.043
2020-02-24 | 19:42 | 50.044
2020-02-24 | 19:42 | 50.046
2020-02-24 | 19:42 | 50.046
2020-02-24 | 19:42 | 50.045
2020-02-24 | 19:42 | 50.045
2020-02-24 | 19:42 | 50.042
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.043
2020-02-24 | 19:42 | 50.041
2020-02-24 | 19:42 | 50.042
2020-02-24 | 19:42 | 50.042
2020-02-24 | 19:42 | 50.044
2020-02-24 | 19:42 | 50.048
2020-02-24 | 19:42 | 50.048
2020-02-24 | 19:42 | 50.049
2020-02-24 | 19:42 | 50.051
2020-02-24 | 19:42 | 50.055
2020-02-24 | 19:42 | 50.057
2020-02-24 | 19:42 | 50.063
2020-02-24 | 19:42 | 50.069
2020-02-24 | 19:42 | 50.075
2020-02-24 | 19:42 | 50.082
2020-02-24 | 19:42 | 50.089
2020-02-24 | 19:42 | 50.092
2020-02-24 | 19:42 | 50.095
2020-02-24 | 19:42 | 50.096
2020-02-24 | 19:42 | 50.096
2020-02-24 | 19:43 | 50.095
2020-02-24 | 19:43 | 50.097
2020-02-24 | 19:43 | 50.098
2020-02-24 | 19:43 | 50.099
2020-02-24 | 19:43 | 50.099
2020-02-24 | 19:43 | 50.098
2020-02-24 | 19:43 | 50.096
2020-02-24 | 19:43 | 50.091
2020-02-24 | 19:43 | 50.088
2020-02-24 | 19:43 | 50.086
2020-02-24 | 19:43 | 50.084
2020-02-24 | 19:43 | 50.083
2020-02-24 | 19:43 | 50.081
2020-02-24 | 19:43 | 50.08
2020-02-24 | 19:43 | 50.079
2020-02-24 | 19:43 | 50.082
2020-02-24 | 19:43 | 50.084
2020-02-24 | 19:43 | 50.087
2020-02-24 | 19:43 | 50.089
2020-02-24 | 19:43 | 50.094
2020-02-24 | 19:43 | 50.095
2020-02-24 | 19:43 | 50.097
2020-02-24 | 19:43 | 50.098
2020-02-24 | 19:43 | 50.103
2020-02-24 | 19:43 | 50.108
2020-02-24 | 19:43 | 50.113
2020-02-24 | 19:43 | 50.113
2020-02-24 | 19:43 | 50.114
2020-02-24 | 19:43 | 50.115
2020-02-24 | 19:43 | 50.115
2020-02-24 | 19:43 | 50.111
2020-02-24 | 19:43 | 50.104
2020-02-24 | 19:43 | 50.097
2020-02-24 | 19:43 | 50.091
2020-02-24 | 19:43 | 50.087
2020-02-24 | 19:43 | 50.082
2020-02-24 | 19:43 | 50.078
2020-02-24 | 19:43 | 50.075
2020-02-24 | 19:43 | 50.072
2020-02-24 | 19:43 | 50.073
2020-02-24 | 19:43 | 50.071
2020-02-24 | 19:43 | 50.071
2020-02-24 | 19:43 | 50.066
2020-02-24 | 19:43 | 50.063
2020-02-24 | 19:43 | 50.06
2020-02-24 | 19:43 | 50.061
2020-02-24 | 19:43 | 50.063
2020-02-24 | 19:43 | 50.065
2020-02-24 | 19:43 | 50.067
2020-02-24 | 19:43 | 50.068
2020-02-24 | 19:43 | 50.067
2020-02-24 | 19:43 | 50.066
2020-02-24 | 19:43 | 50.063
2020-02-24 | 19:43 | 50.06
2020-02-24 | 19:43 | 50.056
2020-02-24 | 19:43 | 50.054
2020-02-24 | 19:43 | 50.049
2020-02-24 | 19:43 | 50.048
2020-02-24 | 19:43 | 50.046
2020-02-24 | 19:44 | 50.043
2020-02-24 | 19:44 | 50.044
2020-02-24 | 19:44 | 50.048
2020-02-24 | 19:44 | 50.052
2020-02-24 | 19:44 | 50.054
2020-02-24 | 19:44 | 50.057
2020-02-24 | 19:44 | 50.058
2020-02-24 | 19:44 | 50.059
2020-02-24 | 19:44 | 50.058
2020-02-24 | 19:44 | 50.057
2020-02-24 | 19:44 | 50.054
2020-02-24 | 19:44 | 50.051
2020-02-24 | 19:44 | 50.046
2020-02-24 | 19:44 | 50.043
2020-02-24 | 19:44 | 50.039
2020-02-24 | 19:44 | 50.036
2020-02-24 | 19:44 | 50.033
2020-02-24 | 19:44 | 50.029
2020-02-24 | 19:44 | 50.029
2020-02-24 | 19:44 | 50.028
2020-02-24 | 19:44 | 50.03
2020-02-24 | 19:44 | 50.031
2020-02-24 | 19:44 | 50.031
2020-02-24 | 19:44 | 50.03
2020-02-24 | 19:44 | 50.029
2020-02-24 | 19:44 | 50.027
2020-02-24 | 19:44 | 50.028
2020-02-24 | 19:44 | 50.025
2020-02-24 | 19:44 | 50.025
2020-02-24 | 19:44 | 50.026
2020-02-24 | 19:44 | 50.026
2020-02-24 | 19:44 | 50.027
2020-02-24 | 19:44 | 50.029
2020-02-24 | 19:44 | 50.03
2020-02-24 | 19:44 | 50.029
2020-02-24 | 19:44 | 50.03
2020-02-24 | 19:44 | 50.032
2020-02-24 | 19:44 | 50.033
2020-02-24 | 19:44 | 50.033
2020-02-24 | 19:44 | 50.029
2020-02-24 | 19:44 | 50.023
2020-02-24 | 19:44 | 50.017
2020-02-24 | 19:44 | 50.013
2020-02-24 | 19:44 | 50.009
2020-02-24 | 19:44 | 50.007
2020-02-24 | 19:44 | 50.006
2020-02-24 | 19:44 | 50.004
2020-02-24 | 19:44 | 50.005
2020-02-24 | 19:44 | 50.005
2020-02-24 | 19:44 | 50.003
2020-02-24 | 19:44 | 50.003
2020-02-24 | 19:44 | 50.002
2020-02-24 | 19:44 | 50.003
2020-02-24 | 19:44 | 50.004
2020-02-24 | 19:44 | 50.008
2020-02-24 | 19:44 | 50.01
2020-02-24 | 19:44 | 50.012
2020-02-24 | 19:44 | 50.013
2020-02-24 | 19:44 | 50.013
2020-02-24 | 19:44 | 50.016
2020-02-24 | 19:44 | 50.016
2020-02-24 | 19:45 | 50.018
2020-02-24 | 19:45 | 50.018
2020-02-24 | 19:45 | 50.016
2020-02-24 | 19:45 | 50.015
2020-02-24 | 19:45 | 50.015
2020-02-24 | 19:45 | 50.014
2020-02-24 | 19:45 | 50.013
2020-02-24 | 19:45 | 50.013
2020-02-24 | 19:45 | 50.012
2020-02-24 | 19:45 | 50.01
2020-02-24 | 19:45 | 50.011
2020-02-24 | 19:45 | 50.011
2020-02-24 | 19:45 | 50.01
2020-02-24 | 19:45 | 50.009
2020-02-24 | 19:45 | 50.006
2020-02-24 | 19:45 | 50.006
2020-02-24 | 19:45 | 50.004
2020-02-24 | 19:45 | 50.004
2020-02-24 | 19:45 | 50.003
2020-02-24 | 19:45 | 50.002
2020-02-24 | 19:45 | 50.002
2020-02-24 | 19:45 | 50.002
2020-02-24 | 19:45 | 50.003
2020-02-24 | 19:45 | 50.004
2020-02-24 | 19:45 | 50.004
2020-02-24 | 19:45 | 50.005
2020-02-24 | 19:45 | 50.004
2020-02-24 | 19:45 | 50.003
2020-02-24 | 19:45 | 49.999
2020-02-24 | 19:45 | 49.992
2020-02-24 | 19:45 | 49.985
2020-02-24 | 19:45 | 49.976
2020-02-24 | 19:45 | 49.968
2020-02-24 | 19:45 | 49.958
2020-02-24 | 19:45 | 49.948
2020-02-24 | 19:45 | 49.94
2020-02-24 | 19:45 | 49.936
2020-02-24 | 19:45 | 49.932
2020-02-24 | 19:45 | 49.931
2020-02-24 | 19:45 | 49.929
2020-02-24 | 19:45 | 49.931
2020-02-24 | 19:45 | 49.935
2020-02-24 | 19:45 | 49.938
2020-02-24 | 19:45 | 49.941
2020-02-24 | 19:45 | 49.942
2020-02-24 | 19:45 | 49.943
2020-02-24 | 19:45 | 49.942
2020-02-24 | 19:45 | 49.941
2020-02-24 | 19:45 | 49.939
2020-02-24 | 19:45 | 49.939
2020-02-24 | 19:45 | 49.938
2020-02-24 | 19:45 | 49.937
2020-02-24 | 19:45 | 49.938
2020-02-24 | 19:45 | 49.938
2020-02-24 | 19:45 | 49.939
2020-02-24 | 19:45 | 49.941
2020-02-24 | 19:45 | 49.94
2020-02-24 | 19:45 | 49.94
2020-02-24 | 19:45 | 49.94
2020-02-24 | 19:46 | 49.937
2020-02-24 | 19:46 | 49.934
2020-02-24 | 19:46 | 49.931
2020-02-24 | 19:46 | 49.93
2020-02-24 | 19:46 | 49.928
2020-02-24 | 19:46 | 49.926
2020-02-24 | 19:46 | 49.924
2020-02-24 | 19:46 | 49.923
2020-02-24 | 19:46 | 49.923
2020-02-24 | 19:46 | 49.921
2020-02-24 | 19:46 | 49.921
2020-02-24 | 19:46 | 49.92
2020-02-24 | 19:46 | 49.919
2020-02-24 | 19:46 | 49.918
2020-02-24 | 19:46 | 49.917
2020-02-24 | 19:46 | 49.917
2020-02-24 | 19:46 | 49.916
2020-02-24 | 19:46 | 49.917
2020-02-24 | 19:46 | 49.919
2020-02-24 | 19:46 | 49.919
2020-02-24 | 19:46 | 49.92
2020-02-24 | 19:46 | 49.92
2020-02-24 | 19:46 | 49.921
2020-02-24 | 19:46 | 49.92
2020-02-24 | 19:46 | 49.919
2020-02-24 | 19:46 | 49.919
2020-02-24 | 19:46 | 49.919
2020-02-24 | 19:46 | 49.917
2020-02-24 | 19:46 | 49.916
2020-02-24 | 19:46 | 49.913
2020-02-24 | 19:46 | 49.911
2020-02-24 | 19:46 | 49.912
2020-02-24 | 19:46 | 49.912
2020-02-24 | 19:46 | 49.914
2020-02-24 | 19:46 | 49.917
2020-02-24 | 19:46 | 49.92
2020-02-24 | 19:46 | 49.921
2020-02-24 | 19:46 | 49.922
2020-02-24 | 19:46 | 49.924
2020-02-24 | 19:46 | 49.924
2020-02-24 | 19:46 | 49.927
2020-02-24 | 19:46 | 49.93
2020-02-24 | 19:46 | 49.932
2020-02-24 | 19:46 | 49.934
2020-02-24 | 19:46 | 49.936
2020-02-24 | 19:46 | 49.936
2020-02-24 | 19:46 | 49.934
2020-02-24 | 19:46 | 49.933
2020-02-24 | 19:46 | 49.932
2020-02-24 | 19:46 | 49.932
2020-02-24 | 19:46 | 49.931
2020-02-24 | 19:46 | 49.928
2020-02-24 | 19:46 | 49.927
2020-02-24 | 19:46 | 49.925
2020-02-24 | 19:46 | 49.922
2020-02-24 | 19:46 | 49.92
2020-02-24 | 19:46 | 49.918
2020-02-24 | 19:46 | 49.916
2020-02-24 | 19:46 | 49.915
2020-02-24 | 19:46 | 49.914
2020-02-24 | 19:46 | 49.914
2020-02-24 | 19:47 | 49.913
2020-02-24 | 19:47 | 49.916
2020-02-24 | 19:47 | 49.918
2020-02-24 | 19:47 | 49.918
2020-02-24 | 19:47 | 49.918
2020-02-24 | 19:47 | 49.918
2020-02-24 | 19:47 | 49.917
2020-02-24 | 19:47 | 49.914
2020-02-24 | 19:47 | 49.91
2020-02-24 | 19:47 | 49.907
2020-02-24 | 19:47 | 49.903
2020-02-24 | 19:47 | 49.902
2020-02-24 | 19:47 | 49.903
2020-02-24 | 19:47 | 49.904
2020-02-24 | 19:47 | 49.907
2020-02-24 | 19:47 | 49.911
2020-02-24 | 19:47 | 49.914
2020-02-24 | 19:47 | 49.917
2020-02-24 | 19:47 | 49.918
2020-02-24 | 19:47 | 49.92
2020-02-24 | 19:47 | 49.921
2020-02-24 | 19:47 | 49.921
2020-02-24 | 19:47 | 49.922
2020-02-24 | 19:47 | 49.923
2020-02-24 | 19:47 | 49.921
2020-02-24 | 19:47 | 49.919
2020-02-24 | 19:47 | 49.918
2020-02-24 | 19:47 | 49.919
2020-02-24 | 19:47 | 49.922
2020-02-24 | 19:47 | 49.925
2020-02-24 | 19:47 | 49.928
2020-02-24 | 19:47 | 49.93
2020-02-24 | 19:47 | 49.933
2020-02-24 | 19:47 | 49.933
2020-02-24 | 19:47 | 49.936
2020-02-24 | 19:47 | 49.939
2020-02-24 | 19:47 | 49.94
2020-02-24 | 19:47 | 49.941
2020-02-24 | 19:47 | 49.939
2020-02-24 | 19:47 | 49.938
2020-02-24 | 19:47 | 49.933
2020-02-24 | 19:47 | 49.931
2020-02-24 | 19:47 | 49.927
2020-02-24 | 19:47 | 49.925
2020-02-24 | 19:47 | 49.923
2020-02-24 | 19:47 | 49.921
2020-02-24 | 19:47 | 49.922
2020-02-24 | 19:47 | 49.924
2020-02-24 | 19:47 | 49.925
2020-02-24 | 19:47 | 49.928
2020-02-24 | 19:47 | 49.93
2020-02-24 | 19:47 | 49.933
2020-02-24 | 19:47 | 49.937
2020-02-24 | 19:47 | 49.939
2020-02-24 | 19:47 | 49.941
2020-02-24 | 19:47 | 49.94
2020-02-24 | 19:47 | 49.939
2020-02-24 | 19:47 | 49.938
2020-02-24 | 19:47 | 49.937
2020-02-24 | 19:48 | 49.936
2020-02-24 | 19:48 | 49.935
2020-02-24 | 19:48 | 49.934
2020-02-24 | 19:48 | 49.932
2020-02-24 | 19:48 | 49.93
2020-02-24 | 19:48 | 49.929
2020-02-24 | 19:48 | 49.929
2020-02-24 | 19:48 | 49.93
2020-02-24 | 19:48 | 49.93
2020-02-24 | 19:48 | 49.931
2020-02-24 | 19:48 | 49.931
2020-02-24 | 19:48 | 49.932
2020-02-24 | 19:48 | 49.933
2020-02-24 | 19:48 | 49.934
2020-02-24 | 19:48 | 49.936
2020-02-24 | 19:48 | 49.937
2020-02-24 | 19:48 | 49.937
2020-02-24 | 19:48 | 49.938
2020-02-24 | 19:48 | 49.939
2020-02-24 | 19:48 | 49.94
2020-02-24 | 19:48 | 49.942
2020-02-24 | 19:48 | 49.943
2020-02-24 | 19:48 | 49.943
2020-02-24 | 19:48 | 49.942
2020-02-24 | 19:48 | 49.94
2020-02-24 | 19:48 | 49.939
2020-02-24 | 19:48 | 49.937
2020-02-24 | 19:48 | 49.934
2020-02-24 | 19:48 | 49.93
2020-02-24 | 19:48 | 49.927
2020-02-24 | 19:48 | 49.923
2020-02-24 | 19:48 | 49.921
2020-02-24 | 19:48 | 49.918
2020-02-24 | 19:48 | 49.916
2020-02-24 | 19:48 | 49.914
2020-02-24 | 19:48 | 49.91
2020-02-24 | 19:48 | 49.907
2020-02-24 | 19:48 | 49.902
2020-02-24 | 19:48 | 49.901
2020-02-24 | 19:48 | 49.897
2020-02-24 | 19:48 | 49.896
2020-02-24 | 19:48 | 49.894
2020-02-24 | 19:48 | 49.892
2020-02-24 | 19:48 | 49.892
2020-02-24 | 19:48 | 49.888
2020-02-24 | 19:48 | 49.886
2020-02-24 | 19:48 | 49.883
2020-02-24 | 19:48 | 49.879
2020-02-24 | 19:48 | 49.876
2020-02-24 | 19:48 | 49.874
2020-02-24 | 19:48 | 49.87
2020-02-24 | 19:48 | 49.871
2020-02-24 | 19:48 | 49.875
2020-02-24 | 19:48 | 49.876
2020-02-24 | 19:48 | 49.88
2020-02-24 | 19:48 | 49.886
2020-02-24 | 19:48 | 49.892
2020-02-24 | 19:48 | 49.894
2020-02-24 | 19:48 | 49.894
2020-02-24 | 19:48 | 49.893
2020-02-24 | 19:48 | 49.89
2020-02-24 | 19:49 | 49.886
2020-02-24 | 19:49 | 49.884
2020-02-24 | 19:49 | 49.882
2020-02-24 | 19:49 | 49.883
2020-02-24 | 19:49 | 49.883
2020-02-24 | 19:49 | 49.883
2020-02-24 | 19:49 | 49.882
2020-02-24 | 19:49 | 49.882
2020-02-24 | 19:49 | 49.881
2020-02-24 | 19:49 | 49.88
2020-02-24 | 19:49 | 49.879
2020-02-24 | 19:49 | 49.878
2020-02-24 | 19:49 | 49.876
2020-02-24 | 19:49 | 49.875
2020-02-24 | 19:49 | 49.873
2020-02-24 | 19:49 | 49.87
2020-02-24 | 19:49 | 49.867
2020-02-24 | 19:49 | 49.868
2020-02-24 | 19:49 | 49.87
2020-02-24 | 19:49 | 49.871
2020-02-24 | 19:49 | 49.876
2020-02-24 | 19:49 | 49.879
2020-02-24 | 19:49 | 49.884
2020-02-24 | 19:49 | 49.891
2020-02-24 | 19:49 | 49.897
2020-02-24 | 19:49 | 49.9
2020-02-24 | 19:49 | 49.903
2020-02-24 | 19:49 | 49.905
2020-02-24 | 19:49 | 49.906
2020-02-24 | 19:49 | 49.908
2020-02-24 | 19:49 | 49.91
2020-02-24 | 19:49 | 49.911
2020-02-24 | 19:49 | 49.912
2020-02-24 | 19:49 | 49.913
2020-02-24 | 19:49 | 49.911
2020-02-24 | 19:49 | 49.911
2020-02-24 | 19:49 | 49.914
2020-02-24 | 19:49 | 49.914
2020-02-24 | 19:49 | 49.913
2020-02-24 | 19:49 | 49.913
2020-02-24 | 19:49 | 49.911
2020-02-24 | 19:49 | 49.91
2020-02-24 | 19:49 | 49.906
2020-02-24 | 19:49 | 49.901
2020-02-24 | 19:49 | 49.897
2020-02-24 | 19:49 | 49.896
2020-02-24 | 19:49 | 49.895
2020-02-24 | 19:49 | 49.895
2020-02-24 | 19:49 | 49.896
2020-02-24 | 19:49 | 49.897
2020-02-24 | 19:49 | 49.895
2020-02-24 | 19:49 | 49.892
2020-02-24 | 19:49 | 49.89
2020-02-24 | 19:49 | 49.885
2020-02-24 | 19:49 | 49.882
2020-02-24 | 19:49 | 49.879
2020-02-24 | 19:49 | 49.878
2020-02-24 | 19:49 | 49.876
2020-02-24 | 19:49 | 49.873
2020-02-24 | 19:50 | 49.873
2020-02-24 | 19:50 | 49.874
2020-02-24 | 19:50 | 49.873
2020-02-24 | 19:50 | 49.872
2020-02-24 | 19:50 | 49.873
2020-02-24 | 19:50 | 49.875
2020-02-24 | 19:50 | 49.876
2020-02-24 | 19:50 | 49.875
2020-02-24 | 19:50 | 49.876
2020-02-24 | 19:50 | 49.876
2020-02-24 | 19:50 | 49.874
2020-02-24 | 19:50 | 49.873
2020-02-24 | 19:50 | 49.875
2020-02-24 | 19:50 | 49.877
2020-02-24 | 19:50 | 49.88
2020-02-24 | 19:50 | 49.884
2020-02-24 | 19:50 | 49.887
2020-02-24 | 19:50 | 49.888
2020-02-24 | 19:50 | 49.887
2020-02-24 | 19:50 | 49.886
2020-02-24 | 19:50 | 49.885
2020-02-24 | 19:50 | 49.883
2020-02-24 | 19:50 | 49.878
2020-02-24 | 19:50 | 49.872
2020-02-24 | 19:50 | 49.868
2020-02-24 | 19:50 | 49.869
2020-02-24 | 19:50 | 49.872
2020-02-24 | 19:50 | 49.877
2020-02-24 | 19:50 | 49.88
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.883
2020-02-24 | 19:50 | 49.883
2020-02-24 | 19:50 | 49.883
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.881
2020-02-24 | 19:50 | 49.879
2020-02-24 | 19:50 | 49.877
2020-02-24 | 19:50 | 49.877
2020-02-24 | 19:50 | 49.877
2020-02-24 | 19:50 | 49.88
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.884
2020-02-24 | 19:50 | 49.884
2020-02-24 | 19:50 | 49.886
2020-02-24 | 19:50 | 49.887
2020-02-24 | 19:50 | 49.888
2020-02-24 | 19:50 | 49.886
2020-02-24 | 19:50 | 49.885
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.88
2020-02-24 | 19:50 | 49.88
2020-02-24 | 19:50 | 49.879
2020-02-24 | 19:50 | 49.878
2020-02-24 | 19:50 | 49.879
2020-02-24 | 19:50 | 49.882
2020-02-24 | 19:50 | 49.885
2020-02-24 | 19:50 | 49.888
2020-02-24 | 19:50 | 49.891
2020-02-24 | 19:50 | 49.893
2020-02-24 | 19:51 | 49.897
2020-02-24 | 19:51 | 49.899
2020-02-24 | 19:51 | 49.9
2020-02-24 | 19:51 | 49.9
2020-02-24 | 19:51 | 49.901
2020-02-24 | 19:51 | 49.9
2020-02-24 | 19:51 | 49.899
2020-02-24 | 19:51 | 49.9
2020-02-24 | 19:51 | 49.901
2020-02-24 | 19:51 | 49.903
2020-02-24 | 19:51 | 49.904
2020-02-24 | 19:51 | 49.904
2020-02-24 | 19:51 | 49.905
2020-02-24 | 19:51 | 49.906
2020-02-24 | 19:51 | 49.909
2020-02-24 | 19:51 | 49.91
2020-02-24 | 19:51 | 49.909
2020-02-24 | 19:51 | 49.909
2020-02-24 | 19:51 | 49.911
2020-02-24 | 19:51 | 49.913
2020-02-24 | 19:51 | 49.915
2020-02-24 | 19:51 | 49.92
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:51 | 49.919
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:51 | 49.916
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:51 | 49.92
2020-02-24 | 19:51 | 49.921
2020-02-24 | 19:51 | 49.92
2020-02-24 | 19:51 | 49.92
2020-02-24 | 19:51 | 49.919
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:51 | 49.917
2020-02-24 | 19:51 | 49.919
2020-02-24 | 19:51 | 49.919
2020-02-24 | 19:51 | 49.917
2020-02-24 | 19:51 | 49.917
2020-02-24 | 19:51 | 49.915
2020-02-24 | 19:51 | 49.916
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:51 | 49.917
2020-02-24 | 19:51 | 49.916
2020-02-24 | 19:51 | 49.916
2020-02-24 | 19:51 | 49.915
2020-02-24 | 19:51 | 49.915
2020-02-24 | 19:51 | 49.916
2020-02-24 | 19:51 | 49.913
2020-02-24 | 19:51 | 49.909
2020-02-24 | 19:51 | 49.905
2020-02-24 | 19:51 | 49.903
2020-02-24 | 19:51 | 49.901
2020-02-24 | 19:51 | 49.905
2020-02-24 | 19:51 | 49.908
2020-02-24 | 19:51 | 49.91
2020-02-24 | 19:51 | 49.912
2020-02-24 | 19:51 | 49.916
2020-02-24 | 19:51 | 49.918
2020-02-24 | 19:52 | 49.923
2020-02-24 | 19:52 | 49.924
2020-02-24 | 19:52 | 49.925
2020-02-24 | 19:52 | 49.925
2020-02-24 | 19:52 | 49.923
2020-02-24 | 19:52 | 49.92
2020-02-24 | 19:52 | 49.917
2020-02-24 | 19:52 | 49.913
2020-02-24 | 19:52 | 49.91
2020-02-24 | 19:52 | 49.906
2020-02-24 | 19:52 | 49.905
2020-02-24 | 19:52 | 49.905
2020-02-24 | 19:52 | 49.907
2020-02-24 | 19:52 | 49.909
2020-02-24 | 19:52 | 49.911
2020-02-24 | 19:52 | 49.914
2020-02-24 | 19:52 | 49.918
2020-02-24 | 19:52 | 49.92
2020-02-24 | 19:52 | 49.922
2020-02-24 | 19:52 | 49.925
2020-02-24 | 19:52 | 49.928
2020-02-24 | 19:52 | 49.927
2020-02-24 | 19:52 | 49.928
2020-02-24 | 19:52 | 49.928
2020-02-24 | 19:52 | 49.93
2020-02-24 | 19:52 | 49.933
2020-02-24 | 19:52 | 49.937
2020-02-24 | 19:52 | 49.937
2020-02-24 | 19:52 | 49.936
2020-02-24 | 19:52 | 49.936
2020-02-24 | 19:52 | 49.936
2020-02-24 | 19:52 | 49.937
2020-02-24 | 19:52 | 49.938
2020-02-24 | 19:52 | 49.937
2020-02-24 | 19:52 | 49.935
2020-02-24 | 19:52 | 49.935
2020-02-24 | 19:52 | 49.934
2020-02-24 | 19:52 | 49.937
2020-02-24 | 19:52 | 49.939
2020-02-24 | 19:52 | 49.942
2020-02-24 | 19:52 | 49.943
2020-02-24 | 19:52 | 49.944
2020-02-24 | 19:52 | 49.946
2020-02-24 | 19:52 | 49.949
2020-02-24 | 19:52 | 49.95
2020-02-24 | 19:52 | 49.95
2020-02-24 | 19:52 | 49.952
2020-02-24 | 19:52 | 49.953
2020-02-24 | 19:52 | 49.956
2020-02-24 | 19:52 | 49.955
2020-02-24 | 19:52 | 49.956
2020-02-24 | 19:52 | 49.959
2020-02-24 | 19:52 | 49.962
2020-02-24 | 19:52 | 49.965
2020-02-24 | 19:52 | 49.967
2020-02-24 | 19:52 | 49.97
2020-02-24 | 19:52 | 49.972
2020-02-24 | 19:52 | 49.972
2020-02-24 | 19:52 | 49.975
2020-02-24 | 19:52 | 49.975
2020-02-24 | 19:52 | 49.974
2020-02-24 | 19:53 | 49.972
2020-02-24 | 19:53 | 49.969
2020-02-24 | 19:53 | 49.971
2020-02-24 | 19:53 | 49.971
2020-02-24 | 19:53 | 49.975
2020-02-24 | 19:53 | 49.977
2020-02-24 | 19:53 | 49.977
2020-02-24 | 19:53 | 49.981
2020-02-24 | 19:53 | 49.988
2020-02-24 | 19:53 | 49.992
2020-02-24 | 19:53 | 49.997
2020-02-24 | 19:53 | 49.999
2020-02-24 | 19:53 | 50.001
2020-02-24 | 19:53 | 50.002
2020-02-24 | 19:53 | 50.003
2020-02-24 | 19:53 | 50.004
2020-02-24 | 19:53 | 50.003
2020-02-24 | 19:53 | 50.004
2020-02-24 | 19:53 | 50.007
2020-02-24 | 19:53 | 50.005
2020-02-24 | 19:53 | 50.004
2020-02-24 | 19:53 | 50.002
2020-02-24 | 19:53 | 49.999
2020-02-24 | 19:53 | 49.996
2020-02-24 | 19:53 | 49.992
2020-02-24 | 19:53 | 49.988
2020-02-24 | 19:53 | 49.985
2020-02-24 | 19:53 | 49.982
2020-02-24 | 19:53 | 49.981

## Event 20200227-1
In UTC
Date | Time | Freq
2020-02-27 | 9:00 | 49.971
2020-02-27 | 9:00 | 49.97
2020-02-27 | 9:00 | 49.968
2020-02-27 | 9:00 | 49.965
2020-02-27 | 9:00 | 49.961
2020-02-27 | 9:00 | 49.96
2020-02-27 | 9:00 | 49.958
2020-02-27 | 9:00 | 49.959
2020-02-27 | 9:00 | 49.962
2020-02-27 | 9:00 | 49.963
2020-02-27 | 9:00 | 49.965
2020-02-27 | 9:00 | 49.965
2020-02-27 | 9:00 | 49.965
2020-02-27 | 9:00 | 49.966
2020-02-27 | 9:00 | 49.969
2020-02-27 | 9:00 | 49.972
2020-02-27 | 9:00 | 49.972
2020-02-27 | 9:00 | 49.974
2020-02-27 | 9:00 | 49.975
2020-02-27 | 9:00 | 49.977
2020-02-27 | 9:00 | 49.979
2020-02-27 | 9:00 | 49.985
2020-02-27 | 9:00 | 49.989
2020-02-27 | 9:00 | 49.994
2020-02-27 | 9:00 | 49.995
2020-02-27 | 9:00 | 49.999
2020-02-27 | 9:00 | 50.004
2020-02-27 | 9:00 | 50.009
2020-02-27 | 9:00 | 50.015
2020-02-27 | 9:00 | 50.019
2020-02-27 | 9:00 | 50.023
2020-02-27 | 9:01 | 50.027
2020-02-27 | 9:01 | 50.029
2020-02-27 | 9:01 | 50.031
2020-02-27 | 9:01 | 50.033
2020-02-27 | 9:01 | 50.034
2020-02-27 | 9:01 | 50.033
2020-02-27 | 9:01 | 50.034
2020-02-27 | 9:01 | 50.034
2020-02-27 | 9:01 | 50.035
2020-02-27 | 9:01 | 50.037
2020-02-27 | 9:01 | 50.04
2020-02-27 | 9:01 | 50.043
2020-02-27 | 9:01 | 50.045
2020-02-27 | 9:01 | 50.045
2020-02-27 | 9:01 | 50.046
2020-02-27 | 9:01 | 50.045
2020-02-27 | 9:01 | 50.045
2020-02-27 | 9:01 | 50.044
2020-02-27 | 9:01 | 50.042
2020-02-27 | 9:01 | 50.038
2020-02-27 | 9:01 | 50.035
2020-02-27 | 9:01 | 50.032
2020-02-27 | 9:01 | 50.03
2020-02-27 | 9:01 | 50.027
2020-02-27 | 9:01 | 50.026
2020-02-27 | 9:01 | 50.026
2020-02-27 | 9:01 | 50.027
2020-02-27 | 9:01 | 50.027
2020-02-27 | 9:01 | 50.03
2020-02-27 | 9:01 | 50.031
2020-02-27 | 9:01 | 50.032
2020-02-27 | 9:01 | 50.032
2020-02-27 | 9:01 | 50.031
2020-02-27 | 9:01 | 50.031
2020-02-27 | 9:01 | 50.032
2020-02-27 | 9:01 | 50.032
2020-02-27 | 9:01 | 50.029
2020-02-27 | 9:01 | 50.027
2020-02-27 | 9:01 | 50.024
2020-02-27 | 9:01 | 50.022
2020-02-27 | 9:01 | 50.021
2020-02-27 | 9:01 | 50.02
2020-02-27 | 9:01 | 50.02
2020-02-27 | 9:01 | 50.019
2020-02-27 | 9:01 | 50.017
2020-02-27 | 9:01 | 50.014
2020-02-27 | 9:01 | 50.011
2020-02-27 | 9:01 | 50.009
2020-02-27 | 9:01 | 50.012
2020-02-27 | 9:01 | 50.012
2020-02-27 | 9:01 | 50.015
2020-02-27 | 9:01 | 50.016
2020-02-27 | 9:01 | 50.018
2020-02-27 | 9:01 | 50.021
2020-02-27 | 9:01 | 50.026
2020-02-27 | 9:01 | 50.029
2020-02-27 | 9:01 | 50.031
2020-02-27 | 9:01 | 50.029
2020-02-27 | 9:01 | 50.029
2020-02-27 | 9:02 | 50.03
2020-02-27 | 9:02 | 50.028
2020-02-27 | 9:02 | 50.03
2020-02-27 | 9:02 | 50.029
2020-02-27 | 9:02 | 50.029
2020-02-27 | 9:02 | 50.03
2020-02-27 | 9:02 | 50.012
2020-02-27 | 9:02 | 49.993
2020-02-27 | 9:02 | 49.971
2020-02-27 | 9:02 | 49.953
2020-02-27 | 9:02 | 49.938
2020-02-27 | 9:02 | 49.925
2020-02-27 | 9:02 | 49.914
2020-02-27 | 9:02 | 49.905
2020-02-27 | 9:02 | 49.899
2020-02-27 | 9:02 | 49.893
2020-02-27 | 9:02 | 49.89
2020-02-27 | 9:02 | 49.889
2020-02-27 | 9:02 | 49.887
2020-02-27 | 9:02 | 49.889
2020-02-27 | 9:02 | 49.889
2020-02-27 | 9:02 | 49.891
2020-02-27 | 9:02 | 49.891
2020-02-27 | 9:02 | 49.895
2020-02-27 | 9:02 | 49.897
2020-02-27 | 9:02 | 49.901
2020-02-27 | 9:02 | 49.902
2020-02-27 | 9:02 | 49.905
2020-02-27 | 9:02 | 49.905
2020-02-27 | 9:02 | 49.906
2020-02-27 | 9:02 | 49.903
2020-02-27 | 9:02 | 49.904
2020-02-27 | 9:02 | 49.897
2020-02-27 | 9:02 | 49.893
2020-02-27 | 9:02 | 49.888
2020-02-27 | 9:02 | 49.886
2020-02-27 | 9:02 | 49.882
2020-02-27 | 9:02 | 49.881
2020-02-27 | 9:02 | 49.88
2020-02-27 | 9:02 | 49.882
2020-02-27 | 9:02 | 49.882
2020-02-27 | 9:02 | 49.883
2020-02-27 | 9:02 | 49.882
2020-02-27 | 9:02 | 49.883
2020-02-27 | 9:02 | 49.883
2020-02-27 | 9:02 | 49.884
2020-02-27 | 9:02 | 49.884
2020-02-27 | 9:02 | 49.884
2020-02-27 | 9:02 | 49.885
2020-02-27 | 9:02 | 49.883
2020-02-27 | 9:02 | 49.885
2020-02-27 | 9:02 | 49.888
2020-02-27 | 9:02 | 49.889
2020-02-27 | 9:02 | 49.889
2020-02-27 | 9:02 | 49.891
2020-02-27 | 9:02 | 49.89
2020-02-27 | 9:02 | 49.889
2020-02-27 | 9:02 | 49.888
2020-02-27 | 9:02 | 49.882
2020-02-27 | 9:02 | 49.88
2020-02-27 | 9:02 | 49.875
2020-02-27 | 9:03 | 49.875
2020-02-27 | 9:03 | 49.876
2020-02-27 | 9:03 | 49.876
2020-02-27 | 9:03 | 49.878
2020-02-27 | 9:03 | 49.878
2020-02-27 | 9:03 | 49.88
2020-02-27 | 9:03 | 49.882
2020-02-27 | 9:03 | 49.883
2020-02-27 | 9:03 | 49.887
2020-02-27 | 9:03 | 49.89
2020-02-27 | 9:03 | 49.894
2020-02-27 | 9:03 | 49.899
2020-02-27 | 9:03 | 49.901
2020-02-27 | 9:03 | 49.907
2020-02-27 | 9:03 | 49.909
2020-02-27 | 9:03 | 49.913
2020-02-27 | 9:03 | 49.916
2020-02-27 | 9:03 | 49.919
2020-02-27 | 9:03 | 49.919
2020-02-27 | 9:03 | 49.918
2020-02-27 | 9:03 | 49.918
2020-02-27 | 9:03 | 49.917
2020-02-27 | 9:03 | 49.915
2020-02-27 | 9:03 | 49.913
2020-02-27 | 9:03 | 49.91
2020-02-27 | 9:03 | 49.903
2020-02-27 | 9:03 | 49.9
2020-02-27 | 9:03 | 49.895
2020-02-27 | 9:03 | 49.892
2020-02-27 | 9:03 | 49.887
2020-02-27 | 9:03 | 49.884
2020-02-27 | 9:03 | 49.883
2020-02-27 | 9:03 | 49.881
2020-02-27 | 9:03 | 49.882
2020-02-27 | 9:03 | 49.883
2020-02-27 | 9:03 | 49.883
2020-02-27 | 9:03 | 49.885
2020-02-27 | 9:03 | 49.885
2020-02-27 | 9:03 | 49.885
2020-02-27 | 9:03 | 49.888
2020-02-27 | 9:03 | 49.887
2020-02-27 | 9:03 | 49.887
2020-02-27 | 9:03 | 49.887
2020-02-27 | 9:03 | 49.889
2020-02-27 | 9:03 | 49.888
2020-02-27 | 9:03 | 49.888
2020-02-27 | 9:03 | 49.888
2020-02-27 | 9:03 | 49.889
2020-02-27 | 9:03 | 49.887
2020-02-27 | 9:03 | 49.885
2020-02-27 | 9:03 | 49.885
2020-02-27 | 9:03 | 49.884
2020-02-27 | 9:03 | 49.882
2020-02-27 | 9:03 | 49.881
2020-02-27 | 9:03 | 49.881
2020-02-27 | 9:03 | 49.88
2020-02-27 | 9:03 | 49.88
2020-02-27 | 9:03 | 49.881
2020-02-27 | 9:03 | 49.88
2020-02-27 | 9:04 | 49.881
2020-02-27 | 9:04 | 49.88
2020-02-27 | 9:04 | 49.88
2020-02-27 | 9:04 | 49.877
2020-02-27 | 9:04 | 49.877
2020-02-27 | 9:04 | 49.878
2020-02-27 | 9:04 | 49.88
2020-02-27 | 9:04 | 49.882
2020-02-27 | 9:04 | 49.887
2020-02-27 | 9:04 | 49.89
2020-02-27 | 9:04 | 49.895
2020-02-27 | 9:04 | 49.898
2020-02-27 | 9:04 | 49.903
2020-02-27 | 9:04 | 49.903
2020-02-27 | 9:04 | 49.906
2020-02-27 | 9:04 | 49.909
2020-02-27 | 9:04 | 49.912
2020-02-27 | 9:04 | 49.912
2020-02-27 | 9:04 | 49.913
2020-02-27 | 9:04 | 49.914
2020-02-27 | 9:04 | 49.916
2020-02-27 | 9:04 | 49.915
2020-02-27 | 9:04 | 49.918
2020-02-27 | 9:04 | 49.918
2020-02-27 | 9:04 | 49.92
2020-02-27 | 9:04 | 49.921
2020-02-27 | 9:04 | 49.921
2020-02-27 | 9:04 | 49.922
2020-02-27 | 9:04 | 49.923
2020-02-27 | 9:04 | 49.923
2020-02-27 | 9:04 | 49.922
2020-02-27 | 9:04 | 49.919
2020-02-27 | 9:04 | 49.919
2020-02-27 | 9:04 | 49.918
2020-02-27 | 9:04 | 49.916
2020-02-27 | 9:04 | 49.917
2020-02-27 | 9:04 | 49.917
2020-02-27 | 9:04 | 49.916
2020-02-27 | 9:04 | 49.916
2020-02-27 | 9:04 | 49.914
2020-02-27 | 9:04 | 49.913
2020-02-27 | 9:04 | 49.912
2020-02-27 | 9:04 | 49.911
2020-02-27 | 9:04 | 49.91
2020-02-27 | 9:04 | 49.907
2020-02-27 | 9:04 | 49.906
2020-02-27 | 9:04 | 49.907
2020-02-27 | 9:04 | 49.907
2020-02-27 | 9:04 | 49.907
2020-02-27 | 9:04 | 49.908
2020-02-27 | 9:04 | 49.906
2020-02-27 | 9:04 | 49.904
2020-02-27 | 9:04 | 49.902
2020-02-27 | 9:04 | 49.901
2020-02-27 | 9:04 | 49.899
2020-02-27 | 9:04 | 49.896
2020-02-27 | 9:04 | 49.893
2020-02-27 | 9:04 | 49.893
2020-02-27 | 9:04 | 49.893
2020-02-27 | 9:04 | 49.893
2020-02-27 | 9:04 | 49.893
2020-02-27 | 9:05 | 49.891
2020-02-27 | 9:05 | 49.891
2020-02-27 | 9:05 | 49.89
2020-02-27 | 9:05 | 49.889
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.885
2020-02-27 | 9:05 | 49.884
2020-02-27 | 9:05 | 49.88
2020-02-27 | 9:05 | 49.88
2020-02-27 | 9:05 | 49.879
2020-02-27 | 9:05 | 49.882
2020-02-27 | 9:05 | 49.883
2020-02-27 | 9:05 | 49.887
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.89
2020-02-27 | 9:05 | 49.892
2020-02-27 | 9:05 | 49.893
2020-02-27 | 9:05 | 49.891
2020-02-27 | 9:05 | 49.89
2020-02-27 | 9:05 | 49.891
2020-02-27 | 9:05 | 49.891
2020-02-27 | 9:05 | 49.893
2020-02-27 | 9:05 | 49.894
2020-02-27 | 9:05 | 49.893
2020-02-27 | 9:05 | 49.892
2020-02-27 | 9:05 | 49.892
2020-02-27 | 9:05 | 49.891
2020-02-27 | 9:05 | 49.89
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.885
2020-02-27 | 9:05 | 49.885
2020-02-27 | 9:05 | 49.887
2020-02-27 | 9:05 | 49.888
2020-02-27 | 9:05 | 49.894
2020-02-27 | 9:05 | 49.898
2020-02-27 | 9:05 | 49.903
2020-02-27 | 9:05 | 49.907
2020-02-27 | 9:05 | 49.91
2020-02-27 | 9:05 | 49.915
2020-02-27 | 9:05 | 49.919
2020-02-27 | 9:05 | 49.922
2020-02-27 | 9:05 | 49.926
2020-02-27 | 9:05 | 49.925
2020-02-27 | 9:05 | 49.925
2020-02-27 | 9:05 | 49.926
2020-02-27 | 9:05 | 49.925
2020-02-27 | 9:05 | 49.922
2020-02-27 | 9:05 | 49.922
2020-02-27 | 9:05 | 49.921
2020-02-27 | 9:05 | 49.919
2020-02-27 | 9:05 | 49.922
2020-02-27 | 9:05 | 49.926
2020-02-27 | 9:05 | 49.928
2020-02-27 | 9:05 | 49.93
2020-02-27 | 9:05 | 49.931
2020-02-27 | 9:05 | 49.933
2020-02-27 | 9:06 | 49.935
2020-02-27 | 9:06 | 49.936
2020-02-27 | 9:06 | 49.935
2020-02-27 | 9:06 | 49.935
2020-02-27 | 9:06 | 49.934
2020-02-27 | 9:06 | 49.935
2020-02-27 | 9:06 | 49.938
2020-02-27 | 9:06 | 49.939
2020-02-27 | 9:06 | 49.94
2020-02-27 | 9:06 | 49.941
2020-02-27 | 9:06 | 49.942
2020-02-27 | 9:06 | 49.944
2020-02-27 | 9:06 | 49.944
2020-02-27 | 9:06 | 49.945
2020-02-27 | 9:06 | 49.947
2020-02-27 | 9:06 | 49.948
2020-02-27 | 9:06 | 49.949
2020-02-27 | 9:06 | 49.95
2020-02-27 | 9:06 | 49.948
2020-02-27 | 9:06 | 49.948
2020-02-27 | 9:06 | 49.948
2020-02-27 | 9:06 | 49.947
2020-02-27 | 9:06 | 49.947
2020-02-27 | 9:06 | 49.947
2020-02-27 | 9:06 | 49.947
2020-02-27 | 9:06 | 49.945
2020-02-27 | 9:06 | 49.942
2020-02-27 | 9:06 | 49.94
2020-02-27 | 9:06 | 49.938
2020-02-27 | 9:06 | 49.938
2020-02-27 | 9:06 | 49.938
2020-02-27 | 9:06 | 49.94
2020-02-27 | 9:06 | 49.943
2020-02-27 | 9:06 | 49.945
2020-02-27 | 9:06 | 49.948
2020-02-27 | 9:06 | 49.951
2020-02-27 | 9:06 | 49.953
2020-02-27 | 9:06 | 49.955
2020-02-27 | 9:06 | 49.955
2020-02-27 | 9:06 | 49.954
2020-02-27 | 9:06 | 49.952
2020-02-27 | 9:06 | 49.948
2020-02-27 | 9:06 | 49.942
2020-02-27 | 9:06 | 49.937
2020-02-27 | 9:06 | 49.933
2020-02-27 | 9:06 | 49.93
2020-02-27 | 9:06 | 49.927
2020-02-27 | 9:06 | 49.926
2020-02-27 | 9:06 | 49.924
2020-02-27 | 9:06 | 49.925
2020-02-27 | 9:06 | 49.927
2020-02-27 | 9:06 | 49.928
2020-02-27 | 9:06 | 49.932
2020-02-27 | 9:06 | 49.934
2020-02-27 | 9:06 | 49.938
2020-02-27 | 9:06 | 49.942
2020-02-27 | 9:06 | 49.943
2020-02-27 | 9:06 | 49.945
2020-02-27 | 9:06 | 49.947
2020-02-27 | 9:06 | 49.949
2020-02-27 | 9:06 | 49.95
2020-02-27 | 9:07 | 49.948
2020-02-27 | 9:07 | 49.948
2020-02-27 | 9:07 | 49.946
2020-02-27 | 9:07 | 49.944
2020-02-27 | 9:07 | 49.943
2020-02-27 | 9:07 | 49.945
2020-02-27 | 9:07 | 49.946
2020-02-27 | 9:07 | 49.948
2020-02-27 | 9:07 | 49.951
2020-02-27 | 9:07 | 49.956
2020-02-27 | 9:07 | 49.958
2020-02-27 | 9:07 | 49.961
2020-02-27 | 9:07 | 49.965
2020-02-27 | 9:07 | 49.968
2020-02-27 | 9:07 | 49.97
2020-02-27 | 9:07 | 49.972
2020-02-27 | 9:07 | 49.971
2020-02-27 | 9:07 | 49.972
2020-02-27 | 9:07 | 49.971
2020-02-27 | 9:07 | 49.97
2020-02-27 | 9:07 | 49.969
2020-02-27 | 9:07 | 49.968
2020-02-27 | 9:07 | 49.967
2020-02-27 | 9:07 | 49.965
2020-02-27 | 9:07 | 49.963
2020-02-27 | 9:07 | 49.96
2020-02-27 | 9:07 | 49.956
2020-02-27 | 9:07 | 49.954
2020-02-27 | 9:07 | 49.953
2020-02-27 | 9:07 | 49.953
2020-02-27 | 9:07 | 49.953
2020-02-27 | 9:07 | 49.954
2020-02-27 | 9:07 | 49.954
2020-02-27 | 9:07 | 49.955
2020-02-27 | 9:07 | 49.954
2020-02-27 | 9:07 | 49.956
2020-02-27 | 9:07 | 49.953
2020-02-27 | 9:07 | 49.951
2020-02-27 | 9:07 | 49.949
2020-02-27 | 9:07 | 49.949
2020-02-27 | 9:07 | 49.951
2020-02-27 | 9:07 | 49.95
2020-02-27 | 9:07 | 49.951
2020-02-27 | 9:07 | 49.954
2020-02-27 | 9:07 | 49.953
2020-02-27 | 9:07 | 49.955
2020-02-27 | 9:07 | 49.955
2020-02-27 | 9:07 | 49.955
2020-02-27 | 9:07 | 49.956
2020-02-27 | 9:07 | 49.958
2020-02-27 | 9:07 | 49.957
2020-02-27 | 9:07 | 49.957
2020-02-27 | 9:07 | 49.957
2020-02-27 | 9:07 | 49.956
2020-02-27 | 9:07 | 49.957
2020-02-27 | 9:07 | 49.958
2020-02-27 | 9:07 | 49.959
2020-02-27 | 9:07 | 49.965
2020-02-27 | 9:07 | 49.97
2020-02-27 | 9:08 | 49.975
2020-02-27 | 9:08 | 49.977
2020-02-27 | 9:08 | 49.977
2020-02-27 | 9:08 | 49.978
2020-02-27 | 9:08 | 49.979
2020-02-27 | 9:08 | 49.976
2020-02-27 | 9:08 | 49.976
2020-02-27 | 9:08 | 49.972
2020-02-27 | 9:08 | 49.971
2020-02-27 | 9:08 | 49.969
2020-02-27 | 9:08 | 49.968
2020-02-27 | 9:08 | 49.967
2020-02-27 | 9:08 | 49.965
2020-02-27 | 9:08 | 49.966
2020-02-27 | 9:08 | 49.967
2020-02-27 | 9:08 | 49.969
2020-02-27 | 9:08 | 49.971
2020-02-27 | 9:08 | 49.972
2020-02-27 | 9:08 | 49.975
2020-02-27 | 9:08 | 49.979
2020-02-27 | 9:08 | 49.982
2020-02-27 | 9:08 | 49.983
2020-02-27 | 9:08 | 49.986
2020-02-27 | 9:08 | 49.988
2020-02-27 | 9:08 | 49.991
2020-02-27 | 9:08 | 49.99
2020-02-27 | 9:08 | 49.991
2020-02-27 | 9:08 | 49.987
2020-02-27 | 9:08 | 49.983
2020-02-27 | 9:08 | 49.98
2020-02-27 | 9:08 | 49.977
2020-02-27 | 9:08 | 49.973
2020-02-27 | 9:08 | 49.971
2020-02-27 | 9:08 | 49.969
2020-02-27 | 9:08 | 49.968
2020-02-27 | 9:08 | 49.966
2020-02-27 | 9:08 | 49.966
2020-02-27 | 9:08 | 49.961
2020-02-27 | 9:08 | 49.957
2020-02-27 | 9:08 | 49.955
2020-02-27 | 9:08 | 49.955
2020-02-27 | 9:08 | 49.955
2020-02-27 | 9:08 | 49.956
2020-02-27 | 9:08 | 49.957
2020-02-27 | 9:08 | 49.96
2020-02-27 | 9:08 | 49.962
2020-02-27 | 9:08 | 49.961
2020-02-27 | 9:08 | 49.961
2020-02-27 | 9:08 | 49.96
2020-02-27 | 9:08 | 49.96
2020-02-27 | 9:08 | 49.963
2020-02-27 | 9:08 | 49.962
2020-02-27 | 9:08 | 49.962
2020-02-27 | 9:08 | 49.961
2020-02-27 | 9:08 | 49.961
2020-02-27 | 9:08 | 49.961
2020-02-27 | 9:08 | 49.959
2020-02-27 | 9:08 | 49.959
2020-02-27 | 9:08 | 49.957
2020-02-27 | 9:08 | 49.952
2020-02-27 | 9:08 | 49.952
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.949
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.952
2020-02-27 | 9:09 | 49.952
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.954
2020-02-27 | 9:09 | 49.954
2020-02-27 | 9:09 | 49.955
2020-02-27 | 9:09 | 49.954
2020-02-27 | 9:09 | 49.954
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.952
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.952
2020-02-27 | 9:09 | 49.952
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.949
2020-02-27 | 9:09 | 49.948
2020-02-27 | 9:09 | 49.946
2020-02-27 | 9:09 | 49.944
2020-02-27 | 9:09 | 49.941
2020-02-27 | 9:09 | 49.939
2020-02-27 | 9:09 | 49.937
2020-02-27 | 9:09 | 49.935
2020-02-27 | 9:09 | 49.935
2020-02-27 | 9:09 | 49.935
2020-02-27 | 9:09 | 49.934
2020-02-27 | 9:09 | 49.932
2020-02-27 | 9:09 | 49.931
2020-02-27 | 9:09 | 49.932
2020-02-27 | 9:09 | 49.933
2020-02-27 | 9:09 | 49.933
2020-02-27 | 9:09 | 49.934
2020-02-27 | 9:09 | 49.934
2020-02-27 | 9:09 | 49.94
2020-02-27 | 9:09 | 49.946
2020-02-27 | 9:09 | 49.95
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.956
2020-02-27 | 9:09 | 49.958
2020-02-27 | 9:09 | 49.958
2020-02-27 | 9:09 | 49.957
2020-02-27 | 9:09 | 49.956
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:09 | 49.951
2020-02-27 | 9:09 | 49.948
2020-02-27 | 9:09 | 49.949
2020-02-27 | 9:09 | 49.948
2020-02-27 | 9:09 | 49.951
2020-02-27 | 9:09 | 49.953
2020-02-27 | 9:10 | 49.956
2020-02-27 | 9:10 | 49.96
2020-02-27 | 9:10 | 49.961
2020-02-27 | 9:10 | 49.962
2020-02-27 | 9:10 | 49.966
2020-02-27 | 9:10 | 49.97
2020-02-27 | 9:10 | 49.974
2020-02-27 | 9:10 | 49.976
2020-02-27 | 9:10 | 49.977
2020-02-27 | 9:10 | 49.979
2020-02-27 | 9:10 | 49.979
2020-02-27 | 9:10 | 49.979
2020-02-27 | 9:10 | 49.98
2020-02-27 | 9:10 | 49.982
2020-02-27 | 9:10 | 49.984
2020-02-27 | 9:10 | 49.988
2020-02-27 | 9:10 | 49.991
2020-02-27 | 9:10 | 49.993
2020-02-27 | 9:10 | 49.994
2020-02-27 | 9:10 | 49.997
2020-02-27 | 9:10 | 49.996
2020-02-27 | 9:10 | 49.995
2020-02-27 | 9:10 | 49.994
2020-02-27 | 9:10 | 49.992
2020-02-27 | 9:10 | 49.99
2020-02-27 | 9:10 | 49.989
2020-02-27 | 9:10 | 49.989
2020-02-27 | 9:10 | 49.988
2020-02-27 | 9:10 | 49.989
2020-02-27 | 9:10 | 49.989
2020-02-27 | 9:10 | 49.991
2020-02-27 | 9:10 | 49.996
2020-02-27 | 9:10 | 49.998
2020-02-27 | 9:10 | 49.997
2020-02-27 | 9:10 | 49.998
2020-02-27 | 9:10 | 50
2020-02-27 | 9:10 | 50.004
2020-02-27 | 9:10 | 50.005
2020-02-27 | 9:10 | 50.005
2020-02-27 | 9:10 | 50.008
2020-02-27 | 9:10 | 50.011
2020-02-27 | 9:10 | 50.011
2020-02-27 | 9:10 | 50.012
2020-02-27 | 9:10 | 50.014
2020-02-27 | 9:10 | 50.016
2020-02-27 | 9:10 | 50.016
2020-02-27 | 9:10 | 50.016
2020-02-27 | 9:10 | 50.017
2020-02-27 | 9:10 | 50.018
2020-02-27 | 9:10 | 50.018
2020-02-27 | 9:10 | 50.018
2020-02-27 | 9:10 | 50.017
2020-02-27 | 9:10 | 50.014
2020-02-27 | 9:10 | 50.009
2020-02-27 | 9:10 | 50.006
2020-02-27 | 9:10 | 50.002
2020-02-27 | 9:10 | 49.998
2020-02-27 | 9:10 | 49.995
2020-02-27 | 9:10 | 49.99
2020-02-27 | 9:10 | 49.985
2020-02-27 | 9:10 | 49.982
2020-02-27 | 9:11 | 49.981
2020-02-27 | 9:11 | 49.979
2020-02-27 | 9:11 | 49.979
2020-02-27 | 9:11 | 49.977
2020-02-27 | 9:11 | 49.977
2020-02-27 | 9:11 | 49.975
2020-02-27 | 9:11 | 49.975
2020-02-27 | 9:11 | 49.975
2020-02-27 | 9:11 | 49.975
2020-02-27 | 9:11 | 49.977
2020-02-27 | 9:11 | 49.979
2020-02-27 | 9:11 | 49.981
2020-02-27 | 9:11 | 49.981
2020-02-27 | 9:11 | 49.982
2020-02-27 | 9:11 | 49.983
2020-02-27 | 9:11 | 49.984
2020-02-27 | 9:11 | 49.984
2020-02-27 | 9:11 | 49.985
2020-02-27 | 9:11 | 49.987
2020-02-27 | 9:11 | 49.988
2020-02-27 | 9:11 | 49.987
2020-02-27 | 9:11 | 49.985
2020-02-27 | 9:11 | 49.985
2020-02-27 | 9:11 | 49.982
2020-02-27 | 9:11 | 49.979
2020-02-27 | 9:11 | 49.975
2020-02-27 | 9:11 | 49.971
2020-02-27 | 9:11 | 49.967
2020-02-27 | 9:11 | 49.963