## Note
Note to 2020 ETYS Appendix B
Where overhead line circuits are strung on the same transmission towers, their proximity to each other can lead to current and voltage in one circuit inducing current and voltage in the other. This mutual coupling between circuits can affect the Positive Phase Sequence parameters of overhead line circuits. The Positive Phase Sequence values in these tables are taken from PowerFactory models used by National Grid for 2020 ETYS analysis which include these mutual coupling effects.
When using power analysis applications that are not capable of modelling mutual coupling, it may be necessary to adjust overhead line parameters in line with accepted industry assumptions. These adjustments are likely to only have minor impact on power flow but can have material impact on voltages over larger networks. ETYS data users are advised to contact National Grid for advice if intending to use this data in this way.
All the ratings provided in the subsequent sections represent the post fault thermal ratings of the equipment, with the exception of those with the value '9999' (in tab B-2-1a). Elements with ratings of 9999 are representative of circuit breakers/bus couplers that are encountered during the PSS/e to PowerFactory conversion process. Additionally, there are few line circuit breakers included in tab B-2-1a with R=0.0100, X=0.0100 and B= 0.0000.
All future year data is non-binding and is liable to change.

## Menu
Electricity Ten Year Statement (ETYS) 2020
Appendix B - Supplementary Technical Data
Table | Title
B.1.1a | SHE Transmission Index of Substation Codes
B.1.1b | SPT Index of Substation Codes
B.1.1c | NGET Index of Substation Codes
B.1.1d | OFTO Index of Substation Codes
B.2.1a | SHE Transmission Circuits 2020/21
B.2.1b | SPT Circuits 2020/21
B.2.1c | NGET Circuits 2020/21
B.2.1d | OFTO Circuits 2020/21
B.2.2a | SHE Transmission Circuit Changes 2021/22 to 2029/30
B.2.2b | SPT Circuit Changes 2021/22 to 2029/30
B.2.2c | NGET Circuit Changes 2021/22 to 2029/30
B.2.2d | OFTO Circuit Changes 2021/22 to 2029/30
B.3.1a | SHE Transmission Transformers Winter 2020/21
B.3.1b | SPT Transformers Winter 2020/21
B.3.1c | NGET Transformers Winter 2020/21
B.3.1d | OFTO Transformers Winter 2020/21
B.3.2a | SHE Transmission Transformer Changes 2021/22 to 2029/30
B.3.2b | SPT Transformer Changes 2021/22 to 2029/30
B.3.2c | NGET Transformer Changes 2021/22 to 2029/30
B.3.2d | OFTO Transformer Changes 2021/22 to 2029/30
B.4.1a | SHE Transmission Reactive Compensation Equipment Winter 2020/21
B.4.1b | SPT Reactive Compensation Equipment Winter 2020/21
B.4.1c | NGET Reactive Compensation Equipment Winter 2020/21
B.4.1d | OFTO Reactive Compensation Equipment Winter 2020/21
B.4.2a | SHE Transmission Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.4.2b | SPT Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.4.2c | NGET Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.4.2d | OFTO Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.5.1 | Intra GB HVDC 2020/21 to 2029/30

## B-1-1a
B.1.1a - SHE Transmission Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABBA | ABERDEEN BAY WINDFARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 33
ABNE | ABERNETHY | 132
ABNE | ABERNETHY | 33
ACHR | A-CHRUACH WINDFARM | 275
ACHR | A-CHRUACH WINDFARM | 132
ACHR | A-CHRUACH WINDFARM | 33
AIGA | AIGAS HYDRO | 132
ALNE | ALNESS GSP | 132
ALNE | ALNESS GSP | 33
ALTN | ALTNABREAC | 132
ALTN | ALTNABREAC | 33
ALYT | ALYTH | 400
ALYT | ALYTH | 275
ALYT | ALYTH | 33
AMUL | AMULREE | 132
ANSU | AN SUIDHE | 275
ANSU | AN SUIDHE | 132
ANSU | AN SUIDHE | 33
ARBR | ARBROATH | 132
ARBR | ARBROATH | 33
ARDK | ARDKINGLAS WIND | 132
ARDK | ARDKINGLAS WIND | 33
ARMO | ARDMORE | 132
ARMO | ARDMORE | 33
ARNI | ARNISH SUBSTATION | 132
ARNI | ARNISH SUBSTATION | 33
BALA | BALALLAN TEE POINT | 132
BEAT | BEATRICE SUBSTATION | 400
BEAU | BEAULY | 400
BEAU | BEAULY | 275
BEAU | BEAULY | 132
BEAU | BEAULY | 33
BEIN | BEINNEUN WIND FARM | 132
BEIN | BEINNEUN WIND FARM | 33
BERB | BERRY BURN | 275
BERB | BERRY BURN | 33
BETH | BEINN THARSUINN WIND | 132
BETH | BEINN THARSUINN WIND | 33
BEWF | BEAW FIELD | 132
BEWF | BEAW FIELD | 33
BHLA | BHLARAIDH WIND FARM | 132
BHLA | BHLARAIDH WIND FARM | 33
BIHI | BIRKHILL | 132
BLEX | BHLARAIDH EXTENSION | 132
BLEX | BHLARAIDH EXTENSION | 33
BLGH | BLARGHOUR | 132
BLGH | BLARGHOUR | 33
BLHI | BLACKHILLOCK | 400
BLHI | BLACKHILLOCK | 275
BLHI | BLACKHILLOCK | 132
BLHI | BLACKHILLOCK | 33
BOAG | BOAT OF GARTEN | 132
BOAG | BOAT OF GARTEN | 33
BRCW | BRACO WEST | 275
BRCW | BRACO WEST | 33
BREC | BRECHIN | 132
BRID | BRIDGE OF DUN | 132
BRID | BRIDGE OF DUN | 33
BROA | BROADFORD | 132
BROA | BROADFORD | 33
BROR | BRORA | 132
BROR | BRORA | 33
BUMU | BURGHMUIR | 132
BUMU | BURGHMUIR | 33
CAAD | CARRADALE | 132
CAAD | CARRADALE | 33
CAID | CAIRN DUHIE WIND FARM | 275
CAID | CAIRN DUHIE WIND FARM | 33
CAIN | CAIRNFORD | 275
CAIN | CAIRNFORD | 33
CASS | CASSLEY | 132
CASS | CASSLEY | 33
CEAN | CEANNACROC | 132
CEAN | CEANNACROC | 33
CHAR | CHARLESTON | 132
CHAR | CHARLESTON | 33
CLAC | CLACHAN | 132
CLAC | CLACHAN | 33
CLAY | CLAYHILLS | 132
CLAY | CLAYHILLS | 33
CLGO | CLASH GOUR WIND FARM | 275
CLGO | CLASH GOUR WIND FARM | 132
CLGO | CLASH GOUR WIND FARM | 33
CLOI | CLOICHE WIND FARM | 132
CLOI | CLOICHE WIND FARM | 33
CLSO | CLASHINDARROCH WIND FARM | 132
CLSO | CLASHINDARROCH WIND FARM | 33
CLUN | CLUNIE | 132
COGA | CORRIEGARTH WIND FARM | 132
COGA | CORRIEGARTH WIND FARM | 33
COGL | COIRE GLAS PUMPED STORAGE | 400
CONN | CONNAGILL | 275
CONN | CONNAGILL | 132
CONN | CONNAGILL | 33
CORI | CORRIEMOILLIE | 132
CORI | CORRIEMOILLIE | 33
COST | COSTA HEAD | 33
COUA | COUPAR ANGUS | 132
COUA | COUPAR ANGUS | 33
COUW | COUR WIND FARM | 33
CRAI | CRAIGIEBUCKLER | 132
CRAI | CRAIGIEBUCKLER | 33
CRDH | CREAG DHUBH | 275
CRDH | CREAG DHUBH | 132
CRDH | CREAG DHUBH | 33
CREA | CREAG RIABHACH WINDFARM | 132
CREA | CREAG RIABHACH WINDFARM | 33
CRSS | CROSSAIG | 275
CRSS | CROSSAIG | 220
CRSS | CROSSAIG | 132
CRSS | CROSSAIG | 33
CULL | CULLIGRAN | 132
DAAS | DALLAS SUBSTATION | 275
DAAS | DALLAS SUBSTATION | 33
DEAN | DEANIE | 132
DENS | DENSIDE | 132
DLCH | DALCHORK | 132
DONW | DOUNREAY WEST | 275
DORE | DORENELL WIND FARM | 132
DORE | DORENELL WIND FARM | 33
DOUN | DOUNREAY | 400
DOUN | DOUNREAY | 275
DOUN | DOUNREAY | 220
DOUN | DOUNREAY | 132
DOUN | DOUNREAY | 33
DRUL | DRUIM LETHANN WIND FARM | 132
DRUL | DRUIM LETHANN WIND FARM | 33
DUBE | DUNBEATH | 132
DUBE | DUNBEATH | 33
DUCC | DUNMORE CABLE COMPOUND | 132
DUDH | DUDHOPE | 132
DUDH | DUDHOPE | 33
DUGR | DUNVEGAN GRID | 132
DUGR | DUNVEGAN GRID | 33
DUNM | DUNMAGLASS | 132
DUNM | DUNMAGLASS | 33
DUNO | DUNOON | 132
DUNO | DUNOON | 33
DYCE | DYCE | 132
DYCE | DYCE | 33
EDIN | EDINBANE 132/33KV | 132
EDIN | EDINBANE 132/33KV | 33
ELCH | ELCHIES | 132
ELCH | ELCHIES | 33
ELGI | ELGIN | 132
ELGI | ELGIN | 33
ENEI | ENERGY ISLES WIND FARM | 132
ENEI | ENERGY ISLES WIND FARM | 33
ERRO | ERROCHTY | 132
FAAR | FARR WINDFARM | 132
FAAR | FARR WINDFARM | 33
FARI | FARIGAIG | 275
FARI | FARIGAIG | 132
FARI | FARIGAIG | 33
FASN | FASNAKYLE | 275
FASN | FASNAKYLE | 33
FAUG | FORT AUGUSTUS | 400
FAUG | FORT AUGUSTUS | 275
FAUG | FORT AUGUSTUS | 132
FAUG | FORT AUGUSTUS | 33
FERO | FERNOCH WIND | 132
FERO | FERNOCH WIND | 33
FETT | FETTERESSO | 400
FETT | FETTERESSO | 275
FETT | FETTERESSO | 132
FETT | FETTERESSO | 33
FIDD | FIDDES | 132
FIDD | FIDDES | 33
FINL | FINLARIG | 132
FINS | ORKNEY FINSTOWN | 132
FINS | ORKNEY FINSTOWN | 33
FOFO | FIRTHOF FORTH ONSHORE | 275
FOGG | FOGGIETON | 132
FOYE | FOYERS | 275
FRAS | FRASERBURGH | 132
FRAS | FRASERBURGH | 33
FWIL | FORT WILLIAM | 132
FWIL | FORT WILLIAM | 33
FYRI | FYRISH | 275
FYRI | FYRISH | 132
FYRI | FYRISH | 33
GILB | GILLS BAY SUBSTATION | 132
GLAG | GLENAGNES | 132
GLDO | GLENDOE SUBSTATION | 132
GLEN | GLENMORISTON | 132
GLFA | GLENFARCLAS | 132
GLFA | GLENFARCLAS | 33
GLKO | GLEN KYLLACHY WIND FARM - ONSHORE | 132
GLKO | GLEN KYLLACHY WIND FARM - ONSHORE | 33
GLNU | GLEN ULLINISH WINDFARM | 132
GLNU | GLEN ULLINISH WINDFARM | 33
GLSH | GELNSHERO WINDFARM | 132
GLSH | GELNSHERO WINDFARM | 33
GORW | GORDONBUSH WINDFARM | 275
GORW | GORDONBUSH WINDFARM | 33
GRIF | GRIFFIN WINDFARM (SSE) | 132
GRIF | GRIFFIN WINDFARM (SSE) | 33
GRUB | GRUDIE BRIDGE | 132
GRUB | GRUDIE BRIDGE | 33
HEST | HESTA HEAD | 33
INGA | INVERGARRY | 400
INGA | INVERGARRY | 132
INGA | INVERGARRY | 33
INNE | INVERNESS | 132
INNE | INVERNESS | 33
INRU | INVERUGIE | 132
INVE | INVERARAY | 132
INVR | INVERARNAN | 132
INVR | INVERARNAN | 33
KEIT | KEITH | 275
KEIT | KEITH | 132
KEIT | KEITH | 33
KIIN | KILLIN | 132
KIIN | KILLIN | 33
KILC | KILLIN CASCADE GROUP | 132
KILO | KINLOCHLEVEN 132KV SUBSTATION | 132
KILO | KINLOCHLEVEN 132KV SUBSTATION | 33
KINA | KINARDOCHY | 275
KINB | KINCARDINE BOUNDARY | 275
KINT | KINTORE | 400
KINT | KINTORE | 275
KINT | KINTORE | 132
KINT | KINTORE | 33
KIOR | KILMORACK | 132
KNOC | KNOCKNAGAEL | 275
KNOC | KNOCKNAGAEL | 132
KNOC | KNOCKNAGAEL | 33
LAGG | LAGGAN | 132
LAIR | LAIRG | 132
LAIR | LAIRG | 33
LIMK | LIMEKILNS WINDFARM | 132
LIMK | LIMEKILNS WINDFARM | 33
LOCB | LOCH BUIDHE | 275
LOCB | LOCH BUIDHE | 132
LOCB | LOCH BUIDHE | 33
LOCH | LOCHAY | 132
LOCL | LOCH LUNDIE | 132
LUIC | LUICHART | 132
LUMB | LUMBS | 132
LUNA | LUNANHEAD | 132
LUNA | LUNANHEAD | 33
LUND | LUNDAVRA | 132
LYND | LYNDHURST | 132
LYND | LYNDHURST | 33
MACD | MACDUFF | 132
MACD | MACDUFF | 33
MELG | MELGARVE SUBSTATION | 400
MELG | MELGARVE SUBSTATION | 132
MELG | MELGARVE SUBSTATION | 33
MILC | MILTON OF CRAIGIE | 132
MILC | MILTON OF CRAIGIE | 33
MILS | MILLENNIUM SOUTH WINDFARM | 132
MILS | MILLENNIUM SOUTH WINDFARM | 33
MILW | MILLENIUM WIND | 132
MILW | MILLENIUM WIND | 33
MORF | MORAY EAST ONSHORE SUBSTATION | 400
MORF | MORAY EAST ONSHORE SUBSTATION | 275
MOSS | MOSSFORD | 132
MOTA | MOULTAIVE | 132
MSHL | MOSSY HILL | 132
MSHL | MOSSY HILL | 33
MUAI | MUAITHEBHEAL WIND FARM | 132
MUAI | MUAITHEBHEAL WIND FARM | 33
MYBE | MYBSTER EXTENSION | 132
MYBS | MYBSTER | 132
MYBS | MYBSTER | 33
NAIR | NAIRN | 132
NAIR | NAIRN | 33
NANT | NANT (LOCH NANT) | 132
NEDE | NEW DEER | 400
NEDE | NEW DEER | 275
NESQ | NESS OF QUOYS | 33
NWGL | NORTH CONNECT (NORWEGIAN LINK 2) | 400
OFPH | OFFSHORE PROJECT H | 275
OFPK | OFFSHORE PROJECT K | 400
OFPN | OFFSHORE PROJECT N | 400
ORRI | ORRIN | 132
ORRI | ORRIN | 33
PEHE | PETERHEAD | 400
PEHE | PETERHEAD | 275
PEHE | PETERHEAD | 132
PEHE | PETERHEAD | 33
PEHG | PETERHEAD GRANGE | 132
PEHG | PETERHEAD GRANGE | 33
PENF | PENTLAND FIRTH (MEYGEN) | 132
PENF | PENTLAND FIRTH (MEYGEN) | 33
PERS | PERSLEY | 275
PERS | PERSLEY | 132
PERS | PERSLEY | 33
PORA | PORT ANN | 275
PORA | PORT ANN | 132
PORA | PORT ANN | 33
QUOI | QUOICH | 132
RANN | RANNOCH | 132
RANN | RANNOCH | 33
REDM | REDMOSS | 132
REDM | REDMOSS | 33
ROTI | ROTHIENORMAN | 400
ROTI | ROTHIENORMAN | 275
ROTI | ROTHIENORMAN | 132
ROTI | ROTHIENORMAN | 33
SALA | SALLACHY WIND FARM | 132
SALA | SALLACHY WIND FARM | 33
SFEE | ST FERGUS EAST | 132
SFEG | ST FERGUS GAS TERMINAL | 132
SFEM | ST FERGUS MOBIL | 132
SFER | ST FERGUS | 132
SFEV | ST FERGUS VSD | 132
SFIL | ST FILLANS | 132
SHDM | SHEIRDRIM | 132
SHDM | SHEIRDRIM | 33
SHET | SHETLAND 132KV SUBSTATION | 132
SHIN | SHIN | 132
SHIN | SHIN | 33
SLKB | SLACKBUIE | 132
SLOY | SLOY | 132
SPIT | SPITTAL | 400
SPIT | SPITTAL | 275
SPIT | SPITTAL | 132
SPIT | SPITTAL | 33
STOR | STORNOWAY | 132
STRB | STRATH BRORA WIND | 275
STRB | STRATH BRORA WIND | 33
STRI | STRICHEN | 132
STRI | STRICHEN | 33
STRL | STRONELAIRG WIND FARM (SSE) | 132
STRL | STRONELAIRG WIND FARM (SSE) | 33
STRW | STRATHY WIND | 132
STRW | STRATHY WIND | 33
STWN | STORNOWAY WIND | 132
STWN | STORNOWAY WIND | 33
TARL | TARLAND | 132
TARL | TARLAND | 33
TAYN | TAYNUILT | 132
TAYN | TAYNUILT | 33
TEAL | TEALING | 275
TEAL | TEALING | 132
TEAL | TEALING | 33
THSO | THURSO | 132
THUS | THURSO SOUTH | 275
THUS | THURSO SOUTH | 132
THUS | THURSO SOUTH | 33
TOMT | TOMATIN | 275
TOMT | TOMATIN | 132
TOMT | TOMATIN | 33
TUMB | TUMMEL BRIDGE | 132
TUMM | TUMMEL | 400
TUMM | TUMMEL | 275
TUMM | TUMMEL | 132
TUMM | TUMMEL | 33
WHIB | WHITE BRIDGE | 132
WILW | WILLOW | 132
WIOW | WILLOWDALE | 132
WIOW | WILLOWDALE | 33
WOHI | WOODHILL | 132
WOHI | WOODHILL | 33
YELL | YELL | 132

## B-1-1b
B.1.1b - SPT Index of Substation Codes
Site Code | Site Name | Voltage (kV)
AIKE | AIKENGALL | 33
AIRI | AIRIES | 33
ANDE | ANDERSHAW | 33
AREC | ARECLEOCH | 132
AREC | ARECLEOCH | 33
AREX | ARECLEOCH EXTENSION | 132
AREX | ARECLEOCH EXTENSION | 33
ARFO | ARTFIELD FOREST WF | 33
ASVA | ASSEL VALLEY | 33
AUCH | AUCHENCROSH | 275
AUCW | AUCHENWYND | 132
AURO | AUCHROBERT | 33
AYR- | AYR | 275
AYR- | AYR | 33
BAGA | BATHGATE | 132
BAGA | BATHGATE | 33
BAGA | BATHGATE RAIL | 25
BAIN | BAINSFORD | 33
BENB | BENBRACK WIND FARM | 132
BENB | BENBRACK WIND FARM | 33
BERW | BERWICK | 132
BERW | BERWICK | 33
BLAH | BLACKHILL | 132
BLAH | BLACKHILL | 33
BLCW | BLACKCRAIG | 132
BLCW | BLACKCRAIG | 33
BLKL | BLACKLAW | 132
BLKL | BLACKLAW | 33
BLLX | BLACKLAW EXTENSION | 132
BLLX | BLACKLAW EXTENSION | 33
BONB | BONNYBRIDGE BORDER NODE | 400
BONB | BONNYBRIDGE BORDER NODE | 275
BONN | BONNYBRIDGE | 400
BONN | BONNYBRIDGE | 132
BONN | BONNYBRIDGE | 33
BONN | BONNYBRIDGE | 25
BPGR | BP GRANGEMOUTH | 33
BRAE | BRAEHEAD | 132
BRAP | BRAEHEAD PARK | 132
BRAP | BRAEHEAD PARK | 33
BRNX | BRANXTON | 400
BROC | BROKEN CROSS | 132
BROX | BROXBURN | 132
BROX | BROXBURN | 33
BUSB | BUSBY | 275
CAFA | CARSFAD | 132
CAFA | CARSFAD | 11
CALD | CALDER WATER | 33
CAMI | CAMILLA BES | 33
CATY | CARNTYNE | 132
CATY | CARNTYNE | 33
CATY | CARNTYNE | 25
CHAP | CHAPELCROSS | 132
CHAP | CHAPELCROSS | 33
CHAS | CHARLOTTE STREET | 275
CHAS | CHARLOTTE STREET | 33
CHMO | CHIRMORIE | 132
CLAU | CLAUCHRIE | 132
CLAU | CLAUCHRIE | 33
CLYM | CLYDE'S MILL | 275
CLYM | CLYDE'S MILL | 33
CLYN | CLYDE NORTH | 275
CLYN | CLYDE NORTH | 33
CLYS | CLYDE SOUTH | 275
CLYS | CLYDE SOUTH | 33
COAL | COALBURN | 400
COAL | COALBURN | 132
COAL | COALBURN | 33
COAT | COATBRIDGE | 275
COAT | COATBRIDGE | 33
COCK | COCKENZIE | 400
COCK | COCKENZIE | 275
COCK | COCKENZIE | 33
COYL | COYLTON | 275
COYL | COYLTON | 132
COYL | COYLTON | 33
COYT | COYLTON TEE | 132
COYW | COYLTON WEST | 275
CRCK | CARRICK | 275
CRCK | CARRICK | 33
CRDE | CROSSDYKES EXTENSION | 33
CRDY | CROSSDYKES | 33
CROE | CROOKEDSTANE | 33
CROO | CROOKSTON | 132
CROO | CROOKSTON | 33
CRUA | CRUACHAN | 275
CRYR | CRYSTAL RIG | 400
CRYR | CRYSTAL RIG | 132
CRYR | CRYSTAL RIG | 33
CUMB | CUMBERNAULD | 132
CUMB | CUMBERNAULD | 33
CUMH | CUMBERHEAD | 132
CUMH | CUMBERHEAD WF SUBSTATION | 33
CUMW | CUMBERHEAD WEST | 132
CUMW | CUMBERHEAD WEST | 33
CUPA | CUPAR | 132
CUPA | CUPAR | 33
CURR | CURRIE | 275
CURR | CURRIE | 132
CURR | CURRIE | 33
CURR | CURRIE | 25
CURR | CURRIE | 11
DALB | DALMALLY BORDER NODE | 275
DALL | DALMALLY | 275
DALM | DALMARNOCK | 275
DALM | DALMARNOCK | 132
DALM | DALMARNOCK | 33
DALQ | DALQUHANDY | 33
DALS | DALSWINTON | 33
DENN | DENNY NORTH | 400
DENN | DENNY NORTH | 275
DENN | DENNY NORTH | 132
DENN | DENNY NORTH | 33
DESA | DERSALLOCH | 33
DEVM | DEVOL MOOR | 400
DEVM | DEVOL MOOR | 132
DEVM | DEVOL MOOR | 33
DEVM | DEVOL MOOR | 25
DEVO | DEVONSIDE | 132
DEVO | DEVONSIDE | 33
DEWP | DEWAR PLACE | 275
DEWP | DEWAR PLACE | 33
DONO | DOUGLAS NORTH | 132
DOWE | DOUGLAS WEST | 33
DOWX | DOUGLAS WEST EXTENSION | 33
DRCR | DRUMCROSS | 132
DRCR | DRUMCROSS | 33
DRUM | DRUMCHAPEL | 275
DRUM | DRUMCHAPEL | 33
DUMF | DUMFRIES | 132
DUMF | DUMFRIES | 33
DUNB | DUNBAR | 132
DUNB | DUNBAR | 33
DUNE | DUNLAW EXTENSION | 132
DUNE | DUNLAW EXTENSION | 33
DUNF | DUNFERMLINE | 132
DUNF | DUNFERMLINE | 33
DUNH | DUNHILL | 33
EARB | EARLSBURN | 33
EAST | EARLSTOUN | 132
EAST | EARLSTOUN | 11
ECCF | ECCLEFECHAN | 132
ECCF | ECCLEFECHAN | 25
ECCL | ECCLES | 400
ECCL | ECCLES | 132
ECCL | ECCLES | 33
EERH | EASTERHOUSE | 275
EERH | EASTERHOUSE | 33
EKIL | EAST KILBRIDE | 275
EKIL | EAST KILBRIDE | 33
EKIS | EAST KILBRIDE SOUTH | 275
EKIS | EAST KILBRIDE SOUTH | 33
ELDE | ELDERSLIE | 132
ELDE | ELDERSLIE | 33
ELVA | ELVANFOOT | 400
ELVA | ELVANFOOT | 275
ELVA | ELVANFOOT | 132
ELVA | ELVANFOOT | 33
ELVA | ELVANFOOT | 25
ELVN | ELVANFOOT NORTH 132KV | 132
ELVN | ELVANFOOT NORTH 400KV | 400
ENHI | ENOCH HILL | 132
ENHI | ENOCH HILL WIND FARM | 33
ERSK | ERSKINE | 132
ERSK | ERSKINE | 33
ESST | ESSENSIDE | 132
EUCH | EUCHANHEAD | 33
EUCH | EUCHANHEAD | 132
EWEH | EWE HILL | 132
EWEH | EWE HILL | 33
EXON | EXXON MOBIL | 33
EXON | EXXON MOBIL | 11
FALL | FALLAGO | 400
FALL | FALLAGO | 33
FASI | FAW SIDE | 132
FIFE | FIFE ENERGY | 132
FINN | FINNIESTON | 132
FINN | FINNIESTON | 33
GALA | GALASHIELS | 132
GALA | GALASHIELS | 33
GARB | GARELOCH BOUNDARY | 132
GARE | GARELOCH | 132
GAWH | GALAWHISTLE | 132
GAWH | GALAWHISTLE | 33
GBRN | GREENBURN | 132
GHPS | GLENMUCKLOCH | 400
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 132
GIFF | GIFFNOCK | 275
GIFF | GIFFNOCK | 33
GLAP | GLEN APP | 33
GLGL | GLENGLASS | 132
GLGL | GLENGLASS | 33
GLLE | GLENLEE | 132
GLLE | GLENLEE | 11
GLLU | GLENLUCE | 132
GLLU | GLENLUCE | 33
GLMU | GLENMUCKLOCH | 33
GLNI | GLENNISTON | 132
GLNI | GLENNISTON | 33
GLRB | GLENROTHES BOUNDARY | 275
GLRO | GLENROTHES | 275
GLRO | GLENROTHES | 33
GNSH | GLENSHIMMEROCH | 132
GNSH | GLENSHIMMEROCH | 33
GORG | GORGIE | 132
GORG | GORGIE | 33
GOVA | GOVAN | 132
GOVA | GOVAN | 33
GRGR | GREENGAIRS WIND FARM | 33
GRMO | GRANGEMOUTH | 275
GRMO | GRANGEMOUTH | 33
GRNA | GRETNA | 400
GRNA | GRETNA | 132
GRNA | GRETNA | 33
HADH | HADYARD HILL | 132
HADH | HADYARD HILL | 33
HAGH | HAGSHAW HILL PHASE 2 | 33
HAGR | HAGGS ROAD | 132
HAGR | HAGGS ROAD | 33
HAGS | HAGSHAW HILL PHASE 1 | 33
HAKB | HARKER BORDER NODE | 400
HAKB | HARKER BORDER NODE | 132
HARE | HARESTANES | 132
HARE | HARESTANES | 33
HARG | HARTING RIG | 33
HARH | HARBURN HEAD | 33
HAWI | HAWICK | 132
HAWI | HAWICK | 33
HELE | HELENSBURGH | 132
HELE | HELENSBURGH | 33
HOLM | HOLM HILL | 132
HOPR | HOPSRIG | 132
HUCS | HUNTERSTON CONVERTER STATION | 400
HUER | HUNTERSTON | 400
HUER | HUNTERSTON | 132
HUER | HUNTERSTON | 33
HUNE | HUNTERSTON EAST | 400
HUNF | HUNTERSTON FARM | 132
HUNF | HUNTERSTON FARM | 33
HUNN | HUNTERSTON NORTH | 220
INKE | INVERKEITHING | 132
INKE | INVERKEITHING | 33
INVB | INVERARNAN BORDER | 275
INVR | INVERARNAN | 275
INWI | INNERWICK | 132
INWI | INNERWICK | 25
JOHN | JOHNSTONE | 33
JUNA | JUNCTION A | 132
JUNV | JUNCTION V | 132
KAIM | KAIMES | 275
KAIM | KAIMES | 33
KEIH | KEITHSHILL | 33
KENE | KENNOXHEAD WINDFARM EXTENSION | 33
KENN | KENNOXHEAD | 132
KENN | KENNOXHEAD | 33
KEOO | KENDOON | 132
KEOO | KENDOON | 11
KIER | KILLERMONT | 132
KIER | KILLERMONT | 33
KILB | KILBOWIE | 132
KILB | KILBOWIE | 33
KILB | KILBOWIE | 11
KILG | KILGALLIOCH | 275
KILG | KILGALLIOCH | 33
KILS | KILMARNOCK SOUTH | 400
KILS | KILMARNOCK SOUTH | 275
KILS | KILMARNOCK SOUTH | 132
KILS | KILMARNOCK SOUTH | 33
KILT | KILMARNOCK TOWN | 275
KILT | KILMARNOCK TOWN | 33
KILW | KILWINNING | 132
KILW | KILWINNING | 33
KINB | KINCARDINE BOUNDARY | 275
KINC | KINCARDINE | 275
KINC | KINCARDINE | 33
KNOK | KNOCKODHAR | 132
KNOK | KNOCKODHAR | 33
KYPE | KYPE MUIR | 132
KYPE | KYPE MUIR | 33
LAMB | LAMBHILL | 275
LEGO | LESMAHAGOW | 132
LEGO | LESMAHAGOW GSP | 33
LETH | LETHANS | 132
LEVE | LEVEN | 33
LEVT | LEVEN TEE | 132
LING | LIVINGSTON | 132
LING | LIVINGSTON | 33
LINM | LINNMILL | 132
LINM | LINNMILL | 33
LOAN | LONGANNET | 275
LOBU | LONGHILL BURN WF | 33
LOGN | LOCHGOIN | 33
LOPA | LONGPARK | 33
LORG | LORG COLLECTOR SUBSTATION | 132
LORG | LORG WIND FARM | 33
MAHI | MARK HILL | 275
MAHI | MARK HILL | 132
MAHI | MARK HILL | 33
MARG | MARGREE | 132
MARM | MARSHALL MEADOWS | 132
MAYB | MAYBOLE | 132
MAYB | MAYBOLE | 33
MAYT | MAYBOLE TEE | 132
MEAD | MEADOWHEAD | 132
MEAD | MEADOWHEAD | 11
MIDM | MIDDLE MUIR | 132
MIDM | MIDDLE MUIR | 33
MINN | MINNYGAP | 33
MINS | MINSCA | 33
MOFF | MOFFAT | 400
MOFF | MOFFAT | 132
MOFF | MOFFAT GSP | 33
MONQ | MONQUHILL | 33
MOSH | MOSSMORRAN SHELL | 132
MOSH | MOSSMORRAN SHELL | 11
MOSM | MOSSMORRAN | 275
MOSM | MOSSMORRAN | 132
MOSM | MOSSMORRAN | 33
NEAR | NEWARTHILL | 275
NEAR | NEWARTHILL | 33
NECU | NEW CUMNOCK | 275
NECU | NEW CUMNOCK | 132
NECU | NEW CUMNOCK | 33
NEIL | NEILSTON | 400
NEIL | NEILSTON | 275
NEIL | NEILSTON | 132
NEIL | NEILSTON | 33
NETS | NEWTON STEWART | 132
NETS | NEWTON STEWART | 33
NLEI | NORTH LOWTHER | 33
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 132
NOKY | NORTH KYLE | 132
NOKY | NORTH KYLE | 33
OFOA | OLD FOREST OF AE | 132
OFOA | OLD FOREST OF AE | 33
OHLL | OVERHILL | 132
OHLL | OVERHILL | 33
PAIS | PAISLEY | 132
PAIS | PAISLEY | 33
PART | PARTICK | 132
PART | PARTICK | 33
PENC | PENCLOE | 33
POGB | POGBIE | 33
POLK | POLKEMMET | 33
POOB | PORTOBELLO | 275
POOB | PORTOBELLO | 33
POOB | PORTOBELLO | 25
PORD | PORT DUNDAS | 275
PORD | PORT DUNDAS | 33
PRST | PRIESTGILL | 33
RAVE | RAVENSCRAIG | 33
REDH | REDHOUSE | 132
REDH | REDHOUSE | 33
ROAR | ROARING HILL | 33
ROBP | ROTHES BIOPOWER | 33
SACO | SALTCOATS | 132
SACO | SALTCOATS | 33
SACO | SALTCOATS | 25
SAKN | SANDY KNOWE | 132
SAKN | SANDY KNOWE | 33
SANQ | SANQUHAR WIND FARM | 132
SANX | ST ANDREWS CROSS | 132
SANX | ST ANDREWS CROSS | 33
SANX | ST ANDREWS CROSS | 25
SCOP | SCOOP HILL WIND FARM | 132
SHRG | SHEPHERDS RIG | 132
SHRG | SHEPHERDS RIG | 33
SHRU | SHRUBHILL | 275
SHRU | SHRUBHILL | 33
SIGH | SIGHTHILL | 275
SIGH | SIGHTHILL | 33
SMEA | SMEATON | 400
SMEA | SMEATON | 275
SMEA | SMEATON | 132
SMEA | SMEATON | 33
SNED | SNEDDON LAW | 33
SNQR | SANQUHAR | 33
SOKY | SOUTH KYLE | 132
SOKY | SOUTH KYLE | 33
SOLW | SOLWAY BANK | 33
SPAV | SPANGO VALLEY | 132
SPAV | SPANGO VALLEY | 33
STCR | STEVEN'S CROFT | 33
STHA | STRATHAVEN | 400
STHA | STRATHAVEN | 275
STHA | STRATHAVEN | 33
STIR | STIRLING | 132
STIR | STIRLING | 33
STLE | STRATHLEVEN | 132
STLE | STRATHLEVEN | 33
STLE | STRATHLEVEN | 25
STNO | STRANOCH | 132
STNO | STRANOCH | 33
STWB | STELLA WEST BORDER NODE | 400
TELR | TELFORD ROAD | 132
TELR | TELFORD ROAD | 33
TODD | TODDLEBURN | 33
TONG | TONGLAND | 132
TONG | TONGLAND | 33
TONG | TONGLAND | 11
TORH | TORR HILL | 33
TORM | TORMYWHEEL | 33
TORN | TORNESS | 400
TORN | TORNESS | 132
TORN | TORNESS | 33
TRLO | TRALORG | 33
TRSN | TROSTON | 132
TRSN | TROSTON | 33
TWEN | TWENTYSHILLING | 33
VIRD | VIRIDOR | 33
WESE | WESTERDOD | 132
WFIB | WESTFIELD BOUNDARY | 275
WFIE | WESTFIELD | 275
WFIE | WESTFIELD | 132
WFIE | WESTFIELD | 33
WGEO | WEST GEORGE STREET | 275
WGEO | WEST GEORGE STREET | 33
WHBR | WHITELAW BRAE | 33
WHHO | WHITEHOUSE | 275
WHHO | WHITEHOUSE | 33
WHLL | WHITESIDE HILL | 33
WHTB | WHISTLEFIELD BOUNDARY | 132
WHTL | WHISTLEFIELD | 132
WHTL | WHISTLEFIELD | 33
WISH | WISHAW (GOWKTHRAPPLE) | 400
WISH | WISHAW (GOWKTHRAPPLE) | 275
WISH | WISHAW (GOWKTHRAPPLE) | 132
WISH | WISHAW (GOWKTHRAPPLE) | 33
WISH | WISHAW (GOWKTHRAPPLE) | 25
WIYH | WINDYHILL | 400
WIYH | WINDYHILL | 275
WIYH | WINDYHILL | 132
WIYH | WINDYHILL | 33
WLEE | WHITELEE | 275
WLEE | WHITELEE | 33
WLEX | WHITELEE EXTENSION | 275
WLEX | WHITELEE EXTENSION | 33
WNDR | WINDY RIG | 33

## B-1-1c
B.1.1c - NGET Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABTH | ABERTHAW | 275
ABTH | ABERTHAW | 132
ABHA | ABHAM | 400
ABHA | ABHAM | 132
ACTL | ACTON LANE | 22
ALDW | ALDWARKE | 275
ALST | ALPHA STEEL | 33
ALVE | ALVERDISCOTT | 400
ALVE | ALVERDISCOTT | 132
AMEM | AMERSHAM MAIN | 400
AMEM | AMERSHAM MAIN | 132
AUST | AUST | 400
AXMI | AXMINSTER | 400
BAGB | BAGLAN BAY | 275
BARK | BARKING | 400
BARK | BARKING | 275
BARK | BARKING | 132
BARP | BARKING PS | 275
BEDD | BEDDINGTON | 400
BEDD | BEDDINGTON | 275
BEDD | BEDDINGTON | 132
BEDT | BEDDINGTON TEE | 132
BESW | BERKSWELL | 275
BESW | BERKSWELL | 132
BICF | BICKER FEN | 400
BICF | BICKER FEN | 132
BIRK | BIRKENHEAD | 275
BIRK | BIRKENHEAD | 132
BISW | BISHOPS WOOD | 275
BISW | BISHOPS WOOD | 132
BLYT | BLYTH | 400
BLYT | BLYTH | 275
BLYT | BLYTH | 132
BLYT | BLYTH | 66
BODE | BODELWYDDAN | 400
BODE | BODELWYDDAN | 132
BOLN | BOLNEY | 400
BOLN | BOLNEY | 132
BOTW | BOTLEY WOOD | 400
BOTW | BOTLEY WOOD | 132
BRAW | BRADFORD WEST | 400
BRAW | BRADFORD WEST | 275
BRAW | BRADFORD WEST | 132
BRAI | BRAINTREE | 132
BRAI | BRAINTREE | 400
BRFO | BRAMFORD | 400
BRFO | BRAMFORD | 132
BRLE | BRAMLEY | 400
BRLE | BRAMLEY | 132
BRED | BREDBURY | 275
BRED | BREDBURY | 132
BRGN | BRELSTON GREEN | 400
BRWA | BRIDGWATER | 400
BRWA | BRIDGWATER | 275
BRIM | BRIMSDOWN | 275
BRIM | BRIMSDOWN | 132
BRIN | BRINSWORTH | 400
BRIN | BRINSWORTH | 275
BRIT | BRITNED | 400
BULL | BULLS LODGE | 400
BURW | BURWELL MAIN | 400
BURW | BURWELL MAIN | 132
BUSH | BUSHBURY | 400
BUSH | BUSHBURY | 275
BUSH | BUSHBURY | 132
BUST | BUSTLEHOLME | 400
BUST | BUSTLEHOLME | 275
BUST | BUSTLEHOLME | 132
CAML | CAMBLESFORTH | 66
CAMA | CAMBRIDGE ARMS | 132
CANT | CANTERBURY NORTH | 132
CANT | CANTERBURY NORTH | 400
CAPE | CAPENHURST | 400
CAPE | CAPENHURST | 275
CAPE | CAPENHURST | 132
CARE | CARDIFF EAST | 275
CARE | CARDIFF EAST | 132
CARR | CARRINGTON | 400
CARR | CARRINGTON | 275
CARR | CARRINGTON | 132
CELL | CELLARHEAD | 400
CELL | CELLARHEAD | 132
CHUE | CHAFFORD HUNDRED EAST | 400
CHUW | CHAFFORD HUNDRED WEST | 400
CHSI | CHESSINGTON | 275
CHSI | CHESSINGTON | 132
CHTE | CHESTERFIELD | 275
CHTE | CHESTERFIELD | 132
CHTM | CHETNEY MARSH | 400
CHIC | CHICKERELL | 400
CHIC | CHICKERELL | 132
CHIL | CHILLING | 400
CILF | CILFYNYDD | 400
CILF | CILFYNYDD | 275
CITR | CITY ROAD | 400
CITR | CITY ROAD | 132
CLEH | CLEVE HILL | 400
CONQ | CONNAHS QUAY | 400
CONQ | CONNAHS QUAY | 132
COSO | CORYTON SOUTH | 400
COTT | COTTAM | 400
COVE | COVENTRY | 275
COVE | COVENTRY | 132
COWB | COWBRIDGE | 275
COWT | COWBRIDGE TEE | 275
COWL | COWLEY | 400
COWL | COWLEY | 132
CREB | CREYKE BECK | 400
CREB | CREYKE BECK | 275
CREB | CREYKE BECK | 132
CULJ | CULHAM JET | 400
DAIN | DAINES | 400
DAIN | DAINES | 275
DAMC | DAMHEAD CREEK | 400
DEES | DEESIDE | 400
DIDC | DIDCOT | 400
DINO | DINORWIG | 400
DRAK | DRAKELOW | 400
DRAK | DRAKELOW | 275
DRAK | DRAKELOW | 132
DRAX | DRAX | 400
DRAX | DRAX | 132
DUBR | DUNFORD BRIDGE | 400
DUNG | DUNGENESS | 400
DUNG | DUNGENESS | 275
EALI | EALING | 66
EALI | EALING | 275
ECLA | EAST CLAYDON | 400
ECLA | EAST CLAYDON | 132
EASO | EATON SOCON | 400
EASO | EATON SOCON | 132
EGGB | EGGBOROUGH | 400
ELLA | ELLAND | 275
ELLA | ELLAND | 132
ELST | ELSTREE | 400
ELST | ELSTREE | 275
ELST | ELSTREE | 132
ENDE | ENDERBY | 400
ENDE | ENDERBY | 132
EXET | EXETER | 400
EXET | EXETER MAIN | 132
FAWL | FAWLEY | 400
FAWL | FAWLEY | 132
FECK | FECKENHAM | 400
FECK | FECKENHAM | 275
FENW | FENWICK TEE | 400
FERR | FERRYBRIDGE | 400
FERR | FERRYBRIDGE | 275
FERR | FERRYBRIDGE | 132
FFES | FFESTINIOG | 275
FIDF | FIDDLERS FERRY | 275
FIDF | FIDDLERS FERRY | 132
FLEE | FLEET | 400
FLEE | FLEET | 132
FLIB | FLINTSHIRE BRIDGE | 400
FOUR | FOURSTONES | 275
FRIN | FRISTON | 400
FROD | FRODSHAM | 400
FROD | FRODSHAM | 275
FROD | FRODSHAM | 132
GART | GARTH CABLE COMPOUND | 400
GRAI | GRAIN | 400
GRAI | GRAIN | 132
GRAN | GRANGE | 66
GRTO | GRANGETOWN | 275
GREN | GRENDON | 400
GREN | GRENDON | 132
GRST | GREYSTONES | 275
GRIW | GRIMSBY WEST | 400
GRIW | GRIMSBY WEST | 132
HACK | HACKNEY | 400
HACK | HACKNEY | 275
HACK | HACKNEY | 132
HAMB | HAMBLETON | 400
HAMH | HAMS HALL | 400
HAMH | HAMS HALL | 275
HAMH | HAMS HALL | 132
HARK | HARKER | 400
HARK | HARKER | 275
HARK | HARKER | 132
HATL | HARTLEPOOL | 275
HARM | HARTMOOR | 275
HAWP | HAWTHORN PIT | 400
HAWP | HAWTHORN PIT | 275
HEDD | HEDDON TEE | 400
HEDO | HEDON | 275
HEND | HENDON | 132
HEYS | HEYSHAM | 400
HEYS | HEYSHAM | 132
HIGM | HIGH MARNHAM | 400
HIGM | HIGH MARNHAM | 275
HIBU | HIGHBURY | 400
HIBU | HIGHBURY | 132
HINP | HINKLEY POINT | 400
HINP | HINKLEY POINT | 275
HORP | HORSESHOE POINT | 400
HUMR | HUMBER REFINERY | 400
HURS | HURST | 275
HURS | HURST | 132
HUTT | HUTTON | 400
HUTT | HUTTON | 132
IMPP | IMPERIAL PARK | 400
INCE | INCE | 132
INDQ | INDIAN QUEENS | 400
INDQ | INDIAN QUEENS | 132
IROA | IRON ACTON | 275
IROA | IRON ACTON | 132
IRON | IRONBRIDGE | 400
IRON | IRONBRIDGE | 132
ISLI | ISLINGTON | 132
IVER | IVER | 400
IVER | IVER | 275
IVER | IVER | 132
JORD | JORDANTHORPE | 275
KEAD | KEADBY | 400
KEAD | KEADBY | 132
KEAP | KEADBY POWER | 400
KEAR | KEARSLEY | 400
KEAR | KEARSLEY | 275
KEAR | KEARSLEY | 132
KEMS | KEMSLEY | 400
KEMS | KEMSLEY | 132
KENG | KENSAL GREEN | 400
KILL | KILLINGHOLME | 400
KINO | KINGSNORTH | 400
KINO | KINGSNORTH | 132
KIBY | KIRKBY | 275
KIBY | KIRKBY | 132
KIRK | KIRKSTALL | 275
KIRK | KIRKSTALL | 132
KITW | KITWELL | 275
KITW | KITWELL | 132
KNAR | KNARESBOROUGH | 275
KNAR | KNARESBOROUGH | 132
LACK | LACKENBY | 400
LACK | LACKENBY | 275
LAKE | LAKESIDE CABLE COOLING STATION | 400
LALE | LALEHAM | 275
LALE | LALEHAM | 132
LAND | LANDULPH | 400
LAND | LANDULPH | 132
LAGA | LANGAGE | 400
LEMR | LEA MARSTON | 132
LEGA | LEGACY | 400
LEGA | LEGACY | 132
LEIB | LEIGHTON BUZZARD | 400
LEIB | LEIGHTON BUZZARD | 275
LEIS | LEISTON | 400
LEIS | LEISTON | 132
LEWO | LEWINGDON WOOD | 400
LISD | LISTER DRIVE | 275
LISD | LISTER DRIVE | 132
LITB | LITTLE BARFORD | 400
LITT | LITTLEBROOK | 400
LITT | LITTLEBROOK | 275
LITT | LITTLEBROOK | 132
LODR | LODGE ROAD | 66
LOFI | LONGFIELD | 400
LOVE | LOVEDEAN | 400
LOVE | LOVEDEAN | 275
LOVE | LOVEDEAN | 132
LOXT | LOXTON | 400
MACC | MACCLESFIELD | 400
MACC | MACCLESFIELD | 275
MANN | MANNINGTON | 400
MANN | MANNINGTON | 132
MANS | MANSFIELD | 400
MAWO | MARCHWOOD | 400
MAGA | MARGAM | 275
MEDW | MEDWAY | 400
MELK | MELKSHAM | 400
MELK | MELKSHAM | 275
MELK | MELKSHAM | 132
MIDL | MIDDLETON | 400
MILH | MILL HILL | 275
MILH | MILL HILL | 132
MITY | MINETY | 400
MITY | MINETY | 132
MONF | MONK FRYSTON | 400
MONF | MONK FRYSTON | 275
MODO | MOULSFORD DOWN | 400
NECH | NECHELLS | 275
NECH | NECHELLS | 132
NECT | NECTON | 400
NECT | NECTON | 132
NEEP | NEEPSEND | 400
NEEP | NEEPSEND | 275
NEWX | NEW CROSS | 275
NEWX | NEW CROSS | 132
NEWK | NEWARK | 400
NWBY | NEWBY SEALING END COMPOUND | 400
NEHO | NEWHOUSE | 400
NINF | NINFIELD | 400
NINF | NINFIELD | 132
NHYD | NORTH HYDE | 275
NFLE | NORTHFLEET EAST | 400
NFLE | NORTHFLEET EAST | 132
NFLW | NORTHFLEET WEST | 400
NFLW | NORTHFLEET WEST | 132
NORT | NORTON | 400
NORT | NORTON | 275
NORT | NORTON | 132
NORL | NORTON LEES | 275
NORW | NORWICH | 400
NORW | NORWICH | 132
NORM | NORWICH MAIN | 400
NOTR | NORWICH TROWSE | 132
NUNT | NUNTHORPE SEALING END COMPOUND | 400
NURS | NURSLING | 400
NURS | NURSLING | 132
OCKH | OCKER HILL | 275
OCKH | OCKER HILL | 132
OFFE | OFFERTON | 275
OLDB | OLDBURY | 400
OLDB | OLDBURY | 275
OLDB | OLDBURY | 132
OLDS | OLDBURY ON SEVERN | 132
OSBA | OSBALDWICK | 400
OSBA | OSBALDWICK | 132
PADI | PADIHAM | 400
PADI | PADIHAM | 132
PAFB | PATFORD BRIDGE | 400
PELH | PELHAM | 400
PELH | PELHAM | 132
PEMB | PEMBROKE | 400
PEMB | PEMBROKE | 132
PENN | PENN | 400
PENN | PENN | 275
PENN | PENN | 132
PERH | PENRHOS | 132
PENT | PENTIR | 400
PENT | PENTIR | 132
PEWO | PENWORTHAM | 400
PEWO | PENWORTHAM | 275
PENE | PENWORTHAM EAST | 132
PENW | PENWORTHAM WEST | 132
PITS | PITSMOOR | 275
POPP | POPPLETON | 275
PORH | PORT HAM | 132
PUDM | PUDDING MILL LANE | 400
PURI | PURITON TEE | 400
PYLE | PYLE | 275
PYLE | PYLE | 132
QUER | QUERNMOOR | 400
RAIN | RAINHILL | 275
RAIN | RAINHILL | 132
RASS | RASSAU | 400
RASS | RASSAU | 132
RATS | RATCLIFFE-ON-SOAR | 400
RATS | RATCLIFFE-ON-SOAR | 275
RATS | RATCLIFFE-ON-SOAR | 132
RAYL | RAYLEIGH | 400
RAYM | RAYLEIGH MAIN | 132
REBR | REDBRIDGE | 275
RHIG | RHIGOS | 400
RICH | RICHBOROUGH | 400
ROCH | ROCHDALE | 400
ROCH | ROCHDALE | 275
ROCH | ROCHDALE | 132
ROCK | ROCKSAVAGE | 400
ROCK | ROCKSAVAGE | 132
ROWD | ROWDOWN | 400
RUGE | RUGELEY | 400
RUGE | RUGELEY | 132
RYEH | RYE HOUSE | 400
RYEH | RYE HOUSE | 132
RYHA | RYHALL | 400
SAEN | SALTEND NORTH | 275
SAEN | SALTEND NORTH | 132
SAES | SALTEND SOUTH | 275
SALH | SALTHOLME | 400
SALH | SALTHOLME | 275
SALH | SALTHOLME | 132
SAFO | SANDFORD | 400
SEAB | SEABANK | 400
SEAB | SEABANK | 132
SELL | SELLINDGE | 400
SELL | SELLINDGE | 275
SELL | SELLINDGE | 132
SHEE | SHEERNESS | 132
SHEC | SHEFFIELD CITY | 275
SHRE | SHREWSBURY | 400
SHRE | SHREWSBURY | 132
SHUR | SHURTON | 400
SING | SINGLEWELL | 400
SING | SINGLEWELL | 275
SIZE | SIZEWELL | 400
SIZE | SIZEWELL | 132
SKLG | SKELTON GRANGE | 275
SKLG | SKELTON GRANGE | 132
SHBA | SOUTH HUMBER BANK | 400
SMAN | SOUTH MANCHESTER | 275
SMAN | SOUTH MANCHESTER | 132
SSHI | SOUTH SHIELDS | 275
SPLN | SPALDING NORTH | 400
SPEN | SPENNYMOOR | 400
SPEN | SPENNYMOOR | 275
SPEN | SPENNYMOOR | 132
SASA | ST ASAPH | 132
SJOW | ST JOHNS WOOD | 132
SJOW | ST JOHNS WOOD | 400
SJOW | ST JOHNS WOOD | 275
STAL | STALYBRIDGE | 400
STAL | STALYBRIDGE | 275
STAL | STALYBRIDGE | 132
STAH | STANAH | 400
STAH | STANAH | 132
STAY | STAYTHORPE | 400
STYC | STAYTHORPE C | 132
STEN | STELLA NORTH | 132
STES | STELLA SOUTH | 132
STEW | STELLA WEST | 400
STEW | STELLA WEST | 275
STSB | STOCKSBRIDGE | 400
STOB | STOKE BARDOLPH | 400
STOB | STOKE BARDOLPH | 132
SUND | SUNDON | 400
SUND | SUNDON | 132
SUTB | SUTTON BRIDGE | 400
SWAN | SWANSEA NORTH | 400
SWAN | SWANSEA NORTH | 275
SWAN | SWANSEA NORTH | 132
TAUN | TAUNTON | 400
TAUN | TAUNTON | 132
TEMP | TEMPLEBOROUGH | 275
THTO | THORNTON | 400
THOM | THORPE MARSH | 400
THOM | THORPE MARSH | 275
THUR | THURCROFT | 275
TILB | TILBURY | 400
TILB | TILBURY | 275
TILB | TILBURY | 132
TINP | TINSLEY PARK | 275
TODP | TOD POINT | 400
TODP | TOD POINT | 275
TOTT | TOTTENHAM | 275
TOTT | TOTTENHAM | 132
TOTE | TOTTENHAM EAST | 275
TOTW | TOTTENHAM WEST | 275
TRAW | TRAWSFYNYDD | 400
TRAW | TRAWSFYNYDD | 275
TRAW | TRAWSFYNYDD | 132
TREM | TREMORFA | 275
TREU | TREUDDYN TEE | 400
TYNE | TYNEMOUTH | 275
TYNE | TYNEMOUTH | 132
UPPB | UPPER BOAT | 275
UPPB | UPPER BOAT | 132
USKM | USKMOUTH | 275
USKM | USKMOUTH | 132
WALF | WALFORD | 400
WALH | WALHAM | 400
WALP | WALPOLE | 400
WALP | WALPOLE | 132
WALX | WALTHAM CROSS | 400
WALX | WALTHAM CROSS | 275
WARL | WARLEY | 275
WARL | WARLEY | 132
WASF | WASHWAY FARM | 275
WASF | WASHWAY FARM | 132
WATS | WATFORD SOUTH | 275
WATS | WATFORD SOUTH | 132
WBOL | WEST BOLDON | 275
WBUR | WEST BURTON | 400
WBUR | WEST BURTON | 132
WHAM | WEST HAM | 400
WHAM | WEST HAM | 132
WMEL | WEST MELTON | 275
WMEL | WEST MELTON | 132
WTHU | WEST THURROCK | 400
WTHU | WEST THURROCK | 275
WWEY | WEST WEYBRIDGE | 400
WWEY | WEST WEYBRIDGE | 275
WWEY | WEST WEYBRIDGE | 132
WHGA | WHITEGATE | 275
WHGA | WHITEGATE | 132
WHSO | WHITSON | 400
WHSO | WHITSON | 275
WIEN | WILLENHALL | 275
WIEN | WILLENHALL | 132
WISD | WILLESDEN | 400
WISD | WILLESDEN | 275
WISD | WILLESDEN | 132
WILL | WILLINGTON | 132
WILE | WILLINGTON EAST | 400
WILT | WILTON | 275
WIMB | WIMBLEDON | 400
WIMB | WIMBLEDON | 275
WIMB | WIMBLEDON | 132
WIBA | WINCOBANK | 275
WYLF | WYLFA | 400
WYLF | WYLFA | 132
WYMO | WYMONDLEY | 400

## B-1-1d
B.1.1d - OFTO Index of Substation Codes
Site Code | Site Name
BEAT | BEATRICE ONSHORE
BEIW | BEATRICE OFFSHORE
BOSO | BARROW ONSHORE
BOSW | BARROW OFFSHORE
BBWO | BURBO BANK EXTENSION ONSHORE
BBWW | BURBO BANK EXTENSION OFFSHORE
BRST | BURSTALL
CLTO | CLACTON
DOGB | DOGGER BANK ONSHORE
DUDW | DUDGEON OFFSHORE
DUDO | DUDGEON ONSHORE
EAAW | EAST ANGLIA OFFSHORE
FOFW | FIRTH OF FORTH ONSHORE
FOFO | FIRTH OF FORTH OFFSHORE
GANW | GALLOPER NORTH OFFSHORE
GALO | GALLOPER ONSHORE
GGON | GREATER GABBARD ONSHORE
GREG | GREATER GABBARD OFFSHORE
GUNS | GUNFLEET SANDS OFFSHORE
GWAW | GWYNT-Y-MOR OFFSHORE A
GWBW | GWYNT-Y-MOR OFFSHORE B
GWYO | GWYNT-Y-MOR ONSHORE
HOWA | HORNSEA P1 220KV ONSHORE
HOWW | HORNSEA OFFSHORE
HOWR | HORNSEA P1 220KV REACTOR SUBSTATION
HUMO | HUMBER GATEWAY ONSHORE
HUMW | HUMBER GATEWAY OFFSHORE
INCW | INCH CAPE OFFSHORE
INCO | INCH CAPE ONSHORE
LINO | LINCS ONSHORE
LINS | LINCS OFFSHORE
LONO | LONDON ARRAY ONSHORE
LOAW | LONDON ARRAY OFFSHORE
MOWE | MORAY EAST OFFSHORE
MORF | MORAY EAST ONSHORE
NNGO | NEART NA GAOITHE ONSHORE
NNGW | NEART NA GAOITHE OFFSHORE
ORMO | ORMONDE ONSHORE
ORMW | ORMONDE OFFSHORE
RACO | RACE BANK ONSHORE
RACW | RACE BANK OFFSHORE
RAMW | RAMPION OFFSHORE
RORE | ROBIN RIGG EAST ONSHORE
RORW | ROBIN RIGG WEST ONSHORE
RREW | ROBIN RIGG EAST OFFSHORE
RRWW | ROBIN RIGG WEST OFFSHORE
SALL | SALLE
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2
THAW | THANET WIND ONSHORE
THOW | THANET WIND OFFSHORE
TKNO | TRITON KNOLL ONSHORE
TKNE | TRITON KNOLL EAST OFFSHORE
TKNW | TRITON KNOLL WEST OFFSHORE
TWNE | TWINEHAM ONSHORE
WAAO | WALNEY 1 ONSHORE
WAAW | WALNEY 1 OFFSHORE
WABO | WALNEY 2 ONSHORE
WABW | WALNEY 2 OFFSHORE
WACW | WALNEY 3 OFFSHORE
WADW | WALNEY 4 OFFSHORE
WOWE | WALNEY EXTENSION
WDSO | WEST OF DUDDON SANDS ONSHORE
WDSW | WEST OF DUDDON SANDS OFFSHORE
WERO | WESTERMOST ROUGH ONSHORE
WERW | WESTERMOST ROUGH OFFSHORE

## B-2-1a
B.2.1a - SHE Transmission Circuits for 2020/21
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABBA1- | DYCE1J | 0 | 7.8 | Cable | 0.1092 | 1.2324 | 10.14 | 173 | 158 | 158 | 158
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.2199 | 132 | 123 | 106 | 123
ABNE1R | AMUL1G | 28.099 | 0.001 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
ABNE1R | ABNE1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ACHR1R | INVE1J | 21.17 | 0 | OHL | 3.002 | 4.9754 | 1.035 | 99 | 92 | 79 | 92
ACHR1R | PORA1R | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
AIGA1Q | KIOR1Q | 2.8 | 0.12 | Composite | 0.264 | 0.594 | 0.66 | 126 | 117 | 101 | 117
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
AMUL1E | BUMU1R | 17.8 | 0 | OHL | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
ANSU1- | INVE1K | 11.13 | 0 | OHL | 1.578 | 2.615 | 0.544 | 99 | 92 | 79 | 92
ANSU1- | PORA1Q | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99 | 92 | 79 | 92
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123
ARBR1R | DENS1R | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123
ARDK1- | INVE1J | 9 | 0 | OHL | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123
ARDK1- | SLOY1T | 10 | 0 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 99 | 92 | 79 | 92
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 126 | 117 | 101 | 117
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136
BEAU1J | BEAU1R | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 465 | 445 | 415 | 445
BEAU1J | BEAU1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU1K | KIOR1Q | 1.24 | 0.06 | Composite | 0.13 | 0.29 | 0.06 | 126 | 117 | 101 | 117
BEAU1K | BEAU1S | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 465 | 445 | 415 | 445
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123
BEAU1N | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU1N | BEAU1K | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136
BEAU1P | BEAU1L | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1Q | BEAU1M | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1R | INNE1Q | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1S | INNE1R | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1T | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU2J | FASN2- | 24.29 | 1.01 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU2J | BEAU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU4- | FAUG4- | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BEIN11 | CEAN1Q | 0.87 | 0 | OHL | 0.099 | 0.205 | 0.042 | 254 | 247 | 237 | 247
BEIN11 | MILW1S | 2.8 | 0 | OHL | 0.319 | 0.66 | 0.135 | 254 | 247 | 237 | 247
BERB2Q | KNOC2J | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
BHLA11 | GLEN1Q | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 230 | 217 | 217 | 217
BIHI1Q | CHAR1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
BIHI1Q | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
BIHI1Q | COUA1Q | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
BIHI1R | CHAR1- | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
BIHI1R | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
BIHI1R | COUA1R | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
BLHI1J | KEIT1K | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.171 | 5.295 | 1.286 | 241 | 230 | 210 | 230
BLHI1J | BLHI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI1K | KEIT1J | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.171 | 5.297 | 1.318 | 241 | 230 | 210 | 230
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.044 | 13.793 | 580 | 546 | 546 | 546
BLHI2J | BERB2Q | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2J | BLHI2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.0456 | 14.286 | 580 | 546 | 546 | 546
BLHI2K | CAIN2- | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2L | KINT2J | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2M | PEHERSV1 | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BLHI4- | BLHI4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 1272 | 1272 | 1272 | 1272
BLHI4- | BEAT4- | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
BOAG1L | TOMT1K | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 227 | 200 | 200 | 200
BOAG1M | TOMT1J | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 255 | 255 | 242 | 250
BOAG1P | GLFA1- | 24.82 | 0 | OHL | 2.5189 | 5.7753 | 1.228 | 126 | 117 | 101 | 117
BOAG1Q | BOAG1L | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209
BOAG1Q | BOAG1P | 0 | 8.4 | Cable | 0.0558 | 1.271 | 11.48 | 227 | 209 | 209 | 209
BOAG1R | BOAG1M | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209
BONB2J | BRCW2K | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BONB4- | TUMM4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670
BRCW2J | TUMM2K | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
BRCW2J | BRCW2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104
BREC1Q | BREC1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.12 | 0.27 | 0.06 | 126 | 117 | 101 | 117
BROR1Q | DUBE1Q | 38.8 | 0 | OHL | 3.94 | 9.01 | 1.91 | 126 | 117 | 101 | 117
BROR1Q | LOCB1K | 22.12 | 0 | OHL | 2.2511 | 5.1536 | 1.096 | 126 | 117 | 101 | 117
BUMU1Q | CHAR1- | 42.2 | 0 | OHL | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
BUMU1Q | BUMU1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880
CASS1Q | LAIR1Q | 28 | 0 | OHL | 2.84 | 6.75 | 1.33 | 126 | 117 | 101 | 117
CHAR1- | CHAR1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 229 | 211 | 183 | 211
CHAR1S | GLAG1Q | 1.4 | 0.91 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 126 | 126 | 126
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 1.4 | 0.91 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 126 | 126 | 126
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117
CLAC1Q | SLOY1K | 14.2 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
CLAY1Q | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLAY1R | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1R | CLUN1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 126 | 117 | 101 | 117
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 126 | 117 | 101 | 117
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7002 | 2.8782 | 0.778 | 241 | 230 | 210 | 230
COGA1C | FARI1J | 0 | 4.11 | Cable | 0.065 | 0.334 | 6.245 | 220 | 209 | 209 | 209
CONN1C | STRW1C | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 241 | 230 | 210 | 230
CONN1J | CONN1C | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN2J | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 702 | 665 | 599 | 665
CONN2J | LOCB2J | 76.07 | 0.27 | Composite | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446
CORI1J | CORI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 132 | 123 | 106 | 123
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 132 | 123 | 106 | 123
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 145 | 131 | 116 | 131
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 145 | 131 | 116 | 131
CRSS1J | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | PORA1Q | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
CRSS1R | PORA1R | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 126 | 117 | 101 | 117
DAAS2- | KNOC2K | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160
DENS1R | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DOUN2- | THUS2J | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DUBE1Q | MYBS1R | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 117 | 101 | 117
DUCC1J | ORRI1S | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
DUCC1K | ORRI1T | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
DUDH1Q | GLAG1Q | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92
DUNM1- | DUNM1C | 6 | 0 | OHL | 0.3023 | 1.2424 | 0.336 | 241 | 230 | 210 | 230
DUNM1C | FARI1K | 0 | 4.07 | Cable | 0.064 | 0.28 | 6.175 | 210 | 196 | 196 | 196
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1Q | DYCE1J | 1.93 | 0 | OHL | 0.0978 | 0.4332 | 0.33 | 241 | 230 | 210 | 230
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.5187 | 2.2781 | 0.525 | 145 | 131 | 116 | 131
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.6335 | 2.2972 | 0.519 | 145 | 131 | 116 | 131
ELGI1L | NAIR1Q | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1M | NAIR1R | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1Q | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1Q | ELGI1L | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1R | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1R | ELGI1M | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1J | WHIB1A | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
ERRO1J | ERRO1A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1J | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ERRO1J | ERRO1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1K | WHIB1B | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
ERRO1K | ERRO1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123
FAAR1Q | TOMT1K | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FAAR1R | TOMT1J | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FARI2J | KNOC2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
FARI2K | KNOC2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
FASN2- | FAUG2J | 24.38 | 1.02 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.01 | 0.012 | 0.002 | 126 | 117 | 101 | 117
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127
FAUG1- | FAUG1P | 0 | 0.59 | Cable | 0.01 | 0.0602 | 0.868 | 202 | 202 | 202 | 202
FAUG1- | FAUG1M | 0 | 0.29 | Cable | 0.01 | 0.0225 | 0.486 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 0 | 0.2 | Cable | 0.01 | 0.0157 | 0.339 | 220 | 209 | 209 | 209
FAUG1- | LAGG1Q | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 254 | 247 | 237 | 247
FAUG1- | LAGG1R | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 254 | 247 | 237 | 247
FAUG1M | LOCL1Q | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1P | LOCL1S | 8.66 | 0 | OHL | 0.4365 | 1.7942 | 0.485 | 241 | 230 | 210 | 230
FAUG2J | FAUG2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FAUG4- | MELG4J | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.7089 | 1.0659 | 0.265 | 99 | 92 | 79 | 92
FERO1S | INVE1J | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
FERO1S | TAYN1R | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92
FETT2P | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 880 | 760 | 880
FETT2P | TEAL2K | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
FETT2P | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2Q | KINB2J | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT2Q | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 885 | 760 | 885
FETT2Q | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FIDD1Q | FOGG1R | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD1Q | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FIDD1R | FIDD1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 126 | 117 | 101 | 117
FOGG1Q | KINT1- | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 98 | 90 | 98
FOGG1Q | TARL1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
FOGG1R | TARL1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
FOYE2- | FOYE2J | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
FOYE2- | FARI2J | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FOYE2- | FARI2K | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LUND1- | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FYRI1J | FYRI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FYRI2J | LOCB2K | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
GARB1Q | SLOY1K | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
GARB1R | SLOY1J | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GARB1S | SLOY1J | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
GARB1T | SLOY1K | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.546 | 1.132 | 0.232 | 254 | 247 | 237 | 247
GLFA1- | KEIT1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117
GLRB2- | TEAL2K | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 702 | 665 | 599 | 665
GRIF1S | WHIB1H | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
GRIF1T | WHIB1G | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 132 | 123 | 106 | 123
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 132 | 123 | 106 | 123
INGA1Q | LOCL1Q | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.1051 | 0.3818 | 6.326 | 146 | 142 | 142 | 142
INNE1J | INNE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INNE1K | INNE1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1042 | 0.3784 | 6.27 | 146 | 142 | 142 | 142
INNE1Q | NAIR1Q | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1R | NAIR1R | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 142 | 128 | 142
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 150 | 142 | 128 | 142
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 150 | 142 | 128 | 142
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 117 | 101 | 117
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 126 | 117 | 101 | 117
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 126 | 117 | 101 | 117
INRU1S | PEHE1- | 0 | 3 | Cable | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181
INVE1J | INVE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
INVE1K | SLOY1J | 22.6 | 0 | OHL | 2.29 | 5.25 | 1.11 | 126 | 117 | 101 | 117
INVR1- | KIIN1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
INVR1- | KIIN1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
INVR1- | SLOY1K | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126
KEIT1J | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123
KEIT1K | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123
KEIT3- | KEIT3A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 126 | 117 | 101 | 117
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99 | 92 | 79 | 92
KILC1Q | TAYN1Q | 7.52 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILO1- | LUND1- | 15.2 | 0 | OHL | 1.054 | 3.441 | 0.775 | 126 | 117 | 101 | 117
KINB2K | TEAL2J | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.0154 | 0.354 | 148 | 140 | 140 | 140
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.0148 | 0.341 | 148 | 140 | 140 | 140
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT1- | KINT1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT2J | TEAL2J | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 952 | 952 | 925 | 952
KINT2J | KINT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT2K | TEAL2K | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | PEHE2Q | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KNOC2J | KNOC2N | 0 | 0.51 | Cable | 0.0012 | 0.0157 | 3.005 | 850 | 793 | 793 | 793
KNOC2J | KNOC2P | 0 | 0.17 | Cable | 0.0004 | 0.0053 | 1.006 | 850 | 793 | 793 | 793
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.042 | 8.36 | 930 | 900 | 900 | 900
KNOC2J | KNOC2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KNOC2M | KNOC2K | 0 | 1.29 | Cable | 0.01 | 0.037 | 7.336 | 930 | 900 | 900 | 900
KNOC2N | TOMT2K | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765
KNOC2P | TOMT2J | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.648 | 1.344 | 0.276 | 254 | 247 | 237 | 247
LAIR1Q | SHIN1- | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 126 | 117 | 101 | 117
LOCB1J | MYBS1Q | 81.61 | 0 | OHL | 8.2998 | 19.0008 | 4.028 | 126 | 117 | 101 | 117
LOCB1J | SHIN1- | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 117 | 101 | 117
LOCB1J | LOCB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB1K | SHIN1- | 12.18 | 0 | OHL | 1.239 | 2.8365 | 0.604 | 126 | 117 | 101 | 117
LOCB2J | LOCB2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB2K | STRB2- | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 702 | 665 | 599 | 665
LOCL1S | QUOI1Q | 18.3 | 0 | OHL | 0.9219 | 3.7893 | 1.025 | 241 | 230 | 210 | 230
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
MELG1J | STRL1- | 0 | 10 | Cable | 0.0752 | 0.806 | 18.176 | 317 | 281 | 281 | 281
MELG1J | MELG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MELG4J | TUMM4- | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670
MELG4J | MELG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1R | MILC1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1R | MILC1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 229 | 211 | 183 | 211
MILC1S | MILC1V | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 229 | 211 | 183 | 211
MILW1S | MILW1Q | 1.3 | 0 | OHL | 0.065 | 0.2691 | 0.073 | 241 | 230 | 210 | 230
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1S | SPIT1M | 4.5 | 0 | OHL | 0.104 | 1.002 | 0.237 | 463 | 444 | 415 | 444
MYBS1T | SPIT1K | 4.5 | 0 | OHL | 0.104 | 1.002 | 0.237 | 463 | 444 | 415 | 444
MYBS3M | MYBS3N | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1R | ORRI1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
PEHE2- | PEHE2S | 0 | 1 | Cable | 0.01 | 0.033 | 14.21 | 776 | 776 | 776 | 776
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE2- | PEHE2Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2- | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2R | PEHERSV2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2T | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.032 | 13.51 | 776 | 776 | 776 | 776
PEHE2U | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2V | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2W | PEHEMEC1 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHEMEC1 | PEHEMEC2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC1 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC2 | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC3 | PEHEMEC4 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC4 | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC5 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHERSV1 | PEHEMEC4 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHERSV2 | PEHEMEC2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS1Q | PERS1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS2Q | PERS2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 150 | 142 | 128 | 142
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
SFEG1Q | SFEG1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1R | SFEG1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1S | SFEG1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1J | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1K | SFER1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1K | SFER1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1L | SFEM1Q | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1L | SFEG1Q | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 150 | 142 | 128 | 142
SFER1M | SFEM1R | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1M | SFEG1R | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 150 | 142 | 128 | 142
SHET1J | SHET1R | 0 | 1 | Cable | 0.01 | 0.11 | 0 | 720 | 720 | 720 | 720
SLOY1J | SLOY1N | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 117 | 101 | 117
SLOY1J | SLOY1P | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 117 | 101 | 117
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123
SLOY1J | SLOY1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SLOY1K | SLOY1L | 1.29 | 0.01 | Composite | 0.13 | 0.3 | 0.06 | 126 | 117 | 101 | 117
SLOY1K | SLOY1M | 1.29 | 0.01 | Composite | 0.13 | 0.3 | 0.06 | 126 | 117 | 101 | 117
SPIT2J | THUS2J | 12.1 | 0 | OHL | 0.0605 | 0.6655 | 2.577 | 965 | 925 | 865 | 925
SPIT2J | SPIT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SPIT2K | SPIT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 960 | 960 | 960 | 960
SPIT2K | THUS2K | 12.1 | 0 | OHL | 0.0605 | 0.6655 | 2.577 | 965 | 925 | 865 | 925
STRW12 | STRW1C | 0 | 0.35 | Cable | 0.01 | 0.0631 | 0.48 | 200 | 178 | 178 | 178
TEAL2J | WFIB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2J | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
THUS1J | THUS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TOMT1K | TOMT1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TOMT2K | TOMT2J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TUMM2J | TUMM2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147

## B-2-1b
B.2.1b - SPT Circuits for 2020/21
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0422 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0422 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.716 | 3.8726 | 0.9882 | 171 | 152 | 152 | 152
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.72 | 3.8943 | 0.9935 | 171 | 152 | 152 | 152
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.9576 | 4.8683 | 1.5223 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.9569 | 4.8645 | 1.4665 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430
BLAH1- | GLGL1Q | 12.6 | 0.435 | Composite | 0.4848 | 2.7278 | 1.2134 | 134 | 123 | 123 | 123
BLAH1- | GLGL1R | 12.6 | 0.44 | Composite | 0.485 | 2.7281 | 1.2195 | 134 | 123 | 123 | 123
BLAH3A | WNDR3- | 0 | 5 | Cable | 1.1433 | 4.2657 | 0.6455 | 51 | 51 | 51 | 51
BLAH3B | PENC3- | 0 | 1.5 | Cable | 0.0267 | 0.1431 | 1.7503 | 40 | 38 | 38 | 38
BLAH3B | PENC3- | 0 | 1.5 | Cable | 0.0267 | 0.1431 | 1.7503 | 40 | 38 | 38 | 38
BLCW1- | MARG1- | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 166 | 159 | 147 | 159
BLCW3- | BLCW3A | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 31 | 31 | 31 | 31
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2976 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 4.04 | 0.3 | parallelComposite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234
BONN1- | STIR1S | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BPGR3- | BPGR3R | 0 | 0 | Series Reactor | 0.2755 | 25 | 0 | 96 | 96 | 96 | 96
BPGR3- | BPGR3R | 0 | 0 | SeriesReactor | 0.2755 | 25 | 0 | 96 | 96 | 96 | 96
BRAE1G | BRAP1- | 0 | 2.1 | Cable | 0.0418 | 0.1748 | 3.0232 | 250 | 250 | 250 | 250
BRAE1G | GOVA1R | 0 | 4.03 | Cable | 0.175 | 0.2752 | 7.984 | 125 | 113 | 110 | 113
BRAE1P | GOVA1Q | 0 | 4.03 | Cable | 0.175 | 0.2752 | 7.984 | 125 | 113 | 110 | 113
BRAE1P | PAIS1Q | 4.52 | 0 | OHL | 0.0885 | 0.8142 | 0.2833 | 268 | 268 | 268 | 268
BRAP1- | ERSK1Q | 3.17 | 5.4 | Composite | 0.4479 | 1.0975 | 12.4447 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4955 | 1.1727 | 12.9637 | 102 | 79 | 79 | 79
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 750 | 690 | 630 | 690
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.2337 | 0.5239 | 0.1455 | 132 | 123 | 106 | 123
CAFA5- | CAFA5R | 0 | 0 | SeriesReactor | 0.3333 | 21.1544 | 0 | 30 | 30 | 30 | 30
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CHAP1- | DUMF1- | 26.9 | 0.125 | Composite | 1.065 | 6.0817 | 1.5576 | 171 | 155 | 155 | 155
CHAP1- | DUMF1- | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | ECCF1J | 6.569 | 0.23 | Composite | 0.6009 | 1.515 | 0.651 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.185 | Composite | 0.6 | 1.5109 | 0.5882 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.1811 | 3.0837 | 0.9878 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 1.1797 | 3.0784 | 0.9358 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.019 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 9.17 | 0 | OHL | 0.0207 | 0.3232 | 2.9288 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.22 | 0 | OHL | 0.1223 | 1.9018 | 17.3649 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.0445 | 0.1289 | 23.8486 | 291 | 245 | 245 | 245
COAL1- | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180
COAL1- | LINM1R | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 134 | 123 | 123 | 123
COAL1- | MIDM1- | 0 | 14.47 | Cable | 0.4086 | 0.9392 | 17.8217 | 158 | 146 | 146 | 146
COAL1A | GAWH1Q | 0 | 10.5 | Cable | 0.1651 | 0.9039 | 17.3003 | 241 | 241 | 241 | 241
COAL1A | LINM1Q | 5.774 | 3.2 | Composite | 0.2502 | 1.6499 | 3.0753 | 134 | 123 | 123 | 123
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0779 | 0.756 | 5.0669 | 1120 | 1060 | 990 | 1060
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0405 | 0.3931 | 2.6346 | 1120 | 1060 | 990 | 1060
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.1427 | 1.4132 | 35.4499 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.1427 | 1.413 | 35.4444 | 1090 | 1030 | 925 | 1030
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4027 | 1.0118 | 0.5089 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8423 | 2.157 | 1.0619 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.29 | 0.08 | Composite | 0.0057 | 0.0515 | 0.4645 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.0058 | 0.0522 | 0.3778 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.6159 | 4.1178 | 1.1779 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4941 | 2.6834 | 0.984 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.4943 | 2.6844 | 0.9979 | 229 | 211 | 183 | 211
CRUA2Q | CRUA2S | 0 | 0.4 | Cable | 0.0001 | 0.0103 | 2.0513 | 283 | 283 | 283 | 283
CRUA2R | CRUA2T | 0 | 0.4 | Cable | 0.0001 | 0.0103 | 2.0513 | 283 | 283 | 283 | 283
CRUA2S | DALL2- | 8.16 | 0 | OHL | 0.0345 | 0.3333 | 2.2691 | 570 | 570 | 570 | 570
CRUA2T | DALL2- | 8.16 | 0 | OHL | 0.0345 | 0.3333 | 2.2691 | 570 | 570 | 570 | 570
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0184 | 0.2733 | 8.179 | 2470 | 2350 | 2150 | 2350
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 935 | 785 | 785 | 785
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.2634 | 0.9635 | 5.1125 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2627 | 0.9613 | 5.0951 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.18 | 0 | OHL | 0.1915 | 1.7367 | 11.6698 | 1090 | 1030 | 920 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1372 | 1324 | 1228 | 1324
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1372 | 1324 | 1228 | 1324
CURR2- | KINC2- | 55.82 | 0 | OHL | 0.2534 | 2.2983 | 15.4435 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0174 | 0.1034 | 6.0397 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0172 | 0.1027 | 5.9404 | 120 | 120 | 120 | 120
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 957 | 881 | 762 | 881
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 123 | 106 | 123
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.6915 | 1.7146 | 0.386 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.6806 | 1.6869 | 0.38 | 107 | 107 | 101 | 107
DEVM4- | HUNE4- | 50.471 | 0.167 | Composite | 0.0909 | 0.9984 | 33.1263 | 1316 | 1067 | 1067 | 1067
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.047 | 0.5444 | 17.7745 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1T | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 164 | 130 | 130 | 130
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8944 | 7.5329 | 1.5454 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNB1Q | DUNB1S | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 90 | 90 | 90 | 90
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNB1R | DUNB1T | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 90 | 90 | 90 | 90
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131
DUNE3- | KEIH3- | 0 | 3.5 | Cable | 3.9126 | 3.7846 | 0.2381 | 17 | 17 | 17 | 17
DUNE3- | POGB3- | 0 | 3.809 | Cable | 4.4534 | 3.8498 | 0.3049 | 21 | 20 | 20 | 20
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | SeriesCapacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | ECCL4D | 0 | 0 | SeriesCapacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 46.23 | 0 | OHL | 0.1043 | 1.6221 | 14.8036 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 0 | 2.79 | Cable | 0.12 | 0.559 | 0.684 | 229 | 211 | 183 | 211
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1517 | 0.8271 | 0.4569 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 0 | 2.79 | Cable | 0.121 | 0.561 | 0.73 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1523 | 0.8319 | 0.5267 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1155 | 1.2673 | 38.8356 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0414 | 0.4544 | 13.9258 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
EWEH1Q | GRNA1- | 15.7 | 0.12 | Composite | 1.1828 | 3.4623 | 0.9844 | 131 | 131 | 131 | 131
EWEH3- | CRDY3B | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 45 | 39 | 39 | 39
EWEH3- | CRDY3A | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 45 | 39 | 39 | 39
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2473 | 2349 | 2148 | 2349
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1- | 15.313 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123
GARB1R | STLE1- | 26.909 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.03 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.061 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.082 | 0.33 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.74 | 0.162 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105
GLGL3- | SNQR3- | 0 | 2.3 | Cable | 0.6364 | 2.0111 | 0.2699 | 30 | 30 | 30 | 30
GLGL3- | WHLL3- | 0 | 1.2 | Cable | 0.332 | 1.5811 | 0.1408 | 30 | 30 | 30 | 30
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.6969 | 1.6787 | 0.405 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 171 | 171 | 171 | 171
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 130 | 125 | 110 | 125
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 154 | 141 | 154
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.359 | 0.7999 | 0.7252 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 875 | 875 | 760 | 875
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 955 | 885 | 760 | 885
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068 | 0.6175 | 4.1318 | 1050 | 965 | 880 | 965
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.017 | 0.047 | 0.066 | 1000 | 1000 | 1000 | 1000
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.012 | 0.035 | 0.049 | 1000 | 1000 | 1000 | 1000
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 5.0386 | 12.9578 | 2.7219 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.4329 | 1.1257 | 0.2305 | 132 | 123 | 106 | 123
GRNA4- | GRNA4C | 0 | 0 | SeriesCapacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2210 | 2130 | 1980 | 2130
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.304 | 1.375 | 21.563 | 184 | 184 | 184 | 184
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 4.5812 | 11.7697 | 2.4781 | 132 | 123 | 106 | 123
HELE1- | WIYH1- | 24.799 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1448 | 1448 | 1448 | 1448
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1448 | 1448 | 1448 | 1448
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUER4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | NEIL4Q | 35.617 | 0.167 | Composite | 0.0716 | 0.7351 | 23.4602 | 1320 | 1070 | 1070 | 1070
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.6051 | 3.1847 | 6.8629 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4354 | 2.2253 | 6.6009 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4909 | 2.779 | 0.643 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3218 | 1.8217 | 0.4215 | 151 | 151 | 151 | 151
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1120 | 1060 | 990 | 1060
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1822 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240
KAIM3- | KAIM3A | 0 | 0 | SeriesReactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120
KAIM3- | KAIM3B | 0 | 0 | SeriesReactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120
KEOO1- | NECU1R | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 133 | 123 | 106 | 123
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6165 | 100 | 80 | 60 | 80
KIER1R | WIYH1- | 2.089 | 4.095 | Composite | 0.3833 | 0.9197 | 7.4586 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0175 | 0.154 | 2.0858 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0178 | 0.1548 | 2.24 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 760 | 620 | 620 | 620
KINB2K | KINC2- | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 910 | 885 | 760 | 885
KINC2- | LOAN2Q | 4.28 | 0.31 | Composite | 0.0192 | 0.1938 | 4.4396 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 4.28 | 0.17 | Composite | 0.0189 | 0.1899 | 2.8506 | 765 | 620 | 620 | 620
LAMB2- | LAMB2T | 0 | 0.001 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0182 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0192 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1050 | 965 | 880 | 965
LAMB2T | LOAN2- | 53.67 | 0.225 | Composite | 0.1948 | 2.0808 | 18.1931 | 795 | 620 | 620 | 620
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1120 | 1060 | 990 | 1060
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | SeriesReactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | SeriesReactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | MOSM2L | 26.196 | 0.194 | Composite | 0.1186 | 1.0915 | 8.8674 | 760 | 620 | 620 | 620
LOAN2- | WFIE2- | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 760 | 620 | 620 | 620
MAHI3- | TRLO3- | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 40 | 30 | 30 | 30
MARG1- | NECU1Q | 34.35 | 0.9 | Composite | 1.1487 | 6.9058 | 3.4859 | 241 | 230 | 210 | 230
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1567 | 3.0101 | 0.9444 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29
MOFF4- | MOFF4C | 0 | 0 | SeriesCapacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | MOSM2L | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 955 | 885 | 760 | 885
MOSM2- | MOSM2T | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 955 | 885 | 760 | 885
MOSM2T | WFIE2- | 2.943 | 0 | OHL | 0.0133 | 0.1221 | 0.8005 | 955 | 885 | 760 | 885
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1109 | 1.0864 | 6.9028 | 957 | 881 | 764 | 881
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 1390 | 1280 | 1110 | 1280
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1344 | 1.2615 | 34.9418 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0233 | 0.2267 | 6.8043 | 2000 | 1920 | 1790 | 1920
STIR1S | WFIE1A | 37.6 | 5.816 | Composite | 3.218 | 9.4053 | 8.7867 | 162 | 154 | 141 | 154
STLE1- | WIYH1- | 12.892 | 0.291 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 950 | 885 | 760 | 885
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WIYH2- | WIYH2R | 0 | 0 | SeriesReactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
B.2.1c - NGET Circuits for 2020/21
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.041714 | 0.50275 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 1389 | 1284 | 1108 | 1284
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.041714 | 0.50275 | 15.6941 | 1389 | 1284 | 1108 | 1284
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629
ABTH21 | UPPB22 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882
ABTH22 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879
ABTH22 | UPPB21 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 595
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911
AMEM4A | IVER4A | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2009 | 1911 | 1746 | 1911
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933
AMEM4B | IVER4B | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933
AXMI41 | CHIC4A | 39.5 | 0 | OHL | 0.0429 | 0.687 | 26.0389 | 2779 | 2568 | 2217 | 2568
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2771 | 2568 | 2217 | 2568
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115
BAGB21 | SWAN21 | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431
BARK21 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK21 | REBR21 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081
BARK22 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK22 | REBR22 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0155 | 0.191 | 5.6429 | 2009 | 1911 | 1746 | 1911
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0156 | 0.1915 | 10.4541 | 2009 | 1909 | 1710 | 1909
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.0692 | 0.7576 | 7.8243 | 944 | 882 | 762 | 835
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 694
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0689 | 0.7539 | 6.2735 | 762 | 762 | 662 | 662
BEDD23 | WIMB2A | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 806
BEDD4A | ROWD42 | 0 | 11.676 | Cable | 0.0079 | 0.138 | 127.4459 | 1309 | 1309 | 1309 | 1309
BEDD4B | ROWD41 | 0 | 11.676 | Cable | 0.0105 | 0.0957 | 210.168 | 1415 | 1415 | 1223 | 1223
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 56.939 | 0.631 | Composite | 0.2314 | 2.4189 | 22.4142 | 819 | 819 | 638 | 638
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1236 | 1176 | 1074 | 1176
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1236 | 1176 | 1074 | 1176
BLYT41 | HEDD4A | 26.636 | 0.121 | Composite | 0.042634 | 0.514 | 18.0175 | 2199 | 2092 | 1911 | 2092
BLYT41 | HEDD4B | 26.636 | 0.49 | Composite | 0.042929 | 0.51943 | 24.1171 | 2199 | 2092 | 1911 | 2092
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOTW41 | FAWL41 | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 1109 | 901 | 901
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0451 | 0.8316 | 32.2964 | 2779 | 2568 | 2217 | 2568
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0134 | 0.2147 | 8.1357 | 2779 | 2568 | 2217 | 2568
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.065 | 1.1398 | 43.92 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0358 | 0.5745 | 21.7727 | 2779 | 2568 | 2217 | 2568
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1204 | 1115 | 1018 | 1115
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 2470 | 2350 | 2146 | 2350
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0768 | 0.8127 | 5.4608 | 948 | 882 | 753 | 753
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.762 | 850 | 850 | 675 | 675
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1093 | 1031 | 925 | 1031
BRIM2B | TOTT24 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1085 | 1031 | 925 | 1031
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1093 | 1031 | 925 | 1031
BRIM2C | TOTT22 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT23 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499
BRIN21 | NORL22 | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2568 | 2217 | 2568
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.078851 | 0.94951 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.078851 | 0.94951 | 29.6914 | 2199 | 2092 | 1911 | 2092
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0224 | 0.3591 | 13.6101 | 2779 | 2568 | 2217 | 2568
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3102 | 2935 | 2765 | 2935
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2910 | 2238 | 2515
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3102 | 2935 | 2765 | 2935
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3102 | 2935 | 2765 | 2935
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762
BUSH21 | WIEN21 | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 681
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 635
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 635
BUST41 | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568
BUST41 | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119
CANT41 | RICH41 | 25 | 0 | OHL | 0.039925 | 0.48076 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 25 | 0 | OHL | 0.039925 | 0.48076 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | SELL4A | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2750 | 2750 | 2420 | 2750
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2570 | 2570 | 2220 | 2570
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665
CARR41 | DAIN42 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9776 | 3102 | 3048 | 2958 | 3048
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO41 | 56.9 | 0 | OHL | 0.09878 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR4A | DAIN42 | 2.063 | 0 | OHL | 0.0035 | 0.0404 | 1.2165 | 1507 | 1507 | 1507 | 1507
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1553 | 1553 | 1553 | 1553
CELL41 | DAIN42 | 53.412 | 2.31 | parallel Composite | 0.0847 | 1.031 | 76.931 | 2508 | 2508 | 2300 | 2300
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.071884 | 0.8656 | 27.0675 | 2175 | 2069 | 1890 | 2069
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073001 | 0.87907 | 27.4871 | 2175 | 2069 | 1890 | 2069
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0495 | 0.6067 | 18.9879 | 3102 | 3048 | 2958 | 3048
CHIC41 | EXET41 | 75.92 | 0 | OHL | 0.0824 | 1.3205 | 50.0469 | 2779 | 2568 | 2217 | 2568
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829
CHIC4A | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHUE4A | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591
CHUE4A | WTHU4D | 2.4188 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048
CHUE4B | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591
CHUE4B | WTHU4C | 2.5806 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048
CILF2A | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF2B | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136
CLEH41 | CANT41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048
CLEH41 | KEMS41 | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048
CONQ41 | CAPE4A | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CONQ41 | CAPE4B | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389
CONQ41 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 3075 | 2876 | 2663 | 2876
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 2423 | 2327 | 2167 | 2327
COTT41 | GREN41 | 129.478 | 0 | OHL | 0.2293 | 2.5548 | 75.7188 | 2009 | 1911 | 1746 | 1911
COTT41 | KEAD41 | 34.628 | 0 | OHL | 0.0595 | 0.6858 | 20.1792 | 2212 | 2125 | 1979 | 2125
COTT41 | KEAD41 | 34.479 | 0 | OHL | 0.0592 | 0.6828 | 20.0931 | 2212 | 2125 | 1979 | 2125
COTT41 | RYHA42 | 76.891 | 0 | OHL | 0.0834 | 1.3374 | 50.6872 | 2779 | 2569 | 2217 | 2569
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0506 | 0.5544 | 21.5604 | 2212 | 2125 | 1979 | 2052
COTT42 | RYHA41 | 76.816 | 0 | OHL | 0.0834 | 1.3361 | 50.638 | 2779 | 2569 | 2217 | 2569
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0105 | 0.1321 | 3.9942 | 3326 | 3160 | 2971 | 3160
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0619 | 1.1211 | 9.699 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.007 | 0.113 | 4.2822 | 2771 | 2568 | 2217 | 2568
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0125 | 0.2001 | 7.5827 | 2779 | 2568 | 2217 | 2568
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0394 | 0.6314 | 23.9301 | 2779 | 2568 | 2217 | 2568
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0537 | 0.9095 | 34.8191 | 2779 | 2568 | 2217 | 2568
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 979
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879
CREB2A | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB2B | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 2771 | 2771 | 2663 | 2771
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO41 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO42 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CULJ41 | DIDC41 | 4.898 | 0 | OHL | 0.0053 | 0.0852 | 3.2288 | 2771 | 2568 | 2217 | 2568
DAIN41 | CARR41 | 2.545 | 0 | OHL | 0.0043 | 0.0496 | 1.5076 | 2169 | 2084 | 1940 | 2084
DAIN41 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0541 | 0.6511 | 66.8001 | 2397 | 2300 | 2144 | 2300
DAIN42 | CONQ41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
DINO41 | PENT41 | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9578 | 1623 | 1623 | 1571 | 1571
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1604 | 1604 | 1557 | 1557
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2009 | 1911 | 1746 | 1911
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1769 | 1320 | 1320 | 1320
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2089 | 2089 | 1878 | 1878
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2771 | 2568 | 2217 | 2568
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505
DRAX42 | THTO42 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2779 | 2568 | 2217 | 2568
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3066 | 2830 | 2418 | 2830
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 2779 | 2568 | 2217 | 2568
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2217 | 2217 | 1801 | 1801
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2779 | 2568 | 2217 | 2568
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST21 | MILH21 | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430
ELST21 | MILH21 | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST4A | ELST41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0749 | 0.6969 | 20.0233 | 1590 | 1500 | 1346 | 1500
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0747 | 0.6944 | 19.9464 | 1590 | 1500 | 1346 | 1500
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911
FAWL41 | LOVE41 | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 1109 | 901 | 901
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4527 | 1967 | 1874 | 1712 | 1874
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1967 | 1875 | 1712 | 1875
FENW4A | DRAX41 | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823
FERR2A | FERR23 | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115
FERR2B | FERR22 | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 981
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 480 | 480 | 330 | 330
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512
FIDF21 | FIDF23 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF22 | FIDF24 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF22 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF23 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF24 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 2212 | 2125 | 1979 | 2125
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 2212 | 2125 | 1979 | 2125
FOUR21 | HARK21 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3102 | 2935 | 2633 | 2813
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390
GRAI41 | TILB41 | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2003 | 2003 | 1939 | 2003
GREN41 | STAY41 | 101.832 | 0 | OHL | 0.1852 | 2.0259 | 59.0223 | 2514 | 2439 | 2314 | 2439
GREN41 | SUND41 | 39.75 | 0 | OHL | 0.0723 | 0.7909 | 23.0368 | 2009 | 1911 | 1746 | 1911
GREN41 | SUND42 | 39.955 | 0 | OHL | 0.0727 | 0.795 | 23.1553 | 2009 | 1911 | 1746 | 1911
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GRSA21 | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119
GRSA21 | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1000
GRSA21 | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 9999 | 9999 | 9999
GRSA21 | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 9999 | 9999 | 9999
GRSB21 | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRSB21 | LACK2C | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRSB21 | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 9999 | 9999 | 9999
GRSB21 | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 180 | 9999 | 9999 | 9999
GWYN4A | BODE41 | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | BODE41 | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HACK2A | TOTT2B | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK2B | TOTT2A | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HAKB1- | HARK13 | 0 | 1 | OHL | 0.7047 | 2.0317 | 0.451 | 132 | 123 | 106 | 123
HAMH1B | LEMR11 | 0 | 1 | Cable | 0.016 | 0.098 | 1.942 | 229 | 229 | 229 | 229
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1362 | 1285 | 1202 | 1285
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1206 | 1.5777 | 77.2944 | 2009 | 1912 | 1746 | 1912
HARK13 | JUNV1- | 0 | 1 | OHL | 1.194 | 2.729 | 0.743 | 132 | 123 | 106 | 123
HARK21 | HARK21 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 1.4546 | 0 | 1524 | 1524 | 1524 | 1524
HARK21 | HARK21 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.31736 | 0 | 1524 | 1524 | 1524 | 1524
HARK21 | HARK21 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -1.4546 | 0 | 1524 | 1524 | 1524 | 1524
HARK21 | HARK21 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.31736 | 0 | 1524 | 1524 | 1524 | 1524
HARK22 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HARK41 | HAKB4- | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2169 | 2084 | 1940 | 2084
HARK41 | HAKB4B | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2170 | 2084 | 1941 | 2084
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1204 | 1115 | 1018 | 1115
HATL21 | HARM21 | 13.983 | 0 | OHL | 0.0531 | 0.5772 | 3.9082 | 1093 | 1031 | 925 | 1031
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0332 | 0.335 | 2.0887 | 1382 | 1279 | 1157 | 1279
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1148 | 1086 | 1021 | 1086
HATL21 | WBOL21 | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1093 | 1031 | 926 | 1031
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 801
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1093 | 1031 | 925 | 1031
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2545 | 2421 | 2211 | 2421
HEDD4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
HEDD4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
HEDD4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
HEDD4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664
HEYS41 | HAMB4A | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299
HEYS41 | HAMB4B | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3111 | 3326
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3326 | 3160 | 2971 | 3160
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HIBU41 | HACK41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0254 | 0.2958 | 13.2571 | 2212 | 2125 | 1979 | 2125
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056
HINP21 | BRWA2A | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 767 | 620 | 620
HINP21 | BRWA2B | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 762 | 762 | 619 | 619
HINP41 | MELK41 | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | MELK41 | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | TAUN41 | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1979 | 2125
HINP41 | TAUN42 | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1979 | 2125
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771
HURS21 | LITT2A | 5.164 | 2.613 | Composite | 0.0288 | 0.2786 | 27.8693 | 864 | 864 | 824 | 855
HURS21 | LITT2B | 5.14 | 2.659 | Composite | 0.0288 | 0.2786 | 28.329 | 864 | 861 | 824 | 861
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 882 | 704 | 784
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 882 | 704 | 784
HUTT41 | HUTT41 | 0 | 0 | Thyristor Controlled Series Capacitor | 0 | -0.51142 | 0 | 2770 | 2770 | 2770 | 2770
HUTT41 | HUTT41 | 0 | 0 | Thyristor Controlled Series Capacitor | 0 | -0.51142 | 0 | 2770 | 2770 | 2770 | 2770
HUTT41 | HUTT41 | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2470 | 2470 | 2470 | 2470
HUTT41 | HUTT41 | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2470 | 2470 | 2470 | 2470
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424
INCE11 | CAPE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 3.2486 | 258 | 258 | 240 | 240
INCE11 | CAPE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 3.2416 | 240 | 240 | 240 | 240
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284
IROA11 | OLDS12 | 0 | 1 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372
IROA12 | OLDS12 | 0 | 1 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524
IROA21 | MELK2B | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750
IRON41 | LEGA4A | 62.073 | 0 | OHL | 0.09913 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.024161 | 0.29094 | 9.0977 | 2397 | 2302 | 2144 | 2302
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 841 | 841 | 665 | 665
JORD21 | NORL2B | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381
KEAD41 | GART4B | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3180 | 3000 | 2692 | 3000
KEAD42 | FENW4A | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0308 | 0.4944 | 18.7376 | 2779 | 2568 | 2217 | 2568
KEAD43 | GART4A | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3180 | 3000 | 2692 | 3000
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0307 | 0.4916 | 18.6331 | 3326 | 3160 | 2971 | 3160
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 830 | 830 | 665 | 665
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084
KEMS41 | CANT41 | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0623 | 0.726 | 23.0007 | 3102 | 2935 | 2765 | 2935
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0617 | 0.7176 | 22.7061 | 1927 | 1833 | 1674 | 1833
KENG41 | SJOW41 | 0 | 6 | Cable | 0.0027 | 0.0473 | 43.6608 | 1327 | 1298 | 1200 | 1298
KENG41 | SJOW41 | 0 | 6 | Cable | 0.0027 | 0.0473 | 43.6608 | 1327 | 1298 | 1200 | 1298
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 1327 | 1298 | 1200 | 1298
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 1327 | 1298 | 1200 | 1298
KENG41 | WLSD41 | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1730 | 1600 | 1730
KENG41 | WLSD42 | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1730 | 1600 | 1730
KIBY22 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY22 | WASF21 | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KILL41 | KILL41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2750 | 2750 | 2750 | 2750
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720
KINO41 | KINO41 | 0 | 0 | Series Reactor | 0.0027 | 2 | 0 | 2002 | 2002 | 2002 | 2002
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
KINO41 | TILB41 | 15.4784 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2003 | 2003 | 1948 | 1948
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619
KITW21 | OCKH21 | 13.738 | 0.222 | Composite | 0.0525 | 0.5743 | 6.2479 | 772 | 772 | 619 | 619
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 551 | 512 | 442 | 512
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 551 | 512 | 442 | 512
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1148 | 1086 | 1021 | 1086
LACK41 | NORT41 | 22.443 | 0.25 | Composite | 0.0404 | 0.4515 | 17.428 | 1831 | 1739 | 1588 | 1739
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213
LAND41 | LAGA41 | 21.224 | 0 | OHL | 0.033893 | 0.40814 | 12.7628 | 2423 | 2327 | 2168 | 2327
LAND42 | LAGA41 | 21.355 | 0 | OHL | 0.034102 | 0.41077 | 12.8376 | 1389 | 1284 | 1108 | 1284
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA4B | SHRE4A | 46.944 | 0 | OHL | 0.074969 | 0.90276 | 28.2295 | 2002 | 2002 | 2002 | 2002
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIS4A | BRFO41 | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2779 | 2569 | 2217 | 2569
LISD21 | LISD21 | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 740 | 740 | 740
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 1390 | 1284 | 1109 | 1284
LITT41 | WTHU41 | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LITT41 | WTHU42 | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LOFI4A | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOFI4B | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568
MACC41 | STAL42 | 31.196 | 0 | OHL | 0.062 | 0.617 | 18.1761 | 1710 | 1627 | 1488 | 1627
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3160 | 2971 | 3160
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 682 | 629 | 538 | 629
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2518 | 2395 | 2188 | 2395
NECT4A | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3299 | 3078 | 3299
NECT4B | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3258 | 3060 | 3258
NECT4B | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381
NEEP4A | STSB4A | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293
OCKH21 | WIEN21 | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 599
OCKH2A | WIEN21 | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0375 | 0.3474 | 2.2265 | 1093 | 1031 | 925 | 1031
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2771 | 2568 | 2217 | 2568
PADI41 | PEWO41 | 37.608 | 0 | OHL | 0.055602 | 0.70488 | 23.1779 | 2169 | 2084 | 1940 | 2084
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2779 | 2568 | 2217 | 2568
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2779 | 2569 | 2217 | 2569
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2771 | 2771 | 2692 | 2771
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 217.727 | 5.468 | parallel Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0633 | 0.9555 | 131.5497 | 1135 | 1135 | 992 | 992
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PERH11 | WYLF11 | 19.94 | 0 | OHL | 0.475 | 4.232 | 1.0947 | 330 | 330 | 300 | 300
PERH11 | WYLF11 | 19.94 | 0 | OHL | 0.475 | 4.232 | 1.0947 | 333 | 307 | 304 | 331
PEWO21 | PEWO21 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.225 | 0 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.55537 | 0 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 10.978 | 0 | OHL | 0.0415 | -0.22479 | 3.0984 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 11.236 | 0 | OHL | 0.0258 | -0.55537 | 3.8519 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 0 | 10.239 | Cable | 0.0173 | 0.225 | 60.8154 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 0 | 9.518 | Cable | 0.0228 | 0.55537 | 86.3283 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.22479 | 0 | 1524 | 1524 | 1524 | 1524
PEWO21 | PEWO21 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.55537 | 0 | 1524 | 1524 | 1524 | 1524
PEWO21 | WASF21 | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO22 | WASF22 | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO41 | HAMB4A | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2189
PEWO41 | HAMB4B | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2189
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 439 | 439 | 381 | 381
PUDM41 | CITR41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136
QUER4A | PEWO41 | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
QUER4B | PEWO41 | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2757 | 2147 | 2056 | 1904 | 2056
RATS41 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2147 | 2056 | 1904 | 2056
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 2212 | 2125 | 1979 | 2125
REBR21 | TOTT21 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127
REBR22 | TOTT22 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 419 | 419 | 404 | 404
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 665
RYEH41 | RYEH4A | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2780 | 2780 | 2780 | 2780
RYEH41 | RYEH4B | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569
RYEH41 | WALX4A | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2779 | 2568 | 2217 | 2568
RYEH4A | WALX4B | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2779 | 2568 | 2217 | 2568
RYHA42 | EASO4B | 58.95 | 0 | OHL | 0.064 | 1.0253 | 38.8593 | 2780 | 2780 | 2780 | 2780
RYHA4B | EASO4A | 58.769 | 0 | OHL | 0.0638 | 1.0222 | 38.7404 | 2779 | 2569 | 2217 | 2569
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1749 | 1664 | 1520 | 1664
SALH41 | SALH41 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.125 | 0 | 2217 | 2217 | 2217 | 2217
SALH41 | SALH41 | 21.134 | 2 | Composite | 0.0276 | -0.125 | 0 | 2217 | 2217 | 2217 | 2217
SALH41 | SALH41 | 21.134 | 2 | Composite | 0.0276 | 0.125 | 0 | 2217 | 2217 | 2217 | 2217
SALH41 | SALH41 | 83.839 | 0 | OHL | 0.1132 | -0.125 | 0 | 2217 | 2217 | 2217 | 2217
SALH41 | SALH41 | 83.839 | 0 | OHL | 0.1132 | 0.125 | 0 | 2217 | 2217 | 2217 | 2217
SALH41 | SALH41 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.125 | 0 | 2217 | 2217 | 2217 | 2217
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424
SELL41 | CANT41 | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048
SELL41 | SELL41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860
SELL41 | SELL4A | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4A | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL41 | SELL4B | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3326 | 3326 | 3326
SELL4B | SELL41 | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL4E | SELL41 | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL4F | DUNG41 | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830
SELL4F | SELL41 | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SHRE4B | SHRE4A | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 2170 | 9999 | 9999 | 9999
SING41 | KINO41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748
SING41 | NFLE41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748
SIZE41 | BRFO41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
SIZE41 | LEIS4A | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2779 | 2569 | 2217 | 2569
SJOW21 | TOTT23 | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 868 | 835 | 682 | 762
SJOW21 | TOTT24 | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 868 | 835 | 682 | 762
SJOW41 | HIBU41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
SJOW41 | HIBU41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2350 | 2146 | 2350
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2350 | 2146 | 2350
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SSHI21 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1236 | 1176 | 1065 | 1176
SSHI21 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1093 | 1031 | 925 | 1031
STAH4A | HAMB4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
STAH4B | HAMB4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
STAL42 | STSB4A | 28.555 | 5.057 | Composite | 0.0343 | 0.5535 | 95.384 | 1649 | 1528 | 1399 | 1528
STAL4A | THOM41 | 71.245 | 4.978 | Composite | 0.0791 | 1.2942 | 122.4093 | 1330 | 1171 | 1001 | 1171
STEN11 | STES11 | 0 | 1 | Cable | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 181
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3048 | 2935 | 2692 | 2935
SUTB41 | WALP41 | 3.85 | 0 | OHL | 0.008 | 0.0773 | 2.2055 | 1340 | 1340 | 1150 | 1340
SWAN41 | PEMB41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2779 | 2568 | 2217 | 2568
SWAN41 | PEMB41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2568 | 2217 | 2568
SWAN41 | RHIG41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 421 | 421 | 381 | 381
THOM21 | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698
THOM41 | BRIN41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395
THUR2A | THUR21 | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1120 | 1060 | 990 | 1060
TILB41 | TILB4B | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
TILB4A | TILB41 | 0.0581 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641
TREU4B | CONQ41 | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1093 | 1031 | 912 | 1031
USKM12 | USKM11 | 0 | 0 | Series Reactor | 0.25 | 20 | 0 | 2002 | 2002 | 2002 | 2002
USKM21 | USKM22 | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956
USKM22 | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641
USKM2B | USKM21 | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629
WBUR42 | WBUR41 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 40 | 40 | 40 | 40
WHAM4A | PUDM41 | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 2780 | 9999 | 9999 | 9999
WISD21 | EALI21 | 0 | 8.075 | Cable | 0.002 | 0.0229 | 10.13 | 665 | 665 | 665 | 665
WTHU41 | WTHU41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WTHU42 | WTHU42 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400

## B-2-1d
B.2.1d - OFTO Transmission Circuits for 2020/21
OFTO | Station | Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
Hornsea One Limited | Hornsea 1 Wind Farm | KILL41 | HOWA41 | 0 | 0.52 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | KILL41 | HOWA41 | 0 | 0.5 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | HOWA21 | HOWR2A | 0 | 105.103 | Cable | 0.68384 | 3.2701 | 292.1283 | 380 | 220
|  | HOWR2A | HOWW21 | 0 | 66.2 | Cable | 0.4924 | 1.6413 | 175.1469 | 380 | 220
|  | HOWA21 | HOWR2A | 0 | 104.903 | Cable | 0.69628 | 3.1955 | 303.8973 | 380 | 220
|  | HOWR2A | HOWW22 | 0 | 72.2 | Cable | 0.47736 | 1.7155 | 203.0972 | 380 | 220
|  | HOWW21 | HOWW22 | 0 | 12.3 | Cable | 0.15756 | 0.30496 | 34.5997 | 364 | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | HUMW11 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 122 | 132
|  | HUMO12 | HUMW12 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 122 | 132
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | BOSW11 | 0 | 29.45 | Cable | 1.634 | 2.451 | 25.197 | 106 | 132
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BODE41 | BBWO41 | 0 | 0.6 | Cable | 0.0012606 | 0.0090575 | 7.0016 | 277.8 | 400
|  | BBWO21 | BBWW21 | 0 | 34.622 | Cable | 0.38748 | 0.93347 | 103.7511 | 286.2 | 220
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDO11 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
|  | DUDW12 | DUDO11 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
East Anglia One Limited | East Anglia Offshore Wind Farm | BRFO41 | BRST41 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRFO41 | BRST42 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRST21 | EAAW21 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
|  | BRST22 | EAAW22 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO12 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO11 | GANW11 | 0 | 45.8 | Cable | 1.23 | 2.8301 | 58.38 | 180.6 | 132
|  | GALO12 | GANW12 | 0 | 45.8 | Cable | 1.23 | 2.8301 | 58.38 | 180.6 | 132
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO11 | ORMW11 | 0 | 44.347 | Cable | 0.7323 | 3.104 | 46.68 | 158 | 132
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SALL11 | 0 | 44.8 | Cable | 0.010219 | 0.036202 | 0.55272 | 178 | 132
|  | SSBW11 | SALL12 | 0 | 42.9 | Cable | 0.009695 | 0.034676 | 0.53192 | 178 | 132
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO21 | TKNW21 | 0 | 107.8 | Cable | 0.57 | 3.15 | 313 | 427 | 220
|  | BICF41 | TKNO41 | 0 | 2.01 | Cable | 0.004 | 0.02 | 18.6 | 505 | 400
|  | BICF41 | TKNO41 | 0 | 1.78 | Cable | 0.004 | 0.02 | 16.5 | 505 | 400
Diamond Transmission Partners Walney Extension Limited | Walney Extension Wind Farm | WOWE21 | WACW21 | 0 | 80.1 | Cable | 0.9432 | 1.99 | 251.59 | 340 | 220
|  | WADW21 | WACW21 | 0 | 22.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 220
|  | WOWE22 | WADW21 | 0 | 66 | Cable | 0.9432 | 1.99 | 251.59 | 340 | 220
|  | MIDL41 | WOWE41 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
|  | MIDL41 | WOWE42 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
WoDS Transmission plc | West of Duddon Sands | WDSW11 | WDSO11 | 0 | 42.08 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | WDSW12 | WDSO12 | 0 | 42.08 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | HEYS41 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
|  | HEYS41 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERW11 | WERO11 | 0 | 25.8335 | Cable | 0.29494 | 1.4823 | 45.7125 | 140 | 150
|  | WERO21 | HEDO21 | 0 | 0.368 | Cable | 0.003209 | 0.012987 | 1.3567 | 256.7809 | 275
|  | WERO22 | HEDO21 | 0 | 0.329 | Cable | 0.0024822 | 0.010046 | 1.0494 | 256.7809 | 275
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GGON11 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GGON12 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GGON13 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GALO11 | GGON11 | 0 | 17 | Cable | 0.36 | 0.0107 | 0.205 | 150 | 132
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS11 | 0 | 12.789 | Cable | 0.3254 | 0.8061 | 15.5518 | 158 | 132
Blue Transmission London Array Limited | London Array Offshore Wind Farm | CLEH41 | LONO4A | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
|  | CLEH41 | LONO4B | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
|  | LONO11 | LOAW11 | 0 | 53.798 | Cable | 1.5829 | 2.9755 | 73.1044 | 167 | 150
|  | LONO12 | LOAW12 | 0 | 53.848 | Cable | 1.5837 | 2.9766 | 73.1539 | 167 | 150
|  | LONO13 | LOAW13 | 0 | 52.657 | Cable | 1.5488 | 2.9125 | 71.5816 | 167 | 150
|  | LONO14 | LOAW14 | 0 | 52.682 | Cable | 1.5492 | 2.9137 | 71.6099 | 167 | 150
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | GWYO11 | GWBW11 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 150 | 132
|  | GWYO11 | GWBW12 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 150 | 132
|  | GWYO12 | GWAW11 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 150 | 132
|  | GWYO12 | GWAW12 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 150 | 132
TC Beatrice OFTO Limited | Beatrice Wind Farm | BEIW21 | BEIW22 | 0 | 1.315 | Cable | 0.033 | 0.014 | 4.119 | 321 | 220
|  | BEIW21 | BEAT21 | 0 | 89.2 | Cable | 0.8221 | 2.262 | 291.8746 | 321 | 220
|  | BEIW22 | BEAT22 | 0 | 89.2 | Cable | 0.8221 | 2.262 | 291.8746 | 321 | 220
|  | BEAT4A | BLHI41 | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 400
|  | BEAT4B | BLHI42 | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 400
TC Lincs OFTO Limited | Lincolnshire Offshore Windfarm | LINS11 | LINO11 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
|  | LINS12 | LINO12 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
Diamond Transmission Partners RB Limited | Race Bank Offshore | RACW21 | RACO21 | 0 | 82.5 | Cable | 0.487 | 2.1112 | 2.4784 | 302 | 220
|  | RACW22 | RACO22 | 0 | 83.5 | Cable | 0.4934 | 2.136 | 2.5075 | 302 | 220
|  | WALP41 | RACO41 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | WALP41 | RACO42 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | RACW21 | RACW22 | 0 | 6.7 | Cable | 0.0433 | 0.1661 | 19.4582 | 302 | 220
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RREW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
| Robin Rigg West Offshore Wind Farm | RORW11 | RRWW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | BOLN41 | TWNE41 | 0 | 0.6 | Cable | 0.0028 | 0.0042 | 4.4179 | 411 | 400
|  | BOLN41 | TWNE42 | 0 | 0.76 | Cable | 0.0036 | 0.0053 | 5.6068 | 411 | 400
|  | TWNE11 | RAMW11 | 0 | 42.35 | Cable | 0.7285 | 1.9531 | 75.95 | 210 | 150
|  | TWNE12 | RAMW12 | 0 | 42.29 | Cable | 0.7275 | 1.9502 | 75.84 | 210 | 150
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | THOW11 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
|  | THAW12 | THOW12 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO11 | WAAO1A | 0 | 2.9 | Cable | 0.076045 | 0.13688 | 3.5539 | 192 | 132
|  | WAAO1A | WAAW11 | 0 | 43.7 | Cable | 1.2943 | 2.3298 | 55.0577 | 164 | 132
Blue Transmission Walney 2 OFTO | Walney 2 Offshore Wind Farm | WABO11 | WABO1A | 0 | 5.23 | Cable | 0.15 | 0.27 | 6.384 | 192 | 132
|  | WABO1A | WABW11 | 0 | 44.13 | Cable | 1.266 | 2.279 | 53.869 | 164 | 132

## B-2-2a
B.2.2a - SHE Transmission Circuit Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BEAU1J | BEAU1R | 2021 | Change | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1K | BEAU1S | 2021 | Change | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1R | INNE1Q | 2021 | Change | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BEAU1S | INNE1R | 2021 | Change | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BLHI2L | KINT2J | 2021 | Remove | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2L | ROTI2J | 2021 | Addition | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI2M | PEHERSV1 | 2021 | Remove | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BLHI2M | ROTI2K | 2021 | Addition | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
CLAC1Q | SLOY1F | 2021 | Change | 13 | 0 | OHL | 1.3183 | 3.0212 | 0.641 | 132 | 123 | 106 | 123
DOUN1- | LIMK1- | 2021 | Addition | 0 | 4 | Cable | 0.364 | 0.864 | 0.216 | 126 | 117 | 101 | 117
DUNM1- | DUNM1T | 2021 | Change | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 241 | 230 | 210 | 230
DUNM1T | ABED1- | 2021 | Addition | 5 | 0 | OHL | 0.25 | 1.035 | 0.28 | 163 | 152 | 131 | 152
DUNM1T | DUNM1C | 2021 | Change | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 241 | 230 | 210 | 230
ELGI1L | NAIR1Q | 2021 | Change | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1M | NAIR1R | 2021 | Change | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1Q | ELGI1L | 2021 | Change | 0 | 1.8 | Cable | 0.0354 | 0.052 | 1.41 | 251 | 252 | 252 | 252
ELGI1Q | KEIT1- | 2021 | Change | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ELGI1R | ELGI1M | 2021 | Change | 0 | 1.8 | Cable | 0.0354 | 0.052 | 1.41 | 251 | 252 | 252 | 252
ELGI1R | KEIT1- | 2021 | Change | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
INNE1Q | NAIR1Q | 2021 | Remove | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1Q | SLKB1J | 2021 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INNE1R | NAIR1R | 2021 | Remove | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1R | SLKB1K | 2021 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INVE1J | ACHR1R | 2021 | Change | 21.17 | 0 | OHL | 0.3387 | 3.9588 | 1.291 | 739 | 710 | 662 | 710
INVE1K | ANSU1- | 2021 | Change | 11.13 | 0 | OHL | 0.1781 | 2.0813 | 0.679 | 739 | 710 | 662 | 710
INVE1K | SLOY1E | 2021 | Change | 21.4 | 0 | OHL | 2.1684 | 4.9712 | 1.051 | 126 | 117 | 101 | 117
INVR1- | INVR1A | 2021 | Change | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126
INVR1- | INVR1B | 2021 | Change | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126
INVR1A | INVR1C | 2021 | Change | 0 | 4.5 | Cable | 0.0306 | 0.6975 | 6.3 | 213 | 190 | 190 | 190
INVR1B | INVR1D | 2021 | Change | 0 | 4.5 | Cable | 0.0306 | 0.6975 | 6.3 | 213 | 190 | 190 | 190
KIIN1- | INVR1C | 2021 | Change | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126
KIIN1- | INVR1D | 2021 | Change | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126
KINT2K | PEHE2Q | 2021 | Remove | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
NAIR1Q | SLKB1L | 2021 | Addition | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
NAIR1R | SLKB1M | 2021 | Addition | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
PEHE2Q | NEDE2K | 2021 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHERSV1 | NEDE2J | 2021 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PORA1Q | ANSU1- | 2021 | Change | 24.27 | 0 | OHL | 0.3883 | 4.5385 | 1.481 | 739 | 710 | 662 | 710
PORA1R | ACHR1R | 2021 | Remove | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
PORA1R | PORA1T | 2021 | Addition | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1S | ACHR1R | 2021 | Addition | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
PORA1S | PORA1U | 2021 | Addition | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
ROTI2J | KINT2J | 2021 | Addition | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2021 | Addition | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
ROTI2K | KINT2K | 2021 | Addition | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2K | NEDE2K | 2021 | Addition | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
SLKB1J | SLKB1L | 2021 | Addition | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLKB1K | SLKB1M | 2021 | Addition | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLOY11 | SLOY1E | 2021 | Addition | 0 | 1.2 | Cable | 0.0082 | 0.186 | 1.68 | 213 | 190 | 190 | 190
SLOY12 | SLOY1A | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY12 | SLOY1B | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY12 | SLOY1F | 2021 | Change | 0 | 1.2 | Cable | 0.0082 | 0.186 | 1.68 | 213 | 190 | 190 | 190
SLOY1J | SLOY1C | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY1J | SLOY1D | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY1L | SLOY1B | 2021 | Change | 0.49 | 0.01 | Composite | 0.05 | 0.1154 | 0.023 | 126 | 117 | 101 | 117
SLOY1M | SLOY1A | 2021 | Change | 0.49 | 0.01 | Composite | 0.05 | 0.1154 | 0.023 | 126 | 117 | 101 | 117
SLOY1N | SLOY1C | 2021 | Change | 0.6 | 0 | OHL | 0.0643 | 0.1457 | 0.03 | 126 | 117 | 101 | 117
SLOY1P | SLOY1D | 2021 | Change | 0.6 | 0 | OHL | 0.0643 | 0.1457 | 0.03 | 126 | 117 | 101 | 117
TOMT1K | GLKO1- | 2021 | Addition | 0 | 3 | Cable | 0.4 | 0.67 | 0.16 | 99 | 92 | 79 | 92
ABNE1Q | ABNE1S | 2022 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ABNE1Q | CHAR1- | 2022 | Change | 24.5 | 0 | OHL | 1.0449 | 5.3324 | 1.297 | 183 | 160 | 149 | 160
ABNE1R | ABNE1T | 2022 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ABNE1R | AMUL1G | 2022 | Change | 28.097 | 0 | OHL | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
ABNE1S | ABNE1T | 2022 | Addition | 1 | 0 | OHL | 0.0002 | 0.0004 | 0 | 132 | 123 | 106 | 123
ABNE1S | CHAR1- | 2022 | Addition | 24.5 | 0 | OHL | 1.0449 | 5.3324 | 1.297 | 183 | 160 | 149 | 160
ABNE1T | BUMU1Q | 2022 | Addition | 17 | 0 | OHL | 1.7991 | 4.0929 | 0.881 | 132 | 123 | 106 | 123
BUMU1Q | CHAR1- | 2022 | Remove | 42.2 | 0 | OHL | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
FAUG1P | LOCL1S | 2022 | Remove | 8.66 | 0 | OHL | 0.4365 | 1.7942 | 0.485 | 241 | 230 | 210 | 230
FAUG1P | MILS1Q | 2022 | Addition | 5.41 | 0 | OHL | 0.2727 | 1.1208 | 0.303 | 241 | 230 | 210 | 230
LAIR1Q | LAIR1R | 2022 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LAIR1Q | LOCB1J | 2022 | Addition | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
LAIR1Q | SHIN1- | 2022 | Remove | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 126 | 117 | 101 | 117
LAIR1R | LOCB1K | 2022 | Addition | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
LOCL1S | MILS1Q | 2022 | Addition | 3.25 | 0 | OHL | 0.1638 | 0.6734 | 0.182 | 203 | 193 | 176 | 193
ACHR1R | PORA1R | 2024 | Addition | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ACHR1R | PORA1S | 2024 | Remove | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ALYT2A | ALYT2B | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | FETT2P | 2024 | Addition | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2024 | Addition | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2024 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2024 | Addition | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2024 | Addition | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2024 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
BEWF1- | ENEI1- | 2024 | Addition | 0 | 34 | Cable | 1.716 | 7.04 | 1.904 | 162 | 154 | 141 | 154
BEWF1- | SHET1R | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLEX1- | FAUG1J | 2024 | Addition | 20 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 241 | 230 | 210 | 230
BLHI2L | ROTI2J | 2024 | Remove | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2K | 2024 | Remove | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI4- | BLHI4A | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI4- | ROTI4J | 2024 | Addition | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BLHI4- | ROTI4K | 2024 | Addition | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BRCW2J | KINA2K | 2024 | Addition | 59.8 | 0 | OHL | 0.1638 | 2.4224 | 17.089 | 1910 | 1830 | 1710 | 1830
BRCW2J | TUMM2K | 2024 | Remove | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
CDWE1- | DORE12 | 2024 | Addition | 0 | 0.1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CHAR1S | LYND1Q | 2024 | Change | 1.9 | 0 | OHL | 0.081 | 0.4135 | 0.101 | 183 | 160 | 149 | 160
CHAR1T | LYND1R | 2024 | Change | 1.9 | 0 | OHL | 0.081 | 0.4135 | 0.101 | 183 | 160 | 149 | 160
CRDH1J | CRDH1K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRDH1J | INVE1K | 2024 | Addition | 10.12 | 0 | OHL | 1.4405 | 2.3785 | 0.496 | 99 | 92 | 79 | 92
CRDH1J | KILC1Q | 2024 | Addition | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92
CRDH1K | FERO1S | 2024 | Addition | 5.02 | 0 | OHL | 0.7118 | 1.1784 | 0.246 | 99 | 92 | 79 | 92
CRDH2J | CRDH2K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRDH2J | DALB2A | 2024 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
CRDH2K | DALB2B | 2024 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
CREA1- | LAIR1R | 2024 | Addition | 22 | 0 | OHL | 2.234 | 5.128 | 1.083 | 132 | 123 | 106 | 123
CRSS1Q | PORA1Q | 2024 | Change | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
CRSS1R | PORA1R | 2024 | Change | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
FERO1S | INVE1J | 2024 | Remove | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
FETT2P | KINT2K | 2024 | Change | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT2P | TEAL2K | 2024 | Remove | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
FETT2Q | KINB2J | 2024 | Remove | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT2Q | KINT2K | 2024 | Change | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
GARB1Q | SLOY1K | 2024 | Change | 14.23 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1R | SLOY1J | 2024 | Change | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1S | SLOY1J | 2024 | Change | 14.23 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1T | SLOY1K | 2024 | Change | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GILB1J | GILB1K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GILB1J | GILB1L | 2024 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1J | PENF1- | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GILB1K | GILB1M | 2024 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1L | THUS1L | 2024 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
GILB1M | THUS1M | 2024 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
GLRB2- | TEAL2K | 2024 | Change | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
INRU1Q | PEHE1- | 2024 | Change | 6.7 | 0 | OHL | 1.1457 | 4.1339 | 0.208 | 224 | 177 | 158 | 177
INRU1R | PEHE1- | 2024 | Change | 6.7 | 0 | OHL | 1.1457 | 4.1339 | 0.208 | 224 | 177 | 158 | 177
INVE1K | KILC1Q | 2024 | Remove | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
KINA2J | KINA2K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINA2J | TUMM2K | 2024 | Addition | 3 | 0 | OHL | 0.0082 | 0.1216 | 0.858 | 1910 | 1830 | 1710 | 1830
KINB2K | TEAL2J | 2024 | Remove | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
KINT2J | ROTI2J | 2024 | Remove | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
KINT2J | TEAL2A | 2024 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2J | TEAL2J | 2024 | Remove | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | ROTI2K | 2024 | Remove | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
KINT2K | TEAL2B | 2024 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | TEAL2K | 2024 | Remove | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT4J | ROTI4J | 2024 | Addition | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920
KINT4K | ROTI4K | 2024 | Addition | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920
LOCB1J | SHIN1- | 2024 | Change | 12.19 | 0 | OHL | 1.3897 | 2.7671 | 0.61 | 255 | 247 | 237 | 247
LOCB1K | SHIN1- | 2024 | Change | 12.19 | 0 | OHL | 1.3897 | 2.7671 | 0.61 | 255 | 247 | 237 | 247
MORF2- | NEDE2K | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MORF4- | NEDE4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MSHL1- | SHET1J | 2024 | Addition | 0 | 20 | Cable | 1.82 | 4.32 | 1.08 | 126 | 119 | 108 | 119
NEDE2J | NEDE2K | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NEDE2J | PEHERSV1 | 2024 | Remove | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
NEDE2J | ROTI2J | 2024 | Remove | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
NEDE2K | PEHE2Q | 2024 | Remove | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
NEDE2K | ROTI2K | 2024 | Remove | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
NEDE4J | NEDE4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NEDE4J | PEHE4J | 2024 | Addition | 22.39 | 0 | OHL | 0.0448 | 0.4322 | 13.173 | 2000 | 1920 | 1790 | 1920
NEDE4J | ROTI4J | 2024 | Addition | 24.97 | 0 | OHL | 0.0499 | 0.4819 | 14.689 | 2000 | 1920 | 1790 | 1920
NEDE4K | PEHE4K | 2024 | Addition | 22.39 | 0 | OHL | 0.0448 | 0.4322 | 13.173 | 2000 | 1920 | 1790 | 1920
NEDE4K | ROTI4K | 2024 | Addition | 24.97 | 0 | OHL | 0.0499 | 0.4819 | 14.689 | 2000 | 1920 | 1790 | 1920
NESQ30 | THUS3- | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE4J | PEHE4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA1Q | PORA1U | 2024 | Addition | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1S | PORA1U | 2024 | Remove | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
ROTI2J | ROTI2K | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ROTI4J | ROTI4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SHET1J | SHET1M | 2024 | Addition | 0 | 1 | Cable | 0.1 | 1 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2B | TEAL2K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2J | TEAL2A | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2J | WFIB2- | 2024 | Change | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
THUS1J | THUS1L | 2024 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
THUS1K | THUS1M | 2024 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
ACHR1R | INVE1J | 2026 | Remove | 21.17 | 0 | OHL | 0.3387 | 3.9588 | 1.291 | 739 | 710 | 662 | 710
ACHR1R | PORA1R | 2026 | Remove | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ACHR2- | CRDH2J | 2026 | Addition | 31.37 | 0 | OHL | 0.1255 | 1.2861 | 8.846 | 1290 | 1240 | 1160 | 1240
ACHR2- | PORA2M | 2026 | Addition | 14.23 | 0 | OHL | 0.0569 | 0.5834 | 4.013 | 1290 | 1240 | 1160 | 1240
ALYT2A | ALYT2B | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | FETT2P | 2026 | Remove | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2026 | Remove | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2026 | Remove | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2K | 2026 | Addition | 16.2 | 0 | OHL | 0.0685 | 0.6615 | 4.505 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2026 | Remove | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2026 | Remove | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2J | 2026 | Addition | 16.2 | 0 | OHL | 0.0685 | 0.6615 | 4.505 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2026 | Remove | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT4J | ALYT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT4J | FETT4Q | 2026 | Addition | 67.35 | 0 | OHL | 0.1347 | 1.2999 | 39.622 | 2000 | 1920 | 1790 | 1920
ALYT4J | KINB4J | 2026 | Addition | 69.98 | 0 | OHL | 0.14 | 1.3506 | 41.169 | 2000 | 1920 | 1790 | 1920
ALYT4K | FETT4R | 2026 | Addition | 67.35 | 0 | OHL | 0.1347 | 1.2999 | 39.622 | 2000 | 1920 | 1790 | 1920
ALYT4K | KINB4K | 2026 | Addition | 69.98 | 0 | OHL | 0.14 | 1.3506 | 41.169 | 2000 | 1920 | 1790 | 1920
ANSU1- | INVE1K | 2026 | Remove | 11.13 | 0 | OHL | 0.1781 | 2.0813 | 0.679 | 739 | 710 | 662 | 710
ANSU1- | PORA1Q | 2026 | Remove | 24.27 | 0 | OHL | 0.3883 | 4.5385 | 1.481 | 739 | 710 | 662 | 710
ANSU2- | CRDH2K | 2026 | Addition | 21.33 | 0 | OHL | 0.0853 | 0.8745 | 6.015 | 1290 | 1240 | 1160 | 1240
ANSU2- | PORA2L | 2026 | Addition | 24.27 | 0 | OHL | 0.0971 | 0.9951 | 6.844 | 1290 | 1240 | 1160 | 1240
ARMO1J | DUGR1Q | 2026 | Change | 14 | 0 | OHL | 0.7058 | 2.91 | 0.784 | 241 | 230 | 210 | 230
ARMO3- | ARMO3J | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | ARNI1J | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | ARNI1Q | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | DRUL1- | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | MUAI1- | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | STWN1- | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU4- | BEAU4R | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BERB2Q | CLGO2A | 2026 | Addition | 0 | 0.46 | Cable | 0.0026 | 0.019 | 0.126 | 935 | 880 | 790 | 880
BEWF1- | ENEI1- | 2026 | Change | 34 | 0 | OHL | 1.714 | 7.038 | 1.904 | 241 | 230 | 210 | 230
BLHI1J | ELCH1- | 2026 | Addition | 24 | 0 | OHL | 1.2 | 4.968 | 1.344 | 241 | 230 | 210 | 230
BLHI2A | CLGO2A | 2026 | Addition | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880
BLHI2B | BLHI2K | 2026 | Addition | 0 | 0 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2B | DAAS2- | 2026 | Addition | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2J | BERB2Q | 2026 | Remove | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BLHI2J | BLHI2A | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2K | DAAS2- | 2026 | Remove | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BROA1- | EDIN1- | 2026 | Addition | 46.06 | 0 | OHL | 1.089 | 9.771 | 2.539 | 448 | 430 | 398 | 430
BROA1- | LOCL1S | 2026 | Addition | 81.7 | 0 | OHL | 1.9307 | 17.3312 | 4.503 | 448 | 430 | 398 | 430
BROA1- | QUOI1Q | 2026 | Addition | 63.41 | 0 | OHL | 1.4985 | 13.4519 | 3.495 | 448 | 430 | 398 | 430
BROA1Q | EDIN1- | 2026 | Remove | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92
BROA1Q | QUOI1Q | 2026 | Remove | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92
CASS1Q | SALA1- | 2026 | Addition | 6 | 0 | OHL | 0.63 | 1.308 | 0.318 | 126 | 117 | 101 | 117
CLGO2- | DAAS2- | 2026 | Addition | 13.37 | 0 | OHL | 0.0757 | 0.5503 | 3.645 | 935 | 880 | 790 | 880
CLGO2- | KNOC2K | 2026 | Addition | 46.85 | 0 | OHL | 0.2653 | 1.9287 | 12.774 | 935 | 880 | 790 | 880
CLOI1- | CLOI11 | 2026 | Addition | 8 | 0 | OHL | 0.256 | 1.744 | 0.424 | 280 | 270 | 245 | 270
CLOI1- | MELG1K | 2026 | Addition | 0 | 0.2 | Cable | 0.0053 | 0.0306 | 0.543 | 220 | 211 | 211 | 211
CONN1D | STRW17 | 2026 | Addition | 12.12 | 0 | OHL | 0.6109 | 2.5094 | 0.679 | 241 | 230 | 210 | 230
CONN1K | CONN1D | 2026 | Addition | 0 | 0.66 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 2026 | Change | 76.34 | 0 | OHL | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CONN2K | DOUN2- | 2026 | Addition | 8.77 | 0 | OHL | 0.0526 | 0.4826 | 1.86 | 702 | 665 | 599 | 665
CONN2K | GORW2- | 2026 | Addition | 49.33 | 0 | OHL | 0.296 | 2.7134 | 10.46 | 702 | 665 | 599 | 665
CRDH1J | INVE1K | 2026 | Remove | 0 | 0 | OHL | 1.4405 | 2.3785 | 0.496 | 99 | 92 | 79 | 92
CRSS1J | CRSS1R | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | CRSS1R | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | PORA1Q | 2026 | Remove | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
CRSS1R | PORA1R | 2026 | Remove | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
CRSS1R | SHDM1- | 2026 | Addition | 10 | 0 | OHL | 0.5 | 2.07 | 0.56 | 241 | 230 | 210 | 230
CRSS2J | PORA2L | 2026 | Addition | 48.3 | 0 | OHL | 0.1932 | 1.9803 | 13.621 | 1290 | 1240 | 1160 | 1240
CRSS2K | PORA2M | 2026 | Addition | 48.3 | 0 | OHL | 0.1932 | 1.9803 | 13.621 | 1290 | 1240 | 1160 | 1240
DAAS2- | KNOC2K | 2026 | Remove | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
DOUN2- | GORW2- | 2026 | Remove | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DOUN2A | DOUN2B | 2026 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 292 | 292 | 292 | 292
DOUN2B | DOUN2C | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 294 | 294 | 294 | 294
DOUN2C | FINS2C | 2026 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 270 | 270 | 270 | 270
DOUN2D | DOUN2E | 2026 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 240 | 240 | 240 | 240
DOUN2E | DOUN2F | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 240 | 240 | 240 | 240
DOUN2F | FINS2F | 2026 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 240 | 240 | 240 | 240
DUGR1Q | EDIN1- | 2026 | Remove | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92
DUGR1Q | GLNU1- | 2026 | Addition | 8.49 | 0 | OHL | 4.5472 | 18.8256 | 5.093 | 241 | 230 | 210 | 230
EDIN1- | GLNU1- | 2026 | Addition | 0.5 | 0 | OHL | 0.0118 | 0.1061 | 0.028 | 448 | 430 | 398 | 430
FAUG1- | FAUG1M | 2026 | Remove | 0 | 0.29 | Cable | 0.01 | 0.0225 | 0.486 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 2026 | Remove | 0 | 0.2 | Cable | 0.01 | 0.0157 | 0.339 | 220 | 209 | 209 | 209
FAUG1- | FAUG1P | 2026 | Change | 0.59 | 0 | OHL | 0.0139 | 0.1252 | 0.033 | 448 | 430 | 398 | 430
FAUG1- | QUOI1Q | 2026 | Addition | 27.55 | 0 | OHL | 0.651 | 5.8445 | 1.519 | 448 | 430 | 398 | 430
FAUG1M | LOCL1Q | 2026 | Remove | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 2026 | Remove | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1P | MILS1Q | 2026 | Change | 5.41 | 0 | OHL | 0.1278 | 1.1477 | 0.298 | 448 | 430 | 398 | 430
FAUG4J | INGA4K | 2026 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940 | 1860 | 1720 | 1860
FAUG4K | INGA4J | 2026 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940 | 1860 | 1720 | 1860
FETT2P | FETT2R | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2P | KINT2K | 2026 | Remove | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT2Q | FETT2R | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2Q | KINT2K | 2026 | Remove | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT4J | FETT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4Q | FETT4J | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4Q | KINT4J | 2026 | Addition | 32.15 | 0 | OHL | 0.0643 | 0.6205 | 18.914 | 2000 | 1920 | 1790 | 1920
FETT4R | FETT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4R | KINT4K | 2026 | Addition | 32.15 | 0 | OHL | 0.0643 | 0.6205 | 18.914 | 2000 | 1920 | 1790 | 1920
FINS2A | FINS2B | 2026 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 292 | 292 | 292 | 292
FINS2B | FINS2C | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 294 | 294 | 294 | 294
FINS2D | FINS2E | 2026 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 240 | 240 | 240 | 240
FINS2E | FINS2F | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 240 | 240 | 240 | 240
FWIL1Q | INGA1J | 2026 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1Q | LOCL1Q | 2026 | Remove | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | INGA1K | 2026 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 2026 | Remove | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
GILB1K | PENF1B | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GLSH1J | MELG1J | 2026 | Addition | 0 | 0.2 | Cable | 0.0027 | 0.0153 | 0.271 | 220 | 211 | 211 | 211
INGA1J | INGA1K | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INGA1Q | INGA1K | 2026 | Addition | 0 | 2.4 | Cable | 0.1224 | 0.5376 | 0.125 | 187 | 177 | 158 | 177
INGA1Q | LOCL1Q | 2026 | Remove | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
KINT4J | KINT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCL1S | MILS1Q | 2026 | Change | 3.25 | 0 | OHL | 0.0768 | 0.6895 | 0.179 | 448 | 430 | 398 | 430
LOCL1S | QUOI1Q | 2026 | Remove | 18.3 | 0 | OHL | 0.9219 | 3.7893 | 1.025 | 241 | 230 | 210 | 230
NWGL4- | PEHE4J | 2026 | Addition | 0 | 1 | Cable | 0.1 | 0.3 | 0 | 9999 | 9999 | 9999 | 9999
PORA1Q | PORA1U | 2026 | Remove | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1R | PORA1T | 2026 | Remove | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1T | PORA1U | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA2J | PORA2K | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA2J | PORA2M | 2026 | Addition | 0 | 5.6 | Cable | 0.0224 | 0.2296 | 1.579 | 1290 | 1240 | 1160 | 1240
PORA2K | PORA2L | 2026 | Addition | 0 | 5.6 | Cable | 0.0224 | 0.2296 | 1.579 | 1290 | 1240 | 1160 | 1240
ALTN1- | CONN1J | 2029 | Addition | 18 | 0 | OHL | 1.638 | 3.888 | 0.972 | 150 | 142 | 128 | 142
BERB2Q | CAID2- | 2029 | Addition | 7.99 | 0 | OHL | 0.0452 | 0.3288 | 2.178 | 935 | 880 | 790 | 880
BERB2Q | KNOC2J | 2029 | Remove | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
BETH1A | BETH1B | 2029 | Addition | 12.5 | 0 | OHL | 0.625 | 2.5875 | 0.7 | 224 | 211 | 189 | 211
BETH1A | FYRI1J | 2029 | Addition | 0 | 0.5 | Cable | 0.0103 | 0.0424 | 0.674 | 190 | 174 | 174 | 174
BETH1B | BETH1C | 2029 | Addition | 0 | 6 | Cable | 0.1233 | 0.5091 | 8.092 | 190 | 174 | 174 | 174
BLGH1- | CRDH1J | 2029 | Addition | 10 | 0 | OHL | 0.91 | 2.16 | 0.54 | 150 | 142 | 128 | 142
CAID2- | KNOC2J | 2029 | Addition | 38.99 | 0 | OHL | 0.2208 | 1.6052 | 10.631 | 935 | 880 | 790 | 880
COGL4- | COGL4J | 2029 | Addition | 0 | 1.95 | Cable | 0.0015 | 0.0264 | 9.165 | 930 | 900 | 900 | 900
COGL4- | COGL4K | 2029 | Addition | 0 | 1.95 | Cable | 0.0015 | 0.0264 | 9.165 | 930 | 900 | 900 | 900
COGL4J | INGA4J | 2029 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1470 | 1350 | 1170 | 1350
COGL4K | INGA4K | 2029 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1470 | 1350 | 1170 | 1350
DOUN2- | OFPH2- | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4J | DOUN4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4J | SPIT4J | 2029 | Addition | 15.4 | 0 | OHL | 0.0206 | 0.2826 | 9.541 | 2810 | 2700 | 2510 | 2700
DOUN4K | SPIT4K | 2029 | Addition | 15.4 | 0 | OHL | 0.0206 | 0.2826 | 9.541 | 2810 | 2700 | 2510 | 2700
GILB1J | PENF1C | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MOTA1Q | SHIN1- | 2029 | Change | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 106 | 117
OFPK4- | PEHE4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
OFPN4- | PEHE4J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
SPIT4J | SPIT4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999

## B-2-2b
B.2.2b - SPT Circuit Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
COAL1- | DONO1- | 2021 | Addition | 0 | 4.5 | Cable | 0.1271 | 0.2921 | 5.5423 | 165 | 165 | 165 | 165
COAL1- | MIDM1- | 2021 | Remove | 0 | 14.47 | Cable | 0.4086 | 0.9392 | 17.8217 | 158 | 146 | 146 | 146
COAL1A | LINM1Q | 2021 | Change | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
DONO1- | MIDM1- | 2021 | Addition | 0 | 10.57 | Cable | 0.2985 | 0.6861 | 13.0183 | 158 | 146 | 146 | 146
GLNI1- | MOSM1A | 2021 | Change | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 265 | 246 | 212 | 246
GLNI1- | MOSM1B | 2021 | Change | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 265 | 246 | 212 | 246
KAIM2- | SMEA2- | 2021 | Change | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1300 | 1230 | 1150 | 1230
LEVT1R | WFIE1B | 2021 | Change | 18.707 | 0 | OHL | 1.4753 | 4.1917 | 0.9554 | 143 | 142 | 128 | 142
REDH1- | WFIE1A | 2021 | Change | 10.097 | 0 | OHL | 0.695 | 2.2577 | 0.5197 | 157 | 152 | 141 | 152
AREX1A | CHMO1T | 2022 | Addition | 4.7 | 0 | OHL | 0.3571 | 1.0182 | 0.2484 | 284 | 278 | 270 | 278
AREX1A | MAHI1X | 2022 | Addition | 7.5 | 0 | OHL | 0.5699 | 1.6247 | 0.3964 | 365 | 360 | 350 | 360
AYR-2Q | COYW2S | 2022 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1050 | 965 | 880 | 965
AYR-2R | COYW2T | 2022 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1050 | 965 | 880 | 965
CHAP1- | GRNA1- | 2022 | Change | 12.83 | 0.35 | Composite | 0.9812 | 3.1043 | 0.9907 | 167 | 160 | 148 | 160
CHAP1- | GRNA1- | 2022 | Change | 12.83 | 0.3 | Composite | 0.9799 | 3.0991 | 0.9387 | 167 | 160 | 148 | 160
COAL1A | CUMH1- | 2022 | Addition | 0 | 7.7 | Cable | 0.1211 | 0.6629 | 12.6869 | 241 | 241 | 241 | 241
COAL1A | GAWH1Q | 2022 | Remove | 0 | 10.5 | Cable | 0.1651 | 0.9039 | 17.3003 | 241 | 241 | 241 | 241
COCK4Q | ECCL4A | 2022 | Change | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 2022 | Change | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1090 | 1030 | 925 | 1030
CUMH1- | GAWH1Q | 2022 | Addition | 0 | 3.2 | Cable | 0.0503 | 0.2755 | 5.2725 | 241 | 241 | 241 | 241
DENN2- | LAMB2T | 2022 | Addition | 32.18 | 0 | OHL | 0.1451 | 1.3095 | 8.9356 | 953 | 882 | 762 | 882
DENN2- | LOAN2- | 2022 | Addition | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1C | 2022 | Change | 6.4 | 4.3 | Composite | 0.5762 | 1.7993 | 6.3388 | 135 | 125 | 108 | 125
DEVM1- | ERSK1Q | 2022 | Change | 16.5 | 0 | OHL | 1.0026 | 3.563 | 0.8861 | 213 | 202 | 185 | 202
DEVM4- | HUNE4- | 2022 | Remove | 50.471 | 0.167 | Composite | 0.0909 | 0.9984 | 33.1263 | 1316 | 1067 | 1067 | 1067
DEVM4- | NEIL4R | 2022 | Addition | 28.474 | 0 | OHL | 0.0582 | 0.5967 | 15.8233 | 1995 | 1926 | 1787 | 1926
DEVM4- | WIYH4Q | 2022 | Change | 28.908 | 0 | OHL | 0.0586 | 0.5888 | 16.3967 | 1995 | 1926 | 1787 | 1926
ELDE1Q | JOHN1Q | 2022 | Change | 0 | 3.9 | Cable | 0.1101 | 0.2531 | 4.8034 | 120 | 120 | 120 | 120
ELDE1R | JOHN1R | 2022 | Change | 0 | 3.9 | Cable | 0.1101 | 0.2531 | 4.8034 | 120 | 120 | 120 | 120
EWEH1Q | GRNA1- | 2022 | Change | 15.9 | 0.3 | Composite | 1.2123 | 3.4542 | 1.6286 | 262 | 262 | 262 | 262
EWEH1Q | HOPR1- | 2022 | Addition | 6 | 0 | OHL | 0.4507 | 1.3202 | 0.316 | 199 | 191 | 175 | 191
GLGL1Q | SAKN1- | 2022 | Addition | 0 | 7 | Cable | 0.1977 | 0.4544 | 8.6214 | 134 | 123 | 123 | 123
HUNE4- | NEIL4Q | 2022 | Change | 35.198 | 0 | OHL | 0.068 | 0.7118 | 20.1554 | 1469 | 1351 | 1164 | 1351
HUNE4- | NEIL4R | 2022 | Addition | 34.97 | 0 | OHL | 0.0675 | 0.7072 | 20.0247 | 1995 | 1926 | 1787 | 1926
LAMB2T | LOAN2- | 2022 | Remove | 53.67 | 0.225 | Composite | 0.1948 | 2.0808 | 18.1931 | 795 | 620 | 620 | 620
MAHI1B | MAHI1X | 2022 | Addition | 0 | 0.5 | Cable | 0.0032 | 0.0298 | 0.8758 | 365 | 360 | 350 | 360
NECU1C | SOKY1- | 2022 | Addition | 0 | 4.5 | Cable | 0.0292 | 0.2677 | 7.8824 | 242 | 223 | 192 | 223
NEIL2- | WIYH2R | 2022 | Change | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1372 | 1324 | 1228 | 1324
AREX1- | AREX1A | 2024 | addition | 0 | 2.5 | Cable | 0.0445 | 0.2384 | 2.9171 | 85 | 85 | 85 | 85
BENB1- | BENB1B | 2024 | addition | 3 | 0 | OHL | 0.2251 | 0.6606 | 0.1578 | 167 | 160 | 148 | 160
BENB1B | GNSH1- | 2024 | addition | 30.35 | 0.9 | Composite | 1.3071 | 6.1749 | 3.2285 | 241 | 241 | 241 | 241
BENB1B | NECU1B | 2024 | addition | 4 | 0 | OHL | 0.1038 | 0.7722 | 0.2394 | 482 | 445 | 385 | 445
BERW1Q | ECCL1- | 2024 | Change | 21.54 | 0.31 | Composite | 1.622 | 4.903 | 1.5274 | 132 | 123 | 106 | 123
BERW1Q | MARM1- | 2024 | addition | 4.2 | 0 | OHL | 0.3155 | 0.9241 | 0.2212 | 167 | 160 | 148 | 160
BERW1R | ECCL1- | 2024 | Change | 21.54 | 0.27 | Composite | 1.6213 | 4.8991 | 1.4716 | 132 | 123 | 106 | 123
BERW1R | MARM1- | 2024 | addition | 4.2 | 0 | OHL | 0.3155 | 0.9241 | 0.2212 | 167 | 160 | 148 | 160
BLAH1- | GLGL1- | 2024 | Change | 13.6 | 0.375 | Composite | 0.5154 | 2.926 | 1.6551 | 268 | 246 | 246 | 246
BLAH1- | GLGL1- | 2024 | Change | 13.6 | 0.375 | Composite | 0.5154 | 2.926 | 1.6551 | 268 | 246 | 246 | 246
BLCW1- | GNSH1- | 2024 | addition | 1.8 | 0 | OHL | 0.135 | 0.3964 | 0.0947 | 167 | 160 | 148 | 160
BLCW1- | MARG1- | 2024 | Remove | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 166 | 159 | 147 | 159
BRAP1- | ERSK1Q | 2024 | Change | 3.17 | 5.4 | Composite | 0.3985 | 1.1026 | 12.4454 | 167 | 160 | 148 | 160
BRAP1- | ERSK1R | 2024 | Change | 3.45 | 6.23 | Composite | 0.4418 | 1.1771 | 12.9647 | 167 | 160 | 148 | 160
BROC1- | BROC1T | 2024 | addition | 0 | 0.2 | Cable | 0.0056 | 0.013 | 0.2463 | 134 | 123 | 123 | 123
BROC1T | COAL1A | 2024 | addition | 0 | 3.2 | Cable | 0.0261 | 0.2614 | 5.959 | 293 | 293 | 293 | 293
BROC1T | LINM1Q | 2024 | addition | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 416 | 395 | 361 | 395
CHMO1- | CHMO1T | 2024 | addition | 0.3 | 0 | OHL | 0.0225 | 0.066 | 0.0158 | 167 | 160 | 147 | 160
CHMO1T | STNO1- | 2024 | addition | 4.5 | 0 | OHL | 0.3376 | 0.991 | 0.2367 | 167 | 160 | 147 | 160
COAL1A | LINM1Q | 2024 | Remove | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
COAL1B | CUMH1- | 2024 | Change | 0 | 7.7 | Cable | 0.1195 | 0.6543 | 13.0164 | 241 | 241 | 241 | 241
COAL1B | CUMW1- | 2024 | addition | 0 | 9.1 | Cable | 0.257 | 0.5907 | 11.955 | 120 | 120 | 120 | 120
COAL1B | DONO1- | 2024 | Change | 0 | 4.5 | Cable | 0.0635 | 0.146 | 11.0847 | 330 | 330 | 330 | 330
COAL1B | KENN1- | 2024 | addition | 15.4 | 2 | Composite | 1.2117 | 3.5211 | 3.2733 | 167 | 161 | 150 | 161
COYL2- | CRCK2- | 2024 | addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
COYL2- | MAHI2- | 2024 | Remove | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
CRCK2- | MAHI2- | 2024 | addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
CROO1Q | NEIL1- | 2024 | Change | 12.56 | 0.22 | Composite | 0.4737 | 2.7011 | 0.9855 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 2024 | Change | 12.56 | 0.23 | Composite | 0.4738 | 2.702 | 0.9994 | 229 | 211 | 183 | 211
CURR1A | GORG1Q | 2024 | Change | 1.49 | 5.8 | Composite | 0.261 | 0.9656 | 5.1127 | 111 | 100 | 92 | 100
CURR1B | GORG1R | 2024 | Change | 1.49 | 5.78 | Composite | 0.2603 | 0.9634 | 5.0953 | 111 | 100 | 92 | 100
DALB2A | DALL2- | 2024 | addition | 0 | 0 | Cable | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000
DALB2B | DALL2- | 2024 | addition | 0 | 0 | Cable | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000
DENN2- | LOAN2Z | 2024 | Addition | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2- | 2024 | Remove | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
ELDE1Q | NEIL1- | 2024 | Change | 3.82 | 0.18 | Composite | 0.1455 | 0.8324 | 0.4574 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 2024 | Change | 3.82 | 0.23 | Composite | 0.1461 | 0.8373 | 0.5271 | 229 | 211 | 183 | 211
ELVA1- | NLEI1- | 2024 | addition | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 217 | 198 | 217
ENHI1- | NECU1C | 2024 | addition | 0 | 4.4 | Cable | 0.1242 | 0.2856 | 5.7805 | 134 | 123 | 123 | 123
GHPS1- | GLGL1- | 2024 | addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 482 | 445 | 385 | 445
GHPS1- | GLGL1- | 2024 | addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 482 | 445 | 385 | 445
GHPS1- | LETH1- | 2024 | addition | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 200 | 200 | 200 | 200
GLGL1- | SAKN1- | 2024 | Change | 0 | 7 | Cable | 0.1977 | 0.4544 | 8.6214 | 134 | 123 | 123 | 123
GLGL1- | SANQ1- | 2024 | addition | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277
GLLE1- | NETS1- | 2024 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLLE1- | NETS1- | 2024 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLNI1- | WFIE1B | 2024 | Change | 7.11 | 0 | OHL | 0.5359 | 1.6524 | 0.3546 | 332 | 318 | 294 | 318
GLRB2- | GLRO2- | 2024 | Change | 14.68 | 0 | OHL | 0.0662 | 0.6092 | 3.9929 | 1096 | 1029 | 924 | 1029
GLRO2- | WFIE2- | 2024 | Change | 12.08 | 0 | OHL | 0.0545 | 0.5013 | 3.2857 | 1096 | 1029 | 924 | 1029
GORG1Q | TELR1Q | 2024 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GORG1R | TELR1R | 2024 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GRNA1- | HAWI1- | 2024 | Change | 55.35 | 0 | OHL | 5.0077 | 12.6881 | 2.7627 | 133 | 124 | 107 | 124
GRNA1- | JUNV1- | 2024 | Change | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 167 | 155 | 134 | 155
HAWI1- | JUNV1- | 2024 | Change | 50.34 | 0 | OHL | 4.5503 | 11.4999 | 2.5189 | 132 | 123 | 106 | 123
HOLM1- | HOLM1T | 2024 | addition | 8 | 0 | OHL | 0.6078 | 1.7331 | 0.4228 | 366 | 359 | 350 | 359
HOLM1- | LORG1- | 2024 | addition | 10 | 0 | OHL | 0.5312 | 2.1273 | 0.5456 | 242 | 232 | 212 | 232
HOLM1- | SHRG1- | 2024 | addition | 1.01 | 0 | OHL | 0.0759 | 0.2222 | 0.0532 | 167 | 160 | 148 | 359
HOLM1T | KEOO1- | 2024 | addition | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 133 | 123 | 106 | 123
HOLM1T | NECU1B | 2024 | addition | 16.35 | 0 | OHL | 0.4243 | 3.1565 | 0.9785 | 482 | 445 | 385 | 445
KEOO1- | NECU1B | 2024 | Remove | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 133 | 123 | 106 | 123
KINB2J | KINC2- | 2024 | Change | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2024 | Change | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 1090 | 1030 | 925 | 1030
LOAN2- | MOSM2L | 2024 | Change | 26.196 | 0.194 | Composite | 0.1184 | 1.0894 | 10.6096 | 1096 | 1029 | 924 | 1029
LOAN2Z | WFIE2- | 2024 | Addition | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
LOAN2- | WFIE2- | 2024 | Remove | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 760 | 620 | 620 | 620
MARG1- | NECU1B | 2024 | Remove | 34.35 | 0.9 | Composite | 1.1487 | 6.9058 | 3.4859 | 241 | 230 | 210 | 230
MOSM2- | MOSM2L | 2024 | Change | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 1090 | 1030 | 925 | 1030
MOSM2- | MOSM2T | 2024 | Change | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 1096 | 1029 | 924 | 1029
MOSM2T | WFIE2- | 2024 | Change | 2.943 | 0 | OHL | 0.0133 | 0.1221 | 0.8005 | 1096 | 1029 | 924 | 1029
NECU1B | OHLL1- | 2024 | addition | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180
NECU1C | NOKY1- | 2024 | addition | 0 | 1.3 | Cable | 0.0084 | 0.0774 | 2.2771 | 261 | 261 | 261 | 261
WFIB2- | WFIE2- | 2024 | Change | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1096 | 1029 | 924 | 1029
BENB1B | GNSH1- | 2026 | Remove | 30.35 | 0.9 | Composite | 1.3071 | 6.1749 | 3.2285 | 241 | 241 | 241 | 241
BENB1B | KEOO1Q | 2026 | Addition | 20.25 | 0 | OHL | 0.5256 | 3.9095 | 1.2119 | 352 | 325 | 281 | 325
BRNX4- | CRYR4- | 2026 | Addition | 13.86 | 0 | OHL | 0.0178 | 0.2543 | 8.5869 | 2522 | 2397 | 2189 | 2397
BRNX4- | ECCL4A | 2026 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2522 | 2397 | 2189 | 2397
BRNX4- | ECCL4B | 2026 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2522 | 2397 | 2189 | 2397
BRNX4- | SMEA4Q | 2026 | Addition | 58.82 | 0 | OHL | 0.0774 | 1.1407 | 35.1217 | 2473 | 2349 | 2148 | 2349
BRNX4- | TORN4- | 2026 | Addition | 0 | 2.1 | Cable | 0.0005 | 0.014 | 46.7008 | 1040 | 900 | 900 | 900
BRNX4- | TORN4- | 2026 | Addition | 0 | 1.94 | Cable | 0.0005 | 0.013 | 43.1426 | 945 | 800 | 800 | 800
CAFA1Q | KEOO1- | 2026 | Change | 2.58 | 0 | OHL | 0.198 | 0.5682 | 0.1357 | 135 | 126 | 110 | 130
CHAP1- | HAKB1- | 2026 | Change | 14.72 | 0 | OHL | 1.1184 | 3.1888 | 0.7779 | 284 | 278 | 270 | 274
CLAU1- | MAHI1C | 2026 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 167 | 160 | 147 | 160
COAL1A | LEGO1Q | 2026 | Addition | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123
COAL1A | LEGO1R | 2026 | Addition | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123
CRYR4- | TORN4- | 2026 | Remove | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 935 | 785 | 785 | 785
DENN2- | LAMB2- | 2026 | Change | 31.991 | 0 | OHL | 0.1353 | 1.3066 | 8.8961 | 1372 | 1324 | 1228 | 1324
DENN2- | LAMB2T | 2026 | Change | 32.18 | 0 | OHL | 0.1361 | 1.3147 | 8.9474 | 1372 | 1324 | 1228 | 1324
DENN2- | LOAN2Z | 2026 | Remove | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2- | 2026 | Addition | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DEVM1- | SPAV1Q | 2026 | Change | 7.63 | 0 | OHL | 0.5726 | 1.7268 | 0.3878 | 167 | 160 | 148 | 160
DEVM1- | SPAV1R | 2026 | Change | 7.51 | 0 | OHL | 0.5636 | 1.699 | 0.3818 | 167 | 160 | 148 | 160
DUMF1- | TONG1Q | 2026 | Remove | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNF1Q | INKE1Q | 2026 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
DUNF1R | INKE1R | 2026 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
EAST1Q | GLLE1- | 2026 | Change | 1.5 | 0.3 | Composite | 0.1236 | 0.3498 | 0.4484 | 133 | 124 | 107 | 124
ECCL4A | TORN4- | 2026 | Remove | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | TORN4- | 2026 | Remove | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
EKIL3A | EKIL3B | 2026 | Addition | 0 | 0 | Series Reactor | 0.6667 | 61.6631 | 0 | 30 | 30 | 30 | 30
EUCH1- | LORG1- | 2026 | Addition | 3.5 | 0 | OHL | 0.2629 | 0.7701 | 0.1843 | 167 | 160 | 148 | 160
FASI1- | FASI1A | 2026 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 185
FASI1- | FASI1B | 2026 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 184
FASI1A | HAWI1D | 2026 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1A | JUNV1- | 2026 | Addition | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 132 | 123 | 106 | 123
FASI1B | HAWI1C | 2026 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1B | JUNV1A | 2026 | Addition | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191
GALA1- | HAWI1- | 2026 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1- | 2026 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1B | 2026 | Remove | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARE1S | WHTL1S | 2026 | Change | 1.68 | 0 | OHL | 0.1261 | 0.3772 | 0.086 | 167 | 160 | 148 | 160
GARE1T | WHTL1T | 2026 | Change | 1.67 | 0 | OHL | 0.1253 | 0.3749 | 0.0855 | 167 | 160 | 148 | 160
GLLE1- | KEOO1- | 2026 | Change | 7.68 | 0 | OHL | 0.1993 | 1.4827 | 0.4596 | 482 | 445 | 385 | 445
GLLE1- | KEOO1Q | 2026 | Addition | 10.68 | 0 | OHL | 0.2772 | 2.0619 | 0.6391 | 482 | 445 | 385 | 445
GLLE1- | TONG1- | 2026 | Addition | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 198 | 186 | 168 | 186
GLLE1- | TONG1- | 2026 | Change | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 198 | 186 | 168 | 186
GNSH1- | KEOO1Q | 2026 | Addition | 10.1 | 0.9 | Composite | 0.5506 | 2.226 | 2.0339 | 241 | 241 | 241 | 241
GNSH1- | TRSN1- | 2026 | Addition | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 149 | 160
GRNA1- | HAWI1- | 2026 | Remove | 55.35 | 0 | OHL | 5.0077 | 12.6881 | 2.7627 | 133 | 124 | 107 | 124
GRNA1- | JUNV1- | 2026 | Change | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA1- | JUNV1A | 2026 | Addition | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA4- | HAKB4B | 2026 | Change | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2370 | 2270 | 2270 | 2270
HAKB4- | MOFF4C | 2026 | Change | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2370 | 2270 | 2270 | 2270
HAWI1- | JUNV1- | 2026 | Remove | 50.34 | 0 | OHL | 4.5503 | 11.4999 | 2.5189 | 132 | 123 | 106 | 123
HOLM1T | KEOO1- | 2026 | Change | 10.9 | 0 | OHL | 0.2829 | 2.1044 | 0.6523 | 386 | 356 | 308 | 356
KINB2J | KINC2- | 2026 | Remove | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2026 | Remove | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 1090 | 1030 | 925 | 1030
KINB4J | KINC4A | 2026 | Addition | 10.5 | 0 | OHL | 0.0229 | 0.2213 | 5.8026 | 1590 | 1500 | 1350 | 1500
KINB4K | KINC4S | 2026 | Addition | 10.15 | 0 | OHL | 0.0222 | 0.2143 | 5.6016 | 1590 | 1500 | 1350 | 1500
KINC4B | KINC4S | 2026 | Addition | 0 | 0.35 | Cable | 0.0002 | 0.0047 | 3.8917 | 1590 | 1500 | 1350 | 1500
KNOK1- | MAHI1C | 2026 | Addition | 3 | 0 | OHL | 0.1594 | 0.6382 | 0.1637 | 242 | 232 | 216 | 232
LAMB2- | WIYH2- | 2026 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1372 | 1324 | 1228 | 1324
LAMB2T | WIYH2- | 2026 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1372 | 1324 | 1228 | 1324
LOAN2- | MOSM2L | 2026 | Change | 26.196 | 0.194 | Composite | 0.1186 | 1.0915 | 8.8674 | 1090 | 1030 | 925 | 1030
LOAN2- | WFIE2- | 2026 | Addition | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 1090 | 1030 | 925 | 1030
LOAN2Z | WFIE2- | 2026 | Remove | 29.209 | 0 | OHL | 0.1319 | 1.2141 | 9.3165 | 1090 | 1030 | 925 | 1030
MOFF1- | SCOP1- | 2026 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
MOFF1- | SCOP1- | 2026 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
SMEA4Q | STHA4B | 2026 | Change | 75.76 | 0 | OHL | 0.1547 | 1.5403 | 43.1224 | 1995 | 1926 | 1787 | 1926
SMEA4Q | TORN4- | 2026 | Remove | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 2026 | Change | 61.77 | 0 | OHL | 0.1265 | 1.2657 | 34.9519 | 1995 | 1926 | 1787 | 1926
STHA4A | WISH4- | 2026 | Change | 11.6 | 0 | OHL | 0.0234 | 0.2267 | 6.7974 | 1995 | 1926 | 1787 | 1926
WHTB1S | WHTL1S | 2026 | Change | 2.05 | 0 | OHL | 0.1538 | 0.4602 | 0.105 | 167 | 160 | 148 | 160
WHTB1T | WHTL1T | 2026 | Change | 2.05 | 0 | OHL | 0.1538 | 0.4602 | 0.105 | 167 | 160 | 148 | 160
BONN2- | DENN2- | 2029 | Addition | 3.25 | 1 | Composite | 0.0152 | 0.1771 | 6.0833 | 1372 | 1324 | 1228 | 1324
BONN2- | NEAR2T | 2029 | Addition | 17 | 0 | OHL | 0.0739 | 0.7786 | 4.3296 | 1372 | 1324 | 1228 | 1324
BONN2A | DENN2- | 2029 | Remove | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 2029 | Remove | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BONN4- | DENN4- | 2029 | Addition | 3.25 | 0.75 | Composite | 0.0069 | 0.0754 | 18.43 | 1995 | 1926 | 1786 | 1926
BONN4- | WISH4- | 2029 | Addition | 40.36 | 0 | OHL | 0.083 | 0.8736 | 21.7471 | 1995 | 1926 | 1786 | 1926
BRNX4- | BRNX4A | 2029 | Addition | 0 | 0.25 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770
CHAP1- | DUMF1- | 2029 | Remove | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | GRNA1- | 2029 | Change | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 167 | 160 | 147 | 160
CHAP1- | GRNA1- | 2029 | Change | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 167 | 160 | 147 | 160
CHAP1- | OFOA1T | 2029 | Addition | 24.82 | 0.18 | Composite | 0.984 | 5.6173 | 1.5274 | 171 | 155 | 155 | 155
COCK4Q | ECCL4A | 2029 | Change | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1995 | 1926 | 1786 | 1926
COCK4R | ECCL4B | 2029 | Change | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1995 | 1926 | 1786 | 1926
CURR2- | GRMO2- | 2029 | Change | 42.18 | 0 | OHL | 0.1798 | 1.7435 | 11.6852 | 1372 | 1324 | 1228 | 1324
CURR2- | KINC2- | 2029 | Change | 57.14 | 0 | OHL | 0.2435 | 2.3619 | 15.8296 | 1372 | 1324 | 1228 | 1324
DUMF1- | OFOA1T | 2029 | Addition | 2.08 | 0 | OHL | 0.0822 | 0.4694 | 0.1069 | 229 | 212 | 183 | 212
ECCL1- | GALA1- | 2029 | Change | 30.14 | 0 | OHL | 1.6015 | 6.6324 | 1.5764 | 242 | 232 | 214 | 232
ECCL1- | GALA1- | 2029 | Change | 30.58 | 0 | OHL | 1.6249 | 6.7325 | 1.5989 | 242 | 232 | 214 | 232
EERH2- | NEAR2Q | 2029 | Remove | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EERH2- | NEAR2T | 2029 | Addition | 7.74 | 0 | OHL | 0.0332 | 0.3289 | 2.0967 | 1372 | 1266 | 1096 | 1266
ELVA4- | STHA4A | 2029 | Remove | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ELVN4- | ELVA4- | 2029 | Addition | 0.001 | 0 | OHL | 0 | 0 | 0 | 2210 | 2130 | 1980 | 2130
ELVN4- | GHPS4- | 2029 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
ELVN4- | GHPS4- | 2029 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
ELVN4- | STHA4A | 2029 | Addition | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
GBRN1- | NECU1C | 2029 | Addition | 8 | 0 | OHL | 0.6001 | 1.7617 | 0.4208 | 167 | 160 | 147 | 160
GRMO2- | KINC2- | 2029 | Change | 14.96 | 0 | OHL | 0.0638 | 0.6184 | 4.1444 | 1372 | 1324 | 1228 | 1324
NEAR2- | NEAR2T | 2029 | Addition | 7.6 | 0 | OHL | 0.0331 | 0.3481 | 1.9356 | 1372 | 1324 | 1228 | 1324
NEAR2- | WISH2- | 2029 | Change | 15.76 | 0 | OHL | 0.0685 | 0.7218 | 4.0138 | 1372 | 1324 | 1228 | 1324
NEAR2Q | WISH2- | 2029 | Remove | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
OFOA1T | OFOA1- | 2029 | Addition | 20 | 0 | OHL | 1.5025 | 4.4007 | 1.0533 | 167 | 160 | 147 | 160
SMEA4Q | STHA4B | 2029 | Remove | 75.76 | 0 | OHL | 0.1547 | 1.5403 | 43.1224 | 1995 | 1926 | 1787 | 1926
SMEA4Q | WISH4- | 2029 | Addition | 61.77 | 0 | OHL | 0.1265 | 1.2657 | 34.9519 | 1995 | 1926 | 1787 | 1926
STHA4B | WISH4- | 2029 | Addition | 13.99 | 0 | OHL | 0.0285 | 0.2854 | 7.9774 | 1995 | 1926 | 1787 | 1926

## B-2-2c
B.2.2c - NGET Circuit Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BLYT21 | TYNE21 | 2021 | Change | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1310 | 1220 | 1310
BLYT21 | TYNE2A | 2021 | Change | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1310 | 1220 | 1310
BOTW41 | CHIL41 | 2021 | Addition | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 3820 | 3630 | 3320 | 3630
BOTW41 | FAWL41 | 2021 | Remove | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 901 | 901 | 901
CHIL41 | FAWL41 | 2021 | Addition | 0 | 3.57 | Cable | 0.0018 | 0.0112 | 109.0992 | 900 | 700 | 700 | 900
CHIL41 | FAWL41 | 2021 | Addition | 0 | 3.57 | Cable | 0.0018 | 0.0112 | 109.0992 | 900 | 700 | 700 | 900
CHIL41 | LOVE41 | 2021 | Addition | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 3820 | 3630 | 3320 | 3630
FAWL41 | LOVE41 | 2021 | Remove | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 901 | 901 | 901
HATL21 | HARM21 | 2021 | Change | 13.983 | 0 | OHL | 0.0472 | 0.5702 | 3.9648 | 1093 | 1031 | 925 | 1031
HATL21 | SALH21 | 2021 | Change | 7.794 | 0 | OHL | 0.0327 | 0.3353 | 2.0878 | 1382 | 1279 | 1157 | 1279
HATL21 | WBOL21 | 2021 | Remove | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1093 | 1031 | 926 | 1031
HAWP21 | HATL21 | 2021 | Addition | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1090 | 1090 | 1090 | 1090
HAWP21 | OFFE21 | 2021 | Change | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1180 | 1120 | 1020 | 1120
OFFE21 | WBOL21 | 2021 | Change | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1180 | 1120 | 1020 | 1120
RAYL41 | TILB4A | 2021 | Change | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 3100 | 2914 | 2635 | 2945
SSHI21 | TYNE2A | 2021 | Change | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1360 | 1310 | 1220 | 1310
SSHI21 | WBOL21 | 2021 | Change | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1180 | 1120 | 1020 | 1120
TYNE21 | WBOL21 | 2021 | Change | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1180 | 1120 | 1020 | 1120
WBOL21 | HAWP21 | 2021 | Addition | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1180 | 1120 | 1020 | 1120
HINP41 | MELK41 | 2022 | Remove | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | SAFO41 | 2022 | Addition | 24.54 | 8.15 | Composite | 0.0376 | 0.5627 | 203.1782 | 2009 | 1911 | 1746 | 1911
HINP41 | SHUR41 | 2022 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 3100 | 3050 | 2960 | 3050
HINP41 | TAUN41 | 2022 | Remove | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1980 | 2125
MELK41 | SAFO41 | 2022 | Addition | 86.94 | 8.15 | Composite | 0.12082 | 1.5237 | 232.9123 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA41 | 2022 | Change | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2550 | 2550 | 2550 | 2550
NORT41 | OSBA42 | 2022 | Change | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2009 | 2009 | 2009 | 2009
SHUR41 | SHUR41 | 2022 | Addition | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2000 | 2000 | 2000 | 2000
SHUR41 | TAUN41 | 2022 | Addition | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1980 | 2125
SJOW21 | TOTT23 | 2022 | Remove | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 868 | 868 | 868 | 868
SJOW21 | TOTT24 | 2022 | Remove | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 868 | 868 | 868 | 868
HINP22 | BRWA2A | 2023 | Remove | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 620 | 620 | 620
HINP41 | SHUR41 | 2023 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 3100 | 3050 | 2960 | 3050
HINP41 | TAUN42 | 2023 | Remove | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1980 | 2125
PURI4A | BRWA4A | 2023 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 2030 | 1930 | 1770 | 1930
SHUR41 | PURI4A | 2023 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 3050 | 2960 | 3050
SHUR41 | TAUN42 | 2023 | Addition | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1980 | 2125
BLYT21 | BLYT21 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT21 | BLYT21 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT21 | BLYT21 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT21 | BLYT21 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BRAI4A | BRFO41 | 2024 | Change | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3100 | 2914 | 2635 | 2945
BRAI4A | BULL41 | 2024 | Change | 12.343 | 0 | OHL | 0.0121 | 0.2133 | 8.2261 | 3100 | 2914 | 2635 | 2945
BRAI4B | PELH41 | 2024 | Change | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 3100 | 2914 | 2635 | 2945
BRAI4B | RAYL41 | 2024 | Change | 33.03 | 0 | OHL | 0.0325 | 0.5709 | 22.0036 | 3100 | 2914 | 2635 | 2945
BRLE41 | MELK41 | 2024 | Change | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1710 | 1607 | 1454 | 1625
BRLE41 | MELK41 | 2024 | Change | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1710 | 1607 | 1454 | 1625
BULL41 | RAYL41 | 2024 | Change | 20.646 | 0 | OHL | 0.0203 | 0.3568 | 13.7565 | 3100 | 2914 | 2635 | 2945
ELST4A | SUND41 | 2024 | Change | 34.834 | 0 | OHL | 0.0556 | 0.6699 | 20.9635 | 2400 | 2256 | 2040 | 2280
ELST4B | SUND42 | 2024 | Change | 34.706 | 0 | OHL | 0.0554 | 0.6674 | 20.8867 | 1590 | 1500 | 1346 | 1500
GRAI41 | GRAW4A | 2024 | Addition | 9.634 | 0 | OHL | 0.0105 | 0.1676 | 6.3509 | 3102 | 2813 | 2633 | 2813
GRAI41 | GRAW4B | 2024 | Addition | 1.7 | 0.2445 | Composite | 0.0021 | 0.0324 | 3.4557 | 2003 | 2003 | 1939 | 2003
GRAI41 | KINO41 | 2024 | Remove | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3102 | 2813 | 2633 | 2813
GRAI41 | TILB41 | 2024 | Remove | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2003 | 2003 | 1939 | 2003
GRAW41 | GRAW4A | 2024 | Addition | 0 | 0.2 | Cable | 0.0001 | 0.0025 | 2.5133 | 3102 | 2813 | 2633 | 2813
GRAW41 | GRAW4B | 2024 | Addition | 0 | 0.2 | Cable | 0.0001 | 0.0025 | 2.5133 | 3102 | 2813 | 2633 | 2813
GRAW4A | KINO41 | 2024 | Addition | 9.807 | 0.8 | parallel Composite | 0.0108 | 0.1732 | 17.4426 | 3102 | 2813 | 2633 | 2813
GRAW4B | TILB41 | 2024 | Addition | 24.9424 | 1.805 | Composite | 0.0283 | 0.4536 | 52.5445 | 2003 | 2003 | 1939 | 2003
HINP21 | BRWA2B | 2024 | Remove | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 762 | 619 | 619 | 619
HINP41 | MELK41 | 2024 | Remove | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | SEAB41 | 2024 | Addition | 53.385 | 8.15 | Composite | 0.0697 | 1.1063 | 220.9169 | 2009 | 1911 | 1746 | 1911
MELK41 | PURI4A | 2024 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 2009 | 1911 | 1746 | 1911
MELK41 | PURI4B | 2024 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 2009 | 1911 | 1746 | 1911
MELK41 | SAFO41 | 2024 | Remove | 86.94 | 8.15 | Composite | 0.12082 | 1.5237 | 232.9123 | 2009 | 1911 | 1746 | 1911
MELK41 | SEAB41 | 2024 | Remove | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MELK41 | SEAB4A | 2024 | Addition | 53.528 | 0 | OHL | 0.05975 | 0.9445 | 34.8716 | 2545 | 2421 | 2211 | 2421
PURI4B | BRWA4B | 2024 | Addition | 3.6 | 0.4 | Composite | 0.0058 | 0.0738 | 11.4004 | 300 | 300 | 300 | 300
SAFO41 | SEAB4A | 2024 | Addition | 28.845 | 0 | OHL | 0.0322 | 0.5436 | 17.7387 | 3190 | 3060 | 2850 | 3060
SEAB41 | SEAB4A | 2024 | Addition | 0.03 | 0 | OHL | 3.9e-05 | 0.000577 | 0.018069 | 2545 | 2421 | 2211 | 2421
SHUR41 | PURI4B | 2024 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 3050 | 2960 | 3050
THTO41 | THTO43 | 2024 | Addition | 0 | 0 | Series Reactor | 0.0016 | 2 | 0 | 2400 | 2400 | 2400 | 2400
THTO42 | THTO42 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.125 | 0 | 3100 | 3100 | 3100 | 3100
THTO42 | THTO42 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB41 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB41 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB41 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB41 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.3125 | 0 | 3100 | 3100 | 3100 | 3100
BOLN41 | NINF41 | 2026 | Remove | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 2026 | Remove | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
GRAI41 | GRAW4A | 2026 | Change | 9.634 | 0 | OHL | 0.0085 | 0.1654 | 6.4875 | 3300 | 2970 | 2805 | 3135
GRAI41 | GRAW4B | 2026 | Change | 1.7 | 0.2445 | Composite | 0.0017 | 0.032 | 3.4799 | 3300 | 2970 | 2805 | 3135
GRAW4A | KINO41 | 2026 | Change | 9.807 | 0.8 | parallel Composite | 0.0088 | 0.171 | 17.5792 | 3300 | 2970 | 2805 | 3135
GRAW4B | TILB41 | 2026 | Change | 24.9424 | 1.805 | Composite | 0.0232 | 0.4481 | 52.8966 | 3300 | 2970 | 2805 | 3135
HAKB1- | HARK13 | 2026 | Change | 8.49 | 0 | OHL | 0.6448 | 1.8386 | 0.4485 | 284 | 274 | 254 | 274
HARK13 | JUNV1- | 2026 | Change | 12.135 | 0 | OHL | 0.9147 | 2.8202 | 0.6058 | 199 | 191 | 178 | 191
HARK13 | JUNV1A | 2026 | Addition | 12.135 | 0 | OHL | 0.9147 | 2.8202 | 0.6058 | 199 | 191 | 178 | 191
HURS21 | LITT2A | 2026 | Change | 5.164 | 2.613 | Composite | 0.0274 | 0.2841 | 14.8804 | 1298 | 1298 | 1200 | 1298
HURS21 | LITT2B | 2026 | Change | 5.14 | 2.659 | Composite | 0.0273 | 0.2842 | 15.1114 | 1298 | 1298 | 1200 | 1298
HURS21 | NEWX21 | 2026 | Change | 0 | 21.106 | Cable | 0.0304 | 0.5278 | 108.8888 | 1298 | 1298 | 1200 | 1298
HURS21 | NEWX21 | 2026 | Change | 0 | 21.864 | Cable | 0.0315 | 0.5467 | 112.7994 | 1298 | 1298 | 1200 | 1298
KINO41 | TILB41 | 2026 | Change | 15.4784 | 1.835 | Composite | 0.0149 | 0.2859 | 47.1231 | 3300 | 2970 | 2805 | 3135
LHOR4A | BOLN41 | 2026 | Addition | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935
LHOR4A | NINF41 | 2026 | Addition | 23.304 | 0 | OHL | 0.0253 | 0.4053 | 15.3623 | 3102 | 2935 | 2765 | 2935
LHOR4B | BOLN41 | 2026 | Addition | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935
LHOR4B | NINF41 | 2026 | Addition | 23.304 | 0 | OHL | 0.0253 | 0.4053 | 15.3623 | 3102 | 2935 | 2765 | 2935
NECT41 | KINL41 | 2026 | Addition | 2.7 | 0 | OHL | 0.0024 | 0.046 | 1.8212 | 2520 | 2520 | 2520 | 2520
NECT41 | WALP41 | 2026 | Addition | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NECT4A | WALP41 | 2026 | Remove | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3299 | 3078 | 3299
NECT4B | WALP41 | 2026 | Remove | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NEWX21 | WIMB21 | 2026 | Remove | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 779 | 779 | 779
NEWX21 | WIMB21 | 2026 | Remove | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 813 | 813 | 813
NEWX41 | BENR41 | 2026 | Addition | 0 | 4 | Cable | 0.0036 | 0.042 | 72 | 1298 | 1298 | 1200 | 1298
NEWX42 | WIMB41 | 2026 | Addition | 0 | 12 | Cable | 0.0108 | 0.126 | 216 | 1298 | 1298 | 1200 | 1298
WALP41 | KINL41 | 2026 | Addition | 44.319 | 0 | OHL | 0.0393 | 0.7609 | 29.7952 | 2520 | 2520 | 2520 | 2520
WIMB41 | BENR41 | 2026 | Addition | 0 | 8 | Cable | 0.0072 | 0.084 | 144 | 1298 | 1298 | 1200 | 1298
BRAI4A | BRFO41 | 2029 | Addition | 49.529 | 0 | OHL | 0.046 | 0.853 | 33.1401 | 3100 | 2914 | 2635 | 2945
BRAI4A | BRFO41 | 2029 | Remove | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3100 | 2914 | 2635 | 2945
BRAI4B | BRFO41 | 2029 | Addition | 49.529 | 0 | OHL | 0.0461 | 0.8531 | 33.1365 | 3100 | 2914 | 2635 | 2945
BRAI4B | PELH41 | 2029 | Remove | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 3100 | 2914 | 2635 | 2945
BRFO41 | PELH41 | 2029 | Addition | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3273 | 3100 | 3100 | 3820 | 3100
BRFO41 | PELH41 | 2029 | Change | 69.301 | 0 | OHL | 0.0656 | 1.1949 | 46.3241 | 3102 | 2935 | 2765 | 2935
CANT41 | SELL4A | 2029 | Change | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3100 | 2914 | 2635 | 2945
CANT41 | SELL4B | 2029 | Change | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3100 | 2914 | 2635 | 2945
DUNG41 | SELL4E | 2029 | Change | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3100 | 2914 | 2635 | 2945
DUNG41 | SELL4F | 2029 | Change | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3100 | 2914 | 2635 | 2945
HAWP21 | NORT21 | 2029 | Remove | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 801 | 720 | 801
KNAR21 | MONF21 | 2029 | Remove | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 551 | 512 | 442 | 512
KNAR21 | POPP21 | 2029 | Remove | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 551 | 512 | 442 | 512
KNAR21 | TADT2A | 2029 | Addition | 25 | 0 | OHL | 0.1969 | 1.0483 | 6.8757 | 551 | 512 | 442 | 512
KNAR21 | TADT2B | 2029 | Addition | 25 | 0 | OHL | 0.1969 | 1.0483 | 6.8757 | 551 | 512 | 442 | 512
MONF21 | TADT2A | 2029 | Addition | 13.531 | 0.141 | Composite | 0.05 | 0.526 | 5.229 | 2200 | 2200 | 2200 | 2200
MONF22 | POPP21 | 2029 | Remove | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 682 | 629 | 538 | 629
MONF22 | TADT2B | 2029 | Addition | 13.531 | 0 | OHL | 0.0497 | 0.5232 | 4.0291 | 2200 | 2200 | 2200 | 2200
NORT41 | HAWP41 | 2029 | Addition | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 2780 | 2780 | 2780 | 2780
NORT41 | OSBA41 | 2029 | Remove | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2550 | 2550 | 2550 | 2550
NORT41 | OSBA42 | 2029 | Remove | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2009 | 1911 | 1746 | 1911
OBST4A | NORT41 | 2029 | Addition | 77.639 | 0 | OHL | 0.1 | 1.4648 | 47.5893 | 2550 | 2550 | 2550 | 2550
OBST4A | POPP4B | 2029 | Addition | 6.2 | 0 | OHL | 0.0054 | 0.1065 | 4.175 | 2810 | 2810 | 2810 | 2810
OBST4B | NORT41 | 2029 | Addition | 77.639 | 0 | OHL | 0.1 | 1.4648 | 47.5893 | 2009 | 1911 | 1746 | 1911
OBST4B | POPP4A | 2029 | Addition | 6.2 | 0 | OHL | 0.0054 | 0.1065 | 4.175 | 2810 | 2810 | 2810 | 2810
OSBA41 | OBST4A | 2029 | Addition | 6.2 | 0 | OHL | 0.0113 | 0.1234 | 3.5932 | 2550 | 2550 | 2550 | 2550
OSBA42 | OBST4B | 2029 | Addition | 6.2 | 0 | OHL | 0.0113 | 0.1234 | 3.5932 | 2009 | 1911 | 1746 | 1911
TADT2A | POPP21 | 2029 | Addition | 24.192 | 0 | OHL | 0.0888 | 0.9354 | 7.2035 | 2200 | 2200 | 2200 | 2200
TADT2B | POPP21 | 2029 | Addition | 24.192 | 0 | OHL | 0.0888 | 0.9354 | 7.2035 | 2200 | 2200 | 2200 | 2200

## B-2-2d
B.2.2d - OFTO Circuit Changes 2021/22 to 2029/30
Wind Farm | Node 1 | Node 2 | Year | Status | Interconnection Type | Rated DC Voltage (kV) | Rated AC Voltage (kV) | Length(km) | Rating (MVA)
Firth of Forth 1 Offshore Wind Farm | FOFW61 | FOFW62 | 2021 | Addition | AC | N/A | 66 | 11.33 | TBC
| FOFO21 | FOFW21 | 2021 | Addition | AC | N/A | 275 | 75 | TBC
| FOFO21 | FOFW22 | 2021 | Addition | AC | N/A | 275 | 75 | TBC
| TEAL21 | FOFO21 | 2021 | Addition | AC | N/A | 275 | 0.5 | TBC
| TEAL21 | FOFO21 | 2021 | Addition | AC | N/A | 275 | 0.5 | TBC
Hornsea 1 Offshore Wind Farm | HOWA21 | HOWR2A | 2021 | Addition | AC | N/A | 220 | 104.703 | 1328
| HOWR2A | HOWW23 | 2021 | Addition | AC | N/A | 220 | 85 | 380
| HOWW22 | HOWW23 | 2021 | Addition | AC | N/A | 220 | 13.9 | 364
Moray East offshore Wind Farm | MOWE21 | MORF21 | 2021 | Addition | AC | N/A | 220 | 90.69 | 312
| MOWE22 | MORF22 | 2021 | Addition | AC | N/A | 220 | 90.69 | 312
| MOWE23 | MORF23 | 2021 | Addition | AC | N/A | 220 | 90.69 | 312
| NEDE21 | Moray Firth 275kV -1 | 2021 | Addition | AC | N/A | 275 | 0.06 | 398
| NEDE21 | Moray Firth 275kV -2 | 2021 | Addition | AC | N/A | 275 | 0.1 | 398
| NEDE21 | Moray Firth 275kV -3 | 2021 | Addition | AC | N/A | 275 | 0.15 | 398
Triton Knoll Offshore Wind Farm | TKNO21 | TKNE21 | 2021 | Addition | AC | N/A | 220 | 57.8 | 428
Inch Cape Offshore Wind Farm | INCW21 | INCO21 | 2022 | Addition | AC | N/A | 220 | 85.5 | 550
| INCW22 | INCO22 | 2022 | Addition | AC | N/A | 220 | 85.5 | 550
| INCO21 | COCK21 | 2022 | Addition | AC | N/A | 275 | TBC | TBC
| INCO22 | COCK21 | 2022 | Addition | AC | N/A | 275 | TBC | TBC
Neart Na Gaoithe Offshore Wind Farm | NNGW21 | NNGO21 | 2022 | Addition | AC | N/A | 220 | 51.021 | 230
| NNGW22 | NNGO22 | 2022 | Addition | AC | N/A | 220 | 50.783 | 230
| NNGO41 | CRYA41 | 2022 | Addition | AC | N/A | 400 | 0.289 | 400
| NNGO42 | CRYB41 | 2022 | Addition | AC | N/A | 400 | 0.394 | 400
Dogger bank 1 offshore Wind Farm | Dogger bank 1A offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | AC | N/A | 220 | 8 | 174
| Dogger bank 1A offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | AC | N/A | 220 | 8 | 174
| Dogger bank 1B offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | AC | N/A | 220 | 8 | 174
| Dogger bank 1B offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | AC | N/A | 220 | 8 | 174
| Dogger bank offshore 320kV | Dogger bank onshore 320kV | 2024 | Addition | HVDC | 320 | TBC | 245 | TBC
| Dogger bank offshore 320kV | Dogger bank onshore 320kV | 2024 | Addition | HVDC | 320 | TBC | 245 | TBC
| Dogger bank onshore 400kV | CREB41 | 2024 | Addition | AC | N/A | 400 | 8 | TBC
| Dogger bank onshore 400kV | CREB41 | 2024 | Addition | AC | N/A | 400 | 8 | TBC
Doggerbank 4 Offshore wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2024 | Addition | AC | N/A | 220 | 6 | 252
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2024 | Addition | AC | N/A | 220 | 6 | 252
| Doggerbank 4 Offshore | Doggerbank 4 Onshore | 2024 | Addition | HVDC | 320 | TBC | 187 | 1031
| Doggerbank 4 Offshore | Doggerbank 4 Onshore | 2024 | Addition | HVDC | 320 | TBC | 187 | 1031
| Doggerbank 4 Onshore 400kV | CREB41 | 2024 | Addition | A/C | N/A | 400 | TBC | TBC
| Doggerbank 4 Onshore 400kV | CREB41 | 2024 | Addition | A/C | N/A | 400 | TBC | TBC
East Anglia 3 Offshore Wind Farm | East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | AC | N/A | 220 | TBC | TBC
| East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | AC | N/A | 220 | TBC | TBC
| East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | AC | N/A | 220 | TBC | TBC
| East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | AC | N/A | 220 | TBC | TBC
| East Anglia Offshore | East Anglia Onshore | 2024 | Addition | HVDC | 320 | TBC | TBC | TBC
| East Anglia Offshore | East Anglia Onshore | 2024 | Addition | HVDC | 320 | TBC | TBC | TBC
| East Anglia Onshore | BRFO41 | 2024 | Addition | AC | N/A | 400 | TBC | TBC
Firth of Forth 1 Wind Farm | FOFW62 | FOFW63 | 2024 | Addition | AC | N/A | 66 | 11.33 | TBC
| FOFO21 | FOFW23 | 2024 | Addition | AC | N/A | 275 | 75 | TBC
Hornsea 2 Offshore Wind Farm | Hornsea 2A Offshore | Hornsea 2 Onshore | 2024 | Addition | A/C | N/A | 220 | 167 | TBC
| Hornsea 2B Offshore | Hornsea 2 Onshore | 2024 | Addition | A/C | N/A | 220 | 167 | TBC
| Hornsea 2C Offshore | Hornsea 2 Onshore | 2024 | Addition | A/C | N/A | 220 | 167 | TBC
| Hornsea 2A Offshore | Hornsea 2B Offshore | 2024 | Addition | A/C | N/A | 220 | 12 | TBC
| Hornsea 2B Offshore | Hornsea 2C Offshore | 2024 | Addition | A/C | N/A | 220 | 12 | TBC
| Hornsea 2 Onshore | KILL41 | 2024 | Addition | A/C | N/A | 400 | 0.7 | TBC
| Hornsea 2 Onshore | KILL41 | 2024 | Addition | A/C | N/A | 400 | 0.7 | TBC
Hornsea 3 Offshore Wind Farm | Hornsea 3A-1 Offshore 500kV | Hornsea 3A-1 Onshore 500kV | 2024 | Addition | HVDC | ±400 | 500 | 220 | 750
| Hornsea 3A Onshore 400kV | NORM41 | 2024 | Addition | AC | N/A | 400 | 1.8 | 1596
Moray West Offshore Wind Farm | Moray West Offshore 220kV | Moray West Onshore 220kV | 2024 | Addition | AC | N/A | 220 | 72 | TBC
| Moray West Offshore 220kV | Moray West Onshore 220kV | 2024 | Addition | AC | N/A | 220 | 72 | TBC
| Moray West Onshore 220kV | BLHI41 | 2024 | Addition | AC | N/A | 400 | 0.5 | TBC
| Moray West Onshore 220kV | BLHI41 | 2024 | Addition | AC | N/A | 400 | 0.5 | TBC
| Moray West Offshore P1 66kV | Moray West Offshore P2 66kV | 2024 | Addition | AC | N/A | 66 | TBC | TBC
Sofia Offshore Offshore Wind Farm | Sofia offshore windfarm TBC | Sofia onshore windfarm TBC | 2024 | Addition | HVDC | 320 | TBC | 237
| Sofia onshore windfarm 400kV | LACK41 | 2024 | Addition | AC | N/A | 400 | 2 | TBC
Dogger Bank 4B Offshore Wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2026 | Addition | A/C | N/A | 220 | 6 | 252
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2026 | Addition | A/C | N/A | 220 | 6 | 252
East Anglia 6A Offshore Wind Farm | East Anglia 6A Offshore-2 | East Anglia 6A Onshore-1 | 2026 | Addition | HVDC | ±320 | 400 | 100 | 900
| East Anglia 6A Offshore-2 | East Anglia 6A Onshore-1 | 2026 | Addition | HVDC | ±320 | 400 | 100 | 900
| East Anglia 6A Onshore-1 | NECT41 | 2026 | Addition | AC | N/A | 400 | N/A | N/A
East Anglia 6B Offshore Wind Farm | East Anglia 6B Offshore-2 | East Anglia 6B Onshore-1 | 2026 | Addition | HVDC | ±320 | 400 | 100 | 900
| East Anglia 6B Offshore-2 | East Anglia 6B Onshore-1 | 2026 | Addition | HVDC | ±320 | 400 | 100 | 900
| East Anglia 6B Onshore-1 | NECT41 | 2026 | Addition | AC | N/A | 400 | N/A | N/A
Firth of Forth 2A Offshore Wind Farm | Offshore 66KV-1 | Offshore 66KV-2 | 2026 | Addition | AC | N/A | 66 | N/A | N/A
| Offshore 66KV-2 | Offshore 66KV-3 | 2026 | Addition | AC | N/A | 66 | N/A | N/A
| Offshore 275kV-1 | Onshore 275kV-1 | 2026 | Addition | AC | N/A | 275 | 77.4 | N/A
| Offshore 275kV-2 | Onshore 275kV-1 | 2026 | Addition | AC | N/A | 275 | 77.4 | N/A
| Offshore 275kV-3 | Onshore 275kV-1 | 2026 | Addition | AC | N/A | 275 | 77.4 | N/A
| Onshore 400kV-1 | BRNX41 | 2026 | Addition | AC | N/A | 400 | N/A | N/A
| Onshore 400kV-1 | BRNX41 | 2026 | Addition | AC | N/A | 400 | N/A | N/A
| Hornsea 3A-2 Offshore 500kV | Hornsea 3A-2 Onshore 500kV | 2026 | Addition | HVDC | ±400 | 500 | 220 | 750
| Hornsea 3B-1 Offshore 500kV | Hornsea 3B-1 Onshore 500kV | 2026 | Addition | HVDC | ±400 | 500 | 220 | 750
| Hornsea 3B Onshore 400kV | NORM41 | 2026 | Addition | AC | N/A | 400 | 1.8 | 1596
Sheringham and Dudgeon Extension Wind Farm | Offshore 220kV-1 | Onshore 220kV-1 | 2026 | Addition | AC | N/A | 220 | 82 | TBC
| Offshore 220kV-2 | Onshore 220kV-2 | 2026 | Addition | AC | N/A | 220 | 82 | TBC
| Onshore 400kV-1 | NORM41 | 2026 | Addition | AC | N/A | 400 | 0.5 | TBC
| Onshore 400kV-2 | NORM41 | 2026 | Addition | AC | N/A | 400 | 0.5 | TBC
Codling Offshore Wind Farm | Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | AC | N/A | 220 | 97 | 655
| Codling Onshore 220kV | Codling Onshore 220kV | 2029 | Addition | AC | N/A | 220 | 22 | 1040
| Codling Onshore 220kV | Codling Onshore 220kV | 2029 | Addition | AC | N/A | 220 | 22 | 1040
| Codling Onshore 220kV | Codling Onshore 220kV | 2029 | Addition | AC | N/A | 220 | 22 | 1040
| Codling Onshore 220kV | Codling Onshore 220kV | 2029 | Addition | AC | N/A | 220 | 22 | 1040
Dogger Bank 2 Offshore Wind Farm | Offshore-2 | Onshore-1 | 2026 | Addition | HVDC | ±300 | TBC | N/A | 1500
| Onshore 400kV | LACK41 | 2026 | Addition | AC | N/A | 400 | N/A | N/A
EA One North Farm | EA1N Offshore 220kV-1 | EA1N Onshore 220kV | 2029 | Addition | AC | N/A | 220 | TBC | TBC
| EA1N Offshore 220kV-2 | EA1N Onshore 220kV | 2029 | Addition | AC | N/A | 220 | TBC | TBC
| EA1N Onshore 400kV | LEIS41 | 2029 | Addition | AC | N/A | 400 | TBC | TBC
East Anglia 4A Wind Farm | East Anglia 4A Offshore-2 | East Anglia 4A Onshore-1 | 2029 | Addition | HVDC | ±320 | TBC | 134 | TBC
| East Anglia 4A Offshore-2 | East Anglia 4A Onshore-1 | 2029 | Addition | HVDC | ±320 | TBC | 134 | TBC
| East Anglia 4A 400kV | NECT41 | 2029 | Addition | AC | N/A | 400 | TBC | TBC
East Anglia 5A Wind Farm | East Anglia 5A Offshore-2 | East Anglia 5A Onshore-1 | 2029 | Addition | HVDC | ±320 | TBC | 134 | TBC
| East Anglia 5A Offshore-2 | East Anglia 5A Onshore-1 | 2029 | Addition | HVDC | ±320 | TBC | 134 | TBC
| East Anglia 5A 400kV | NECT41 | 2029 | Addition | AC | N/A | 400 | TBC | TBC
Firth of Forth 2B Offshore Wind Farm | Offshore 66KV-4 | Offshore 66KV-5 | 2029 | Addition | AC | N/A | 66 | N/A | N/A
| Offshore 66KV-5 | Offshore 66KV-6 | 2029 | Addition | AC | N/A | 66 | N/A | N/A
| Offshore 275kV-4 | Onshore 275kV-2 | 2029 | Addition | AC | N/A | 275 | 72.3 | N/A
| Offshore 275kV-5 | Onshore 275kV-2 | 2029 | Addition | AC | N/A | 275 | 72.3 | N/A
| Offshore 275kV-6 | Onshore 275kV-2 | 2029 | Addition | AC | N/A | 275 | 72.3 | N/A
| Onshore 400kV-2 | BRNX41 | 2029 | Addition | AC | N/A | 400 | N/A | N/A
| Onshore 400kV-2 | BRNX41 | 2029 | Addition | AC | N/A | 400 | N/A | N/A
Hornsea 4 WinfdFarm | Offshore 275kV-1 | Reactive Platform-1 | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Offshore 275kV-2 | Reactive Platform-2 | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Offshore 275kV-3 | Reactive Platform-3 | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Reactive Platform-1 | Onshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Reactive Platform-2 | Onshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Reactive Platform-3 | Onshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Onshore 400kV | CREB41 | 2029 | Addition | AC | N/A | 400 | 0.5 | TBC
| Offshore 275kV-4 | Reactive Platform-4 | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Offshore 275kV-5 | Reactive Platform-5 | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Reactive Platform-4 | Onshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Reactive Platform-5 | Onshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| Onshore 400kV | CREB41 | 2029 | Addition | AC | N/A | 400 | 0.5 | TBC
Racebank Extension Wind Farm | Offshore Platform 220kV-1 | Onshore 220kV-1 | 2029 | Addition | AC | N/A | 220 | TBC | TBC
| Offshore Platform 220kV-2 | Onshore 220kV-2 | 2029 | Addition | AC | N/A | 220 | TBC | TBC
| Onshore 400 kV-1 | Mablethorpe 400kV | 2029 | Addition | AC | N/A | 400 | TBC | TBC
| Onshore 400 kV-2 | Mablethorpe 400kV | 2029 | Addition | AC | N/A | 400 | TBC | TBC
| Hornsea 3B-2 Offshore 500kV | Hornsea 3B-2 Onshore 500kV | 2029 | Addition | HVDC | ±400 | 500 | 220 | 750
Thanet Extension Offshore Wind Farm | Offshore-1 | Onshore-1 | 2029 | Addition | AC | N/A | TBC | TBC | TBC
| Offshore-1 | Onshore-1 | 2029 | Addition | AC | N/A | TBC | TBC | TBC
| Onshore 400kV | RICH41 | 2029 | Addition | AC | N/A | TBC | TBC | TBC
| Onshore 400kV | RICH41 | 2029 | Addition | AC | N/A | TBC | TBC | TBC
West of Orkney Offshore Wind Farm | West of Orkney Offshore 275kV | West of Orkney Offshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| West of Orkney Offshore 275kV | West of Orkney Offshore 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| West of Orkney Offshore 275kV | Dounreay 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC
| West of Orkney Offshore 275kV | Dounreay 275kV | 2029 | Addition | AC | N/A | 275 | TBC | TBC

## B-3-1a
B.3.1a - SHE Transmission Transformers for 2020/21
Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
ACHR1R | ACHR3- | 0.36 | 18 | 0 | 90
AIGA1Q | AIGA5- | 1.76 | 44.89 | 0 | 22.5
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.615 | 17.82 | -0.026 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU2J | BEAU1J | 0.6786 | 12.2312 | -0.0009 | 120
BEAU2J | BEAU1J | 0.6786 | 12.1644 | -0.0009 | 120
BEAU2K | BEAU1K | 0.6786 | 12.1895 | -0.0009 | 120
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.0004 | 1200
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.0004 | 1200
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 0.1486 | 5.3035 | -0.0006 | 360
BLHI2K | BLHI1K | 0.1506 | 5.3034 | -0.0006 | 360
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2L | 0.0252 | 1.1997 | -0.0005 | 1200
BLHI4- | BLHI2M | 0.0253 | 1.2081 | -0.0005 | 1200
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRCW2J | BRCW3- | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 0.42 | 20 | 0 | 120
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 39 | 0 | 30
BROR1- | BROR3- | 0.763 | 25.144 | 0 | 45
BUMU1Q | BUMU3- | 0.366 | 25.37 | -0.034 | 90
BUMU1R | BUMU3- | 0.376 | 25.42 | -0.035 | 90
CAAD1Q | CAAD3- | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1Q | CAAD3J | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3- | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1R | CAAD3J | 0.5 | 25 | 0 | 90
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120
CASS1Q | CASS3- | 1.518 | 39.871 | 0 | 30
CEAN1Q | CEAN5- | 1.182 | 36.714 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAC1Q | CLAC5J | 0.75 | 25 | 0 | 60
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
CLUN1Q | CLUN5J | 0.71 | 19.53 | 0 | 60
CLUN1R | CLUN5K | 0.71 | 19.55 | 0 | 60
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90
CONN2J | CONN1J | 0.143 | 5.3036 | -0.0006 | 360
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
CORI1J | CORI3J | 8.3 | 27.5 | 0 | 60
COUA1Q | COUA3- | 0.2143 | 25.0741 | -0.0067 | 120
COUA1R | COUA3- | 0.2151 | 25.1241 | -0.0092 | 120
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
CRSS1J | COUW31 | 0.3629 | 18.0297 | -0.0123 | 90
CRSS1J | CRSS1Q | 0.0582 | 2.145 | 0 | 240
CRSS1K | CRSS1R | 0.0582 | 2.1492 | 0 | 240
CRSS2A | CRSS1J | 0.2466 | 9.0008 | -0.0005 | 240
CRSS2B | CRSS1K | 0.2459 | 9.0175 | -0.0005 | 240
CULL1Q | CULL5- | 1.46 | 37.6 | 0 | 25
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DEAN1Q | DEAN5- | 1.01 | 25.1 | 0 | 40
DORE11 | DORE31 | 0.21 | 9.89 | 0 | 120
DORE12 | DORE32 | 0.21 | 9.89 | 0 | 120
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DOUN2- | DOUN1- | 0.2112 | 7.7054 | -0.0005 | 240
DOUN2- | DOUN1- | 0.2237 | 7.9135 | -0.0006 | 240
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.617 | 17.65 | -0.029 | 60
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120
DUNO1Q | DUNO3- | 2 | 24.49 | 0 | 45
DUNO1R | DUNO3- | 2 | 24.5801 | 0 | 45
DYCE1Q | DYCE3- | 0.4015 | 24.819 | -0.0194 | 90
DYCE1R | DYCE3- | 0.3974 | 24.7301 | -0.0007 | 90
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1J | ERRO1A | 0.04 | 1.942 | 0 | 240
ERRO1J | ERRO5L | 0.72 | 26.6 | 0 | 60
ERRO1K | ERRO1B | 0.04 | 1.942 | 0 | 240
ERRO1K | ERRO5J | 0.72 | 26.6 | 0 | 60
ERRO1T | ERRO1J | 0.068 | 3.73 | 0 | 150
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FARI2J | FARI1J | 0.4989 | 8.2933 | -0.038 | 120
FARI2K | FARI1K | 0.4955 | 8.3186 | -0.038 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1Q | FAUG3- | 2.23 | 64.33 | 0 | 15
FAUG2J | FAUG1- | 0.2606 | 7.7039 | -0.0005 | 240
FAUG2K | FAUG1- | 0.2629 | 7.7038 | -0.0005 | 240
FAUG4- | FAUG1- | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 0.3185 | 8.4523 | -0.013 | 240
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FETT2R | FETT1- | 0.217 | 4.2737 | -0.0006 | 240
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FINL1Q | FINL5- | 0.96 | 27.11 | 0 | 45
FRAS1Q | FRAS3- | 0.642 | 26.904 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.904 | 0 | 45
FWIL1Q | FWIL3- | 0.499 | 24.995 | 0 | 120
FWIL1R | FWIL3- | 0.499 | 24.995 | 0 | 120
FYRI2J | FYRI1J | 0.0967 | 3.8863 | -0.0006 | 480
FYRI2K | FYRI1K | 0.0971 | 3.8738 | -0.0006 | 480
GLDO1G | GLDO8- | 0.206 | 10.681 | 0 | 120
GLEN1Q | GLEN5- | 0.55 | 21.94 | 0 | 70
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90
INGA1Q | INGA5- | 1.287 | 25 | 0 | 30
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
INVB2A | INVR1- | 0.2217 | 4.3026 | -0.0071 | 240
INVB2B | INVR1- | 0.2164 | 4.257 | -0.0066 | 240
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEIT3A | 0.499 | 24.995 | 0 | 90
KEIT2Q | KEIT1- | 0.2735 | 8.6123 | -0.0007 | 240
KEIT2R | KEIT1- | 0.3328 | 8.9105 | -0.0389 | 240
KIIN1- | KIIN3- | 0.772 | 24.877 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.521 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.78 | 0 | 45
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT1- | 0.3771 | 10.1929 | -0.018 | 240
KINT2K | KINT1- | 0.3751 | 10.2314 | -0.0147 | 240
KINT2K | KINT1- | 0.6786 | 12.1477 | -0.0009 | 120
KIOR1Q | KIOR5- | 1.78 | 45.42 | 0 | 22.5
KNOC2J | KNOC1J | 0.2216 | 4.311 | -0.0076 | 240
KNOC2K | KNOC1J | 0.2205 | 4.3319 | -0.0006 | 240
LAIR1Q | LAIR3- | 0.425 | 24.674 | 0 | 90
LOCB2J | LOCB1J | 0.2181 | 8.1262 | -0.0007 | 240
LOCB2K | LOCB1K | 0.22 | 8.197 | -0.0007 | 240
LOCH1- | LOCH5J | 1.93 | 38.52 | 0 | 25
LOCH1- | LOCH5K | 1.93 | 38.2 | 0 | 25
LUIC1Q | LUIC5J | 0.763 | 37.548 | 0 | 45
LUIC1R | LUIC5K | 0.7668 | 37.548 | 0 | 45
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.429 | 25.741 | 0 | 90
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MELG4J | MELG1J | 0.108 | 3.957 | -0.0007 | 480
MELG4K | MELG1K | 0.106 | 3.957 | -0.0007 | 480
MILC1R | MILC3- | 0.78 | 24.83 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.13 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MOSS1Q | MOSS5- | 1.192 | 36.847 | 0 | 30
MOSS1R | MOSS5- | 1.2267 | 36.913 | 0 | 30
MYBS1S | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1S | MYBS3M | 0.2645 | 24.6069 | -0.024 | 120
MYBS1T | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3N | 0.2578 | 24.757 | -0.024 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6 | 0 | 60
NANT1Q | NANT5- | 1.47 | 56.67 | 0 | 30
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
ORRI1R | ORRI5- | 2.17 | 48.75 | 0 | 20
PEHE1- | PEHS5- | 2.58 | 42.33 | 0 | 15
PEHE2- | PEHE1- | 0.2649 | 9.2254 | -0.0005 | 240
PEHE2Q | PEHE1- | 0.4842 | 9.9549 | -0.0178 | 240
PEHE2R | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.4 | 0 | 45
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PERS2Q | PERS1Q | 0.3363 | 8.9062 | -0.0412 | 240
PERS2R | PERS1R | 0.3341 | 8.8645 | -0.0419 | 240
PORA1Q | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 1.803 | 29.812 | 0 | 30
QUOI1- | QUOI5- | 1.34 | 33.13 | 0 | 30
RANN1Q | RANN3Q | 0.43 | 24.66 | 0 | 90
RANN1R | RANN3Q | 0.43 | 24.66 | 0 | 90
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
SFEG1Q | SFEG5- | 2.28 | 93.87 | 0 | 30
SFEG1R | SFEG5- | 2.28 | 92.8 | 0 | 30
SFEM1Q | SFEM5J | 1.8 | 41.19 | 0 | 27
SFEM1R | SFEM5K | 1.8 | 41.19 | 0 | 27
SFIL1Q | SFIL5- | 1.99 | 39.48 | 0 | 25
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
SHIN1- | SHIN5- | 1.4823 | 80.16 | 0 | 40
SLOY1L | SLOY5L | 0.79 | 23.08 | 0 | 50
SLOY1M | SLOY5M | 0.79 | 22.9 | 0 | 50
SLOY1N | SLOY5N | 0.79 | 22.98 | 0 | 50
SLOY1P | SLOY5P | 0.8 | 23.2 | 0 | 50
SPIT2J | SPIT1J | 0.218 | 8.185 | -0.0007 | 240
SPIT2J | SPIT1J | 0.218 | 8.23 | -0.0007 | 240
SPIT2K | SPIT1K | 0.131 | 4.99 | -0.0006 | 360
SPIT2K | SPIT1M | 0.129 | 4.99 | -0.0006 | 360
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
STRL1- | STRL3P | 0.2 | 17.74 | -0.01 | 120
STRL1- | STRL3Q | 0.2 | 17.65 | -0.01 | 120
STRL1- | STRL3R | 0.2 | 17.67 | -0.01 | 120
STRW12 | STRW31 | 0.05 | 18 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.53 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.787 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.787 | 0 | 90
TEAL2J | TEAL1- | 0.3619 | 10.1602 | -0.0118 | 180
TEAL2K | TEAL1- | 0.2564 | 11.7305 | -0.0131 | 180
TEAL2K | TEAL1- | 0.5506 | 11.8761 | -0.0008 | 180
THUS1J | THUS3- | 0.2621 | 24.6736 | -0.022 | 120
THUS1K | THUS3- | 0.2614 | 24.7403 | -0.02 | 120
THUS2J | THUS1J | 0.0985 | 3.9363 | -0.0005 | 480
THUS2K | THUS1K | 0.1 | 3.9362 | -0.0006 | 480
TOMT2J | TOMT1J | 0.098 | 3.905 | -0.0006 | 480
TOMT2K | TOMT1K | 0.098 | 3.905 | -0.0006 | 480
TUMB1Q | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMB1R | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMM2J | TUMM1J | 0.259 | 7.7457 | -0.0005 | 240
TUMM2K | TUMM1K | 0.2595 | 7.829 | -0.0005 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.24 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
B.3.1b - SPT Transformers for 2020/21
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3C | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3A | 0.5214 | 27.5617 | -0.1031 | 120
CLYM2- | CLYM3A | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3B | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1- | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1A | 0.1216 | 9.6242 | -0.0793 | 240
COAL4- | COAL1A | 0.0914 | 6.4382 | -0.0751 | 360
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1718 | 8.665 | -0.0204 | 120
COYL2- | COYL1- | 0.3396 | 12.8288 | -0.2375 | 120
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR1- | CRYR31 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR1- | CRYR32 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR1B | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1A | 0.1079 | 8.5702 | -0.0341 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 160
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 160
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3A | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3B | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1S | DUNB3B | 0.4121 | 28.9304 | -0.0087 | 90
DUNB1T | DUNB3B | 0.3569 | 28.82 | -0.0089 | 90
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EKIL2S | EKIL3- | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3- | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3A | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3B | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 0.5259 | 26.8282 | -0.0075 | 60
ERSK1R | ERSK3- | 0.5296 | 27.1115 | -0.0073 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 0.4311 | 25.9297 | -0.0244 | 90
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3A | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3B | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60
GORG1R | GORG3- | 0.8167 | 26.9876 | -0.0071 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.3876 | 19.4628 | -0.0275 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.5381 | 25.2943 | -0.0108 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1- | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1- | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
JOHN1Q | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60
JOHN1R | JOHN3- | 0.7078 | 27.9911 | -0.013 | 60
KAIM2- | KAIM3A | 0.4944 | 20.244 | -0.245 | 120
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILS4T | KILS2- | 0.0148 | 1.6509 | -0.1193 | 1000
KILT2Q | KILT3- | 0.4927 | 18.4934 | -0.1756 | 120
KILT2R | KILT3- | 0.4976 | 18.4933 | -0.1775 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KYPE1- | KYPE3- | 0.1922 | 14.207 | -0.0113 | 120
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MIDM1- | MIDM3- | 0.4664 | 13.6087 | -0.0075 | 60
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37.5
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37.5
MOSM1A | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1B | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1A | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1B | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1173 | 8.6992 | -0.0311 | 240
NECU2- | NECU1- | 0.1173 | 8.5659 | -0.0322 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0297 | 240
NECU2- | NECU1Q | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 0.1164 | 8.5534 | -0.0287 | 240
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 90
REDH1- | REDH3- | 0.94 | 20.7787 | 0 | 60
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SANX1Q | SANX3- | 0.8844 | 21.5485 | -0.309 | 60
SANX1R | SANX3- | 0.8767 | 21.2319 | -0.3087 | 60
SHRU2Q | SHRU3- | 0.4926 | 19.9939 | -0.2739 | 120
SHRU2R | SHRU3- | 0.2914 | 23.7232 | -0.0252 | 120
SIGH2Q | SIGH3A | 0.4564 | 27.5518 | -0.032 | 180
SIGH2R | SIGH3A | 0.4281 | 27.53 | -0.0372 | 180
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4722 | 18.7441 | -0.1542 | 120
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 120
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1- | STLE3S | 0.4217 | 25.741 | -0.028 | 90
STLE1- | STLE3S | 0.4235 | 25.6743 | -0.0254 | 90
TELR1Q | TELR3- | 0.9688 | 26.4656 | -0.0572 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG1R | 0.0267 | 1.3331 | 0 | 90
TONG1- | TONG3- | 0.533 | 26.9114 | -0.0078 | 60
TONG1- | TONG3- | 0.5309 | 27.0615 | -0.008 | 60
TONG1Q | TONG1R | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WESE1- | AIKE3A | 0.5667 | 13.2333 | 0 | 90
WESE1- | AIKE3B | 0.5667 | 13.2333 | 0 | 90
WFIE1A | WFIE3- | 0.9889 | 20.4928 | 0 | 60
WFIE1B | WFIE3- | 0.9528 | 20.5613 | 0 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH2- | WISH3- | 0.4821 | 24.1785 | -0.226 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.1517 | 8.707 | -0.1161 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.2306 | 12.2562 | -0.0292 | 120
WLEX2- | WLEX3B | 0.2306 | 12.2728 | -0.0271 | 120
WLEX2- | WLEX3C | 0.2306 | 12.2728 | -0.0275 | 120

## B-3-1c
B.3.1c - NGET Transformer Parameters for 2020/21
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA4A | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275
ABHA4B | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 279
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211
ABTH21 | ABTH13 | 0.0977 | 8.1994 | -1.7127 | 212
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALVE4A | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275
AMEM4A | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270
AMEM4B | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 275
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARK11 | 0.1646 | 8.0383 | -0.1808 | 211
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 258
BEDD21 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 240
BEDD21 | BEDT1A | 0.2264 | 12.2479 | -0.6062 | 126
BEDD22 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 240
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD23 | BEDT1B | 0.2264 | 12.2479 | -0.6062 | 126
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 867
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 273
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT4A | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT4B | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 277
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 276
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 278
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 278
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 312
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRFO41 | BRFO1* | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 272
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 271
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1096
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270
BRLE41 | BRLE1A | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE1B | 0.1303 | 7.8698 | -0.4285 | 263
BRWA2A | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BURW41 | BURW11 | 0.1372 | 8.0197 | -0.1238 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 240
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 278
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 265
BUST41 | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST41 | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT11 | 0.1658 | 8.426 | -0.2939 | 264
CANT41 | CANT12 | 0.1509 | 8.2849 | -0.3279 | 264
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 279
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 180
CAPE41 | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886
CAPE42 | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272
CARR4A | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CARR4B | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 280
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 273
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 278
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 255
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 249
CHSI21 | CHSI11 | 0.2264 | 12.2479 | -0.6062 | 126
CHSI21 | CHSI11 | 0.2264 | 12.2479 | -0.6062 | 126
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 251
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 278
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 251
CILF41 | CILF2A | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF2B | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277
CITR41 | CITR12 | 0.0997 | 8.0088 | -0.093 | 266
CONQ41 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259
CONQ41 | CONQ12 | 0.1045 | 7.8806 | -0.0998 | 240
CONQ41 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 279
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 266
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 849
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EASO41 | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
EASO41 | EASO12 | 0.103 | 7.9231 | -0.0638 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 272
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211
ELST21 | ELST12 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST13 | 0.1985 | 8.1167 | -0.4624 | 189
ELST21 | ELST13 | 0.1954 | 8.0796 | -0.2295 | 189
ELST21 | ELST1A | 0.3567 | 11.136 | -0.7303 | 126
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 212
ELST22 | ELST11 | 0.1923 | 8.081 | -1.4418 | 189
ELST22 | ELST1B | 0.3567 | 11.136 | -0.7303 | 127
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1100
ELST4B | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139
FECK41 | FECK21 | 0.0211 | 1.6463 | -14.2471 | 1114
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FERR21 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR21 | FERR61 | 0.237 | 10.8633 | -0.263 | 204
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278
FERR4A | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR4A | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113
FIDF21 | FIDF12 | 0.2847 | 12.2467 | -1.4346 | 120
FIDF21 | FIDF13 | 0.1594 | 8.6081 | -0.2215 | 261
FIDF22 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271
FIDF23 | FIDF11 | 0.2847 | 12.2467 | -1.4346 | 120
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 240
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 240
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 300
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 146
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD1A | 0.054 | 4.8906 | -0.1253 | 499
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063
FROD41 | WEAV71 | 0.3209 | 20.5475 | -0.1224 | 80
FROD41 | WEAV71 | 0.3209 | 20.5475 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN12 | 0.1035 | 7.8472 | -0.0758 | 240
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268
HACK2A | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK2B | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK2A | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 137
HARK22 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 0.0321 | 2.4344 | -0.0528 | 555
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK22 | 0.0292 | 2.402 | -0.2732 | 573
HARK41 | HARK22 | 0.0376 | 2.3797 | -3.9009 | 547
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 191
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1063
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2750
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 539
HINP41 | HINP21 | 0.0376 | 2.3797 | -3.9009 | 507
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 279
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 279
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 217
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 250
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 278
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 279
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 265
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 125
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER22 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER4A | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1135
IVER4A | IVER22 | 0.0326 | 2.3798 | -3.9003 | 500
IVER4B | IVER21 | 0.0326 | 2.3798 | -3.9003 | 500
IVER4B | IVER23 | 0.0132 | 1.4627 | -2.0624 | 841
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 276
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 256
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278
KEAD4C | KEAD41 | 0.0002 | 0.2873 | 0 | 2750
KEAD4D | KEAD41 | 0.0002 | 0.4178 | 0 | 2750
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 257
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 236
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 240
KIBY22 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261
KIBY22 | KIBY11 | 0.1681 | 8.3396 | -1.4878 | 211
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 278
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 269
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 279
KIRK21 | KIRK11 | 0.1575 | 8.0988 | -0.027 | 266
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264
KIRK2A | KIRK21 | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
LACK41 | LACK2C | 0.0174 | 1.598 | -0.1503 | 1154
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 240
LEGA4A | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEGA4B | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEIS4A | LEIS11 | 0.103 | 7.9231 | -0.0638 | 272
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 267
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 253
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 240
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 240
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 274
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 884
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 279
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 240
MELK41 | MELK1* | 0.1041 | 7.8535 | -0.0851 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MELK41 | MELK2B | 0 | 1.692 | 0 | 886
MILH21 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH21 | MILH11 | 0.179 | 8.3648 | -4.7616 | 211
MILH21 | MILH12 | 0.1266 | 8.6449 | -1.9406 | 264
MILH21 | MILH12 | 0.179 | 8.3648 | -4.7616 | 199
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 263
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 240
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 263
MITY41 | MITY12 | 0.137 | 7.9818 | -0.1471 | 240
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1138
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 270
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 269
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 272
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 886
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2C | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 187
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF12 | 0.1509 | 7.9378 | -0.9251 | 253
NORL2A | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORL2B | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORM41 | NORW11 | 0.1509 | 7.9378 | -0.9251 | 253
NORM41 | NORW11 | 0.1307 | 7.9515 | -0.1098 | 240
NORM41 | NORW13 | 0.1509 | 7.9378 | -0.9251 | 267
NORM41 | NORW1C | 0.1264 | 8.4534 | -0.357 | 277
NORM41 | NORW1D | 0.1118 | 8.3874 | -0.0906 | 278
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 280
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 253
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 252
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 262
OCKH21 | OCKH1* | 0.179 | 8.3648 | -4.7616 | 202
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH2A | OCKH21 | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 100
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 115
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB4A | OLDB21 | 0.0146 | 1.609 | -1.8746 | 1115
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 274
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 240
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN4A | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138
PENN4B | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 257
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255
PEWO2A | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO2B | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278
PEWO41 | PEWO21 | 0.021 | 1.669 | -12.6082 | 876
PEWO41 | PEWO22 | 0.0189 | 1.6132 | -0.7226 | 1129
PEWO41 | PEWO22 | 0.0178 | 1.5995 | -1.2431 | 845
PEWO41 | PEWO2B | 0.0175 | 1.5879 | -4.0069 | 1139
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 120
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 110
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 279
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270
RATS41 | RATS11 | 0.103 | 7.9231 | -0.0638 | 262
RATS41 | RATS11 | 0.1046 | 7.8493 | -0.0881 | 240
RATS41 | RATS12 | 0.1373 | 8.1976 | -0.1719 | 278
RATS41 | RATS12 | 0.1278 | 8.0061 | -0.2276 | 277
RATS41 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 278
RAYL41 | RAYM11 | 0.1309 | 7.8656 | -0.4549 | 262
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240
RAYL41 | RAYM11 | 0.1759 | 7.9134 | -0.267 | 240
REBR21 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132
REBR21 | REBR31 | 0.665 | 28.1922 | -0.151 | 112
REBR22 | REBR32 | 0.665 | 28.1922 | -0.151 | 111
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH12 | 0.2847 | 12.2467 | -1.4346 | 140
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RYEH41 | RYEH13 | 0.1372 | 8.0197 | -0.1238 | 253
RYEH4A | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260
RYEH4B | RYEH12 | 0.1326 | 8.774 | -0.7141 | 260
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1307 | 7.9515 | -0.1098 | 276
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273
SELL41 | SELL12 | 0.103 | 7.9231 | -0.0638 | 270
SELL41 | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 269
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 240
SJOW21 | SJOW13 | 0.1441 | 8.6238 | -0.2707 | 251
SJOW41 | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 270
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 804
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 279
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN42 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 240
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL11 | 0.2188 | 8.097 | -1.9861 | 280
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 279
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189
STAL41 | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271
STAY4A | STAY41 | 0.0002 | 0.4178 | -13.831 | 2750
STEW21 | STEN11 | 0.3392 | 11.9012 | -0.7294 | 141
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 274
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1172
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STSB4A | STSB41 | 0.0003 | 0.1825 | 0 | 1999
SUND41 | SUND11 | 0.1303 | 7.8698 | -0.4285 | 278
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250
SWAN21 | SWAN11 | 0.1646 | 8.0383 | -0.1808 | 211
SWAN21 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 240
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210
SWAN4A | SWAN21 | 0.0178 | 1.5995 | -1.2431 | 851
TAUN42 | TAUN11 | 0.1759 | 7.9134 | -0.267 | 279
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
THOM21 | THOM61 | 0.3985 | 16.203 | -0.4431 | 122
THOM41 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 879
THOM41 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879
THOM42 | THOM21 | 0.0152 | 1.6463 | -0.1118 | 1100
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 180
TILB21 | TILB11 | 0.3792 | 12.0524 | -0.3982 | 131
TILB21 | TILB12 | 0.3792 | 12.0524 | -0.3982 | 134
TILB41 | TILB13 | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 1153
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102
TINP21 | TINP32 | 0.4758 | 20.0944 | -0.4489 | 111
TINP21 | TINP34 | 0.5083 | 24.0899 | -0.1921 | 135
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP22 | TINP33 | 0.5083 | 24.0899 | -0.1921 | 172
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 139
TOTT21 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265
TOTT22 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198
TOTT23 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT24 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 279
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 262
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 222
UPPB22 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 105
UPPB22 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 105
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 312
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 263
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 266
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 253
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 240
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 240
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 274
WALX4A | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4B | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1137
WALX4B | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1137
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264
WASF21 | WASF1A | 0.197 | 7.9698 | -0.2553 | 207
WASF22 | WASF1B | 0.197 | 7.9698 | -0.2553 | 207
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 279
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 139
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 264
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 263
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 271
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263
WHAM4A | WHAM41 | 0.001 | 0.35 | 0 | 2000
WHAM4B | WHAM41 | 0.001 | 0.35 | 0 | 2000
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO32 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.5913 | 19.0842 | -0.4269 | 100
WHSO4A | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIEN21 | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 296
WIEN21 | WIEN11 | 0.1594 | 8.6081 | -0.2215 | 288
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278
WILE41 | WILL21 | 0.0268 | 2.7989 | -0.3188 | 686
WILL21 | WILL11 | 0.2847 | 12.2467 | -1.4346 | 140
WILL21 | WILL12 | 0.2847 | 12.2467 | -1.4346 | 140
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206
WIMB21 | WIMB11 | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB12 | 0.1845 | 7.8956 | -0.1938 | 249
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 249
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WLSD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949
WLSD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 1000
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197
WTHU4* | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.2188 | 8.097 | -1.9861 | 280
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250
WWEY22 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 202
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY4A | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY4A | WWEY22 | 0.0185 | 1.614 | -0.5638 | 886
WWEY4B | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845
WWEY4B | WWEY23 | 0.0178 | 1.5995 | -1.2431 | 845
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273

## B-3-1d
B.3.1d- OFTO Transformers for 2020/21
OFTO | Site | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
Hornsea One Limited | Hornsea 1 Wind Farm | HOWA41 | HOWA21 | 0.016279 | 2.6767 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWW21 | HOWW31 | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW21 | HOWW31 | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW22 | HOWW32 | 0.0875 | 5.925 | 0 | 240 | 220/34
|  | HOWW22 | HOWW32 | 0.0875 | 5.925 | 0 | 240 | 220/34
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HEDO21 | HUMO11 | 0.1875 | 11.4375 | 0 | 160 | 275/132/33
|  | HEDO21 | HUMO12 | 0.1875 | 11.4375 | 0 | 160 | 275/132/33
|  | HUMO11 | HUMW31 | 0.23192 | 8.5714 | 0 | 140 | 132/33
|  | HUMO12 | HUMW32 | 0.23192 | 8.5714 | 0 | 140 | 132/33
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW11 | BOSW31 | 0.316 | 15.0833 | 0 | 120 | 132/33
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | BBWO21 | 0.08075 | 5.8994 | -0.1779 | 200 | 400/220/15.5
|  | BBWO41 | BBWO21 | 0.07975 | 5.7994 | -0.1779 | 200 | 400/220/15.5
|  | BBWW21 | BBWW31 | 0.11508 | 6.0889 | -0.8147 | 200 | 220/34
|  | BBWW21 | BBWW32 | 0.11573 | 6.0739 | -0.8147 | 200 | 220/34
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDW31 | 0.13 | 6 | 0 | 200 | 132/33
|  | DUDW12 | DUDW32 | 0.13 | 6 | 0 | 200 | 132/33
|  | NECT41 | DUDO11 | 0.09 | 6 | -0.2956 | 200 | 400/132/33
|  | NECT41 | DUDO11 | 0.09 | 6 | -0.2956 | 200 | 400/132/33
East Anglia One Limited | East Anglia Offshore Wind Farm | BRST41 | BRST21 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | BRST41 | BRST21 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | EAAW21 | EAAW61 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW22 | EAAW62 | 0.1037 | 7.035 | 0 | 200 | 220/66
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GANW11 | GANW31 | 0.003778 | 0.12122 | 0 | 180 | 132/33/33
|  | GANW12 | GANW32 | 0.003778 | 0.12222 | 0 | 180 | 132/33/33
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMW11 | ORMW31 | 0.464 | 14.421 | 0 | 85 | 132/33
|  | ORMW11 | ORMW32 | 0.465 | 14.479 | 0 | 85 | 132/33
|  | ORMO11 | ORMO31 | 0.348 | 13.465 | 0 | 110 | 132/33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SSAW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSAW11 | SSAW32 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW32 | 0.23 | 12.07 | 0 | 90 | 132/33
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNW21 | TKNW61 | 0.07 | 3.33 | 0 | 420 | 220/66
|  | TKNO41 | TKNO21 | 0.036 | 3.78 | 0 | 450/450/260 | 400/220/33
|  | TKNO41 | TKNO21 | 0.036 | 3.78 | 0 | 450/450/260 | 400/220/33
Diamond Transmission Partners Walney Extension Limited | Walney Extension Wind Farm | WACW21 | WACW31 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WACW21 | WACW32 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WADW21 | WADW31 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WADW21 | WADW32 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WOWE41 | WOWE21 | 0.0255 | 2.617 | 0 | 470 | 400/227
|  | WOWE42 | WOWE22 | 0.0255 | 2.617 | 0 | 470 | 400/227
WoDS Transmission plc | West of Duddon Sands | WDSO41 | WDSO11 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
|  | WDSO42 | WDSO12 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
|  | WDSW11 | WDSW31 | 0.20833 | 5 | 0 | 240 | 155/34
|  | WDSW12 | WDSW32 | 0.20833 | 5 | 0 | 240 | 155/34
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO21 | WERO11 | 0.09 | 6.62 | 0 | 180/180/110 | 275/150/34
|  | WERO22 | WERO11 | 0.09 | 6.58 | 0 | 180/180/110 | 275/150/34
|  | WERW11 | WERW31 | 0.12 | 7.14 | 0 | 140 | 150/34
|  | WERW11 | WERW32 | 0.12 | 7.14 | 0 | 140 | 150/34
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GANW14 | GANW3A | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GANW14 | GANW3B | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GREG11 | GREG31/GREG32 | 0.4 | 23.44 | 0 | 180/90/90 | 132/33/33
|  | GREG12 | GREG33 | 0.4 | 23.44 | 0 | 180/90/90 | 132/33/33
|  | GREG13 | GREG34/GREG35 | 0.4 | 23.44 | 0 | 180/90/90 | 132/33/33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | LONO11 | 0.33 | 6.4556 | 0 | 180/180/90 | 400/150/13.9
|  | LONO42 | LONO12 | 0.33 | 6.4111 | 0 | 180/180/90 | 400/150/13.9
|  | LONO41 | LONO13 | 0.33 | 6.4611 | 0 | 180/180/90 | 400/150/13.9
|  | LONO42 | LONO14 | 0.33 | 6.4389 | 0 | 180/180/90 | 400/150/13.9
|  | LOAW11 | LOAW31 | 0.402 | 6.56 | 0 | 180 | 150/33
|  | LOAW12 | LOAW32 | 0.4045 | 6.57 | 0 | 180 | 150/33
|  | LOAW13 | LOAW33 | 0.407 | 6.58 | 0 | 180 | 150/33
|  | LOAW14 | LOAW34 | 0.4045 | 6.57 | 0 | 180 | 150/33
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | BODE41 | GWYO11 | 0.054688 | 3.5313 | 0 | 320/320/60 | 400/132/13.9
|  | BODE42 | GWYO12 | 0.054688 | 3.5313 | 0 | 320/320/60 | 400/132/13.9
|  | GWAW11 | GWAW31 | 0.15625 | 11.3313 | 0 | 160 | 132/33
|  | GWAW12 | GWAW32 | 0.15625 | 11.3625 | 0 | 160 | 132/33
|  | GWBW11 | GWBW31 | 0.15625 | 11.3438 | 0 | 160 | 132/33
|  | GWBW12 | GWBW32 | 0.15625 | 11.375 | 0 | 160 | 132/33
TC Beatrice OFTO Limited | Beatrice Wind Farm | BEAT41 | BEAT21 | 0.173 | 16.03 | 0 | 320/320/170 | 400/220/33
|  | BEAT42 | BEAT22 | 0.173 | 16.03 | 0 | 320/320/170 | 400/220/33
|  | BEIW21 | BEIW31 | 0.235 | 17.5 | 0 | 310 | 220/33
|  | BEIW22 | BEIW32 | 0.235 | 17.5 | 0 | 310 | 220/33
TC Lincs OFTO Limited | Lincs Wind Farm | LINO41 | LINO11 | 0.11 | 14 | 0 | 300/300/115 | 400/132/13
|  | LINO42 | LINO12 | 0.11 | 14 | 0 | 300/300/115 | 400/132/13
|  | LINS11 | LINS31 | 0.22 | 12 | 5.83 | 240 | 132/33
|  | LINS12 | LINS32 | 0.22 | 12 | 5.83 | 240 | 132/33
Diamond Transmission Partners RB Limited | Race Bank Offshore Wind Farm | RACO41 | RACO21 | 0.03165 | 3.1526 | 0 | 360 | 400/220
|  | RACO42 | RACO22 | 0.031779 | 3.1582 | 0 | 360 | 400/220
|  | RACW21 | RACW31 | 0.11449 | 6.0389 | 0 | 200 | 220/34
|  | RACW21 | RACW32 | 0.11465 | 6.0789 | 0 | 200 | 220/34
|  | RACW21 | RACW33 | 0.11476 | 6.0989 | 0 | 200 | 220/34
|  | RACW21 | RACW34 | 0.11435 | 6.0689 | 0 | 200 | 220/34
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | RAMW11 | RAMW3A | 0.33 | 12.23 | -0.144 | 240 | 150/33
|  | RAMW12 | RAMW3B | 0.33 | 12.76 | -0.144 | 240 | 150/33
|  | TWNE41 | TWNE11 | 0.17 | 12.24 | -1.9406 | 240 | 400/150/33
|  | TWNE42 | TWNE12 | 0.17 | 12.74 | -1.9406 | 240 | 400/150/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW11 | THOW31/33 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
|  | THOW12 | THOW32/34 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAW11 | WAAW3A | 0.42 | 8.75 | 0 | 120 | 132/33
|  | WAAW11 | WAAW3B | 0.42 | 8.75 | 0 | 120 | 132/33
Blue Transmission Walney 2 OFTO | Walney 2 Offshore Wind Farm | WABW11 | WABW3A | 0.2395 | 8.2882 | 0 | 120 | 132/33
|  | WABW11 | WABW3B | 0.2432 | 8.3214 | 0 | 120 | 132/33

## B-3-2a
B.3.2a - SHE TransmissionTransformer Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABED1- | ABED3- | 2021 | Addition | 0.33 | 21.7 | 0 | 60
ABNE1Q | ABNE3- | 2021 | Change | 0.2621 | 24.6736 | -0.0222 | 120
ABNE1R | ABNE3- | 2021 | Change | 0.2614 | 24.7403 | -0.0197 | 120
FARI2K | FARI1K | 2021 | Change | 0.2184 | 8.2304 | -0.0007 | 240
FAUG1Q | FAUG3- | 2021 | Change | 1.1951 | 25.0827 | -0.0007 | 45
FAUG4- | FAUG1- | 2021 | Remove | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 2021 | Remove | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1J | 2021 | Addition | 0.108 | 3.957 | -0.0007 | 480
FAUG4K | FAUG1K | 2021 | Addition | 0.108 | 3.957 | -0.0007 | 480
GLKO1- | GLKO3J | 2021 | Addition | 0.36 | 18 | 0 | 60
LIMK1- | LIMK3- | 2021 | Addition | 0.36 | 18 | 0 | 120
LOCH1- | LOCH5J | 2021 | Change | 1.968 | 79.976 | -0.0008 | 36
LOCH1- | LOCH5K | 2021 | Change | 1.968 | 79.976 | -0.0008 | 36
PORA1Q | PORA3- | 2021 | Remove | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 2021 | Remove | 1.803 | 29.812 | 0 | 30
PORA1T | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
ROTI2J | ROTI3- | 2021 | Addition | 0.21 | 24.52 | 0 | 120
ROTI2J | ROTI3- | 2021 | Addition | 0.21 | 24.52 | 0 | 120
SFEG1Q | SFEG5- | 2021 | Change | 1.5768 | 75.5085 | -0.0328 | 40
SFEG1R | SFEG5- | 2021 | Change | 1.5768 | 75.5085 | -0.0328 | 40
CAAD1Q | CAAD3J | 2022 | Change | 0.0026 | 0.2467 | -0.0002 | 120
CAAD1R | CAAD3J | 2022 | Change | 0.0026 | 0.2467 | -0.0002 | 120
MILS1Q | MILS3J | 2022 | Addition | 0.0036 | 0.18 | 0 | 60
ARBR1Q | ARBR3- | 2024 | Change | 0.3974 | 24.7301 | -0.0007 | 90
ARBR1R | ARBR3- | 2024 | Change | 0.4015 | 24.819 | -0.0194 | 90
BEAU2J | BEAU1J | 2024 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BEAU2J | BEAU1J | 2024 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BEAU2K | BEAU1K | 2024 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BEWF1- | BEWF3- | 2024 | Addition | 0.36 | 18 | 0 | 90
BLEX1- | BLEX3- | 2024 | Addition | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 2024 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
BLHI2K | BLHI1K | 2024 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
BLHI4- | BLHI2L | 2024 | Remove | 0.0252 | 1.1997 | -0.0005 | 1200
BLHI4- | BLHI2M | 2024 | Remove | 0.0253 | 1.2081 | -0.0005 | 1200
CDWE1- | CDWE3- | 2024 | Addition | 0.9 | 18 | 0 | 60
CONN2J | CONN1J | 2024 | Change | 0.218 | 8.23 | -0.0007 | 240
CORI1J | CORI3J | 2024 | Change | 1 | 20 | 0 | 90
CRDH2J | CRDH1J | 2024 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRDH2K | CRDH1K | 2024 | Addition | 0.098 | 3.936 | -0.0006 | 480
CREA1- | CREA3- | 2024 | Addition | 0.4 | 20 | 0 | 90
ENEI1- | ENEI3- | 2024 | Addition | 0.08 | 4 | 0 | 150
KINT4J | KINT2K | 2024 | Addition | 0.0252 | 1.1997 | -0.0005 | 1200
KINT4K | KINT2J | 2024 | Addition | 0.0253 | 1.2081 | -0.0005 | 1200
LYND1Q | LYND3- | 2024 | Change | 0.5 | 25 | 0 | 120
LYND1R | LYND3- | 2024 | Change | 0.5 | 25 | 0 | 120
MSHL1- | MSHL3- | 2024 | Addition | 0.36 | 17.9968 | 0 | 90
PEHE4J | PEHE2Q | 2024 | Addition | 0.026 | 1.533 | -0.0005 | 1200
PEHE4K | PEHERSV1 | 2024 | Addition | 0.026 | 1.533 | -0.0005 | 1200
PEHG1Q | PEHG3- | 2024 | Change | 0.5 | 25 | 0 | 90
PEHG1R | PEHG3- | 2024 | Change | 0.5 | 25 | 0 | 90
PENF1- | PENF3A | 2024 | Addition | 0.252 | 12.6 | 0 | 60
REDM1Q | REDM3- | 2024 | Change | 0.3974 | 24.7301 | -0.0007 | 90
REDM1R | REDM3- | 2024 | Change | 0.4015 | 24.819 | -0.0194 | 90
ROTI1J | ROTI3- | 2024 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI1K | ROTI3- | 2024 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI2J | ROTI3- | 2024 | Remove | 0.21 | 24.52 | 0 | 120
ROTI2J | ROTI3- | 2024 | Remove | 0.21 | 24.52 | 0 | 120
ROTI4J | ROTI1J | 2024 | Addition | 0.2149 | 8.0138 | -0.013 | 240
ROTI4K | ROTI1K | 2024 | Addition | 0.2149 | 8.0138 | -0.013 | 240
SLOY1L | SLOY5L | 2024 | Change | 0.79 | 23.08 | 0 | 60
SLOY1M | SLOY5M | 2024 | Change | 0.79 | 22.9 | 0 | 60
SLOY1N | SLOY5N | 2024 | Change | 0.79 | 22.98 | 0 | 60
SLOY1P | SLOY5P | 2024 | Change | 0.8 | 23.2 | 0 | 60
TEAL2A | TEAL2J | 2024 | Addition | 0.005 | 0.4 | 0 | 700
TEAL2B | TEAL2K | 2024 | Addition | 0.005 | 0.4 | 0 | 700
ACHR1R | ACHR3- | 2026 | Remove | 0.36 | 18 | 0 | 90
ACHR2- | ACHR3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
AIGA1Q | AIGA5- | 2026 | Change | 1.76 | 44.89 | 0 | 30
ALYT4J | ALYT2A | 2026 | Addition | 0.017 | 1.59 | -0.0005 | 1000
ALYT4K | ALYT2B | 2026 | Addition | 0.017 | 1.59 | -0.0005 | 1000
ANSU1- | ANSU3- | 2026 | Remove | 0.817 | 27.121 | 0 | 45
ANSU2- | ANSU3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
ARNI1K | ARNI3- | 2026 | Addition | 0.36 | 18 | 0 | 60
BLHI2J | BLHI2A | 2026 | Addition | 0.005 | 0.4 | 0 | 865
BLHI2K | BLHI2B | 2026 | Addition | 0.005 | 0.4 | 0 | 865
BROA1- | BROA3- | 2026 | Addition | 0.5 | 25 | 0 | 45
BROA1- | BROA3- | 2026 | Addition | 1.19 | 39 | 0 | 30
BROA1Q | BROA3- | 2026 | Remove | 1.19 | 39 | 0 | 30
CLGO1- | CLGO3- | 2026 | Addition | 0.36 | 18 | 0 | 270
CLGO2- | CLGO1- | 2026 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CLGO2A | CLGO1- | 2026 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CLOI11 | CLOI3- | 2026 | Addition | 0.36 | 18 | 0 | 120
CLOI11 | CLOI3- | 2026 | Addition | 0.36 | 18 | 0 | 120
CONN2J | CONN1J | 2026 | Remove | 0.218 | 8.23 | -0.0007 | 240
CONN2J | CONN1K | 2026 | Addition | 0.143 | 5.3036 | -0.0006 | 360
CONN2K | CONN1J | 2026 | Addition | 0.218 | 8.23 | -0.0007 | 240
CRSS1J | CRSS1Q | 2026 | Remove | 0.0582 | 2.145 | 0 | 240
CRSS1K | CRSS1R | 2026 | Remove | 0.0582 | 2.1492 | 0 | 240
CRSS2J | CRSS1Q | 2026 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRSS2K | CRSS1R | 2026 | Addition | 0.098 | 3.936 | -0.0006 | 480
CULL1Q | CULL5- | 2026 | Change | 1.46 | 37.6 | 0 | 30
DEAN1Q | DEAN5- | 2026 | Change | 1.01 | 25.1 | 0 | 45
DOUN2- | DOUN2A | 2026 | Addition | 0.066 | 5.333 | 0 | 360
DOUN2- | DOUN2D | 2026 | Addition | 0.066 | 5.333 | 0 | 360
DRUL1- | DRUL3- | 2026 | Addition | 0.36 | 18 | 0 | 60
DUNO1Q | DUNO3- | 2026 | Change | 0.4697 | 26.318 | 0 | 90
DUNO1R | DUNO3- | 2026 | Change | 0.4697 | 26.318 | 0 | 90
EDIN1- | GLNU3- | 2026 | Addition | 0.36 | 18 | 0 | 60
ELCH1- | ELCH3- | 2026 | Addition | 0.75 | 15 | 0 | 120
ENEI1- | ENEI3A | 2026 | Addition | 0.36 | 18 | 0 | 60
FETT2R | FETT1- | 2026 | Remove | 0.217 | 4.2737 | -0.0006 | 240
FETT4J | FETT1- | 2026 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FETT4K | FETT1- | 2026 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FINS1- | COST3- | 2026 | Addition | 0.54 | 18 | 0 | 45
FINS1- | FINS3- | 2026 | Addition | 0.451 | 25 | 0 | 120
FINS1- | FINS3- | 2026 | Addition | 0.451 | 25 | 0 | 120
FINS1- | HEST3- | 2026 | Addition | 0.54 | 18 | 0 | 45
FINS2A | FINS1- | 2026 | Addition | 0.044 | 5.833 | 0 | 360
FINS2D | FINS1- | 2026 | Addition | 0.044 | 5.833 | 0 | 360
GLEN1Q | GLEN5- | 2026 | Change | 0.55 | 21.94 | 0 | 90
GLSH1J | GLSH31 | 2026 | Addition | 0.6 | 17.4 | 0 | 120
GLSH1J | GLSH32 | 2026 | Addition | 0.6 | 17.4 | 0 | 120
INGA4J | INGA1K | 2026 | Addition | 0.131 | 7.952 | -0.11 | 240
INGA4K | INGA1J | 2026 | Addition | 0.131 | 7.952 | -0.11 | 240
KINT1- | KINT3- | 2026 | Remove | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 2026 | Change | 0.36 | 18 | 0 | 120
KINT2K | KINT1- | 2026 | Change | 0.3751 | 10.2314 | -0.015 | 240
KIOR1Q | KIOR5- | 2026 | Change | 1.78 | 45.42 | 0 | 36
MELG4J | MELG1J | 2026 | Addition | 0.108 | 3.957 | -0.0007 | 480
MELG4K | MELG1K | 2026 | Addition | 0.106 | 3.957 | -0.0007 | 480
MUAI1- | MUAI3A | 2026 | Addition | 0.36 | 18 | 0 | 90
MUAI1- | MUAI3B | 2026 | Addition | 0.36 | 18 | 0 | 90
PENF1B | PENF3B | 2026 | Addition | 3.6 | 18 | 0 | 96
PORA1T | PORA3- | 2026 | Remove | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 2026 | Remove | 1.803 | 29.812 | 0 | 30
PORA2J | PORA3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
PORA2K | PORA3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
SALA1- | SALA3- | 2026 | Addition | 0.36 | 17.99 | 0 | 90
SFIL1Q | SFIL5- | 2026 | Change | 1.99 | 39.48 | 0 | 45
SHDM1- | SHDM3- | 2026 | Addition | 0.3629 | 18.0297 | 0 | 90
STRW13 | STRW33 | 2026 | Addition | 0.5 | 25 | 0 | 90
STRW13 | STRW34 | 2026 | Addition | 0.5 | 25 | 0 | 90
STRW1C | STRW35 | 2026 | Addition | 0.36 | 18 | 0 | 120
STWN1- | STWN3J | 2026 | Addition | 0.36 | 18 | 0 | 90
STWN1- | STWN3K | 2026 | Addition | 0.36 | 18 | 0 | 90
TUMB1Q | TUMB5- | 2026 | Change | 1.63 | 77.76 | 0 | 45
TUMB1R | TUMB5- | 2026 | Change | 1.63 | 77.76 | 0 | 45
ALTN1- | ALTN3- | 2029 | Addition | 0.36 | 18 | 0 | 90
BETH1C | BETH3A | 2029 | Addition | 0.24 | 18 | 0 | 120
BLGH1- | BLGH3- | 2029 | Addition | 0.36 | 17.9968 | 0 | 90
CAID2- | CAID3- | 2029 | Addition | 0.36 | 18 | 0 | 120
COGA1- | COGA3A | 2029 | Addition | 0.324 | 17.9 | 0 | 120
DOUN4J | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN4J | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN4K | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN4K | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
LAIR1Q | LAIR3A | 2029 | Addition | 0.36 | 18 | 0 | 60
PENF1C | PENF3C | 2029 | Addition | 3.6 | 18 | 0 | 96

## B-3-2b
B.3.2b - SPT Transformer Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
DONO1- | DONO3- | 2021 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
MIDM1- | KENE3- | 2021 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
CHAS2Q | CHAS3A | 2022 | Addition | 0.5214 | 27.5617 | -0.1031 | 120
CUMH1- | CUMH3A | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
ELVA1- | ELVA3A | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
ELVA2R | ELVA1- | 2022 | Addition | 0.0984 | 5.8325 | -0.2121 | 360
HOPR1- | HOPR3A | 2022 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
KYPE1- | HARG3- | 2022 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
MAHI2- | MAHI1B | 2022 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1164 | 8.5534 | -0.0287 | 240
NECU2- | NECU1C | 2022 | Addition | 0.1111 | 6.6657 | -0.0006 | 360
NECU2- | NECU1C | 2022 | Addition | 0.1111 | 6.6657 | -0.0006 | 360
NEIL4R | NEIL2- | 2022 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
SAKN1- | SAKN3- | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
SOKY1- | SOKY3- | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
SOKY1- | SOKY3- | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CHAS2Q | CHAS3C | 2022 | Remove | 0.4875 | 18.1601 | -0.1331 | 120
COYL2- | COYL1- | 2022 | Change | 0.1476 | 8.7488 | -0.1299 | 240
COYL2- | COYL1- | 2022 | Change | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1Q | 2022 | Remove | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 2022 | Remove | 0.1164 | 8.5534 | -0.0287 | 240
AREX1- | AREX3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
BENB1- | BENB3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
ENHI1- | ENHI3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
FALL4- | FALL3C | 2024 | Addition | 0.2564 | 16.6647 | 0 | 120
MOFF1- | MOFF3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
NETS1- | NETS3- | 2024 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
REDH1- | REDH3- | 2024 | Change | 0.6267 | 27.5484 | 0 | 90
COAL4- | COAL1A | 2024 | Remove | 0.0914 | 6.4382 | -0.0751 | 360
COAL4- | COAL1B | 2024 | Addition | 0.0914 | 6.4382 | -0.0751 | 360
COAL4- | COAL1B | 2024 | Addition | 0.0914 | 6.4382 | -0.0751 | 360
CRCK2- | CRCK3- | 2024 | Addition | 0.2857 | 19.998 | 0 | 90
CUMW1- | CUMW3- | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DONO1- | DONO3A | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GNSH1- | GNSH3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
HOPR1- | CRDE3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
KENN1- | KENN3- | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
LORG1- | LORG3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
NLEI1- | NLEI3A | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NLEI1- | NLEI3B | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NOKY1- | NOKY3A | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
NOKY1- | NOKY3B | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
OHLL1- | OHLL3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
SHRG1- | SHRG3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
STNO1- | STNO3- | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CLAU1- | CLAU3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
DENN4- | DENN2- | 2026 | Addition | 0.0164 | 1.6449 | -0.1161 | 1000
EUCH1- | EUCH3- | 2026 | Addition | 0.1922 | 14.207 | -0.0113 | 120
KINC4A | KINC2- | 2026 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
KINC4B | KINC2- | 2026 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
KNOK1- | KNOK3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
KNOK1- | KNOK3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
LEGO1Q | LEGO3- | 2026 | Addition | 0.3119 | 21.8311 | 0 | 60
LEGO1R | LEGO3- | 2026 | Addition | 0.3119 | 21.8311 | 0 | 60
MAHI2- | MAHI1C | 2026 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
MOFF4- | MOFF1- | 2026 | Addition | 0.1483 | 10.0614 | -0.3432 | 240
PORD2R | PORD3- | 2026 | Change | 0.2857 | 31.1098 | 0 | 90
STHA2A | STHA3- | 2026 | Change | 0.2857 | 31.1098 | 0 | 90
TONG1- | TONG1R | 2026 | Remove | 0.0267 | 1.3331 | 0 | 90
TONG1Q | TONG1R | 2026 | Remove | 0.0125 | 2.5 | 0 | 90
TRSN1- | TRSN3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
WGEO2R | WGEO3- | 2026 | Change | 0.2857 | 31.1098 | 0 | 90
BONN2A | BONN1- | 2029 | Remove | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 2029 | Remove | 0.1559 | 8.9445 | -0.1694 | 240
BONN4- | BONN1- | 2029 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
BONN4- | BONN1- | 2029 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
GHPS1- | GHPS3A | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GHPS1- | GHPS3B | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
OFOA1- | OFOA3- | 2029 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
WFIE1A | WFIE3- | 2029 | Change | 0.5296 | 27.1115 | -0.0073 | 60
WFIE1B | WFIE3- | 2029 | Change | 0.5296 | 27.1115 | -0.0073 | 60

## B-3-2c
B.3.2c - NGET Transformer Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ELST21 | ELST15 | 2021 | Remove | 0.3567 | 11.136 | -0.7303 | 126
ELST22 | ELST16 | 2021 | Remove | 0.3567 | 11.136 | -0.7303 | 127
SJOW41 | SJOW21 | 2021 | Addition | 0.0224 | 2.5703 | -0.5831 | 800
TAUN41 | TAUN11 | 2021 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
HARK41 | HARK21 | 2022 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK41 | HARK21 | 2022 | Remove | 0.0321 | 2.4344 | -0.0528 | 555
SJOW41 | SJOW21 | 2022 | Remove | 0.0224 | 2.5703 | -0.5831 | 800
BRWA2A | BRWA11 | 2024 | Remove | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 2024 | Remove | 0.167 | 7.9774 | -0.2092 | 255
BRWA4A | BRWA11 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
BRWA4B | BRWA11 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
HARK41 | HARK22 | 2024 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK41 | HARK22 | 2024 | Remove | 0.0376 | 2.3797 | -3.9009 | 547
SAFO41 | SAFO11 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
SAFO41 | SAFO12 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
SEAB41 | SEAB11 | 2024 | Remove | 0.1307 | 7.9515 | -0.1098 | 276
WIMB21 | WIMB11 | 2024 | Remove | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB12 | 2024 | Remove | 0.1845 | 7.8956 | -0.1938 | 249
WIMB41 | WIMB11 | 2024 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2024 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
BENR41 | BENR11 | 2026 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
BENR41 | BENR12 | 2026 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
LHOR4A | LEWE12 | 2026 | Addition | 0.1373 | 8.1976 | -0.1719 | 278
LHOR4B | LEWE11 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 278
NEWX41 | NEWX21 | 2026 | Addition | 0.0132 | 1.4627 | -2.0624 | 1100
NEWX42 | NEWX21 | 2026 | Addition | 0.0132 | 1.4627 | -2.0624 | 1100
HAWP41 | HAWP21 | 2029 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
POPP4A | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063
POPP4A | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063
POPP4B | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063
POPP4B | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063

## B-3-2d
B.3.2d - OFTO Transformer Changes 2021/22 to 2029/30
Wind Farm | Node 1 | Node 2 | Year | Status | Rating(MVA) | Voltage(kV)
Firth of Forth 1 Offshore Wind Farm | FOFW21 | FOFW61 | 2021 | Addition | 400 | 275/66
| FOFW22 | FOFW62 | 2021 | Addition | 400 | 275/66
| FOFW23 | FOFW63 | 2021 | Addition | 400 | 275/66
| FOFO21 | FOFO31 | 2021 | Addition | 320 | 275/33
| FOFO21 | FOFO32 | 2021 | Addition | 320 | 275/33
Hornsea 1 Offshore Wind Farm | HOWW23 | HOWW33 | 2021 | Addition | 240 | 220/34
| HOWW23 | HOWW33 | 2021 | Addition | 240 | 220/34
Moray East Offshore Wind Farm | MOWE21 | MOWE61 | 2021 | Addition | 315 | 220/66
| MOWE22 | MOWE62 | 2021 | Addition | 315 | 220/66
| MOWE23 | MOWE63 | 2021 | Addition | 315 | 220/66
| Moray Firth 275kV -1 | MORF21 | 2021 | Addition | 340 | 275(400)/220
| Moray Firth 275kV -2 | MORF22 | 2021 | Addition | 340 | 275(400)/220
| Moray Firth 275kV -3 | MORF23 | 2021 | Addition | 340 | 275(400)/220
Triton Knoll Offshore Wind Farm | TKNE21 | TKNE61 | 2021 | Addition | 420 | 220/66
Inch Cape Offshore Wind Farm | INCW61 | INCW21 | 2022 | Addition | 550 | 66/220
| INCW62 | INCW22 | 2022 | Addition | 550 | 66/220
| INCO21 | INCO21 | 2022 | Addition | 550 | 220/275/LV
| INCO22 | INCO22 | 2022 | Addition | 550 | 220/275/LV
Neart Na Gaoithe Offshore Wind Farm | NNGW31 | NNGW21 | 2022 | Addition | 230 | 220/66
| NNGW32 | NNGW22 | 2022 | Addition | 230 | 220/66
| NNGO21 | NNGO41 | 2022 | Addition | 260/230/170 | 400/220/33
| NNGO22 | NNGO42 | 2022 | Addition | 260/230/170 | 400/220/33
Dogger bank 1 Offshore Wind Farm | Dogger bank 1A offshore 33kV | Dogger bank 1A offshore 220kV | 2024 | Addition | 280/140/140 | 220/33/33
| Dogger bank 1A offshore 33kV | Dogger bank 1A offshore 220kV | 2024 | Addition | 280/140/140 | 220/33/33
| Dogger bank 1B offshore 33kV | Dogger bank 1B offshore 220kV | 2024 | Addition | 280/140/140 | 220/33/33
| Dogger bank 1B offshore 33kV | Dogger bank 1B offshore 220kV | 2024 | Addition | 280/140/140 | 220/33/33
| Dogger bank offshore 220kV | Dogger bank offshore TBC | 2024 | Addition | TBC | 132/TBC
| Dogger bank onshore TBC | Dogger bank onshore 400kV | 2024 | Addition | TBC | 400/TBC
Doggerbank 4 Offshore wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore | 2024 | Addition | TBC | 220/TBC
| Doggerbank 4 Onshore | Doggerbank 4 Onshore 400kV | 2024 | Addition | TBC | TBC/400
East Anglia 3 Offshore Wind Farm | East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | 200 | 220/33/33
| East Anglia Offshore 220kV | East Anglia Offshore TBC | 2024 | Addition | TBC | 220/TBC
| East Anglia Onshore TBC | East Anglia Onshore 400kV | 2024 | Addition | TBC | 220/TBC
Hornsea 2 Offshore Wind Farm | Hornsea 2A Offshore 66kV | Hornsea 2A Offshore 220kV | 2024 | Addition | 270 | 220/66
| Hornsea 2A Offshore 66kV | Hornsea 2A Offshore 220kV | 2024 | Addition | 270 | 220/66
| Hornsea 2B Offshore 66kV | Hornsea 2B Offshore 220kV | 2024 | Addition | 270 | 220/66
| Hornsea 2B Offshore 66kV | Hornsea 2B Offshore 220kV | 2024 | Addition | 270 | 220/66
| Hornsea 2C Offshore 66kV | Hornsea 2C Offshore 220kV | 2024 | Addition | 270 | 220/66
| Hornsea 2C Offshore 66kV | Hornsea 2C Offshore 220kV | 2024 | Addition | 270 | 220/66
| Hornsea Onshore 220kV | Hornsea Onshore 400kV | 2024 | Addition | 470 | 400/220
| Hornsea Onshore 220kV | Hornsea Onshore 400kV | 2024 | Addition | 470 | 400/220
| Hornsea Onshore 220kV | Hornsea Onshore 400kV | 2024 | Addition | 470 | 400/220
Hornsea 3 Offshore Wind Farm | Hornsea 3A-1 Offshore 66kV | Hornsea 3A-1 Offshore 500kV | 2024 | Addition | 850 | 500/66
| Hornsea 3A-1 Onshore 500kV | Hornsea 3A Onshore 400kV | 2024 | Addition | 850 | 500/400
| Hornsea 3A-2 Onshore 500kV | Hornsea 3A Onshore 400kV | 2024 | Addition | 850 | 500/400
Moray West Offshore Wind Farm | Moray West Offshore P1 220kV | Moray West Offshore P1 66kV | 2024 | Addition | TBC | 220/66
| Moray West Offshore P2 220kV | Moray West Offshore P2 66kV | 2024 | Addition | TBC | 220/66
| Moray West Onshore 400kV | Moray West Onshore 220kV | 2024 | Addition | TBC | 400/220
| Moray West Onshore 400kV | Moray West Onshore 220kV | 2024 | Addition | TBC | 400/220
Sofia Offshore Wind Farm | Sofia Offshore TBC | Sofia offshore 66kV | 2024 | Addition | TBC | TBC/66
| Sofia Offshore TBC | Sofia offshore 66kV | 2024 | Addition | TBC | TBC/66
Dogger Bank 2 offshore Wind Farm | Offshore 220kV-1 | Offshore 66kV-1 | 2026 | Addition | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-2 | 2026 | Addition | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-3 | 2026 | Addition | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-4 | 2026 | Addition | TBC | 220/66
| Offshore-2 | Offshore 220kV-1 | 2026 | Addition | TBC | TBC
| Onshore-1 | Onshore 400kV | 2026 | Addition | TBC | TBC
Dogger Bank 4 Offshore Wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2026 | Addition | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2026 | Addition | 280/140/140 | 220/33/33
East Anglia 6A Offshore Wind Farm | East Anglia 6A Offshore-2 | East Anglia 6A Offshore-1 | 2026 | Addition | TBC | TBC
| East Anglia 6A Offshore-2 | East Anglia 6A Offshore-1 | 2026 | Addition | TBC | TBC
East Anglia 6B Offshore Wind Farm | East Anglia 6B Offshore-2 | East Anglia 6B Offshore-1 | 2026 | Addition | TBC | TBC
| East Anglia 6B Offshore-2 | East Anglia 6B Offshore-1 | 2026 | Addition | TBC | TBC
Firth of Forth 2 Offshore Wind Farm | Offshore 66KV-1 | Offshore 275kV-1 | 2026 | Addition | 430 | 275/66
| Offshore 66KV-2 | Offshore 275kV-2 | 2026 | Addition | 430 | 275/66
| Offshore 66KV-3 | Offshore 275kV-3 | 2026 | Addition | 430 | 275/66
| Onshore 275kV-1 | Onshore 400kV-1 | 2026 | Addition | 430 | 400/275
| Onshore 275kV-1 | Onshore 400kV-1 | 2026 | Addition | 430 | 400/275
| Onshore 275kV-1 | Onshore 400kV-1 | 2026 | Addition | 430 | 400/275
Hornsea 3 Offshore Wind Farm | Hornsea 3A-2 Offshore 66kV | Hornsea 3A-2 Offshore 500kV | 2026 | Addition | 850 | 500/66
| Hornsea 3B-1 Offshore 66kV | Hornsea 3B-1 Offshore 500kV | 2026 | Addition | 850 | 500/66
| Hornsea 3B-1 Onshore 500kV | Hornsea 3B Onshore 400kV | 2026 | Addition | 850 | 500/400
| Hornsea 3B-2 Onshore 500kV | Hornsea 3B Onshore 400kV | 2026 | Addition | 850 | 500/400
Sheringham and Dudgeon Extension Wind Farm | Offshore 66kV-1 | Offshore 220kV-1 | 2026 | Addition | 185 | 220/66
| Offshore 66kV-2 | Offshore 220kV-1 | 2026 | Addition | 185 | 220/66
| Offshore 66kV-3 | Offshore 220kV-2 | 2026 | Addition | 225 | 220/66
| Offshore 66kV-4 | Offshore 220kV-2 | 2026 | Addition | 225 | 220/66
| Onshore 220kV-1 | Onshore 400kV-1 | 2026 | Addition | 450 | 400/220
| Onshore 220kV-2 | Onshore 400kV-2 | 2026 | Addition | 450 | 400/220
Codling Wind Farm | Codling Offshore 220kV | Codling Offshore 33kV | 2029 | Addition | 280/140/140 | 220/33/33
| Codling Offshore 220kV | Codling Offshore 33kV | 2029 | Addition | 280/140/140 | 220/33/33
| Codling Offshore 220kV | Codling Offshore 33kV | 2029 | Addition | 280/140/140 | 220/33/33
| Codling Offshore 220kV | Codling Offshore 33kV | 2029 | Addition | 280/140/140 | 220/33/33
| Codling Onshore 400kV | Codling Onshore 220kV | 2029 | Addition | TBC | 400/220
| Codling Onshore 400kV | Codling Onshore 220kV | 2029 | Addition | TBC | 400/220
EA One North Wind Farm | EA1N Offshore 220kV-1 | EA1N Offshore 66kV-2 | 2029 | Addition | 525 | 220/66
| EA1N Offshore 220kV-2 | EA1N Offshore 66kV-1 | 2029 | Addition | 525 | 220/66
| EA1N Onshore 220kV | EA1N Onshore 400kV | 2029 | Addition | TBC | 400/220
| EA1N Onshore 220kV | EA1N Onshore 400kV | 2029 | Addition | TBC | 400/220
East Anglia 4A Wind Farm | East Anglia 4A Offshore-2 | East Anglia 4A Offshore-1 | 2029 | Addition | TBC | TBC
| East Anglia 4A Offshore-2 | East Anglia 4A Offshore-1 | 2029 | Addition | TBC | TBC
| East Anglia 4A Onshore-1 | East Anglia 4A 400kV | 2029 | Addition | TBC | TBC
East Anglia 5A Wind Farm | East Anglia 5A Offshore-2 | East Anglia 5A Offshore-1 | 2029 | Addition | TBC | TBC
| East Anglia 5A Offshore-2 | East Anglia 5A Offshore-1 | 2029 | Addition | TBC | TBC
| East Anglia 5A Onshore-1 | East Anglia 5A 400kV | 2029 | Addition | TBC | TBC
Firth of Forth 2 Offshore Wind Farm | Offshore 66KV-4 | Offshore 275kV-4 | 2029 | Addition | 430 | 275/66
| Offshore 66KV-5 | Offshore 275kV-5 | 2029 | Addition | 430 | 275/66
| Offshore 66KV-6 | Offshore 275kV-6 | 2029 | Addition | 430 | 275/66
| Onshore 275kV-2 | Onshore 400kV-2 | 2029 | Addition | 430 | 400/275
| Onshore 275kV-2 | Onshore 400kV-2 | 2029 | Addition | 430 | 400/275
| Onshore 275kV-2 | Onshore 400kV-2 | 2029 | Addition | 430 | 400/275
Hornsea 3 Offshore Wind Farm | Hornsea 3B-2 Offshore 66kV | Hornsea 3B-2 Offshore 500kV | 2029 | Addition | 850 | 500/66
Hornsea 4 Offshore Wind Farm | Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-3 | Offshore 66kV-5 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-3 | Offshore 66kV-6 | 2029 | Addition | 338 | 275/66
| Onshore 400kV | Onshore 275kV | 2029 | Addition | 594 | 400/275
| Onshore 400kV | Onshore 275kV | 2029 | Addition | 594 | 400/275
| Onshore 400kV | Onshore 275kV | 2029 | Addition | 594 | 400/275
| Offshore 275kV-4 | Offshore 66kV-7 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-4 | Offshore 66kV-8 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-5 | Offshore 66kV-9 | 2029 | Addition | 338 | 275/66
| Offshore 275kV-5 | Offshore 66kV-10 | 2029 | Addition | 338 | 275/66
| Onshore 400kV | Onshore 275kV | 2029 | Addition | 594 | 400/275
| Onshore 400kV | Onshore 275kV | 2029 | Addition | 594 | 400/275
Racebank Extension Wind Farm | Offshore Platform 220kV-1 | Offshore Platform 66kV-1 | 2029 | Addition | TBC | 220/66
| Offshore Platform 220kV-2 | Offshore Platform 66kV-2 | 2029 | Addition | TBC | 220/66
| Onshore 400 kV-1 | Onshore 220kV-1 | 2029 | Addition | TBC | 400/220
| Onshore 400 kV-2 | Onshore 220kV-2 | 2029 | Addition | TBC | 400/220
Thanet Extension Wind Farm | Offshore-1 | Offshore-2 | 2029 | Addition | TBC | TBC
| Offshore-1 | Offshore-2 | 2029 | Addition | TBC | TBC
| Onshore-1 | Onshore 400KV | 2029 | Addition | TBC | TBC
| Onshore-1 | Onshore 400KV | 2029 | Addition | TBC | TBC
West of Orkney Wind Farm | West of Orkney Offshore 275kV | West of Orkney Offshore 66kV | 2029 | Addition | 400/200/200 | 275/66/66
| West of Orkney Offshore 275kV | West of Orkney Offshore 66kV | 2029 | Addition | 400/200/200 | 275/66/66

## B-4-1a
B.4.1a - SHE Transmission Reactive Compensation Equipment for 2020/21
Site Name | Node | Unit Number | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
BEAULY | BEAU1J | 1 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1K | 2 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU3U | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU3V | 2 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
CROSSAIG | CRSS3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Z | 4 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT1- | 1 |  | 100 | Shunt Reactor | 132
KINTORE | KINT1- | 2 |  | 100 | Shunt Reactor | 132
KINTORE | KINT3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
MACDUFF | MACD3- | 1 | 10 |  | Mechanically Switched Capacitor | 33
MELGARVE | MELG4J | 1 | 100 | 100 | STATCOM | 400
MELGARVE | MELG4K | 1 | 100 | 100 | STATCOM | 400
TEALING | TEAL1- | 1 |  | 100 | Shunt Reactor | 132
TEALING | TEAL1- | 1 | 90 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL3W | 1 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 2 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275

## B-4-1b
B.4.1b - SPT Reactive Compensation Equipment 2020/21
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BONNYBRIDGE | BONN3U | 1 |  | 60 | Reactor | 33
BONNYBRIDGE | BONN3V | 2 |  | 60 | Reactor | 33
COALBURN | COAL3U | 1 |  | 60 | Reactor | 33
COCKENZIE | COCK2- | 1 | 230 |  | MSCDN | 275
CRYSTAL RIG | CRYR3V | 1 |  | 60 | Reactor | 33
CURRIE | CURR3W | 3 |  | 60 | Reactor | 33
DEWAR PLACE | DEWP3- | 1 |  | 60 | Reactor | 33
DEWAR PLACE | DEWP3- | 2 |  | 60 | Reactor | 33
ECCLES | ECCL3V | 1 |  | 60 | Reactor | 33
ELVANFOOT | ELVA4- | 1 | 225 |  | MSCDN | 400
ELVANFOOT | ELVA3V | 1 |  | 60 | Reactor | 33
HUNTERSTON NORTH | HUNN3W | 1 |  | 60 | Reactor | 33
HUNTERSTON NORTH | HUNN3X | 2 |  | 60 | Reactor | 33
KILLGALLIOCH WIND FARM | KILG2- | 1 |  | 60 | Reactor | 275
KILMARNOCK SOUTH | KILS3U | 4 |  | 60 | Reactor | 33
LONGANNET | LOAN2- | 1 | 230 |  | MSCDN | 275
LONGANNET | LOAN2- | 2 | 230 |  | MSCDN | 275
MARK HILL | MAHI3U | 2 |  | 60 | Reactor | 33
MOFFAT | MOFF4- | 1 | 230 |  | MSCDN | 400
MOFFAT | MOFF3U | 1 |  | 60 | Reactor | 33
NEILSTON | NEIL3U | 1 |  | 60 | Reactor | 33
NEILSTON | NEIL3V | 2 |  | 60 | Reactor | 33
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 33 | Sync Comp | 275
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 70 | STATCOM | 275
SMEATON | SMEA3U | 1 |  | 60 | Reactor | 33
SMEATON | SMEA3V | 1 |  | 60 | Reactor | 33
TORNESS | TORN4- | 1 |  | 150 | Reactor | 400
TORNESS | TORN4- | 2 |  | 150 | Reactor | 400
WINDYHILL | WIYH3W | 3 |  | 60 | Reactor | 33
WINDYHILL | WIYH2- | 1 | 150 |  | MSCDN | 275
WISHAW | WISH3W | 1 |  | 60 | Reactor | 33

## B-4-1c
B.4.1c - NGET Reactive Compensation Equipment for 2020/21
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
ABERTHAW | ABTH11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
ABERTHAW | ABTH11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
ABHAM | ABHA11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
ABHAM | ABHA11 | 3 | 45 |  | Mechanically Switched Capacitor | 132
BARKING | BARK21 | 2B WDG 1 |  | 30 | Reactor | 275
BARKING | BARK21 | 2B WDG 2 |  | 30 | Reactor | 275
BARKING | BARK21 | 4B WDG 1 |  | 30 | Reactor | 275
BARKING | BARK21 | 4B WDG 2 |  | 30 | Reactor | 275
BEDDINGTON | BEDD21 | 1B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 2B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 3B | 155 |  | Mechanically Switched Capacitor | 275
BEDDINGTON | BEDD21 | 3B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 4B | 155 |  | Mechanically Switched Capacitor | 275
BEDDINGTON | BEDD21 | 4B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 5B |  | 100 | Reactor | 275
BEDDINGTON | BEDD21 | 6A |  | 100 | Reactor | 275
BERKSWELL | BESW11 | 1 |  | 60 | Reactor | 132
BERKSWELL | BESW11 | 2 |  | 60 | Reactor | 132
BERKSWELL | BESW11 | 3 |  | 60 | Reactor | 132
BERKSWELL | BESW21 | 4 | 155 |  | Mechanically Switched Capacitor | 275
BIRKENHEAD | BIRK21 | 4 WDG A |  | 30 | Reactor | 275
BIRKENHEAD | BIRK21 | 4 WDG B |  | 30 | Reactor | 275
BISHOPS WOOD | BISW11 | A | 60 |  | Mechanically Switched Capacitor | 132
BISHOPS WOOD | BISW11 | B | 60 |  | Mechanically Switched Capacitor | 132
BISHOPS WOOD | BISW11 | C | 60 |  | Mechanically Switched Capacitor | 132
BLYTH | BLYT21 | 1 | 155 |  | Mechanically Switched Capacitor | 275
BLYTH | BLYT21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
BOLNEY | BOLN11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN41 | 1 |  | 55 | Reactor | 400
BOLNEY | BOLN41 | 2 |  | 55 | Reactor | 400
BOLNEY | BOLN41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
BOLNEY | BOLN41 | 6 | 100 | 225 | SVC | 400
BOLNEY | BOLN41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
BRADFORD WEST | BRAW21 | 3 |  | 60 | Reactor | 275
BRADFORD WEST | BRAW21 | 4 WDG A |  | 30 | Reactor | 275
BRADFORD WEST | BRAW21 | 4 WDG B |  | 30 | Reactor | 275
BRAMFORD | BRFO11 | A | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO11 | B | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO11 | C | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO41 | 1 |  | 200 | Reactor | 400
BREDBURY | BRED21 | 1 WDG 1 |  | 30 | Reactor | 275
BREDBURY | BRED21 | 1 WDG 2 |  | 30 | Reactor | 275
BREDBURY | BRED21 | 3 WDG 1 |  | 30 | Reactor | 275
BREDBURY | BRED21 | 3 WDG 2 |  | 30 | Reactor | 275
BRIDGEWATER | BRWA11 | 1A | 45 |  | Mechanically Switched Capacitor | 132
BRIDGEWATER | BRWA11 | 1B | 45 |  | Mechanically Switched Capacitor | 132
BRIDGEWATER | BRWA2A | G | 60 | 60 | SVC | 275
BUSHBURY | BUSH11 | A | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH11 | B | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH11 | C | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
BUSHBURY | BUSH21 | 3 |  | 60 | Reactor | 275
BUSTLEHOLM | BUST21 | 4 | 20 |  | Mechanically Switched Capacitor | 275
BUSTLEHOLM | BUST21 | 4 |  | 60 | Reactor | 275
BUSTLEHOLM | BUST21 | 1 WDG A |  | 30 | Reactor | 275
BUSTLEHOLM | BUST21 | 1 WDG B |  | 30 | Reactor | 275
CANTERBURY | CANT41 | 4 |  | 200 | Reactor | 400
CAPENHURST | CAPE21 | 1 | 155 |  | Mechanically Switched Capacitor | 275
CELLARHEAD | CELL11 | 2A | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL11 | 2B | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
CELLARHEAD | CELL41 | 8 | 225 |  | Mechanically Switched Capacitor | 400
CELLARHEAD | CELL41 | 5 | 95 | 150 | SVC | 400
CELLARHEAD | CELL41 | 6 | 95 | 150 | SVC | 400
CELLARHEAD | CELL41 | 2 WDG A |  | 30 | Reactor | 400
CELLARHEAD | CELL41 | 2 WDG B |  | 30 | Reactor | 400
CELLARHEAD | CELL41 | 3 WDG A |  | 30 | Reactor | 400
CELLARHEAD | CELL41 | 3 WDG B |  | 30 | Reactor | 400
CHESTERFIELD | CHTE21 | 4 |  | 60 | Reactor | 275
CHICKERELL | CHIC41 | 2 |  | 60 | Reactor | 400
CHICKERELL | CHIC42 | 2 | 230 |  | Mechanically Switched Capacitor | 400
CILFYNYDD | CILF41 | 1 |  | 60 | Reactor | 400
CILFYNYDD | CILF41 | 2 |  | 60 | Reactor | 400
CILFYNYDD | CILF41 | 4 |  | 200 | Reactor | 400
CILFYNYDD | CILF41 | 6 |  | 200 | Reactor | 400
CITY ROAD | CITR41 | 2 | 55 |  | Mechanically Switched Capacitor | 400
CITY ROAD | CITR41 | 4 | 55 |  | Mechanically Switched Capacitor | 400
CITY ROAD | CITR41 | 1 |  | 200 | Reactor | 400
CONNAH'S QUAY | CONQ41 | 1 WDG 1 |  | 30 | Reactor | 400
CONNAH'S QUAY | CONQ41 | 1 WDG 2 |  | 30 | Reactor | 400
COVENTRY | COVE11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE21 | 3 |  | 60 | Reactor | 275
COVENTRY | COVE21 | A | 60 | 60 | SVC | 275
COWLEY | COWL11 | A | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL11 | B | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL11 | C | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL41 | 2 |  | 200 | Reactor | 400
COWLEY | COWL41 | 3 |  | 200 | Reactor | 400
DRAKELOW | DRAK41 | 3 | 230 |  | Mechanically Switched Capacitor | 400
DRAKELOW | DRAK41 | 4 |  | 200 | Reactor | 400
DRAKELOW | DRAK41 | 6 |  | 200 | Reactor | 400
DRAX | DRAX41 | 1 |  | 60 | Reactor | 400
DRAX | DRAX41 | 2 |  | 60 | Reactor | 400
EAST CLAYDON | ECLA12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
EAST CLAYDON | ECLA40 | 6 | 202 | 225 | SVC | 400
EAST CLAYDON | ECLA41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
EAST CLAYDON | ECLA41 | 7 | 230 |  | Mechanically Switched Capacitor | 400
EAST CLAYDON | ECLA41 | 1 WDG A |  | 30 | Reactor | 400
EAST CLAYDON | ECLA41 | 1 WDG B |  | 30 | Reactor | 400
EAST CLAYDON | ECLA41 | 2 WDG A |  | 30 | Reactor | 400
EAST CLAYDON | ECLA41 | 2 WDG B |  | 30 | Reactor | 400
ELLAND | ELLA21 | 2 |  | 60 | Reactor | 275
ELSTREE | ELST21 | M | 60 | 60 | SVC | 275
ELSTREE | ELST22 | L | 60 | 60 | SVC | 275
ELSTREE | ELST41 | 1 |  | 200 | Reactor | 400
ENDERBY | ENDE41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
ENDERBY | ENDE41 | 2 | 230 |  | Mechanically Switched Capacitor | 400
EXETER | EXET11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
EXETER | EXET41 | 1 | 25 |  | Mechanically Switched Capacitor | 400
EXETER | EXET41 | 2 | 25 |  | Mechanically Switched Capacitor | 400
EXETER | EXET41 | 3 | 95 | 150 | SVC | 400
EXETER | EXET41 | 5 | 95 | 150 | SVC | 400
FECKENHAM | FECK21 | 6 | 125 | 145 | SVC | 275
FECKENHAM | FECK41 | 4 WDG A |  | 30 | Reactor | 400
FECKENHAM | FECK41 | 4 WDG A |  | 30 | Reactor | 400
FECKENHAM | FECK41 | 4 WDG B |  | 30 | Reactor | 400
FECKENHAM | FECK41 | 4 WDG B |  | 30 | Reactor | 400
FLEET | FLEE11 | 2A | 50 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 2B | 50 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 2C | 50 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
FLEET | FLEE41 | 3A WDG 1 |  | 30 | Reactor | 400
FLEET | FLEE41 | 3A WDG 2 |  | 30 | Reactor | 400
FLEET | FLEE41 | 4A WDG 1 |  | 30 | Reactor | 400
FLEET | FLEE41 | 4A WDG 2 |  | 30 | Reactor | 400
GRAIN | GRAI41 | 1 |  | 200 | Reactor | 400
GRENDON | GREN11 | 1A | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN11 | 1B | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN11 | 1C | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN41 | 1 |  | 60 | Reactor | 400
GRENDON | GREN41 | 3 | 230 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN41 | 4 | 225 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN41 | 6 | 225 |  | Mechanically Switched Capacitor | 400
GREYSTONES | GRSB21 | 1 |  | 100 | Reactor | 275
GREYSTONES | GRSB21 | 3 |  | 100 | Reactor | 275
HAMS HALL | HAMH40 | 2 | 230 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH40 | 3 | 230 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH41 | 4 |  | 200 | Reactor | 400
HARKER | HARK21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
HARKER | HARK21 | 7 | 125 | 145 | SVC | 275
HARKER | HARK22 | 8 | 125 | 145 | SVC | 275
HARKER | HARK41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
HARKER | HARK41 | 3A | 225 |  | Mechanically Switched Capacitor | 400
HARKER | HARK41 | 3B | 225 |  | Mechanically Switched Capacitor | 400
HURST | HURS21 | 2 |  | 60 | Reactor | 275
HURST | HURS21 | 3 |  | 60 | Reactor | 275
HURST | HURS21 | 4 |  | 100 | Reactor | 275
HURST | HURS21 | 7 |  | 100 | Reactor | 275
HURST | HURS21 | 1 |  | 100 | Reactor | 275
HURST | HURS21 | 2A |  | 100 | Reactor | 275
HURST | HURS21 | 2B | 155 |  | Mechanically Switched Capacitor | 275
HUTTON | HUTT41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
INDIAN QUEENS | INDQ11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ41 | 2 |  | 200 | Reactor | 400
INDIAN QUEENS | INDQ41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
INDIAN QUEENS | INDQ41 | 1 |  | 60 | Reactor | 400
IRON ACTON | IROA21 | 6 | 45 |  | Mechanically Switched Capacitor | 132
IRON ACTON | IROA21 | E | 60 | 60 | SVC | 275
IRON ACTON | IROA21 | F | 60 | 60 | SVC | 275
IRONBRIDGE | IRON11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
IVER | IVER21 | 1A |  | 60 | Reactor | 275
IVER | IVER21 | 3A |  | 60 | Reactor | 275
IVER | IVER4A | 6B |  | 55 | Reactor | 400
IVER | IVER4B | 5A |  | 55 | Reactor | 400
JORDANTHORPE | JORD21 | 2 |  | 60 | Reactor | 275
KEARSLEY | KEAR11 | A | 50 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | B | 50 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | C | 50 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR41 | 3A |  | 60 | Reactor | 400
KINGSNORTH | KINO41 | 3 |  | 200 | Reactor | 400
KINGSNORTH | KINO41 | 4 |  | 200 | Reactor | 400
KINGSNORTH | KINO41 | 1 WDG 1 |  | 25 | Reactor | 400
KINGSNORTH | KINO41 | 1 WDG 2 |  | 25 | Reactor | 400
KINGSNORTH | KINO41 | 2 WDG 1 |  | 25 | Reactor | 400
KINGSNORTH | KINO41 | 2 WDG 2 |  | 25 | Reactor | 400
KIRKBY | KIBY41 | 1A | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY41 | 4A | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY42 | 2A | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY42 | 3B | 45 |  | Mechanically Switched Capacitor | 132
KIRKSTALL | KIRK21 | 2 |  | 60 | Reactor | 275
KIRKSTALL | KIRK21 | 4 |  | 60 | Reactor | 275
KIRKSTALL | KIRK21 | 3 | 150 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK21 | A | 20 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK21 | B | 20 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK21 | C | 20 |  | Mechanically Switched Capacitor | 275
LALEHAM | LALE21 | 1 |  | 100 | Reactor | 275
LALEHAM | LALE21 | 2 |  | 100 | Reactor | 275
LALEHAM | LALE21 | 3 |  | 100 | Reactor | 275
LANDULPH | LAND11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
LANDULPH | LAND41 | 2 WDG A |  | 30 | Reactor | 400
LANDULPH | LAND41 | 2 WDG B |  | 30 | Reactor | 400
LANDULPH | LAND42 | 3 |  | 200 | Reactor | 400
LANDULPH | LAND42 | H | 60 | 60 | SVC | 400
LEGACY | LEGA41 | 1 |  | 60 | Reactor | 400
LEGACY | LEGA41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
LEGACY | LEGA41 | 2 |  | 60 | Reactor | 400
LISTER DRIVE | LISD21 | 1 |  | 100 | Reactor | 275
LOVEDEAN | LOVE41 | 2 | 230 |  | Mechanically Switched Capacitor | 400
LOVEDEAN | LOVE41 | 3 |  | 60 | Reactor | 400
LOVEDEAN | LOVE41 | 5 | 95 | 150 | SVC | 400
LOVEDEAN | LOVE41 | 7 |  | 200 | Reactor | 400
LOVEDEAN | LOVE41 | 1 |  | 200 | Reactor | 400
LOVEDEAN | LOVE41 | 4A |  | 60 | Reactor | 400
MANNINGTON | MANN11 | A | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | A | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | B | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | B | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | C | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | C | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN41 | 1 | 95 | 150 | SVC | 400
MANNINGTON | MANN41 | 2 | 95 | 150 | SVC | 400
MELKSHAM | MELK11 | A | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK11 | B | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK11 | C | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK41 | 5 |  | 60 | Reactor | 400
MELKSHAM | MELK41 | 6 |  | 60 | Reactor | 400
MELKSHAM | MELK41 | 1 |  | 200 | Reactor | 400
MILL HILL | MILH21 | 1B WDNG 1 |  | 25 | Reactor | 275
MILL HILL | MILH21 | 1B WDNG 2 |  | 25 | Reactor | 275
MILL HILL | MILH21 | 2A WDNG 1 |  | 25 | Reactor | 275
MILL HILL | MILH21 | 2A WDNG 2 |  | 25 | Reactor | 275
MONK FRYSTON | MONF22 | 1 | 155 |  | Mechanically Switched Capacitor | 275
NECHELLS | NECH21 | WDG 1 |  | 30 | Reactor | 275
NECHELLS | NECH21 | A |  | 60 | Reactor | 275
NECHELLS | NECH21 | WDG 2 |  | 30 | Reactor | 275
NEWCROSS | NEWX21 | 5 |  | 100 | Reactor | 275
NEWCROSS | NEWX21 | 6 |  | 100 | Reactor | 275
NINFIELD | NINF41 | 1 |  | 200 | Reactor | 400
NINFIELD | NINF41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
NINFIELD | NINF41 | 5 | 100 | 225 | SVC | 400
NINFIELD | NINF41 | 6 | 150 | 200 | SVC | 400
NORWICH TROWSE | NORW11 | A | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW11 | B | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW11 | C | 60 |  | Mechanically Switched Capacitor | 132
NURSLING | NURS41 | 2 |  | 60 | Reactor | 400
OCKER HILL | OCKH21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
OLDBURY | OLDB21 | WDG A |  | 30 | Reactor | 275
OLDBURY | OLDB21 | WDG B |  | 30 | Reactor | 275
PELHAM | PELH41 | 3 |  | 200 | Reactor | 400
PELHAM | PELH41 | 5 | 120 | 150 | SVC | 400
PELHAM | PELH41 | 6 | 120 | 150 | SVC | 400
PELHAM | PELH41 | 1 WDG A |  | 25 | Reactor | 400
PELHAM | PELH41 | 1 WDG B |  | 25 | Reactor | 400
PELHAM | PELH41 | 2 WDG A |  | 25 | Reactor | 400
PELHAM | PELH41 | 2 WDG B |  | 25 | Reactor | 400
PEMBROKE | PEMB41 | 1 |  | 60 | Reactor | 400
PEMBROKE | PEMB41 | 2 |  | 60 | Reactor | 400
PENN | PENN21 | B | 60 | 60 | SVC | 275
PENTIR | PENT41 | 2 |  | 200 | Reactor | 400
PENTIR | PENT41 | 5 |  | 200 | Reactor | 400
PENWORTHAM | PEWO41 | 6 |  | 60 | Reactor | 400
PITSMOOR | PITS21 | 3 |  | 60 | Reactor | 275
PITSMOOR | PITS21 | 4 |  | 60 | Reactor | 275
PORT HAM | PORH11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
PORT HAM | PORH11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
PYLE | PYLE21 | J | 60 | 60 | SVC | 275
PYLE | PYLE21 | K | 60 | 60 | SVC | 275
RAINHILL | RAIN11 | 2 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN11 | 4 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN12 | 1 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
RATCLIFFE-ON-SOAR | RATS41 | 2 |  | 200 | Reactor | 400
RATCLIFFE-ON-SOAR | RATS41 | 3 |  | 60 | Reactor | 400
RAYLEIGH | RAYL41 | 5 |  | 60 | Reactor | 400
RICHBOROUGH | RICH41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
RICHBOROUGH | RICH41 | 1 | 225 | 100 | SVC | 400
ROCHDALE | ROCH11 | A | 60 |  | Mechanically Switched Capacitor | 132
ROCHDALE | ROCH11 | B | 60 |  | Mechanically Switched Capacitor | 132
ROCHDALE | ROCH11 | C | 60 |  | Mechanically Switched Capacitor | 132
SELLINDGE | SELL41 | 1 | 155 | 200 | SVC | 400
SELLINDGE | SELL41 | 2 | 155 | 200 | SVC | 400
SKELTON GRANGE | SKLG11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG21 | 3 |  | 100 | Reactor | 275
SKELTON GRANGE | SKLG21 | 6 | 150 |  | Mechanically Switched Capacitor | 275
SPENNYMOOR | SPEN41 | 1 |  | 60 | Reactor | 400
ST JOHNS WOOD | SJOW12 | A | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW12 | B | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW12 | C | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW21 | 1 | 144 | 150 | SVC | 275
ST JOHNS WOOD | SJOW21 | 2B |  | 55 | Reactor | 275
ST JOHNS WOOD | SJOW21 | 3 | 144 | 150 | SVC | 275
ST JOHNS WOOD | SJOW41 | 2 |  | 200 | Reactor | 400
ST JOHNS WOOD | SJOW41 | 4 |  | 200 | Reactor | 400
ST JOHNS WOOD | SJOW41 | 1 |  | 200 | Reactor | 400
STAYTHORPE | STAY41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
STELLA WEST | STEW21 | 2 |  | 100 | Reactor | 275
STELLA WEST | STEW41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
STELLA WEST | STEW41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND41 | 5 WDG 1 |  | 30 | Reactor | 400
SUNDON | SUND41 | 5 WDG 2 |  | 30 | Reactor | 400
SUNDON | SUND42 | 2 | 230 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND42 | 8 WDG 1 |  | 30 | Reactor | 400
SUNDON | SUND42 | 8 WDG 2 |  | 30 | Reactor | 400
SWANSEA | SWAN11 | A | 60 |  | Mechanically Switched Capacitor | 132
SWANSEA | SWAN11 | B | 60 |  | Mechanically Switched Capacitor | 132
SWANSEA | SWAN11 | C | 60 |  | Mechanically Switched Capacitor | 132
THORPE MARSH | THOM41 | 2 |  | 200 | Reactor | 400
THORPE MARSH | THOM42 | 6 |  | 200 | Reactor | 400
TOTTENHAM | TOTT21 | 5 |  | 100 | Reactor | 275
TOTTENHAM | TOTT23 | 1 |  | 100 | Reactor | 275
TOTTENHAM | TOTT24 | 3 |  | 100 | Reactor | 275
TYNEMOUTH | TYNE21 | 2A |  | 60 | Reactor | 275
USKMOUTH | USKM11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
WALHAM | WALH41 | 1 | 60 |  | Mechanically Switched Capacitor | 400
WALHAM | WALH41 | 2 |  | 60 | Reactor | 400
WALHAM | WALH41 | 3 |  | 60 | Reactor | 400
WALHAM | WALH41 | 4 |  | 220 | Reactor | 400
WALPOLE | WALP11 | 4A | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 4C | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 4B | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP41 | 3 |  | 55 | Reactor | 400
WALPOLE | WALP41 | 1 |  | 55 | Reactor | 400
WALPOLE | WALP41 | 2 |  | 55 | Reactor | 400
WARLEY | WARL11 | B | 50 |  | Mechanically Switched Capacitor | 132
WARLEY | WARL11 | A | 50 |  | Mechanically Switched Capacitor | 132
WARLEY | WARL11 | C | 50 |  | Mechanically Switched Capacitor | 132
WEST BURTON | WBUR42 | 1 |  | 200 | Reactor | 400
WEST HAM | WHAM41 | 4 | 230 |  | Mechanically Switched Capacitor | 400
WEST HAM | WHAM41 | 1 |  | 200 | Reactor | 400
WEST MELTON | WMEL12 | 3A | 45 |  | Mechanically Switched Capacitor | 132
WEST MELTON | WMEL12 | 3B | 45 |  | Mechanically Switched Capacitor | 132
WEST MELTON | WMEL12 | 3C | 45 |  | Mechanically Switched Capacitor | 132
WEST WEYBRIDGE | WWEY41 | 1 |  | 100 | Reactor | 400
WHITEGATE | WHGA20 | 4A |  | 60 | Reactor | 275
WHITEGATE | WHGA20 | 4B |  | 60 | Reactor | 275
WHITEGATE | WHGA21 | 2 | 150 |  | Mechanically Switched Capacitor | 275
WILLESDEN | WISD21 | 2B |  | 55 | Reactor | 275
WILLESDEN | WISD21 | 3B WDG 1 |  | 25 | Reactor | 275
WILLESDEN | WISD21 | 3B WDG 2 |  | 25 | Reactor | 275
WILLINGTON | WILE41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WILLINGTON | WILE41 | 8 | 95 | 150 | SVC | 400
WIMBLEDON | WIMB21 | 2 |  | 100 | Reactor | 275
WIMBLEDON | WIMB21 | 4 |  | 100 | Reactor | 275
WIMBLEDON | WIMB41 | 5 |  | 200 | Reactor | 400
WIMBLEDON | WIMB41 | 6 |  | 225 | Reactor | 400
WYMONDLEY | WYMO41 | 3 |  | 200 | Reactor | 400
WYMONDLEY | WYMO41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WYMONDLEY | WYMO41 | 2 | 230 |  | Mechanically Switched Capacitor | 400

## B-4-1d
B.4.1d - OFTO Reactive Compensation Equipment for 2020/21
OFTO | Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Tapping
Hornsea One Limited | Hornsea 1 Wind Farm | HOWA41 | SHR3 |  | 75 | Shunt Reactor | 400
|  | HOWA41 | SHR4 |  | 75 | Shunt Reactor | 400
|  | HOWA21 | VSR-1 |  | 300 | Shunt Reactor | 220 | 120-300
|  | HOWA21 | VSR-2 |  | 300 | Shunt Reactor | 220 | 120-300
|  | HOWR2A | SHR1 |  | 220 | Shunt Reactor | 220
|  | HOWR2A | SHR2 |  | 220 | Shunt Reactor | 220
|  | HOWW21 | SHR1 |  | 85 | Shunt Reactor | 220
|  | HOWW22 | SHR1 |  | 105 | Shunt Reactor | 220
|  | HOWA21 | SVC1 | 160 | 200 | SVC | 220
|  | HOWA21 | SVC2 | 160 | 200 | SVC | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | SHR1 |  | 28.2 | Shunt Reactor | 132
|  | HUMO12 | SHR2 |  | 28.2 | Shunt Reactor | 132
|  | HUMO31 | MSR1A |  | 28 | Shunt Reactor | 33
|  | HUMO32 | MSR1B |  | 28 | Shunt Reactor | 33
|  | HUMO31 | MSR2A |  | 28 | Shunt Reactor | 33
|  | HUMO32 | MSR2B |  | 28 | Shunt Reactor | 33
|  | HUMO31 | SVC1 | 24 | 24 | SVC | 33
|  | HUMO32 | SVC2 | 24 | 24 | SVC | 33
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | 1 |  | 24 | Shunt Reactor | 132
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | 1 |  | 60 | Shunt Reactor | 400
|  | BBWO21 | 1 |  | 125 | Shunt Reactor | 220 | 50-125
|  | BBWO41 | SVC1 | 50 | 50 | SVC | 15.5
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDO11 | SHR1 |  | 85 | Shunt Reactor | 132
|  | DUDO11 | SHR2 |  | 85 | Shunt Reactor | 132
|  | DUDO31 | SVC1 | 125 | 125 | SVC | 33
|  | DUDO32 | SVC2 | 125 | 125 | SVC | 33
East Anglia One Limited | East Anglia Offshore Wind Farm | EAAW21 | SH1 |  | 174 | Shunt Reactor | 220
|  | EAAW21 | SH2 |  | 174 | Shunt Reactor | 220
|  | BRST21 | VSR-1 |  | 228 | Shunt Reactor | 220 | 114-228
|  | BRST21 | VSR-2 |  | 228 | Shunt Reactor | 220 | 114-228
|  | BRST41 | SVC1 | 215 | 215 | SVC | 34.5
|  | BRST41 | SVC2 | 215 | 215 | SVC | 34.5
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | SVC1 | 70 | 70 | SVC | 132
|  | GALO12 | SVC2 | 70 | 70 | SVC | 132
|  | GALO11 | MSR 05 |  | 85 | Shunt Reactor | 132
|  | GALO12 | MSR 06 |  | 85 | Shunt Reactor | 132
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO31 | SR1 |  | 35 | Shunt Reactor | 33
|  | ORMO31 | SR2 |  | 35 | Shunt Reactor | 33
|  | ORMO31 | SVC 1 | 28 | 28 | SVC | 33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SALL11 | 1 |  | 60 | Shunt Reactor | 132 | 30-60
|  | SALL12 | 2 |  | 60 | Shunt Reactor | 132 | 30-60
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO21 | SHR2 |  | 172 | Shunt Reactor | 220
|  | TKNW21 | SHR4 |  | 43 | Shunt Reactor | 220
|  | TKNO31 | MSR2B |  | 163 | Shunt Reactor | 33
|  | TKNO31 | MSR2C |  | 163 | Shunt Reactor | 33
|  | TKNO31 | SVC2A | 143 | 143 | SVC | 33
Diamond Transmission Partners Walney Extension Limited | Walney Extension Wind Farm | WOWE41 | SHR1 |  | 62 | Shunt Reactor | 400
|  | WOWE21 | VSR-1 |  | 250 | Shunt Reactor | 220 | 125-250
|  | WACW21 | SHR1 |  | 90 | Shunt Reactor | 220
|  | WOWE21 | SVC1 | 70 | 70 | SVC | 220
|  | WOWE42 | SHR2 |  | 62 | Shunt Reactor | 400
|  | WOWE22 | VSR-2 |  | 250 | Shunt Reactor | 220 | 125-250
|  | WADW21 | SHR2 |  | 90 | Shunt Reactor | 220
|  | WOWE22 | SVC2 | 70 | 70 | SVC | 220
WoDS Transmission plc | West of Duddon Sands | WDSO41 | SR1 |  | 30 | Shunt Reactor | 13.9
|  | WDSO42 | SR2 |  | 30 | Shunt Reactor | 13.9
|  | WDSO11 | SR3 |  | 60 | Shunt Reactor | 155
|  | WDSO12 | SR4 |  | 60 | Shunt Reactor | 155
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO31 | Statcom1 | 25 | 25 | SVC | 33
|  | WERO31 | Statcom2 | 25 | 25 | SVC | 33
|  | WERO31 | 1 |  | 50 | Shunt Reactor | 33
Greater Gabbard Offshore Winds Ltd | Greater Gabbard Offshore Wind Farm | GGON51 | 1 | 55 |  | MSC | 13.9(secondary)
|  | GGON52 | 1 | 55 |  | MSC | 13.9(secondary)
|  | GGON53 | 1 | 55 |  | MSC | 13.9(secondary)
|  | GGON51 | 1 |  | 43 | MSR | 13.9(secondary)
|  | GGON52 | 1 |  | 43 | MSR | 13.9(secondary)
|  | GGON53 | 1 |  | 43 | MSR | 13.9(secondary)
|  | GANW3A | 1 |  | 30 | Shunt Reactor | 33
|  | GANW3B | 1 |  | 30 | Shunt Reactor | 33
|  | GGON51 | 1 | 50 | 50 | SVC | 13.9(secondary)
|  | GGON52 | 2 | 50 | 50 | SVC | 13.9(secondary)
|  | GGON53 | 3 | 50 | 50 | SVC | 13.9(secondary)
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | SVC PLUS 1A | 52 | 52 | SVC | 13.9(tertiary)
|  | LONO42 | SVC PLUS 2A | 52 | 52 | SVC | 13.9(tertiary)
|  | LONO43 | SVC PLUS 1B | 52 | 52 | SVC | 13.9(tertiary)
|  | LONO44 | SVC PLUS 2B | 52 | 52 | SVC | 13.9(tertiary)
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | GWYO11 | SVC-1 | 95 | 95 | SVC | 13.9(tertiary)
|  | GWYO12 | SVC-2 | 95 | 95 | SVC | 13.9(tertiary)
|  | GWYO11 | MSR1A |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO11 | MSR1B |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO12 | MSR2A |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO12 | MSR2B |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO11 | MSC1A |  | 30 | MSC | 13.9(tertiary)
|  | GWYO11 | MSC1B |  | 30 | MSC | 13.9(tertiary)
|  | GWYO12 | MSC2A |  | 30 | MSC | 13.9(tertiary)
|  | GWYO12 | MSC2B |  | 30 | MSC | 13.9(tertiary)
TC Beatrice OFTO Limited | Beatrice offshore Windfarm | BEAT21 | SHR1 |  | 115 | Shunt Reactor | 220
|  | BEAT22 | SHR2 |  | 115 | Shunt Reactor | 220
|  | BEAT21 | SHR3 |  | 115 | Shunt Reactor | 220
|  | BEAT22 | SHR4 |  | 115 | Shunt Reactor | 220
|  | BEAT41 | SVC1 | 144 | 155 | SVC | 33 (Tertiary)
|  | BEAT42 | SVC2 | 144 | 155 | SVC | 33 (Tertiary)
TC Lincs OFTO Limited | Lincs Wind Farm | LINO41 | MSC3 | 31.15 |  | MSC | 13.9(Tertiary)
|  | LINO42 | MSC5 | 31.15 |  | MSC | 13.9(Tertiary)
|  | LINO43 | MSR2 |  | 60 | Shunt Reactor | 13.9(Tertiary)
|  | LINO44 | MSR4 |  | 60 | Shunt Reactor | 13.9(Tertiary)
|  | LINO45 | SVC Plus 1 | 94 | 139 | SVC | 13.9(Tertiary)
|  | LINO11 | SR1 |  | 46 | Shunt Reactor | 132 | 1 to 7
|  | LINO11 | SR2 |  | 46 | Shunt Reactor | 132 | 1 to 7
|  | LINS31 | SR1 |  | 40 | Shunt Reactor | 33
|  | LINS32 | SR2 |  | 40 | Shunt Reactor | 33
Diamond Transmission Partners RB Limited | Race Bank Offshore windfarm | RACO21 | VSR1 |  | 200 | Variable Shunt Reactor | 220 | 120-200
|  | RACO22 | VSR2 |  | 200 | Variable Shunt Reactor | 220 | 120-200
|  | RACW21 | SR1 |  | 90 | Shunt Reactor | 220
|  | RACW22 | SR2 |  | 90 | Shunt Reactor | 220
|  | RACO21 | STATCOM1 | 120 | 120 | SVC | 28 (Secondary)
|  | RACO22 | STATCOM1 | 120 | 120 | SVC | 28(Secondary)
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | Reactor 1/2/3 |  | 18 | Shunt Reactor | 33 (Secondary)
|  | RORE11 | Capacitor 1/2 | 12 |  | MSC | 33 (Secondary)
| Robin Rigg West Offshore Wind Farm | RORW11 | Reactor 1/2/3 |  | 18 | Shunt Reactor | 33 (Secondary)
|  | RORW11 | Capacitor 1/2 | 12 |  | MSC | 33 (Secondary)
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | TWNE41 | SVC1 | 65 | 65 | SVC | 33 (tertiary)
|  | TWNE42 | SVC2 | 65 | 65 | SVC | 33 (tertiary)
|  | TWNE11 | SHR1 |  | 64 | Shunt Reactor | 150
|  | TWNE12 | SHR2 |  | 64 | Shunt Reactor | 150
|  | TWNE31 | TSR1 |  | 46 | TSR | 33
|  | TWNE32 | TSR2 |  |  | TSR | 33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | SVC 1 | 49.3 | 49.3 | SVC | 132
|  | THAW12 | SVC 2 | 49.3 | 49.3 | SVC | 132
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO1A | RCT1 |  | 64 | Shunt Reactor | 132
Blue Transmission Walney 2 OFTO | Walney 2 Offshore Wind Farm | WABO1A | RCT1 |  | 80 | Shunt Reactor | 132 | 1 to 31

## B-4-2a
B.4.2a - SHE Transmission Reactive Compensation Equipment changes for 2021/22 to 2029/30
Site Name | Node | Unit Number | Year | Status | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ALYTH | ALYT2A | 1 | 2024 | Addition | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | ALYT2A | 1 | 2024 | Addition | 225 | 225 | SVC | 275
KINARDOCHY | KINA2K | 1 | 2024 | Addition | 100 |  | Mechanically Switched Capacitor | 275
KINARDOCHY | KINA2J | 1 | 2024 | Addition | 225 | 225 | SVC | 275
ALYTH | ALYT2A | 1 | 2026 | Remove | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | ALYT4J | 1 | 2026 | Addition | 100 |  | Mechanically Switched Capacitor | 400
DOUNREAY | DOUN3Y | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
DOUNREAY | DOUN3Z | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
ORKNEY FINSTOWN | FINS3Y | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
ORKNEY FINSTOWN | FINS3Z | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
ALYTH | ALYT2A | 1 | 2026 | Remove | 225 | 225 | SVC | 275
ALYTH | ALYT4J | 1 | 2026 | Addition | 225 | 225 | SVC | 400
ORKNEY FINSTOWN | FINS1- | 1 | 2026 | Addition | 70 | 35 | Synchronous Condenser | 132
ORKNEY FINSTOWN | FINS1- | 2 | 2026 | Addition | 70 | 35 | Synchronous Condenser | 132

## B-4-2b
B.4.2b - SPT Reactive Compensation Equipment 2021/22 to 2029/30
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
COALBURN | Addition | 2024 | COAL3V | 2 |  | 60 | Reactor | 33
GRETNA | Addition | 2024 | GRNA3U | 1 |  | 60 | Reactor | 33
STRATHAVEN | Addition | 2024 | STHA3U | 3 |  | 60 | Reactor | 33
STRATHAVEN | Addition | 2024 | STHA3V | 4 |  | 60 | Reactor | 33
MARK HILL | Addition | 2024 | MAHI1- | 1 | 75 | 75 | STATCOM | 132
HUNTERSTON | Addition | 2024 | HUER4- | 1 |  | 200 | Reactor | 400
HUNTERSTON SYNCH COMP | Addition | 2026 | HUER4- | 1 | 300 | 140 | Sync Comp | 400
KINCARDINE SYNCH COMP | Addition | 2026 | KINC2- | 1 | 300 | 140 | Sync Comp | 275
STRATHAVEN SYNCH COMP | Addition | 2026 | STHA4A | 1 | 150 | 70 | Sync Comp | 400
STRATHAVEN SYNCH COMP | Addition | 2026 | STHA4B | 1 | 150 | 70 | Sync Comp | 400
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4A | 1 | 150 | 70 | Sync Comp | 275
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4A | 1 | 150 | 150 | STATCOM | 275
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4B | 1 | 150 | 70 | Sync Comp | 275
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4B | 1 | 150 | 150 | STATCOM | 275

## B-4-2c
B.4.2c - NGET Reactive Compensation Equipment 2021/22 to 2029/30
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BURWELL | Addition | 2022 | BURW41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
BURWELL | Addition | 2022 | BURW41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
BOLNEY | Addition | 2024 | BOLN41 | 8 | 225 |  | Mechanically Switched Capacitor | 400
BOLNEY | Addition | 2024 | BOLN41 | 1 | 65 |  | Mechanically Switched Capacitor | 400
BOLNEY | Addition | 2024 | BOLN41 | 9 | 225 | 100 | SVC | 400
BRIDGEWATER | Remove | 2024 | BRWA2A | G | 60 | 60 | SVC | 275
NINEFIELD | Addition | 2024 | NINF41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
NINEFIELD | Addition | 2024 | NINF41 | 1 | 65 |  | Mechanically Switched Capacitor | 400
NINFIELD | Addition | 2024 | NINF41 | 9 | 225 | 100 | SVC | 400
PENTIR | Remove | 2024 | PENT41 | 1 |  | 200 | Reactor | 400
Sandford | Addition | 2024 | SAFO41 | 1 |  | 200 | Shunt Reactor | 400
Sandford | Addition | 2024 | SAFO41 | 2 |  | 200 | Shunt Reactor | 400
WIMBLEDON | Remove | 2024 | WIMB21 | 2 |  | 100 | Reactor | 275
WIMBLEDON | Remove | 2024 | WIMB21 | 4 |  | 100 | Reactor | 275
BRAINTREE | Addition | 2029 | BRAI11 | 1 |  | 200 | Reactor | 132
BRAINTREE | Addition | 2029 | BRAI11 | 2 |  | 200 | Reactor | 132

## B-4-2d
B.4.2d - OFTO Reactive Compensation Equipment, 2021/22 to 2029/30
Wind Farm | Year | Status | Node 1 | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage(kV)
Firth of Forth 1 Offshore Wind Farm | 2021 | Addition | FOFW21 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFW22 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFW23 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO21 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO21 | SHR2 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO21 | SHR3 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO31 | SVC1 | TBC | TBC | SVC | 33
| 2021 | Addition | FOFO32 | SVC2 | TBC | TBC | SVC | 33
Hornsea 1 offshore Wind Farm | 2021 | Addition | HOWA21 | VSR-3 |  | 300 | Shunt Reactor | 220
| 2021 | Addition | HOWR2A | SHR3 |  | 220 | Shunt Reactor | 220
| 2021 | Addition | HOWW23 | SHR1 |  | 135 | Shunt Reactor | 220
| 2021 | Addition | HOWA21 | SVC3 | 160 | 200 | SVC | 33
Moray East Offshore Wind Farm | 2021 | Addition | MOWE21 | SHR1 |  | 75 | Shunt Reactor | 220
| 2021 | Addition | MOWE22 | SHR1 |  | 75 | Shunt Reactor | 220
| 2021 | Addition | MOWE23 | SHR1 |  | 75 | Shunt Reactor | 220
| 2021 | Addition | MORF21 | SHR1A |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF21 | SHR1B |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF22 | SHR2A |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF22 | SHR2B |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF23 | SHR3A |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF23 | SHR3B |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF31 | MSR1 |  | 133 | Shunt Reactor | 33
| 2021 | Addition | MORF31 | SVC1 | 174 | 197 | SVC | 33
| 2021 | Addition | MORF32 | MSR2 |  | 133 | Shunt Reactor | 33
| 2021 | Addition | MORF32 | SVC2 | 174 | 197 | SVC | 33
| 2021 | Addition | MORF33 | MSR3 |  | 133 | Shunt Reactor | 33
| 2021 | Addition | MORF33 | SVC3 | 174 | 197 | SVC | 33
Triton Knoll Offshore Wind Farm | 2021 | Addition | TKNO21 | SHR1 |  | 172 | Shunt Reactor | 220
| 2021 | Addition | TKNE21 | SHR3 |  | 43 | Shunt Reactor | 220
| 2021 | Addition | TKNO32 | SVC1A | 143 | 143 | SVC | 33
| 2021 | Addition | TKNO32 | MSR1B |  | 163 | Shunt Reactor | 33
| 2021 | Addition | TKNO32 | MSR1C |  | 163 | Shunt Reactor | 33
Inch Cape Offshore Wind Farm | 2022 | Addition | INCO21 | TBC | TBC | TBC | SVC | LV-Tertiary
| 2022 | Addition | INCO22 | TBC | TBC | TBC | SVC | LV-Tertiary
| 2022 | Addition | INCW21 | TBC | TBC | TBC | SHR | 220
| 2022 | Addition | INCW22 | TBC | TBC | TBC | SHR | 220
| 2022 | Addition | INCO21 | TBC | TBC | TBC | SHR | 220
| 2022 | Addition | INCO22 | TBC | TBC | TBC | SHR | 220
Neart Na Gaoithe Offshore Wind Farm | 2022 | Addition | NNGW21 | 1 |  | 125 | SHR1 | 220
| 2022 | Addition | NNGW22 | 1 |  | 125 | SHR1 | 220
| 2022 | Addition | NNGO41 | TBC | 75 | 75 | SVC | 33(Tertiary)
| 2022 | Addition | NNGO42 | TBC | 75 | 75 | SVC | 33(Tertiary)
Dogger bank 1 offshore Wind Farm | 2024 | Addition | Dogger bank 1 Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Dogger bank 1 Offshore | TBC | TBC | TBC | SVC | TBC
Doggerbank 4 Offshore wind Farm | 2024 | Addition | Doggerbank 4 Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Doggerbank 4 Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Doggerbank 4 Onshore 400kV | 1 | TBC | TBC | SVC | 400
| 2024 | Addition | Doggerbank 4 Onshore 400kV | 2 |  | TBC | Shunt Reactor | 400
East Anglia 3 Offshore Wind Farm | 2024 | Addition | East Anglia Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | East Anglia Offshore | TBC | TBC | TBC | SVC | TBC
Hornsea 2 Offshore Wind Farm | 2024 | Addition | Hornsea 2A Offshore 220kV | 1 |  | 90 | SHR1 | 220
| 2024 | Addition | Hornsea 2B Offshore 220kV | 2 |  | 90 | SHR2 | 220
| 2024 | Addition | Hornsea 2C Offshore 220kV | 3 |  | 90 | SHR3 | 220
| 2024 | Addition | Hornsea 2A Offshore 220kV | TBC |  | 240 | SHR | 220
| 2024 | Addition | Hornsea 2B Offshore 220kV | TBC |  | 240 | SHR | 220
| 2024 | Addition | Hornsea 2C Offshore 220kV | TBC |  | 240 | SHR | 220
| 2024 | Addition | Hornsea 2A Onshore 220kV | 1 | 180 | 180 | DRC01 | 220
| 2024 | Addition | Hornsea 2B Onshore 220kV | 2 | 180 | 180 | DRC02 | 220
| 2024 | Addition | Hornsea 2C Onshore 220kV | 3 | 180 | 180 | DRC03 | 220
| 2024 | Addition | Hornsea 2A Onshore 220kV | 1 |  | 140-275 | VSR1 | 220
| 2024 | Addition | Hornsea 2B Onshore 220kV | 1 |  | 140-275 | VSR2 | 220
| 2024 | Addition | Hornsea 2C Onshore 220kV | 1 |  | 140-275 | VSR3 | 220
Hornsea 3 Offshore Wind Farm | 2024 | Addition | Hornsea 3A Onshore 400kV | 1 | TBC | TBC | Shunt Reactor | TBC
| 2024 | Addition | Hornsea 3A Onshore 400kV | 1 | TBC | TBC | SVC | TBC
Moray West Offshore Wind Farm | 2024 | Addition | Moray West Offshore P1 220kV | TBC | TBC | TBC | SHR | 220
| 2024 | Addition | Moray West Offshore P2 220kV | TBC | TBC | TBC | SHR | 220
Sofia Offshore Wind Farm | 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SHR | TBC
| 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SHR | TBC
| 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SVC | TBC
Dogger Bank 2 Offshore Wind Farm | 2026 | Addition | Onshore 400kV | 1 | TBC | TBC | SVC | 400
| 2026 | Addition | Onshore 400kV | 2 | TBC | TBC | SVC | 400
East Anglia 6A Offshore Wind Farm | 2026 | Addition | East Anglia 6A Onshore-1 | 1 | TBC | TBC | SVC | 400
East Anglia 6B Offshore Wind Farm | 2026 | Addition | East Anglia 6A Onshore-1 | 1 | TBC | TBC | SVC | 400
Firth of Forth 2 Offshore Wind Farm | 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 2 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 3 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 2 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 3 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 4 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 5 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 6 | TBC | TBC | Shunt Reactor | 400
Hornsea 3 Offshore Wind Farm | 2026 | Addition | Hornsea 3B Onshore 400kV | 1 | TBC | TBC | Shunt Reactor | TBC
| 2026 | Addition | Hornsea 3B Onshore 400kV | 1 | TBC | TBC | SVC | TBC
Sheringham and Dudgeon Extension Wind Farm | 2026 | Addition | Offshore 220kV-1 | 1 | TBC | TBC | Shunt Reactor | 220
| 2026 | Addition | Offshore 220kV-2 | 2 | TBC | TBC | Shunt Reactor | 220
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | Shunt Reactor | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-2 | 1 | TBC | TBC | Shunt Reactor | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | SVC | Tertiary Voltage
Codling Wind Farm | 2029 | 2029 | Codling Offshore 220kV | TBC |  | 243 | SHR | 220
| 2029 | 2029 | Codling Offshore 220kV | TBC |  | 243 | SHR | 220
| 2029 | 2029 | Codling Onshore 220kV | TBC |  | 650 | SHR | 220
| 2029 | 2029 | Codling Onshore 220kV | TBC |  | 450 | TCR | 220
EA One North Wind Farm | 2029 | 2029 | EA1N Offshore 220kV-1 | 1 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Offshore 220kV-2 | 2 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Onshore 220kV | 1 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Onshore 220kV | 2 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Onshore 400kV | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | 2029 | EA1N Onshore 400kV | 2 | TBC | TBC | SVC | Tertiary Voltage
East Anglia 4A Wind Farm | 2029 | 2029 | East Anglia 4A 400kV | 1 | TBC | TBC | SVC | 400
| 2029 | 2029 | East Anglia 4A 400kV | 1 |  | TBC | Shunt Reactor | 400
East Anglia 5A Wind Farm | 2029 | 2029 | East Anglia 5A 400kV | 1 | TBC | TBC | SVC | 400
| 2029 | 2029 | East Anglia 5A 400kV | 1 |  | TBC | Shunt Reactor | 400
Firth of Forth 2 Wind Farm | 2029 | Addition | Onshore 400kV-2 | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | Addition | Onshore 400kV-2 | 2 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | Addition | Onshore 400kV-2 | 3 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | Addition | Onshore 400kV-2 | 1 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 2 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 3 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 4 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 5 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 6 | TBC | TBC | Shunt Reactor | 400
Hornsea 4 Offshore Wind Farm | 2029 | 2029 | Offshore 275kV-1 | 1 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Offshore 275kV-2 | 2 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Offshore 275kV-3 | 3 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-1 | 1 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-2 | 2 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-3 | 3 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 1 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 2 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 3 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 4 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 5 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 6 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 1 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 275kV | 2 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 275kV | 3 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 400kV | 1 |  | 75 | Shunt Reactor | 400
| 2029 | 2029 | Offshore 275kV-4 | 4 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Offshore 275kV-5 | 5 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-2 | 4 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-3 | 5 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 7 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 8 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 9 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 10 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 4 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 275kV | 5 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 400kV | 2 |  | 75 | Shunt Reactor | 400
Racebank Extension Wind Farm | 2029 | Addition | Offshore Platform 220kV-1 | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Offshore Platform 220kV-2 | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Onshore 220kV-1 | 1 | TBC | TBC | VSR | TBC
| 2029 | Addition | Onshore 220kV-2 | 2 | TBC | TBC | VSR | TBC
| 2029 | Addition | Onshore 220kV-1 | 1 | TBC | TBC | SVC | TBC
| 2029 | Addition | Onshore 220kV-2 | 2 | TBC | TBC | SVC | TBC
Thanet Extension Wind Farm | 2029 | Addition | Offshore-1 | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Offshore-1 | 2 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Onshore 400kV | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Onshore 400kV | 1 | TBC | TBC | SVC | TBC
West of Orkney Wind Farm | 2029 | 2029 | West of Orkney Offshore 275kV | TBC |  | TBC | SHR | TBC
| 2029 | 2029 | West of Orkney Offshore 275kV | TBC |  | TBC | SHR | TBC
| 2029 | 2029 | West of Orkney Offshore 275kV | TBC | TBC | TBC | SVC | TBC
| 2029 | 2029 | West of Orkney Offshore 275kV | TBC | TBC | TBC | SVC | TBC

## B-5-1
B.5.1 - Intra GB HVDC 2020/21 to 2029/30
Interconnector Name | Existing | Planned from year | Node 1 | Node 2 | Type | Rated Voltage (kV) | Length(km) | Metallic Return | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Node 1 MVAr Gen | Node 1 MVAr Abs | Node 2 MVAr Gen | Node 2 MVAr Abs
Western HVDC Link | Yes | N/A | HUCS41 | FLIB41 | LCC | ±600 | 422 | No | 2250 | 2250 | 2250 | 2250 | 688 | 1946 | 1710 | 705
Caithness Moray Multi-Terminal Link - Terminal 1 | Yes | N/A | SPIT2 | Central DC Substation | VSC | ±320 | 31 | No | 800 | 800 | 800 | 800 | 263 | 263 | N/A | N/A
Caithness Moray Multi-Terminal Link - Terminal 2 | Yes | N/A | BLHI4 | Central DC Substation | VSC | ±320 | 136 | No | 1200 | 1200 | 1200 | 1200 | 394 | 394 | N/A | N/A
Caithness Moray Shetland Multi-Terminal Link - Terminal 3 | No | 2024 | KERG1 | Central DC Substation | VSC | ±320 | 269 | No | 600 | 600 | 600 | 600 | 197 | 197 | N/A | N/A
Western Isle HVDC Link | No | 2026 | BEAU4 | ARNI1 | VSC | ±320 | 159 | No | 600 | 600 | 600 | 600 | 197 | 197 | 197 | 197
Offshore HVDC - SCD1 | No | 2028 | SIZE41 | CANT41 | TBC | TBC | TBC | No | 2000 | 2000 | 2000 | 2000 | TBC | TBC | TBC | TBC
Eastern HVDC Link | No | 2029 | PEHE4 | DRAX41 | VSC | ±320 | 339 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | TBC | TBC
West of Orkney HVDC Link | No | 2029 | SPIT4 | PEHE4 | VSC | ±320 | 145 | No | 2250 | 2250 | 2250 | 2250 | 749 | 749 | 749 | 749
Eastern HVDC Link | No | 2029 | BRNX4- | HAWP41 | VSC | TBC | TBC | No | 2000 | 2000 | 2000 | 2000 | 660 | 660 | TBC | TBC