## Note
Note to 2020 ETYS Appendix B
All the ratings provided in the subsequent sections represent the post fault thermal ratings of the equipment, with the exception of those with the value '9999' (in tab B-2-1a). Elements with ratings of 9999 are representative of circuit breakers/bus couplers that are encountered during the PSS/e to PowerFactory conversion process. Additionally, there are few line circuit breakers included in tab B-2-1a with R=0.0100, X=0.0100 and B= 0.0000.
All future year data is non-binding and is liable to change.

## Menu
Electricity Ten Year Statement (ETYS) 2020
Appendix B - Supplementary Technical Data
Table | Title
B.1.1a | SHE Transmission Index of Substation Codes
B.1.1b | SPT Index of Substation Codes
B.1.1c | NGET Index of Substation Codes
B.1.1d | OFTO Index of Substation Codes
B.2.1a | SHE Transmission Circuits 2020/21
B.2.1b | SPT Circuits 2020/21
B.2.1c | NGET Circuits 2020/21
B.2.1d | OFTO Circuits 2020/21
B.2.2a | SHE Transmission Circuit Changes 2021/22 to 2029/30
B.2.2b | SPT Circuit Changes 2021/22 to 2029/30
B.2.2c | NGET Circuit Changes 2021/22 to 2029/30
B.2.2d | OFTO Circuit Changes 2021/22 to 2029/30
B.3.1a | SHE Transmission Transformers Winter 2020/21
B.3.1b | SPT Transformers Winter 2020/21
B.3.1c | NGET Transformers Winter 2020/21
B.3.1d | OFTO Transformers Winter 2020/21
B.3.2a | SHE Transmission Transformer Changes 2021/22 to 2029/30
B.3.2b | SPT Transformer Changes 2021/22 to 2029/30
B.3.2c | NGET Transformer Changes 2021/22 to 2029/30
B.3.2d | OFTO Transformer Changes 2021/22 to 2029/30
B.4.1a | SHE Transmission Reactive Compensation Equipment Winter 2020/21
B.4.1b | SPT Reactive Compensation Equipment Winter 2020/21
B.4.1c | NGET Reactive Compensation Equipment Winter 2020/21
B.4.1d | OFTO Reactive Compensation Equipment Winter 2020/21
B.4.2a | SHE Transmission Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.4.2b | SPT Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.4.2c | NGET Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.4.2d | OFTO Reactive Compensation Equipment Changes 2021/22 to 2029/30
B.5.1 | Intra GB HVDC 2020/21 to 2029/30

## B-1-1a
B.1.1a - SHE Transmission Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABBA | ABERDEEN BAY WINDFARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 33
ABNE | ABERNETHY | 132
ABNE | ABERNETHY | 33
ACHR | A-CHRUACH WINDFARM | 275
ACHR | A-CHRUACH WINDFARM | 132
ACHR | A-CHRUACH WINDFARM | 33
AIGA | AIGAS HYDRO | 132
ALNE | ALNESS GSP | 132
ALNE | ALNESS GSP | 33
ALTN | ALTNABREAC | 132
ALTN | ALTNABREAC | 33
ALYT | ALYTH | 400
ALYT | ALYTH | 275
ALYT | ALYTH | 33
AMUL | AMULREE | 132
ANSU | AN SUIDHE | 275
ANSU | AN SUIDHE | 132
ANSU | AN SUIDHE | 33
ARBR | ARBROATH | 132
ARBR | ARBROATH | 33
ARDK | ARDKINGLAS WIND | 132
ARDK | ARDKINGLAS WIND | 33
ARMO | ARDMORE | 132
ARMO | ARDMORE | 33
ARNI | ARNISH SUBSTATION | 132
ARNI | ARNISH SUBSTATION | 33
BALA | BALALLAN TEE POINT | 132
BEAT | BEATRICE SUBSTATION | 400
BEAU | BEAULY | 400
BEAU | BEAULY | 275
BEAU | BEAULY | 132
BEAU | BEAULY | 33
BEIN | BEINNEUN WIND FARM | 132
BEIN | BEINNEUN WIND FARM | 33
BERB | BERRY BURN | 275
BERB | BERRY BURN | 33
BETH | BEINN THARSUINN WIND | 132
BETH | BEINN THARSUINN WIND | 33
BEWF | BEAW FIELD | 132
BEWF | BEAW FIELD | 33
BHLA | BHLARAIDH WIND FARM | 132
BHLA | BHLARAIDH WIND FARM | 33
BIHI | BIRKHILL | 132
BLEX | BHLARAIDH EXTENSION | 132
BLEX | BHLARAIDH EXTENSION | 33
BLGH | BLARGHOUR | 132
BLGH | BLARGHOUR | 33
BLHI | BLACKHILLOCK | 400
BLHI | BLACKHILLOCK | 275
BLHI | BLACKHILLOCK | 132
BLHI | BLACKHILLOCK | 33
BOAG | BOAT OF GARTEN | 132
BOAG | BOAT OF GARTEN | 33
BRCW | BRACO WEST | 275
BRCW | BRACO WEST | 33
BREC | BRECHIN | 132
BRID | BRIDGE OF DUN | 132
BRID | BRIDGE OF DUN | 33
BROA | BROADFORD | 132
BROA | BROADFORD | 33
BROR | BRORA | 132
BROR | BRORA | 33
BUMU | BURGHMUIR | 132
BUMU | BURGHMUIR | 33
CAAD | CARRADALE | 132
CAAD | CARRADALE | 33
CAID | CAIRN DUHIE WIND FARM | 275
CAID | CAIRN DUHIE WIND FARM | 33
CAIN | CAIRNFORD | 275
CAIN | CAIRNFORD | 33
CASS | CASSLEY | 132
CASS | CASSLEY | 33
CEAN | CEANNACROC | 132
CEAN | CEANNACROC | 33
CHAR | CHARLESTON | 132
CHAR | CHARLESTON | 33
CLAC | CLACHAN | 132
CLAC | CLACHAN | 33
CLAY | CLAYHILLS | 132
CLAY | CLAYHILLS | 33
CLGO | CLASH GOUR WIND FARM | 275
CLGO | CLASH GOUR WIND FARM | 132
CLGO | CLASH GOUR WIND FARM | 33
CLOI | CLOICHE WIND FARM | 132
CLOI | CLOICHE WIND FARM | 33
CLSO | CLASHINDARROCH WIND FARM | 132
CLSO | CLASHINDARROCH WIND FARM | 33
CLUN | CLUNIE | 132
COGA | CORRIEGARTH WIND FARM | 132
COGA | CORRIEGARTH WIND FARM | 33
COGL | COIRE GLAS PUMPED STORAGE | 400
CONN | CONNAGILL | 275
CONN | CONNAGILL | 132
CONN | CONNAGILL | 33
CORI | CORRIEMOILLIE | 132
CORI | CORRIEMOILLIE | 33
COST | COSTA HEAD | 33
COUA | COUPAR ANGUS | 132
COUA | COUPAR ANGUS | 33
COUW | COUR WIND FARM | 33
CRAI | CRAIGIEBUCKLER | 132
CRAI | CRAIGIEBUCKLER | 33
CRDH | CREAG DHUBH | 275
CRDH | CREAG DHUBH | 132
CRDH | CREAG DHUBH | 33
CREA | CREAG RIABHACH WINDFARM | 132
CREA | CREAG RIABHACH WINDFARM | 33
CRSS | CROSSAIG | 275
CRSS | CROSSAIG | 220
CRSS | CROSSAIG | 132
CRSS | CROSSAIG | 33
CULL | CULLIGRAN | 132
DAAS | DALLAS SUBSTATION | 275
DAAS | DALLAS SUBSTATION | 33
DEAN | DEANIE | 132
DENS | DENSIDE | 132
DLCH | DALCHORK | 132
DONW | DOUNREAY WEST | 275
DORE | DORENELL WIND FARM | 132
DORE | DORENELL WIND FARM | 33
DOUN | DOUNREAY | 400
DOUN | DOUNREAY | 275
DOUN | DOUNREAY | 220
DOUN | DOUNREAY | 132
DOUN | DOUNREAY | 33
DRUL | DRUIM LETHANN WIND FARM | 132
DRUL | DRUIM LETHANN WIND FARM | 33
DUBE | DUNBEATH | 132
DUBE | DUNBEATH | 33
DUCC | DUNMORE CABLE COMPOUND | 132
DUDH | DUDHOPE | 132
DUDH | DUDHOPE | 33
DUGR | DUNVEGAN GRID | 132
DUGR | DUNVEGAN GRID | 33
DUNM | DUNMAGLASS | 132
DUNM | DUNMAGLASS | 33
DUNO | DUNOON | 132
DUNO | DUNOON | 33
DYCE | DYCE | 132
DYCE | DYCE | 33
EDIN | EDINBANE 132/33KV | 132
EDIN | EDINBANE 132/33KV | 33
ELCH | ELCHIES | 132
ELCH | ELCHIES | 33
ELGI | ELGIN | 132
ELGI | ELGIN | 33
ENEI | ENERGY ISLES WIND FARM | 132
ENEI | ENERGY ISLES WIND FARM | 33
ERRO | ERROCHTY | 132
FAAR | FARR WINDFARM | 132
FAAR | FARR WINDFARM | 33
FARI | FARIGAIG | 275
FARI | FARIGAIG | 132
FARI | FARIGAIG | 33
FASN | FASNAKYLE | 275
FASN | FASNAKYLE | 33
FAUG | FORT AUGUSTUS | 400
FAUG | FORT AUGUSTUS | 275
FAUG | FORT AUGUSTUS | 132
FAUG | FORT AUGUSTUS | 33
FERO | FERNOCH WIND | 132
FERO | FERNOCH WIND | 33
FETT | FETTERESSO | 400
FETT | FETTERESSO | 275
FETT | FETTERESSO | 132
FETT | FETTERESSO | 33
FIDD | FIDDES | 132
FIDD | FIDDES | 33
FINL | FINLARIG | 132
FINS | ORKNEY FINSTOWN | 132
FINS | ORKNEY FINSTOWN | 33
FOFO | FIRTHOF FORTH ONSHORE | 275
FOGG | FOGGIETON | 132
FOYE | FOYERS | 275
FRAS | FRASERBURGH | 132
FRAS | FRASERBURGH | 33
FWIL | FORT WILLIAM | 132
FWIL | FORT WILLIAM | 33
FYRI | FYRISH | 275
FYRI | FYRISH | 132
FYRI | FYRISH | 33
GILB | GILLS BAY SUBSTATION | 132
GLAG | GLENAGNES | 132
GLDO | GLENDOE SUBSTATION | 132
GLEN | GLENMORISTON | 132
GLFA | GLENFARCLAS | 132
GLFA | GLENFARCLAS | 33
GLKO | GLEN KYLLACHY WIND FARM - ONSHORE | 132
GLKO | GLEN KYLLACHY WIND FARM - ONSHORE | 33
GLNU | GLEN ULLINISH WINDFARM | 132
GLNU | GLEN ULLINISH WINDFARM | 33
GLSH | GELNSHERO WINDFARM | 132
GLSH | GELNSHERO WINDFARM | 33
GORW | GORDONBUSH WINDFARM | 275
GORW | GORDONBUSH WINDFARM | 33
GRIF | GRIFFIN WINDFARM (SSE) | 132
GRIF | GRIFFIN WINDFARM (SSE) | 33
GRUB | GRUDIE BRIDGE | 132
GRUB | GRUDIE BRIDGE | 33
HEST | HESTA HEAD | 33
INGA | INVERGARRY | 400
INGA | INVERGARRY | 132
INGA | INVERGARRY | 33
INNE | INVERNESS | 132
INNE | INVERNESS | 33
INRU | INVERUGIE | 132
INVE | INVERARAY | 132
INVR | INVERARNAN | 132
INVR | INVERARNAN | 33
KEIT | KEITH | 275
KEIT | KEITH | 132
KEIT | KEITH | 33
KIIN | KILLIN | 132
KIIN | KILLIN | 33
KILC | KILLIN CASCADE GROUP | 132
KILO | KINLOCHLEVEN 132KV SUBSTATION | 132
KILO | KINLOCHLEVEN 132KV SUBSTATION | 33
KINA | KINARDOCHY | 275
KINB | KINCARDINE BOUNDARY | 275
KINT | KINTORE | 400
KINT | KINTORE | 275
KINT | KINTORE | 132
KINT | KINTORE | 33
KIOR | KILMORACK | 132
KNOC | KNOCKNAGAEL | 275
KNOC | KNOCKNAGAEL | 132
KNOC | KNOCKNAGAEL | 33
LAGG | LAGGAN | 132
LAIR | LAIRG | 132
LAIR | LAIRG | 33
LIMK | LIMEKILNS WINDFARM | 132
LIMK | LIMEKILNS WINDFARM | 33
LOCB | LOCH BUIDHE | 275
LOCB | LOCH BUIDHE | 132
LOCB | LOCH BUIDHE | 33
LOCH | LOCHAY | 132
LOCL | LOCH LUNDIE | 132
LUIC | LUICHART | 132
LUMB | LUMBS | 132
LUNA | LUNANHEAD | 132
LUNA | LUNANHEAD | 33
LUND | LUNDAVRA | 132
LYND | LYNDHURST | 132
LYND | LYNDHURST | 33
MACD | MACDUFF | 132
MACD | MACDUFF | 33
MELG | MELGARVE SUBSTATION | 400
MELG | MELGARVE SUBSTATION | 132
MELG | MELGARVE SUBSTATION | 33
MILC | MILTON OF CRAIGIE | 132
MILC | MILTON OF CRAIGIE | 33
MILS | MILLENNIUM SOUTH WINDFARM | 132
MILS | MILLENNIUM SOUTH WINDFARM | 33
MILW | MILLENIUM WIND | 132
MILW | MILLENIUM WIND | 33
MORF | MORAY EAST ONSHORE SUBSTATION | 400
MORF | MORAY EAST ONSHORE SUBSTATION | 275
MOSS | MOSSFORD | 132
MOTA | MOULTAIVE | 132
MSHL | MOSSY HILL | 132
MSHL | MOSSY HILL | 33
MUAI | MUAITHEBHEAL WIND FARM | 132
MUAI | MUAITHEBHEAL WIND FARM | 33
MYBE | MYBSTER EXTENSION | 132
MYBS | MYBSTER | 132
MYBS | MYBSTER | 33
NAIR | NAIRN | 132
NAIR | NAIRN | 33
NANT | NANT (LOCH NANT) | 132
NEDE | NEW DEER | 400
NEDE | NEW DEER | 275
NESQ | NESS OF QUOYS | 33
NWGL | NORTH CONNECT (NORWEGIAN LINK 2) | 400
OFPH | OFFSHORE PROJECT H | 275
OFPK | OFFSHORE PROJECT K | 400
OFPN | OFFSHORE PROJECT N | 400
ORRI | ORRIN | 132
ORRI | ORRIN | 33
PEHE | PETERHEAD | 400
PEHE | PETERHEAD | 275
PEHE | PETERHEAD | 132
PEHE | PETERHEAD | 33
PEHG | PETERHEAD GRANGE | 132
PEHG | PETERHEAD GRANGE | 33
PENF | PENTLAND FIRTH (MEYGEN) | 132
PENF | PENTLAND FIRTH (MEYGEN) | 33
PERS | PERSLEY | 275
PERS | PERSLEY | 132
PERS | PERSLEY | 33
PORA | PORT ANN | 275
PORA | PORT ANN | 132
PORA | PORT ANN | 33
QUOI | QUOICH | 132
RANN | RANNOCH | 132
RANN | RANNOCH | 33
REDM | REDMOSS | 132
REDM | REDMOSS | 33
ROTI | ROTHIENORMAN | 400
ROTI | ROTHIENORMAN | 275
ROTI | ROTHIENORMAN | 132
ROTI | ROTHIENORMAN | 33
SALA | SALLACHY WIND FARM | 132
SALA | SALLACHY WIND FARM | 33
SFEE | ST FERGUS EAST | 132
SFEG | ST FERGUS GAS TERMINAL | 132
SFEM | ST FERGUS MOBIL | 132
SFER | ST FERGUS | 132
SFEV | ST FERGUS VSD | 132
SFIL | ST FILLANS | 132
SHDM | SHEIRDRIM | 132
SHDM | SHEIRDRIM | 33
SHET | SHETLAND 132KV SUBSTATION | 132
SHIN | SHIN | 132
SHIN | SHIN | 33
SLKB | SLACKBUIE | 132
SLOY | SLOY | 132
SPIT | SPITTAL | 400
SPIT | SPITTAL | 275
SPIT | SPITTAL | 132
SPIT | SPITTAL | 33
STOR | STORNOWAY | 132
STRB | STRATH BRORA WIND | 275
STRB | STRATH BRORA WIND | 33
STRI | STRICHEN | 132
STRI | STRICHEN | 33
STRL | STRONELAIRG WIND FARM (SSE) | 132
STRL | STRONELAIRG WIND FARM (SSE) | 33
STRW | STRATHY WIND | 132
STRW | STRATHY WIND | 33
STWN | STORNOWAY WIND | 132
STWN | STORNOWAY WIND | 33
TARL | TARLAND | 132
TARL | TARLAND | 33
TAYN | TAYNUILT | 132
TAYN | TAYNUILT | 33
TEAL | TEALING | 275
TEAL | TEALING | 132
TEAL | TEALING | 33
THSO | THURSO | 132
THUS | THURSO SOUTH | 275
THUS | THURSO SOUTH | 132
THUS | THURSO SOUTH | 33
TOMT | TOMATIN | 275
TOMT | TOMATIN | 132
TOMT | TOMATIN | 33
TUMB | TUMMEL BRIDGE | 132
TUMM | TUMMEL | 400
TUMM | TUMMEL | 275
TUMM | TUMMEL | 132
TUMM | TUMMEL | 33
WHIB | WHITE BRIDGE | 132
WILW | WILLOW | 132
WIOW | WILLOWDALE | 132
WIOW | WILLOWDALE | 33
WOHI | WOODHILL | 132
WOHI | WOODHILL | 33
YELL | YELL | 132

## B-1-1b
B.1.1b - SPT Index of Substation Codes
Site Code | Site Name | Voltage (kV)
AIKE | AIKENGALL | 33
AIRI | AIRIES | 33
ANDE | ANDERSHAW | 33
AREC | ARECLEOCH | 132
AREC | ARECLEOCH | 33
AREX | ARECLEOCH EXTENSION | 132
AREX | ARECLEOCH EXTENSION | 33
ARFO | ARTFIELD FOREST WF | 33
ASVA | ASSEL VALLEY | 33
AUCH | AUCHENCROSH | 275
AUCW | AUCHENWYND | 132
AURO | AUCHROBERT | 33
AYR- | AYR | 275
AYR- | AYR | 33
BAGA | BATHGATE | 132
BAGA | BATHGATE | 33
BAGA | BATHGATE RAIL | 25
BAIN | BAINSFORD | 33
BENB | BENBRACK WIND FARM | 132
BENB | BENBRACK WIND FARM | 33
BERW | BERWICK | 132
BERW | BERWICK | 33
BLAH | BLACKHILL | 132
BLAH | BLACKHILL | 33
BLCW | BLACKCRAIG | 132
BLCW | BLACKCRAIG | 33
BLKL | BLACKLAW | 132
BLKL | BLACKLAW | 33
BLLX | BLACKLAW EXTENSION | 132
BLLX | BLACKLAW EXTENSION | 33
BONB | BONNYBRIDGE BORDER NODE | 400
BONB | BONNYBRIDGE BORDER NODE | 275
BONN | BONNYBRIDGE | 400
BONN | BONNYBRIDGE | 132
BONN | BONNYBRIDGE | 33
BONN | BONNYBRIDGE | 25
BPGR | BP GRANGEMOUTH | 33
BRAE | BRAEHEAD | 132
BRAP | BRAEHEAD PARK | 132
BRAP | BRAEHEAD PARK | 33
BRNX | BRANXTON | 400
BROC | BROKEN CROSS | 132
BROX | BROXBURN | 132
BROX | BROXBURN | 33
BUSB | BUSBY | 275
CAFA | CARSFAD | 132
CAFA | CARSFAD | 11
CALD | CALDER WATER | 33
CAMI | CAMILLA BES | 33
CATY | CARNTYNE | 132
CATY | CARNTYNE | 33
CATY | CARNTYNE | 25
CHAP | CHAPELCROSS | 132
CHAP | CHAPELCROSS | 33
CHAS | CHARLOTTE STREET | 275
CHAS | CHARLOTTE STREET | 33
CHMO | CHIRMORIE | 132
CLAU | CLAUCHRIE | 132
CLAU | CLAUCHRIE | 33
CLYM | CLYDE'S MILL | 275
CLYM | CLYDE'S MILL | 33
CLYN | CLYDE NORTH | 275
CLYN | CLYDE NORTH | 33
CLYS | CLYDE SOUTH | 275
CLYS | CLYDE SOUTH | 33
COAL | COALBURN | 400
COAL | COALBURN | 132
COAL | COALBURN | 33
COAT | COATBRIDGE | 275
COAT | COATBRIDGE | 33
COCK | COCKENZIE | 400
COCK | COCKENZIE | 275
COCK | COCKENZIE | 33
COYL | COYLTON | 275
COYL | COYLTON | 132
COYL | COYLTON | 33
COYT | COYLTON TEE | 132
COYW | COYLTON WEST | 275
CRCK | CARRICK | 275
CRCK | CARRICK | 33
CRDE | CROSSDYKES EXTENSION | 33
CRDY | CROSSDYKES | 33
CROE | CROOKEDSTANE | 33
CROO | CROOKSTON | 132
CROO | CROOKSTON | 33
CRUA | CRUACHAN | 275
CRYR | CRYSTAL RIG | 400
CRYR | CRYSTAL RIG | 132
CRYR | CRYSTAL RIG | 33
CUMB | CUMBERNAULD | 132
CUMB | CUMBERNAULD | 33
CUMH | CUMBERHEAD | 132
CUMH | CUMBERHEAD WF SUBSTATION | 33
CUMW | CUMBERHEAD WEST | 132
CUMW | CUMBERHEAD WEST | 33
CUPA | CUPAR | 132
CUPA | CUPAR | 33
CURR | CURRIE | 275
CURR | CURRIE | 132
CURR | CURRIE | 33
CURR | CURRIE | 25
CURR | CURRIE | 11
DALB | DALMALLY BORDER NODE | 275
DALL | DALMALLY | 275
DALM | DALMARNOCK | 275
DALM | DALMARNOCK | 132
DALM | DALMARNOCK | 33
DALQ | DALQUHANDY | 33
DALS | DALSWINTON | 33
DENN | DENNY NORTH | 400
DENN | DENNY NORTH | 275
DENN | DENNY NORTH | 132
DENN | DENNY NORTH | 33
DESA | DERSALLOCH | 33
DEVM | DEVOL MOOR | 400
DEVM | DEVOL MOOR | 132
DEVM | DEVOL MOOR | 33
DEVM | DEVOL MOOR | 25
DEVO | DEVONSIDE | 132
DEVO | DEVONSIDE | 33
DEWP | DEWAR PLACE | 275
DEWP | DEWAR PLACE | 33
DONO | DOUGLAS NORTH | 132
DOWE | DOUGLAS WEST | 33
DOWX | DOUGLAS WEST EXTENSION | 33
DRCR | DRUMCROSS | 132
DRCR | DRUMCROSS | 33
DRUM | DRUMCHAPEL | 275
DRUM | DRUMCHAPEL | 33
DUMF | DUMFRIES | 132
DUMF | DUMFRIES | 33
DUNB | DUNBAR | 132
DUNB | DUNBAR | 33
DUNE | DUNLAW EXTENSION | 132
DUNE | DUNLAW EXTENSION | 33
DUNF | DUNFERMLINE | 132
DUNF | DUNFERMLINE | 33
DUNH | DUNHILL | 33
EARB | EARLSBURN | 33
EAST | EARLSTOUN | 132
EAST | EARLSTOUN | 11
ECCF | ECCLEFECHAN | 132
ECCF | ECCLEFECHAN | 25
ECCL | ECCLES | 400
ECCL | ECCLES | 132
ECCL | ECCLES | 33
EERH | EASTERHOUSE | 275
EERH | EASTERHOUSE | 33
EKIL | EAST KILBRIDE | 275
EKIL | EAST KILBRIDE | 33
EKIS | EAST KILBRIDE SOUTH | 275
EKIS | EAST KILBRIDE SOUTH | 33
ELDE | ELDERSLIE | 132
ELDE | ELDERSLIE | 33
ELVA | ELVANFOOT | 400
ELVA | ELVANFOOT | 275
ELVA | ELVANFOOT | 132
ELVA | ELVANFOOT | 33
ELVA | ELVANFOOT | 25
ELVN | ELVANFOOT NORTH 132KV | 132
ELVN | ELVANFOOT NORTH 400KV | 400
ENHI | ENOCH HILL | 132
ENHI | ENOCH HILL WIND FARM | 33
ERSK | ERSKINE | 132
ERSK | ERSKINE | 33
ESST | ESSENSIDE | 132
EUCH | EUCHANHEAD | 33
EUCH | EUCHANHEAD | 132
EWEH | EWE HILL | 132
EWEH | EWE HILL | 33
EXON | EXXON MOBIL | 33
EXON | EXXON MOBIL | 11
FALL | FALLAGO | 400
FALL | FALLAGO | 33
FASI | FAW SIDE | 132
FIFE | FIFE ENERGY | 132
FINN | FINNIESTON | 132
FINN | FINNIESTON | 33
GALA | GALASHIELS | 132
GALA | GALASHIELS | 33
GARB | GARELOCH BOUNDARY | 132
GARE | GARELOCH | 132
GAWH | GALAWHISTLE | 132
GAWH | GALAWHISTLE | 33
GBRN | GREENBURN | 132
GHPS | GLENMUCKLOCH | 400
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 132
GIFF | GIFFNOCK | 275
GIFF | GIFFNOCK | 33
GLAP | GLEN APP | 33
GLGL | GLENGLASS | 132
GLGL | GLENGLASS | 33
GLLE | GLENLEE | 132
GLLE | GLENLEE | 11
GLLU | GLENLUCE | 132
GLLU | GLENLUCE | 33
GLMU | GLENMUCKLOCH | 33
GLNI | GLENNISTON | 132
GLNI | GLENNISTON | 33
GLRB | GLENROTHES BOUNDARY | 275
GLRO | GLENROTHES | 275
GLRO | GLENROTHES | 33
GNSH | GLENSHIMMEROCH | 132
GNSH | GLENSHIMMEROCH | 33
GORG | GORGIE | 132
GORG | GORGIE | 33
GOVA | GOVAN | 132
GOVA | GOVAN | 33
GRGR | GREENGAIRS WIND FARM | 33
GRMO | GRANGEMOUTH | 275
GRMO | GRANGEMOUTH | 33
GRNA | GRETNA | 400
GRNA | GRETNA | 132
GRNA | GRETNA | 33
HADH | HADYARD HILL | 132
HADH | HADYARD HILL | 33
HAGH | HAGSHAW HILL PHASE 2 | 33
HAGR | HAGGS ROAD | 132
HAGR | HAGGS ROAD | 33
HAGS | HAGSHAW HILL PHASE 1 | 33
HAKB | HARKER BORDER NODE | 400
HAKB | HARKER BORDER NODE | 132
HARE | HARESTANES | 132
HARE | HARESTANES | 33
HARG | HARTING RIG | 33
HARH | HARBURN HEAD | 33
HAWI | HAWICK | 132
HAWI | HAWICK | 33
HELE | HELENSBURGH | 132
HELE | HELENSBURGH | 33
HOLM | HOLM HILL | 132
HOPR | HOPSRIG | 132
HUCS | HUNTERSTON CONVERTER STATION | 400
HUER | HUNTERSTON | 400
HUER | HUNTERSTON | 132
HUER | HUNTERSTON | 33
HUNE | HUNTERSTON EAST | 400
HUNF | HUNTERSTON FARM | 132
HUNF | HUNTERSTON FARM | 33
HUNN | HUNTERSTON NORTH | 220
INKE | INVERKEITHING | 132
INKE | INVERKEITHING | 33
INVB | INVERARNAN BORDER | 275
INVR | INVERARNAN | 275
INWI | INNERWICK | 132
INWI | INNERWICK | 25
JOHN | JOHNSTONE | 33
JUNA | JUNCTION A | 132
JUNV | JUNCTION V | 132
KAIM | KAIMES | 275
KAIM | KAIMES | 33
KEIH | KEITHSHILL | 33
KENE | KENNOXHEAD WINDFARM EXTENSION | 33
KENN | KENNOXHEAD | 132
KENN | KENNOXHEAD | 33
KEOO | KENDOON | 132
KEOO | KENDOON | 11
KIER | KILLERMONT | 132
KIER | KILLERMONT | 33
KILB | KILBOWIE | 132
KILB | KILBOWIE | 33
KILB | KILBOWIE | 11
KILG | KILGALLIOCH | 275
KILG | KILGALLIOCH | 33
KILS | KILMARNOCK SOUTH | 400
KILS | KILMARNOCK SOUTH | 275
KILS | KILMARNOCK SOUTH | 132
KILS | KILMARNOCK SOUTH | 33
KILT | KILMARNOCK TOWN | 275
KILT | KILMARNOCK TOWN | 33
KILW | KILWINNING | 132
KILW | KILWINNING | 33
KINB | KINCARDINE BOUNDARY | 275
KINC | KINCARDINE | 275
KINC | KINCARDINE | 33
KNOK | KNOCKODHAR | 132
KNOK | KNOCKODHAR | 33
KYPE | KYPE MUIR | 132
KYPE | KYPE MUIR | 33
LAMB | LAMBHILL | 275
LEGO | LESMAHAGOW | 132
LEGO | LESMAHAGOW GSP | 33
LETH | LETHANS | 132
LEVE | LEVEN | 33
LEVT | LEVEN TEE | 132
LING | LIVINGSTON | 132
LING | LIVINGSTON | 33
LINM | LINNMILL | 132
LINM | LINNMILL | 33
LOAN | LONGANNET | 275
LOBU | LONGHILL BURN WF | 33
LOGN | LOCHGOIN | 33
LOPA | LONGPARK | 33
LORG | LORG COLLECTOR SUBSTATION | 132
LORG | LORG WIND FARM | 33
MAHI | MARK HILL | 275
MAHI | MARK HILL | 132
MAHI | MARK HILL | 33
MARG | MARGREE | 132
MARM | MARSHALL MEADOWS | 132
MAYB | MAYBOLE | 132
MAYB | MAYBOLE | 33
MAYT | MAYBOLE TEE | 132
MEAD | MEADOWHEAD | 132
MEAD | MEADOWHEAD | 11
MIDM | MIDDLE MUIR | 132
MIDM | MIDDLE MUIR | 33
MINN | MINNYGAP | 33
MINS | MINSCA | 33
MOFF | MOFFAT | 400
MOFF | MOFFAT | 132
MOFF | MOFFAT GSP | 33
MONQ | MONQUHILL | 33
MOSH | MOSSMORRAN SHELL | 132
MOSH | MOSSMORRAN SHELL | 11
MOSM | MOSSMORRAN | 275
MOSM | MOSSMORRAN | 132
MOSM | MOSSMORRAN | 33
NEAR | NEWARTHILL | 275
NEAR | NEWARTHILL | 33
NECU | NEW CUMNOCK | 275
NECU | NEW CUMNOCK | 132
NECU | NEW CUMNOCK | 33
NEIL | NEILSTON | 400
NEIL | NEILSTON | 275
NEIL | NEILSTON | 132
NEIL | NEILSTON | 33
NETS | NEWTON STEWART | 132
NETS | NEWTON STEWART | 33
NLEI | NORTH LOWTHER | 33
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 132
NOKY | NORTH KYLE | 132
NOKY | NORTH KYLE | 33
OFOA | OLD FOREST OF AE | 132
OFOA | OLD FOREST OF AE | 33
OHLL | OVERHILL | 132
OHLL | OVERHILL | 33
PAIS | PAISLEY | 132
PAIS | PAISLEY | 33
PART | PARTICK | 132
PART | PARTICK | 33
PENC | PENCLOE | 33
POGB | POGBIE | 33
POLK | POLKEMMET | 33
POOB | PORTOBELLO | 275
POOB | PORTOBELLO | 33
POOB | PORTOBELLO | 25
PORD | PORT DUNDAS | 275
PORD | PORT DUNDAS | 33
PRST | PRIESTGILL | 33
RAVE | RAVENSCRAIG | 33
REDH | REDHOUSE | 132
REDH | REDHOUSE | 33
ROAR | ROARING HILL | 33
ROBP | ROTHES BIOPOWER | 33
SACO | SALTCOATS | 132
SACO | SALTCOATS | 33
SACO | SALTCOATS | 25
SAKN | SANDY KNOWE | 132
SAKN | SANDY KNOWE | 33
SANQ | SANQUHAR WIND FARM | 132
SANX | ST ANDREWS CROSS | 132
SANX | ST ANDREWS CROSS | 33
SANX | ST ANDREWS CROSS | 25
SCOP | SCOOP HILL WIND FARM | 132
SHRG | SHEPHERDS RIG | 132
SHRG | SHEPHERDS RIG | 33
SHRU | SHRUBHILL | 275
SHRU | SHRUBHILL | 33
SIGH | SIGHTHILL | 275
SIGH | SIGHTHILL | 33
SMEA | SMEATON | 400
SMEA | SMEATON | 275
SMEA | SMEATON | 132
SMEA | SMEATON | 33
SNED | SNEDDON LAW | 33
SNQR | SANQUHAR | 33
SOKY | SOUTH KYLE | 132
SOKY | SOUTH KYLE | 33
SOLW | SOLWAY BANK | 33
SPAV | SPANGO VALLEY | 132
SPAV | SPANGO VALLEY | 33
STCR | STEVEN'S CROFT | 33
STHA | STRATHAVEN | 400
STHA | STRATHAVEN | 275
STHA | STRATHAVEN | 33
STIR | STIRLING | 132
STIR | STIRLING | 33
STLE | STRATHLEVEN | 132
STLE | STRATHLEVEN | 33
STLE | STRATHLEVEN | 25
STNO | STRANOCH | 132
STNO | STRANOCH | 33
STWB | STELLA WEST BORDER NODE | 400
TELR | TELFORD ROAD | 132
TELR | TELFORD ROAD | 33
TODD | TODDLEBURN | 33
TONG | TONGLAND | 132
TONG | TONGLAND | 33
TONG | TONGLAND | 11
TORH | TORR HILL | 33
TORM | TORMYWHEEL | 33
TORN | TORNESS | 400
TORN | TORNESS | 132
TORN | TORNESS | 33
TRLO | TRALORG | 33
TRSN | TROSTON | 132
TRSN | TROSTON | 33
TWEN | TWENTYSHILLING | 33
VIRD | VIRIDOR | 33
WESE | WESTERDOD | 132
WFIB | WESTFIELD BOUNDARY | 275
WFIE | WESTFIELD | 275
WFIE | WESTFIELD | 132
WFIE | WESTFIELD | 33
WGEO | WEST GEORGE STREET | 275
WGEO | WEST GEORGE STREET | 33
WHBR | WHITELAW BRAE | 33
WHHO | WHITEHOUSE | 275
WHHO | WHITEHOUSE | 33
WHLL | WHITESIDE HILL | 33
WHTB | WHISTLEFIELD BOUNDARY | 132
WHTL | WHISTLEFIELD | 132
WHTL | WHISTLEFIELD | 33
WISH | WISHAW (GOWKTHRAPPLE) | 400
WISH | WISHAW (GOWKTHRAPPLE) | 275
WISH | WISHAW (GOWKTHRAPPLE) | 132
WISH | WISHAW (GOWKTHRAPPLE) | 33
WISH | WISHAW (GOWKTHRAPPLE) | 25
WIYH | WINDYHILL | 400
WIYH | WINDYHILL | 275
WIYH | WINDYHILL | 132
WIYH | WINDYHILL | 33
WLEE | WHITELEE | 275
WLEE | WHITELEE | 33
WLEX | WHITELEE EXTENSION | 275
WLEX | WHITELEE EXTENSION | 33
WNDR | WINDY RIG | 33

## B-1-1c
B.1.1c - NGET Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABTH | ABERTHAW | 275
ABTH | ABERTHAW | 132
ABHA | ABHAM | 400
ABHA | ABHAM | 132
ACTL | ACTON LANE | 22
ALDW | ALDWARKE | 275
ALST | ALPHA STEEL | 33
ALVE | ALVERDISCOTT | 400
ALVE | ALVERDISCOTT | 132
AMEM | AMERSHAM MAIN | 400
AMEM | AMERSHAM MAIN | 132
AUST | AUST | 400
AXMI | AXMINSTER | 400
BAGB | BAGLAN BAY | 275
BARK | BARKING | 400
BARK | BARKING | 275
BARK | BARKING | 132
BARP | BARKING PS | 275
BEDD | BEDDINGTON | 400
BEDD | BEDDINGTON | 275
BEDD | BEDDINGTON | 132
BEDT | BEDDINGTON TEE | 132
BESW | BERKSWELL | 275
BESW | BERKSWELL | 132
BICF | BICKER FEN | 400
BICF | BICKER FEN | 132
BIRK | BIRKENHEAD | 275
BIRK | BIRKENHEAD | 132
BISW | BISHOPS WOOD | 275
BISW | BISHOPS WOOD | 132
BLYT | BLYTH | 400
BLYT | BLYTH | 275
BLYT | BLYTH | 132
BLYT | BLYTH | 66
BODE | BODELWYDDAN | 400
BODE | BODELWYDDAN | 132
BOLN | BOLNEY | 400
BOLN | BOLNEY | 132
BOTW | BOTLEY WOOD | 400
BOTW | BOTLEY WOOD | 132
BRAW | BRADFORD WEST | 400
BRAW | BRADFORD WEST | 275
BRAW | BRADFORD WEST | 132
BRAI | BRAINTREE | 132
BRAI | BRAINTREE | 400
BRFO | BRAMFORD | 400
BRFO | BRAMFORD | 132
BRLE | BRAMLEY | 400
BRLE | BRAMLEY | 132
BRED | BREDBURY | 275
BRED | BREDBURY | 132
BRGN | BRELSTON GREEN | 400
BRWA | BRIDGWATER | 400
BRWA | BRIDGWATER | 275
BRIM | BRIMSDOWN | 275
BRIM | BRIMSDOWN | 132
BRIN | BRINSWORTH | 400
BRIN | BRINSWORTH | 275
BRIT | BRITNED | 400
BULL | BULLS LODGE | 400
BURW | BURWELL MAIN | 400
BURW | BURWELL MAIN | 132
BUSH | BUSHBURY | 400
BUSH | BUSHBURY | 275
BUSH | BUSHBURY | 132
BUST | BUSTLEHOLME | 400
BUST | BUSTLEHOLME | 275
BUST | BUSTLEHOLME | 132
CAML | CAMBLESFORTH | 66
CAMA | CAMBRIDGE ARMS | 132
CANT | CANTERBURY NORTH | 132
CANT | CANTERBURY NORTH | 400
CAPE | CAPENHURST | 400
CAPE | CAPENHURST | 275
CAPE | CAPENHURST | 132
CARE | CARDIFF EAST | 275
CARE | CARDIFF EAST | 132
CARR | CARRINGTON | 400
CARR | CARRINGTON | 275
CARR | CARRINGTON | 132
CELL | CELLARHEAD | 400
CELL | CELLARHEAD | 132
CHUE | CHAFFORD HUNDRED EAST | 400
CHUW | CHAFFORD HUNDRED WEST | 400
CHSI | CHESSINGTON | 275
CHSI | CHESSINGTON | 132
CHTE | CHESTERFIELD | 275
CHTE | CHESTERFIELD | 132
CHTM | CHETNEY MARSH | 400
CHIC | CHICKERELL | 400
CHIC | CHICKERELL | 132
CHIL | CHILLING | 400
CILF | CILFYNYDD | 400
CILF | CILFYNYDD | 275
CITR | CITY ROAD | 400
CITR | CITY ROAD | 132
CLEH | CLEVE HILL | 400
CONQ | CONNAHS QUAY | 400
CONQ | CONNAHS QUAY | 132
COSO | CORYTON SOUTH | 400
COTT | COTTAM | 400
COVE | COVENTRY | 275
COVE | COVENTRY | 132
COWB | COWBRIDGE | 275
COWT | COWBRIDGE TEE | 275
COWL | COWLEY | 400
COWL | COWLEY | 132
CREB | CREYKE BECK | 400
CREB | CREYKE BECK | 275
CREB | CREYKE BECK | 132
CULJ | CULHAM JET | 400
DAIN | DAINES | 400
DAIN | DAINES | 275
DAMC | DAMHEAD CREEK | 400
DEES | DEESIDE | 400
DIDC | DIDCOT | 400
DINO | DINORWIG | 400
DRAK | DRAKELOW | 400
DRAK | DRAKELOW | 275
DRAK | DRAKELOW | 132
DRAX | DRAX | 400
DRAX | DRAX | 132
DUBR | DUNFORD BRIDGE | 400
DUNG | DUNGENESS | 400
DUNG | DUNGENESS | 275
EALI | EALING | 66
EALI | EALING | 275
ECLA | EAST CLAYDON | 400
ECLA | EAST CLAYDON | 132
EASO | EATON SOCON | 400
EASO | EATON SOCON | 132
EGGB | EGGBOROUGH | 400
ELLA | ELLAND | 275
ELLA | ELLAND | 132
ELST | ELSTREE | 400
ELST | ELSTREE | 275
ELST | ELSTREE | 132
ENDE | ENDERBY | 400
ENDE | ENDERBY | 132
EXET | EXETER | 400
EXET | EXETER MAIN | 132
FAWL | FAWLEY | 400
FAWL | FAWLEY | 132
FECK | FECKENHAM | 400
FECK | FECKENHAM | 275
FENW | FENWICK TEE | 400
FERR | FERRYBRIDGE | 400
FERR | FERRYBRIDGE | 275
FERR | FERRYBRIDGE | 132
FFES | FFESTINIOG | 275
FIDF | FIDDLERS FERRY | 275
FIDF | FIDDLERS FERRY | 132
FLEE | FLEET | 400
FLEE | FLEET | 132
FLIB | FLINTSHIRE BRIDGE | 400
FOUR | FOURSTONES | 275
FRIN | FRISTON | 400
FROD | FRODSHAM | 400
FROD | FRODSHAM | 275
FROD | FRODSHAM | 132
GART | GARTH CABLE COMPOUND | 400
GRAI | GRAIN | 400
GRAI | GRAIN | 132
GRAN | GRANGE | 66
GRTO | GRANGETOWN | 275
GREN | GRENDON | 400
GREN | GRENDON | 132
GRST | GREYSTONES | 275
GRIW | GRIMSBY WEST | 400
GRIW | GRIMSBY WEST | 132
HACK | HACKNEY | 400
HACK | HACKNEY | 275
HACK | HACKNEY | 132
HAMB | HAMBLETON | 400
HAMH | HAMS HALL | 400
HAMH | HAMS HALL | 275
HAMH | HAMS HALL | 132
HARK | HARKER | 400
HARK | HARKER | 275
HARK | HARKER | 132
HATL | HARTLEPOOL | 275
HARM | HARTMOOR | 275
HAWP | HAWTHORN PIT | 400
HAWP | HAWTHORN PIT | 275
HEDD | HEDDON TEE | 400
HEDO | HEDON | 275
HEND | HENDON | 132
HEYS | HEYSHAM | 400
HEYS | HEYSHAM | 132
HIGM | HIGH MARNHAM | 400
HIGM | HIGH MARNHAM | 275
HIBU | HIGHBURY | 400
HIBU | HIGHBURY | 132
HINP | HINKLEY POINT | 400
HINP | HINKLEY POINT | 275
HORP | HORSESHOE POINT | 400
HUMR | HUMBER REFINERY | 400
HURS | HURST | 275
HURS | HURST | 132
HUTT | HUTTON | 400
HUTT | HUTTON | 132
IMPP | IMPERIAL PARK | 400
INCE | INCE | 132
INDQ | INDIAN QUEENS | 400
INDQ | INDIAN QUEENS | 132
IROA | IRON ACTON | 275
IROA | IRON ACTON | 132
IRON | IRONBRIDGE | 400
IRON | IRONBRIDGE | 132
ISLI | ISLINGTON | 132
IVER | IVER | 400
IVER | IVER | 275
IVER | IVER | 132
JORD | JORDANTHORPE | 275
KEAD | KEADBY | 400
KEAD | KEADBY | 132
KEAP | KEADBY POWER | 400
KEAR | KEARSLEY | 400
KEAR | KEARSLEY | 275
KEAR | KEARSLEY | 132
KEMS | KEMSLEY | 400
KEMS | KEMSLEY | 132
KENG | KENSAL GREEN | 400
KILL | KILLINGHOLME | 400
KINO | KINGSNORTH | 400
KINO | KINGSNORTH | 132
KIBY | KIRKBY | 275
KIBY | KIRKBY | 132
KIRK | KIRKSTALL | 275
KIRK | KIRKSTALL | 132
KITW | KITWELL | 275
KITW | KITWELL | 132
KNAR | KNARESBOROUGH | 275
KNAR | KNARESBOROUGH | 132
LACK | LACKENBY | 400
LACK | LACKENBY | 275
LAKE | LAKESIDE CABLE COOLING STATION | 400
LALE | LALEHAM | 275
LALE | LALEHAM | 132
LAND | LANDULPH | 400
LAND | LANDULPH | 132
LAGA | LANGAGE | 400
LEMR | LEA MARSTON | 132
LEGA | LEGACY | 400
LEGA | LEGACY | 132
LEIB | LEIGHTON BUZZARD | 400
LEIB | LEIGHTON BUZZARD | 275
LEIS | LEISTON | 400
LEIS | LEISTON | 132
LEWO | LEWINGDON WOOD | 400
LISD | LISTER DRIVE | 275
LISD | LISTER DRIVE | 132
LITB | LITTLE BARFORD | 400
LITT | LITTLEBROOK | 400
LITT | LITTLEBROOK | 275
LITT | LITTLEBROOK | 132
LODR | LODGE ROAD | 66
LOFI | LONGFIELD | 400
LOVE | LOVEDEAN | 400
LOVE | LOVEDEAN | 275
LOVE | LOVEDEAN | 132
LOXT | LOXTON | 400
MACC | MACCLESFIELD | 400
MACC | MACCLESFIELD | 275
MANN | MANNINGTON | 400
MANN | MANNINGTON | 132
MANS | MANSFIELD | 400
MAWO | MARCHWOOD | 400
MAGA | MARGAM | 275
MEDW | MEDWAY | 400
MELK | MELKSHAM | 400
MELK | MELKSHAM | 275
MELK | MELKSHAM | 132
MIDL | MIDDLETON | 400
MILH | MILL HILL | 275
MILH | MILL HILL | 132
MITY | MINETY | 400
MITY | MINETY | 132
MONF | MONK FRYSTON | 400
MONF | MONK FRYSTON | 275
MODO | MOULSFORD DOWN | 400
NECH | NECHELLS | 275
NECH | NECHELLS | 132
NECT | NECTON | 400
NECT | NECTON | 132
NEEP | NEEPSEND | 400
NEEP | NEEPSEND | 275
NEWX | NEW CROSS | 275
NEWX | NEW CROSS | 132
NEWK | NEWARK | 400
NWBY | NEWBY SEALING END COMPOUND | 400
NEHO | NEWHOUSE | 400
NINF | NINFIELD | 400
NINF | NINFIELD | 132
NHYD | NORTH HYDE | 275
NFLE | NORTHFLEET EAST | 400
NFLE | NORTHFLEET EAST | 132
NFLW | NORTHFLEET WEST | 400
NFLW | NORTHFLEET WEST | 132
NORT | NORTON | 400
NORT | NORTON | 275
NORT | NORTON | 132
NORL | NORTON LEES | 275
NORW | NORWICH | 400
NORW | NORWICH | 132
NORM | NORWICH MAIN | 400
NOTR | NORWICH TROWSE | 132
NUNT | NUNTHORPE SEALING END COMPOUND | 400
NURS | NURSLING | 400
NURS | NURSLING | 132
OCKH | OCKER HILL | 275
OCKH | OCKER HILL | 132
OFFE | OFFERTON | 275
OLDB | OLDBURY | 400
OLDB | OLDBURY | 275
OLDB | OLDBURY | 132
OLDS | OLDBURY ON SEVERN | 132
OSBA | OSBALDWICK | 400
OSBA | OSBALDWICK | 132
PADI | PADIHAM | 400
PADI | PADIHAM | 132
PAFB | PATFORD BRIDGE | 400
PELH | PELHAM | 400
PELH | PELHAM | 132
PEMB | PEMBROKE | 400
PEMB | PEMBROKE | 132
PENN | PENN | 400
PENN | PENN | 275
PENN | PENN | 132
PERH | PENRHOS | 132
PENT | PENTIR | 400
PENT | PENTIR | 132
PEWO | PENWORTHAM | 400
PEWO | PENWORTHAM | 275
PENE | PENWORTHAM EAST | 132
PENW | PENWORTHAM WEST | 132
PITS | PITSMOOR | 275
POPP | POPPLETON | 275
PORH | PORT HAM | 132
PUDM | PUDDING MILL LANE | 400
PURI | PURITON TEE | 400
PYLE | PYLE | 275
PYLE | PYLE | 132
QUER | QUERNMOOR | 400
RAIN | RAINHILL | 275
RAIN | RAINHILL | 132
RASS | RASSAU | 400
RASS | RASSAU | 132
RATS | RATCLIFFE-ON-SOAR | 400
RATS | RATCLIFFE-ON-SOAR | 275
RATS | RATCLIFFE-ON-SOAR | 132
RAYL | RAYLEIGH | 400
RAYM | RAYLEIGH MAIN | 132
REBR | REDBRIDGE | 275
RHIG | RHIGOS | 400
RICH | RICHBOROUGH | 400
ROCH | ROCHDALE | 400
ROCH | ROCHDALE | 275
ROCH | ROCHDALE | 132
ROCK | ROCKSAVAGE | 400
ROCK | ROCKSAVAGE | 132
ROWD | ROWDOWN | 400
RUGE | RUGELEY | 400
RUGE | RUGELEY | 132
RYEH | RYE HOUSE | 400
RYEH | RYE HOUSE | 132
RYHA | RYHALL | 400
SAEN | SALTEND NORTH | 275
SAEN | SALTEND NORTH | 132
SAES | SALTEND SOUTH | 275
SALH | SALTHOLME | 400
SALH | SALTHOLME | 275
SALH | SALTHOLME | 132
SAFO | SANDFORD | 400
SEAB | SEABANK | 400
SEAB | SEABANK | 132
SELL | SELLINDGE | 400
SELL | SELLINDGE | 275
SELL | SELLINDGE | 132
SHEE | SHEERNESS | 132
SHEC | SHEFFIELD CITY | 275
SHRE | SHREWSBURY | 400
SHRE | SHREWSBURY | 132
SHUR | SHURTON | 400
SING | SINGLEWELL | 400
SING | SINGLEWELL | 275
SIZE | SIZEWELL | 400
SIZE | SIZEWELL | 132
SKLG | SKELTON GRANGE | 275
SKLG | SKELTON GRANGE | 132
SHBA | SOUTH HUMBER BANK | 400
SMAN | SOUTH MANCHESTER | 275
SMAN | SOUTH MANCHESTER | 132
SSHI | SOUTH SHIELDS | 275
SPLN | SPALDING NORTH | 400
SPEN | SPENNYMOOR | 400
SPEN | SPENNYMOOR | 275
SPEN | SPENNYMOOR | 132
SASA | ST ASAPH | 132
SJOW | ST JOHNS WOOD | 132
SJOW | ST JOHNS WOOD | 400
SJOW | ST JOHNS WOOD | 275
STAL | STALYBRIDGE | 400
STAL | STALYBRIDGE | 275
STAL | STALYBRIDGE | 132
STAH | STANAH | 400
STAH | STANAH | 132
STAY | STAYTHORPE | 400
STYC | STAYTHORPE C | 132
STEN | STELLA NORTH | 132
STES | STELLA SOUTH | 132
STEW | STELLA WEST | 400
STEW | STELLA WEST | 275
STSB | STOCKSBRIDGE | 400
STOB | STOKE BARDOLPH | 400
STOB | STOKE BARDOLPH | 132
SUND | SUNDON | 400
SUND | SUNDON | 132
SUTB | SUTTON BRIDGE | 400
SWAN | SWANSEA NORTH | 400
SWAN | SWANSEA NORTH | 275
SWAN | SWANSEA NORTH | 132
TAUN | TAUNTON | 400
TAUN | TAUNTON | 132
TEMP | TEMPLEBOROUGH | 275
THTO | THORNTON | 400
THOM | THORPE MARSH | 400
THOM | THORPE MARSH | 275
THUR | THURCROFT | 275
TILB | TILBURY | 400
TILB | TILBURY | 275
TILB | TILBURY | 132
TINP | TINSLEY PARK | 275
TODP | TOD POINT | 400
TODP | TOD POINT | 275
TOTT | TOTTENHAM | 275
TOTT | TOTTENHAM | 132
TOTE | TOTTENHAM EAST | 275
TOTW | TOTTENHAM WEST | 275
TRAW | TRAWSFYNYDD | 400
TRAW | TRAWSFYNYDD | 275
TRAW | TRAWSFYNYDD | 132
TREM | TREMORFA | 275
TREU | TREUDDYN TEE | 400
TYNE | TYNEMOUTH | 275
TYNE | TYNEMOUTH | 132
UPPB | UPPER BOAT | 275
UPPB | UPPER BOAT | 132
USKM | USKMOUTH | 275
USKM | USKMOUTH | 132
WALF | WALFORD | 400
WALH | WALHAM | 400
WALP | WALPOLE | 400
WALP | WALPOLE | 132
WALX | WALTHAM CROSS | 400
WALX | WALTHAM CROSS | 275
WARL | WARLEY | 275
WARL | WARLEY | 132
WASF | WASHWAY FARM | 275
WASF | WASHWAY FARM | 132
WATS | WATFORD SOUTH | 275
WATS | WATFORD SOUTH | 132
WBOL | WEST BOLDON | 275
WBUR | WEST BURTON | 400
WBUR | WEST BURTON | 132
WHAM | WEST HAM | 400
WHAM | WEST HAM | 132
WMEL | WEST MELTON | 275
WMEL | WEST MELTON | 132
WTHU | WEST THURROCK | 400
WTHU | WEST THURROCK | 275
WWEY | WEST WEYBRIDGE | 400
WWEY | WEST WEYBRIDGE | 275
WWEY | WEST WEYBRIDGE | 132
WHGA | WHITEGATE | 275
WHGA | WHITEGATE | 132
WHSO | WHITSON | 400
WHSO | WHITSON | 275
WIEN | WILLENHALL | 275
WIEN | WILLENHALL | 132
WISD | WILLESDEN | 400
WISD | WILLESDEN | 275
WISD | WILLESDEN | 132
WILL | WILLINGTON | 132
WILE | WILLINGTON EAST | 400
WILT | WILTON | 275
WIMB | WIMBLEDON | 400
WIMB | WIMBLEDON | 275
WIMB | WIMBLEDON | 132
WIBA | WINCOBANK | 275
WYLF | WYLFA | 400
WYLF | WYLFA | 132
WYMO | WYMONDLEY | 400

## B-1-1d
B.1.1d - OFTO Index of Substation Codes
Site Code | Site Name
BEAT | BEATRICE ONSHORE
BEIW | BEATRICE OFFSHORE
BOSO | BARROW ONSHORE
BOSW | BARROW OFFSHORE
BBWO | BURBO BANK EXTENSION ONSHORE
BBWW | BURBO BANK EXTENSION OFFSHORE
BRST | BURSTALL
CLTO | CLACTON
CODL | CODLING ONSHORE WINDFARM
DOGB | DOGGER BANK ONSHORE
DUDW | DUDGEON OFFSHORE
DUDO | DUDGEON ONSHORE
EAAW | EAST ANGLIA OFFSHORE
FOFW | FIRTH OF FORTH ONSHORE
FOFO | FIRTH OF FORTH OFFSHORE
GANW | GALLOPER NORTH OFFSHORE
GALO | GALLOPER ONSHORE
GGON | GREATER GABBARD ONSHORE
GREG | GREATER GABBARD OFFSHORE
GUNS | GUNFLEET SANDS OFFSHORE
GWAW | GWYNT-Y-MOR OFFSHORE A
GWBW | GWYNT-Y-MOR OFFSHORE B
GWYO | GWYNT-Y-MOR ONSHORE
HOWA | HORNSEA P1 220KV ONSHORE
HOWW | HORNSEA OFFSHORE
HOWR | HORNSEA P1 220KV REACTOR SUBSTATION
HUMO | HUMBER GATEWAY ONSHORE
HUMW | HUMBER GATEWAY OFFSHORE
INCW | INCH CAPE OFFSHORE
INCO | INCH CAPE ONSHORE
LINO | LINCS ONSHORE
LINS | LINCS OFFSHORE
LONO | LONDON ARRAY ONSHORE
LOAW | LONDON ARRAY OFFSHORE
MOWE | MORAY EAST OFFSHORE
MORF | MORAY EAST ONSHORE
NNGO | NEART NA GAOITHE ONSHORE
NNGW | NEART NA GAOITHE OFFSHORE
ORMO | ORMONDE ONSHORE
ORMW | ORMONDE OFFSHORE
RACO | RACE BANK ONSHORE
RACW | RACE BANK OFFSHORE
RAMW | RAMPION OFFSHORE
RORE | ROBIN RIGG EAST ONSHORE
RORW | ROBIN RIGG WEST ONSHORE
RREW | ROBIN RIGG EAST OFFSHORE
RRWW | ROBIN RIGG WEST OFFSHORE
SALL | SALLE
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2
THAW | THANET WIND ONSHORE
THOW | THANET WIND OFFSHORE
TKNO | TRITON KNOLL ONSHORE
TKNE | TRITON KNOLL EAST OFFSHORE
TKNW | TRITON KNOLL WEST OFFSHORE
TWNE | TWINEHAM ONSHORE
WAAO | WALNEY 1 ONSHORE
WAAW | WALNEY 1 OFFSHORE
WABO | WALNEY 2 ONSHORE
WABW | WALNEY 2 OFFSHORE
WACW | WALNEY 3 OFFSHORE
WADW | WALNEY 4 OFFSHORE
WOWE | WALNEY EXTENSION
WDSO | WEST OF DUDDON SANDS ONSHORE
WDSW | WEST OF DUDDON SANDS OFFSHORE
WERO | WESTERMOST ROUGH ONSHORE
WERW | WESTERMOST ROUGH OFFSHORE

## B-2-1a
B.2.1a - SHE Transmission Circuits for 2020/21
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABBA1- | DYCE1J | 0 | 7.8 | Cable | 0.1092 | 1.2324 | 10.14 | 173 | 158 | 158 | 158
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.2199 | 132 | 123 | 106 | 123
ABNE1R | AMUL1G | 28.099 | 0.001 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
ABNE1R | ABNE1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ACHR1R | INVE1J | 21.17 | 0 | OHL | 3.002 | 4.9754 | 1.035 | 99 | 92 | 79 | 92
ACHR1R | PORA1R | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
AIGA1Q | KIOR1Q | 2.8 | 0.12 | Composite | 0.264 | 0.594 | 0.66 | 126 | 117 | 101 | 117
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
AMUL1E | BUMU1R | 17.8 | 0 | OHL | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
ANSU1- | INVE1K | 11.13 | 0 | OHL | 1.578 | 2.615 | 0.544 | 99 | 92 | 79 | 92
ANSU1- | PORA1Q | 24.27 | 0 | OHL | 3.442 | 5.705 | 1.186 | 99 | 92 | 79 | 92
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123
ARBR1R | DENS1R | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123
ARDK1- | INVE1J | 9 | 0 | OHL | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123
ARDK1- | SLOY1T | 10 | 0 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 99 | 92 | 79 | 92
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 126 | 117 | 101 | 117
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136
BEAU1J | BEAU1R | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 465 | 445 | 415 | 445
BEAU1J | BEAU1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU1K | KIOR1Q | 1.24 | 0.06 | Composite | 0.13 | 0.29 | 0.06 | 126 | 117 | 101 | 117
BEAU1K | BEAU1S | 0 | 2.42 | Cable | 0.0882 | 0.2222 | 2.866 | 152 | 140 | 140 | 140
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 465 | 445 | 415 | 445
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123
BEAU1N | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU1N | BEAU1K | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136
BEAU1P | BEAU1L | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1Q | BEAU1M | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1R | INNE1Q | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1S | INNE1R | 13.44 | 0 | OHL | 1.3695 | 3.1323 | 0.663 | 126 | 117 | 101 | 117
BEAU1T | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU2J | FASN2- | 24.29 | 1.01 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU2J | BEAU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU4- | FAUG4- | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BEIN11 | CEAN1Q | 0.87 | 0 | OHL | 0.099 | 0.205 | 0.042 | 254 | 247 | 237 | 247
BEIN11 | MILW1S | 2.8 | 0 | OHL | 0.319 | 0.66 | 0.135 | 254 | 247 | 237 | 247
BERB2Q | KNOC2J | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
BHLA11 | GLEN1Q | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 230 | 217 | 217 | 217
BIHI1Q | CHAR1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
BIHI1Q | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
BIHI1Q | COUA1Q | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
BIHI1R | CHAR1- | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
BIHI1R | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
BIHI1R | COUA1R | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
BLHI1J | KEIT1K | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.171 | 5.295 | 1.286 | 241 | 230 | 210 | 230
BLHI1J | BLHI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI1K | KEIT1J | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.171 | 5.297 | 1.318 | 241 | 230 | 210 | 230
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.044 | 13.793 | 580 | 546 | 546 | 546
BLHI2J | BERB2Q | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2J | BLHI2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.0456 | 14.286 | 580 | 546 | 546 | 546
BLHI2K | CAIN2- | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2L | KINT2J | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2M | PEHERSV1 | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BLHI4- | BLHI4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 1272 | 1272 | 1272 | 1272
BLHI4- | BEAT4- | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
BOAG1L | TOMT1K | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 227 | 200 | 200 | 200
BOAG1M | TOMT1J | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 255 | 255 | 242 | 250
BOAG1P | GLFA1- | 24.82 | 0 | OHL | 2.5189 | 5.7753 | 1.228 | 126 | 117 | 101 | 117
BOAG1Q | BOAG1L | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209
BOAG1Q | BOAG1P | 0 | 8.4 | Cable | 0.0558 | 1.271 | 11.48 | 227 | 209 | 209 | 209
BOAG1R | BOAG1M | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209
BONB2J | BRCW2K | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BONB4- | TUMM4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670
BRCW2J | TUMM2K | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
BRCW2J | BRCW2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104
BREC1Q | BREC1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.12 | 0.27 | 0.06 | 126 | 117 | 101 | 117
BROR1Q | DUBE1Q | 38.8 | 0 | OHL | 3.94 | 9.01 | 1.91 | 126 | 117 | 101 | 117
BROR1Q | LOCB1K | 22.12 | 0 | OHL | 2.2511 | 5.1536 | 1.096 | 126 | 117 | 101 | 117
BUMU1Q | CHAR1- | 42.2 | 0 | OHL | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
BUMU1Q | BUMU1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880
CASS1Q | LAIR1Q | 28 | 0 | OHL | 2.84 | 6.75 | 1.33 | 126 | 117 | 101 | 117
CHAR1- | CHAR1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 229 | 211 | 183 | 211
CHAR1S | GLAG1Q | 1.4 | 0.91 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 126 | 126 | 126
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 1.4 | 0.91 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 126 | 126 | 126
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117
CLAC1Q | SLOY1K | 14.2 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
CLAY1Q | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLAY1R | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1R | CLUN1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 126 | 117 | 101 | 117
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 126 | 117 | 101 | 117
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7002 | 2.8782 | 0.778 | 241 | 230 | 210 | 230
COGA1C | FARI1J | 0 | 4.11 | Cable | 0.065 | 0.334 | 6.245 | 220 | 209 | 209 | 209
CONN1C | STRW1C | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 241 | 230 | 210 | 230
CONN1J | CONN1C | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN2J | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 702 | 665 | 599 | 665
CONN2J | LOCB2J | 76.07 | 0.27 | Composite | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446
CORI1J | CORI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 132 | 123 | 106 | 123
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 132 | 123 | 106 | 123
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 145 | 131 | 116 | 131
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 145 | 131 | 116 | 131
CRSS1J | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | PORA1Q | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
CRSS1R | PORA1R | 48.3 | 0 | OHL | 6.8386 | 11.356 | 2.352 | 99 | 92 | 79 | 92
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 126 | 117 | 101 | 117
DAAS2- | KNOC2K | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160
DENS1R | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DOUN2- | THUS2J | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DUBE1Q | MYBS1R | 20.8 | 0 | OHL | 2.12 | 4.86 | 1.03 | 126 | 117 | 101 | 117
DUCC1J | ORRI1S | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
DUCC1K | ORRI1T | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
DUDH1Q | GLAG1Q | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92
DUNM1- | DUNM1C | 6 | 0 | OHL | 0.3023 | 1.2424 | 0.336 | 241 | 230 | 210 | 230
DUNM1C | FARI1K | 0 | 4.07 | Cable | 0.064 | 0.28 | 6.175 | 210 | 196 | 196 | 196
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1Q | DYCE1J | 1.93 | 0 | OHL | 0.0978 | 0.4332 | 0.33 | 241 | 230 | 210 | 230
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.5187 | 2.2781 | 0.525 | 145 | 131 | 116 | 131
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.6335 | 2.2972 | 0.519 | 145 | 131 | 116 | 131
ELGI1L | NAIR1Q | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1M | NAIR1R | 32.9 | 0 | OHL | 3.3458 | 7.6395 | 1.626 | 126 | 117 | 101 | 117
ELGI1Q | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1Q | ELGI1L | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ELGI1R | KEIT1- | 27.7 | 0 | OHL | 2.81 | 6.43 | 1.37 | 126 | 117 | 101 | 117
ELGI1R | ELGI1M | 0 | 1.89 | Cable | 0.0372 | 0.0546 | 1.481 | 150 | 130 | 130 | 130
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1J | WHIB1A | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
ERRO1J | ERRO1A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1J | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ERRO1J | ERRO1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1K | WHIB1B | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
ERRO1K | ERRO1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123
FAAR1Q | TOMT1K | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FAAR1R | TOMT1J | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FARI2J | KNOC2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
FARI2K | KNOC2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
FASN2- | FAUG2J | 24.38 | 1.02 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.01 | 0.012 | 0.002 | 126 | 117 | 101 | 117
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127
FAUG1- | FAUG1P | 0 | 0.59 | Cable | 0.01 | 0.0602 | 0.868 | 202 | 202 | 202 | 202
FAUG1- | FAUG1M | 0 | 0.29 | Cable | 0.01 | 0.0225 | 0.486 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 0 | 0.2 | Cable | 0.01 | 0.0157 | 0.339 | 220 | 209 | 209 | 209
FAUG1- | LAGG1Q | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 254 | 247 | 237 | 247
FAUG1- | LAGG1R | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 254 | 247 | 237 | 247
FAUG1M | LOCL1Q | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1P | LOCL1S | 8.66 | 0 | OHL | 0.4365 | 1.7942 | 0.485 | 241 | 230 | 210 | 230
FAUG2J | FAUG2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FAUG4- | MELG4J | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.7089 | 1.0659 | 0.265 | 99 | 92 | 79 | 92
FERO1S | INVE1J | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
FERO1S | TAYN1R | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92
FETT2P | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 880 | 760 | 880
FETT2P | TEAL2K | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
FETT2P | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2Q | KINB2J | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT2Q | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 955 | 885 | 760 | 885
FETT2Q | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FIDD1Q | FOGG1R | 25.4 | 0 | OHL | 3.004 | 6.157 | 1.238 | 112 | 104 | 90 | 104
FIDD1Q | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FIDD1R | FIDD1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 126 | 117 | 101 | 117
FOGG1Q | KINT1- | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 98 | 90 | 98
FOGG1Q | TARL1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
FOGG1R | TARL1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
FOYE2- | FOYE2J | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
FOYE2- | FARI2J | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FOYE2- | FARI2K | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LUND1- | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FYRI1J | FYRI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FYRI2J | LOCB2K | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
GARB1Q | SLOY1K | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
GARB1R | SLOY1J | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GARB1S | SLOY1J | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
GARB1T | SLOY1K | 14.9 | 0 | OHL | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.546 | 1.132 | 0.232 | 254 | 247 | 237 | 247
GLFA1- | KEIT1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117
GLRB2- | TEAL2K | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 702 | 665 | 599 | 665
GRIF1S | WHIB1H | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
GRIF1T | WHIB1G | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 132 | 123 | 106 | 123
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 132 | 123 | 106 | 123
INGA1Q | LOCL1Q | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.1051 | 0.3818 | 6.326 | 146 | 142 | 142 | 142
INNE1J | INNE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INNE1K | INNE1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1042 | 0.3784 | 6.27 | 146 | 142 | 142 | 142
INNE1Q | NAIR1Q | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1R | NAIR1R | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 142 | 128 | 142
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 150 | 142 | 128 | 142
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 150 | 142 | 128 | 142
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 117 | 101 | 117
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 126 | 117 | 101 | 117
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 126 | 117 | 101 | 117
INRU1S | PEHE1- | 0 | 3 | Cable | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181
INVE1J | INVE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
INVE1K | SLOY1J | 22.6 | 0 | OHL | 2.29 | 5.25 | 1.11 | 126 | 117 | 101 | 117
INVR1- | KIIN1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
INVR1- | KIIN1- | 33.68 | 0 | OHL | 3.43 | 7.84 | 1.66 | 132 | 126 | 106 | 126
INVR1- | SLOY1K | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126
KEIT1J | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123
KEIT1K | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123
KEIT3- | KEIT3A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 126 | 117 | 101 | 117
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99 | 92 | 79 | 92
KILC1Q | TAYN1Q | 7.52 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILO1- | LUND1- | 15.2 | 0 | OHL | 1.054 | 3.441 | 0.775 | 126 | 117 | 101 | 117
KINB2K | TEAL2J | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.0154 | 0.354 | 148 | 140 | 140 | 140
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.0148 | 0.341 | 148 | 140 | 140 | 140
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT1- | KINT1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT2J | TEAL2J | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 952 | 952 | 925 | 952
KINT2J | KINT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT2K | TEAL2K | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | PEHE2Q | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KNOC2J | KNOC2N | 0 | 0.51 | Cable | 0.0012 | 0.0157 | 3.005 | 850 | 793 | 793 | 793
KNOC2J | KNOC2P | 0 | 0.17 | Cable | 0.0004 | 0.0053 | 1.006 | 850 | 793 | 793 | 793
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.042 | 8.36 | 930 | 900 | 900 | 900
KNOC2J | KNOC2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KNOC2M | KNOC2K | 0 | 1.29 | Cable | 0.01 | 0.037 | 7.336 | 930 | 900 | 900 | 900
KNOC2N | TOMT2K | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765
KNOC2P | TOMT2J | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.648 | 1.344 | 0.276 | 254 | 247 | 237 | 247
LAIR1Q | SHIN1- | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 126 | 117 | 101 | 117
LOCB1J | MYBS1Q | 81.61 | 0 | OHL | 8.2998 | 19.0008 | 4.028 | 126 | 117 | 101 | 117
LOCB1J | SHIN1- | 12.19 | 0 | OHL | 1.2402 | 2.8392 | 0.602 | 126 | 117 | 101 | 117
LOCB1J | LOCB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB1K | SHIN1- | 12.18 | 0 | OHL | 1.239 | 2.8365 | 0.604 | 126 | 117 | 101 | 117
LOCB2J | LOCB2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB2K | STRB2- | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 702 | 665 | 599 | 665
LOCL1S | QUOI1Q | 18.3 | 0 | OHL | 0.9219 | 3.7893 | 1.025 | 241 | 230 | 210 | 230
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
MELG1J | STRL1- | 0 | 10 | Cable | 0.0752 | 0.806 | 18.176 | 317 | 281 | 281 | 281
MELG1J | MELG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MELG4J | TUMM4- | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670
MELG4J | MELG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1R | MILC1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1R | MILC1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 229 | 211 | 183 | 211
MILC1S | MILC1V | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 229 | 211 | 183 | 211
MILW1S | MILW1Q | 1.3 | 0 | OHL | 0.065 | 0.2691 | 0.073 | 241 | 230 | 210 | 230
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1S | SPIT1M | 4.5 | 0 | OHL | 0.104 | 1.002 | 0.237 | 463 | 444 | 415 | 444
MYBS1T | SPIT1K | 4.5 | 0 | OHL | 0.104 | 1.002 | 0.237 | 463 | 444 | 415 | 444
MYBS3M | MYBS3N | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1R | ORRI1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
PEHE2- | PEHE2S | 0 | 1 | Cable | 0.01 | 0.033 | 14.21 | 776 | 776 | 776 | 776
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE2- | PEHE2Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2- | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2R | PEHERSV2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2T | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.032 | 13.51 | 776 | 776 | 776 | 776
PEHE2U | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2V | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2W | PEHEMEC1 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHEMEC1 | PEHEMEC2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC1 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC2 | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC3 | PEHEMEC4 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC4 | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC5 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHERSV1 | PEHEMEC4 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHERSV2 | PEHEMEC2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS1Q | PERS1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS2Q | PERS2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 150 | 142 | 128 | 142
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
SFEG1Q | SFEG1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1R | SFEG1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1S | SFEG1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1J | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1K | SFER1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1K | SFER1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFER1L | SFEM1Q | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1L | SFEG1Q | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 150 | 142 | 128 | 142
SFER1M | SFEM1R | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1M | SFEG1R | 2.1 | 0 | OHL | 0.25 | 0.49 | 0.1 | 150 | 142 | 128 | 142
SHET1J | SHET1R | 0 | 1 | Cable | 0.01 | 0.11 | 0 | 720 | 720 | 720 | 720
SLOY1J | SLOY1N | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 117 | 101 | 117
SLOY1J | SLOY1P | 1.4 | 0 | OHL | 0.15 | 0.34 | 0.07 | 126 | 117 | 101 | 117
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123
SLOY1J | SLOY1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SLOY1K | SLOY1L | 1.29 | 0.01 | Composite | 0.13 | 0.3 | 0.06 | 126 | 117 | 101 | 117
SLOY1K | SLOY1M | 1.29 | 0.01 | Composite | 0.13 | 0.3 | 0.06 | 126 | 117 | 101 | 117
SPIT2J | THUS2J | 12.1 | 0 | OHL | 0.0605 | 0.6655 | 2.577 | 965 | 925 | 865 | 925
SPIT2J | SPIT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SPIT2K | SPIT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 960 | 960 | 960 | 960
SPIT2K | THUS2K | 12.1 | 0 | OHL | 0.0605 | 0.6655 | 2.577 | 965 | 925 | 865 | 925
STRW12 | STRW1C | 0 | 0.35 | Cable | 0.01 | 0.0631 | 0.48 | 200 | 178 | 178 | 178
TEAL2J | WFIB2- | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 955 | 885 | 760 | 885
TEAL2J | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
THUS1J | THUS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TOMT1K | TOMT1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TOMT2K | TOMT2J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TUMM2J | TUMM2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147

## B-2-1b
B.2.1b - SPT Circuits for 2020/21
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0422 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0422 | 0.3812 | 2.6022 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.716 | 3.8726 | 0.9882 | 171 | 152 | 152 | 152
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.72 | 3.8943 | 0.9935 | 171 | 152 | 152 | 152
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.9576 | 4.8683 | 1.5223 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.9569 | 4.8645 | 1.4665 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430
BLAH1- | GLGL1Q | 12.6 | 0.435 | Composite | 0.4848 | 2.7278 | 1.2134 | 134 | 123 | 123 | 123
BLAH1- | GLGL1R | 12.6 | 0.44 | Composite | 0.485 | 2.7281 | 1.2195 | 134 | 123 | 123 | 123
BLAH3A | WNDR3- | 0 | 5 | Cable | 1.1433 | 4.2657 | 0.6455 | 51 | 51 | 51 | 51
BLAH3B | PENC3- | 0 | 1.5 | Cable | 0.0267 | 0.1431 | 1.7503 | 40 | 38 | 38 | 38
BLAH3B | PENC3- | 0 | 1.5 | Cable | 0.0267 | 0.1431 | 1.7503 | 40 | 38 | 38 | 38
BLCW1- | MARG1- | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 166 | 159 | 147 | 159
BLCW3- | BLCW3A | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 31 | 31 | 31 | 31
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2976 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 4.04 | 0.3 | parallelComposite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234
BONN1- | STIR1S | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BPGR3- | BPGR3R | 0 | 0 | Series Reactor | 0.2755 | 25 | 0 | 96 | 96 | 96 | 96
BPGR3- | BPGR3R | 0 | 0 | SeriesReactor | 0.2755 | 25 | 0 | 96 | 96 | 96 | 96
BRAE1G | BRAP1- | 0 | 2.1 | Cable | 0.0418 | 0.1748 | 3.0232 | 250 | 250 | 250 | 250
BRAE1G | GOVA1R | 0 | 4.03 | Cable | 0.175 | 0.2752 | 7.984 | 125 | 113 | 110 | 113
BRAE1P | GOVA1Q | 0 | 4.03 | Cable | 0.175 | 0.2752 | 7.984 | 125 | 113 | 110 | 113
BRAE1P | PAIS1Q | 4.52 | 0 | OHL | 0.0885 | 0.8142 | 0.2833 | 268 | 268 | 268 | 268
BRAP1- | ERSK1Q | 3.17 | 5.4 | Composite | 0.4479 | 1.0975 | 12.4447 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4955 | 1.1727 | 12.9637 | 102 | 79 | 79 | 79
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 750 | 690 | 630 | 690
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.2337 | 0.5239 | 0.1455 | 132 | 123 | 106 | 123
CAFA5- | CAFA5R | 0 | 0 | SeriesReactor | 0.3333 | 21.1544 | 0 | 30 | 30 | 30 | 30
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CHAP1- | DUMF1- | 26.9 | 0.125 | Composite | 1.065 | 6.0817 | 1.5576 | 171 | 155 | 155 | 155
CHAP1- | DUMF1- | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | ECCF1J | 6.569 | 0.23 | Composite | 0.6009 | 1.515 | 0.651 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.185 | Composite | 0.6 | 1.5109 | 0.5882 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.1811 | 3.0837 | 0.9878 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 1.1797 | 3.0784 | 0.9358 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.019 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 9.17 | 0 | OHL | 0.0207 | 0.3232 | 2.9288 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.22 | 0 | OHL | 0.1223 | 1.9018 | 17.3649 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.0445 | 0.1289 | 23.8486 | 291 | 245 | 245 | 245
COAL1- | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180
COAL1- | LINM1R | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 134 | 123 | 123 | 123
COAL1- | MIDM1- | 0 | 14.47 | Cable | 0.4086 | 0.9392 | 17.8217 | 158 | 146 | 146 | 146
COAL1A | GAWH1Q | 0 | 10.5 | Cable | 0.1651 | 0.9039 | 17.3003 | 241 | 241 | 241 | 241
COAL1A | LINM1Q | 5.774 | 3.2 | Composite | 0.2502 | 1.6499 | 3.0753 | 134 | 123 | 123 | 123
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0779 | 0.756 | 5.0669 | 1120 | 1060 | 990 | 1060
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0405 | 0.3931 | 2.6346 | 1120 | 1060 | 990 | 1060
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.1427 | 1.4132 | 35.4499 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.1427 | 1.413 | 35.4444 | 1090 | 1030 | 925 | 1030
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4027 | 1.0118 | 0.5089 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8423 | 2.157 | 1.0619 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.29 | 0.08 | Composite | 0.0057 | 0.0515 | 0.4645 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.0058 | 0.0522 | 0.3778 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.6159 | 4.1178 | 1.1779 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4941 | 2.6834 | 0.984 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.4943 | 2.6844 | 0.9979 | 229 | 211 | 183 | 211
CRUA2Q | CRUA2S | 0 | 0.4 | Cable | 0.0001 | 0.0103 | 2.0513 | 283 | 283 | 283 | 283
CRUA2R | CRUA2T | 0 | 0.4 | Cable | 0.0001 | 0.0103 | 2.0513 | 283 | 283 | 283 | 283
CRUA2S | DALL2- | 8.16 | 0 | OHL | 0.0345 | 0.3333 | 2.2691 | 570 | 570 | 570 | 570
CRUA2T | DALL2- | 8.16 | 0 | OHL | 0.0345 | 0.3333 | 2.2691 | 570 | 570 | 570 | 570
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0184 | 0.2733 | 8.179 | 2470 | 2350 | 2150 | 2350
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 935 | 785 | 785 | 785
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.2634 | 0.9635 | 5.1125 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2627 | 0.9613 | 5.0951 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.18 | 0 | OHL | 0.1915 | 1.7367 | 11.6698 | 1090 | 1030 | 920 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1372 | 1324 | 1228 | 1324
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1372 | 1324 | 1228 | 1324
CURR2- | KINC2- | 55.82 | 0 | OHL | 0.2534 | 2.2983 | 15.4435 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0174 | 0.1034 | 6.0397 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0172 | 0.1027 | 5.9404 | 120 | 120 | 120 | 120
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 957 | 881 | 762 | 881
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 123 | 106 | 123
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.6915 | 1.7146 | 0.386 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.6806 | 1.6869 | 0.38 | 107 | 107 | 101 | 107
DEVM4- | HUNE4- | 50.471 | 0.167 | Composite | 0.0909 | 0.9984 | 33.1263 | 1316 | 1067 | 1067 | 1067
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.047 | 0.5444 | 17.7745 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1T | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 164 | 130 | 130 | 130
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8944 | 7.5329 | 1.5454 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNB1Q | DUNB1S | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 90 | 90 | 90 | 90
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNB1R | DUNB1T | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 90 | 90 | 90 | 90
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131
DUNE3- | KEIH3- | 0 | 3.5 | Cable | 3.9126 | 3.7846 | 0.2381 | 17 | 17 | 17 | 17
DUNE3- | POGB3- | 0 | 3.809 | Cable | 4.4534 | 3.8498 | 0.3049 | 21 | 20 | 20 | 20
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | SeriesCapacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | ECCL4D | 0 | 0 | SeriesCapacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 46.23 | 0 | OHL | 0.1043 | 1.6221 | 14.8036 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 0 | 2.79 | Cable | 0.12 | 0.559 | 0.684 | 229 | 211 | 183 | 211
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1517 | 0.8271 | 0.4569 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 0 | 2.79 | Cable | 0.121 | 0.561 | 0.73 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1523 | 0.8319 | 0.5267 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1155 | 1.2673 | 38.8356 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0414 | 0.4544 | 13.9258 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
EWEH1Q | GRNA1- | 15.7 | 0.12 | Composite | 1.1828 | 3.4623 | 0.9844 | 131 | 131 | 131 | 131
EWEH3- | CRDY3B | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 45 | 39 | 39 | 39
EWEH3- | CRDY3A | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 45 | 39 | 39 | 39
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2473 | 2349 | 2148 | 2349
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1- | 15.313 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123
GARB1R | STLE1- | 26.909 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.03 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.061 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.082 | 0.33 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.74 | 0.162 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105
GLGL3- | SNQR3- | 0 | 2.3 | Cable | 0.6364 | 2.0111 | 0.2699 | 30 | 30 | 30 | 30
GLGL3- | WHLL3- | 0 | 1.2 | Cable | 0.332 | 1.5811 | 0.1408 | 30 | 30 | 30 | 30
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.6969 | 1.6787 | 0.405 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 171 | 171 | 171 | 171
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 130 | 125 | 110 | 125
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 154 | 141 | 154
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.359 | 0.7999 | 0.7252 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 875 | 875 | 760 | 875
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 955 | 885 | 760 | 885
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068 | 0.6175 | 4.1318 | 1050 | 965 | 880 | 965
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.017 | 0.047 | 0.066 | 1000 | 1000 | 1000 | 1000
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.012 | 0.035 | 0.049 | 1000 | 1000 | 1000 | 1000
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 5.0386 | 12.9578 | 2.7219 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.4329 | 1.1257 | 0.2305 | 132 | 123 | 106 | 123
GRNA4- | GRNA4C | 0 | 0 | SeriesCapacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2210 | 2130 | 1980 | 2130
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.304 | 1.375 | 21.563 | 184 | 184 | 184 | 184
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 4.5812 | 11.7697 | 2.4781 | 132 | 123 | 106 | 123
HELE1- | WIYH1- | 24.799 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1448 | 1448 | 1448 | 1448
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1448 | 1448 | 1448 | 1448
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUER4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | NEIL4Q | 35.617 | 0.167 | Composite | 0.0716 | 0.7351 | 23.4602 | 1320 | 1070 | 1070 | 1070
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.6051 | 3.1847 | 6.8629 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4354 | 2.2253 | 6.6009 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4909 | 2.779 | 0.643 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3218 | 1.8217 | 0.4215 | 151 | 151 | 151 | 151
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1120 | 1060 | 990 | 1060
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1822 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240
KAIM3- | KAIM3A | 0 | 0 | SeriesReactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120
KAIM3- | KAIM3B | 0 | 0 | SeriesReactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120
KEOO1- | NECU1R | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 133 | 123 | 106 | 123
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6165 | 100 | 80 | 60 | 80
KIER1R | WIYH1- | 2.089 | 4.095 | Composite | 0.3833 | 0.9197 | 7.4586 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0175 | 0.154 | 2.0858 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0178 | 0.1548 | 2.24 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 760 | 620 | 620 | 620
KINB2K | KINC2- | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 910 | 885 | 760 | 885
KINC2- | LOAN2Q | 4.28 | 0.31 | Composite | 0.0192 | 0.1938 | 4.4396 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 4.28 | 0.17 | Composite | 0.0189 | 0.1899 | 2.8506 | 765 | 620 | 620 | 620
LAMB2- | LAMB2T | 0 | 0.001 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0182 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0192 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1050 | 965 | 880 | 965
LAMB2T | LOAN2- | 53.67 | 0.225 | Composite | 0.1948 | 2.0808 | 18.1931 | 795 | 620 | 620 | 620
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1120 | 1060 | 990 | 1060
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | SeriesReactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | SeriesReactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | MOSM2L | 26.196 | 0.194 | Composite | 0.1186 | 1.0915 | 8.8674 | 760 | 620 | 620 | 620
LOAN2- | WFIE2- | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 760 | 620 | 620 | 620
MAHI3- | TRLO3- | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 40 | 30 | 30 | 30
MARG1- | NECU1Q | 34.35 | 0.9 | Composite | 1.1487 | 6.9058 | 3.4859 | 241 | 230 | 210 | 230
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1567 | 3.0101 | 0.9444 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29
MOFF4- | MOFF4C | 0 | 0 | SeriesCapacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | MOSM2L | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 955 | 885 | 760 | 885
MOSM2- | MOSM2T | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 955 | 885 | 760 | 885
MOSM2T | WFIE2- | 2.943 | 0 | OHL | 0.0133 | 0.1221 | 0.8005 | 955 | 885 | 760 | 885
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1109 | 1.0864 | 6.9028 | 957 | 881 | 764 | 881
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 1390 | 1280 | 1110 | 1280
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1344 | 1.2615 | 34.9418 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0233 | 0.2267 | 6.8043 | 2000 | 1920 | 1790 | 1920
STIR1S | WFIE1A | 37.6 | 5.816 | Composite | 3.218 | 9.4053 | 8.7867 | 162 | 154 | 141 | 154
STLE1- | WIYH1- | 12.892 | 0.291 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 950 | 885 | 760 | 885
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WIYH2- | WIYH2R | 0 | 0 | SeriesReactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
B.2.1c - NGET Circuits for 2020/21
Node1 | Node2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.041714 | 0.50275 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 1389 | 1284 | 1108 | 1284
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.041714 | 0.50275 | 15.6941 | 1389 | 1284 | 1108 | 1284
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629
ABTH21 | UPPB22 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882
ABTH22 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879
ABTH22 | UPPB21 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 595
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911
AMEM4A | IVER4A | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2009 | 1911 | 1746 | 1911
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933
AMEM4B | IVER4B | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933
AXMI41 | CHIC4A | 39.5 | 0 | OHL | 0.0429 | 0.687 | 26.0389 | 2779 | 2568 | 2217 | 2568
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2771 | 2568 | 2217 | 2568
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115
BAGB21 | SWAN21 | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431
BARK21 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK21 | REBR21 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081
BARK22 | BARP21 | 2.6 | 0.39 | Composite | 0.0106 | 0.1154 | 4.5169 | 850 | 850 | 850 | 850
BARK22 | REBR22 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0156 | 0.1915 | 10.4541 | 2009 | 1909 | 1710 | 1909
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0155 | 0.191 | 5.6429 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.0692 | 0.7576 | 7.8243 | 944 | 882 | 762 | 835
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 694
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0689 | 0.7539 | 6.2735 | 762 | 762 | 662 | 662
BEDD23 | WIMB2A | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 806
BEDD4A | ROWD42 | 0 | 11.676 | Cable | 0.0079 | 0.138 | 127.4459 | 1309 | 1309 | 1309 | 1309
BEDD4B | ROWD41 | 0 | 11.676 | Cable | 0.0105 | 0.0957 | 210.168 | 1415 | 1415 | 1223 | 1223
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 56.939 | 0.631 | Composite | 0.2314 | 2.4189 | 22.4142 | 819 | 819 | 638 | 638
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1236 | 1176 | 1074 | 1176
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1236 | 1176 | 1074 | 1176
BLYT41 | HEDD4A | 26.636 | 0.121 | Composite | 0.042634 | 0.514 | 18.0175 | 2199 | 2092 | 1911 | 2092
BLYT41 | HEDD4B | 26.636 | 0.49 | Composite | 0.042929 | 0.51943 | 24.1171 | 2199 | 2092 | 1911 | 2092
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOTW41 | FAWL41 | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 1109 | 901 | 901
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0451 | 0.8316 | 32.2964 | 2779 | 2568 | 2217 | 2568
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0134 | 0.2147 | 8.1357 | 2779 | 2568 | 2217 | 2568
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.065 | 1.1398 | 43.92 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0358 | 0.5745 | 21.7727 | 2779 | 2568 | 2217 | 2568
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1204 | 1115 | 1018 | 1115
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 2470 | 2350 | 2146 | 2350
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0768 | 0.8127 | 5.4608 | 948 | 882 | 753 | 753
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.762 | 850 | 850 | 675 | 675
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1093 | 1031 | 925 | 1031
BRIM2B | TOTT24 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1085 | 1031 | 925 | 1031
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1093 | 1031 | 925 | 1031
BRIM2C | TOTT22 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT23 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499
BRIN21 | NORL22 | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2568 | 2217 | 2568
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1389 | 1284 | 1108 | 1284
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.078851 | 0.94951 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.078851 | 0.94951 | 29.6914 | 2199 | 2092 | 1911 | 2092
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0224 | 0.3591 | 13.6101 | 2779 | 2568 | 2217 | 2568
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3102 | 2935 | 2765 | 2935
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2910 | 2238 | 2515
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3102 | 2935 | 2765 | 2935
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3102 | 2935 | 2765 | 2935
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762
BUSH21 | WIEN21 | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 681
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 635
BUST21 | NECH21 | 2.648 | 7.673 | Composite | 0.0251 | 0.3262 | 84.1239 | 725 | 713 | 599 | 635
BUST41 | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568
BUST41 | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119
CANT41 | RICH41 | 25 | 0 | OHL | 0.039925 | 0.48076 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 25 | 0 | OHL | 0.039925 | 0.48076 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | SELL4A | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2750 | 2750 | 2420 | 2750
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2570 | 2570 | 2220 | 2570
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665
CARR41 | DAIN42 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9776 | 3102 | 3048 | 2958 | 3048
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO41 | 56.9 | 0 | OHL | 0.09878 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR4A | DAIN42 | 2.063 | 0 | OHL | 0.0035 | 0.0404 | 1.2165 | 1507 | 1507 | 1507 | 1507
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1553 | 1553 | 1553 | 1553
CELL41 | DAIN42 | 53.412 | 2.31 | parallel Composite | 0.0847 | 1.031 | 76.931 | 2508 | 2508 | 2300 | 2300
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.071884 | 0.8656 | 27.0675 | 2175 | 2069 | 1890 | 2069
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073001 | 0.87907 | 27.4871 | 2175 | 2069 | 1890 | 2069
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0495 | 0.6067 | 18.9879 | 3102 | 3048 | 2958 | 3048
CHIC41 | EXET41 | 75.92 | 0 | OHL | 0.0824 | 1.3205 | 50.0469 | 2779 | 2568 | 2217 | 2568
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829
CHIC4A | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHUE4A | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591
CHUE4A | WTHU4D | 2.4188 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048
CHUE4B | TILB41 | 13.0448 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591
CHUE4B | WTHU4C | 2.5806 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048
CILF2A | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF2B | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136
CLEH41 | CANT41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048
CLEH41 | KEMS41 | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048
CONQ41 | CAPE4A | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CONQ41 | CAPE4B | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389
CONQ41 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 3075 | 2876 | 2663 | 2876
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 2423 | 2327 | 2167 | 2327
COTT41 | GREN41 | 129.478 | 0 | OHL | 0.2293 | 2.5548 | 75.7188 | 2009 | 1911 | 1746 | 1911
COTT41 | KEAD41 | 34.628 | 0 | OHL | 0.0595 | 0.6858 | 20.1792 | 2212 | 2125 | 1979 | 2125
COTT41 | KEAD41 | 34.479 | 0 | OHL | 0.0592 | 0.6828 | 20.0931 | 2212 | 2125 | 1979 | 2125
COTT41 | RYHA42 | 76.891 | 0 | OHL | 0.0834 | 1.3374 | 50.6872 | 2779 | 2569 | 2217 | 2569
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0506 | 0.5544 | 21.5604 | 2212 | 2125 | 1979 | 2052
COTT42 | RYHA41 | 76.816 | 0 | OHL | 0.0834 | 1.3361 | 50.638 | 2779 | 2569 | 2217 | 2569
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0105 | 0.1321 | 3.9942 | 3326 | 3160 | 2971 | 3160
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0619 | 1.1211 | 9.699 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.007 | 0.113 | 4.2822 | 2771 | 2568 | 2217 | 2568
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0125 | 0.2001 | 7.5827 | 2779 | 2568 | 2217 | 2568
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0394 | 0.6314 | 23.9301 | 2779 | 2568 | 2217 | 2568
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0537 | 0.9095 | 34.8191 | 2779 | 2568 | 2217 | 2568
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 979
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879
CREB2A | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB2B | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 2771 | 2771 | 2663 | 2771
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO41 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO43 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CULJ41 | DIDC41 | 4.898 | 0 | OHL | 0.0053 | 0.0852 | 3.2288 | 2771 | 2568 | 2217 | 2568
DAIN41 | CARR41 | 2.545 | 0 | OHL | 0.0043 | 0.0496 | 1.5076 | 2169 | 2084 | 1940 | 2084
DAIN41 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0541 | 0.6511 | 66.8001 | 2397 | 2300 | 2144 | 2300
DAIN42 | CONQ41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1604 | 1604 | 1557 | 1557
DINO41 | PENT41 | 4.545 | 6.183 | Composite | 0.0093 | 0.1402 | 126.9578 | 1623 | 1623 | 1571 | 1571
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2009 | 1911 | 1746 | 1911
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1769 | 1320 | 1320 | 1320
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2089 | 2089 | 1878 | 1878
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2771 | 2568 | 2217 | 2568
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505
DRAX42 | THTO42 | 22.579 | 0 | OHL | 0.0245 | 0.3927 | 14.8844 | 2779 | 2568 | 2217 | 2568
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3066 | 2830 | 2418 | 2830
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 2779 | 2568 | 2217 | 2568
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2217 | 2217 | 1801 | 1801
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2779 | 2568 | 2217 | 2568
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST21 | MILH21 | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430
ELST21 | MILH21 | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST4A | ELST41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0749 | 0.6969 | 20.0233 | 1590 | 1500 | 1346 | 1500
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0747 | 0.6944 | 19.9464 | 1590 | 1500 | 1346 | 1500
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911
FAWL41 | LOVE41 | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 1109 | 901 | 901
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4527 | 1967 | 1874 | 1712 | 1874
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1967 | 1875 | 1712 | 1875
FENW4A | DRAX41 | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823
FERR2A | FERR23 | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115
FERR2B | FERR22 | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 981
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 480 | 480 | 330 | 330
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512
FIDF21 | FIDF23 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF22 | FIDF24 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF22 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF23 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF24 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 2212 | 2125 | 1979 | 2125
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 2212 | 2125 | 1979 | 2125
FOUR21 | HARK23 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3102 | 2935 | 2633 | 2813
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390
GRAI41 | TILB41 | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2003 | 2003 | 1939 | 2003
GREN41 | STAY41 | 101.832 | 0 | OHL | 0.1852 | 2.0259 | 59.0223 | 2514 | 2439 | 2314 | 2439
GREN41 | SUND41 | 39.75 | 0 | OHL | 0.0723 | 0.7909 | 23.0368 | 2009 | 1911 | 1746 | 1911
GREN41 | SUND42 | 39.955 | 0 | OHL | 0.0727 | 0.795 | 23.1553 | 2009 | 1911 | 1746 | 1911
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GRSA21 | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119
GRSA21 | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1000
GRSA21 | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 249 | 249 | 229 | 249
GRSA21 | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 249 | 249 | 229 | 249
GRSB21 | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRSB21 | LACK2C | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRSB21 | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 198 | 198 | 180 | 198
GRSB21 | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 249 | 249 | 229 | 249
GWYN4A | BODE41 | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | BODE41 | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HACK2A | TOTT2B | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK2B | TOTT2A | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 955 | 882 | 762 | 882
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HAKB1- | HARK13 | 0 | 1 | OHL | 0.7047 | 2.0317 | 0.451 | 132 | 123 | 106 | 123
HAMH1B | LEMR11 | 0 | 1 | Cable | 0.016 | 0.098 | 1.942 | 229 | 229 | 229 | 229
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1362 | 1285 | 1202 | 1285
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1206 | 1.5777 | 77.2944 | 2009 | 1912 | 1746 | 1912
HARK13 | JUNV1- | 0 | 1 | OHL | 1.194 | 2.729 | 0.743 | 132 | 123 | 106 | 123
HARK21 | HARK23 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -1.4546 | 0 | 1524 | 1524 | 1524 | 1524
HARK21 | HARK23 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 1.4546 | 0 | 1524 | 1524 | 1524 | 1524
HARK22 | HARK24 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.31736 | 0 | 1524 | 1524 | 1524 | 1524
HARK22 | HARK24 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.31736 | 0 | 1524 | 1524 | 1524 | 1524
HARK24 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HARK41 | HAKB4- | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2169 | 2084 | 1940 | 2084
HARK41 | HAKB4B | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2170 | 2084 | 1941 | 2084
HARK41 | HUTT42 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARK41 | HUTT43 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1204 | 1115 | 1018 | 1115
HATL21 | HARM21 | 13.983 | 0 | OHL | 0.0531 | 0.5772 | 3.9082 | 1093 | 1031 | 925 | 1031
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0332 | 0.335 | 2.0887 | 1382 | 1279 | 1157 | 1279
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1148 | 1086 | 1021 | 1086
HATL21 | WBOL21 | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1093 | 1031 | 926 | 1031
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 801
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1093 | 1031 | 925 | 1031
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2545 | 2421 | 2211 | 2421
HEDD4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
HEDD4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
HEDD4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
HEDD4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664
HEYS41 | HAMB4A | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299
HEYS41 | HAMB4B | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3111 | 3326
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3326 | 3160 | 2971 | 3160
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HIBU41 | HACK41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1327 | 1298 | 1200 | 1298
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0254 | 0.2958 | 13.2571 | 2212 | 2125 | 1979 | 2125
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056
HINP21 | BRWA2A | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 767 | 620 | 620
HINP21 | BRWA2B | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 762 | 762 | 619 | 619
HINP41 | MELK41 | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | MELK41 | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | TAUN41 | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1979 | 2125
HINP41 | TAUN42 | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1979 | 2125
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771
HURS21 | LITT2A | 5.164 | 2.613 | Composite | 0.0288 | 0.2786 | 27.8693 | 864 | 864 | 824 | 855
HURS21 | LITT2B | 5.14 | 2.659 | Composite | 0.0288 | 0.2786 | 28.329 | 864 | 861 | 824 | 861
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 882 | 704 | 784
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 882 | 704 | 784
HUTT41 | HUTT42 | 0 | 0 | Thyristor Controlled Series Capacitor | 0 | -0.51142 | 0 | 2770 | 2770 | 2770 | 2770
HUTT41 | HUTT43 | 0 | 0 | Thyristor Controlled Series Capacitor | 0 | -0.51142 | 0 | 2770 | 2770 | 2770 | 2770
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424
INCE11 | CAPE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 3.2486 | 258 | 258 | 240 | 240
INCE11 | CAPE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 3.2416 | 240 | 240 | 240 | 240
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284
IROA11 | OLDS12 | 0 | 1 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372
IROA12 | OLDS12 | 0 | 1 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524
IROA21 | MELK2B | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750
IRON41 | LEGA4A | 62.073 | 0 | OHL | 0.09913 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.024161 | 0.29094 | 9.0977 | 2397 | 2302 | 2144 | 2302
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 841 | 841 | 665 | 665
JORD21 | NORL2B | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381
KEAD41 | GART4B | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3180 | 3000 | 2692 | 3000
KEAD42 | FENW4A | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0308 | 0.4944 | 18.7376 | 2779 | 2568 | 2217 | 2568
KEAD43 | GART4A | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3180 | 3000 | 2692 | 3000
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0307 | 0.4916 | 18.6331 | 3326 | 3160 | 2971 | 3160
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 830 | 830 | 665 | 665
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084
KEMS41 | CANT41 | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0623 | 0.726 | 23.0007 | 3102 | 2935 | 2765 | 2935
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0617 | 0.7176 | 22.7061 | 1927 | 1833 | 1674 | 1833
KENG41 | SJOW41 | 0 | 6 | Cable | 0.0027 | 0.0473 | 43.6608 | 1327 | 1298 | 1200 | 1298
KENG41 | SJOW41 | 0 | 6 | Cable | 0.0027 | 0.0473 | 43.6608 | 1327 | 1298 | 1200 | 1298
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 1327 | 1298 | 1200 | 1298
KENG41 | WIMB41 | 0 | 13 | Cable | 0.0075 | 0.13 | 120.0672 | 1327 | 1298 | 1200 | 1298
KENG41 | WLSD41 | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1730 | 1600 | 1730
KENG41 | WLSD42 | 0 | 3 | Cable | 0.002 | 0.0355 | 32.7456 | 1770 | 1730 | 1600 | 1730
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 698
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 619
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | WASF2B | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KIBY22 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY22 | WASF2A | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KILL41 | KILL41 | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2750 | 2750 | 2750 | 2750
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720
KINO41 | KINO41 | 0 | 0 | Series Reactor | 0.0027 | 2 | 0 | 2002 | 2002 | 2002 | 2002
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
KINO41 | TILB41 | 15.4784 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2003 | 2003 | 1948 | 1948
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619
KITW21 | OCKH21 | 13.738 | 0.222 | Composite | 0.0525 | 0.5743 | 6.2479 | 772 | 772 | 619 | 619
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 551 | 512 | 442 | 512
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 551 | 512 | 442 | 512
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1148 | 1086 | 1021 | 1086
LACK41 | SALH41 | 9.893 | 0.25 | Composite | 0.017853 | 0.19576 | 10.3336 | 1831 | 1739 | 1588 | 1739
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213
LAND41 | LAGA41 | 21.224 | 0 | OHL | 0.033893 | 0.40814 | 12.7628 | 2423 | 2327 | 2168 | 2327
LAND42 | LAGA41 | 21.355 | 0 | OHL | 0.034102 | 0.41077 | 12.8376 | 1389 | 1284 | 1108 | 1284
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA4B | SHRE4A | 46.944 | 0 | OHL | 0.074969 | 0.90276 | 28.2295 | 2002 | 2002 | 2002 | 2002
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIS4A | BRFO41 | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2779 | 2569 | 2217 | 2569
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 750 | 740 | 740
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 1390 | 1284 | 1109 | 1284
LITT41 | WTHU4E | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LITT41 | WTHU4F | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LOFI4A | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOFI4B | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568
MACC41 | STAL42 | 31.196 | 0 | OHL | 0.062 | 0.617 | 18.1761 | 1710 | 1627 | 1488 | 1627
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3160 | 2971 | 3160
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 682 | 629 | 538 | 629
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2518 | 2395 | 2188 | 2395
NECT4A | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3299 | 3078 | 3299
NECT4B | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3258 | 3060 | 3258
NECT4B | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381
NEEP4A | STSB4A | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SALH42 | 12.55 | 0 | OHL | 0.022512 | 0.25577 | 7.0944 | 1831 | 1739 | 1588 | 1739
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.027604 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.027604 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
OCKH21 | WIEN21 | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 599
OCKH2A | WIEN21 | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0375 | 0.3474 | 2.2265 | 1093 | 1031 | 925 | 1031
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2771 | 2568 | 2217 | 2568
PADI41 | PEWO41 | 37.608 | 0 | OHL | 0.055602 | 0.70488 | 23.1779 | 2169 | 2084 | 1940 | 2084
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2779 | 2568 | 2217 | 2568
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2779 | 2569 | 2217 | 2569
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2771 | 2771 | 2692 | 2771
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 217.727 | 5.468 | parallel Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0633 | 0.9555 | 131.5497 | 1135 | 1135 | 992 | 992
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PERH11 | WYLF11 | 19.94 | 0 | OHL | 0.475 | 4.232 | 1.0947 | 330 | 330 | 300 | 300
PERH11 | WYLF11 | 19.94 | 0 | OHL | 0.475 | 4.232 | 1.0947 | 333 | 307 | 304 | 331
PEWO2A | PEWO2C | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.22479 | 0 | 1524 | 1524 | 1524 | 1524
PEWO2A | PEWO2C | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.225 | 0 | 1524 | 1524 | 1524 | 1524
PEWO2B | PEWO2D | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.55537 | 0 | 1524 | 1524 | 1524 | 1524
PEWO2B | PEWO2D | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.55537 | 0 | 1524 | 1524 | 1524 | 1524
PEWO2C | WASF2A | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO2D | WASF2B | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO41 | HAMB4A | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2189
PEWO41 | HAMB4B | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2189
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 439 | 439 | 381 | 381
PUDM41 | CITR41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136
QUER4A | PEWO41 | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
QUER4B | PEWO41 | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2757 | 2147 | 2056 | 1904 | 2056
RATS41 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2147 | 2056 | 1904 | 2056
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 2212 | 2125 | 1979 | 2125
REBR21 | TOTT21 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127
REBR22 | TOTT22 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 419 | 419 | 404 | 404
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 665
RYEH41 | RYEH4A | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2780 | 2780 | 2780 | 2780
RYEH41 | RYEH4B | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569
RYEH41 | WALX4A | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2779 | 2568 | 2217 | 2568
RYEH4A | WALX4B | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2779 | 2568 | 2217 | 2568
RYHA42 | EASO4B | 58.95 | 0 | OHL | 0.064 | 1.0253 | 38.8593 | 2780 | 2780 | 2780 | 2780
RYHA4B | EASO4A | 58.769 | 0 | OHL | 0.0638 | 1.0222 | 38.7404 | 2779 | 2569 | 2217 | 2569
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1749 | 1664 | 1520 | 1664
SALH41 | SALH42 | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.125 | 0 | 2217 | 2217 | 2217 | 2217
SALH41 | SALH42 | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.125 | 0 | 2217 | 2217 | 2217 | 2217
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424
SELL41 | CANT41 | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048
SELL41 | SELL41 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860
SELL41 | SELL4A | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL41 | SELL4A | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4B | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3326 | 3326 | 3326
SELL41 | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3326 | 3326 | 3326
SELL4B | SELL41 | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL4E | SELL41 | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL4F | DUNG41 | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830
SELL4F | SELL41 | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SING41 | KINO41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748
SING41 | NFLE41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748
SIZE41 | BRFO41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
SIZE41 | LEIS4A | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2779 | 2569 | 2217 | 2569
SJOW21 | TOTT23 | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 868 | 835 | 682 | 762
SJOW21 | TOTT24 | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 868 | 835 | 682 | 762
SJOW41 | HIBU41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
SJOW41 | HIBU41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1327 | 1298 | 1200 | 1298
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2350 | 2146 | 2350
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2350 | 2146 | 2350
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SSHI21 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1236 | 1176 | 1065 | 1176
SSHI21 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1093 | 1031 | 925 | 1031
STAH4A | HAMB4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
STAH4B | HAMB4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
STAL42 | STSB4A | 28.555 | 5.057 | Composite | 0.0343 | 0.5535 | 95.384 | 1649 | 1528 | 1399 | 1528
STAL4A | THOM41 | 71.245 | 4.978 | Composite | 0.0791 | 1.2942 | 122.4093 | 1330 | 1171 | 1001 | 1171
STEN11 | STES11 | 0 | 1 | Cable | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 181
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3048 | 2935 | 2692 | 2935
SUTB41 | WALP41 | 3.85 | 0 | OHL | 0.008 | 0.0773 | 2.2055 | 1340 | 1340 | 1150 | 1340
SWAN41 | PEMB41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2779 | 2568 | 2217 | 2568
SWAN41 | PEMB41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2568 | 2217 | 2568
SWAN41 | RHIG41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 421 | 421 | 381 | 381
THOM21 | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698
THOM41 | BRIN41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395
THUR2A | THUR21 | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1120 | 1060 | 990 | 1060
TILB41 | TILB4A | 0.0581 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TILB41 | TILB4B | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641
TREU4B | CONQ41 | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1093 | 1031 | 912 | 1031
USKM12 | USKM11 | 0 | 0 | Series Reactor | 0.25 | 20 | 0 | 2002 | 2002 | 2002 | 2002
USKM21 | USKM22 | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956
USKM22 | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641
USKM2B | USKM21 | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629
WBUR42 | WBUR41 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 40 | 40 | 40 | 40
WHAM4A | PUDM41 | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136
WISD21 | EALI21 | 0 | 8.075 | Cable | 0.002 | 0.0229 | 10.13 | 665 | 665 | 665 | 665
WTHU4C | WTHU4E | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WTHU4D | WTHU4F | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400

## B-2-1d
B.2.1d - OFTO Transmission Circuits for 2020/21
OFTO | Station | Node 1 | Node 2 | OHL Length(km) | Cable Length(km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
Hornsea One Limited | Hornsea 1 Wind Farm | KILL41 | HOWA41 | 0 | 0.52 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | KILL41 | HOWA41 | 0 | 0.5 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | HOWA21 | HOWR2A | 0 | 105.103 | Cable | 0.68384 | 3.2701 | 292.1283 | 380 | 220
|  | HOWR2A | HOWW21 | 0 | 66.2 | Cable | 0.4924 | 1.6413 | 175.1469 | 380 | 220
|  | HOWA21 | HOWR2A | 0 | 104.903 | Cable | 0.69628 | 3.1955 | 303.8973 | 380 | 220
|  | HOWR2A | HOWW22 | 0 | 72.2 | Cable | 0.47736 | 1.7155 | 203.0972 | 380 | 220
|  | HOWW21 | HOWW22 | 0 | 12.3 | Cable | 0.15756 | 0.30496 | 34.5997 | 364 | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | HUMW11 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 122 | 132
|  | HUMO12 | HUMW12 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 122 | 132
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | BOSW11 | 0 | 29.45 | Cable | 1.634 | 2.451 | 25.197 | 106 | 132
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BODE41 | BBWO41 | 0 | 0.6 | Cable | 0.0012606 | 0.0090575 | 7.0016 | 277.8 | 400
|  | BBWO21 | BBWW21 | 0 | 34.622 | Cable | 0.38748 | 0.93347 | 103.7511 | 286.2 | 220
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDO11 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
|  | DUDW12 | DUDO11 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
East Anglia One Limited | East Anglia Offshore Wind Farm | BRFO41 | BRST41 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRFO41 | BRST42 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRST21 | EAAW21 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
|  | BRST22 | EAAW22 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO12 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO11 | GANW11 | 0 | 45.8 | Cable | 1.23 | 2.8301 | 58.38 | 180.6 | 132
|  | GALO12 | GANW12 | 0 | 45.8 | Cable | 1.23 | 2.8301 | 58.38 | 180.6 | 132
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO11 | ORMW11 | 0 | 44.347 | Cable | 0.7323 | 3.104 | 46.68 | 158 | 132
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SALL11 | 0 | 44.4 | Cable | 1.2127 | 3.3331 | 54.81 | 178 | 132
|  | SSBW11 | SALL12 | 0 | 42.5 | Cable | 1.144 | 3.2022 | 52.73 | 178 | 132
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO21 | TKNW21 | 0 | 106.8 | Cable | 0.56 | 3.13 | 310 | 427 | 220
|  | BICF41 | TKNO41 | 0 | 2.01 | Cable | 0.004 | 0.02 | 18.6 | 505 | 400
|  | BICF41 | TKNO41 | 0 | 1.78 | Cable | 0.004 | 0.02 | 16.5 | 505 | 400
Diamond Transmission Partners Walney Extension Limited | Walney Extension Wind Farm | WOWE21 | WACW21 | 0 | 80.1 | Cable | 0.9432 | 1.99 | 251.59 | 340 | 220
|  | WADW21 | WACW21 | 0 | 22.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 220
|  | WOWE22 | WADW21 | 0 | 66 | Cable | 0.9432 | 1.99 | 251.59 | 340 | 220
|  | MIDL41 | WOWE41 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
|  | MIDL41 | WOWE42 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
WoDS Transmission plc | West of Duddon Sands | WDSW11 | WDSO11 | 0 | 42.08 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | WDSW12 | WDSO12 | 0 | 42.08 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | HEYS41 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
|  | HEYS41 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERW11 | WERO11 | 0 | 25.8335 | Cable | 0.29494 | 1.4823 | 45.7125 | 140 | 150
|  | WERO21 | HEDO21 | 0 | 0.368 | Cable | 0.003209 | 0.012987 | 1.3567 | 256.7809 | 275
|  | WERO22 | HEDO21 | 0 | 0.329 | Cable | 0.0024822 | 0.010046 | 1.0494 | 256.7809 | 275
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GGON11 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GGON12 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GGON13 | LEIS11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GALO11 | GGON11 | 0 | 17 | Cable | 0.36 | 1.07 | 20.5 | 150 | 132
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS11 | 0 | 12.789 | Cable | 0.3254 | 0.8061 | 15.5518 | 158 | 132
Blue Transmission London Array Limited | London Array Offshore Wind Farm | CLEH41 | LONO4A | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
|  | CLEH41 | LONO4B | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
|  | LONO11 | LOAW11 | 0 | 53.798 | Cable | 1.5829 | 2.9755 | 73.1044 | 167 | 150
|  | LONO12 | LOAW12 | 0 | 53.848 | Cable | 1.5837 | 2.9766 | 73.1539 | 167 | 150
|  | LONO13 | LOAW13 | 0 | 52.657 | Cable | 1.5488 | 2.9125 | 71.5816 | 167 | 150
|  | LONO14 | LOAW14 | 0 | 52.682 | Cable | 1.5492 | 2.9137 | 71.6099 | 167 | 150
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | GWYO11 | GWBW11 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 150 | 132
|  | GWYO11 | GWBW12 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 150 | 132
|  | GWYO12 | GWAW11 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 150 | 132
|  | GWYO12 | GWAW12 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 150 | 132
TC Beatrice OFTO Limited | Beatrice Wind Farm | BEIW21 | BEIW22 | 0 | 1.315 | Cable | 0.033 | 0.014 | 4.119 | 321 | 220
|  | BEIW21 | BEAT21 | 0 | 89.2 | Cable | 0.8221 | 2.262 | 291.8746 | 321 | 220
|  | BEIW22 | BEAT22 | 0 | 89.2 | Cable | 0.8221 | 2.262 | 291.8746 | 321 | 220
|  | BEAT4A | BLHI41 | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 400
|  | BEAT4B | BLHI42 | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 400
TC Lincs OFTO Limited | Lincolnshire Offshore Windfarm | LINS11 | LINO11 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
|  | LINS12 | LINO12 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
Diamond Transmission Partners RB Limited | Race Bank Offshore | RACW21 | RACO21 | 0 | 82.5 | Cable | 0.487 | 2.1112 | 247.8447 | 302 | 220
|  | RACW22 | RACO22 | 0 | 83.5 | Cable | 0.4934 | 2.136 | 250.7489 | 302 | 220
|  | WALP41 | RACO41 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | WALP41 | RACO42 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | RACW21 | RACW22 | 0 | 6.7 | Cable | 0.0433 | 0.1661 | 19.4582 | 302 | 220
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RREW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
| Robin Rigg West Offshore Wind Farm | RORW11 | RRWW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | BOLN41 | TWNE41 | 0 | 0.6 | Cable | 0.0028 | 0.0042 | 4.4179 | 411 | 400
|  | BOLN41 | TWNE42 | 0 | 0.76 | Cable | 0.0036 | 0.0053 | 5.6068 | 411 | 400
|  | TWNE11 | RAMW11 | 0 | 42.35 | Cable | 0.7285 | 1.9531 | 75.95 | 210 | 150
|  | TWNE12 | RAMW12 | 0 | 42.29 | Cable | 0.7275 | 1.9502 | 75.84 | 210 | 150
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | THOW11 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
|  | THAW12 | THOW12 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO11 | WAAO1A | 0 | 2.9 | Cable | 0.076045 | 0.13688 | 3.5539 | 192 | 132
|  | WAAO1A | WAAW11 | 0 | 43.7 | Cable | 1.2943 | 2.3298 | 55.0577 | 164 | 132
Blue Transmission Walney 2 OFTO | Walney 2 Offshore Wind Farm | WABO11 | WABO1A | 0 | 5.23 | Cable | 0.15 | 0.27 | 6.384 | 192 | 132
|  | WABO1A | WABW11 | 0 | 44.13 | Cable | 1.266 | 2.279 | 53.869 | 164 | 132

## B-2-2a
B.2.2a - SHE Transmission Circuit Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BEAU1J | BEAU1R | 2021 | Change | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1K | BEAU1S | 2021 | Change | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1R | INNE1Q | 2021 | Change | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BEAU1S | INNE1R | 2021 | Change | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BLHI2L | KINT2J | 2021 | Remove | 58.6 | 0 | OHL | 0.3 | 2.54 | 15.3 | 1090 | 1030 | 920 | 1030
BLHI2L | ROTI2J | 2021 | Addition | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI2M | PEHERSV1 | 2021 | Remove | 82.72 | 0 | OHL | 0.42 | 3.576 | 21.598 | 1090 | 1030 | 920 | 1030
BLHI2M | ROTI2K | 2021 | Addition | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
CLAC1Q | SLOY1F | 2021 | Change | 13 | 0 | OHL | 1.3183 | 3.0212 | 0.641 | 132 | 123 | 106 | 123
DOUN1- | LIMK1- | 2021 | Addition | 0 | 4 | Cable | 0.364 | 0.864 | 0.216 | 126 | 117 | 101 | 117
DUNM1- | DUNM1T | 2021 | Change | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 241 | 230 | 210 | 230
DUNM1T | ABED1- | 2021 | Addition | 5 | 0 | OHL | 0.25 | 1.035 | 0.28 | 163 | 152 | 131 | 152
DUNM1T | DUNM1C | 2021 | Change | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 241 | 230 | 210 | 230
ELGI1L | NAIR1Q | 2021 | Change | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1M | NAIR1R | 2021 | Change | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1Q | ELGI1L | 2021 | Change | 0 | 1.8 | Cable | 0.0354 | 0.052 | 1.41 | 251 | 252 | 252 | 252
ELGI1Q | KEIT1- | 2021 | Change | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ELGI1R | ELGI1M | 2021 | Change | 0 | 1.8 | Cable | 0.0354 | 0.052 | 1.41 | 251 | 252 | 252 | 252
ELGI1R | KEIT1- | 2021 | Change | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
INNE1Q | NAIR1Q | 2021 | Remove | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1Q | SLKB1J | 2021 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INNE1R | NAIR1R | 2021 | Remove | 29.3 | 0 | OHL | 2.863 | 6.6 | 3.1 | 126 | 117 | 101 | 117
INNE1R | SLKB1K | 2021 | Addition | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INVE1J | ACHR1R | 2021 | Change | 21.17 | 0 | OHL | 0.3387 | 3.9588 | 1.291 | 739 | 710 | 662 | 710
INVE1K | ANSU1- | 2021 | Change | 11.13 | 0 | OHL | 0.1781 | 2.0813 | 0.679 | 739 | 710 | 662 | 710
INVE1K | SLOY1E | 2021 | Change | 21.4 | 0 | OHL | 2.1684 | 4.9712 | 1.051 | 126 | 117 | 101 | 117
INVR1- | INVR1A | 2021 | Change | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126
INVR1- | INVR1B | 2021 | Change | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126
INVR1A | INVR1C | 2021 | Change | 0 | 4.5 | Cable | 0.0306 | 0.6975 | 6.3 | 213 | 190 | 190 | 190
INVR1B | INVR1D | 2021 | Change | 0 | 4.5 | Cable | 0.0306 | 0.6975 | 6.3 | 213 | 190 | 190 | 190
KIIN1- | INVR1C | 2021 | Change | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126
KIIN1- | INVR1D | 2021 | Change | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126
KINT2K | PEHE2Q | 2021 | Remove | 70.5 | 0 | OHL | 0.36 | 3.07 | 18.48 | 1090 | 1030 | 920 | 1030
NAIR1Q | SLKB1L | 2021 | Addition | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
NAIR1R | SLKB1M | 2021 | Addition | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
PEHE2Q | NEDE2K | 2021 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PEHERSV1 | NEDE2J | 2021 | Addition | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
PORA1Q | ANSU1- | 2021 | Change | 24.27 | 0 | OHL | 0.3883 | 4.5385 | 1.481 | 739 | 710 | 662 | 710
PORA1R | ACHR1R | 2021 | Remove | 14.23 | 0 | OHL | 2.018 | 3.3446 | 0.695 | 99 | 92 | 79 | 92
PORA1R | PORA1T | 2021 | Addition | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1S | ACHR1R | 2021 | Addition | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
PORA1S | PORA1U | 2021 | Addition | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
ROTI2J | KINT2J | 2021 | Addition | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2J | NEDE2J | 2021 | Addition | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
ROTI2K | KINT2K | 2021 | Addition | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
ROTI2K | NEDE2K | 2021 | Addition | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
SLKB1J | SLKB1L | 2021 | Addition | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLKB1K | SLKB1M | 2021 | Addition | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLOY11 | SLOY1E | 2021 | Addition | 0 | 1.2 | Cable | 0.0082 | 0.186 | 1.68 | 213 | 190 | 190 | 190
SLOY12 | SLOY1A | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY12 | SLOY1B | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY12 | SLOY1F | 2021 | Change | 0 | 1.2 | Cable | 0.0082 | 0.186 | 1.68 | 213 | 190 | 190 | 190
SLOY1J | SLOY1C | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY1J | SLOY1D | 2021 | Change | 0 | 0.8 | Cable | 0.0054 | 0.124 | 1.12 | 213 | 190 | 190 | 190
SLOY1L | SLOY1B | 2021 | Change | 0.49 | 0.01 | Composite | 0.05 | 0.1154 | 0.023 | 126 | 117 | 101 | 117
SLOY1M | SLOY1A | 2021 | Change | 0.49 | 0.01 | Composite | 0.05 | 0.1154 | 0.023 | 126 | 117 | 101 | 117
SLOY1N | SLOY1C | 2021 | Change | 0.6 | 0 | OHL | 0.0643 | 0.1457 | 0.03 | 126 | 117 | 101 | 117
SLOY1P | SLOY1D | 2021 | Change | 0.6 | 0 | OHL | 0.0643 | 0.1457 | 0.03 | 126 | 117 | 101 | 117
TOMT1K | GLKO1- | 2021 | Addition | 0 | 3 | Cable | 0.4 | 0.67 | 0.16 | 99 | 92 | 79 | 92
ABNE1Q | ABNE1S | 2022 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ABNE1Q | CHAR1- | 2022 | Change | 24.5 | 0 | OHL | 1.0449 | 5.3324 | 1.297 | 183 | 160 | 149 | 160
ABNE1R | ABNE1T | 2022 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ABNE1R | AMUL1G | 2022 | Change | 28.097 | 0 | OHL | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
ABNE1S | ABNE1T | 2022 | Addition | 1 | 0 | OHL | 0.0002 | 0.0004 | 0 | 132 | 123 | 106 | 123
ABNE1S | CHAR1- | 2022 | Addition | 24.5 | 0 | OHL | 1.0449 | 5.3324 | 1.297 | 183 | 160 | 149 | 160
ABNE1T | BUMU1Q | 2022 | Addition | 17 | 0 | OHL | 1.7991 | 4.0929 | 0.881 | 132 | 123 | 106 | 123
BUMU1Q | CHAR1- | 2022 | Remove | 42.2 | 0 | OHL | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
FAUG1P | LOCL1S | 2022 | Remove | 8.66 | 0 | OHL | 0.4365 | 1.7942 | 0.485 | 241 | 230 | 210 | 230
FAUG1P | MILS1Q | 2022 | Addition | 5.41 | 0 | OHL | 0.2727 | 1.1208 | 0.303 | 241 | 230 | 210 | 230
LAIR1Q | LAIR1R | 2022 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LAIR1Q | LOCB1J | 2022 | Addition | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
LAIR1Q | SHIN1- | 2022 | Remove | 10.5 | 0 | OHL | 1.06 | 2.52 | 0.5 | 126 | 117 | 101 | 117
LAIR1R | LOCB1K | 2022 | Addition | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
LOCL1S | MILS1Q | 2022 | Addition | 3.25 | 0 | OHL | 0.1638 | 0.6734 | 0.182 | 203 | 193 | 176 | 193
ACHR1R | PORA1R | 2024 | Addition | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ACHR1R | PORA1S | 2024 | Remove | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ALYT2A | ALYT2B | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | FETT2P | 2024 | Addition | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2024 | Addition | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2024 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2024 | Addition | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2024 | Addition | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2024 | Addition | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
BEWF1- | ENEI1- | 2024 | Addition | 0 | 34 | Cable | 1.716 | 7.04 | 1.904 | 162 | 154 | 141 | 154
BEWF1- | SHET1R | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLEX1- | FAUG1J | 2024 | Addition | 20 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 241 | 230 | 210 | 230
BLHI2L | ROTI2J | 2024 | Remove | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI2M | ROTI2K | 2024 | Remove | 35.36 | 0 | OHL | 0.1768 | 1.5558 | 9.335 | 1090 | 1030 | 925 | 1030
BLHI4- | BLHI4A | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI4- | ROTI4J | 2024 | Addition | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BLHI4- | ROTI4K | 2024 | Addition | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BRCW2J | KINA2K | 2024 | Addition | 59.8 | 0 | OHL | 0.1638 | 2.4224 | 17.089 | 1910 | 1830 | 1710 | 1830
BRCW2J | TUMM2K | 2024 | Remove | 62.8 | 0 | OHL | 0.172 | 2.544 | 17.947 | 1910 | 1830 | 1710 | 1830
CDWE1- | DORE12 | 2024 | Addition | 0 | 0.1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CHAR1S | LYND1Q | 2024 | Change | 1.9 | 0 | OHL | 0.081 | 0.4135 | 0.101 | 183 | 160 | 149 | 160
CHAR1T | LYND1R | 2024 | Change | 1.9 | 0 | OHL | 0.081 | 0.4135 | 0.101 | 183 | 160 | 149 | 160
CRDH1J | CRDH1K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRDH1J | INVE1K | 2024 | Addition | 10.12 | 0 | OHL | 1.4405 | 2.3785 | 0.496 | 99 | 92 | 79 | 92
CRDH1J | KILC1Q | 2024 | Addition | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92
CRDH1K | FERO1S | 2024 | Addition | 5.02 | 0 | OHL | 0.7118 | 1.1784 | 0.246 | 99 | 92 | 79 | 92
CRDH2J | CRDH2K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRDH2J | DALB2A | 2024 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
CRDH2K | DALB2B | 2024 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
CREA1- | LAIR1R | 2024 | Addition | 22 | 0 | OHL | 2.234 | 5.128 | 1.083 | 132 | 123 | 106 | 123
CRSS1Q | PORA1Q | 2024 | Change | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
CRSS1R | PORA1R | 2024 | Change | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
FERO1S | INVE1J | 2024 | Remove | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
FETT2P | KINT2K | 2024 | Change | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT2P | TEAL2K | 2024 | Remove | 83.55 | 0 | OHL | 0.4226 | 3.6513 | 21.994 | 955 | 880 | 760 | 880
FETT2Q | KINB2J | 2024 | Remove | 137.33 | 0 | OHL | 0.6853 | 5.8914 | 35.895 | 955 | 885 | 760 | 885
FETT2Q | KINT2K | 2024 | Change | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
GARB1Q | SLOY1K | 2024 | Change | 14.23 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1R | SLOY1J | 2024 | Change | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1S | SLOY1J | 2024 | Change | 14.23 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1T | SLOY1K | 2024 | Change | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GILB1J | GILB1K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GILB1J | GILB1L | 2024 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1J | PENF1- | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GILB1K | GILB1M | 2024 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1L | THUS1L | 2024 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
GILB1M | THUS1M | 2024 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
GLRB2- | TEAL2K | 2024 | Change | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
INRU1Q | PEHE1- | 2024 | Change | 6.7 | 0 | OHL | 1.1457 | 4.1339 | 0.208 | 224 | 177 | 158 | 177
INRU1R | PEHE1- | 2024 | Change | 6.7 | 0 | OHL | 1.1457 | 4.1339 | 0.208 | 224 | 177 | 158 | 177
INVE1K | KILC1Q | 2024 | Remove | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
KINA2J | KINA2K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINA2J | TUMM2K | 2024 | Addition | 3 | 0 | OHL | 0.0082 | 0.1216 | 0.858 | 1910 | 1830 | 1710 | 1830
KINB2K | TEAL2J | 2024 | Remove | 86.18 | 0 | OHL | 0.4329 | 3.735 | 23 | 955 | 880 | 760 | 880
KINT2J | ROTI2J | 2024 | Remove | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
KINT2J | TEAL2A | 2024 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2J | TEAL2J | 2024 | Remove | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | ROTI2K | 2024 | Remove | 23.24 | 0 | OHL | 0.093 | 1.0226 | 6.135 | 1380 | 1320 | 1230 | 1320
KINT2K | TEAL2B | 2024 | Addition | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | TEAL2K | 2024 | Remove | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT4J | ROTI4J | 2024 | Addition | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920
KINT4K | ROTI4K | 2024 | Addition | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920
LOCB1J | SHIN1- | 2024 | Change | 12.19 | 0 | OHL | 1.3897 | 2.7671 | 0.61 | 255 | 247 | 237 | 247
LOCB1K | SHIN1- | 2024 | Change | 12.19 | 0 | OHL | 1.3897 | 2.7671 | 0.61 | 255 | 247 | 237 | 247
MORF2- | NEDE2K | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MORF4- | NEDE4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MSHL1- | SHET1J | 2024 | Addition | 0 | 20 | Cable | 1.82 | 4.32 | 1.08 | 126 | 119 | 108 | 119
NEDE2J | NEDE2K | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NEDE2J | PEHERSV1 | 2024 | Remove | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
NEDE2J | ROTI2J | 2024 | Remove | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
NEDE2K | PEHE2Q | 2024 | Remove | 22.39 | 0 | OHL | 0.112 | 0.9852 | 5.911 | 1090 | 1030 | 925 | 1030
NEDE2K | ROTI2K | 2024 | Remove | 24.97 | 0 | OHL | 0.1248 | 1.0986 | 6.592 | 1090 | 1030 | 925 | 1030
NEDE4J | NEDE4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NEDE4J | PEHE4J | 2024 | Addition | 22.39 | 0 | OHL | 0.0448 | 0.4322 | 13.173 | 2000 | 1920 | 1790 | 1920
NEDE4J | ROTI4J | 2024 | Addition | 24.97 | 0 | OHL | 0.0499 | 0.4819 | 14.689 | 2000 | 1920 | 1790 | 1920
NEDE4K | PEHE4K | 2024 | Addition | 22.39 | 0 | OHL | 0.0448 | 0.4322 | 13.173 | 2000 | 1920 | 1790 | 1920
NEDE4K | ROTI4K | 2024 | Addition | 24.97 | 0 | OHL | 0.0499 | 0.4819 | 14.689 | 2000 | 1920 | 1790 | 1920
NESQ30 | THUS3- | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE4J | PEHE4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA1Q | PORA1U | 2024 | Addition | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1S | PORA1U | 2024 | Remove | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
ROTI2J | ROTI2K | 2024 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ROTI4J | ROTI4K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SHET1J | SHET1M | 2024 | Addition | 0 | 1 | Cable | 0.1 | 1 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2B | TEAL2K | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2J | TEAL2A | 2024 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2J | WFIB2- | 2024 | Change | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
THUS1J | THUS1L | 2024 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
THUS1K | THUS1M | 2024 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
ACHR1R | INVE1J | 2026 | Remove | 21.17 | 0 | OHL | 0.3387 | 3.9588 | 1.291 | 739 | 710 | 662 | 710
ACHR1R | PORA1R | 2026 | Remove | 14.23 | 0 | OHL | 0.2277 | 2.661 | 0.868 | 739 | 710 | 662 | 710
ACHR2- | CRDH2J | 2026 | Addition | 31.37 | 0 | OHL | 0.1255 | 1.2861 | 8.846 | 1290 | 1240 | 1160 | 1240
ACHR2- | PORA2M | 2026 | Addition | 14.23 | 0 | OHL | 0.0569 | 0.5834 | 4.013 | 1290 | 1240 | 1160 | 1240
ALYT2A | ALYT2B | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | FETT2P | 2026 | Remove | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2026 | Remove | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 2026 | Remove | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2K | 2026 | Addition | 16.2 | 0 | OHL | 0.0685 | 0.6615 | 4.505 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2026 | Remove | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2026 | Remove | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2J | 2026 | Addition | 16.2 | 0 | OHL | 0.0685 | 0.6615 | 4.505 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2026 | Remove | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT4J | ALYT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT4J | FETT4Q | 2026 | Addition | 67.35 | 0 | OHL | 0.1347 | 1.2999 | 39.622 | 2000 | 1920 | 1790 | 1920
ALYT4J | KINB4J | 2026 | Addition | 69.98 | 0 | OHL | 0.14 | 1.3506 | 41.169 | 2000 | 1920 | 1790 | 1920
ALYT4K | FETT4R | 2026 | Addition | 67.35 | 0 | OHL | 0.1347 | 1.2999 | 39.622 | 2000 | 1920 | 1790 | 1920
ALYT4K | KINB4K | 2026 | Addition | 69.98 | 0 | OHL | 0.14 | 1.3506 | 41.169 | 2000 | 1920 | 1790 | 1920
ANSU1- | INVE1K | 2026 | Remove | 11.13 | 0 | OHL | 0.1781 | 2.0813 | 0.679 | 739 | 710 | 662 | 710
ANSU1- | PORA1Q | 2026 | Remove | 24.27 | 0 | OHL | 0.3883 | 4.5385 | 1.481 | 739 | 710 | 662 | 710
ANSU2- | CRDH2K | 2026 | Addition | 21.33 | 0 | OHL | 0.0853 | 0.8745 | 6.015 | 1290 | 1240 | 1160 | 1240
ANSU2- | PORA2L | 2026 | Addition | 24.27 | 0 | OHL | 0.0971 | 0.9951 | 6.844 | 1290 | 1240 | 1160 | 1240
ARMO1J | DUGR1Q | 2026 | Change | 14 | 0 | OHL | 0.7058 | 2.91 | 0.784 | 241 | 230 | 210 | 230
ARMO3- | ARMO3J | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | ARNI1J | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | ARNI1Q | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | DRUL1- | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | MUAI1- | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ARNI1K | STWN1- | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU4- | BEAU4R | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BERB2Q | CLGO2A | 2026 | Addition | 0 | 0.46 | Cable | 0.0026 | 0.019 | 0.126 | 935 | 880 | 790 | 880
BEWF1- | ENEI1- | 2026 | Change | 34 | 0 | OHL | 1.714 | 7.038 | 1.904 | 241 | 230 | 210 | 230
BLHI1J | ELCH1- | 2026 | Addition | 24 | 0 | OHL | 1.2 | 4.968 | 1.344 | 241 | 230 | 210 | 230
BLHI2A | CLGO2A | 2026 | Addition | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880
BLHI2B | BLHI2K | 2026 | Addition | 0 | 0 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2B | DAAS2- | 2026 | Addition | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2J | BERB2Q | 2026 | Remove | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BLHI2J | BLHI2A | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2K | DAAS2- | 2026 | Remove | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BROA1- | EDIN1- | 2026 | Addition | 46.06 | 0 | OHL | 1.089 | 9.771 | 2.539 | 448 | 430 | 398 | 430
BROA1- | LOCL1S | 2026 | Addition | 81.7 | 0 | OHL | 1.9307 | 17.3312 | 4.503 | 448 | 430 | 398 | 430
BROA1- | QUOI1Q | 2026 | Addition | 63.41 | 0 | OHL | 1.4985 | 13.4519 | 3.495 | 448 | 430 | 398 | 430
BROA1Q | EDIN1- | 2026 | Remove | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92
BROA1Q | QUOI1Q | 2026 | Remove | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92
CASS1Q | SALA1- | 2026 | Addition | 6 | 0 | OHL | 0.63 | 1.308 | 0.318 | 126 | 117 | 101 | 117
CLGO2- | DAAS2- | 2026 | Addition | 13.37 | 0 | OHL | 0.0757 | 0.5503 | 3.645 | 935 | 880 | 790 | 880
CLGO2- | KNOC2K | 2026 | Addition | 46.85 | 0 | OHL | 0.2653 | 1.9287 | 12.774 | 935 | 880 | 790 | 880
CLOI1- | CLOI11 | 2026 | Addition | 8 | 0 | OHL | 0.256 | 1.744 | 0.424 | 280 | 270 | 245 | 270
CLOI1- | MELG1K | 2026 | Addition | 0 | 0.2 | Cable | 0.0053 | 0.0306 | 0.543 | 220 | 211 | 211 | 211
CONN1D | STRW17 | 2026 | Addition | 12.12 | 0 | OHL | 0.6109 | 2.5094 | 0.679 | 241 | 230 | 210 | 230
CONN1K | CONN1D | 2026 | Addition | 0 | 0.66 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178
CONN2J | LOCB2J | 2026 | Change | 76.34 | 0 | OHL | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CONN2K | DOUN2- | 2026 | Addition | 8.77 | 0 | OHL | 0.0526 | 0.4826 | 1.86 | 702 | 665 | 599 | 665
CONN2K | GORW2- | 2026 | Addition | 49.33 | 0 | OHL | 0.296 | 2.7134 | 10.46 | 702 | 665 | 599 | 665
CRDH1J | INVE1K | 2026 | Remove | 0 | 0 | OHL | 1.4405 | 2.3785 | 0.496 | 99 | 92 | 79 | 92
CRSS1J | CRSS1R | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | CRSS1R | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | PORA1Q | 2026 | Remove | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
CRSS1R | PORA1R | 2026 | Remove | 48.3 | 0 | OHL | 0.7728 | 9.0321 | 2.946 | 739 | 710 | 662 | 710
CRSS1R | SHDM1- | 2026 | Addition | 10 | 0 | OHL | 0.5 | 2.07 | 0.56 | 241 | 230 | 210 | 230
CRSS2J | PORA2L | 2026 | Addition | 48.3 | 0 | OHL | 0.1932 | 1.9803 | 13.621 | 1290 | 1240 | 1160 | 1240
CRSS2K | PORA2M | 2026 | Addition | 48.3 | 0 | OHL | 0.1932 | 1.9803 | 13.621 | 1290 | 1240 | 1160 | 1240
DAAS2- | KNOC2K | 2026 | Remove | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
DOUN2- | GORW2- | 2026 | Remove | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DOUN2A | DOUN2B | 2026 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 292 | 292 | 292 | 292
DOUN2B | DOUN2C | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 294 | 294 | 294 | 294
DOUN2C | FINS2C | 2026 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 270 | 270 | 270 | 270
DOUN2D | DOUN2E | 2026 | Addition | 0 | 2 | Cable | 0.011 | 0.05 | 5.315 | 240 | 240 | 240 | 240
DOUN2E | DOUN2F | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 240 | 240 | 240 | 240
DOUN2F | FINS2F | 2026 | Addition | 0 | 60 | Cable | 0.818 | 1.612 | 142.296 | 240 | 240 | 240 | 240
DUGR1Q | EDIN1- | 2026 | Remove | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92
DUGR1Q | GLNU1- | 2026 | Addition | 8.49 | 0 | OHL | 4.5472 | 18.8256 | 5.093 | 241 | 230 | 210 | 230
EDIN1- | GLNU1- | 2026 | Addition | 0.5 | 0 | OHL | 0.0118 | 0.1061 | 0.028 | 448 | 430 | 398 | 430
FAUG1- | FAUG1M | 2026 | Remove | 0 | 0.29 | Cable | 0.01 | 0.0225 | 0.486 | 220 | 209 | 209 | 209
FAUG1- | FAUG1N | 2026 | Remove | 0 | 0.2 | Cable | 0.01 | 0.0157 | 0.339 | 220 | 209 | 209 | 209
FAUG1- | FAUG1P | 2026 | Change | 0.59 | 0 | OHL | 0.0139 | 0.1252 | 0.033 | 448 | 430 | 398 | 430
FAUG1- | QUOI1Q | 2026 | Addition | 27.55 | 0 | OHL | 0.651 | 5.8445 | 1.519 | 448 | 430 | 398 | 430
FAUG1M | LOCL1Q | 2026 | Remove | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 2026 | Remove | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1P | MILS1Q | 2026 | Change | 5.41 | 0 | OHL | 0.1278 | 1.1477 | 0.298 | 448 | 430 | 398 | 430
FAUG4J | INGA4K | 2026 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940 | 1860 | 1720 | 1860
FAUG4K | INGA4J | 2026 | Addition | 8.5 | 0 | OHL | 0.0175 | 0.1625 | 4.88 | 1940 | 1860 | 1720 | 1860
FETT2P | FETT2R | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2P | KINT2K | 2026 | Remove | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT2Q | FETT2R | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2Q | KINT2K | 2026 | Remove | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT4J | FETT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4Q | FETT4J | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4Q | KINT4J | 2026 | Addition | 32.15 | 0 | OHL | 0.0643 | 0.6205 | 18.914 | 2000 | 1920 | 1790 | 1920
FETT4R | FETT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4R | KINT4K | 2026 | Addition | 32.15 | 0 | OHL | 0.0643 | 0.6205 | 18.914 | 2000 | 1920 | 1790 | 1920
FINS2A | FINS2B | 2026 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 292 | 292 | 292 | 292
FINS2B | FINS2C | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 294 | 294 | 294 | 294
FINS2D | FINS2E | 2026 | Addition | 0 | 12 | Cable | 0.067 | 0.3 | 31.89 | 240 | 240 | 240 | 240
FINS2E | FINS2F | 2026 | Addition | 0 | 0.5 | Cable | 0.002 | 0.01 | 1.666 | 240 | 240 | 240 | 240
FWIL1Q | INGA1J | 2026 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1Q | LOCL1Q | 2026 | Remove | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | INGA1K | 2026 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 2026 | Remove | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
GILB1K | PENF1B | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GLSH1J | MELG1J | 2026 | Addition | 0 | 0.2 | Cable | 0.0027 | 0.0153 | 0.271 | 220 | 211 | 211 | 211
INGA1J | INGA1K | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INGA1Q | INGA1K | 2026 | Addition | 0 | 2.4 | Cable | 0.1224 | 0.5376 | 0.125 | 187 | 177 | 158 | 177
INGA1Q | LOCL1Q | 2026 | Remove | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
KINT4J | KINT4K | 2026 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCL1S | MILS1Q | 2026 | Change | 3.25 | 0 | OHL | 0.0768 | 0.6895 | 0.179 | 448 | 430 | 398 | 430
LOCL1S | QUOI1Q | 2026 | Remove | 18.3 | 0 | OHL | 0.9219 | 3.7893 | 1.025 | 241 | 230 | 210 | 230
NWGL4- | PEHE4J | 2026 | Addition | 0 | 1 | Cable | 0.1 | 0.3 | 0 | 9999 | 9999 | 9999 | 9999
PORA1Q | PORA1U | 2026 | Remove | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1R | PORA1T | 2026 | Remove | 5.6 | 0 | OHL | 0.778 | 1.25 | 0.274 | 99 | 92 | 79 | 92
PORA1T | PORA1U | 2026 | Remove | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA2J | PORA2K | 2026 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA2J | PORA2M | 2026 | Addition | 0 | 5.6 | Cable | 0.0224 | 0.2296 | 1.579 | 1290 | 1240 | 1160 | 1240
PORA2K | PORA2L | 2026 | Addition | 0 | 5.6 | Cable | 0.0224 | 0.2296 | 1.579 | 1290 | 1240 | 1160 | 1240
ALTN1- | CONN1J | 2029 | Addition | 18 | 0 | OHL | 1.638 | 3.888 | 0.972 | 150 | 142 | 128 | 142
BERB2Q | CAID2- | 2029 | Addition | 7.99 | 0 | OHL | 0.0452 | 0.3288 | 2.178 | 935 | 880 | 790 | 880
BERB2Q | KNOC2J | 2029 | Remove | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
BETH1A | BETH1B | 2029 | Addition | 12.5 | 0 | OHL | 0.625 | 2.5875 | 0.7 | 224 | 211 | 189 | 211
BETH1A | FYRI1J | 2029 | Addition | 0 | 0.5 | Cable | 0.0103 | 0.0424 | 0.674 | 190 | 174 | 174 | 174
BETH1B | BETH1C | 2029 | Addition | 0 | 6 | Cable | 0.1233 | 0.5091 | 8.092 | 190 | 174 | 174 | 174
BLGH1- | CRDH1J | 2029 | Addition | 10 | 0 | OHL | 0.91 | 2.16 | 0.54 | 150 | 142 | 128 | 142
CAID2- | KNOC2J | 2029 | Addition | 38.99 | 0 | OHL | 0.2208 | 1.6052 | 10.631 | 935 | 880 | 790 | 880
COGL4- | COGL4J | 2029 | Addition | 0 | 1.95 | Cable | 0.0015 | 0.0264 | 9.165 | 930 | 900 | 900 | 900
COGL4- | COGL4K | 2029 | Addition | 0 | 1.95 | Cable | 0.0015 | 0.0264 | 9.165 | 930 | 900 | 900 | 900
COGL4J | INGA4J | 2029 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1470 | 1350 | 1170 | 1350
COGL4K | INGA4K | 2029 | Addition | 10 | 0 | OHL | 0.0206 | 0.1988 | 5.792 | 1470 | 1350 | 1170 | 1350
DOUN2- | OFPH2- | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4J | DOUN4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4J | SPIT4J | 2029 | Addition | 15.4 | 0 | OHL | 0.0206 | 0.2826 | 9.541 | 2810 | 2700 | 2510 | 2700
DOUN4K | SPIT4K | 2029 | Addition | 15.4 | 0 | OHL | 0.0206 | 0.2826 | 9.541 | 2810 | 2700 | 2510 | 2700
GILB1J | PENF1C | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MOTA1Q | SHIN1- | 2029 | Change | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 106 | 117
OFPK4- | PEHE4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
OFPN4- | PEHE4J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
SPIT4J | SPIT4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999

## B-2-2b
B.2.2b - SPT Circuit Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
COAL1- | DONO1- | 2021 | Addition | 0 | 4.5 | Cable | 0.1271 | 0.2921 | 5.5423 | 165 | 165 | 165 | 165
COAL1- | MIDM1- | 2021 | Remove | 0 | 14.47 | Cable | 0.4086 | 0.9392 | 17.8217 | 158 | 146 | 146 | 146
COAL1A | LINM1Q | 2021 | Change | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
DONO1- | MIDM1- | 2021 | Addition | 0 | 10.57 | Cable | 0.2985 | 0.6861 | 13.0183 | 158 | 146 | 146 | 146
GLNI1- | MOSM1A | 2021 | Change | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 265 | 246 | 212 | 246
GLNI1- | MOSM1B | 2021 | Change | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 265 | 246 | 212 | 246
KAIM2- | SMEA2- | 2021 | Change | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1300 | 1230 | 1150 | 1230
LEVT1R | WFIE1B | 2021 | Change | 18.707 | 0 | OHL | 1.4753 | 4.1917 | 0.9554 | 143 | 142 | 128 | 142
REDH1- | WFIE1A | 2021 | Change | 10.097 | 0 | OHL | 0.695 | 2.2577 | 0.5197 | 157 | 152 | 141 | 152
AREX1A | CHMO1T | 2022 | Addition | 4.7 | 0 | OHL | 0.3571 | 1.0182 | 0.2484 | 284 | 278 | 270 | 278
AREX1A | MAHI1X | 2022 | Addition | 7.5 | 0 | OHL | 0.5699 | 1.6247 | 0.3964 | 365 | 360 | 350 | 360
AYR-2Q | COYW2S | 2022 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1050 | 965 | 880 | 965
AYR-2R | COYW2T | 2022 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1050 | 965 | 880 | 965
CHAP1- | GRNA1- | 2022 | Change | 12.83 | 0.35 | Composite | 0.9812 | 3.1043 | 0.9907 | 167 | 160 | 148 | 160
CHAP1- | GRNA1- | 2022 | Change | 12.83 | 0.3 | Composite | 0.9799 | 3.0991 | 0.9387 | 167 | 160 | 148 | 160
COAL1A | CUMH1- | 2022 | Addition | 0 | 7.7 | Cable | 0.1211 | 0.6629 | 12.6869 | 241 | 241 | 241 | 241
COAL1A | GAWH1Q | 2022 | Remove | 0 | 10.5 | Cable | 0.1651 | 0.9039 | 17.3003 | 241 | 241 | 241 | 241
COCK4Q | ECCL4A | 2022 | Change | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1090 | 1030 | 925 | 1030
COCK4R | ECCL4B | 2022 | Change | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1090 | 1030 | 925 | 1030
CUMH1- | GAWH1Q | 2022 | Addition | 0 | 3.2 | Cable | 0.0503 | 0.2755 | 5.2725 | 241 | 241 | 241 | 241
DENN2- | LAMB2T | 2022 | Addition | 32.18 | 0 | OHL | 0.1451 | 1.3095 | 8.9356 | 953 | 882 | 762 | 882
DENN2- | LOAN2- | 2022 | Addition | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1C | 2022 | Change | 6.4 | 4.3 | Composite | 0.5762 | 1.7993 | 6.3388 | 135 | 125 | 108 | 125
DEVM1- | ERSK1Q | 2022 | Change | 16.5 | 0 | OHL | 1.0026 | 3.563 | 0.8861 | 213 | 202 | 185 | 202
DEVM4- | HUNE4- | 2022 | Remove | 50.471 | 0.167 | Composite | 0.0909 | 0.9984 | 33.1263 | 1316 | 1067 | 1067 | 1067
DEVM4- | NEIL4R | 2022 | Addition | 28.474 | 0 | OHL | 0.0582 | 0.5967 | 15.8233 | 1995 | 1926 | 1787 | 1926
DEVM4- | WIYH4Q | 2022 | Change | 28.908 | 0 | OHL | 0.0586 | 0.5888 | 16.3967 | 1995 | 1926 | 1787 | 1926
ELDE1Q | JOHN1Q | 2022 | Change | 0 | 3.9 | Cable | 0.1101 | 0.2531 | 4.8034 | 120 | 120 | 120 | 120
ELDE1R | JOHN1R | 2022 | Change | 0 | 3.9 | Cable | 0.1101 | 0.2531 | 4.8034 | 120 | 120 | 120 | 120
EWEH1Q | GRNA1- | 2022 | Change | 15.9 | 0.3 | Composite | 1.2123 | 3.4542 | 1.6286 | 262 | 262 | 262 | 262
EWEH1Q | HOPR1- | 2022 | Addition | 6 | 0 | OHL | 0.4507 | 1.3202 | 0.316 | 199 | 191 | 175 | 191
GLGL1Q | SAKN1- | 2022 | Addition | 0 | 7 | Cable | 0.1977 | 0.4544 | 8.6214 | 134 | 123 | 123 | 123
HUNE4- | NEIL4Q | 2022 | Change | 35.198 | 0 | OHL | 0.068 | 0.7118 | 20.1554 | 1469 | 1351 | 1164 | 1351
HUNE4- | NEIL4R | 2022 | Addition | 34.97 | 0 | OHL | 0.0675 | 0.7072 | 20.0247 | 1995 | 1926 | 1787 | 1926
LAMB2T | LOAN2- | 2022 | Remove | 53.67 | 0.225 | Composite | 0.1948 | 2.0808 | 18.1931 | 795 | 620 | 620 | 620
MAHI1B | MAHI1X | 2022 | Addition | 0 | 0.5 | Cable | 0.0032 | 0.0298 | 0.8758 | 365 | 360 | 350 | 360
NECU1C | SOKY1- | 2022 | Addition | 0 | 4.5 | Cable | 0.0292 | 0.2677 | 7.8824 | 242 | 223 | 192 | 223
NEIL2- | WIYH2R | 2022 | Change | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1372 | 1324 | 1228 | 1324
AREX1- | AREX1A | 2024 | addition | 0 | 2.5 | Cable | 0.0445 | 0.2384 | 2.9171 | 85 | 85 | 85 | 85
BENB1- | BENB1B | 2024 | addition | 3 | 0 | OHL | 0.2251 | 0.6606 | 0.1578 | 167 | 160 | 148 | 160
BENB1B | GNSH1- | 2024 | addition | 30.35 | 0.9 | Composite | 1.3071 | 6.1749 | 3.2285 | 241 | 241 | 241 | 241
BENB1B | NECU1B | 2024 | addition | 4 | 0 | OHL | 0.1038 | 0.7722 | 0.2394 | 482 | 445 | 385 | 445
BERW1Q | ECCL1- | 2024 | Change | 21.54 | 0.31 | Composite | 1.622 | 4.903 | 1.5274 | 132 | 123 | 106 | 123
BERW1Q | MARM1- | 2024 | addition | 4.2 | 0 | OHL | 0.3155 | 0.9241 | 0.2212 | 167 | 160 | 148 | 160
BERW1R | ECCL1- | 2024 | Change | 21.54 | 0.27 | Composite | 1.6213 | 4.8991 | 1.4716 | 132 | 123 | 106 | 123
BERW1R | MARM1- | 2024 | addition | 4.2 | 0 | OHL | 0.3155 | 0.9241 | 0.2212 | 167 | 160 | 148 | 160
BLAH1- | GLGL1- | 2024 | Change | 13.6 | 0.375 | Composite | 0.5154 | 2.926 | 1.6551 | 268 | 246 | 246 | 246
BLAH1- | GLGL1- | 2024 | Change | 13.6 | 0.375 | Composite | 0.5154 | 2.926 | 1.6551 | 268 | 246 | 246 | 246
BLCW1- | GNSH1- | 2024 | addition | 1.8 | 0 | OHL | 0.135 | 0.3964 | 0.0947 | 167 | 160 | 148 | 160
BLCW1- | MARG1- | 2024 | Remove | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 166 | 159 | 147 | 159
BRAP1- | ERSK1Q | 2024 | Change | 3.17 | 5.4 | Composite | 0.3985 | 1.1026 | 12.4454 | 167 | 160 | 148 | 160
BRAP1- | ERSK1R | 2024 | Change | 3.45 | 6.23 | Composite | 0.4418 | 1.1771 | 12.9647 | 167 | 160 | 148 | 160
BROC1- | BROC1T | 2024 | addition | 0 | 0.2 | Cable | 0.0056 | 0.013 | 0.2463 | 134 | 123 | 123 | 123
BROC1T | COAL1A | 2024 | addition | 0 | 3.2 | Cable | 0.0261 | 0.2614 | 5.959 | 293 | 293 | 293 | 293
BROC1T | LINM1Q | 2024 | addition | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 416 | 395 | 361 | 395
CHMO1- | CHMO1T | 2024 | addition | 0.3 | 0 | OHL | 0.0225 | 0.066 | 0.0158 | 167 | 160 | 147 | 160
CHMO1T | STNO1- | 2024 | addition | 4.5 | 0 | OHL | 0.3376 | 0.991 | 0.2367 | 167 | 160 | 147 | 160
COAL1A | LINM1Q | 2024 | Remove | 5.774 | 3.2 | Composite | 0.1634 | 1.5637 | 6.2562 | 293 | 293 | 293 | 293
COAL1B | CUMH1- | 2024 | Change | 0 | 7.7 | Cable | 0.1195 | 0.6543 | 13.0164 | 241 | 241 | 241 | 241
COAL1B | CUMW1- | 2024 | addition | 0 | 9.1 | Cable | 0.257 | 0.5907 | 11.955 | 120 | 120 | 120 | 120
COAL1B | DONO1- | 2024 | Change | 0 | 4.5 | Cable | 0.0635 | 0.146 | 11.0847 | 330 | 330 | 330 | 330
COAL1B | KENN1- | 2024 | addition | 15.4 | 2 | Composite | 1.2117 | 3.5211 | 3.2733 | 167 | 161 | 150 | 161
COYL2- | CRCK2- | 2024 | addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
COYL2- | MAHI2- | 2024 | Remove | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
CRCK2- | MAHI2- | 2024 | addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
CROO1Q | NEIL1- | 2024 | Change | 12.56 | 0.22 | Composite | 0.4737 | 2.7011 | 0.9855 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 2024 | Change | 12.56 | 0.23 | Composite | 0.4738 | 2.702 | 0.9994 | 229 | 211 | 183 | 211
CURR1A | GORG1Q | 2024 | Change | 1.49 | 5.8 | Composite | 0.261 | 0.9656 | 5.1127 | 111 | 100 | 92 | 100
CURR1B | GORG1R | 2024 | Change | 1.49 | 5.78 | Composite | 0.2603 | 0.9634 | 5.0953 | 111 | 100 | 92 | 100
DALB2A | DALL2- | 2024 | addition | 0 | 0 | Cable | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000
DALB2B | DALL2- | 2024 | addition | 0 | 0 | Cable | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000
DENN2- | LOAN2Z | 2024 | Addition | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2- | 2024 | Remove | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
ELDE1Q | NEIL1- | 2024 | Change | 3.82 | 0.18 | Composite | 0.1455 | 0.8324 | 0.4574 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 2024 | Change | 3.82 | 0.23 | Composite | 0.1461 | 0.8373 | 0.5271 | 229 | 211 | 183 | 211
ELVA1- | NLEI1- | 2024 | addition | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 217 | 198 | 217
ENHI1- | NECU1C | 2024 | addition | 0 | 4.4 | Cable | 0.1242 | 0.2856 | 5.7805 | 134 | 123 | 123 | 123
GHPS1- | GLGL1- | 2024 | addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 482 | 445 | 385 | 445
GHPS1- | GLGL1- | 2024 | addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 482 | 445 | 385 | 445
GHPS1- | LETH1- | 2024 | addition | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 200 | 200 | 200 | 200
GLGL1- | SAKN1- | 2024 | Change | 0 | 7 | Cable | 0.1977 | 0.4544 | 8.6214 | 134 | 123 | 123 | 123
GLGL1- | SANQ1- | 2024 | addition | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277
GLLE1- | NETS1- | 2024 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLLE1- | NETS1- | 2024 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLNI1- | WFIE1B | 2024 | Change | 7.11 | 0 | OHL | 0.5359 | 1.6524 | 0.3546 | 332 | 318 | 294 | 318
GLRB2- | GLRO2- | 2024 | Change | 14.68 | 0 | OHL | 0.0662 | 0.6092 | 3.9929 | 1096 | 1029 | 924 | 1029
GLRO2- | WFIE2- | 2024 | Change | 12.08 | 0 | OHL | 0.0545 | 0.5013 | 3.2857 | 1096 | 1029 | 924 | 1029
GORG1Q | TELR1Q | 2024 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GORG1R | TELR1R | 2024 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GRNA1- | HAWI1- | 2024 | Change | 55.35 | 0 | OHL | 5.0077 | 12.6881 | 2.7627 | 133 | 124 | 107 | 124
GRNA1- | JUNV1- | 2024 | Change | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 167 | 155 | 134 | 155
HAWI1- | JUNV1- | 2024 | Change | 50.34 | 0 | OHL | 4.5503 | 11.4999 | 2.5189 | 132 | 123 | 106 | 123
HOLM1- | HOLM1T | 2024 | addition | 8 | 0 | OHL | 0.6078 | 1.7331 | 0.4228 | 366 | 359 | 350 | 359
HOLM1- | LORG1- | 2024 | addition | 10 | 0 | OHL | 0.5312 | 2.1273 | 0.5456 | 242 | 232 | 212 | 232
HOLM1- | SHRG1- | 2024 | addition | 1.01 | 0 | OHL | 0.0759 | 0.2222 | 0.0532 | 167 | 160 | 148 | 359
HOLM1T | KEOO1- | 2024 | addition | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 133 | 123 | 106 | 123
HOLM1T | NECU1B | 2024 | addition | 16.35 | 0 | OHL | 0.4243 | 3.1565 | 0.9785 | 482 | 445 | 385 | 445
KEOO1- | NECU1B | 2024 | Remove | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 133 | 123 | 106 | 123
KINB2J | KINC2- | 2024 | Change | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2024 | Change | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 1090 | 1030 | 925 | 1030
LOAN2- | MOSM2L | 2024 | Change | 26.196 | 0.194 | Composite | 0.1184 | 1.0894 | 10.6096 | 1096 | 1029 | 924 | 1029
LOAN2Z | WFIE2- | 2024 | Addition | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
LOAN2- | WFIE2- | 2024 | Remove | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 760 | 620 | 620 | 620
MARG1- | NECU1B | 2024 | Remove | 34.35 | 0.9 | Composite | 1.1487 | 6.9058 | 3.4859 | 241 | 230 | 210 | 230
MOSM2- | MOSM2L | 2024 | Change | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 1090 | 1030 | 925 | 1030
MOSM2- | MOSM2T | 2024 | Change | 5.3 | 0 | OHL | 0.0245 | 0.2419 | 1.3502 | 1096 | 1029 | 924 | 1029
MOSM2T | WFIE2- | 2024 | Change | 2.943 | 0 | OHL | 0.0133 | 0.1221 | 0.8005 | 1096 | 1029 | 924 | 1029
NECU1B | OHLL1- | 2024 | addition | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180
NECU1C | NOKY1- | 2024 | addition | 0 | 1.3 | Cable | 0.0084 | 0.0774 | 2.2771 | 261 | 261 | 261 | 261
WFIB2- | WFIE2- | 2024 | Change | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1096 | 1029 | 924 | 1029
BENB1B | GNSH1- | 2026 | Remove | 30.35 | 0.9 | Composite | 1.3071 | 6.1749 | 3.2285 | 241 | 241 | 241 | 241
BENB1B | KEOO1Q | 2026 | Addition | 20.25 | 0 | OHL | 0.5256 | 3.9095 | 1.2119 | 352 | 325 | 281 | 325
BRNX4- | CRYR4- | 2026 | Addition | 13.86 | 0 | OHL | 0.0178 | 0.2543 | 8.5869 | 2522 | 2397 | 2189 | 2397
BRNX4- | ECCL4A | 2026 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2522 | 2397 | 2189 | 2397
BRNX4- | ECCL4B | 2026 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2522 | 2397 | 2189 | 2397
BRNX4- | SMEA4Q | 2026 | Addition | 58.82 | 0 | OHL | 0.0774 | 1.1407 | 35.1217 | 2473 | 2349 | 2148 | 2349
BRNX4- | TORN4- | 2026 | Addition | 0 | 2.1 | Cable | 0.0005 | 0.014 | 46.7008 | 1040 | 900 | 900 | 900
BRNX4- | TORN4- | 2026 | Addition | 0 | 1.94 | Cable | 0.0005 | 0.013 | 43.1426 | 945 | 800 | 800 | 800
CAFA1Q | KEOO1- | 2026 | Change | 2.58 | 0 | OHL | 0.198 | 0.5682 | 0.1357 | 135 | 126 | 110 | 130
CHAP1- | HAKB1- | 2026 | Change | 14.72 | 0 | OHL | 1.1184 | 3.1888 | 0.7779 | 284 | 278 | 270 | 274
CLAU1- | MAHI1C | 2026 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 167 | 160 | 147 | 160
COAL1A | LEGO1Q | 2026 | Addition | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123
COAL1A | LEGO1R | 2026 | Addition | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123
CRYR4- | TORN4- | 2026 | Remove | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 935 | 785 | 785 | 785
DENN2- | LAMB2- | 2026 | Change | 31.991 | 0 | OHL | 0.1353 | 1.3066 | 8.8961 | 1372 | 1324 | 1228 | 1324
DENN2- | LAMB2T | 2026 | Change | 32.18 | 0 | OHL | 0.1361 | 1.3147 | 8.9474 | 1372 | 1324 | 1228 | 1324
DENN2- | LOAN2Z | 2026 | Remove | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2- | 2026 | Addition | 21.59 | 0 |  | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DEVM1- | SPAV1Q | 2026 | Change | 7.63 | 0 | OHL | 0.5726 | 1.7268 | 0.3878 | 167 | 160 | 148 | 160
DEVM1- | SPAV1R | 2026 | Change | 7.51 | 0 | OHL | 0.5636 | 1.699 | 0.3818 | 167 | 160 | 148 | 160
DUMF1- | TONG1Q | 2026 | Remove | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNF1Q | INKE1Q | 2026 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
DUNF1R | INKE1R | 2026 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
EAST1Q | GLLE1- | 2026 | Change | 1.5 | 0.3 | Composite | 0.1236 | 0.3498 | 0.4484 | 133 | 124 | 107 | 124
ECCL4A | TORN4- | 2026 | Remove | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | TORN4- | 2026 | Remove | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
EKIL3A | EKIL3B | 2026 | Addition | 0 | 0 | Series Reactor | 0.6667 | 61.6631 | 0 | 30 | 30 | 30 | 30
EUCH1- | LORG1- | 2026 | Addition | 3.5 | 0 | OHL | 0.2629 | 0.7701 | 0.1843 | 167 | 160 | 148 | 160
FASI1- | FASI1A | 2026 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 185
FASI1- | FASI1B | 2026 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 184
FASI1A | HAWI1D | 2026 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1A | JUNV1- | 2026 | Addition | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 132 | 123 | 106 | 123
FASI1B | HAWI1C | 2026 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1B | JUNV1A | 2026 | Addition | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191
GALA1- | HAWI1- | 2026 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1- | 2026 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1B | 2026 | Remove | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARE1S | WHTL1S | 2026 | Change | 1.68 | 0 | OHL | 0.1261 | 0.3772 | 0.086 | 167 | 160 | 148 | 160
GARE1T | WHTL1T | 2026 | Change | 1.67 | 0 | OHL | 0.1253 | 0.3749 | 0.0855 | 167 | 160 | 148 | 160
GLLE1- | KEOO1- | 2026 | Change | 7.68 | 0 | OHL | 0.1993 | 1.4827 | 0.4596 | 482 | 445 | 385 | 445
GLLE1- | KEOO1Q | 2026 | Addition | 10.68 | 0 | OHL | 0.2772 | 2.0619 | 0.6391 | 482 | 445 | 385 | 445
GLLE1- | TONG1- | 2026 | Addition | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 198 | 186 | 168 | 186
GLLE1- | TONG1- | 2026 | Change | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 198 | 186 | 168 | 186
GNSH1- | KEOO1Q | 2026 | Addition | 10.1 | 0.9 | Composite | 0.5506 | 2.226 | 2.0339 | 241 | 241 | 241 | 241
GNSH1- | TRSN1- | 2026 | Addition | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 149 | 160
GRNA1- | HAWI1- | 2026 | Remove | 55.35 | 0 | OHL | 5.0077 | 12.6881 | 2.7627 | 133 | 124 | 107 | 124
GRNA1- | JUNV1- | 2026 | Change | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA1- | JUNV1A | 2026 | Addition | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA4- | HAKB4B | 2026 | Change | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2370 | 2270 | 2270 | 2270
HAKB4- | MOFF4C | 2026 | Change | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2370 | 2270 | 2270 | 2270
HAWI1- | JUNV1- | 2026 | Remove | 50.34 | 0 | OHL | 4.5503 | 11.4999 | 2.5189 | 132 | 123 | 106 | 123
HOLM1T | KEOO1- | 2026 | Change | 10.9 | 0 | OHL | 0.2829 | 2.1044 | 0.6523 | 386 | 356 | 308 | 356
KINB2J | KINC2- | 2026 | Remove | 10.325 | 0.385 | Composite | 0.0467 | 0.4237 | 7.0632 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2026 | Remove | 10.71 | 0 | OHL | 0.0483 | 0.4363 | 2.9716 | 1090 | 1030 | 925 | 1030
KINB4J | KINC4A | 2026 | Addition | 10.5 | 0 | OHL | 0.0229 | 0.2213 | 5.8026 | 1590 | 1500 | 1350 | 1500
KINB4K | KINC4S | 2026 | Addition | 10.15 | 0 | OHL | 0.0222 | 0.2143 | 5.6016 | 1590 | 1500 | 1350 | 1500
KINC4B | KINC4S | 2026 | Addition | 0 | 0.35 | Cable | 0.0002 | 0.0047 | 3.8917 | 1590 | 1500 | 1350 | 1500
KNOK1- | MAHI1C | 2026 | Addition | 3 | 0 | OHL | 0.1594 | 0.6382 | 0.1637 | 242 | 232 | 216 | 232
LAMB2- | WIYH2- | 2026 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1372 | 1324 | 1228 | 1324
LAMB2T | WIYH2- | 2026 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1372 | 1324 | 1228 | 1324
LOAN2- | MOSM2L | 2026 | Change | 26.196 | 0.194 | Composite | 0.1186 | 1.0915 | 8.8674 | 1090 | 1030 | 925 | 1030
LOAN2- | WFIE2- | 2026 | Addition | 29.169 | 0.154 | Composite | 0.1319 | 1.2141 | 9.3165 | 1090 | 1030 | 925 | 1030
LOAN2Z | WFIE2- | 2026 | Remove | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
MOFF1- | SCOP1- | 2026 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
MOFF1- | SCOP1- | 2026 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
SMEA4Q | STHA4B | 2026 | Change | 75.76 | 0 | OHL | 0.1547 | 1.5403 | 43.1224 | 1995 | 1926 | 1787 | 1926
SMEA4Q | TORN4- | 2026 | Remove | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 2026 | Change | 61.77 | 0 | OHL | 0.1265 | 1.2657 | 34.9519 | 1995 | 1926 | 1787 | 1926
STHA4A | WISH4- | 2026 | Change | 11.6 | 0 | OHL | 0.0234 | 0.2267 | 6.7974 | 1995 | 1926 | 1787 | 1926
WHTB1S | WHTL1S | 2026 | Change | 2.05 | 0 | OHL | 0.1538 | 0.4602 | 0.105 | 167 | 160 | 148 | 160
WHTB1T | WHTL1T | 2026 | Change | 2.05 | 0 | OHL | 0.1538 | 0.4602 | 0.105 | 167 | 160 | 148 | 160
BONN2- | DENN2- | 2029 | Addition | 3.25 | 1 | Composite | 0.0152 | 0.1771 | 6.0833 | 1372 | 1324 | 1228 | 1324
BONN2- | NEAR2T | 2029 | Addition | 17 | 0 | OHL | 0.0739 | 0.7786 | 4.3296 | 1372 | 1324 | 1228 | 1324
BONN2A | DENN2- | 2029 | Remove | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 2029 | Remove | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BONN4- | DENN4- | 2029 | Addition | 3.25 | 0.75 | Composite | 0.0069 | 0.0754 | 18.43 | 1995 | 1926 | 1786 | 1926
BONN4- | WISH4- | 2029 | Addition | 40.36 | 0 | OHL | 0.083 | 0.8736 | 21.7471 | 1995 | 1926 | 1786 | 1926
BRNX4- | BRNX4A | 2029 | Addition | 0 | 0.25 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770
CHAP1- | DUMF1- | 2029 | Remove | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | GRNA1- | 2029 | Change | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 167 | 160 | 147 | 160
CHAP1- | GRNA1- | 2029 | Change | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 167 | 160 | 147 | 160
CHAP1- | OFOA1T | 2029 | Addition | 24.82 | 0.18 | Composite | 0.984 | 5.6173 | 1.5274 | 171 | 155 | 155 | 155
COCK4Q | ECCL4A | 2029 | Change | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1995 | 1926 | 1786 | 1926
COCK4R | ECCL4B | 2029 | Change | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1995 | 1926 | 1786 | 1926
CURR2- | GRMO2- | 2029 | Change | 42.18 | 0 | OHL | 0.1798 | 1.7435 | 11.6852 | 1372 | 1324 | 1228 | 1324
CURR2- | KINC2- | 2029 | Change | 57.14 | 0 | OHL | 0.2435 | 2.3619 | 15.8296 | 1372 | 1324 | 1228 | 1324
DUMF1- | OFOA1T | 2029 | Addition | 2.08 | 0 | OHL | 0.0822 | 0.4694 | 0.1069 | 229 | 212 | 183 | 212
ECCL1- | GALA1- | 2029 | Change | 30.14 | 0 | OHL | 1.6015 | 6.6324 | 1.5764 | 242 | 232 | 214 | 232
ECCL1- | GALA1- | 2029 | Change | 30.58 | 0 | OHL | 1.6249 | 6.7325 | 1.5989 | 242 | 232 | 214 | 232
EERH2- | NEAR2Q | 2029 | Remove | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EERH2- | NEAR2T | 2029 | Addition | 7.74 | 0 | OHL | 0.0332 | 0.3289 | 2.0967 | 1372 | 1266 | 1096 | 1266
ELVA4- | STHA4A | 2029 | Remove | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ELVN4- | ELVA4- | 2029 | Addition | 0.001 | 0 | OHL | 0 | 0 | 0 | 2210 | 2130 | 1980 | 2130
ELVN4- | GHPS4- | 2029 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
ELVN4- | GHPS4- | 2029 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
ELVN4- | STHA4A | 2029 | Addition | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
GBRN1- | NECU1C | 2029 | Addition | 8 | 0 | OHL | 0.6001 | 1.7617 | 0.4208 | 167 | 160 | 147 | 160
GRMO2- | KINC2- | 2029 | Change | 14.96 | 0 | OHL | 0.0638 | 0.6184 | 4.1444 | 1372 | 1324 | 1228 | 1324
NEAR2- | NEAR2T | 2029 | Addition | 7.6 | 0 | OHL | 0.0331 | 0.3481 | 1.9356 | 1372 | 1324 | 1228 | 1324
NEAR2- | WISH2- | 2029 | Change | 15.76 | 0 | OHL | 0.0685 | 0.7218 | 4.0138 | 1372 | 1324 | 1228 | 1324
NEAR2Q | WISH2- | 2029 | Remove | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
OFOA1T | OFOA1- | 2029 | Addition | 20 | 0 | OHL | 1.5025 | 4.4007 | 1.0533 | 167 | 160 | 147 | 160
SMEA4Q | STHA4B | 2029 | Remove | 75.76 | 0 | OHL | 0.1547 | 1.5403 | 43.1224 | 1995 | 1926 | 1787 | 1926
SMEA4Q | WISH4- | 2029 | Addition | 61.77 | 0 | OHL | 0.1265 | 1.2657 | 34.9519 | 1995 | 1926 | 1787 | 1926
STHA4B | WISH4- | 2029 | Addition | 13.99 | 0 | OHL | 0.0285 | 0.2854 | 7.9774 | 1995 | 1926 | 1787 | 1926

## B-2-2c
B.2.2c - NGET Circuit Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Autumn Rating (MVA) | Summer Rating (MVA) | Spring Rating (MVA)
BLYT21 | TYNE21 | 2021 | Change | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1310 | 1220 | 1310
BLYT21 | TYNE2A | 2021 | Change | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1310 | 1220 | 1310
BOTW41 | CHIL41 | 2021 | Addition | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 3820 | 3630 | 3320 | 3630
BOTW41 | FAWL41 | 2021 | Remove | 7.479 | 3.57 | Composite | 0.0102 | 0.1509 | 59.5766 | 1109 | 901 | 901 | 901
CHIL41 | FAWL41 | 2021 | Addition | 0 | 3.57 | Cable | 0.0018 | 0.0112 | 109.0992 | 900 | 700 | 700 | 900
CHIL41 | FAWL41 | 2021 | Addition | 0 | 3.57 | Cable | 0.0018 | 0.0112 | 109.0992 | 900 | 700 | 700 | 900
CHIL41 | LOVE41 | 2021 | Addition | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 3820 | 3630 | 3320 | 3630
FAWL41 | LOVE41 | 2021 | Remove | 22.379 | 3.885 | Composite | 0.0237 | 0.4115 | 74.7979 | 1109 | 901 | 901 | 901
HATL21 | HARM21 | 2021 | Change | 13.983 | 0 | OHL | 0.0472 | 0.5702 | 3.9648 | 1093 | 1031 | 925 | 1031
HATL21 | SALH21 | 2021 | Change | 7.794 | 0 | OHL | 0.0327 | 0.3353 | 2.0878 | 1382 | 1279 | 1157 | 1279
HATL21 | WBOL21 | 2021 | Remove | 49.164 | 0 | OHL | 0.1929 | 2.0384 | 13.6728 | 1093 | 1031 | 926 | 1031
HAWP21 | HATL21 | 2021 | Addition | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1090 | 1090 | 1090 | 1090
HAWP21 | OFFE21 | 2021 | Change | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1180 | 1120 | 1020 | 1120
OFFE21 | WBOL21 | 2021 | Change | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1180 | 1120 | 1020 | 1120
RAYL41 | TILB4A | 2021 | Change | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 3100 | 2914 | 2635 | 2945
SSHI21 | TYNE2A | 2021 | Change | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1360 | 1310 | 1220 | 1310
SSHI21 | WBOL21 | 2021 | Change | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1180 | 1120 | 1020 | 1120
TYNE21 | WBOL21 | 2021 | Change | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1180 | 1120 | 1020 | 1120
WBOL21 | HAWP21 | 2021 | Addition | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1180 | 1120 | 1020 | 1120
HINP41 | MELK41 | 2022 | Remove | 86.448 | 0 | OHL | 0.1573 | 1.72 | 50.0998 | 2009 | 1911 | 1746 | 1911
HINP41 | SAFO41 | 2022 | Addition | 24.54 | 8.15 | Composite | 0.0376 | 0.5627 | 203.1782 | 2009 | 1911 | 1746 | 1911
HINP41 | SHUR41 | 2022 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 3100 | 3050 | 2960 | 3050
HINP41 | TAUN41 | 2022 | Remove | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1980 | 2125
MELK41 | SAFO41 | 2022 | Addition | 86.94 | 8.15 | Composite | 0.12082 | 1.5237 | 232.9123 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA41 | 2022 | Change | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2550 | 2550 | 2550 | 2550
NORT41 | OSBA42 | 2022 | Change | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2009 | 2009 | 2009 | 2009
SHUR41 | SHUR41 | 2022 | Addition | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2000 | 2000 | 2000 | 2000
SHUR41 | TAUN41 | 2022 | Addition | 26.644 | 0 | OHL | 0.0485 | 0.5301 | 15.4408 | 2212 | 2125 | 1980 | 2125
SJOW21 | TOTT23 | 2022 | Remove | 0 | 16.368 | Cable | 0.0295 | 0.3601 | 177.9201 | 868 | 868 | 868 | 868
SJOW21 | TOTT24 | 2022 | Remove | 0 | 16.508 | Cable | 0.0297 | 0.3632 | 179.4419 | 868 | 868 | 868 | 868
HINP22 | BRWA2A | 2023 | Remove | 17.867 | 0.61 | Composite | 0.0827 | 0.7732 | 11.4779 | 767 | 620 | 620 | 620
HINP41 | SHUR41 | 2023 | Addition | 1 | 0 | OHL | 0.0018 | 0.0199 | 0.5795 | 3100 | 3050 | 2960 | 3050
HINP41 | TAUN42 | 2023 | Remove | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1980 | 2125
PURI4A | BRWA4A | 2023 | Addition | 4 | 0 | OHL | 0.0062 | 0.0767 | 2.4004 | 2030 | 1930 | 1770 | 1930
SHUR41 | PURI4A | 2023 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 3050 | 2960 | 3050
SHUR41 | TAUN42 | 2023 | Addition | 26.657 | 0 | OHL | 0.0485 | 0.5304 | 15.4483 | 2212 | 2125 | 1980 | 2125
BLYT21 | BLYT22 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT21 | BLYT22 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT21 | BLYT23 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT21 | BLYT23 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.5289 | 0 | 2217 | 2217 | 2217 | 2217
BLYT22 | TYNE2A | 2024 | Change | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1236 | 1176 | 1074 | 1176
BLYT23 | TYNE21 | 2024 | Change | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1236 | 1176 | 1074 | 1176
BRAI4A | BRFO41 | 2024 | Change | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3100 | 2914 | 2635 | 2945
BRAI4A | BULL41 | 2024 | Change | 12.343 | 0 | OHL | 0.0121 | 0.2133 | 8.2261 | 3100 | 2914 | 2635 | 2945
BRAI4B | PELH41 | 2024 | Change | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 3100 | 2914 | 2635 | 2945
BRAI4B | RAYL41 | 2024 | Change | 33.03 | 0 | OHL | 0.0325 | 0.5709 | 22.0036 | 3100 | 2914 | 2635 | 2945
BRLE41 | MELK41 | 2024 | Change | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1710 | 1607 | 1454 | 1625
BRLE41 | MELK41 | 2024 | Change | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8635 | 1710 | 1607 | 1454 | 1625
BULL41 | RAYL41 | 2024 | Change | 20.646 | 0 | OHL | 0.0203 | 0.3568 | 13.7565 | 3100 | 2914 | 2635 | 2945
CREB41 | THTO44 | 2024 | Change | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
ELST4A | SUND41 | 2024 | Change | 34.834 | 0 | OHL | 0.0556 | 0.6699 | 20.9635 | 2400 | 2256 | 2040 | 2280
ELST4B | SUND42 | 2024 | Change | 34.706 | 0 | OHL | 0.0554 | 0.6674 | 20.8867 | 1590 | 1500 | 1346 | 1500
GRAI41 | GRAW4A | 2024 | Addition | 9.634 | 0 | OHL | 0.0105 | 0.1676 | 6.3509 | 3102 | 2813 | 2633 | 2813
GRAI41 | GRAW4B | 2024 | Addition | 1.7 | 0.2445 | Composite | 0.0021 | 0.0324 | 3.4557 | 2003 | 2003 | 1939 | 2003
GRAI41 | KINO41 | 2024 | Remove | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3102 | 2813 | 2633 | 2813
GRAI41 | TILB41 | 2024 | Remove | 26.6424 | 2.0495 | Composite | 0.0302 | 0.4832 | 61.2333 | 2003 | 2003 | 1939 | 2003
GRAW41 | GRAW4A | 2024 | Addition | 0 | 0.2 | Cable | 0.0001 | 0.0025 | 2.5133 | 3102 | 2813 | 2633 | 2813
GRAW41 | GRAW4B | 2024 | Addition | 0 | 0.2 | Cable | 0.0001 | 0.0025 | 2.5133 | 3102 | 2813 | 2633 | 2813
GRAW4A | KINO41 | 2024 | Addition | 9.807 | 0.8 | parallel Composite | 0.0108 | 0.1732 | 17.4426 | 3102 | 2813 | 2633 | 2813
GRAW4B | TILB41 | 2024 | Addition | 24.9424 | 1.805 | Composite | 0.0283 | 0.4536 | 52.5445 | 2003 | 2003 | 1939 | 2003
HINP21 | BRWA2B | 2024 | Remove | 17.867 | 0.68 | Composite | 0.0828 | 0.7752 | 12.2388 | 762 | 619 | 619 | 619
HINP41 | MELK41 | 2024 | Remove | 86.439 | 0 | OHL | 0.1572 | 1.7198 | 50.0946 | 2009 | 1911 | 1746 | 1911
HINP41 | SEAB41 | 2024 | Addition | 53.385 | 8.15 | Composite | 0.0697 | 1.1063 | 220.9169 | 2009 | 1911 | 1746 | 1911
MELK41 | PURI4A | 2024 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 2009 | 1911 | 1746 | 1911
MELK41 | PURI4B | 2024 | Addition | 78.5 | 0 | OHL | 0.1223 | 1.5103 | 46.977 | 2009 | 1911 | 1746 | 1911
MELK41 | SAFO41 | 2024 | Remove | 86.94 | 8.15 | Composite | 0.12082 | 1.5237 | 232.9123 | 2009 | 1911 | 1746 | 1911
MELK41 | SEAB41 | 2024 | Remove | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MELK41 | SEAB4A | 2024 | Addition | 53.528 | 0 | OHL | 0.05975 | 0.9445 | 34.8716 | 2545 | 2421 | 2211 | 2421
PURI4B | BRWA4B | 2024 | Addition | 3.6 | 0.4 | Composite | 0.0058 | 0.0738 | 11.4004 | 300 | 300 | 300 | 300
SAFO41 | SEAB4A | 2024 | Addition | 28.845 | 0 | OHL | 0.0322 | 0.5436 | 17.7387 | 3190 | 3060 | 2850 | 3060
SEAB41 | SEAB4A | 2024 | Addition | 0.03 | 0 | OHL | 3.9e-05 | 0.000577 | 0.018069 | 2545 | 2421 | 2211 | 2421
SHUR41 | PURI4B | 2024 | Addition | 15 | 0 | OHL | 0.0234 | 0.2878 | 9.0015 | 3100 | 3050 | 2960 | 3050
THTO41 | THTO43 | 2024 | Addition | 0 | 0 | Series Reactor | 0.0016 | 2 | 0 | 2400 | 2400 | 2400 | 2400
THTO43 | THTO44 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.125 | 0 | 3100 | 3100 | 3100 | 3100
THTO43 | THTO44 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB42 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB42 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB43 | 2024 | Addition | 0 | 0 | Series Capacitor (Power Control Device) | 0 | -0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB41 | TILB43 | 2024 | Addition | 0 | 0 | Series Reactor(Power Control Device) | 0 | 0.3125 | 0 | 3100 | 3100 | 3100 | 3100
TILB42 | TILB4A | 2024 | Change | 0.0581 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TILB43 | TILB4B | 2024 | Change | 0.0589 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
BOLN41 | NINF41 | 2026 | Remove | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 2026 | Remove | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
GRAI41 | GRAW4A | 2026 | Change | 9.634 | 0 | OHL | 0.0085 | 0.1654 | 6.4875 | 3300 | 2970 | 2805 | 3135
GRAI41 | GRAW4B | 2026 | Change | 1.7 | 0.2445 | Composite | 0.0017 | 0.032 | 3.4799 | 3300 | 2970 | 2805 | 3135
GRAW4A | KINO41 | 2026 | Change | 9.807 | 0.8 | parallel Composite | 0.0088 | 0.171 | 17.5792 | 3300 | 2970 | 2805 | 3135
GRAW4B | TILB41 | 2026 | Change | 24.9424 | 1.805 | Composite | 0.0232 | 0.4481 | 52.8966 | 3300 | 2970 | 2805 | 3135
HAKB1- | HARK13 | 2026 | Change | 8.49 | 0 | OHL | 0.6448 | 1.8386 | 0.4485 | 284 | 274 | 254 | 274
HARK13 | JUNV1- | 2026 | Change | 12.135 | 0 | OHL | 0.9147 | 2.8202 | 0.6058 | 199 | 191 | 178 | 191
HARK13 | JUNV1A | 2026 | Addition | 12.135 | 0 | OHL | 0.9147 | 2.8202 | 0.6058 | 199 | 191 | 178 | 191
HURS21 | LITT2A | 2026 | Change | 5.164 | 2.613 | Composite | 0.0274 | 0.2841 | 14.8804 | 1298 | 1298 | 1200 | 1298
HURS21 | LITT2B | 2026 | Change | 5.14 | 2.659 | Composite | 0.0273 | 0.2842 | 15.1114 | 1298 | 1298 | 1200 | 1298
HURS21 | NEWX21 | 2026 | Change | 0 | 21.106 | Cable | 0.0304 | 0.5278 | 108.8888 | 1298 | 1298 | 1200 | 1298
HURS21 | NEWX21 | 2026 | Change | 0 | 21.864 | Cable | 0.0315 | 0.5467 | 112.7994 | 1298 | 1298 | 1200 | 1298
KINO41 | TILB41 | 2026 | Change | 15.4784 | 1.835 | Composite | 0.0149 | 0.2859 | 47.1231 | 3300 | 2970 | 2805 | 3135
LHOR4A | BOLN41 | 2026 | Addition | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935
LHOR4A | NINF41 | 2026 | Addition | 23.304 | 0 | OHL | 0.0253 | 0.4053 | 15.3623 | 3102 | 2935 | 2765 | 2935
LHOR4B | BOLN41 | 2026 | Addition | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935
LHOR4B | NINF41 | 2026 | Addition | 23.304 | 0 | OHL | 0.0253 | 0.4053 | 15.3623 | 3102 | 2935 | 2765 | 2935
NECT41 | KINL41 | 2026 | Addition | 2.7 | 0 | OHL | 0.0024 | 0.046 | 1.8212 | 2520 | 2520 | 2520 | 2520
NECT41 | WALP41 | 2026 | Addition | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NECT4A | WALP41 | 2026 | Remove | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3299 | 3078 | 3299
NECT4B | WALP41 | 2026 | Remove | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NEWX21 | WIMB21 | 2026 | Remove | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 779 | 779 | 779
NEWX21 | WIMB21 | 2026 | Remove | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 813 | 813 | 813
NEWX41 | BENR41 | 2026 | Addition | 0 | 4 | Cable | 0.0036 | 0.042 | 72 | 1298 | 1298 | 1200 | 1298
NEWX42 | WIMB41 | 2026 | Addition | 0 | 12 | Cable | 0.0108 | 0.126 | 216 | 1298 | 1298 | 1200 | 1298
WALP41 | KINL41 | 2026 | Addition | 44.319 | 0 | OHL | 0.0393 | 0.7609 | 29.7952 | 2520 | 2520 | 2520 | 2520
WIMB41 | BENR41 | 2026 | Addition | 0 | 8 | Cable | 0.0072 | 0.084 | 144 | 1298 | 1298 | 1200 | 1298
BRAI4A | BRFO41 | 2029 | Addition | 49.529 | 0 | OHL | 0.046 | 0.853 | 33.1401 | 3100 | 2914 | 2635 | 2945
BRAI4A | BRFO41 | 2029 | Remove | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3100 | 2914 | 2635 | 2945
BRAI4B | BRFO41 | 2029 | Addition | 49.529 | 0 | OHL | 0.0461 | 0.8531 | 33.1365 | 3100 | 2914 | 2635 | 2945
BRAI4B | PELH41 | 2029 | Remove | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 3100 | 2914 | 2635 | 2945
BRFO41 | PELH41 | 2029 | Addition | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3273 | 3100 | 3100 | 3820 | 3100
BRFO41 | PELH41 | 2029 | Change | 69.301 | 0 | OHL | 0.0656 | 1.1949 | 46.3241 | 3102 | 2935 | 2765 | 2935
CANT41 | SELL4A | 2029 | Change | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3100 | 2914 | 2635 | 2945
CANT41 | SELL4B | 2029 | Change | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3100 | 2914 | 2635 | 2945
DUNG41 | SELL4E | 2029 | Change | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3100 | 2914 | 2635 | 2945
DUNG41 | SELL4F | 2029 | Change | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3100 | 2914 | 2635 | 2945
HAWP21 | NORT21 | 2029 | Remove | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 801 | 720 | 801
KNAR21 | MONF21 | 2029 | Remove | 38.531 | 0.141 | Composite | 0.3393 | 1.6165 | 11.7825 | 551 | 512 | 442 | 512
KNAR21 | POPP21 | 2029 | Remove | 49.192 | 0 | OHL | 0.3318 | 2.3014 | 12.3127 | 551 | 512 | 442 | 512
KNAR21 | TADT2A | 2029 | Addition | 25 | 0 | OHL | 0.1969 | 1.0483 | 6.8757 | 551 | 512 | 442 | 512
KNAR21 | TADT2B | 2029 | Addition | 25 | 0 | OHL | 0.1969 | 1.0483 | 6.8757 | 551 | 512 | 442 | 512
MONF21 | TADT2A | 2029 | Addition | 13.531 | 0.141 | Composite | 0.05 | 0.526 | 5.229 | 2200 | 2200 | 2200 | 2200
MONF22 | POPP21 | 2029 | Remove | 37.84 | 0 | OHL | 0.2776 | 1.8247 | 9.1701 | 682 | 629 | 538 | 629
MONF22 | TADT2B | 2029 | Addition | 13.531 | 0 | OHL | 0.0497 | 0.5232 | 4.0291 | 2200 | 2200 | 2200 | 2200
NORT41 | HAWP41 | 2029 | Addition | 30.157 | 0 | OHL | 0.0327 | 0.5245 | 19.8799 | 2780 | 2780 | 2780 | 2780
NORT41 | OSBA41 | 2029 | Remove | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2550 | 2550 | 2550 | 2550
NORT41 | OSBA42 | 2029 | Remove | 83.839 | 0 | OHL | 0.1097 | 1.5842 | 51.2941 | 2009 | 1911 | 1746 | 1911
OBST4A | NORT41 | 2029 | Addition | 77.639 | 0 | OHL | 0.1 | 1.4648 | 47.5893 | 2550 | 2550 | 2550 | 2550
OBST4A | POPP4B | 2029 | Addition | 6.2 | 0 | OHL | 0.0054 | 0.1065 | 4.175 | 2810 | 2810 | 2810 | 2810
OBST4B | NORT41 | 2029 | Addition | 77.639 | 0 | OHL | 0.1 | 1.4648 | 47.5893 | 2009 | 1911 | 1746 | 1911
OBST4B | POPP4A | 2029 | Addition | 6.2 | 0 | OHL | 0.0054 | 0.1065 | 4.175 | 2810 | 2810 | 2810 | 2810
OSBA41 | OBST4A | 2029 | Addition | 6.2 | 0 | OHL | 0.0113 | 0.1234 | 3.5932 | 2550 | 2550 | 2550 | 2550
OSBA42 | OBST4B | 2029 | Addition | 6.2 | 0 | OHL | 0.0113 | 0.1234 | 3.5932 | 2009 | 1911 | 1746 | 1911
TADT2A | POPP21 | 2029 | Addition | 24.192 | 0 | OHL | 0.0888 | 0.9354 | 7.2035 | 2200 | 2200 | 2200 | 2200
TADT2B | POPP21 | 2029 | Addition | 24.192 | 0 | OHL | 0.0888 | 0.9354 | 7.2035 | 2200 | 2200 | 2200 | 2200

## B-2-2d
B.2.2d - OFTO Circuit Changes 2021/22 to 2029/30
Wind Farm | Node 1 | Node 2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Interconnection Type | Rated DC Voltage (kV) | Rated AC Voltage (kV) | Rating (MVA)
Firth of Forth 1 Wind Farm | FOFO21 | FOFW21 | 2021 | Addition | 0 | 76 | Cable | TBC | TBC | TBC | AC | N/A | 275 | 400
| FOFO21 | FOFW22 | 2021 | Addition | 0 | 74 | Cable | TBC | TBC | TBC | AC | N/A | 275 | 400
| TEAL21 | FOFO21 | 2021 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| TEAL21 | FOFO21 | 2021 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Hornsea 1 Offshore Wind Farm | HOWA21 | HOWR2A | 2021 | Addition | 0 | 104.703 | Cable | 0.6809 | 3.2601 | 291.07 | AC | N/A | 220 | 1328
| HOWR2A | HOWW23 | 2021 | Addition | 0 | 85 | Cable | 0.63223 | 2.1074 | 224.8866 | AC | N/A | 220 | 380
| HOWW22 | HOWW23 | 2021 | Addition | 0 | 13.9 | Cable | 0.17806 | 0.34463 | 39.1004 | AC | N/A | 220 | 364
Moray East offshore Wind Farm | MOWE21 | MORF21 | 2021 | Addition | 0 | 90.69 | Cable | 0.632 | 2.405 | 284.21 | AC | N/A | 220 | 312
| MOWE22 | MORF22 | 2021 | Addition | 0 | 97.8 | Cable | 0.632 | 2.405 | 304.75 | AC | N/A | 220 | 312
| MOWE23 | MORF23 | 2021 | Addition | 0 | 91.48 | Cable | 0.632 | 2.405 | 286.49 | AC | N/A | 220 | 312
| NEDE21 | MORF21 | 2021 | Addition | 0 | 0.06 | Cable | 0 | 0.001 | 0.27 | AC | N/A | 275 | 398
| NEDE21 | MORF22 | 2021 | Addition | 0 | 0.1 | Cable | 0 | 0.002 | 0.42 | AC | N/A | 275 | 398
| NEDE21 | MORF23 | 2021 | Addition | 0 | 0.15 | Cable | 0.001 | 0.003 | 0.67 | AC | N/A | 275 | 398
Triton Knoll Offshore Wind Farm | TKNO21 | TKNE21 | 2021 | Addition | 0 | 107.8 | Cable | 0.57 | 3.15 | 313 | AC | N/A | 220 | 427
Inch Cape Offshore Wind Farm | INCW21 | INCO21 | 2022 | Addition | 0 | 85.5 | Cable | 0.0045 | 0.0187 | 247 | AC | N/A | 220 | 550
| INCW22 | INCO22 | 2022 | Addition | 0 | 85.5 | Cable | 0.0045 | 0.0187 | 247 | AC | N/A | 220 | 550
| INCO21 | COCK21 | 2022 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| INCO22 | COCK21 | 2022 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
Neart Na Gaoithe Offshore Wind Farm | NNGW21 | NNGO21 | 2022 | Addition | 0 | 51.021 | Cable | 0.318 | 1.329 | 119.6799 | AC | N/A | 220 | 230
| NNGW22 | NNGO22 | 2022 | Addition | 0 | 50.783 | Cable | 0.318 | 1.329 | 119.6799 | AC | N/A | 220 | 230
| NNGO41 | CRYA41 | 2022 | Addition | 0 | 0.289 | Cable | 0.0224 | 0.0258 | 0.0681 | AC | N/A | 400 | 400
| NNGO42 | CRYB41 | 2022 | Addition | 0 | 0.394 | Cable | 0.0306 | 0.0351 | 0.0928 | AC | N/A | 400 | 400
Dogger bank 1 offshore Wind Farm | Dogger bank 1A offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | 0 | 8 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 174
| Dogger bank 1A offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | 0 | 8 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 174
| Dogger bank 1B offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | 0 | 8 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 174
| Dogger bank 1B offshore 220kV | Dogger bank offshore 220kV | 2024 | Addition | 0 | 8 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 174
| Dogger bank offshore 320kV | Dogger bank onshore 320kV | 2024 | Addition | 0 | 245 | Cable | TBC | TBC | TBC | HVDC | 320 | TBC | TBC
| Dogger bank offshore 320kV | Dogger bank onshore 320kV | 2024 | Addition | 0 | 245 | Cable | TBC | TBC | TBC | HVDC | 320 | TBC | TBC
| Dogger bank onshore 400kV | CREB41 | 2024 | Addition | 0 | 8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Dogger bank onshore 400kV | CREB41 | 2024 | Addition | 0 | 8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Doggerbank 4 Offshore wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2024 | Addition | 0 | 6 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 252
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2024 | Addition | 0 | 6 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 252
| Doggerbank 4 Offshore | Doggerbank 4 Onshore | 2024 | Addition | 0 | 187 | Cable | TBC | TBC | TBC | HVDC | 320 | TBC | 1031
| Doggerbank 4 Offshore | Doggerbank 4 Onshore | 2024 | Addition | 0 | 187 | Cable | TBC | TBC | TBC | HVDC | 320 | TBC | 1031
| Doggerbank 4 Onshore 400kV | CREB41 | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | A/C | N/A | 400 | TBC
| Doggerbank 4 Onshore 400kV | CREB41 | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | A/C | N/A | 400 | TBC
East Anglia 3 Offshore Wind Farm | East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| East Anglia Offshore 220kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| East Anglia Offshore | East Anglia Onshore | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | HVDC | 320 | TBC | TBC
| East Anglia Offshore | East Anglia Onshore | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | HVDC | 320 | TBC | TBC
| East Anglia Onshore | BRFO41 | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | TBC
Firth of Forth 1 Wind Farm | TEAL21 | FOFO21 | 2024 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| FOFO21 | FOFW23 | 2024 | Addition | 0 | 87 | Cable | TBC | TBC | TBC | AC | N/A | 275 | 400
Hornsea 2 Offshore Wind Farm | Hornsea 2A Offshore | Hornsea 2A Reactve Comp Station | 2024 | Addition | 0 | 62.2 | Cable | 0.43409 | 1.5443 | 170.9198 | A/C | N/A | 220 | TBC
| Hornsea 2A Reactve Comp Station | Hornsea 2 Onshore | 2024 | Addition | 0 | 103.4 | TBC | 0.60012 | 2.4573 | 348.0374 | A/C | N/A | 220 | TBC
| Hornsea 2B Offshore | Hornsea 2B Reactve Comp Station | 2024 | Addition | 0 | 60.2 | Cable | 0.42012 | 1.4946 | 165.4277 | A/C | N/A | 220 | TBC
| Hornsea 2B Reactve Comp Station | Hornsea 2 Onshore | 2024 | Addition | 0 | 103.7 | TBC | 0.60235 | 2.4648 | 348.9223 | A/C | N/A | 220 | TBC
| Hornsea 2C Offshore | Hornsea 2C Reactve Comp Station | 2024 | Addition | 0 | 61.6 | Cable | 0.42992 | 1.5294 | 169.2655 | A/C | N/A | 220 | TBC
| Hornsea 2C Reactve Comp Station | Hornsea 2 Onshore | 2024 | Addition | 0 | 103.55 | TBC | 0.60123 | 2.4611 | 348.4798 | A/C | N/A | 220 | TBC
| Hornsea 2A Offshore | Hornsea 2B Offshore | 2024 | Addition | 0 | 12 | Cable | TBC | TBC | TBC | A/C | N/A | 220 | TBC
| Hornsea 2B Offshore | Hornsea 2C Offshore | 2024 | Addition | 0 | 12 | Cable | TBC | TBC | TBC | A/C | N/A | 220 | TBC
| Hornsea 2 Onshore | KILL41 | 2024 | Addition | 0 | 0.36 | Cable | 0.0002 | 0.003 | 4.23 | A/C | N/A | 400 | 935
| Hornsea 2 Onshore | KILL41 | 2024 | Addition | 0 | 0.36 | Cable | 0.0002 | 0.003 | 4.23 | A/C | N/A | 400 | 935
Hornsea 3 Offshore Wind Farm | Hornsea 3A-1 Offshore 500kV | Hornsea 3A-1 Onshore 500kV | 2024 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±400 | 500 | 750
| Hornsea 3A Onshore 400kV | NORM41 | 2024 | Addition | 0 | 1.8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | 1596
Moray West Offshore Wind Farm | Moray West Offshore 220kV | Moray West Onshore 220kV | 2024 | Addition | 0 | 72 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Moray West Offshore 220kV | Moray West Onshore 220kV | 2024 | Addition | 0 | 72 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Moray West Onshore 220kV | BLHI41 | 2024 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Moray West Onshore 220kV | BLHI41 | 2024 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Moray West Offshore P1 66kV | Moray West Offshore P2 66kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 66 | TBC
Sofia Offshore Offshore Wind Farm | Sofia offshore TBC | Sofia onshore TBC | 2024 | Addition | 0 | 237 | Cable | TBC | TBC | TBC | HVDC | 320 | TBC
| Sofia onshore 400kV | LACK41 | 2024 | Addition | 0 | 2 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Dogger Bank 4B Offshore Wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2026 | Addition | 0 | 6 | Cable | TBC | TBC | TBC | A/C | N/A | 220 | 252
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 220kV | 2026 | Addition | 0 | 6 | Cable | TBC | TBC | TBC | A/C | N/A | 220 | 252
East Anglia 6A Offshore Wind Farm | East Anglia 6A Offshore-2 | East Anglia 6A Onshore-1 | 2026 | Addition | 0 | 100 | Cable | TBC | TBC | TBC | HVDC | ±320 | 400 | 900
| East Anglia 6A Offshore-2 | East Anglia 6A Onshore-1 | 2026 | Addition | 0 | 100 | Cable | TBC | TBC | TBC | HVDC | ±320 | 400 | 900
| East Anglia 6A Onshore-1 | NECT41 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
East Anglia 6B Offshore Wind Farm | East Anglia 6B Offshore-2 | East Anglia 6B Onshore-1 | 2026 | Addition | 0 | 100 | Cable | TBC | TBC | TBC | HVDC | ±320 | 400 | 900
| East Anglia 6B Offshore-2 | East Anglia 6B Onshore-1 | 2026 | Addition | 0 | 100 | Cable | TBC | TBC | TBC | HVDC | ±320 | 400 | 900
| East Anglia 6B Onshore-1 | NECT41 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
Firth of Forth 2A Offshore Wind Farm | Offshore 66KV-1 | Offshore 66KV-2 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 66 | N/A
| Offshore 66KV-2 | Offshore 66KV-3 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 66 | N/A
| Offshore 275kV-1 | Onshore 275kV-1 | 2026 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | N/A
| Offshore 275kV-2 | Onshore 275kV-1 | 2026 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | N/A
| Offshore 275kV-3 | Onshore 275kV-1 | 2026 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | N/A
| Onshore 400kV-1 | BRNX41 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
| Onshore 400kV-1 | BRNX41 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
| Hornsea 3A-2 Offshore 500kV | Hornsea 3A-2 Onshore 500kV | 2026 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±400 | 500 | 750
| Hornsea 3B-1 Offshore 500kV | Hornsea 3B-1 Onshore 500kV | 2026 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±400 | 500 | 750
| Hornsea 3B Onshore 400kV | NORM41 | 2026 | Addition | 0 | 1.8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | 1596
Sheringham and Dudgeon Extension Wind Farm | Offshore 220kV-1 | Onshore 220kV-1 | 2026 | Addition | 0 | 82 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Offshore 220kV-2 | Onshore 220kV-2 | 2026 | Addition | 0 | 82 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 400kV-1 | NORM41 | 2026 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 400kV-2 | NORM41 | 2026 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Codling Offshore Wind Farm | Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| Codling Offshore 220kV | Codling Offshore 220kV | 2029 | Addition | 0 | 97 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 655
| CODL21 | CODL22 | 2029 | Addition | 0 | 22 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 1040
| CODL21 | CODL22 | 2029 | Addition | 0 | 22 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 1040
| CODL21 | CODL22 | 2029 | Addition | 0 | 22 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 1040
| CODL21 | CODL22 | 2029 | Addition | 0 | 22 | Cable | TBC | TBC | TBC | AC | N/A | 220 | 1040
Dogger Bank 2 Offshore Wind Farm | Offshore-2 | Onshore-1 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | HVDC | ±300 | TBC | 1500
| Onshore 400kV | LACK41 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
EA One North Farm | EA1N Offshore 220kV-1 | EA1N Onshore 220kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| EA1N Offshore 220kV-2 | EA1N Onshore 220kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| EA1N Onshore 400kV | LEIS41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | TBC
East Anglia 4A Wind Farm | East Anglia 4A Offshore-2 | East Anglia 4A Onshore-1 | 2029 | Addition | 0 | 134 | Cable | TBC | TBC | TBC | HVDC | ±320 | TBC | TBC
| East Anglia 4A Offshore-2 | East Anglia 4A Onshore-1 | 2029 | Addition | 0 | 134 | Cable | TBC | TBC | TBC | HVDC | ±320 | TBC | TBC
| East Anglia 4A 400kV | NECT41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | TBC
East Anglia 5A Wind Farm | East Anglia 5A Offshore-2 | East Anglia 5A Onshore-1 | 2029 | Addition | 0 | 134 | Cable | TBC | TBC | TBC | HVDC | ±320 | TBC | TBC
| East Anglia 5A Offshore-2 | East Anglia 5A Onshore-1 | 2029 | Addition | 0 | 134 | Cable | TBC | TBC | TBC | HVDC | ±320 | TBC | TBC
| East Anglia 5A 400kV | NECT41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | TBC
Firth of Forth 2B Offshore Wind Farm | Offshore 66KV-4 | Offshore 66KV-5 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 66 | N/A
| Offshore 66KV-5 | Offshore 66KV-6 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 66 | N/A
| Offshore 275kV-4 | Onshore 275kV-2 | 2029 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | N/A
| Offshore 275kV-5 | Onshore 275kV-2 | 2029 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | N/A
| Offshore 275kV-6 | Onshore 275kV-2 | 2029 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | N/A
| Onshore 400kV-2 | BRNX41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
| Onshore 400kV-2 | BRNX41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | N/A
Hornsea 4 WinfdFarm | Offshore 275kV-1 | Reactive Platform-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 275kV-2 | Reactive Platform-2 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 275kV-3 | Reactive Platform-3 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Reactive Platform-1 | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Reactive Platform-2 | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Reactive Platform-3 | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 400kV | CREB41 | 2029 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Offshore 275kV-4 | Reactive Platform-4 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 275kV-5 | Reactive Platform-5 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Reactive Platform-4 | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Reactive Platform-5 | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 400kV | CREB41 | 2029 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Racebank Extension Wind Farm | Offshore Platform 220kV-1 | Onshore 220kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Offshore Platform 220kV-2 | Onshore 220kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 400 kV-1 | Mablethorpe 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 400 kV-2 | Mablethorpe 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 400 | TBC
Hornsea 3 Offshore Wind Farm | Hornsea 3B-2 Offshore 500kV | Hornsea 3B-2 Onshore 500kV | 2029 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±400 | 500 | 750
Thanet Extension Offshore Wind Farm | Offshore-1 | Onshore-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | TBC | TBC
| Offshore-1 | Onshore-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | TBC | TBC
| Onshore 400kV | RICH41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | TBC | TBC
| Onshore 400kV | RICH41 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | TBC | TBC
West of Orkney Offshore Wind Farm | West of Orkney Offshore 275kV | West of Orkney Offshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| West of Orkney Offshore 275kV | West of Orkney Offshore 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| West of Orkney Offshore 275kV | Dounreay 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC
| West of Orkney Offshore 275kV | Dounreay 275kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | AC | N/A | 275 | TBC

## B-3-1a
B.3.1a - SHE Transmission Transformers for 2020/21
Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
ACHR1R | ACHR3- | 0.36 | 18 | 0 | 90
AIGA1Q | AIGA5- | 1.76 | 44.89 | 0 | 22.5
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.615 | 17.82 | -0.026 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU2J | BEAU1J | 0.6786 | 12.2312 | -0.0009 | 120
BEAU2J | BEAU1J | 0.6786 | 12.1644 | -0.0009 | 120
BEAU2K | BEAU1K | 0.6786 | 12.1895 | -0.0009 | 120
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.0004 | 1200
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.0004 | 1200
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 0.1486 | 5.3035 | -0.0006 | 360
BLHI2K | BLHI1K | 0.1506 | 5.3034 | -0.0006 | 360
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.0005 | 1200
BLHI4- | BLHI2L | 0.0252 | 1.1997 | -0.0005 | 1200
BLHI4- | BLHI2M | 0.0253 | 1.2081 | -0.0005 | 1200
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRCW2J | BRCW3- | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 0.42 | 20 | 0 | 120
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 39 | 0 | 30
BROR1- | BROR3- | 0.763 | 25.144 | 0 | 45
BUMU1Q | BUMU3- | 0.366 | 25.37 | -0.034 | 90
BUMU1R | BUMU3- | 0.376 | 25.42 | -0.035 | 90
CAAD1Q | CAAD3- | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1Q | CAAD3J | 0.5 | 25 | 0 | 90
CAAD1R | CAAD3- | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1R | CAAD3J | 0.5 | 25 | 0 | 90
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120
CASS1Q | CASS3- | 1.518 | 39.871 | 0 | 30
CEAN1Q | CEAN5- | 1.182 | 36.714 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAC1Q | CLAC5J | 0.75 | 25 | 0 | 60
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
CLUN1Q | CLUN5J | 0.71 | 19.53 | 0 | 60
CLUN1R | CLUN5K | 0.71 | 19.55 | 0 | 60
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90
CONN2J | CONN1J | 0.143 | 5.3036 | -0.0006 | 360
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
CORI1J | CORI3J | 8.3 | 27.5 | 0 | 60
COUA1Q | COUA3- | 0.2143 | 25.0741 | -0.0067 | 120
COUA1R | COUA3- | 0.2151 | 25.1241 | -0.0092 | 120
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
CRSS1J | COUW31 | 0.3629 | 18.0297 | -0.0123 | 90
CRSS1J | CRSS1Q | 0.0582 | 2.145 | 0 | 240
CRSS1K | CRSS1R | 0.0582 | 2.1492 | 0 | 240
CRSS2A | CRSS1J | 0.2466 | 9.0008 | -0.0005 | 240
CRSS2B | CRSS1K | 0.2459 | 9.0175 | -0.0005 | 240
CULL1Q | CULL5- | 1.46 | 37.6 | 0 | 25
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DEAN1Q | DEAN5- | 1.01 | 25.1 | 0 | 40
DORE11 | DORE31 | 0.21 | 9.89 | 0 | 120
DORE12 | DORE32 | 0.21 | 9.89 | 0 | 120
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DOUN2- | DOUN1- | 0.2112 | 7.7054 | -0.0005 | 240
DOUN2- | DOUN1- | 0.2237 | 7.9135 | -0.0006 | 240
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.617 | 17.65 | -0.029 | 60
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120
DUNO1Q | DUNO3- | 2 | 24.49 | 0 | 45
DUNO1R | DUNO3- | 2 | 24.5801 | 0 | 45
DYCE1Q | DYCE3- | 0.4015 | 24.819 | -0.0194 | 90
DYCE1R | DYCE3- | 0.3974 | 24.7301 | -0.0007 | 90
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1J | ERRO1A | 0.04 | 1.942 | 0 | 240
ERRO1J | ERRO5L | 0.72 | 26.6 | 0 | 60
ERRO1K | ERRO1B | 0.04 | 1.942 | 0 | 240
ERRO1K | ERRO5J | 0.72 | 26.6 | 0 | 60
ERRO1T | ERRO1J | 0.068 | 3.73 | 0 | 150
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FARI2J | FARI1J | 0.4989 | 8.2933 | -0.038 | 120
FARI2K | FARI1K | 0.4955 | 8.3186 | -0.038 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1Q | FAUG3- | 2.23 | 64.33 | 0 | 15
FAUG2J | FAUG1- | 0.2606 | 7.7039 | -0.0005 | 240
FAUG2K | FAUG1- | 0.2629 | 7.7038 | -0.0005 | 240
FAUG4- | FAUG1- | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 0.3185 | 8.4523 | -0.013 | 240
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FETT2R | FETT1- | 0.217 | 4.2737 | -0.0006 | 240
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD1B | 0.11 | 4.11 | 0 | 150
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FINL1Q | FINL5- | 0.96 | 27.11 | 0 | 45
FRAS1Q | FRAS3- | 0.642 | 26.904 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.904 | 0 | 45
FWIL1Q | FWIL3- | 0.499 | 24.995 | 0 | 120
FWIL1R | FWIL3- | 0.499 | 24.995 | 0 | 120
FYRI2J | FYRI1J | 0.0967 | 3.8863 | -0.0006 | 480
FYRI2K | FYRI1K | 0.0971 | 3.8738 | -0.0006 | 480
GLDO1G | GLDO8- | 0.206 | 10.681 | 0 | 120
GLEN1Q | GLEN5- | 0.55 | 21.94 | 0 | 70
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90
INGA1Q | INGA5- | 1.287 | 25 | 0 | 30
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
INVB2A | INVR1- | 0.2217 | 4.3026 | -0.0071 | 240
INVB2B | INVR1- | 0.2164 | 4.257 | -0.0066 | 240
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEIT3A | 0.499 | 24.995 | 0 | 90
KEIT2Q | KEIT1- | 0.2735 | 8.6123 | -0.0007 | 240
KEIT2R | KEIT1- | 0.3328 | 8.9105 | -0.0389 | 240
KIIN1- | KIIN3- | 0.772 | 24.877 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.521 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.78 | 0 | 45
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT1- | 0.3771 | 10.1929 | -0.018 | 240
KINT2K | KINT1- | 0.3751 | 10.2314 | -0.0147 | 240
KINT2K | KINT1- | 0.6786 | 12.1477 | -0.0009 | 120
KIOR1Q | KIOR5- | 1.78 | 45.42 | 0 | 22.5
KNOC2J | KNOC1J | 0.2216 | 4.311 | -0.0076 | 240
KNOC2K | KNOC1J | 0.2205 | 4.3319 | -0.0006 | 240
LAIR1Q | LAIR3- | 0.425 | 24.674 | 0 | 90
LOCB2J | LOCB1J | 0.2181 | 8.1262 | -0.0007 | 240
LOCB2K | LOCB1K | 0.22 | 8.197 | -0.0007 | 240
LOCH1- | LOCH5J | 1.93 | 38.52 | 0 | 25
LOCH1- | LOCH5K | 1.93 | 38.2 | 0 | 25
LUIC1Q | LUIC5J | 0.763 | 37.548 | 0 | 45
LUIC1R | LUIC5K | 0.7668 | 37.548 | 0 | 45
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.429 | 25.741 | 0 | 90
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MELG4J | MELG1J | 0.108 | 3.957 | -0.0007 | 480
MELG4K | MELG1K | 0.106 | 3.957 | -0.0007 | 480
MILC1R | MILC3- | 0.78 | 24.83 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.13 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MOSS1Q | MOSS5- | 1.192 | 36.847 | 0 | 30
MOSS1R | MOSS5- | 1.2267 | 36.913 | 0 | 30
MYBS1S | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1S | MYBS3M | 0.2645 | 24.6069 | -0.024 | 120
MYBS1T | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3N | 0.2578 | 24.757 | -0.024 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6 | 0 | 60
NANT1Q | NANT5- | 1.47 | 56.67 | 0 | 30
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
ORRI1R | ORRI5- | 2.17 | 48.75 | 0 | 20
PEHE1- | PEHS5- | 2.58 | 42.33 | 0 | 15
PEHE2- | PEHE1- | 0.2649 | 9.2254 | -0.0005 | 240
PEHE2Q | PEHE1- | 0.4842 | 9.9549 | -0.0178 | 240
PEHE2R | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.4 | 0 | 45
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PERS2Q | PERS1Q | 0.3363 | 8.9062 | -0.0412 | 240
PERS2R | PERS1R | 0.3341 | 8.8645 | -0.0419 | 240
PORA1Q | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 1.803 | 29.812 | 0 | 30
QUOI1- | QUOI5- | 1.34 | 33.13 | 0 | 30
RANN1Q | RANN3Q | 0.43 | 24.66 | 0 | 90
RANN1R | RANN3Q | 0.43 | 24.66 | 0 | 90
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
SFEG1Q | SFEG5- | 2.28 | 93.87 | 0 | 30
SFEG1R | SFEG5- | 2.28 | 92.8 | 0 | 30
SFEM1Q | SFEM5J | 1.8 | 41.19 | 0 | 27
SFEM1R | SFEM5K | 1.8 | 41.19 | 0 | 27
SFIL1Q | SFIL5- | 1.99 | 39.48 | 0 | 25
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
SHIN1- | SHIN5- | 1.4823 | 80.16 | 0 | 40
SLOY1L | SLOY5L | 0.79 | 23.08 | 0 | 50
SLOY1M | SLOY5M | 0.79 | 22.9 | 0 | 50
SLOY1N | SLOY5N | 0.79 | 22.98 | 0 | 50
SLOY1P | SLOY5P | 0.8 | 23.2 | 0 | 50
SPIT2J | SPIT1J | 0.218 | 8.185 | -0.0007 | 240
SPIT2J | SPIT1J | 0.218 | 8.23 | -0.0007 | 240
SPIT2K | SPIT1K | 0.131 | 4.99 | -0.0006 | 360
SPIT2K | SPIT1M | 0.129 | 4.99 | -0.0006 | 360
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
STRL1- | STRL3P | 0.2 | 17.74 | -0.01 | 120
STRL1- | STRL3Q | 0.2 | 17.65 | -0.01 | 120
STRL1- | STRL3R | 0.2 | 17.67 | -0.01 | 120
STRW12 | STRW31 | 0.05 | 18 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.53 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.787 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.787 | 0 | 90
TEAL2J | TEAL1- | 0.3619 | 10.1602 | -0.0118 | 180
TEAL2K | TEAL1- | 0.2564 | 11.7305 | -0.0131 | 180
TEAL2K | TEAL1- | 0.5506 | 11.8761 | -0.0008 | 180
THUS1J | THUS3- | 0.2621 | 24.6736 | -0.022 | 120
THUS1K | THUS3- | 0.2614 | 24.7403 | -0.02 | 120
THUS2J | THUS1J | 0.0985 | 3.9363 | -0.0005 | 480
THUS2K | THUS1K | 0.1 | 3.9362 | -0.0006 | 480
TOMT2J | TOMT1J | 0.098 | 3.905 | -0.0006 | 480
TOMT2K | TOMT1K | 0.098 | 3.905 | -0.0006 | 480
TUMB1Q | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMB1R | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMM2J | TUMM1J | 0.259 | 7.7457 | -0.0005 | 240
TUMM2K | TUMM1K | 0.2595 | 7.829 | -0.0005 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.24 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
B.3.1b - SPT Transformers for 2020/21
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3C | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3A | 0.5214 | 27.5617 | -0.1031 | 120
CLYM2- | CLYM3A | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3B | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1- | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1A | 0.1216 | 9.6242 | -0.0793 | 240
COAL4- | COAL1A | 0.0914 | 6.4382 | -0.0751 | 360
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1718 | 8.665 | -0.0204 | 120
COYL2- | COYL1- | 0.3396 | 12.8288 | -0.2375 | 120
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR1- | CRYR31 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR1- | CRYR32 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR1B | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1A | 0.1079 | 8.5702 | -0.0341 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 160
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 160
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3A | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3B | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1S | DUNB3B | 0.4121 | 28.9304 | -0.0087 | 90
DUNB1T | DUNB3B | 0.3569 | 28.82 | -0.0089 | 90
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EKIL2S | EKIL3- | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3- | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3A | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3B | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 0.5259 | 26.8282 | -0.0075 | 60
ERSK1R | ERSK3- | 0.5296 | 27.1115 | -0.0073 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 0.4311 | 25.9297 | -0.0244 | 90
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3A | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3B | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60
GORG1R | GORG3- | 0.8167 | 26.9876 | -0.0071 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.3876 | 19.4628 | -0.0275 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.5381 | 25.2943 | -0.0108 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1- | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1- | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
JOHN1Q | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60
JOHN1R | JOHN3- | 0.7078 | 27.9911 | -0.013 | 60
KAIM2- | KAIM3A | 0.4944 | 20.244 | -0.245 | 120
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILS4T | KILS2- | 0.0148 | 1.6509 | -0.1193 | 1000
KILT2Q | KILT3- | 0.4927 | 18.4934 | -0.1756 | 120
KILT2R | KILT3- | 0.4976 | 18.4933 | -0.1775 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KYPE1- | KYPE3- | 0.1922 | 14.207 | -0.0113 | 120
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MIDM1- | MIDM3- | 0.4664 | 13.6087 | -0.0075 | 60
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37.5
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37.5
MOSM1A | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1B | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1A | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1B | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1173 | 8.6992 | -0.0311 | 240
NECU2- | NECU1- | 0.1173 | 8.5659 | -0.0322 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0297 | 240
NECU2- | NECU1Q | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 0.1164 | 8.5534 | -0.0287 | 240
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 90
REDH1- | REDH3- | 0.94 | 20.7787 | 0 | 60
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SANX1Q | SANX3- | 0.8844 | 21.5485 | -0.309 | 60
SANX1R | SANX3- | 0.8767 | 21.2319 | -0.3087 | 60
SHRU2Q | SHRU3- | 0.4926 | 19.9939 | -0.2739 | 120
SHRU2R | SHRU3- | 0.2914 | 23.7232 | -0.0252 | 120
SIGH2Q | SIGH3A | 0.4564 | 27.5518 | -0.032 | 180
SIGH2R | SIGH3A | 0.4281 | 27.53 | -0.0372 | 180
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4722 | 18.7441 | -0.1542 | 120
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 120
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1- | STLE3S | 0.4217 | 25.741 | -0.028 | 90
STLE1- | STLE3S | 0.4235 | 25.6743 | -0.0254 | 90
TELR1Q | TELR3- | 0.9688 | 26.4656 | -0.0572 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG1R | 0.0267 | 1.3331 | 0 | 90
TONG1- | TONG3- | 0.533 | 26.9114 | -0.0078 | 60
TONG1- | TONG3- | 0.5309 | 27.0615 | -0.008 | 60
TONG1Q | TONG1R | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WESE1- | AIKE3A | 0.5667 | 13.2333 | 0 | 90
WESE1- | AIKE3B | 0.5667 | 13.2333 | 0 | 90
WFIE1A | WFIE3- | 0.9889 | 20.4928 | 0 | 60
WFIE1B | WFIE3- | 0.9528 | 20.5613 | 0 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH2- | WISH3- | 0.4821 | 24.1785 | -0.226 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.1517 | 8.707 | -0.1161 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.2306 | 12.2562 | -0.0292 | 120
WLEX2- | WLEX3B | 0.2306 | 12.2728 | -0.0271 | 120
WLEX2- | WLEX3C | 0.2306 | 12.2728 | -0.0275 | 120

## B-3-1c
B.3.1c - NGET Transformer Parameters for 2020/21
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA4A | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275
ABHA4B | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 279
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211
ABTH21 | ABTH13 | 0.0977 | 8.1994 | -1.7127 | 212
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALVE4A | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275
AMEM4A | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270
AMEM4B | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 275
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARK11 | 0.1646 | 8.0383 | -0.1808 | 211
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 258
BEDD21 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 240
BEDD21 | BEDT1A | 0.2264 | 12.2479 | -0.6062 | 126
BEDD22 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 240
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 240
BEDD23 | BEDT1B | 0.2264 | 12.2479 | -0.6062 | 126
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 867
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 273
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209
BLYT4A | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT4B | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1100
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 276
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 277
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 278
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 278
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 312
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRFO41 | BRFO1* | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 271
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 272
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1096
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270
BRLE41 | BRLE1A | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE1B | 0.1303 | 7.8698 | -0.4285 | 263
BRWA2A | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 0.167 | 7.9774 | -0.2092 | 255
BURW41 | BURW11 | 0.1372 | 8.0197 | -0.1238 | 240
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BURW41 | BURW11 | 0.1675 | 8.2453 | -0.6567 | 253
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 240
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 265
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 278
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST41 | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST41 | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT11 | 0.1658 | 8.426 | -0.2939 | 264
CANT41 | CANT12 | 0.1509 | 8.2849 | -0.3279 | 264
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 279
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 180
CAPE41 | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886
CAPE42 | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272
CARR4A | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CARR4B | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 273
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 280
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 278
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254
CHSI21 | CHSI11 | 0.2264 | 12.2479 | -0.6062 | 126
CHSI21 | CHSI11 | 0.2264 | 12.2479 | -0.6062 | 126
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 249
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 255
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 251
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 251
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 278
CILF41 | CILF2A | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF2B | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR12 | 0.0997 | 8.0088 | -0.093 | 266
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 278
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259
CONQ41 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261
CONQ41 | CONQ12 | 0.1045 | 7.8806 | -0.0998 | 240
CONQ41 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 266
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 279
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 240
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB21 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 849
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 180
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 750
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EASO41 | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
EASO41 | EASO12 | 0.103 | 7.9231 | -0.0638 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 272
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279
ELST21 | ELST12 | 0.1221 | 8.0467 | -0.0391 | 240
ELST21 | ELST13 | 0.1985 | 8.1167 | -0.4624 | 189
ELST21 | ELST13 | 0.1954 | 8.0796 | -0.2295 | 189
ELST21 | ELST1A | 0.3567 | 11.136 | -0.7303 | 126
ELST22 | ELST11 | 0.1923 | 8.081 | -1.4418 | 189
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 212
ELST22 | ELST1B | 0.3567 | 11.136 | -0.7303 | 127
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1100
ELST4B | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 278
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139
FECK41 | FECK21 | 0.0211 | 1.6463 | -14.2471 | 1114
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199
FERR21 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR21 | FERR61 | 0.237 | 10.8633 | -0.263 | 204
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 180
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278
FERR4A | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR4A | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113
FIDF21 | FIDF12 | 0.2847 | 12.2467 | -1.4346 | 120
FIDF21 | FIDF13 | 0.1594 | 8.6081 | -0.2215 | 261
FIDF22 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271
FIDF23 | FIDF11 | 0.2847 | 12.2467 | -1.4346 | 120
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 240
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 240
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 300
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 146
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD1A | 0.054 | 4.8906 | -0.1253 | 499
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063
FROD41 | WEAV71 | 0.3209 | 20.5475 | -0.1224 | 80
FROD41 | WEAV71 | 0.3209 | 20.5475 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN12 | 0.1035 | 7.8472 | -0.0758 | 240
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268
HACK2A | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK2B | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK2A | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 137
HARK22 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK22 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK21 | 0.0321 | 2.4344 | -0.0528 | 555
HARK41 | HARK22 | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK22 | 0.0292 | 2.402 | -0.2732 | 573
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 191
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1063
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 240
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2750
HINP41 | HINP21 | 0.0376 | 2.3797 | -3.9009 | 507
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 539
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 279
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
HUTT41 | HUTT71 | 0.3195 | 20.7975 | -0.0003 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 279
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 217
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 250
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 278
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 265
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 279
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 125
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER22 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER4A | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1135
IVER4A | IVER22 | 0.0326 | 2.3798 | -3.9003 | 500
IVER4B | IVER21 | 0.0326 | 2.3798 | -3.9003 | 500
IVER4B | IVER23 | 0.0132 | 1.4627 | -2.0624 | 841
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 256
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 276
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278
KEAD4C | KEAD41 | 0.0002 | 0.2873 | 0 | 2750
KEAD4D | KEAD41 | 0.0002 | 0.4178 | 0 | 2750
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 257
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 236
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 240
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279
KIBY22 | KIBY11 | 0.1681 | 8.3396 | -1.4878 | 211
KIBY22 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 269
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 278
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264
KIRK21 | KIRK11 | 0.1575 | 8.0988 | -0.027 | 266
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 279
KIRK2A | KIRK21 | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
LACK41 | LACK2C | 0.0174 | 1.598 | -0.1503 | 1154
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 240
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA4A | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEGA4B | LEGA41 | 0.001 | 0.35 | 0 | 2000
LEIS4A | LEIS11 | 0.103 | 7.9231 | -0.0638 | 272
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 240
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 253
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 267
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 240
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 274
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 884
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 240
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 279
MELK41 | MELK1* | 0.1041 | 7.8535 | -0.0851 | 240
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MELK41 | MELK2B | 0 | 1.692 | 0 | 886
MILH21 | MILH11 | 0.179 | 8.3648 | -4.7616 | 211
MILH21 | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH21 | MILH12 | 0.179 | 8.3648 | -4.7616 | 199
MILH21 | MILH12 | 0.1266 | 8.6449 | -1.9406 | 264
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 240
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 263
MITY41 | MITY12 | 0.137 | 7.9818 | -0.1471 | 240
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 263
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1138
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 269
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 270
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 240
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 272
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 886
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 240
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 180
NHYD2C | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 187
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278
NINF41 | NINF12 | 0.1509 | 7.9378 | -0.9251 | 253
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273
NORL2A | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORL2B | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORM41 | NORW11 | 0.1307 | 7.9515 | -0.1098 | 240
NORM41 | NORW11 | 0.1509 | 7.9378 | -0.9251 | 253
NORM41 | NORW13 | 0.1509 | 7.9378 | -0.9251 | 267
NORM41 | NORW1C | 0.1264 | 8.4534 | -0.357 | 277
NORM41 | NORW1D | 0.1118 | 8.3874 | -0.0906 | 278
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 280
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 252
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 253
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 262
OCKH21 | OCKH1* | 0.179 | 8.3648 | -4.7616 | 202
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH2A | OCKH21 | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 100
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 115
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB4A | OLDB21 | 0.0146 | 1.609 | -1.8746 | 1115
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 240
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 274
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN4A | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138
PENN4B | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 257
PEWO2A | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO2B | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278
PEWO41 | PEWO2A | 0.0178 | 1.5995 | -1.2431 | 845
PEWO41 | PEWO2A | 0.0189 | 1.6132 | -0.7226 | 1129
PEWO41 | PEWO2B | 0.021 | 1.669 | -12.6082 | 876
PEWO41 | PEWO2B | 0.0175 | 1.5879 | -4.0069 | 1139
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 110
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 120
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 279
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273
RATS41 | RATS11 | 0.1046 | 7.8493 | -0.0881 | 240
RATS41 | RATS11 | 0.103 | 7.9231 | -0.0638 | 262
RATS41 | RATS12 | 0.1278 | 8.0061 | -0.2276 | 277
RATS41 | RATS12 | 0.1373 | 8.1976 | -0.1719 | 278
RATS41 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240
RAYL41 | RAYM11 | 0.1759 | 7.9134 | -0.267 | 240
RAYL41 | RAYM11 | 0.1309 | 7.8656 | -0.4549 | 262
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 278
REBR21 | REBR31 | 0.665 | 28.1922 | -0.151 | 112
REBR21 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132
REBR22 | REBR32 | 0.665 | 28.1922 | -0.151 | 111
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
RICH41 | RICH11 | 0.148 | 7.4973 | -0.3849 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH12 | 0.2847 | 12.2467 | -1.4346 | 140
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RYEH41 | RYEH13 | 0.1372 | 8.0197 | -0.1238 | 253
RYEH4A | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260
RYEH4B | RYEH12 | 0.1326 | 8.774 | -0.7141 | 260
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1307 | 7.9515 | -0.1098 | 276
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273
SELL41 | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275
SELL41 | SELL12 | 0.103 | 7.9231 | -0.0638 | 270
SELL41 | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115
SHRE4A | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 269
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | LODR62 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 240
SJOW21 | SJOW13 | 0.1441 | 8.6238 | -0.2707 | 251
SJOW41 | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 270
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 240
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 804
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 279
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN41 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SPEN42 | SPEN11 | 0.1264 | 8.4534 | -0.357 | 278
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
SSHI21 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 240
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 240
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 279
STAL21 | STAL11 | 0.2188 | 8.097 | -1.9861 | 280
STAL41 | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271
STAY4A | STAY41 | 0.0002 | 0.4178 | -13.831 | 2750
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138
STEW21 | STEN11 | 0.3392 | 11.9012 | -0.7294 | 141
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 274
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1172
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 240
STSB4A | STSB41 | 0.0003 | 0.1825 | 0 | 1999
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252
SUND41 | SUND11 | 0.1303 | 7.8698 | -0.4285 | 278
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254
SWAN21 | SWAN11 | 0.1646 | 8.0383 | -0.1808 | 211
SWAN21 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 240
SWAN41 | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 240
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210
SWAN4A | SWAN21 | 0.0178 | 1.5995 | -1.2431 | 851
TAUN42 | TAUN11 | 0.1759 | 7.9134 | -0.267 | 279
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
THOM21 | THOM61 | 0.3985 | 16.203 | -0.4431 | 122
THOM41 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 879
THOM41 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879
THOM42 | THOM21 | 0.0152 | 1.6463 | -0.1118 | 1100
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
TILB21 | TILB11 | 0.3792 | 12.0524 | -0.3982 | 131
TILB21 | TILB12 | 0.3792 | 12.0524 | -0.3982 | 134
TILB41 | TILB13 | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 1153
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102
TINP21 | TINP32 | 0.4758 | 20.0944 | -0.4489 | 111
TINP21 | TINP34 | 0.5083 | 24.0899 | -0.1921 | 135
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP22 | TINP33 | 0.5083 | 24.0899 | -0.1921 | 172
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 139
TOTT21 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265
TOTT22 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198
TOTT23 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT24 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW21 | TRAW11 | 0.2847 | 12.2467 | -1.4346 | 140
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 279
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 222
UPPB21 | UPPB11 | 0.0979 | 8.4415 | -0.018 | 262
UPPB22 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 105
UPPB22 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 105
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 312
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 263
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 240
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 240
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 253
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 266
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274
WALP41 | WALP11 | 0.1175 | 8.6648 | -0.4173 | 274
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278
WALX4A | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4B | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1137
WALX4B | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1137
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WASF2A | WASF1A | 0.197 | 7.9698 | -0.2553 | 207
WASF2B | WASF1B | 0.197 | 7.9698 | -0.2553 | 207
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 279
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 139
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 263
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 264
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 271
WHAM4A | WHAM41 | 0.001 | 0.35 | 0 | 2000
WHAM4B | WHAM41 | 0.001 | 0.35 | 0 | 2000
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO31 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO21 | WHSO32 | 0.5913 | 19.1375 | -0.4269 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.5913 | 19.0842 | -0.4269 | 100
WHSO4A | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIEN21 | WIEN11 | 0.1594 | 8.6081 | -0.2215 | 288
WIEN21 | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 296
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278
WILE41 | WILL21 | 0.0268 | 2.7989 | -0.3188 | 686
WILL21 | WILL11 | 0.2847 | 12.2467 | -1.4346 | 140
WILL21 | WILL12 | 0.2847 | 12.2467 | -1.4346 | 140
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206
WIMB21 | WIMB11 | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB12 | 0.1845 | 7.8956 | -0.1938 | 249
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 249
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201
WLSD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949
WLSD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 1000
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WTHU4* | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.2188 | 8.097 | -1.9861 | 280
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250
WWEY22 | WWEY11 | 0.1954 | 8.0796 | -0.2295 | 202
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY4A | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY4A | WWEY22 | 0.0185 | 1.614 | -0.5638 | 886
WWEY4B | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845
WWEY4B | WWEY23 | 0.0178 | 1.5995 | -1.2431 | 845
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273

## B-3-1d
B.3.1d- OFTO Transformers for 2020/21
OFTO | Site | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
Hornsea One Limited | Hornsea 1 Wind Farm | HOWA41 | HOWA21 | 0.016279 | 2.6767 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWW21 | HOWW31 | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW21 | HOWW31 | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW22 | HOWW32 | 0.0875 | 5.925 | 0 | 240 | 220/34
|  | HOWW22 | HOWW32 | 0.0875 | 5.925 | 0 | 240 | 220/34
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HEDO21 | HUMO11 | 0.1875 | 11.4375 | 0 | 160 | 275/132/33
|  | HEDO21 | HUMO12 | 0.1875 | 11.4375 | 0 | 160 | 275/132/33
|  | HUMO11 | HUMW31 | 0.23192 | 8.5714 | 0 | 140 | 132/33
|  | HUMO12 | HUMW32 | 0.23192 | 8.5714 | 0 | 140 | 132/33
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW11 | BOSW31 | 0.316 | 15.0833 | 0 | 120 | 132/33
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | BBWO21 | 0.08075 | 5.8994 | -0.1779 | 200 | 400/220/15.5
|  | BBWO41 | BBWO21 | 0.07975 | 5.7994 | -0.1779 | 200 | 400/220/15.5
|  | BBWW21 | BBWW31 | 0.11508 | 6.0889 | -0.8147 | 200 | 220/34
|  | BBWW21 | BBWW32 | 0.11573 | 6.0739 | -0.8147 | 200 | 220/34
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDW31 | 0.13 | 6 | 0 | 200 | 132/33
|  | DUDW12 | DUDW32 | 0.13 | 6 | 0 | 200 | 132/33
|  | NECT41 | DUDO11 | 0.09 | 6 | -0.2956 | 200 | 400/132/33
|  | NECT41 | DUDO11 | 0.09 | 6 | -0.2956 | 200 | 400/132/33
East Anglia One Limited | East Anglia Offshore Wind Farm | BRST41 | BRST21 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | BRST41 | BRST21 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | EAAW21 | EAAW61 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW22 | EAAW62 | 0.1037 | 7.035 | 0 | 200 | 220/66
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GANW11 | GANW31 | 0.003778 | 0.12122 | 0 | 180 | 132/33/33
|  | GANW12 | GANW32 | 0.003778 | 0.12222 | 0 | 180 | 132/33/33
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMW11 | ORMW31 | 0.464 | 14.421 | 0 | 85 | 132/33
|  | ORMW11 | ORMW32 | 0.465 | 14.479 | 0 | 85 | 132/33
|  | ORMO11 | ORMO31 | 0.348 | 13.465 | 0 | 110 | 132/33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SSAW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSAW11 | SSAW32 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW32 | 0.23 | 12.07 | 0 | 90 | 132/33
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNW21 | TKNW61 | 0.07 | 3.33 | 0 | 420 | 220/66
|  | TKNO41 | TKNO21 | 0.036 | 3.78 | 0 | 450/450/260 | 400/220/33
|  | TKNO41 | TKNO21 | 0.036 | 3.78 | 0 | 450/450/260 | 400/220/33
Diamond Transmission Partners Walney Extension Limited | Walney Extension Wind Farm | WACW21 | WACW31 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WACW21 | WACW32 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WADW21 | WADW31 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WADW21 | WADW32 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WOWE41 | WOWE21 | 0.0255 | 2.617 | 0 | 470 | 400/227
|  | WOWE42 | WOWE22 | 0.0255 | 2.617 | 0 | 470 | 400/227
WoDS Transmission plc | West of Duddon Sands | WDSO41 | WDSO11 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
|  | WDSO42 | WDSO12 | 0.20833 | 5 | 0 | 240/240/80 | 400/155/13.9
|  | WDSW11 | WDSW31 | 0.20833 | 5 | 0 | 240 | 155/34
|  | WDSW12 | WDSW32 | 0.20833 | 5 | 0 | 240 | 155/34
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO21 | WERO11 | 0.09 | 6.62 | 0 | 180/180/110 | 275/150/34
|  | WERO22 | WERO11 | 0.09 | 6.58 | 0 | 180/180/110 | 275/150/34
|  | WERW11 | WERW31 | 0.12 | 7.14 | 0 | 140 | 150/34
|  | WERW11 | WERW32 | 0.12 | 7.14 | 0 | 140 | 150/34
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GANW14 | GANW3A | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GANW14 | GANW3B | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GREG11 | GREG31/GREG32 | 0.4 | 23.44 | 0 | 180/90/90 | 132/33/33
|  | GREG12 | GREG33 | 0.4 | 23.44 | 0 | 180/90/90 | 132/33/33
|  | GREG13 | GREG34/GREG35 | 0.4 | 23.44 | 0 | 180/90/90 | 132/33/33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | LONO11 | 0.33 | 6.4556 | 0 | 180/180/90 | 400/150/13.9
|  | LONO42 | LONO12 | 0.33 | 6.4111 | 0 | 180/180/90 | 400/150/13.9
|  | LONO41 | LONO13 | 0.33 | 6.4611 | 0 | 180/180/90 | 400/150/13.9
|  | LONO42 | LONO14 | 0.33 | 6.4389 | 0 | 180/180/90 | 400/150/13.9
|  | LOAW11 | LOAW31 | 0.402 | 6.56 | 0 | 180 | 150/33
|  | LOAW12 | LOAW32 | 0.4045 | 6.57 | 0 | 180 | 150/33
|  | LOAW13 | LOAW33 | 0.407 | 6.58 | 0 | 180 | 150/33
|  | LOAW14 | LOAW34 | 0.4045 | 6.57 | 0 | 180 | 150/33
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | BODE41 | GWYO11 | 0.054688 | 3.5313 | 0 | 320/320/60 | 400/132/13.9
|  | BODE42 | GWYO12 | 0.054688 | 3.5313 | 0 | 320/320/60 | 400/132/13.9
|  | GWAW11 | GWAW31 | 0.15625 | 11.3313 | 0 | 160 | 132/33
|  | GWAW12 | GWAW32 | 0.15625 | 11.3625 | 0 | 160 | 132/33
|  | GWBW11 | GWBW31 | 0.15625 | 11.3438 | 0 | 160 | 132/33
|  | GWBW12 | GWBW32 | 0.15625 | 11.375 | 0 | 160 | 132/33
TC Beatrice OFTO Limited | Beatrice Wind Farm | BEAT41 | BEAT21 | 0.173 | 16.03 | 0 | 320/320/170 | 400/220/33
|  | BEAT42 | BEAT22 | 0.173 | 16.03 | 0 | 320/320/170 | 400/220/33
|  | BEIW21 | BEIW31 | 0.235 | 17.5 | 0 | 310 | 220/33
|  | BEIW22 | BEIW32 | 0.235 | 17.5 | 0 | 310 | 220/33
TC Lincs OFTO Limited | Lincs Wind Farm | LINO41 | LINO11 | 0.11 | 14 | 0 | 300/300/115 | 400/132/13
|  | LINO42 | LINO12 | 0.11 | 14 | 0 | 300/300/115 | 400/132/13
|  | LINS11 | LINS31 | 0.22 | 12 | 5.83 | 240 | 132/33
|  | LINS12 | LINS32 | 0.22 | 12 | 5.83 | 240 | 132/33
Diamond Transmission Partners RB Limited | Race Bank Offshore Wind Farm | RACO41 | RACO21 | 0.03165 | 3.1526 | 0 | 360 | 400/220
|  | RACO42 | RACO22 | 0.031779 | 3.1582 | 0 | 360 | 400/220
|  | RACW21 | RACW31 | 0.11449 | 6.0389 | 0 | 200 | 220/34
|  | RACW21 | RACW32 | 0.11465 | 6.0789 | 0 | 200 | 220/34
|  | RACW21 | RACW33 | 0.11476 | 6.0989 | 0 | 200 | 220/34
|  | RACW21 | RACW34 | 0.11435 | 6.0689 | 0 | 200 | 220/34
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | RAMW11 | RAMW3A | 0.33 | 12.23 | -0.144 | 240 | 150/33
|  | RAMW12 | RAMW3B | 0.33 | 12.76 | -0.144 | 240 | 150/33
|  | TWNE41 | TWNE11 | 0.17 | 12.24 | -1.9406 | 240 | 400/150/33
|  | TWNE42 | TWNE12 | 0.17 | 12.74 | -1.9406 | 240 | 400/150/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW11 | THOW31/33 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
|  | THOW12 | THOW32/34 | 0.18056 | 12.5556 | 0 | 180/90/90 | 132/33/33
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAW11 | WAAW3A | 0.42 | 8.75 | 0 | 120 | 132/33
|  | WAAW11 | WAAW3B | 0.42 | 8.75 | 0 | 120 | 132/33
Blue Transmission Walney 2 OFTO | Walney 2 Offshore Wind Farm | WABW11 | WABW3A | 0.2395 | 8.2882 | 0 | 120 | 132/33
|  | WABW11 | WABW3B | 0.2432 | 8.3214 | 0 | 120 | 132/33

## B-3-2a
B.3.2a - SHE TransmissionTransformer Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABED1- | ABED3- | 2021 | Addition | 0.33 | 21.7 | 0 | 60
ABNE1Q | ABNE3- | 2021 | Change | 0.2621 | 24.6736 | -0.0222 | 120
ABNE1R | ABNE3- | 2021 | Change | 0.2614 | 24.7403 | -0.0197 | 120
FARI2K | FARI1K | 2021 | Change | 0.2184 | 8.2304 | -0.0007 | 240
FAUG1Q | FAUG3- | 2021 | Change | 1.1951 | 25.0827 | -0.0007 | 45
FAUG4- | FAUG1- | 2021 | Remove | 0.2149 | 8.0138 | -0.013 | 240
FAUG4- | FAUG1- | 2021 | Remove | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG4J | FAUG1- | 2021 | Addition | 0.3185 | 8.4523 | -0.013 | 240
FAUG4J | FAUG1J | 2021 | Addition | 0.108 | 3.957 | -0.0007 | 480
FAUG4K | FAUG1K | 2021 | Addition | 0.108 | 3.957 | -0.0007 | 480
GLKO1- | GLKO3J | 2021 | Addition | 0.36 | 18 | 0 | 60
LIMK1- | LIMK3- | 2021 | Addition | 0.36 | 18 | 0 | 120
LOCH1- | LOCH5J | 2021 | Change | 1.968 | 79.976 | -0.0008 | 36
LOCH1- | LOCH5K | 2021 | Change | 1.968 | 79.976 | -0.0008 | 36
PORA1Q | PORA3- | 2021 | Remove | 1.803 | 29.812 | 0 | 30
PORA1R | PORA3- | 2021 | Remove | 1.803 | 29.812 | 0 | 30
PORA1T | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 2021 | Addition | 1.803 | 29.812 | 0 | 30
ROTI2J | ROTI3- | 2021 | Addition | 0.21 | 24.52 | 0 | 120
ROTI2J | ROTI3- | 2021 | Addition | 0.21 | 24.52 | 0 | 120
SFEG1Q | SFEG5- | 2021 | Change | 1.5768 | 75.5085 | -0.0328 | 40
SFEG1R | SFEG5- | 2021 | Change | 1.5768 | 75.5085 | -0.0328 | 40
CAAD1Q | CAAD3J | 2022 | Change | 0.0026 | 0.2467 | -0.0002 | 120
CAAD1R | CAAD3J | 2022 | Change | 0.0026 | 0.2467 | -0.0002 | 120
MILS1Q | MILS3J | 2022 | Addition | 0.0036 | 0.18 | 0 | 60
ARBR1Q | ARBR3- | 2024 | Change | 0.3974 | 24.7301 | -0.0007 | 90
ARBR1R | ARBR3- | 2024 | Change | 0.4015 | 24.819 | -0.0194 | 90
BEAU2J | BEAU1J | 2024 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BEAU2J | BEAU1J | 2024 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BEAU2K | BEAU1K | 2024 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BEWF1- | BEWF3- | 2024 | Addition | 0.36 | 18 | 0 | 90
BLEX1- | BLEX3- | 2024 | Addition | 0.36 | 18 | 0 | 120
BLHI2J | BLHI1J | 2024 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
BLHI2K | BLHI1K | 2024 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
BLHI4- | BLHI2L | 2024 | Remove | 0.0252 | 1.1997 | -0.0005 | 1200
BLHI4- | BLHI2M | 2024 | Remove | 0.0253 | 1.2081 | -0.0005 | 1200
CDWE1- | CDWE3- | 2024 | Addition | 0.9 | 18 | 0 | 60
CONN2J | CONN1J | 2024 | Change | 0.218 | 8.23 | -0.0007 | 240
CORI1J | CORI3J | 2024 | Change | 1 | 20 | 0 | 90
CRDH2J | CRDH1J | 2024 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRDH2K | CRDH1K | 2024 | Addition | 0.098 | 3.936 | -0.0006 | 480
CREA1- | CREA3- | 2024 | Addition | 0.4 | 20 | 0 | 90
ENEI1- | ENEI3- | 2024 | Addition | 0.08 | 4 | 0 | 150
KINT4J | KINT2K | 2024 | Addition | 0.0252 | 1.1997 | -0.0005 | 1200
KINT4K | KINT2J | 2024 | Addition | 0.0253 | 1.2081 | -0.0005 | 1200
LYND1Q | LYND3- | 2024 | Change | 0.5 | 25 | 0 | 120
LYND1R | LYND3- | 2024 | Change | 0.5 | 25 | 0 | 120
MSHL1- | MSHL3- | 2024 | Addition | 0.36 | 17.9968 | 0 | 90
PEHE4J | PEHE2Q | 2024 | Addition | 0.026 | 1.533 | -0.0005 | 1200
PEHE4K | PEHERSV1 | 2024 | Addition | 0.026 | 1.533 | -0.0005 | 1200
PEHG1Q | PEHG3- | 2024 | Change | 0.5 | 25 | 0 | 90
PEHG1R | PEHG3- | 2024 | Change | 0.5 | 25 | 0 | 90
PENF1- | PENF3A | 2024 | Addition | 0.252 | 12.6 | 0 | 60
REDM1Q | REDM3- | 2024 | Change | 0.3974 | 24.7301 | -0.0007 | 90
REDM1R | REDM3- | 2024 | Change | 0.4015 | 24.819 | -0.0194 | 90
ROTI1J | ROTI3- | 2024 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI1K | ROTI3- | 2024 | Addition | 0.4181 | 24.9965 | 0 | 120
ROTI2J | ROTI3- | 2024 | Remove | 0.21 | 24.52 | 0 | 120
ROTI2J | ROTI3- | 2024 | Remove | 0.21 | 24.52 | 0 | 120
ROTI4J | ROTI1J | 2024 | Addition | 0.2149 | 8.0138 | -0.013 | 240
ROTI4K | ROTI1K | 2024 | Addition | 0.2149 | 8.0138 | -0.013 | 240
SLOY1L | SLOY5L | 2024 | Change | 0.79 | 23.08 | 0 | 60
SLOY1M | SLOY5M | 2024 | Change | 0.79 | 22.9 | 0 | 60
SLOY1N | SLOY5N | 2024 | Change | 0.79 | 22.98 | 0 | 60
SLOY1P | SLOY5P | 2024 | Change | 0.8 | 23.2 | 0 | 60
TEAL2A | TEAL2J | 2024 | Addition | 0.005 | 0.4 | 0 | 700
TEAL2B | TEAL2K | 2024 | Addition | 0.005 | 0.4 | 0 | 700
ACHR1R | ACHR3- | 2026 | Remove | 0.36 | 18 | 0 | 90
ACHR2- | ACHR3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
AIGA1Q | AIGA5- | 2026 | Change | 1.76 | 44.89 | 0 | 30
ALYT4J | ALYT2A | 2026 | Addition | 0.017 | 1.59 | -0.0005 | 1000
ALYT4K | ALYT2B | 2026 | Addition | 0.017 | 1.59 | -0.0005 | 1000
ANSU1- | ANSU3- | 2026 | Remove | 0.817 | 27.121 | 0 | 45
ANSU2- | ANSU3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
ARNI1K | ARNI3- | 2026 | Addition | 0.36 | 18 | 0 | 60
BLHI2J | BLHI2A | 2026 | Addition | 0.005 | 0.4 | 0 | 865
BLHI2K | BLHI2B | 2026 | Addition | 0.005 | 0.4 | 0 | 865
BROA1- | BROA3- | 2026 | Addition | 0.5 | 25 | 0 | 45
BROA1- | BROA3- | 2026 | Addition | 1.19 | 39 | 0 | 30
BROA1Q | BROA3- | 2026 | Remove | 1.19 | 39 | 0 | 30
CLGO1- | CLGO3- | 2026 | Addition | 0.36 | 18 | 0 | 270
CLGO2- | CLGO1- | 2026 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CLGO2A | CLGO1- | 2026 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CLOI11 | CLOI3- | 2026 | Addition | 0.36 | 18 | 0 | 120
CLOI11 | CLOI3- | 2026 | Addition | 0.36 | 18 | 0 | 120
CONN2J | CONN1J | 2026 | Remove | 0.218 | 8.23 | -0.0007 | 240
CONN2J | CONN1K | 2026 | Addition | 0.143 | 5.3036 | -0.0006 | 360
CONN2K | CONN1J | 2026 | Addition | 0.218 | 8.23 | -0.0007 | 240
CRSS1J | CRSS1Q | 2026 | Remove | 0.0582 | 2.145 | 0 | 240
CRSS1K | CRSS1R | 2026 | Remove | 0.0582 | 2.1492 | 0 | 240
CRSS2J | CRSS1Q | 2026 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRSS2K | CRSS1R | 2026 | Addition | 0.098 | 3.936 | -0.0006 | 480
CULL1Q | CULL5- | 2026 | Change | 1.46 | 37.6 | 0 | 30
DEAN1Q | DEAN5- | 2026 | Change | 1.01 | 25.1 | 0 | 45
DOUN2- | DOUN2A | 2026 | Addition | 0.066 | 5.333 | 0 | 360
DOUN2- | DOUN2D | 2026 | Addition | 0.066 | 5.333 | 0 | 360
DRUL1- | DRUL3- | 2026 | Addition | 0.36 | 18 | 0 | 60
DUNO1Q | DUNO3- | 2026 | Change | 0.4697 | 26.318 | 0 | 90
DUNO1R | DUNO3- | 2026 | Change | 0.4697 | 26.318 | 0 | 90
EDIN1- | GLNU3- | 2026 | Addition | 0.36 | 18 | 0 | 60
ELCH1- | ELCH3- | 2026 | Addition | 0.75 | 15 | 0 | 120
ENEI1- | ENEI3A | 2026 | Addition | 0.36 | 18 | 0 | 60
FETT2R | FETT1- | 2026 | Remove | 0.217 | 4.2737 | -0.0006 | 240
FETT4J | FETT1- | 2026 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FETT4K | FETT1- | 2026 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FINS1- | COST3- | 2026 | Addition | 0.54 | 18 | 0 | 45
FINS1- | FINS3- | 2026 | Addition | 0.451 | 25 | 0 | 120
FINS1- | FINS3- | 2026 | Addition | 0.451 | 25 | 0 | 120
FINS1- | HEST3- | 2026 | Addition | 0.54 | 18 | 0 | 45
FINS2A | FINS1- | 2026 | Addition | 0.044 | 5.833 | 0 | 360
FINS2D | FINS1- | 2026 | Addition | 0.044 | 5.833 | 0 | 360
GLEN1Q | GLEN5- | 2026 | Change | 0.55 | 21.94 | 0 | 90
GLSH1J | GLSH31 | 2026 | Addition | 0.6 | 17.4 | 0 | 120
GLSH1J | GLSH32 | 2026 | Addition | 0.6 | 17.4 | 0 | 120
INGA4J | INGA1K | 2026 | Addition | 0.131 | 7.952 | -0.11 | 240
INGA4K | INGA1J | 2026 | Addition | 0.131 | 7.952 | -0.11 | 240
KINT1- | KINT3- | 2026 | Remove | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 2026 | Change | 0.36 | 18 | 0 | 120
KINT2K | KINT1- | 2026 | Change | 0.3751 | 10.2314 | -0.015 | 240
KIOR1Q | KIOR5- | 2026 | Change | 1.78 | 45.42 | 0 | 36
MELG4J | MELG1J | 2026 | Addition | 0.108 | 3.957 | -0.0007 | 480
MELG4K | MELG1K | 2026 | Addition | 0.106 | 3.957 | -0.0007 | 480
MUAI1- | MUAI3A | 2026 | Addition | 0.36 | 18 | 0 | 90
MUAI1- | MUAI3B | 2026 | Addition | 0.36 | 18 | 0 | 90
PENF1B | PENF3B | 2026 | Addition | 3.6 | 18 | 0 | 96
PORA1T | PORA3- | 2026 | Remove | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 2026 | Remove | 1.803 | 29.812 | 0 | 30
PORA2J | PORA3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
PORA2K | PORA3- | 2026 | Addition | 0.258 | 20.06 | 0 | 120
SALA1- | SALA3- | 2026 | Addition | 0.36 | 17.99 | 0 | 90
SFIL1Q | SFIL5- | 2026 | Change | 1.99 | 39.48 | 0 | 45
SHDM1- | SHDM3- | 2026 | Addition | 0.3629 | 18.0297 | 0 | 90
STRW13 | STRW33 | 2026 | Addition | 0.5 | 25 | 0 | 90
STRW13 | STRW34 | 2026 | Addition | 0.5 | 25 | 0 | 90
STRW1C | STRW35 | 2026 | Addition | 0.36 | 18 | 0 | 120
STWN1- | STWN3J | 2026 | Addition | 0.36 | 18 | 0 | 90
STWN1- | STWN3K | 2026 | Addition | 0.36 | 18 | 0 | 90
TUMB1Q | TUMB5- | 2026 | Change | 1.63 | 77.76 | 0 | 45
TUMB1R | TUMB5- | 2026 | Change | 1.63 | 77.76 | 0 | 45
ALTN1- | ALTN3- | 2029 | Addition | 0.36 | 18 | 0 | 90
BETH1C | BETH3A | 2029 | Addition | 0.24 | 18 | 0 | 120
BLGH1- | BLGH3- | 2029 | Addition | 0.36 | 17.9968 | 0 | 90
CAID2- | CAID3- | 2029 | Addition | 0.36 | 18 | 0 | 120
COGA1- | COGA3A | 2029 | Addition | 0.324 | 17.9 | 0 | 120
DOUN4J | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN4J | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN4K | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN4K | DOUN2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
LAIR1Q | LAIR3A | 2029 | Addition | 0.36 | 18 | 0 | 60
PENF1C | PENF3C | 2029 | Addition | 3.6 | 18 | 0 | 96

## B-3-2b
B.3.2b - SPT Transformer Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
DONO1- | DONO3- | 2021 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
MIDM1- | KENE3- | 2021 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
CHAS2Q | CHAS3A | 2022 | Addition | 0.5214 | 27.5617 | -0.1031 | 120
CUMH1- | CUMH3A | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
ELVA1- | ELVA3A | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
ELVA2R | ELVA1- | 2022 | Addition | 0.0984 | 5.8325 | -0.2121 | 360
HOPR1- | HOPR3A | 2022 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
KYPE1- | HARG3- | 2022 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
MAHI2- | MAHI1B | 2022 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1B | 2022 | Addition | 0.1164 | 8.5534 | -0.0287 | 240
NECU2- | NECU1C | 2022 | Addition | 0.1111 | 6.6657 | -0.0006 | 360
NECU2- | NECU1C | 2022 | Addition | 0.1111 | 6.6657 | -0.0006 | 360
NEIL4R | NEIL2- | 2022 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
SAKN1- | SAKN3- | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
SOKY1- | SOKY3- | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
SOKY1- | SOKY3- | 2022 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CHAS2Q | CHAS3C | 2022 | Remove | 0.4875 | 18.1601 | -0.1331 | 120
COYL2- | COYL1- | 2022 | Change | 0.1476 | 8.7488 | -0.1299 | 240
COYL2- | COYL1- | 2022 | Change | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1Q | 2022 | Remove | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 2022 | Remove | 0.1164 | 8.5534 | -0.0287 | 240
AREX1- | AREX3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
BENB1- | BENB3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
ENHI1- | ENHI3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
FALL4- | FALL3C | 2024 | Addition | 0.2564 | 16.6647 | 0 | 120
MOFF1- | MOFF3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
NETS1- | NETS3- | 2024 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
REDH1- | REDH3- | 2024 | Change | 0.6267 | 27.5484 | 0 | 90
COAL4- | COAL1A | 2024 | Remove | 0.0914 | 6.4382 | -0.0751 | 360
COAL4- | COAL1B | 2024 | Addition | 0.0914 | 6.4382 | -0.0751 | 360
COAL4- | COAL1B | 2024 | Addition | 0.0914 | 6.4382 | -0.0751 | 360
CRCK2- | CRCK3- | 2024 | Addition | 0.2857 | 19.998 | 0 | 90
CUMW1- | CUMW3- | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DONO1- | DONO3A | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GNSH1- | GNSH3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
HOPR1- | CRDE3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
KENN1- | KENN3- | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
LORG1- | LORG3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
NLEI1- | NLEI3A | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NLEI1- | NLEI3B | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NOKY1- | NOKY3A | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
NOKY1- | NOKY3B | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
OHLL1- | OHLL3- | 2024 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
SHRG1- | SHRG3- | 2024 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
STNO1- | STNO3- | 2024 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CLAU1- | CLAU3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
DENN4- | DENN2- | 2026 | Addition | 0.0164 | 1.6449 | -0.1161 | 1000
EUCH1- | EUCH3- | 2026 | Addition | 0.1922 | 14.207 | -0.0113 | 120
KINC4A | KINC2- | 2026 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
KINC4B | KINC2- | 2026 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
KNOK1- | KNOK3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
KNOK1- | KNOK3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
LEGO1Q | LEGO3- | 2026 | Addition | 0.3119 | 21.8311 | 0 | 60
LEGO1R | LEGO3- | 2026 | Addition | 0.3119 | 21.8311 | 0 | 60
MAHI2- | MAHI1C | 2026 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
MOFF4- | MOFF1- | 2026 | Addition | 0.1483 | 10.0614 | -0.3432 | 240
PORD2R | PORD3- | 2026 | Change | 0.2857 | 31.1098 | 0 | 90
STHA2A | STHA3- | 2026 | Change | 0.2857 | 31.1098 | 0 | 90
TONG1- | TONG1R | 2026 | Remove | 0.0267 | 1.3331 | 0 | 90
TONG1Q | TONG1R | 2026 | Remove | 0.0125 | 2.5 | 0 | 90
TRSN1- | TRSN3- | 2026 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
WGEO2R | WGEO3- | 2026 | Change | 0.2857 | 31.1098 | 0 | 90
BONN2A | BONN1- | 2029 | Remove | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 2029 | Remove | 0.1559 | 8.9445 | -0.1694 | 240
BONN4- | BONN1- | 2029 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
BONN4- | BONN1- | 2029 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
GHPS1- | GHPS3A | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GHPS1- | GHPS3B | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
OFOA1- | OFOA3- | 2029 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
WFIE1A | WFIE3- | 2029 | Change | 0.5296 | 27.1115 | -0.0073 | 60
WFIE1B | WFIE3- | 2029 | Change | 0.5296 | 27.1115 | -0.0073 | 60

## B-3-2c
B.3.2c - NGET Transformer Changes 2021/22 to 2029/30
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ELST21 | ELST15 | 2021 | Remove | 0.3567 | 11.136 | -0.7303 | 126
ELST22 | ELST16 | 2021 | Remove | 0.3567 | 11.136 | -0.7303 | 127
SJOW41 | SJOW21 | 2021 | Addition | 0.0224 | 2.5703 | -0.5831 | 800
TAUN41 | TAUN11 | 2021 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
HARK41 | HARK21 | 2022 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK41 | HARK21 | 2022 | Remove | 0.0321 | 2.4344 | -0.0528 | 555
SJOW41 | SJOW21 | 2022 | Remove | 0.0224 | 2.5703 | -0.5831 | 800
BRWA2A | BRWA11 | 2024 | Remove | 0.167 | 7.9774 | -0.2092 | 255
BRWA2B | BRWA11 | 2024 | Remove | 0.167 | 7.9774 | -0.2092 | 255
BRWA4A | BRWA11 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
BRWA4B | BRWA11 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
HARK41 | HARK22 | 2024 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK41 | HARK22 | 2024 | Remove | 0.0376 | 2.3797 | -3.9009 | 547
SAFO41 | SAFO11 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
SAFO41 | SAFO12 | 2024 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
SEAB41 | SEAB11 | 2024 | Remove | 0.1307 | 7.9515 | -0.1098 | 276
WIMB21 | WIMB11 | 2024 | Remove | 0.167 | 7.9774 | -0.2092 | 255
WIMB21 | WIMB12 | 2024 | Remove | 0.1845 | 7.8956 | -0.1938 | 249
WIMB41 | WIMB11 | 2024 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB12 | 2024 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
BENR41 | BENR11 | 2026 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
BENR41 | BENR12 | 2026 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
LHOR4A | LEWE12 | 2026 | Addition | 0.1373 | 8.1976 | -0.1719 | 278
LHOR4B | LEWE11 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 278
NEWX41 | NEWX21 | 2026 | Addition | 0.0132 | 1.4627 | -2.0624 | 1100
NEWX42 | NEWX21 | 2026 | Addition | 0.0132 | 1.4627 | -2.0624 | 1100
HAWP41 | HAWP21 | 2029 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
POPP4A | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063
POPP4A | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063
POPP4B | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063
POPP4B | POPP21 | 2029 | Addition | 0.009 | 1.3333 | 0 | 1063

## B-3-2d
B.3.2d - OFTO Transformer Changes 2021/22 to 2029/30
Wind Farm | Node 1 | Node 2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating(MVA) | Voltage(kV)
Firth of Forth 1 Offshore Wind Farm | FOFW21 | FOFW61 | 2021 | Addition | TBC | TBC | TBC | 400 | 275/66
| FOFW22 | FOFW62 | 2021 | Addition | TBC | TBC | TBC | 400 | 275/66
Hornsea 1 Offshore Wind Farm | HOWW23 | HOWW33 | 2021 | Addition | 0.0875 | 5.9208 | −− | 240 | 220/34
| HOWW23 | HOWW33 | 2021 | Addition | 0.0875 | 5.9042 | −− | 240 | 220/34
Moray East Offshore Wind Farm | MOWE21 | MOWE61 | 2021 | Addition | 0.08 | 4.53 | −− | 315 | 220/66
| MOWE22 | MOWE62 | 2021 | Addition | 0.08 | 4.53 | −− | 315 | 220/66
| MOWE23 | MOWE63 | 2021 | Addition | 0.08 | 4.53 | −− | 315 | 220/66
| MORF21 | MORF21 | 2021 | Addition | 0.097 | 4.74 | −− | 340 | 275/220
| MORF22 | MORF22 | 2021 | Addition | 0.097 | 4.74 | −− | 340 | 275/220
| MORF23 | MORF23 | 2021 | Addition | 0.097 | 4.74 | −− | 340 | 275/220
Triton Knoll Offshore Wind Farm | TKNE21 | TKNE61 | 2021 | Addition | 0.07 | 3.33 | 0 | 420 | 220/66
Inch Cape Offshore Wind Farm | INCW61 | INCW21 | 2022 | Addition | TBC | 16 | −− | 550 | 66/220
| INCW62 | INCW22 | 2022 | Addition | TBC | 16 | −− | 550 | 66/220
| INCO21 | INCO21 | 2022 | Addition | TBC | 16 | −− | 550 | 220/275/LV
| INCO22 | INCO22 | 2022 | Addition | TBC | 16 | −− | 550 | 220/275/LV
Neart Na Gaoithe Offshore Wind Farm | NNGW31 | NNGW21 | 2022 | Addition | 0.12 | 12 | −− | 230 | 220/66
| NNGW32 | NNGW22 | 2022 | Addition | 0.12 | 12 | −− | 230 | 220/66
| NNGO21 | NNGO41 | 2022 | Addition | 0.1 | 10 | −− | 260/230/170 | 400/220/33
| NNGO22 | NNGO42 | 2022 | Addition | 0.1 | 10 | −− | 260/230/170 | 400/220/33
Firth of Forth 1 Offshore Wind Farm | FOFW23 | FOFW63 | 2024 | Addition | TBC | TBC | TBC | 400 | 275/66
Dogger bank 1 Offshore Wind Farm | Dogger bank 1A offshore 33kV | Dogger bank 1A offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Dogger bank 1A offshore 33kV | Dogger bank 1A offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Dogger bank 1B offshore 33kV | Dogger bank 1B offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Dogger bank 1B offshore 33kV | Dogger bank 1B offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Dogger bank offshore 220kV | Dogger bank offshore TBC | 2024 | Addition | TBC | TBC | TBC | TBC | 132/TBC
| Dogger bank onshore TBC | Dogger bank onshore 400kV | 2024 | Addition | TBC | TBC | TBC | TBC | 400/TBC
Doggerbank 4 Offshore wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2024 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore | 2024 | Addition | TBC | TBC | TBC | TBC | 220/TBC
| Doggerbank 4 Onshore | Doggerbank 4 Onshore 400kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC/400
East Anglia 3 Offshore Wind Farm | East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 200 | 220/33/33
| East Anglia Offshore 33kV | East Anglia Offshore 220kV | 2024 | Addition | TBC | TBC | TBC | 200 | 220/33/33
| East Anglia Offshore 220kV | East Anglia Offshore TBC | 2024 | Addition | TBC | TBC | TBC | TBC | 220/TBC
| East Anglia Onshore TBC | East Anglia Onshore 400kV | 2024 | Addition | TBC | TBC | TBC | TBC | 220/TBC
Hornsea 2 Offshore Wind Farm | Hornsea 2A Offshore 66kV | Hornsea 2A Offshore 220kV | 2024 | Addition | 0.216 | 13.31 | −− | 270 | 220/66
| Hornsea 2A Offshore 66kV | Hornsea 2A Offshore 220kV | 2024 | Addition | 0.216 | 13.3 | −− | 270 | 220/66
| Hornsea 2B Offshore 66kV | Hornsea 2B Offshore 220kV | 2024 | Addition | 0.214 | 13.37 | −− | 270 | 220/66
| Hornsea 2B Offshore 66kV | Hornsea 2B Offshore 220kV | 2024 | Addition | 0.214 | 13.33 | −− | 270 | 220/66
| Hornsea 2C Offshore 66kV | Hornsea 2C Offshore 220kV | 2024 | Addition | 0.214 | 13.25 | −− | 270 | 220/66
| Hornsea 2C Offshore 66kV | Hornsea 2C Offshore 220kV | 2024 | Addition | 0.215 | 13.24 | −− | 270 | 220/66
| Hornsea Onshore 220kV | Hornsea Onshore 400kV | 2024 | Addition | 0.14 | 11.86 | −− | 475 | 400/220
| Hornsea Onshore 220kV | Hornsea Onshore 400kV | 2024 | Addition | 0.14 | 11.86 | −− | 475 | 400/220
| Hornsea Onshore 220kV | Hornsea Onshore 400kV | 2024 | Addition | 0.14 | 11.86 | −− | 475 | 400/220
Hornsea 3 Offshore Wind Farm | Hornsea 3A-1 Offshore 66kV | Hornsea 3A-1 Offshore 500kV | 2024 | Addition | TBC | TBC | TBC | 850 | 500/66
| Hornsea 3A-1 Onshore 500kV | Hornsea 3A Onshore 400kV | 2024 | Addition | TBC | TBC | TBC | 850 | 500/400
| Hornsea 3A-2 Onshore 500kV | Hornsea 3A Onshore 400kV | 2024 | Addition | TBC | TBC | TBC | 850 | 500/400
Moray West Offshore Wind Farm | Moray West Offshore P1 220kV | Moray West Offshore P1 66kV | 2024 | Addition | TBC | TBC | TBC | TBC | 220/66
| Moray West Offshore P2 220kV | Moray West Offshore P2 66kV | 2024 | Addition | TBC | TBC | TBC | TBC | 220/66
| Moray West Onshore 400kV | Moray West Onshore 220kV | 2024 | Addition | TBC | TBC | TBC | TBC | 400/220
| Moray West Onshore 400kV | Moray West Onshore 220kV | 2024 | Addition | TBC | TBC | TBC | TBC | 400/220
Sofia Offshore Wind Farm | Sofia Offshore TBC | Sofia offshore 66kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC/66
| Sofia Offshore TBC | Sofia offshore 66kV | 2024 | Addition | TBC | TBC | TBC | TBC | TBC/66
Dogger Bank 2 offshore Wind Farm | Offshore 220kV-1 | Offshore 66kV-1 | 2026 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-2 | 2026 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-3 | 2026 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-4 | 2026 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore-2 | Offshore 220kV-1 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC
| Onshore-1 | Onshore 400kV | 2026 | Addition | TBC | TBC | TBC | TBC | TBC
Dogger Bank 4 Offshore Wind Farm | Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2026 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| Doggerbank 4 Offshore 220kV | Doggerbank 4 Offshore 33kV | 2026 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
East Anglia 6A Offshore Wind Farm | East Anglia 6A Offshore-2 | East Anglia 6A Offshore-1 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC
| East Anglia 6A Offshore-2 | East Anglia 6A Offshore-1 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC
East Anglia 6B Offshore Wind Farm | East Anglia 6B Offshore-2 | East Anglia 6B Offshore-1 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC
| East Anglia 6B Offshore-2 | East Anglia 6B Offshore-1 | 2026 | Addition | TBC | TBC | TBC | TBC | TBC
Firth of Forth 2 Offshore Wind Farm | Offshore 66KV-1 | Offshore 275kV-1 | 2026 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 66KV-2 | Offshore 275kV-2 | 2026 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 66KV-3 | Offshore 275kV-3 | 2026 | Addition | TBC | TBC | TBC | 430 | 275/66
| Onshore 275kV-1 | Onshore 400kV-1 | 2026 | Addition | TBC | TBC | TBC | 430 | 400/275
| Onshore 275kV-1 | Onshore 400kV-1 | 2026 | Addition | TBC | TBC | TBC | 430 | 400/275
| Onshore 275kV-1 | Onshore 400kV-1 | 2026 | Addition | TBC | TBC | TBC | 430 | 400/275
Hornsea 3 Offshore Wind Farm | Hornsea 3A-2 Offshore 66kV | Hornsea 3A-2 Offshore 500kV | 2026 | Addition | TBC | TBC | TBC | 850 | 500/66
| Hornsea 3B-1 Offshore 66kV | Hornsea 3B-1 Offshore 500kV | 2026 | Addition | TBC | TBC | TBC | 850 | 500/66
| Hornsea 3B-1 Onshore 500kV | Hornsea 3B Onshore 400kV | 2026 | Addition | TBC | TBC | TBC | 850 | 500/400
| Hornsea 3B-2 Onshore 500kV | Hornsea 3B Onshore 400kV | 2026 | Addition | TBC | TBC | TBC | 850 | 500/400
Sheringham and Dudgeon Extension Wind Farm | Offshore 66kV-1 | Offshore 220kV-1 | 2026 | Addition | TBC | TBC | TBC | 185 | 220/66
| Offshore 66kV-2 | Offshore 220kV-1 | 2026 | Addition | TBC | TBC | TBC | 185 | 220/66
| Offshore 66kV-3 | Offshore 220kV-2 | 2026 | Addition | TBC | TBC | TBC | 225 | 220/66
| Offshore 66kV-4 | Offshore 220kV-2 | 2026 | Addition | TBC | TBC | TBC | 225 | 220/66
| Onshore 220kV-1 | Onshore 400kV-1 | 2026 | Addition | TBC | TBC | TBC | 450 | 400/220
| Onshore 220kV-2 | Onshore 400kV-2 | 2026 | Addition | TBC | TBC | TBC | 450 | 400/220
Codling Wind Farm | CODW21 | CODW31 | 2029 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| CODW22 | CODW32 | 2029 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| CODW23 | CODW33 | 2029 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| CODW24 | CODW34 | 2029 | Addition | TBC | TBC | TBC | 280/140/140 | 220/33/33
| CODL41 | CODL22 | 2029 | Addition | 0.02 | 1.61 | TBC | 580 | 400/220
| CODL41 | CODL22 | 2029 | Addition | 0.02 | 1.61 | TBC | 580 | 400/220
EA One North Wind Farm | EA1N Offshore 220kV-1 | EA1N Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | 525 | 220/66
| EA1N Offshore 220kV-2 | EA1N Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 525 | 220/66
| EA1N Onshore 220kV | EA1N Onshore 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
| EA1N Onshore 220kV | EA1N Onshore 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
East Anglia 4A Wind Farm | East Anglia 4A Offshore-2 | East Anglia 4A Offshore-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| East Anglia 4A Offshore-2 | East Anglia 4A Offshore-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| East Anglia 4A Onshore-1 | East Anglia 4A 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
East Anglia 5A Wind Farm | East Anglia 5A Offshore-2 | East Anglia 5A Offshore-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| East Anglia 5A Offshore-2 | East Anglia 5A Offshore-1 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| East Anglia 5A Onshore-1 | East Anglia 5A 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
Firth of Forth 2 Offshore Wind Farm | Offshore 66KV-4 | Offshore 275kV-4 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 66KV-5 | Offshore 275kV-5 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 66KV-6 | Offshore 275kV-6 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Onshore 275kV-2 | Onshore 400kV-2 | 2029 | Addition | TBC | TBC | TBC | 430 | 400/275
| Onshore 275kV-2 | Onshore 400kV-2 | 2029 | Addition | TBC | TBC | TBC | 430 | 400/275
| Onshore 275kV-2 | Onshore 400kV-2 | 2029 | Addition | TBC | TBC | TBC | 430 | 400/275
Hornsea 3 Offshore Wind Farm | Hornsea 3B-2 Offshore 66kV | Hornsea 3B-2 Offshore 500kV | 2029 | Addition | TBC | TBC | TBC | 850 | 500/66
Hornsea 4 Offshore Wind Farm | Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-3 | Offshore 66kV-5 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-3 | Offshore 66kV-6 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Onshore 400kV | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
| Onshore 400kV | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
| Onshore 400kV | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
| Offshore 275kV-4 | Offshore 66kV-7 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-4 | Offshore 66kV-8 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-5 | Offshore 66kV-9 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Offshore 275kV-5 | Offshore 66kV-10 | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| Onshore 400kV | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
| Onshore 400kV | Onshore 275kV | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
Racebank Extension Wind Farm | Offshore Platform 220kV-1 | Offshore Platform 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore Platform 220kV-2 | Offshore Platform 66kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Onshore 400 kV-1 | Onshore 220kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400 kV-2 | Onshore 220kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
Thanet Extension Wind Farm | Offshore-1 | Offshore-2 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| Offshore-1 | Offshore-2 | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| Onshore-1 | Onshore 400KV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
| Onshore-1 | Onshore 400KV | 2029 | Addition | TBC | TBC | TBC | TBC | TBC
West of Orkney Wind Farm | West of Orkney Offshore 275kV | West of Orkney Offshore 66kV | 2029 | Addition | TBC | TBC | TBC | 400/200/200 | 275/66/66
| West of Orkney Offshore 275kV | West of Orkney Offshore 66kV | 2029 | Addition | TBC | TBC | TBC | 400/200/200 | 275/66/66

## B-4-1a
B.4.1a - SHE Transmission Reactive Compensation Equipment for 2020/21
Site Name | Node | Unit Number | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
BEAULY | BEAU1J | 1 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU1K | 2 | 45 |  | Mechanically Switched Capacitor | 132
BEAULY | BEAU3U | 1 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU3V | 2 |  | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
CROSSAIG | CRSS3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3X | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 3 |  | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Z | 4 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT1- | 1 |  | 100 | Shunt Reactor | 132
KINTORE | KINT1- | 2 |  | 100 | Shunt Reactor | 132
KINTORE | KINT3W | 1 |  | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 2 |  | 60 | Shunt Reactor - SGT tertiary | 33
MACDUFF | MACD3- | 1 | 10 |  | Mechanically Switched Capacitor | 33
MELGARVE | MELG4J | 1 | 100 | 100 | STATCOM | 400
MELGARVE | MELG4K | 1 | 100 | 100 | STATCOM | 400
TEALING | TEAL1- | 1 |  | 100 | Shunt Reactor | 132
TEALING | TEAL1- | 1 | 90 |  | Mechanically Switched Capacitor | 132
TEALING | TEAL3W | 1 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 2 |  | 30 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275

## B-4-1b
B.4.1b - SPT Reactive Compensation Equipment 2020/21
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BONNYBRIDGE | BONN3U | 1 |  | 60 | Reactor | 33
BONNYBRIDGE | BONN3V | 2 |  | 60 | Reactor | 33
COALBURN | COAL3U | 1 |  | 60 | Reactor | 33
COCKENZIE | COCK2- | 1 | 230 |  | MSCDN | 275
CRYSTAL RIG | CRYR3V | 1 |  | 60 | Reactor | 33
CURRIE | CURR3W | 3 |  | 60 | Reactor | 33
DEWAR PLACE | DEWP3- | 1 |  | 60 | Reactor | 33
DEWAR PLACE | DEWP3- | 2 |  | 60 | Reactor | 33
ECCLES | ECCL3V | 1 |  | 60 | Reactor | 33
ELVANFOOT | ELVA4- | 1 | 225 |  | MSCDN | 400
ELVANFOOT | ELVA3V | 1 |  | 60 | Reactor | 33
HUNTERSTON NORTH | HUNN3W | 1 |  | 60 | Reactor | 33
HUNTERSTON NORTH | HUNN3X | 2 |  | 60 | Reactor | 33
KILLGALLIOCH WIND FARM | KILG2- | 1 |  | 60 | Reactor | 275
KILMARNOCK SOUTH | KILS3U | 4 |  | 60 | Reactor | 33
LONGANNET | LOAN2- | 1 | 230 |  | MSCDN | 275
LONGANNET | LOAN2- | 2 | 230 |  | MSCDN | 275
MARK HILL | MAHI3U | 2 |  | 60 | Reactor | 33
MOFFAT | MOFF4- | 1 | 230 |  | MSCDN | 400
MOFFAT | MOFF3U | 1 |  | 60 | Reactor | 33
NEILSTON | NEIL3U | 1 |  | 60 | Reactor | 33
NEILSTON | NEIL3V | 2 |  | 60 | Reactor | 33
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 33 | Sync Comp | 275
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 70 | STATCOM | 275
SMEATON | SMEA3U | 1 |  | 60 | Reactor | 33
SMEATON | SMEA3V | 1 |  | 60 | Reactor | 33
TORNESS | TORN4- | 1 |  | 150 | Reactor | 400
TORNESS | TORN4- | 2 |  | 150 | Reactor | 400
WINDYHILL | WIYH3W | 3 |  | 60 | Reactor | 33
WINDYHILL | WIYH2- | 1 | 150 |  | MSCDN | 275
WISHAW | WISH3W | 1 |  | 60 | Reactor | 33

## B-4-1c
B.4.1c - NGET Reactive Compensation Equipment for 2020/21
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
ABERTHAW | ABTH11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
ABERTHAW | ABTH11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
ABHAM | ABHA11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
ABHAM | ABHA11 | 3 | 45 |  | Mechanically Switched Capacitor | 132
BARKING | BARK21 | 2B WDG 1 |  | 30 | Reactor | 275
BARKING | BARK21 | 2B WDG 2 |  | 30 | Reactor | 275
BARKING | BARK21 | 4B WDG 1 |  | 30 | Reactor | 275
BARKING | BARK21 | 4B WDG 2 |  | 30 | Reactor | 275
BEDDINGTON | BEDD21 | 1B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 2B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 3B | 155 |  | Mechanically Switched Capacitor | 275
BEDDINGTON | BEDD21 | 3B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 4B | 155 |  | Mechanically Switched Capacitor | 275
BEDDINGTON | BEDD21 | 4B |  | 60 | Reactor | 275
BEDDINGTON | BEDD21 | 5B |  | 100 | Reactor | 275
BEDDINGTON | BEDD21 | 6A |  | 100 | Reactor | 275
BERKSWELL | BESW11 | 1 |  | 60 | Reactor | 132
BERKSWELL | BESW11 | 2 |  | 60 | Reactor | 132
BERKSWELL | BESW11 | 3 |  | 60 | Reactor | 132
BERKSWELL | BESW21 | 4 | 155 |  | Mechanically Switched Capacitor | 275
BIRKENHEAD | BIRK21 | 4 WDG A |  | 30 | Reactor | 275
BIRKENHEAD | BIRK21 | 4 WDG B |  | 30 | Reactor | 275
BISHOPS WOOD | BISW11 | A | 60 |  | Mechanically Switched Capacitor | 132
BISHOPS WOOD | BISW11 | B | 60 |  | Mechanically Switched Capacitor | 132
BISHOPS WOOD | BISW11 | C | 60 |  | Mechanically Switched Capacitor | 132
BLYTH | BLYT21 | 1 | 155 |  | Mechanically Switched Capacitor | 275
BLYTH | BLYT21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
BOLNEY | BOLN11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
BOLNEY | BOLN41 | 1 |  | 55 | Reactor | 400
BOLNEY | BOLN41 | 2 |  | 55 | Reactor | 400
BOLNEY | BOLN41 | 5 | 225 |  | Mechanically Switched Capacitor | 400
BOLNEY | BOLN41 | 6 | 100 | 225 | SVC | 400
BOLNEY | BOLN41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
BRADFORD WEST | BRAW21 | 3 |  | 60 | Reactor | 275
BRADFORD WEST | BRAW21 | 4 WDG A |  | 30 | Reactor | 275
BRADFORD WEST | BRAW21 | 4 WDG B |  | 30 | Reactor | 275
BRAMFORD | BRFO11 | A | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO11 | B | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO11 | C | 60 |  | Mechanically Switched Capacitor | 132
BRAMFORD | BRFO41 | 1 |  | 200 | Reactor | 400
BREDBURY | BRED21 | 1 WDG 1 |  | 30 | Reactor | 275
BREDBURY | BRED21 | 1 WDG 2 |  | 30 | Reactor | 275
BREDBURY | BRED21 | 3 WDG 1 |  | 30 | Reactor | 275
BREDBURY | BRED21 | 3 WDG 2 |  | 30 | Reactor | 275
BRIDGEWATER | BRWA11 | 1A | 45 |  | Mechanically Switched Capacitor | 132
BRIDGEWATER | BRWA11 | 1B | 45 |  | Mechanically Switched Capacitor | 132
BRIDGEWATER | BRWA2A | G | 60 | 60 | SVC | 275
BUSHBURY | BUSH11 | A | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH11 | B | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH11 | C | 60 |  | Mechanically Switched Capacitor | 132
BUSHBURY | BUSH21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
BUSHBURY | BUSH21 | 3 |  | 60 | Reactor | 275
BUSTLEHOLM | BUST21 | 4 | 20 |  | Mechanically Switched Capacitor | 275
BUSTLEHOLM | BUST21 | 4 |  | 60 | Reactor | 275
BUSTLEHOLM | BUST21 | 1 WDG A |  | 30 | Reactor | 275
BUSTLEHOLM | BUST21 | 1 WDG B |  | 30 | Reactor | 275
CANTERBURY | CANT41 | 4 |  | 200 | Reactor | 400
CAPENHURST | CAPE21 | 1 | 155 |  | Mechanically Switched Capacitor | 275
CELLARHEAD | CELL11 | 2A | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL11 | 2B | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL12 | 1 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL12 | 4 | 60 |  | Mechanically Switched Capacitor | 132
CELLARHEAD | CELL41 | 7 | 225 |  | Mechanically Switched Capacitor | 400
CELLARHEAD | CELL41 | 8 | 225 |  | Mechanically Switched Capacitor | 400
CELLARHEAD | CELL41 | 5 | 95 | 150 | SVC | 400
CELLARHEAD | CELL41 | 6 | 95 | 150 | SVC | 400
CELLARHEAD | CELL41 | 2 WDG A |  | 30 | Reactor | 400
CELLARHEAD | CELL41 | 2 WDG B |  | 30 | Reactor | 400
CELLARHEAD | CELL41 | 3 WDG A |  | 30 | Reactor | 400
CELLARHEAD | CELL41 | 3 WDG B |  | 30 | Reactor | 400
CHESTERFIELD | CHTE21 | 4 |  | 60 | Reactor | 275
CHICKERELL | CHIC41 | 2 |  | 60 | Reactor | 400
CHICKERELL | CHIC42 | 2 | 230 |  | Mechanically Switched Capacitor | 400
CILFYNYDD | CILF41 | 1 |  | 60 | Reactor | 400
CILFYNYDD | CILF41 | 2 |  | 60 | Reactor | 400
CILFYNYDD | CILF41 | 4 |  | 200 | Reactor | 400
CILFYNYDD | CILF41 | 6 |  | 200 | Reactor | 400
CITY ROAD | CITR41 | 2 | 55 |  | Mechanically Switched Capacitor | 400
CITY ROAD | CITR41 | 4 | 55 |  | Mechanically Switched Capacitor | 400
CITY ROAD | CITR41 | 1 |  | 200 | Reactor | 400
CONNAH'S QUAY | CONQ41 | 1 WDG 1 |  | 30 | Reactor | 400
CONNAH'S QUAY | CONQ41 | 1 WDG 2 |  | 30 | Reactor | 400
COVENTRY | COVE11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
COVENTRY | COVE21 | 3 |  | 60 | Reactor | 275
COVENTRY | COVE21 | A | 60 | 60 | SVC | 275
COWLEY | COWL11 | A | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL11 | B | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL11 | C | 60 |  | Mechanically Switched Capacitor | 132
COWLEY | COWL41 | 2 |  | 200 | Reactor | 400
COWLEY | COWL41 | 3 |  | 200 | Reactor | 400
DRAKELOW | DRAK41 | 3 | 230 |  | Mechanically Switched Capacitor | 400
DRAKELOW | DRAK41 | 4 |  | 200 | Reactor | 400
DRAKELOW | DRAK41 | 6 |  | 200 | Reactor | 400
DRAX | DRAX41 | 1 |  | 60 | Reactor | 400
DRAX | DRAX41 | 2 |  | 60 | Reactor | 400
EAST CLAYDON | ECLA12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
EAST CLAYDON | ECLA40 | 6 | 202 | 225 | SVC | 400
EAST CLAYDON | ECLA41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
EAST CLAYDON | ECLA41 | 7 | 230 |  | Mechanically Switched Capacitor | 400
EAST CLAYDON | ECLA41 | 1 WDG A |  | 30 | Reactor | 400
EAST CLAYDON | ECLA41 | 1 WDG B |  | 30 | Reactor | 400
EAST CLAYDON | ECLA41 | 2 WDG A |  | 30 | Reactor | 400
EAST CLAYDON | ECLA41 | 2 WDG B |  | 30 | Reactor | 400
ELLAND | ELLA21 | 2 |  | 60 | Reactor | 275
ELSTREE | ELST21 | M | 60 | 60 | SVC | 275
ELSTREE | ELST22 | L | 60 | 60 | SVC | 275
ELSTREE | ELST41 | 1 |  | 200 | Reactor | 400
ENDERBY | ENDE41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
ENDERBY | ENDE41 | 2 | 230 |  | Mechanically Switched Capacitor | 400
EXETER | EXET11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
EXETER | EXET41 | 1 | 25 |  | Mechanically Switched Capacitor | 400
EXETER | EXET41 | 2 | 25 |  | Mechanically Switched Capacitor | 400
EXETER | EXET41 | 3 | 95 | 150 | SVC | 400
EXETER | EXET41 | 5 | 95 | 150 | SVC | 400
FECKENHAM | FECK21 | 6 | 125 | 145 | SVC | 275
FECKENHAM | FECK41 | 4 WDG A |  | 30 | Reactor | 400
FECKENHAM | FECK41 | 4 WDG A |  | 30 | Reactor | 400
FECKENHAM | FECK41 | 4 WDG B |  | 30 | Reactor | 400
FECKENHAM | FECK41 | 4 WDG B |  | 30 | Reactor | 400
FLEET | FLEE11 | 2A | 50 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 2B | 50 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE11 | 2C | 50 |  | Mechanically Switched Capacitor | 132
FLEET | FLEE41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
FLEET | FLEE41 | 3A WDG 1 |  | 30 | Reactor | 400
FLEET | FLEE41 | 3A WDG 2 |  | 30 | Reactor | 400
FLEET | FLEE41 | 4A WDG 1 |  | 30 | Reactor | 400
FLEET | FLEE41 | 4A WDG 2 |  | 30 | Reactor | 400
GRAIN | GRAI41 | 1 |  | 200 | Reactor | 400
GRENDON | GREN11 | 1A | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN11 | 1B | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN11 | 1C | 60 |  | Mechanically Switched Capacitor | 132
GRENDON | GREN41 | 1 |  | 60 | Reactor | 400
GRENDON | GREN41 | 3 | 230 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN41 | 4 | 225 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
GRENDON | GREN41 | 6 | 225 |  | Mechanically Switched Capacitor | 400
GREYSTONES | GRSB21 | 1 |  | 100 | Reactor | 275
GREYSTONES | GRSB21 | 3 |  | 100 | Reactor | 275
HAMS HALL | HAMH40 | 2 | 230 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH40 | 3 | 230 |  | Mechanically Switched Capacitor | 400
HAMS HALL | HAMH41 | 4 |  | 200 | Reactor | 400
HARKER | HARK21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
HARKER | HARK21 | 7 | 125 | 145 | SVC | 275
HARKER | HARK22 | 8 | 125 | 145 | SVC | 275
HARKER | HARK41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
HARKER | HARK41 | 3A | 225 |  | Mechanically Switched Capacitor | 400
HARKER | HARK41 | 3B | 225 |  | Mechanically Switched Capacitor | 400
HURST | HURS21 | 2 |  | 60 | Reactor | 275
HURST | HURS21 | 3 |  | 60 | Reactor | 275
HURST | HURS21 | 4 |  | 100 | Reactor | 275
HURST | HURS21 | 7 |  | 100 | Reactor | 275
HURST | HURS21 | 1 |  | 100 | Reactor | 275
HURST | HURS21 | 2A |  | 100 | Reactor | 275
HURST | HURS21 | 2B | 155 |  | Mechanically Switched Capacitor | 275
HUTTON | HUTT41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
INDIAN QUEENS | INDQ11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
INDIAN QUEENS | INDQ41 | 2 |  | 200 | Reactor | 400
INDIAN QUEENS | INDQ41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
INDIAN QUEENS | INDQ41 | 1 |  | 60 | Reactor | 400
IRON ACTON | IROA21 | 6 | 45 |  | Mechanically Switched Capacitor | 132
IRON ACTON | IROA21 | E | 60 | 60 | SVC | 275
IRON ACTON | IROA21 | F | 60 | 60 | SVC | 275
IRONBRIDGE | IRON11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON12 | 2 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON12 | 3 | 60 |  | Mechanically Switched Capacitor | 132
IRONBRIDGE | IRON41 | 5 | 230 |  | Mechanically Switched Capacitor | 400
IVER | IVER21 | 1A |  | 60 | Reactor | 275
IVER | IVER21 | 3A |  | 60 | Reactor | 275
IVER | IVER4A | 6B |  | 55 | Reactor | 400
IVER | IVER4B | 5A |  | 55 | Reactor | 400
JORDANTHORPE | JORD21 | 2 |  | 60 | Reactor | 275
KEARSLEY | KEAR11 | A | 50 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | B | 50 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR11 | C | 50 |  | Mechanically Switched Capacitor | 132
KEARSLEY | KEAR41 | 3A |  | 60 | Reactor | 400
KINGSNORTH | KINO41 | 3 |  | 200 | Reactor | 400
KINGSNORTH | KINO41 | 4 |  | 200 | Reactor | 400
KINGSNORTH | KINO41 | 1 WDG 1 |  | 25 | Reactor | 400
KINGSNORTH | KINO41 | 1 WDG 2 |  | 25 | Reactor | 400
KINGSNORTH | KINO41 | 2 WDG 1 |  | 25 | Reactor | 400
KINGSNORTH | KINO41 | 2 WDG 2 |  | 25 | Reactor | 400
KIRKBY | KIBY41 | 1A | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY41 | 4A | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY42 | 2A | 45 |  | Mechanically Switched Capacitor | 132
KIRKBY | KIBY42 | 3B | 45 |  | Mechanically Switched Capacitor | 132
KIRKSTALL | KIRK21 | 2 |  | 60 | Reactor | 275
KIRKSTALL | KIRK21 | 4 |  | 60 | Reactor | 275
KIRKSTALL | KIRK21 | 3 | 150 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK21 | A | 20 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK21 | B | 20 |  | Mechanically Switched Capacitor | 275
LACKENBY | LACK21 | C | 20 |  | Mechanically Switched Capacitor | 275
LALEHAM | LALE21 | 1 |  | 100 | Reactor | 275
LALEHAM | LALE21 | 2 |  | 100 | Reactor | 275
LALEHAM | LALE21 | 3 |  | 100 | Reactor | 275
LANDULPH | LAND11 | 1 | 60 |  | Mechanically Switched Capacitor | 132
LANDULPH | LAND41 | 2 WDG A |  | 30 | Reactor | 400
LANDULPH | LAND41 | 2 WDG B |  | 30 | Reactor | 400
LANDULPH | LAND42 | 3 |  | 200 | Reactor | 400
LANDULPH | LAND42 | H | 60 | 60 | SVC | 400
LEGACY | LEGA41 | 1 |  | 60 | Reactor | 400
LEGACY | LEGA41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
LEGACY | LEGA41 | 2 |  | 60 | Reactor | 400
LISTER DRIVE | LISD21 | 1 |  | 100 | Reactor | 275
LOVEDEAN | LOVE41 | 2 | 230 |  | Mechanically Switched Capacitor | 400
LOVEDEAN | LOVE41 | 3 |  | 60 | Reactor | 400
LOVEDEAN | LOVE41 | 5 | 95 | 150 | SVC | 400
LOVEDEAN | LOVE41 | 7 |  | 200 | Reactor | 400
LOVEDEAN | LOVE41 | 1 |  | 200 | Reactor | 400
LOVEDEAN | LOVE41 | 4A |  | 60 | Reactor | 400
MANNINGTON | MANN11 | A | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | A | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | B | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | B | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | C | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN11 | C | 60 |  | Mechanically Switched Capacitor | 132
MANNINGTON | MANN41 | 1 | 95 | 150 | SVC | 400
MANNINGTON | MANN41 | 2 | 95 | 150 | SVC | 400
MELKSHAM | MELK11 | A | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK11 | B | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK11 | C | 60 |  | Mechanically Switched Capacitor | 132
MELKSHAM | MELK41 | 5 |  | 60 | Reactor | 400
MELKSHAM | MELK41 | 6 |  | 60 | Reactor | 400
MELKSHAM | MELK41 | 1 |  | 200 | Reactor | 400
MILL HILL | MILH21 | 1B WDNG 1 |  | 25 | Reactor | 275
MILL HILL | MILH21 | 1B WDNG 2 |  | 25 | Reactor | 275
MILL HILL | MILH21 | 2A WDNG 1 |  | 25 | Reactor | 275
MILL HILL | MILH21 | 2A WDNG 2 |  | 25 | Reactor | 275
MONK FRYSTON | MONF22 | 1 | 155 |  | Mechanically Switched Capacitor | 275
NECHELLS | NECH21 | WDG 1 |  | 30 | Reactor | 275
NECHELLS | NECH21 | A |  | 60 | Reactor | 275
NECHELLS | NECH21 | WDG 2 |  | 30 | Reactor | 275
NEWCROSS | NEWX21 | 5 |  | 100 | Reactor | 275
NEWCROSS | NEWX21 | 6 |  | 100 | Reactor | 275
NINFIELD | NINF41 | 1 |  | 200 | Reactor | 400
NINFIELD | NINF41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
NINFIELD | NINF41 | 5 | 100 | 225 | SVC | 400
NINFIELD | NINF41 | 6 | 150 | 200 | SVC | 400
NORWICH TROWSE | NORW11 | A | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW11 | B | 60 |  | Mechanically Switched Capacitor | 132
NORWICH TROWSE | NORW11 | C | 60 |  | Mechanically Switched Capacitor | 132
NURSLING | NURS41 | 2 |  | 60 | Reactor | 400
OCKER HILL | OCKH21 | 2 | 155 |  | Mechanically Switched Capacitor | 275
OLDBURY | OLDB21 | WDG A |  | 30 | Reactor | 275
OLDBURY | OLDB21 | WDG B |  | 30 | Reactor | 275
PELHAM | PELH41 | 3 |  | 200 | Reactor | 400
PELHAM | PELH41 | 5 | 120 | 150 | SVC | 400
PELHAM | PELH41 | 6 | 120 | 150 | SVC | 400
PELHAM | PELH41 | 1 WDG A |  | 25 | Reactor | 400
PELHAM | PELH41 | 1 WDG B |  | 25 | Reactor | 400
PELHAM | PELH41 | 2 WDG A |  | 25 | Reactor | 400
PELHAM | PELH41 | 2 WDG B |  | 25 | Reactor | 400
PEMBROKE | PEMB41 | 1 |  | 60 | Reactor | 400
PEMBROKE | PEMB41 | 2 |  | 60 | Reactor | 400
PENN | PENN21 | B | 60 | 60 | SVC | 275
PENTIR | PENT41 | 2 |  | 200 | Reactor | 400
PENTIR | PENT41 | 5 |  | 200 | Reactor | 400
PENWORTHAM | PEWO41 | 6 |  | 60 | Reactor | 400
PITSMOOR | PITS21 | 3 |  | 60 | Reactor | 275
PITSMOOR | PITS21 | 4 |  | 60 | Reactor | 275
PORT HAM | PORH11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
PORT HAM | PORH11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
PYLE | PYLE21 | J | 60 | 60 | SVC | 275
PYLE | PYLE21 | K | 60 | 60 | SVC | 275
RAINHILL | RAIN11 | 2 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN11 | 4 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN12 | 1 | 45 |  | Mechanically Switched Capacitor | 132
RAINHILL | RAIN12 | 3 | 45 |  | Mechanically Switched Capacitor | 132
RATCLIFFE-ON-SOAR | RATS41 | 2 |  | 200 | Reactor | 400
RATCLIFFE-ON-SOAR | RATS41 | 3 |  | 60 | Reactor | 400
RAYLEIGH | RAYL41 | 5 |  | 60 | Reactor | 400
RICHBOROUGH | RICH41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
RICHBOROUGH | RICH41 | 1 | 225 | 100 | SVC | 400
ROCHDALE | ROCH11 | A | 60 |  | Mechanically Switched Capacitor | 132
ROCHDALE | ROCH11 | B | 60 |  | Mechanically Switched Capacitor | 132
ROCHDALE | ROCH11 | C | 60 |  | Mechanically Switched Capacitor | 132
SELLINDGE | SELL41 | 1 | 155 | 200 | SVC | 400
SELLINDGE | SELL41 | 2 | 155 | 200 | SVC | 400
SKELTON GRANGE | SKLG11 | 2 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG11 | 3 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG11 | 4 | 60 |  | Mechanically Switched Capacitor | 132
SKELTON GRANGE | SKLG21 | 3 |  | 100 | Reactor | 275
SKELTON GRANGE | SKLG21 | 6 | 150 |  | Mechanically Switched Capacitor | 275
SPENNYMOOR | SPEN41 | 1 |  | 60 | Reactor | 400
ST JOHNS WOOD | SJOW12 | A | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW12 | B | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW12 | C | 60 |  | Mechanically Switched Capacitor | 132
ST JOHNS WOOD | SJOW21 | 1 | 144 | 150 | SVC | 275
ST JOHNS WOOD | SJOW21 | 2B |  | 55 | Reactor | 275
ST JOHNS WOOD | SJOW21 | 3 | 144 | 150 | SVC | 275
ST JOHNS WOOD | SJOW41 | 2 |  | 200 | Reactor | 400
ST JOHNS WOOD | SJOW41 | 4 |  | 200 | Reactor | 400
ST JOHNS WOOD | SJOW41 | 1 |  | 200 | Reactor | 400
STAYTHORPE | STAY41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
STELLA WEST | STEW21 | 2 |  | 100 | Reactor | 275
STELLA WEST | STEW41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
STELLA WEST | STEW41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND41 | 1 | 230 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND41 | 5 WDG 1 |  | 30 | Reactor | 400
SUNDON | SUND41 | 5 WDG 2 |  | 30 | Reactor | 400
SUNDON | SUND42 | 2 | 230 |  | Mechanically Switched Capacitor | 400
SUNDON | SUND42 | 8 WDG 1 |  | 30 | Reactor | 400
SUNDON | SUND42 | 8 WDG 2 |  | 30 | Reactor | 400
SWANSEA | SWAN11 | A | 60 |  | Mechanically Switched Capacitor | 132
SWANSEA | SWAN11 | B | 60 |  | Mechanically Switched Capacitor | 132
SWANSEA | SWAN11 | C | 60 |  | Mechanically Switched Capacitor | 132
THORPE MARSH | THOM41 | 2 |  | 200 | Reactor | 400
THORPE MARSH | THOM42 | 6 |  | 200 | Reactor | 400
TOTTENHAM | TOTT21 | 5 |  | 100 | Reactor | 275
TOTTENHAM | TOTT23 | 1 |  | 100 | Reactor | 275
TOTTENHAM | TOTT24 | 3 |  | 100 | Reactor | 275
TYNEMOUTH | TYNE21 | 2A |  | 60 | Reactor | 275
USKMOUTH | USKM11 | 1 | 45 |  | Mechanically Switched Capacitor | 132
WALHAM | WALH41 | 1 | 60 |  | Mechanically Switched Capacitor | 400
WALHAM | WALH41 | 2 |  | 60 | Reactor | 400
WALHAM | WALH41 | 3 |  | 60 | Reactor | 400
WALHAM | WALH41 | 4 |  | 220 | Reactor | 400
WALPOLE | WALP11 | 4A | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 4C | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP11 | 4B | 60 |  | Mechanically Switched Capacitor | 132
WALPOLE | WALP41 | 3 |  | 55 | Reactor | 400
WALPOLE | WALP41 | 1 |  | 55 | Reactor | 400
WALPOLE | WALP41 | 2 |  | 55 | Reactor | 400
WARLEY | WARL11 | B | 50 |  | Mechanically Switched Capacitor | 132
WARLEY | WARL11 | A | 50 |  | Mechanically Switched Capacitor | 132
WARLEY | WARL11 | C | 50 |  | Mechanically Switched Capacitor | 132
WEST BURTON | WBUR42 | 1 |  | 200 | Reactor | 400
WEST HAM | WHAM41 | 4 | 230 |  | Mechanically Switched Capacitor | 400
WEST HAM | WHAM41 | 1 |  | 200 | Reactor | 400
WEST MELTON | WMEL12 | 3A | 45 |  | Mechanically Switched Capacitor | 132
WEST MELTON | WMEL12 | 3B | 45 |  | Mechanically Switched Capacitor | 132
WEST MELTON | WMEL12 | 3C | 45 |  | Mechanically Switched Capacitor | 132
WEST WEYBRIDGE | WWEY41 | 1 |  | 100 | Reactor | 400
WHITEGATE | WHGA20 | 4A |  | 60 | Reactor | 275
WHITEGATE | WHGA20 | 4B |  | 60 | Reactor | 275
WHITEGATE | WHGA21 | 2 | 150 |  | Mechanically Switched Capacitor | 275
WILLESDEN | WISD21 | 2B |  | 55 | Reactor | 275
WILLESDEN | WISD21 | 3B WDG 1 |  | 25 | Reactor | 275
WILLESDEN | WISD21 | 3B WDG 2 |  | 25 | Reactor | 275
WILLINGTON | WILE41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WILLINGTON | WILE41 | 8 | 95 | 150 | SVC | 400
WIMBLEDON | WIMB21 | 2 |  | 100 | Reactor | 275
WIMBLEDON | WIMB21 | 4 |  | 100 | Reactor | 275
WIMBLEDON | WIMB41 | 5 |  | 200 | Reactor | 400
WIMBLEDON | WIMB41 | 6 |  | 225 | Reactor | 400
WYMONDLEY | WYMO41 | 3 |  | 200 | Reactor | 400
WYMONDLEY | WYMO41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
WYMONDLEY | WYMO41 | 2 | 230 |  | Mechanically Switched Capacitor | 400

## B-4-1d
B.4.1d - OFTO Reactive Compensation Equipment for 2020/21
OFTO | Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Tapping
Hornsea One Limited | Hornsea 1 Wind Farm | HOWA41 | SHR3 |  | 75 | Shunt Reactor | 400
|  | HOWA41 | SHR4 |  | 75 | Shunt Reactor | 400
|  | HOWA21 | VSR-1 |  | 300 | Shunt Reactor | 220 | 120-300
|  | HOWA21 | VSR-2 |  | 300 | Shunt Reactor | 220 | 120-300
|  | HOWR2A | SHR1 |  | 220 | Shunt Reactor | 220
|  | HOWR2A | SHR2 |  | 220 | Shunt Reactor | 220
|  | HOWW21 | SHR1 |  | 85 | Shunt Reactor | 220
|  | HOWW22 | SHR1 |  | 105 | Shunt Reactor | 220
|  | HOWA21 | SVC1 | 160 | 200 | SVC | 220
|  | HOWA21 | SVC2 | 160 | 200 | SVC | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | SHR1 |  | 28.2 | Shunt Reactor | 132
|  | HUMO12 | SHR2 |  | 28.2 | Shunt Reactor | 132
|  | HUMO31 | MSR1A |  | 28 | Shunt Reactor | 33
|  | HUMO32 | MSR1B |  | 28 | Shunt Reactor | 33
|  | HUMO31 | MSR2A |  | 28 | Shunt Reactor | 33
|  | HUMO32 | MSR2B |  | 28 | Shunt Reactor | 33
|  | HUMO31 | SVC1 | 24 | 24 | SVC | 33
|  | HUMO32 | SVC2 | 24 | 24 | SVC | 33
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | 1 |  | 24 | Shunt Reactor | 132
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | 1 |  | 60 | Shunt Reactor | 400
|  | BBWO21 | 1 |  | 125 | Shunt Reactor | 220 | 50-125
|  | BBWO41 | SVC1 | 50 | 50 | SVC | 15.5
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDO11 | SHR1 |  | 85 | Shunt Reactor | 132
|  | DUDO11 | SHR2 |  | 85 | Shunt Reactor | 132
|  | DUDO31 | SVC1 | 125 | 125 | SVC | 33
|  | DUDO32 | SVC2 | 125 | 125 | SVC | 33
East Anglia One Limited | East Anglia Offshore Wind Farm | EAAW21 | SH1 |  | 174 | Shunt Reactor | 220
|  | EAAW21 | SH2 |  | 174 | Shunt Reactor | 220
|  | BRST21 | VSR-1 |  | 228 | Shunt Reactor | 220 | 114-228
|  | BRST21 | VSR-2 |  | 228 | Shunt Reactor | 220 | 114-228
|  | BRST41 | SVC1 | 215 | 215 | SVC | 34.5
|  | BRST41 | SVC2 | 215 | 215 | SVC | 34.5
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | SVC1 | 70 | 70 | SVC | 132
|  | GALO12 | SVC2 | 70 | 70 | SVC | 132
|  | GALO11 | MSR 05 |  | 85 | Shunt Reactor | 132
|  | GALO12 | MSR 06 |  | 85 | Shunt Reactor | 132
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO31 | SR1 |  | 35 | Shunt Reactor | 33
|  | ORMO31 | SR2 |  | 35 | Shunt Reactor | 33
|  | ORMO31 | SVC 1 | 28 | 28 | SVC | 33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SALL11 | 1 |  | 60 | Shunt Reactor | 132 | 30-60
|  | SALL12 | 2 |  | 60 | Shunt Reactor | 132 | 30-60
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO21 | SHR2 |  | 172 | Shunt Reactor | 220
|  | TKNW21 | SHR4 |  | 43 | Shunt Reactor | 220
|  | TKNO31 | MSR2B |  | 163 | Shunt Reactor | 33
|  | TKNO31 | MSR2C |  | 163 | Shunt Reactor | 33
|  | TKNO31 | SVC2A | 143 | 143 | SVC | 33
Diamond Transmission Partners Walney Extension Limited | Walney Extension Wind Farm | WOWE41 | SHR1 |  | 62 | Shunt Reactor | 400
|  | WOWE21 | VSR-1 |  | 250 | Shunt Reactor | 220 | 125-250
|  | WACW21 | SHR1 |  | 90 | Shunt Reactor | 220
|  | WOWE21 | SVC1 | 70 | 70 | SVC | 220
|  | WOWE42 | SHR2 |  | 62 | Shunt Reactor | 400
|  | WOWE22 | VSR-2 |  | 250 | Shunt Reactor | 220 | 125-250
|  | WADW21 | SHR2 |  | 90 | Shunt Reactor | 220
|  | WOWE22 | SVC2 | 70 | 70 | SVC | 220
WoDS Transmission plc | West of Duddon Sands | WDSO41 | SR1 |  | 30 | Shunt Reactor | 13.9
|  | WDSO42 | SR2 |  | 30 | Shunt Reactor | 13.9
|  | WDSO11 | SR3 |  | 60 | Shunt Reactor | 155
|  | WDSO12 | SR4 |  | 60 | Shunt Reactor | 155
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO31 | Statcom1 | 25 | 25 | SVC | 33
|  | WERO31 | Statcom2 | 25 | 25 | SVC | 33
|  | WERO31 | 1 |  | 50 | Shunt Reactor | 33
Greater Gabbard Offshore Winds Ltd | Greater Gabbard Offshore Wind Farm | GGON51 | 1 | 55 |  | MSC | 13.9(secondary)
|  | GGON52 | 1 | 55 |  | MSC | 13.9(secondary)
|  | GGON53 | 1 | 55 |  | MSC | 13.9(secondary)
|  | GGON51 | 1 |  | 43 | MSR | 13.9(secondary)
|  | GGON52 | 1 |  | 43 | MSR | 13.9(secondary)
|  | GGON53 | 1 |  | 43 | MSR | 13.9(secondary)
|  | GANW3A | 1 |  | 30 | Shunt Reactor | 33
|  | GANW3B | 1 |  | 30 | Shunt Reactor | 33
|  | GGON51 | 1 | 50 | 50 | SVC | 13.9(secondary)
|  | GGON52 | 2 | 50 | 50 | SVC | 13.9(secondary)
|  | GGON53 | 3 | 50 | 50 | SVC | 13.9(secondary)
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | SVC PLUS 1A | 52 | 52 | SVC | 13.9(tertiary)
|  | LONO42 | SVC PLUS 2A | 52 | 52 | SVC | 13.9(tertiary)
|  | LONO43 | SVC PLUS 1B | 52 | 52 | SVC | 13.9(tertiary)
|  | LONO44 | SVC PLUS 2B | 52 | 52 | SVC | 13.9(tertiary)
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | GWYO11 | SVC-1 | 95 | 95 | SVC | 13.9(tertiary)
|  | GWYO12 | SVC-2 | 95 | 95 | SVC | 13.9(tertiary)
|  | GWYO11 | MSR1A |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO11 | MSR1B |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO12 | MSR2A |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO12 | MSR2B |  | 60 | Shunt Reactor | 13.9(tertiary)
|  | GWYO11 | MSC1A |  | 30 | MSC | 13.9(tertiary)
|  | GWYO11 | MSC1B |  | 30 | MSC | 13.9(tertiary)
|  | GWYO12 | MSC2A |  | 30 | MSC | 13.9(tertiary)
|  | GWYO12 | MSC2B |  | 30 | MSC | 13.9(tertiary)
TC Beatrice OFTO Limited | Beatrice offshore Windfarm | BEAT21 | SHR1 |  | 115 | Shunt Reactor | 220
|  | BEAT22 | SHR2 |  | 115 | Shunt Reactor | 220
|  | BEAT21 | SHR3 |  | 115 | Shunt Reactor | 220
|  | BEAT22 | SHR4 |  | 115 | Shunt Reactor | 220
|  | BEAT41 | SVC1 | 144 | 155 | SVC | 33 (Tertiary)
|  | BEAT42 | SVC2 | 144 | 155 | SVC | 33 (Tertiary)
TC Lincs OFTO Limited | Lincs Wind Farm | LINO41 | MSC3 | 31.15 |  | MSC | 13.9(Tertiary)
|  | LINO42 | MSC5 | 31.15 |  | MSC | 13.9(Tertiary)
|  | LINO43 | MSR2 |  | 60 | Shunt Reactor | 13.9(Tertiary)
|  | LINO44 | MSR4 |  | 60 | Shunt Reactor | 13.9(Tertiary)
|  | LINO45 | SVC Plus 1 | 94 | 139 | SVC | 13.9(Tertiary)
|  | LINO11 | SR1 |  | 46 | Shunt Reactor | 132 | 1 to 7
|  | LINO11 | SR2 |  | 46 | Shunt Reactor | 132 | 1 to 7
|  | LINS31 | SR1 |  | 40 | Shunt Reactor | 33
|  | LINS32 | SR2 |  | 40 | Shunt Reactor | 33
Diamond Transmission Partners RB Limited | Race Bank Offshore windfarm | RACO21 | VSR1 |  | 200 | Variable Shunt Reactor | 220 | 120-200
|  | RACO22 | VSR2 |  | 200 | Variable Shunt Reactor | 220 | 120-200
|  | RACW21 | SR1 |  | 90 | Shunt Reactor | 220
|  | RACW22 | SR2 |  | 90 | Shunt Reactor | 220
|  | RACO21 | STATCOM1 | 120 | 120 | SVC | 28 (Secondary)
|  | RACO22 | STATCOM1 | 120 | 120 | SVC | 28(Secondary)
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | Reactor 1/2/3 |  | 18 | Shunt Reactor | 33 (Secondary)
|  | RORE11 | Capacitor 1/2 | 12 |  | MSC | 33 (Secondary)
| Robin Rigg West Offshore Wind Farm | RORW11 | Reactor 1/2/3 |  | 18 | Shunt Reactor | 33 (Secondary)
|  | RORW11 | Capacitor 1/2 | 12 |  | MSC | 33 (Secondary)
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | TWNE41 | SVC1 | 65 | 65 | SVC | 33 (tertiary)
|  | TWNE42 | SVC2 | 65 | 65 | SVC | 33 (tertiary)
|  | TWNE11 | SHR1 |  | 64 | Shunt Reactor | 150
|  | TWNE12 | SHR2 |  | 64 | Shunt Reactor | 150
|  | TWNE31 | TSR1 |  | 46 | TSR | 33
|  | TWNE32 | TSR2 |  |  | TSR | 33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | SVC 1 | 49.3 | 49.3 | SVC | 132
|  | THAW12 | SVC 2 | 49.3 | 49.3 | SVC | 132
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO1A | RCT1 |  | 64 | Shunt Reactor | 132
Blue Transmission Walney 2 OFTO | Walney 2 Offshore Wind Farm | WABO1A | RCT1 |  | 80 | Shunt Reactor | 132 | 1 to 31

## B-4-2a
B.4.2a - SHE Transmission Reactive Compensation Equipment changes for 2021/22 to 2029/30
Site Name | Node | Unit Number | Year | Status | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ALYTH | ALYT2A | 1 | 2024 | Addition | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | ALYT2A | 1 | 2024 | Addition | 225 | 225 | SVC | 275
KINARDOCHY | KINA2K | 1 | 2024 | Addition | 100 |  | Mechanically Switched Capacitor | 275
KINARDOCHY | KINA2J | 1 | 2024 | Addition | 225 | 225 | SVC | 275
ALYTH | ALYT2A | 1 | 2026 | Remove | 100 |  | Mechanically Switched Capacitor | 275
ALYTH | ALYT4J | 1 | 2026 | Addition | 100 |  | Mechanically Switched Capacitor | 400
DOUNREAY | DOUN3Y | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
DOUNREAY | DOUN3Z | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
ORKNEY FINSTOWN | FINS3Y | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
ORKNEY FINSTOWN | FINS3Z | 1 | 2026 | Addition |  | 90 | Shunt Reactor | 33
ALYTH | ALYT2A | 1 | 2026 | Remove | 225 | 225 | SVC | 275
ALYTH | ALYT4J | 1 | 2026 | Addition | 225 | 225 | SVC | 400
ORKNEY FINSTOWN | FINS1- | 1 | 2026 | Addition | 70 | 35 | Synchronous Condenser | 132
ORKNEY FINSTOWN | FINS1- | 2 | 2026 | Addition | 70 | 35 | Synchronous Condenser | 132

## B-4-2b
B.4.2b - SPT Reactive Compensation Equipment 2021/22 to 2029/30
Site Name | Change Type | Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
COALBURN | Addition | 2024 | COAL3V | 2 |  | 60 | Reactor | 33
GRETNA | Addition | 2024 | GRNA3U | 1 |  | 60 | Reactor | 33
STRATHAVEN | Addition | 2024 | STHA3U | 3 |  | 60 | Reactor | 33
STRATHAVEN | Addition | 2024 | STHA3V | 4 |  | 60 | Reactor | 33
MARK HILL | Addition | 2024 | MAHI1- | 1 | 75 | 75 | STATCOM | 132
HUNTERSTON | Addition | 2024 | HUER4- | 1 |  | 200 | Reactor | 400
HUNTERSTON SYNCH COMP | Addition | 2026 | HUER4- | 1 | 300 | 140 | Sync Comp | 400
KINCARDINE SYNCH COMP | Addition | 2026 | KINC2- | 1 | 300 | 140 | Sync Comp | 275
STRATHAVEN SYNCH COMP | Addition | 2026 | STHA4A | 1 | 150 | 70 | Sync Comp | 400
STRATHAVEN SYNCH COMP | Addition | 2026 | STHA4B | 1 | 150 | 70 | Sync Comp | 400
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4A | 1 | 150 | 70 | Sync Comp | 275
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4A | 1 | 150 | 150 | STATCOM | 275
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4B | 1 | 150 | 70 | Sync Comp | 275
ECCLES HYBRID REACTIVE COMPENSATION | Addition | 2026 | ECCL4B | 1 | 150 | 150 | STATCOM | 275

## B-4-2c
B.4.2c - NGET Reactive Compensation Equipment 2021/22 to 2029/30
Site Name | Change Type | Commissioning Year | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
BURWELL | Addition | 2022 | BURW41 | 1 | 225 |  | Mechanically Switched Capacitor | 400
BURWELL | Addition | 2022 | BURW41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
BOLNEY | Addition | 2024 | BOLN41 | 8 | 225 |  | Mechanically Switched Capacitor | 400
BOLNEY | Addition | 2024 | BOLN41 | 1 | 65 |  | Mechanically Switched Capacitor | 400
BOLNEY | Addition | 2024 | BOLN41 | 9 | 225 | 100 | SVC | 400
BRIDGEWATER | Remove | 2024 | BRWA2A | G | 60 | 60 | SVC | 275
NINEFIELD | Addition | 2024 | NINF41 | 2 | 225 |  | Mechanically Switched Capacitor | 400
NINEFIELD | Addition | 2024 | NINF41 | 1 | 65 |  | Mechanically Switched Capacitor | 400
NINFIELD | Addition | 2024 | NINF41 | 9 | 225 | 100 | SVC | 400
PENTIR | Remove | 2024 | PENT41 | 1 |  | 200 | Reactor | 400
Sandford | Addition | 2024 | SAFO41 | 1 |  | 200 | Shunt Reactor | 400
Sandford | Addition | 2024 | SAFO41 | 2 |  | 200 | Shunt Reactor | 400
WIMBLEDON | Remove | 2024 | WIMB21 | 2 |  | 100 | Reactor | 275
WIMBLEDON | Remove | 2024 | WIMB21 | 4 |  | 100 | Reactor | 275
BRAINTREE | Addition | 2029 | BRAI11 | 1 |  | 200 | Reactor | 132
BRAINTREE | Addition | 2029 | BRAI11 | 2 |  | 200 | Reactor | 132

## B-4-2d
B.4.2d - OFTO Reactive Compensation Equipment, 2021/22 to 2029/30
Wind Farm | Year | Status | Node 1 | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage(kV)
Firth of Forth 1 Offshore Wind Farm | 2021 | Addition | FOFW21 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFW22 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFW23 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO21 | SHR1 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO21 | SHR2 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO21 | SHR3 |  | TBC | Shunt Reactor | 275
| 2021 | Addition | FOFO31 | SVC1 | TBC | TBC | SVC | 33
| 2021 | Addition | FOFO32 | SVC2 | TBC | TBC | SVC | 33
Hornsea 1 offshore Wind Farm | 2021 | Addition | HOWA21 | VSR-3 |  | 300 | Shunt Reactor | 220
| 2021 | Addition | HOWR2A | SHR3 |  | 220 | Shunt Reactor | 220
| 2021 | Addition | HOWW23 | SHR1 |  | 135 | Shunt Reactor | 220
| 2021 | Addition | HOWA21 | SVC3 | 160 | 200 | SVC | 33
Moray East Offshore Wind Farm | 2021 | Addition | MOWE21 | SHR1 |  | 75 | Shunt Reactor | 220
| 2021 | Addition | MOWE22 | SHR1 |  | 75 | Shunt Reactor | 220
| 2021 | Addition | MOWE23 | SHR1 |  | 75 | Shunt Reactor | 220
| 2021 | Addition | MORF21 | SHR1A |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF21 | SHR1B |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF22 | SHR2A |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF22 | SHR2B |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF23 | SHR3A |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF23 | SHR3B |  | 110 | Shunt Reactor | 220
| 2021 | Addition | MORF31 | MSR1 |  | 133 | Shunt Reactor | 33
| 2021 | Addition | MORF31 | SVC1 | 174 | 197 | SVC | 33
| 2021 | Addition | MORF32 | MSR2 |  | 133 | Shunt Reactor | 33
| 2021 | Addition | MORF32 | SVC2 | 174 | 197 | SVC | 33
| 2021 | Addition | MORF33 | MSR3 |  | 133 | Shunt Reactor | 33
| 2021 | Addition | MORF33 | SVC3 | 174 | 197 | SVC | 33
Triton Knoll Offshore Wind Farm | 2021 | Addition | TKNO21 | SHR1 |  | 172 | Shunt Reactor | 220
| 2021 | Addition | TKNE21 | SHR3 |  | 43 | Shunt Reactor | 220
| 2021 | Addition | TKNO32 | SVC1A | 143 | 143 | SVC | 33
| 2021 | Addition | TKNO32 | MSR1B |  | 163 | Shunt Reactor | 33
| 2021 | Addition | TKNO32 | MSR1C |  | 163 | Shunt Reactor | 33
Inch Cape Offshore Wind Farm | 2022 | Addition | INCO21 | TBC | TBC | TBC | SVC | LV-Tertiary
| 2022 | Addition | INCO22 | TBC | TBC | TBC | SVC | LV-Tertiary
| 2022 | Addition | INCW21 | TBC | TBC | TBC | SHR | 220
| 2022 | Addition | INCW22 | TBC | TBC | TBC | SHR | 220
| 2022 | Addition | INCO21 | TBC | TBC | TBC | SHR | 220
| 2022 | Addition | INCO22 | TBC | TBC | TBC | SHR | 220
Neart Na Gaoithe Offshore Wind Farm | 2022 | Addition | NNGW21 | 1 |  | 125 | SHR1 | 220
| 2022 | Addition | NNGW22 | 1 |  | 125 | SHR1 | 220
| 2022 | Addition | NNGO41 | TBC | 75 | 75 | SVC | 33(Tertiary)
| 2022 | Addition | NNGO42 | TBC | 75 | 75 | SVC | 33(Tertiary)
Firth of Forth 1 Offshore Wind Farm | 2024 | Addition | FOFO33 | SVC3 | TBC | TBC | SVC | 33
Dogger bank 1 offshore Wind Farm | 2024 | Addition | Dogger bank 1 Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Dogger bank 1 Offshore | TBC | TBC | TBC | SVC | TBC
Doggerbank 4 Offshore wind Farm | 2024 | Addition | Doggerbank 4 Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Doggerbank 4 Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Doggerbank 4 Onshore 400kV | 1 | TBC | TBC | SVC | 400
| 2024 | Addition | Doggerbank 4 Onshore 400kV | 2 |  | TBC | Shunt Reactor | 400
East Anglia 3 Offshore Wind Farm | 2024 | Addition | East Anglia Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | East Anglia Offshore | TBC | TBC | TBC | SVC | TBC
Hornsea 2 Offshore Wind Farm | 2024 | Addition | Hornsea 2 Onshore 400kV | 3 |  | 85 | SHR | 400
| 2024 | Addition | Hornsea 2 Onshore 400kV | 4 |  | 85 | SHR | 400
| 2024 | Addition | Hornsea 2A Offshore 220kV | 1 |  | 90 | SHR1 | 220
| 2024 | Addition | Hornsea 2B Offshore 220kV | 2 |  | 90 | SHR2 | 220
| 2024 | Addition | Hornsea 2C Offshore 220kV | 3 |  | 90 | SHR3 | 220
| 2024 | Addition | Hornsea 2A Reactve Comp Station | 1 |  | 170 | SHR | 220
| 2024 | Addition | Hornsea 2B Reactve Comp Station | 2 |  | 170 | SHR | 220
| 2024 | Addition | Hornsea 2C Reactve Comp Station | 3 |  | 170 | SHR | 220
| 2024 | Addition | Hornsea 2 Onshore 220kV | 1 | 240 | 240 | SVC1 | 220
| 2024 | Addition | Hornsea 2 Onshore 220kV | 2 | 240 | 240 | SVC2 | 220
| 2024 | Addition | Hornsea 2 Onshore 220kV | 3 | 240 | 240 | SVC3 | 220
| 2024 | Addition | Hornsea 2 Onshore 220kV | 1 |  | 300 | VSR1 | 220
| 2024 | Addition | Hornsea 2 Onshore 220kV | 1 |  | 300 | VSR2 | 220
| 2024 | Addition | Hornsea 2 Onshore 220kV | 1 |  | 300 | VSR3 | 220
Hornsea 3 Offshore Wind Farm | 2024 | Addition | Hornsea 3A Onshore 400kV | 1 | TBC | TBC | Shunt Reactor | TBC
| 2024 | Addition | Hornsea 3A Onshore 400kV | 1 | TBC | TBC | SVC | TBC
Moray West Offshore Wind Farm | 2024 | Addition | Moray West Offshore P1 220kV | TBC | TBC | TBC | SHR | 220
| 2024 | Addition | Moray West Offshore P2 220kV | TBC | TBC | TBC | SHR | 220
Sofia Offshore Wind Farm | 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SHR | TBC
| 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SHR | TBC
| 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SVC | TBC
| 2024 | Addition | Sofia Offshore | TBC | TBC | TBC | SVC | TBC
Dogger Bank 2 Offshore Wind Farm | 2026 | Addition | Onshore 400kV | 1 | TBC | TBC | SVC | 400
| 2026 | Addition | Onshore 400kV | 2 | TBC | TBC | SVC | 400
East Anglia 6A Offshore Wind Farm | 2026 | Addition | East Anglia 6A Onshore-1 | 1 | TBC | TBC | SVC | 400
East Anglia 6B Offshore Wind Farm | 2026 | Addition | East Anglia 6A Onshore-1 | 1 | TBC | TBC | SVC | 400
Firth of Forth 2 Offshore Wind Farm | 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 2 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 3 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 2 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 3 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 4 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 5 | TBC | TBC | Shunt Reactor | 400
| 2026 | Addition | Onshore 400kV-1 | 6 | TBC | TBC | Shunt Reactor | 400
Hornsea 3 Offshore Wind Farm | 2026 | Addition | Hornsea 3B Onshore 400kV | 1 | TBC | TBC | Shunt Reactor | TBC
| 2026 | Addition | Hornsea 3B Onshore 400kV | 1 | TBC | TBC | SVC | TBC
Sheringham and Dudgeon Extension Wind Farm | 2026 | Addition | Offshore 220kV-1 | 1 | TBC | TBC | Shunt Reactor | 220
| 2026 | Addition | Offshore 220kV-2 | 2 | TBC | TBC | Shunt Reactor | 220
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | Shunt Reactor | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-2 | 1 | TBC | TBC | Shunt Reactor | Tertiary Voltage
| 2026 | Addition | Onshore 400kV-1 | 1 | TBC | TBC | SVC | Tertiary Voltage
Codling Wind Farm | 2029 | 2029 | Codling Offshore 220kV | TBC |  | 243 | SHR | 220
| 2029 | 2029 | Codling Offshore 220kV | TBC |  | 243 | SHR | 220
| 2029 | 2029 | Codling Onshore 220kV | TBC |  | 650 | SHR | 220
| 2029 | 2029 | Codling Onshore 220kV | TBC |  | 450 | TCR | 220
EA One North Wind Farm | 2029 | 2029 | EA1N Offshore 220kV-1 | 1 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Offshore 220kV-2 | 2 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Onshore 220kV | 1 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Onshore 220kV | 2 |  | TBC | Shunt Reactor | 220
| 2029 | 2029 | EA1N Onshore 400kV | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | 2029 | EA1N Onshore 400kV | 2 | TBC | TBC | SVC | Tertiary Voltage
East Anglia 4A Wind Farm | 2029 | 2029 | East Anglia 4A 400kV | 1 | TBC | TBC | SVC | 400
| 2029 | 2029 | East Anglia 4A 400kV | 1 |  | TBC | Shunt Reactor | 400
East Anglia 5A Wind Farm | 2029 | 2029 | East Anglia 5A 400kV | 1 | TBC | TBC | SVC | 400
| 2029 | 2029 | East Anglia 5A 400kV | 1 |  | TBC | Shunt Reactor | 400
Firth of Forth 2 Wind Farm | 2029 | Addition | Onshore 400kV-2 | 1 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | Addition | Onshore 400kV-2 | 2 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | Addition | Onshore 400kV-2 | 3 | TBC | TBC | SVC | Tertiary Voltage
| 2029 | Addition | Onshore 400kV-2 | 1 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 2 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 3 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 4 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 5 | TBC | TBC | Shunt Reactor | 400
| 2029 | Addition | Onshore 400kV-2 | 6 | TBC | TBC | Shunt Reactor | 400
Hornsea 4 Offshore Wind Farm | 2029 | 2029 | Offshore 275kV-1 | 1 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Offshore 275kV-2 | 2 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Offshore 275kV-3 | 3 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-1 | 1 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-2 | 2 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-3 | 3 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 1 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 2 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 3 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 4 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 5 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 6 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 1 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 275kV | 2 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 275kV | 3 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 400kV | 1 |  | 75 | Shunt Reactor | 400
| 2029 | 2029 | Offshore 275kV-4 | 4 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Offshore 275kV-5 | 5 |  | 100 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-2 | 4 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Reactive Platform-3 | 5 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 7 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 8 |  | 120-300 | VSR | 275
| 2029 | 2029 | Onshore 275kV | 9 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 10 |  | 150 | Shunt Reactor | 275
| 2029 | 2029 | Onshore 275kV | 4 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 275kV | 5 | 200 | 200 | SVC | 275
| 2029 | 2029 | Onshore 400kV | 2 |  | 75 | Shunt Reactor | 400
Racebank Extension Wind Farm | 2029 | Addition | Offshore Platform 220kV-1 | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Offshore Platform 220kV-2 | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Onshore 220kV-1 | 1 | TBC | TBC | VSR | TBC
| 2029 | Addition | Onshore 220kV-2 | 2 | TBC | TBC | VSR | TBC
| 2029 | Addition | Onshore 220kV-1 | 1 | TBC | TBC | SVC | TBC
| 2029 | Addition | Onshore 220kV-2 | 2 | TBC | TBC | SVC | TBC
Thanet Extension Wind Farm | 2029 | Addition | Offshore-1 | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Offshore-1 | 2 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Onshore 400kV | 1 | TBC | TBC | Shunt Reactor | TBC
| 2029 | Addition | Onshore 400kV | 1 | TBC | TBC | SVC | TBC
West of Orkney Wind Farm | 2029 | 2029 | West of Orkney Offshore 275kV | TBC |  | TBC | SHR | TBC
| 2029 | 2029 | West of Orkney Offshore 275kV | TBC |  | TBC | SHR | TBC
| 2029 | 2029 | West of Orkney Offshore 275kV | TBC | TBC | TBC | SVC | TBC
| 2029 | 2029 | West of Orkney Offshore 275kV | TBC | TBC | TBC | SVC | TBC

## B-5-1
B.5.1 - Intra GB HVDC 2020/21 to 2029/30
Interconnector Name | Existing | Planned from year | Node 1 | Node 2 | Type | Rated Voltage (kV) | Length(km) | Metallic Return | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Node 1 MVAr Gen | Node 1 MVAr Abs | Node 2 MVAr Gen | Node 2 MVAr Abs
Western HVDC Link | Yes | N/A | HUCS41 | FLIB41 | LCC | ±600 | 422 | No | 2250 | 2250 | 2250 | 2250 | 688 | 1946 | 1710 | 705
Caithness Moray Multi-Terminal Link - Terminal 1 | Yes | N/A | SPIT2 | Central DC Substation | VSC | ±320 | 31 | No | 800 | 800 | 800 | 800 | 263 | 263 | N/A | N/A
Caithness Moray Multi-Terminal Link - Terminal 2 | Yes | N/A | BLHI4 | Central DC Substation | VSC | ±320 | 136 | No | 1200 | 1200 | 1200 | 1200 | 394 | 394 | N/A | N/A
Caithness Moray Shetland Multi-Terminal Link - Terminal 3 | No | 2024 | KERG1 | Central DC Substation | VSC | ±320 | 269 | No | 600 | 600 | 600 | 600 | 197 | 197 | N/A | N/A
Western Isle HVDC Link | No | 2026 | BEAU4 | ARNI1 | VSC | ±320 | 159 | No | 600 | 600 | 600 | 600 | 197 | 197 | 197 | 197
Offshore HVDC - SCD1 | No | 2028 | SIZE41 | CANT41 | TBC | TBC | TBC | No | 2000 | 2000 | 2000 | 2000 | TBC | TBC | TBC | TBC
Eastern HVDC Link | No | 2029 | PEHE4 | DRAX41 | VSC | ±320 | 339 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | TBC | TBC
West of Orkney HVDC Link | No | 2029 | SPIT4 | PEHE4 | VSC | ±320 | 145 | No | 2250 | 2250 | 2250 | 2250 | 749 | 749 | 749 | 749
Eastern HVDC Link | No | 2029 | BRNX4- | HAWP41 | VSC | TBC | TBC | No | 2000 | 2000 | 2000 | 2000 | 660 | 660 | TBC | TBC