## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF value may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in GWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | System Imbalance | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20201001-1 | Trip of PEMB-41 |  | 2020-10-01 | 3:43 | N/A | Refer to tab 'Event 20201001-1' | 49.908 | 49.865 | -0.0197 | 402 | -402 | N/A | N/A | N/A | 508.7749
Event 20201002-1 | Trip of IFA Bipole 1 |  | 2020-10-02 | 9:30 | N/A | Refer to tab 'Event 20201002-1' | 50.018 | 49.594 | -0.102 | 1000 | -1000 | N/A | N/A | N/A | 243.1078
Event 20201008-1 | Trip of IFA Bipole 2 | Ramp off gradually | 2020-10-08 | 18:23 | N/A | Refer to tab 'Event 20201008-1' | 50.063 | 49.808 | N/A | 1000 | -1000 | N/A | N/A | N/A | N/A
Event 20201011-1 | Trip of DIDCB5 | Ramp off gradually | 2020-10-11 | 23:00 | N/A | Refer to tab 'Event 20201011-1' | 50.01 | 49.956 | N/A | 734 | -734 | N/A | N/A | N/A | N/A
Event 20201014-1 | Trip of LNMTH-1/2/3 | Unit 1 at 11:24:30, unit 2at 12:26:30, unit 3at 13:29:50, | 2020-10-14 | 11:24 | N/A | Refer to tab 'Event 20201014-1' | 50.05 | 49.763 | N/A | LNMTH-1 132, LNMTH-2 123, LNMTH-3 74 | -329 | N/A | N/A | N/A | N/A
Event 20201025-1 | Trip of WL HVDC |  | 2020-10-25 | 4:42 | N/A | Refer to tab 'Event 20201025-1' | 49.976 | 49.715 | -0.197 | HUNB-7 57, HUNB-8 65, TONG-1 11, TONG-2 11, AIRSW-1 27, CRYRW-1 18, FSDLW-1 15 | -590 | N/A | N/A | 77.5% | 141 | The event caused embedded generation losses
Event 20201030-1 | Trip of HOWAO-1/2/3 |  | 2020-10-30 | 11:11 | N/A | Refer to tab 'Event 20201030-1' | 50.066 | 49.604 | -0.14 | HOWAO-1 398, HOWAO-2 398, HOWAO-3 389 | -1185 | N/A | N/A | N/A | 209.9312

## Event 20201001-1
In UTC
Date | Time | Freq
2020-10-01 | 2:41 | 49.957
2020-10-01 | 2:41 | 49.956
2020-10-01 | 2:41 | 49.956
2020-10-01 | 2:41 | 49.956
2020-10-01 | 2:41 | 49.956
2020-10-01 | 2:41 | 49.955
2020-10-01 | 2:41 | 49.953
2020-10-01 | 2:41 | 49.951
2020-10-01 | 2:41 | 49.95
2020-10-01 | 2:41 | 49.949
2020-10-01 | 2:41 | 49.948
2020-10-01 | 2:41 | 49.947
2020-10-01 | 2:41 | 49.946
2020-10-01 | 2:41 | 49.945
2020-10-01 | 2:41 | 49.943
2020-10-01 | 2:41 | 49.941
2020-10-01 | 2:41 | 49.94
2020-10-01 | 2:41 | 49.939
2020-10-01 | 2:41 | 49.939
2020-10-01 | 2:41 | 49.939
2020-10-01 | 2:41 | 49.94
2020-10-01 | 2:41 | 49.942
2020-10-01 | 2:41 | 49.946
2020-10-01 | 2:41 | 49.948
2020-10-01 | 2:41 | 49.951
2020-10-01 | 2:41 | 49.953
2020-10-01 | 2:41 | 49.955
2020-10-01 | 2:41 | 49.955
2020-10-01 | 2:41 | 49.953
2020-10-01 | 2:41 | 49.954
2020-10-01 | 2:42 | 49.956
2020-10-01 | 2:42 | 49.957
2020-10-01 | 2:42 | 49.959
2020-10-01 | 2:42 | 49.961
2020-10-01 | 2:42 | 49.963
2020-10-01 | 2:42 | 49.963
2020-10-01 | 2:42 | 49.964
2020-10-01 | 2:42 | 49.965
2020-10-01 | 2:42 | 49.966
2020-10-01 | 2:42 | 49.965
2020-10-01 | 2:42 | 49.967
2020-10-01 | 2:42 | 49.968
2020-10-01 | 2:42 | 49.969
2020-10-01 | 2:42 | 49.972
2020-10-01 | 2:42 | 49.973
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.976
2020-10-01 | 2:42 | 49.976
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.976
2020-10-01 | 2:42 | 49.976
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.973
2020-10-01 | 2:42 | 49.973
2020-10-01 | 2:42 | 49.972
2020-10-01 | 2:42 | 49.971
2020-10-01 | 2:42 | 49.971
2020-10-01 | 2:42 | 49.972
2020-10-01 | 2:42 | 49.973
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.976
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.972
2020-10-01 | 2:42 | 49.969
2020-10-01 | 2:42 | 49.968
2020-10-01 | 2:42 | 49.967
2020-10-01 | 2:42 | 49.966
2020-10-01 | 2:42 | 49.968
2020-10-01 | 2:42 | 49.97
2020-10-01 | 2:42 | 49.972
2020-10-01 | 2:42 | 49.972
2020-10-01 | 2:42 | 49.974
2020-10-01 | 2:42 | 49.975
2020-10-01 | 2:42 | 49.973
2020-10-01 | 2:42 | 49.97
2020-10-01 | 2:42 | 49.966
2020-10-01 | 2:42 | 49.963
2020-10-01 | 2:42 | 49.96
2020-10-01 | 2:43 | 49.959
2020-10-01 | 2:43 | 49.96
2020-10-01 | 2:43 | 49.961
2020-10-01 | 2:43 | 49.964
2020-10-01 | 2:43 | 49.966
2020-10-01 | 2:43 | 49.967
2020-10-01 | 2:43 | 49.966
2020-10-01 | 2:43 | 49.965
2020-10-01 | 2:43 | 49.965
2020-10-01 | 2:43 | 49.963
2020-10-01 | 2:43 | 49.959
2020-10-01 | 2:43 | 49.955
2020-10-01 | 2:43 | 49.953
2020-10-01 | 2:43 | 49.95
2020-10-01 | 2:43 | 49.948
2020-10-01 | 2:43 | 49.945
2020-10-01 | 2:43 | 49.943
2020-10-01 | 2:43 | 49.946
2020-10-01 | 2:43 | 49.947
2020-10-01 | 2:43 | 49.948
2020-10-01 | 2:43 | 49.949
2020-10-01 | 2:43 | 49.948
2020-10-01 | 2:43 | 49.949
2020-10-01 | 2:43 | 49.949
2020-10-01 | 2:43 | 49.947
2020-10-01 | 2:43 | 49.946
2020-10-01 | 2:43 | 49.942
2020-10-01 | 2:43 | 49.938
2020-10-01 | 2:43 | 49.935
2020-10-01 | 2:43 | 49.934
2020-10-01 | 2:43 | 49.932
2020-10-01 | 2:43 | 49.929
2020-10-01 | 2:43 | 49.927
2020-10-01 | 2:43 | 49.926
2020-10-01 | 2:43 | 49.926
2020-10-01 | 2:43 | 49.927
2020-10-01 | 2:43 | 49.926
2020-10-01 | 2:43 | 49.926
2020-10-01 | 2:43 | 49.925
2020-10-01 | 2:43 | 49.924
2020-10-01 | 2:43 | 49.924
2020-10-01 | 2:43 | 49.924
2020-10-01 | 2:43 | 49.925
2020-10-01 | 2:43 | 49.925
2020-10-01 | 2:43 | 49.922
2020-10-01 | 2:43 | 49.921
2020-10-01 | 2:43 | 49.918
2020-10-01 | 2:43 | 49.916
2020-10-01 | 2:43 | 49.914
2020-10-01 | 2:43 | 49.911
2020-10-01 | 2:43 | 49.91
2020-10-01 | 2:43 | 49.909
2020-10-01 | 2:43 | 49.908
2020-10-01 | 2:43 | 49.907
2020-10-01 | 2:43 | 49.907
2020-10-01 | 2:43 | 49.908
2020-10-01 | 2:43 | 49.908
2020-10-01 | 2:43 | 49.908
2020-10-01 | 2:43 | 49.896
2020-10-01 | 2:44 | 49.884
2020-10-01 | 2:44 | 49.874
2020-10-01 | 2:44 | 49.868
2020-10-01 | 2:44 | 49.866
2020-10-01 | 2:44 | 49.865
2020-10-01 | 2:44 | 49.866
2020-10-01 | 2:44 | 49.867
2020-10-01 | 2:44 | 49.87
2020-10-01 | 2:44 | 49.871
2020-10-01 | 2:44 | 49.875
2020-10-01 | 2:44 | 49.877
2020-10-01 | 2:44 | 49.879
2020-10-01 | 2:44 | 49.88
2020-10-01 | 2:44 | 49.881
2020-10-01 | 2:44 | 49.881
2020-10-01 | 2:44 | 49.88
2020-10-01 | 2:44 | 49.879
2020-10-01 | 2:44 | 49.879
2020-10-01 | 2:44 | 49.879
2020-10-01 | 2:44 | 49.878
2020-10-01 | 2:44 | 49.876
2020-10-01 | 2:44 | 49.875
2020-10-01 | 2:44 | 49.875
2020-10-01 | 2:44 | 49.876
2020-10-01 | 2:44 | 49.876
2020-10-01 | 2:44 | 49.876
2020-10-01 | 2:44 | 49.877
2020-10-01 | 2:44 | 49.878
2020-10-01 | 2:44 | 49.877
2020-10-01 | 2:44 | 49.877
2020-10-01 | 2:44 | 49.876
2020-10-01 | 2:44 | 49.874
2020-10-01 | 2:44 | 49.873
2020-10-01 | 2:44 | 49.871
2020-10-01 | 2:44 | 49.867
2020-10-01 | 2:44 | 49.863
2020-10-01 | 2:44 | 49.862
2020-10-01 | 2:44 | 49.861
2020-10-01 | 2:44 | 49.86
2020-10-01 | 2:44 | 49.86
2020-10-01 | 2:44 | 49.862
2020-10-01 | 2:44 | 49.863
2020-10-01 | 2:44 | 49.864
2020-10-01 | 2:44 | 49.864
2020-10-01 | 2:44 | 49.864
2020-10-01 | 2:44 | 49.866
2020-10-01 | 2:44 | 49.866
2020-10-01 | 2:44 | 49.865
2020-10-01 | 2:44 | 49.863
2020-10-01 | 2:44 | 49.861
2020-10-01 | 2:44 | 49.861
2020-10-01 | 2:44 | 49.863
2020-10-01 | 2:44 | 49.863
2020-10-01 | 2:44 | 49.864
2020-10-01 | 2:44 | 49.864
2020-10-01 | 2:44 | 49.866
2020-10-01 | 2:44 | 49.864
2020-10-01 | 2:44 | 49.863
2020-10-01 | 2:44 | 49.86
2020-10-01 | 2:44 | 49.86
2020-10-01 | 2:44 | 49.858
2020-10-01 | 2:45 | 49.854
2020-10-01 | 2:45 | 49.851
2020-10-01 | 2:45 | 49.85
2020-10-01 | 2:45 | 49.85
2020-10-01 | 2:45 | 49.852
2020-10-01 | 2:45 | 49.855
2020-10-01 | 2:45 | 49.858
2020-10-01 | 2:45 | 49.862
2020-10-01 | 2:45 | 49.863
2020-10-01 | 2:45 | 49.862
2020-10-01 | 2:45 | 49.861
2020-10-01 | 2:45 | 49.862
2020-10-01 | 2:45 | 49.864
2020-10-01 | 2:45 | 49.864
2020-10-01 | 2:45 | 49.863
2020-10-01 | 2:45 | 49.862
2020-10-01 | 2:45 | 49.861
2020-10-01 | 2:45 | 49.86
2020-10-01 | 2:45 | 49.859
2020-10-01 | 2:45 | 49.858
2020-10-01 | 2:45 | 49.858
2020-10-01 | 2:45 | 49.856
2020-10-01 | 2:45 | 49.856
2020-10-01 | 2:45 | 49.854
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.852
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.852
2020-10-01 | 2:45 | 49.851
2020-10-01 | 2:45 | 49.851
2020-10-01 | 2:45 | 49.852
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.854
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.852
2020-10-01 | 2:45 | 49.851
2020-10-01 | 2:45 | 49.85
2020-10-01 | 2:45 | 49.848
2020-10-01 | 2:45 | 49.847
2020-10-01 | 2:45 | 49.847
2020-10-01 | 2:45 | 49.847
2020-10-01 | 2:45 | 49.85
2020-10-01 | 2:45 | 49.849
2020-10-01 | 2:45 | 49.85
2020-10-01 | 2:45 | 49.851
2020-10-01 | 2:45 | 49.853
2020-10-01 | 2:45 | 49.854
2020-10-01 | 2:45 | 49.856
2020-10-01 | 2:45 | 49.857
2020-10-01 | 2:45 | 49.859
2020-10-01 | 2:45 | 49.862
2020-10-01 | 2:45 | 49.863
2020-10-01 | 2:45 | 49.865
2020-10-01 | 2:45 | 49.866
2020-10-01 | 2:45 | 49.866
2020-10-01 | 2:46 | 49.866
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.863
2020-10-01 | 2:46 | 49.864
2020-10-01 | 2:46 | 49.866
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.87
2020-10-01 | 2:46 | 49.871
2020-10-01 | 2:46 | 49.872
2020-10-01 | 2:46 | 49.869
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.866
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.863
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.867
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.871
2020-10-01 | 2:46 | 49.87
2020-10-01 | 2:46 | 49.87
2020-10-01 | 2:46 | 49.869
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.863
2020-10-01 | 2:46 | 49.86
2020-10-01 | 2:46 | 49.858
2020-10-01 | 2:46 | 49.854
2020-10-01 | 2:46 | 49.855
2020-10-01 | 2:46 | 49.855
2020-10-01 | 2:46 | 49.857
2020-10-01 | 2:46 | 49.857
2020-10-01 | 2:46 | 49.858
2020-10-01 | 2:46 | 49.859
2020-10-01 | 2:46 | 49.86
2020-10-01 | 2:46 | 49.862
2020-10-01 | 2:46 | 49.862
2020-10-01 | 2:46 | 49.862
2020-10-01 | 2:46 | 49.86
2020-10-01 | 2:46 | 49.861
2020-10-01 | 2:46 | 49.86
2020-10-01 | 2:46 | 49.861
2020-10-01 | 2:46 | 49.862
2020-10-01 | 2:46 | 49.865
2020-10-01 | 2:46 | 49.867
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.869
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.868
2020-10-01 | 2:46 | 49.866
2020-10-01 | 2:46 | 49.864
2020-10-01 | 2:46 | 49.86
2020-10-01 | 2:46 | 49.857
2020-10-01 | 2:46 | 49.857
2020-10-01 | 2:46 | 49.856
2020-10-01 | 2:46 | 49.857
2020-10-01 | 2:46 | 49.859
2020-10-01 | 2:46 | 49.861
2020-10-01 | 2:46 | 49.864
2020-10-01 | 2:47 | 49.867
2020-10-01 | 2:47 | 49.868
2020-10-01 | 2:47 | 49.869
2020-10-01 | 2:47 | 49.869
2020-10-01 | 2:47 | 49.869
2020-10-01 | 2:47 | 49.869
2020-10-01 | 2:47 | 49.868
2020-10-01 | 2:47 | 49.868
2020-10-01 | 2:47 | 49.869
2020-10-01 | 2:47 | 49.866
2020-10-01 | 2:47 | 49.869
2020-10-01 | 2:47 | 49.87
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.872
2020-10-01 | 2:47 | 49.873
2020-10-01 | 2:47 | 49.873
2020-10-01 | 2:47 | 49.874
2020-10-01 | 2:47 | 49.874
2020-10-01 | 2:47 | 49.875
2020-10-01 | 2:47 | 49.876
2020-10-01 | 2:47 | 49.877
2020-10-01 | 2:47 | 49.877
2020-10-01 | 2:47 | 49.877
2020-10-01 | 2:47 | 49.877
2020-10-01 | 2:47 | 49.878
2020-10-01 | 2:47 | 49.877
2020-10-01 | 2:47 | 49.875
2020-10-01 | 2:47 | 49.874
2020-10-01 | 2:47 | 49.872
2020-10-01 | 2:47 | 49.872
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.87
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.87
2020-10-01 | 2:47 | 49.871
2020-10-01 | 2:47 | 49.873
2020-10-01 | 2:47 | 49.875
2020-10-01 | 2:47 | 49.878
2020-10-01 | 2:47 | 49.881
2020-10-01 | 2:47 | 49.883
2020-10-01 | 2:47 | 49.885
2020-10-01 | 2:47 | 49.888
2020-10-01 | 2:47 | 49.889
2020-10-01 | 2:47 | 49.889
2020-10-01 | 2:47 | 49.889
2020-10-01 | 2:47 | 49.891
2020-10-01 | 2:47 | 49.893
2020-10-01 | 2:47 | 49.896
2020-10-01 | 2:47 | 49.898
2020-10-01 | 2:47 | 49.899
2020-10-01 | 2:47 | 49.9
2020-10-01 | 2:47 | 49.899
2020-10-01 | 2:47 | 49.9
2020-10-01 | 2:47 | 49.9
2020-10-01 | 2:47 | 49.9
2020-10-01 | 2:47 | 49.9
2020-10-01 | 2:47 | 49.9
2020-10-01 | 2:48 | 49.9
2020-10-01 | 2:48 | 49.898
2020-10-01 | 2:48 | 49.899
2020-10-01 | 2:48 | 49.9
2020-10-01 | 2:48 | 49.901
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.903
2020-10-01 | 2:48 | 49.904
2020-10-01 | 2:48 | 49.905
2020-10-01 | 2:48 | 49.905
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.907
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.903
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.903
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.904
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.905
2020-10-01 | 2:48 | 49.904
2020-10-01 | 2:48 | 49.901
2020-10-01 | 2:48 | 49.898
2020-10-01 | 2:48 | 49.898
2020-10-01 | 2:48 | 49.899
2020-10-01 | 2:48 | 49.901
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.908
2020-10-01 | 2:48 | 49.909
2020-10-01 | 2:48 | 49.909
2020-10-01 | 2:48 | 49.909
2020-10-01 | 2:48 | 49.91
2020-10-01 | 2:48 | 49.91
2020-10-01 | 2:48 | 49.909
2020-10-01 | 2:48 | 49.908
2020-10-01 | 2:48 | 49.905
2020-10-01 | 2:48 | 49.903
2020-10-01 | 2:48 | 49.903
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.902
2020-10-01 | 2:48 | 49.904
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.907
2020-10-01 | 2:48 | 49.908
2020-10-01 | 2:48 | 49.907
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.907
2020-10-01 | 2:48 | 49.908
2020-10-01 | 2:48 | 49.908
2020-10-01 | 2:48 | 49.908
2020-10-01 | 2:48 | 49.906
2020-10-01 | 2:48 | 49.907
2020-10-01 | 2:48 | 49.907
2020-10-01 | 2:49 | 49.907
2020-10-01 | 2:49 | 49.907
2020-10-01 | 2:49 | 49.908
2020-10-01 | 2:49 | 49.907
2020-10-01 | 2:49 | 49.907
2020-10-01 | 2:49 | 49.906
2020-10-01 | 2:49 | 49.906
2020-10-01 | 2:49 | 49.906
2020-10-01 | 2:49 | 49.909
2020-10-01 | 2:49 | 49.91
2020-10-01 | 2:49 | 49.912
2020-10-01 | 2:49 | 49.914
2020-10-01 | 2:49 | 49.916
2020-10-01 | 2:49 | 49.917
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.919
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.919
2020-10-01 | 2:49 | 49.92
2020-10-01 | 2:49 | 49.922
2020-10-01 | 2:49 | 49.923
2020-10-01 | 2:49 | 49.923
2020-10-01 | 2:49 | 49.923
2020-10-01 | 2:49 | 49.922
2020-10-01 | 2:49 | 49.922
2020-10-01 | 2:49 | 49.92
2020-10-01 | 2:49 | 49.919
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.918
2020-10-01 | 2:49 | 49.919
2020-10-01 | 2:49 | 49.92
2020-10-01 | 2:49 | 49.923
2020-10-01 | 2:49 | 49.925
2020-10-01 | 2:49 | 49.93
2020-10-01 | 2:49 | 49.933
2020-10-01 | 2:49 | 49.937
2020-10-01 | 2:49 | 49.94
2020-10-01 | 2:49 | 49.94
2020-10-01 | 2:49 | 49.941
2020-10-01 | 2:49 | 49.941
2020-10-01 | 2:49 | 49.941
2020-10-01 | 2:49 | 49.94
2020-10-01 | 2:49 | 49.939
2020-10-01 | 2:49 | 49.937
2020-10-01 | 2:49 | 49.937
2020-10-01 | 2:49 | 49.937
2020-10-01 | 2:49 | 49.936
2020-10-01 | 2:49 | 49.935
2020-10-01 | 2:49 | 49.934
2020-10-01 | 2:49 | 49.932
2020-10-01 | 2:49 | 49.93
2020-10-01 | 2:49 | 49.93
2020-10-01 | 2:49 | 49.929
2020-10-01 | 2:49 | 49.929
2020-10-01 | 2:49 | 49.929
2020-10-01 | 2:50 | 49.93
2020-10-01 | 2:50 | 49.933
2020-10-01 | 2:50 | 49.934
2020-10-01 | 2:50 | 49.937
2020-10-01 | 2:50 | 49.938
2020-10-01 | 2:50 | 49.939
2020-10-01 | 2:50 | 49.939
2020-10-01 | 2:50 | 49.938
2020-10-01 | 2:50 | 49.936
2020-10-01 | 2:50 | 49.934
2020-10-01 | 2:50 | 49.932
2020-10-01 | 2:50 | 49.93
2020-10-01 | 2:50 | 49.928
2020-10-01 | 2:50 | 49.927
2020-10-01 | 2:50 | 49.927
2020-10-01 | 2:50 | 49.929
2020-10-01 | 2:50 | 49.932
2020-10-01 | 2:50 | 49.934
2020-10-01 | 2:50 | 49.937
2020-10-01 | 2:50 | 49.939
2020-10-01 | 2:50 | 49.94
2020-10-01 | 2:50 | 49.941
2020-10-01 | 2:50 | 49.94
2020-10-01 | 2:50 | 49.938
2020-10-01 | 2:50 | 49.935
2020-10-01 | 2:50 | 49.933
2020-10-01 | 2:50 | 49.931
2020-10-01 | 2:50 | 49.933
2020-10-01 | 2:50 | 49.936
2020-10-01 | 2:50 | 49.938
2020-10-01 | 2:50 | 49.939
2020-10-01 | 2:50 | 49.939
2020-10-01 | 2:50 | 49.938
2020-10-01 | 2:50 | 49.936
2020-10-01 | 2:50 | 49.935
2020-10-01 | 2:50 | 49.934
2020-10-01 | 2:50 | 49.932
2020-10-01 | 2:50 | 49.929
2020-10-01 | 2:50 | 49.927
2020-10-01 | 2:50 | 49.926
2020-10-01 | 2:50 | 49.924
2020-10-01 | 2:50 | 49.925
2020-10-01 | 2:50 | 49.926
2020-10-01 | 2:50 | 49.929
2020-10-01 | 2:50 | 49.933
2020-10-01 | 2:50 | 49.936
2020-10-01 | 2:50 | 49.939
2020-10-01 | 2:50 | 49.941
2020-10-01 | 2:50 | 49.943
2020-10-01 | 2:50 | 49.943
2020-10-01 | 2:50 | 49.942
2020-10-01 | 2:50 | 49.941
2020-10-01 | 2:50 | 49.94
2020-10-01 | 2:50 | 49.94
2020-10-01 | 2:50 | 49.94
2020-10-01 | 2:50 | 49.938
2020-10-01 | 2:50 | 49.937
2020-10-01 | 2:50 | 49.936
2020-10-01 | 2:50 | 49.935
2020-10-01 | 2:50 | 49.936
2020-10-01 | 2:50 | 49.935
2020-10-01 | 2:51 | 49.935
2020-10-01 | 2:51 | 49.935
2020-10-01 | 2:51 | 49.935
2020-10-01 | 2:51 | 49.936
2020-10-01 | 2:51 | 49.937
2020-10-01 | 2:51 | 49.938
2020-10-01 | 2:51 | 49.939
2020-10-01 | 2:51 | 49.939
2020-10-01 | 2:51 | 49.941
2020-10-01 | 2:51 | 49.943
2020-10-01 | 2:51 | 49.946
2020-10-01 | 2:51 | 49.947
2020-10-01 | 2:51 | 49.949
2020-10-01 | 2:51 | 49.949
2020-10-01 | 2:51 | 49.95
2020-10-01 | 2:51 | 49.951
2020-10-01 | 2:51 | 49.95
2020-10-01 | 2:51 | 49.949
2020-10-01 | 2:51 | 49.948
2020-10-01 | 2:51 | 49.949
2020-10-01 | 2:51 | 49.95
2020-10-01 | 2:51 | 49.952
2020-10-01 | 2:51 | 49.954
2020-10-01 | 2:51 | 49.957
2020-10-01 | 2:51 | 49.959
2020-10-01 | 2:51 | 49.96
2020-10-01 | 2:51 | 49.962
2020-10-01 | 2:51 | 49.963
2020-10-01 | 2:51 | 49.965
2020-10-01 | 2:51 | 49.967
2020-10-01 | 2:51 | 49.966
2020-10-01 | 2:51 | 49.966
2020-10-01 | 2:51 | 49.968
2020-10-01 | 2:51 | 49.969
2020-10-01 | 2:51 | 49.97
2020-10-01 | 2:51 | 49.97
2020-10-01 | 2:51 | 49.971
2020-10-01 | 2:51 | 49.97
2020-10-01 | 2:51 | 49.971
2020-10-01 | 2:51 | 49.97
2020-10-01 | 2:51 | 49.971
2020-10-01 | 2:51 | 49.971
2020-10-01 | 2:51 | 49.971
2020-10-01 | 2:51 | 49.972
2020-10-01 | 2:51 | 49.972
2020-10-01 | 2:51 | 49.973
2020-10-01 | 2:51 | 49.975
2020-10-01 | 2:51 | 49.975
2020-10-01 | 2:51 | 49.977
2020-10-01 | 2:51 | 49.978
2020-10-01 | 2:51 | 49.979
2020-10-01 | 2:51 | 49.981
2020-10-01 | 2:51 | 49.982
2020-10-01 | 2:51 | 49.983
2020-10-01 | 2:51 | 49.982
2020-10-01 | 2:51 | 49.981
2020-10-01 | 2:51 | 49.98
2020-10-01 | 2:51 | 49.979
2020-10-01 | 2:51 | 49.977
2020-10-01 | 2:52 | 49.974
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.969
2020-10-01 | 2:52 | 49.969
2020-10-01 | 2:52 | 49.968
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.972
2020-10-01 | 2:52 | 49.974
2020-10-01 | 2:52 | 49.976
2020-10-01 | 2:52 | 49.978
2020-10-01 | 2:52 | 49.98
2020-10-01 | 2:52 | 49.982
2020-10-01 | 2:52 | 49.981
2020-10-01 | 2:52 | 49.98
2020-10-01 | 2:52 | 49.979
2020-10-01 | 2:52 | 49.98
2020-10-01 | 2:52 | 49.98
2020-10-01 | 2:52 | 49.982
2020-10-01 | 2:52 | 49.984
2020-10-01 | 2:52 | 49.984
2020-10-01 | 2:52 | 49.983
2020-10-01 | 2:52 | 49.982
2020-10-01 | 2:52 | 49.983
2020-10-01 | 2:52 | 49.981
2020-10-01 | 2:52 | 49.978
2020-10-01 | 2:52 | 49.976
2020-10-01 | 2:52 | 49.973
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.969
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.972
2020-10-01 | 2:52 | 49.974
2020-10-01 | 2:52 | 49.975
2020-10-01 | 2:52 | 49.976
2020-10-01 | 2:52 | 49.975
2020-10-01 | 2:52 | 49.975
2020-10-01 | 2:52 | 49.975
2020-10-01 | 2:52 | 49.975
2020-10-01 | 2:52 | 49.975
2020-10-01 | 2:52 | 49.973
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.971
2020-10-01 | 2:52 | 49.97
2020-10-01 | 2:52 | 49.972
2020-10-01 | 2:52 | 49.974
2020-10-01 | 2:52 | 49.976
2020-10-01 | 2:52 | 49.978
2020-10-01 | 2:52 | 49.98
2020-10-01 | 2:52 | 49.982
2020-10-01 | 2:52 | 49.982
2020-10-01 | 2:53 | 49.983
2020-10-01 | 2:53 | 49.985
2020-10-01 | 2:53 | 49.985
2020-10-01 | 2:53 | 49.984
2020-10-01 | 2:53 | 49.983
2020-10-01 | 2:53 | 49.982
2020-10-01 | 2:53 | 49.982
2020-10-01 | 2:53 | 49.982
2020-10-01 | 2:53 | 49.981
2020-10-01 | 2:53 | 49.981
2020-10-01 | 2:53 | 49.983
2020-10-01 | 2:53 | 49.984
2020-10-01 | 2:53 | 49.984
2020-10-01 | 2:53 | 49.985
2020-10-01 | 2:53 | 49.986
2020-10-01 | 2:53 | 49.987
2020-10-01 | 2:53 | 49.986
2020-10-01 | 2:53 | 49.988
2020-10-01 | 2:53 | 49.991
2020-10-01 | 2:53 | 49.992
2020-10-01 | 2:53 | 49.993
2020-10-01 | 2:53 | 49.995
2020-10-01 | 2:53 | 49.997
2020-10-01 | 2:53 | 50
2020-10-01 | 2:53 | 50.001
2020-10-01 | 2:53 | 50.001
2020-10-01 | 2:53 | 50.003
2020-10-01 | 2:53 | 50.003
2020-10-01 | 2:53 | 50.003

## Event 20201002-1
In UTC
Date | Time | Freq
2020-10-02 | 8:29 | 50.008
2020-10-02 | 8:29 | 50.009
2020-10-02 | 8:29 | 50.008
2020-10-02 | 8:29 | 50.006
2020-10-02 | 8:29 | 50.006
2020-10-02 | 8:29 | 50.003
2020-10-02 | 8:29 | 50
2020-10-02 | 8:29 | 49.996
2020-10-02 | 8:29 | 49.991
2020-10-02 | 8:29 | 49.987
2020-10-02 | 8:29 | 49.981
2020-10-02 | 8:29 | 49.978
2020-10-02 | 8:29 | 49.974
2020-10-02 | 8:29 | 49.973
2020-10-02 | 8:29 | 49.972
2020-10-02 | 8:29 | 49.969
2020-10-02 | 8:29 | 49.965
2020-10-02 | 8:29 | 49.963
2020-10-02 | 8:29 | 49.961
2020-10-02 | 8:29 | 49.96
2020-10-02 | 8:29 | 49.958
2020-10-02 | 8:29 | 49.958
2020-10-02 | 8:29 | 49.959
2020-10-02 | 8:29 | 49.961
2020-10-02 | 8:29 | 49.963
2020-10-02 | 8:29 | 49.967
2020-10-02 | 8:29 | 49.969
2020-10-02 | 8:29 | 49.971
2020-10-02 | 8:29 | 49.973
2020-10-02 | 8:29 | 49.975
2020-10-02 | 8:30 | 49.977
2020-10-02 | 8:30 | 49.978
2020-10-02 | 8:30 | 49.982
2020-10-02 | 8:30 | 49.987
2020-10-02 | 8:30 | 49.989
2020-10-02 | 8:30 | 49.993
2020-10-02 | 8:30 | 49.997
2020-10-02 | 8:30 | 50.004
2020-10-02 | 8:30 | 50.01
2020-10-02 | 8:30 | 50.014
2020-10-02 | 8:30 | 50.017
2020-10-02 | 8:30 | 50.018
2020-10-02 | 8:30 | 50.016
2020-10-02 | 8:30 | 50.016
2020-10-02 | 8:30 | 50.016
2020-10-02 | 8:30 | 50.015
2020-10-02 | 8:30 | 50.016
2020-10-02 | 8:30 | 50.017
2020-10-02 | 8:30 | 50.016
2020-10-02 | 8:30 | 50.015
2020-10-02 | 8:30 | 50.011
2020-10-02 | 8:30 | 50.009
2020-10-02 | 8:30 | 50.006
2020-10-02 | 8:30 | 50.001
2020-10-02 | 8:30 | 49.998
2020-10-02 | 8:30 | 49.997
2020-10-02 | 8:30 | 49.994
2020-10-02 | 8:30 | 49.993
2020-10-02 | 8:30 | 49.992
2020-10-02 | 8:30 | 49.991
2020-10-02 | 8:30 | 49.99
2020-10-02 | 8:30 | 49.986
2020-10-02 | 8:30 | 49.984
2020-10-02 | 8:30 | 49.983
2020-10-02 | 8:30 | 49.98
2020-10-02 | 8:30 | 49.977
2020-10-02 | 8:30 | 49.975
2020-10-02 | 8:30 | 49.974
2020-10-02 | 8:30 | 49.973
2020-10-02 | 8:30 | 49.97
2020-10-02 | 8:30 | 49.967
2020-10-02 | 8:30 | 49.888
2020-10-02 | 8:30 | 49.8
2020-10-02 | 8:30 | 49.733
2020-10-02 | 8:30 | 49.682
2020-10-02 | 8:30 | 49.646
2020-10-02 | 8:30 | 49.616
2020-10-02 | 8:30 | 49.597
2020-10-02 | 8:30 | 49.596
2020-10-02 | 8:30 | 49.597
2020-10-02 | 8:30 | 49.599
2020-10-02 | 8:30 | 49.601
2020-10-02 | 8:30 | 49.601
2020-10-02 | 8:30 | 49.602
2020-10-02 | 8:30 | 49.607
2020-10-02 | 8:30 | 49.611
2020-10-02 | 8:30 | 49.619
2020-10-02 | 8:30 | 49.629
2020-10-02 | 8:30 | 49.642
2020-10-02 | 8:30 | 49.658
2020-10-02 | 8:30 | 49.675
2020-10-02 | 8:31 | 49.691
2020-10-02 | 8:31 | 49.706
2020-10-02 | 8:31 | 49.719
2020-10-02 | 8:31 | 49.732
2020-10-02 | 8:31 | 49.744
2020-10-02 | 8:31 | 49.753
2020-10-02 | 8:31 | 49.76
2020-10-02 | 8:31 | 49.765
2020-10-02 | 8:31 | 49.77
2020-10-02 | 8:31 | 49.775
2020-10-02 | 8:31 | 49.778
2020-10-02 | 8:31 | 49.778
2020-10-02 | 8:31 | 49.778
2020-10-02 | 8:31 | 49.778
2020-10-02 | 8:31 | 49.777
2020-10-02 | 8:31 | 49.778
2020-10-02 | 8:31 | 49.779
2020-10-02 | 8:31 | 49.78
2020-10-02 | 8:31 | 49.782
2020-10-02 | 8:31 | 49.783
2020-10-02 | 8:31 | 49.784
2020-10-02 | 8:31 | 49.783
2020-10-02 | 8:31 | 49.781
2020-10-02 | 8:31 | 49.779
2020-10-02 | 8:31 | 49.775
2020-10-02 | 8:31 | 49.772
2020-10-02 | 8:31 | 49.768
2020-10-02 | 8:31 | 49.766
2020-10-02 | 8:31 | 49.767
2020-10-02 | 8:31 | 49.768
2020-10-02 | 8:31 | 49.769
2020-10-02 | 8:31 | 49.771
2020-10-02 | 8:31 | 49.776
2020-10-02 | 8:31 | 49.782
2020-10-02 | 8:31 | 49.786
2020-10-02 | 8:31 | 49.787
2020-10-02 | 8:31 | 49.789
2020-10-02 | 8:31 | 49.789
2020-10-02 | 8:31 | 49.79
2020-10-02 | 8:31 | 49.79
2020-10-02 | 8:31 | 49.791
2020-10-02 | 8:31 | 49.791
2020-10-02 | 8:31 | 49.791
2020-10-02 | 8:31 | 49.789
2020-10-02 | 8:31 | 49.79
2020-10-02 | 8:31 | 49.79
2020-10-02 | 8:31 | 49.79
2020-10-02 | 8:31 | 49.789
2020-10-02 | 8:31 | 49.788
2020-10-02 | 8:31 | 49.787
2020-10-02 | 8:31 | 49.789
2020-10-02 | 8:31 | 49.789
2020-10-02 | 8:31 | 49.787
2020-10-02 | 8:31 | 49.785
2020-10-02 | 8:31 | 49.784
2020-10-02 | 8:31 | 49.782
2020-10-02 | 8:31 | 49.782
2020-10-02 | 8:31 | 49.78
2020-10-02 | 8:31 | 49.783
2020-10-02 | 8:32 | 49.786
2020-10-02 | 8:32 | 49.789
2020-10-02 | 8:32 | 49.789
2020-10-02 | 8:32 | 49.788
2020-10-02 | 8:32 | 49.787
2020-10-02 | 8:32 | 49.788
2020-10-02 | 8:32 | 49.789
2020-10-02 | 8:32 | 49.79
2020-10-02 | 8:32 | 49.787
2020-10-02 | 8:32 | 49.786
2020-10-02 | 8:32 | 49.787
2020-10-02 | 8:32 | 49.788
2020-10-02 | 8:32 | 49.788
2020-10-02 | 8:32 | 49.79
2020-10-02 | 8:32 | 49.789
2020-10-02 | 8:32 | 49.79
2020-10-02 | 8:32 | 49.791
2020-10-02 | 8:32 | 49.792
2020-10-02 | 8:32 | 49.792
2020-10-02 | 8:32 | 49.792
2020-10-02 | 8:32 | 49.79
2020-10-02 | 8:32 | 49.792
2020-10-02 | 8:32 | 49.79
2020-10-02 | 8:32 | 49.791
2020-10-02 | 8:32 | 49.792
2020-10-02 | 8:32 | 49.793
2020-10-02 | 8:32 | 49.794
2020-10-02 | 8:32 | 49.796
2020-10-02 | 8:32 | 49.8
2020-10-02 | 8:32 | 49.804
2020-10-02 | 8:32 | 49.813
2020-10-02 | 8:32 | 49.82
2020-10-02 | 8:32 | 49.828
2020-10-02 | 8:32 | 49.837
2020-10-02 | 8:32 | 49.848
2020-10-02 | 8:32 | 49.857
2020-10-02 | 8:32 | 49.863
2020-10-02 | 8:32 | 49.868
2020-10-02 | 8:32 | 49.87
2020-10-02 | 8:32 | 49.87
2020-10-02 | 8:32 | 49.871
2020-10-02 | 8:32 | 49.871
2020-10-02 | 8:32 | 49.872
2020-10-02 | 8:32 | 49.873
2020-10-02 | 8:32 | 49.876
2020-10-02 | 8:32 | 49.877
2020-10-02 | 8:32 | 49.878
2020-10-02 | 8:32 | 49.878
2020-10-02 | 8:32 | 49.879
2020-10-02 | 8:32 | 49.88
2020-10-02 | 8:32 | 49.88
2020-10-02 | 8:32 | 49.882
2020-10-02 | 8:32 | 49.882
2020-10-02 | 8:32 | 49.882
2020-10-02 | 8:32 | 49.882
2020-10-02 | 8:32 | 49.883
2020-10-02 | 8:32 | 49.885
2020-10-02 | 8:32 | 49.887
2020-10-02 | 8:32 | 49.889
2020-10-02 | 8:32 | 49.891
2020-10-02 | 8:32 | 49.894
2020-10-02 | 8:33 | 49.895
2020-10-02 | 8:33 | 49.896
2020-10-02 | 8:33 | 49.896
2020-10-02 | 8:33 | 49.895
2020-10-02 | 8:33 | 49.896
2020-10-02 | 8:33 | 49.895
2020-10-02 | 8:33 | 49.895
2020-10-02 | 8:33 | 49.895
2020-10-02 | 8:33 | 49.895
2020-10-02 | 8:33 | 49.896
2020-10-02 | 8:33 | 49.899
2020-10-02 | 8:33 | 49.902
2020-10-02 | 8:33 | 49.906
2020-10-02 | 8:33 | 49.911
2020-10-02 | 8:33 | 49.916
2020-10-02 | 8:33 | 49.92
2020-10-02 | 8:33 | 49.925
2020-10-02 | 8:33 | 49.929
2020-10-02 | 8:33 | 49.931
2020-10-02 | 8:33 | 49.933
2020-10-02 | 8:33 | 49.933
2020-10-02 | 8:33 | 49.932
2020-10-02 | 8:33 | 49.934
2020-10-02 | 8:33 | 49.937
2020-10-02 | 8:33 | 49.94
2020-10-02 | 8:33 | 49.943
2020-10-02 | 8:33 | 49.947
2020-10-02 | 8:33 | 49.951
2020-10-02 | 8:33 | 49.954
2020-10-02 | 8:33 | 49.956
2020-10-02 | 8:33 | 49.955
2020-10-02 | 8:33 | 49.955
2020-10-02 | 8:33 | 49.955
2020-10-02 | 8:33 | 49.955
2020-10-02 | 8:33 | 49.953
2020-10-02 | 8:33 | 49.949
2020-10-02 | 8:33 | 49.944
2020-10-02 | 8:33 | 49.94
2020-10-02 | 8:33 | 49.937
2020-10-02 | 8:33 | 49.936
2020-10-02 | 8:33 | 49.937
2020-10-02 | 8:33 | 49.936
2020-10-02 | 8:33 | 49.937
2020-10-02 | 8:33 | 49.939
2020-10-02 | 8:33 | 49.939
2020-10-02 | 8:33 | 49.941
2020-10-02 | 8:33 | 49.941
2020-10-02 | 8:33 | 49.94
2020-10-02 | 8:33 | 49.94
2020-10-02 | 8:33 | 49.94
2020-10-02 | 8:33 | 49.939
2020-10-02 | 8:33 | 49.941
2020-10-02 | 8:33 | 49.942
2020-10-02 | 8:33 | 49.947
2020-10-02 | 8:33 | 49.95
2020-10-02 | 8:33 | 49.95
2020-10-02 | 8:33 | 49.952
2020-10-02 | 8:33 | 49.954
2020-10-02 | 8:33 | 49.956
2020-10-02 | 8:34 | 49.959
2020-10-02 | 8:34 | 49.958
2020-10-02 | 8:34 | 49.956
2020-10-02 | 8:34 | 49.952
2020-10-02 | 8:34 | 49.95
2020-10-02 | 8:34 | 49.945
2020-10-02 | 8:34 | 49.943
2020-10-02 | 8:34 | 49.941
2020-10-02 | 8:34 | 49.942
2020-10-02 | 8:34 | 49.946
2020-10-02 | 8:34 | 49.949
2020-10-02 | 8:34 | 49.952
2020-10-02 | 8:34 | 49.954
2020-10-02 | 8:34 | 49.957
2020-10-02 | 8:34 | 49.961
2020-10-02 | 8:34 | 49.964
2020-10-02 | 8:34 | 49.967
2020-10-02 | 8:34 | 49.968
2020-10-02 | 8:34 | 49.968
2020-10-02 | 8:34 | 49.97
2020-10-02 | 8:34 | 49.969
2020-10-02 | 8:34 | 49.968
2020-10-02 | 8:34 | 49.966
2020-10-02 | 8:34 | 49.966
2020-10-02 | 8:34 | 49.964
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.962
2020-10-02 | 8:34 | 49.958
2020-10-02 | 8:34 | 49.956
2020-10-02 | 8:34 | 49.951
2020-10-02 | 8:34 | 49.948
2020-10-02 | 8:34 | 49.945
2020-10-02 | 8:34 | 49.944
2020-10-02 | 8:34 | 49.944
2020-10-02 | 8:34 | 49.944
2020-10-02 | 8:34 | 49.945
2020-10-02 | 8:34 | 49.947
2020-10-02 | 8:34 | 49.949
2020-10-02 | 8:34 | 49.953
2020-10-02 | 8:34 | 49.96
2020-10-02 | 8:34 | 49.967
2020-10-02 | 8:34 | 49.972
2020-10-02 | 8:34 | 49.974
2020-10-02 | 8:34 | 49.976
2020-10-02 | 8:34 | 49.977
2020-10-02 | 8:34 | 49.978
2020-10-02 | 8:34 | 49.978
2020-10-02 | 8:34 | 49.975
2020-10-02 | 8:34 | 49.973
2020-10-02 | 8:34 | 49.971
2020-10-02 | 8:34 | 49.97
2020-10-02 | 8:34 | 49.97
2020-10-02 | 8:34 | 49.972
2020-10-02 | 8:34 | 49.976
2020-10-02 | 8:34 | 49.982
2020-10-02 | 8:34 | 49.988
2020-10-02 | 8:35 | 49.992
2020-10-02 | 8:35 | 49.993
2020-10-02 | 8:35 | 49.995
2020-10-02 | 8:35 | 49.997
2020-10-02 | 8:35 | 49.997
2020-10-02 | 8:35 | 49.999
2020-10-02 | 8:35 | 50.001
2020-10-02 | 8:35 | 50.001
2020-10-02 | 8:35 | 50.003
2020-10-02 | 8:35 | 50.005
2020-10-02 | 8:35 | 50.007
2020-10-02 | 8:35 | 50.009
2020-10-02 | 8:35 | 50.01
2020-10-02 | 8:35 | 50.015
2020-10-02 | 8:35 | 50.018
2020-10-02 | 8:35 | 50.02
2020-10-02 | 8:35 | 50.022
2020-10-02 | 8:35 | 50.022
2020-10-02 | 8:35 | 50.022
2020-10-02 | 8:35 | 50.022
2020-10-02 | 8:35 | 50.023
2020-10-02 | 8:35 | 50.024
2020-10-02 | 8:35 | 50.022
2020-10-02 | 8:35 | 50.019
2020-10-02 | 8:35 | 50.017
2020-10-02 | 8:35 | 50.014
2020-10-02 | 8:35 | 50.014
2020-10-02 | 8:35 | 50.014
2020-10-02 | 8:35 | 50.014

## Event 20201008-1
In UTC
Date | Time | Freq
2020-10-08 | 17:21 | 50.008
2020-10-08 | 17:21 | 50.005
2020-10-08 | 17:21 | 50.001
2020-10-08 | 17:21 | 50.001
2020-10-08 | 17:21 | 50
2020-10-08 | 17:21 | 50.002
2020-10-08 | 17:21 | 50.003
2020-10-08 | 17:21 | 50.005
2020-10-08 | 17:21 | 50.006
2020-10-08 | 17:21 | 50.007
2020-10-08 | 17:21 | 50.008
2020-10-08 | 17:21 | 50.009
2020-10-08 | 17:21 | 50.012
2020-10-08 | 17:21 | 50.013
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.015
2020-10-08 | 17:21 | 50.016
2020-10-08 | 17:21 | 50.017
2020-10-08 | 17:21 | 50.017
2020-10-08 | 17:21 | 50.017
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.013
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.014
2020-10-08 | 17:21 | 50.013
2020-10-08 | 17:21 | 50.015
2020-10-08 | 17:21 | 50.016
2020-10-08 | 17:22 | 50.018
2020-10-08 | 17:22 | 50.02
2020-10-08 | 17:22 | 50.022
2020-10-08 | 17:22 | 50.022
2020-10-08 | 17:22 | 50.022
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.02
2020-10-08 | 17:22 | 50.02
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.022
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.019
2020-10-08 | 17:22 | 50.017
2020-10-08 | 17:22 | 50.017
2020-10-08 | 17:22 | 50.017
2020-10-08 | 17:22 | 50.017
2020-10-08 | 17:22 | 50.017
2020-10-08 | 17:22 | 50.017
2020-10-08 | 17:22 | 50.016
2020-10-08 | 17:22 | 50.016
2020-10-08 | 17:22 | 50.015
2020-10-08 | 17:22 | 50.015
2020-10-08 | 17:22 | 50.018
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.024
2020-10-08 | 17:22 | 50.025
2020-10-08 | 17:22 | 50.025
2020-10-08 | 17:22 | 50.023
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.02
2020-10-08 | 17:22 | 50.018
2020-10-08 | 17:22 | 50.019
2020-10-08 | 17:22 | 50.021
2020-10-08 | 17:22 | 50.024
2020-10-08 | 17:22 | 50.026
2020-10-08 | 17:22 | 50.029
2020-10-08 | 17:22 | 50.03
2020-10-08 | 17:22 | 50.031
2020-10-08 | 17:22 | 50.035
2020-10-08 | 17:22 | 50.037
2020-10-08 | 17:22 | 50.04
2020-10-08 | 17:22 | 50.041
2020-10-08 | 17:22 | 50.042
2020-10-08 | 17:22 | 50.045
2020-10-08 | 17:22 | 50.049
2020-10-08 | 17:22 | 50.055
2020-10-08 | 17:22 | 50.056
2020-10-08 | 17:22 | 50.059
2020-10-08 | 17:22 | 50.061
2020-10-08 | 17:22 | 50.062
2020-10-08 | 17:22 | 50.062
2020-10-08 | 17:22 | 50.062
2020-10-08 | 17:22 | 50.062
2020-10-08 | 17:22 | 50.06
2020-10-08 | 17:22 | 50.058
2020-10-08 | 17:22 | 50.057
2020-10-08 | 17:22 | 50.057
2020-10-08 | 17:22 | 50.057
2020-10-08 | 17:22 | 50.058
2020-10-08 | 17:22 | 50.061
2020-10-08 | 17:23 | 50.063
2020-10-08 | 17:23 | 50.063
2020-10-08 | 17:23 | 50.061
2020-10-08 | 17:23 | 50.059
2020-10-08 | 17:23 | 50.057
2020-10-08 | 17:23 | 50.055
2020-10-08 | 17:23 | 50.053
2020-10-08 | 17:23 | 50.051
2020-10-08 | 17:23 | 50.048
2020-10-08 | 17:23 | 50.046
2020-10-08 | 17:23 | 50.045
2020-10-08 | 17:23 | 50.045
2020-10-08 | 17:23 | 50.044
2020-10-08 | 17:23 | 50.044
2020-10-08 | 17:23 | 50.043
2020-10-08 | 17:23 | 50.041
2020-10-08 | 17:23 | 50.04
2020-10-08 | 17:23 | 50.039
2020-10-08 | 17:23 | 50.037
2020-10-08 | 17:23 | 50.034
2020-10-08 | 17:23 | 50.029
2020-10-08 | 17:23 | 50.026
2020-10-08 | 17:23 | 50.022
2020-10-08 | 17:23 | 50.017
2020-10-08 | 17:23 | 50.014
2020-10-08 | 17:23 | 50.011
2020-10-08 | 17:23 | 50.009
2020-10-08 | 17:23 | 50.007
2020-10-08 | 17:23 | 50.006
2020-10-08 | 17:23 | 50.004
2020-10-08 | 17:23 | 50.002
2020-10-08 | 17:23 | 50.001
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 49.998
2020-10-08 | 17:23 | 49.998
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 50
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 50
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 49.998
2020-10-08 | 17:23 | 49.999
2020-10-08 | 17:23 | 49.997
2020-10-08 | 17:23 | 49.994
2020-10-08 | 17:23 | 49.989
2020-10-08 | 17:23 | 49.983
2020-10-08 | 17:23 | 49.976
2020-10-08 | 17:23 | 49.967
2020-10-08 | 17:23 | 49.96
2020-10-08 | 17:23 | 49.951
2020-10-08 | 17:23 | 49.945
2020-10-08 | 17:23 | 49.939
2020-10-08 | 17:23 | 49.934
2020-10-08 | 17:23 | 49.93
2020-10-08 | 17:23 | 49.926
2020-10-08 | 17:23 | 49.923
2020-10-08 | 17:23 | 49.919
2020-10-08 | 17:24 | 49.913
2020-10-08 | 17:24 | 49.908
2020-10-08 | 17:24 | 49.901
2020-10-08 | 17:24 | 49.896
2020-10-08 | 17:24 | 49.891
2020-10-08 | 17:24 | 49.888
2020-10-08 | 17:24 | 49.888
2020-10-08 | 17:24 | 49.888
2020-10-08 | 17:24 | 49.889
2020-10-08 | 17:24 | 49.89
2020-10-08 | 17:24 | 49.891
2020-10-08 | 17:24 | 49.892
2020-10-08 | 17:24 | 49.891
2020-10-08 | 17:24 | 49.89
2020-10-08 | 17:24 | 49.889
2020-10-08 | 17:24 | 49.885
2020-10-08 | 17:24 | 49.882
2020-10-08 | 17:24 | 49.881
2020-10-08 | 17:24 | 49.878
2020-10-08 | 17:24 | 49.879
2020-10-08 | 17:24 | 49.878
2020-10-08 | 17:24 | 49.879
2020-10-08 | 17:24 | 49.878
2020-10-08 | 17:24 | 49.879
2020-10-08 | 17:24 | 49.877
2020-10-08 | 17:24 | 49.873
2020-10-08 | 17:24 | 49.87
2020-10-08 | 17:24 | 49.868
2020-10-08 | 17:24 | 49.865
2020-10-08 | 17:24 | 49.861
2020-10-08 | 17:24 | 49.856
2020-10-08 | 17:24 | 49.853
2020-10-08 | 17:24 | 49.849
2020-10-08 | 17:24 | 49.848
2020-10-08 | 17:24 | 49.846
2020-10-08 | 17:24 | 49.845
2020-10-08 | 17:24 | 49.842
2020-10-08 | 17:24 | 49.841
2020-10-08 | 17:24 | 49.839
2020-10-08 | 17:24 | 49.838
2020-10-08 | 17:24 | 49.836
2020-10-08 | 17:24 | 49.834
2020-10-08 | 17:24 | 49.832
2020-10-08 | 17:24 | 49.831
2020-10-08 | 17:24 | 49.829
2020-10-08 | 17:24 | 49.827
2020-10-08 | 17:24 | 49.828
2020-10-08 | 17:24 | 49.828
2020-10-08 | 17:24 | 49.829
2020-10-08 | 17:24 | 49.829
2020-10-08 | 17:24 | 49.827
2020-10-08 | 17:24 | 49.825
2020-10-08 | 17:24 | 49.822
2020-10-08 | 17:24 | 49.819
2020-10-08 | 17:24 | 49.815
2020-10-08 | 17:24 | 49.812
2020-10-08 | 17:24 | 49.81
2020-10-08 | 17:24 | 49.809
2020-10-08 | 17:24 | 49.809
2020-10-08 | 17:24 | 49.809
2020-10-08 | 17:24 | 49.808
2020-10-08 | 17:25 | 49.808
2020-10-08 | 17:25 | 49.808
2020-10-08 | 17:25 | 49.808
2020-10-08 | 17:25 | 49.809
2020-10-08 | 17:25 | 49.812
2020-10-08 | 17:25 | 49.815
2020-10-08 | 17:25 | 49.819
2020-10-08 | 17:25 | 49.824
2020-10-08 | 17:25 | 49.829
2020-10-08 | 17:25 | 49.835
2020-10-08 | 17:25 | 49.841
2020-10-08 | 17:25 | 49.848
2020-10-08 | 17:25 | 49.854
2020-10-08 | 17:25 | 49.863
2020-10-08 | 17:25 | 49.872
2020-10-08 | 17:25 | 49.877
2020-10-08 | 17:25 | 49.883
2020-10-08 | 17:25 | 49.888
2020-10-08 | 17:25 | 49.897
2020-10-08 | 17:25 | 49.906
2020-10-08 | 17:25 | 49.913
2020-10-08 | 17:25 | 49.919
2020-10-08 | 17:25 | 49.922
2020-10-08 | 17:25 | 49.925
2020-10-08 | 17:25 | 49.925
2020-10-08 | 17:25 | 49.922
2020-10-08 | 17:25 | 49.922
2020-10-08 | 17:25 | 49.916
2020-10-08 | 17:25 | 49.913
2020-10-08 | 17:25 | 49.909
2020-10-08 | 17:25 | 49.906
2020-10-08 | 17:25 | 49.901
2020-10-08 | 17:25 | 49.897
2020-10-08 | 17:25 | 49.895
2020-10-08 | 17:25 | 49.892
2020-10-08 | 17:25 | 49.889
2020-10-08 | 17:25 | 49.886
2020-10-08 | 17:25 | 49.882
2020-10-08 | 17:25 | 49.879
2020-10-08 | 17:25 | 49.878
2020-10-08 | 17:25 | 49.879
2020-10-08 | 17:25 | 49.879
2020-10-08 | 17:25 | 49.878
2020-10-08 | 17:25 | 49.88
2020-10-08 | 17:25 | 49.88
2020-10-08 | 17:25 | 49.882
2020-10-08 | 17:25 | 49.883
2020-10-08 | 17:25 | 49.885
2020-10-08 | 17:25 | 49.888
2020-10-08 | 17:25 | 49.89
2020-10-08 | 17:25 | 49.895
2020-10-08 | 17:25 | 49.898
2020-10-08 | 17:25 | 49.901
2020-10-08 | 17:25 | 49.903
2020-10-08 | 17:25 | 49.907
2020-10-08 | 17:25 | 49.908
2020-10-08 | 17:25 | 49.909
2020-10-08 | 17:25 | 49.91
2020-10-08 | 17:25 | 49.91
2020-10-08 | 17:26 | 49.91
2020-10-08 | 17:26 | 49.913
2020-10-08 | 17:26 | 49.912
2020-10-08 | 17:26 | 49.913
2020-10-08 | 17:26 | 49.914
2020-10-08 | 17:26 | 49.915
2020-10-08 | 17:26 | 49.915
2020-10-08 | 17:26 | 49.916
2020-10-08 | 17:26 | 49.916
2020-10-08 | 17:26 | 49.918
2020-10-08 | 17:26 | 49.919
2020-10-08 | 17:26 | 49.921
2020-10-08 | 17:26 | 49.923
2020-10-08 | 17:26 | 49.924
2020-10-08 | 17:26 | 49.925
2020-10-08 | 17:26 | 49.928
2020-10-08 | 17:26 | 49.929
2020-10-08 | 17:26 | 49.932
2020-10-08 | 17:26 | 49.934
2020-10-08 | 17:26 | 49.935
2020-10-08 | 17:26 | 49.936
2020-10-08 | 17:26 | 49.937
2020-10-08 | 17:26 | 49.937
2020-10-08 | 17:26 | 49.939
2020-10-08 | 17:26 | 49.942
2020-10-08 | 17:26 | 49.943
2020-10-08 | 17:26 | 49.944
2020-10-08 | 17:26 | 49.944
2020-10-08 | 17:26 | 49.944
2020-10-08 | 17:26 | 49.943
2020-10-08 | 17:26 | 49.94
2020-10-08 | 17:26 | 49.938
2020-10-08 | 17:26 | 49.935
2020-10-08 | 17:26 | 49.933
2020-10-08 | 17:26 | 49.931
2020-10-08 | 17:26 | 49.93
2020-10-08 | 17:26 | 49.93
2020-10-08 | 17:26 | 49.931
2020-10-08 | 17:26 | 49.934
2020-10-08 | 17:26 | 49.934
2020-10-08 | 17:26 | 49.934
2020-10-08 | 17:26 | 49.932
2020-10-08 | 17:26 | 49.928
2020-10-08 | 17:26 | 49.926
2020-10-08 | 17:26 | 49.925
2020-10-08 | 17:26 | 49.922
2020-10-08 | 17:26 | 49.923
2020-10-08 | 17:26 | 49.922
2020-10-08 | 17:26 | 49.921
2020-10-08 | 17:26 | 49.918
2020-10-08 | 17:26 | 49.916
2020-10-08 | 17:26 | 49.913
2020-10-08 | 17:26 | 49.91
2020-10-08 | 17:26 | 49.909
2020-10-08 | 17:26 | 49.909
2020-10-08 | 17:26 | 49.91
2020-10-08 | 17:26 | 49.913
2020-10-08 | 17:26 | 49.916
2020-10-08 | 17:26 | 49.918
2020-10-08 | 17:26 | 49.92
2020-10-08 | 17:26 | 49.922
2020-10-08 | 17:27 | 49.923
2020-10-08 | 17:27 | 49.923
2020-10-08 | 17:27 | 49.924
2020-10-08 | 17:27 | 49.927
2020-10-08 | 17:27 | 49.929
2020-10-08 | 17:27 | 49.929
2020-10-08 | 17:27 | 49.933
2020-10-08 | 17:27 | 49.938
2020-10-08 | 17:27 | 49.944
2020-10-08 | 17:27 | 49.947
2020-10-08 | 17:27 | 49.949
2020-10-08 | 17:27 | 49.951
2020-10-08 | 17:27 | 49.953
2020-10-08 | 17:27 | 49.954
2020-10-08 | 17:27 | 49.955
2020-10-08 | 17:27 | 49.956
2020-10-08 | 17:27 | 49.958
2020-10-08 | 17:27 | 49.959
2020-10-08 | 17:27 | 49.96
2020-10-08 | 17:27 | 49.96
2020-10-08 | 17:27 | 49.959
2020-10-08 | 17:27 | 49.958
2020-10-08 | 17:27 | 49.953
2020-10-08 | 17:27 | 49.949
2020-10-08 | 17:27 | 49.944
2020-10-08 | 17:27 | 49.94
2020-10-08 | 17:27 | 49.937
2020-10-08 | 17:27 | 49.934
2020-10-08 | 17:27 | 49.931
2020-10-08 | 17:27 | 49.929
2020-10-08 | 17:27 | 49.927
2020-10-08 | 17:27 | 49.926
2020-10-08 | 17:27 | 49.928
2020-10-08 | 17:27 | 49.926
2020-10-08 | 17:27 | 49.927
2020-10-08 | 17:27 | 49.927
2020-10-08 | 17:27 | 49.93
2020-10-08 | 17:27 | 49.933
2020-10-08 | 17:27 | 49.936
2020-10-08 | 17:27 | 49.937
2020-10-08 | 17:27 | 49.935
2020-10-08 | 17:27 | 49.934
2020-10-08 | 17:27 | 49.935
2020-10-08 | 17:27 | 49.937
2020-10-08 | 17:27 | 49.941
2020-10-08 | 17:27 | 49.943
2020-10-08 | 17:27 | 49.945
2020-10-08 | 17:27 | 49.947
2020-10-08 | 17:27 | 49.948
2020-10-08 | 17:27 | 49.948
2020-10-08 | 17:27 | 49.95
2020-10-08 | 17:27 | 49.951
2020-10-08 | 17:27 | 49.949
2020-10-08 | 17:27 | 49.946
2020-10-08 | 17:27 | 49.943
2020-10-08 | 17:27 | 49.94
2020-10-08 | 17:27 | 49.938
2020-10-08 | 17:27 | 49.936
2020-10-08 | 17:27 | 49.935
2020-10-08 | 17:27 | 49.935
2020-10-08 | 17:28 | 49.935
2020-10-08 | 17:28 | 49.933
2020-10-08 | 17:28 | 49.933
2020-10-08 | 17:28 | 49.934
2020-10-08 | 17:28 | 49.932
2020-10-08 | 17:28 | 49.93
2020-10-08 | 17:28 | 49.926
2020-10-08 | 17:28 | 49.923
2020-10-08 | 17:28 | 49.916
2020-10-08 | 17:28 | 49.913
2020-10-08 | 17:28 | 49.912
2020-10-08 | 17:28 | 49.911
2020-10-08 | 17:28 | 49.912
2020-10-08 | 17:28 | 49.913
2020-10-08 | 17:28 | 49.915
2020-10-08 | 17:28 | 49.914
2020-10-08 | 17:28 | 49.914
2020-10-08 | 17:28 | 49.914
2020-10-08 | 17:28 | 49.914
2020-10-08 | 17:28 | 49.914
2020-10-08 | 17:28 | 49.915
2020-10-08 | 17:28 | 49.916
2020-10-08 | 17:28 | 49.917
2020-10-08 | 17:28 | 49.916
2020-10-08 | 17:28 | 49.916
2020-10-08 | 17:28 | 49.915
2020-10-08 | 17:28 | 49.913
2020-10-08 | 17:28 | 49.91
2020-10-08 | 17:28 | 49.91
2020-10-08 | 17:28 | 49.91
2020-10-08 | 17:28 | 49.907
2020-10-08 | 17:28 | 49.906
2020-10-08 | 17:28 | 49.902
2020-10-08 | 17:28 | 49.899
2020-10-08 | 17:28 | 49.896
2020-10-08 | 17:28 | 49.893
2020-10-08 | 17:28 | 49.887
2020-10-08 | 17:28 | 49.885
2020-10-08 | 17:28 | 49.886
2020-10-08 | 17:28 | 49.887
2020-10-08 | 17:28 | 49.891
2020-10-08 | 17:28 | 49.892
2020-10-08 | 17:28 | 49.894
2020-10-08 | 17:28 | 49.895
2020-10-08 | 17:28 | 49.895
2020-10-08 | 17:28 | 49.897
2020-10-08 | 17:28 | 49.898
2020-10-08 | 17:28 | 49.899
2020-10-08 | 17:28 | 49.9
2020-10-08 | 17:28 | 49.902
2020-10-08 | 17:28 | 49.903
2020-10-08 | 17:28 | 49.906
2020-10-08 | 17:28 | 49.907
2020-10-08 | 17:28 | 49.909
2020-10-08 | 17:28 | 49.909
2020-10-08 | 17:28 | 49.909
2020-10-08 | 17:28 | 49.911
2020-10-08 | 17:28 | 49.913
2020-10-08 | 17:28 | 49.912
2020-10-08 | 17:28 | 49.913
2020-10-08 | 17:29 | 49.912
2020-10-08 | 17:29 | 49.908
2020-10-08 | 17:29 | 49.908
2020-10-08 | 17:29 | 49.906
2020-10-08 | 17:29 | 49.904
2020-10-08 | 17:29 | 49.9
2020-10-08 | 17:29 | 49.896
2020-10-08 | 17:29 | 49.894
2020-10-08 | 17:29 | 49.892
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.887
2020-10-08 | 17:29 | 49.884
2020-10-08 | 17:29 | 49.883
2020-10-08 | 17:29 | 49.883
2020-10-08 | 17:29 | 49.883
2020-10-08 | 17:29 | 49.882
2020-10-08 | 17:29 | 49.881
2020-10-08 | 17:29 | 49.881
2020-10-08 | 17:29 | 49.88
2020-10-08 | 17:29 | 49.882
2020-10-08 | 17:29 | 49.883
2020-10-08 | 17:29 | 49.884
2020-10-08 | 17:29 | 49.886
2020-10-08 | 17:29 | 49.888
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.888
2020-10-08 | 17:29 | 49.887
2020-10-08 | 17:29 | 49.887
2020-10-08 | 17:29 | 49.887
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.888
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.888
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.886
2020-10-08 | 17:29 | 49.888
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.892
2020-10-08 | 17:29 | 49.89
2020-10-08 | 17:29 | 49.889
2020-10-08 | 17:29 | 49.887
2020-10-08 | 17:29 | 49.885
2020-10-08 | 17:29 | 49.881
2020-10-08 | 17:29 | 49.878
2020-10-08 | 17:29 | 49.875
2020-10-08 | 17:29 | 49.872
2020-10-08 | 17:29 | 49.866
2020-10-08 | 17:29 | 49.862
2020-10-08 | 17:29 | 49.857
2020-10-08 | 17:29 | 49.855
2020-10-08 | 17:29 | 49.853
2020-10-08 | 17:29 | 49.849
2020-10-08 | 17:29 | 49.845
2020-10-08 | 17:30 | 49.842
2020-10-08 | 17:30 | 49.838
2020-10-08 | 17:30 | 49.837
2020-10-08 | 17:30 | 49.836
2020-10-08 | 17:30 | 49.838
2020-10-08 | 17:30 | 49.841
2020-10-08 | 17:30 | 49.842
2020-10-08 | 17:30 | 49.843
2020-10-08 | 17:30 | 49.845
2020-10-08 | 17:30 | 49.844
2020-10-08 | 17:30 | 49.841
2020-10-08 | 17:30 | 49.84
2020-10-08 | 17:30 | 49.838
2020-10-08 | 17:30 | 49.838
2020-10-08 | 17:30 | 49.836
2020-10-08 | 17:30 | 49.837
2020-10-08 | 17:30 | 49.839
2020-10-08 | 17:30 | 49.842
2020-10-08 | 17:30 | 49.845
2020-10-08 | 17:30 | 49.85
2020-10-08 | 17:30 | 49.852
2020-10-08 | 17:30 | 49.851
2020-10-08 | 17:30 | 49.851
2020-10-08 | 17:30 | 49.852
2020-10-08 | 17:30 | 49.851
2020-10-08 | 17:30 | 49.849
2020-10-08 | 17:30 | 49.848
2020-10-08 | 17:30 | 49.846
2020-10-08 | 17:30 | 49.844
2020-10-08 | 17:30 | 49.843
2020-10-08 | 17:30 | 49.84
2020-10-08 | 17:30 | 49.837
2020-10-08 | 17:30 | 49.832
2020-10-08 | 17:30 | 49.83
2020-10-08 | 17:30 | 49.829
2020-10-08 | 17:30 | 49.829
2020-10-08 | 17:30 | 49.829
2020-10-08 | 17:30 | 49.829
2020-10-08 | 17:30 | 49.828
2020-10-08 | 17:30 | 49.826
2020-10-08 | 17:30 | 49.823
2020-10-08 | 17:30 | 49.82
2020-10-08 | 17:30 | 49.817
2020-10-08 | 17:30 | 49.814
2020-10-08 | 17:30 | 49.812
2020-10-08 | 17:30 | 49.811
2020-10-08 | 17:30 | 49.813
2020-10-08 | 17:30 | 49.815
2020-10-08 | 17:30 | 49.818
2020-10-08 | 17:30 | 49.819
2020-10-08 | 17:30 | 49.821
2020-10-08 | 17:30 | 49.822
2020-10-08 | 17:30 | 49.823
2020-10-08 | 17:30 | 49.824
2020-10-08 | 17:30 | 49.824
2020-10-08 | 17:30 | 49.825
2020-10-08 | 17:30 | 49.825
2020-10-08 | 17:30 | 49.826
2020-10-08 | 17:30 | 49.826
2020-10-08 | 17:30 | 49.827
2020-10-08 | 17:30 | 49.828
2020-10-08 | 17:31 | 49.829
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.829
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.829
2020-10-08 | 17:31 | 49.83
2020-10-08 | 17:31 | 49.831
2020-10-08 | 17:31 | 49.832
2020-10-08 | 17:31 | 49.833
2020-10-08 | 17:31 | 49.833
2020-10-08 | 17:31 | 49.833
2020-10-08 | 17:31 | 49.832
2020-10-08 | 17:31 | 49.832
2020-10-08 | 17:31 | 49.834
2020-10-08 | 17:31 | 49.836
2020-10-08 | 17:31 | 49.838
2020-10-08 | 17:31 | 49.843
2020-10-08 | 17:31 | 49.847
2020-10-08 | 17:31 | 49.848
2020-10-08 | 17:31 | 49.849
2020-10-08 | 17:31 | 49.849
2020-10-08 | 17:31 | 49.847
2020-10-08 | 17:31 | 49.846
2020-10-08 | 17:31 | 49.847
2020-10-08 | 17:31 | 49.847
2020-10-08 | 17:31 | 49.847
2020-10-08 | 17:31 | 49.845
2020-10-08 | 17:31 | 49.843
2020-10-08 | 17:31 | 49.842
2020-10-08 | 17:31 | 49.841
2020-10-08 | 17:31 | 49.839
2020-10-08 | 17:31 | 49.84
2020-10-08 | 17:31 | 49.839
2020-10-08 | 17:31 | 49.84
2020-10-08 | 17:31 | 49.84
2020-10-08 | 17:31 | 49.84
2020-10-08 | 17:31 | 49.84
2020-10-08 | 17:31 | 49.837
2020-10-08 | 17:31 | 49.836
2020-10-08 | 17:31 | 49.835
2020-10-08 | 17:31 | 49.834
2020-10-08 | 17:31 | 49.832
2020-10-08 | 17:31 | 49.831
2020-10-08 | 17:31 | 49.83
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.827
2020-10-08 | 17:31 | 49.827
2020-10-08 | 17:31 | 49.827
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.829
2020-10-08 | 17:31 | 49.83
2020-10-08 | 17:31 | 49.83
2020-10-08 | 17:31 | 49.829
2020-10-08 | 17:31 | 49.828
2020-10-08 | 17:31 | 49.824
2020-10-08 | 17:31 | 49.823
2020-10-08 | 17:31 | 49.82
2020-10-08 | 17:31 | 49.818
2020-10-08 | 17:32 | 49.818
2020-10-08 | 17:32 | 49.818
2020-10-08 | 17:32 | 49.82
2020-10-08 | 17:32 | 49.822
2020-10-08 | 17:32 | 49.822
2020-10-08 | 17:32 | 49.821
2020-10-08 | 17:32 | 49.819
2020-10-08 | 17:32 | 49.819
2020-10-08 | 17:32 | 49.818
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.816
2020-10-08 | 17:32 | 49.815
2020-10-08 | 17:32 | 49.816
2020-10-08 | 17:32 | 49.816
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.822
2020-10-08 | 17:32 | 49.823
2020-10-08 | 17:32 | 49.826
2020-10-08 | 17:32 | 49.826
2020-10-08 | 17:32 | 49.827
2020-10-08 | 17:32 | 49.828
2020-10-08 | 17:32 | 49.828
2020-10-08 | 17:32 | 49.831
2020-10-08 | 17:32 | 49.834
2020-10-08 | 17:32 | 49.837
2020-10-08 | 17:32 | 49.838
2020-10-08 | 17:32 | 49.839
2020-10-08 | 17:32 | 49.84
2020-10-08 | 17:32 | 49.841
2020-10-08 | 17:32 | 49.842
2020-10-08 | 17:32 | 49.841
2020-10-08 | 17:32 | 49.841
2020-10-08 | 17:32 | 49.84
2020-10-08 | 17:32 | 49.839
2020-10-08 | 17:32 | 49.837
2020-10-08 | 17:32 | 49.836
2020-10-08 | 17:32 | 49.834
2020-10-08 | 17:32 | 49.831
2020-10-08 | 17:32 | 49.828
2020-10-08 | 17:32 | 49.824
2020-10-08 | 17:32 | 49.823
2020-10-08 | 17:32 | 49.821
2020-10-08 | 17:32 | 49.82
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.818
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.817
2020-10-08 | 17:32 | 49.815
2020-10-08 | 17:32 | 49.812
2020-10-08 | 17:32 | 49.81
2020-10-08 | 17:32 | 49.808
2020-10-08 | 17:32 | 49.806
2020-10-08 | 17:32 | 49.805
2020-10-08 | 17:32 | 49.805
2020-10-08 | 17:32 | 49.806
2020-10-08 | 17:32 | 49.808
2020-10-08 | 17:32 | 49.808
2020-10-08 | 17:32 | 49.809
2020-10-08 | 17:33 | 49.812
2020-10-08 | 17:33 | 49.815
2020-10-08 | 17:33 | 49.819
2020-10-08 | 17:33 | 49.822
2020-10-08 | 17:33 | 49.823
2020-10-08 | 17:33 | 49.826
2020-10-08 | 17:33 | 49.83
2020-10-08 | 17:33 | 49.835
2020-10-08 | 17:33 | 49.841
2020-10-08 | 17:33 | 49.846
2020-10-08 | 17:33 | 49.85
2020-10-08 | 17:33 | 49.855
2020-10-08 | 17:33 | 49.856
2020-10-08 | 17:33 | 49.859
2020-10-08 | 17:33 | 49.86
2020-10-08 | 17:33 | 49.862
2020-10-08 | 17:33 | 49.863
2020-10-08 | 17:33 | 49.864
2020-10-08 | 17:33 | 49.865
2020-10-08 | 17:33 | 49.864
2020-10-08 | 17:33 | 49.863
2020-10-08 | 17:33 | 49.861
2020-10-08 | 17:33 | 49.857
2020-10-08 | 17:33 | 49.854
2020-10-08 | 17:33 | 49.852
2020-10-08 | 17:33 | 49.849
2020-10-08 | 17:33 | 49.846
2020-10-08 | 17:33 | 49.843
2020-10-08 | 17:33 | 49.841
2020-10-08 | 17:33 | 49.838
2020-10-08 | 17:33 | 49.835
2020-10-08 | 17:33 | 49.832
2020-10-08 | 17:33 | 49.829
2020-10-08 | 17:33 | 49.827
2020-10-08 | 17:33 | 49.824
2020-10-08 | 17:33 | 49.821
2020-10-08 | 17:33 | 49.818
2020-10-08 | 17:33 | 49.812
2020-10-08 | 17:33 | 49.805
2020-10-08 | 17:33 | 49.798
2020-10-08 | 17:33 | 49.794
2020-10-08 | 17:33 | 49.789
2020-10-08 | 17:33 | 49.786
2020-10-08 | 17:33 | 49.785
2020-10-08 | 17:33 | 49.786
2020-10-08 | 17:33 | 49.788
2020-10-08 | 17:33 | 49.791
2020-10-08 | 17:33 | 49.793
2020-10-08 | 17:33 | 49.795
2020-10-08 | 17:33 | 49.796
2020-10-08 | 17:33 | 49.796
2020-10-08 | 17:33 | 49.798
2020-10-08 | 17:33 | 49.8
2020-10-08 | 17:33 | 49.801
2020-10-08 | 17:33 | 49.803
2020-10-08 | 17:33 | 49.805
2020-10-08 | 17:33 | 49.81
2020-10-08 | 17:33 | 49.812
2020-10-08 | 17:33 | 49.814
2020-10-08 | 17:34 | 49.815
2020-10-08 | 17:34 | 49.817
2020-10-08 | 17:34 | 49.82
2020-10-08 | 17:34 | 49.822
2020-10-08 | 17:34 | 49.822
2020-10-08 | 17:34 | 49.821
2020-10-08 | 17:34 | 49.823
2020-10-08 | 17:34 | 49.824
2020-10-08 | 17:34 | 49.825
2020-10-08 | 17:34 | 49.825
2020-10-08 | 17:34 | 49.825
2020-10-08 | 17:34 | 49.826
2020-10-08 | 17:34 | 49.828
2020-10-08 | 17:34 | 49.829
2020-10-08 | 17:34 | 49.83
2020-10-08 | 17:34 | 49.83
2020-10-08 | 17:34 | 49.83
2020-10-08 | 17:34 | 49.832
2020-10-08 | 17:34 | 49.831
2020-10-08 | 17:34 | 49.831
2020-10-08 | 17:34 | 49.831
2020-10-08 | 17:34 | 49.831
2020-10-08 | 17:34 | 49.832
2020-10-08 | 17:34 | 49.832
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.835
2020-10-08 | 17:34 | 49.836
2020-10-08 | 17:34 | 49.835
2020-10-08 | 17:34 | 49.836
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.833
2020-10-08 | 17:34 | 49.832
2020-10-08 | 17:34 | 49.833
2020-10-08 | 17:34 | 49.836
2020-10-08 | 17:34 | 49.838
2020-10-08 | 17:34 | 49.838
2020-10-08 | 17:34 | 49.839
2020-10-08 | 17:34 | 49.842
2020-10-08 | 17:34 | 49.842
2020-10-08 | 17:34 | 49.842
2020-10-08 | 17:34 | 49.839
2020-10-08 | 17:34 | 49.837
2020-10-08 | 17:34 | 49.834
2020-10-08 | 17:34 | 49.832
2020-10-08 | 17:34 | 49.83
2020-10-08 | 17:34 | 49.828
2020-10-08 | 17:34 | 49.825
2020-10-08 | 17:34 | 49.825
2020-10-08 | 17:34 | 49.825
2020-10-08 | 17:34 | 49.824
2020-10-08 | 17:34 | 49.824
2020-10-08 | 17:34 | 49.824
2020-10-08 | 17:34 | 49.826
2020-10-08 | 17:34 | 49.827
2020-10-08 | 17:34 | 49.831
2020-10-08 | 17:34 | 49.833
2020-10-08 | 17:34 | 49.835
2020-10-08 | 17:35 | 49.837
2020-10-08 | 17:35 | 49.838
2020-10-08 | 17:35 | 49.838
2020-10-08 | 17:35 | 49.839
2020-10-08 | 17:35 | 49.838
2020-10-08 | 17:35 | 49.837
2020-10-08 | 17:35 | 49.835
2020-10-08 | 17:35 | 49.834
2020-10-08 | 17:35 | 49.835
2020-10-08 | 17:35 | 49.834
2020-10-08 | 17:35 | 49.834
2020-10-08 | 17:35 | 49.836
2020-10-08 | 17:35 | 49.837
2020-10-08 | 17:35 | 49.838
2020-10-08 | 17:35 | 49.841
2020-10-08 | 17:35 | 49.844
2020-10-08 | 17:35 | 49.846
2020-10-08 | 17:35 | 49.848
2020-10-08 | 17:35 | 49.85
2020-10-08 | 17:35 | 49.851
2020-10-08 | 17:35 | 49.853
2020-10-08 | 17:35 | 49.858
2020-10-08 | 17:35 | 49.865
2020-10-08 | 17:35 | 49.87
2020-10-08 | 17:35 | 49.876
2020-10-08 | 17:35 | 49.882
2020-10-08 | 17:35 | 49.885
2020-10-08 | 17:35 | 49.888
2020-10-08 | 17:35 | 49.892
2020-10-08 | 17:35 | 49.896
2020-10-08 | 17:35 | 49.897
2020-10-08 | 17:35 | 49.897
2020-10-08 | 17:35 | 49.896
2020-10-08 | 17:35 | 49.895
2020-10-08 | 17:35 | 49.893
2020-10-08 | 17:35 | 49.891
2020-10-08 | 17:35 | 49.887
2020-10-08 | 17:35 | 49.885
2020-10-08 | 17:35 | 49.881
2020-10-08 | 17:35 | 49.878
2020-10-08 | 17:35 | 49.874
2020-10-08 | 17:35 | 49.874
2020-10-08 | 17:35 | 49.874
2020-10-08 | 17:35 | 49.874
2020-10-08 | 17:35 | 49.874
2020-10-08 | 17:35 | 49.874
2020-10-08 | 17:35 | 49.875
2020-10-08 | 17:35 | 49.877
2020-10-08 | 17:35 | 49.877
2020-10-08 | 17:35 | 49.878
2020-10-08 | 17:35 | 49.88
2020-10-08 | 17:35 | 49.883
2020-10-08 | 17:35 | 49.884
2020-10-08 | 17:35 | 49.885
2020-10-08 | 17:35 | 49.886
2020-10-08 | 17:35 | 49.888
2020-10-08 | 17:35 | 49.889
2020-10-08 | 17:35 | 49.889
2020-10-08 | 17:35 | 49.89
2020-10-08 | 17:35 | 49.891
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.889
2020-10-08 | 17:36 | 49.888
2020-10-08 | 17:36 | 49.889
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.89
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.893
2020-10-08 | 17:36 | 49.893
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.892
2020-10-08 | 17:36 | 49.891
2020-10-08 | 17:36 | 49.888
2020-10-08 | 17:36 | 49.884
2020-10-08 | 17:36 | 49.879
2020-10-08 | 17:36 | 49.875
2020-10-08 | 17:36 | 49.869
2020-10-08 | 17:36 | 49.866
2020-10-08 | 17:36 | 49.863
2020-10-08 | 17:36 | 49.862
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.861
2020-10-08 | 17:36 | 49.862
2020-10-08 | 17:36 | 49.861
2020-10-08 | 17:36 | 49.861
2020-10-08 | 17:36 | 49.859
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.858
2020-10-08 | 17:36 | 49.858
2020-10-08 | 17:36 | 49.859
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.861
2020-10-08 | 17:36 | 49.861
2020-10-08 | 17:36 | 49.861
2020-10-08 | 17:36 | 49.859
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.859
2020-10-08 | 17:36 | 49.86
2020-10-08 | 17:36 | 49.859
2020-10-08 | 17:36 | 49.858
2020-10-08 | 17:36 | 49.857
2020-10-08 | 17:36 | 49.858
2020-10-08 | 17:36 | 49.857
2020-10-08 | 17:36 | 49.858
2020-10-08 | 17:37 | 49.856
2020-10-08 | 17:37 | 49.853
2020-10-08 | 17:37 | 49.851
2020-10-08 | 17:37 | 49.851
2020-10-08 | 17:37 | 49.851
2020-10-08 | 17:37 | 49.85
2020-10-08 | 17:37 | 49.851
2020-10-08 | 17:37 | 49.852
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.856
2020-10-08 | 17:37 | 49.858
2020-10-08 | 17:37 | 49.859
2020-10-08 | 17:37 | 49.861
2020-10-08 | 17:37 | 49.863
2020-10-08 | 17:37 | 49.865
2020-10-08 | 17:37 | 49.865
2020-10-08 | 17:37 | 49.864
2020-10-08 | 17:37 | 49.863
2020-10-08 | 17:37 | 49.862
2020-10-08 | 17:37 | 49.861
2020-10-08 | 17:37 | 49.859
2020-10-08 | 17:37 | 49.857
2020-10-08 | 17:37 | 49.857
2020-10-08 | 17:37 | 49.855
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.852
2020-10-08 | 17:37 | 49.852
2020-10-08 | 17:37 | 49.853
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.856
2020-10-08 | 17:37 | 49.857
2020-10-08 | 17:37 | 49.859
2020-10-08 | 17:37 | 49.857
2020-10-08 | 17:37 | 49.855
2020-10-08 | 17:37 | 49.853
2020-10-08 | 17:37 | 49.852
2020-10-08 | 17:37 | 49.853
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.854
2020-10-08 | 17:37 | 49.852
2020-10-08 | 17:37 | 49.85
2020-10-08 | 17:37 | 49.848
2020-10-08 | 17:37 | 49.846
2020-10-08 | 17:37 | 49.842
2020-10-08 | 17:37 | 49.841
2020-10-08 | 17:37 | 49.841
2020-10-08 | 17:37 | 49.84
2020-10-08 | 17:37 | 49.841
2020-10-08 | 17:37 | 49.84
2020-10-08 | 17:37 | 49.84
2020-10-08 | 17:37 | 49.839
2020-10-08 | 17:37 | 49.837
2020-10-08 | 17:37 | 49.834
2020-10-08 | 17:37 | 49.833
2020-10-08 | 17:37 | 49.831
2020-10-08 | 17:37 | 49.831
2020-10-08 | 17:37 | 49.831
2020-10-08 | 17:38 | 49.832
2020-10-08 | 17:38 | 49.834
2020-10-08 | 17:38 | 49.837
2020-10-08 | 17:38 | 49.839
2020-10-08 | 17:38 | 49.842
2020-10-08 | 17:38 | 49.846
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.852
2020-10-08 | 17:38 | 49.855
2020-10-08 | 17:38 | 49.857
2020-10-08 | 17:38 | 49.86
2020-10-08 | 17:38 | 49.862
2020-10-08 | 17:38 | 49.865
2020-10-08 | 17:38 | 49.865
2020-10-08 | 17:38 | 49.866
2020-10-08 | 17:38 | 49.865
2020-10-08 | 17:38 | 49.867
2020-10-08 | 17:38 | 49.868
2020-10-08 | 17:38 | 49.869
2020-10-08 | 17:38 | 49.869
2020-10-08 | 17:38 | 49.87
2020-10-08 | 17:38 | 49.868
2020-10-08 | 17:38 | 49.87
2020-10-08 | 17:38 | 49.869
2020-10-08 | 17:38 | 49.868
2020-10-08 | 17:38 | 49.867
2020-10-08 | 17:38 | 49.865
2020-10-08 | 17:38 | 49.862
2020-10-08 | 17:38 | 49.86
2020-10-08 | 17:38 | 49.858
2020-10-08 | 17:38 | 49.857
2020-10-08 | 17:38 | 49.856
2020-10-08 | 17:38 | 49.856
2020-10-08 | 17:38 | 49.856
2020-10-08 | 17:38 | 49.853
2020-10-08 | 17:38 | 49.851
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.848
2020-10-08 | 17:38 | 49.846
2020-10-08 | 17:38 | 49.846
2020-10-08 | 17:38 | 49.847
2020-10-08 | 17:38 | 49.847
2020-10-08 | 17:38 | 49.847
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.849
2020-10-08 | 17:38 | 49.85
2020-10-08 | 17:38 | 49.85
2020-10-08 | 17:38 | 49.852
2020-10-08 | 17:38 | 49.854
2020-10-08 | 17:38 | 49.855
2020-10-08 | 17:38 | 49.859
2020-10-08 | 17:38 | 49.861
2020-10-08 | 17:38 | 49.864
2020-10-08 | 17:38 | 49.864
2020-10-08 | 17:38 | 49.863
2020-10-08 | 17:38 | 49.863
2020-10-08 | 17:38 | 49.862
2020-10-08 | 17:39 | 49.863
2020-10-08 | 17:39 | 49.864
2020-10-08 | 17:39 | 49.864
2020-10-08 | 17:39 | 49.866
2020-10-08 | 17:39 | 49.87
2020-10-08 | 17:39 | 49.873
2020-10-08 | 17:39 | 49.875
2020-10-08 | 17:39 | 49.876
2020-10-08 | 17:39 | 49.877
2020-10-08 | 17:39 | 49.88
2020-10-08 | 17:39 | 49.883
2020-10-08 | 17:39 | 49.885
2020-10-08 | 17:39 | 49.888
2020-10-08 | 17:39 | 49.888
2020-10-08 | 17:39 | 49.888
2020-10-08 | 17:39 | 49.889
2020-10-08 | 17:39 | 49.89
2020-10-08 | 17:39 | 49.89
2020-10-08 | 17:39 | 49.889
2020-10-08 | 17:39 | 49.887
2020-10-08 | 17:39 | 49.886
2020-10-08 | 17:39 | 49.884
2020-10-08 | 17:39 | 49.88
2020-10-08 | 17:39 | 49.878
2020-10-08 | 17:39 | 49.877
2020-10-08 | 17:39 | 49.877
2020-10-08 | 17:39 | 49.879
2020-10-08 | 17:39 | 49.879
2020-10-08 | 17:39 | 49.88
2020-10-08 | 17:39 | 49.879
2020-10-08 | 17:39 | 49.881
2020-10-08 | 17:39 | 49.882
2020-10-08 | 17:39 | 49.881
2020-10-08 | 17:39 | 49.882
2020-10-08 | 17:39 | 49.883
2020-10-08 | 17:39 | 49.883
2020-10-08 | 17:39 | 49.88
2020-10-08 | 17:39 | 49.878
2020-10-08 | 17:39 | 49.877
2020-10-08 | 17:39 | 49.876
2020-10-08 | 17:39 | 49.877
2020-10-08 | 17:39 | 49.878
2020-10-08 | 17:39 | 49.879
2020-10-08 | 17:39 | 49.88
2020-10-08 | 17:39 | 49.881
2020-10-08 | 17:39 | 49.883
2020-10-08 | 17:39 | 49.883
2020-10-08 | 17:39 | 49.884
2020-10-08 | 17:39 | 49.885
2020-10-08 | 17:39 | 49.887
2020-10-08 | 17:39 | 49.888
2020-10-08 | 17:39 | 49.886
2020-10-08 | 17:39 | 49.883
2020-10-08 | 17:39 | 49.88
2020-10-08 | 17:39 | 49.876
2020-10-08 | 17:39 | 49.875
2020-10-08 | 17:39 | 49.874
2020-10-08 | 17:39 | 49.871
2020-10-08 | 17:39 | 49.868
2020-10-08 | 17:40 | 49.865
2020-10-08 | 17:40 | 49.862
2020-10-08 | 17:40 | 49.858
2020-10-08 | 17:40 | 49.857
2020-10-08 | 17:40 | 49.855
2020-10-08 | 17:40 | 49.855
2020-10-08 | 17:40 | 49.854
2020-10-08 | 17:40 | 49.853
2020-10-08 | 17:40 | 49.853
2020-10-08 | 17:40 | 49.854
2020-10-08 | 17:40 | 49.854
2020-10-08 | 17:40 | 49.854
2020-10-08 | 17:40 | 49.857
2020-10-08 | 17:40 | 49.861
2020-10-08 | 17:40 | 49.865
2020-10-08 | 17:40 | 49.871
2020-10-08 | 17:40 | 49.876
2020-10-08 | 17:40 | 49.881
2020-10-08 | 17:40 | 49.886
2020-10-08 | 17:40 | 49.892
2020-10-08 | 17:40 | 49.895
2020-10-08 | 17:40 | 49.899
2020-10-08 | 17:40 | 49.9
2020-10-08 | 17:40 | 49.902
2020-10-08 | 17:40 | 49.901
2020-10-08 | 17:40 | 49.899
2020-10-08 | 17:40 | 49.898
2020-10-08 | 17:40 | 49.896
2020-10-08 | 17:40 | 49.894
2020-10-08 | 17:40 | 49.894
2020-10-08 | 17:40 | 49.892
2020-10-08 | 17:40 | 49.891
2020-10-08 | 17:40 | 49.891
2020-10-08 | 17:40 | 49.891
2020-10-08 | 17:40 | 49.89
2020-10-08 | 17:40 | 49.89
2020-10-08 | 17:40 | 49.889
2020-10-08 | 17:40 | 49.89
2020-10-08 | 17:40 | 49.888
2020-10-08 | 17:40 | 49.889
2020-10-08 | 17:40 | 49.892
2020-10-08 | 17:40 | 49.891
2020-10-08 | 17:40 | 49.89
2020-10-08 | 17:40 | 49.89
2020-10-08 | 17:40 | 49.892
2020-10-08 | 17:40 | 49.895
2020-10-08 | 17:40 | 49.897
2020-10-08 | 17:40 | 49.899
2020-10-08 | 17:40 | 49.902
2020-10-08 | 17:40 | 49.903
2020-10-08 | 17:40 | 49.904
2020-10-08 | 17:40 | 49.905
2020-10-08 | 17:40 | 49.905
2020-10-08 | 17:40 | 49.906
2020-10-08 | 17:40 | 49.909
2020-10-08 | 17:40 | 49.91
2020-10-08 | 17:40 | 49.911
2020-10-08 | 17:40 | 49.913
2020-10-08 | 17:40 | 49.914
2020-10-08 | 17:40 | 49.915
2020-10-08 | 17:40 | 49.917
2020-10-08 | 17:41 | 49.919
2020-10-08 | 17:41 | 49.922
2020-10-08 | 17:41 | 49.924
2020-10-08 | 17:41 | 49.925
2020-10-08 | 17:41 | 49.927
2020-10-08 | 17:41 | 49.929
2020-10-08 | 17:41 | 49.928
2020-10-08 | 17:41 | 49.929
2020-10-08 | 17:41 | 49.929
2020-10-08 | 17:41 | 49.929
2020-10-08 | 17:41 | 49.926
2020-10-08 | 17:41 | 49.924
2020-10-08 | 17:41 | 49.919
2020-10-08 | 17:41 | 49.917
2020-10-08 | 17:41 | 49.915
2020-10-08 | 17:41 | 49.915
2020-10-08 | 17:41 | 49.916
2020-10-08 | 17:41 | 49.917
2020-10-08 | 17:41 | 49.916
2020-10-08 | 17:41 | 49.918
2020-10-08 | 17:41 | 49.92
2020-10-08 | 17:41 | 49.924
2020-10-08 | 17:41 | 49.927
2020-10-08 | 17:41 | 49.929
2020-10-08 | 17:41 | 49.931
2020-10-08 | 17:41 | 49.933
2020-10-08 | 17:41 | 49.934
2020-10-08 | 17:41 | 49.935
2020-10-08 | 17:41 | 49.936
2020-10-08 | 17:41 | 49.937
2020-10-08 | 17:41 | 49.938
2020-10-08 | 17:41 | 49.94
2020-10-08 | 17:41 | 49.942
2020-10-08 | 17:41 | 49.943
2020-10-08 | 17:41 | 49.943
2020-10-08 | 17:41 | 49.942
2020-10-08 | 17:41 | 49.94
2020-10-08 | 17:41 | 49.94
2020-10-08 | 17:41 | 49.939
2020-10-08 | 17:41 | 49.94
2020-10-08 | 17:41 | 49.942
2020-10-08 | 17:41 | 49.945
2020-10-08 | 17:41 | 49.946
2020-10-08 | 17:41 | 49.946
2020-10-08 | 17:41 | 49.945
2020-10-08 | 17:41 | 49.944
2020-10-08 | 17:41 | 49.942
2020-10-08 | 17:41 | 49.939
2020-10-08 | 17:41 | 49.938
2020-10-08 | 17:41 | 49.939
2020-10-08 | 17:41 | 49.942
2020-10-08 | 17:41 | 49.945
2020-10-08 | 17:41 | 49.95
2020-10-08 | 17:41 | 49.953
2020-10-08 | 17:41 | 49.957
2020-10-08 | 17:41 | 49.958
2020-10-08 | 17:41 | 49.96
2020-10-08 | 17:41 | 49.962
2020-10-08 | 17:41 | 49.961
2020-10-08 | 17:42 | 49.961
2020-10-08 | 17:42 | 49.959
2020-10-08 | 17:42 | 49.959
2020-10-08 | 17:42 | 49.958
2020-10-08 | 17:42 | 49.961
2020-10-08 | 17:42 | 49.962
2020-10-08 | 17:42 | 49.963
2020-10-08 | 17:42 | 49.965
2020-10-08 | 17:42 | 49.968
2020-10-08 | 17:42 | 49.971
2020-10-08 | 17:42 | 49.974
2020-10-08 | 17:42 | 49.974
2020-10-08 | 17:42 | 49.975
2020-10-08 | 17:42 | 49.976
2020-10-08 | 17:42 | 49.978
2020-10-08 | 17:42 | 49.978
2020-10-08 | 17:42 | 49.979
2020-10-08 | 17:42 | 49.98
2020-10-08 | 17:42 | 49.982
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.985
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.983
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.985
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.986
2020-10-08 | 17:42 | 49.986
2020-10-08 | 17:42 | 49.984
2020-10-08 | 17:42 | 49.985
2020-10-08 | 17:42 | 49.988
2020-10-08 | 17:42 | 49.99
2020-10-08 | 17:42 | 49.992
2020-10-08 | 17:42 | 49.995
2020-10-08 | 17:42 | 49.998
2020-10-08 | 17:42 | 50.002
2020-10-08 | 17:42 | 50.004
2020-10-08 | 17:42 | 50.006
2020-10-08 | 17:42 | 50.006
2020-10-08 | 17:42 | 50.006
2020-10-08 | 17:42 | 50.006
2020-10-08 | 17:42 | 50.004
2020-10-08 | 17:42 | 50.002
2020-10-08 | 17:42 | 49.999
2020-10-08 | 17:42 | 49.994
2020-10-08 | 17:42 | 49.991
2020-10-08 | 17:42 | 49.985
2020-10-08 | 17:42 | 49.98
2020-10-08 | 17:42 | 49.977
2020-10-08 | 17:42 | 49.975
2020-10-08 | 17:42 | 49.973
2020-10-08 | 17:42 | 49.971
2020-10-08 | 17:42 | 49.969
2020-10-08 | 17:42 | 49.967
2020-10-08 | 17:42 | 49.965
2020-10-08 | 17:42 | 49.964
2020-10-08 | 17:42 | 49.963
2020-10-08 | 17:42 | 49.963
2020-10-08 | 17:43 | 49.963
2020-10-08 | 17:43 | 49.962
2020-10-08 | 17:43 | 49.963
2020-10-08 | 17:43 | 49.965
2020-10-08 | 17:43 | 49.963
2020-10-08 | 17:43 | 49.966
2020-10-08 | 17:43 | 49.968
2020-10-08 | 17:43 | 49.968
2020-10-08 | 17:43 | 49.967
2020-10-08 | 17:43 | 49.967
2020-10-08 | 17:43 | 49.967
2020-10-08 | 17:43 | 49.969
2020-10-08 | 17:43 | 49.968
2020-10-08 | 17:43 | 49.967
2020-10-08 | 17:43 | 49.966
2020-10-08 | 17:43 | 49.964
2020-10-08 | 17:43 | 49.963
2020-10-08 | 17:43 | 49.962
2020-10-08 | 17:43 | 49.961
2020-10-08 | 17:43 | 49.959
2020-10-08 | 17:43 | 49.959
2020-10-08 | 17:43 | 49.959
2020-10-08 | 17:43 | 49.959
2020-10-08 | 17:43 | 49.959
2020-10-08 | 17:43 | 49.959
2020-10-08 | 17:43 | 49.958
2020-10-08 | 17:43 | 49.958
2020-10-08 | 17:43 | 49.957
2020-10-08 | 17:43 | 49.958

## Event 20201011-1
In UTC
Date | Time | Freq
2020-10-11 | 21:59 | 50.065
2020-10-11 | 21:59 | 50.064
2020-10-11 | 21:59 | 50.064
2020-10-11 | 21:59 | 50.066
2020-10-11 | 21:59 | 50.067
2020-10-11 | 21:59 | 50.067
2020-10-11 | 21:59 | 50.068
2020-10-11 | 21:59 | 50.069
2020-10-11 | 21:59 | 50.07
2020-10-11 | 21:59 | 50.071
2020-10-11 | 21:59 | 50.073
2020-10-11 | 21:59 | 50.07
2020-10-11 | 21:59 | 50.071
2020-10-11 | 21:59 | 50.07
2020-10-11 | 21:59 | 50.07
2020-10-11 | 21:59 | 50.071
2020-10-11 | 21:59 | 50.073
2020-10-11 | 21:59 | 50.073
2020-10-11 | 21:59 | 50.073
2020-10-11 | 21:59 | 50.074
2020-10-11 | 21:59 | 50.074
2020-10-11 | 21:59 | 50.075
2020-10-11 | 21:59 | 50.074
2020-10-11 | 21:59 | 50.071
2020-10-11 | 21:59 | 50.07
2020-10-11 | 21:59 | 50.069
2020-10-11 | 21:59 | 50.069
2020-10-11 | 21:59 | 50.071
2020-10-11 | 21:59 | 50.075
2020-10-11 | 21:59 | 50.077
2020-10-11 | 22:00 | 50.079
2020-10-11 | 22:00 | 50.079
2020-10-11 | 22:00 | 50.08
2020-10-11 | 22:00 | 50.082
2020-10-11 | 22:00 | 50.081
2020-10-11 | 22:00 | 50.08
2020-10-11 | 22:00 | 50.08
2020-10-11 | 22:00 | 50.079
2020-10-11 | 22:00 | 50.079
2020-10-11 | 22:00 | 50.079
2020-10-11 | 22:00 | 50.08
2020-10-11 | 22:00 | 50.081
2020-10-11 | 22:00 | 50.08
2020-10-11 | 22:00 | 50.077
2020-10-11 | 22:00 | 50.074
2020-10-11 | 22:00 | 50.075
2020-10-11 | 22:00 | 50.073
2020-10-11 | 22:00 | 50.072
2020-10-11 | 22:00 | 50.071
2020-10-11 | 22:00 | 50.068
2020-10-11 | 22:00 | 50.066
2020-10-11 | 22:00 | 50.062
2020-10-11 | 22:00 | 50.058
2020-10-11 | 22:00 | 50.054
2020-10-11 | 22:00 | 50.052
2020-10-11 | 22:00 | 50.05
2020-10-11 | 22:00 | 50.048
2020-10-11 | 22:00 | 50.046
2020-10-11 | 22:00 | 50.043
2020-10-11 | 22:00 | 50.039
2020-10-11 | 22:00 | 50.034
2020-10-11 | 22:00 | 50.028
2020-10-11 | 22:00 | 50.023
2020-10-11 | 22:00 | 50.017
2020-10-11 | 22:00 | 50.015
2020-10-11 | 22:00 | 50.014
2020-10-11 | 22:00 | 50.014
2020-10-11 | 22:00 | 50.015
2020-10-11 | 22:00 | 50.016
2020-10-11 | 22:00 | 50.014
2020-10-11 | 22:00 | 50.013
2020-10-11 | 22:00 | 50.012
2020-10-11 | 22:00 | 50.012
2020-10-11 | 22:00 | 50.011
2020-10-11 | 22:00 | 50.011
2020-10-11 | 22:00 | 50.01
2020-10-11 | 22:00 | 50.01
2020-10-11 | 22:00 | 50.009
2020-10-11 | 22:00 | 50.008
2020-10-11 | 22:00 | 50.007
2020-10-11 | 22:00 | 50.004
2020-10-11 | 22:00 | 50
2020-10-11 | 22:00 | 49.996
2020-10-11 | 22:00 | 49.992
2020-10-11 | 22:00 | 49.987
2020-10-11 | 22:00 | 49.982
2020-10-11 | 22:00 | 49.978
2020-10-11 | 22:00 | 49.976
2020-10-11 | 22:00 | 49.973
2020-10-11 | 22:00 | 49.97
2020-10-11 | 22:00 | 49.969
2020-10-11 | 22:01 | 49.966
2020-10-11 | 22:01 | 49.966
2020-10-11 | 22:01 | 49.966
2020-10-11 | 22:01 | 49.966
2020-10-11 | 22:01 | 49.967
2020-10-11 | 22:01 | 49.969
2020-10-11 | 22:01 | 49.97
2020-10-11 | 22:01 | 49.971
2020-10-11 | 22:01 | 49.97
2020-10-11 | 22:01 | 49.969
2020-10-11 | 22:01 | 49.969
2020-10-11 | 22:01 | 49.969
2020-10-11 | 22:01 | 49.97
2020-10-11 | 22:01 | 49.969
2020-10-11 | 22:01 | 49.968
2020-10-11 | 22:01 | 49.967
2020-10-11 | 22:01 | 49.967
2020-10-11 | 22:01 | 49.967
2020-10-11 | 22:01 | 49.97
2020-10-11 | 22:01 | 49.973
2020-10-11 | 22:01 | 49.977
2020-10-11 | 22:01 | 49.978
2020-10-11 | 22:01 | 49.977
2020-10-11 | 22:01 | 49.975
2020-10-11 | 22:01 | 49.972
2020-10-11 | 22:01 | 49.968
2020-10-11 | 22:01 | 49.965
2020-10-11 | 22:01 | 49.962
2020-10-11 | 22:01 | 49.959
2020-10-11 | 22:01 | 49.957
2020-10-11 | 22:01 | 49.956
2020-10-11 | 22:01 | 49.956
2020-10-11 | 22:01 | 49.958
2020-10-11 | 22:01 | 49.96
2020-10-11 | 22:01 | 49.961
2020-10-11 | 22:01 | 49.966
2020-10-11 | 22:01 | 49.97
2020-10-11 | 22:01 | 49.974
2020-10-11 | 22:01 | 49.976
2020-10-11 | 22:01 | 49.977
2020-10-11 | 22:01 | 49.977
2020-10-11 | 22:01 | 49.977
2020-10-11 | 22:01 | 49.978
2020-10-11 | 22:01 | 49.982
2020-10-11 | 22:01 | 49.986
2020-10-11 | 22:01 | 49.989
2020-10-11 | 22:01 | 49.992
2020-10-11 | 22:01 | 49.995
2020-10-11 | 22:01 | 49.997
2020-10-11 | 22:01 | 50
2020-10-11 | 22:01 | 50
2020-10-11 | 22:01 | 50
2020-10-11 | 22:01 | 49.998
2020-10-11 | 22:01 | 49.997
2020-10-11 | 22:01 | 49.997
2020-10-11 | 22:01 | 50.001
2020-10-11 | 22:01 | 50.002
2020-10-11 | 22:01 | 50.002
2020-10-11 | 22:01 | 50.003
2020-10-11 | 22:01 | 50.002
2020-10-11 | 22:02 | 50.001
2020-10-11 | 22:02 | 49.999
2020-10-11 | 22:02 | 49.996
2020-10-11 | 22:02 | 49.992
2020-10-11 | 22:02 | 49.988
2020-10-11 | 22:02 | 49.984
2020-10-11 | 22:02 | 49.981
2020-10-11 | 22:02 | 49.981
2020-10-11 | 22:02 | 49.983
2020-10-11 | 22:02 | 49.986
2020-10-11 | 22:02 | 49.988
2020-10-11 | 22:02 | 49.988
2020-10-11 | 22:02 | 49.989
2020-10-11 | 22:02 | 49.99
2020-10-11 | 22:02 | 49.992
2020-10-11 | 22:02 | 49.994
2020-10-11 | 22:02 | 49.996
2020-10-11 | 22:02 | 49.997
2020-10-11 | 22:02 | 49.996
2020-10-11 | 22:02 | 49.996
2020-10-11 | 22:02 | 49.996
2020-10-11 | 22:02 | 49.995
2020-10-11 | 22:02 | 49.995
2020-10-11 | 22:02 | 49.994
2020-10-11 | 22:02 | 49.992
2020-10-11 | 22:02 | 49.991
2020-10-11 | 22:02 | 49.99
2020-10-11 | 22:02 | 49.989
2020-10-11 | 22:02 | 49.987
2020-10-11 | 22:02 | 49.986
2020-10-11 | 22:02 | 49.987
2020-10-11 | 22:02 | 49.988
2020-10-11 | 22:02 | 49.989
2020-10-11 | 22:02 | 49.991
2020-10-11 | 22:02 | 49.993
2020-10-11 | 22:02 | 49.996
2020-10-11 | 22:02 | 50
2020-10-11 | 22:02 | 50.002
2020-10-11 | 22:02 | 50.006
2020-10-11 | 22:02 | 50.011
2020-10-11 | 22:02 | 50.015
2020-10-11 | 22:02 | 50.019
2020-10-11 | 22:02 | 50.02
2020-10-11 | 22:02 | 50.02
2020-10-11 | 22:02 | 50.022
2020-10-11 | 22:02 | 50.024
2020-10-11 | 22:02 | 50.025
2020-10-11 | 22:02 | 50.026
2020-10-11 | 22:02 | 50.026
2020-10-11 | 22:02 | 50.024
2020-10-11 | 22:02 | 50.022
2020-10-11 | 22:02 | 50.02
2020-10-11 | 22:02 | 50.017
2020-10-11 | 22:02 | 50.015
2020-10-11 | 22:02 | 50.013
2020-10-11 | 22:02 | 50.013
2020-10-11 | 22:02 | 50.012
2020-10-11 | 22:02 | 50.011
2020-10-11 | 22:02 | 50.012
2020-10-11 | 22:02 | 50.014
2020-10-11 | 22:03 | 50.016
2020-10-11 | 22:03 | 50.016
2020-10-11 | 22:03 | 50.014
2020-10-11 | 22:03 | 50.014
2020-10-11 | 22:03 | 50.014
2020-10-11 | 22:03 | 50.012
2020-10-11 | 22:03 | 50.011
2020-10-11 | 22:03 | 50.011
2020-10-11 | 22:03 | 50.009
2020-10-11 | 22:03 | 50.009
2020-10-11 | 22:03 | 50.007
2020-10-11 | 22:03 | 50.007
2020-10-11 | 22:03 | 50.008
2020-10-11 | 22:03 | 50.009
2020-10-11 | 22:03 | 50.01
2020-10-11 | 22:03 | 50.01
2020-10-11 | 22:03 | 50.011
2020-10-11 | 22:03 | 50.012
2020-10-11 | 22:03 | 50.013
2020-10-11 | 22:03 | 50.015
2020-10-11 | 22:03 | 50.015
2020-10-11 | 22:03 | 50.015
2020-10-11 | 22:03 | 50.014
2020-10-11 | 22:03 | 50.014
2020-10-11 | 22:03 | 50.013
2020-10-11 | 22:03 | 50.013
2020-10-11 | 22:03 | 50.011
2020-10-11 | 22:03 | 50.01
2020-10-11 | 22:03 | 50.008
2020-10-11 | 22:03 | 50.005
2020-10-11 | 22:03 | 50.003
2020-10-11 | 22:03 | 50.001
2020-10-11 | 22:03 | 50
2020-10-11 | 22:03 | 49.998
2020-10-11 | 22:03 | 49.995
2020-10-11 | 22:03 | 49.992
2020-10-11 | 22:03 | 49.991
2020-10-11 | 22:03 | 49.991
2020-10-11 | 22:03 | 49.99
2020-10-11 | 22:03 | 49.991
2020-10-11 | 22:03 | 49.993
2020-10-11 | 22:03 | 49.993
2020-10-11 | 22:03 | 49.994
2020-10-11 | 22:03 | 49.994
2020-10-11 | 22:03 | 49.995
2020-10-11 | 22:03 | 49.994
2020-10-11 | 22:03 | 49.993
2020-10-11 | 22:03 | 49.996
2020-10-11 | 22:03 | 49.995
2020-10-11 | 22:03 | 49.999
2020-10-11 | 22:03 | 50.006
2020-10-11 | 22:03 | 50.011
2020-10-11 | 22:03 | 50.014
2020-10-11 | 22:03 | 50.017
2020-10-11 | 22:03 | 50.019
2020-10-11 | 22:03 | 50.021
2020-10-11 | 22:03 | 50.024
2020-10-11 | 22:03 | 50.027
2020-10-11 | 22:03 | 50.025
2020-10-11 | 22:04 | 50.026
2020-10-11 | 22:04 | 50.026
2020-10-11 | 22:04 | 50.027
2020-10-11 | 22:04 | 50.029
2020-10-11 | 22:04 | 50.033
2020-10-11 | 22:04 | 50.035
2020-10-11 | 22:04 | 50.037
2020-10-11 | 22:04 | 50.04
2020-10-11 | 22:04 | 50.042
2020-10-11 | 22:04 | 50.046
2020-10-11 | 22:04 | 50.049
2020-10-11 | 22:04 | 50.052
2020-10-11 | 22:04 | 50.054
2020-10-11 | 22:04 | 50.054
2020-10-11 | 22:04 | 50.056
2020-10-11 | 22:04 | 50.056
2020-10-11 | 22:04 | 50.057
2020-10-11 | 22:04 | 50.058
2020-10-11 | 22:04 | 50.058
2020-10-11 | 22:04 | 50.055
2020-10-11 | 22:04 | 50.052
2020-10-11 | 22:04 | 50.05
2020-10-11 | 22:04 | 50.05
2020-10-11 | 22:04 | 50.05
2020-10-11 | 22:04 | 50.051
2020-10-11 | 22:04 | 50.051
2020-10-11 | 22:04 | 50.053
2020-10-11 | 22:04 | 50.054
2020-10-11 | 22:04 | 50.056
2020-10-11 | 22:04 | 50.057
2020-10-11 | 22:04 | 50.057
2020-10-11 | 22:04 | 50.057
2020-10-11 | 22:04 | 50.057
2020-10-11 | 22:04 | 50.057
2020-10-11 | 22:04 | 50.055
2020-10-11 | 22:04 | 50.054
2020-10-11 | 22:04 | 50.053
2020-10-11 | 22:04 | 50.051
2020-10-11 | 22:04 | 50.05
2020-10-11 | 22:04 | 50.047
2020-10-11 | 22:04 | 50.046
2020-10-11 | 22:04 | 50.044
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.044
2020-10-11 | 22:04 | 50.045
2020-10-11 | 22:04 | 50.047
2020-10-11 | 22:04 | 50.047
2020-10-11 | 22:04 | 50.047
2020-10-11 | 22:04 | 50.047
2020-10-11 | 22:04 | 50.047
2020-10-11 | 22:04 | 50.045
2020-10-11 | 22:04 | 50.044
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.044
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.043
2020-10-11 | 22:04 | 50.045
2020-10-11 | 22:04 | 50.045
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.043
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.045
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.043
2020-10-11 | 22:05 | 50.043
2020-10-11 | 22:05 | 50.043
2020-10-11 | 22:05 | 50.044
2020-10-11 | 22:05 | 50.045
2020-10-11 | 22:05 | 50.048
2020-10-11 | 22:05 | 50.048
2020-10-11 | 22:05 | 50.049
2020-10-11 | 22:05 | 50.05
2020-10-11 | 22:05 | 50.05
2020-10-11 | 22:05 | 50.049
2020-10-11 | 22:05 | 50.047
2020-10-11 | 22:05 | 50.045
2020-10-11 | 22:05 | 50.042
2020-10-11 | 22:05 | 50.04
2020-10-11 | 22:05 | 50.039
2020-10-11 | 22:05 | 50.038
2020-10-11 | 22:05 | 50.038
2020-10-11 | 22:05 | 50.04
2020-10-11 | 22:05 | 50.041
2020-10-11 | 22:05 | 50.041
2020-10-11 | 22:05 | 50.039
2020-10-11 | 22:05 | 50.035
2020-10-11 | 22:05 | 50.032
2020-10-11 | 22:05 | 50.029
2020-10-11 | 22:05 | 50.026
2020-10-11 | 22:05 | 50.025
2020-10-11 | 22:05 | 50.023
2020-10-11 | 22:05 | 50.024
2020-10-11 | 22:05 | 50.027
2020-10-11 | 22:05 | 50.031
2020-10-11 | 22:05 | 50.034
2020-10-11 | 22:05 | 50.036
2020-10-11 | 22:05 | 50.038
2020-10-11 | 22:05 | 50.041
2020-10-11 | 22:05 | 50.042
2020-10-11 | 22:05 | 50.042
2020-10-11 | 22:05 | 50.043
2020-10-11 | 22:05 | 50.043
2020-10-11 | 22:05 | 50.046
2020-10-11 | 22:05 | 50.049
2020-10-11 | 22:05 | 50.053
2020-10-11 | 22:05 | 50.057
2020-10-11 | 22:05 | 50.061
2020-10-11 | 22:05 | 50.063
2020-10-11 | 22:05 | 50.065
2020-10-11 | 22:05 | 50.066
2020-10-11 | 22:05 | 50.067
2020-10-11 | 22:05 | 50.067
2020-10-11 | 22:05 | 50.065
2020-10-11 | 22:05 | 50.063
2020-10-11 | 22:05 | 50.061
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.06
2020-10-11 | 22:06 | 50.061
2020-10-11 | 22:06 | 50.061
2020-10-11 | 22:06 | 50.062
2020-10-11 | 22:06 | 50.063
2020-10-11 | 22:06 | 50.062
2020-10-11 | 22:06 | 50.063
2020-10-11 | 22:06 | 50.064
2020-10-11 | 22:06 | 50.064
2020-10-11 | 22:06 | 50.063
2020-10-11 | 22:06 | 50.062
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.059
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.06
2020-10-11 | 22:06 | 50.06
2020-10-11 | 22:06 | 50.06
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.058
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.057
2020-10-11 | 22:06 | 50.056
2020-10-11 | 22:06 | 50.055
2020-10-11 | 22:06 | 50.054
2020-10-11 | 22:06 | 50.052
2020-10-11 | 22:06 | 50.051
2020-10-11 | 22:06 | 50.049
2020-10-11 | 22:06 | 50.048
2020-10-11 | 22:06 | 50.046
2020-10-11 | 22:06 | 50.044
2020-10-11 | 22:06 | 50.041
2020-10-11 | 22:06 | 50.038
2020-10-11 | 22:06 | 50.037
2020-10-11 | 22:06 | 50.036
2020-10-11 | 22:06 | 50.035
2020-10-11 | 22:06 | 50.035
2020-10-11 | 22:06 | 50.033
2020-10-11 | 22:06 | 50.032
2020-10-11 | 22:06 | 50.029
2020-10-11 | 22:07 | 50.026
2020-10-11 | 22:07 | 50.024
2020-10-11 | 22:07 | 50.022
2020-10-11 | 22:07 | 50.021
2020-10-11 | 22:07 | 50.02
2020-10-11 | 22:07 | 50.017
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.02
2020-10-11 | 22:07 | 50.022
2020-10-11 | 22:07 | 50.024
2020-10-11 | 22:07 | 50.023
2020-10-11 | 22:07 | 50.023
2020-10-11 | 22:07 | 50.021
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.018
2020-10-11 | 22:07 | 50.015
2020-10-11 | 22:07 | 50.013
2020-10-11 | 22:07 | 50.011
2020-10-11 | 22:07 | 50.009
2020-10-11 | 22:07 | 50.008
2020-10-11 | 22:07 | 50.007
2020-10-11 | 22:07 | 50.006
2020-10-11 | 22:07 | 50.004
2020-10-11 | 22:07 | 50
2020-10-11 | 22:07 | 49.996
2020-10-11 | 22:07 | 49.991
2020-10-11 | 22:07 | 49.984
2020-10-11 | 22:07 | 49.979
2020-10-11 | 22:07 | 49.977
2020-10-11 | 22:07 | 49.98
2020-10-11 | 22:07 | 49.984
2020-10-11 | 22:07 | 49.988
2020-10-11 | 22:07 | 49.989
2020-10-11 | 22:07 | 49.991
2020-10-11 | 22:07 | 49.991
2020-10-11 | 22:07 | 49.995
2020-10-11 | 22:07 | 49.997
2020-10-11 | 22:07 | 49.997
2020-10-11 | 22:07 | 49.995
2020-10-11 | 22:07 | 49.993
2020-10-11 | 22:07 | 49.993
2020-10-11 | 22:07 | 49.995
2020-10-11 | 22:07 | 49.999
2020-10-11 | 22:07 | 50.003
2020-10-11 | 22:07 | 50.008
2020-10-11 | 22:07 | 50.011
2020-10-11 | 22:07 | 50.014
2020-10-11 | 22:07 | 50.016
2020-10-11 | 22:07 | 50.018
2020-10-11 | 22:07 | 50.02
2020-10-11 | 22:07 | 50.019
2020-10-11 | 22:07 | 50.014
2020-10-11 | 22:07 | 50.01
2020-10-11 | 22:07 | 50.007
2020-10-11 | 22:07 | 50.008
2020-10-11 | 22:08 | 50.008
2020-10-11 | 22:08 | 50.01
2020-10-11 | 22:08 | 50.009
2020-10-11 | 22:08 | 50.008
2020-10-11 | 22:08 | 50.008
2020-10-11 | 22:08 | 50.007
2020-10-11 | 22:08 | 50.006
2020-10-11 | 22:08 | 50.006
2020-10-11 | 22:08 | 50.005
2020-10-11 | 22:08 | 50.004
2020-10-11 | 22:08 | 50.003
2020-10-11 | 22:08 | 50
2020-10-11 | 22:08 | 49.999
2020-10-11 | 22:08 | 49.999
2020-10-11 | 22:08 | 49.997
2020-10-11 | 22:08 | 49.996
2020-10-11 | 22:08 | 49.996
2020-10-11 | 22:08 | 49.995
2020-10-11 | 22:08 | 49.997
2020-10-11 | 22:08 | 50
2020-10-11 | 22:08 | 50.003
2020-10-11 | 22:08 | 50.006
2020-10-11 | 22:08 | 50.01
2020-10-11 | 22:08 | 50.013
2020-10-11 | 22:08 | 50.016
2020-10-11 | 22:08 | 50.02
2020-10-11 | 22:08 | 50.022
2020-10-11 | 22:08 | 50.022
2020-10-11 | 22:08 | 50.021
2020-10-11 | 22:08 | 50.02
2020-10-11 | 22:08 | 50.018
2020-10-11 | 22:08 | 50.016
2020-10-11 | 22:08 | 50.015
2020-10-11 | 22:08 | 50.012
2020-10-11 | 22:08 | 50.009
2020-10-11 | 22:08 | 50.008
2020-10-11 | 22:08 | 50.007
2020-10-11 | 22:08 | 50.005
2020-10-11 | 22:08 | 50.004
2020-10-11 | 22:08 | 50.005
2020-10-11 | 22:08 | 50.006
2020-10-11 | 22:08 | 50.005
2020-10-11 | 22:08 | 50.003
2020-10-11 | 22:08 | 49.999
2020-10-11 | 22:08 | 49.996
2020-10-11 | 22:08 | 49.994
2020-10-11 | 22:08 | 49.99
2020-10-11 | 22:08 | 49.987
2020-10-11 | 22:08 | 49.984
2020-10-11 | 22:08 | 49.98
2020-10-11 | 22:08 | 49.978
2020-10-11 | 22:08 | 49.977
2020-10-11 | 22:08 | 49.976
2020-10-11 | 22:08 | 49.977
2020-10-11 | 22:08 | 49.978
2020-10-11 | 22:08 | 49.98
2020-10-11 | 22:08 | 49.981
2020-10-11 | 22:08 | 49.984
2020-10-11 | 22:08 | 49.986
2020-10-11 | 22:08 | 49.987
2020-10-11 | 22:08 | 49.987
2020-10-11 | 22:09 | 49.989
2020-10-11 | 22:09 | 49.99
2020-10-11 | 22:09 | 49.992
2020-10-11 | 22:09 | 49.994
2020-10-11 | 22:09 | 49.995
2020-10-11 | 22:09 | 49.998
2020-10-11 | 22:09 | 50
2020-10-11 | 22:09 | 50.001
2020-10-11 | 22:09 | 50.003
2020-10-11 | 22:09 | 50.003
2020-10-11 | 22:09 | 50.005
2020-10-11 | 22:09 | 50.007
2020-10-11 | 22:09 | 50.009
2020-10-11 | 22:09 | 50.009
2020-10-11 | 22:09 | 50.01
2020-10-11 | 22:09 | 50.01
2020-10-11 | 22:09 | 50.01
2020-10-11 | 22:09 | 50.011
2020-10-11 | 22:09 | 50.01
2020-10-11 | 22:09 | 50.01
2020-10-11 | 22:09 | 50.01
2020-10-11 | 22:09 | 50.007
2020-10-11 | 22:09 | 50.005
2020-10-11 | 22:09 | 50.002
2020-10-11 | 22:09 | 50.001
2020-10-11 | 22:09 | 50.001
2020-10-11 | 22:09 | 50
2020-10-11 | 22:09 | 49.999
2020-10-11 | 22:09 | 49.996
2020-10-11 | 22:09 | 49.995
2020-10-11 | 22:09 | 49.993
2020-10-11 | 22:09 | 49.995
2020-10-11 | 22:09 | 49.994
2020-10-11 | 22:09 | 49.995
2020-10-11 | 22:09 | 49.994
2020-10-11 | 22:09 | 49.992
2020-10-11 | 22:09 | 49.988
2020-10-11 | 22:09 | 49.985
2020-10-11 | 22:09 | 49.981
2020-10-11 | 22:09 | 49.976
2020-10-11 | 22:09 | 49.972
2020-10-11 | 22:09 | 49.967
2020-10-11 | 22:09 | 49.966
2020-10-11 | 22:09 | 49.965
2020-10-11 | 22:09 | 49.964
2020-10-11 | 22:09 | 49.965
2020-10-11 | 22:09 | 49.964
2020-10-11 | 22:09 | 49.966
2020-10-11 | 22:09 | 49.968
2020-10-11 | 22:09 | 49.97
2020-10-11 | 22:09 | 49.97
2020-10-11 | 22:09 | 49.972
2020-10-11 | 22:09 | 49.974
2020-10-11 | 22:09 | 49.976
2020-10-11 | 22:09 | 49.976
2020-10-11 | 22:09 | 49.977
2020-10-11 | 22:09 | 49.98
2020-10-11 | 22:09 | 49.98
2020-10-11 | 22:09 | 49.98
2020-10-11 | 22:10 | 49.979
2020-10-11 | 22:10 | 49.977
2020-10-11 | 22:10 | 49.977
2020-10-11 | 22:10 | 49.975
2020-10-11 | 22:10 | 49.974
2020-10-11 | 22:10 | 49.972
2020-10-11 | 22:10 | 49.97
2020-10-11 | 22:10 | 49.967
2020-10-11 | 22:10 | 49.965
2020-10-11 | 22:10 | 49.962
2020-10-11 | 22:10 | 49.96
2020-10-11 | 22:10 | 49.956
2020-10-11 | 22:10 | 49.954
2020-10-11 | 22:10 | 49.952
2020-10-11 | 22:10 | 49.951
2020-10-11 | 22:10 | 49.952
2020-10-11 | 22:10 | 49.952
2020-10-11 | 22:10 | 49.954
2020-10-11 | 22:10 | 49.959
2020-10-11 | 22:10 | 49.965
2020-10-11 | 22:10 | 49.97
2020-10-11 | 22:10 | 49.974
2020-10-11 | 22:10 | 49.978
2020-10-11 | 22:10 | 49.981
2020-10-11 | 22:10 | 49.984
2020-10-11 | 22:10 | 49.986
2020-10-11 | 22:10 | 49.986
2020-10-11 | 22:10 | 49.983
2020-10-11 | 22:10 | 49.981
2020-10-11 | 22:10 | 49.976
2020-10-11 | 22:10 | 49.971
2020-10-11 | 22:10 | 49.965
2020-10-11 | 22:10 | 49.958
2020-10-11 | 22:10 | 49.95
2020-10-11 | 22:10 | 49.944
2020-10-11 | 22:10 | 49.939
2020-10-11 | 22:10 | 49.935
2020-10-11 | 22:10 | 49.932
2020-10-11 | 22:10 | 49.929
2020-10-11 | 22:10 | 49.929
2020-10-11 | 22:10 | 49.928
2020-10-11 | 22:10 | 49.928
2020-10-11 | 22:10 | 49.927
2020-10-11 | 22:10 | 49.929
2020-10-11 | 22:10 | 49.93
2020-10-11 | 22:10 | 49.931
2020-10-11 | 22:10 | 49.932
2020-10-11 | 22:10 | 49.933
2020-10-11 | 22:10 | 49.933
2020-10-11 | 22:10 | 49.933
2020-10-11 | 22:10 | 49.931
2020-10-11 | 22:10 | 49.93
2020-10-11 | 22:10 | 49.93
2020-10-11 | 22:10 | 49.93
2020-10-11 | 22:10 | 49.929
2020-10-11 | 22:10 | 49.928
2020-10-11 | 22:10 | 49.928
2020-10-11 | 22:10 | 49.926
2020-10-11 | 22:10 | 49.927
2020-10-11 | 22:10 | 49.927
2020-10-11 | 22:10 | 49.928
2020-10-11 | 22:11 | 49.93
2020-10-11 | 22:11 | 49.933
2020-10-11 | 22:11 | 49.935
2020-10-11 | 22:11 | 49.936
2020-10-11 | 22:11 | 49.937
2020-10-11 | 22:11 | 49.936
2020-10-11 | 22:11 | 49.938
2020-10-11 | 22:11 | 49.944
2020-10-11 | 22:11 | 49.949
2020-10-11 | 22:11 | 49.952
2020-10-11 | 22:11 | 49.954
2020-10-11 | 22:11 | 49.955
2020-10-11 | 22:11 | 49.956
2020-10-11 | 22:11 | 49.958
2020-10-11 | 22:11 | 49.96
2020-10-11 | 22:11 | 49.962
2020-10-11 | 22:11 | 49.963
2020-10-11 | 22:11 | 49.964
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:11 | 49.964
2020-10-11 | 22:11 | 49.961
2020-10-11 | 22:11 | 49.958
2020-10-11 | 22:11 | 49.955
2020-10-11 | 22:11 | 49.952
2020-10-11 | 22:11 | 49.949
2020-10-11 | 22:11 | 49.949
2020-10-11 | 22:11 | 49.949
2020-10-11 | 22:11 | 49.95
2020-10-11 | 22:11 | 49.95
2020-10-11 | 22:11 | 49.95
2020-10-11 | 22:11 | 49.949
2020-10-11 | 22:11 | 49.949
2020-10-11 | 22:11 | 49.947
2020-10-11 | 22:11 | 49.945
2020-10-11 | 22:11 | 49.944
2020-10-11 | 22:11 | 49.943
2020-10-11 | 22:11 | 49.946
2020-10-11 | 22:11 | 49.95
2020-10-11 | 22:11 | 49.952
2020-10-11 | 22:11 | 49.954
2020-10-11 | 22:11 | 49.955
2020-10-11 | 22:11 | 49.957
2020-10-11 | 22:11 | 49.958
2020-10-11 | 22:11 | 49.958
2020-10-11 | 22:11 | 49.956
2020-10-11 | 22:11 | 49.954
2020-10-11 | 22:11 | 49.952
2020-10-11 | 22:11 | 49.951
2020-10-11 | 22:11 | 49.952
2020-10-11 | 22:11 | 49.954
2020-10-11 | 22:11 | 49.958
2020-10-11 | 22:11 | 49.96
2020-10-11 | 22:11 | 49.963
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:11 | 49.965
2020-10-11 | 22:12 | 49.964
2020-10-11 | 22:12 | 49.961
2020-10-11 | 22:12 | 49.96
2020-10-11 | 22:12 | 49.959
2020-10-11 | 22:12 | 49.958
2020-10-11 | 22:12 | 49.957
2020-10-11 | 22:12 | 49.957
2020-10-11 | 22:12 | 49.957
2020-10-11 | 22:12 | 49.956
2020-10-11 | 22:12 | 49.954
2020-10-11 | 22:12 | 49.953
2020-10-11 | 22:12 | 49.952
2020-10-11 | 22:12 | 49.954
2020-10-11 | 22:12 | 49.954
2020-10-11 | 22:12 | 49.956
2020-10-11 | 22:12 | 49.956
2020-10-11 | 22:12 | 49.959
2020-10-11 | 22:12 | 49.961
2020-10-11 | 22:12 | 49.962
2020-10-11 | 22:12 | 49.964
2020-10-11 | 22:12 | 49.965
2020-10-11 | 22:12 | 49.967
2020-10-11 | 22:12 | 49.968
2020-10-11 | 22:12 | 49.97
2020-10-11 | 22:12 | 49.974
2020-10-11 | 22:12 | 49.977
2020-10-11 | 22:12 | 49.979
2020-10-11 | 22:12 | 49.98
2020-10-11 | 22:12 | 49.982
2020-10-11 | 22:12 | 49.984
2020-10-11 | 22:12 | 49.984
2020-10-11 | 22:12 | 49.984
2020-10-11 | 22:12 | 49.984
2020-10-11 | 22:12 | 49.984
2020-10-11 | 22:12 | 49.985
2020-10-11 | 22:12 | 49.985
2020-10-11 | 22:12 | 49.985
2020-10-11 | 22:12 | 49.985
2020-10-11 | 22:12 | 49.983
2020-10-11 | 22:12 | 49.981
2020-10-11 | 22:12 | 49.979
2020-10-11 | 22:12 | 49.976
2020-10-11 | 22:12 | 49.974
2020-10-11 | 22:12 | 49.971
2020-10-11 | 22:12 | 49.969
2020-10-11 | 22:12 | 49.966
2020-10-11 | 22:12 | 49.964
2020-10-11 | 22:12 | 49.962
2020-10-11 | 22:12 | 49.961
2020-10-11 | 22:12 | 49.961
2020-10-11 | 22:12 | 49.96
2020-10-11 | 22:12 | 49.96
2020-10-11 | 22:12 | 49.962
2020-10-11 | 22:12 | 49.964
2020-10-11 | 22:12 | 49.967
2020-10-11 | 22:12 | 49.969
2020-10-11 | 22:12 | 49.97
2020-10-11 | 22:12 | 49.971
2020-10-11 | 22:12 | 49.97
2020-10-11 | 22:12 | 49.971
2020-10-11 | 22:12 | 49.973
2020-10-11 | 22:13 | 49.974
2020-10-11 | 22:13 | 49.976
2020-10-11 | 22:13 | 49.977
2020-10-11 | 22:13 | 49.978
2020-10-11 | 22:13 | 49.978
2020-10-11 | 22:13 | 49.977
2020-10-11 | 22:13 | 49.978
2020-10-11 | 22:13 | 49.979
2020-10-11 | 22:13 | 49.979
2020-10-11 | 22:13 | 49.978
2020-10-11 | 22:13 | 49.977
2020-10-11 | 22:13 | 49.976
2020-10-11 | 22:13 | 49.978
2020-10-11 | 22:13 | 49.98
2020-10-11 | 22:13 | 49.983
2020-10-11 | 22:13 | 49.986
2020-10-11 | 22:13 | 49.988
2020-10-11 | 22:13 | 49.99
2020-10-11 | 22:13 | 49.991
2020-10-11 | 22:13 | 49.992
2020-10-11 | 22:13 | 49.992
2020-10-11 | 22:13 | 49.991
2020-10-11 | 22:13 | 49.989
2020-10-11 | 22:13 | 49.989
2020-10-11 | 22:13 | 49.989
2020-10-11 | 22:13 | 49.991
2020-10-11 | 22:13 | 49.994
2020-10-11 | 22:13 | 49.994
2020-10-11 | 22:13 | 49.993
2020-10-11 | 22:13 | 49.992
2020-10-11 | 22:13 | 49.992
2020-10-11 | 22:13 | 49.991
2020-10-11 | 22:13 | 49.99
2020-10-11 | 22:13 | 49.989
2020-10-11 | 22:13 | 49.987
2020-10-11 | 22:13 | 49.986
2020-10-11 | 22:13 | 49.986
2020-10-11 | 22:13 | 49.991
2020-10-11 | 22:13 | 49.998
2020-10-11 | 22:13 | 50.004
2020-10-11 | 22:13 | 50.01
2020-10-11 | 22:13 | 50.015
2020-10-11 | 22:13 | 50.018
2020-10-11 | 22:13 | 50.021
2020-10-11 | 22:13 | 50.025
2020-10-11 | 22:13 | 50.026
2020-10-11 | 22:13 | 50.026
2020-10-11 | 22:13 | 50.024
2020-10-11 | 22:13 | 50.022
2020-10-11 | 22:13 | 50.02
2020-10-11 | 22:13 | 50.02
2020-10-11 | 22:13 | 50.02
2020-10-11 | 22:13 | 50.02
2020-10-11 | 22:13 | 50.019
2020-10-11 | 22:13 | 50.019
2020-10-11 | 22:13 | 50.021
2020-10-11 | 22:13 | 50.023
2020-10-11 | 22:13 | 50.024
2020-10-11 | 22:13 | 50.025
2020-10-11 | 22:14 | 50.026
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.027
2020-10-11 | 22:14 | 50.027
2020-10-11 | 22:14 | 50.025
2020-10-11 | 22:14 | 50.023
2020-10-11 | 22:14 | 50.021
2020-10-11 | 22:14 | 50.021
2020-10-11 | 22:14 | 50.023
2020-10-11 | 22:14 | 50.025
2020-10-11 | 22:14 | 50.025
2020-10-11 | 22:14 | 50.026
2020-10-11 | 22:14 | 50.027
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.03
2020-10-11 | 22:14 | 50.033
2020-10-11 | 22:14 | 50.036
2020-10-11 | 22:14 | 50.038
2020-10-11 | 22:14 | 50.039
2020-10-11 | 22:14 | 50.039
2020-10-11 | 22:14 | 50.039
2020-10-11 | 22:14 | 50.037
2020-10-11 | 22:14 | 50.037
2020-10-11 | 22:14 | 50.035
2020-10-11 | 22:14 | 50.032
2020-10-11 | 22:14 | 50.03
2020-10-11 | 22:14 | 50.028
2020-10-11 | 22:14 | 50.027
2020-10-11 | 22:14 | 50.025
2020-10-11 | 22:14 | 50.024
2020-10-11 | 22:14 | 50.024
2020-10-11 | 22:14 | 50.023
2020-10-11 | 22:14 | 50.021
2020-10-11 | 22:14 | 50.017
2020-10-11 | 22:14 | 50.014
2020-10-11 | 22:14 | 50.011
2020-10-11 | 22:14 | 50.01
2020-10-11 | 22:14 | 50.008
2020-10-11 | 22:14 | 50.008
2020-10-11 | 22:14 | 50.009
2020-10-11 | 22:14 | 50.01
2020-10-11 | 22:14 | 50.011
2020-10-11 | 22:14 | 50.012
2020-10-11 | 22:14 | 50.013
2020-10-11 | 22:14 | 50.016
2020-10-11 | 22:14 | 50.018
2020-10-11 | 22:14 | 50.02
2020-10-11 | 22:14 | 50.022
2020-10-11 | 22:14 | 50.025
2020-10-11 | 22:14 | 50.026
2020-10-11 | 22:14 | 50.027
2020-10-11 | 22:15 | 50.026
2020-10-11 | 22:15 | 50.027
2020-10-11 | 22:15 | 50.024
2020-10-11 | 22:15 | 50.023
2020-10-11 | 22:15 | 50.02
2020-10-11 | 22:15 | 50.019
2020-10-11 | 22:15 | 50.02
2020-10-11 | 22:15 | 50.021
2020-10-11 | 22:15 | 50.022
2020-10-11 | 22:15 | 50.023
2020-10-11 | 22:15 | 50.022
2020-10-11 | 22:15 | 50.022
2020-10-11 | 22:15 | 50.022
2020-10-11 | 22:15 | 50.022
2020-10-11 | 22:15 | 50.021
2020-10-11 | 22:15 | 50.019
2020-10-11 | 22:15 | 50.017
2020-10-11 | 22:15 | 50.014
2020-10-11 | 22:15 | 50.012
2020-10-11 | 22:15 | 50.011
2020-10-11 | 22:15 | 50.011
2020-10-11 | 22:15 | 50.011
2020-10-11 | 22:15 | 50.012
2020-10-11 | 22:15 | 50.012
2020-10-11 | 22:15 | 50.012
2020-10-11 | 22:15 | 50.012
2020-10-11 | 22:15 | 50.013
2020-10-11 | 22:15 | 50.014
2020-10-11 | 22:15 | 50.015
2020-10-11 | 22:15 | 50.015
2020-10-11 | 22:15 | 50.011
2020-10-11 | 22:15 | 50.009
2020-10-11 | 22:15 | 50.007
2020-10-11 | 22:15 | 50.007
2020-10-11 | 22:15 | 50.006
2020-10-11 | 22:15 | 50.006
2020-10-11 | 22:15 | 50.005
2020-10-11 | 22:15 | 50.004
2020-10-11 | 22:15 | 50.002
2020-10-11 | 22:15 | 50
2020-10-11 | 22:15 | 49.997
2020-10-11 | 22:15 | 49.995
2020-10-11 | 22:15 | 49.991
2020-10-11 | 22:15 | 49.987
2020-10-11 | 22:15 | 49.984
2020-10-11 | 22:15 | 49.982
2020-10-11 | 22:15 | 49.983
2020-10-11 | 22:15 | 49.984
2020-10-11 | 22:15 | 49.985
2020-10-11 | 22:15 | 49.987
2020-10-11 | 22:15 | 49.988
2020-10-11 | 22:15 | 49.99
2020-10-11 | 22:15 | 49.99
2020-10-11 | 22:15 | 49.991
2020-10-11 | 22:15 | 49.991
2020-10-11 | 22:15 | 49.993
2020-10-11 | 22:15 | 49.995
2020-10-11 | 22:15 | 49.998
2020-10-11 | 22:15 | 50.001
2020-10-11 | 22:16 | 50.004
2020-10-11 | 22:16 | 50.008
2020-10-11 | 22:16 | 50.011
2020-10-11 | 22:16 | 50.014
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.017
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.017
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.015
2020-10-11 | 22:16 | 50.014
2020-10-11 | 22:16 | 50.013
2020-10-11 | 22:16 | 50.012
2020-10-11 | 22:16 | 50.012
2020-10-11 | 22:16 | 50.014
2020-10-11 | 22:16 | 50.015
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.017
2020-10-11 | 22:16 | 50.017
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.017
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.02
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.022
2020-10-11 | 22:16 | 50.022
2020-10-11 | 22:16 | 50.023
2020-10-11 | 22:16 | 50.021
2020-10-11 | 22:16 | 50.02
2020-10-11 | 22:16 | 50.018
2020-10-11 | 22:16 | 50.017
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.015
2020-10-11 | 22:16 | 50.013
2020-10-11 | 22:16 | 50.012
2020-10-11 | 22:16 | 50.011
2020-10-11 | 22:16 | 50.011
2020-10-11 | 22:16 | 50.012
2020-10-11 | 22:16 | 50.014
2020-10-11 | 22:16 | 50.016
2020-10-11 | 22:16 | 50.019
2020-10-11 | 22:16 | 50.022
2020-10-11 | 22:16 | 50.024
2020-10-11 | 22:16 | 50.025
2020-10-11 | 22:16 | 50.024
2020-10-11 | 22:16 | 50.024
2020-10-11 | 22:16 | 50.023
2020-10-11 | 22:17 | 50.021
2020-10-11 | 22:17 | 50.021
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.018
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.018
2020-10-11 | 22:17 | 50.02
2020-10-11 | 22:17 | 50.022
2020-10-11 | 22:17 | 50.022
2020-10-11 | 22:17 | 50.02
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.018
2020-10-11 | 22:17 | 50.016
2020-10-11 | 22:17 | 50.014
2020-10-11 | 22:17 | 50.014
2020-10-11 | 22:17 | 50.014
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.017
2020-10-11 | 22:17 | 50.018
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.02
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.017
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.013
2020-10-11 | 22:17 | 50.012
2020-10-11 | 22:17 | 50.013
2020-10-11 | 22:17 | 50.013
2020-10-11 | 22:17 | 50.014
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.015
2020-10-11 | 22:17 | 50.016
2020-10-11 | 22:17 | 50.017
2020-10-11 | 22:17 | 50.016
2020-10-11 | 22:17 | 50.014
2020-10-11 | 22:17 | 50.013
2020-10-11 | 22:17 | 50.013
2020-10-11 | 22:17 | 50.014
2020-10-11 | 22:17 | 50.016
2020-10-11 | 22:17 | 50.019
2020-10-11 | 22:17 | 50.024
2020-10-11 | 22:17 | 50.029
2020-10-11 | 22:17 | 50.033
2020-10-11 | 22:17 | 50.035
2020-10-11 | 22:17 | 50.037
2020-10-11 | 22:17 | 50.037
2020-10-11 | 22:17 | 50.038
2020-10-11 | 22:17 | 50.037
2020-10-11 | 22:17 | 50.037
2020-10-11 | 22:17 | 50.035
2020-10-11 | 22:17 | 50.035
2020-10-11 | 22:17 | 50.036
2020-10-11 | 22:17 | 50.037
2020-10-11 | 22:17 | 50.038
2020-10-11 | 22:18 | 50.038
2020-10-11 | 22:18 | 50.036
2020-10-11 | 22:18 | 50.035
2020-10-11 | 22:18 | 50.033
2020-10-11 | 22:18 | 50.034
2020-10-11 | 22:18 | 50.036
2020-10-11 | 22:18 | 50.037
2020-10-11 | 22:18 | 50.038
2020-10-11 | 22:18 | 50.038
2020-10-11 | 22:18 | 50.039
2020-10-11 | 22:18 | 50.039
2020-10-11 | 22:18 | 50.038
2020-10-11 | 22:18 | 50.037
2020-10-11 | 22:18 | 50.035
2020-10-11 | 22:18 | 50.033
2020-10-11 | 22:18 | 50.031
2020-10-11 | 22:18 | 50.029
2020-10-11 | 22:18 | 50.029
2020-10-11 | 22:18 | 50.029
2020-10-11 | 22:18 | 50.029
2020-10-11 | 22:18 | 50.03
2020-10-11 | 22:18 | 50.03
2020-10-11 | 22:18 | 50.03
2020-10-11 | 22:18 | 50.029
2020-10-11 | 22:18 | 50.03
2020-10-11 | 22:18 | 50.032
2020-10-11 | 22:18 | 50.035
2020-10-11 | 22:18 | 50.036
2020-10-11 | 22:18 | 50.038
2020-10-11 | 22:18 | 50.039
2020-10-11 | 22:18 | 50.038
2020-10-11 | 22:18 | 50.037
2020-10-11 | 22:18 | 50.035
2020-10-11 | 22:18 | 50.034
2020-10-11 | 22:18 | 50.033
2020-10-11 | 22:18 | 50.032
2020-10-11 | 22:18 | 50.032
2020-10-11 | 22:18 | 50.032
2020-10-11 | 22:18 | 50.032
2020-10-11 | 22:18 | 50.03
2020-10-11 | 22:18 | 50.028
2020-10-11 | 22:18 | 50.026
2020-10-11 | 22:18 | 50.024
2020-10-11 | 22:18 | 50.021
2020-10-11 | 22:18 | 50.019
2020-10-11 | 22:18 | 50.015
2020-10-11 | 22:18 | 50.013
2020-10-11 | 22:18 | 50.012
2020-10-11 | 22:18 | 50.011
2020-10-11 | 22:18 | 50.013
2020-10-11 | 22:18 | 50.015
2020-10-11 | 22:18 | 50.017
2020-10-11 | 22:18 | 50.017
2020-10-11 | 22:18 | 50.019
2020-10-11 | 22:18 | 50.021
2020-10-11 | 22:18 | 50.022
2020-10-11 | 22:18 | 50.022
2020-10-11 | 22:18 | 50.022
2020-10-11 | 22:18 | 50.022
2020-10-11 | 22:18 | 50.021
2020-10-11 | 22:18 | 50.022
2020-10-11 | 22:19 | 50.023
2020-10-11 | 22:19 | 50.024
2020-10-11 | 22:19 | 50.026
2020-10-11 | 22:19 | 50.026
2020-10-11 | 22:19 | 50.024
2020-10-11 | 22:19 | 50.025
2020-10-11 | 22:19 | 50.023
2020-10-11 | 22:19 | 50.022
2020-10-11 | 22:19 | 50.021
2020-10-11 | 22:19 | 50.02
2020-10-11 | 22:19 | 50.018
2020-10-11 | 22:19 | 50.017
2020-10-11 | 22:19 | 50.015
2020-10-11 | 22:19 | 50.012
2020-10-11 | 22:19 | 50.013
2020-10-11 | 22:19 | 50.016
2020-10-11 | 22:19 | 50.019
2020-10-11 | 22:19 | 50.019
2020-10-11 | 22:19 | 50.02
2020-10-11 | 22:19 | 50.02
2020-10-11 | 22:19 | 50.022
2020-10-11 | 22:19 | 50.022
2020-10-11 | 22:19 | 50.021
2020-10-11 | 22:19 | 50.019
2020-10-11 | 22:19 | 50.017
2020-10-11 | 22:19 | 50.017
2020-10-11 | 22:19 | 50.017
2020-10-11 | 22:19 | 50.018
2020-10-11 | 22:19 | 50.021
2020-10-11 | 22:19 | 50.02
2020-10-11 | 22:19 | 50.019
2020-10-11 | 22:19 | 50.017
2020-10-11 | 22:19 | 50.016
2020-10-11 | 22:19 | 50.016
2020-10-11 | 22:19 | 50.014
2020-10-11 | 22:19 | 50.011
2020-10-11 | 22:19 | 50.008
2020-10-11 | 22:19 | 50.005
2020-10-11 | 22:19 | 50.001
2020-10-11 | 22:19 | 49.998
2020-10-11 | 22:19 | 49.999
2020-10-11 | 22:19 | 49.998
2020-10-11 | 22:19 | 49.998
2020-10-11 | 22:19 | 50
2020-10-11 | 22:19 | 50.002
2020-10-11 | 22:19 | 50.006
2020-10-11 | 22:19 | 50.008
2020-10-11 | 22:19 | 50.008
2020-10-11 | 22:19 | 50.01
2020-10-11 | 22:19 | 50.01
2020-10-11 | 22:19 | 50.01
2020-10-11 | 22:19 | 50.011
2020-10-11 | 22:19 | 50.014
2020-10-11 | 22:19 | 50.016
2020-10-11 | 22:19 | 50.017
2020-10-11 | 22:19 | 50.019
2020-10-11 | 22:19 | 50.021
2020-10-11 | 22:19 | 50.022
2020-10-11 | 22:19 | 50.025
2020-10-11 | 22:20 | 50.028
2020-10-11 | 22:20 | 50.032
2020-10-11 | 22:20 | 50.036
2020-10-11 | 22:20 | 50.037
2020-10-11 | 22:20 | 50.04
2020-10-11 | 22:20 | 50.04
2020-10-11 | 22:20 | 50.035
2020-10-11 | 22:20 | 50.029
2020-10-11 | 22:20 | 50.026
2020-10-11 | 22:20 | 50.021
2020-10-11 | 22:20 | 50.017
2020-10-11 | 22:20 | 50.013
2020-10-11 | 22:20 | 50.011
2020-10-11 | 22:20 | 50.01
2020-10-11 | 22:20 | 50.009
2020-10-11 | 22:20 | 50.009
2020-10-11 | 22:20 | 50.008
2020-10-11 | 22:20 | 50.007
2020-10-11 | 22:20 | 50.008
2020-10-11 | 22:20 | 50.008
2020-10-11 | 22:20 | 50.008
2020-10-11 | 22:20 | 50.008
2020-10-11 | 22:20 | 50.006
2020-10-11 | 22:20 | 50.006
2020-10-11 | 22:20 | 50.005
2020-10-11 | 22:20 | 50.006
2020-10-11 | 22:20 | 50.004
2020-10-11 | 22:20 | 50.004
2020-10-11 | 22:20 | 50.002
2020-10-11 | 22:20 | 50.001
2020-10-11 | 22:20 | 50
2020-10-11 | 22:20 | 49.999
2020-10-11 | 22:20 | 49.998
2020-10-11 | 22:20 | 49.995
2020-10-11 | 22:20 | 49.991
2020-10-11 | 22:20 | 49.988
2020-10-11 | 22:20 | 49.981
2020-10-11 | 22:20 | 49.975
2020-10-11 | 22:20 | 49.97
2020-10-11 | 22:20 | 49.968
2020-10-11 | 22:20 | 49.968
2020-10-11 | 22:20 | 49.966
2020-10-11 | 22:20 | 49.964
2020-10-11 | 22:20 | 49.963
2020-10-11 | 22:20 | 49.961
2020-10-11 | 22:20 | 49.96
2020-10-11 | 22:20 | 49.961
2020-10-11 | 22:20 | 49.963
2020-10-11 | 22:20 | 49.965
2020-10-11 | 22:20 | 49.965
2020-10-11 | 22:20 | 49.965
2020-10-11 | 22:20 | 49.968
2020-10-11 | 22:20 | 49.969
2020-10-11 | 22:20 | 49.97
2020-10-11 | 22:20 | 49.972
2020-10-11 | 22:20 | 49.97
2020-10-11 | 22:20 | 49.969
2020-10-11 | 22:20 | 49.966
2020-10-11 | 22:20 | 49.965
2020-10-11 | 22:20 | 49.968
2020-10-11 | 22:20 | 49.969
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.977
2020-10-11 | 22:21 | 49.979
2020-10-11 | 22:21 | 49.982
2020-10-11 | 22:21 | 49.987
2020-10-11 | 22:21 | 49.99
2020-10-11 | 22:21 | 49.992
2020-10-11 | 22:21 | 49.994
2020-10-11 | 22:21 | 49.997
2020-10-11 | 22:21 | 49.995
2020-10-11 | 22:21 | 49.994
2020-10-11 | 22:21 | 49.994
2020-10-11 | 22:21 | 49.993
2020-10-11 | 22:21 | 49.993
2020-10-11 | 22:21 | 49.993
2020-10-11 | 22:21 | 49.991
2020-10-11 | 22:21 | 49.988
2020-10-11 | 22:21 | 49.987
2020-10-11 | 22:21 | 49.983
2020-10-11 | 22:21 | 49.98
2020-10-11 | 22:21 | 49.976
2020-10-11 | 22:21 | 49.976
2020-10-11 | 22:21 | 49.975
2020-10-11 | 22:21 | 49.975
2020-10-11 | 22:21 | 49.977
2020-10-11 | 22:21 | 49.981
2020-10-11 | 22:21 | 49.987
2020-10-11 | 22:21 | 49.991
2020-10-11 | 22:21 | 49.992
2020-10-11 | 22:21 | 49.993
2020-10-11 | 22:21 | 49.991
2020-10-11 | 22:21 | 49.99
2020-10-11 | 22:21 | 49.987
2020-10-11 | 22:21 | 49.985
2020-10-11 | 22:21 | 49.981
2020-10-11 | 22:21 | 49.977
2020-10-11 | 22:21 | 49.972
2020-10-11 | 22:21 | 49.968
2020-10-11 | 22:21 | 49.967
2020-10-11 | 22:21 | 49.969
2020-10-11 | 22:21 | 49.97
2020-10-11 | 22:21 | 49.971
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.975
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.972
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.973
2020-10-11 | 22:21 | 49.974
2020-10-11 | 22:22 | 49.976
2020-10-11 | 22:22 | 49.978
2020-10-11 | 22:22 | 49.98
2020-10-11 | 22:22 | 49.981
2020-10-11 | 22:22 | 49.981
2020-10-11 | 22:22 | 49.984
2020-10-11 | 22:22 | 49.985
2020-10-11 | 22:22 | 49.99
2020-10-11 | 22:22 | 49.992
2020-10-11 | 22:22 | 49.993
2020-10-11 | 22:22 | 49.994
2020-10-11 | 22:22 | 49.994
2020-10-11 | 22:22 | 49.995
2020-10-11 | 22:22 | 49.994
2020-10-11 | 22:22 | 49.993
2020-10-11 | 22:22 | 49.991
2020-10-11 | 22:22 | 49.989
2020-10-11 | 22:22 | 49.988
2020-10-11 | 22:22 | 49.987
2020-10-11 | 22:22 | 49.986
2020-10-11 | 22:22 | 49.984
2020-10-11 | 22:22 | 49.982
2020-10-11 | 22:22 | 49.979
2020-10-11 | 22:22 | 49.977
2020-10-11 | 22:22 | 49.976
2020-10-11 | 22:22 | 49.975
2020-10-11 | 22:22 | 49.973
2020-10-11 | 22:22 | 49.97
2020-10-11 | 22:22 | 49.968
2020-10-11 | 22:22 | 49.965
2020-10-11 | 22:22 | 49.965
2020-10-11 | 22:22 | 49.963
2020-10-11 | 22:22 | 49.962
2020-10-11 | 22:22 | 49.958
2020-10-11 | 22:22 | 49.958
2020-10-11 | 22:22 | 49.96
2020-10-11 | 22:22 | 49.96
2020-10-11 | 22:22 | 49.959
2020-10-11 | 22:22 | 49.958
2020-10-11 | 22:22 | 49.957
2020-10-11 | 22:22 | 49.958
2020-10-11 | 22:22 | 49.957
2020-10-11 | 22:22 | 49.957
2020-10-11 | 22:22 | 49.957
2020-10-11 | 22:22 | 49.96
2020-10-11 | 22:22 | 49.962
2020-10-11 | 22:22 | 49.966
2020-10-11 | 22:22 | 49.967
2020-10-11 | 22:22 | 49.967
2020-10-11 | 22:22 | 49.965
2020-10-11 | 22:22 | 49.965
2020-10-11 | 22:22 | 49.962
2020-10-11 | 22:22 | 49.961
2020-10-11 | 22:22 | 49.959
2020-10-11 | 22:22 | 49.956
2020-10-11 | 22:22 | 49.955
2020-10-11 | 22:22 | 49.954
2020-10-11 | 22:22 | 49.956
2020-10-11 | 22:22 | 49.957
2020-10-11 | 22:22 | 49.959
2020-10-11 | 22:22 | 49.958
2020-10-11 | 22:23 | 49.958
2020-10-11 | 22:23 | 49.959
2020-10-11 | 22:23 | 49.959
2020-10-11 | 22:23 | 49.957
2020-10-11 | 22:23 | 49.954
2020-10-11 | 22:23 | 49.952
2020-10-11 | 22:23 | 49.95
2020-10-11 | 22:23 | 49.948
2020-10-11 | 22:23 | 49.947
2020-10-11 | 22:23 | 49.947
2020-10-11 | 22:23 | 49.944
2020-10-11 | 22:23 | 49.944
2020-10-11 | 22:23 | 49.943
2020-10-11 | 22:23 | 49.944
2020-10-11 | 22:23 | 49.945
2020-10-11 | 22:23 | 49.944
2020-10-11 | 22:23 | 49.939
2020-10-11 | 22:23 | 49.936
2020-10-11 | 22:23 | 49.937
2020-10-11 | 22:23 | 49.939
2020-10-11 | 22:23 | 49.942
2020-10-11 | 22:23 | 49.946
2020-10-11 | 22:23 | 49.946
2020-10-11 | 22:23 | 49.948
2020-10-11 | 22:23 | 49.949
2020-10-11 | 22:23 | 49.95
2020-10-11 | 22:23 | 49.952
2020-10-11 | 22:23 | 49.953
2020-10-11 | 22:23 | 49.953
2020-10-11 | 22:23 | 49.95
2020-10-11 | 22:23 | 49.949
2020-10-11 | 22:23 | 49.952
2020-10-11 | 22:23 | 49.951
2020-10-11 | 22:23 | 49.954
2020-10-11 | 22:23 | 49.957
2020-10-11 | 22:23 | 49.96
2020-10-11 | 22:23 | 49.961
2020-10-11 | 22:23 | 49.962
2020-10-11 | 22:23 | 49.963
2020-10-11 | 22:23 | 49.963
2020-10-11 | 22:23 | 49.961
2020-10-11 | 22:23 | 49.959
2020-10-11 | 22:23 | 49.955
2020-10-11 | 22:23 | 49.952
2020-10-11 | 22:23 | 49.95
2020-10-11 | 22:23 | 49.948
2020-10-11 | 22:23 | 49.945
2020-10-11 | 22:23 | 49.942
2020-10-11 | 22:23 | 49.942
2020-10-11 | 22:23 | 49.943
2020-10-11 | 22:23 | 49.945
2020-10-11 | 22:23 | 49.946
2020-10-11 | 22:23 | 49.95
2020-10-11 | 22:23 | 49.952
2020-10-11 | 22:23 | 49.957
2020-10-11 | 22:23 | 49.96
2020-10-11 | 22:23 | 49.962
2020-10-11 | 22:23 | 49.965
2020-10-11 | 22:23 | 49.967
2020-10-11 | 22:24 | 49.97
2020-10-11 | 22:24 | 49.97
2020-10-11 | 22:24 | 49.968
2020-10-11 | 22:24 | 49.966
2020-10-11 | 22:24 | 49.961
2020-10-11 | 22:24 | 49.961
2020-10-11 | 22:24 | 49.957
2020-10-11 | 22:24 | 49.953
2020-10-11 | 22:24 | 49.949
2020-10-11 | 22:24 | 49.947
2020-10-11 | 22:24 | 49.943
2020-10-11 | 22:24 | 49.941
2020-10-11 | 22:24 | 49.939
2020-10-11 | 22:24 | 49.938
2020-10-11 | 22:24 | 49.936
2020-10-11 | 22:24 | 49.935
2020-10-11 | 22:24 | 49.936
2020-10-11 | 22:24 | 49.937
2020-10-11 | 22:24 | 49.94
2020-10-11 | 22:24 | 49.942
2020-10-11 | 22:24 | 49.944
2020-10-11 | 22:24 | 49.942
2020-10-11 | 22:24 | 49.941
2020-10-11 | 22:24 | 49.94
2020-10-11 | 22:24 | 49.939
2020-10-11 | 22:24 | 49.937
2020-10-11 | 22:24 | 49.937
2020-10-11 | 22:24 | 49.939
2020-10-11 | 22:24 | 49.939
2020-10-11 | 22:24 | 49.939
2020-10-11 | 22:24 | 49.937
2020-10-11 | 22:24 | 49.936
2020-10-11 | 22:24 | 49.933
2020-10-11 | 22:24 | 49.931
2020-10-11 | 22:24 | 49.929
2020-10-11 | 22:24 | 49.93
2020-10-11 | 22:24 | 49.93
2020-10-11 | 22:24 | 49.93
2020-10-11 | 22:24 | 49.929
2020-10-11 | 22:24 | 49.928
2020-10-11 | 22:24 | 49.927
2020-10-11 | 22:24 | 49.925
2020-10-11 | 22:24 | 49.923
2020-10-11 | 22:24 | 49.921
2020-10-11 | 22:24 | 49.92
2020-10-11 | 22:24 | 49.92
2020-10-11 | 22:24 | 49.92
2020-10-11 | 22:24 | 49.919
2020-10-11 | 22:24 | 49.918
2020-10-11 | 22:24 | 49.917
2020-10-11 | 22:24 | 49.918
2020-10-11 | 22:24 | 49.918
2020-10-11 | 22:24 | 49.917
2020-10-11 | 22:24 | 49.92
2020-10-11 | 22:24 | 49.92
2020-10-11 | 22:24 | 49.924
2020-10-11 | 22:24 | 49.926
2020-10-11 | 22:24 | 49.928
2020-10-11 | 22:24 | 49.928
2020-10-11 | 22:24 | 49.928
2020-10-11 | 22:24 | 49.928
2020-10-11 | 22:25 | 49.927
2020-10-11 | 22:25 | 49.927
2020-10-11 | 22:25 | 49.926
2020-10-11 | 22:25 | 49.926
2020-10-11 | 22:25 | 49.928
2020-10-11 | 22:25 | 49.932
2020-10-11 | 22:25 | 49.933
2020-10-11 | 22:25 | 49.936
2020-10-11 | 22:25 | 49.937
2020-10-11 | 22:25 | 49.938
2020-10-11 | 22:25 | 49.939
2020-10-11 | 22:25 | 49.938
2020-10-11 | 22:25 | 49.937
2020-10-11 | 22:25 | 49.935
2020-10-11 | 22:25 | 49.932
2020-10-11 | 22:25 | 49.93
2020-10-11 | 22:25 | 49.93
2020-10-11 | 22:25 | 49.933
2020-10-11 | 22:25 | 49.936
2020-10-11 | 22:25 | 49.942
2020-10-11 | 22:25 | 49.945
2020-10-11 | 22:25 | 49.949
2020-10-11 | 22:25 | 49.954
2020-10-11 | 22:25 | 49.958
2020-10-11 | 22:25 | 49.961
2020-10-11 | 22:25 | 49.962
2020-10-11 | 22:25 | 49.962
2020-10-11 | 22:25 | 49.959
2020-10-11 | 22:25 | 49.956
2020-10-11 | 22:25 | 49.956
2020-10-11 | 22:25 | 49.953
2020-10-11 | 22:25 | 49.951
2020-10-11 | 22:25 | 49.951
2020-10-11 | 22:25 | 49.949
2020-10-11 | 22:25 | 49.949
2020-10-11 | 22:25 | 49.948
2020-10-11 | 22:25 | 49.947
2020-10-11 | 22:25 | 49.946
2020-10-11 | 22:25 | 49.949
2020-10-11 | 22:25 | 49.955
2020-10-11 | 22:25 | 49.959
2020-10-11 | 22:25 | 49.964
2020-10-11 | 22:25 | 49.968
2020-10-11 | 22:25 | 49.971
2020-10-11 | 22:25 | 49.97
2020-10-11 | 22:25 | 49.969
2020-10-11 | 22:25 | 49.967
2020-10-11 | 22:25 | 49.966
2020-10-11 | 22:25 | 49.964
2020-10-11 | 22:25 | 49.962
2020-10-11 | 22:25 | 49.963
2020-10-11 | 22:25 | 49.962
2020-10-11 | 22:25 | 49.962
2020-10-11 | 22:25 | 49.963
2020-10-11 | 22:25 | 49.965
2020-10-11 | 22:25 | 49.964
2020-10-11 | 22:25 | 49.962
2020-10-11 | 22:25 | 49.959
2020-10-11 | 22:25 | 49.958
2020-10-11 | 22:26 | 49.961
2020-10-11 | 22:26 | 49.961
2020-10-11 | 22:26 | 49.965
2020-10-11 | 22:26 | 49.969
2020-10-11 | 22:26 | 49.972
2020-10-11 | 22:26 | 49.975
2020-10-11 | 22:26 | 49.977
2020-10-11 | 22:26 | 49.977
2020-10-11 | 22:26 | 49.974
2020-10-11 | 22:26 | 49.974
2020-10-11 | 22:26 | 49.971
2020-10-11 | 22:26 | 49.967
2020-10-11 | 22:26 | 49.965
2020-10-11 | 22:26 | 49.961
2020-10-11 | 22:26 | 49.957
2020-10-11 | 22:26 | 49.954
2020-10-11 | 22:26 | 49.953
2020-10-11 | 22:26 | 49.954
2020-10-11 | 22:26 | 49.954
2020-10-11 | 22:26 | 49.956
2020-10-11 | 22:26 | 49.957
2020-10-11 | 22:26 | 49.956
2020-10-11 | 22:26 | 49.955
2020-10-11 | 22:26 | 49.955
2020-10-11 | 22:26 | 49.955
2020-10-11 | 22:26 | 49.955
2020-10-11 | 22:26 | 49.954
2020-10-11 | 22:26 | 49.953
2020-10-11 | 22:26 | 49.952
2020-10-11 | 22:26 | 49.952
2020-10-11 | 22:26 | 49.953
2020-10-11 | 22:26 | 49.956
2020-10-11 | 22:26 | 49.957
2020-10-11 | 22:26 | 49.958
2020-10-11 | 22:26 | 49.96
2020-10-11 | 22:26 | 49.962
2020-10-11 | 22:26 | 49.96
2020-10-11 | 22:26 | 49.956
2020-10-11 | 22:26 | 49.955
2020-10-11 | 22:26 | 49.953
2020-10-11 | 22:26 | 49.952
2020-10-11 | 22:26 | 49.947
2020-10-11 | 22:26 | 49.944
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.936
2020-10-11 | 22:26 | 49.933
2020-10-11 | 22:26 | 49.934
2020-10-11 | 22:26 | 49.934
2020-10-11 | 22:26 | 49.936
2020-10-11 | 22:26 | 49.938
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.94
2020-10-11 | 22:26 | 49.937
2020-10-11 | 22:26 | 49.936
2020-10-11 | 22:26 | 49.935
2020-10-11 | 22:26 | 49.937
2020-10-11 | 22:26 | 49.939
2020-10-11 | 22:27 | 49.94
2020-10-11 | 22:27 | 49.942
2020-10-11 | 22:27 | 49.943
2020-10-11 | 22:27 | 49.942
2020-10-11 | 22:27 | 49.941
2020-10-11 | 22:27 | 49.939
2020-10-11 | 22:27 | 49.937
2020-10-11 | 22:27 | 49.935
2020-10-11 | 22:27 | 49.932
2020-10-11 | 22:27 | 49.929
2020-10-11 | 22:27 | 49.928
2020-10-11 | 22:27 | 49.93
2020-10-11 | 22:27 | 49.93
2020-10-11 | 22:27 | 49.929
2020-10-11 | 22:27 | 49.929
2020-10-11 | 22:27 | 49.931
2020-10-11 | 22:27 | 49.932
2020-10-11 | 22:27 | 49.933
2020-10-11 | 22:27 | 49.93
2020-10-11 | 22:27 | 49.928
2020-10-11 | 22:27 | 49.926
2020-10-11 | 22:27 | 49.923
2020-10-11 | 22:27 | 49.919
2020-10-11 | 22:27 | 49.919
2020-10-11 | 22:27 | 49.921
2020-10-11 | 22:27 | 49.922
2020-10-11 | 22:27 | 49.924
2020-10-11 | 22:27 | 49.924
2020-10-11 | 22:27 | 49.927
2020-10-11 | 22:27 | 49.931
2020-10-11 | 22:27 | 49.931
2020-10-11 | 22:27 | 49.93
2020-10-11 | 22:27 | 49.927
2020-10-11 | 22:27 | 49.924
2020-10-11 | 22:27 | 49.925
2020-10-11 | 22:27 | 49.924
2020-10-11 | 22:27 | 49.926
2020-10-11 | 22:27 | 49.926
2020-10-11 | 22:27 | 49.926
2020-10-11 | 22:27 | 49.927
2020-10-11 | 22:27 | 49.929
2020-10-11 | 22:27 | 49.931
2020-10-11 | 22:27 | 49.934
2020-10-11 | 22:27 | 49.936
2020-10-11 | 22:27 | 49.94
2020-10-11 | 22:27 | 49.94
2020-10-11 | 22:27 | 49.941
2020-10-11 | 22:27 | 49.943
2020-10-11 | 22:27 | 49.945
2020-10-11 | 22:27 | 49.946
2020-10-11 | 22:27 | 49.948
2020-10-11 | 22:27 | 49.948
2020-10-11 | 22:27 | 49.949
2020-10-11 | 22:27 | 49.95
2020-10-11 | 22:27 | 49.95
2020-10-11 | 22:27 | 49.95
2020-10-11 | 22:27 | 49.948
2020-10-11 | 22:27 | 49.947
2020-10-11 | 22:27 | 49.944
2020-10-11 | 22:28 | 49.944
2020-10-11 | 22:28 | 49.945
2020-10-11 | 22:28 | 49.943
2020-10-11 | 22:28 | 49.941
2020-10-11 | 22:28 | 49.94
2020-10-11 | 22:28 | 49.939
2020-10-11 | 22:28 | 49.937
2020-10-11 | 22:28 | 49.935
2020-10-11 | 22:28 | 49.932
2020-10-11 | 22:28 | 49.931
2020-10-11 | 22:28 | 49.931
2020-10-11 | 22:28 | 49.929
2020-10-11 | 22:28 | 49.929
2020-10-11 | 22:28 | 49.929
2020-10-11 | 22:28 | 49.928
2020-10-11 | 22:28 | 49.927
2020-10-11 | 22:28 | 49.928
2020-10-11 | 22:28 | 49.927
2020-10-11 | 22:28 | 49.929
2020-10-11 | 22:28 | 49.929
2020-10-11 | 22:28 | 49.93
2020-10-11 | 22:28 | 49.929
2020-10-11 | 22:28 | 49.927
2020-10-11 | 22:28 | 49.925
2020-10-11 | 22:28 | 49.925
2020-10-11 | 22:28 | 49.924
2020-10-11 | 22:28 | 49.922
2020-10-11 | 22:28 | 49.919
2020-10-11 | 22:28 | 49.918
2020-10-11 | 22:28 | 49.914
2020-10-11 | 22:28 | 49.911
2020-10-11 | 22:28 | 49.908
2020-10-11 | 22:28 | 49.906
2020-10-11 | 22:28 | 49.905
2020-10-11 | 22:28 | 49.905
2020-10-11 | 22:28 | 49.907
2020-10-11 | 22:28 | 49.907
2020-10-11 | 22:28 | 49.907
2020-10-11 | 22:28 | 49.904
2020-10-11 | 22:28 | 49.902
2020-10-11 | 22:28 | 49.903
2020-10-11 | 22:28 | 49.903
2020-10-11 | 22:28 | 49.903
2020-10-11 | 22:28 | 49.905
2020-10-11 | 22:28 | 49.907
2020-10-11 | 22:28 | 49.908
2020-10-11 | 22:28 | 49.91
2020-10-11 | 22:28 | 49.914
2020-10-11 | 22:28 | 49.914
2020-10-11 | 22:28 | 49.916
2020-10-11 | 22:28 | 49.919
2020-10-11 | 22:28 | 49.92
2020-10-11 | 22:28 | 49.919
2020-10-11 | 22:28 | 49.917
2020-10-11 | 22:28 | 49.915
2020-10-11 | 22:28 | 49.915
2020-10-11 | 22:28 | 49.919
2020-10-11 | 22:28 | 49.923
2020-10-11 | 22:28 | 49.924
2020-10-11 | 22:28 | 49.925
2020-10-11 | 22:28 | 49.926
2020-10-11 | 22:29 | 49.927
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.93
2020-10-11 | 22:29 | 49.928
2020-10-11 | 22:29 | 49.928
2020-10-11 | 22:29 | 49.927
2020-10-11 | 22:29 | 49.927
2020-10-11 | 22:29 | 49.927
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.932
2020-10-11 | 22:29 | 49.934
2020-10-11 | 22:29 | 49.935
2020-10-11 | 22:29 | 49.937
2020-10-11 | 22:29 | 49.94
2020-10-11 | 22:29 | 49.943
2020-10-11 | 22:29 | 49.942
2020-10-11 | 22:29 | 49.94
2020-10-11 | 22:29 | 49.938
2020-10-11 | 22:29 | 49.937
2020-10-11 | 22:29 | 49.936
2020-10-11 | 22:29 | 49.938
2020-10-11 | 22:29 | 49.941
2020-10-11 | 22:29 | 49.945
2020-10-11 | 22:29 | 49.946
2020-10-11 | 22:29 | 49.943
2020-10-11 | 22:29 | 49.943
2020-10-11 | 22:29 | 49.94
2020-10-11 | 22:29 | 49.939
2020-10-11 | 22:29 | 49.938
2020-10-11 | 22:29 | 49.94
2020-10-11 | 22:29 | 49.937
2020-10-11 | 22:29 | 49.935
2020-10-11 | 22:29 | 49.932
2020-10-11 | 22:29 | 49.928
2020-10-11 | 22:29 | 49.927
2020-10-11 | 22:29 | 49.925
2020-10-11 | 22:29 | 49.923
2020-10-11 | 22:29 | 49.922
2020-10-11 | 22:29 | 49.923
2020-10-11 | 22:29 | 49.924
2020-10-11 | 22:29 | 49.927
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.929
2020-10-11 | 22:29 | 49.93
2020-10-11 | 22:29 | 49.93
2020-10-11 | 22:29 | 49.932
2020-10-11 | 22:29 | 49.931
2020-10-11 | 22:29 | 49.931
2020-10-11 | 22:29 | 49.933
2020-10-11 | 22:29 | 49.933
2020-10-11 | 22:29 | 49.934
2020-10-11 | 22:29 | 49.935
2020-10-11 | 22:29 | 49.936
2020-10-11 | 22:29 | 49.936
2020-10-11 | 22:29 | 49.937
2020-10-11 | 22:29 | 49.937
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.94
2020-10-11 | 22:30 | 49.94
2020-10-11 | 22:30 | 49.94
2020-10-11 | 22:30 | 49.94
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.936
2020-10-11 | 22:30 | 49.936
2020-10-11 | 22:30 | 49.937
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.941
2020-10-11 | 22:30 | 49.944
2020-10-11 | 22:30 | 49.946
2020-10-11 | 22:30 | 49.949
2020-10-11 | 22:30 | 49.952
2020-10-11 | 22:30 | 49.953
2020-10-11 | 22:30 | 49.954
2020-10-11 | 22:30 | 49.955
2020-10-11 | 22:30 | 49.955
2020-10-11 | 22:30 | 49.955
2020-10-11 | 22:30 | 49.956
2020-10-11 | 22:30 | 49.957
2020-10-11 | 22:30 | 49.957
2020-10-11 | 22:30 | 49.956
2020-10-11 | 22:30 | 49.955
2020-10-11 | 22:30 | 49.952
2020-10-11 | 22:30 | 49.95
2020-10-11 | 22:30 | 49.947
2020-10-11 | 22:30 | 49.944
2020-10-11 | 22:30 | 49.941
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.933
2020-10-11 | 22:30 | 49.929
2020-10-11 | 22:30 | 49.929
2020-10-11 | 22:30 | 49.929
2020-10-11 | 22:30 | 49.931
2020-10-11 | 22:30 | 49.932
2020-10-11 | 22:30 | 49.933
2020-10-11 | 22:30 | 49.932
2020-10-11 | 22:30 | 49.933
2020-10-11 | 22:30 | 49.933
2020-10-11 | 22:30 | 49.935
2020-10-11 | 22:30 | 49.938
2020-10-11 | 22:30 | 49.94
2020-10-11 | 22:30 | 49.943
2020-10-11 | 22:30 | 49.948
2020-10-11 | 22:30 | 49.95
2020-10-11 | 22:30 | 49.952
2020-10-11 | 22:30 | 49.954
2020-10-11 | 22:30 | 49.956
2020-10-11 | 22:30 | 49.958
2020-10-11 | 22:30 | 49.96
2020-10-11 | 22:30 | 49.962
2020-10-11 | 22:30 | 49.963
2020-10-11 | 22:30 | 49.964
2020-10-11 | 22:30 | 49.962
2020-10-11 | 22:30 | 49.96
2020-10-11 | 22:30 | 49.96
2020-10-11 | 22:30 | 49.958
2020-10-11 | 22:31 | 49.956
2020-10-11 | 22:31 | 49.958
2020-10-11 | 22:31 | 49.96
2020-10-11 | 22:31 | 49.961
2020-10-11 | 22:31 | 49.964
2020-10-11 | 22:31 | 49.965
2020-10-11 | 22:31 | 49.966
2020-10-11 | 22:31 | 49.967
2020-10-11 | 22:31 | 49.967
2020-10-11 | 22:31 | 49.967
2020-10-11 | 22:31 | 49.964
2020-10-11 | 22:31 | 49.961
2020-10-11 | 22:31 | 49.961
2020-10-11 | 22:31 | 49.961
2020-10-11 | 22:31 | 49.963
2020-10-11 | 22:31 | 49.967
2020-10-11 | 22:31 | 49.969
2020-10-11 | 22:31 | 49.972
2020-10-11 | 22:31 | 49.977
2020-10-11 | 22:31 | 49.981
2020-10-11 | 22:31 | 49.984
2020-10-11 | 22:31 | 49.983
2020-10-11 | 22:31 | 49.983
2020-10-11 | 22:31 | 49.98
2020-10-11 | 22:31 | 49.978
2020-10-11 | 22:31 | 49.977
2020-10-11 | 22:31 | 49.977
2020-10-11 | 22:31 | 49.977
2020-10-11 | 22:31 | 49.976
2020-10-11 | 22:31 | 49.976
2020-10-11 | 22:31 | 49.975
2020-10-11 | 22:31 | 49.972
2020-10-11 | 22:31 | 49.969
2020-10-11 | 22:31 | 49.967
2020-10-11 | 22:31 | 49.964
2020-10-11 | 22:31 | 49.961
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.957
2020-10-11 | 22:31 | 49.957
2020-10-11 | 22:31 | 49.957
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.956
2020-10-11 | 22:31 | 49.956
2020-10-11 | 22:31 | 49.954
2020-10-11 | 22:31 | 49.954
2020-10-11 | 22:31 | 49.955
2020-10-11 | 22:31 | 49.955
2020-10-11 | 22:31 | 49.957
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.958
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.96
2020-10-11 | 22:31 | 49.958
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.959
2020-10-11 | 22:31 | 49.96
2020-10-11 | 22:31 | 49.962
2020-10-11 | 22:31 | 49.961
2020-10-11 | 22:32 | 49.963
2020-10-11 | 22:32 | 49.963
2020-10-11 | 22:32 | 49.962
2020-10-11 | 22:32 | 49.962
2020-10-11 | 22:32 | 49.963
2020-10-11 | 22:32 | 49.963
2020-10-11 | 22:32 | 49.961
2020-10-11 | 22:32 | 49.962
2020-10-11 | 22:32 | 49.96
2020-10-11 | 22:32 | 49.96
2020-10-11 | 22:32 | 49.959
2020-10-11 | 22:32 | 49.958
2020-10-11 | 22:32 | 49.958
2020-10-11 | 22:32 | 49.957
2020-10-11 | 22:32 | 49.955
2020-10-11 | 22:32 | 49.953
2020-10-11 | 22:32 | 49.952
2020-10-11 | 22:32 | 49.953
2020-10-11 | 22:32 | 49.954
2020-10-11 | 22:32 | 49.953
2020-10-11 | 22:32 | 49.954
2020-10-11 | 22:32 | 49.956
2020-10-11 | 22:32 | 49.955
2020-10-11 | 22:32 | 49.955
2020-10-11 | 22:32 | 49.954
2020-10-11 | 22:32 | 49.953
2020-10-11 | 22:32 | 49.952
2020-10-11 | 22:32 | 49.95
2020-10-11 | 22:32 | 49.946
2020-10-11 | 22:32 | 49.942
2020-10-11 | 22:32 | 49.94
2020-10-11 | 22:32 | 49.935
2020-10-11 | 22:32 | 49.932
2020-10-11 | 22:32 | 49.93
2020-10-11 | 22:32 | 49.93
2020-10-11 | 22:32 | 49.931
2020-10-11 | 22:32 | 49.932
2020-10-11 | 22:32 | 49.933
2020-10-11 | 22:32 | 49.934
2020-10-11 | 22:32 | 49.935
2020-10-11 | 22:32 | 49.934
2020-10-11 | 22:32 | 49.935
2020-10-11 | 22:32 | 49.936
2020-10-11 | 22:32 | 49.936
2020-10-11 | 22:32 | 49.936
2020-10-11 | 22:32 | 49.939
2020-10-11 | 22:32 | 49.942
2020-10-11 | 22:32 | 49.945
2020-10-11 | 22:32 | 49.948
2020-10-11 | 22:32 | 49.947
2020-10-11 | 22:32 | 49.948
2020-10-11 | 22:32 | 49.949
2020-10-11 | 22:32 | 49.95
2020-10-11 | 22:32 | 49.951
2020-10-11 | 22:32 | 49.951
2020-10-11 | 22:32 | 49.952
2020-10-11 | 22:32 | 49.954
2020-10-11 | 22:32 | 49.957
2020-10-11 | 22:32 | 49.962
2020-10-11 | 22:32 | 49.966
2020-10-11 | 22:32 | 49.971
2020-10-11 | 22:33 | 49.972
2020-10-11 | 22:33 | 49.975
2020-10-11 | 22:33 | 49.975
2020-10-11 | 22:33 | 49.976
2020-10-11 | 22:33 | 49.974
2020-10-11 | 22:33 | 49.97
2020-10-11 | 22:33 | 49.967
2020-10-11 | 22:33 | 49.963
2020-10-11 | 22:33 | 49.959
2020-10-11 | 22:33 | 49.957
2020-10-11 | 22:33 | 49.957
2020-10-11 | 22:33 | 49.959
2020-10-11 | 22:33 | 49.962
2020-10-11 | 22:33 | 49.962
2020-10-11 | 22:33 | 49.963
2020-10-11 | 22:33 | 49.96
2020-10-11 | 22:33 | 49.959
2020-10-11 | 22:33 | 49.956
2020-10-11 | 22:33 | 49.953
2020-10-11 | 22:33 | 49.952
2020-10-11 | 22:33 | 49.95
2020-10-11 | 22:33 | 49.949
2020-10-11 | 22:33 | 49.947
2020-10-11 | 22:33 | 49.946
2020-10-11 | 22:33 | 49.947
2020-10-11 | 22:33 | 49.947
2020-10-11 | 22:33 | 49.948
2020-10-11 | 22:33 | 49.948
2020-10-11 | 22:33 | 49.948
2020-10-11 | 22:33 | 49.948
2020-10-11 | 22:33 | 49.947
2020-10-11 | 22:33 | 49.947
2020-10-11 | 22:33 | 49.947
2020-10-11 | 22:33 | 49.945
2020-10-11 | 22:33 | 49.946
2020-10-11 | 22:33 | 49.948
2020-10-11 | 22:33 | 49.951
2020-10-11 | 22:33 | 49.955
2020-10-11 | 22:33 | 49.956
2020-10-11 | 22:33 | 49.958
2020-10-11 | 22:33 | 49.96
2020-10-11 | 22:33 | 49.962
2020-10-11 | 22:33 | 49.964
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.966
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.967
2020-10-11 | 22:33 | 49.966
2020-10-11 | 22:33 | 49.966
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.965
2020-10-11 | 22:33 | 49.966
2020-10-11 | 22:33 | 49.967
2020-10-11 | 22:33 | 49.969
2020-10-11 | 22:33 | 49.969
2020-10-11 | 22:33 | 49.97
2020-10-11 | 22:34 | 49.97
2020-10-11 | 22:34 | 49.97
2020-10-11 | 22:34 | 49.969
2020-10-11 | 22:34 | 49.967
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.967
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.965
2020-10-11 | 22:34 | 49.965
2020-10-11 | 22:34 | 49.966
2020-10-11 | 22:34 | 49.965
2020-10-11 | 22:34 | 49.965
2020-10-11 | 22:34 | 49.965
2020-10-11 | 22:34 | 49.963
2020-10-11 | 22:34 | 49.961
2020-10-11 | 22:34 | 49.959
2020-10-11 | 22:34 | 49.957
2020-10-11 | 22:34 | 49.954
2020-10-11 | 22:34 | 49.952
2020-10-11 | 22:34 | 49.951
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.951
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.948
2020-10-11 | 22:34 | 49.947
2020-10-11 | 22:34 | 49.945
2020-10-11 | 22:34 | 49.945
2020-10-11 | 22:34 | 49.945
2020-10-11 | 22:34 | 49.943
2020-10-11 | 22:34 | 49.943
2020-10-11 | 22:34 | 49.943
2020-10-11 | 22:34 | 49.945
2020-10-11 | 22:34 | 49.946
2020-10-11 | 22:34 | 49.947
2020-10-11 | 22:34 | 49.948
2020-10-11 | 22:34 | 49.948
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.95
2020-10-11 | 22:34 | 49.951
2020-10-11 | 22:34 | 49.954
2020-10-11 | 22:34 | 49.957
2020-10-11 | 22:34 | 49.958
2020-10-11 | 22:34 | 49.959
2020-10-11 | 22:34 | 49.959
2020-10-11 | 22:34 | 49.959
2020-10-11 | 22:34 | 49.96
2020-10-11 | 22:34 | 49.959
2020-10-11 | 22:34 | 49.959
2020-10-11 | 22:34 | 49.957
2020-10-11 | 22:34 | 49.955
2020-10-11 | 22:35 | 49.953
2020-10-11 | 22:35 | 49.95
2020-10-11 | 22:35 | 49.95
2020-10-11 | 22:35 | 49.951
2020-10-11 | 22:35 | 49.954
2020-10-11 | 22:35 | 49.958
2020-10-11 | 22:35 | 49.961
2020-10-11 | 22:35 | 49.962
2020-10-11 | 22:35 | 49.965
2020-10-11 | 22:35 | 49.966
2020-10-11 | 22:35 | 49.965
2020-10-11 | 22:35 | 49.963
2020-10-11 | 22:35 | 49.961
2020-10-11 | 22:35 | 49.96
2020-10-11 | 22:35 | 49.959
2020-10-11 | 22:35 | 49.958
2020-10-11 | 22:35 | 49.956
2020-10-11 | 22:35 | 49.955
2020-10-11 | 22:35 | 49.954
2020-10-11 | 22:35 | 49.952
2020-10-11 | 22:35 | 49.951
2020-10-11 | 22:35 | 49.947
2020-10-11 | 22:35 | 49.945
2020-10-11 | 22:35 | 49.945
2020-10-11 | 22:35 | 49.945
2020-10-11 | 22:35 | 49.945
2020-10-11 | 22:35 | 49.943
2020-10-11 | 22:35 | 49.942
2020-10-11 | 22:35 | 49.94
2020-10-11 | 22:35 | 49.939
2020-10-11 | 22:35 | 49.937
2020-10-11 | 22:35 | 49.935
2020-10-11 | 22:35 | 49.932
2020-10-11 | 22:35 | 49.931
2020-10-11 | 22:35 | 49.931
2020-10-11 | 22:35 | 49.932
2020-10-11 | 22:35 | 49.933
2020-10-11 | 22:35 | 49.933
2020-10-11 | 22:35 | 49.933
2020-10-11 | 22:35 | 49.932
2020-10-11 | 22:35 | 49.932
2020-10-11 | 22:35 | 49.931
2020-10-11 | 22:35 | 49.93
2020-10-11 | 22:35 | 49.93
2020-10-11 | 22:35 | 49.928
2020-10-11 | 22:35 | 49.928
2020-10-11 | 22:35 | 49.928
2020-10-11 | 22:35 | 49.927
2020-10-11 | 22:35 | 49.926
2020-10-11 | 22:35 | 49.925
2020-10-11 | 22:35 | 49.923
2020-10-11 | 22:35 | 49.92
2020-10-11 | 22:35 | 49.92
2020-10-11 | 22:35 | 49.919
2020-10-11 | 22:35 | 49.921
2020-10-11 | 22:35 | 49.922
2020-10-11 | 22:35 | 49.922
2020-10-11 | 22:35 | 49.923
2020-10-11 | 22:35 | 49.925
2020-10-11 | 22:36 | 49.927
2020-10-11 | 22:36 | 49.927
2020-10-11 | 22:36 | 49.928
2020-10-11 | 22:36 | 49.926
2020-10-11 | 22:36 | 49.926
2020-10-11 | 22:36 | 49.924
2020-10-11 | 22:36 | 49.923
2020-10-11 | 22:36 | 49.923
2020-10-11 | 22:36 | 49.924
2020-10-11 | 22:36 | 49.924
2020-10-11 | 22:36 | 49.925
2020-10-11 | 22:36 | 49.925
2020-10-11 | 22:36 | 49.924
2020-10-11 | 22:36 | 49.925
2020-10-11 | 22:36 | 49.925
2020-10-11 | 22:36 | 49.926
2020-10-11 | 22:36 | 49.928
2020-10-11 | 22:36 | 49.928
2020-10-11 | 22:36 | 49.929
2020-10-11 | 22:36 | 49.929
2020-10-11 | 22:36 | 49.929
2020-10-11 | 22:36 | 49.928
2020-10-11 | 22:36 | 49.926
2020-10-11 | 22:36 | 49.926
2020-10-11 | 22:36 | 49.925
2020-10-11 | 22:36 | 49.923
2020-10-11 | 22:36 | 49.922
2020-10-11 | 22:36 | 49.921
2020-10-11 | 22:36 | 49.922
2020-10-11 | 22:36 | 49.924
2020-10-11 | 22:36 | 49.928
2020-10-11 | 22:36 | 49.929
2020-10-11 | 22:36 | 49.929
2020-10-11 | 22:36 | 49.93
2020-10-11 | 22:36 | 49.93
2020-10-11 | 22:36 | 49.932
2020-10-11 | 22:36 | 49.936
2020-10-11 | 22:36 | 49.942
2020-10-11 | 22:36 | 49.948
2020-10-11 | 22:36 | 49.951
2020-10-11 | 22:36 | 49.952
2020-10-11 | 22:36 | 49.953
2020-10-11 | 22:36 | 49.954
2020-10-11 | 22:36 | 49.956
2020-10-11 | 22:36 | 49.956
2020-10-11 | 22:36 | 49.957
2020-10-11 | 22:36 | 49.955
2020-10-11 | 22:36 | 49.952
2020-10-11 | 22:36 | 49.95
2020-10-11 | 22:36 | 49.947
2020-10-11 | 22:36 | 49.948
2020-10-11 | 22:36 | 49.949
2020-10-11 | 22:36 | 49.951
2020-10-11 | 22:36 | 49.952
2020-10-11 | 22:36 | 49.953
2020-10-11 | 22:36 | 49.955
2020-10-11 | 22:36 | 49.955
2020-10-11 | 22:36 | 49.954
2020-10-11 | 22:36 | 49.952
2020-10-11 | 22:36 | 49.95
2020-10-11 | 22:36 | 49.947
2020-10-11 | 22:37 | 49.945
2020-10-11 | 22:37 | 49.944
2020-10-11 | 22:37 | 49.943
2020-10-11 | 22:37 | 49.943
2020-10-11 | 22:37 | 49.944
2020-10-11 | 22:37 | 49.945
2020-10-11 | 22:37 | 49.946
2020-10-11 | 22:37 | 49.945
2020-10-11 | 22:37 | 49.947
2020-10-11 | 22:37 | 49.947
2020-10-11 | 22:37 | 49.946
2020-10-11 | 22:37 | 49.943
2020-10-11 | 22:37 | 49.941
2020-10-11 | 22:37 | 49.939
2020-10-11 | 22:37 | 49.94
2020-10-11 | 22:37 | 49.942
2020-10-11 | 22:37 | 49.942
2020-10-11 | 22:37 | 49.944
2020-10-11 | 22:37 | 49.944
2020-10-11 | 22:37 | 49.946
2020-10-11 | 22:37 | 49.947
2020-10-11 | 22:37 | 49.948
2020-10-11 | 22:37 | 49.948
2020-10-11 | 22:37 | 49.948
2020-10-11 | 22:37 | 49.948
2020-10-11 | 22:37 | 49.949
2020-10-11 | 22:37 | 49.949
2020-10-11 | 22:37 | 49.95
2020-10-11 | 22:37 | 49.951
2020-10-11 | 22:37 | 49.953
2020-10-11 | 22:37 | 49.954
2020-10-11 | 22:37 | 49.953
2020-10-11 | 22:37 | 49.953
2020-10-11 | 22:37 | 49.955
2020-10-11 | 22:37 | 49.957
2020-10-11 | 22:37 | 49.959
2020-10-11 | 22:37 | 49.958
2020-10-11 | 22:37 | 49.957
2020-10-11 | 22:37 | 49.957
2020-10-11 | 22:37 | 49.956
2020-10-11 | 22:37 | 49.956
2020-10-11 | 22:37 | 49.956
2020-10-11 | 22:37 | 49.955
2020-10-11 | 22:37 | 49.954
2020-10-11 | 22:37 | 49.955
2020-10-11 | 22:37 | 49.957
2020-10-11 | 22:37 | 49.958
2020-10-11 | 22:37 | 49.961
2020-10-11 | 22:37 | 49.964
2020-10-11 | 22:37 | 49.966
2020-10-11 | 22:37 | 49.967
2020-10-11 | 22:37 | 49.967
2020-10-11 | 22:37 | 49.967
2020-10-11 | 22:37 | 49.965
2020-10-11 | 22:37 | 49.963
2020-10-11 | 22:37 | 49.96
2020-10-11 | 22:37 | 49.957
2020-10-11 | 22:37 | 49.955
2020-10-11 | 22:37 | 49.949
2020-10-11 | 22:38 | 49.942
2020-10-11 | 22:38 | 49.936
2020-10-11 | 22:38 | 49.931
2020-10-11 | 22:38 | 49.928
2020-10-11 | 22:38 | 49.927
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.927
2020-10-11 | 22:38 | 49.925
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.922
2020-10-11 | 22:38 | 49.921
2020-10-11 | 22:38 | 49.921
2020-10-11 | 22:38 | 49.919
2020-10-11 | 22:38 | 49.917
2020-10-11 | 22:38 | 49.916
2020-10-11 | 22:38 | 49.918
2020-10-11 | 22:38 | 49.919
2020-10-11 | 22:38 | 49.919
2020-10-11 | 22:38 | 49.92
2020-10-11 | 22:38 | 49.921
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.925
2020-10-11 | 22:38 | 49.927
2020-10-11 | 22:38 | 49.928
2020-10-11 | 22:38 | 49.93
2020-10-11 | 22:38 | 49.932
2020-10-11 | 22:38 | 49.93
2020-10-11 | 22:38 | 49.929
2020-10-11 | 22:38 | 49.929
2020-10-11 | 22:38 | 49.928
2020-10-11 | 22:38 | 49.929
2020-10-11 | 22:38 | 49.927
2020-10-11 | 22:38 | 49.925
2020-10-11 | 22:38 | 49.925
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.924
2020-10-11 | 22:38 | 49.925
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.923
2020-10-11 | 22:38 | 49.925
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.926
2020-10-11 | 22:38 | 49.928
2020-10-11 | 22:38 | 49.931
2020-10-11 | 22:38 | 49.93
2020-10-11 | 22:38 | 49.929
2020-10-11 | 22:38 | 49.928
2020-10-11 | 22:38 | 49.928
2020-10-11 | 22:39 | 49.928
2020-10-11 | 22:39 | 49.928
2020-10-11 | 22:39 | 49.929
2020-10-11 | 22:39 | 49.931
2020-10-11 | 22:39 | 49.931
2020-10-11 | 22:39 | 49.932
2020-10-11 | 22:39 | 49.932
2020-10-11 | 22:39 | 49.932
2020-10-11 | 22:39 | 49.933
2020-10-11 | 22:39 | 49.935
2020-10-11 | 22:39 | 49.936
2020-10-11 | 22:39 | 49.937
2020-10-11 | 22:39 | 49.937
2020-10-11 | 22:39 | 49.938
2020-10-11 | 22:39 | 49.939
2020-10-11 | 22:39 | 49.941
2020-10-11 | 22:39 | 49.942
2020-10-11 | 22:39 | 49.943
2020-10-11 | 22:39 | 49.942
2020-10-11 | 22:39 | 49.942
2020-10-11 | 22:39 | 49.942
2020-10-11 | 22:39 | 49.945
2020-10-11 | 22:39 | 49.947
2020-10-11 | 22:39 | 49.947
2020-10-11 | 22:39 | 49.946
2020-10-11 | 22:39 | 49.944
2020-10-11 | 22:39 | 49.942
2020-10-11 | 22:39 | 49.94
2020-10-11 | 22:39 | 49.938
2020-10-11 | 22:39 | 49.937
2020-10-11 | 22:39 | 49.935
2020-10-11 | 22:39 | 49.933
2020-10-11 | 22:39 | 49.932
2020-10-11 | 22:39 | 49.933
2020-10-11 | 22:39 | 49.935
2020-10-11 | 22:39 | 49.938
2020-10-11 | 22:39 | 49.941
2020-10-11 | 22:39 | 49.943
2020-10-11 | 22:39 | 49.946
2020-10-11 | 22:39 | 49.946
2020-10-11 | 22:39 | 49.946
2020-10-11 | 22:39 | 49.943
2020-10-11 | 22:39 | 49.939
2020-10-11 | 22:39 | 49.935
2020-10-11 | 22:39 | 49.932
2020-10-11 | 22:39 | 49.93
2020-10-11 | 22:39 | 49.93
2020-10-11 | 22:39 | 49.93
2020-10-11 | 22:39 | 49.931
2020-10-11 | 22:39 | 49.933
2020-10-11 | 22:39 | 49.934
2020-10-11 | 22:39 | 49.935
2020-10-11 | 22:39 | 49.936
2020-10-11 | 22:39 | 49.938
2020-10-11 | 22:39 | 49.938
2020-10-11 | 22:39 | 49.939
2020-10-11 | 22:39 | 49.938
2020-10-11 | 22:39 | 49.937
2020-10-11 | 22:39 | 49.936
2020-10-11 | 22:40 | 49.934
2020-10-11 | 22:40 | 49.932
2020-10-11 | 22:40 | 49.931
2020-10-11 | 22:40 | 49.931
2020-10-11 | 22:40 | 49.927
2020-10-11 | 22:40 | 49.925
2020-10-11 | 22:40 | 49.923
2020-10-11 | 22:40 | 49.921
2020-10-11 | 22:40 | 49.919
2020-10-11 | 22:40 | 49.917
2020-10-11 | 22:40 | 49.914
2020-10-11 | 22:40 | 49.912
2020-10-11 | 22:40 | 49.912
2020-10-11 | 22:40 | 49.912
2020-10-11 | 22:40 | 49.912
2020-10-11 | 22:40 | 49.912
2020-10-11 | 22:40 | 49.913
2020-10-11 | 22:40 | 49.912
2020-10-11 | 22:40 | 49.911
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.907
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.91
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.908
2020-10-11 | 22:40 | 49.908
2020-10-11 | 22:40 | 49.907
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.908
2020-10-11 | 22:40 | 49.908
2020-10-11 | 22:40 | 49.91
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.91
2020-10-11 | 22:40 | 49.911
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.91
2020-10-11 | 22:40 | 49.911
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.91
2020-10-11 | 22:40 | 49.909
2020-10-11 | 22:40 | 49.908
2020-10-11 | 22:40 | 49.906
2020-10-11 | 22:40 | 49.906
2020-10-11 | 22:40 | 49.904
2020-10-11 | 22:40 | 49.903
2020-10-11 | 22:40 | 49.902
2020-10-11 | 22:40 | 49.901
2020-10-11 | 22:40 | 49.9
2020-10-11 | 22:40 | 49.899
2020-10-11 | 22:40 | 49.9
2020-10-11 | 22:40 | 49.898
2020-10-11 | 22:40 | 49.898
2020-10-11 | 22:40 | 49.897
2020-10-11 | 22:40 | 49.897
2020-10-11 | 22:40 | 49.899
2020-10-11 | 22:40 | 49.9
2020-10-11 | 22:40 | 49.903
2020-10-11 | 22:40 | 49.905
2020-10-11 | 22:40 | 49.905
2020-10-11 | 22:41 | 49.907
2020-10-11 | 22:41 | 49.906
2020-10-11 | 22:41 | 49.903
2020-10-11 | 22:41 | 49.903
2020-10-11 | 22:41 | 49.898
2020-10-11 | 22:41 | 49.895
2020-10-11 | 22:41 | 49.894
2020-10-11 | 22:41 | 49.894
2020-10-11 | 22:41 | 49.893
2020-10-11 | 22:41 | 49.893
2020-10-11 | 22:41 | 49.893
2020-10-11 | 22:41 | 49.892
2020-10-11 | 22:41 | 49.892
2020-10-11 | 22:41 | 49.89
2020-10-11 | 22:41 | 49.89
2020-10-11 | 22:41 | 49.895
2020-10-11 | 22:41 | 49.897
2020-10-11 | 22:41 | 49.897
2020-10-11 | 22:41 | 49.9
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.9
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.903
2020-10-11 | 22:41 | 49.904
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.904
2020-10-11 | 22:41 | 49.903
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.899
2020-10-11 | 22:41 | 49.898
2020-10-11 | 22:41 | 49.899
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.904
2020-10-11 | 22:41 | 49.907
2020-10-11 | 22:41 | 49.908
2020-10-11 | 22:41 | 49.908
2020-10-11 | 22:41 | 49.907
2020-10-11 | 22:41 | 49.904
2020-10-11 | 22:41 | 49.903
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.901
2020-10-11 | 22:41 | 49.902
2020-10-11 | 22:41 | 49.906
2020-10-11 | 22:41 | 49.91
2020-10-11 | 22:41 | 49.913
2020-10-11 | 22:41 | 49.916
2020-10-11 | 22:41 | 49.916
2020-10-11 | 22:41 | 49.915
2020-10-11 | 22:41 | 49.915
2020-10-11 | 22:42 | 49.915
2020-10-11 | 22:42 | 49.913
2020-10-11 | 22:42 | 49.909
2020-10-11 | 22:42 | 49.91
2020-10-11 | 22:42 | 49.909
2020-10-11 | 22:42 | 49.908
2020-10-11 | 22:42 | 49.908
2020-10-11 | 22:42 | 49.909
2020-10-11 | 22:42 | 49.907
2020-10-11 | 22:42 | 49.907
2020-10-11 | 22:42 | 49.909
2020-10-11 | 22:42 | 49.911
2020-10-11 | 22:42 | 49.911
2020-10-11 | 22:42 | 49.911
2020-10-11 | 22:42 | 49.912
2020-10-11 | 22:42 | 49.91
2020-10-11 | 22:42 | 49.908
2020-10-11 | 22:42 | 49.907
2020-10-11 | 22:42 | 49.907
2020-10-11 | 22:42 | 49.907
2020-10-11 | 22:42 | 49.905
2020-10-11 | 22:42 | 49.906
2020-10-11 | 22:42 | 49.905
2020-10-11 | 22:42 | 49.909
2020-10-11 | 22:42 | 49.911
2020-10-11 | 22:42 | 49.911
2020-10-11 | 22:42 | 49.912
2020-10-11 | 22:42 | 49.912
2020-10-11 | 22:42 | 49.913
2020-10-11 | 22:42 | 49.913
2020-10-11 | 22:42 | 49.912
2020-10-11 | 22:42 | 49.912
2020-10-11 | 22:42 | 49.913
2020-10-11 | 22:42 | 49.912
2020-10-11 | 22:42 | 49.913
2020-10-11 | 22:42 | 49.913
2020-10-11 | 22:42 | 49.914
2020-10-11 | 22:42 | 49.914
2020-10-11 | 22:42 | 49.914
2020-10-11 | 22:42 | 49.915
2020-10-11 | 22:42 | 49.919
2020-10-11 | 22:42 | 49.921
2020-10-11 | 22:42 | 49.922
2020-10-11 | 22:42 | 49.925
2020-10-11 | 22:42 | 49.926
2020-10-11 | 22:42 | 49.926
2020-10-11 | 22:42 | 49.925
2020-10-11 | 22:42 | 49.924
2020-10-11 | 22:42 | 49.923
2020-10-11 | 22:42 | 49.921
2020-10-11 | 22:42 | 49.919
2020-10-11 | 22:42 | 49.92
2020-10-11 | 22:42 | 49.92
2020-10-11 | 22:42 | 49.92
2020-10-11 | 22:42 | 49.921
2020-10-11 | 22:42 | 49.921
2020-10-11 | 22:42 | 49.919
2020-10-11 | 22:42 | 49.919
2020-10-11 | 22:42 | 49.919
2020-10-11 | 22:42 | 49.92
2020-10-11 | 22:42 | 49.922
2020-10-11 | 22:43 | 49.923
2020-10-11 | 22:43 | 49.924
2020-10-11 | 22:43 | 49.924
2020-10-11 | 22:43 | 49.925
2020-10-11 | 22:43 | 49.925
2020-10-11 | 22:43 | 49.925
2020-10-11 | 22:43 | 49.926
2020-10-11 | 22:43 | 49.923
2020-10-11 | 22:43 | 49.924
2020-10-11 | 22:43 | 49.922
2020-10-11 | 22:43 | 49.92
2020-10-11 | 22:43 | 49.921
2020-10-11 | 22:43 | 49.921
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.92
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.919
2020-10-11 | 22:43 | 49.917
2020-10-11 | 22:43 | 49.917
2020-10-11 | 22:43 | 49.914
2020-10-11 | 22:43 | 49.913
2020-10-11 | 22:43 | 49.913
2020-10-11 | 22:43 | 49.913
2020-10-11 | 22:43 | 49.914
2020-10-11 | 22:43 | 49.914
2020-10-11 | 22:43 | 49.913
2020-10-11 | 22:43 | 49.912
2020-10-11 | 22:43 | 49.912
2020-10-11 | 22:43 | 49.911
2020-10-11 | 22:43 | 49.91
2020-10-11 | 22:43 | 49.91
2020-10-11 | 22:43 | 49.91
2020-10-11 | 22:43 | 49.908
2020-10-11 | 22:43 | 49.905
2020-10-11 | 22:43 | 49.904
2020-10-11 | 22:43 | 49.903
2020-10-11 | 22:43 | 49.903
2020-10-11 | 22:43 | 49.905
2020-10-11 | 22:43 | 49.904
2020-10-11 | 22:43 | 49.906
2020-10-11 | 22:43 | 49.905
2020-10-11 | 22:43 | 49.906
2020-10-11 | 22:43 | 49.907
2020-10-11 | 22:43 | 49.906
2020-10-11 | 22:43 | 49.905
2020-10-11 | 22:43 | 49.907
2020-10-11 | 22:43 | 49.909
2020-10-11 | 22:43 | 49.91
2020-10-11 | 22:43 | 49.912
2020-10-11 | 22:43 | 49.912
2020-10-11 | 22:43 | 49.911
2020-10-11 | 22:43 | 49.913
2020-10-11 | 22:43 | 49.912
2020-10-11 | 22:43 | 49.91
2020-10-11 | 22:43 | 49.91
2020-10-11 | 22:44 | 49.908
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.905
2020-10-11 | 22:44 | 49.902
2020-10-11 | 22:44 | 49.899
2020-10-11 | 22:44 | 49.897
2020-10-11 | 22:44 | 49.895
2020-10-11 | 22:44 | 49.894
2020-10-11 | 22:44 | 49.894
2020-10-11 | 22:44 | 49.897
2020-10-11 | 22:44 | 49.901
2020-10-11 | 22:44 | 49.902
2020-10-11 | 22:44 | 49.903
2020-10-11 | 22:44 | 49.904
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.908
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.908
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.905
2020-10-11 | 22:44 | 49.903
2020-10-11 | 22:44 | 49.905
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.907
2020-10-11 | 22:44 | 49.908
2020-10-11 | 22:44 | 49.909
2020-10-11 | 22:44 | 49.911
2020-10-11 | 22:44 | 49.911
2020-10-11 | 22:44 | 49.913
2020-10-11 | 22:44 | 49.914
2020-10-11 | 22:44 | 49.914
2020-10-11 | 22:44 | 49.916
2020-10-11 | 22:44 | 49.916
2020-10-11 | 22:44 | 49.918
2020-10-11 | 22:44 | 49.92
2020-10-11 | 22:44 | 49.92
2020-10-11 | 22:44 | 49.918
2020-10-11 | 22:44 | 49.919
2020-10-11 | 22:44 | 49.919
2020-10-11 | 22:44 | 49.919
2020-10-11 | 22:44 | 49.918
2020-10-11 | 22:44 | 49.918
2020-10-11 | 22:44 | 49.918
2020-10-11 | 22:44 | 49.916
2020-10-11 | 22:44 | 49.914
2020-10-11 | 22:44 | 49.91
2020-10-11 | 22:44 | 49.908
2020-10-11 | 22:44 | 49.906
2020-10-11 | 22:44 | 49.904
2020-10-11 | 22:44 | 49.902
2020-10-11 | 22:44 | 49.901
2020-10-11 | 22:44 | 49.899
2020-10-11 | 22:44 | 49.9
2020-10-11 | 22:44 | 49.901
2020-10-11 | 22:45 | 49.901
2020-10-11 | 22:45 | 49.902
2020-10-11 | 22:45 | 49.901
2020-10-11 | 22:45 | 49.9
2020-10-11 | 22:45 | 49.9
2020-10-11 | 22:45 | 49.9
2020-10-11 | 22:45 | 49.899
2020-10-11 | 22:45 | 49.9
2020-10-11 | 22:45 | 49.901
2020-10-11 | 22:45 | 49.902
2020-10-11 | 22:45 | 49.903
2020-10-11 | 22:45 | 49.903
2020-10-11 | 22:45 | 49.902
2020-10-11 | 22:45 | 49.901
2020-10-11 | 22:45 | 49.899
2020-10-11 | 22:45 | 49.898
2020-10-11 | 22:45 | 49.898
2020-10-11 | 22:45 | 49.897
2020-10-11 | 22:45 | 49.896
2020-10-11 | 22:45 | 49.896
2020-10-11 | 22:45 | 49.895
2020-10-11 | 22:45 | 49.895
2020-10-11 | 22:45 | 49.894
2020-10-11 | 22:45 | 49.893
2020-10-11 | 22:45 | 49.891
2020-10-11 | 22:45 | 49.889
2020-10-11 | 22:45 | 49.889
2020-10-11 | 22:45 | 49.892
2020-10-11 | 22:45 | 49.895
2020-10-11 | 22:45 | 49.897
2020-10-11 | 22:45 | 49.895
2020-10-11 | 22:45 | 49.893
2020-10-11 | 22:45 | 49.892
2020-10-11 | 22:45 | 49.89
2020-10-11 | 22:45 | 49.887
2020-10-11 | 22:45 | 49.886
2020-10-11 | 22:45 | 49.885
2020-10-11 | 22:45 | 49.884
2020-10-11 | 22:45 | 49.88
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.876
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.876
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.876
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.875
2020-10-11 | 22:45 | 49.874
2020-10-11 | 22:45 | 49.874
2020-10-11 | 22:45 | 49.877
2020-10-11 | 22:45 | 49.883
2020-10-11 | 22:45 | 49.889
2020-10-11 | 22:45 | 49.895
2020-10-11 | 22:45 | 49.898
2020-10-11 | 22:45 | 49.9
2020-10-11 | 22:45 | 49.901
2020-10-11 | 22:46 | 49.902
2020-10-11 | 22:46 | 49.904
2020-10-11 | 22:46 | 49.906
2020-10-11 | 22:46 | 49.906
2020-10-11 | 22:46 | 49.904
2020-10-11 | 22:46 | 49.904
2020-10-11 | 22:46 | 49.905
2020-10-11 | 22:46 | 49.907
2020-10-11 | 22:46 | 49.907
2020-10-11 | 22:46 | 49.905
2020-10-11 | 22:46 | 49.907
2020-10-11 | 22:46 | 49.909
2020-10-11 | 22:46 | 49.91
2020-10-11 | 22:46 | 49.91
2020-10-11 | 22:46 | 49.906
2020-10-11 | 22:46 | 49.902
2020-10-11 | 22:46 | 49.901
2020-10-11 | 22:46 | 49.901
2020-10-11 | 22:46 | 49.901
2020-10-11 | 22:46 | 49.9
2020-10-11 | 22:46 | 49.9
2020-10-11 | 22:46 | 49.899
2020-10-11 | 22:46 | 49.899
2020-10-11 | 22:46 | 49.901
2020-10-11 | 22:46 | 49.903
2020-10-11 | 22:46 | 49.905
2020-10-11 | 22:46 | 49.908
2020-10-11 | 22:46 | 49.91
2020-10-11 | 22:46 | 49.911
2020-10-11 | 22:46 | 49.912
2020-10-11 | 22:46 | 49.914
2020-10-11 | 22:46 | 49.915
2020-10-11 | 22:46 | 49.916
2020-10-11 | 22:46 | 49.917
2020-10-11 | 22:46 | 49.92
2020-10-11 | 22:46 | 49.921
2020-10-11 | 22:46 | 49.92
2020-10-11 | 22:46 | 49.92
2020-10-11 | 22:46 | 49.922
2020-10-11 | 22:46 | 49.922
2020-10-11 | 22:46 | 49.923
2020-10-11 | 22:46 | 49.924
2020-10-11 | 22:46 | 49.925
2020-10-11 | 22:46 | 49.926
2020-10-11 | 22:46 | 49.927
2020-10-11 | 22:46 | 49.926
2020-10-11 | 22:46 | 49.924
2020-10-11 | 22:46 | 49.923
2020-10-11 | 22:46 | 49.921
2020-10-11 | 22:46 | 49.918
2020-10-11 | 22:46 | 49.916
2020-10-11 | 22:46 | 49.915
2020-10-11 | 22:46 | 49.914
2020-10-11 | 22:46 | 49.912
2020-10-11 | 22:46 | 49.911
2020-10-11 | 22:46 | 49.91
2020-10-11 | 22:46 | 49.91
2020-10-11 | 22:46 | 49.911
2020-10-11 | 22:46 | 49.912
2020-10-11 | 22:46 | 49.911
2020-10-11 | 22:46 | 49.911
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.91
2020-10-11 | 22:47 | 49.91
2020-10-11 | 22:47 | 49.911
2020-10-11 | 22:47 | 49.911
2020-10-11 | 22:47 | 49.911
2020-10-11 | 22:47 | 49.912
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.911
2020-10-11 | 22:47 | 49.911
2020-10-11 | 22:47 | 49.912
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.914
2020-10-11 | 22:47 | 49.913
2020-10-11 | 22:47 | 49.914
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.914
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.916
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.917
2020-10-11 | 22:47 | 49.92
2020-10-11 | 22:47 | 49.921
2020-10-11 | 22:47 | 49.923
2020-10-11 | 22:47 | 49.924
2020-10-11 | 22:47 | 49.925
2020-10-11 | 22:47 | 49.926
2020-10-11 | 22:47 | 49.927
2020-10-11 | 22:47 | 49.927
2020-10-11 | 22:47 | 49.927
2020-10-11 | 22:47 | 49.926
2020-10-11 | 22:47 | 49.925
2020-10-11 | 22:47 | 49.923
2020-10-11 | 22:47 | 49.921
2020-10-11 | 22:47 | 49.919
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.912
2020-10-11 | 22:47 | 49.915
2020-10-11 | 22:47 | 49.918
2020-10-11 | 22:47 | 49.922
2020-10-11 | 22:47 | 49.926
2020-10-11 | 22:47 | 49.927
2020-10-11 | 22:47 | 49.929
2020-10-11 | 22:47 | 49.929
2020-10-11 | 22:47 | 49.93
2020-10-11 | 22:47 | 49.932
2020-10-11 | 22:47 | 49.933
2020-10-11 | 22:47 | 49.932
2020-10-11 | 22:47 | 49.93
2020-10-11 | 22:47 | 49.929
2020-10-11 | 22:47 | 49.928
2020-10-11 | 22:47 | 49.928
2020-10-11 | 22:47 | 49.928
2020-10-11 | 22:47 | 49.929
2020-10-11 | 22:48 | 49.928
2020-10-11 | 22:48 | 49.926
2020-10-11 | 22:48 | 49.925
2020-10-11 | 22:48 | 49.924
2020-10-11 | 22:48 | 49.924
2020-10-11 | 22:48 | 49.925
2020-10-11 | 22:48 | 49.924
2020-10-11 | 22:48 | 49.923
2020-10-11 | 22:48 | 49.922
2020-10-11 | 22:48 | 49.919
2020-10-11 | 22:48 | 49.918
2020-10-11 | 22:48 | 49.916
2020-10-11 | 22:48 | 49.916
2020-10-11 | 22:48 | 49.916
2020-10-11 | 22:48 | 49.917
2020-10-11 | 22:48 | 49.916
2020-10-11 | 22:48 | 49.916
2020-10-11 | 22:48 | 49.917
2020-10-11 | 22:48 | 49.916
2020-10-11 | 22:48 | 49.914
2020-10-11 | 22:48 | 49.913
2020-10-11 | 22:48 | 49.912
2020-10-11 | 22:48 | 49.911
2020-10-11 | 22:48 | 49.912
2020-10-11 | 22:48 | 49.911
2020-10-11 | 22:48 | 49.91
2020-10-11 | 22:48 | 49.912
2020-10-11 | 22:48 | 49.913
2020-10-11 | 22:48 | 49.914
2020-10-11 | 22:48 | 49.913
2020-10-11 | 22:48 | 49.913
2020-10-11 | 22:48 | 49.913
2020-10-11 | 22:48 | 49.91
2020-10-11 | 22:48 | 49.906
2020-10-11 | 22:48 | 49.901
2020-10-11 | 22:48 | 49.898
2020-10-11 | 22:48 | 49.896
2020-10-11 | 22:48 | 49.895
2020-10-11 | 22:48 | 49.895
2020-10-11 | 22:48 | 49.894
2020-10-11 | 22:48 | 49.894
2020-10-11 | 22:48 | 49.895
2020-10-11 | 22:48 | 49.897
2020-10-11 | 22:48 | 49.898
2020-10-11 | 22:48 | 49.9
2020-10-11 | 22:48 | 49.9
2020-10-11 | 22:48 | 49.902
2020-10-11 | 22:48 | 49.9
2020-10-11 | 22:48 | 49.9
2020-10-11 | 22:48 | 49.899
2020-10-11 | 22:48 | 49.897
2020-10-11 | 22:48 | 49.895
2020-10-11 | 22:48 | 49.896
2020-10-11 | 22:48 | 49.896
2020-10-11 | 22:48 | 49.896
2020-10-11 | 22:48 | 49.898
2020-10-11 | 22:48 | 49.9
2020-10-11 | 22:48 | 49.901
2020-10-11 | 22:48 | 49.902
2020-10-11 | 22:48 | 49.904
2020-10-11 | 22:48 | 49.907
2020-10-11 | 22:49 | 49.907
2020-10-11 | 22:49 | 49.907
2020-10-11 | 22:49 | 49.908
2020-10-11 | 22:49 | 49.909
2020-10-11 | 22:49 | 49.911
2020-10-11 | 22:49 | 49.915
2020-10-11 | 22:49 | 49.917
2020-10-11 | 22:49 | 49.919
2020-10-11 | 22:49 | 49.919
2020-10-11 | 22:49 | 49.921
2020-10-11 | 22:49 | 49.922
2020-10-11 | 22:49 | 49.922
2020-10-11 | 22:49 | 49.922
2020-10-11 | 22:49 | 49.922
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:49 | 49.925
2020-10-11 | 22:49 | 49.923
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:49 | 49.923
2020-10-11 | 22:49 | 49.925
2020-10-11 | 22:49 | 49.925
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:49 | 49.922
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:49 | 49.925
2020-10-11 | 22:49 | 49.925
2020-10-11 | 22:49 | 49.923
2020-10-11 | 22:49 | 49.923
2020-10-11 | 22:49 | 49.923
2020-10-11 | 22:49 | 49.921
2020-10-11 | 22:49 | 49.921
2020-10-11 | 22:49 | 49.919
2020-10-11 | 22:49 | 49.916
2020-10-11 | 22:49 | 49.913
2020-10-11 | 22:49 | 49.911
2020-10-11 | 22:49 | 49.909
2020-10-11 | 22:49 | 49.908
2020-10-11 | 22:49 | 49.907
2020-10-11 | 22:49 | 49.907
2020-10-11 | 22:49 | 49.908
2020-10-11 | 22:49 | 49.911
2020-10-11 | 22:49 | 49.914
2020-10-11 | 22:49 | 49.913
2020-10-11 | 22:49 | 49.914
2020-10-11 | 22:49 | 49.915
2020-10-11 | 22:49 | 49.914
2020-10-11 | 22:49 | 49.915
2020-10-11 | 22:49 | 49.916
2020-10-11 | 22:49 | 49.917
2020-10-11 | 22:49 | 49.918
2020-10-11 | 22:49 | 49.919
2020-10-11 | 22:49 | 49.921
2020-10-11 | 22:49 | 49.923
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:49 | 49.927
2020-10-11 | 22:49 | 49.926
2020-10-11 | 22:49 | 49.925
2020-10-11 | 22:49 | 49.924
2020-10-11 | 22:50 | 49.925
2020-10-11 | 22:50 | 49.925
2020-10-11 | 22:50 | 49.926
2020-10-11 | 22:50 | 49.929
2020-10-11 | 22:50 | 49.93
2020-10-11 | 22:50 | 49.933
2020-10-11 | 22:50 | 49.934
2020-10-11 | 22:50 | 49.934
2020-10-11 | 22:50 | 49.934
2020-10-11 | 22:50 | 49.934
2020-10-11 | 22:50 | 49.932
2020-10-11 | 22:50 | 49.933
2020-10-11 | 22:50 | 49.932
2020-10-11 | 22:50 | 49.931
2020-10-11 | 22:50 | 49.931
2020-10-11 | 22:50 | 49.931
2020-10-11 | 22:50 | 49.933
2020-10-11 | 22:50 | 49.936
2020-10-11 | 22:50 | 49.936
2020-10-11 | 22:50 | 49.936
2020-10-11 | 22:50 | 49.935
2020-10-11 | 22:50 | 49.938
2020-10-11 | 22:50 | 49.938
2020-10-11 | 22:50 | 49.937
2020-10-11 | 22:50 | 49.936
2020-10-11 | 22:50 | 49.935
2020-10-11 | 22:50 | 49.934
2020-10-11 | 22:50 | 49.93
2020-10-11 | 22:50 | 49.93
2020-10-11 | 22:50 | 49.93
2020-10-11 | 22:50 | 49.931
2020-10-11 | 22:50 | 49.93
2020-10-11 | 22:50 | 49.928
2020-10-11 | 22:50 | 49.924
2020-10-11 | 22:50 | 49.919
2020-10-11 | 22:50 | 49.919
2020-10-11 | 22:50 | 49.917
2020-10-11 | 22:50 | 49.915
2020-10-11 | 22:50 | 49.914
2020-10-11 | 22:50 | 49.913
2020-10-11 | 22:50 | 49.914
2020-10-11 | 22:50 | 49.917
2020-10-11 | 22:50 | 49.917
2020-10-11 | 22:50 | 49.917
2020-10-11 | 22:50 | 49.92
2020-10-11 | 22:50 | 49.921
2020-10-11 | 22:50 | 49.922
2020-10-11 | 22:50 | 49.923
2020-10-11 | 22:50 | 49.925
2020-10-11 | 22:50 | 49.925
2020-10-11 | 22:50 | 49.927
2020-10-11 | 22:50 | 49.927
2020-10-11 | 22:50 | 49.926
2020-10-11 | 22:50 | 49.926
2020-10-11 | 22:50 | 49.926
2020-10-11 | 22:50 | 49.926
2020-10-11 | 22:50 | 49.925
2020-10-11 | 22:50 | 49.924
2020-10-11 | 22:50 | 49.921
2020-10-11 | 22:50 | 49.92
2020-10-11 | 22:50 | 49.919
2020-10-11 | 22:51 | 49.919
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.919
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.923
2020-10-11 | 22:51 | 49.926
2020-10-11 | 22:51 | 49.929
2020-10-11 | 22:51 | 49.93
2020-10-11 | 22:51 | 49.932
2020-10-11 | 22:51 | 49.935
2020-10-11 | 22:51 | 49.934
2020-10-11 | 22:51 | 49.934
2020-10-11 | 22:51 | 49.932
2020-10-11 | 22:51 | 49.931
2020-10-11 | 22:51 | 49.93
2020-10-11 | 22:51 | 49.929
2020-10-11 | 22:51 | 49.927
2020-10-11 | 22:51 | 49.926
2020-10-11 | 22:51 | 49.926
2020-10-11 | 22:51 | 49.925
2020-10-11 | 22:51 | 49.923
2020-10-11 | 22:51 | 49.923
2020-10-11 | 22:51 | 49.922
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.922
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.923
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.92
2020-10-11 | 22:51 | 49.921
2020-10-11 | 22:51 | 49.922
2020-10-11 | 22:51 | 49.923
2020-10-11 | 22:51 | 49.925
2020-10-11 | 22:51 | 49.925
2020-10-11 | 22:51 | 49.927
2020-10-11 | 22:51 | 49.925
2020-10-11 | 22:51 | 49.925
2020-10-11 | 22:51 | 49.924
2020-10-11 | 22:51 | 49.925
2020-10-11 | 22:51 | 49.927
2020-10-11 | 22:51 | 49.93
2020-10-11 | 22:51 | 49.931
2020-10-11 | 22:51 | 49.933
2020-10-11 | 22:51 | 49.934
2020-10-11 | 22:51 | 49.933
2020-10-11 | 22:51 | 49.933
2020-10-11 | 22:51 | 49.931
2020-10-11 | 22:51 | 49.93
2020-10-11 | 22:51 | 49.927
2020-10-11 | 22:52 | 49.927
2020-10-11 | 22:52 | 49.926
2020-10-11 | 22:52 | 49.925
2020-10-11 | 22:52 | 49.924
2020-10-11 | 22:52 | 49.924
2020-10-11 | 22:52 | 49.924
2020-10-11 | 22:52 | 49.923
2020-10-11 | 22:52 | 49.922
2020-10-11 | 22:52 | 49.921
2020-10-11 | 22:52 | 49.919
2020-10-11 | 22:52 | 49.918
2020-10-11 | 22:52 | 49.914
2020-10-11 | 22:52 | 49.911
2020-10-11 | 22:52 | 49.909
2020-10-11 | 22:52 | 49.908
2020-10-11 | 22:52 | 49.909
2020-10-11 | 22:52 | 49.91
2020-10-11 | 22:52 | 49.912
2020-10-11 | 22:52 | 49.914
2020-10-11 | 22:52 | 49.916
2020-10-11 | 22:52 | 49.918
2020-10-11 | 22:52 | 49.919
2020-10-11 | 22:52 | 49.92
2020-10-11 | 22:52 | 49.92
2020-10-11 | 22:52 | 49.919
2020-10-11 | 22:52 | 49.917
2020-10-11 | 22:52 | 49.917
2020-10-11 | 22:52 | 49.917
2020-10-11 | 22:52 | 49.919
2020-10-11 | 22:52 | 49.919
2020-10-11 | 22:52 | 49.92
2020-10-11 | 22:52 | 49.92
2020-10-11 | 22:52 | 49.921
2020-10-11 | 22:52 | 49.921
2020-10-11 | 22:52 | 49.92
2020-10-11 | 22:52 | 49.919
2020-10-11 | 22:52 | 49.917
2020-10-11 | 22:52 | 49.917
2020-10-11 | 22:52 | 49.916
2020-10-11 | 22:52 | 49.916
2020-10-11 | 22:52 | 49.914
2020-10-11 | 22:52 | 49.915
2020-10-11 | 22:52 | 49.912
2020-10-11 | 22:52 | 49.911
2020-10-11 | 22:52 | 49.909
2020-10-11 | 22:52 | 49.905
2020-10-11 | 22:52 | 49.903
2020-10-11 | 22:52 | 49.902
2020-10-11 | 22:52 | 49.902
2020-10-11 | 22:52 | 49.903
2020-10-11 | 22:52 | 49.903
2020-10-11 | 22:52 | 49.904
2020-10-11 | 22:52 | 49.906
2020-10-11 | 22:52 | 49.907
2020-10-11 | 22:52 | 49.908
2020-10-11 | 22:52 | 49.911
2020-10-11 | 22:52 | 49.912
2020-10-11 | 22:52 | 49.911
2020-10-11 | 22:52 | 49.91
2020-10-11 | 22:52 | 49.911
2020-10-11 | 22:52 | 49.911
2020-10-11 | 22:53 | 49.911
2020-10-11 | 22:53 | 49.911
2020-10-11 | 22:53 | 49.912
2020-10-11 | 22:53 | 49.914
2020-10-11 | 22:53 | 49.914
2020-10-11 | 22:53 | 49.913
2020-10-11 | 22:53 | 49.914
2020-10-11 | 22:53 | 49.916
2020-10-11 | 22:53 | 49.918
2020-10-11 | 22:53 | 49.919
2020-10-11 | 22:53 | 49.92
2020-10-11 | 22:53 | 49.922
2020-10-11 | 22:53 | 49.924
2020-10-11 | 22:53 | 49.925
2020-10-11 | 22:53 | 49.926
2020-10-11 | 22:53 | 49.926
2020-10-11 | 22:53 | 49.927
2020-10-11 | 22:53 | 49.927
2020-10-11 | 22:53 | 49.929
2020-10-11 | 22:53 | 49.929
2020-10-11 | 22:53 | 49.929
2020-10-11 | 22:53 | 49.928
2020-10-11 | 22:53 | 49.927
2020-10-11 | 22:53 | 49.926
2020-10-11 | 22:53 | 49.925
2020-10-11 | 22:53 | 49.925
2020-10-11 | 22:53 | 49.924
2020-10-11 | 22:53 | 49.924
2020-10-11 | 22:53 | 49.922
2020-10-11 | 22:53 | 49.921
2020-10-11 | 22:53 | 49.919
2020-10-11 | 22:53 | 49.918
2020-10-11 | 22:53 | 49.916
2020-10-11 | 22:53 | 49.916
2020-10-11 | 22:53 | 49.916
2020-10-11 | 22:53 | 49.916
2020-10-11 | 22:53 | 49.918
2020-10-11 | 22:53 | 49.92
2020-10-11 | 22:53 | 49.921
2020-10-11 | 22:53 | 49.921
2020-10-11 | 22:53 | 49.92
2020-10-11 | 22:53 | 49.921
2020-10-11 | 22:53 | 49.924
2020-10-11 | 22:53 | 49.923
2020-10-11 | 22:53 | 49.923
2020-10-11 | 22:53 | 49.924
2020-10-11 | 22:53 | 49.921
2020-10-11 | 22:53 | 49.919
2020-10-11 | 22:53 | 49.916
2020-10-11 | 22:53 | 49.914
2020-10-11 | 22:53 | 49.912
2020-10-11 | 22:53 | 49.912
2020-10-11 | 22:53 | 49.912
2020-10-11 | 22:53 | 49.911
2020-10-11 | 22:53 | 49.909
2020-10-11 | 22:53 | 49.909
2020-10-11 | 22:53 | 49.909
2020-10-11 | 22:53 | 49.908
2020-10-11 | 22:53 | 49.907
2020-10-11 | 22:54 | 49.909
2020-10-11 | 22:54 | 49.909
2020-10-11 | 22:54 | 49.908
2020-10-11 | 22:54 | 49.908
2020-10-11 | 22:54 | 49.907
2020-10-11 | 22:54 | 49.908
2020-10-11 | 22:54 | 49.91
2020-10-11 | 22:54 | 49.914
2020-10-11 | 22:54 | 49.917
2020-10-11 | 22:54 | 49.919
2020-10-11 | 22:54 | 49.92
2020-10-11 | 22:54 | 49.923
2020-10-11 | 22:54 | 49.925
2020-10-11 | 22:54 | 49.925
2020-10-11 | 22:54 | 49.921
2020-10-11 | 22:54 | 49.918
2020-10-11 | 22:54 | 49.917
2020-10-11 | 22:54 | 49.917
2020-10-11 | 22:54 | 49.917
2020-10-11 | 22:54 | 49.918
2020-10-11 | 22:54 | 49.92
2020-10-11 | 22:54 | 49.919
2020-10-11 | 22:54 | 49.921
2020-10-11 | 22:54 | 49.921
2020-10-11 | 22:54 | 49.921
2020-10-11 | 22:54 | 49.921
2020-10-11 | 22:54 | 49.92
2020-10-11 | 22:54 | 49.919
2020-10-11 | 22:54 | 49.918
2020-10-11 | 22:54 | 49.916
2020-10-11 | 22:54 | 49.914
2020-10-11 | 22:54 | 49.913
2020-10-11 | 22:54 | 49.911
2020-10-11 | 22:54 | 49.911
2020-10-11 | 22:54 | 49.91
2020-10-11 | 22:54 | 49.911
2020-10-11 | 22:54 | 49.91
2020-10-11 | 22:54 | 49.91
2020-10-11 | 22:54 | 49.911
2020-10-11 | 22:54 | 49.912
2020-10-11 | 22:54 | 49.913
2020-10-11 | 22:54 | 49.912
2020-10-11 | 22:54 | 49.913
2020-10-11 | 22:54 | 49.912
2020-10-11 | 22:54 | 49.913
2020-10-11 | 22:54 | 49.914
2020-10-11 | 22:54 | 49.914
2020-10-11 | 22:54 | 49.915
2020-10-11 | 22:54 | 49.915
2020-10-11 | 22:54 | 49.914
2020-10-11 | 22:54 | 49.916
2020-10-11 | 22:54 | 49.917
2020-10-11 | 22:54 | 49.916
2020-10-11 | 22:54 | 49.916
2020-10-11 | 22:54 | 49.918
2020-10-11 | 22:54 | 49.921
2020-10-11 | 22:54 | 49.923
2020-10-11 | 22:54 | 49.924
2020-10-11 | 22:54 | 49.925
2020-10-11 | 22:54 | 49.926
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.929
2020-10-11 | 22:55 | 49.929
2020-10-11 | 22:55 | 49.929
2020-10-11 | 22:55 | 49.929
2020-10-11 | 22:55 | 49.928
2020-10-11 | 22:55 | 49.927
2020-10-11 | 22:55 | 49.927
2020-10-11 | 22:55 | 49.927
2020-10-11 | 22:55 | 49.927
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.924
2020-10-11 | 22:55 | 49.923
2020-10-11 | 22:55 | 49.924
2020-10-11 | 22:55 | 49.925
2020-10-11 | 22:55 | 49.924
2020-10-11 | 22:55 | 49.925
2020-10-11 | 22:55 | 49.924
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.929
2020-10-11 | 22:55 | 49.932
2020-10-11 | 22:55 | 49.932
2020-10-11 | 22:55 | 49.933
2020-10-11 | 22:55 | 49.932
2020-10-11 | 22:55 | 49.931
2020-10-11 | 22:55 | 49.931
2020-10-11 | 22:55 | 49.929
2020-10-11 | 22:55 | 49.928
2020-10-11 | 22:55 | 49.927
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.927
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.925
2020-10-11 | 22:55 | 49.925
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.926
2020-10-11 | 22:55 | 49.928
2020-10-11 | 22:55 | 49.93
2020-10-11 | 22:55 | 49.931
2020-10-11 | 22:55 | 49.931
2020-10-11 | 22:55 | 49.932
2020-10-11 | 22:55 | 49.932
2020-10-11 | 22:55 | 49.932
2020-10-11 | 22:55 | 49.933
2020-10-11 | 22:55 | 49.933
2020-10-11 | 22:55 | 49.934
2020-10-11 | 22:55 | 49.934
2020-10-11 | 22:55 | 49.934
2020-10-11 | 22:55 | 49.934
2020-10-11 | 22:55 | 49.933
2020-10-11 | 22:55 | 49.934
2020-10-11 | 22:55 | 49.935
2020-10-11 | 22:55 | 49.937
2020-10-11 | 22:55 | 49.941
2020-10-11 | 22:55 | 49.941
2020-10-11 | 22:55 | 49.944
2020-10-11 | 22:55 | 49.944
2020-10-11 | 22:56 | 49.943
2020-10-11 | 22:56 | 49.942
2020-10-11 | 22:56 | 49.941
2020-10-11 | 22:56 | 49.939
2020-10-11 | 22:56 | 49.936
2020-10-11 | 22:56 | 49.934
2020-10-11 | 22:56 | 49.934
2020-10-11 | 22:56 | 49.935
2020-10-11 | 22:56 | 49.938
2020-10-11 | 22:56 | 49.941
2020-10-11 | 22:56 | 49.943
2020-10-11 | 22:56 | 49.945
2020-10-11 | 22:56 | 49.946
2020-10-11 | 22:56 | 49.948
2020-10-11 | 22:56 | 49.949
2020-10-11 | 22:56 | 49.948
2020-10-11 | 22:56 | 49.947
2020-10-11 | 22:56 | 49.945
2020-10-11 | 22:56 | 49.945
2020-10-11 | 22:56 | 49.946
2020-10-11 | 22:56 | 49.949
2020-10-11 | 22:56 | 49.953
2020-10-11 | 22:56 | 49.957
2020-10-11 | 22:56 | 49.96
2020-10-11 | 22:56 | 49.962
2020-10-11 | 22:56 | 49.962
2020-10-11 | 22:56 | 49.961
2020-10-11 | 22:56 | 49.959
2020-10-11 | 22:56 | 49.958
2020-10-11 | 22:56 | 49.955
2020-10-11 | 22:56 | 49.952
2020-10-11 | 22:56 | 49.95
2020-10-11 | 22:56 | 49.949
2020-10-11 | 22:56 | 49.947
2020-10-11 | 22:56 | 49.947
2020-10-11 | 22:56 | 49.947
2020-10-11 | 22:56 | 49.95
2020-10-11 | 22:56 | 49.953
2020-10-11 | 22:56 | 49.956
2020-10-11 | 22:56 | 49.959
2020-10-11 | 22:56 | 49.962
2020-10-11 | 22:56 | 49.965
2020-10-11 | 22:56 | 49.967
2020-10-11 | 22:56 | 49.967
2020-10-11 | 22:56 | 49.966
2020-10-11 | 22:56 | 49.963
2020-10-11 | 22:56 | 49.963
2020-10-11 | 22:56 | 49.963
2020-10-11 | 22:56 | 49.963
2020-10-11 | 22:56 | 49.964
2020-10-11 | 22:56 | 49.965
2020-10-11 | 22:56 | 49.966
2020-10-11 | 22:56 | 49.968
2020-10-11 | 22:56 | 49.97
2020-10-11 | 22:56 | 49.972
2020-10-11 | 22:56 | 49.974
2020-10-11 | 22:56 | 49.975
2020-10-11 | 22:56 | 49.976
2020-10-11 | 22:56 | 49.976
2020-10-11 | 22:56 | 49.974
2020-10-11 | 22:56 | 49.975
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.974
2020-10-11 | 22:57 | 49.974
2020-10-11 | 22:57 | 49.973
2020-10-11 | 22:57 | 49.973
2020-10-11 | 22:57 | 49.974
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.976
2020-10-11 | 22:57 | 49.978
2020-10-11 | 22:57 | 49.978
2020-10-11 | 22:57 | 49.979
2020-10-11 | 22:57 | 49.979
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.979
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.981
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.98
2020-10-11 | 22:57 | 49.979
2020-10-11 | 22:57 | 49.978
2020-10-11 | 22:57 | 49.977
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.973
2020-10-11 | 22:57 | 49.971
2020-10-11 | 22:57 | 49.969
2020-10-11 | 22:57 | 49.968
2020-10-11 | 22:57 | 49.968
2020-10-11 | 22:57 | 49.969
2020-10-11 | 22:57 | 49.97
2020-10-11 | 22:57 | 49.973
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.976
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.975
2020-10-11 | 22:57 | 49.974
2020-10-11 | 22:57 | 49.972
2020-10-11 | 22:57 | 49.971
2020-10-11 | 22:57 | 49.97
2020-10-11 | 22:57 | 49.97
2020-10-11 | 22:57 | 49.97
2020-10-11 | 22:57 | 49.969
2020-10-11 | 22:57 | 49.968
2020-10-11 | 22:57 | 49.966
2020-10-11 | 22:57 | 49.964
2020-10-11 | 22:57 | 49.964
2020-10-11 | 22:57 | 49.962
2020-10-11 | 22:57 | 49.963
2020-10-11 | 22:57 | 49.964
2020-10-11 | 22:57 | 49.965
2020-10-11 | 22:57 | 49.966
2020-10-11 | 22:57 | 49.968
2020-10-11 | 22:58 | 49.971
2020-10-11 | 22:58 | 49.972
2020-10-11 | 22:58 | 49.974
2020-10-11 | 22:58 | 49.973
2020-10-11 | 22:58 | 49.972
2020-10-11 | 22:58 | 49.973
2020-10-11 | 22:58 | 49.971
2020-10-11 | 22:58 | 49.97
2020-10-11 | 22:58 | 49.967
2020-10-11 | 22:58 | 49.965
2020-10-11 | 22:58 | 49.964
2020-10-11 | 22:58 | 49.966
2020-10-11 | 22:58 | 49.969
2020-10-11 | 22:58 | 49.97
2020-10-11 | 22:58 | 49.972
2020-10-11 | 22:58 | 49.973
2020-10-11 | 22:58 | 49.973
2020-10-11 | 22:58 | 49.972
2020-10-11 | 22:58 | 49.969
2020-10-11 | 22:58 | 49.967
2020-10-11 | 22:58 | 49.965
2020-10-11 | 22:58 | 49.964
2020-10-11 | 22:58 | 49.964
2020-10-11 | 22:58 | 49.966
2020-10-11 | 22:58 | 49.968
2020-10-11 | 22:58 | 49.97
2020-10-11 | 22:58 | 49.972
2020-10-11 | 22:58 | 49.975
2020-10-11 | 22:58 | 49.977
2020-10-11 | 22:58 | 49.979
2020-10-11 | 22:58 | 49.981
2020-10-11 | 22:58 | 49.982
2020-10-11 | 22:58 | 49.982
2020-10-11 | 22:58 | 49.982
2020-10-11 | 22:58 | 49.982
2020-10-11 | 22:58 | 49.982
2020-10-11 | 22:58 | 49.984
2020-10-11 | 22:58 | 49.984
2020-10-11 | 22:58 | 49.985
2020-10-11 | 22:58 | 49.987
2020-10-11 | 22:58 | 49.989
2020-10-11 | 22:58 | 49.989
2020-10-11 | 22:58 | 49.988
2020-10-11 | 22:58 | 49.988
2020-10-11 | 22:58 | 49.987
2020-10-11 | 22:58 | 49.988
2020-10-11 | 22:58 | 49.989
2020-10-11 | 22:58 | 49.988
2020-10-11 | 22:58 | 49.987
2020-10-11 | 22:58 | 49.986
2020-10-11 | 22:58 | 49.986
2020-10-11 | 22:58 | 49.986
2020-10-11 | 22:58 | 49.985
2020-10-11 | 22:58 | 49.984
2020-10-11 | 22:58 | 49.982
2020-10-11 | 22:58 | 49.981
2020-10-11 | 22:58 | 49.981
2020-10-11 | 22:58 | 49.98
2020-10-11 | 22:58 | 49.979
2020-10-11 | 22:58 | 49.98
2020-10-11 | 22:59 | 49.982
2020-10-11 | 22:59 | 49.985
2020-10-11 | 22:59 | 49.987
2020-10-11 | 22:59 | 49.99
2020-10-11 | 22:59 | 49.993
2020-10-11 | 22:59 | 49.997
2020-10-11 | 22:59 | 50.001
2020-10-11 | 22:59 | 50.004
2020-10-11 | 22:59 | 50.006
2020-10-11 | 22:59 | 50.006
2020-10-11 | 22:59 | 50.004
2020-10-11 | 22:59 | 50.002
2020-10-11 | 22:59 | 50.002
2020-10-11 | 22:59 | 50.002
2020-10-11 | 22:59 | 50.001
2020-10-11 | 22:59 | 50.001
2020-10-11 | 22:59 | 50.001
2020-10-11 | 22:59 | 50.002
2020-10-11 | 22:59 | 50.001
2020-10-11 | 22:59 | 50.001
2020-10-11 | 22:59 | 50.003
2020-10-11 | 22:59 | 50.005
2020-10-11 | 22:59 | 50.006
2020-10-11 | 22:59 | 50.007
2020-10-11 | 22:59 | 50.008
2020-10-11 | 22:59 | 50.009
2020-10-11 | 22:59 | 50.012
2020-10-11 | 22:59 | 50.017
2020-10-11 | 22:59 | 50.022
2020-10-11 | 22:59 | 50.026

## Event 20201014-1
In UTC
Date | Time | Freq
2020-10-14 | 10:23 | 49.974
2020-10-14 | 10:23 | 49.976
2020-10-14 | 10:23 | 49.979
2020-10-14 | 10:23 | 49.982
2020-10-14 | 10:23 | 49.984
2020-10-14 | 10:23 | 49.987
2020-10-14 | 10:23 | 49.99
2020-10-14 | 10:23 | 49.994
2020-10-14 | 10:23 | 49.995
2020-10-14 | 10:23 | 49.997
2020-10-14 | 10:23 | 49.996
2020-10-14 | 10:23 | 49.998
2020-10-14 | 10:23 | 50.008
2020-10-14 | 10:23 | 50.021
2020-10-14 | 10:23 | 50.033
2020-10-14 | 10:23 | 50.045
2020-10-14 | 10:23 | 50.054
2020-10-14 | 10:23 | 50.057
2020-10-14 | 10:23 | 50.055
2020-10-14 | 10:23 | 50.056
2020-10-14 | 10:23 | 50.058
2020-10-14 | 10:23 | 50.058
2020-10-14 | 10:23 | 50.059
2020-10-14 | 10:23 | 50.058
2020-10-14 | 10:23 | 50.057
2020-10-14 | 10:23 | 50.058
2020-10-14 | 10:23 | 50.06
2020-10-14 | 10:23 | 50.059
2020-10-14 | 10:23 | 50.06
2020-10-14 | 10:23 | 50.061
2020-10-14 | 10:24 | 50.061
2020-10-14 | 10:24 | 50.061
2020-10-14 | 10:24 | 50.058
2020-10-14 | 10:24 | 50.057
2020-10-14 | 10:24 | 50.058
2020-10-14 | 10:24 | 50.056
2020-10-14 | 10:24 | 50.055
2020-10-14 | 10:24 | 50.056
2020-10-14 | 10:24 | 50.055
2020-10-14 | 10:24 | 50.055
2020-10-14 | 10:24 | 50.053
2020-10-14 | 10:24 | 50.052
2020-10-14 | 10:24 | 50.051
2020-10-14 | 10:24 | 50.05
2020-10-14 | 10:24 | 50.047
2020-10-14 | 10:24 | 50.044
2020-10-14 | 10:24 | 50.041
2020-10-14 | 10:24 | 50.037
2020-10-14 | 10:24 | 50.034
2020-10-14 | 10:24 | 50.031
2020-10-14 | 10:24 | 50.028
2020-10-14 | 10:24 | 50.025
2020-10-14 | 10:24 | 50.022
2020-10-14 | 10:24 | 50.021
2020-10-14 | 10:24 | 50.019
2020-10-14 | 10:24 | 50.02
2020-10-14 | 10:24 | 50.021
2020-10-14 | 10:24 | 50.022
2020-10-14 | 10:24 | 50.023
2020-10-14 | 10:24 | 50.024
2020-10-14 | 10:24 | 50.024
2020-10-14 | 10:24 | 50.025
2020-10-14 | 10:24 | 50.026
2020-10-14 | 10:24 | 50.028
2020-10-14 | 10:24 | 50.031
2020-10-14 | 10:24 | 50.035
2020-10-14 | 10:24 | 50.037
2020-10-14 | 10:24 | 50.037
2020-10-14 | 10:24 | 50.039
2020-10-14 | 10:24 | 50.041
2020-10-14 | 10:24 | 50.041
2020-10-14 | 10:24 | 50.042
2020-10-14 | 10:24 | 50.043
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.047
2020-10-14 | 10:24 | 50.047
2020-10-14 | 10:24 | 50.046
2020-10-14 | 10:24 | 50.044
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.045
2020-10-14 | 10:24 | 50.048
2020-10-14 | 10:24 | 50.051
2020-10-14 | 10:24 | 50.053
2020-10-14 | 10:24 | 50.051
2020-10-14 | 10:24 | 50.052
2020-10-14 | 10:24 | 50.051
2020-10-14 | 10:24 | 50.051
2020-10-14 | 10:25 | 50.05
2020-10-14 | 10:25 | 50.052
2020-10-14 | 10:25 | 50.055
2020-10-14 | 10:25 | 50.056
2020-10-14 | 10:25 | 50.057
2020-10-14 | 10:25 | 50.059
2020-10-14 | 10:25 | 50.059
2020-10-14 | 10:25 | 50.061
2020-10-14 | 10:25 | 50.059
2020-10-14 | 10:25 | 50.057
2020-10-14 | 10:25 | 50.058
2020-10-14 | 10:25 | 50.059
2020-10-14 | 10:25 | 50.059
2020-10-14 | 10:25 | 50.06
2020-10-14 | 10:25 | 50.061
2020-10-14 | 10:25 | 50.06
2020-10-14 | 10:25 | 50.06
2020-10-14 | 10:25 | 50.062
2020-10-14 | 10:25 | 50.064
2020-10-14 | 10:25 | 50.064
2020-10-14 | 10:25 | 50.065
2020-10-14 | 10:25 | 50.066
2020-10-14 | 10:25 | 50.065
2020-10-14 | 10:25 | 50.063
2020-10-14 | 10:25 | 50.063
2020-10-14 | 10:25 | 50.063
2020-10-14 | 10:25 | 50.062
2020-10-14 | 10:25 | 50.061
2020-10-14 | 10:25 | 50.061
2020-10-14 | 10:25 | 50.061
2020-10-14 | 10:25 | 50.059
2020-10-14 | 10:25 | 50.056
2020-10-14 | 10:25 | 50.057
2020-10-14 | 10:25 | 50.058
2020-10-14 | 10:25 | 50.058
2020-10-14 | 10:25 | 50.055
2020-10-14 | 10:25 | 50.056
2020-10-14 | 10:25 | 50.057
2020-10-14 | 10:25 | 50.055
2020-10-14 | 10:25 | 50.05
2020-10-14 | 10:25 | 50.045
2020-10-14 | 10:25 | 50.04
2020-10-14 | 10:25 | 50.035
2020-10-14 | 10:25 | 50.031
2020-10-14 | 10:25 | 50.029
2020-10-14 | 10:25 | 50.025
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.021
2020-10-14 | 10:25 | 50.021
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.023
2020-10-14 | 10:25 | 50.022
2020-10-14 | 10:25 | 50.024
2020-10-14 | 10:25 | 50.027
2020-10-14 | 10:25 | 50.026
2020-10-14 | 10:26 | 50.025
2020-10-14 | 10:26 | 50.025
2020-10-14 | 10:26 | 50.021
2020-10-14 | 10:26 | 50.017
2020-10-14 | 10:26 | 50.013
2020-10-14 | 10:26 | 50.011
2020-10-14 | 10:26 | 50.01
2020-10-14 | 10:26 | 50.006
2020-10-14 | 10:26 | 50.006
2020-10-14 | 10:26 | 50.007
2020-10-14 | 10:26 | 50.007
2020-10-14 | 10:26 | 50.006
2020-10-14 | 10:26 | 50.006
2020-10-14 | 10:26 | 50.004
2020-10-14 | 10:26 | 50
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 50
2020-10-14 | 10:26 | 50.001
2020-10-14 | 10:26 | 50.001
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.996
2020-10-14 | 10:26 | 49.996
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 50
2020-10-14 | 10:26 | 50
2020-10-14 | 10:26 | 50.001
2020-10-14 | 10:26 | 50.001
2020-10-14 | 10:26 | 50.001
2020-10-14 | 10:26 | 50
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.996
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 49.997
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.998
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 49.999
2020-10-14 | 10:26 | 50.001
2020-10-14 | 10:27 | 50.005
2020-10-14 | 10:27 | 50.007
2020-10-14 | 10:27 | 50.008
2020-10-14 | 10:27 | 50.008
2020-10-14 | 10:27 | 50.011
2020-10-14 | 10:27 | 50.014
2020-10-14 | 10:27 | 50.015
2020-10-14 | 10:27 | 50.017
2020-10-14 | 10:27 | 50.018
2020-10-14 | 10:27 | 50.019
2020-10-14 | 10:27 | 50.021
2020-10-14 | 10:27 | 50.023
2020-10-14 | 10:27 | 50.024
2020-10-14 | 10:27 | 50.026
2020-10-14 | 10:27 | 50.028
2020-10-14 | 10:27 | 50.029
2020-10-14 | 10:27 | 50.029
2020-10-14 | 10:27 | 50.028
2020-10-14 | 10:27 | 50.027
2020-10-14 | 10:27 | 50.028
2020-10-14 | 10:27 | 50.028
2020-10-14 | 10:27 | 50.03
2020-10-14 | 10:27 | 50.028
2020-10-14 | 10:27 | 50.028
2020-10-14 | 10:27 | 50.029
2020-10-14 | 10:27 | 50.029
2020-10-14 | 10:27 | 50.03
2020-10-14 | 10:27 | 50.032
2020-10-14 | 10:27 | 50.034
2020-10-14 | 10:27 | 50.036
2020-10-14 | 10:27 | 50.038
2020-10-14 | 10:27 | 50.039
2020-10-14 | 10:27 | 50.041
2020-10-14 | 10:27 | 50.047
2020-10-14 | 10:27 | 50.051
2020-10-14 | 10:27 | 50.055
2020-10-14 | 10:27 | 50.056
2020-10-14 | 10:27 | 50.058
2020-10-14 | 10:27 | 50.059
2020-10-14 | 10:27 | 50.059
2020-10-14 | 10:27 | 50.059
2020-10-14 | 10:27 | 50.058
2020-10-14 | 10:27 | 50.059
2020-10-14 | 10:27 | 50.057
2020-10-14 | 10:27 | 50.057
2020-10-14 | 10:27 | 50.058
2020-10-14 | 10:27 | 50.057
2020-10-14 | 10:27 | 50.057
2020-10-14 | 10:27 | 50.055
2020-10-14 | 10:27 | 50.055
2020-10-14 | 10:27 | 50.052
2020-10-14 | 10:27 | 50.051
2020-10-14 | 10:27 | 50.048
2020-10-14 | 10:27 | 50.046
2020-10-14 | 10:27 | 50.047
2020-10-14 | 10:27 | 50.047
2020-10-14 | 10:27 | 50.049
2020-10-14 | 10:27 | 50.049
2020-10-14 | 10:27 | 50.05
2020-10-14 | 10:28 | 50.049
2020-10-14 | 10:28 | 50.051
2020-10-14 | 10:28 | 50.053
2020-10-14 | 10:28 | 50.052
2020-10-14 | 10:28 | 50.05
2020-10-14 | 10:28 | 50.047
2020-10-14 | 10:28 | 50.047
2020-10-14 | 10:28 | 50.046
2020-10-14 | 10:28 | 50.046
2020-10-14 | 10:28 | 50.048
2020-10-14 | 10:28 | 50.05
2020-10-14 | 10:28 | 50.051
2020-10-14 | 10:28 | 50.051
2020-10-14 | 10:28 | 50.055
2020-10-14 | 10:28 | 50.056
2020-10-14 | 10:28 | 50.057
2020-10-14 | 10:28 | 50.059
2020-10-14 | 10:28 | 50.06
2020-10-14 | 10:28 | 50.059
2020-10-14 | 10:28 | 50.059
2020-10-14 | 10:28 | 50.058
2020-10-14 | 10:28 | 50.058
2020-10-14 | 10:28 | 50.058
2020-10-14 | 10:28 | 50.059
2020-10-14 | 10:28 | 50.061
2020-10-14 | 10:28 | 50.062
2020-10-14 | 10:28 | 50.061
2020-10-14 | 10:28 | 50.063
2020-10-14 | 10:28 | 50.065
2020-10-14 | 10:28 | 50.065
2020-10-14 | 10:28 | 50.065
2020-10-14 | 10:28 | 50.065
2020-10-14 | 10:28 | 50.063
2020-10-14 | 10:28 | 50.06
2020-10-14 | 10:28 | 50.059
2020-10-14 | 10:28 | 50.058
2020-10-14 | 10:28 | 50.057
2020-10-14 | 10:28 | 50.056
2020-10-14 | 10:28 | 50.057
2020-10-14 | 10:28 | 50.053
2020-10-14 | 10:28 | 50.052
2020-10-14 | 10:28 | 50.051
2020-10-14 | 10:28 | 50.048
2020-10-14 | 10:28 | 50.046
2020-10-14 | 10:28 | 50.047
2020-10-14 | 10:28 | 50.047
2020-10-14 | 10:28 | 50.049
2020-10-14 | 10:28 | 50.05
2020-10-14 | 10:28 | 50.049
2020-10-14 | 10:28 | 50.05
2020-10-14 | 10:28 | 50.051
2020-10-14 | 10:28 | 50.051
2020-10-14 | 10:28 | 50.05
2020-10-14 | 10:28 | 50.05
2020-10-14 | 10:28 | 50.053
2020-10-14 | 10:28 | 50.054
2020-10-14 | 10:28 | 50.056
2020-10-14 | 10:28 | 50.058
2020-10-14 | 10:28 | 50.061
2020-10-14 | 10:28 | 50.063
2020-10-14 | 10:28 | 50.062
2020-10-14 | 10:29 | 50.063
2020-10-14 | 10:29 | 50.065
2020-10-14 | 10:29 | 50.066
2020-10-14 | 10:29 | 50.066
2020-10-14 | 10:29 | 50.066
2020-10-14 | 10:29 | 50.064
2020-10-14 | 10:29 | 50.065
2020-10-14 | 10:29 | 50.064
2020-10-14 | 10:29 | 50.064
2020-10-14 | 10:29 | 50.063
2020-10-14 | 10:29 | 50.061
2020-10-14 | 10:29 | 50.06
2020-10-14 | 10:29 | 50.062
2020-10-14 | 10:29 | 50.061
2020-10-14 | 10:29 | 50.062
2020-10-14 | 10:29 | 50.063
2020-10-14 | 10:29 | 50.064
2020-10-14 | 10:29 | 50.064
2020-10-14 | 10:29 | 50.067
2020-10-14 | 10:29 | 50.068
2020-10-14 | 10:29 | 50.069
2020-10-14 | 10:29 | 50.071
2020-10-14 | 10:29 | 50.075
2020-10-14 | 10:29 | 50.075
2020-10-14 | 10:29 | 50.075
2020-10-14 | 10:29 | 50.074
2020-10-14 | 10:29 | 50.069
2020-10-14 | 10:29 | 50.068
2020-10-14 | 10:29 | 50.068
2020-10-14 | 10:29 | 50.064
2020-10-14 | 10:29 | 50.061
2020-10-14 | 10:29 | 50.061
2020-10-14 | 10:29 | 50.062
2020-10-14 | 10:29 | 50.062
2020-10-14 | 10:29 | 50.06
2020-10-14 | 10:29 | 50.06
2020-10-14 | 10:29 | 50.057
2020-10-14 | 10:29 | 50.055
2020-10-14 | 10:29 | 50.052
2020-10-14 | 10:29 | 50.049
2020-10-14 | 10:29 | 50.047
2020-10-14 | 10:29 | 50.046
2020-10-14 | 10:29 | 50.044
2020-10-14 | 10:29 | 50.041
2020-10-14 | 10:29 | 50.041
2020-10-14 | 10:29 | 50.04
2020-10-14 | 10:29 | 50.039
2020-10-14 | 10:29 | 50.038
2020-10-14 | 10:29 | 50.037
2020-10-14 | 10:29 | 50.036
2020-10-14 | 10:29 | 50.038
2020-10-14 | 10:29 | 50.04
2020-10-14 | 10:29 | 50.043
2020-10-14 | 10:29 | 50.049
2020-10-14 | 10:29 | 50.052
2020-10-14 | 10:29 | 50.056
2020-10-14 | 10:29 | 50.061
2020-10-14 | 10:29 | 50.065
2020-10-14 | 10:29 | 50.069
2020-10-14 | 10:30 | 50.072
2020-10-14 | 10:30 | 50.073
2020-10-14 | 10:30 | 50.071
2020-10-14 | 10:30 | 50.07
2020-10-14 | 10:30 | 50.069
2020-10-14 | 10:30 | 50.069
2020-10-14 | 10:30 | 50.071
2020-10-14 | 10:30 | 50.073
2020-10-14 | 10:30 | 50.072
2020-10-14 | 10:30 | 50.07
2020-10-14 | 10:30 | 50.069
2020-10-14 | 10:30 | 50.066
2020-10-14 | 10:30 | 50.065
2020-10-14 | 10:30 | 50.065
2020-10-14 | 10:30 | 50.067
2020-10-14 | 10:30 | 50.068
2020-10-14 | 10:30 | 50.071
2020-10-14 | 10:30 | 50.074
2020-10-14 | 10:30 | 50.078
2020-10-14 | 10:30 | 50.08
2020-10-14 | 10:30 | 50.082
2020-10-14 | 10:30 | 50.084
2020-10-14 | 10:30 | 50.084
2020-10-14 | 10:30 | 50.083
2020-10-14 | 10:30 | 50.086
2020-10-14 | 10:30 | 50.085
2020-10-14 | 10:30 | 50.084
2020-10-14 | 10:30 | 50.084
2020-10-14 | 10:30 | 50.085
2020-10-14 | 10:30 | 50.086
2020-10-14 | 10:30 | 50.085
2020-10-14 | 10:30 | 50.082
2020-10-14 | 10:30 | 50.078
2020-10-14 | 10:30 | 50.076
2020-10-14 | 10:30 | 50.074
2020-10-14 | 10:30 | 50.073
2020-10-14 | 10:30 | 50.071
2020-10-14 | 10:30 | 50.069
2020-10-14 | 10:30 | 50.069
2020-10-14 | 10:30 | 50.07
2020-10-14 | 10:30 | 50.07
2020-10-14 | 10:30 | 50.069
2020-10-14 | 10:30 | 50.068
2020-10-14 | 10:30 | 50.066
2020-10-14 | 10:30 | 50.064
2020-10-14 | 10:30 | 50.062
2020-10-14 | 10:30 | 50.062
2020-10-14 | 10:30 | 50.061
2020-10-14 | 10:30 | 50.061
2020-10-14 | 10:30 | 50.061
2020-10-14 | 10:30 | 50.062
2020-10-14 | 10:30 | 50.062
2020-10-14 | 10:30 | 50.061
2020-10-14 | 10:30 | 50.06
2020-10-14 | 10:30 | 50.057
2020-10-14 | 10:30 | 50.054
2020-10-14 | 10:30 | 50.055
2020-10-14 | 10:30 | 50.053
2020-10-14 | 10:30 | 50.053
2020-10-14 | 10:30 | 50.054
2020-10-14 | 10:30 | 50.058
2020-10-14 | 10:31 | 50.06
2020-10-14 | 10:31 | 50.061
2020-10-14 | 10:31 | 50.058
2020-10-14 | 10:31 | 50.058
2020-10-14 | 10:31 | 50.058
2020-10-14 | 10:31 | 50.051
2020-10-14 | 10:31 | 50.043
2020-10-14 | 10:31 | 50.039
2020-10-14 | 10:31 | 50.034
2020-10-14 | 10:31 | 50.031
2020-10-14 | 10:31 | 50.029
2020-10-14 | 10:31 | 50.028
2020-10-14 | 10:31 | 50.026
2020-10-14 | 10:31 | 50.025
2020-10-14 | 10:31 | 50.025
2020-10-14 | 10:31 | 50.026
2020-10-14 | 10:31 | 50.026
2020-10-14 | 10:31 | 50.025
2020-10-14 | 10:31 | 50.026
2020-10-14 | 10:31 | 50.024
2020-10-14 | 10:31 | 50.022
2020-10-14 | 10:31 | 50.021
2020-10-14 | 10:31 | 50.02
2020-10-14 | 10:31 | 50.017
2020-10-14 | 10:31 | 50.014
2020-10-14 | 10:31 | 50.012
2020-10-14 | 10:31 | 50.011
2020-10-14 | 10:31 | 50.008
2020-10-14 | 10:31 | 50.006
2020-10-14 | 10:31 | 50.007
2020-10-14 | 10:31 | 50.006
2020-10-14 | 10:31 | 50.005
2020-10-14 | 10:31 | 50.002
2020-10-14 | 10:31 | 50.001
2020-10-14 | 10:31 | 50.001
2020-10-14 | 10:31 | 50.004
2020-10-14 | 10:31 | 50.005
2020-10-14 | 10:31 | 50.007
2020-10-14 | 10:31 | 50.008
2020-10-14 | 10:31 | 50.008
2020-10-14 | 10:31 | 50.009
2020-10-14 | 10:31 | 50.012
2020-10-14 | 10:31 | 50.013
2020-10-14 | 10:31 | 50.014
2020-10-14 | 10:31 | 50.013
2020-10-14 | 10:31 | 50.014
2020-10-14 | 10:31 | 50.012
2020-10-14 | 10:31 | 50.011
2020-10-14 | 10:31 | 50.012
2020-10-14 | 10:31 | 50.012
2020-10-14 | 10:31 | 50.011
2020-10-14 | 10:31 | 50.012
2020-10-14 | 10:31 | 50.01
2020-10-14 | 10:31 | 50.01
2020-10-14 | 10:31 | 50.009
2020-10-14 | 10:31 | 50.007
2020-10-14 | 10:31 | 50.004
2020-10-14 | 10:31 | 50.003
2020-10-14 | 10:31 | 50.004
2020-10-14 | 10:32 | 50.006
2020-10-14 | 10:32 | 50.01
2020-10-14 | 10:32 | 50.014
2020-10-14 | 10:32 | 50.017
2020-10-14 | 10:32 | 50.018
2020-10-14 | 10:32 | 50.017
2020-10-14 | 10:32 | 50.017
2020-10-14 | 10:32 | 50.017
2020-10-14 | 10:32 | 50.016
2020-10-14 | 10:32 | 50.015
2020-10-14 | 10:32 | 50.013
2020-10-14 | 10:32 | 50.015
2020-10-14 | 10:32 | 50.016
2020-10-14 | 10:32 | 50.017
2020-10-14 | 10:32 | 50.013
2020-10-14 | 10:32 | 50.011
2020-10-14 | 10:32 | 50.01
2020-10-14 | 10:32 | 50.008
2020-10-14 | 10:32 | 50.005
2020-10-14 | 10:32 | 50.001
2020-10-14 | 10:32 | 49.998
2020-10-14 | 10:32 | 49.995
2020-10-14 | 10:32 | 49.992
2020-10-14 | 10:32 | 49.991
2020-10-14 | 10:32 | 49.989
2020-10-14 | 10:32 | 49.985
2020-10-14 | 10:32 | 49.987
2020-10-14 | 10:32 | 49.987
2020-10-14 | 10:32 | 49.988
2020-10-14 | 10:32 | 49.988
2020-10-14 | 10:32 | 49.989
2020-10-14 | 10:32 | 49.988
2020-10-14 | 10:32 | 49.986
2020-10-14 | 10:32 | 49.983
2020-10-14 | 10:32 | 49.982
2020-10-14 | 10:32 | 49.98
2020-10-14 | 10:32 | 49.981
2020-10-14 | 10:32 | 49.98
2020-10-14 | 10:32 | 49.98
2020-10-14 | 10:32 | 49.979
2020-10-14 | 10:32 | 49.978
2020-10-14 | 10:32 | 49.974
2020-10-14 | 10:32 | 49.972
2020-10-14 | 10:32 | 49.972
2020-10-14 | 10:32 | 49.971
2020-10-14 | 10:32 | 49.972
2020-10-14 | 10:32 | 49.973
2020-10-14 | 10:32 | 49.973
2020-10-14 | 10:32 | 49.973
2020-10-14 | 10:32 | 49.977
2020-10-14 | 10:32 | 49.979
2020-10-14 | 10:32 | 49.982
2020-10-14 | 10:32 | 49.983
2020-10-14 | 10:32 | 49.987
2020-10-14 | 10:32 | 49.989
2020-10-14 | 10:32 | 49.991
2020-10-14 | 10:32 | 49.992
2020-10-14 | 10:32 | 49.994
2020-10-14 | 10:32 | 49.999
2020-10-14 | 10:32 | 50.001
2020-10-14 | 10:32 | 50.003
2020-10-14 | 10:33 | 50.005
2020-10-14 | 10:33 | 50.007
2020-10-14 | 10:33 | 50.011
2020-10-14 | 10:33 | 50.012
2020-10-14 | 10:33 | 50.014
2020-10-14 | 10:33 | 50.014
2020-10-14 | 10:33 | 50.014
2020-10-14 | 10:33 | 50.012
2020-10-14 | 10:33 | 50.011
2020-10-14 | 10:33 | 50.007
2020-10-14 | 10:33 | 50.003
2020-10-14 | 10:33 | 50.002
2020-10-14 | 10:33 | 50
2020-10-14 | 10:33 | 50
2020-10-14 | 10:33 | 49.999
2020-10-14 | 10:33 | 50.001
2020-10-14 | 10:33 | 50.001
2020-10-14 | 10:33 | 50.003
2020-10-14 | 10:33 | 50.004
2020-10-14 | 10:33 | 50.006
2020-10-14 | 10:33 | 50.009
2020-10-14 | 10:33 | 50.01
2020-10-14 | 10:33 | 50.012
2020-10-14 | 10:33 | 50.012
2020-10-14 | 10:33 | 50.01
2020-10-14 | 10:33 | 50.01
2020-10-14 | 10:33 | 50.009
2020-10-14 | 10:33 | 50.01
2020-10-14 | 10:33 | 50.01
2020-10-14 | 10:33 | 50.011
2020-10-14 | 10:33 | 50.011
2020-10-14 | 10:33 | 50.014
2020-10-14 | 10:33 | 50.014
2020-10-14 | 10:33 | 50.012
2020-10-14 | 10:33 | 50.01
2020-10-14 | 10:33 | 50.009
2020-10-14 | 10:33 | 50.005
2020-10-14 | 10:33 | 50.001
2020-10-14 | 10:33 | 49.996
2020-10-14 | 10:33 | 49.992
2020-10-14 | 10:33 | 49.988
2020-10-14 | 10:33 | 49.983
2020-10-14 | 10:33 | 49.976
2020-10-14 | 10:33 | 49.972
2020-10-14 | 10:33 | 49.967
2020-10-14 | 10:33 | 49.962
2020-10-14 | 10:33 | 49.956
2020-10-14 | 10:33 | 49.949
2020-10-14 | 10:33 | 49.944
2020-10-14 | 10:33 | 49.942
2020-10-14 | 10:33 | 49.941
2020-10-14 | 10:33 | 49.941
2020-10-14 | 10:33 | 49.938
2020-10-14 | 10:33 | 49.935
2020-10-14 | 10:33 | 49.934
2020-10-14 | 10:33 | 49.929
2020-10-14 | 10:33 | 49.93
2020-10-14 | 10:33 | 49.931
2020-10-14 | 10:33 | 49.932
2020-10-14 | 10:34 | 49.933
2020-10-14 | 10:34 | 49.935
2020-10-14 | 10:34 | 49.94
2020-10-14 | 10:34 | 49.943
2020-10-14 | 10:34 | 49.945
2020-10-14 | 10:34 | 49.944
2020-10-14 | 10:34 | 49.945
2020-10-14 | 10:34 | 49.946
2020-10-14 | 10:34 | 49.947
2020-10-14 | 10:34 | 49.947
2020-10-14 | 10:34 | 49.945
2020-10-14 | 10:34 | 49.945
2020-10-14 | 10:34 | 49.945
2020-10-14 | 10:34 | 49.944
2020-10-14 | 10:34 | 49.945
2020-10-14 | 10:34 | 49.943
2020-10-14 | 10:34 | 49.942
2020-10-14 | 10:34 | 49.944
2020-10-14 | 10:34 | 49.943
2020-10-14 | 10:34 | 49.943
2020-10-14 | 10:34 | 49.94
2020-10-14 | 10:34 | 49.938
2020-10-14 | 10:34 | 49.937
2020-10-14 | 10:34 | 49.934
2020-10-14 | 10:34 | 49.931
2020-10-14 | 10:34 | 49.927
2020-10-14 | 10:34 | 49.925
2020-10-14 | 10:34 | 49.921
2020-10-14 | 10:34 | 49.919
2020-10-14 | 10:34 | 49.916
2020-10-14 | 10:34 | 49.911
2020-10-14 | 10:34 | 49.907
2020-10-14 | 10:34 | 49.906
2020-10-14 | 10:34 | 49.905
2020-10-14 | 10:34 | 49.904
2020-10-14 | 10:34 | 49.903
2020-10-14 | 10:34 | 49.9
2020-10-14 | 10:34 | 49.899
2020-10-14 | 10:34 | 49.897
2020-10-14 | 10:34 | 49.896
2020-10-14 | 10:34 | 49.895
2020-10-14 | 10:34 | 49.893
2020-10-14 | 10:34 | 49.893
2020-10-14 | 10:34 | 49.893
2020-10-14 | 10:34 | 49.893
2020-10-14 | 10:34 | 49.892
2020-10-14 | 10:34 | 49.891
2020-10-14 | 10:34 | 49.89
2020-10-14 | 10:34 | 49.89
2020-10-14 | 10:34 | 49.89
2020-10-14 | 10:34 | 49.891
2020-10-14 | 10:34 | 49.892
2020-10-14 | 10:34 | 49.893
2020-10-14 | 10:34 | 49.893
2020-10-14 | 10:34 | 49.895
2020-10-14 | 10:34 | 49.897
2020-10-14 | 10:34 | 49.898
2020-10-14 | 10:34 | 49.897
2020-10-14 | 10:34 | 49.898
2020-10-14 | 10:34 | 49.898
2020-10-14 | 10:34 | 49.901
2020-10-14 | 10:35 | 49.901
2020-10-14 | 10:35 | 49.901
2020-10-14 | 10:35 | 49.903
2020-10-14 | 10:35 | 49.904
2020-10-14 | 10:35 | 49.905
2020-10-14 | 10:35 | 49.905
2020-10-14 | 10:35 | 49.904
2020-10-14 | 10:35 | 49.904
2020-10-14 | 10:35 | 49.904
2020-10-14 | 10:35 | 49.905
2020-10-14 | 10:35 | 49.906
2020-10-14 | 10:35 | 49.906
2020-10-14 | 10:35 | 49.907
2020-10-14 | 10:35 | 49.908
2020-10-14 | 10:35 | 49.91
2020-10-14 | 10:35 | 49.909
2020-10-14 | 10:35 | 49.911
2020-10-14 | 10:35 | 49.912
2020-10-14 | 10:35 | 49.911
2020-10-14 | 10:35 | 49.911
2020-10-14 | 10:35 | 49.912
2020-10-14 | 10:35 | 49.913
2020-10-14 | 10:35 | 49.915
2020-10-14 | 10:35 | 49.917
2020-10-14 | 10:35 | 49.92
2020-10-14 | 10:35 | 49.923
2020-10-14 | 10:35 | 49.925
2020-10-14 | 10:35 | 49.926
2020-10-14 | 10:35 | 49.928
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.929
2020-10-14 | 10:35 | 49.927
2020-10-14 | 10:35 | 49.925
2020-10-14 | 10:35 | 49.925
2020-10-14 | 10:35 | 49.925
2020-10-14 | 10:35 | 49.927
2020-10-14 | 10:35 | 49.928
2020-10-14 | 10:35 | 49.929
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.929
2020-10-14 | 10:35 | 49.931
2020-10-14 | 10:35 | 49.932
2020-10-14 | 10:35 | 49.933
2020-10-14 | 10:35 | 49.932
2020-10-14 | 10:35 | 49.932
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.93
2020-10-14 | 10:35 | 49.929
2020-10-14 | 10:35 | 49.928
2020-10-14 | 10:35 | 49.926
2020-10-14 | 10:35 | 49.923
2020-10-14 | 10:35 | 49.923
2020-10-14 | 10:35 | 49.923
2020-10-14 | 10:35 | 49.922
2020-10-14 | 10:36 | 49.921
2020-10-14 | 10:36 | 49.922
2020-10-14 | 10:36 | 49.92
2020-10-14 | 10:36 | 49.918
2020-10-14 | 10:36 | 49.914
2020-10-14 | 10:36 | 49.912
2020-10-14 | 10:36 | 49.912
2020-10-14 | 10:36 | 49.911
2020-10-14 | 10:36 | 49.909
2020-10-14 | 10:36 | 49.908
2020-10-14 | 10:36 | 49.907
2020-10-14 | 10:36 | 49.905
2020-10-14 | 10:36 | 49.906
2020-10-14 | 10:36 | 49.906
2020-10-14 | 10:36 | 49.905
2020-10-14 | 10:36 | 49.905
2020-10-14 | 10:36 | 49.905
2020-10-14 | 10:36 | 49.906
2020-10-14 | 10:36 | 49.906
2020-10-14 | 10:36 | 49.905
2020-10-14 | 10:36 | 49.904
2020-10-14 | 10:36 | 49.902
2020-10-14 | 10:36 | 49.9
2020-10-14 | 10:36 | 49.898
2020-10-14 | 10:36 | 49.898
2020-10-14 | 10:36 | 49.895
2020-10-14 | 10:36 | 49.894
2020-10-14 | 10:36 | 49.894
2020-10-14 | 10:36 | 49.892
2020-10-14 | 10:36 | 49.892
2020-10-14 | 10:36 | 49.892
2020-10-14 | 10:36 | 49.89
2020-10-14 | 10:36 | 49.888
2020-10-14 | 10:36 | 49.885
2020-10-14 | 10:36 | 49.882
2020-10-14 | 10:36 | 49.877
2020-10-14 | 10:36 | 49.872
2020-10-14 | 10:36 | 49.868
2020-10-14 | 10:36 | 49.865
2020-10-14 | 10:36 | 49.863
2020-10-14 | 10:36 | 49.862
2020-10-14 | 10:36 | 49.86
2020-10-14 | 10:36 | 49.861
2020-10-14 | 10:36 | 49.859
2020-10-14 | 10:36 | 49.858
2020-10-14 | 10:36 | 49.853
2020-10-14 | 10:36 | 49.852
2020-10-14 | 10:36 | 49.851
2020-10-14 | 10:36 | 49.854
2020-10-14 | 10:36 | 49.856
2020-10-14 | 10:36 | 49.859
2020-10-14 | 10:36 | 49.863
2020-10-14 | 10:36 | 49.865
2020-10-14 | 10:36 | 49.867
2020-10-14 | 10:36 | 49.867
2020-10-14 | 10:36 | 49.866
2020-10-14 | 10:36 | 49.865
2020-10-14 | 10:36 | 49.866
2020-10-14 | 10:36 | 49.865
2020-10-14 | 10:36 | 49.865
2020-10-14 | 10:36 | 49.864
2020-10-14 | 10:37 | 49.865
2020-10-14 | 10:37 | 49.864
2020-10-14 | 10:37 | 49.865
2020-10-14 | 10:37 | 49.864
2020-10-14 | 10:37 | 49.863
2020-10-14 | 10:37 | 49.862
2020-10-14 | 10:37 | 49.862
2020-10-14 | 10:37 | 49.861
2020-10-14 | 10:37 | 49.863
2020-10-14 | 10:37 | 49.864
2020-10-14 | 10:37 | 49.865
2020-10-14 | 10:37 | 49.867
2020-10-14 | 10:37 | 49.869
2020-10-14 | 10:37 | 49.872
2020-10-14 | 10:37 | 49.873
2020-10-14 | 10:37 | 49.877
2020-10-14 | 10:37 | 49.879
2020-10-14 | 10:37 | 49.882
2020-10-14 | 10:37 | 49.886
2020-10-14 | 10:37 | 49.89
2020-10-14 | 10:37 | 49.894
2020-10-14 | 10:37 | 49.896
2020-10-14 | 10:37 | 49.898
2020-10-14 | 10:37 | 49.9
2020-10-14 | 10:37 | 49.899
2020-10-14 | 10:37 | 49.897
2020-10-14 | 10:37 | 49.898
2020-10-14 | 10:37 | 49.898
2020-10-14 | 10:37 | 49.899
2020-10-14 | 10:37 | 49.899
2020-10-14 | 10:37 | 49.897
2020-10-14 | 10:37 | 49.896
2020-10-14 | 10:37 | 49.893
2020-10-14 | 10:37 | 49.892
2020-10-14 | 10:37 | 49.89
2020-10-14 | 10:37 | 49.889
2020-10-14 | 10:37 | 49.886
2020-10-14 | 10:37 | 49.885
2020-10-14 | 10:37 | 49.884
2020-10-14 | 10:37 | 49.881
2020-10-14 | 10:37 | 49.88
2020-10-14 | 10:37 | 49.877
2020-10-14 | 10:37 | 49.875
2020-10-14 | 10:37 | 49.873
2020-10-14 | 10:37 | 49.873
2020-10-14 | 10:37 | 49.871
2020-10-14 | 10:37 | 49.87
2020-10-14 | 10:37 | 49.868
2020-10-14 | 10:37 | 49.868
2020-10-14 | 10:37 | 49.865
2020-10-14 | 10:37 | 49.864
2020-10-14 | 10:37 | 49.862
2020-10-14 | 10:37 | 49.86
2020-10-14 | 10:37 | 49.859
2020-10-14 | 10:37 | 49.859
2020-10-14 | 10:37 | 49.859
2020-10-14 | 10:37 | 49.859
2020-10-14 | 10:37 | 49.86
2020-10-14 | 10:37 | 49.86
2020-10-14 | 10:38 | 49.861
2020-10-14 | 10:38 | 49.862
2020-10-14 | 10:38 | 49.864
2020-10-14 | 10:38 | 49.864
2020-10-14 | 10:38 | 49.866
2020-10-14 | 10:38 | 49.865
2020-10-14 | 10:38 | 49.866
2020-10-14 | 10:38 | 49.866
2020-10-14 | 10:38 | 49.866
2020-10-14 | 10:38 | 49.866
2020-10-14 | 10:38 | 49.864
2020-10-14 | 10:38 | 49.864
2020-10-14 | 10:38 | 49.863
2020-10-14 | 10:38 | 49.865
2020-10-14 | 10:38 | 49.864
2020-10-14 | 10:38 | 49.865
2020-10-14 | 10:38 | 49.867
2020-10-14 | 10:38 | 49.868
2020-10-14 | 10:38 | 49.869
2020-10-14 | 10:38 | 49.869
2020-10-14 | 10:38 | 49.871
2020-10-14 | 10:38 | 49.874
2020-10-14 | 10:38 | 49.877
2020-10-14 | 10:38 | 49.879
2020-10-14 | 10:38 | 49.882
2020-10-14 | 10:38 | 49.883
2020-10-14 | 10:38 | 49.885
2020-10-14 | 10:38 | 49.887
2020-10-14 | 10:38 | 49.891
2020-10-14 | 10:38 | 49.894
2020-10-14 | 10:38 | 49.896
2020-10-14 | 10:38 | 49.897
2020-10-14 | 10:38 | 49.898
2020-10-14 | 10:38 | 49.899
2020-10-14 | 10:38 | 49.899
2020-10-14 | 10:38 | 49.9
2020-10-14 | 10:38 | 49.899
2020-10-14 | 10:38 | 49.898
2020-10-14 | 10:38 | 49.898
2020-10-14 | 10:38 | 49.896
2020-10-14 | 10:38 | 49.894
2020-10-14 | 10:38 | 49.893
2020-10-14 | 10:38 | 49.89
2020-10-14 | 10:38 | 49.889
2020-10-14 | 10:38 | 49.888
2020-10-14 | 10:38 | 49.886
2020-10-14 | 10:38 | 49.884
2020-10-14 | 10:38 | 49.881
2020-10-14 | 10:38 | 49.878
2020-10-14 | 10:38 | 49.879
2020-10-14 | 10:38 | 49.878
2020-10-14 | 10:38 | 49.88
2020-10-14 | 10:38 | 49.881
2020-10-14 | 10:38 | 49.883
2020-10-14 | 10:38 | 49.885
2020-10-14 | 10:38 | 49.887
2020-10-14 | 10:38 | 49.889
2020-10-14 | 10:38 | 49.891
2020-10-14 | 10:38 | 49.892
2020-10-14 | 10:38 | 49.892
2020-10-14 | 10:38 | 49.893
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.896
2020-10-14 | 10:39 | 49.895
2020-10-14 | 10:39 | 49.895
2020-10-14 | 10:39 | 49.896
2020-10-14 | 10:39 | 49.896
2020-10-14 | 10:39 | 49.899
2020-10-14 | 10:39 | 49.902
2020-10-14 | 10:39 | 49.904
2020-10-14 | 10:39 | 49.905
2020-10-14 | 10:39 | 49.907
2020-10-14 | 10:39 | 49.909
2020-10-14 | 10:39 | 49.912
2020-10-14 | 10:39 | 49.917
2020-10-14 | 10:39 | 49.919
2020-10-14 | 10:39 | 49.92
2020-10-14 | 10:39 | 49.919
2020-10-14 | 10:39 | 49.92
2020-10-14 | 10:39 | 49.92
2020-10-14 | 10:39 | 49.919
2020-10-14 | 10:39 | 49.919
2020-10-14 | 10:39 | 49.92
2020-10-14 | 10:39 | 49.924
2020-10-14 | 10:39 | 49.924
2020-10-14 | 10:39 | 49.928
2020-10-14 | 10:39 | 49.925
2020-10-14 | 10:39 | 49.926
2020-10-14 | 10:39 | 49.924
2020-10-14 | 10:39 | 49.921
2020-10-14 | 10:39 | 49.92
2020-10-14 | 10:39 | 49.918
2020-10-14 | 10:39 | 49.915
2020-10-14 | 10:39 | 49.913
2020-10-14 | 10:39 | 49.91
2020-10-14 | 10:39 | 49.909
2020-10-14 | 10:39 | 49.907
2020-10-14 | 10:39 | 49.904
2020-10-14 | 10:39 | 49.903
2020-10-14 | 10:39 | 49.899
2020-10-14 | 10:39 | 49.898
2020-10-14 | 10:39 | 49.895
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.891
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.892
2020-10-14 | 10:39 | 49.893
2020-10-14 | 10:39 | 49.892
2020-10-14 | 10:39 | 49.894
2020-10-14 | 10:40 | 49.897
2020-10-14 | 10:40 | 49.9
2020-10-14 | 10:40 | 49.9
2020-10-14 | 10:40 | 49.904
2020-10-14 | 10:40 | 49.906
2020-10-14 | 10:40 | 49.908
2020-10-14 | 10:40 | 49.909
2020-10-14 | 10:40 | 49.908
2020-10-14 | 10:40 | 49.913
2020-10-14 | 10:40 | 49.914
2020-10-14 | 10:40 | 49.916
2020-10-14 | 10:40 | 49.918
2020-10-14 | 10:40 | 49.92
2020-10-14 | 10:40 | 49.923
2020-10-14 | 10:40 | 49.927
2020-10-14 | 10:40 | 49.928
2020-10-14 | 10:40 | 49.929
2020-10-14 | 10:40 | 49.931
2020-10-14 | 10:40 | 49.932
2020-10-14 | 10:40 | 49.935
2020-10-14 | 10:40 | 49.939
2020-10-14 | 10:40 | 49.937
2020-10-14 | 10:40 | 49.938
2020-10-14 | 10:40 | 49.938
2020-10-14 | 10:40 | 49.937
2020-10-14 | 10:40 | 49.938
2020-10-14 | 10:40 | 49.935
2020-10-14 | 10:40 | 49.934
2020-10-14 | 10:40 | 49.929
2020-10-14 | 10:40 | 49.927
2020-10-14 | 10:40 | 49.927
2020-10-14 | 10:40 | 49.921
2020-10-14 | 10:40 | 49.92
2020-10-14 | 10:40 | 49.92
2020-10-14 | 10:40 | 49.918
2020-10-14 | 10:40 | 49.916
2020-10-14 | 10:40 | 49.916
2020-10-14 | 10:40 | 49.913
2020-10-14 | 10:40 | 49.915
2020-10-14 | 10:40 | 49.913
2020-10-14 | 10:40 | 49.914
2020-10-14 | 10:40 | 49.912
2020-10-14 | 10:40 | 49.912
2020-10-14 | 10:40 | 49.911
2020-10-14 | 10:40 | 49.913
2020-10-14 | 10:40 | 49.914
2020-10-14 | 10:40 | 49.916
2020-10-14 | 10:40 | 49.917
2020-10-14 | 10:40 | 49.917
2020-10-14 | 10:40 | 49.917
2020-10-14 | 10:40 | 49.917
2020-10-14 | 10:40 | 49.917
2020-10-14 | 10:40 | 49.918
2020-10-14 | 10:40 | 49.92
2020-10-14 | 10:40 | 49.926
2020-10-14 | 10:40 | 49.926
2020-10-14 | 10:40 | 49.93
2020-10-14 | 10:40 | 49.931
2020-10-14 | 10:40 | 49.929
2020-10-14 | 10:40 | 49.929
2020-10-14 | 10:40 | 49.926
2020-10-14 | 10:41 | 49.926
2020-10-14 | 10:41 | 49.925
2020-10-14 | 10:41 | 49.925
2020-10-14 | 10:41 | 49.924
2020-10-14 | 10:41 | 49.924
2020-10-14 | 10:41 | 49.922
2020-10-14 | 10:41 | 49.919
2020-10-14 | 10:41 | 49.915
2020-10-14 | 10:41 | 49.914
2020-10-14 | 10:41 | 49.913
2020-10-14 | 10:41 | 49.915
2020-10-14 | 10:41 | 49.915
2020-10-14 | 10:41 | 49.919
2020-10-14 | 10:41 | 49.925
2020-10-14 | 10:41 | 49.929
2020-10-14 | 10:41 | 49.932
2020-10-14 | 10:41 | 49.936
2020-10-14 | 10:41 | 49.936
2020-10-14 | 10:41 | 49.94
2020-10-14 | 10:41 | 49.942
2020-10-14 | 10:41 | 49.941
2020-10-14 | 10:41 | 49.941
2020-10-14 | 10:41 | 49.941
2020-10-14 | 10:41 | 49.942
2020-10-14 | 10:41 | 49.941
2020-10-14 | 10:41 | 49.941
2020-10-14 | 10:41 | 49.937
2020-10-14 | 10:41 | 49.935
2020-10-14 | 10:41 | 49.931
2020-10-14 | 10:41 | 49.926
2020-10-14 | 10:41 | 49.923
2020-10-14 | 10:41 | 49.922
2020-10-14 | 10:41 | 49.92
2020-10-14 | 10:41 | 49.919
2020-10-14 | 10:41 | 49.92
2020-10-14 | 10:41 | 49.921
2020-10-14 | 10:41 | 49.919
2020-10-14 | 10:41 | 49.918
2020-10-14 | 10:41 | 49.917
2020-10-14 | 10:41 | 49.916
2020-10-14 | 10:41 | 49.913
2020-10-14 | 10:41 | 49.911
2020-10-14 | 10:41 | 49.907
2020-10-14 | 10:41 | 49.904
2020-10-14 | 10:41 | 49.899
2020-10-14 | 10:41 | 49.898
2020-10-14 | 10:41 | 49.899
2020-10-14 | 10:41 | 49.898
2020-10-14 | 10:41 | 49.899
2020-10-14 | 10:41 | 49.899
2020-10-14 | 10:41 | 49.897
2020-10-14 | 10:41 | 49.896
2020-10-14 | 10:41 | 49.895
2020-10-14 | 10:41 | 49.896
2020-10-14 | 10:41 | 49.898
2020-10-14 | 10:41 | 49.897
2020-10-14 | 10:41 | 49.898
2020-10-14 | 10:41 | 49.897
2020-10-14 | 10:41 | 49.898
2020-10-14 | 10:42 | 49.903
2020-10-14 | 10:42 | 49.903
2020-10-14 | 10:42 | 49.904
2020-10-14 | 10:42 | 49.905
2020-10-14 | 10:42 | 49.902
2020-10-14 | 10:42 | 49.902
2020-10-14 | 10:42 | 49.898
2020-10-14 | 10:42 | 49.899
2020-10-14 | 10:42 | 49.898
2020-10-14 | 10:42 | 49.897
2020-10-14 | 10:42 | 49.896
2020-10-14 | 10:42 | 49.897
2020-10-14 | 10:42 | 49.899
2020-10-14 | 10:42 | 49.9
2020-10-14 | 10:42 | 49.903
2020-10-14 | 10:42 | 49.906
2020-10-14 | 10:42 | 49.907
2020-10-14 | 10:42 | 49.908
2020-10-14 | 10:42 | 49.91
2020-10-14 | 10:42 | 49.907
2020-10-14 | 10:42 | 49.907
2020-10-14 | 10:42 | 49.904
2020-10-14 | 10:42 | 49.904
2020-10-14 | 10:42 | 49.901
2020-10-14 | 10:42 | 49.903
2020-10-14 | 10:42 | 49.902
2020-10-14 | 10:42 | 49.901
2020-10-14 | 10:42 | 49.903
2020-10-14 | 10:42 | 49.901
2020-10-14 | 10:42 | 49.9
2020-10-14 | 10:42 | 49.899
2020-10-14 | 10:42 | 49.894
2020-10-14 | 10:42 | 49.891
2020-10-14 | 10:42 | 49.892
2020-10-14 | 10:42 | 49.891
2020-10-14 | 10:42 | 49.891
2020-10-14 | 10:42 | 49.892
2020-10-14 | 10:42 | 49.889
2020-10-14 | 10:42 | 49.889
2020-10-14 | 10:42 | 49.889
2020-10-14 | 10:42 | 49.889
2020-10-14 | 10:42 | 49.889
2020-10-14 | 10:42 | 49.894
2020-10-14 | 10:42 | 49.895
2020-10-14 | 10:42 | 49.897
2020-10-14 | 10:42 | 49.897
2020-10-14 | 10:42 | 49.9
2020-10-14 | 10:42 | 49.903
2020-10-14 | 10:42 | 49.906
2020-10-14 | 10:42 | 49.907
2020-10-14 | 10:42 | 49.907
2020-10-14 | 10:42 | 49.906
2020-10-14 | 10:42 | 49.906
2020-10-14 | 10:42 | 49.907
2020-10-14 | 10:42 | 49.908
2020-10-14 | 10:42 | 49.905
2020-10-14 | 10:42 | 49.904
2020-10-14 | 10:42 | 49.897
2020-10-14 | 10:42 | 49.894
2020-10-14 | 10:42 | 49.892
2020-10-14 | 10:42 | 49.892
2020-10-14 | 10:43 | 49.893
2020-10-14 | 10:43 | 49.899
2020-10-14 | 10:43 | 49.902
2020-10-14 | 10:43 | 49.905
2020-10-14 | 10:43 | 49.906
2020-10-14 | 10:43 | 49.907
2020-10-14 | 10:43 | 49.911
2020-10-14 | 10:43 | 49.912
2020-10-14 | 10:43 | 49.913
2020-10-14 | 10:43 | 49.913
2020-10-14 | 10:43 | 49.91
2020-10-14 | 10:43 | 49.911
2020-10-14 | 10:43 | 49.915
2020-10-14 | 10:43 | 49.915
2020-10-14 | 10:43 | 49.919
2020-10-14 | 10:43 | 49.921
2020-10-14 | 10:43 | 49.925
2020-10-14 | 10:43 | 49.924
2020-10-14 | 10:43 | 49.924
2020-10-14 | 10:43 | 49.923
2020-10-14 | 10:43 | 49.924
2020-10-14 | 10:43 | 49.925
2020-10-14 | 10:43 | 49.924
2020-10-14 | 10:43 | 49.923
2020-10-14 | 10:43 | 49.922
2020-10-14 | 10:43 | 49.925
2020-10-14 | 10:43 | 49.924
2020-10-14 | 10:43 | 49.925
2020-10-14 | 10:43 | 49.921
2020-10-14 | 10:43 | 49.916
2020-10-14 | 10:43 | 49.912
2020-10-14 | 10:43 | 49.911
2020-10-14 | 10:43 | 49.908
2020-10-14 | 10:43 | 49.907
2020-10-14 | 10:43 | 49.906
2020-10-14 | 10:43 | 49.907
2020-10-14 | 10:43 | 49.907
2020-10-14 | 10:43 | 49.903
2020-10-14 | 10:43 | 49.903
2020-10-14 | 10:43 | 49.902
2020-10-14 | 10:43 | 49.903
2020-10-14 | 10:43 | 49.901
2020-10-14 | 10:43 | 49.904
2020-10-14 | 10:43 | 49.905
2020-10-14 | 10:43 | 49.906
2020-10-14 | 10:43 | 49.908
2020-10-14 | 10:43 | 49.911
2020-10-14 | 10:43 | 49.913
2020-10-14 | 10:43 | 49.913
2020-10-14 | 10:43 | 49.913
2020-10-14 | 10:43 | 49.911
2020-10-14 | 10:43 | 49.91
2020-10-14 | 10:43 | 49.912
2020-10-14 | 10:43 | 49.909
2020-10-14 | 10:43 | 49.912
2020-10-14 | 10:43 | 49.91
2020-10-14 | 10:43 | 49.91
2020-10-14 | 10:43 | 49.91
2020-10-14 | 10:43 | 49.911
2020-10-14 | 10:44 | 49.91
2020-10-14 | 10:44 | 49.912
2020-10-14 | 10:44 | 49.912
2020-10-14 | 10:44 | 49.915
2020-10-14 | 10:44 | 49.914
2020-10-14 | 10:44 | 49.916
2020-10-14 | 10:44 | 49.916
2020-10-14 | 10:44 | 49.915
2020-10-14 | 10:44 | 49.914
2020-10-14 | 10:44 | 49.916
2020-10-14 | 10:44 | 49.919
2020-10-14 | 10:44 | 49.922
2020-10-14 | 10:44 | 49.922
2020-10-14 | 10:44 | 49.918
2020-10-14 | 10:44 | 49.916
2020-10-14 | 10:44 | 49.913
2020-10-14 | 10:44 | 49.91
2020-10-14 | 10:44 | 49.91
2020-10-14 | 10:44 | 49.908
2020-10-14 | 10:44 | 49.908
2020-10-14 | 10:44 | 49.909
2020-10-14 | 10:44 | 49.906
2020-10-14 | 10:44 | 49.904
2020-10-14 | 10:44 | 49.9
2020-10-14 | 10:44 | 49.897
2020-10-14 | 10:44 | 49.895
2020-10-14 | 10:44 | 49.894
2020-10-14 | 10:44 | 49.893
2020-10-14 | 10:44 | 49.892
2020-10-14 | 10:44 | 49.89
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.889
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.889
2020-10-14 | 10:44 | 49.891
2020-10-14 | 10:44 | 49.892
2020-10-14 | 10:44 | 49.891
2020-10-14 | 10:44 | 49.89
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.883
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.883
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.888
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.887
2020-10-14 | 10:44 | 49.886
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:44 | 49.886
2020-10-14 | 10:44 | 49.885
2020-10-14 | 10:45 | 49.885
2020-10-14 | 10:45 | 49.887
2020-10-14 | 10:45 | 49.887
2020-10-14 | 10:45 | 49.889
2020-10-14 | 10:45 | 49.891
2020-10-14 | 10:45 | 49.893
2020-10-14 | 10:45 | 49.896
2020-10-14 | 10:45 | 49.899
2020-10-14 | 10:45 | 49.903
2020-10-14 | 10:45 | 49.907
2020-10-14 | 10:45 | 49.914
2020-10-14 | 10:45 | 49.919
2020-10-14 | 10:45 | 49.923
2020-10-14 | 10:45 | 49.929
2020-10-14 | 10:45 | 49.93
2020-10-14 | 10:45 | 49.934
2020-10-14 | 10:45 | 49.936
2020-10-14 | 10:45 | 49.937
2020-10-14 | 10:45 | 49.937
2020-10-14 | 10:45 | 49.937
2020-10-14 | 10:45 | 49.936
2020-10-14 | 10:45 | 49.934
2020-10-14 | 10:45 | 49.933
2020-10-14 | 10:45 | 49.93
2020-10-14 | 10:45 | 49.927
2020-10-14 | 10:45 | 49.923
2020-10-14 | 10:45 | 49.921
2020-10-14 | 10:45 | 49.918
2020-10-14 | 10:45 | 49.912
2020-10-14 | 10:45 | 49.907
2020-10-14 | 10:45 | 49.902
2020-10-14 | 10:45 | 49.905
2020-10-14 | 10:45 | 49.902
2020-10-14 | 10:45 | 49.902
2020-10-14 | 10:45 | 49.899
2020-10-14 | 10:45 | 49.9
2020-10-14 | 10:45 | 49.902
2020-10-14 | 10:45 | 49.9
2020-10-14 | 10:45 | 49.898
2020-10-14 | 10:45 | 49.899
2020-10-14 | 10:45 | 49.9
2020-10-14 | 10:45 | 49.899
2020-10-14 | 10:45 | 49.898
2020-10-14 | 10:45 | 49.9
2020-10-14 | 10:45 | 49.898
2020-10-14 | 10:45 | 49.901
2020-10-14 | 10:45 | 49.904
2020-10-14 | 10:45 | 49.904
2020-10-14 | 10:45 | 49.904
2020-10-14 | 10:45 | 49.906
2020-10-14 | 10:45 | 49.904
2020-10-14 | 10:45 | 49.9
2020-10-14 | 10:45 | 49.902
2020-10-14 | 10:45 | 49.902
2020-10-14 | 10:45 | 49.899
2020-10-14 | 10:45 | 49.899
2020-10-14 | 10:45 | 49.897
2020-10-14 | 10:45 | 49.897
2020-10-14 | 10:45 | 49.9
2020-10-14 | 10:46 | 49.901
2020-10-14 | 10:46 | 49.899
2020-10-14 | 10:46 | 49.9
2020-10-14 | 10:46 | 49.901
2020-10-14 | 10:46 | 49.9
2020-10-14 | 10:46 | 49.9
2020-10-14 | 10:46 | 49.902
2020-10-14 | 10:46 | 49.905
2020-10-14 | 10:46 | 49.907
2020-10-14 | 10:46 | 49.906
2020-10-14 | 10:46 | 49.906
2020-10-14 | 10:46 | 49.91
2020-10-14 | 10:46 | 49.913
2020-10-14 | 10:46 | 49.914
2020-10-14 | 10:46 | 49.915
2020-10-14 | 10:46 | 49.914
2020-10-14 | 10:46 | 49.918
2020-10-14 | 10:46 | 49.922
2020-10-14 | 10:46 | 49.923
2020-10-14 | 10:46 | 49.924
2020-10-14 | 10:46 | 49.927
2020-10-14 | 10:46 | 49.93
2020-10-14 | 10:46 | 49.93
2020-10-14 | 10:46 | 49.933
2020-10-14 | 10:46 | 49.937
2020-10-14 | 10:46 | 49.936
2020-10-14 | 10:46 | 49.937
2020-10-14 | 10:46 | 49.94
2020-10-14 | 10:46 | 49.939
2020-10-14 | 10:46 | 49.938
2020-10-14 | 10:46 | 49.942
2020-10-14 | 10:46 | 49.938
2020-10-14 | 10:46 | 49.942
2020-10-14 | 10:46 | 49.942
2020-10-14 | 10:46 | 49.943
2020-10-14 | 10:46 | 49.943
2020-10-14 | 10:46 | 49.943
2020-10-14 | 10:46 | 49.94
2020-10-14 | 10:46 | 49.939
2020-10-14 | 10:46 | 49.936
2020-10-14 | 10:46 | 49.937
2020-10-14 | 10:46 | 49.935
2020-10-14 | 10:46 | 49.936
2020-10-14 | 10:46 | 49.937
2020-10-14 | 10:46 | 49.939
2020-10-14 | 10:46 | 49.935
2020-10-14 | 10:46 | 49.936
2020-10-14 | 10:46 | 49.936
2020-10-14 | 10:46 | 49.935
2020-10-14 | 10:46 | 49.934
2020-10-14 | 10:46 | 49.934
2020-10-14 | 10:46 | 49.932
2020-10-14 | 10:46 | 49.928
2020-10-14 | 10:46 | 49.926
2020-10-14 | 10:46 | 49.926
2020-10-14 | 10:46 | 49.927
2020-10-14 | 10:46 | 49.93
2020-10-14 | 10:46 | 49.93
2020-10-14 | 10:46 | 49.931
2020-10-14 | 10:46 | 49.93
2020-10-14 | 10:46 | 49.933
2020-10-14 | 10:47 | 49.929
2020-10-14 | 10:47 | 49.925
2020-10-14 | 10:47 | 49.924
2020-10-14 | 10:47 | 49.921
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.915
2020-10-14 | 10:47 | 49.917
2020-10-14 | 10:47 | 49.916
2020-10-14 | 10:47 | 49.915
2020-10-14 | 10:47 | 49.92
2020-10-14 | 10:47 | 49.917
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.921
2020-10-14 | 10:47 | 49.923
2020-10-14 | 10:47 | 49.92
2020-10-14 | 10:47 | 49.921
2020-10-14 | 10:47 | 49.92
2020-10-14 | 10:47 | 49.921
2020-10-14 | 10:47 | 49.92
2020-10-14 | 10:47 | 49.924
2020-10-14 | 10:47 | 49.927
2020-10-14 | 10:47 | 49.928
2020-10-14 | 10:47 | 49.929
2020-10-14 | 10:47 | 49.93
2020-10-14 | 10:47 | 49.931
2020-10-14 | 10:47 | 49.929
2020-10-14 | 10:47 | 49.929
2020-10-14 | 10:47 | 49.924
2020-10-14 | 10:47 | 49.925
2020-10-14 | 10:47 | 49.92
2020-10-14 | 10:47 | 49.921
2020-10-14 | 10:47 | 49.921
2020-10-14 | 10:47 | 49.919
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.916
2020-10-14 | 10:47 | 49.914
2020-10-14 | 10:47 | 49.911
2020-10-14 | 10:47 | 49.916
2020-10-14 | 10:47 | 49.915
2020-10-14 | 10:47 | 49.914
2020-10-14 | 10:47 | 49.916
2020-10-14 | 10:47 | 49.915
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.919
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.917
2020-10-14 | 10:47 | 49.918
2020-10-14 | 10:47 | 49.911
2020-10-14 | 10:47 | 49.911
2020-10-14 | 10:47 | 49.912
2020-10-14 | 10:47 | 49.914
2020-10-14 | 10:47 | 49.913
2020-10-14 | 10:47 | 49.913
2020-10-14 | 10:47 | 49.912
2020-10-14 | 10:47 | 49.915
2020-10-14 | 10:47 | 49.914
2020-10-14 | 10:47 | 49.914
2020-10-14 | 10:47 | 49.917
2020-10-14 | 10:48 | 49.917
2020-10-14 | 10:48 | 49.921
2020-10-14 | 10:48 | 49.925
2020-10-14 | 10:48 | 49.927
2020-10-14 | 10:48 | 49.932
2020-10-14 | 10:48 | 49.935
2020-10-14 | 10:48 | 49.935
2020-10-14 | 10:48 | 49.936
2020-10-14 | 10:48 | 49.939
2020-10-14 | 10:48 | 49.936
2020-10-14 | 10:48 | 49.935
2020-10-14 | 10:48 | 49.938
2020-10-14 | 10:48 | 49.936
2020-10-14 | 10:48 | 49.937
2020-10-14 | 10:48 | 49.938
2020-10-14 | 10:48 | 49.935
2020-10-14 | 10:48 | 49.932
2020-10-14 | 10:48 | 49.932
2020-10-14 | 10:48 | 49.931
2020-10-14 | 10:48 | 49.931
2020-10-14 | 10:48 | 49.93
2020-10-14 | 10:48 | 49.929
2020-10-14 | 10:48 | 49.931
2020-10-14 | 10:48 | 49.93
2020-10-14 | 10:48 | 49.926
2020-10-14 | 10:48 | 49.925
2020-10-14 | 10:48 | 49.923
2020-10-14 | 10:48 | 49.92
2020-10-14 | 10:48 | 49.913
2020-10-14 | 10:48 | 49.909
2020-10-14 | 10:48 | 49.904
2020-10-14 | 10:48 | 49.898
2020-10-14 | 10:48 | 49.895
2020-10-14 | 10:48 | 49.891
2020-10-14 | 10:48 | 49.889
2020-10-14 | 10:48 | 49.889
2020-10-14 | 10:48 | 49.889
2020-10-14 | 10:48 | 49.891
2020-10-14 | 10:48 | 49.889
2020-10-14 | 10:48 | 49.888
2020-10-14 | 10:48 | 49.887
2020-10-14 | 10:48 | 49.889
2020-10-14 | 10:48 | 49.887
2020-10-14 | 10:48 | 49.891
2020-10-14 | 10:48 | 49.895
2020-10-14 | 10:48 | 49.901
2020-10-14 | 10:48 | 49.904
2020-10-14 | 10:48 | 49.911
2020-10-14 | 10:48 | 49.916
2020-10-14 | 10:48 | 49.922
2020-10-14 | 10:48 | 49.924
2020-10-14 | 10:48 | 49.927
2020-10-14 | 10:48 | 49.931
2020-10-14 | 10:48 | 49.932
2020-10-14 | 10:48 | 49.935
2020-10-14 | 10:48 | 49.935
2020-10-14 | 10:48 | 49.939
2020-10-14 | 10:48 | 49.941
2020-10-14 | 10:48 | 49.941
2020-10-14 | 10:48 | 49.942
2020-10-14 | 10:49 | 49.944
2020-10-14 | 10:49 | 49.943
2020-10-14 | 10:49 | 49.946
2020-10-14 | 10:49 | 49.947
2020-10-14 | 10:49 | 49.944
2020-10-14 | 10:49 | 49.943
2020-10-14 | 10:49 | 49.943
2020-10-14 | 10:49 | 49.94
2020-10-14 | 10:49 | 49.938
2020-10-14 | 10:49 | 49.935
2020-10-14 | 10:49 | 49.932
2020-10-14 | 10:49 | 49.936
2020-10-14 | 10:49 | 49.935
2020-10-14 | 10:49 | 49.933
2020-10-14 | 10:49 | 49.931
2020-10-14 | 10:49 | 49.931
2020-10-14 | 10:49 | 49.932
2020-10-14 | 10:49 | 49.934
2020-10-14 | 10:49 | 49.935
2020-10-14 | 10:49 | 49.938
2020-10-14 | 10:49 | 49.939
2020-10-14 | 10:49 | 49.94
2020-10-14 | 10:49 | 49.942
2020-10-14 | 10:49 | 49.943
2020-10-14 | 10:49 | 49.944
2020-10-14 | 10:49 | 49.945
2020-10-14 | 10:49 | 49.946
2020-10-14 | 10:49 | 49.945
2020-10-14 | 10:49 | 49.946
2020-10-14 | 10:49 | 49.946
2020-10-14 | 10:49 | 49.942
2020-10-14 | 10:49 | 49.943
2020-10-14 | 10:49 | 49.942
2020-10-14 | 10:49 | 49.945
2020-10-14 | 10:49 | 49.943
2020-10-14 | 10:49 | 49.94
2020-10-14 | 10:49 | 49.937
2020-10-14 | 10:49 | 49.933
2020-10-14 | 10:49 | 49.929
2020-10-14 | 10:49 | 49.926
2020-10-14 | 10:49 | 49.928
2020-10-14 | 10:49 | 49.924
2020-10-14 | 10:49 | 49.921
2020-10-14 | 10:49 | 49.917
2020-10-14 | 10:49 | 49.918
2020-10-14 | 10:49 | 49.919
2020-10-14 | 10:49 | 49.919
2020-10-14 | 10:49 | 49.921
2020-10-14 | 10:49 | 49.924
2020-10-14 | 10:49 | 49.923
2020-10-14 | 10:49 | 49.922
2020-10-14 | 10:49 | 49.923
2020-10-14 | 10:49 | 49.919
2020-10-14 | 10:49 | 49.921
2020-10-14 | 10:49 | 49.92
2020-10-14 | 10:49 | 49.918
2020-10-14 | 10:49 | 49.917
2020-10-14 | 10:49 | 49.913
2020-10-14 | 10:49 | 49.91
2020-10-14 | 10:49 | 49.909
2020-10-14 | 10:50 | 49.906
2020-10-14 | 10:50 | 49.903
2020-10-14 | 10:50 | 49.898
2020-10-14 | 10:50 | 49.897
2020-10-14 | 10:50 | 49.897
2020-10-14 | 10:50 | 49.896
2020-10-14 | 10:50 | 49.896
2020-10-14 | 10:50 | 49.901
2020-10-14 | 10:50 | 49.902
2020-10-14 | 10:50 | 49.903
2020-10-14 | 10:50 | 49.901
2020-10-14 | 10:50 | 49.899
2020-10-14 | 10:50 | 49.898
2020-10-14 | 10:50 | 49.898
2020-10-14 | 10:50 | 49.895
2020-10-14 | 10:50 | 49.898
2020-10-14 | 10:50 | 49.897
2020-10-14 | 10:50 | 49.893
2020-10-14 | 10:50 | 49.893
2020-10-14 | 10:50 | 49.893
2020-10-14 | 10:50 | 49.894
2020-10-14 | 10:50 | 49.894
2020-10-14 | 10:50 | 49.897
2020-10-14 | 10:50 | 49.898
2020-10-14 | 10:50 | 49.895
2020-10-14 | 10:50 | 49.894
2020-10-14 | 10:50 | 49.893
2020-10-14 | 10:50 | 49.89
2020-10-14 | 10:50 | 49.89
2020-10-14 | 10:50 | 49.886
2020-10-14 | 10:50 | 49.885
2020-10-14 | 10:50 | 49.883
2020-10-14 | 10:50 | 49.883
2020-10-14 | 10:50 | 49.883
2020-10-14 | 10:50 | 49.884
2020-10-14 | 10:50 | 49.882
2020-10-14 | 10:50 | 49.882
2020-10-14 | 10:50 | 49.881
2020-10-14 | 10:50 | 49.884
2020-10-14 | 10:50 | 49.882
2020-10-14 | 10:50 | 49.879
2020-10-14 | 10:50 | 49.878
2020-10-14 | 10:50 | 49.875
2020-10-14 | 10:50 | 49.874
2020-10-14 | 10:50 | 49.871
2020-10-14 | 10:50 | 49.869
2020-10-14 | 10:50 | 49.868
2020-10-14 | 10:50 | 49.87
2020-10-14 | 10:50 | 49.87
2020-10-14 | 10:50 | 49.87
2020-10-14 | 10:50 | 49.87
2020-10-14 | 10:50 | 49.87
2020-10-14 | 10:50 | 49.871
2020-10-14 | 10:50 | 49.872
2020-10-14 | 10:50 | 49.873
2020-10-14 | 10:50 | 49.873
2020-10-14 | 10:50 | 49.873
2020-10-14 | 10:50 | 49.874
2020-10-14 | 10:50 | 49.872
2020-10-14 | 10:50 | 49.875
2020-10-14 | 10:51 | 49.875
2020-10-14 | 10:51 | 49.875
2020-10-14 | 10:51 | 49.875
2020-10-14 | 10:51 | 49.876
2020-10-14 | 10:51 | 49.879
2020-10-14 | 10:51 | 49.88
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.88
2020-10-14 | 10:51 | 49.88
2020-10-14 | 10:51 | 49.882
2020-10-14 | 10:51 | 49.882
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.879
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.879
2020-10-14 | 10:51 | 49.882
2020-10-14 | 10:51 | 49.88
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.883
2020-10-14 | 10:51 | 49.884
2020-10-14 | 10:51 | 49.885
2020-10-14 | 10:51 | 49.884
2020-10-14 | 10:51 | 49.884
2020-10-14 | 10:51 | 49.888
2020-10-14 | 10:51 | 49.889
2020-10-14 | 10:51 | 49.893
2020-10-14 | 10:51 | 49.891
2020-10-14 | 10:51 | 49.893
2020-10-14 | 10:51 | 49.892
2020-10-14 | 10:51 | 49.894
2020-10-14 | 10:51 | 49.894
2020-10-14 | 10:51 | 49.893
2020-10-14 | 10:51 | 49.891
2020-10-14 | 10:51 | 49.888
2020-10-14 | 10:51 | 49.886
2020-10-14 | 10:51 | 49.884
2020-10-14 | 10:51 | 49.883
2020-10-14 | 10:51 | 49.882
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.88
2020-10-14 | 10:51 | 49.879
2020-10-14 | 10:51 | 49.878
2020-10-14 | 10:51 | 49.877
2020-10-14 | 10:51 | 49.88
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.879
2020-10-14 | 10:51 | 49.876
2020-10-14 | 10:51 | 49.874
2020-10-14 | 10:51 | 49.874
2020-10-14 | 10:51 | 49.873
2020-10-14 | 10:51 | 49.87
2020-10-14 | 10:51 | 49.87
2020-10-14 | 10:51 | 49.872
2020-10-14 | 10:51 | 49.876
2020-10-14 | 10:51 | 49.878
2020-10-14 | 10:51 | 49.878
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:51 | 49.881
2020-10-14 | 10:52 | 49.881
2020-10-14 | 10:52 | 49.881
2020-10-14 | 10:52 | 49.883
2020-10-14 | 10:52 | 49.881
2020-10-14 | 10:52 | 49.88
2020-10-14 | 10:52 | 49.881
2020-10-14 | 10:52 | 49.879
2020-10-14 | 10:52 | 49.879
2020-10-14 | 10:52 | 49.879
2020-10-14 | 10:52 | 49.881
2020-10-14 | 10:52 | 49.884
2020-10-14 | 10:52 | 49.885
2020-10-14 | 10:52 | 49.889
2020-10-14 | 10:52 | 49.89
2020-10-14 | 10:52 | 49.894
2020-10-14 | 10:52 | 49.897
2020-10-14 | 10:52 | 49.896
2020-10-14 | 10:52 | 49.899
2020-10-14 | 10:52 | 49.896
2020-10-14 | 10:52 | 49.897
2020-10-14 | 10:52 | 49.894
2020-10-14 | 10:52 | 49.895
2020-10-14 | 10:52 | 49.895
2020-10-14 | 10:52 | 49.892
2020-10-14 | 10:52 | 49.895
2020-10-14 | 10:52 | 49.894
2020-10-14 | 10:52 | 49.892
2020-10-14 | 10:52 | 49.89
2020-10-14 | 10:52 | 49.89
2020-10-14 | 10:52 | 49.888
2020-10-14 | 10:52 | 49.887
2020-10-14 | 10:52 | 49.884
2020-10-14 | 10:52 | 49.881
2020-10-14 | 10:52 | 49.88
2020-10-14 | 10:52 | 49.88
2020-10-14 | 10:52 | 49.882
2020-10-14 | 10:52 | 49.885
2020-10-14 | 10:52 | 49.887
2020-10-14 | 10:52 | 49.889
2020-10-14 | 10:52 | 49.888
2020-10-14 | 10:52 | 49.887
2020-10-14 | 10:52 | 49.887
2020-10-14 | 10:52 | 49.884
2020-10-14 | 10:52 | 49.887
2020-10-14 | 10:52 | 49.888
2020-10-14 | 10:52 | 49.891
2020-10-14 | 10:52 | 49.89
2020-10-14 | 10:52 | 49.887
2020-10-14 | 10:52 | 49.888
2020-10-14 | 10:52 | 49.885
2020-10-14 | 10:52 | 49.884
2020-10-14 | 10:52 | 49.883
2020-10-14 | 10:52 | 49.879
2020-10-14 | 10:52 | 49.878
2020-10-14 | 10:52 | 49.872
2020-10-14 | 10:52 | 49.87
2020-10-14 | 10:52 | 49.87
2020-10-14 | 10:52 | 49.87
2020-10-14 | 10:52 | 49.868
2020-10-14 | 10:52 | 49.87
2020-10-14 | 10:53 | 49.867
2020-10-14 | 10:53 | 49.869
2020-10-14 | 10:53 | 49.867
2020-10-14 | 10:53 | 49.866
2020-10-14 | 10:53 | 49.872
2020-10-14 | 10:53 | 49.871
2020-10-14 | 10:53 | 49.872
2020-10-14 | 10:53 | 49.873
2020-10-14 | 10:53 | 49.873
2020-10-14 | 10:53 | 49.874
2020-10-14 | 10:53 | 49.874
2020-10-14 | 10:53 | 49.873
2020-10-14 | 10:53 | 49.872
2020-10-14 | 10:53 | 49.87
2020-10-14 | 10:53 | 49.868
2020-10-14 | 10:53 | 49.864
2020-10-14 | 10:53 | 49.864
2020-10-14 | 10:53 | 49.863
2020-10-14 | 10:53 | 49.863
2020-10-14 | 10:53 | 49.863
2020-10-14 | 10:53 | 49.865
2020-10-14 | 10:53 | 49.87
2020-10-14 | 10:53 | 49.871
2020-10-14 | 10:53 | 49.872
2020-10-14 | 10:53 | 49.871
2020-10-14 | 10:53 | 49.869
2020-10-14 | 10:53 | 49.87
2020-10-14 | 10:53 | 49.867
2020-10-14 | 10:53 | 49.866
2020-10-14 | 10:53 | 49.866
2020-10-14 | 10:53 | 49.863
2020-10-14 | 10:53 | 49.861
2020-10-14 | 10:53 | 49.861
2020-10-14 | 10:53 | 49.86
2020-10-14 | 10:53 | 49.859
2020-10-14 | 10:53 | 49.859
2020-10-14 | 10:53 | 49.857
2020-10-14 | 10:53 | 49.856
2020-10-14 | 10:53 | 49.853
2020-10-14 | 10:53 | 49.853
2020-10-14 | 10:53 | 49.855
2020-10-14 | 10:53 | 49.853
2020-10-14 | 10:53 | 49.855
2020-10-14 | 10:53 | 49.858
2020-10-14 | 10:53 | 49.857
2020-10-14 | 10:53 | 49.859
2020-10-14 | 10:53 | 49.862
2020-10-14 | 10:53 | 49.863
2020-10-14 | 10:53 | 49.867
2020-10-14 | 10:53 | 49.87
2020-10-14 | 10:53 | 49.873
2020-10-14 | 10:53 | 49.876
2020-10-14 | 10:53 | 49.875
2020-10-14 | 10:53 | 49.875
2020-10-14 | 10:53 | 49.877
2020-10-14 | 10:53 | 49.878
2020-10-14 | 10:53 | 49.88
2020-10-14 | 10:53 | 49.88
2020-10-14 | 10:53 | 49.881
2020-10-14 | 10:54 | 49.88
2020-10-14 | 10:54 | 49.881
2020-10-14 | 10:54 | 49.881
2020-10-14 | 10:54 | 49.88
2020-10-14 | 10:54 | 49.882
2020-10-14 | 10:54 | 49.882
2020-10-14 | 10:54 | 49.884
2020-10-14 | 10:54 | 49.886
2020-10-14 | 10:54 | 49.887
2020-10-14 | 10:54 | 49.889
2020-10-14 | 10:54 | 49.886
2020-10-14 | 10:54 | 49.887
2020-10-14 | 10:54 | 49.889
2020-10-14 | 10:54 | 49.889
2020-10-14 | 10:54 | 49.893
2020-10-14 | 10:54 | 49.895
2020-10-14 | 10:54 | 49.898
2020-10-14 | 10:54 | 49.898
2020-10-14 | 10:54 | 49.901
2020-10-14 | 10:54 | 49.901
2020-10-14 | 10:54 | 49.904
2020-10-14 | 10:54 | 49.905
2020-10-14 | 10:54 | 49.907
2020-10-14 | 10:54 | 49.906
2020-10-14 | 10:54 | 49.91
2020-10-14 | 10:54 | 49.912
2020-10-14 | 10:54 | 49.913
2020-10-14 | 10:54 | 49.912
2020-10-14 | 10:54 | 49.91
2020-10-14 | 10:54 | 49.907
2020-10-14 | 10:54 | 49.903
2020-10-14 | 10:54 | 49.898
2020-10-14 | 10:54 | 49.899
2020-10-14 | 10:54 | 49.897
2020-10-14 | 10:54 | 49.895
2020-10-14 | 10:54 | 49.891
2020-10-14 | 10:54 | 49.891
2020-10-14 | 10:54 | 49.887
2020-10-14 | 10:54 | 49.885
2020-10-14 | 10:54 | 49.882
2020-10-14 | 10:54 | 49.88
2020-10-14 | 10:54 | 49.875
2020-10-14 | 10:54 | 49.871
2020-10-14 | 10:54 | 49.869
2020-10-14 | 10:54 | 49.866
2020-10-14 | 10:54 | 49.867
2020-10-14 | 10:54 | 49.862
2020-10-14 | 10:54 | 49.862
2020-10-14 | 10:54 | 49.86
2020-10-14 | 10:54 | 49.861
2020-10-14 | 10:54 | 49.863
2020-10-14 | 10:54 | 49.861
2020-10-14 | 10:54 | 49.861
2020-10-14 | 10:54 | 49.861
2020-10-14 | 10:54 | 49.858
2020-10-14 | 10:54 | 49.86
2020-10-14 | 10:54 | 49.864
2020-10-14 | 10:54 | 49.864
2020-10-14 | 10:54 | 49.868
2020-10-14 | 10:54 | 49.874
2020-10-14 | 10:54 | 49.878
2020-10-14 | 10:55 | 49.882
2020-10-14 | 10:55 | 49.886
2020-10-14 | 10:55 | 49.89
2020-10-14 | 10:55 | 49.892
2020-10-14 | 10:55 | 49.894
2020-10-14 | 10:55 | 49.897
2020-10-14 | 10:55 | 49.898
2020-10-14 | 10:55 | 49.901
2020-10-14 | 10:55 | 49.906
2020-10-14 | 10:55 | 49.907
2020-10-14 | 10:55 | 49.911
2020-10-14 | 10:55 | 49.912
2020-10-14 | 10:55 | 49.913
2020-10-14 | 10:55 | 49.915
2020-10-14 | 10:55 | 49.917
2020-10-14 | 10:55 | 49.919
2020-10-14 | 10:55 | 49.921
2020-10-14 | 10:55 | 49.923
2020-10-14 | 10:55 | 49.923
2020-10-14 | 10:55 | 49.922
2020-10-14 | 10:55 | 49.92
2020-10-14 | 10:55 | 49.919
2020-10-14 | 10:55 | 49.915
2020-10-14 | 10:55 | 49.913
2020-10-14 | 10:55 | 49.91
2020-10-14 | 10:55 | 49.908
2020-10-14 | 10:55 | 49.905
2020-10-14 | 10:55 | 49.903
2020-10-14 | 10:55 | 49.901
2020-10-14 | 10:55 | 49.9
2020-10-14 | 10:55 | 49.899
2020-10-14 | 10:55 | 49.897
2020-10-14 | 10:55 | 49.895
2020-10-14 | 10:55 | 49.894
2020-10-14 | 10:55 | 49.893
2020-10-14 | 10:55 | 49.892
2020-10-14 | 10:55 | 49.89
2020-10-14 | 10:55 | 49.888
2020-10-14 | 10:55 | 49.886
2020-10-14 | 10:55 | 49.883
2020-10-14 | 10:55 | 49.882
2020-10-14 | 10:55 | 49.88
2020-10-14 | 10:55 | 49.88
2020-10-14 | 10:55 | 49.878
2020-10-14 | 10:55 | 49.877
2020-10-14 | 10:55 | 49.874
2020-10-14 | 10:55 | 49.874
2020-10-14 | 10:55 | 49.874
2020-10-14 | 10:55 | 49.872
2020-10-14 | 10:55 | 49.871
2020-10-14 | 10:55 | 49.872
2020-10-14 | 10:55 | 49.87
2020-10-14 | 10:55 | 49.867
2020-10-14 | 10:55 | 49.866
2020-10-14 | 10:55 | 49.865
2020-10-14 | 10:55 | 49.863
2020-10-14 | 10:55 | 49.861
2020-10-14 | 10:55 | 49.862
2020-10-14 | 10:55 | 49.86
2020-10-14 | 10:56 | 49.86
2020-10-14 | 10:56 | 49.861
2020-10-14 | 10:56 | 49.862
2020-10-14 | 10:56 | 49.863
2020-10-14 | 10:56 | 49.866
2020-10-14 | 10:56 | 49.867
2020-10-14 | 10:56 | 49.868
2020-10-14 | 10:56 | 49.867
2020-10-14 | 10:56 | 49.868
2020-10-14 | 10:56 | 49.868
2020-10-14 | 10:56 | 49.867
2020-10-14 | 10:56 | 49.865
2020-10-14 | 10:56 | 49.865
2020-10-14 | 10:56 | 49.864
2020-10-14 | 10:56 | 49.863
2020-10-14 | 10:56 | 49.861
2020-10-14 | 10:56 | 49.857
2020-10-14 | 10:56 | 49.854
2020-10-14 | 10:56 | 49.852
2020-10-14 | 10:56 | 49.849
2020-10-14 | 10:56 | 49.848
2020-10-14 | 10:56 | 49.845
2020-10-14 | 10:56 | 49.846
2020-10-14 | 10:56 | 49.845
2020-10-14 | 10:56 | 49.844
2020-10-14 | 10:56 | 49.844
2020-10-14 | 10:56 | 49.841
2020-10-14 | 10:56 | 49.84
2020-10-14 | 10:56 | 49.836
2020-10-14 | 10:56 | 49.833
2020-10-14 | 10:56 | 49.829
2020-10-14 | 10:56 | 49.824
2020-10-14 | 10:56 | 49.819
2020-10-14 | 10:56 | 49.813
2020-10-14 | 10:56 | 49.807
2020-10-14 | 10:56 | 49.803
2020-10-14 | 10:56 | 49.798
2020-10-14 | 10:56 | 49.797
2020-10-14 | 10:56 | 49.796
2020-10-14 | 10:56 | 49.797
2020-10-14 | 10:56 | 49.797
2020-10-14 | 10:56 | 49.802
2020-10-14 | 10:56 | 49.803
2020-10-14 | 10:56 | 49.805
2020-10-14 | 10:56 | 49.806
2020-10-14 | 10:56 | 49.808
2020-10-14 | 10:56 | 49.812
2020-10-14 | 10:56 | 49.815
2020-10-14 | 10:56 | 49.818
2020-10-14 | 10:56 | 49.819
2020-10-14 | 10:56 | 49.822
2020-10-14 | 10:56 | 49.824
2020-10-14 | 10:56 | 49.824
2020-10-14 | 10:56 | 49.827
2020-10-14 | 10:56 | 49.829
2020-10-14 | 10:56 | 49.832
2020-10-14 | 10:56 | 49.833
2020-10-14 | 10:56 | 49.832
2020-10-14 | 10:56 | 49.832
2020-10-14 | 10:56 | 49.832
2020-10-14 | 10:56 | 49.831
2020-10-14 | 10:57 | 49.829
2020-10-14 | 10:57 | 49.827
2020-10-14 | 10:57 | 49.828
2020-10-14 | 10:57 | 49.829
2020-10-14 | 10:57 | 49.828
2020-10-14 | 10:57 | 49.83
2020-10-14 | 10:57 | 49.832
2020-10-14 | 10:57 | 49.833
2020-10-14 | 10:57 | 49.835
2020-10-14 | 10:57 | 49.837
2020-10-14 | 10:57 | 49.838
2020-10-14 | 10:57 | 49.841
2020-10-14 | 10:57 | 49.842
2020-10-14 | 10:57 | 49.841
2020-10-14 | 10:57 | 49.841
2020-10-14 | 10:57 | 49.84
2020-10-14 | 10:57 | 49.84
2020-10-14 | 10:57 | 49.839
2020-10-14 | 10:57 | 49.84
2020-10-14 | 10:57 | 49.84
2020-10-14 | 10:57 | 49.839
2020-10-14 | 10:57 | 49.839
2020-10-14 | 10:57 | 49.837
2020-10-14 | 10:57 | 49.835
2020-10-14 | 10:57 | 49.835
2020-10-14 | 10:57 | 49.834
2020-10-14 | 10:57 | 49.832
2020-10-14 | 10:57 | 49.83
2020-10-14 | 10:57 | 49.827
2020-10-14 | 10:57 | 49.825
2020-10-14 | 10:57 | 49.821
2020-10-14 | 10:57 | 49.817
2020-10-14 | 10:57 | 49.814
2020-10-14 | 10:57 | 49.813
2020-10-14 | 10:57 | 49.813
2020-10-14 | 10:57 | 49.81
2020-10-14 | 10:57 | 49.808
2020-10-14 | 10:57 | 49.805
2020-10-14 | 10:57 | 49.804
2020-10-14 | 10:57 | 49.802
2020-10-14 | 10:57 | 49.801
2020-10-14 | 10:57 | 49.801
2020-10-14 | 10:57 | 49.8
2020-10-14 | 10:57 | 49.8
2020-10-14 | 10:57 | 49.798
2020-10-14 | 10:57 | 49.797
2020-10-14 | 10:57 | 49.796
2020-10-14 | 10:57 | 49.797
2020-10-14 | 10:57 | 49.796
2020-10-14 | 10:57 | 49.796
2020-10-14 | 10:57 | 49.798
2020-10-14 | 10:57 | 49.801
2020-10-14 | 10:57 | 49.802
2020-10-14 | 10:57 | 49.804
2020-10-14 | 10:57 | 49.805
2020-10-14 | 10:57 | 49.807
2020-10-14 | 10:57 | 49.808
2020-10-14 | 10:57 | 49.808
2020-10-14 | 10:57 | 49.809
2020-10-14 | 10:58 | 49.809
2020-10-14 | 10:58 | 49.812
2020-10-14 | 10:58 | 49.812
2020-10-14 | 10:58 | 49.814
2020-10-14 | 10:58 | 49.814
2020-10-14 | 10:58 | 49.816
2020-10-14 | 10:58 | 49.816
2020-10-14 | 10:58 | 49.815
2020-10-14 | 10:58 | 49.815
2020-10-14 | 10:58 | 49.819
2020-10-14 | 10:58 | 49.821
2020-10-14 | 10:58 | 49.824
2020-10-14 | 10:58 | 49.828
2020-10-14 | 10:58 | 49.832
2020-10-14 | 10:58 | 49.835
2020-10-14 | 10:58 | 49.836
2020-10-14 | 10:58 | 49.838
2020-10-14 | 10:58 | 49.839
2020-10-14 | 10:58 | 49.841
2020-10-14 | 10:58 | 49.842
2020-10-14 | 10:58 | 49.844
2020-10-14 | 10:58 | 49.844
2020-10-14 | 10:58 | 49.842
2020-10-14 | 10:58 | 49.841
2020-10-14 | 10:58 | 49.84
2020-10-14 | 10:58 | 49.838
2020-10-14 | 10:58 | 49.837
2020-10-14 | 10:58 | 49.837
2020-10-14 | 10:58 | 49.837
2020-10-14 | 10:58 | 49.839
2020-10-14 | 10:58 | 49.84
2020-10-14 | 10:58 | 49.843
2020-10-14 | 10:58 | 49.845
2020-10-14 | 10:58 | 49.847
2020-10-14 | 10:58 | 49.849
2020-10-14 | 10:58 | 49.851
2020-10-14 | 10:58 | 49.855
2020-10-14 | 10:58 | 49.855
2020-10-14 | 10:58 | 49.857
2020-10-14 | 10:58 | 49.858
2020-10-14 | 10:58 | 49.86
2020-10-14 | 10:58 | 49.861
2020-10-14 | 10:58 | 49.862
2020-10-14 | 10:58 | 49.86
2020-10-14 | 10:58 | 49.86
2020-10-14 | 10:58 | 49.859
2020-10-14 | 10:58 | 49.86
2020-10-14 | 10:58 | 49.858
2020-10-14 | 10:58 | 49.857
2020-10-14 | 10:58 | 49.854
2020-10-14 | 10:58 | 49.854
2020-10-14 | 10:58 | 49.854
2020-10-14 | 10:58 | 49.853
2020-10-14 | 10:58 | 49.852
2020-10-14 | 10:58 | 49.85
2020-10-14 | 10:58 | 49.85
2020-10-14 | 10:58 | 49.852
2020-10-14 | 10:58 | 49.856
2020-10-14 | 10:58 | 49.859
2020-10-14 | 10:58 | 49.864
2020-10-14 | 10:58 | 49.869
2020-10-14 | 10:59 | 49.873
2020-10-14 | 10:59 | 49.876
2020-10-14 | 10:59 | 49.878
2020-10-14 | 10:59 | 49.881
2020-10-14 | 10:59 | 49.884
2020-10-14 | 10:59 | 49.885
2020-10-14 | 10:59 | 49.886
2020-10-14 | 10:59 | 49.886
2020-10-14 | 10:59 | 49.886
2020-10-14 | 10:59 | 49.886
2020-10-14 | 10:59 | 49.887
2020-10-14 | 10:59 | 49.889
2020-10-14 | 10:59 | 49.89
2020-10-14 | 10:59 | 49.891
2020-10-14 | 10:59 | 49.892
2020-10-14 | 10:59 | 49.894
2020-10-14 | 10:59 | 49.895
2020-10-14 | 10:59 | 49.898
2020-10-14 | 10:59 | 49.901
2020-10-14 | 10:59 | 49.904
2020-10-14 | 10:59 | 49.906
2020-10-14 | 10:59 | 49.906
2020-10-14 | 10:59 | 49.907
2020-10-14 | 10:59 | 49.905
2020-10-14 | 10:59 | 49.903
2020-10-14 | 10:59 | 49.9
2020-10-14 | 10:59 | 49.899
2020-10-14 | 10:59 | 49.898
2020-10-14 | 10:59 | 49.897
2020-10-14 | 10:59 | 49.896
2020-10-14 | 10:59 | 49.894
2020-10-14 | 10:59 | 49.892
2020-10-14 | 10:59 | 49.889
2020-10-14 | 10:59 | 49.89
2020-10-14 | 10:59 | 49.888
2020-10-14 | 10:59 | 49.886
2020-10-14 | 10:59 | 49.885
2020-10-14 | 10:59 | 49.884
2020-10-14 | 10:59 | 49.884
2020-10-14 | 10:59 | 49.883
2020-10-14 | 10:59 | 49.883
2020-10-14 | 10:59 | 49.884
2020-10-14 | 10:59 | 49.885
2020-10-14 | 10:59 | 49.887
2020-10-14 | 10:59 | 49.891
2020-10-14 | 10:59 | 49.895
2020-10-14 | 10:59 | 49.898
2020-10-14 | 10:59 | 49.9
2020-10-14 | 10:59 | 49.899
2020-10-14 | 10:59 | 49.899
2020-10-14 | 10:59 | 49.898
2020-10-14 | 10:59 | 49.9
2020-10-14 | 10:59 | 49.907
2020-10-14 | 10:59 | 49.904
2020-10-14 | 10:59 | 49.906
2020-10-14 | 10:59 | 49.908
2020-10-14 | 10:59 | 49.908
2020-10-14 | 10:59 | 49.907
2020-10-14 | 10:59 | 49.905
2020-10-14 | 11:00 | 49.902
2020-10-14 | 11:00 | 49.899
2020-10-14 | 11:00 | 49.895
2020-10-14 | 11:00 | 49.893
2020-10-14 | 11:00 | 49.893
2020-10-14 | 11:00 | 49.892
2020-10-14 | 11:00 | 49.893
2020-10-14 | 11:00 | 49.896
2020-10-14 | 11:00 | 49.898
2020-10-14 | 11:00 | 49.901
2020-10-14 | 11:00 | 49.904
2020-10-14 | 11:00 | 49.905
2020-10-14 | 11:00 | 49.905
2020-10-14 | 11:00 | 49.906
2020-10-14 | 11:00 | 49.909
2020-10-14 | 11:00 | 49.909
2020-10-14 | 11:00 | 49.911
2020-10-14 | 11:00 | 49.91
2020-10-14 | 11:00 | 49.91
2020-10-14 | 11:00 | 49.911
2020-10-14 | 11:00 | 49.911
2020-10-14 | 11:00 | 49.913
2020-10-14 | 11:00 | 49.914
2020-10-14 | 11:00 | 49.918
2020-10-14 | 11:00 | 49.922
2020-10-14 | 11:00 | 49.925
2020-10-14 | 11:00 | 49.927
2020-10-14 | 11:00 | 49.93
2020-10-14 | 11:00 | 49.931
2020-10-14 | 11:00 | 49.931
2020-10-14 | 11:00 | 49.93
2020-10-14 | 11:00 | 49.927
2020-10-14 | 11:00 | 49.923
2020-10-14 | 11:00 | 49.919
2020-10-14 | 11:00 | 49.917
2020-10-14 | 11:00 | 49.915
2020-10-14 | 11:00 | 49.913
2020-10-14 | 11:00 | 49.913
2020-10-14 | 11:00 | 49.914
2020-10-14 | 11:00 | 49.914
2020-10-14 | 11:00 | 49.913
2020-10-14 | 11:00 | 49.914
2020-10-14 | 11:00 | 49.914
2020-10-14 | 11:00 | 49.911
2020-10-14 | 11:00 | 49.909
2020-10-14 | 11:00 | 49.906
2020-10-14 | 11:00 | 49.905
2020-10-14 | 11:00 | 49.905
2020-10-14 | 11:00 | 49.908
2020-10-14 | 11:00 | 49.91
2020-10-14 | 11:00 | 49.914
2020-10-14 | 11:00 | 49.917
2020-10-14 | 11:00 | 49.92
2020-10-14 | 11:00 | 49.925
2020-10-14 | 11:00 | 49.929
2020-10-14 | 11:00 | 49.934
2020-10-14 | 11:00 | 49.94
2020-10-14 | 11:00 | 49.943
2020-10-14 | 11:00 | 49.946
2020-10-14 | 11:00 | 49.948
2020-10-14 | 11:00 | 49.95
2020-10-14 | 11:01 | 49.956
2020-10-14 | 11:01 | 49.96
2020-10-14 | 11:01 | 49.961
2020-10-14 | 11:01 | 49.963
2020-10-14 | 11:01 | 49.967
2020-10-14 | 11:01 | 49.971
2020-10-14 | 11:01 | 49.974
2020-10-14 | 11:01 | 49.975
2020-10-14 | 11:01 | 49.977
2020-10-14 | 11:01 | 49.978
2020-10-14 | 11:01 | 49.979
2020-10-14 | 11:01 | 49.98
2020-10-14 | 11:01 | 49.982
2020-10-14 | 11:01 | 49.982
2020-10-14 | 11:01 | 49.983
2020-10-14 | 11:01 | 49.983
2020-10-14 | 11:01 | 49.983
2020-10-14 | 11:01 | 49.986
2020-10-14 | 11:01 | 49.988
2020-10-14 | 11:01 | 49.991
2020-10-14 | 11:01 | 49.993
2020-10-14 | 11:01 | 49.992
2020-10-14 | 11:01 | 49.993
2020-10-14 | 11:01 | 49.993
2020-10-14 | 11:01 | 49.993
2020-10-14 | 11:01 | 49.991
2020-10-14 | 11:01 | 49.99
2020-10-14 | 11:01 | 49.989
2020-10-14 | 11:01 | 49.988
2020-10-14 | 11:01 | 49.988
2020-10-14 | 11:01 | 49.989
2020-10-14 | 11:01 | 49.989
2020-10-14 | 11:01 | 49.993
2020-10-14 | 11:01 | 49.998
2020-10-14 | 11:01 | 50.004
2020-10-14 | 11:01 | 50.008
2020-10-14 | 11:01 | 50.01
2020-10-14 | 11:01 | 50.013
2020-10-14 | 11:01 | 50.016
2020-10-14 | 11:01 | 50.019
2020-10-14 | 11:01 | 50.022
2020-10-14 | 11:01 | 50.025
2020-10-14 | 11:01 | 50.026
2020-10-14 | 11:01 | 50.025
2020-10-14 | 11:01 | 50.028
2020-10-14 | 11:01 | 50.029
2020-10-14 | 11:01 | 50.03
2020-10-14 | 11:01 | 50.032
2020-10-14 | 11:01 | 50.035
2020-10-14 | 11:01 | 50.04
2020-10-14 | 11:01 | 50.043
2020-10-14 | 11:01 | 50.045
2020-10-14 | 11:01 | 50.044
2020-10-14 | 11:01 | 50.044
2020-10-14 | 11:01 | 50.045
2020-10-14 | 11:01 | 50.047
2020-10-14 | 11:01 | 50.048
2020-10-14 | 11:01 | 50.05
2020-10-14 | 11:01 | 50.051
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.053
2020-10-14 | 11:02 | 50.054
2020-10-14 | 11:02 | 50.054
2020-10-14 | 11:02 | 50.053
2020-10-14 | 11:02 | 50.056
2020-10-14 | 11:02 | 50.054
2020-10-14 | 11:02 | 50.053
2020-10-14 | 11:02 | 50.052
2020-10-14 | 11:02 | 50.053
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.05
2020-10-14 | 11:02 | 50.05
2020-10-14 | 11:02 | 50.049
2020-10-14 | 11:02 | 50.049
2020-10-14 | 11:02 | 50.049
2020-10-14 | 11:02 | 50.049
2020-10-14 | 11:02 | 50.049
2020-10-14 | 11:02 | 50.05
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.051
2020-10-14 | 11:02 | 50.053
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.058
2020-10-14 | 11:02 | 50.06
2020-10-14 | 11:02 | 50.062
2020-10-14 | 11:02 | 50.062
2020-10-14 | 11:02 | 50.062
2020-10-14 | 11:02 | 50.063
2020-10-14 | 11:02 | 50.063
2020-10-14 | 11:02 | 50.062
2020-10-14 | 11:02 | 50.059
2020-10-14 | 11:02 | 50.057
2020-10-14 | 11:02 | 50.056
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.054
2020-10-14 | 11:02 | 50.054
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.056
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.055
2020-10-14 | 11:02 | 50.057
2020-10-14 | 11:02 | 50.057
2020-10-14 | 11:02 | 50.057
2020-10-14 | 11:02 | 50.058
2020-10-14 | 11:02 | 50.06
2020-10-14 | 11:02 | 50.063
2020-10-14 | 11:02 | 50.065
2020-10-14 | 11:02 | 50.066
2020-10-14 | 11:02 | 50.066
2020-10-14 | 11:02 | 50.068
2020-10-14 | 11:02 | 50.07
2020-10-14 | 11:02 | 50.071
2020-10-14 | 11:02 | 50.072
2020-10-14 | 11:02 | 50.071
2020-10-14 | 11:02 | 50.07
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.069
2020-10-14 | 11:03 | 50.069
2020-10-14 | 11:03 | 50.069
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.068
2020-10-14 | 11:03 | 50.065
2020-10-14 | 11:03 | 50.066
2020-10-14 | 11:03 | 50.065
2020-10-14 | 11:03 | 50.066
2020-10-14 | 11:03 | 50.066
2020-10-14 | 11:03 | 50.066
2020-10-14 | 11:03 | 50.065
2020-10-14 | 11:03 | 50.066
2020-10-14 | 11:03 | 50.068
2020-10-14 | 11:03 | 50.069
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.071
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.07
2020-10-14 | 11:03 | 50.072
2020-10-14 | 11:03 | 50.074
2020-10-14 | 11:03 | 50.076
2020-10-14 | 11:03 | 50.079
2020-10-14 | 11:03 | 50.078
2020-10-14 | 11:03 | 50.076
2020-10-14 | 11:03 | 50.072
2020-10-14 | 11:03 | 50.067
2020-10-14 | 11:03 | 50.062
2020-10-14 | 11:03 | 50.054
2020-10-14 | 11:03 | 50.045
2020-10-14 | 11:03 | 50.038
2020-10-14 | 11:03 | 50.03
2020-10-14 | 11:03 | 50.021
2020-10-14 | 11:03 | 50.012
2020-10-14 | 11:03 | 50.005
2020-10-14 | 11:03 | 49.995
2020-10-14 | 11:03 | 49.985
2020-10-14 | 11:03 | 49.971
2020-10-14 | 11:03 | 49.959
2020-10-14 | 11:03 | 49.951
2020-10-14 | 11:03 | 49.942
2020-10-14 | 11:03 | 49.938
2020-10-14 | 11:03 | 49.934
2020-10-14 | 11:03 | 49.932
2020-10-14 | 11:03 | 49.93
2020-10-14 | 11:03 | 49.93
2020-10-14 | 11:03 | 49.93
2020-10-14 | 11:03 | 49.931
2020-10-14 | 11:03 | 49.932
2020-10-14 | 11:03 | 49.933
2020-10-14 | 11:03 | 49.934
2020-10-14 | 11:03 | 49.934
2020-10-14 | 11:03 | 49.935
2020-10-14 | 11:03 | 49.935
2020-10-14 | 11:03 | 49.934
2020-10-14 | 11:03 | 49.933
2020-10-14 | 11:04 | 49.933
2020-10-14 | 11:04 | 49.931
2020-10-14 | 11:04 | 49.93
2020-10-14 | 11:04 | 49.928
2020-10-14 | 11:04 | 49.926
2020-10-14 | 11:04 | 49.927
2020-10-14 | 11:04 | 49.927
2020-10-14 | 11:04 | 49.927
2020-10-14 | 11:04 | 49.929
2020-10-14 | 11:04 | 49.929
2020-10-14 | 11:04 | 49.928
2020-10-14 | 11:04 | 49.928
2020-10-14 | 11:04 | 49.927
2020-10-14 | 11:04 | 49.926
2020-10-14 | 11:04 | 49.924
2020-10-14 | 11:04 | 49.922
2020-10-14 | 11:04 | 49.92
2020-10-14 | 11:04 | 49.918
2020-10-14 | 11:04 | 49.915
2020-10-14 | 11:04 | 49.915
2020-10-14 | 11:04 | 49.913
2020-10-14 | 11:04 | 49.913
2020-10-14 | 11:04 | 49.911
2020-10-14 | 11:04 | 49.909
2020-10-14 | 11:04 | 49.908
2020-10-14 | 11:04 | 49.908
2020-10-14 | 11:04 | 49.909
2020-10-14 | 11:04 | 49.908
2020-10-14 | 11:04 | 49.908
2020-10-14 | 11:04 | 49.906
2020-10-14 | 11:04 | 49.904
2020-10-14 | 11:04 | 49.9
2020-10-14 | 11:04 | 49.9
2020-10-14 | 11:04 | 49.897
2020-10-14 | 11:04 | 49.897
2020-10-14 | 11:04 | 49.895
2020-10-14 | 11:04 | 49.893
2020-10-14 | 11:04 | 49.89
2020-10-14 | 11:04 | 49.887
2020-10-14 | 11:04 | 49.883
2020-10-14 | 11:04 | 49.883
2020-10-14 | 11:04 | 49.883
2020-10-14 | 11:04 | 49.88
2020-10-14 | 11:04 | 49.892
2020-10-14 | 11:04 | 49.877
2020-10-14 | 11:04 | 49.876
2020-10-14 | 11:04 | 49.873
2020-10-14 | 11:04 | 49.872
2020-10-14 | 11:04 | 49.873
2020-10-14 | 11:04 | 49.872
2020-10-14 | 11:04 | 49.871
2020-10-14 | 11:04 | 49.872
2020-10-14 | 11:04 | 49.872
2020-10-14 | 11:04 | 49.872
2020-10-14 | 11:04 | 49.873
2020-10-14 | 11:04 | 49.874
2020-10-14 | 11:04 | 49.875
2020-10-14 | 11:04 | 49.879
2020-10-14 | 11:04 | 49.882
2020-10-14 | 11:04 | 49.883
2020-10-14 | 11:04 | 49.884
2020-10-14 | 11:05 | 49.883
2020-10-14 | 11:05 | 49.882
2020-10-14 | 11:05 | 49.883
2020-10-14 | 11:05 | 49.883
2020-10-14 | 11:05 | 49.883
2020-10-14 | 11:05 | 49.882
2020-10-14 | 11:05 | 49.882
2020-10-14 | 11:05 | 49.884
2020-10-14 | 11:05 | 49.883
2020-10-14 | 11:05 | 49.884
2020-10-14 | 11:05 | 49.884
2020-10-14 | 11:05 | 49.886
2020-10-14 | 11:05 | 49.886
2020-10-14 | 11:05 | 49.885
2020-10-14 | 11:05 | 49.886
2020-10-14 | 11:05 | 49.886
2020-10-14 | 11:05 | 49.888
2020-10-14 | 11:05 | 49.892
2020-10-14 | 11:05 | 49.897
2020-10-14 | 11:05 | 49.902
2020-10-14 | 11:05 | 49.906
2020-10-14 | 11:05 | 49.91
2020-10-14 | 11:05 | 49.911
2020-10-14 | 11:05 | 49.914
2020-10-14 | 11:05 | 49.916
2020-10-14 | 11:05 | 49.918
2020-10-14 | 11:05 | 49.92
2020-10-14 | 11:05 | 49.921
2020-10-14 | 11:05 | 49.921
2020-10-14 | 11:05 | 49.922
2020-10-14 | 11:05 | 49.924
2020-10-14 | 11:05 | 49.924
2020-10-14 | 11:05 | 49.925
2020-10-14 | 11:05 | 49.924
2020-10-14 | 11:05 | 49.924
2020-10-14 | 11:05 | 49.924
2020-10-14 | 11:05 | 49.924
2020-10-14 | 11:05 | 49.925
2020-10-14 | 11:05 | 49.926
2020-10-14 | 11:05 | 49.927
2020-10-14 | 11:05 | 49.928
2020-10-14 | 11:05 | 49.929
2020-10-14 | 11:05 | 49.931
2020-10-14 | 11:05 | 49.934
2020-10-14 | 11:05 | 49.936
2020-10-14 | 11:05 | 49.937
2020-10-14 | 11:05 | 49.94
2020-10-14 | 11:05 | 49.943
2020-10-14 | 11:05 | 49.943
2020-10-14 | 11:05 | 49.946
2020-10-14 | 11:05 | 49.949
2020-10-14 | 11:05 | 49.951
2020-10-14 | 11:05 | 49.952
2020-10-14 | 11:05 | 49.952
2020-10-14 | 11:05 | 49.953
2020-10-14 | 11:05 | 49.955
2020-10-14 | 11:05 | 49.956
2020-10-14 | 11:05 | 49.958
2020-10-14 | 11:05 | 49.959
2020-10-14 | 11:06 | 49.961
2020-10-14 | 11:06 | 49.961
2020-10-14 | 11:06 | 49.962
2020-10-14 | 11:06 | 49.964
2020-10-14 | 11:06 | 49.966
2020-10-14 | 11:06 | 49.968
2020-10-14 | 11:06 | 49.972
2020-10-14 | 11:06 | 49.976
2020-10-14 | 11:06 | 49.981
2020-10-14 | 11:06 | 49.984
2020-10-14 | 11:06 | 49.986
2020-10-14 | 11:06 | 49.987
2020-10-14 | 11:06 | 49.987
2020-10-14 | 11:06 | 49.988
2020-10-14 | 11:06 | 49.99
2020-10-14 | 11:06 | 49.993
2020-10-14 | 11:06 | 49.992
2020-10-14 | 11:06 | 49.995
2020-10-14 | 11:06 | 49.994
2020-10-14 | 11:06 | 49.996
2020-10-14 | 11:06 | 49.996
2020-10-14 | 11:06 | 49.996
2020-10-14 | 11:06 | 49.997
2020-10-14 | 11:06 | 49.996
2020-10-14 | 11:06 | 49.998
2020-10-14 | 11:06 | 49.999
2020-10-14 | 11:06 | 50.001
2020-10-14 | 11:06 | 50.002
2020-10-14 | 11:06 | 50.003
2020-10-14 | 11:06 | 50.001
2020-10-14 | 11:06 | 49.999
2020-10-14 | 11:06 | 49.996
2020-10-14 | 11:06 | 49.992
2020-10-14 | 11:06 | 49.988
2020-10-14 | 11:06 | 49.983
2020-10-14 | 11:06 | 49.981
2020-10-14 | 11:06 | 49.981
2020-10-14 | 11:06 | 49.981
2020-10-14 | 11:06 | 49.981
2020-10-14 | 11:06 | 49.981
2020-10-14 | 11:06 | 49.982
2020-10-14 | 11:06 | 49.984
2020-10-14 | 11:06 | 49.983
2020-10-14 | 11:06 | 49.985
2020-10-14 | 11:06 | 49.989
2020-10-14 | 11:06 | 49.993
2020-10-14 | 11:06 | 49.994
2020-10-14 | 11:06 | 49.996
2020-10-14 | 11:06 | 49.997
2020-10-14 | 11:06 | 49.999
2020-10-14 | 11:06 | 49.999
2020-10-14 | 11:06 | 49.999
2020-10-14 | 11:06 | 50
2020-10-14 | 11:06 | 50.001
2020-10-14 | 11:06 | 50
2020-10-14 | 11:06 | 50
2020-10-14 | 11:06 | 50.001
2020-10-14 | 11:06 | 50.001
2020-10-14 | 11:06 | 50.002
2020-10-14 | 11:06 | 50.002
2020-10-14 | 11:06 | 50.004
2020-10-14 | 11:07 | 50.005
2020-10-14 | 11:07 | 50.004
2020-10-14 | 11:07 | 50.004
2020-10-14 | 11:07 | 50.004
2020-10-14 | 11:07 | 50.002
2020-10-14 | 11:07 | 50
2020-10-14 | 11:07 | 49.997
2020-10-14 | 11:07 | 49.997
2020-10-14 | 11:07 | 49.996
2020-10-14 | 11:07 | 49.996
2020-10-14 | 11:07 | 49.993
2020-10-14 | 11:07 | 49.992
2020-10-14 | 11:07 | 49.991
2020-10-14 | 11:07 | 49.988
2020-10-14 | 11:07 | 49.984
2020-10-14 | 11:07 | 49.982
2020-10-14 | 11:07 | 49.98
2020-10-14 | 11:07 | 49.977
2020-10-14 | 11:07 | 49.976
2020-10-14 | 11:07 | 49.973
2020-10-14 | 11:07 | 49.974
2020-10-14 | 11:07 | 49.974
2020-10-14 | 11:07 | 49.977
2020-10-14 | 11:07 | 49.978
2020-10-14 | 11:07 | 49.979
2020-10-14 | 11:07 | 49.979
2020-10-14 | 11:07 | 49.981
2020-10-14 | 11:07 | 49.981
2020-10-14 | 11:07 | 49.983
2020-10-14 | 11:07 | 49.983
2020-10-14 | 11:07 | 49.983
2020-10-14 | 11:07 | 49.983
2020-10-14 | 11:07 | 49.982
2020-10-14 | 11:07 | 49.985
2020-10-14 | 11:07 | 49.985
2020-10-14 | 11:07 | 49.985
2020-10-14 | 11:07 | 49.986
2020-10-14 | 11:07 | 49.985
2020-10-14 | 11:07 | 49.984
2020-10-14 | 11:07 | 49.982
2020-10-14 | 11:07 | 49.981
2020-10-14 | 11:07 | 49.983
2020-10-14 | 11:07 | 49.984
2020-10-14 | 11:07 | 49.985
2020-10-14 | 11:07 | 49.986
2020-10-14 | 11:07 | 49.986
2020-10-14 | 11:07 | 49.989
2020-10-14 | 11:07 | 49.989
2020-10-14 | 11:07 | 49.988
2020-10-14 | 11:07 | 49.989
2020-10-14 | 11:07 | 49.99
2020-10-14 | 11:07 | 49.99
2020-10-14 | 11:07 | 49.99
2020-10-14 | 11:07 | 49.991
2020-10-14 | 11:07 | 49.993
2020-10-14 | 11:07 | 49.995
2020-10-14 | 11:07 | 49.998
2020-10-14 | 11:07 | 50
2020-10-14 | 11:07 | 50.003
2020-10-14 | 11:08 | 50.005
2020-10-14 | 11:08 | 50.006
2020-10-14 | 11:08 | 50.008
2020-10-14 | 11:08 | 50.01
2020-10-14 | 11:08 | 50.013
2020-10-14 | 11:08 | 50.017
2020-10-14 | 11:08 | 50.019
2020-10-14 | 11:08 | 50.022
2020-10-14 | 11:08 | 50.023
2020-10-14 | 11:08 | 50.024
2020-10-14 | 11:08 | 50.027
2020-10-14 | 11:08 | 50.028
2020-10-14 | 11:08 | 50.028
2020-10-14 | 11:08 | 50.028
2020-10-14 | 11:08 | 50.027
2020-10-14 | 11:08 | 50.026
2020-10-14 | 11:08 | 50.024
2020-10-14 | 11:08 | 50.024
2020-10-14 | 11:08 | 50.021
2020-10-14 | 11:08 | 50.02
2020-10-14 | 11:08 | 50.016
2020-10-14 | 11:08 | 50.012
2020-10-14 | 11:08 | 50.008
2020-10-14 | 11:08 | 50.006
2020-10-14 | 11:08 | 50.001
2020-10-14 | 11:08 | 49.999
2020-10-14 | 11:08 | 49.997
2020-10-14 | 11:08 | 49.994
2020-10-14 | 11:08 | 49.991
2020-10-14 | 11:08 | 49.99
2020-10-14 | 11:08 | 49.987
2020-10-14 | 11:08 | 49.985
2020-10-14 | 11:08 | 49.985
2020-10-14 | 11:08 | 49.983
2020-10-14 | 11:08 | 49.985
2020-10-14 | 11:08 | 49.986
2020-10-14 | 11:08 | 49.988
2020-10-14 | 11:08 | 49.988
2020-10-14 | 11:08 | 49.988
2020-10-14 | 11:08 | 49.989
2020-10-14 | 11:08 | 49.989
2020-10-14 | 11:08 | 49.991
2020-10-14 | 11:08 | 49.992
2020-10-14 | 11:08 | 49.994
2020-10-14 | 11:08 | 49.996
2020-10-14 | 11:08 | 49.999
2020-10-14 | 11:08 | 50.002
2020-10-14 | 11:08 | 50.004
2020-10-14 | 11:08 | 50.005
2020-10-14 | 11:08 | 50.006
2020-10-14 | 11:08 | 50.009
2020-10-14 | 11:08 | 50.01
2020-10-14 | 11:08 | 50.013
2020-10-14 | 11:08 | 50.014
2020-10-14 | 11:08 | 50.017
2020-10-14 | 11:08 | 50.018
2020-10-14 | 11:08 | 50.019
2020-10-14 | 11:08 | 50.021
2020-10-14 | 11:08 | 50.021
2020-10-14 | 11:08 | 50.02
2020-10-14 | 11:08 | 50.023
2020-10-14 | 11:09 | 50.023
2020-10-14 | 11:09 | 50.024
2020-10-14 | 11:09 | 50.023
2020-10-14 | 11:09 | 50.022
2020-10-14 | 11:09 | 50.02
2020-10-14 | 11:09 | 50.02
2020-10-14 | 11:09 | 50.02
2020-10-14 | 11:09 | 50.017
2020-10-14 | 11:09 | 50.017
2020-10-14 | 11:09 | 50.015
2020-10-14 | 11:09 | 50.014
2020-10-14 | 11:09 | 50.014
2020-10-14 | 11:09 | 50.016
2020-10-14 | 11:09 | 50.015
2020-10-14 | 11:09 | 50.016
2020-10-14 | 11:09 | 50.016
2020-10-14 | 11:09 | 50.015
2020-10-14 | 11:09 | 50.014
2020-10-14 | 11:09 | 50.013
2020-10-14 | 11:09 | 50.01
2020-10-14 | 11:09 | 50.009
2020-10-14 | 11:09 | 50.007
2020-10-14 | 11:09 | 50.007
2020-10-14 | 11:09 | 50.006
2020-10-14 | 11:09 | 50.004
2020-10-14 | 11:09 | 50.003
2020-10-14 | 11:09 | 50.003
2020-10-14 | 11:09 | 50.001
2020-10-14 | 11:09 | 49.999
2020-10-14 | 11:09 | 49.996
2020-10-14 | 11:09 | 49.993
2020-10-14 | 11:09 | 49.99
2020-10-14 | 11:09 | 49.987
2020-10-14 | 11:09 | 49.983
2020-10-14 | 11:09 | 49.985
2020-10-14 | 11:09 | 49.986
2020-10-14 | 11:09 | 49.99
2020-10-14 | 11:09 | 49.994
2020-10-14 | 11:09 | 49.997
2020-10-14 | 11:09 | 50.001
2020-10-14 | 11:09 | 50.003
2020-10-14 | 11:09 | 50.007
2020-10-14 | 11:09 | 50.009
2020-10-14 | 11:09 | 50.01
2020-10-14 | 11:09 | 50.011
2020-10-14 | 11:09 | 50.013
2020-10-14 | 11:09 | 50.015
2020-10-14 | 11:09 | 50.017
2020-10-14 | 11:09 | 50.018
2020-10-14 | 11:09 | 50.018
2020-10-14 | 11:09 | 50.017
2020-10-14 | 11:09 | 50.016
2020-10-14 | 11:09 | 50.015
2020-10-14 | 11:09 | 50.013
2020-10-14 | 11:09 | 50.011
2020-10-14 | 11:09 | 50.012
2020-10-14 | 11:09 | 50.012
2020-10-14 | 11:09 | 50.012
2020-10-14 | 11:09 | 50.012
2020-10-14 | 11:10 | 50.012
2020-10-14 | 11:10 | 50.012
2020-10-14 | 11:10 | 50.012
2020-10-14 | 11:10 | 50.011
2020-10-14 | 11:10 | 50.01
2020-10-14 | 11:10 | 50.008
2020-10-14 | 11:10 | 50.006
2020-10-14 | 11:10 | 50.006
2020-10-14 | 11:10 | 50.007
2020-10-14 | 11:10 | 50.005
2020-10-14 | 11:10 | 50.007
2020-10-14 | 11:10 | 50.008
2020-10-14 | 11:10 | 50.01
2020-10-14 | 11:10 | 50.012
2020-10-14 | 11:10 | 50.014
2020-10-14 | 11:10 | 50.016
2020-10-14 | 11:10 | 50.015
2020-10-14 | 11:10 | 50.015
2020-10-14 | 11:10 | 50.014
2020-10-14 | 11:10 | 50.014
2020-10-14 | 11:10 | 50.014
2020-10-14 | 11:10 | 50.014
2020-10-14 | 11:10 | 50.016
2020-10-14 | 11:10 | 50.016
2020-10-14 | 11:10 | 50.015
2020-10-14 | 11:10 | 50.012
2020-10-14 | 11:10 | 50.011
2020-10-14 | 11:10 | 50.007
2020-10-14 | 11:10 | 50.007
2020-10-14 | 11:10 | 50.006
2020-10-14 | 11:10 | 50.006
2020-10-14 | 11:10 | 50.002
2020-10-14 | 11:10 | 50
2020-10-14 | 11:10 | 49.994
2020-10-14 | 11:10 | 49.994
2020-10-14 | 11:10 | 49.989
2020-10-14 | 11:10 | 49.987
2020-10-14 | 11:10 | 49.985
2020-10-14 | 11:10 | 49.984
2020-10-14 | 11:10 | 49.986
2020-10-14 | 11:10 | 49.986
2020-10-14 | 11:10 | 49.989
2020-10-14 | 11:10 | 49.989
2020-10-14 | 11:10 | 49.99
2020-10-14 | 11:10 | 49.99
2020-10-14 | 11:10 | 49.99
2020-10-14 | 11:10 | 49.99
2020-10-14 | 11:10 | 49.99
2020-10-14 | 11:10 | 49.989
2020-10-14 | 11:10 | 49.987
2020-10-14 | 11:10 | 49.985
2020-10-14 | 11:10 | 49.981
2020-10-14 | 11:10 | 49.98
2020-10-14 | 11:10 | 49.98
2020-10-14 | 11:10 | 49.98
2020-10-14 | 11:10 | 49.978
2020-10-14 | 11:10 | 49.974
2020-10-14 | 11:10 | 49.967
2020-10-14 | 11:10 | 49.956
2020-10-14 | 11:10 | 49.942
2020-10-14 | 11:10 | 49.93
2020-10-14 | 11:11 | 49.917
2020-10-14 | 11:11 | 49.908
2020-10-14 | 11:11 | 49.896
2020-10-14 | 11:11 | 49.889
2020-10-14 | 11:11 | 49.88
2020-10-14 | 11:11 | 49.88
2020-10-14 | 11:11 | 49.883
2020-10-14 | 11:11 | 49.883
2020-10-14 | 11:11 | 49.884
2020-10-14 | 11:11 | 49.882
2020-10-14 | 11:11 | 49.88
2020-10-14 | 11:11 | 49.878
2020-10-14 | 11:11 | 49.876
2020-10-14 | 11:11 | 49.872
2020-10-14 | 11:11 | 49.869
2020-10-14 | 11:11 | 49.865
2020-10-14 | 11:11 | 49.859
2020-10-14 | 11:11 | 49.854
2020-10-14 | 11:11 | 49.85
2020-10-14 | 11:11 | 49.845
2020-10-14 | 11:11 | 49.839
2020-10-14 | 11:11 | 49.831
2020-10-14 | 11:11 | 49.825
2020-10-14 | 11:11 | 49.823
2020-10-14 | 11:11 | 49.83
2020-10-14 | 11:11 | 49.836
2020-10-14 | 11:11 | 49.843
2020-10-14 | 11:11 | 49.851
2020-10-14 | 11:11 | 49.855
2020-10-14 | 11:11 | 49.858
2020-10-14 | 11:11 | 49.859
2020-10-14 | 11:11 | 49.859
2020-10-14 | 11:11 | 49.859
2020-10-14 | 11:11 | 49.856
2020-10-14 | 11:11 | 49.856
2020-10-14 | 11:11 | 49.855
2020-10-14 | 11:11 | 49.854
2020-10-14 | 11:11 | 49.853
2020-10-14 | 11:11 | 49.853
2020-10-14 | 11:11 | 49.854
2020-10-14 | 11:11 | 49.855
2020-10-14 | 11:11 | 49.856
2020-10-14 | 11:11 | 49.857
2020-10-14 | 11:11 | 49.858
2020-10-14 | 11:11 | 49.858
2020-10-14 | 11:11 | 49.857
2020-10-14 | 11:11 | 49.856
2020-10-14 | 11:11 | 49.855
2020-10-14 | 11:11 | 49.852
2020-10-14 | 11:11 | 49.851
2020-10-14 | 11:11 | 49.848
2020-10-14 | 11:11 | 49.849
2020-10-14 | 11:11 | 49.848
2020-10-14 | 11:11 | 49.849
2020-10-14 | 11:11 | 49.848
2020-10-14 | 11:11 | 49.847
2020-10-14 | 11:11 | 49.848
2020-10-14 | 11:11 | 49.848
2020-10-14 | 11:11 | 49.851
2020-10-14 | 11:12 | 49.854
2020-10-14 | 11:12 | 49.859
2020-10-14 | 11:12 | 49.861
2020-10-14 | 11:12 | 49.865
2020-10-14 | 11:12 | 49.871
2020-10-14 | 11:12 | 49.872
2020-10-14 | 11:12 | 49.877
2020-10-14 | 11:12 | 49.878
2020-10-14 | 11:12 | 49.882
2020-10-14 | 11:12 | 49.885
2020-10-14 | 11:12 | 49.888
2020-10-14 | 11:12 | 49.89
2020-10-14 | 11:12 | 49.891
2020-10-14 | 11:12 | 49.893
2020-10-14 | 11:12 | 49.896
2020-10-14 | 11:12 | 49.897
2020-10-14 | 11:12 | 49.9
2020-10-14 | 11:12 | 49.902
2020-10-14 | 11:12 | 49.903
2020-10-14 | 11:12 | 49.904
2020-10-14 | 11:12 | 49.904
2020-10-14 | 11:12 | 49.906
2020-10-14 | 11:12 | 49.908
2020-10-14 | 11:12 | 49.908
2020-10-14 | 11:12 | 49.909
2020-10-14 | 11:12 | 49.909
2020-10-14 | 11:12 | 49.911
2020-10-14 | 11:12 | 49.91
2020-10-14 | 11:12 | 49.909
2020-10-14 | 11:12 | 49.908
2020-10-14 | 11:12 | 49.908
2020-10-14 | 11:12 | 49.906
2020-10-14 | 11:12 | 49.905
2020-10-14 | 11:12 | 49.903
2020-10-14 | 11:12 | 49.902
2020-10-14 | 11:12 | 49.901
2020-10-14 | 11:12 | 49.901
2020-10-14 | 11:12 | 49.901
2020-10-14 | 11:12 | 49.901
2020-10-14 | 11:12 | 49.902
2020-10-14 | 11:12 | 49.901
2020-10-14 | 11:12 | 49.902
2020-10-14 | 11:12 | 49.902
2020-10-14 | 11:12 | 49.901
2020-10-14 | 11:12 | 49.9
2020-10-14 | 11:12 | 49.899
2020-10-14 | 11:12 | 49.897
2020-10-14 | 11:12 | 49.894
2020-10-14 | 11:12 | 49.891
2020-10-14 | 11:12 | 49.887
2020-10-14 | 11:12 | 49.883
2020-10-14 | 11:12 | 49.88
2020-10-14 | 11:12 | 49.878
2020-10-14 | 11:12 | 49.876
2020-10-14 | 11:12 | 49.875
2020-10-14 | 11:12 | 49.874
2020-10-14 | 11:12 | 49.873
2020-10-14 | 11:12 | 49.872
2020-10-14 | 11:12 | 49.871
2020-10-14 | 11:12 | 49.871
2020-10-14 | 11:12 | 49.871
2020-10-14 | 11:13 | 49.872
2020-10-14 | 11:13 | 49.871
2020-10-14 | 11:13 | 49.872
2020-10-14 | 11:13 | 49.871
2020-10-14 | 11:13 | 49.871
2020-10-14 | 11:13 | 49.871
2020-10-14 | 11:13 | 49.874
2020-10-14 | 11:13 | 49.88
2020-10-14 | 11:13 | 49.887
2020-10-14 | 11:13 | 49.893
2020-10-14 | 11:13 | 49.897
2020-10-14 | 11:13 | 49.901
2020-10-14 | 11:13 | 49.903
2020-10-14 | 11:13 | 49.905
2020-10-14 | 11:13 | 49.908
2020-10-14 | 11:13 | 49.911
2020-10-14 | 11:13 | 49.914
2020-10-14 | 11:13 | 49.917
2020-10-14 | 11:13 | 49.919
2020-10-14 | 11:13 | 49.92
2020-10-14 | 11:13 | 49.92
2020-10-14 | 11:13 | 49.919
2020-10-14 | 11:13 | 49.918
2020-10-14 | 11:13 | 49.917
2020-10-14 | 11:13 | 49.915
2020-10-14 | 11:13 | 49.912
2020-10-14 | 11:13 | 49.909
2020-10-14 | 11:13 | 49.905
2020-10-14 | 11:13 | 49.901
2020-10-14 | 11:13 | 49.897
2020-10-14 | 11:13 | 49.891
2020-10-14 | 11:13 | 49.888
2020-10-14 | 11:13 | 49.885
2020-10-14 | 11:13 | 49.884
2020-10-14 | 11:13 | 49.883
2020-10-14 | 11:13 | 49.886
2020-10-14 | 11:13 | 49.886
2020-10-14 | 11:13 | 49.891
2020-10-14 | 11:13 | 49.893
2020-10-14 | 11:13 | 49.895
2020-10-14 | 11:13 | 49.895
2020-10-14 | 11:13 | 49.895
2020-10-14 | 11:13 | 49.896
2020-10-14 | 11:13 | 49.895
2020-10-14 | 11:13 | 49.894
2020-10-14 | 11:13 | 49.892
2020-10-14 | 11:13 | 49.893
2020-10-14 | 11:13 | 49.893
2020-10-14 | 11:13 | 49.892
2020-10-14 | 11:13 | 49.893
2020-10-14 | 11:13 | 49.894
2020-10-14 | 11:13 | 49.896
2020-10-14 | 11:13 | 49.898
2020-10-14 | 11:13 | 49.899
2020-10-14 | 11:13 | 49.9
2020-10-14 | 11:13 | 49.901
2020-10-14 | 11:13 | 49.901
2020-10-14 | 11:13 | 49.9
2020-10-14 | 11:13 | 49.899
2020-10-14 | 11:14 | 49.898
2020-10-14 | 11:14 | 49.898
2020-10-14 | 11:14 | 49.899
2020-10-14 | 11:14 | 49.9
2020-10-14 | 11:14 | 49.9
2020-10-14 | 11:14 | 49.9
2020-10-14 | 11:14 | 49.9
2020-10-14 | 11:14 | 49.901
2020-10-14 | 11:14 | 49.9
2020-10-14 | 11:14 | 49.901
2020-10-14 | 11:14 | 49.901
2020-10-14 | 11:14 | 49.902
2020-10-14 | 11:14 | 49.902
2020-10-14 | 11:14 | 49.903
2020-10-14 | 11:14 | 49.905
2020-10-14 | 11:14 | 49.905
2020-10-14 | 11:14 | 49.906
2020-10-14 | 11:14 | 49.906
2020-10-14 | 11:14 | 49.907
2020-10-14 | 11:14 | 49.906
2020-10-14 | 11:14 | 49.906
2020-10-14 | 11:14 | 49.907
2020-10-14 | 11:14 | 49.906
2020-10-14 | 11:14 | 49.907
2020-10-14 | 11:14 | 49.907
2020-10-14 | 11:14 | 49.908
2020-10-14 | 11:14 | 49.907
2020-10-14 | 11:14 | 49.908
2020-10-14 | 11:14 | 49.909
2020-10-14 | 11:14 | 49.91
2020-10-14 | 11:14 | 49.909
2020-10-14 | 11:14 | 49.906
2020-10-14 | 11:14 | 49.903
2020-10-14 | 11:14 | 49.901
2020-10-14 | 11:14 | 49.899
2020-10-14 | 11:14 | 49.896
2020-10-14 | 11:14 | 49.894
2020-10-14 | 11:14 | 49.893
2020-10-14 | 11:14 | 49.892
2020-10-14 | 11:14 | 49.89
2020-10-14 | 11:14 | 49.89
2020-10-14 | 11:14 | 49.891
2020-10-14 | 11:14 | 49.891
2020-10-14 | 11:14 | 49.893
2020-10-14 | 11:14 | 49.89
2020-10-14 | 11:14 | 49.889
2020-10-14 | 11:14 | 49.889
2020-10-14 | 11:14 | 49.889
2020-10-14 | 11:14 | 49.891
2020-10-14 | 11:14 | 49.894
2020-10-14 | 11:14 | 49.896
2020-10-14 | 11:14 | 49.898
2020-10-14 | 11:14 | 49.902
2020-10-14 | 11:14 | 49.904
2020-10-14 | 11:14 | 49.905
2020-10-14 | 11:14 | 49.907
2020-10-14 | 11:14 | 49.908
2020-10-14 | 11:14 | 49.909
2020-10-14 | 11:14 | 49.91
2020-10-14 | 11:14 | 49.912
2020-10-14 | 11:14 | 49.912
2020-10-14 | 11:15 | 49.912
2020-10-14 | 11:15 | 49.909
2020-10-14 | 11:15 | 49.909
2020-10-14 | 11:15 | 49.91
2020-10-14 | 11:15 | 49.911
2020-10-14 | 11:15 | 49.912
2020-10-14 | 11:15 | 49.914
2020-10-14 | 11:15 | 49.919
2020-10-14 | 11:15 | 49.923
2020-10-14 | 11:15 | 49.925
2020-10-14 | 11:15 | 49.929
2020-10-14 | 11:15 | 49.928
2020-10-14 | 11:15 | 49.93
2020-10-14 | 11:15 | 49.932
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.937
2020-10-14 | 11:15 | 49.938
2020-10-14 | 11:15 | 49.939
2020-10-14 | 11:15 | 49.94
2020-10-14 | 11:15 | 49.94
2020-10-14 | 11:15 | 49.939
2020-10-14 | 11:15 | 49.937
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.937
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.935
2020-10-14 | 11:15 | 49.933
2020-10-14 | 11:15 | 49.933
2020-10-14 | 11:15 | 49.932
2020-10-14 | 11:15 | 49.931
2020-10-14 | 11:15 | 49.929
2020-10-14 | 11:15 | 49.929
2020-10-14 | 11:15 | 49.93
2020-10-14 | 11:15 | 49.929
2020-10-14 | 11:15 | 49.932
2020-10-14 | 11:15 | 49.933
2020-10-14 | 11:15 | 49.935
2020-10-14 | 11:15 | 49.935
2020-10-14 | 11:15 | 49.935
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.938
2020-10-14 | 11:15 | 49.938
2020-10-14 | 11:15 | 49.94
2020-10-14 | 11:15 | 49.938
2020-10-14 | 11:15 | 49.937
2020-10-14 | 11:15 | 49.937
2020-10-14 | 11:15 | 49.936
2020-10-14 | 11:15 | 49.935
2020-10-14 | 11:15 | 49.934
2020-10-14 | 11:15 | 49.933
2020-10-14 | 11:15 | 49.932
2020-10-14 | 11:15 | 49.931
2020-10-14 | 11:15 | 49.929
2020-10-14 | 11:15 | 49.927
2020-10-14 | 11:15 | 49.926
2020-10-14 | 11:16 | 49.926
2020-10-14 | 11:16 | 49.925
2020-10-14 | 11:16 | 49.924
2020-10-14 | 11:16 | 49.923
2020-10-14 | 11:16 | 49.923
2020-10-14 | 11:16 | 49.921
2020-10-14 | 11:16 | 49.921
2020-10-14 | 11:16 | 49.921
2020-10-14 | 11:16 | 49.923
2020-10-14 | 11:16 | 49.924
2020-10-14 | 11:16 | 49.923
2020-10-14 | 11:16 | 49.923
2020-10-14 | 11:16 | 49.924
2020-10-14 | 11:16 | 49.926
2020-10-14 | 11:16 | 49.927
2020-10-14 | 11:16 | 49.93
2020-10-14 | 11:16 | 49.933
2020-10-14 | 11:16 | 49.936
2020-10-14 | 11:16 | 49.939
2020-10-14 | 11:16 | 49.943
2020-10-14 | 11:16 | 49.946
2020-10-14 | 11:16 | 49.948
2020-10-14 | 11:16 | 49.951
2020-10-14 | 11:16 | 49.952
2020-10-14 | 11:16 | 49.954
2020-10-14 | 11:16 | 49.956
2020-10-14 | 11:16 | 49.955
2020-10-14 | 11:16 | 49.955
2020-10-14 | 11:16 | 49.954
2020-10-14 | 11:16 | 49.952
2020-10-14 | 11:16 | 49.948
2020-10-14 | 11:16 | 49.944
2020-10-14 | 11:16 | 49.942
2020-10-14 | 11:16 | 49.94
2020-10-14 | 11:16 | 49.938
2020-10-14 | 11:16 | 49.936
2020-10-14 | 11:16 | 49.933
2020-10-14 | 11:16 | 49.928
2020-10-14 | 11:16 | 49.924
2020-10-14 | 11:16 | 49.92
2020-10-14 | 11:16 | 49.918
2020-10-14 | 11:16 | 49.915
2020-10-14 | 11:16 | 49.914
2020-10-14 | 11:16 | 49.913
2020-10-14 | 11:16 | 49.912
2020-10-14 | 11:16 | 49.91
2020-10-14 | 11:16 | 49.908
2020-10-14 | 11:16 | 49.907
2020-10-14 | 11:16 | 49.907
2020-10-14 | 11:16 | 49.906
2020-10-14 | 11:16 | 49.908
2020-10-14 | 11:16 | 49.908
2020-10-14 | 11:16 | 49.909
2020-10-14 | 11:16 | 49.91
2020-10-14 | 11:16 | 49.911
2020-10-14 | 11:16 | 49.913
2020-10-14 | 11:16 | 49.914
2020-10-14 | 11:16 | 49.914
2020-10-14 | 11:16 | 49.915
2020-10-14 | 11:16 | 49.915
2020-10-14 | 11:16 | 49.915
2020-10-14 | 11:17 | 49.916
2020-10-14 | 11:17 | 49.914
2020-10-14 | 11:17 | 49.913
2020-10-14 | 11:17 | 49.911
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.913
2020-10-14 | 11:17 | 49.913
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.913
2020-10-14 | 11:17 | 49.914
2020-10-14 | 11:17 | 49.915
2020-10-14 | 11:17 | 49.915
2020-10-14 | 11:17 | 49.916
2020-10-14 | 11:17 | 49.914
2020-10-14 | 11:17 | 49.913
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.911
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.91
2020-10-14 | 11:17 | 49.911
2020-10-14 | 11:17 | 49.91
2020-10-14 | 11:17 | 49.911
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.912
2020-10-14 | 11:17 | 49.909
2020-10-14 | 11:17 | 49.909
2020-10-14 | 11:17 | 49.907
2020-10-14 | 11:17 | 49.907
2020-10-14 | 11:17 | 49.905
2020-10-14 | 11:17 | 49.904
2020-10-14 | 11:17 | 49.901
2020-10-14 | 11:17 | 49.897
2020-10-14 | 11:17 | 49.894
2020-10-14 | 11:17 | 49.89
2020-10-14 | 11:17 | 49.887
2020-10-14 | 11:17 | 49.883
2020-10-14 | 11:17 | 49.882
2020-10-14 | 11:17 | 49.88
2020-10-14 | 11:17 | 49.88
2020-10-14 | 11:17 | 49.881
2020-10-14 | 11:17 | 49.882
2020-10-14 | 11:17 | 49.882
2020-10-14 | 11:17 | 49.883
2020-10-14 | 11:17 | 49.882
2020-10-14 | 11:17 | 49.881
2020-10-14 | 11:17 | 49.881
2020-10-14 | 11:17 | 49.881
2020-10-14 | 11:17 | 49.881
2020-10-14 | 11:17 | 49.882
2020-10-14 | 11:17 | 49.883
2020-10-14 | 11:17 | 49.883
2020-10-14 | 11:17 | 49.883
2020-10-14 | 11:17 | 49.883
2020-10-14 | 11:17 | 49.885
2020-10-14 | 11:17 | 49.886
2020-10-14 | 11:17 | 49.889
2020-10-14 | 11:17 | 49.892
2020-10-14 | 11:18 | 49.895
2020-10-14 | 11:18 | 49.896
2020-10-14 | 11:18 | 49.9
2020-10-14 | 11:18 | 49.902
2020-10-14 | 11:18 | 49.906
2020-10-14 | 11:18 | 49.91
2020-10-14 | 11:18 | 49.912
2020-10-14 | 11:18 | 49.912
2020-10-14 | 11:18 | 49.912
2020-10-14 | 11:18 | 49.911
2020-10-14 | 11:18 | 49.91
2020-10-14 | 11:18 | 49.91
2020-10-14 | 11:18 | 49.91
2020-10-14 | 11:18 | 49.91
2020-10-14 | 11:18 | 49.911
2020-10-14 | 11:18 | 49.91
2020-10-14 | 11:18 | 49.907
2020-10-14 | 11:18 | 49.903
2020-10-14 | 11:18 | 49.903
2020-10-14 | 11:18 | 49.9
2020-10-14 | 11:18 | 49.899
2020-10-14 | 11:18 | 49.897
2020-10-14 | 11:18 | 49.896
2020-10-14 | 11:18 | 49.894
2020-10-14 | 11:18 | 49.892
2020-10-14 | 11:18 | 49.891
2020-10-14 | 11:18 | 49.893
2020-10-14 | 11:18 | 49.893
2020-10-14 | 11:18 | 49.894
2020-10-14 | 11:18 | 49.894
2020-10-14 | 11:18 | 49.896
2020-10-14 | 11:18 | 49.894
2020-10-14 | 11:18 | 49.893
2020-10-14 | 11:18 | 49.89
2020-10-14 | 11:18 | 49.889
2020-10-14 | 11:18 | 49.886
2020-10-14 | 11:18 | 49.883
2020-10-14 | 11:18 | 49.882
2020-10-14 | 11:18 | 49.882
2020-10-14 | 11:18 | 49.882
2020-10-14 | 11:18 | 49.882
2020-10-14 | 11:18 | 49.88
2020-10-14 | 11:18 | 49.877
2020-10-14 | 11:18 | 49.875
2020-10-14 | 11:18 | 49.874
2020-10-14 | 11:18 | 49.875
2020-10-14 | 11:18 | 49.874
2020-10-14 | 11:18 | 49.874
2020-10-14 | 11:18 | 49.872
2020-10-14 | 11:18 | 49.873
2020-10-14 | 11:18 | 49.875
2020-10-14 | 11:18 | 49.878
2020-10-14 | 11:18 | 49.878
2020-10-14 | 11:18 | 49.881
2020-10-14 | 11:18 | 49.882
2020-10-14 | 11:18 | 49.884
2020-10-14 | 11:18 | 49.887
2020-10-14 | 11:18 | 49.89
2020-10-14 | 11:18 | 49.892
2020-10-14 | 11:18 | 49.893
2020-10-14 | 11:18 | 49.894
2020-10-14 | 11:19 | 49.893
2020-10-14 | 11:19 | 49.892
2020-10-14 | 11:19 | 49.892
2020-10-14 | 11:19 | 49.892
2020-10-14 | 11:19 | 49.891
2020-10-14 | 11:19 | 49.891
2020-10-14 | 11:19 | 49.891
2020-10-14 | 11:19 | 49.892
2020-10-14 | 11:19 | 49.891
2020-10-14 | 11:19 | 49.892
2020-10-14 | 11:19 | 49.892
2020-10-14 | 11:19 | 49.894
2020-10-14 | 11:19 | 49.895
2020-10-14 | 11:19 | 49.897
2020-10-14 | 11:19 | 49.898
2020-10-14 | 11:19 | 49.899
2020-10-14 | 11:19 | 49.898
2020-10-14 | 11:19 | 49.899
2020-10-14 | 11:19 | 49.9
2020-10-14 | 11:19 | 49.902
2020-10-14 | 11:19 | 49.903
2020-10-14 | 11:19 | 49.907
2020-10-14 | 11:19 | 49.91
2020-10-14 | 11:19 | 49.912
2020-10-14 | 11:19 | 49.911
2020-10-14 | 11:19 | 49.912
2020-10-14 | 11:19 | 49.911
2020-10-14 | 11:19 | 49.909
2020-10-14 | 11:19 | 49.908
2020-10-14 | 11:19 | 49.905
2020-10-14 | 11:19 | 49.901
2020-10-14 | 11:19 | 49.897
2020-10-14 | 11:19 | 49.894
2020-10-14 | 11:19 | 49.89
2020-10-14 | 11:19 | 49.886
2020-10-14 | 11:19 | 49.883
2020-10-14 | 11:19 | 49.881
2020-10-14 | 11:19 | 49.879
2020-10-14 | 11:19 | 49.876
2020-10-14 | 11:19 | 49.874
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.873
2020-10-14 | 11:19 | 49.873
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.873
2020-10-14 | 11:19 | 49.872
2020-10-14 | 11:19 | 49.875
2020-10-14 | 11:19 | 49.876
2020-10-14 | 11:19 | 49.88
2020-10-14 | 11:19 | 49.882
2020-10-14 | 11:19 | 49.883
2020-10-14 | 11:19 | 49.884
2020-10-14 | 11:19 | 49.885
2020-10-14 | 11:19 | 49.885
2020-10-14 | 11:19 | 49.888
2020-10-14 | 11:20 | 49.888
2020-10-14 | 11:20 | 49.89
2020-10-14 | 11:20 | 49.888
2020-10-14 | 11:20 | 49.89
2020-10-14 | 11:20 | 49.889
2020-10-14 | 11:20 | 49.89
2020-10-14 | 11:20 | 49.889
2020-10-14 | 11:20 | 49.887
2020-10-14 | 11:20 | 49.886
2020-10-14 | 11:20 | 49.884
2020-10-14 | 11:20 | 49.884
2020-10-14 | 11:20 | 49.883
2020-10-14 | 11:20 | 49.882
2020-10-14 | 11:20 | 49.88
2020-10-14 | 11:20 | 49.88
2020-10-14 | 11:20 | 49.879
2020-10-14 | 11:20 | 49.878
2020-10-14 | 11:20 | 49.877
2020-10-14 | 11:20 | 49.875
2020-10-14 | 11:20 | 49.872
2020-10-14 | 11:20 | 49.871
2020-10-14 | 11:20 | 49.869
2020-10-14 | 11:20 | 49.868
2020-10-14 | 11:20 | 49.866
2020-10-14 | 11:20 | 49.866
2020-10-14 | 11:20 | 49.865
2020-10-14 | 11:20 | 49.864
2020-10-14 | 11:20 | 49.864
2020-10-14 | 11:20 | 49.862
2020-10-14 | 11:20 | 49.861
2020-10-14 | 11:20 | 49.858
2020-10-14 | 11:20 | 49.855
2020-10-14 | 11:20 | 49.851
2020-10-14 | 11:20 | 49.848
2020-10-14 | 11:20 | 49.845
2020-10-14 | 11:20 | 49.844
2020-10-14 | 11:20 | 49.843
2020-10-14 | 11:20 | 49.841
2020-10-14 | 11:20 | 49.841
2020-10-14 | 11:20 | 49.84
2020-10-14 | 11:20 | 49.84
2020-10-14 | 11:20 | 49.842
2020-10-14 | 11:20 | 49.844
2020-10-14 | 11:20 | 49.846
2020-10-14 | 11:20 | 49.849
2020-10-14 | 11:20 | 49.852
2020-10-14 | 11:20 | 49.854
2020-10-14 | 11:20 | 49.852
2020-10-14 | 11:20 | 49.854
2020-10-14 | 11:20 | 49.852
2020-10-14 | 11:20 | 49.853
2020-10-14 | 11:20 | 49.854
2020-10-14 | 11:20 | 49.853
2020-10-14 | 11:20 | 49.853
2020-10-14 | 11:20 | 49.854
2020-10-14 | 11:20 | 49.855
2020-10-14 | 11:20 | 49.853
2020-10-14 | 11:20 | 49.852
2020-10-14 | 11:20 | 49.852
2020-10-14 | 11:20 | 49.851
2020-10-14 | 11:20 | 49.852
2020-10-14 | 11:21 | 49.856
2020-10-14 | 11:21 | 49.862
2020-10-14 | 11:21 | 49.864
2020-10-14 | 11:21 | 49.865
2020-10-14 | 11:21 | 49.868
2020-10-14 | 11:21 | 49.871
2020-10-14 | 11:21 | 49.874
2020-10-14 | 11:21 | 49.877
2020-10-14 | 11:21 | 49.879
2020-10-14 | 11:21 | 49.883
2020-10-14 | 11:21 | 49.887
2020-10-14 | 11:21 | 49.889
2020-10-14 | 11:21 | 49.889
2020-10-14 | 11:21 | 49.888
2020-10-14 | 11:21 | 49.886
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.883
2020-10-14 | 11:21 | 49.881
2020-10-14 | 11:21 | 49.881
2020-10-14 | 11:21 | 49.883
2020-10-14 | 11:21 | 49.882
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.885
2020-10-14 | 11:21 | 49.886
2020-10-14 | 11:21 | 49.886
2020-10-14 | 11:21 | 49.885
2020-10-14 | 11:21 | 49.884
2020-10-14 | 11:21 | 49.885
2020-10-14 | 11:21 | 49.885
2020-10-14 | 11:21 | 49.886
2020-10-14 | 11:21 | 49.887
2020-10-14 | 11:21 | 49.888
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.889
2020-10-14 | 11:21 | 49.889
2020-10-14 | 11:21 | 49.889
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.891
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.891
2020-10-14 | 11:21 | 49.891
2020-10-14 | 11:21 | 49.889
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.89
2020-10-14 | 11:21 | 49.891
2020-10-14 | 11:21 | 49.894
2020-10-14 | 11:21 | 49.898
2020-10-14 | 11:21 | 49.898
2020-10-14 | 11:21 | 49.898
2020-10-14 | 11:21 | 49.897
2020-10-14 | 11:21 | 49.895
2020-10-14 | 11:21 | 49.893
2020-10-14 | 11:22 | 49.892
2020-10-14 | 11:22 | 49.89
2020-10-14 | 11:22 | 49.888
2020-10-14 | 11:22 | 49.887
2020-10-14 | 11:22 | 49.884
2020-10-14 | 11:22 | 49.884
2020-10-14 | 11:22 | 49.883
2020-10-14 | 11:22 | 49.884
2020-10-14 | 11:22 | 49.886
2020-10-14 | 11:22 | 49.887
2020-10-14 | 11:22 | 49.889
2020-10-14 | 11:22 | 49.891
2020-10-14 | 11:22 | 49.892
2020-10-14 | 11:22 | 49.894
2020-10-14 | 11:22 | 49.892
2020-10-14 | 11:22 | 49.889
2020-10-14 | 11:22 | 49.888
2020-10-14 | 11:22 | 49.885
2020-10-14 | 11:22 | 49.882
2020-10-14 | 11:22 | 49.879
2020-10-14 | 11:22 | 49.877
2020-10-14 | 11:22 | 49.874
2020-10-14 | 11:22 | 49.87
2020-10-14 | 11:22 | 49.867
2020-10-14 | 11:22 | 49.865
2020-10-14 | 11:22 | 49.862
2020-10-14 | 11:22 | 49.858
2020-10-14 | 11:22 | 49.856
2020-10-14 | 11:22 | 49.853
2020-10-14 | 11:22 | 49.851
2020-10-14 | 11:22 | 49.851
2020-10-14 | 11:22 | 49.849
2020-10-14 | 11:22 | 49.849
2020-10-14 | 11:22 | 49.851
2020-10-14 | 11:22 | 49.85
2020-10-14 | 11:22 | 49.849
2020-10-14 | 11:22 | 49.848
2020-10-14 | 11:22 | 49.849
2020-10-14 | 11:22 | 49.847
2020-10-14 | 11:22 | 49.849
2020-10-14 | 11:22 | 49.851
2020-10-14 | 11:22 | 49.853
2020-10-14 | 11:22 | 49.857
2020-10-14 | 11:22 | 49.861
2020-10-14 | 11:22 | 49.865
2020-10-14 | 11:22 | 49.867
2020-10-14 | 11:22 | 49.869
2020-10-14 | 11:22 | 49.87
2020-10-14 | 11:22 | 49.87
2020-10-14 | 11:22 | 49.873
2020-10-14 | 11:22 | 49.875
2020-10-14 | 11:22 | 49.876
2020-10-14 | 11:22 | 49.875
2020-10-14 | 11:22 | 49.876
2020-10-14 | 11:22 | 49.876
2020-10-14 | 11:22 | 49.874
2020-10-14 | 11:22 | 49.875
2020-10-14 | 11:22 | 49.875
2020-10-14 | 11:22 | 49.877
2020-10-14 | 11:22 | 49.878
2020-10-14 | 11:22 | 49.877
2020-10-14 | 11:23 | 49.877
2020-10-14 | 11:23 | 49.878
2020-10-14 | 11:23 | 49.88
2020-10-14 | 11:23 | 49.878
2020-10-14 | 11:23 | 49.878
2020-10-14 | 11:23 | 49.879
2020-10-14 | 11:23 | 49.88
2020-10-14 | 11:23 | 49.88
2020-10-14 | 11:23 | 49.881
2020-10-14 | 11:23 | 49.883
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.888
2020-10-14 | 11:23 | 49.889
2020-10-14 | 11:23 | 49.889
2020-10-14 | 11:23 | 49.889
2020-10-14 | 11:23 | 49.891
2020-10-14 | 11:23 | 49.89
2020-10-14 | 11:23 | 49.889
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.888
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.887
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.885
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.886
2020-10-14 | 11:23 | 49.883
2020-10-14 | 11:23 | 49.882
2020-10-14 | 11:23 | 49.879
2020-10-14 | 11:23 | 49.877
2020-10-14 | 11:23 | 49.873
2020-10-14 | 11:23 | 49.872
2020-10-14 | 11:23 | 49.871
2020-10-14 | 11:23 | 49.87
2020-10-14 | 11:23 | 49.871
2020-10-14 | 11:23 | 49.869
2020-10-14 | 11:23 | 49.869
2020-10-14 | 11:23 | 49.87
2020-10-14 | 11:23 | 49.871
2020-10-14 | 11:23 | 49.873
2020-10-14 | 11:23 | 49.874
2020-10-14 | 11:23 | 49.876
2020-10-14 | 11:23 | 49.877
2020-10-14 | 11:23 | 49.877
2020-10-14 | 11:23 | 49.877
2020-10-14 | 11:23 | 49.877
2020-10-14 | 11:23 | 49.878
2020-10-14 | 11:23 | 49.879
2020-10-14 | 11:23 | 49.881
2020-10-14 | 11:24 | 49.884
2020-10-14 | 11:24 | 49.888
2020-10-14 | 11:24 | 49.891
2020-10-14 | 11:24 | 49.894
2020-10-14 | 11:24 | 49.896
2020-10-14 | 11:24 | 49.9
2020-10-14 | 11:24 | 49.901
2020-10-14 | 11:24 | 49.903
2020-10-14 | 11:24 | 49.905
2020-10-14 | 11:24 | 49.905
2020-10-14 | 11:24 | 49.907
2020-10-14 | 11:24 | 49.906
2020-10-14 | 11:24 | 49.907
2020-10-14 | 11:24 | 49.907
2020-10-14 | 11:24 | 49.91
2020-10-14 | 11:24 | 49.911
2020-10-14 | 11:24 | 49.914
2020-10-14 | 11:24 | 49.915
2020-10-14 | 11:24 | 49.916
2020-10-14 | 11:24 | 49.915
2020-10-14 | 11:24 | 49.916
2020-10-14 | 11:24 | 49.913
2020-10-14 | 11:24 | 49.911
2020-10-14 | 11:24 | 49.908
2020-10-14 | 11:24 | 49.906
2020-10-14 | 11:24 | 49.907
2020-10-14 | 11:24 | 49.907
2020-10-14 | 11:24 | 49.908
2020-10-14 | 11:24 | 49.91
2020-10-14 | 11:24 | 49.911
2020-10-14 | 11:24 | 49.913
2020-10-14 | 11:24 | 49.914
2020-10-14 | 11:24 | 49.915
2020-10-14 | 11:24 | 49.916
2020-10-14 | 11:24 | 49.918
2020-10-14 | 11:24 | 49.918
2020-10-14 | 11:24 | 49.917
2020-10-14 | 11:24 | 49.915
2020-10-14 | 11:24 | 49.91
2020-10-14 | 11:24 | 49.908
2020-10-14 | 11:24 | 49.905
2020-10-14 | 11:24 | 49.901
2020-10-14 | 11:24 | 49.901
2020-10-14 | 11:24 | 49.9
2020-10-14 | 11:24 | 49.9
2020-10-14 | 11:24 | 49.9
2020-10-14 | 11:24 | 49.897
2020-10-14 | 11:24 | 49.895
2020-10-14 | 11:24 | 49.893
2020-10-14 | 11:24 | 49.891
2020-10-14 | 11:24 | 49.889
2020-10-14 | 11:24 | 49.884
2020-10-14 | 11:24 | 49.881
2020-10-14 | 11:24 | 49.878
2020-10-14 | 11:24 | 49.877
2020-10-14 | 11:24 | 49.875
2020-10-14 | 11:24 | 49.875
2020-10-14 | 11:24 | 49.872
2020-10-14 | 11:24 | 49.872
2020-10-14 | 11:24 | 49.874
2020-10-14 | 11:24 | 49.874
2020-10-14 | 11:25 | 49.877
2020-10-14 | 11:25 | 49.877
2020-10-14 | 11:25 | 49.877
2020-10-14 | 11:25 | 49.876
2020-10-14 | 11:25 | 49.877
2020-10-14 | 11:25 | 49.875
2020-10-14 | 11:25 | 49.877
2020-10-14 | 11:25 | 49.876
2020-10-14 | 11:25 | 49.877
2020-10-14 | 11:25 | 49.879
2020-10-14 | 11:25 | 49.879
2020-10-14 | 11:25 | 49.881
2020-10-14 | 11:25 | 49.882
2020-10-14 | 11:25 | 49.882
2020-10-14 | 11:25 | 49.881
2020-10-14 | 11:25 | 49.882
2020-10-14 | 11:25 | 49.883
2020-10-14 | 11:25 | 49.884
2020-10-14 | 11:25 | 49.885
2020-10-14 | 11:25 | 49.887
2020-10-14 | 11:25 | 49.891
2020-10-14 | 11:25 | 49.894
2020-10-14 | 11:25 | 49.897
2020-10-14 | 11:25 | 49.899
2020-10-14 | 11:25 | 49.9
2020-10-14 | 11:25 | 49.903
2020-10-14 | 11:25 | 49.905
2020-10-14 | 11:25 | 49.906
2020-10-14 | 11:25 | 49.907
2020-10-14 | 11:25 | 49.909
2020-10-14 | 11:25 | 49.911
2020-10-14 | 11:25 | 49.91
2020-10-14 | 11:25 | 49.91
2020-10-14 | 11:25 | 49.909
2020-10-14 | 11:25 | 49.907
2020-10-14 | 11:25 | 49.904
2020-10-14 | 11:25 | 49.899
2020-10-14 | 11:25 | 49.897
2020-10-14 | 11:25 | 49.894
2020-10-14 | 11:25 | 49.892
2020-10-14 | 11:25 | 49.893
2020-10-14 | 11:25 | 49.893
2020-10-14 | 11:25 | 49.894
2020-10-14 | 11:25 | 49.897
2020-10-14 | 11:25 | 49.899
2020-10-14 | 11:25 | 49.903
2020-10-14 | 11:25 | 49.906
2020-10-14 | 11:25 | 49.908
2020-10-14 | 11:25 | 49.912
2020-10-14 | 11:25 | 49.914
2020-10-14 | 11:25 | 49.916
2020-10-14 | 11:25 | 49.917
2020-10-14 | 11:25 | 49.919
2020-10-14 | 11:25 | 49.919
2020-10-14 | 11:25 | 49.92
2020-10-14 | 11:25 | 49.92
2020-10-14 | 11:25 | 49.921
2020-10-14 | 11:25 | 49.92
2020-10-14 | 11:25 | 49.921
2020-10-14 | 11:26 | 49.923
2020-10-14 | 11:26 | 49.926
2020-10-14 | 11:26 | 49.928
2020-10-14 | 11:26 | 49.929
2020-10-14 | 11:26 | 49.929
2020-10-14 | 11:26 | 49.931
2020-10-14 | 11:26 | 49.931
2020-10-14 | 11:26 | 49.932
2020-10-14 | 11:26 | 49.933
2020-10-14 | 11:26 | 49.933
2020-10-14 | 11:26 | 49.935
2020-10-14 | 11:26 | 49.932
2020-10-14 | 11:26 | 49.931
2020-10-14 | 11:26 | 49.928
2020-10-14 | 11:26 | 49.926
2020-10-14 | 11:26 | 49.923
2020-10-14 | 11:26 | 49.921
2020-10-14 | 11:26 | 49.919
2020-10-14 | 11:26 | 49.919
2020-10-14 | 11:26 | 49.917
2020-10-14 | 11:26 | 49.917
2020-10-14 | 11:26 | 49.919
2020-10-14 | 11:26 | 49.919
2020-10-14 | 11:26 | 49.922
2020-10-14 | 11:26 | 49.923
2020-10-14 | 11:26 | 49.925
2020-10-14 | 11:26 | 49.929
2020-10-14 | 11:26 | 49.932
2020-10-14 | 11:26 | 49.932
2020-10-14 | 11:26 | 49.932
2020-10-14 | 11:26 | 49.931
2020-10-14 | 11:26 | 49.93
2020-10-14 | 11:26 | 49.929
2020-10-14 | 11:26 | 49.926
2020-10-14 | 11:26 | 49.926
2020-10-14 | 11:26 | 49.925
2020-10-14 | 11:26 | 49.925
2020-10-14 | 11:26 | 49.923
2020-10-14 | 11:26 | 49.923
2020-10-14 | 11:26 | 49.92
2020-10-14 | 11:26 | 49.916
2020-10-14 | 11:26 | 49.914
2020-10-14 | 11:26 | 49.911
2020-10-14 | 11:26 | 49.908
2020-10-14 | 11:26 | 49.907
2020-10-14 | 11:26 | 49.905
2020-10-14 | 11:26 | 49.904
2020-10-14 | 11:26 | 49.902
2020-10-14 | 11:26 | 49.899
2020-10-14 | 11:26 | 49.895
2020-10-14 | 11:26 | 49.894
2020-10-14 | 11:26 | 49.892
2020-10-14 | 11:26 | 49.89
2020-10-14 | 11:26 | 49.886
2020-10-14 | 11:26 | 49.882
2020-10-14 | 11:26 | 49.878
2020-10-14 | 11:26 | 49.877
2020-10-14 | 11:26 | 49.875
2020-10-14 | 11:26 | 49.874
2020-10-14 | 11:26 | 49.873
2020-10-14 | 11:26 | 49.873
2020-10-14 | 11:27 | 49.873
2020-10-14 | 11:27 | 49.873
2020-10-14 | 11:27 | 49.874
2020-10-14 | 11:27 | 49.876
2020-10-14 | 11:27 | 49.877
2020-10-14 | 11:27 | 49.877
2020-10-14 | 11:27 | 49.878
2020-10-14 | 11:27 | 49.878
2020-10-14 | 11:27 | 49.88
2020-10-14 | 11:27 | 49.877
2020-10-14 | 11:27 | 49.873
2020-10-14 | 11:27 | 49.867
2020-10-14 | 11:27 | 49.864
2020-10-14 | 11:27 | 49.86
2020-10-14 | 11:27 | 49.857
2020-10-14 | 11:27 | 49.855
2020-10-14 | 11:27 | 49.852
2020-10-14 | 11:27 | 49.85
2020-10-14 | 11:27 | 49.849
2020-10-14 | 11:27 | 49.848
2020-10-14 | 11:27 | 49.846
2020-10-14 | 11:27 | 49.846
2020-10-14 | 11:27 | 49.844
2020-10-14 | 11:27 | 49.844
2020-10-14 | 11:27 | 49.844
2020-10-14 | 11:27 | 49.845
2020-10-14 | 11:27 | 49.845
2020-10-14 | 11:27 | 49.845
2020-10-14 | 11:27 | 49.845
2020-10-14 | 11:27 | 49.844
2020-10-14 | 11:27 | 49.842
2020-10-14 | 11:27 | 49.841
2020-10-14 | 11:27 | 49.841
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.84
2020-10-14 | 11:27 | 49.841
2020-10-14 | 11:27 | 49.842
2020-10-14 | 11:27 | 49.842
2020-10-14 | 11:27 | 49.841
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.839
2020-10-14 | 11:27 | 49.838
2020-10-14 | 11:27 | 49.837
2020-10-14 | 11:27 | 49.836
2020-10-14 | 11:27 | 49.836
2020-10-14 | 11:27 | 49.835
2020-10-14 | 11:27 | 49.835
2020-10-14 | 11:27 | 49.834
2020-10-14 | 11:27 | 49.833
2020-10-14 | 11:27 | 49.832
2020-10-14 | 11:27 | 49.831
2020-10-14 | 11:27 | 49.831
2020-10-14 | 11:27 | 49.831
2020-10-14 | 11:27 | 49.83
2020-10-14 | 11:28 | 49.831
2020-10-14 | 11:28 | 49.831
2020-10-14 | 11:28 | 49.833
2020-10-14 | 11:28 | 49.835
2020-10-14 | 11:28 | 49.835
2020-10-14 | 11:28 | 49.838
2020-10-14 | 11:28 | 49.839
2020-10-14 | 11:28 | 49.839
2020-10-14 | 11:28 | 49.84
2020-10-14 | 11:28 | 49.842
2020-10-14 | 11:28 | 49.845
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.847
2020-10-14 | 11:28 | 49.847
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.845
2020-10-14 | 11:28 | 49.844
2020-10-14 | 11:28 | 49.843
2020-10-14 | 11:28 | 49.842
2020-10-14 | 11:28 | 49.839
2020-10-14 | 11:28 | 49.837
2020-10-14 | 11:28 | 49.836
2020-10-14 | 11:28 | 49.835
2020-10-14 | 11:28 | 49.835
2020-10-14 | 11:28 | 49.836
2020-10-14 | 11:28 | 49.838
2020-10-14 | 11:28 | 49.837
2020-10-14 | 11:28 | 49.838
2020-10-14 | 11:28 | 49.838
2020-10-14 | 11:28 | 49.836
2020-10-14 | 11:28 | 49.836
2020-10-14 | 11:28 | 49.833
2020-10-14 | 11:28 | 49.833
2020-10-14 | 11:28 | 49.831
2020-10-14 | 11:28 | 49.831
2020-10-14 | 11:28 | 49.831
2020-10-14 | 11:28 | 49.829
2020-10-14 | 11:28 | 49.83
2020-10-14 | 11:28 | 49.831
2020-10-14 | 11:28 | 49.833
2020-10-14 | 11:28 | 49.836
2020-10-14 | 11:28 | 49.836
2020-10-14 | 11:28 | 49.838
2020-10-14 | 11:28 | 49.839
2020-10-14 | 11:28 | 49.839
2020-10-14 | 11:28 | 49.842
2020-10-14 | 11:28 | 49.842
2020-10-14 | 11:28 | 49.843
2020-10-14 | 11:28 | 49.845
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.847
2020-10-14 | 11:28 | 49.848
2020-10-14 | 11:28 | 49.847
2020-10-14 | 11:28 | 49.848
2020-10-14 | 11:28 | 49.846
2020-10-14 | 11:28 | 49.845
2020-10-14 | 11:28 | 49.843
2020-10-14 | 11:28 | 49.841
2020-10-14 | 11:29 | 49.84
2020-10-14 | 11:29 | 49.836
2020-10-14 | 11:29 | 49.833
2020-10-14 | 11:29 | 49.831
2020-10-14 | 11:29 | 49.829
2020-10-14 | 11:29 | 49.827
2020-10-14 | 11:29 | 49.827
2020-10-14 | 11:29 | 49.827
2020-10-14 | 11:29 | 49.828
2020-10-14 | 11:29 | 49.829
2020-10-14 | 11:29 | 49.83
2020-10-14 | 11:29 | 49.831
2020-10-14 | 11:29 | 49.831
2020-10-14 | 11:29 | 49.832
2020-10-14 | 11:29 | 49.834
2020-10-14 | 11:29 | 49.836
2020-10-14 | 11:29 | 49.838
2020-10-14 | 11:29 | 49.837
2020-10-14 | 11:29 | 49.837
2020-10-14 | 11:29 | 49.828
2020-10-14 | 11:29 | 49.822
2020-10-14 | 11:29 | 49.815
2020-10-14 | 11:29 | 49.81
2020-10-14 | 11:29 | 49.809
2020-10-14 | 11:29 | 49.808
2020-10-14 | 11:29 | 49.807
2020-10-14 | 11:29 | 49.805
2020-10-14 | 11:29 | 49.804
2020-10-14 | 11:29 | 49.801
2020-10-14 | 11:29 | 49.801
2020-10-14 | 11:29 | 49.798
2020-10-14 | 11:29 | 49.794
2020-10-14 | 11:29 | 49.79
2020-10-14 | 11:29 | 49.785
2020-10-14 | 11:29 | 49.782
2020-10-14 | 11:29 | 49.778
2020-10-14 | 11:29 | 49.777
2020-10-14 | 11:29 | 49.776
2020-10-14 | 11:29 | 49.776
2020-10-14 | 11:29 | 49.775
2020-10-14 | 11:29 | 49.775
2020-10-14 | 11:29 | 49.774
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:29 | 49.772
2020-10-14 | 11:29 | 49.771
2020-10-14 | 11:29 | 49.77
2020-10-14 | 11:29 | 49.769
2020-10-14 | 11:29 | 49.769
2020-10-14 | 11:29 | 49.772
2020-10-14 | 11:29 | 49.772
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:29 | 49.774
2020-10-14 | 11:29 | 49.774
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:29 | 49.774
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:29 | 49.773
2020-10-14 | 11:30 | 49.775
2020-10-14 | 11:30 | 49.776
2020-10-14 | 11:30 | 49.779
2020-10-14 | 11:30 | 49.78
2020-10-14 | 11:30 | 49.781
2020-10-14 | 11:30 | 49.782
2020-10-14 | 11:30 | 49.78
2020-10-14 | 11:30 | 49.777
2020-10-14 | 11:30 | 49.774
2020-10-14 | 11:30 | 49.773
2020-10-14 | 11:30 | 49.772
2020-10-14 | 11:30 | 49.771
2020-10-14 | 11:30 | 49.77
2020-10-14 | 11:30 | 49.77
2020-10-14 | 11:30 | 49.769
2020-10-14 | 11:30 | 49.769
2020-10-14 | 11:30 | 49.766
2020-10-14 | 11:30 | 49.764
2020-10-14 | 11:30 | 49.763
2020-10-14 | 11:30 | 49.763
2020-10-14 | 11:30 | 49.763
2020-10-14 | 11:30 | 49.765
2020-10-14 | 11:30 | 49.764
2020-10-14 | 11:30 | 49.764
2020-10-14 | 11:30 | 49.765
2020-10-14 | 11:30 | 49.766
2020-10-14 | 11:30 | 49.767
2020-10-14 | 11:30 | 49.767
2020-10-14 | 11:30 | 49.768
2020-10-14 | 11:30 | 49.767
2020-10-14 | 11:30 | 49.769
2020-10-14 | 11:30 | 49.767
2020-10-14 | 11:30 | 49.768
2020-10-14 | 11:30 | 49.768
2020-10-14 | 11:30 | 49.767
2020-10-14 | 11:30 | 49.768
2020-10-14 | 11:30 | 49.767
2020-10-14 | 11:30 | 49.77
2020-10-14 | 11:30 | 49.772
2020-10-14 | 11:30 | 49.778
2020-10-14 | 11:30 | 49.782
2020-10-14 | 11:30 | 49.786
2020-10-14 | 11:30 | 49.788
2020-10-14 | 11:30 | 49.792
2020-10-14 | 11:30 | 49.796
2020-10-14 | 11:30 | 49.802
2020-10-14 | 11:30 | 49.807
2020-10-14 | 11:30 | 49.813
2020-10-14 | 11:30 | 49.815
2020-10-14 | 11:30 | 49.816
2020-10-14 | 11:30 | 49.817
2020-10-14 | 11:30 | 49.817
2020-10-14 | 11:30 | 49.818
2020-10-14 | 11:30 | 49.818
2020-10-14 | 11:30 | 49.819
2020-10-14 | 11:30 | 49.819
2020-10-14 | 11:30 | 49.82
2020-10-14 | 11:30 | 49.821
2020-10-14 | 11:30 | 49.821
2020-10-14 | 11:30 | 49.823
2020-10-14 | 11:30 | 49.824
2020-10-14 | 11:31 | 49.828
2020-10-14 | 11:31 | 49.828
2020-10-14 | 11:31 | 49.83
2020-10-14 | 11:31 | 49.831
2020-10-14 | 11:31 | 49.832
2020-10-14 | 11:31 | 49.833
2020-10-14 | 11:31 | 49.835
2020-10-14 | 11:31 | 49.835
2020-10-14 | 11:31 | 49.837
2020-10-14 | 11:31 | 49.836
2020-10-14 | 11:31 | 49.837
2020-10-14 | 11:31 | 49.837
2020-10-14 | 11:31 | 49.837
2020-10-14 | 11:31 | 49.837
2020-10-14 | 11:31 | 49.837
2020-10-14 | 11:31 | 49.84
2020-10-14 | 11:31 | 49.842
2020-10-14 | 11:31 | 49.845
2020-10-14 | 11:31 | 49.85
2020-10-14 | 11:31 | 49.852
2020-10-14 | 11:31 | 49.855
2020-10-14 | 11:31 | 49.855
2020-10-14 | 11:31 | 49.857
2020-10-14 | 11:31 | 49.855
2020-10-14 | 11:31 | 49.857
2020-10-14 | 11:31 | 49.857
2020-10-14 | 11:31 | 49.857
2020-10-14 | 11:31 | 49.857
2020-10-14 | 11:31 | 49.856
2020-10-14 | 11:31 | 49.856
2020-10-14 | 11:31 | 49.854
2020-10-14 | 11:31 | 49.855
2020-10-14 | 11:31 | 49.856
2020-10-14 | 11:31 | 49.858
2020-10-14 | 11:31 | 49.859
2020-10-14 | 11:31 | 49.861
2020-10-14 | 11:31 | 49.861
2020-10-14 | 11:31 | 49.863
2020-10-14 | 11:31 | 49.865
2020-10-14 | 11:31 | 49.869
2020-10-14 | 11:31 | 49.872
2020-10-14 | 11:31 | 49.874
2020-10-14 | 11:31 | 49.877
2020-10-14 | 11:31 | 49.88
2020-10-14 | 11:31 | 49.881
2020-10-14 | 11:31 | 49.883
2020-10-14 | 11:31 | 49.882
2020-10-14 | 11:31 | 49.883
2020-10-14 | 11:31 | 49.882
2020-10-14 | 11:31 | 49.881
2020-10-14 | 11:31 | 49.879
2020-10-14 | 11:31 | 49.879
2020-10-14 | 11:31 | 49.878
2020-10-14 | 11:31 | 49.879
2020-10-14 | 11:31 | 49.878
2020-10-14 | 11:31 | 49.878
2020-10-14 | 11:31 | 49.878
2020-10-14 | 11:31 | 49.876
2020-10-14 | 11:31 | 49.876
2020-10-14 | 11:32 | 49.875
2020-10-14 | 11:32 | 49.875
2020-10-14 | 11:32 | 49.874
2020-10-14 | 11:32 | 49.873
2020-10-14 | 11:32 | 49.87
2020-10-14 | 11:32 | 49.871
2020-10-14 | 11:32 | 49.872
2020-10-14 | 11:32 | 49.873
2020-10-14 | 11:32 | 49.872
2020-10-14 | 11:32 | 49.871
2020-10-14 | 11:32 | 49.873
2020-10-14 | 11:32 | 49.874
2020-10-14 | 11:32 | 49.876
2020-10-14 | 11:32 | 49.879
2020-10-14 | 11:32 | 49.882
2020-10-14 | 11:32 | 49.883
2020-10-14 | 11:32 | 49.885
2020-10-14 | 11:32 | 49.886
2020-10-14 | 11:32 | 49.887
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.891
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.891
2020-10-14 | 11:32 | 49.891
2020-10-14 | 11:32 | 49.891
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.889
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.889
2020-10-14 | 11:32 | 49.888
2020-10-14 | 11:32 | 49.887
2020-10-14 | 11:32 | 49.886
2020-10-14 | 11:32 | 49.883
2020-10-14 | 11:32 | 49.88
2020-10-14 | 11:32 | 49.877
2020-10-14 | 11:32 | 49.876
2020-10-14 | 11:32 | 49.874
2020-10-14 | 11:32 | 49.873
2020-10-14 | 11:32 | 49.874
2020-10-14 | 11:32 | 49.876
2020-10-14 | 11:32 | 49.879
2020-10-14 | 11:32 | 49.883
2020-10-14 | 11:32 | 49.886
2020-10-14 | 11:32 | 49.889
2020-10-14 | 11:32 | 49.89
2020-10-14 | 11:32 | 49.892
2020-10-14 | 11:32 | 49.892
2020-10-14 | 11:32 | 49.893
2020-10-14 | 11:32 | 49.893
2020-10-14 | 11:32 | 49.893
2020-10-14 | 11:32 | 49.894
2020-10-14 | 11:32 | 49.895
2020-10-14 | 11:32 | 49.898
2020-10-14 | 11:32 | 49.9
2020-10-14 | 11:32 | 49.902
2020-10-14 | 11:32 | 49.904
2020-10-14 | 11:32 | 49.905
2020-10-14 | 11:32 | 49.906
2020-10-14 | 11:33 | 49.907
2020-10-14 | 11:33 | 49.908
2020-10-14 | 11:33 | 49.909
2020-10-14 | 11:33 | 49.911
2020-10-14 | 11:33 | 49.912
2020-10-14 | 11:33 | 49.913
2020-10-14 | 11:33 | 49.913
2020-10-14 | 11:33 | 49.914
2020-10-14 | 11:33 | 49.913
2020-10-14 | 11:33 | 49.914
2020-10-14 | 11:33 | 49.914
2020-10-14 | 11:33 | 49.915
2020-10-14 | 11:33 | 49.916
2020-10-14 | 11:33 | 49.915
2020-10-14 | 11:33 | 49.918
2020-10-14 | 11:33 | 49.92
2020-10-14 | 11:33 | 49.922
2020-10-14 | 11:33 | 49.924
2020-10-14 | 11:33 | 49.927
2020-10-14 | 11:33 | 49.93
2020-10-14 | 11:33 | 49.932
2020-10-14 | 11:33 | 49.934
2020-10-14 | 11:33 | 49.936
2020-10-14 | 11:33 | 49.937
2020-10-14 | 11:33 | 49.938
2020-10-14 | 11:33 | 49.938
2020-10-14 | 11:33 | 49.94
2020-10-14 | 11:33 | 49.94
2020-10-14 | 11:33 | 49.942
2020-10-14 | 11:33 | 49.942
2020-10-14 | 11:33 | 49.944
2020-10-14 | 11:33 | 49.945
2020-10-14 | 11:33 | 49.948
2020-10-14 | 11:33 | 49.95
2020-10-14 | 11:33 | 49.949
2020-10-14 | 11:33 | 49.948
2020-10-14 | 11:33 | 49.945
2020-10-14 | 11:33 | 49.944
2020-10-14 | 11:33 | 49.942
2020-10-14 | 11:33 | 49.941
2020-10-14 | 11:33 | 49.941
2020-10-14 | 11:33 | 49.942
2020-10-14 | 11:33 | 49.945
2020-10-14 | 11:33 | 49.949
2020-10-14 | 11:33 | 49.954
2020-10-14 | 11:33 | 49.958
2020-10-14 | 11:33 | 49.963
2020-10-14 | 11:33 | 49.965
2020-10-14 | 11:33 | 49.967
2020-10-14 | 11:33 | 49.967
2020-10-14 | 11:33 | 49.968
2020-10-14 | 11:33 | 49.965
2020-10-14 | 11:33 | 49.964
2020-10-14 | 11:33 | 49.962
2020-10-14 | 11:33 | 49.96
2020-10-14 | 11:33 | 49.959
2020-10-14 | 11:33 | 49.958
2020-10-14 | 11:33 | 49.959
2020-10-14 | 11:33 | 49.959
2020-10-14 | 11:34 | 49.959
2020-10-14 | 11:34 | 49.959
2020-10-14 | 11:34 | 49.956
2020-10-14 | 11:34 | 49.955
2020-10-14 | 11:34 | 49.953
2020-10-14 | 11:34 | 49.951
2020-10-14 | 11:34 | 49.95
2020-10-14 | 11:34 | 49.951
2020-10-14 | 11:34 | 49.95
2020-10-14 | 11:34 | 49.951
2020-10-14 | 11:34 | 49.953
2020-10-14 | 11:34 | 49.955
2020-10-14 | 11:34 | 49.959
2020-10-14 | 11:34 | 49.962
2020-10-14 | 11:34 | 49.964
2020-10-14 | 11:34 | 49.962
2020-10-14 | 11:34 | 49.961
2020-10-14 | 11:34 | 49.958
2020-10-14 | 11:34 | 49.958
2020-10-14 | 11:34 | 49.958
2020-10-14 | 11:34 | 49.959
2020-10-14 | 11:34 | 49.959
2020-10-14 | 11:34 | 49.958
2020-10-14 | 11:34 | 49.957
2020-10-14 | 11:34 | 49.954
2020-10-14 | 11:34 | 49.953
2020-10-14 | 11:34 | 49.951
2020-10-14 | 11:34 | 49.95
2020-10-14 | 11:34 | 49.948
2020-10-14 | 11:34 | 49.944
2020-10-14 | 11:34 | 49.942
2020-10-14 | 11:34 | 49.938
2020-10-14 | 11:34 | 49.936
2020-10-14 | 11:34 | 49.933
2020-10-14 | 11:34 | 49.932
2020-10-14 | 11:34 | 49.933
2020-10-14 | 11:34 | 49.934
2020-10-14 | 11:34 | 49.936
2020-10-14 | 11:34 | 49.938
2020-10-14 | 11:34 | 49.939
2020-10-14 | 11:34 | 49.943
2020-10-14 | 11:34 | 49.945
2020-10-14 | 11:34 | 49.948
2020-10-14 | 11:34 | 49.949
2020-10-14 | 11:34 | 49.951
2020-10-14 | 11:34 | 49.951
2020-10-14 | 11:34 | 49.953
2020-10-14 | 11:34 | 49.955
2020-10-14 | 11:34 | 49.953
2020-10-14 | 11:34 | 49.955
2020-10-14 | 11:34 | 49.954
2020-10-14 | 11:34 | 49.956
2020-10-14 | 11:34 | 49.957
2020-10-14 | 11:34 | 49.959
2020-10-14 | 11:34 | 49.962
2020-10-14 | 11:34 | 49.964
2020-10-14 | 11:34 | 49.966
2020-10-14 | 11:34 | 49.964
2020-10-14 | 11:34 | 49.964
2020-10-14 | 11:34 | 49.964
2020-10-14 | 11:34 | 49.964
2020-10-14 | 11:35 | 49.966
2020-10-14 | 11:35 | 49.967
2020-10-14 | 11:35 | 49.966
2020-10-14 | 11:35 | 49.967
2020-10-14 | 11:35 | 49.967
2020-10-14 | 11:35 | 49.965
2020-10-14 | 11:35 | 49.965
2020-10-14 | 11:35 | 49.962
2020-10-14 | 11:35 | 49.961
2020-10-14 | 11:35 | 49.96
2020-10-14 | 11:35 | 49.958
2020-10-14 | 11:35 | 49.958
2020-10-14 | 11:35 | 49.959
2020-10-14 | 11:35 | 49.959
2020-10-14 | 11:35 | 49.958
2020-10-14 | 11:35 | 49.958
2020-10-14 | 11:35 | 49.957
2020-10-14 | 11:35 | 49.953
2020-10-14 | 11:35 | 49.952
2020-10-14 | 11:35 | 49.951
2020-10-14 | 11:35 | 49.949
2020-10-14 | 11:35 | 49.95
2020-10-14 | 11:35 | 49.949
2020-10-14 | 11:35 | 49.949
2020-10-14 | 11:35 | 49.95
2020-10-14 | 11:35 | 49.952
2020-10-14 | 11:35 | 49.954
2020-10-14 | 11:35 | 49.957
2020-10-14 | 11:35 | 49.958
2020-10-14 | 11:35 | 49.96
2020-10-14 | 11:35 | 49.962
2020-10-14 | 11:35 | 49.965
2020-10-14 | 11:35 | 49.966
2020-10-14 | 11:35 | 49.969
2020-10-14 | 11:35 | 49.97
2020-10-14 | 11:35 | 49.971
2020-10-14 | 11:35 | 49.972
2020-10-14 | 11:35 | 49.972
2020-10-14 | 11:35 | 49.973
2020-10-14 | 11:35 | 49.973
2020-10-14 | 11:35 | 49.975
2020-10-14 | 11:35 | 49.976
2020-10-14 | 11:35 | 49.977
2020-10-14 | 11:35 | 49.977
2020-10-14 | 11:35 | 49.978
2020-10-14 | 11:35 | 49.98
2020-10-14 | 11:35 | 49.981
2020-10-14 | 11:35 | 49.983
2020-10-14 | 11:35 | 49.982
2020-10-14 | 11:35 | 49.982
2020-10-14 | 11:35 | 49.981
2020-10-14 | 11:35 | 49.981
2020-10-14 | 11:35 | 49.981
2020-10-14 | 11:35 | 49.982
2020-10-14 | 11:35 | 49.985
2020-10-14 | 11:35 | 49.987
2020-10-14 | 11:35 | 49.989
2020-10-14 | 11:35 | 49.99
2020-10-14 | 11:35 | 49.992
2020-10-14 | 11:36 | 49.995
2020-10-14 | 11:36 | 49.996
2020-10-14 | 11:36 | 49.998
2020-10-14 | 11:36 | 49.997
2020-10-14 | 11:36 | 49.997
2020-10-14 | 11:36 | 49.997
2020-10-14 | 11:36 | 49.997
2020-10-14 | 11:36 | 49.996
2020-10-14 | 11:36 | 49.993
2020-10-14 | 11:36 | 49.991
2020-10-14 | 11:36 | 49.988
2020-10-14 | 11:36 | 49.986
2020-10-14 | 11:36 | 49.983
2020-10-14 | 11:36 | 49.984
2020-10-14 | 11:36 | 49.984
2020-10-14 | 11:36 | 49.984
2020-10-14 | 11:36 | 49.984
2020-10-14 | 11:36 | 49.981
2020-10-14 | 11:36 | 49.98
2020-10-14 | 11:36 | 49.979
2020-10-14 | 11:36 | 49.98
2020-10-14 | 11:36 | 49.98
2020-10-14 | 11:36 | 49.981
2020-10-14 | 11:36 | 49.981
2020-10-14 | 11:36 | 49.982
2020-10-14 | 11:36 | 49.983
2020-10-14 | 11:36 | 49.985
2020-10-14 | 11:36 | 49.987
2020-10-14 | 11:36 | 49.986
2020-10-14 | 11:36 | 49.987
2020-10-14 | 11:36 | 49.987
2020-10-14 | 11:36 | 49.985
2020-10-14 | 11:36 | 49.983
2020-10-14 | 11:36 | 49.98
2020-10-14 | 11:36 | 49.98
2020-10-14 | 11:36 | 49.978
2020-10-14 | 11:36 | 49.977
2020-10-14 | 11:36 | 49.975
2020-10-14 | 11:36 | 49.974
2020-10-14 | 11:36 | 49.973
2020-10-14 | 11:36 | 49.972
2020-10-14 | 11:36 | 49.971
2020-10-14 | 11:36 | 49.97
2020-10-14 | 11:36 | 49.97
2020-10-14 | 11:36 | 49.97
2020-10-14 | 11:36 | 49.971
2020-10-14 | 11:36 | 49.971
2020-10-14 | 11:36 | 49.97
2020-10-14 | 11:36 | 49.971
2020-10-14 | 11:36 | 49.972
2020-10-14 | 11:36 | 49.973
2020-10-14 | 11:36 | 49.974
2020-10-14 | 11:36 | 49.976
2020-10-14 | 11:36 | 49.978
2020-10-14 | 11:36 | 49.978
2020-10-14 | 11:36 | 49.979
2020-10-14 | 11:36 | 49.978
2020-10-14 | 11:36 | 49.978
2020-10-14 | 11:36 | 49.976
2020-10-14 | 11:36 | 49.976
2020-10-14 | 11:36 | 49.975
2020-10-14 | 11:37 | 49.973
2020-10-14 | 11:37 | 49.97
2020-10-14 | 11:37 | 49.968
2020-10-14 | 11:37 | 49.961
2020-10-14 | 11:37 | 49.957
2020-10-14 | 11:37 | 49.951
2020-10-14 | 11:37 | 49.947
2020-10-14 | 11:37 | 49.941
2020-10-14 | 11:37 | 49.94
2020-10-14 | 11:37 | 49.939
2020-10-14 | 11:37 | 49.939
2020-10-14 | 11:37 | 49.938
2020-10-14 | 11:37 | 49.939
2020-10-14 | 11:37 | 49.941
2020-10-14 | 11:37 | 49.943
2020-10-14 | 11:37 | 49.947
2020-10-14 | 11:37 | 49.948
2020-10-14 | 11:37 | 49.949
2020-10-14 | 11:37 | 49.948
2020-10-14 | 11:37 | 49.949
2020-10-14 | 11:37 | 49.949
2020-10-14 | 11:37 | 49.95
2020-10-14 | 11:37 | 49.952
2020-10-14 | 11:37 | 49.956
2020-10-14 | 11:37 | 49.957
2020-10-14 | 11:37 | 49.956
2020-10-14 | 11:37 | 49.956
2020-10-14 | 11:37 | 49.957
2020-10-14 | 11:37 | 49.959
2020-10-14 | 11:37 | 49.96
2020-10-14 | 11:37 | 49.962
2020-10-14 | 11:37 | 49.966
2020-10-14 | 11:37 | 49.968
2020-10-14 | 11:37 | 49.969
2020-10-14 | 11:37 | 49.97
2020-10-14 | 11:37 | 49.973
2020-10-14 | 11:37 | 49.974
2020-10-14 | 11:37 | 49.976
2020-10-14 | 11:37 | 49.978
2020-10-14 | 11:37 | 49.981
2020-10-14 | 11:37 | 49.984
2020-10-14 | 11:37 | 49.987
2020-10-14 | 11:37 | 49.99
2020-10-14 | 11:37 | 49.991
2020-10-14 | 11:37 | 49.994
2020-10-14 | 11:37 | 49.994
2020-10-14 | 11:37 | 49.995
2020-10-14 | 11:37 | 49.997
2020-10-14 | 11:37 | 49.997
2020-10-14 | 11:37 | 49.996
2020-10-14 | 11:37 | 49.997
2020-10-14 | 11:37 | 49.998
2020-10-14 | 11:37 | 49.998
2020-10-14 | 11:37 | 50
2020-10-14 | 11:37 | 50.001
2020-10-14 | 11:37 | 50.001
2020-10-14 | 11:37 | 50.004
2020-10-14 | 11:37 | 50.005
2020-10-14 | 11:37 | 50.008
2020-10-14 | 11:38 | 50.011
2020-10-14 | 11:38 | 50.016
2020-10-14 | 11:38 | 50.019
2020-10-14 | 11:38 | 50.021
2020-10-14 | 11:38 | 50.023
2020-10-14 | 11:38 | 50.025
2020-10-14 | 11:38 | 50.029
2020-10-14 | 11:38 | 50.031
2020-10-14 | 11:38 | 50.034
2020-10-14 | 11:38 | 50.036
2020-10-14 | 11:38 | 50.037
2020-10-14 | 11:38 | 50.037
2020-10-14 | 11:38 | 50.035
2020-10-14 | 11:38 | 50.034
2020-10-14 | 11:38 | 50.031
2020-10-14 | 11:38 | 50.031
2020-10-14 | 11:38 | 50.031
2020-10-14 | 11:38 | 50.032
2020-10-14 | 11:38 | 50.031
2020-10-14 | 11:38 | 50.031
2020-10-14 | 11:38 | 50.029
2020-10-14 | 11:38 | 50.028
2020-10-14 | 11:38 | 50.028
2020-10-14 | 11:38 | 50.028
2020-10-14 | 11:38 | 50.028
2020-10-14 | 11:38 | 50.027
2020-10-14 | 11:38 | 50.026
2020-10-14 | 11:38 | 50.023
2020-10-14 | 11:38 | 50.017
2020-10-14 | 11:38 | 50.009
2020-10-14 | 11:38 | 50.001
2020-10-14 | 11:38 | 49.99
2020-10-14 | 11:38 | 49.979
2020-10-14 | 11:38 | 49.969
2020-10-14 | 11:38 | 49.956
2020-10-14 | 11:38 | 49.948
2020-10-14 | 11:38 | 49.942
2020-10-14 | 11:38 | 49.937
2020-10-14 | 11:38 | 49.933
2020-10-14 | 11:38 | 49.931
2020-10-14 | 11:38 | 49.929
2020-10-14 | 11:38 | 49.927
2020-10-14 | 11:38 | 49.928
2020-10-14 | 11:38 | 49.928
2020-10-14 | 11:38 | 49.927
2020-10-14 | 11:38 | 49.926
2020-10-14 | 11:38 | 49.929
2020-10-14 | 11:38 | 49.931
2020-10-14 | 11:38 | 49.934
2020-10-14 | 11:38 | 49.937
2020-10-14 | 11:38 | 49.941
2020-10-14 | 11:38 | 49.943
2020-10-14 | 11:38 | 49.943
2020-10-14 | 11:38 | 49.943
2020-10-14 | 11:38 | 49.946
2020-10-14 | 11:38 | 49.948
2020-10-14 | 11:38 | 49.953
2020-10-14 | 11:38 | 49.954
2020-10-14 | 11:38 | 49.957
2020-10-14 | 11:38 | 49.957
2020-10-14 | 11:39 | 49.958
2020-10-14 | 11:39 | 49.958
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.955
2020-10-14 | 11:39 | 49.954
2020-10-14 | 11:39 | 49.952
2020-10-14 | 11:39 | 49.953
2020-10-14 | 11:39 | 49.954
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.958
2020-10-14 | 11:39 | 49.959
2020-10-14 | 11:39 | 49.96
2020-10-14 | 11:39 | 49.961
2020-10-14 | 11:39 | 49.963
2020-10-14 | 11:39 | 49.963
2020-10-14 | 11:39 | 49.96
2020-10-14 | 11:39 | 49.958
2020-10-14 | 11:39 | 49.957
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.955
2020-10-14 | 11:39 | 49.955
2020-10-14 | 11:39 | 49.955
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.956
2020-10-14 | 11:39 | 49.955
2020-10-14 | 11:39 | 49.952
2020-10-14 | 11:39 | 49.952
2020-10-14 | 11:39 | 49.951
2020-10-14 | 11:39 | 49.951
2020-10-14 | 11:39 | 49.947
2020-10-14 | 11:39 | 49.941
2020-10-14 | 11:39 | 49.937
2020-10-14 | 11:39 | 49.933
2020-10-14 | 11:39 | 49.931
2020-10-14 | 11:39 | 49.928
2020-10-14 | 11:39 | 49.927
2020-10-14 | 11:39 | 49.927
2020-10-14 | 11:39 | 49.925
2020-10-14 | 11:39 | 49.926
2020-10-14 | 11:39 | 49.925
2020-10-14 | 11:39 | 49.923
2020-10-14 | 11:39 | 49.922
2020-10-14 | 11:39 | 49.921
2020-10-14 | 11:39 | 49.92
2020-10-14 | 11:39 | 49.92
2020-10-14 | 11:39 | 49.92
2020-10-14 | 11:39 | 49.92
2020-10-14 | 11:39 | 49.92
2020-10-14 | 11:39 | 49.922
2020-10-14 | 11:39 | 49.923
2020-10-14 | 11:39 | 49.923
2020-10-14 | 11:39 | 49.925
2020-10-14 | 11:39 | 49.925
2020-10-14 | 11:39 | 49.922
2020-10-14 | 11:39 | 49.921
2020-10-14 | 11:39 | 49.916
2020-10-14 | 11:39 | 49.915
2020-10-14 | 11:39 | 49.913
2020-10-14 | 11:40 | 49.914
2020-10-14 | 11:40 | 49.914
2020-10-14 | 11:40 | 49.913
2020-10-14 | 11:40 | 49.911
2020-10-14 | 11:40 | 49.912
2020-10-14 | 11:40 | 49.912
2020-10-14 | 11:40 | 49.914
2020-10-14 | 11:40 | 49.915
2020-10-14 | 11:40 | 49.916
2020-10-14 | 11:40 | 49.918
2020-10-14 | 11:40 | 49.919
2020-10-14 | 11:40 | 49.92
2020-10-14 | 11:40 | 49.923
2020-10-14 | 11:40 | 49.924
2020-10-14 | 11:40 | 49.927
2020-10-14 | 11:40 | 49.928
2020-10-14 | 11:40 | 49.929
2020-10-14 | 11:40 | 49.931
2020-10-14 | 11:40 | 49.933
2020-10-14 | 11:40 | 49.935
2020-10-14 | 11:40 | 49.938
2020-10-14 | 11:40 | 49.939
2020-10-14 | 11:40 | 49.94
2020-10-14 | 11:40 | 49.939
2020-10-14 | 11:40 | 49.935
2020-10-14 | 11:40 | 49.933
2020-10-14 | 11:40 | 49.93
2020-10-14 | 11:40 | 49.927
2020-10-14 | 11:40 | 49.924
2020-10-14 | 11:40 | 49.922
2020-10-14 | 11:40 | 49.919
2020-10-14 | 11:40 | 49.916
2020-10-14 | 11:40 | 49.917
2020-10-14 | 11:40 | 49.919
2020-10-14 | 11:40 | 49.921
2020-10-14 | 11:40 | 49.922
2020-10-14 | 11:40 | 49.925
2020-10-14 | 11:40 | 49.927
2020-10-14 | 11:40 | 49.928
2020-10-14 | 11:40 | 49.93
2020-10-14 | 11:40 | 49.931
2020-10-14 | 11:40 | 49.932
2020-10-14 | 11:40 | 49.931
2020-10-14 | 11:40 | 49.932
2020-10-14 | 11:40 | 49.932
2020-10-14 | 11:40 | 49.93
2020-10-14 | 11:40 | 49.93
2020-10-14 | 11:40 | 49.93
2020-10-14 | 11:40 | 49.928
2020-10-14 | 11:40 | 49.927
2020-10-14 | 11:40 | 49.925
2020-10-14 | 11:40 | 49.926
2020-10-14 | 11:40 | 49.927
2020-10-14 | 11:40 | 49.929
2020-10-14 | 11:40 | 49.929
2020-10-14 | 11:40 | 49.931
2020-10-14 | 11:40 | 49.93
2020-10-14 | 11:40 | 49.929
2020-10-14 | 11:40 | 49.928
2020-10-14 | 11:40 | 49.929
2020-10-14 | 11:41 | 49.929
2020-10-14 | 11:41 | 49.93
2020-10-14 | 11:41 | 49.932
2020-10-14 | 11:41 | 49.934
2020-10-14 | 11:41 | 49.934
2020-10-14 | 11:41 | 49.935
2020-10-14 | 11:41 | 49.937
2020-10-14 | 11:41 | 49.938
2020-10-14 | 11:41 | 49.94
2020-10-14 | 11:41 | 49.941
2020-10-14 | 11:41 | 49.945
2020-10-14 | 11:41 | 49.947
2020-10-14 | 11:41 | 49.949
2020-10-14 | 11:41 | 49.951
2020-10-14 | 11:41 | 49.954
2020-10-14 | 11:41 | 49.956
2020-10-14 | 11:41 | 49.958
2020-10-14 | 11:41 | 49.962
2020-10-14 | 11:41 | 49.963
2020-10-14 | 11:41 | 49.962
2020-10-14 | 11:41 | 49.964
2020-10-14 | 11:41 | 49.964
2020-10-14 | 11:41 | 49.966
2020-10-14 | 11:41 | 49.967
2020-10-14 | 11:41 | 49.97
2020-10-14 | 11:41 | 49.971
2020-10-14 | 11:41 | 49.971
2020-10-14 | 11:41 | 49.973
2020-10-14 | 11:41 | 49.972
2020-10-14 | 11:41 | 49.971
2020-10-14 | 11:41 | 49.972
2020-10-14 | 11:41 | 49.97
2020-10-14 | 11:41 | 49.97
2020-10-14 | 11:41 | 49.968
2020-10-14 | 11:41 | 49.965
2020-10-14 | 11:41 | 49.962
2020-10-14 | 11:41 | 49.96
2020-10-14 | 11:41 | 49.957
2020-10-14 | 11:41 | 49.955
2020-10-14 | 11:41 | 49.953
2020-10-14 | 11:41 | 49.951
2020-10-14 | 11:41 | 49.95
2020-10-14 | 11:41 | 49.95
2020-10-14 | 11:41 | 49.95
2020-10-14 | 11:41 | 49.95
2020-10-14 | 11:41 | 49.948
2020-10-14 | 11:41 | 49.947
2020-10-14 | 11:41 | 49.946
2020-10-14 | 11:41 | 49.946
2020-10-14 | 11:41 | 49.942
2020-10-14 | 11:41 | 49.941
2020-10-14 | 11:41 | 49.942
2020-10-14 | 11:41 | 49.941
2020-10-14 | 11:41 | 49.944
2020-10-14 | 11:41 | 49.945
2020-10-14 | 11:41 | 49.949
2020-10-14 | 11:41 | 49.951
2020-10-14 | 11:41 | 49.955
2020-10-14 | 11:41 | 49.958
2020-10-14 | 11:41 | 49.963
2020-10-14 | 11:42 | 49.969
2020-10-14 | 11:42 | 49.974
2020-10-14 | 11:42 | 49.979
2020-10-14 | 11:42 | 49.981
2020-10-14 | 11:42 | 49.984
2020-10-14 | 11:42 | 49.986
2020-10-14 | 11:42 | 49.987
2020-10-14 | 11:42 | 49.989
2020-10-14 | 11:42 | 49.989
2020-10-14 | 11:42 | 49.988
2020-10-14 | 11:42 | 49.991
2020-10-14 | 11:42 | 49.99
2020-10-14 | 11:42 | 49.991
2020-10-14 | 11:42 | 49.991
2020-10-14 | 11:42 | 49.988
2020-10-14 | 11:42 | 49.985
2020-10-14 | 11:42 | 49.981
2020-10-14 | 11:42 | 49.974
2020-10-14 | 11:42 | 49.968
2020-10-14 | 11:42 | 49.963
2020-10-14 | 11:42 | 49.957
2020-10-14 | 11:42 | 49.952
2020-10-14 | 11:42 | 49.947
2020-10-14 | 11:42 | 49.941
2020-10-14 | 11:42 | 49.937
2020-10-14 | 11:42 | 49.935
2020-10-14 | 11:42 | 49.932
2020-10-14 | 11:42 | 49.932
2020-10-14 | 11:42 | 49.931
2020-10-14 | 11:42 | 49.931
2020-10-14 | 11:42 | 49.93
2020-10-14 | 11:42 | 49.931
2020-10-14 | 11:42 | 49.929
2020-10-14 | 11:42 | 49.928
2020-10-14 | 11:42 | 49.928
2020-10-14 | 11:42 | 49.927
2020-10-14 | 11:42 | 49.927
2020-10-14 | 11:42 | 49.929
2020-10-14 | 11:42 | 49.93
2020-10-14 | 11:42 | 49.932
2020-10-14 | 11:42 | 49.934
2020-10-14 | 11:42 | 49.938
2020-10-14 | 11:42 | 49.942
2020-10-14 | 11:42 | 49.946
2020-10-14 | 11:42 | 49.949
2020-10-14 | 11:42 | 49.949
2020-10-14 | 11:42 | 49.951
2020-10-14 | 11:42 | 49.953
2020-10-14 | 11:42 | 49.954
2020-10-14 | 11:42 | 49.956
2020-10-14 | 11:42 | 49.956
2020-10-14 | 11:42 | 49.956
2020-10-14 | 11:42 | 49.957
2020-10-14 | 11:42 | 49.956
2020-10-14 | 11:42 | 49.957
2020-10-14 | 11:42 | 49.957
2020-10-14 | 11:42 | 49.958
2020-10-14 | 11:42 | 49.958
2020-10-14 | 11:42 | 49.959
2020-10-14 | 11:42 | 49.958
2020-10-14 | 11:43 | 49.958
2020-10-14 | 11:43 | 49.958
2020-10-14 | 11:43 | 49.957
2020-10-14 | 11:43 | 49.959
2020-10-14 | 11:43 | 49.961
2020-10-14 | 11:43 | 49.962
2020-10-14 | 11:43 | 49.961
2020-10-14 | 11:43 | 49.958
2020-10-14 | 11:43 | 49.96
2020-10-14 | 11:43 | 49.961
2020-10-14 | 11:43 | 49.962
2020-10-14 | 11:43 | 49.964
2020-10-14 | 11:43 | 49.966
2020-10-14 | 11:43 | 49.968
2020-10-14 | 11:43 | 49.968
2020-10-14 | 11:43 | 49.968
2020-10-14 | 11:43 | 49.969
2020-10-14 | 11:43 | 49.969
2020-10-14 | 11:43 | 49.969
2020-10-14 | 11:43 | 49.97
2020-10-14 | 11:43 | 49.971
2020-10-14 | 11:43 | 49.973
2020-10-14 | 11:43 | 49.973
2020-10-14 | 11:43 | 49.973
2020-10-14 | 11:43 | 49.974
2020-10-14 | 11:43 | 49.974
2020-10-14 | 11:43 | 49.976
2020-10-14 | 11:43 | 49.98
2020-10-14 | 11:43 | 49.983
2020-10-14 | 11:43 | 49.985
2020-10-14 | 11:43 | 49.989
2020-10-14 | 11:43 | 49.989
2020-10-14 | 11:43 | 49.989
2020-10-14 | 11:43 | 49.99
2020-10-14 | 11:43 | 49.99
2020-10-14 | 11:43 | 49.988
2020-10-14 | 11:43 | 49.988
2020-10-14 | 11:43 | 49.989
2020-10-14 | 11:43 | 49.991
2020-10-14 | 11:43 | 49.994
2020-10-14 | 11:43 | 49.995
2020-10-14 | 11:43 | 49.997
2020-10-14 | 11:43 | 49.998
2020-10-14 | 11:43 | 50
2020-10-14 | 11:43 | 50.001
2020-10-14 | 11:43 | 50.001
2020-10-14 | 11:43 | 50.002
2020-10-14 | 11:43 | 50.004
2020-10-14 | 11:43 | 50.006
2020-10-14 | 11:43 | 50.009
2020-10-14 | 11:43 | 50.011
2020-10-14 | 11:43 | 50.011
2020-10-14 | 11:43 | 50.011
2020-10-14 | 11:43 | 50.011
2020-10-14 | 11:43 | 50.01
2020-10-14 | 11:43 | 50.006
2020-10-14 | 11:43 | 50.004
2020-10-14 | 11:43 | 50.001
2020-10-14 | 11:43 | 49.998
2020-10-14 | 11:43 | 49.995
2020-10-14 | 11:44 | 49.992
2020-10-14 | 11:44 | 49.989
2020-10-14 | 11:44 | 49.987
2020-10-14 | 11:44 | 49.985
2020-10-14 | 11:44 | 49.982
2020-10-14 | 11:44 | 49.978
2020-10-14 | 11:44 | 49.978
2020-10-14 | 11:44 | 49.977
2020-10-14 | 11:44 | 49.975
2020-10-14 | 11:44 | 49.976
2020-10-14 | 11:44 | 49.978
2020-10-14 | 11:44 | 49.979
2020-10-14 | 11:44 | 49.979
2020-10-14 | 11:44 | 49.981
2020-10-14 | 11:44 | 49.981
2020-10-14 | 11:44 | 49.982
2020-10-14 | 11:44 | 49.983
2020-10-14 | 11:44 | 49.984
2020-10-14 | 11:44 | 49.985
2020-10-14 | 11:44 | 49.985
2020-10-14 | 11:44 | 49.985
2020-10-14 | 11:44 | 49.986
2020-10-14 | 11:44 | 49.988
2020-10-14 | 11:44 | 49.988
2020-10-14 | 11:44 | 49.988
2020-10-14 | 11:44 | 49.988
2020-10-14 | 11:44 | 49.989
2020-10-14 | 11:44 | 49.987
2020-10-14 | 11:44 | 49.989
2020-10-14 | 11:44 | 49.989
2020-10-14 | 11:44 | 49.989
2020-10-14 | 11:44 | 49.988
2020-10-14 | 11:44 | 49.99
2020-10-14 | 11:44 | 49.991
2020-10-14 | 11:44 | 49.992
2020-10-14 | 11:44 | 49.994
2020-10-14 | 11:44 | 49.994
2020-10-14 | 11:44 | 49.996
2020-10-14 | 11:44 | 49.997
2020-10-14 | 11:44 | 49.997
2020-10-14 | 11:44 | 49.996
2020-10-14 | 11:44 | 49.996
2020-10-14 | 11:44 | 49.994
2020-10-14 | 11:44 | 49.993
2020-10-14 | 11:44 | 49.993
2020-10-14 | 11:44 | 49.99
2020-10-14 | 11:44 | 49.99
2020-10-14 | 11:44 | 49.991
2020-10-14 | 11:44 | 49.99
2020-10-14 | 11:44 | 49.992
2020-10-14 | 11:44 | 49.994
2020-10-14 | 11:44 | 49.993
2020-10-14 | 11:44 | 49.995
2020-10-14 | 11:44 | 49.995
2020-10-14 | 11:44 | 49.997
2020-10-14 | 11:44 | 49.999
2020-10-14 | 11:44 | 50.001
2020-10-14 | 11:44 | 50
2020-10-14 | 11:44 | 50
2020-10-14 | 11:44 | 49.999
2020-10-14 | 11:44 | 49.996
2020-10-14 | 11:45 | 49.995
2020-10-14 | 11:45 | 49.99
2020-10-14 | 11:45 | 49.989
2020-10-14 | 11:45 | 49.985
2020-10-14 | 11:45 | 49.981
2020-10-14 | 11:45 | 49.978
2020-10-14 | 11:45 | 49.976
2020-10-14 | 11:45 | 49.974
2020-10-14 | 11:45 | 49.971
2020-10-14 | 11:45 | 49.97
2020-10-14 | 11:45 | 49.968
2020-10-14 | 11:45 | 49.965
2020-10-14 | 11:45 | 49.962
2020-10-14 | 11:45 | 49.96
2020-10-14 | 11:45 | 49.957
2020-10-14 | 11:45 | 49.956
2020-10-14 | 11:45 | 49.955
2020-10-14 | 11:45 | 49.953
2020-10-14 | 11:45 | 49.952
2020-10-14 | 11:45 | 49.948
2020-10-14 | 11:45 | 49.946
2020-10-14 | 11:45 | 49.943
2020-10-14 | 11:45 | 49.941
2020-10-14 | 11:45 | 49.942
2020-10-14 | 11:45 | 49.942
2020-10-14 | 11:45 | 49.943
2020-10-14 | 11:45 | 49.943
2020-10-14 | 11:45 | 49.944
2020-10-14 | 11:45 | 49.945
2020-10-14 | 11:45 | 49.947
2020-10-14 | 11:45 | 49.948
2020-10-14 | 11:45 | 49.947
2020-10-14 | 11:45 | 49.949
2020-10-14 | 11:45 | 49.952
2020-10-14 | 11:45 | 49.955
2020-10-14 | 11:45 | 49.957
2020-10-14 | 11:45 | 49.959
2020-10-14 | 11:45 | 49.962
2020-10-14 | 11:45 | 49.964
2020-10-14 | 11:45 | 49.965
2020-10-14 | 11:45 | 49.967
2020-10-14 | 11:45 | 49.969
2020-10-14 | 11:45 | 49.968
2020-10-14 | 11:45 | 49.969
2020-10-14 | 11:45 | 49.968
2020-10-14 | 11:45 | 49.97
2020-10-14 | 11:45 | 49.97
2020-10-14 | 11:45 | 49.972
2020-10-14 | 11:45 | 49.974
2020-10-14 | 11:45 | 49.976
2020-10-14 | 11:45 | 49.976
2020-10-14 | 11:45 | 49.974
2020-10-14 | 11:45 | 49.97
2020-10-14 | 11:45 | 49.968
2020-10-14 | 11:45 | 49.968
2020-10-14 | 11:45 | 49.967
2020-10-14 | 11:45 | 49.967
2020-10-14 | 11:45 | 49.967
2020-10-14 | 11:45 | 49.966
2020-10-14 | 11:46 | 49.966
2020-10-14 | 11:46 | 49.965
2020-10-14 | 11:46 | 49.963
2020-10-14 | 11:46 | 49.959
2020-10-14 | 11:46 | 49.955
2020-10-14 | 11:46 | 49.951
2020-10-14 | 11:46 | 49.949
2020-10-14 | 11:46 | 49.945
2020-10-14 | 11:46 | 49.942
2020-10-14 | 11:46 | 49.937
2020-10-14 | 11:46 | 49.935
2020-10-14 | 11:46 | 49.934
2020-10-14 | 11:46 | 49.934
2020-10-14 | 11:46 | 49.935
2020-10-14 | 11:46 | 49.936
2020-10-14 | 11:46 | 49.938
2020-10-14 | 11:46 | 49.939
2020-10-14 | 11:46 | 49.942
2020-10-14 | 11:46 | 49.942
2020-10-14 | 11:46 | 49.943
2020-10-14 | 11:46 | 49.942
2020-10-14 | 11:46 | 49.942
2020-10-14 | 11:46 | 49.941
2020-10-14 | 11:46 | 49.938
2020-10-14 | 11:46 | 49.936
2020-10-14 | 11:46 | 49.933
2020-10-14 | 11:46 | 49.932
2020-10-14 | 11:46 | 49.931
2020-10-14 | 11:46 | 49.93
2020-10-14 | 11:46 | 49.93
2020-10-14 | 11:46 | 49.928
2020-10-14 | 11:46 | 49.928
2020-10-14 | 11:46 | 49.925
2020-10-14 | 11:46 | 49.925
2020-10-14 | 11:46 | 49.924
2020-10-14 | 11:46 | 49.924
2020-10-14 | 11:46 | 49.923
2020-10-14 | 11:46 | 49.922
2020-10-14 | 11:46 | 49.92
2020-10-14 | 11:46 | 49.918
2020-10-14 | 11:46 | 49.917
2020-10-14 | 11:46 | 49.915
2020-10-14 | 11:46 | 49.911
2020-10-14 | 11:46 | 49.907
2020-10-14 | 11:46 | 49.906
2020-10-14 | 11:46 | 49.905
2020-10-14 | 11:46 | 49.907
2020-10-14 | 11:46 | 49.908
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.911
2020-10-14 | 11:46 | 49.912
2020-10-14 | 11:46 | 49.911
2020-10-14 | 11:46 | 49.911
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.909
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.91
2020-10-14 | 11:46 | 49.911
2020-10-14 | 11:47 | 49.909
2020-10-14 | 11:47 | 49.91
2020-10-14 | 11:47 | 49.91
2020-10-14 | 11:47 | 49.912
2020-10-14 | 11:47 | 49.913
2020-10-14 | 11:47 | 49.916
2020-10-14 | 11:47 | 49.919
2020-10-14 | 11:47 | 49.923
2020-10-14 | 11:47 | 49.927
2020-10-14 | 11:47 | 49.93
2020-10-14 | 11:47 | 49.933
2020-10-14 | 11:47 | 49.937
2020-10-14 | 11:47 | 49.939
2020-10-14 | 11:47 | 49.942
2020-10-14 | 11:47 | 49.944
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.947
2020-10-14 | 11:47 | 49.947
2020-10-14 | 11:47 | 49.947
2020-10-14 | 11:47 | 49.947
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.944
2020-10-14 | 11:47 | 49.944
2020-10-14 | 11:47 | 49.943
2020-10-14 | 11:47 | 49.943
2020-10-14 | 11:47 | 49.942
2020-10-14 | 11:47 | 49.941
2020-10-14 | 11:47 | 49.94
2020-10-14 | 11:47 | 49.939
2020-10-14 | 11:47 | 49.94
2020-10-14 | 11:47 | 49.942
2020-10-14 | 11:47 | 49.943
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.945
2020-10-14 | 11:47 | 49.947
2020-10-14 | 11:47 | 49.949
2020-10-14 | 11:47 | 49.951
2020-10-14 | 11:47 | 49.954
2020-10-14 | 11:47 | 49.958
2020-10-14 | 11:47 | 49.963
2020-10-14 | 11:47 | 49.966
2020-10-14 | 11:47 | 49.968
2020-10-14 | 11:47 | 49.969
2020-10-14 | 11:47 | 49.968
2020-10-14 | 11:47 | 49.968
2020-10-14 | 11:47 | 49.968
2020-10-14 | 11:47 | 49.965
2020-10-14 | 11:47 | 49.964
2020-10-14 | 11:47 | 49.962
2020-10-14 | 11:47 | 49.962
2020-10-14 | 11:47 | 49.961
2020-10-14 | 11:47 | 49.96
2020-10-14 | 11:47 | 49.961
2020-10-14 | 11:47 | 49.962
2020-10-14 | 11:47 | 49.963
2020-10-14 | 11:47 | 49.963
2020-10-14 | 11:48 | 49.964
2020-10-14 | 11:48 | 49.965
2020-10-14 | 11:48 | 49.965
2020-10-14 | 11:48 | 49.965
2020-10-14 | 11:48 | 49.965
2020-10-14 | 11:48 | 49.965
2020-10-14 | 11:48 | 49.965
2020-10-14 | 11:48 | 49.964
2020-10-14 | 11:48 | 49.964
2020-10-14 | 11:48 | 49.962
2020-10-14 | 11:48 | 49.96
2020-10-14 | 11:48 | 49.958
2020-10-14 | 11:48 | 49.956
2020-10-14 | 11:48 | 49.955
2020-10-14 | 11:48 | 49.954
2020-10-14 | 11:48 | 49.954
2020-10-14 | 11:48 | 49.955
2020-10-14 | 11:48 | 49.955
2020-10-14 | 11:48 | 49.957
2020-10-14 | 11:48 | 49.958
2020-10-14 | 11:48 | 49.961
2020-10-14 | 11:48 | 49.963
2020-10-14 | 11:48 | 49.966
2020-10-14 | 11:48 | 49.968
2020-10-14 | 11:48 | 49.972
2020-10-14 | 11:48 | 49.978
2020-10-14 | 11:48 | 49.983
2020-10-14 | 11:48 | 49.986
2020-10-14 | 11:48 | 49.987
2020-10-14 | 11:48 | 49.987
2020-10-14 | 11:48 | 49.987
2020-10-14 | 11:48 | 49.985
2020-10-14 | 11:48 | 49.986
2020-10-14 | 11:48 | 49.983
2020-10-14 | 11:48 | 49.982
2020-10-14 | 11:48 | 49.982
2020-10-14 | 11:48 | 49.98
2020-10-14 | 11:48 | 49.979
2020-10-14 | 11:48 | 49.978
2020-10-14 | 11:48 | 49.977
2020-10-14 | 11:48 | 49.977
2020-10-14 | 11:48 | 49.976
2020-10-14 | 11:48 | 49.976
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.972
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.976
2020-10-14 | 11:48 | 49.976
2020-10-14 | 11:48 | 49.975
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:48 | 49.974
2020-10-14 | 11:49 | 49.973
2020-10-14 | 11:49 | 49.973
2020-10-14 | 11:49 | 49.972
2020-10-14 | 11:49 | 49.974
2020-10-14 | 11:49 | 49.974
2020-10-14 | 11:49 | 49.975
2020-10-14 | 11:49 | 49.977
2020-10-14 | 11:49 | 49.978
2020-10-14 | 11:49 | 49.98
2020-10-14 | 11:49 | 49.981
2020-10-14 | 11:49 | 49.981
2020-10-14 | 11:49 | 49.979
2020-10-14 | 11:49 | 49.978
2020-10-14 | 11:49 | 49.98
2020-10-14 | 11:49 | 49.983
2020-10-14 | 11:49 | 49.985
2020-10-14 | 11:49 | 49.988
2020-10-14 | 11:49 | 49.991
2020-10-14 | 11:49 | 49.992
2020-10-14 | 11:49 | 49.994
2020-10-14 | 11:49 | 49.995
2020-10-14 | 11:49 | 49.997
2020-10-14 | 11:49 | 49.997
2020-10-14 | 11:49 | 49.995
2020-10-14 | 11:49 | 49.994
2020-10-14 | 11:49 | 49.992
2020-10-14 | 11:49 | 49.991
2020-10-14 | 11:49 | 49.989
2020-10-14 | 11:49 | 49.987
2020-10-14 | 11:49 | 49.985
2020-10-14 | 11:49 | 49.984
2020-10-14 | 11:49 | 49.98
2020-10-14 | 11:49 | 49.978
2020-10-14 | 11:49 | 49.975
2020-10-14 | 11:49 | 49.972
2020-10-14 | 11:49 | 49.969
2020-10-14 | 11:49 | 49.965
2020-10-14 | 11:49 | 49.962
2020-10-14 | 11:49 | 49.959
2020-10-14 | 11:49 | 49.957
2020-10-14 | 11:49 | 49.957
2020-10-14 | 11:49 | 49.956
2020-10-14 | 11:49 | 49.955
2020-10-14 | 11:49 | 49.955
2020-10-14 | 11:49 | 49.955
2020-10-14 | 11:49 | 49.955
2020-10-14 | 11:49 | 49.955
2020-10-14 | 11:49 | 49.954
2020-10-14 | 11:49 | 49.955
2020-10-14 | 11:49 | 49.957
2020-10-14 | 11:49 | 49.959
2020-10-14 | 11:49 | 49.959
2020-10-14 | 11:49 | 49.96
2020-10-14 | 11:49 | 49.961
2020-10-14 | 11:49 | 49.962
2020-10-14 | 11:49 | 49.965
2020-10-14 | 11:49 | 49.965
2020-10-14 | 11:49 | 49.967
2020-10-14 | 11:49 | 49.969
2020-10-14 | 11:50 | 49.971
2020-10-14 | 11:50 | 49.973
2020-10-14 | 11:50 | 49.973
2020-10-14 | 11:50 | 49.973
2020-10-14 | 11:50 | 49.972
2020-10-14 | 11:50 | 49.972
2020-10-14 | 11:50 | 49.972
2020-10-14 | 11:50 | 49.972
2020-10-14 | 11:50 | 49.971
2020-10-14 | 11:50 | 49.971
2020-10-14 | 11:50 | 49.971
2020-10-14 | 11:50 | 49.97
2020-10-14 | 11:50 | 49.971
2020-10-14 | 11:50 | 49.972
2020-10-14 | 11:50 | 49.974
2020-10-14 | 11:50 | 49.975
2020-10-14 | 11:50 | 49.979
2020-10-14 | 11:50 | 49.98
2020-10-14 | 11:50 | 49.983
2020-10-14 | 11:50 | 49.985
2020-10-14 | 11:50 | 49.987
2020-10-14 | 11:50 | 49.991
2020-10-14 | 11:50 | 49.992
2020-10-14 | 11:50 | 49.996
2020-10-14 | 11:50 | 50
2020-10-14 | 11:50 | 50.003
2020-10-14 | 11:50 | 50.007
2020-10-14 | 11:50 | 50.01
2020-10-14 | 11:50 | 50.012
2020-10-14 | 11:50 | 50.012
2020-10-14 | 11:50 | 50.014
2020-10-14 | 11:50 | 50.015
2020-10-14 | 11:50 | 50.015
2020-10-14 | 11:50 | 50.014
2020-10-14 | 11:50 | 50.013
2020-10-14 | 11:50 | 50.012
2020-10-14 | 11:50 | 50.011
2020-10-14 | 11:50 | 50.011
2020-10-14 | 11:50 | 50.008
2020-10-14 | 11:50 | 50.005
2020-10-14 | 11:50 | 50.002
2020-10-14 | 11:50 | 49.999
2020-10-14 | 11:50 | 49.995
2020-10-14 | 11:50 | 49.992
2020-10-14 | 11:50 | 49.988
2020-10-14 | 11:50 | 49.986
2020-10-14 | 11:50 | 49.983
2020-10-14 | 11:50 | 49.982
2020-10-14 | 11:50 | 49.98
2020-10-14 | 11:50 | 49.979
2020-10-14 | 11:50 | 49.98
2020-10-14 | 11:50 | 49.981
2020-10-14 | 11:50 | 49.982
2020-10-14 | 11:50 | 49.982
2020-10-14 | 11:50 | 49.983
2020-10-14 | 11:50 | 49.984
2020-10-14 | 11:50 | 49.985
2020-10-14 | 11:50 | 49.987
2020-10-14 | 11:50 | 49.987
2020-10-14 | 11:50 | 49.988
2020-10-14 | 11:50 | 49.987
2020-10-14 | 11:51 | 49.986
2020-10-14 | 11:51 | 49.985
2020-10-14 | 11:51 | 49.982
2020-10-14 | 11:51 | 49.981
2020-10-14 | 11:51 | 49.98
2020-10-14 | 11:51 | 49.98
2020-10-14 | 11:51 | 49.981
2020-10-14 | 11:51 | 49.98
2020-10-14 | 11:51 | 49.98
2020-10-14 | 11:51 | 49.979
2020-10-14 | 11:51 | 49.979
2020-10-14 | 11:51 | 49.979
2020-10-14 | 11:51 | 49.978
2020-10-14 | 11:51 | 49.978
2020-10-14 | 11:51 | 49.977
2020-10-14 | 11:51 | 49.978
2020-10-14 | 11:51 | 49.979
2020-10-14 | 11:51 | 49.979
2020-10-14 | 11:51 | 49.977
2020-10-14 | 11:51 | 49.975
2020-10-14 | 11:51 | 49.973
2020-10-14 | 11:51 | 49.974
2020-10-14 | 11:51 | 49.972
2020-10-14 | 11:51 | 49.973
2020-10-14 | 11:51 | 49.969
2020-10-14 | 11:51 | 49.969
2020-10-14 | 11:51 | 49.967
2020-10-14 | 11:51 | 49.965
2020-10-14 | 11:51 | 49.962
2020-10-14 | 11:51 | 49.96
2020-10-14 | 11:51 | 49.957
2020-10-14 | 11:51 | 49.958
2020-10-14 | 11:51 | 49.956
2020-10-14 | 11:51 | 49.957
2020-10-14 | 11:51 | 49.954
2020-10-14 | 11:51 | 49.955
2020-10-14 | 11:51 | 49.953
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.95
2020-10-14 | 11:51 | 49.95
2020-10-14 | 11:51 | 49.95
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.952
2020-10-14 | 11:51 | 49.952
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.95
2020-10-14 | 11:51 | 49.949
2020-10-14 | 11:51 | 49.948
2020-10-14 | 11:51 | 49.949
2020-10-14 | 11:51 | 49.949
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.951
2020-10-14 | 11:51 | 49.952
2020-10-14 | 11:51 | 49.953
2020-10-14 | 11:51 | 49.954
2020-10-14 | 11:51 | 49.956
2020-10-14 | 11:51 | 49.956
2020-10-14 | 11:52 | 49.954
2020-10-14 | 11:52 | 49.954
2020-10-14 | 11:52 | 49.952
2020-10-14 | 11:52 | 49.952
2020-10-14 | 11:52 | 49.953
2020-10-14 | 11:52 | 49.954
2020-10-14 | 11:52 | 49.955
2020-10-14 | 11:52 | 49.955
2020-10-14 | 11:52 | 49.953
2020-10-14 | 11:52 | 49.952
2020-10-14 | 11:52 | 49.951
2020-10-14 | 11:52 | 49.951
2020-10-14 | 11:52 | 49.95
2020-10-14 | 11:52 | 49.949
2020-10-14 | 11:52 | 49.949
2020-10-14 | 11:52 | 49.95
2020-10-14 | 11:52 | 49.95
2020-10-14 | 11:52 | 49.95
2020-10-14 | 11:52 | 49.952
2020-10-14 | 11:52 | 49.951
2020-10-14 | 11:52 | 49.951
2020-10-14 | 11:52 | 49.951
2020-10-14 | 11:52 | 49.953
2020-10-14 | 11:52 | 49.957
2020-10-14 | 11:52 | 49.959
2020-10-14 | 11:52 | 49.964
2020-10-14 | 11:52 | 49.969
2020-10-14 | 11:52 | 49.974
2020-10-14 | 11:52 | 49.977
2020-10-14 | 11:52 | 49.979
2020-10-14 | 11:52 | 49.98
2020-10-14 | 11:52 | 49.98
2020-10-14 | 11:52 | 49.981
2020-10-14 | 11:52 | 49.981
2020-10-14 | 11:52 | 49.981
2020-10-14 | 11:52 | 49.98
2020-10-14 | 11:52 | 49.979
2020-10-14 | 11:52 | 49.976
2020-10-14 | 11:52 | 49.974
2020-10-14 | 11:52 | 49.972
2020-10-14 | 11:52 | 49.971
2020-10-14 | 11:52 | 49.969
2020-10-14 | 11:52 | 49.969
2020-10-14 | 11:52 | 49.968
2020-10-14 | 11:52 | 49.967
2020-10-14 | 11:52 | 49.965
2020-10-14 | 11:52 | 49.965
2020-10-14 | 11:52 | 49.964
2020-10-14 | 11:52 | 49.964
2020-10-14 | 11:52 | 49.963
2020-10-14 | 11:52 | 49.963
2020-10-14 | 11:52 | 49.963
2020-10-14 | 11:52 | 49.964
2020-10-14 | 11:52 | 49.966
2020-10-14 | 11:52 | 49.966
2020-10-14 | 11:52 | 49.968
2020-10-14 | 11:52 | 49.97
2020-10-14 | 11:52 | 49.971
2020-10-14 | 11:52 | 49.973
2020-10-14 | 11:52 | 49.976
2020-10-14 | 11:52 | 49.979
2020-10-14 | 11:53 | 49.981
2020-10-14 | 11:53 | 49.984
2020-10-14 | 11:53 | 49.986
2020-10-14 | 11:53 | 49.986
2020-10-14 | 11:53 | 49.985
2020-10-14 | 11:53 | 49.984
2020-10-14 | 11:53 | 49.981
2020-10-14 | 11:53 | 49.98
2020-10-14 | 11:53 | 49.981
2020-10-14 | 11:53 | 49.981
2020-10-14 | 11:53 | 49.982
2020-10-14 | 11:53 | 49.98
2020-10-14 | 11:53 | 49.981
2020-10-14 | 11:53 | 49.982
2020-10-14 | 11:53 | 49.983
2020-10-14 | 11:53 | 49.983
2020-10-14 | 11:53 | 49.985
2020-10-14 | 11:53 | 49.984
2020-10-14 | 11:53 | 49.984
2020-10-14 | 11:53 | 49.985
2020-10-14 | 11:53 | 49.986
2020-10-14 | 11:53 | 49.983
2020-10-14 | 11:53 | 49.983
2020-10-14 | 11:53 | 49.98
2020-10-14 | 11:53 | 49.979
2020-10-14 | 11:53 | 49.977
2020-10-14 | 11:53 | 49.975
2020-10-14 | 11:53 | 49.975
2020-10-14 | 11:53 | 49.976
2020-10-14 | 11:53 | 49.977
2020-10-14 | 11:53 | 49.975
2020-10-14 | 11:53 | 49.974
2020-10-14 | 11:53 | 49.973
2020-10-14 | 11:53 | 49.972
2020-10-14 | 11:53 | 49.972
2020-10-14 | 11:53 | 49.972
2020-10-14 | 11:53 | 49.97
2020-10-14 | 11:53 | 49.97
2020-10-14 | 11:53 | 49.971
2020-10-14 | 11:53 | 49.974
2020-10-14 | 11:53 | 49.975
2020-10-14 | 11:53 | 49.975
2020-10-14 | 11:53 | 49.974
2020-10-14 | 11:53 | 49.973
2020-10-14 | 11:53 | 49.974
2020-10-14 | 11:53 | 49.973
2020-10-14 | 11:53 | 49.973
2020-10-14 | 11:53 | 49.973
2020-10-14 | 11:53 | 49.969
2020-10-14 | 11:53 | 49.966
2020-10-14 | 11:53 | 49.962
2020-10-14 | 11:53 | 49.96
2020-10-14 | 11:53 | 49.959
2020-10-14 | 11:53 | 49.956
2020-10-14 | 11:53 | 49.955
2020-10-14 | 11:53 | 49.952
2020-10-14 | 11:53 | 49.951
2020-10-14 | 11:53 | 49.951
2020-10-14 | 11:53 | 49.951
2020-10-14 | 11:54 | 49.952
2020-10-14 | 11:54 | 49.954
2020-10-14 | 11:54 | 49.955
2020-10-14 | 11:54 | 49.954
2020-10-14 | 11:54 | 49.955
2020-10-14 | 11:54 | 49.956
2020-10-14 | 11:54 | 49.957
2020-10-14 | 11:54 | 49.959
2020-10-14 | 11:54 | 49.961
2020-10-14 | 11:54 | 49.961
2020-10-14 | 11:54 | 49.963
2020-10-14 | 11:54 | 49.963
2020-10-14 | 11:54 | 49.966
2020-10-14 | 11:54 | 49.966
2020-10-14 | 11:54 | 49.968
2020-10-14 | 11:54 | 49.968
2020-10-14 | 11:54 | 49.968
2020-10-14 | 11:54 | 49.969
2020-10-14 | 11:54 | 49.97
2020-10-14 | 11:54 | 49.97
2020-10-14 | 11:54 | 49.973
2020-10-14 | 11:54 | 49.973
2020-10-14 | 11:54 | 49.972
2020-10-14 | 11:54 | 49.971
2020-10-14 | 11:54 | 49.97
2020-10-14 | 11:54 | 49.967
2020-10-14 | 11:54 | 49.966
2020-10-14 | 11:54 | 49.964
2020-10-14 | 11:54 | 49.964
2020-10-14 | 11:54 | 49.965
2020-10-14 | 11:54 | 49.965
2020-10-14 | 11:54 | 49.964
2020-10-14 | 11:54 | 49.962
2020-10-14 | 11:54 | 49.962
2020-10-14 | 11:54 | 49.96
2020-10-14 | 11:54 | 49.958
2020-10-14 | 11:54 | 49.956
2020-10-14 | 11:54 | 49.954
2020-10-14 | 11:54 | 49.953
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.948
2020-10-14 | 11:54 | 49.947
2020-10-14 | 11:54 | 49.944
2020-10-14 | 11:54 | 49.942
2020-10-14 | 11:54 | 49.944
2020-10-14 | 11:54 | 49.944
2020-10-14 | 11:54 | 49.946
2020-10-14 | 11:54 | 49.948
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.95
2020-10-14 | 11:54 | 49.952
2020-10-14 | 11:54 | 49.951
2020-10-14 | 11:54 | 49.954
2020-10-14 | 11:54 | 49.953
2020-10-14 | 11:54 | 49.953
2020-10-14 | 11:54 | 49.954
2020-10-14 | 11:54 | 49.954
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.953
2020-10-14 | 11:55 | 49.955
2020-10-14 | 11:55 | 49.956
2020-10-14 | 11:55 | 49.957
2020-10-14 | 11:55 | 49.958
2020-10-14 | 11:55 | 49.957
2020-10-14 | 11:55 | 49.955
2020-10-14 | 11:55 | 49.955
2020-10-14 | 11:55 | 49.955
2020-10-14 | 11:55 | 49.955
2020-10-14 | 11:55 | 49.953
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.951
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.948
2020-10-14 | 11:55 | 49.945
2020-10-14 | 11:55 | 49.944
2020-10-14 | 11:55 | 49.942
2020-10-14 | 11:55 | 49.941
2020-10-14 | 11:55 | 49.941
2020-10-14 | 11:55 | 49.941
2020-10-14 | 11:55 | 49.941
2020-10-14 | 11:55 | 49.943
2020-10-14 | 11:55 | 49.946
2020-10-14 | 11:55 | 49.947
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.951
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.952
2020-10-14 | 11:55 | 49.953
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.953
2020-10-14 | 11:55 | 49.952
2020-10-14 | 11:55 | 49.951
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.949
2020-10-14 | 11:55 | 49.949
2020-10-14 | 11:55 | 49.949
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.951
2020-10-14 | 11:55 | 49.952
2020-10-14 | 11:55 | 49.953
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.954
2020-10-14 | 11:55 | 49.952
2020-10-14 | 11:55 | 49.95
2020-10-14 | 11:55 | 49.948
2020-10-14 | 11:55 | 49.946
2020-10-14 | 11:55 | 49.945
2020-10-14 | 11:55 | 49.942
2020-10-14 | 11:55 | 49.941
2020-10-14 | 11:55 | 49.942
2020-10-14 | 11:55 | 49.939
2020-10-14 | 11:55 | 49.938
2020-10-14 | 11:56 | 49.936
2020-10-14 | 11:56 | 49.936
2020-10-14 | 11:56 | 49.934
2020-10-14 | 11:56 | 49.932
2020-10-14 | 11:56 | 49.931
2020-10-14 | 11:56 | 49.93
2020-10-14 | 11:56 | 49.93
2020-10-14 | 11:56 | 49.932
2020-10-14 | 11:56 | 49.934
2020-10-14 | 11:56 | 49.935
2020-10-14 | 11:56 | 49.937
2020-10-14 | 11:56 | 49.939
2020-10-14 | 11:56 | 49.941
2020-10-14 | 11:56 | 49.944
2020-10-14 | 11:56 | 49.945
2020-10-14 | 11:56 | 49.946
2020-10-14 | 11:56 | 49.945
2020-10-14 | 11:56 | 49.947
2020-10-14 | 11:56 | 49.948
2020-10-14 | 11:56 | 49.949
2020-10-14 | 11:56 | 49.95
2020-10-14 | 11:56 | 49.948
2020-10-14 | 11:56 | 49.948
2020-10-14 | 11:56 | 49.947
2020-10-14 | 11:56 | 49.944
2020-10-14 | 11:56 | 49.944
2020-10-14 | 11:56 | 49.941
2020-10-14 | 11:56 | 49.939
2020-10-14 | 11:56 | 49.937
2020-10-14 | 11:56 | 49.937
2020-10-14 | 11:56 | 49.938
2020-10-14 | 11:56 | 49.935
2020-10-14 | 11:56 | 49.93
2020-10-14 | 11:56 | 49.926
2020-10-14 | 11:56 | 49.923
2020-10-14 | 11:56 | 49.92
2020-10-14 | 11:56 | 49.919
2020-10-14 | 11:56 | 49.916
2020-10-14 | 11:56 | 49.914
2020-10-14 | 11:56 | 49.912
2020-10-14 | 11:56 | 49.913
2020-10-14 | 11:56 | 49.912
2020-10-14 | 11:56 | 49.912
2020-10-14 | 11:56 | 49.913
2020-10-14 | 11:56 | 49.913
2020-10-14 | 11:56 | 49.914
2020-10-14 | 11:56 | 49.914
2020-10-14 | 11:56 | 49.914
2020-10-14 | 11:56 | 49.913
2020-10-14 | 11:56 | 49.915
2020-10-14 | 11:56 | 49.918
2020-10-14 | 11:56 | 49.919
2020-10-14 | 11:56 | 49.921
2020-10-14 | 11:56 | 49.923
2020-10-14 | 11:56 | 49.924
2020-10-14 | 11:56 | 49.925
2020-10-14 | 11:56 | 49.925
2020-10-14 | 11:56 | 49.924
2020-10-14 | 11:56 | 49.924
2020-10-14 | 11:56 | 49.923
2020-10-14 | 11:56 | 49.924
2020-10-14 | 11:57 | 49.923
2020-10-14 | 11:57 | 49.924
2020-10-14 | 11:57 | 49.924
2020-10-14 | 11:57 | 49.924
2020-10-14 | 11:57 | 49.926
2020-10-14 | 11:57 | 49.926
2020-10-14 | 11:57 | 49.928
2020-10-14 | 11:57 | 49.927
2020-10-14 | 11:57 | 49.927
2020-10-14 | 11:57 | 49.927
2020-10-14 | 11:57 | 49.926
2020-10-14 | 11:57 | 49.924
2020-10-14 | 11:57 | 49.923
2020-10-14 | 11:57 | 49.921
2020-10-14 | 11:57 | 49.919
2020-10-14 | 11:57 | 49.917
2020-10-14 | 11:57 | 49.916
2020-10-14 | 11:57 | 49.914
2020-10-14 | 11:57 | 49.913
2020-10-14 | 11:57 | 49.911
2020-10-14 | 11:57 | 49.909
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:57 | 49.904
2020-10-14 | 11:57 | 49.903
2020-10-14 | 11:57 | 49.902
2020-10-14 | 11:57 | 49.903
2020-10-14 | 11:57 | 49.902
2020-10-14 | 11:57 | 49.905
2020-10-14 | 11:57 | 49.904
2020-10-14 | 11:57 | 49.905
2020-10-14 | 11:57 | 49.905
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:57 | 49.905
2020-10-14 | 11:57 | 49.904
2020-10-14 | 11:57 | 49.9
2020-10-14 | 11:57 | 49.901
2020-10-14 | 11:57 | 49.901
2020-10-14 | 11:57 | 49.901
2020-10-14 | 11:57 | 49.9
2020-10-14 | 11:57 | 49.899
2020-10-14 | 11:57 | 49.899
2020-10-14 | 11:57 | 49.899
2020-10-14 | 11:57 | 49.9
2020-10-14 | 11:57 | 49.904
2020-10-14 | 11:57 | 49.905
2020-10-14 | 11:57 | 49.905
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:57 | 49.907
2020-10-14 | 11:57 | 49.908
2020-10-14 | 11:57 | 49.91
2020-10-14 | 11:57 | 49.91
2020-10-14 | 11:57 | 49.91
2020-10-14 | 11:57 | 49.909
2020-10-14 | 11:57 | 49.909
2020-10-14 | 11:57 | 49.907
2020-10-14 | 11:57 | 49.906
2020-10-14 | 11:58 | 49.905
2020-10-14 | 11:58 | 49.903
2020-10-14 | 11:58 | 49.904
2020-10-14 | 11:58 | 49.903
2020-10-14 | 11:58 | 49.902
2020-10-14 | 11:58 | 49.902
2020-10-14 | 11:58 | 49.902
2020-10-14 | 11:58 | 49.902
2020-10-14 | 11:58 | 49.904
2020-10-14 | 11:58 | 49.903
2020-10-14 | 11:58 | 49.903
2020-10-14 | 11:58 | 49.903
2020-10-14 | 11:58 | 49.904
2020-10-14 | 11:58 | 49.906
2020-10-14 | 11:58 | 49.908
2020-10-14 | 11:58 | 49.91
2020-10-14 | 11:58 | 49.91
2020-10-14 | 11:58 | 49.912
2020-10-14 | 11:58 | 49.914
2020-10-14 | 11:58 | 49.912
2020-10-14 | 11:58 | 49.912
2020-10-14 | 11:58 | 49.914
2020-10-14 | 11:58 | 49.915
2020-10-14 | 11:58 | 49.916
2020-10-14 | 11:58 | 49.918
2020-10-14 | 11:58 | 49.919
2020-10-14 | 11:58 | 49.922
2020-10-14 | 11:58 | 49.923
2020-10-14 | 11:58 | 49.925
2020-10-14 | 11:58 | 49.926
2020-10-14 | 11:58 | 49.927
2020-10-14 | 11:58 | 49.927
2020-10-14 | 11:58 | 49.928
2020-10-14 | 11:58 | 49.93
2020-10-14 | 11:58 | 49.93
2020-10-14 | 11:58 | 49.931
2020-10-14 | 11:58 | 49.93
2020-10-14 | 11:58 | 49.929
2020-10-14 | 11:58 | 49.926
2020-10-14 | 11:58 | 49.925
2020-10-14 | 11:58 | 49.925
2020-10-14 | 11:58 | 49.927
2020-10-14 | 11:58 | 49.927
2020-10-14 | 11:58 | 49.927
2020-10-14 | 11:58 | 49.929
2020-10-14 | 11:58 | 49.93
2020-10-14 | 11:58 | 49.932
2020-10-14 | 11:58 | 49.934
2020-10-14 | 11:58 | 49.936
2020-10-14 | 11:58 | 49.937
2020-10-14 | 11:58 | 49.937
2020-10-14 | 11:58 | 49.939
2020-10-14 | 11:58 | 49.939
2020-10-14 | 11:58 | 49.938
2020-10-14 | 11:58 | 49.935
2020-10-14 | 11:58 | 49.934
2020-10-14 | 11:58 | 49.935
2020-10-14 | 11:58 | 49.933
2020-10-14 | 11:58 | 49.933
2020-10-14 | 11:58 | 49.934
2020-10-14 | 11:58 | 49.935
2020-10-14 | 11:59 | 49.934
2020-10-14 | 11:59 | 49.933
2020-10-14 | 11:59 | 49.931
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.929
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.931
2020-10-14 | 11:59 | 49.932
2020-10-14 | 11:59 | 49.931
2020-10-14 | 11:59 | 49.933
2020-10-14 | 11:59 | 49.932
2020-10-14 | 11:59 | 49.932
2020-10-14 | 11:59 | 49.932
2020-10-14 | 11:59 | 49.936
2020-10-14 | 11:59 | 49.936
2020-10-14 | 11:59 | 49.938
2020-10-14 | 11:59 | 49.938
2020-10-14 | 11:59 | 49.938
2020-10-14 | 11:59 | 49.937
2020-10-14 | 11:59 | 49.934
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.926
2020-10-14 | 11:59 | 49.923
2020-10-14 | 11:59 | 49.924
2020-10-14 | 11:59 | 49.922
2020-10-14 | 11:59 | 49.924
2020-10-14 | 11:59 | 49.924
2020-10-14 | 11:59 | 49.926
2020-10-14 | 11:59 | 49.924
2020-10-14 | 11:59 | 49.926
2020-10-14 | 11:59 | 49.929
2020-10-14 | 11:59 | 49.933
2020-10-14 | 11:59 | 49.933
2020-10-14 | 11:59 | 49.936
2020-10-14 | 11:59 | 49.936
2020-10-14 | 11:59 | 49.937
2020-10-14 | 11:59 | 49.936
2020-10-14 | 11:59 | 49.935
2020-10-14 | 11:59 | 49.932
2020-10-14 | 11:59 | 49.932
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.931
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.929
2020-10-14 | 11:59 | 49.929
2020-10-14 | 11:59 | 49.929
2020-10-14 | 11:59 | 49.93
2020-10-14 | 11:59 | 49.931
2020-10-14 | 11:59 | 49.933
2020-10-14 | 11:59 | 49.935
2020-10-14 | 11:59 | 49.938
2020-10-14 | 11:59 | 49.939
2020-10-14 | 11:59 | 49.943
2020-10-14 | 11:59 | 49.942
2020-10-14 | 11:59 | 49.944
2020-10-14 | 11:59 | 49.944
2020-10-14 | 12:00 | 49.945
2020-10-14 | 12:00 | 49.945
2020-10-14 | 12:00 | 49.946
2020-10-14 | 12:00 | 49.948
2020-10-14 | 12:00 | 49.95
2020-10-14 | 12:00 | 49.953
2020-10-14 | 12:00 | 49.956
2020-10-14 | 12:00 | 49.96
2020-10-14 | 12:00 | 49.963
2020-10-14 | 12:00 | 49.965
2020-10-14 | 12:00 | 49.966
2020-10-14 | 12:00 | 49.966
2020-10-14 | 12:00 | 49.968
2020-10-14 | 12:00 | 49.968
2020-10-14 | 12:00 | 49.97
2020-10-14 | 12:00 | 49.971
2020-10-14 | 12:00 | 49.973
2020-10-14 | 12:00 | 49.975
2020-10-14 | 12:00 | 49.977
2020-10-14 | 12:00 | 49.977
2020-10-14 | 12:00 | 49.975
2020-10-14 | 12:00 | 49.972
2020-10-14 | 12:00 | 49.97
2020-10-14 | 12:00 | 49.969
2020-10-14 | 12:00 | 49.967
2020-10-14 | 12:00 | 49.967
2020-10-14 | 12:00 | 49.966
2020-10-14 | 12:00 | 49.968
2020-10-14 | 12:00 | 49.97
2020-10-14 | 12:00 | 49.971
2020-10-14 | 12:00 | 49.973
2020-10-14 | 12:00 | 49.971
2020-10-14 | 12:00 | 49.97
2020-10-14 | 12:00 | 49.968
2020-10-14 | 12:00 | 49.969
2020-10-14 | 12:00 | 49.969
2020-10-14 | 12:00 | 49.972
2020-10-14 | 12:00 | 49.974
2020-10-14 | 12:00 | 49.975
2020-10-14 | 12:00 | 49.976
2020-10-14 | 12:00 | 49.976
2020-10-14 | 12:00 | 49.974
2020-10-14 | 12:00 | 49.974
2020-10-14 | 12:00 | 49.974
2020-10-14 | 12:00 | 49.971
2020-10-14 | 12:00 | 49.969
2020-10-14 | 12:00 | 49.968
2020-10-14 | 12:00 | 49.965
2020-10-14 | 12:00 | 49.963
2020-10-14 | 12:00 | 49.962
2020-10-14 | 12:00 | 49.961
2020-10-14 | 12:00 | 49.96
2020-10-14 | 12:00 | 49.96
2020-10-14 | 12:00 | 49.96
2020-10-14 | 12:00 | 49.961
2020-10-14 | 12:00 | 49.96
2020-10-14 | 12:00 | 49.961
2020-10-14 | 12:00 | 49.963
2020-10-14 | 12:00 | 49.965
2020-10-14 | 12:00 | 49.966
2020-10-14 | 12:00 | 49.968
2020-10-14 | 12:01 | 49.969
2020-10-14 | 12:01 | 49.971
2020-10-14 | 12:01 | 49.973
2020-10-14 | 12:01 | 49.976
2020-10-14 | 12:01 | 49.976
2020-10-14 | 12:01 | 49.979
2020-10-14 | 12:01 | 49.977
2020-10-14 | 12:01 | 49.978
2020-10-14 | 12:01 | 49.979
2020-10-14 | 12:01 | 49.98
2020-10-14 | 12:01 | 49.981
2020-10-14 | 12:01 | 49.983
2020-10-14 | 12:01 | 49.986
2020-10-14 | 12:01 | 49.988
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.989
2020-10-14 | 12:01 | 49.988
2020-10-14 | 12:01 | 49.986
2020-10-14 | 12:01 | 49.984
2020-10-14 | 12:01 | 49.984
2020-10-14 | 12:01 | 49.984
2020-10-14 | 12:01 | 49.986
2020-10-14 | 12:01 | 49.986
2020-10-14 | 12:01 | 49.988
2020-10-14 | 12:01 | 49.986
2020-10-14 | 12:01 | 49.984
2020-10-14 | 12:01 | 49.983
2020-10-14 | 12:01 | 49.982
2020-10-14 | 12:01 | 49.98
2020-10-14 | 12:01 | 49.98
2020-10-14 | 12:01 | 49.981
2020-10-14 | 12:01 | 49.981
2020-10-14 | 12:01 | 49.98
2020-10-14 | 12:01 | 49.981
2020-10-14 | 12:01 | 49.983
2020-10-14 | 12:01 | 49.984
2020-10-14 | 12:01 | 49.986
2020-10-14 | 12:01 | 49.987
2020-10-14 | 12:01 | 49.988
2020-10-14 | 12:01 | 49.989
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.989
2020-10-14 | 12:01 | 49.987
2020-10-14 | 12:01 | 49.987
2020-10-14 | 12:01 | 49.987
2020-10-14 | 12:01 | 49.984
2020-10-14 | 12:01 | 49.985
2020-10-14 | 12:01 | 49.987
2020-10-14 | 12:01 | 49.988
2020-10-14 | 12:01 | 49.99
2020-10-14 | 12:01 | 49.994
2020-10-14 | 12:01 | 49.996
2020-10-14 | 12:01 | 49.997
2020-10-14 | 12:01 | 50
2020-10-14 | 12:01 | 50.002
2020-10-14 | 12:02 | 50.002
2020-10-14 | 12:02 | 50.002
2020-10-14 | 12:02 | 50.001
2020-10-14 | 12:02 | 50
2020-10-14 | 12:02 | 49.998
2020-10-14 | 12:02 | 49.998
2020-10-14 | 12:02 | 49.996
2020-10-14 | 12:02 | 49.994
2020-10-14 | 12:02 | 49.993
2020-10-14 | 12:02 | 49.991
2020-10-14 | 12:02 | 49.99
2020-10-14 | 12:02 | 49.989
2020-10-14 | 12:02 | 49.988
2020-10-14 | 12:02 | 49.99
2020-10-14 | 12:02 | 49.991
2020-10-14 | 12:02 | 49.992
2020-10-14 | 12:02 | 49.993
2020-10-14 | 12:02 | 49.992
2020-10-14 | 12:02 | 49.991
2020-10-14 | 12:02 | 49.99
2020-10-14 | 12:02 | 49.991
2020-10-14 | 12:02 | 49.992
2020-10-14 | 12:02 | 49.994
2020-10-14 | 12:02 | 49.998
2020-10-14 | 12:02 | 50
2020-10-14 | 12:02 | 50.003
2020-10-14 | 12:02 | 50.004
2020-10-14 | 12:02 | 50.005
2020-10-14 | 12:02 | 50.006
2020-10-14 | 12:02 | 50.005
2020-10-14 | 12:02 | 50.004
2020-10-14 | 12:02 | 50.002
2020-10-14 | 12:02 | 50
2020-10-14 | 12:02 | 49.997
2020-10-14 | 12:02 | 49.996
2020-10-14 | 12:02 | 49.994
2020-10-14 | 12:02 | 49.994
2020-10-14 | 12:02 | 49.992
2020-10-14 | 12:02 | 49.993
2020-10-14 | 12:02 | 49.994
2020-10-14 | 12:02 | 49.993
2020-10-14 | 12:02 | 49.993
2020-10-14 | 12:02 | 49.994
2020-10-14 | 12:02 | 49.996
2020-10-14 | 12:02 | 49.997
2020-10-14 | 12:02 | 49.997
2020-10-14 | 12:02 | 49.999
2020-10-14 | 12:02 | 50.001
2020-10-14 | 12:02 | 50.002
2020-10-14 | 12:02 | 50.004
2020-10-14 | 12:02 | 50.005
2020-10-14 | 12:02 | 50.006
2020-10-14 | 12:02 | 50.007
2020-10-14 | 12:02 | 50.009
2020-10-14 | 12:02 | 50.01
2020-10-14 | 12:02 | 50.012
2020-10-14 | 12:02 | 50.014
2020-10-14 | 12:02 | 50.015
2020-10-14 | 12:02 | 50.016
2020-10-14 | 12:02 | 50.018
2020-10-14 | 12:02 | 50.018
2020-10-14 | 12:03 | 50.019
2020-10-14 | 12:03 | 50.018
2020-10-14 | 12:03 | 50.02
2020-10-14 | 12:03 | 50.021
2020-10-14 | 12:03 | 50.022
2020-10-14 | 12:03 | 50.022
2020-10-14 | 12:03 | 50.025
2020-10-14 | 12:03 | 50.027
2020-10-14 | 12:03 | 50.027
2020-10-14 | 12:03 | 50.025
2020-10-14 | 12:03 | 50.025
2020-10-14 | 12:03 | 50.025
2020-10-14 | 12:03 | 50.027
2020-10-14 | 12:03 | 50.027
2020-10-14 | 12:03 | 50.027
2020-10-14 | 12:03 | 50.028
2020-10-14 | 12:03 | 50.028
2020-10-14 | 12:03 | 50.027
2020-10-14 | 12:03 | 50.026
2020-10-14 | 12:03 | 50.024
2020-10-14 | 12:03 | 50.021
2020-10-14 | 12:03 | 50.019
2020-10-14 | 12:03 | 50.016
2020-10-14 | 12:03 | 50.013
2020-10-14 | 12:03 | 50.01
2020-10-14 | 12:03 | 50.008
2020-10-14 | 12:03 | 50.005
2020-10-14 | 12:03 | 50.004
2020-10-14 | 12:03 | 50.002
2020-10-14 | 12:03 | 50.002
2020-10-14 | 12:03 | 50
2020-10-14 | 12:03 | 50
2020-10-14 | 12:03 | 49.998
2020-10-14 | 12:03 | 50
2020-10-14 | 12:03 | 50
2020-10-14 | 12:03 | 50.001
2020-10-14 | 12:03 | 50.001
2020-10-14 | 12:03 | 50.001
2020-10-14 | 12:03 | 49.999
2020-10-14 | 12:03 | 49.997
2020-10-14 | 12:03 | 49.996
2020-10-14 | 12:03 | 49.995
2020-10-14 | 12:03 | 49.993
2020-10-14 | 12:03 | 49.99
2020-10-14 | 12:03 | 49.987
2020-10-14 | 12:03 | 49.985
2020-10-14 | 12:03 | 49.981
2020-10-14 | 12:03 | 49.979
2020-10-14 | 12:03 | 49.978
2020-10-14 | 12:03 | 49.977
2020-10-14 | 12:03 | 49.978
2020-10-14 | 12:03 | 49.976
2020-10-14 | 12:03 | 49.974
2020-10-14 | 12:03 | 49.972
2020-10-14 | 12:03 | 49.971
2020-10-14 | 12:03 | 49.971
2020-10-14 | 12:03 | 49.975
2020-10-14 | 12:03 | 49.978
2020-10-14 | 12:03 | 49.978
2020-10-14 | 12:04 | 49.981
2020-10-14 | 12:04 | 49.981
2020-10-14 | 12:04 | 49.983
2020-10-14 | 12:04 | 49.985
2020-10-14 | 12:04 | 49.986
2020-10-14 | 12:04 | 49.985
2020-10-14 | 12:04 | 49.985
2020-10-14 | 12:04 | 49.985
2020-10-14 | 12:04 | 49.983
2020-10-14 | 12:04 | 49.982
2020-10-14 | 12:04 | 49.984
2020-10-14 | 12:04 | 49.984
2020-10-14 | 12:04 | 49.984
2020-10-14 | 12:04 | 49.986
2020-10-14 | 12:04 | 49.987
2020-10-14 | 12:04 | 49.988
2020-10-14 | 12:04 | 49.988
2020-10-14 | 12:04 | 49.989
2020-10-14 | 12:04 | 49.988
2020-10-14 | 12:04 | 49.986
2020-10-14 | 12:04 | 49.985
2020-10-14 | 12:04 | 49.984
2020-10-14 | 12:04 | 49.982
2020-10-14 | 12:04 | 49.982
2020-10-14 | 12:04 | 49.981
2020-10-14 | 12:04 | 49.981
2020-10-14 | 12:04 | 49.981
2020-10-14 | 12:04 | 49.979
2020-10-14 | 12:04 | 49.979
2020-10-14 | 12:04 | 49.977
2020-10-14 | 12:04 | 49.975
2020-10-14 | 12:04 | 49.973
2020-10-14 | 12:04 | 49.972
2020-10-14 | 12:04 | 49.97
2020-10-14 | 12:04 | 49.967
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.96
2020-10-14 | 12:04 | 49.959
2020-10-14 | 12:04 | 49.957
2020-10-14 | 12:04 | 49.957
2020-10-14 | 12:04 | 49.959
2020-10-14 | 12:04 | 49.96
2020-10-14 | 12:04 | 49.959
2020-10-14 | 12:04 | 49.961
2020-10-14 | 12:04 | 49.962
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.965
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.963
2020-10-14 | 12:04 | 49.963
2020-10-14 | 12:04 | 49.962
2020-10-14 | 12:04 | 49.963
2020-10-14 | 12:04 | 49.963
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.964
2020-10-14 | 12:04 | 49.965
2020-10-14 | 12:04 | 49.967
2020-10-14 | 12:04 | 49.968
2020-10-14 | 12:04 | 49.97
2020-10-14 | 12:05 | 49.969
2020-10-14 | 12:05 | 49.971
2020-10-14 | 12:05 | 49.974
2020-10-14 | 12:05 | 49.98
2020-10-14 | 12:05 | 49.982
2020-10-14 | 12:05 | 49.984
2020-10-14 | 12:05 | 49.986
2020-10-14 | 12:05 | 49.989
2020-10-14 | 12:05 | 49.993
2020-10-14 | 12:05 | 49.996
2020-10-14 | 12:05 | 49.998
2020-10-14 | 12:05 | 50.001
2020-10-14 | 12:05 | 50.003
2020-10-14 | 12:05 | 50.006
2020-10-14 | 12:05 | 50.008
2020-10-14 | 12:05 | 50.008
2020-10-14 | 12:05 | 50.008
2020-10-14 | 12:05 | 50.008
2020-10-14 | 12:05 | 50.008
2020-10-14 | 12:05 | 50.008
2020-10-14 | 12:05 | 50.007
2020-10-14 | 12:05 | 50.005
2020-10-14 | 12:05 | 50.003
2020-10-14 | 12:05 | 50.001
2020-10-14 | 12:05 | 49.999
2020-10-14 | 12:05 | 49.998
2020-10-14 | 12:05 | 49.996
2020-10-14 | 12:05 | 49.991
2020-10-14 | 12:05 | 49.988
2020-10-14 | 12:05 | 49.987
2020-10-14 | 12:05 | 49.986
2020-10-14 | 12:05 | 49.984
2020-10-14 | 12:05 | 49.984
2020-10-14 | 12:05 | 49.984
2020-10-14 | 12:05 | 49.985
2020-10-14 | 12:05 | 49.985
2020-10-14 | 12:05 | 49.986
2020-10-14 | 12:05 | 49.985
2020-10-14 | 12:05 | 49.987
2020-10-14 | 12:05 | 49.987
2020-10-14 | 12:05 | 49.987
2020-10-14 | 12:05 | 49.987
2020-10-14 | 12:05 | 49.989
2020-10-14 | 12:05 | 49.991
2020-10-14 | 12:05 | 49.993
2020-10-14 | 12:05 | 49.994
2020-10-14 | 12:05 | 49.995
2020-10-14 | 12:05 | 49.994
2020-10-14 | 12:05 | 49.992
2020-10-14 | 12:05 | 49.989
2020-10-14 | 12:05 | 49.989
2020-10-14 | 12:05 | 49.989
2020-10-14 | 12:05 | 49.991
2020-10-14 | 12:05 | 49.991
2020-10-14 | 12:05 | 49.991
2020-10-14 | 12:05 | 49.991
2020-10-14 | 12:05 | 49.99
2020-10-14 | 12:05 | 49.988
2020-10-14 | 12:05 | 49.986
2020-10-14 | 12:06 | 49.986
2020-10-14 | 12:06 | 49.987
2020-10-14 | 12:06 | 49.989
2020-10-14 | 12:06 | 49.993
2020-10-14 | 12:06 | 49.997
2020-10-14 | 12:06 | 50.001
2020-10-14 | 12:06 | 50.005
2020-10-14 | 12:06 | 50.01
2020-10-14 | 12:06 | 50.013
2020-10-14 | 12:06 | 50.016
2020-10-14 | 12:06 | 50.017
2020-10-14 | 12:06 | 50.018
2020-10-14 | 12:06 | 50.02
2020-10-14 | 12:06 | 50.021
2020-10-14 | 12:06 | 50.021
2020-10-14 | 12:06 | 50.022
2020-10-14 | 12:06 | 50.021
2020-10-14 | 12:06 | 50.019
2020-10-14 | 12:06 | 50.016
2020-10-14 | 12:06 | 50.014
2020-10-14 | 12:06 | 50.013
2020-10-14 | 12:06 | 50.013
2020-10-14 | 12:06 | 50.014
2020-10-14 | 12:06 | 50.014
2020-10-14 | 12:06 | 50.015
2020-10-14 | 12:06 | 50.014
2020-10-14 | 12:06 | 50.013
2020-10-14 | 12:06 | 50.011
2020-10-14 | 12:06 | 50.009
2020-10-14 | 12:06 | 50.008
2020-10-14 | 12:06 | 50.006
2020-10-14 | 12:06 | 50.005
2020-10-14 | 12:06 | 50.005
2020-10-14 | 12:06 | 50.004
2020-10-14 | 12:06 | 50.003
2020-10-14 | 12:06 | 50
2020-10-14 | 12:06 | 49.999
2020-10-14 | 12:06 | 49.996
2020-10-14 | 12:06 | 49.993
2020-10-14 | 12:06 | 49.992
2020-10-14 | 12:06 | 49.992
2020-10-14 | 12:06 | 49.991
2020-10-14 | 12:06 | 49.988
2020-10-14 | 12:06 | 49.987
2020-10-14 | 12:06 | 49.987
2020-10-14 | 12:06 | 49.988
2020-10-14 | 12:06 | 49.986
2020-10-14 | 12:06 | 49.984
2020-10-14 | 12:06 | 49.983
2020-10-14 | 12:06 | 49.983
2020-10-14 | 12:06 | 49.982
2020-10-14 | 12:06 | 49.982
2020-10-14 | 12:06 | 49.983
2020-10-14 | 12:06 | 49.985
2020-10-14 | 12:06 | 49.985
2020-10-14 | 12:06 | 49.986
2020-10-14 | 12:06 | 49.988
2020-10-14 | 12:06 | 49.989
2020-10-14 | 12:06 | 49.988
2020-10-14 | 12:06 | 49.99
2020-10-14 | 12:06 | 49.99
2020-10-14 | 12:07 | 49.99
2020-10-14 | 12:07 | 49.989
2020-10-14 | 12:07 | 49.988
2020-10-14 | 12:07 | 49.988
2020-10-14 | 12:07 | 49.991
2020-10-14 | 12:07 | 49.993
2020-10-14 | 12:07 | 49.994
2020-10-14 | 12:07 | 49.993
2020-10-14 | 12:07 | 49.994
2020-10-14 | 12:07 | 49.995
2020-10-14 | 12:07 | 49.996
2020-10-14 | 12:07 | 49.996
2020-10-14 | 12:07 | 49.998
2020-10-14 | 12:07 | 50
2020-10-14 | 12:07 | 50.002
2020-10-14 | 12:07 | 50.004
2020-10-14 | 12:07 | 50.004
2020-10-14 | 12:07 | 50.004
2020-10-14 | 12:07 | 50.004
2020-10-14 | 12:07 | 50.005
2020-10-14 | 12:07 | 50.007
2020-10-14 | 12:07 | 50.007
2020-10-14 | 12:07 | 50.008
2020-10-14 | 12:07 | 50.009
2020-10-14 | 12:07 | 50.01
2020-10-14 | 12:07 | 50.009
2020-10-14 | 12:07 | 50.006
2020-10-14 | 12:07 | 50.004
2020-10-14 | 12:07 | 50.003
2020-10-14 | 12:07 | 50.003
2020-10-14 | 12:07 | 50.003
2020-10-14 | 12:07 | 50.001
2020-10-14 | 12:07 | 50.001
2020-10-14 | 12:07 | 50.001
2020-10-14 | 12:07 | 50.001
2020-10-14 | 12:07 | 50.002
2020-10-14 | 12:07 | 50.004
2020-10-14 | 12:07 | 50.006
2020-10-14 | 12:07 | 50.009
2020-10-14 | 12:07 | 50.013
2020-10-14 | 12:07 | 50.017
2020-10-14 | 12:07 | 50.017
2020-10-14 | 12:07 | 50.019
2020-10-14 | 12:07 | 50.017
2020-10-14 | 12:07 | 50.015
2020-10-14 | 12:07 | 50.013
2020-10-14 | 12:07 | 50.011
2020-10-14 | 12:07 | 50.01
2020-10-14 | 12:07 | 50.008
2020-10-14 | 12:07 | 50.006
2020-10-14 | 12:07 | 50.003
2020-10-14 | 12:07 | 50.001
2020-10-14 | 12:07 | 49.999
2020-10-14 | 12:07 | 49.996
2020-10-14 | 12:07 | 49.995
2020-10-14 | 12:07 | 49.993
2020-10-14 | 12:07 | 49.991
2020-10-14 | 12:07 | 49.988
2020-10-14 | 12:07 | 49.988
2020-10-14 | 12:08 | 49.987
2020-10-14 | 12:08 | 49.986
2020-10-14 | 12:08 | 49.986
2020-10-14 | 12:08 | 49.985
2020-10-14 | 12:08 | 49.986
2020-10-14 | 12:08 | 49.987
2020-10-14 | 12:08 | 49.987
2020-10-14 | 12:08 | 49.987
2020-10-14 | 12:08 | 49.988
2020-10-14 | 12:08 | 49.988
2020-10-14 | 12:08 | 49.989
2020-10-14 | 12:08 | 49.99
2020-10-14 | 12:08 | 49.992
2020-10-14 | 12:08 | 49.995
2020-10-14 | 12:08 | 49.999
2020-10-14 | 12:08 | 50.003
2020-10-14 | 12:08 | 50.008
2020-10-14 | 12:08 | 50.012
2020-10-14 | 12:08 | 50.016
2020-10-14 | 12:08 | 50.016
2020-10-14 | 12:08 | 50.016
2020-10-14 | 12:08 | 50.017
2020-10-14 | 12:08 | 50.015
2020-10-14 | 12:08 | 50.016
2020-10-14 | 12:08 | 50.014
2020-10-14 | 12:08 | 50.014
2020-10-14 | 12:08 | 50.014
2020-10-14 | 12:08 | 50.017
2020-10-14 | 12:08 | 50.018
2020-10-14 | 12:08 | 50.019
2020-10-14 | 12:08 | 50.021
2020-10-14 | 12:08 | 50.02
2020-10-14 | 12:08 | 50.019
2020-10-14 | 12:08 | 50.018
2020-10-14 | 12:08 | 50.016
2020-10-14 | 12:08 | 50.013
2020-10-14 | 12:08 | 50.01
2020-10-14 | 12:08 | 50.006
2020-10-14 | 12:08 | 50.004
2020-10-14 | 12:08 | 50.001
2020-10-14 | 12:08 | 50
2020-10-14 | 12:08 | 49.997
2020-10-14 | 12:08 | 49.995
2020-10-14 | 12:08 | 49.993
2020-10-14 | 12:08 | 49.991
2020-10-14 | 12:08 | 49.989
2020-10-14 | 12:08 | 49.986
2020-10-14 | 12:08 | 49.979
2020-10-14 | 12:08 | 49.976
2020-10-14 | 12:08 | 49.973
2020-10-14 | 12:08 | 49.969
2020-10-14 | 12:08 | 49.966
2020-10-14 | 12:08 | 49.963
2020-10-14 | 12:08 | 49.963
2020-10-14 | 12:08 | 49.962
2020-10-14 | 12:08 | 49.961
2020-10-14 | 12:08 | 49.961
2020-10-14 | 12:08 | 49.961
2020-10-14 | 12:08 | 49.962
2020-10-14 | 12:08 | 49.962
2020-10-14 | 12:08 | 49.961
2020-10-14 | 12:09 | 49.961
2020-10-14 | 12:09 | 49.959
2020-10-14 | 12:09 | 49.957
2020-10-14 | 12:09 | 49.957
2020-10-14 | 12:09 | 49.955
2020-10-14 | 12:09 | 49.956
2020-10-14 | 12:09 | 49.956
2020-10-14 | 12:09 | 49.959
2020-10-14 | 12:09 | 49.959
2020-10-14 | 12:09 | 49.96
2020-10-14 | 12:09 | 49.958
2020-10-14 | 12:09 | 49.958
2020-10-14 | 12:09 | 49.956
2020-10-14 | 12:09 | 49.954
2020-10-14 | 12:09 | 49.953
2020-10-14 | 12:09 | 49.951
2020-10-14 | 12:09 | 49.951
2020-10-14 | 12:09 | 49.952
2020-10-14 | 12:09 | 49.953
2020-10-14 | 12:09 | 49.955
2020-10-14 | 12:09 | 49.957
2020-10-14 | 12:09 | 49.959
2020-10-14 | 12:09 | 49.959
2020-10-14 | 12:09 | 49.961
2020-10-14 | 12:09 | 49.962
2020-10-14 | 12:09 | 49.963
2020-10-14 | 12:09 | 49.962
2020-10-14 | 12:09 | 49.963
2020-10-14 | 12:09 | 49.963
2020-10-14 | 12:09 | 49.964
2020-10-14 | 12:09 | 49.965
2020-10-14 | 12:09 | 49.964
2020-10-14 | 12:09 | 49.963
2020-10-14 | 12:09 | 49.963
2020-10-14 | 12:09 | 49.962
2020-10-14 | 12:09 | 49.963
2020-10-14 | 12:09 | 49.965
2020-10-14 | 12:09 | 49.967
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.969
2020-10-14 | 12:09 | 49.967
2020-10-14 | 12:09 | 49.966
2020-10-14 | 12:09 | 49.967
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.967
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.967
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.967
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.969
2020-10-14 | 12:09 | 49.97
2020-10-14 | 12:09 | 49.97
2020-10-14 | 12:09 | 49.969
2020-10-14 | 12:09 | 49.968
2020-10-14 | 12:09 | 49.966
2020-10-14 | 12:09 | 49.966
2020-10-14 | 12:10 | 49.965
2020-10-14 | 12:10 | 49.967
2020-10-14 | 12:10 | 49.969
2020-10-14 | 12:10 | 49.972
2020-10-14 | 12:10 | 49.975
2020-10-14 | 12:10 | 49.979
2020-10-14 | 12:10 | 49.982
2020-10-14 | 12:10 | 49.988
2020-10-14 | 12:10 | 49.993
2020-10-14 | 12:10 | 49.997
2020-10-14 | 12:10 | 49.999
2020-10-14 | 12:10 | 50.002
2020-10-14 | 12:10 | 50.004
2020-10-14 | 12:10 | 50.004
2020-10-14 | 12:10 | 50.006
2020-10-14 | 12:10 | 50.007
2020-10-14 | 12:10 | 50.008
2020-10-14 | 12:10 | 50.01
2020-10-14 | 12:10 | 50.012
2020-10-14 | 12:10 | 50.015
2020-10-14 | 12:10 | 50.015
2020-10-14 | 12:10 | 50.017
2020-10-14 | 12:10 | 50.017
2020-10-14 | 12:10 | 50.016
2020-10-14 | 12:10 | 50.017
2020-10-14 | 12:10 | 50.016
2020-10-14 | 12:10 | 50.016
2020-10-14 | 12:10 | 50.016
2020-10-14 | 12:10 | 50.016
2020-10-14 | 12:10 | 50.016
2020-10-14 | 12:10 | 50.018
2020-10-14 | 12:10 | 50.018
2020-10-14 | 12:10 | 50.019
2020-10-14 | 12:10 | 50.02
2020-10-14 | 12:10 | 50.02
2020-10-14 | 12:10 | 50.022
2020-10-14 | 12:10 | 50.022
2020-10-14 | 12:10 | 50.024
2020-10-14 | 12:10 | 50.021
2020-10-14 | 12:10 | 50.019
2020-10-14 | 12:10 | 50.019
2020-10-14 | 12:10 | 50.017
2020-10-14 | 12:10 | 50.015
2020-10-14 | 12:10 | 50.011
2020-10-14 | 12:10 | 50.009
2020-10-14 | 12:10 | 50.006
2020-10-14 | 12:10 | 50.003
2020-10-14 | 12:10 | 50.001
2020-10-14 | 12:10 | 50
2020-10-14 | 12:10 | 50
2020-10-14 | 12:10 | 49.998
2020-10-14 | 12:10 | 49.996
2020-10-14 | 12:10 | 49.995
2020-10-14 | 12:10 | 49.994
2020-10-14 | 12:10 | 49.993
2020-10-14 | 12:10 | 49.992
2020-10-14 | 12:10 | 49.99
2020-10-14 | 12:10 | 49.988
2020-10-14 | 12:10 | 49.988
2020-10-14 | 12:10 | 49.985
2020-10-14 | 12:10 | 49.982
2020-10-14 | 12:11 | 49.981
2020-10-14 | 12:11 | 49.979
2020-10-14 | 12:11 | 49.976
2020-10-14 | 12:11 | 49.975
2020-10-14 | 12:11 | 49.973
2020-10-14 | 12:11 | 49.973
2020-10-14 | 12:11 | 49.973
2020-10-14 | 12:11 | 49.975
2020-10-14 | 12:11 | 49.978
2020-10-14 | 12:11 | 49.979
2020-10-14 | 12:11 | 49.982
2020-10-14 | 12:11 | 49.984
2020-10-14 | 12:11 | 49.984
2020-10-14 | 12:11 | 49.986
2020-10-14 | 12:11 | 49.986
2020-10-14 | 12:11 | 49.987
2020-10-14 | 12:11 | 49.987
2020-10-14 | 12:11 | 49.986
2020-10-14 | 12:11 | 49.985
2020-10-14 | 12:11 | 49.984
2020-10-14 | 12:11 | 49.984
2020-10-14 | 12:11 | 49.981
2020-10-14 | 12:11 | 49.98
2020-10-14 | 12:11 | 49.976
2020-10-14 | 12:11 | 49.973
2020-10-14 | 12:11 | 49.97
2020-10-14 | 12:11 | 49.968
2020-10-14 | 12:11 | 49.966
2020-10-14 | 12:11 | 49.967
2020-10-14 | 12:11 | 49.969
2020-10-14 | 12:11 | 49.967
2020-10-14 | 12:11 | 49.965
2020-10-14 | 12:11 | 49.967
2020-10-14 | 12:11 | 49.964
2020-10-14 | 12:11 | 49.966
2020-10-14 | 12:11 | 49.967
2020-10-14 | 12:11 | 49.967
2020-10-14 | 12:11 | 49.966
2020-10-14 | 12:11 | 49.965
2020-10-14 | 12:11 | 49.965
2020-10-14 | 12:11 | 49.965
2020-10-14 | 12:11 | 49.965
2020-10-14 | 12:11 | 49.966
2020-10-14 | 12:11 | 49.966
2020-10-14 | 12:11 | 49.966
2020-10-14 | 12:11 | 49.964
2020-10-14 | 12:11 | 49.964
2020-10-14 | 12:11 | 49.963
2020-10-14 | 12:11 | 49.964
2020-10-14 | 12:11 | 49.965
2020-10-14 | 12:11 | 49.963
2020-10-14 | 12:11 | 49.96
2020-10-14 | 12:11 | 49.96
2020-10-14 | 12:11 | 49.959
2020-10-14 | 12:11 | 49.96
2020-10-14 | 12:11 | 49.959
2020-10-14 | 12:11 | 49.958
2020-10-14 | 12:11 | 49.958
2020-10-14 | 12:11 | 49.96
2020-10-14 | 12:12 | 49.962
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.964
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.964
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.964
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.964
2020-10-14 | 12:12 | 49.962
2020-10-14 | 12:12 | 49.961
2020-10-14 | 12:12 | 49.962
2020-10-14 | 12:12 | 49.962
2020-10-14 | 12:12 | 49.962
2020-10-14 | 12:12 | 49.962
2020-10-14 | 12:12 | 49.963
2020-10-14 | 12:12 | 49.964
2020-10-14 | 12:12 | 49.966
2020-10-14 | 12:12 | 49.967
2020-10-14 | 12:12 | 49.967
2020-10-14 | 12:12 | 49.968
2020-10-14 | 12:12 | 49.969
2020-10-14 | 12:12 | 49.97
2020-10-14 | 12:12 | 49.97
2020-10-14 | 12:12 | 49.97
2020-10-14 | 12:12 | 49.97
2020-10-14 | 12:12 | 49.969
2020-10-14 | 12:12 | 49.968
2020-10-14 | 12:12 | 49.966
2020-10-14 | 12:12 | 49.966
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.965
2020-10-14 | 12:12 | 49.963
2020-10-14 | 12:12 | 49.96
2020-10-14 | 12:12 | 49.96
2020-10-14 | 12:12 | 49.958
2020-10-14 | 12:12 | 49.955
2020-10-14 | 12:12 | 49.953
2020-10-14 | 12:12 | 49.951
2020-10-14 | 12:12 | 49.949
2020-10-14 | 12:12 | 49.947
2020-10-14 | 12:12 | 49.947
2020-10-14 | 12:12 | 49.948
2020-10-14 | 12:12 | 49.949
2020-10-14 | 12:12 | 49.949
2020-10-14 | 12:12 | 49.95
2020-10-14 | 12:12 | 49.951
2020-10-14 | 12:12 | 49.952
2020-10-14 | 12:12 | 49.954
2020-10-14 | 12:12 | 49.953
2020-10-14 | 12:12 | 49.953
2020-10-14 | 12:12 | 49.954
2020-10-14 | 12:12 | 49.953
2020-10-14 | 12:12 | 49.955
2020-10-14 | 12:12 | 49.955
2020-10-14 | 12:12 | 49.956
2020-10-14 | 12:12 | 49.958
2020-10-14 | 12:12 | 49.958
2020-10-14 | 12:13 | 49.961
2020-10-14 | 12:13 | 49.961
2020-10-14 | 12:13 | 49.964
2020-10-14 | 12:13 | 49.966
2020-10-14 | 12:13 | 49.969
2020-10-14 | 12:13 | 49.97
2020-10-14 | 12:13 | 49.971
2020-10-14 | 12:13 | 49.972
2020-10-14 | 12:13 | 49.974
2020-10-14 | 12:13 | 49.976
2020-10-14 | 12:13 | 49.977
2020-10-14 | 12:13 | 49.978
2020-10-14 | 12:13 | 49.977
2020-10-14 | 12:13 | 49.976
2020-10-14 | 12:13 | 49.974
2020-10-14 | 12:13 | 49.971
2020-10-14 | 12:13 | 49.969
2020-10-14 | 12:13 | 49.968
2020-10-14 | 12:13 | 49.967
2020-10-14 | 12:13 | 49.966
2020-10-14 | 12:13 | 49.966
2020-10-14 | 12:13 | 49.967
2020-10-14 | 12:13 | 49.966
2020-10-14 | 12:13 | 49.967
2020-10-14 | 12:13 | 49.968
2020-10-14 | 12:13 | 49.969
2020-10-14 | 12:13 | 49.973
2020-10-14 | 12:13 | 49.977
2020-10-14 | 12:13 | 49.98
2020-10-14 | 12:13 | 49.981
2020-10-14 | 12:13 | 49.981
2020-10-14 | 12:13 | 49.982
2020-10-14 | 12:13 | 49.982
2020-10-14 | 12:13 | 49.984
2020-10-14 | 12:13 | 49.987
2020-10-14 | 12:13 | 49.99
2020-10-14 | 12:13 | 49.992
2020-10-14 | 12:13 | 49.992
2020-10-14 | 12:13 | 49.993
2020-10-14 | 12:13 | 49.995
2020-10-14 | 12:13 | 49.996
2020-10-14 | 12:13 | 49.994
2020-10-14 | 12:13 | 49.994
2020-10-14 | 12:13 | 49.993
2020-10-14 | 12:13 | 49.991
2020-10-14 | 12:13 | 49.99
2020-10-14 | 12:13 | 49.989
2020-10-14 | 12:13 | 49.988
2020-10-14 | 12:13 | 49.99
2020-10-14 | 12:13 | 49.989
2020-10-14 | 12:13 | 49.992
2020-10-14 | 12:13 | 49.994
2020-10-14 | 12:13 | 49.995
2020-10-14 | 12:13 | 49.996
2020-10-14 | 12:13 | 49.999
2020-10-14 | 12:13 | 50.001
2020-10-14 | 12:13 | 50.003
2020-10-14 | 12:13 | 50.005
2020-10-14 | 12:13 | 50.006
2020-10-14 | 12:14 | 50.005
2020-10-14 | 12:14 | 50.005
2020-10-14 | 12:14 | 50.004
2020-10-14 | 12:14 | 50.004
2020-10-14 | 12:14 | 50.001
2020-10-14 | 12:14 | 49.998
2020-10-14 | 12:14 | 49.995
2020-10-14 | 12:14 | 49.992
2020-10-14 | 12:14 | 49.989
2020-10-14 | 12:14 | 49.987
2020-10-14 | 12:14 | 49.985
2020-10-14 | 12:14 | 49.987
2020-10-14 | 12:14 | 49.985
2020-10-14 | 12:14 | 49.986
2020-10-14 | 12:14 | 49.984
2020-10-14 | 12:14 | 49.983
2020-10-14 | 12:14 | 49.984
2020-10-14 | 12:14 | 49.986
2020-10-14 | 12:14 | 49.987
2020-10-14 | 12:14 | 49.987
2020-10-14 | 12:14 | 49.987
2020-10-14 | 12:14 | 49.986
2020-10-14 | 12:14 | 49.986
2020-10-14 | 12:14 | 49.986
2020-10-14 | 12:14 | 49.985
2020-10-14 | 12:14 | 49.983
2020-10-14 | 12:14 | 49.981
2020-10-14 | 12:14 | 49.979
2020-10-14 | 12:14 | 49.976
2020-10-14 | 12:14 | 49.972
2020-10-14 | 12:14 | 49.969
2020-10-14 | 12:14 | 49.966
2020-10-14 | 12:14 | 49.966
2020-10-14 | 12:14 | 49.965
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.965
2020-10-14 | 12:14 | 49.966
2020-10-14 | 12:14 | 49.967
2020-10-14 | 12:14 | 49.967
2020-10-14 | 12:14 | 49.967
2020-10-14 | 12:14 | 49.967
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.962
2020-10-14 | 12:14 | 49.959
2020-10-14 | 12:14 | 49.957
2020-10-14 | 12:14 | 49.956
2020-10-14 | 12:14 | 49.957
2020-10-14 | 12:14 | 49.959
2020-10-14 | 12:14 | 49.961
2020-10-14 | 12:14 | 49.964
2020-10-14 | 12:14 | 49.968
2020-10-14 | 12:14 | 49.97
2020-10-14 | 12:14 | 49.971
2020-10-14 | 12:14 | 49.972
2020-10-14 | 12:14 | 49.973
2020-10-14 | 12:14 | 49.975
2020-10-14 | 12:14 | 49.975
2020-10-14 | 12:15 | 49.976
2020-10-14 | 12:15 | 49.976
2020-10-14 | 12:15 | 49.976
2020-10-14 | 12:15 | 49.977
2020-10-14 | 12:15 | 49.979
2020-10-14 | 12:15 | 49.98
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.984
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.982
2020-10-14 | 12:15 | 49.981
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.983
2020-10-14 | 12:15 | 49.984
2020-10-14 | 12:15 | 49.985
2020-10-14 | 12:15 | 49.985
2020-10-14 | 12:15 | 49.984
2020-10-14 | 12:15 | 49.981
2020-10-14 | 12:15 | 49.979
2020-10-14 | 12:15 | 49.976
2020-10-14 | 12:15 | 49.975
2020-10-14 | 12:15 | 49.972
2020-10-14 | 12:15 | 49.969
2020-10-14 | 12:15 | 49.969
2020-10-14 | 12:15 | 49.967
2020-10-14 | 12:15 | 49.967
2020-10-14 | 12:15 | 49.965
2020-10-14 | 12:15 | 49.964
2020-10-14 | 12:15 | 49.962
2020-10-14 | 12:15 | 49.959
2020-10-14 | 12:15 | 49.959
2020-10-14 | 12:15 | 49.959
2020-10-14 | 12:15 | 49.958
2020-10-14 | 12:15 | 49.957
2020-10-14 | 12:15 | 49.957
2020-10-14 | 12:15 | 49.955
2020-10-14 | 12:15 | 49.955
2020-10-14 | 12:15 | 49.954
2020-10-14 | 12:15 | 49.953
2020-10-14 | 12:15 | 49.955
2020-10-14 | 12:15 | 49.956
2020-10-14 | 12:15 | 49.959
2020-10-14 | 12:15 | 49.96
2020-10-14 | 12:15 | 49.961
2020-10-14 | 12:15 | 49.964
2020-10-14 | 12:15 | 49.965
2020-10-14 | 12:15 | 49.967
2020-10-14 | 12:15 | 49.97
2020-10-14 | 12:15 | 49.973
2020-10-14 | 12:15 | 49.975
2020-10-14 | 12:15 | 49.976
2020-10-14 | 12:15 | 49.975
2020-10-14 | 12:15 | 49.976
2020-10-14 | 12:15 | 49.978
2020-10-14 | 12:15 | 49.979
2020-10-14 | 12:16 | 49.979
2020-10-14 | 12:16 | 49.979
2020-10-14 | 12:16 | 49.981
2020-10-14 | 12:16 | 49.984
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.988
2020-10-14 | 12:16 | 49.988
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.987
2020-10-14 | 12:16 | 49.987
2020-10-14 | 12:16 | 49.985
2020-10-14 | 12:16 | 49.985
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.986
2020-10-14 | 12:16 | 49.989
2020-10-14 | 12:16 | 49.992
2020-10-14 | 12:16 | 49.995
2020-10-14 | 12:16 | 49.997
2020-10-14 | 12:16 | 50
2020-10-14 | 12:16 | 50.003
2020-10-14 | 12:16 | 50.006
2020-10-14 | 12:16 | 50.009
2020-10-14 | 12:16 | 50.011
2020-10-14 | 12:16 | 50.012
2020-10-14 | 12:16 | 50.012
2020-10-14 | 12:16 | 50.012
2020-10-14 | 12:16 | 50.011
2020-10-14 | 12:16 | 50.01
2020-10-14 | 12:16 | 50.006
2020-10-14 | 12:16 | 50.003
2020-10-14 | 12:16 | 50
2020-10-14 | 12:16 | 49.999
2020-10-14 | 12:16 | 49.997
2020-10-14 | 12:16 | 49.996
2020-10-14 | 12:16 | 49.996
2020-10-14 | 12:16 | 49.993
2020-10-14 | 12:16 | 49.992
2020-10-14 | 12:16 | 49.989
2020-10-14 | 12:16 | 49.987
2020-10-14 | 12:16 | 49.985
2020-10-14 | 12:16 | 49.983
2020-10-14 | 12:16 | 49.981
2020-10-14 | 12:16 | 49.983
2020-10-14 | 12:16 | 49.984
2020-10-14 | 12:16 | 49.987
2020-10-14 | 12:16 | 49.99
2020-10-14 | 12:16 | 49.992
2020-10-14 | 12:16 | 49.995
2020-10-14 | 12:16 | 49.996
2020-10-14 | 12:16 | 49.998
2020-10-14 | 12:16 | 49.999
2020-10-14 | 12:16 | 50.002
2020-10-14 | 12:16 | 50.004
2020-10-14 | 12:16 | 50.005
2020-10-14 | 12:16 | 50.008
2020-10-14 | 12:16 | 50.009
2020-10-14 | 12:16 | 50.01
2020-10-14 | 12:16 | 50.012
2020-10-14 | 12:17 | 50.014
2020-10-14 | 12:17 | 50.015
2020-10-14 | 12:17 | 50.02
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.021
2020-10-14 | 12:17 | 50.02
2020-10-14 | 12:17 | 50.02
2020-10-14 | 12:17 | 50.019
2020-10-14 | 12:17 | 50.021
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.021
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.025
2020-10-14 | 12:17 | 50.025
2020-10-14 | 12:17 | 50.025
2020-10-14 | 12:17 | 50.024
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.023
2020-10-14 | 12:17 | 50.024
2020-10-14 | 12:17 | 50.025
2020-10-14 | 12:17 | 50.024
2020-10-14 | 12:17 | 50.023
2020-10-14 | 12:17 | 50.022
2020-10-14 | 12:17 | 50.021
2020-10-14 | 12:17 | 50.02
2020-10-14 | 12:17 | 50.02
2020-10-14 | 12:17 | 50.019
2020-10-14 | 12:17 | 50.018
2020-10-14 | 12:17 | 50.018
2020-10-14 | 12:17 | 50.017
2020-10-14 | 12:17 | 50.015
2020-10-14 | 12:17 | 50.013
2020-10-14 | 12:17 | 50.011
2020-10-14 | 12:17 | 50.009
2020-10-14 | 12:17 | 50.007
2020-10-14 | 12:17 | 50.005
2020-10-14 | 12:17 | 50.002
2020-10-14 | 12:17 | 50
2020-10-14 | 12:17 | 49.998
2020-10-14 | 12:17 | 49.997
2020-10-14 | 12:17 | 49.994
2020-10-14 | 12:17 | 49.989
2020-10-14 | 12:17 | 49.987
2020-10-14 | 12:17 | 49.987
2020-10-14 | 12:17 | 49.987
2020-10-14 | 12:17 | 49.985
2020-10-14 | 12:17 | 49.985
2020-10-14 | 12:17 | 49.985
2020-10-14 | 12:17 | 49.986
2020-10-14 | 12:17 | 49.986
2020-10-14 | 12:17 | 49.988
2020-10-14 | 12:17 | 49.99
2020-10-14 | 12:17 | 49.993
2020-10-14 | 12:17 | 49.995
2020-10-14 | 12:17 | 50
2020-10-14 | 12:17 | 50.003
2020-10-14 | 12:17 | 50.006
2020-10-14 | 12:18 | 50.01
2020-10-14 | 12:18 | 50.014
2020-10-14 | 12:18 | 50.017
2020-10-14 | 12:18 | 50.018
2020-10-14 | 12:18 | 50.018
2020-10-14 | 12:18 | 50.021
2020-10-14 | 12:18 | 50.023
2020-10-14 | 12:18 | 50.026
2020-10-14 | 12:18 | 50.028
2020-10-14 | 12:18 | 50.03
2020-10-14 | 12:18 | 50.031
2020-10-14 | 12:18 | 50.031
2020-10-14 | 12:18 | 50.033
2020-10-14 | 12:18 | 50.035
2020-10-14 | 12:18 | 50.035
2020-10-14 | 12:18 | 50.033
2020-10-14 | 12:18 | 50.031
2020-10-14 | 12:18 | 50.029
2020-10-14 | 12:18 | 50.025
2020-10-14 | 12:18 | 50.02
2020-10-14 | 12:18 | 50.017
2020-10-14 | 12:18 | 50.017
2020-10-14 | 12:18 | 50.018
2020-10-14 | 12:18 | 50.019
2020-10-14 | 12:18 | 50.018
2020-10-14 | 12:18 | 50.018
2020-10-14 | 12:18 | 50.02
2020-10-14 | 12:18 | 50.021
2020-10-14 | 12:18 | 50.021
2020-10-14 | 12:18 | 50.022
2020-10-14 | 12:18 | 50.026
2020-10-14 | 12:18 | 50.03
2020-10-14 | 12:18 | 50.032
2020-10-14 | 12:18 | 50.034
2020-10-14 | 12:18 | 50.037
2020-10-14 | 12:18 | 50.039
2020-10-14 | 12:18 | 50.041
2020-10-14 | 12:18 | 50.043
2020-10-14 | 12:18 | 50.045
2020-10-14 | 12:18 | 50.048
2020-10-14 | 12:18 | 50.05
2020-10-14 | 12:18 | 50.05
2020-10-14 | 12:18 | 50.049
2020-10-14 | 12:18 | 50.049
2020-10-14 | 12:18 | 50.048
2020-10-14 | 12:18 | 50.046
2020-10-14 | 12:18 | 50.044
2020-10-14 | 12:18 | 50.044
2020-10-14 | 12:18 | 50.044
2020-10-14 | 12:18 | 50.043
2020-10-14 | 12:18 | 50.042
2020-10-14 | 12:18 | 50.043
2020-10-14 | 12:18 | 50.044
2020-10-14 | 12:18 | 50.045
2020-10-14 | 12:18 | 50.046
2020-10-14 | 12:18 | 50.045
2020-10-14 | 12:18 | 50.046
2020-10-14 | 12:18 | 50.047
2020-10-14 | 12:18 | 50.048
2020-10-14 | 12:18 | 50.049
2020-10-14 | 12:18 | 50.051
2020-10-14 | 12:19 | 50.051
2020-10-14 | 12:19 | 50.051
2020-10-14 | 12:19 | 50.05
2020-10-14 | 12:19 | 50.048
2020-10-14 | 12:19 | 50.047
2020-10-14 | 12:19 | 50.045
2020-10-14 | 12:19 | 50.043
2020-10-14 | 12:19 | 50.044
2020-10-14 | 12:19 | 50.045
2020-10-14 | 12:19 | 50.047
2020-10-14 | 12:19 | 50.046
2020-10-14 | 12:19 | 50.047
2020-10-14 | 12:19 | 50.047
2020-10-14 | 12:19 | 50.048
2020-10-14 | 12:19 | 50.047
2020-10-14 | 12:19 | 50.046
2020-10-14 | 12:19 | 50.046
2020-10-14 | 12:19 | 50.045
2020-10-14 | 12:19 | 50.044
2020-10-14 | 12:19 | 50.045
2020-10-14 | 12:19 | 50.046
2020-10-14 | 12:19 | 50.048
2020-10-14 | 12:19 | 50.05
2020-10-14 | 12:19 | 50.051
2020-10-14 | 12:19 | 50.052
2020-10-14 | 12:19 | 50.054
2020-10-14 | 12:19 | 50.054
2020-10-14 | 12:19 | 50.055
2020-10-14 | 12:19 | 50.057
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.061
2020-10-14 | 12:19 | 50.062
2020-10-14 | 12:19 | 50.062
2020-10-14 | 12:19 | 50.061
2020-10-14 | 12:19 | 50.061
2020-10-14 | 12:19 | 50.06
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.058
2020-10-14 | 12:19 | 50.056
2020-10-14 | 12:19 | 50.057
2020-10-14 | 12:19 | 50.057
2020-10-14 | 12:19 | 50.055
2020-10-14 | 12:19 | 50.053
2020-10-14 | 12:19 | 50.051
2020-10-14 | 12:19 | 50.05
2020-10-14 | 12:19 | 50.051
2020-10-14 | 12:19 | 50.053
2020-10-14 | 12:19 | 50.057
2020-10-14 | 12:19 | 50.059
2020-10-14 | 12:19 | 50.063
2020-10-14 | 12:19 | 50.065
2020-10-14 | 12:19 | 50.066
2020-10-14 | 12:19 | 50.068
2020-10-14 | 12:19 | 50.07
2020-10-14 | 12:19 | 50.072
2020-10-14 | 12:20 | 50.073
2020-10-14 | 12:20 | 50.073
2020-10-14 | 12:20 | 50.075
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.078
2020-10-14 | 12:20 | 50.08
2020-10-14 | 12:20 | 50.079
2020-10-14 | 12:20 | 50.078
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.074
2020-10-14 | 12:20 | 50.073
2020-10-14 | 12:20 | 50.071
2020-10-14 | 12:20 | 50.071
2020-10-14 | 12:20 | 50.073
2020-10-14 | 12:20 | 50.075
2020-10-14 | 12:20 | 50.075
2020-10-14 | 12:20 | 50.074
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.078
2020-10-14 | 12:20 | 50.081
2020-10-14 | 12:20 | 50.083
2020-10-14 | 12:20 | 50.084
2020-10-14 | 12:20 | 50.085
2020-10-14 | 12:20 | 50.083
2020-10-14 | 12:20 | 50.081
2020-10-14 | 12:20 | 50.079
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.075
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.076
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.077
2020-10-14 | 12:20 | 50.078
2020-10-14 | 12:20 | 50.08
2020-10-14 | 12:20 | 50.08
2020-10-14 | 12:20 | 50.08
2020-10-14 | 12:20 | 50.081
2020-10-14 | 12:20 | 50.083
2020-10-14 | 12:20 | 50.085
2020-10-14 | 12:20 | 50.087
2020-10-14 | 12:20 | 50.088
2020-10-14 | 12:20 | 50.09
2020-10-14 | 12:20 | 50.09
2020-10-14 | 12:20 | 50.09
2020-10-14 | 12:20 | 50.088
2020-10-14 | 12:20 | 50.088
2020-10-14 | 12:20 | 50.09
2020-10-14 | 12:20 | 50.091
2020-10-14 | 12:20 | 50.092
2020-10-14 | 12:20 | 50.092
2020-10-14 | 12:20 | 50.093
2020-10-14 | 12:20 | 50.092
2020-10-14 | 12:20 | 50.092
2020-10-14 | 12:21 | 50.093
2020-10-14 | 12:21 | 50.096
2020-10-14 | 12:21 | 50.097
2020-10-14 | 12:21 | 50.097
2020-10-14 | 12:21 | 50.098
2020-10-14 | 12:21 | 50.099
2020-10-14 | 12:21 | 50.099
2020-10-14 | 12:21 | 50.099
2020-10-14 | 12:21 | 50.099
2020-10-14 | 12:21 | 50.097
2020-10-14 | 12:21 | 50.096
2020-10-14 | 12:21 | 50.097
2020-10-14 | 12:21 | 50.094
2020-10-14 | 12:21 | 50.093
2020-10-14 | 12:21 | 50.092
2020-10-14 | 12:21 | 50.09
2020-10-14 | 12:21 | 50.088
2020-10-14 | 12:21 | 50.086
2020-10-14 | 12:21 | 50.085
2020-10-14 | 12:21 | 50.084
2020-10-14 | 12:21 | 50.081
2020-10-14 | 12:21 | 50.08
2020-10-14 | 12:21 | 50.079
2020-10-14 | 12:21 | 50.08
2020-10-14 | 12:21 | 50.08
2020-10-14 | 12:21 | 50.082
2020-10-14 | 12:21 | 50.081
2020-10-14 | 12:21 | 50.082
2020-10-14 | 12:21 | 50.083
2020-10-14 | 12:21 | 50.085
2020-10-14 | 12:21 | 50.084
2020-10-14 | 12:21 | 50.084
2020-10-14 | 12:21 | 50.084
2020-10-14 | 12:21 | 50.083
2020-10-14 | 12:21 | 50.083
2020-10-14 | 12:21 | 50.081
2020-10-14 | 12:21 | 50.078
2020-10-14 | 12:21 | 50.076
2020-10-14 | 12:21 | 50.074
2020-10-14 | 12:21 | 50.071
2020-10-14 | 12:21 | 50.071
2020-10-14 | 12:21 | 50.071
2020-10-14 | 12:21 | 50.071
2020-10-14 | 12:21 | 50.071
2020-10-14 | 12:21 | 50.072
2020-10-14 | 12:21 | 50.074
2020-10-14 | 12:21 | 50.075
2020-10-14 | 12:21 | 50.075
2020-10-14 | 12:21 | 50.075
2020-10-14 | 12:21 | 50.075
2020-10-14 | 12:21 | 50.075
2020-10-14 | 12:21 | 50.076
2020-10-14 | 12:21 | 50.076
2020-10-14 | 12:21 | 50.076
2020-10-14 | 12:21 | 50.077
2020-10-14 | 12:21 | 50.077
2020-10-14 | 12:21 | 50.076
2020-10-14 | 12:21 | 50.076
2020-10-14 | 12:21 | 50.077
2020-10-14 | 12:22 | 50.078
2020-10-14 | 12:22 | 50.079
2020-10-14 | 12:22 | 50.078
2020-10-14 | 12:22 | 50.079
2020-10-14 | 12:22 | 50.077
2020-10-14 | 12:22 | 50.075
2020-10-14 | 12:22 | 50.074
2020-10-14 | 12:22 | 50.073
2020-10-14 | 12:22 | 50.074
2020-10-14 | 12:22 | 50.074
2020-10-14 | 12:22 | 50.071
2020-10-14 | 12:22 | 50.07
2020-10-14 | 12:22 | 50.067
2020-10-14 | 12:22 | 50.065
2020-10-14 | 12:22 | 50.064
2020-10-14 | 12:22 | 50.064
2020-10-14 | 12:22 | 50.064
2020-10-14 | 12:22 | 50.062
2020-10-14 | 12:22 | 50.061
2020-10-14 | 12:22 | 50.06
2020-10-14 | 12:22 | 50.062
2020-10-14 | 12:22 | 50.064
2020-10-14 | 12:22 | 50.068
2020-10-14 | 12:22 | 50.071
2020-10-14 | 12:22 | 50.074
2020-10-14 | 12:22 | 50.077
2020-10-14 | 12:22 | 50.079
2020-10-14 | 12:22 | 50.081
2020-10-14 | 12:22 | 50.082
2020-10-14 | 12:22 | 50.082
2020-10-14 | 12:22 | 50.082
2020-10-14 | 12:22 | 50.081
2020-10-14 | 12:22 | 50.08
2020-10-14 | 12:22 | 50.08
2020-10-14 | 12:22 | 50.079
2020-10-14 | 12:22 | 50.078
2020-10-14 | 12:22 | 50.076
2020-10-14 | 12:22 | 50.073
2020-10-14 | 12:22 | 50.07
2020-10-14 | 12:22 | 50.07
2020-10-14 | 12:22 | 50.068
2020-10-14 | 12:22 | 50.067
2020-10-14 | 12:22 | 50.067
2020-10-14 | 12:22 | 50.069
2020-10-14 | 12:22 | 50.07
2020-10-14 | 12:22 | 50.07
2020-10-14 | 12:22 | 50.07
2020-10-14 | 12:22 | 50.068
2020-10-14 | 12:22 | 50.067
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.065
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.067
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.066
2020-10-14 | 12:22 | 50.065
2020-10-14 | 12:22 | 50.064
2020-10-14 | 12:22 | 50.063
2020-10-14 | 12:23 | 50.064
2020-10-14 | 12:23 | 50.064
2020-10-14 | 12:23 | 50.064
2020-10-14 | 12:23 | 50.064
2020-10-14 | 12:23 | 50.064
2020-10-14 | 12:23 | 50.064
2020-10-14 | 12:23 | 50.065
2020-10-14 | 12:23 | 50.066
2020-10-14 | 12:23 | 50.068
2020-10-14 | 12:23 | 50.071
2020-10-14 | 12:23 | 50.074
2020-10-14 | 12:23 | 50.075
2020-10-14 | 12:23 | 50.076
2020-10-14 | 12:23 | 50.077
2020-10-14 | 12:23 | 50.077
2020-10-14 | 12:23 | 50.077
2020-10-14 | 12:23 | 50.079
2020-10-14 | 12:23 | 50.08
2020-10-14 | 12:23 | 50.081
2020-10-14 | 12:23 | 50.08
2020-10-14 | 12:23 | 50.08
2020-10-14 | 12:23 | 50.082
2020-10-14 | 12:23 | 50.081
2020-10-14 | 12:23 | 50.082
2020-10-14 | 12:23 | 50.081
2020-10-14 | 12:23 | 50.081
2020-10-14 | 12:23 | 50.08
2020-10-14 | 12:23 | 50.077
2020-10-14 | 12:23 | 50.075
2020-10-14 | 12:23 | 50.073
2020-10-14 | 12:23 | 50.073
2020-10-14 | 12:23 | 50.073
2020-10-14 | 12:23 | 50.072
2020-10-14 | 12:23 | 50.07
2020-10-14 | 12:23 | 50.069
2020-10-14 | 12:23 | 50.069
2020-10-14 | 12:23 | 50.069
2020-10-14 | 12:23 | 50.07
2020-10-14 | 12:23 | 50.073
2020-10-14 | 12:23 | 50.077
2020-10-14 | 12:23 | 50.077
2020-10-14 | 12:23 | 50.079
2020-10-14 | 12:23 | 50.079
2020-10-14 | 12:23 | 50.082
2020-10-14 | 12:23 | 50.083
2020-10-14 | 12:23 | 50.085
2020-10-14 | 12:23 | 50.085
2020-10-14 | 12:23 | 50.085
2020-10-14 | 12:23 | 50.085
2020-10-14 | 12:23 | 50.085
2020-10-14 | 12:23 | 50.086
2020-10-14 | 12:23 | 50.088
2020-10-14 | 12:23 | 50.092
2020-10-14 | 12:23 | 50.094
2020-10-14 | 12:23 | 50.096
2020-10-14 | 12:23 | 50.098
2020-10-14 | 12:23 | 50.1
2020-10-14 | 12:23 | 50.099
2020-10-14 | 12:23 | 50.098
2020-10-14 | 12:24 | 50.097
2020-10-14 | 12:24 | 50.096
2020-10-14 | 12:24 | 50.095
2020-10-14 | 12:24 | 50.092
2020-10-14 | 12:24 | 50.09
2020-10-14 | 12:24 | 50.088
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.087
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.082
2020-10-14 | 12:24 | 50.079
2020-10-14 | 12:24 | 50.079
2020-10-14 | 12:24 | 50.079
2020-10-14 | 12:24 | 50.083
2020-10-14 | 12:24 | 50.085
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.088
2020-10-14 | 12:24 | 50.087
2020-10-14 | 12:24 | 50.087
2020-10-14 | 12:24 | 50.087
2020-10-14 | 12:24 | 50.086
2020-10-14 | 12:24 | 50.084
2020-10-14 | 12:24 | 50.081
2020-10-14 | 12:24 | 50.08
2020-10-14 | 12:24 | 50.079
2020-10-14 | 12:24 | 50.079
2020-10-14 | 12:24 | 50.08
2020-10-14 | 12:24 | 50.08
2020-10-14 | 12:24 | 50.081
2020-10-14 | 12:24 | 50.081
2020-10-14 | 12:24 | 50.078
2020-10-14 | 12:24 | 50.074
2020-10-14 | 12:24 | 50.071
2020-10-14 | 12:24 | 50.068
2020-10-14 | 12:24 | 50.067
2020-10-14 | 12:24 | 50.065
2020-10-14 | 12:24 | 50.063
2020-10-14 | 12:24 | 50.062
2020-10-14 | 12:24 | 50.062
2020-10-14 | 12:24 | 50.062
2020-10-14 | 12:24 | 50.064
2020-10-14 | 12:25 | 50.068
2020-10-14 | 12:25 | 50.07
2020-10-14 | 12:25 | 50.073
2020-10-14 | 12:25 | 50.075
2020-10-14 | 12:25 | 50.076
2020-10-14 | 12:25 | 50.075
2020-10-14 | 12:25 | 50.076
2020-10-14 | 12:25 | 50.078
2020-10-14 | 12:25 | 50.079
2020-10-14 | 12:25 | 50.082
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.086
2020-10-14 | 12:25 | 50.086
2020-10-14 | 12:25 | 50.087
2020-10-14 | 12:25 | 50.086
2020-10-14 | 12:25 | 50.085
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.082
2020-10-14 | 12:25 | 50.079
2020-10-14 | 12:25 | 50.076
2020-10-14 | 12:25 | 50.074
2020-10-14 | 12:25 | 50.073
2020-10-14 | 12:25 | 50.073
2020-10-14 | 12:25 | 50.073
2020-10-14 | 12:25 | 50.073
2020-10-14 | 12:25 | 50.073
2020-10-14 | 12:25 | 50.074
2020-10-14 | 12:25 | 50.074
2020-10-14 | 12:25 | 50.074
2020-10-14 | 12:25 | 50.074
2020-10-14 | 12:25 | 50.076
2020-10-14 | 12:25 | 50.078
2020-10-14 | 12:25 | 50.079
2020-10-14 | 12:25 | 50.082
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.085
2020-10-14 | 12:25 | 50.086
2020-10-14 | 12:25 | 50.086
2020-10-14 | 12:25 | 50.085
2020-10-14 | 12:25 | 50.085
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.082
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.084
2020-10-14 | 12:25 | 50.083
2020-10-14 | 12:25 | 50.081
2020-10-14 | 12:25 | 50.08
2020-10-14 | 12:25 | 50.08
2020-10-14 | 12:25 | 50.079
2020-10-14 | 12:26 | 50.078
2020-10-14 | 12:26 | 50.077
2020-10-14 | 12:26 | 50.075
2020-10-14 | 12:26 | 50.075
2020-10-14 | 12:26 | 50.075
2020-10-14 | 12:26 | 50.075
2020-10-14 | 12:26 | 50.075
2020-10-14 | 12:26 | 50.073
2020-10-14 | 12:26 | 50.072
2020-10-14 | 12:26 | 50.07
2020-10-14 | 12:26 | 50.071
2020-10-14 | 12:26 | 50.069
2020-10-14 | 12:26 | 50.069
2020-10-14 | 12:26 | 50.071
2020-10-14 | 12:26 | 50.072
2020-10-14 | 12:26 | 50.072
2020-10-14 | 12:26 | 50.073
2020-10-14 | 12:26 | 50.073
2020-10-14 | 12:26 | 50.074
2020-10-14 | 12:26 | 50.074
2020-10-14 | 12:26 | 50.072
2020-10-14 | 12:26 | 50.071
2020-10-14 | 12:26 | 50.069
2020-10-14 | 12:26 | 50.066
2020-10-14 | 12:26 | 50.064
2020-10-14 | 12:26 | 50.062
2020-10-14 | 12:26 | 50.061
2020-10-14 | 12:26 | 50.061
2020-10-14 | 12:26 | 50.06
2020-10-14 | 12:26 | 50.058
2020-10-14 | 12:26 | 50.055
2020-10-14 | 12:26 | 50.053
2020-10-14 | 12:26 | 50.049
2020-10-14 | 12:26 | 50.047
2020-10-14 | 12:26 | 50.046
2020-10-14 | 12:26 | 50.045
2020-10-14 | 12:26 | 50.045
2020-10-14 | 12:26 | 50.045
2020-10-14 | 12:26 | 50.043
2020-10-14 | 12:26 | 50.042
2020-10-14 | 12:26 | 50.041
2020-10-14 | 12:26 | 50.041
2020-10-14 | 12:26 | 50.04
2020-10-14 | 12:26 | 50.039
2020-10-14 | 12:26 | 50.039
2020-10-14 | 12:26 | 50.039
2020-10-14 | 12:26 | 50.038
2020-10-14 | 12:26 | 50.037
2020-10-14 | 12:26 | 50.036
2020-10-14 | 12:26 | 50.036
2020-10-14 | 12:26 | 50.033
2020-10-14 | 12:26 | 50.031
2020-10-14 | 12:26 | 50.029
2020-10-14 | 12:26 | 50.028
2020-10-14 | 12:26 | 50.025
2020-10-14 | 12:26 | 50.024
2020-10-14 | 12:26 | 50.025
2020-10-14 | 12:26 | 50.028
2020-10-14 | 12:26 | 50.03
2020-10-14 | 12:26 | 50.034
2020-10-14 | 12:26 | 50.037
2020-10-14 | 12:27 | 50.04
2020-10-14 | 12:27 | 50.041
2020-10-14 | 12:27 | 50.042
2020-10-14 | 12:27 | 50.043
2020-10-14 | 12:27 | 50.044
2020-10-14 | 12:27 | 50.044
2020-10-14 | 12:27 | 50.044
2020-10-14 | 12:27 | 50.046
2020-10-14 | 12:27 | 50.049
2020-10-14 | 12:27 | 50.05
2020-10-14 | 12:27 | 50.051
2020-10-14 | 12:27 | 50.05
2020-10-14 | 12:27 | 50.051
2020-10-14 | 12:27 | 50.05
2020-10-14 | 12:27 | 50.05
2020-10-14 | 12:27 | 50.048
2020-10-14 | 12:27 | 50.046
2020-10-14 | 12:27 | 50.044
2020-10-14 | 12:27 | 50.043
2020-10-14 | 12:27 | 50.04
2020-10-14 | 12:27 | 50.039
2020-10-14 | 12:27 | 50.04
2020-10-14 | 12:27 | 50.042
2020-10-14 | 12:27 | 50.043
2020-10-14 | 12:27 | 50.043
2020-10-14 | 12:27 | 50.043
2020-10-14 | 12:27 | 50.042
2020-10-14 | 12:27 | 50.041
2020-10-14 | 12:27 | 50.041
2020-10-14 | 12:27 | 50.041
2020-10-14 | 12:27 | 50.04
2020-10-14 | 12:27 | 50.038
2020-10-14 | 12:27 | 50.037
2020-10-14 | 12:27 | 50.035
2020-10-14 | 12:27 | 50.036
2020-10-14 | 12:27 | 50.036
2020-10-14 | 12:27 | 50.036
2020-10-14 | 12:27 | 50.037
2020-10-14 | 12:27 | 50.039
2020-10-14 | 12:27 | 50.039
2020-10-14 | 12:27 | 50.039
2020-10-14 | 12:27 | 50.04
2020-10-14 | 12:27 | 50.04
2020-10-14 | 12:27 | 50.039
2020-10-14 | 12:27 | 50.037
2020-10-14 | 12:27 | 50.036
2020-10-14 | 12:27 | 50.034
2020-10-14 | 12:27 | 50.031
2020-10-14 | 12:27 | 50.029
2020-10-14 | 12:27 | 50.027
2020-10-14 | 12:27 | 50.026
2020-10-14 | 12:27 | 50.026
2020-10-14 | 12:27 | 50.025
2020-10-14 | 12:27 | 50.025
2020-10-14 | 12:27 | 50.026
2020-10-14 | 12:27 | 50.027
2020-10-14 | 12:27 | 50.029
2020-10-14 | 12:27 | 50.031
2020-10-14 | 12:27 | 50.032
2020-10-14 | 12:28 | 50.032
2020-10-14 | 12:28 | 50.033
2020-10-14 | 12:28 | 50.034
2020-10-14 | 12:28 | 50.033
2020-10-14 | 12:28 | 50.032
2020-10-14 | 12:28 | 50.031
2020-10-14 | 12:28 | 50.031
2020-10-14 | 12:28 | 50.033
2020-10-14 | 12:28 | 50.033
2020-10-14 | 12:28 | 50.033
2020-10-14 | 12:28 | 50.034
2020-10-14 | 12:28 | 50.035
2020-10-14 | 12:28 | 50.034
2020-10-14 | 12:28 | 50.033
2020-10-14 | 12:28 | 50.031
2020-10-14 | 12:28 | 50.029
2020-10-14 | 12:28 | 50.027
2020-10-14 | 12:28 | 50.026
2020-10-14 | 12:28 | 50.024
2020-10-14 | 12:28 | 50.024
2020-10-14 | 12:28 | 50.023
2020-10-14 | 12:28 | 50.023
2020-10-14 | 12:28 | 50.023
2020-10-14 | 12:28 | 50.023
2020-10-14 | 12:28 | 50.023
2020-10-14 | 12:28 | 50.022
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.02
2020-10-14 | 12:28 | 50.018
2020-10-14 | 12:28 | 50.019
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.02
2020-10-14 | 12:28 | 50.019
2020-10-14 | 12:28 | 50.02
2020-10-14 | 12:28 | 50.019
2020-10-14 | 12:28 | 50.017
2020-10-14 | 12:28 | 50.014
2020-10-14 | 12:28 | 50.013
2020-10-14 | 12:28 | 50.013
2020-10-14 | 12:28 | 50.012
2020-10-14 | 12:28 | 50.012
2020-10-14 | 12:28 | 50.015
2020-10-14 | 12:28 | 50.015
2020-10-14 | 12:28 | 50.017
2020-10-14 | 12:28 | 50.017
2020-10-14 | 12:28 | 50.017
2020-10-14 | 12:28 | 50.02
2020-10-14 | 12:28 | 50.02
2020-10-14 | 12:28 | 50.02
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.021
2020-10-14 | 12:28 | 50.019
2020-10-14 | 12:28 | 50.015
2020-10-14 | 12:28 | 50.01
2020-10-14 | 12:28 | 50.011
2020-10-14 | 12:28 | 50.011
2020-10-14 | 12:28 | 50.012
2020-10-14 | 12:29 | 50.011
2020-10-14 | 12:29 | 50.009
2020-10-14 | 12:29 | 50.011
2020-10-14 | 12:29 | 50.011
2020-10-14 | 12:29 | 50.013
2020-10-14 | 12:29 | 50.014
2020-10-14 | 12:29 | 50.014
2020-10-14 | 12:29 | 50.017
2020-10-14 | 12:29 | 50.018
2020-10-14 | 12:29 | 50.019
2020-10-14 | 12:29 | 50.02
2020-10-14 | 12:29 | 50.023
2020-10-14 | 12:29 | 50.026
2020-10-14 | 12:29 | 50.027
2020-10-14 | 12:29 | 50.028
2020-10-14 | 12:29 | 50.027
2020-10-14 | 12:29 | 50.026
2020-10-14 | 12:29 | 50.026
2020-10-14 | 12:29 | 50.025
2020-10-14 | 12:29 | 50.026
2020-10-14 | 12:29 | 50.025
2020-10-14 | 12:29 | 50.024
2020-10-14 | 12:29 | 50.024
2020-10-14 | 12:29 | 50.026
2020-10-14 | 12:29 | 50.028
2020-10-14 | 12:29 | 50.03
2020-10-14 | 12:29 | 50.03
2020-10-14 | 12:29 | 50.03
2020-10-14 | 12:29 | 50.031
2020-10-14 | 12:29 | 50.03
2020-10-14 | 12:29 | 50.028
2020-10-14 | 12:29 | 50.027
2020-10-14 | 12:29 | 50.024
2020-10-14 | 12:29 | 50.023
2020-10-14 | 12:29 | 50.024
2020-10-14 | 12:29 | 50.023
2020-10-14 | 12:29 | 50.022
2020-10-14 | 12:29 | 50.022
2020-10-14 | 12:29 | 50.021
2020-10-14 | 12:29 | 50.022
2020-10-14 | 12:29 | 50.022
2020-10-14 | 12:29 | 50.021
2020-10-14 | 12:29 | 50.021
2020-10-14 | 12:29 | 50.022
2020-10-14 | 12:29 | 50.025
2020-10-14 | 12:29 | 50.03
2020-10-14 | 12:29 | 50.034
2020-10-14 | 12:29 | 50.038
2020-10-14 | 12:29 | 50.04
2020-10-14 | 12:29 | 50.041
2020-10-14 | 12:29 | 50.043
2020-10-14 | 12:29 | 50.046
2020-10-14 | 12:29 | 50.049
2020-10-14 | 12:29 | 50.053
2020-10-14 | 12:29 | 50.054
2020-10-14 | 12:29 | 50.055
2020-10-14 | 12:29 | 50.055
2020-10-14 | 12:29 | 50.054
2020-10-14 | 12:29 | 50.053
2020-10-14 | 12:30 | 50.052
2020-10-14 | 12:30 | 50.051
2020-10-14 | 12:30 | 50.05
2020-10-14 | 12:30 | 50.049
2020-10-14 | 12:30 | 50.048
2020-10-14 | 12:30 | 50.049
2020-10-14 | 12:30 | 50.05
2020-10-14 | 12:30 | 50.049
2020-10-14 | 12:30 | 50.049
2020-10-14 | 12:30 | 50.046
2020-10-14 | 12:30 | 50.046
2020-10-14 | 12:30 | 50.046
2020-10-14 | 12:30 | 50.046
2020-10-14 | 12:30 | 50.049
2020-10-14 | 12:30 | 50.051
2020-10-14 | 12:30 | 50.052
2020-10-14 | 12:30 | 50.05
2020-10-14 | 12:30 | 50.05
2020-10-14 | 12:30 | 50.051
2020-10-14 | 12:30 | 50.053
2020-10-14 | 12:30 | 50.053
2020-10-14 | 12:30 | 50.052
2020-10-14 | 12:30 | 50.051
2020-10-14 | 12:30 | 50.05
2020-10-14 | 12:30 | 50.048
2020-10-14 | 12:30 | 50.046
2020-10-14 | 12:30 | 50.044
2020-10-14 | 12:30 | 50.043
2020-10-14 | 12:30 | 50.042
2020-10-14 | 12:30 | 50.041

## Event 20201025-1
In UTC
Date | Time | Freq
2020-10-25 | 4:40 | 49.974
2020-10-25 | 4:40 | 49.976
2020-10-25 | 4:40 | 49.976
2020-10-25 | 4:40 | 49.976
2020-10-25 | 4:40 | 49.975
2020-10-25 | 4:40 | 49.979
2020-10-25 | 4:40 | 49.982
2020-10-25 | 4:40 | 49.986
2020-10-25 | 4:40 | 49.989
2020-10-25 | 4:40 | 49.991
2020-10-25 | 4:40 | 49.993
2020-10-25 | 4:40 | 49.996
2020-10-25 | 4:40 | 49.997
2020-10-25 | 4:40 | 49.998
2020-10-25 | 4:40 | 49.998
2020-10-25 | 4:40 | 49.999
2020-10-25 | 4:40 | 50
2020-10-25 | 4:40 | 50
2020-10-25 | 4:40 | 50.002
2020-10-25 | 4:40 | 50.002
2020-10-25 | 4:40 | 50
2020-10-25 | 4:40 | 49.999
2020-10-25 | 4:40 | 49.997
2020-10-25 | 4:40 | 49.995
2020-10-25 | 4:40 | 49.992
2020-10-25 | 4:40 | 49.989
2020-10-25 | 4:40 | 49.986
2020-10-25 | 4:40 | 49.983
2020-10-25 | 4:40 | 49.983
2020-10-25 | 4:40 | 49.984
2020-10-25 | 4:40 | 49.984
2020-10-25 | 4:41 | 49.983
2020-10-25 | 4:41 | 49.983
2020-10-25 | 4:41 | 49.984
2020-10-25 | 4:41 | 49.984
2020-10-25 | 4:41 | 49.984
2020-10-25 | 4:41 | 49.983
2020-10-25 | 4:41 | 49.982
2020-10-25 | 4:41 | 49.984
2020-10-25 | 4:41 | 49.986
2020-10-25 | 4:41 | 49.989
2020-10-25 | 4:41 | 49.992
2020-10-25 | 4:41 | 49.995
2020-10-25 | 4:41 | 49.997
2020-10-25 | 4:41 | 49.998
2020-10-25 | 4:41 | 50
2020-10-25 | 4:41 | 50.003
2020-10-25 | 4:41 | 50.005
2020-10-25 | 4:41 | 50.008
2020-10-25 | 4:41 | 50.01
2020-10-25 | 4:41 | 50.012
2020-10-25 | 4:41 | 50.013
2020-10-25 | 4:41 | 50.01
2020-10-25 | 4:41 | 50.009
2020-10-25 | 4:41 | 50.006
2020-10-25 | 4:41 | 50.002
2020-10-25 | 4:41 | 49.999
2020-10-25 | 4:41 | 49.992
2020-10-25 | 4:41 | 49.985
2020-10-25 | 4:41 | 49.982
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.977
2020-10-25 | 4:41 | 49.974
2020-10-25 | 4:41 | 49.972
2020-10-25 | 4:41 | 49.973
2020-10-25 | 4:41 | 49.974
2020-10-25 | 4:41 | 49.975
2020-10-25 | 4:41 | 49.977
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.98
2020-10-25 | 4:41 | 49.98
2020-10-25 | 4:41 | 49.981
2020-10-25 | 4:41 | 49.982
2020-10-25 | 4:41 | 49.981
2020-10-25 | 4:41 | 49.981
2020-10-25 | 4:41 | 49.98
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.979
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.977
2020-10-25 | 4:41 | 49.978
2020-10-25 | 4:41 | 49.977
2020-10-25 | 4:42 | 49.976
2020-10-25 | 4:42 | 49.968
2020-10-25 | 4:42 | 49.836
2020-10-25 | 4:42 | 49.767
2020-10-25 | 4:42 | 49.715
2020-10-25 | 4:42 | 49.729
2020-10-25 | 4:42 | 49.758
2020-10-25 | 4:42 | 49.793
2020-10-25 | 4:42 | 49.825
2020-10-25 | 4:42 | 49.869
2020-10-25 | 4:42 | 49.901
2020-10-25 | 4:42 | 49.918
2020-10-25 | 4:42 | 49.928
2020-10-25 | 4:42 | 49.926
2020-10-25 | 4:42 | 49.923
2020-10-25 | 4:42 | 49.919
2020-10-25 | 4:42 | 49.916
2020-10-25 | 4:42 | 49.918
2020-10-25 | 4:42 | 49.923
2020-10-25 | 4:42 | 49.928
2020-10-25 | 4:42 | 49.932
2020-10-25 | 4:42 | 49.934
2020-10-25 | 4:42 | 49.935
2020-10-25 | 4:42 | 49.937
2020-10-25 | 4:42 | 49.94
2020-10-25 | 4:42 | 49.942
2020-10-25 | 4:42 | 49.943
2020-10-25 | 4:42 | 49.941
2020-10-25 | 4:42 | 49.938
2020-10-25 | 4:42 | 49.936
2020-10-25 | 4:42 | 49.934
2020-10-25 | 4:42 | 49.934
2020-10-25 | 4:42 | 49.936
2020-10-25 | 4:42 | 49.939
2020-10-25 | 4:42 | 49.945
2020-10-25 | 4:42 | 49.947
2020-10-25 | 4:42 | 49.95
2020-10-25 | 4:42 | 49.953
2020-10-25 | 4:42 | 49.957
2020-10-25 | 4:42 | 49.956
2020-10-25 | 4:42 | 49.953
2020-10-25 | 4:42 | 49.952
2020-10-25 | 4:42 | 49.95
2020-10-25 | 4:42 | 49.949
2020-10-25 | 4:42 | 49.947
2020-10-25 | 4:42 | 49.951
2020-10-25 | 4:42 | 49.958
2020-10-25 | 4:42 | 49.967
2020-10-25 | 4:42 | 49.976
2020-10-25 | 4:42 | 49.979
2020-10-25 | 4:42 | 49.982
2020-10-25 | 4:42 | 49.984
2020-10-25 | 4:42 | 49.985
2020-10-25 | 4:42 | 49.984
2020-10-25 | 4:42 | 49.983
2020-10-25 | 4:42 | 49.982
2020-10-25 | 4:42 | 49.981
2020-10-25 | 4:42 | 49.981
2020-10-25 | 4:42 | 49.981
2020-10-25 | 4:42 | 49.979
2020-10-25 | 4:42 | 49.976
2020-10-25 | 4:43 | 49.974
2020-10-25 | 4:43 | 49.973
2020-10-25 | 4:43 | 49.972
2020-10-25 | 4:43 | 49.974
2020-10-25 | 4:43 | 49.976
2020-10-25 | 4:43 | 49.979
2020-10-25 | 4:43 | 49.984
2020-10-25 | 4:43 | 49.987
2020-10-25 | 4:43 | 49.989
2020-10-25 | 4:43 | 49.989
2020-10-25 | 4:43 | 49.989
2020-10-25 | 4:43 | 49.991
2020-10-25 | 4:43 | 49.993
2020-10-25 | 4:43 | 49.994
2020-10-25 | 4:43 | 49.993
2020-10-25 | 4:43 | 49.993
2020-10-25 | 4:43 | 49.994
2020-10-25 | 4:43 | 49.993
2020-10-25 | 4:43 | 49.992
2020-10-25 | 4:43 | 49.992
2020-10-25 | 4:43 | 49.992
2020-10-25 | 4:43 | 49.993
2020-10-25 | 4:43 | 49.994
2020-10-25 | 4:43 | 49.994
2020-10-25 | 4:43 | 49.996
2020-10-25 | 4:43 | 49.998
2020-10-25 | 4:43 | 50
2020-10-25 | 4:43 | 50.002
2020-10-25 | 4:43 | 50.004

## Event 20201030-1
In UTC
Date | Time | Freq
2020-10-30 | 11:09 | 50.029
2020-10-30 | 11:09 | 50.027
2020-10-30 | 11:09 | 50.026
2020-10-30 | 11:09 | 50.023
2020-10-30 | 11:09 | 50.023
2020-10-30 | 11:09 | 50.021
2020-10-30 | 11:09 | 50.02
2020-10-30 | 11:09 | 50.018
2020-10-30 | 11:09 | 50.018
2020-10-30 | 11:09 | 50.015
2020-10-30 | 11:09 | 50.017
2020-10-30 | 11:09 | 50.016
2020-10-30 | 11:09 | 50.015
2020-10-30 | 11:09 | 50.014
2020-10-30 | 11:09 | 50.013
2020-10-30 | 11:09 | 50.013
2020-10-30 | 11:09 | 50.015
2020-10-30 | 11:09 | 50.019
2020-10-30 | 11:09 | 50.022
2020-10-30 | 11:09 | 50.023
2020-10-30 | 11:09 | 50.026
2020-10-30 | 11:09 | 50.028
2020-10-30 | 11:09 | 50.032
2020-10-30 | 11:09 | 50.037
2020-10-30 | 11:09 | 50.039
2020-10-30 | 11:09 | 50.042
2020-10-30 | 11:09 | 50.045
2020-10-30 | 11:09 | 50.046
2020-10-30 | 11:09 | 50.048
2020-10-30 | 11:09 | 50.049
2020-10-30 | 11:10 | 50.051
2020-10-30 | 11:10 | 50.048
2020-10-30 | 11:10 | 50.049
2020-10-30 | 11:10 | 50.047
2020-10-30 | 11:10 | 50.043
2020-10-30 | 11:10 | 50.04
2020-10-30 | 11:10 | 50.036
2020-10-30 | 11:10 | 50.033
2020-10-30 | 11:10 | 50.03
2020-10-30 | 11:10 | 50.028
2020-10-30 | 11:10 | 50.03
2020-10-30 | 11:10 | 50.032
2020-10-30 | 11:10 | 50.032
2020-10-30 | 11:10 | 50.033
2020-10-30 | 11:10 | 50.035
2020-10-30 | 11:10 | 50.036
2020-10-30 | 11:10 | 50.038
2020-10-30 | 11:10 | 50.042
2020-10-30 | 11:10 | 50.044
2020-10-30 | 11:10 | 50.045
2020-10-30 | 11:10 | 50.047
2020-10-30 | 11:10 | 50.048
2020-10-30 | 11:10 | 50.05
2020-10-30 | 11:10 | 50.054
2020-10-30 | 11:10 | 50.055
2020-10-30 | 11:10 | 50.058
2020-10-30 | 11:10 | 50.06
2020-10-30 | 11:10 | 50.06
2020-10-30 | 11:10 | 50.055
2020-10-30 | 11:10 | 50.054
2020-10-30 | 11:10 | 50.052
2020-10-30 | 11:10 | 50.053
2020-10-30 | 11:10 | 50.052
2020-10-30 | 11:10 | 50.053
2020-10-30 | 11:10 | 50.05
2020-10-30 | 11:10 | 50.05
2020-10-30 | 11:10 | 50.05
2020-10-30 | 11:10 | 50.048
2020-10-30 | 11:10 | 50.048
2020-10-30 | 11:10 | 50.047
2020-10-30 | 11:10 | 50.048
2020-10-30 | 11:10 | 50.048
2020-10-30 | 11:10 | 50.047
2020-10-30 | 11:10 | 50.049
2020-10-30 | 11:10 | 50.054
2020-10-30 | 11:10 | 50.059
2020-10-30 | 11:10 | 50.06
2020-10-30 | 11:10 | 50.062
2020-10-30 | 11:10 | 50.062
2020-10-30 | 11:10 | 50.064
2020-10-30 | 11:10 | 50.063
2020-10-30 | 11:10 | 50.059
2020-10-30 | 11:10 | 50.059
2020-10-30 | 11:10 | 50.057
2020-10-30 | 11:10 | 50.055
2020-10-30 | 11:10 | 50.057
2020-10-30 | 11:10 | 50.058
2020-10-30 | 11:10 | 50.057
2020-10-30 | 11:10 | 50.061
2020-10-30 | 11:10 | 50.064
2020-10-30 | 11:10 | 50.065
2020-10-30 | 11:11 | 50.062
2020-10-30 | 11:11 | 50.063
2020-10-30 | 11:11 | 50.062
2020-10-30 | 11:11 | 50.061
2020-10-30 | 11:11 | 50.06
2020-10-30 | 11:11 | 50.061
2020-10-30 | 11:11 | 50.061
2020-10-30 | 11:11 | 50.06
2020-10-30 | 11:11 | 50.06
2020-10-30 | 11:11 | 50.063
2020-10-30 | 11:11 | 50.066
2020-10-30 | 11:11 | 50.069
2020-10-30 | 11:11 | 50.069
2020-10-30 | 11:11 | 50.071
2020-10-30 | 11:11 | 50.071
2020-10-30 | 11:11 | 50.072
2020-10-30 | 11:11 | 50.07
2020-10-30 | 11:11 | 50.038
2020-10-30 | 11:11 | 49.926
2020-10-30 | 11:11 | 49.831
2020-10-30 | 11:11 | 49.762
2020-10-30 | 11:11 | 49.709
2020-10-30 | 11:11 | 49.677
2020-10-30 | 11:11 | 49.66
2020-10-30 | 11:11 | 49.651
2020-10-30 | 11:11 | 49.645
2020-10-30 | 11:11 | 49.645
2020-10-30 | 11:11 | 49.643
2020-10-30 | 11:11 | 49.644
2020-10-30 | 11:11 | 49.642
2020-10-30 | 11:11 | 49.642
2020-10-30 | 11:11 | 49.643
2020-10-30 | 11:11 | 49.644
2020-10-30 | 11:11 | 49.646
2020-10-30 | 11:11 | 49.645
2020-10-30 | 11:11 | 49.642
2020-10-30 | 11:11 | 49.639
2020-10-30 | 11:11 | 49.635
2020-10-30 | 11:11 | 49.631
2020-10-30 | 11:11 | 49.627
2020-10-30 | 11:11 | 49.623
2020-10-30 | 11:11 | 49.62
2020-10-30 | 11:11 | 49.619
2020-10-30 | 11:11 | 49.615
2020-10-30 | 11:11 | 49.613
2020-10-30 | 11:11 | 49.615
2020-10-30 | 11:11 | 49.615
2020-10-30 | 11:11 | 49.619
2020-10-30 | 11:11 | 49.621
2020-10-30 | 11:11 | 49.626
2020-10-30 | 11:11 | 49.628
2020-10-30 | 11:11 | 49.63
2020-10-30 | 11:11 | 49.629
2020-10-30 | 11:11 | 49.627
2020-10-30 | 11:11 | 49.624
2020-10-30 | 11:11 | 49.622
2020-10-30 | 11:11 | 49.62
2020-10-30 | 11:11 | 49.62
2020-10-30 | 11:11 | 49.619
2020-10-30 | 11:12 | 49.615
2020-10-30 | 11:12 | 49.612
2020-10-30 | 11:12 | 49.612
2020-10-30 | 11:12 | 49.614
2020-10-30 | 11:12 | 49.614
2020-10-30 | 11:12 | 49.615
2020-10-30 | 11:12 | 49.615
2020-10-30 | 11:12 | 49.616
2020-10-30 | 11:12 | 49.618
2020-10-30 | 11:12 | 49.619
2020-10-30 | 11:12 | 49.62
2020-10-30 | 11:12 | 49.618
2020-10-30 | 11:12 | 49.618
2020-10-30 | 11:12 | 49.622
2020-10-30 | 11:12 | 49.624
2020-10-30 | 11:12 | 49.624
2020-10-30 | 11:12 | 49.623
2020-10-30 | 11:12 | 49.621
2020-10-30 | 11:12 | 49.62
2020-10-30 | 11:12 | 49.618
2020-10-30 | 11:12 | 49.62
2020-10-30 | 11:12 | 49.622
2020-10-30 | 11:12 | 49.624
2020-10-30 | 11:12 | 49.624
2020-10-30 | 11:12 | 49.624
2020-10-30 | 11:12 | 49.623
2020-10-30 | 11:12 | 49.622
2020-10-30 | 11:12 | 49.621
2020-10-30 | 11:12 | 49.618
2020-10-30 | 11:12 | 49.613
2020-10-30 | 11:12 | 49.609
2020-10-30 | 11:12 | 49.605
2020-10-30 | 11:12 | 49.613
2020-10-30 | 11:12 | 49.625
2020-10-30 | 11:12 | 49.634
2020-10-30 | 11:12 | 49.64
2020-10-30 | 11:12 | 49.646
2020-10-30 | 11:12 | 49.651
2020-10-30 | 11:12 | 49.657
2020-10-30 | 11:12 | 49.665
2020-10-30 | 11:12 | 49.674
2020-10-30 | 11:12 | 49.68
2020-10-30 | 11:12 | 49.686
2020-10-30 | 11:12 | 49.691
2020-10-30 | 11:12 | 49.696
2020-10-30 | 11:12 | 49.7
2020-10-30 | 11:12 | 49.705
2020-10-30 | 11:12 | 49.711
2020-10-30 | 11:12 | 49.718
2020-10-30 | 11:12 | 49.723
2020-10-30 | 11:12 | 49.725
2020-10-30 | 11:12 | 49.728
2020-10-30 | 11:12 | 49.733
2020-10-30 | 11:12 | 49.736
2020-10-30 | 11:12 | 49.739
2020-10-30 | 11:12 | 49.741
2020-10-30 | 11:12 | 49.742
2020-10-30 | 11:12 | 49.746
2020-10-30 | 11:12 | 49.751
2020-10-30 | 11:12 | 49.755
2020-10-30 | 11:12 | 49.76
2020-10-30 | 11:13 | 49.764
2020-10-30 | 11:13 | 49.768
2020-10-30 | 11:13 | 49.772
2020-10-30 | 11:13 | 49.774
2020-10-30 | 11:13 | 49.778
2020-10-30 | 11:13 | 49.781
2020-10-30 | 11:13 | 49.786
2020-10-30 | 11:13 | 49.791
2020-10-30 | 11:13 | 49.796
2020-10-30 | 11:13 | 49.8
2020-10-30 | 11:13 | 49.803
2020-10-30 | 11:13 | 49.805
2020-10-30 | 11:13 | 49.806
2020-10-30 | 11:13 | 49.805
2020-10-30 | 11:13 | 49.803
2020-10-30 | 11:13 | 49.802
2020-10-30 | 11:13 | 49.799
2020-10-30 | 11:13 | 49.797
2020-10-30 | 11:13 | 49.796
2020-10-30 | 11:13 | 49.796
2020-10-30 | 11:13 | 49.797
2020-10-30 | 11:13 | 49.798
2020-10-30 | 11:13 | 49.801
2020-10-30 | 11:13 | 49.803
2020-10-30 | 11:13 | 49.806
2020-10-30 | 11:13 | 49.807
2020-10-30 | 11:13 | 49.807
2020-10-30 | 11:13 | 49.807
2020-10-30 | 11:13 | 49.808
2020-10-30 | 11:13 | 49.807
2020-10-30 | 11:13 | 49.807
2020-10-30 | 11:13 | 49.808
2020-10-30 | 11:13 | 49.807
2020-10-30 | 11:13 | 49.808
2020-10-30 | 11:13 | 49.809
2020-10-30 | 11:13 | 49.812
2020-10-30 | 11:13 | 49.816
2020-10-30 | 11:13 | 49.819
2020-10-30 | 11:13 | 49.822
2020-10-30 | 11:13 | 49.825
2020-10-30 | 11:13 | 49.826
2020-10-30 | 11:13 | 49.826
2020-10-30 | 11:13 | 49.827
2020-10-30 | 11:13 | 49.828
2020-10-30 | 11:13 | 49.83
2020-10-30 | 11:13 | 49.83
2020-10-30 | 11:13 | 49.833
2020-10-30 | 11:13 | 49.837
2020-10-30 | 11:13 | 49.839
2020-10-30 | 11:13 | 49.842
2020-10-30 | 11:13 | 49.843
2020-10-30 | 11:13 | 49.843
2020-10-30 | 11:13 | 49.842
2020-10-30 | 11:13 | 49.84
2020-10-30 | 11:13 | 49.836
2020-10-30 | 11:13 | 49.833
2020-10-30 | 11:13 | 49.832
2020-10-30 | 11:13 | 49.833
2020-10-30 | 11:13 | 49.834
2020-10-30 | 11:14 | 49.838
2020-10-30 | 11:14 | 49.839
2020-10-30 | 11:14 | 49.84
2020-10-30 | 11:14 | 49.84
2020-10-30 | 11:14 | 49.839
2020-10-30 | 11:14 | 49.84
2020-10-30 | 11:14 | 49.839
2020-10-30 | 11:14 | 49.839
2020-10-30 | 11:14 | 49.838
2020-10-30 | 11:14 | 49.838
2020-10-30 | 11:14 | 49.839
2020-10-30 | 11:14 | 49.841
2020-10-30 | 11:14 | 49.845
2020-10-30 | 11:14 | 49.848
2020-10-30 | 11:14 | 49.851
2020-10-30 | 11:14 | 49.854
2020-10-30 | 11:14 | 49.857
2020-10-30 | 11:14 | 49.857
2020-10-30 | 11:14 | 49.856
2020-10-30 | 11:14 | 49.855
2020-10-30 | 11:14 | 49.853
2020-10-30 | 11:14 | 49.848
2020-10-30 | 11:14 | 49.844
2020-10-30 | 11:14 | 49.843
2020-10-30 | 11:14 | 49.841
2020-10-30 | 11:14 | 49.84
2020-10-30 | 11:14 | 49.843
2020-10-30 | 11:14 | 49.844
2020-10-30 | 11:14 | 49.845
2020-10-30 | 11:14 | 49.845
2020-10-30 | 11:14 | 49.846
2020-10-30 | 11:14 | 49.847
2020-10-30 | 11:14 | 49.849
2020-10-30 | 11:14 | 49.85
2020-10-30 | 11:14 | 49.852
2020-10-30 | 11:14 | 49.853
2020-10-30 | 11:14 | 49.853
2020-10-30 | 11:14 | 49.854
2020-10-30 | 11:14 | 49.853
2020-10-30 | 11:14 | 49.851
2020-10-30 | 11:14 | 49.849
2020-10-30 | 11:14 | 49.847
2020-10-30 | 11:14 | 49.845
2020-10-30 | 11:14 | 49.845
2020-10-30 | 11:14 | 49.845
2020-10-30 | 11:14 | 49.847
2020-10-30 | 11:14 | 49.846
2020-10-30 | 11:14 | 49.847
2020-10-30 | 11:14 | 49.85
2020-10-30 | 11:14 | 49.85
2020-10-30 | 11:14 | 49.851
2020-10-30 | 11:14 | 49.853
2020-10-30 | 11:14 | 49.854
2020-10-30 | 11:14 | 49.858
2020-10-30 | 11:14 | 49.862
2020-10-30 | 11:14 | 49.863
2020-10-30 | 11:14 | 49.866
2020-10-30 | 11:14 | 49.87
2020-10-30 | 11:14 | 49.873
2020-10-30 | 11:14 | 49.873
2020-10-30 | 11:14 | 49.876
2020-10-30 | 11:15 | 49.877
2020-10-30 | 11:15 | 49.879
2020-10-30 | 11:15 | 49.88
2020-10-30 | 11:15 | 49.881
2020-10-30 | 11:15 | 49.882
2020-10-30 | 11:15 | 49.885
2020-10-30 | 11:15 | 49.886
2020-10-30 | 11:15 | 49.889
2020-10-30 | 11:15 | 49.892
2020-10-30 | 11:15 | 49.895
2020-10-30 | 11:15 | 49.898
2020-10-30 | 11:15 | 49.903
2020-10-30 | 11:15 | 49.906
2020-10-30 | 11:15 | 49.907
2020-10-30 | 11:15 | 49.908
2020-10-30 | 11:15 | 49.909
2020-10-30 | 11:15 | 49.908
2020-10-30 | 11:15 | 49.909
2020-10-30 | 11:15 | 49.909
2020-10-30 | 11:15 | 49.909
2020-10-30 | 11:15 | 49.908
2020-10-30 | 11:15 | 49.907
2020-10-30 | 11:15 | 49.907
2020-10-30 | 11:15 | 49.91
2020-10-30 | 11:15 | 49.911
2020-10-30 | 11:15 | 49.912
2020-10-30 | 11:15 | 49.913
2020-10-30 | 11:15 | 49.916
2020-10-30 | 11:15 | 49.92
2020-10-30 | 11:15 | 49.922
2020-10-30 | 11:15 | 49.922
2020-10-30 | 11:15 | 49.921
2020-10-30 | 11:15 | 49.922
2020-10-30 | 11:15 | 49.924
2020-10-30 | 11:15 | 49.926
2020-10-30 | 11:15 | 49.927
2020-10-30 | 11:15 | 49.928
2020-10-30 | 11:15 | 49.932
2020-10-30 | 11:15 | 49.935
2020-10-30 | 11:15 | 49.938
2020-10-30 | 11:15 | 49.939
2020-10-30 | 11:15 | 49.937
2020-10-30 | 11:15 | 49.935
2020-10-30 | 11:15 | 49.935
2020-10-30 | 11:15 | 49.935
2020-10-30 | 11:15 | 49.936
2020-10-30 | 11:15 | 49.936
2020-10-30 | 11:15 | 49.937
2020-10-30 | 11:15 | 49.938
2020-10-30 | 11:15 | 49.942
2020-10-30 | 11:15 | 49.945
2020-10-30 | 11:15 | 49.947
2020-10-30 | 11:15 | 49.948
2020-10-30 | 11:15 | 49.948
2020-10-30 | 11:15 | 49.949
2020-10-30 | 11:15 | 49.949
2020-10-30 | 11:15 | 49.947
2020-10-30 | 11:15 | 49.945
2020-10-30 | 11:15 | 49.944
2020-10-30 | 11:16 | 49.943
2020-10-30 | 11:16 | 49.943
2020-10-30 | 11:16 | 49.943
2020-10-30 | 11:16 | 49.945
2020-10-30 | 11:16 | 49.947
2020-10-30 | 11:16 | 49.948
2020-10-30 | 11:16 | 49.949
2020-10-30 | 11:16 | 49.95
2020-10-30 | 11:16 | 49.952
2020-10-30 | 11:16 | 49.952
2020-10-30 | 11:16 | 49.952
2020-10-30 | 11:16 | 49.95
2020-10-30 | 11:16 | 49.949
2020-10-30 | 11:16 | 49.948
2020-10-30 | 11:16 | 49.948
2020-10-30 | 11:16 | 49.95
2020-10-30 | 11:16 | 49.95
2020-10-30 | 11:16 | 49.952
2020-10-30 | 11:16 | 49.954
2020-10-30 | 11:16 | 49.956
2020-10-30 | 11:16 | 49.959
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.959
2020-10-30 | 11:16 | 49.957
2020-10-30 | 11:16 | 49.957
2020-10-30 | 11:16 | 49.959
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.961
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.96
2020-10-30 | 11:16 | 49.961
2020-10-30 | 11:16 | 49.963
2020-10-30 | 11:16 | 49.968
2020-10-30 | 11:16 | 49.97
2020-10-30 | 11:16 | 49.97
2020-10-30 | 11:16 | 49.967
2020-10-30 | 11:16 | 49.963
2020-10-30 | 11:16 | 49.961
2020-10-30 | 11:16 | 49.956
2020-10-30 | 11:16 | 49.952
2020-10-30 | 11:16 | 49.95
2020-10-30 | 11:16 | 49.948
2020-10-30 | 11:16 | 49.946
2020-10-30 | 11:16 | 49.944
2020-10-30 | 11:16 | 49.941
2020-10-30 | 11:16 | 49.941
2020-10-30 | 11:16 | 49.941
2020-10-30 | 11:16 | 49.941
2020-10-30 | 11:16 | 49.943
2020-10-30 | 11:16 | 49.946
2020-10-30 | 11:16 | 49.948
2020-10-30 | 11:16 | 49.95
2020-10-30 | 11:16 | 49.952
2020-10-30 | 11:16 | 49.957
2020-10-30 | 11:16 | 49.962
2020-10-30 | 11:16 | 49.966
2020-10-30 | 11:16 | 49.972
2020-10-30 | 11:16 | 49.976
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.983
2020-10-30 | 11:17 | 49.984
2020-10-30 | 11:17 | 49.986
2020-10-30 | 11:17 | 49.984
2020-10-30 | 11:17 | 49.984
2020-10-30 | 11:17 | 49.985
2020-10-30 | 11:17 | 49.986
2020-10-30 | 11:17 | 49.985
2020-10-30 | 11:17 | 49.982
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.98
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.982
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.982
2020-10-30 | 11:17 | 49.984
2020-10-30 | 11:17 | 49.983
2020-10-30 | 11:17 | 49.982
2020-10-30 | 11:17 | 49.98
2020-10-30 | 11:17 | 49.978
2020-10-30 | 11:17 | 49.977
2020-10-30 | 11:17 | 49.976
2020-10-30 | 11:17 | 49.977
2020-10-30 | 11:17 | 49.977
2020-10-30 | 11:17 | 49.979
2020-10-30 | 11:17 | 49.981
2020-10-30 | 11:17 | 49.983
2020-10-30 | 11:17 | 49.985
2020-10-30 | 11:17 | 49.987
2020-10-30 | 11:17 | 49.988
2020-10-30 | 11:17 | 49.989
2020-10-30 | 11:17 | 49.99
2020-10-30 | 11:17 | 49.991
2020-10-30 | 11:17 | 49.992
2020-10-30 | 11:17 | 49.99
2020-10-30 | 11:17 | 49.99
2020-10-30 | 11:17 | 49.989
2020-10-30 | 11:17 | 49.991
2020-10-30 | 11:17 | 49.991
2020-10-30 | 11:17 | 49.989
2020-10-30 | 11:17 | 49.987
2020-10-30 | 11:17 | 49.985
2020-10-30 | 11:17 | 49.985
2020-10-30 | 11:17 | 49.987
2020-10-30 | 11:17 | 49.991
2020-10-30 | 11:17 | 49.993
2020-10-30 | 11:17 | 49.997
2020-10-30 | 11:17 | 50.001
2020-10-30 | 11:17 | 50.004
2020-10-30 | 11:17 | 50.005
2020-10-30 | 11:17 | 50.005
2020-10-30 | 11:17 | 50.007
2020-10-30 | 11:17 | 50.009
2020-10-30 | 11:17 | 50.014
2020-10-30 | 11:17 | 50.019
2020-10-30 | 11:18 | 50.024
2020-10-30 | 11:18 | 50.028
2020-10-30 | 11:18 | 50.031
2020-10-30 | 11:18 | 50.034
2020-10-30 | 11:18 | 50.035
2020-10-30 | 11:18 | 50.038
2020-10-30 | 11:18 | 50.041
2020-10-30 | 11:18 | 50.044
2020-10-30 | 11:18 | 50.047
2020-10-30 | 11:18 | 50.046
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.05
2020-10-30 | 11:18 | 50.05
2020-10-30 | 11:18 | 50.052
2020-10-30 | 11:18 | 50.052
2020-10-30 | 11:18 | 50.053
2020-10-30 | 11:18 | 50.054
2020-10-30 | 11:18 | 50.053
2020-10-30 | 11:18 | 50.051
2020-10-30 | 11:18 | 50.05
2020-10-30 | 11:18 | 50.049
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.048
2020-10-30 | 11:18 | 50.047
2020-10-30 | 11:18 | 50.047
2020-10-30 | 11:18 | 50.047