# DATED                                                                    2021

NATIONAL GRID ELECTRICITY SYSTEM OPERATOR LIMITED

and

[Company name]

SERVICE AGREEMENT

FOR THE PROVISION

OF A STABILITY COMPENSATION SERVICE

at

[Site name]

Contract Log No: [National Grid to provide]

Subject to Contract

Draft v.1

© National Grid Electricity System Operator Limited

TABLE OF CONTENTS

CLAUSE HEADING                                                                                  PAGE NO.

1.	DEFINITIONS AND INTERPRETATION	3

2.	COMMENCEMENT AND TERM	4

3.	IMPLEMENTATION OF THE WORKS	4

5.	SERVICE FEES	9

6.	REPROVING TESTS	10

7.	MONITORING	11

8.	GRID CODE	12

9.	PAYMENT	13

10.	TERMINATION AND SUSPENSION	15

11.	LIMITATION OF LIABILITY	18

12.	METERING	20

13.	CONFIDENTIALITY AND ANNOUNCEMENTS	20

14.	DISCLOSURE OF INFORMATION	22

15.	DISPUTE RESOLUTION	22

16.	ENTIRE AGREEMENT	23

17.	FORCE MAJEURE	24

18.	VARIATIONS	24

19.	NO PARTNERSHIP	24

20.	WARRANTIES AND INDEMNITY	24

21.	CHANGE IN LAW	25

22.	CUSC	26

23.	ANTI-BRIBERY	26

24.	EMR	26

SCHEDULE A – Definitions	29

SCHEDULE B – Provider Details	37

SCHEDULE C –  Post Tender Milestones	38

SCHEDULE D – Proving Tests and Reproving Tests	40

SCHEDULE E - Technical Performance Requirements	41

SCHEDULE F - Payments	48

SCHEDULE G – Notices	53

SCHEDULE H – Redeclaration Forms/ Restoration Notice	54

THIS AGREEMENT is made the [              ] of [                                                 ] 2021

BETWEEN:-

- NATIONAL GRID ELECTRICITY SYSTEM OPERATOR LIMITED, a company registered in England with number 11014226 whose registered office is at 1-3 Strand, London, WC2N 5EH (the “Company” which expression shall include its permitted successors and/or assigns);

- [Company name] a company registered in England with number [Company number] whose registered office is at [                     ] (the “Provider” which expression shall include its permitted successors and/or assigns),

each a “Party” and, together, the “Parties”.

WHEREAS:-

- The Company issued an Invitation to Tender (“ITT”) for the NOA Stability Pathfinder Phase 2 service on [       ] 2021 for the provision of a stability compensation service in Scotland and the Provider has submitted a tender for the provision of such service from its Facility.

- The Parties have entered into this Agreement in accordance with the rules of the ITT.

NOW IT IS HEREBY AGREED as follows:-

# DEFINITIONS AND INTERPRETATION

  - Unless the subject matter or context otherwise requires or is inconsistent therewith, terms and expressions defined in paragraph 11.3 of the Connection and Use of System Code, the Glossary and Definitions section of the Grid Code or in Schedule A shall have the same meanings where used in this Agreement.

  - In this Agreement:-

    - except where the context otherwise requires, references to a particular Clause, Paragraph, Schedule or Appendix shall be a reference to that Clause, Clause, Paragraph, Schedule or Appendix in or to this Agreement;

    - the table of contents and headings are inserted for convenience only and shall be ignored in construing this Agreement;

    - references to the words “include” or “including” are to be construed without limitation;

    - except where the context otherwise requires, any reference to an Act of Parliament or any Part or Section or other provision of, or Schedule to, an Act of Parliament shall be construed, at the particular time, as including a reference to any amendment, modification, extension or re-enactment thereof then in force and to all instruments, orders or regulations then in force and made under or deriving validity from the relevant Act of Parliament;

    - references to the masculine shall include the feminine and references in the singular shall include references in the plural and vice versa;

    - except where the context otherwise requires, any reference to a “person” includes any individual, partnership, firm, company, corporation, joint venture, trust, association, organisation or other entity, in each case whether or not having separate legal personality; and

    - the Schedules form part of and are incorporated in this Agreement and references to this Agreement shall include references to the Schedules provided always that in the event of inconsistency or conflict between any matters set out in any Schedule and any matter set out in the main body of this Agreement the latter shall prevail.

# COMMENCEMENT AND TERM

  - The provisions of this Agreement shall, subject to Clause 2.2, apply from the date stated on the front page of this Agreement and, subject always to earlier termination in accordance with Clause 9 (Termination), shall continue in force and effect until the expiry of the Service Term.

  - This Agreement, other than this Clause 2 and Clauses [10 (Termination and Suspension) to 23 (Anti-Bribery)], shall in all respects be conditional on:

    - [the accession of the Provider to the BSC and the registration of the Facility as a BM Unit];

    - [the Provider becoming bound by the relevant Bilateral Agreement] ;

    - [the Provider acceding to the CUSC]; and

    - delivery by the Provider to the Company of Acceptable Security for an amount equal to the LAD Cap,

(together, the “Conditions Precedent”) by no later than the Longstop Date.

# IMPLEMENTATION OF THE WORKS

  - The Provider shall use reasonable endeavours to complete the Works in accordance with Good Industry Practice by the Scheduled Operations Date and, without limiting that obligation, shall use reasonable endeavours to satisfy the Post Tender Milestones by not later than the PTM Date.

  - The Provider shall notify the Company by no later than the PTM Date when it considers it has satisfied the Post Tender Milestones and shall provide reasonable evidence thereof. The Company shall, acting reasonably, notify the Provider in writing as soon as reasonably practicable after receipt of the Provider’s notice either:

    - that it considers the Post Tender Milestones have been satisfied (or, in its absolute discretion, waives any such requirement), in which event the Provider shall then continue to use reasonable endeavours to complete the Works by the Scheduled Operations Date; or

    - that it considers that the requirements of the Post Tender Milestones have not been satisfied in which event the provisions of Clause 3.3 shall apply.

  - If the Provider fails to give notice under Clause 3.2 or the Company issues a notice under Clause 3.2.2, the Company may request such evidence or additional evidence regarding the Provider’s progress toward satisfaction of the Post Tender Milestones as it may reasonably require and the Parties shall meet to consider in good faith whether there are reasonable prospects that the Post Tender Milestones will be satisfied within two (2) months after the PTM Date. Once the Company considers that it is in possession of sufficient evidence, it shall, save to the extent that the provisions of Clause 17 (Force Majeure) apply, make a determination and notify the Provider in writing either:

    - that it considers there to be a reasonable prospect that the Post Tender Milestones will be satisfied within two (2) months after the PTM Date, in which event the Provider shall then continue to use reasonable endeavours to complete the Works by the Scheduled Operations Date; or

    - that it considers there is no reasonable prospect of the Provider being capable of satisfying the Post Tender Milestones within two (2) months after the PTM Date, in which event this Agreement (to the extent then in force) shall terminate on the date of the Company’s notice.

  - The Provider shall notify the Company in writing when the Works are substantially completed and the Facility is capable in the Provider's opinion of providing the Stability Compensation Service; the Parties shall then agree the date on which the Provider shall carry out a Proving Test of the Facility. [The Provider’s confirmation must be accompanied by evidence to the Company’s reasonable satisfaction that the Provider has: (i) acceded to the BSC and registered the Facility as a BM Unit; (ii) become bound by the relevant Bilateral Agreement; and (iii) acceded to the CUSC.]

  - As soon as possible after the date on which the Proving Test has been completed, the Company shall notify the Provider whether it has passed or failed the Proving Test. Any dispute as to whether the Proving Test has been passed or failed may be referred by either Party to the Expert for determination.

  - If the Facility has not successfully passed the Proving Test by the Scheduled Operations Date then, save to the extent due to an event or circumstance of Force Majeure, the Provider shall pay to the Company, without deduction or set off, liquidated damages at the LAD Rate provided always that such liquidated damages shall not in any event exceed the LAD Cap.

  - If at any time the aggregate amount of liquidated damages payable under Clause 3.6 is equal to the LAD Cap and the Facility has not successfully completed the Proving Test then, save to the extent due to an event or circumstance of Force Majeure, the Company shall have the right to terminate this Agreement by written notice to the Provider.

  - For the purposes of Clause 3.73.6, liquidated damages shall be payable by the Provider to the Company on a monthly basis in accordance with Clause 9 (Payment) and the due date shall be ascertained accordingly.

  - If Force Majeure prevents successful completion of the Proving Test by the date falling twelve (12) months after the Scheduled Operations Date, the Company shall have the right to terminate this Agreement by written notice to the Provider.

- SERVICE PROVISION

Provision of Stability Compensation Service

  - The Provider agrees with effect from the Commercial Operations Date and throughout the Service Term to power, operate, maintain and repair the Facility and associated Plant and Apparatus in accordance with Good Industry Practice with a view to making the Facility Available in accordance with the Technical Performance Requirements, subject to planned maintenance and inspection periods agreed pursuant to Clause 4.10 (Maintenance of the Facility) and to deliver the Stability Compensation Service at the Point of Stability in accordance with the Company’s Instructions.

  - The Provider agrees at all times:

    - by the issue of Redeclarations and Restoration Notices to keep the Company updated as to the true levels of Inertia Capability, Reactive Capability and SCL Capability that the Facility is capable of providing; and

    - to maintain a single point of remote control in respect of the Connection Site of the Facility to facilitate the issue of Instructions and Instructions to End by the Company.

Stability Compensation Service Unavailability

  - The Provider shall, without delay on becoming aware that the Facility is no longer, or will no longer be, capable of providing to the full extent the Contracted Inertia Capability, Contracted Reactive Capability and the Contracted SCL Capability promptly notify the Company  [by facsimile] in the form set out in Forms A - C (as applicable) in Schedule H ( “Redeclaration”).  Each Redeclaration shall specify:

    - the level of Inertia Capability, Reactive Capability and SCL Capability  which the Facility will be capable of providing (if any);

    - the reasons for the reduction in the Inertia Capability, the Reactive Capability and the SCL Capability, which must be explained in reasonable detail and relate only to technical issues concerning the Facility; and

    - specify the steps that the Provider will take in order to restore the Contracted Inertia Capability, the Contracted Reactive Capability and the Contracted SCL Capability.

  - Following a Redeclaration, the Provider shall take all reasonable steps to restore the Contracted Inertia Capability, Contracted Reactive Capability and/or the Contracted SCL Capability (as the context requires) and keep the Company reasonably informed of progress in restoring such capability. The Provider shall, in the case of Contracted Inertia Capability and Contracted SCL Capability, notify the Company by facsimile in the form set out in Form D in Schedule H or, in the case of Contracted Reactive Capability, notify the Company by facsimile in the form set out in Form C in Schedule H (“Restoration Notice”) when that capability has been restored. The Provider shall, if so required by the Company by notice in writing, undertake a Reproving Test in accordance with Clause 6 (Reproving Tests) following the date of the Restoration Notice or if (in the absence of a Restoration Notice) the Company considers at any time that the Provider is not implementing the steps referred to in Clause 4.3.3.

Instruction of the Stability Compensation Service

  - It is acknowledged by the Provider that, in relation to any Settlement Period in which the Facility is Available, the Company shall have the right (but not any obligation) to issue an instruction (“Instruction”) to provide the Stability Compensation Service (including the required Reactive Power Mode and the required level of Reactive Power, being within the Contracted Reactive Capability or any reduced Reactive Capability specified in a Redeclaration) from the Facility, and subsequently notify the Provider when it no longer requires the provision of the Stability Compensation Service from the Facility (“Instruction to End”).

  - Following receipt of an Instruction, the Provider shall acknowledge receipt as soon as possible (but in any case by no later than [	] minutes from receipt of an Instruction) and shall take all necessary steps to ensure that the Facility is Synchronised to the Total System and, thereafter, operates throughout each Instructed Settlement Period in accordance with the Technical Performance Requirements until the time notified in the relevant Instruction to End.

Failure to comply with Instruction

  - If an Instruction is issued by the Company and:

    - the Facility fails to Synchronise (if not already Synchronised) within [  ] minutes of the time instructed by the Company then the Facility shall be treated as Unavailable in the Settlement Period in which the failure occurred and each subsequent Settlement Period until the Facility does Synchronise; and/or

    - in the absence of a Redeclaration stating that the Inertia Capability is 0, the Facility fails to provide Inertia Capability, then the Facility shall be treated as incapable of providing Inertia Capability in the Settlement Period in which the failure occurred and each subsequent Settlement Period until the Facility has been demonstrated to the Company’s satisfaction to have Inertia Capability which may, at the Company’s discretion, be by the Facility successfully passing a Reproving Test; and/or

    - in the absence of a Redeclaration stating that the SCL Capability is 0, the Facility fails to provide SCL Capability, then the Facility shall be treated as incapable of providing SCL Capability in the Settlement Period in which the failure occurred and each subsequent Settlement Period until the Facility has been demonstrated to the Company’s satisfaction to have SCL Capability which may, at the Company’s discretion, be by the Facility successfully passing a Reproving Test.

  - Promptly following each failure under Clause 4.7 the Provider shall notify the Company of the causes of the failure.

  - The Parties agree and acknowledge that Instructions, Instructions to End and also confirmations by the Provider of Instructions and Instructions to End transmitted and stored on EDL shall (except during periods when EDL is unavailable for whatever reason in which case communication shall be made by telephone, e-mail or facsimile (whichever is appropriate)) be conclusive evidence of the giving and/or receipt of any communication required to be given pursuant to the terms of Clauses 4.5 and 4.6.

Maintenance of the Facility

  - The Provider shall, prior to the commencement of each Contract Year, notify the Company in writing of the dates and times of all planned maintenance and inspection periods applicable to the Facility (“Maintenance Plan”) for the forthcoming Contract Year (except that for the first Contract Year, the Maintenance Plan shall be applicable for the purposes of this Agreement only for that part of the Contract Year commencing on the Service Commencement Date). The Provider may propose modifications to the Maintenance Plan from time to time during the Contract Year on no less than twenty-eight (28) days notice. The Maintenance Plan may include up to a maximum of fifteen (15) days of planned outages in any Contract Year (to be reduced on a pro rata basis if the Maintenance Plan covers a period of less than twelve (12) calendar months).

  - Within fourteen (14) days of the Provider’s notification of the Maintenance Plan or any modification thereto under Clause 4.10, the Company shall notify the Provider of its agreement with or objections to the Maintenance Plan or any modification thereto and, if the Company shall make no notification within such time, it shall become binding on the Parties. The Parties shall act in good faith and use reasonable endeavours to resolve any objections notified by the Company taking into account maintenance practices consistent with Good Industry Practice and the Maintenance Plan shall be amended accordingly.

Substitution of the Facility

  - If at any time the Provider notifies the Company that it wishes to substitute the Facility (the “Retired Facility”) with any other facility at the same Point of Stability which has a Response Time equal to or better than the Retired Facility and can achieve not less than the Contracted SCL Capability and Contracted Inertia Capability  (the “Substitute Facility”) it shall take such steps as the Company may reasonably require, including:

    - submission to the Company of a Maintenance Plan in respect of the Substitute Facility and approval of that Maintenance Plan by the Company on the basis set out in Clause 4.10 which shall apply in respect of the Substitute Facility mutatis mutandis; and

    - the successful completion of a Proving Test of the Substitute Facility pursuant to the principles set out in Schedule D, Part A to verify that the Substitute Facility is capable of providing the Stability Compensation Service in accordance with the Technical Performance Requirements.

  - If the Company confirms that it is satisfied with the steps taken by the Provider in accordance with Clause 4.12 (but not otherwise), the Parties shall, with effect from the date of such confirmation, treat the Substitute Facility as the Facility for all purposes of this Agreement.

# SERVICE FEES

  - The Company shall pay to the Provider in respect of each month in the Service Term:

    - a sum calculated in accordance with Schedule F, Part A, paragraph A.1 (“Availability Payment”) by reference to each Settlement Period in which the Facility is either: (i) Available and capable of providing Inertia Capability and/or SCL Capability, in which case the Availability Payment will be calculated by reference to the Contracted Inertia Capability and Contracted SCL Capability or, in each case, any lower values specified in a Redeclaration; or (ii) on an Approved Outage, in which case the Availability Payment will be calculated by reference to the Contracted Inertia Capability and Contracted SCL Capability; and

    - a sum calculated in accordance with Schedule F, Part B (“Reactive Power Payment”) by reference to each Instructed Settlement Period.

  - The Provider shall pay to the Company:

    - in respect of each month (when applicable), a sum calculated in accordance with Schedule F, Part A, paragraph A.2 (“Availability Rebate”), which shall not exceed the amount of the Availability Payment for that month; and

    - in respect of each Contract Year, if any amount in respect of the monthly Availability Rebates for the Contract Year has not been off-set against monthly Availability Payments and remains due and payable by the Provider, a sum calculated following the end of that Contract Year or on earlier termination under Clause 9 (Termination) in accordance with Schedule F, Part A, paragraph A.3 (“Annual Reconciliation Payment”), which shall not exceed the aggregate amount of Availability Payments for that Contract Year.

  - No payment shall be made by the Company pursuant to Clause 5.1 in relation to any Settlement Period in respect of which the Provider fails to comply with any of its obligations under Clause 4 (Service Provision) of this Agreement.

# REPROVING TESTS

  - Without prejudice to the Company’s right to conduct a test in accordance with Grid Code OC5.5.1, the Company shall have the right: (i) pursuant to Clause 4.4, Clause 4.7.2 or Clause 4.7.3; or (ii) otherwise not more than twice in any twelve (12) month period,  by notice in writing (“Test Notice”) to require the Provider to carry out a Reproving Test at a time no sooner than seven (7) Business Days after the time of issue of the Test Notice to determine whether the Facility is capable of operating in accordance with the Technical Operating Requirements, including providing the Contracted Inertia Capability, the Contracted Reactive Capability and the Contracted SCL Capability.

  - Upon receipt of a Test Notice, the Provider shall not issue a Redeclaration in respect of the time and the duration that the Reproving Test is instructed to be carried out (unless the Facility would be Unavailable by reason of a forced outage or maintenance specified in the Maintenance Plan or by reason of an event or circumstance of Force Majeure).

  - To commence a Reproving Test, the Company shall give the Provider an Instruction.  The performance of the Facility in response to that Instruction shall be assessed by the Company by reference to metering referred to in Clause 12 (Metering) and/or any Monitoring Equipment and at the option of the Provider shall be carried out in the presence of a reasonable number of representatives of the Provider and, if so requested, its lenders. If such metering and/or Monitoring Equipment is functioning accurately and indicates that the Provider is unable to comply with such Instruction then the Company shall notify the Provider that the Facility has failed the Reproving Test.

  - If the Facility fails a Reproving Test the values established by that test for Inertia Capability, Reactive Capability and/or SCL Capability shall become the values for Contracted Inertia Capability, Contracted Reactive Capability and/or Contracted SCL Capability.  For the purposes of this Clause 6 the Provider may require the Company to carry out one or more further Reproving Tests, on any Business Day on not less than forty eight (48) hours’ notice, which shall be carried out in accordance with the provisions of this Clause 6 as if the Company had issued an instruction at the time of notice from the Provider, and the values for Contracted Inertia Capability, Contracted Reactive Capability and/or Contracted SCL Capability shall be determined by the latest of such tests.

  - If a dispute arises relating to the performance of the Facility during a Reproving Test, the Company and the Provider shall attempt to resolve the dispute by discussion, and if they fail to reach agreement the Company shall carry out a further Reproving Test on any Business Day on not less than forty eight (48) hours’ notice which shall be carried out in accordance with the provisions of this Clause 6. If the Facility passes such further Reproving Test, it shall be deemed to have passed the first Reproving Test. If the Facility fails such further Reproving Test and a dispute arises on that further Reproving Test, the provisions of Clause 15 (Dispute Resolution) shall apply.

  - An instruction issued by the Company as part of a test in accordance with Grid Code OC5.5.1 or a Reproving Test carried out pursuant to this Clause 6 shall constitute an Instruction.

  - Subject to Clause 6.5, each Party shall bear its own costs incurred in connection with all Reproving Tests carried out pursuant to this Clause 6.

# MONITORING

  - After due consultation with the Provider, and upon reasonable prior notice to the Provider, the Company (and, subject to Clause 7.2.1, any approved sub-contractor) may install such monitoring equipment in accordance with Good Industry Practice as the Company considers necessary to monitor the Availability, capability and performance (including without limitation compliance with the Technical Performance Requirements) of the Facility, or any associated Plant or Apparatus owned and operated by the Provider (the “Monitoring Equipment”).The Monitoring Equipment which the Company wishes to install shall not interfere with the operation or maintenance of the Facility and shall be subject to inspection and approval by the Provider, such approval not to be unreasonably withheld or delayed. At the request of the Provider and with the consent of the Company (such consent not to be unreasonably withheld or delayed) the Provider shall be entitled (at its own cost) to install the Monitoring Equipment.  All ownership rights in such Monitoring Equipment shall at all times remain vested in the Company.

  - Where installation of the Monitoring Equipment is to be carried out by the Company (which shall be at the Company’s own cost), then:

    - the Provider shall provide to the Company all relevant information and assistance reasonably requested by the Company to install the Monitoring Equipment, and shall allow, subject to the Provider’s approval where necessary (such approval not to be unreasonably withheld or delayed), the Company and its employees and the Company’s authorised agents, suppliers, contractors and (subject to Clause 7.2.1) sub-contractors necessary access to the Facility and the Provider’s Plant and Apparatus and such other parts of the Connection Site as the Company may reasonably require provided however that such access shall not impair or adversely interfere with the operation or maintenance of the Facility.  Without limitation, the Provider shall be responsible at all times for ensuring that all necessary signals from the Facility are made available to the Monitoring Equipment at one location on the Connection Site; and

    - subject always to the Provider’s approval (not to be unreasonably withheld or delayed), the Company may sub-contract the installation of the Monitoring Equipment. Any sub-contractor nominated by the Company shall also be the subject of approval by the Provider (not to be unreasonably withheld or delayed).  For the avoidance of doubt, the Provider may request the removal of any particular sub-contractor if in its reasonable opinion the sub-contractor is in material breach of any relevant site safety or security procedures.

  - Where installation of the Monitoring Equipment is to be carried out by the Provider, then:

    - the Provider shall carry out the installation in accordance with Good Industry Practice and keep the Company updated on the progress of such installation;

    - the Provider shall permit the Company to carry out a Monitoring Equipment Proving Test (and such subsequent Monitoring Equipment Proving Test as may be reasonably required);

    - if the Monitoring Equipment fails to pass a Monitoring Equipment Proving Test on more than two occasions, the Provider shall permit the Company to carry out such installation, and the provisions of Clause 7.2 shall apply; and

    - the Provider shall be responsible at all times for ensuring that all necessary signals from the Facility are made available to the Monitoring Equipment at one location on the Connection Site.

  - The Provider hereby grants to the Company at the Company’s own cost the right to collect and record relevant data from the Monitoring Equipment once installed (without adversely interfering with the operation or maintenance of the Facility) which the Company undertakes to use solely for the purposes of this Agreement. Without prejudice to the rights under Clause 12 (Metering), the Company shall upon request and at the Provider’s own cost provide to the Provider copies of such data.

  - The cost of the Monitoring Equipment including the cost of (subject always to Clause 7.1) installing, repairing, maintaining, inspecting, retaining and (subject always to Clause 7.6) removing the Monitoring Equipment, and the collection of data therefrom, shall be borne by the Company.

  - The Provider shall, on reasonable notice in writing at any time from the Company or following expiry or termination of this Agreement:

    - permit the Company and its employees and the Company’s authorised agents, suppliers and contractors all necessary access to the Facility and the Provider’s Plant and Apparatus and such other parts of the Connection Site as the Company may reasonably require to remove the Monitoring Equipment provided however that such access shall not impair or adversely interfere with the operation or maintenance of the Facility; or

    - in circumstances where the Provider installed the Monitoring Equipment in accordance with Clause 7.3, remove the Monitoring Equipment and return it to the Company in good and serviceable condition.

  - For the purposes of this Agreement, the accuracy of the Monitoring Equipment shall be maintained in accordance with manufacturer’s tolerances or otherwise as agreed between the Parties in writing from time to time.

# GRID CODE

It is acknowledged by both Parties that the provision of the Stability Compensation Service in accordance with the terms hereof shall not relieve the Provider of any of its obligations set out in the Grid Code including without limitation its obligations (where applicable to the Provider) set out in Grid Code CC8.1 to provide Reactive Power (supplied otherwise than by means of the Stability Compensation Service) in accordance with Grid Code CC6.3.2 and CC6.3.4.

# PAYMENT

  - As soon as reasonably practicable and no later than eight (8) Business Days following the end of each calendar month the Company shall send to the Provider a statement (the “Monthly Statement”) consisting of:-

    - its calculation of the Availability Payment due to the Provider and any Availability Rebate due to the Company in respect of the previous calendar month;

    - in relation to the last calendar month in the Contract Year, its calculation of the Annual Availability Reconciliation Payment due from the Provider;

    - its calculation of the Reactive Power Payment due to the Provider in respect of the previous calendar month;

    - if relevant, adjustments to be made (net of interest) in relation to disputes concerning Availability Payments or Reactive Power Payments any month prior to the previous month; and

    - the net sum due to or from the Provider as a result thereof.

  - If the Provider disagrees with any dates times facts or calculations set out in the Monthly Statement, it shall state by notice in writing to the Company the reasons and facts which it relies upon in support of such disagreement. The Parties shall discuss and endeavour to resolve the matter and any adjustments agreed shall be included in the Monthly Statement next following the date of resolution of the dispute. The dates, times, facts and calculations set out in the Monthly Statement shall be binding upon the Parties until such time as they are reversed or revised by agreement between the Parties or otherwise determined pursuant to Clause 15 (Dispute Resolution).

  - Where:-

    - the Company discovers that any previous Monthly Statement contains an arithmetic error or omission; or

    - the Company becomes aware of any facts concerning matters provided by this Clause 9 (other than errors or omissions falling within Clause 9.3.1) which show that the payment made by or to the Provider was incorrect; or

    - the Provider establishes to the Company’s reasonable satisfaction that it was entitled to receive any additional payment, then the Company shall adjust the account between itself and the Provider in the next Monthly Statement which the Company issues, setting out the reason for the adjustment and the provisions of Clause 9.2 shall apply mutatis mutandis to such adjustment.

  - The Company shall pay to the Provider the amount shown as due from the Company in the Monthly Statement within three (3) Business Days after the date of issue.  The Provider shall pay to the Company the amount shown as due from the Provider in such statement within three (3) Business Days of the date on which the statement is issued.

  - If either Party (the “Defaulting Party”) fails to pay any amount properly due under this Agreement on the due date, then the Defaulting Party shall pay to the other Party interest on such overdue amount at the Base Rate plus three per cent (3%) from the due date on which such payment was properly due to (but excluding) the date of actual payment.  Any interest shall accrue from day to day.

  - If it is agreed or otherwise determined under Clause 9.2 that the Provider was entitled to a further payment from the Company, the Provider shall be entitled to interest at the Base Rate on the amount of such further payment from the date on which that sum would have been payable had it been included in the Monthly Statement for each Relevant Settlement Period until the date of payment.

  - If it is agreed or otherwise determined under Clause 9.2 that the Provider was not entitled to any payment it has received, the Company shall be entitled to interest at the Base Rate on the amount so paid from the date of payment until the date of repayment or the date when the Company makes a payment to the Provider which takes such payment into account.

  - Notwithstanding any other provision of this Agreement, the Parties shall not be limited in any way as to the evidence they may rely upon in any proceedings arising out of or in connection with payment for the Stability Compensation Service under this Agreement and the Parties agree that in the event and to the extent that either Party succeeds in proving in any such proceedings that the Stability Compensation  Service was or was not provided, the successful Party shall (without prejudice to any liquidated damages provision of this Agreement) be entitled to repayment of the sums already paid or payment of sums not paid as the case may be in respect of the Stability Compensation Service.

  - Save as otherwise expressly provided in this Agreement, sums payable by one Party to the other pursuant to this Agreement whether by way of charges, interest or otherwise shall (except to the extent otherwise required by law) be paid in full, free and clear of and without deduction, set-off or deferment in respect of any disputes or claims whatsoever save for sums the subject of a final award or judgement (after exhaustion of all appeals if this opportunity is taken) or which by agreement between the Company and the Provider may be so deducted or set off.

  - All amounts specified hereunder shall be exclusive of any Value Added Tax or other similar tax and the Company shall pay to the Provider Value Added Tax at the rate for the time being and from time to time properly chargeable in respect of the making available and/or supply of the Stability Compensation Service under this Agreement.

  - All payments by the Company to the Provider under this Agreement will be made by payment to the bank account details of which are notified to the Company by the Provider from time to time.

  - The submission of all Monthly Statements and facts and other evidence in support thereof and any questions in connection therewith from the Company to the Provider and vice versa in accordance with this Clause 9 must be made, in the absence of agreement to the contrary between the Parties, by 19.00 hours on the Business Day concerned.

  - The Provider hereby irrevocably consents to the operation of a self-billing system by the Company with regard to the payment for the Stability Compensation Service and will at all times throughout the Term maintain such consent. The Provider hereby undertakes to do (at the Company’s cost) all acts and things reasonably necessary to enable the Company to comply with the regulations of HM Customs and Excise as regards the self-billing of the Stability Compensation Service.

  - The provisions of this Clause 9 shall survive termination of this Agreement.

# TERMINATION AND SUSPENSION

Automatic Termination

  - This Agreement shall terminate automatically upon:-

    - the Provider ceasing to be a BSC Party solely as a result of the Provider’s election or a material breach by the Provider of its obligations under such agreement; or

    - the Provider ceasing to be a party to the CUSC Framework Agreement solely as a result of the Provider’s election or a material breach by the Provider of its obligations under such agreement; or

    - [the revocation or withdrawal of the Generation Licence solely as a result of the Provider’s election or a material breach by the Provider of its obligations under such licence]; or

    - termination of the applicable Bilateral Agreement solely as a result of the Provider’s election or a material breach by the Provider of its obligations under such agreement(s),

and the Provider cannot comply in all material respects with its obligations under this Agreement.

Termination by the Provider

  - The Provider may, by notice in writing to the Company, terminate this Agreement in the event that:

    - the Company shall fail to pay (other than by inadvertent error in funds transmission which is discovered by the Provider, notified to the Company and corrected within five (5) Business Days following such notification) any material sum properly due or owing from it pursuant to this Agreement according to its terms and such non-payment remains unremedied and not disputed in good faith and upon reasonable grounds at the expiry of fifteen (15) Business Days immediately following receipt by the Company of written notice from the Provider of such non-payment; or

    - without prejudice to Clause 10.1, the Company shall commit any material breach (other than a breach under Clause 10.2.1) of this Agreement (or persistent breaches of this Agreement which taken as a whole are material), or shall commit a breach of any of the material obligations on its part to be observed under this Agreement, and the Provider shall have served written notice on the Company requiring it to remedy such default (if it is capable of remedy) within thirty (30) days or such longer period as may be reasonably necessary to remedy the default and the Company shall have failed to remedy such default to the reasonable satisfaction of the Provider within the specified period; or

    - in respect of the Company:-

    - an order of the High Court is made or an effective resolution passed for its  winding-up or dissolution; or

    - a receiver (which expression shall include an administrative receiver within the meaning of Section 29 of the Insolvency Act 1986) of the whole or any material part of its assets or undertaking is appointed; or

    - an administration order under Section 8 of the Insolvency Act 1986 is made or an administrator has been appointed (whether out of court or otherwise) or if a voluntary arrangement is proposed by the Company under Section 1 of that Act; or

    - it enters into any scheme of arrangement (other than for the purpose of reconstruction or amalgamation upon terms and within such period as may previously have been approved in writing by the Authority); or

    - any of the events referred to in (a) to (d) above has occurred and is continuing and the Company is unable to pay its debts within the meaning of Section 123 (1) or (2) of the Insolvency Act 1986 save that such section shall have effect as if for £750 there was inserted £250,000 (and the Company shall not be deemed to be unable to pay its debts if any demand for payment is being contested in good faith by it with recourse to all appropriate measures and procedures);

and in any such case within twenty eight (28) days of appointment of the liquidator, receiver, administrative receiver, administrator, nominee or other similar officer, such person has not provided to the Provider a guarantee of future performance by the Company of this Agreement in such form and amount as the Provider may reasonably require.

Termination by the Company

  - The Company may, by notice in writing to the Provider, terminate this Agreement in the event that:-

    - without prejudice to Clause 10.1, the Provider shall commit any material breach (other than a breach under Clause 10.3.2) of this Agreement (or persistent breaches of this Agreement which taken as a whole are material), or shall commit a breach of any of the material obligations on its part to be observed under this Agreement, and the Company shall have served written notice on the Provider requiring it to remedy such default (if it is capable of remedy) within thirty (30) days or such longer period as may be reasonably necessary to remedy the default and the Provider shall have failed to remedy such default to the reasonable satisfaction of the Company within the specified period; or

    - the Provider shall fail to pay (other than by inadvertent error in funds transmission which is discovered by the Company, notified to the Provider and corrected within five (5) Business Days following such notification) any material sum properly due or owing from it pursuant to this Agreement according to its terms and such non-payment remains unremedied and not disputed in good faith and upon reasonable grounds at the expiry of fifteen (15) Business Days immediately following receipt by the Provider of written notice from the Company of such non-payment; or

    - the Facility remains Unavailable for more than thirty (30) consecutive days; or

    - in respect of the Provider:-

- an order of the High Court is made or an effective resolution passed for its  winding-up or dissolution; or

- a receiver (which expression shall include an administrative receiver within the meaning of Section 29 Insolvency Act 1986) of the whole or any material part of its assets or undertaking is appointed; or

- an administration order under Section 8 of the Insolvency Act 1986 is made or an administrator has been appointed (whether out of court or otherwise) or if a voluntary arrangement is proposed by the Provider under Section 1 of that Act; or

- it enters into any scheme of arrangement (other than for the purpose of reconstruction or amalgamation upon terms and within such period as may previously have been approved in writing by the Authority); or

- any of the events referred to in (a) to (d) above has occurred and is continuing and the Provider is unable to pay its debts within the meaning of Section 123 (1) or (2) of the Insolvency Act 1986 save that such section shall have effect as if for £750 there was inserted £250,000 (and the Provider shall not be deemed to be unable to pay its debts if any demand for payment is being contested in good faith by it with recourse to all appropriate measures and procedures)

and in any such case within twenty eight (28) days of appointment of the liquidator, receiver, administrative receiver, administrator, nominee or other similar officer, such person has not provided to the Company a guarantee of future performance by the Provider of this Agreement in such form and amount as the Company may reasonably require.

Other termination rights

  - The provisions of this Clause 10 are additional to any other rights of termination expressly provided. Termination of this Agreement under this Clause 10 or any other provision of this Agreement shall be without prejudice to the rights and remedies to which a Party may be entitled hereunder and shall not affect any accrued rights obligations or liabilities of either Party nor the coming into or continuance in force of any provision hereof which is expressly or by implication intended to come into or continue in force on or after such termination.

  - For the avoidance of doubt, unless otherwise expressly provided herein, references in this Agreement to termination of this Agreement shall mean termination of all of the provisions of this Agreement and not otherwise.

Suspension

  - If at any time the operation of the Facility is subject to restrictions imposed by the Local TO that, in the Company’s reasonable opinion, have a material and continuing adverse effect on the provision of the Stability Compensation Service from the Facility, the Company may, by notice in writing to the Provider, suspend all rights and obligations of the Parties in relation to the Stability Compensation Service until such time as the Company is reasonably satisfied that such restrictions are no longer being applied by the Local TO whereupon the Company shall by further notice (“Notice of Resumption”) in writing to the Provider end the suspension of the Parties’ respective rights and obligations. The Provider shall resume performance of the Stability Compensation Service and its entitlement to Availability Payments shall resume with effect from the time and date specified in the Notice of Resumption. The Service Term shall not be extended by reason of any period of suspension.

# LIMITATION OF LIABILITY

  - Subject to Clause 11.2 and save and to the extent that any provision of this Agreement provides for an indemnity or the payment of liquidated damages, the Parties agree and acknowledge that neither Party (the “Party Liable”) nor any of its officers, employees or agents shall be liable to the other Party for loss arising from any breach of this Agreement other than for loss directly resulting from such breach and which at the date of this Agreement was reasonably foreseeable as not unlikely to occur in the ordinary course of events from such breach, provided that the liability of any Party in respect of all claims for such loss shall not exceed five million pounds sterling (£5 million) per incident or series of incidents.

  - Nothing in this Agreement shall exclude or limit the liability of the Party Liable for death or personal injury resulting from the negligence of the Party Liable or any of its officers, employees or agents and the Party Liable shall indemnify and keep indemnified the other Party, its officers, employees or agents, from and against all such and any loss or liability which such other Party may suffer or incur by reason of any claim on account of death or personal injury resulting from the negligence of the Party Liable or any of its officers, employees or agents.

  - Subject to Clause 11.2 and save where any provision of this Agreement provides for an indemnity or the payment of liquidated damages neither the Party Liable nor any of its officers, employees or agents shall in any circumstances whatsoever be liable to the other Party for:-

    - any loss of profit, loss of revenue, loss of use, loss of contract or loss of goodwill; or

    - any indirect or consequential loss.

  - Each Party acknowledges and agrees that the other Party holds the benefit of Clauses 11.1 and 11.2 and 11.3 for itself and as trustee and agent for its officers, employees and agents.  In exercising any right or power as trustee hereunder neither Party shall be restricted by any provision of this Agreement as to the manner in which it exercises its discretion (if any).

  - The rights and remedies provided by this Agreement to the Parties are exclusive and not cumulative and exclude and are in place of all substantive (but not procedural) rights or remedies express or implied and provided by common law or statute in respect of the subject matter of this Agreement, including any rights either Party may possess in tort which shall include actions brought in negligence and/or nuisance.  Accordingly, each of the Parties hereby waives to the fullest extent possible such rights and remedies provided by common law or statute and releases the other Party, its officers, employees and agents to the same extent from all duties, liabilities, responsibilities or obligations provided by common law or statute in respect of the matters dealt with in this Agreement and undertakes not to enforce any of the same except as expressly provided herein.  For the avoidance of doubt nothing in this Clause 11.5 shall prevent or restrict any Party enforcing or claiming damages in respect of breach of any payment obligation (including the right for either Party to sue for direct damages to enforce any payment obligation or any future payment obligations under this Agreement) owed to it under or pursuant to this Agreement.

  - For the avoidance of doubt, the Parties acknowledge and agree that nothing in this Agreement shall exclude or restrict or otherwise prejudice or affect any of the rights, powers, privileges, remedies, duties and obligations of the Secretary of State or the Authority under the Act, any Licence or otherwise howsoever.

  - Each of Clauses 11.1, 11.2, 11.3 and 11.4 shall:-

    - be construed as a separate and severable contract term, and if one or more of such Clauses is held to be invalid, unlawful or otherwise unenforceable the other or others of such Clauses shall remain in full force and effect and shall continue to bind the Parties; and

    - survive termination of this Agreement.

  - For the avoidance of doubt, nothing in this Clause 11 shall prevent or restrict any Party enforcing or claiming damages in respect of breach of any payment obligation (including the right for either Party to sue for direct damages to enforce any payment obligation or any future payment obligation under this Agreement) owed to it under or pursuant to this Agreement.

  - Each Party acknowledges and agrees that the provisions of this Clause 11 have been the subject of discussion and negotiation and are fair and reasonable having regard to the circumstances as at the date of this Agreement.

  - For the avoidance of doubt none of the officers, employees, agents, shareholders or Affiliates of either Party shall have any liability to the other Party hereunder.

# METERING

  - The relationship between the Parties with respect to Energy Metering Equipment shall be regulated in accordance with Sections K and L of the Balancing and Settlement Code.

  - The relationship between the Parties with respect to Operational Metering Equipment shall be regulated by section 6 of the Connection and Use of System Code.

  - The Provider hereby consents (and where required pursuant to the Balancing and Settlement Code agrees to give its consent) to the disclosure to and use by the Company for the purposes of this Agreement of all and any generation, demand and other operating data relating to the Facility.

# CONFIDENTIALITY AND ANNOUNCEMENTS

  - Subject to the exceptions provided in Clause 13.3 (and to the extent otherwise expressly permitted by this Agreement), neither Party shall, at any time, whether before or after the expiry or sooner termination of this Agreement, without the prior consent of the other Party in writing (such consent not to be unreasonably withheld or delayed), divulge or suffer or permit its officers, employees, agents or contractors to divulge to any person or permit use by any person (other than disclosure to or use by any of its or their respective officers or employees to the extent that such disclosure and use is required to enable such persons properly to carry out their duties in connection with this Agreement):-

    - any of the contents of this Agreement;

    - any commercially confidential information relating to the negotiations concerning the entering into of this Agreement;

    - any commercially confidential information which may come to a Party’s knowledge in the course of such negotiations; or

    - any commercially confidential information concerning the operations, contracts, commercial or financial arrangements or affairs of the other Party.

  - Each Party undertakes to use information referred to in Clause 13.1 and disclosed to it by the other Party solely for the purposes of this Agreement and shall not use it for any other purpose or for the purposes of any third party.

  - The restrictions imposed by Clause 13.1 shall not apply to the disclosure of any information:

    - which now or hereafter comes into the public domain otherwise than as a result of a breach of a confidentiality obligation or which either Party can show was in its written records prior to the date of disclosure of the same by the other Party, under this Agreement or which it receives from a third party independently entitled to disclose it;

    - which is required by law or pursuant to the rules of the Electricity Arbitration Association in England and Wales or pursuant to the rules or regulations of the Financial Services Authority to be disclosed to any person who is authorised by law or pursuant to the rules of the Electricity Arbitration Association in England and Wales or pursuant to the rules or regulations of the Financial Services Authority to receive the same;

    - which is required to be disclosed by the regulations of any recognised exchange upon which the share capital of the Party making the disclosure (or its parent undertaking) is or is proposed to be from time to time listed or dealt in, or is required to be disclosed by the Panel on Takeovers and Mergers;

    - to a court, arbitrator or administrative tribunal in the course of proceedings before it to which the disclosing Party is a party;

    - pursuant to any Licence of the Party concerned;

    - to any authorised consultants, banks, financiers, insurers or professional advisers to the disclosing Party;

    - by the Provider to a third party who is a party to a power purchase agreement in respect of the electricity generated by the Facility and with whom all (or some of) the risks and benefits arising from the Agreement will be shared provided such party is subject to confidentiality undertakings which are no less onerous than those to which the Provider is subject to under this Agreement;

    - by either Party to any parent, subsidiary or fellow subsidiary undertaking on a “need to know” basis only; or

    - required or expressly permitted to be disclosed under the terms of any agreement or arrangement to which both the Parties have agreed to be bound.

  - In this Clause 13, the words “parent undertaking”, “subsidiary undertaking” and “fellow subsidiary undertaking” shall have the meanings as provided in sections 1161 and 1162 of the Companies Act 2006.

  - Before either Party discloses any information in any of the circumstances described in Clauses 13.3.6 to 13.3.8 (other than to its authorised professional advisers), it shall notify the other Party of its intention to make such disclosure and (in the case where the disclosing Party is the Provider) procure the execution and delivery to that Party of an undertaking executed by the person to whom the disclosure is proposed to be made being in the same terms mutatis mutandis as the undertakings contained in this Clause 13.

  - No public announcement or statement regarding the signature, performance or termination of this Agreement shall be issued or made by either Party unless:

    - to the extent legally possible, before it is issued or made, both the Parties have been furnished with a copy of it and have approved it (such approval not to be unreasonably withheld or delayed); or

    - it is necessary to do so in order to comply with any applicable law or the regulations of any recognised stock exchange upon which the share capital of such Party is from time to time listed or dealt in.

  - With respect to the information referred to in Clause 13.1 both Parties shall ensure that:-

    - such information is disseminated within their respective organisations on a “need to know” basis only;

    - employees, directors, agents, consultants and professional advisers who are in receipt of such information are made fully aware of the Party’s obligations of confidence in relation thereto; and

    - any copies of such information, whether in hard copy or computerised form, will clearly identify the information as confidential.

  - Notwithstanding any other provision of this Agreement, the provisions of this Clause 13 shall continue to bind a person after termination of this Agreement, in whole or in part, for whatever reason.

# DISCLOSURE OF INFORMATION

  - The Provider hereby consents to the disclosure and use by the Company in such manner or form as it thinks fit of data and other information relating to this Agreement and the provision of the Stability Compensation Service (including payments made to the Provider hereunder):

    - for the purposes of any or all of the statements published from time to time pursuant to Standard Condition C16 of the Transmission Licence; or

    - for the purposes of publishing data, including (without limitation) information as to the Availability (and performance) of the Provider as the Company reasonably considers is required to be so published for the purposes of ensuring transparency in its procurement and use of the Stability Compensation Service.

# DISPUTE RESOLUTION

  - Save where expressly stated in this Agreement to the contrary and subject to any contrary provision of the Act or any Licence or the rights, powers, duties and obligations of the Authority or the Secretary of State under the Act, any Licence or otherwise howsoever, any dispute or difference of whatever nature howsoever arising under out of or in connection with this Agreement between the Parties shall be and is hereby referred to arbitration pursuant to the arbitration rules of the Electricity Arbitration Association in force from time to time.  Provided always that prior to any such referral to arbitration the Parties agree to attempt to resolve the dispute in question promptly, equitably and in a good faith manner and (where commensurate with the nature and extent of the dispute) at a senior officer level.

  - Where any provision in this Agreement provides, or the Parties have agreed, for a dispute or difference between the Parties to be referred to an independent expert (“Expert”) the following provisions shall apply, and neither Party shall commence proceedings in any court in respect of or otherwise in connection with such dispute:

    - the Expert shall be jointly appointed by the Parties and shall be a person of good repute with the relevant skills and technical experience to be able to make a fair and reasoned determination having regard to the nature of the dispute or difference;

    - the Parties agree that the Expert shall act as an expert and not as an arbitrator and shall decide those matters referred to him using his skill, experience and knowledge and with regard to all such other matters as he in his sole discretion considers appropriate;

    - if the Parties cannot agree upon the selection of an Expert, the Expert shall be selected on the application of either Party by the President for the Law Society of England and Wales;

    - all references to the Expert shall be made in writing by either Party with notice to the other being given contemporaneously, and the Parties shall promptly supply the Expert with such documents and information as he may request when considering any referral;

    - the Expert shall be requested to use his best endeavours to give his decision upon the question before him as soon as possible in writing following its referral to him, his decision shall, in the absence of fraud or manifest error, be final and binding upon the Parties;

    - the Parties shall equally share the Expert’s fees and expenses unless the Expert determines otherwise; and

    - save to the extent otherwise expressly provided herein or in the determination by the Expert, this Clause shall, to the extent necessary for the Parties to perform their obligations under this Agreement, continue to bind the Parties after termination.

# ENTIRE AGREEMENT

This Agreement contains or expressly refers to the entire agreement between the Parties with respect to the subject matter of this Agreement, and expressly excludes any warranty, condition or other undertaking implied at law or by custom, and supersedes all previous agreements and understandings between the Parties with respect thereto and each of the Parties acknowledges and confirms that it is not aware of any representation, warranty or other undertaking not fully reflected in the terms of this Agreement upon which it has relied upon entering into this Agreement. To the extent that any such representation, warranty or other undertaking exists, each Party irrevocably and unconditionally waives any right it may have to claim damages for breach of warranty and/or to rescind this Agreement, unless such warranty or misrepresentation was made or given fraudulently.

# FORCE MAJEURE

  - In so far as either Party is prevented from performing any of its obligations under this Agreement due to an event or circumstance of Force Majeure, then the rights and obligations of the Parties shall be suspended for as long as and to the extent that the circumstance of Force Majeure prevents such performance. For the avoidance of doubt:

    - the Provider shall not be entitled to any Availability Payment and the Company shall not be entitled to any Availability Rebate to the extent that the Facility is Unavailable by reason of Force Majeure; and

    - the Parties agree that the term Force Majeure when used in this Agreement shall exclude events or circumstances (which shall include the measures put in place by the Government in relation to Coronavirus and the Coronavirus Disease) commencing prior to the date the Provider submitted its tender, but shall include restrictions (but not non-legally binding guidance or advice) introduced by the Government after the date the Provider submitted its tender.

  - The Party affected by the Force Majeure shall give to the other Party immediately upon becoming aware of an event or circumstance of Force Majeure, a written communication describing the Force Majeure (including, without limitation, the nature of the occurrence and its expected duration) and the obligations which it is prevented from performing and shall continue to furnish regular reports with respect thereto to the other Party during the period of Force Majeure.

  - As soon as is reasonably practicable, following an event or circumstance of Force Majeure, the Parties shall meet to discuss how best to continue their respective obligations as set out in this Agreement.

  - For the avoidance of doubt the non-performance of either Party’s obligations pursuant to this Agreement arising prior to the event or circumstance of Force Majeure, shall not be excused as a result of the event or circumstance of Force Majeure.

  - Either Party shall have a right to terminate this Agreement if a Party has been prevented from performing its obligations due to an event of Force Majeure for a continuous period of six (6) calendar months.

# VARIATIONS

No variation to the terms of this Agreement shall be effective unless made in writing and signed by or on behalf of both the Company and the Provider.

# NO PARTNERSHIP

The Parties are independent contractors.  Nothing contained herein shall be deemed to create an association, joint venture, partnership or principal/agent relationship between the Parties or to impose any partnership obligation or liability on either Party.  Neither Party shall have any right, power or authority to enter into any agreement or commitment, act on behalf of, or otherwise bind the other Party in any way.

# WARRANTIES AND INDEMNITY

  - The Provider hereby warrants and represents to the Company that:

    - it has full power and authority to enter into this Agreement and perform its obligations hereunder, including without limitation that the availability and delivery of the Stability Compensation Service from the Facility pursuant to and in accordance with this Agreement does not cause it to be in breach of, or to otherwise be non-compliant with, any Legal Requirement and/or any agreement with any person;

    - it will not do anything in connection with this Agreement that will cause it to be in breach of, or to otherwise be non-compliant with, any Legal Requirement and/or any agreement with any person; and

    - save where the Provider has sought and been granted written consent by the Company (such consent to be at the Company’s sole discretion) and [save in relation to a Permitted Service], it is not a party to an agreement or arrangement with the Company or any Public Distribution System Operator or electricity supplier or other person to provide any service from the Facility which may impair the Provider being Available and/or its ability to provide the Stability Compensation Service and/or perform its obligations under this Agreement. The Provider repeats this warranty and representation on acknowledgement of each Instruction.

  - In the event that any warranty or representation made under Clause 20.1 is breached, the Provider shall indemnify the Company against all and any losses, liabilities, claims, expenses that may be suffered or incurred by the Company as a direct result of that breach and all and any claims and demands which may be brought against the Company by any other person connected to or using the User System of a Public Distribution System Operator or any other User System or the owner of operator of any User System or any other person whatever arising out of or resulting from such breach. Any legal costs and expenses reasonably incurred in the contesting of such claims, including the court costs and the reasonable fees of lawyers and other professional advisers, shall be treated as direct losses.

  - The provisions of this Clause 20 shall continue to bind the Parties after termination of this Agreement.

- CHANGE IN LAW

  - If any Change in Law which could not have been foreseen acting in accordance with Good Industry Practice:

    - causes the provisions of this Agreement to become inconsistent with any Law or Directive; or

    - materially increases or decreases the Provider’s costs of performing this Agreement,

each, a “Relevant Change in Law”, either Party may by notice to the other require the other Party to meet to discuss such circumstances.  Each Party shall in good faith seek to agree the amendments (“Required Amendments”) which  should be made to this Agreement as are necessary to achieve (insofar as possible) the same balance of benefits, liabilities, risk and reward between the Parties in respect of the subject matter of this Agreement as applied immediately prior to the Relevant Change in Law.

If the Parties are unable to agree pursuant to Clause 20.1 whether there has been a Relevant Change in Law and/or upon the Required Amendments, then either Party may refer such issues for determination by an Expert in accordance with Clause 15.2.

Neither Party shall be liable to the other Party for a failure to perform any obligation under this Agreement which becomes prohibited or otherwise impossible to perform by reason of a Change in Law.

# CUSC

The provisions of Paragraphs 6.14 (Transfer and Sub-contracting), 6.20 (Waiver), 6.21     (Notices), 6.22 (Third Party Rights), 6.23 (Jurisdiction), 6.24 (Counterparts), 6.25 (Governing Law) and 6.26 (Severance of Terms) of the CUSC shall apply to this Agreement as if set out in full herein

# ANTI-BRIBERY

  - Each Party shall:

    - comply with all Anti-Bribery Laws;

    - not engage in any activity, practice or conduct which would constitute an offence under sections 1, 2 or 6 of the Bribery Act if such activity, practice or conduct had been carried out in the UK;

    - have and shall maintain in place throughout the term of this Agreement its own policies and procedures, including Adequate Procedures to ensure compliance with the Anti-Bribery Laws, and this Clause 23.1, and will enforce them where appropriate; and

    - procure and ensure that all of its Associated Persons and/or other persons who are performing services and/or providing goods in connection with this Agreement comply with this Clause 23.

  - Without prejudice to any other rights or remedies either Party may terminate this Agreement on written notice to the other Party specifying the date on which this Agreement will terminate in the event of a breach of this Clause 23.

# EMR

  - Notwithstanding any confidentiality obligations and any restriction on the use or disclosure of information set out in this Agreement, the Provider consents to the Company and each of its subsidiaries using all and any information or data supplied to or acquired by it in any year under or in connection with this Agreement for the purpose of carrying out its EMR Functions.

  - The provisions relating to the resolution of disputes set out in this Agreement (if any) are subject to any contrary provision of an EMR Document.

  - Where for the purposes of this provision only:

| “AF Rules” | has the meaning given to “allocation framework” in section 13(2) of the Energy Act 2013; |
| --- | --- |
| “Capacity Market Rules” | means the rules made under section 34 of the Energy Act 2013 as modified from time to time in accordance with that section and The Electricity Capacity Regulations 2014; |
| “EMR Document” | means The Energy Act 2013, The Electricity Capacity Regulations 2014, the Capacity Market Rules, The Contracts for Difference (Allocation) Regulations 2014, The Contracts for Difference (Definition of Eligible Provider) Regulations 2014, The Contracts for Difference (Electricity Supplier Obligations) Regulations 2014, The Electricity Market Reform (General) Regulations 2014, the AF Rules and any other regulations or instruments made under Chapter 2 (contracts for difference), Chapter 3 (capacity market) or Chapter 4 (investment contracts) of Part 2 of the Energy Act 2013 which are in force from time to time; and |
| “EMR Functions” | has the meaning given to “EMR functions” in Chapter 5 of Part 2 of the Energy Act 2013. |

IN WITNESS WHEREOF the hands of the duly authorised representatives of the Parties at the date first above written

SIGNED on behalf of		)

NATIONAL GRID ELECTRICITY 	)

SYSTEM OPERATOR LIMITED	)

SIGNED on behalf of 		)

[Provider name]		)

# SCHEDULE A – Definitions

| “Acceptable Security” | - an on-demand without proof or conditions irrevocable performance bond or guarantee in a form reasonably satisfactory to the Company issued by a Rated Bank payable in Sterling in London; or - an irrevocable standby letter of credit in a form reasonably satisfactory to the Company issued by a Rated Bank payable in Sterling in London; or - a cash deposit in Sterling in an Escrow Account; - a parent company guarantee in terms and from an issuer satisfactory to the Company; or - such other form of security acceptable to the Company which shall be in such form as is included in the Company’s then current policy and procedure; |
| --- | --- |
| “Adequate Procedures” | shall be determined in accordance with section 7(2) of the Bribery Act (and any guidance issued under section 8 of that Act); |
| “Agreement” | this agreement (including the Schedules and the Appendices thereto) as amended, extended, supplemented, novated or modified from time to time; |
| “Annual Reconciliation Payment” | has the meaning given to that term in Clause 5.2.2 (Service Fees); |
| “Anti-Bribery Laws” | shall mean all applicable laws, statutes, regulations, and codes of mandatory application relating to anti-bribery and anti-corruption including but not limited to the Bribery Act; |
| “Associated Person” | shall have the meaning ascribed to it in section 8 of the Bribery Act and shall include but is not limited to any employees, agents and/or subcontractors of the Provider or the Company as applicable in relation to the provision of the Stability Compensation Service; |
| “Approved Outage” | means a planned outage of the Facility the times and dates for which are specified in the Maintenance Plan; |
| “Authority” | means the Gas and Electricity Markets Authority; |
| “Available” | means the Facility is capable of Energising and Synchronising in response to an Instruction and providing either SCL Capability or Inertia Capability (or both) (excluding any period in which the Facility is expressly treated as not available for the Stability Compensation Service) and the terms “Availability”, “Unavailable” and “Unavailability” shall be construed accordingly; |
| “Availability Payment” | has the meaning given to it in Clause 5.1.1 (Service Fees); |
| “Availability Rebate” | has the meaning given to that term in Clause 5.2.1 (Service Fees); |
| “Balancing and Settlement Code” or “BSC” | as defined in the Public Electricity Supply Licence; |
| “Base Rate” | means the Bank of England Official Rate from time to time provided that, if at any time the Bank of England Official Rate is a negative rate, then 0%; |
| “BM Unit” | has the meaning set out in the BSC, except for the purposes of this Agreement the reference to “a Party” in the BSC shall be a reference to the Provider; |
| “Bribery Act” | the Bribery Act 2010; |
| “Business Day” | a week-day (other than a Saturday or a Sunday) on which banks are open for domestic business in the City of London; |
| “Change in Law” | means the occurrence of any of the following events after the date of this Agreement: - the coming into effect of any Law or Directive that is not in effect as at the date of this Agreement; - the repeal, replacement or amendment of any Law or Directive; or - a change in the interpretation of any Competent Authority of any Law or Directive; |
| “Commercial Operations Date” | means, unless otherwise agreed between the Parties, the day after the date on which the Facility passes the Proving Test, being a date falling between 1 April 2022 and 1 April 2024 (both dates inclusive); |
| “Competent Authority” | means the Authority or any local, national or supra-national agency, authority, department, inspectorate, minister, official, court, tribunal or public or statutory person (whether autonomous or not) of the United Kingdom (or the government thereof) or the member states of the European Union which have jurisdiction over the Company or the subject matter of this Agreement; |
| “Conditions Precedent” | has the meaning given to it in Clause 2.2 (Commencement and Term); |
| “Connection Site” | the location more particularly described in the Bilateral Agreement; |
| “Connection and Use of System Code” or “CUSC” | the connection and use of system code drawn up pursuant to the Transmission Licence as from time to time revised in accordance with the Transmission Licence; references in this Agreement to any specific provision or part of the Connection and Use of System Code shall be construed as references to such provision or part as from time to time amended; |
| “Contract Rate” | means the rate (expressed in £/Settlement Period) to be used for the calculation of Availability Payments specified by the Provider in its Tender Submission and set out in Schedule B, Part B; |
| “Contract Year” | means each period of twelve (12) calendar months commencing on 1 April in each year of the Service Term save that the first such year (“Contract Year 1”) shall commence on the Commercial Operations Date and end on the next following March 31. The expression “Contract Year 4” and similar expressions shall be construed accordingly; |
| “Contracted Inertia Capability” | the Inertia Capability of the Facility specified in the Provider’s Tender Submission as the same may be amended from time to time in accordance with Clause 6.4; |
| “Contracted Reactive Capability” | the Reactive Capability of the Facility specified in the Provider’s Tender Submission as the same may be amended from time to time in accordance with Clause 6.4; |
| “Contracted SCL Capability” | the SCL Capability of the Facility specified in the Provider’s Tender Submission as the same may be amended from time to time in accordance with Clause 6.4; |
| “Coronavirus” | has the meaning given to it in the Coronavirus Act as at the date hereof; |
| “Coronavirus Disease” | has the meaning given to it in the Coronavirus Act as at the date hereof; |
| “Distribution Licence” | means a licence issued under section 6(1)(c) of the Electricity Act 1989; |
| “EDL” | means the electronic despatch logging mechanism by which the Company communicates with the Provider and the Provider communicates with Company in respect of the Facility for the purposes of sending and acknowledging Instructions and Instructions to End; |
| “Escrow Account” | means a separately designated interest-bearing bank account in the name of the Company established by a mandate in such terms as the Company may require and signed by both the Company and the Provider at a branch of Barclays Bank PLC or another bank in the City of London as notified by the Company to the Provider; |
| “Expert” | has the meaning given to that term in Clause 15.2; |
| “Facility” | means the facility described in Schedule B, Part A; |
| “Fast Fault Current” | has the meaning given to that term in the Grid Code; |
| “Force Majeure” | in relation to either Party any event, circumstance or condition which is beyond the reasonable control of such Party (not being, without limitation an event or circumstance caused by the negligence or lack of care and attention of that Party or its officers or employees, agents, contractors and sub-contractors) which, despite all reasonable endeavours of the Party claiming Force Majeure to prevent it or mitigate its effects, causes a material delay or disruption in the performance of any obligation imposed hereunder, but subject thereto including act of God, epidemic or pandemic, strike, lockout or other industrial disturbance, act of the public enemy, war declared or undeclared, threat of war, terrorist act, blockade, revolution, riot, insurrection, civil commotion, public demonstration, sabotage, act of vandalism, lightening, fire, storm, flood, earthquake, accumulation of snow or ice, lack of water arising from weather or environmental problems, explosion, governmental restraint, Act of Parliament, other legislation, bye law and Directive (not being any order, regulation or direction under Section 32, 33, 34 and 35 of the Act) provided always that (i) lack of funds and (ii) operational constraints imposed by the Local DNO shall not be interpreted as a cause beyond the reasonable control of that Party; |
| “Grid Code” | has the meaning given to it in the Company’s Licence; |
| “Grid Entry Point” | has the meaning given to it in the Grid Code; |
| “Inertia Capability” | in relation to the Facility, its ability to provide Inertia Power, being the Contracted Inertia Capability or such lesser capability specified in a Redeclaration; |
| “Inertia Power” | has the meaning given to it in Part A of Schedule E; |
| “Indicative Post Tender Milestones” | means those indicative milestones, and requisite evidence, set out in Schedule C; |
| “Industry Document” | the Licences, the BSC, the CUSC, the Grid Code and all other agreements, documents or codes with which the Provider is obliged to comply under the Act or its Licence; |
| “Instructed Settlement Period” | means a Settlement Period that is subject to an Instruction; |
| “Instruction” | has the meaning given to it in Clause 4.5; |
| “Instruction to End” | has the meaning given to it in Clause 4.5; |
| “ITT” | has the meaning given to it in recital A; |
| “LAD Cap” | means a sum equal to the LAD Rate multiplied by 180 days; |
| “LAD Rate” | means a daily rate equal to the Contract Rate multiplied by the number of Settlement Periods in the day and then multiplied by two; |
| “Law or Directive” | - any law (including the common law); - any statute, statutory instrument, regulation, instruction, direction, rule or requirement of any Competent Authority; - any condition or other requirement of any Licence or other required authorisation, licence, consent, permit or approval (or of any exemption from the requirement to have the same); and - any provision of any Industry Document; |
| “Legal Requirement” | has the meaning given to it in the BSC; |
| “Licence” | means a licence issued under section 6(1) of the electricity act 1989; |
| “Local TO” | means the owner of that part of the NETS to which the Facility is connected or (in the case of an embedded Facility) the owner of that part of the NETS in which the associated Grid Supply Point is located; |
| “Longstop Date” | the date falling thirty (30) Business Days after the date of this Agreement; |
| “Maintenance Plan” | has the meaning given to it in Clause 4.10; |
| “Monitoring Equipment” | the meaning given to it in Clause 7.1; |
| “Monitoring Equipment Proving Test” | one or more tests (such testing as the Company may reasonably require) to verify that the Monitoring Equipment is capable of carrying out the monitoring and recording functions required of it as described in Clause 7.1; |
| “National Electricity Transmission System” or “NETS” | has the meaning given to that term in the Company’s Licence; |
| “Party Liable” | has the meaning given to it in Clause 11.1(Limitation of Liability); |
| “Permitted Service” | [participation in the Balancing Mechanism, [Response], [Reserve], Constraint Management, Enhanced Reactive, Capacity Market and Black Start]; |
| “Point of Stability” | the point on the NETS (at 132kV or higher) where the Facility is directly or radially connected, being the point where, unless otherwise stated, the Stability Compensation Service must be delivered; |
| “Proving Test” | a proving test of the Facility undertaken after the Commercial Operations Date in accordance with Clause 3.4 or a proving test of a Substitute Facility undertaken in accordance with Clause 4.12, in either case, in compliance with the principles set out in Schedule D Part A to verify that the Facility is capable of providing the Stability Compensation Service in accordance with the Technical Performance Requirements, including the Contracted Inertia Capability, Contracted Reactive Capability and Contracted SCL Capability; |
| “Post Tender Milestones” | the milestones set out in Schedule C; |
| “PTM Date” | means the date falling six (6) months before the Scheduled Operations Date; |
| “Public Electricity Supply Licence” | a licence granted under Section 6(1)(c) of the Electricity Act 1989 prior to the coming into force of section 30 of the Utilities Act 2000; |
| “Rated Bank” | means a City of London branch of a bank with a rating of at least A- (Standard and Poor’s long-term rating) or A3 (Moody’s long-term rating); |
| “Reactive Capability” | the ability of the Facility to absorb or produce Reactive Power being the Contracted Reactive Capability or such lesser capability specified in a Redeclaration; |
| “Reactive Power Fee” | means the amount (expressed in £/Mvarh) specified for the relevant month in the column headed “X=1” in the document titled, “Obligatory Reactive Power Service Default Payment Rates” published each month on the National Grid web site; |
| “Reactive Power Mode” | means ‘target voltage mode’ or ‘constant Mvar mode’ as described in the Technical Performance Requirements; |
| “Reactive Power Payment” | has the meaning attributed to it in Clause 5.1.2; |
| “Redeclaration” | has the meaning attributed to it in Clause 4.3; |
| “Reproving Test” | in relation to the Facility, a test undertaken in accordance with Clause 6 in compliance with the principles set out in Schedule D Part B to verify that the Facility is capable of providing the Stability Compensation Service in accordance with the Technical Performance Requirements, including the Contracted Inertia Capability, Contracted Reactive Capability and Contracted SCL Capability; |
| “Restoration Notice” | has the meaning attributed to it in Clause 4.4; |
| “Scheduled Operations Date” | [ ], being the date specified by the Provider in its Tender Submission by which it expects to have completed the Works and the Facility to have passed the Proving Test; |
| “SCL Capability” | in relation to the Facility, its short circuit level contribution, being the Contracted SCL Capability or such lesser capability specified in a Redeclaration; |
| “Service Term” | means the period commencing at 00:00:00 hours on the Commercial Operations Date and ending at 23:59:59 on 31st March 2030; |
| “Stability Compensation Service” | means the service of making the Facility Available and responding to the Company’s Instructions in accordance with this Agreement; |
| “Synchronised” | the condition where the Facility is connected to the busbars of the Total System so that the frequencies and phase relationships of the Facility and the Total System are identical, like terms shall be construed accordingly e.g. “Synchronism”; |
| “Synchronous Compensation” | means the operation of rotating synchronous apparatus for the specific purpose of providing this Stability Compensation Service; |
| “Technical Performance Requirements” | those technical, performance and other requirements set out or referred to in Schedule E, including the Contracted Inertia Capability, the Contracted Reactive Capability and the Contracted SCL Capability; |
| “Tender” | means the procurement process for the provision of the Stability Compensation Service undertaken pursuant to the ITT; |
| “Tender Submission” | a submission made in response to the ITT; |
| “User System Entry Point” | has the meaning given to it in the Grid Code; |
| “Works” | means [the design, construction, commissioning and testing of the Facility] [the modification, commissioning and testing of the Facility]. |

SCHEDULE B – Provider Details

Part A – Facility

[			]

Part B – Contract Rate

(in £/Settlement Period) [£               ]

Part C – Reactive Meter Details

| BM Unit No | Metering Subsystem ID | Outstation ID | Channel Number | Meter Register ID | Measurement Quantity ID (RI or RE) | Loss Adjustment Factor |
| --- | --- | --- | --- | --- | --- | --- |

SCHEDULE C –  Post Tender Milestones

|  | Milestone | Evidence Required |
| --- | --- | --- |
| 1. | Agreed financing in place sufficient to fund completion of the Works. | Evidence should include internal governance sign-off and, where third party funding is required, a Letter of Intent from the funding party (subject to that party’s due diligence process), confirming that there are no conditions of that financing that may negatively impact on the provision of the Stability Compensation Service. The documentation must be specific to the Provider and the Facility. |
| 2. | The grant by the relevant local planning authority (on terms and conditions reasonably acceptable to the Company) of permission for the proposed erection, construction operation and/or site clearance required (including all and any ancillary erections, structures and equipment, plant and apparatus) and use of the Facility for the provision of the Stability Compensation Service in accordance with the terms of the Agreement. | Copy of all relevant consents or (at the Company’s sole discretion) a declaration by the Provider that it has obtained the necessary planning permission) that may be required to enable the Provider to deliver its project for the purposes of providing the Stability Compensation Service in accordance with the terms of the Agreement |
| 3. | The Provider has either a leasehold or freehold interest in land upon which the Facility is (or is to be) situated | Evidence to the Company’s reasonable satisfaction which may (at the Company’s sole discretion) be by way of a declaration by the Provider that it has met these obligations. |
| 4. | The Provider has commenced development and construction operations at the site. | Evidence (to the Company’s reasonable satisfaction) or (at the Company’s sole discretion) a declaration by the Provider that it has met these obligations. |
| 5. | The Provider has in place (as can reasonably be expected to be in place by the PTM Date), without limitation, those consents, permissions, approvals, licences, exemptions and other permits (in legally effectual form) as may be necessary to commence, carry out, maintain and ensure the provision of the Stability Compensation Service in accordance with the terms of the Agreement. | Evidence to the Company’s reasonable satisfaction which may (at the Company’s sole discretion) be by way of a certificate from an independent consultant (based in the United Kingdom and who has sufficient experience and expertise in assessing the consenting requirements for the construction and operation of facilities similar to the Provider’s system) that the Provider has, or can reasonably be expected to have, the necessary consents, permissions, approvals, licences, exemptions and other permits in place to enable the Provider to perform the Stability Compensation Service in accordance with the terms of the Agreement by no later than the Commercial Operations Date. |
| 6. | Entry by the Provider into a binding agreement (on terms acceptable to the Company) for the connection of the Facility to the public electricity supplier distribution system or to the National Electricity Transmission System to receive a supply or electricity from and export electricity into the Distribution System or the National Electricity Transmission System. | Unless evidence was fully provided at the Tender stage, evidence to the Company’s reasonable satisfaction or (at the Company’s sole discretion) a declaration by the Provider that it has entered into a suitable grid connection agreement that will enable the Provider to deliver the Stability Compensation Service in accordance with the terms of the Agreement. |
| 7. | The Provider has put in place the necessary orders for all necessary plant, equipment, apparatus, machinery and other materials with long procurement and/or delivery periods. | Evidence to the Company’s reasonable satisfaction. |
| 8. | Entry by the Provider into a binding engineering procurement and construction contract and/or a supply agreement with an original equipment manufacturer (as applicable) for the provision of relevant equipment and services in developing the Facility (including all ancillary and associated works in relation thereto) on terms and conditions reasonably acceptable to the Company. | Unless a contract was entered into at the Tender stage, evidence to the Company’s reasonable satisfaction which may be by way of a certificate from an independent consultant who has sufficient experience and expertise in assessing the necessary requirements for the construction and operation of facilities similar to the Provider’s system in the United Kingdom that, given the terms of such agreements, there is a reasonable prospect of the Facility being Commissioned in time to deliver the Stability Compensation Service by no later than the Scheduled Operations Date. |

SCHEDULE D – Proving Tests and Reproving Tests

Part A –Proving Test

The Provider agrees that it or it’s agent shall undertake a Proving Test ahead of the Commercial Operations Date to ensure operability of the Stability Compensation Service and to test whether the Facility is capable of providing the Reactive Capability, the Inertia Capability and the SCL Capability, specified in the Provider’s Tender Submission.

The level and scope of tests required will depend on the solution and build programme, but will include (without limitation) the following tests:

•	Open circuit test

•	On load Voltage steps

•	Transforming tapping

•	Under-excitation limiter

•	Over-excitation limiter

- Physical testing to demonstrate that the performance of the Facility matches the performance submitted in the feasibility study. including (without limitation):

  - demonstration of the value and behaviour of inertia meeting those set out in schedule E

  - demonstration of the value and behaviour of Short Circuit Level meeting those set out in schedule E

The Company shall provide a full set of test requirements no less than 1 year before the Scheduled Operations Date.

Part B – Reproving Test

The Provider agrees that it or it’s agent shall undertake Reproving Tests (including any re-tests), if required, during the Service Term, where requested by the Company in accordance with the provisions of Clause 6 (Reproving Test) of this Agreement to test whether the Facility is capable of providing the Stability Compensation Service, including the Contracted Reactive Capability, Contracted SCL Capability and Contracted Inertia Capability.

The level and scope of tests required will depend on the technology of the Facility and will include those tests specified in Part A.  The Company may require the Provider to undertake any additional tests it considers necessary to identify the cause of any suspected non-compliance with the requirements of this Agreement.

SCHEDULE E - Technical Performance Requirements

Part A - Stability Requirements

1.1        The Provider shall:

    - ensure that during a fault, the short circuit level contribution from the Facility will be XX MVA at the Point of Stability. Short circuit level defined as in Equation 1

Short circuit level  MVA=3 *Rated voltage kV*Fault currentkA 	Equation 1

Where:

the fault current is defined as the instantaneous positive sequence RMS fault current seen at 100ms after a 3-phase symmetrical fault at the Point of Stability;

and Rated voltage is defined as the voltage of first busbar at the Point of Stability.

    - provide an inertia response with an inertia of XX MW.s or MJ.

    - Inertia shall be defined as in Equations 2 and 3:

    - Inertia= H × Srating 	Equation 2

#### H= ∆P f02 SratingRoCoF 	Equation 3

#### Where:

    - H is the inertia constant (s) defined in Equation 3;

#### Srating is the solution rating (MVA);

#### ∆P is the solution active power output for a frequency event (MW);

    - f0 is the pre-fault system frequency (Hz); and

    - RoCoF is the rate of change of frequency of the system (Hz/s).

    - For a Grid Forming Converter, H must be set such that inertia power is provided without hitting converter’s overload or rated capability for a RoCoF of less than 1Hz/s.

Fault ride-through and transient stabilisation requirement

  - The Facility must be able to:

    - operate across a range of transmission short circuit levels between [x] and [y]

    - fully comply with the applicable requirements of the Grid Code including but not limited to the Planning Code (PC), Connection Condition (CC’s) or European Connection Condition (ECC’s), Compliance Processes (CP’s) or European Compliance Processes (ECP’s), Operating Codes, Balancing Codes and Data Registration Code (DRC);

For the avoidance of doubt where this Schedule E refers to a specific section of Grid Code the Facility is expected to comply with the referred section in addition to its normal Grid Code obligations;

    - during a fault or voltage depression which falls below 0.9 pu at the Point of Stability, keep the phase, magnitude and frequency of the Internal Voltage Source fixed at its pre-fault value during and immediately after the fault. In the event that the resulting fault current would have exceeded its maximum overload capability or rated capability, a limited fault current can be supplied up to its maximum overload capability providing this value is reflected in Part A 1.1.1;

    - following an instantaneous vector shift/phase angle change at the Point of Stability provide an instantaneous response (starting within 5ms) in active and/ or reactive current proportional to the angle change up to the values in Part A 1.1.1 and Part A 1.1.2;

In the event that the resulting current would exceed the maximum overload capability or rated capability, a limited current can be supplied up to its maximum overload capability providing this value is reflected in Part A 1.1.1 and Part A 1.1.2;

    - inherently respond to a change in the system frequency by importing or exporting Inertia power into the system proportional to the rate of change of frequency of the system.

    - In the event that the resulting Inertia power would have exceeded its maximum overload capability or rated capability, a limited Inertia Power can be supplied up to its maximum overload capability providing this value is reflected in Part A 1.1.1.

    - For the purposes of this Schedule E, “Inertia Power” means the (start of an) instantaneous short-term transfer of active power from the Facility to or from the system following a system frequency change as a result of an instantaneous change in generation or demand on the system. This should occur without the need for any change in the Internal Voltage Source of the Facility.

    - start importing or exporting inertia power to respond to a change in the system frequency within 5ms;

    - provide reactive current and inertia power response to the system consistent with the performance of a voltage source behind an effective impedance. For frequencies below 5Hz additional power transfer can occur due to control based real power requirements.  The control system can respond to changes in external signals but with a bandwidth below 5 Hz to avoid AC System resonance problems;

    - provide continuous voltage support through the injection of reactive current during a fault condition as defined in ECC.6.3.15. During a fault or voltage disturbance, priority should be given to the injection of reactive current whilst ensuring that active power recovery satisfies the requirements of ECC.6.3.15 (as applicable), though equally the performance expected from a synchronous machine would also be considered appropriate for this requirement;

    - start responding within 5ms of fault clearance during an over-voltage condition at the Point of Stability, as described in paragraph 1.2.18, with reactive current absorption;

    - in the event where the voltage at the Grid Entry Point or User System Entry Point falls below the voltage level specified in ECC.6.1.4, be capable of reactive current injection at the Grid Entry Point or User System Entry Point as soon as possible and starting within at least within 5ms of the voltage disturbance using the whole machine rating and proportional to the size of the voltage dip.

In the event that the resulting reactive current injection current would have exceeded its maximum overload capability or rated capability, a limited current can be supplied up to its maximum overload capability;

    - ensure continuous and controllable operation shall be possible at all system voltages specified in ECC6.1.4.1 of the Grid Code;

    - ensure continuous and controllable operation shall be possible at all system frequencies specified in ECC6.1.2.1.2 of the Grid Code;

    - ensure continuous and controllable operation shall be possible at all system rate of change of frequencies up to 1Hz/s;

    - ride through voltage depressions at the Grid Entry Point or User System Entry Point or Transmission Interface Point of down to 0pu for up to 140ms;

    - ride through the family of voltage depressions curves defined in ECC.6.3.15;

    - withstand, and ride through, any rate of change of frequency occurring ≤ 1Hz/s (for GFC ≤ 2 Hz/s) on average or in absolute change across a sampled window of 500ms;

    - withstand, and ride through, any rate of change of frequency instantaneously measured exceeding 1Hz/s within the sampled window period;

    - withstand an initial RMS over-voltage at the Grid Entry Point or User System Entry Point or Transmission Interface Point, of up to 1.4p.u. for 100ms after fault clearance followed by a reduction in over-voltage towards no more than 1.05pu as per the requirements of TGN(E)288;

    - confirm the ability of the Facility to operate repeatedly through balanced and unbalanced faults and System disturbances each time the voltage at the Grid Entry Point or User System Entry Point or Transmission Interface Point falls outside the limits specified in ECC.6.1.4.  Demonstration of this capability would be satisfied by EU Generators and HVDC System Owners and Non-CUSC Parties supplying the protection settings of their Grid Forming Plant, informing the Company of the maximum number of repeated operations that can be performed under such conditions and any limiting factors to repeated operation such as protection or thermal rating.

Power Oscillation Damping

    - The Facility shall be capable of Active Power and/or Reactive Power oscillation damping achieved over a duration of 20s. The power oscillation damping shall:

      - inherently or through a control system contribute to damping sub-synchronous frequency oscillations in the system’s Active Power or Reactive Power range over a frequency bandwidth of 0.3-2 Hz;

      - inject active or reactive current adequately in antiphase to achieve a reduction in oscillations (as described in 1.2.19.1) at the Point of Stability;

      - change the amount of active or reactive current injection proportional to the amplitude of the oscillations;

      - ensure the influence of any subsidiary control functions be no more than 10% of the machine rating.

    - If the Facility is to operate with a Power System Stabilizers (PSS) capability as specified through its Bilateral Connection Agreement and the Grid Code, then this PSS mode shall be used instead of the Power Oscillation damping specified in 1.2.20. If at any time during the term of the Stability Compensation Service, the Facility is not operating with a PSS then, the Facility will need to meet requirements set out in 1.1.20.

Part B - Continuous Voltage Requirements

General requirement

- The Facility shall, following an Instruction, provide Reactive Power within the range set out in the following table:

|  | MW | Minimum Mvar (+ve for lag, -ve for lead) | Maximum Mvar (+ve for lag, -ve for lead) |
| --- | --- | --- | --- |
| AT RATED MW |  |  |  |
| AT FULL OUTPUT(MW) |  |  |  |
| MINIMUM OUTPUT (MW) |  |  |  |

The reactive range values must be achievable at the Grid Entry Point or User System Entry Point or Transmission Interface Point as applicable. Operating at any point within this reactive range should not limit the ability to provide the stability requirements set out in Part A.

- The Facility’s excitation and voltage control shall be,

  - in accordance with paragraph 3 if the Facility is connecting as a generator or interconnector under the Grid Code; or

  - in accordance with paragraph 4 if the Facility is connecting as demand and/or is a 0MW connection under the Grid Code.

- Generation or interconnector connection

  - The Facility’s excitation and voltage control shall be in accordance with the relevant section of the Grid Code as specified in the Facility’s Bilateral Connection Agreement.

- Demand and/or 0 MW connection

  - Control Modes:  General

    - The Facility must be able to operate in either ‘Target Voltage’ or ‘Constant MVAr’ mode.

    - In ‘Target Voltage’ mode, the unit Reactive Power injected or absorbed shall be directly proportional to the deviation of the system (HV) voltage from the preselected ‘Target Voltage.’. In this mode, the Facility must also provide the stability requirements set out in Part A.

    - In ‘Constant MVAr’ mode, the MVAr output of the Facility equals the ‘Target MVAr’ setting.  The Facility must still respond rapidly to sudden changes in system voltage, its output returning steadily to the target value over a definable subsequent period. In this mode, the Facility must also provide the stability requirements set out in Part A.

    - The Facility must be able to switch between ‘Target Voltage ’mode and ‘Constant MVAr’ mode on instruction from the company within an agreed time scale of no longer than 30 minutes.

  - Target Voltage Mode

Slope Characteristic:

    - A change in voltage (at the point of connection to the NETS) shall cause a change in reactive current according to a linear slope characteristic, defined as the change in system voltage to cause the Reactive Power output of the Facility to move from zero to full capacitive (over-excited).  Control according to the slope characteristic shall be achievable over the full range of reactive outputs and system voltages. Different slopes may be requested in the capacitive and inductive direction.

    - The slope shall be adjustable over the reactive range 2% to 7%.  The setting tolerance shall be better than ±0.5% of system voltage. The Slope shall be adjustable remotely and following an Instruction by the Company. The Facility must provide such data as the Company reasonably requires for system modelling studies.

Float Condition:

    - The float condition, at which reactive power is zero, shall be changed by adjustment of target voltage (at the point of connection to the NETS) over the range 0.95 to 1.05 pu.

    - The range of slope adjustments is to be available over the full range of target voltage adjustments.

Response Time:

    - For a sustained change in the NETS voltage, the change in the sustained Reactive Power will be determined by the slope.

    - For a step change in the System voltage, the change in sustained reactive current will be achieved as follows;

      - 95% of the total change to be achieved within 1 second; and

      - all oscillations greater than 5% of full load current to have ceased within 5 seconds.

  - Constant MVAr Mode

    - The control system shall adjust the target voltage so that the MVAr output of the Facility equals the ‘Constant MVAr’ setting.  The Facility will thus still respond rapidly to sudden changes in system voltage, its output returning steadily to within (+/ -  2% of unit MVAr rating) of the target value over the subsequent 5 minute period.

    - Should the voltage on the NETS vary outside adjustable preset limits, the Facility must automatically be switched to Target Voltage Mode to control the abnormal system voltage.  This change of operating mode shall be alarmed to alert the Company operator to a possible abnormal system condition. The preset limits shall be adjustable between 0.93 and 1.07 pu, with a resolution of 0.005 pu.

    - The requirements of the ‘Constant MVAr’ mode must be achievable for all system short circuit levels specified in Part A 1.2.1. Constant MVAr control must be achievable at any MVAr output and at any system voltage within the limits defined in paragraph 1 of Part B and at any system voltage and frequencies as defined in 1.2.11 to 1.2.12 of Part A.

Part C - Control and Indication Facilities

- Where applicable, the transformer tap position shall be provided for by the Provider at the Company’s operational metering system control and data acquisition (SCADA) outstation interface, as specified in the Provider’s Bilateral Connection Agreement.

- Where applicable, the following facilities for voltage/reactive power control to the Company’s Instructions shall be provided by the Provider at a manned control point:

  - Start-up of machine and transition to Stability Compensation mode;

  - Shut-down of Stability Compensation mode;

  - Target voltage setting (resolution 1kV) (for Target Voltage control mode);

  - Target MVAr setting (resolution 1MVAr) (for Constant MVAr control mode);

  - Control mode selection (Target Voltage or Constant MVAr);

  - Slope setting (range 2% to 7%, resolution 0.5%.)

- The following additional facilities for voltage/reactive power control shall be provided by the Provider.  The Provider shall use all reasonable endeavours to adjust any of the following specified quantities on the Company’s instruction within 24 hours’ notice (adjustments including 3.1 and 3.2 shall not be made unless instructed by the Company):

  - change the time for switching between Target Voltage mode and Constant MVAr mode (the value shall be within the range 5 minutes to 30 minutes, with a resolution of 5 minutes);

  - change the voltage limits for transition to Target Voltage mode (the setting shall be within range 0.93 to 1.07 pu. with a resolution of 0.005 pu).

Part D - Model Provision

The Provider will prior to commissioning the Facility, submit a steady state and transient model in accordance with Grid Code PC.A.5.3.2 c option 2 or PC.A.5.4.2 as appropriate. The Company may accept a DIGSILENT PowerFactory Model V15 provided that this is an open model (i.e. transfer functions visible and not containing DLL code). The Provider must submit an EMT PSCAD model if the Company requests before or after commissioning of the Facility.

The Provider shall submit a performance chart in accordance with Grid Code OC2.4.2.1

SCHEDULE F - Payments

Part A – Availability Payment

This Part A sets out the calculation of the payments in respect of Availability and comprises the following elements:

A.1	the monthly Availability Payment;

A.2	the monthly Availability Rebate;

A.3	the Annual Reconciliation Payment; and

A.4	the indexation of the Contract Rate.

A.1 – Monthly Availability Payment

A.1	The Availability Payment APm for each calendar month m in the Contract Year is calculated as:

APm = ∑jm [{(ACij * Max(ASCij, FMAj) * TA)} + {(ACsj * Max(ASCsj, FMAj) * TA)}/2] * CRj

Where:

∑jm		is the summation for all Settlement Periods j in calendar month m;

ACij		is the Contracted Inertia Capability of the Facility in Settlement Period j or any lower value notified in a Redeclaration, divided by the Inertia Capability specified in the Provider’s Tender Submission (expressed as a decimal fraction);

ASCij		is 1 where the Facility is Available and capable of providing Inertia Capability in Settlement Period j, otherwise 0;

FMAj		is 1 where the Facility is on an Approved Outage in Settlement Period j, otherwise 0;

TAi		is a factor: (i) if the value of ACij is less than 0.9, equal to 0.7; or (ii) otherwise, equal to 1;

ACsj		is the Contracted SCL Capability of the Facility in Settlement Period j or any lower value notified in a Redeclaration, divided by the SCL Capability specified in the Provider’s Tender Submission (expressed as a decimal fraction);

ASCsj		is 1 where the Facility is Available and capable of providing SCL Capability in Settlement Period j, otherwise 0;

TAs	is a factor: (i) if the value of ACsj is less than 0.9, equal to 0.7; or (ii) otherwise, equal to 1;

CRj		is the Contract Rate applicable in Settlement Period j (expressed in £/Settlement Period).

A.2 – Monthly Availability Rebate

A.2.1	The Availability Rebate (ARm) for each calendar month in the Contract Year is calculated as follows

ARm=MinACm+ULm, APm

Where:

ACm		is the sum calculated in accordance with paragraph A.2.2 below

ULm		is the unrecovered Availability Rebate as at month m, calculated in accordance with paragraph A.2.3 below.

A.2.2	The charge for Unavailability (ACm) in calendar month m of the Contract Year is calculated as:

ACm = [(AAim - TAim) * CR * 1,000] + [(AAsm - TAsm) * CR * 1,000]

Where:

AAim	is a fraction (expressed as a percentage) the numerator of which is the aggregate number of Settlement Periods in month m in which the Facility was either: (i) Available to provide Contracted Inertia Capability; or (ii) on an Approved Outage, and the denominator of which is the aggregate number of Settlement Periods in month m ;

TAim	is the Target Availability (expressed as a percentage) for Contracted Inertia Capability for month m, being [  ]%;

AAsm	is a fraction (expressed as a percentage) the numerator of which is the aggregate number of Settlement Periods in month m in which the Facility was either: (i) Available to provide Contracted SCL Capability; or (ii) on an Approved Outage, and the denominator of which is the aggregate number of Settlement Periods in month m;

TAsm	is the Target Availability (expressed as a percentage) for Contracted SCL Capability for month m, being [  ]%; and

CR		is the Contract Rate, indexed in accordance with paragraph A.4 below.

A.2.3	The unrecovered Availability Rebate (ULm) for each calendar month m in the Contract Year is:

Where m = 1, the monthly unrecovered Availability Rebate (ULm) will be 0;

Where m > 1, the monthly unrecovered Availability Rebate (ULm) will be calculated as:

ULm=1m-1ACm-1m-1ARm

Where:

		is the summation of the monthly values for ACm and ARm in all calendar months up to and including the previous month in the Contract Year.

A.3 – Annual Reconciliation Payment

The Annual Reconciliation Payment (ARLfinal) is calculated for a Contract Year as follows:

ARLfinal = Min {Max (ULm12 – (APm12 – AR m12), 0), ∑ APm - ARm}

Where:

		is the sum of all monthly values for APm and ARm in the Contract Year;

ULm12		is the unrecovered Availability Rebate in the final month of the Contract Year;

APm12		is the Availability Payment in respect of the final month of the Contract Year;

ARm12		is the Availability Rebate in respect of the final month of the Contract Year.

A.4 – Indexation of Contract Rate

The Availability Payment will be calculated by reference to the Contract Rate, subject to indexation as follows:

A.4.1 	The Contract Rate will be adjusted annually (commencing with Contract Year 4) to take account of general price inflation.  The index used will be the Consumer Prices Index (“CPI”) with 2015 = 100 base.  The source of the CPI index is the monthly Office for National Statistics Statistical bulletin.

A.4.2	The Contract Rate will therefore be increased (or reduced as appropriate) for Contract Year 4 by the following factor:-

CPI

CPI

1

2

Where:

CPI2 is the CPI for the month of March immediately preceding Contract Year 4; and

CPI1 is the CPI for the month of March immediately preceding Contract Year 3.

CPI

CPI

1

3

A.4.3	The relevant price will then be increased (or reduced as appropriate) for Contract Year 5 by the following factor:-

Where:

CPI3 is the CPI for the month of March immediately preceding Contract Year 5; and

CPI1 is the CPI for the month of March immediately preceding Contract Year 3.

A.4.4	In subsequent Contract Years, indexation will continue in accordance with the above, with always the numerator of the factor representing the CPI for the month of March immediately preceding the Contract Year under consideration and the denominator of the factor being CPI for the month of March immediately preceding Contract Year 3.

.

A.4.5	In the event that CPI ceases to be published or is not published in respect of any relevant month or it is not practicable to use CPI because of a change in the method of compilation or some other reason, indexation for the purpose of this paragraph A.4 shall be calculated by the Company using an index agreed by the Parties with a view to determining the relevant price after indexation that would be closest to the relevant price after indexation if CPI had continued to be available.

Part B- Reactive Power Payment

The Reactive Power Payment in respect of calendar month m (“RPm”) is calculated as follows:

(Ulead

RF

=

RPm

+

month

j=1

*



Ulag)

Where:

is the summation over all Instructed Settlement Periods j in calendar month;

RF	is the Reactive Power Fee (expressed in £/MVArh);

Ulag	is the metered quantity of Reactive Power (expressed in MVArh) produced by the Facility; and

Ulead 	is the metered quantity of Reactive Power (expressed in MVArh) absorbed by Facility.

SCHEDULE G – Notices

The Company’s address for service of Notices:

National Grid Electricity System Operator Limited

Faraday House

Warwick Technology Park

Gallows Hill

Warwick CV34 6DA

Facsimile number: 01926 656613

For the attention of: The Company Secretary

Copy to: Head of Commercial

The Provider’s address for service of Notices:

[Company name]

[Company Address]

Facsimile number:				[		]

For the attention of:  				[		]

Operational telephone contact number 	[		]

Operational contact 				[		]

SCHEDULE H – Redeclaration Forms/ Restoration Notice

FORM A

STABILITY COMPENSATION SERVICE FAX FORM FOR

REDECLARATION OF INERTIA CAPABILITY

| Facility: |  |  | Tel: |  |
| --- | --- | --- | --- | --- |
| Contract Number: |  |  | Standby Tel: |  |
| Company Name: |  |  | Fax: |  |
| Company Address: |  |  | Standby Fax: |  |

We hereby notify you that the Contracted Inertia Capability of the above Facility will be reduced to [  ] as follows:

Period commencing:

| Unavailability Period |  | Estimated Restoration of Availability |  |
| --- | --- | --- | --- |
| Date | Time | Date | Time |

Reasons for the Contracted Inertia Capability being reduced and the steps being taken to restore Contracted Inertia Capability:

Fax Sent By (Print name): ........................................    Date: ....................Time: .................

Signature:  .........................................

Acknowledged by National Grid Electricity System Operator Limited

(Print name): …………………………………………

Signature: ....................................................................   Date: ..................... Time: ..................

National Grid Electricity System Operator Control

Fax number: [	            	]	         Standby Fax: [		        ]

Telephone:  [		    ]			Standby Phone: [	            ]

Email: [                               ]

FORM B

STABILITY COMPENSATION SERVICE FAX FORM FOR

REDECLARATION OF SCL CAPABILITY

| Facility: |  |  | Tel: |  |
| --- | --- | --- | --- | --- |
| Contract Number: |  |  | Standby Tel: |  |
| Company Name: |  |  | Fax: |  |
| Company Address: |  |  | Standby Fax: |  |

We hereby notify you that the Contracted SCL Capability of the above Facility will be reduced to a level of [    ] as follows:

Period commencing:

| Unavailability Period |  | Estimated Restoration of Contracted SCL Capability |  |
| --- | --- | --- | --- |
| Date | Time | Date | Time |

Reasons for the Contracted SCL Capability being reduced and the steps being taken to restore Contracted SCL Capability:

Fax Sent By (Print name): ........................................    Date: ....................Time: .................

Signature:  .........................................

Acknowledged by National Grid Electricity System Operator Limited

(Print name): …………………………………………

Signature: ....................................................................   Date: ..................... Time: ..................

National Grid Electricity System Operator Control

Fax number: [	            	]	         Standby Fax: [		        ]

Telephone:  [		    ]			Standby Phone: [	            ]

Email: [                               ]

FORM C

STABILITY COMPENSATION SERVICE FAX FORM FOR

REDECLARATION OR RESTORATION OF REACTIVE CAPABILITY

| To: | National Electricity Transmission System Control Centre |
| --- | --- |
| From: | [Enter Company Name & Location] |

REVISED REACTIVE POWER CAPABILITY DATA – GENERATING UNITS EXCLUDING POWER PARK MODULES AND DC CONVERTERS

| Notification Time/Date: |  | HRS MINS DD MM YY . / / |
| --- | --- | --- |
| Start Time/Date: |  | HRS MINS DD MM YY . / / |

| GENERATING UNIT * id |  |
| --- | --- |
| [for BM Units quote the NG BM Unit id, for other units quote the Genset id used for OC2 Output Usable submissions] |  |

REVISION TO THE CONTRACTED REACTIVE CAPABILITY):

|  | MW | Minimum Mvar (+ve for lag, -ve for lead) | Maximum Mvar (+ve for lag, -ve for lead) |
| --- | --- | --- | --- |
| AT RATED MW |  |  |  |
| AT FULL OUTPUT(MW) |  |  |  |
| MINIMUM OUTPUT (MW) |  |  |  |

COMMENTS e.g. generator transformer tap restrictions, predicted end time if known

Steps being taken to restore Contracted Reactive Capability:

| Redeclaration made by (Name & Signature) |  |
| --- | --- |

Receipt Acknowledgement from National Grid ESO

| Legible (tick box) |  | Illegible (tick box) |  |
| --- | --- | --- | --- |

| Explanation: |  |
| --- | --- |
| Time: |  |
| Date: |  |
| Signature |  |

*For a CCGT Module or a Cascade Hydro Scheme, the redeclaration is for a Generating Unit within a CCGT or Cascade Hydro Scheme.

FORM D

STABILITY COMPENSATION SERVICE FAX FORM FOR

RESTORATION NOTICE

| Facility: |  |  | Tel: |  |
| --- | --- | --- | --- | --- |
| Contract Number: |  |  | Standby Tel: |  |
| Company Name: |  |  | Fax: |  |
| Company Address: |  |  | Standby Fax: |  |

We hereby notify you that the [Contracted Inertia Capability] [Contracted SCL Capability] of the Facility will be restored with effect from the period commencing:

| Date | Time |
| --- | --- |

Reason for Restoration of [Contracted Inertia Capability] [Contracted SCL Capability] :

Fax Sent By (Print name): ........................................    Date: ....................Time: .................

Signature:  .........................................

###### Acknowledged by National Grid Electricity System Operator

###### (Print name): …………………………………………

Signature: ................................................ 	          Date: ..................... Time: ..................

National Grid Electricity System Operator Control

National Grid Electricity System Operator Control

Fax number: [	            	]	         Standby Fax: [		        ]

Telephone:   [		    ]			Standby Phone: [	            ]

Email: [                              ]

Existing plant only – for new build this is covered in clause 3.4. If the Provider’s Facility comprises a number of BM Units and the Provider wishes to use more than one unit to provide the service, this contract form will need to be adapted.

Existing plant only – for new build this is covered in PTMs.

Existing plant only – for new build this is covered in clause 3.4.

Post Tender Milestones to be refined and agreed prior to contract award

Delete in the case of existing plant as the Conditions Precedent will cover these requirements.

This will be agreed during the Tender process depending on the Facility and technology type

This payment will not apply to the extent that the Provider is entitled to payment for OPRPS

Note: this clause will be updated once further NGESO requirements have been identified.

Delete where not applicable and replace with “not used”

Note: this clause will be updated once further requirements have been identified.

This will require further consideration in light of the requirement for additionality

Note: this list of services is indicative only and may need to be revised in the light of the additionality requirements.

To be taken from the relevant Provider’s Tender Submission and will need to be inserted following the award a contract.

Delete whichever option does not apply. It is assumed that, in the case of existing plant, some Works will be required to modify the Facility.

This schedule sets out the specific details – namely the Facility in Part A and the Contract Rate in Part B

The Indicative Post Tender Milestones set out above will be discussed with the Company during the Tender process and the Provider may (acting in good faith) indicate any other milestones (and the suggested evidence) which it considers appropriate to its proposed solution.  This schedule shall then be amended accordingly

This schedule is subject to review and updating

Values will be site specific and to be provided by the ESO at the feasibility stage (expected to within the range of 3-13 kA)

If the Facility has a source of active power, it is expected to inject active and reactive power as needed. For a Facility without a source of Active Power, only Reactive Power injection is required.

Reactive generation and absorption values to be as specified by the provider in its Tender Submission.

Guidance on the behaviour of the target voltage mode outside of preset limit will be provided by the company upon contract signature.

This form will be updated to include separate values for Inertia and SCL.

If Inertia Capability is unavailable, insert 0

If SCL Capability is unavailable, insert 0