## Key
Which Proforma Template to use?
Transmission | To be used for Transmission connections and connections to the tertiary windings of supergrid transformers
Distribution | To be used for connections on the distribution network
Aggregator | To be used by aggregators. Aggregators should fill in the relevant details for all the sub-units which form part of the aggregated unit.
Which Section do I need to fill in?
| Filled By | Due Date
Section A- Technical Information | Prospective Provider | 13.12.2019
Section B - Technical Information | NGESO | 07.02.2020
Section C- Commercial Tender | Prospective Provider | 28.02.2020
Category of Information
Minimum requirement which need to be met in order to be eligible to participate in the tender
Other Information required for the technical and commercial assessment
Notes
By filling this tender proforma, you are giving NGESO your consent to share the relevant technical information with the Network Owners in order to carry out the necessary technical assessment. Commercial information will not be shared.
Any submissions which do not meet the minimum technical requirements will not be progressed further in the assessment.
Please send your responses via email to commercial.operation@nationalgrideso.com
If you have any questions, please contact commercial.operation@nationalgrideso.com or call 01926 654611.

## Transmission
Tender Proforma - Firm Contract for Transmission Connections
Section A- To be completed by prospective providers by 13.12.2019
Identifier | A1 | Power Generating Facility/ Asset Name | Name of the generator/ asset offering the service | XXX-1 | XXX-2 | XXX-3 | XXX-4
| A2 | Company Name
| A3 | Company Contact Details | Contact Name, Address, Email, Phone Number
| A4 | Registered Capacity (MW) (if applicable)
| A5 | Fuel Type | E.g. Biomass, Diesel, CHP, Storage etc
Location | A6 | Please select your connection status from the drop-down list. | Please select the applicable option from the dropdown list.
| A7 | Electrical Single line Diagram of your connection (if available) | Please provide an electrical layout diagram of your existing or proposed connection if available.
| A8 | Connection Point Voltage Level | Please specify the voltage of your existing or proposed point of connection.
| A9 | Connection Point on the Transmission Network | Please specify the name of the substation/ asset that you are connected to or intend to connect to.
| A10 | Postcode of Connection point (if known) | Postcode of Transmission Connection, if known
| A11 | When do you expect to connect to the network? (for new connections only)
Technical Capability | A12 | Contracted MVAr Capability | Please specify the maximum MVAr value you are tendering for. This should not be smaller than 15 MVAr. Max size depends on voltage level. See slide 23 of the tender pack for details.
| A13 | Can your solution operate in constant reactive power mode? | Y/N
| A14 | Are you available to provide a reactive power service from 01/04/2022 until 01/04/2031? | Y/N
| A15 | Can you guarantee 24/7 availability outside of planned or unplanned outages? | Y/N
| A16 | Do you need to produce active power to provide the reactive power service? | Y/N
| A17 | If the answer to A16 is 'Y', what is the minimum active power level that is required?
| A18 | Is your solution able to remain connected or stable in the event of faults causing the voltage at the Grid Entry Point or User System Entry Pont to drop to 0 pu for 140 ms? | Y/N
Dispatch | A19 | Can you acknowledge a dispatch instruction within 2 minutes of it being issued? | Y/N
| A20 | Is your solution dispatchable via EDL/EDT or over VPN via IEC104 server? | Y/N (Please specify dispatch mechanism)
| A21 | What is the minimum notice period that you require to enact the service? | Please note that this should be no longer than 30 mins.
Other | A22 | Comments | Please let us know if there is anything else we should be aware of when assessing this offer e.g. typical outage windows etc.
Section B - To be completed by NGESO by 07.02.2020
| B1 | Effectiveness of solution | NGESO will provide the effectiveness of your solution
| B2 | List of Reinforcements (if applicable)
| B3 | Cost of Reinforcements (if applicable)
| B4 | Earliest Date the Reinforcements can be delivered (if applicable)
| B5 | Comments
Section C - To be completed by prospective providers by 28.02.2020
| C1 | Availability Fee (£/Settlement Period) | Please note that this should be inclusive of losses
| C2 | Losses Calculated | Please provide details of how the losses have been calculated
| C3 | Comments

## Distribution
Tender Proforma - Firm Contract for Distribution Connections
Section A- To be completed by prospective providers by 13.12.2019
Identifier | A1 | Power Generating Facility/ Asset Name | Name of the generator/asset offering the service | XXX-1 | XXX-2 | XXX-3 | XXX-4
| A2 | Company Name
| A3 | Company Contact Details | Contact Name, Address, Email, Phone Number
| A4 | Registered Capacity (MW) (if Applicable)
| A5 | Metering Point Administration Number (MPAN) (if Applicable) | 13 digit Number to include Distributor ID, Meter Point ID number and Check Digit
| A6 | Fuel Type | E.g. Biomass, Diesel, CHP, Storage etc
Location | A7 | Please select your connection status from the drop-down list. | Please select the applicable option from the dropdown list.
| A8 | Electrical Single line Diagram of your connection (if available) | Please provide an electrical layout diagram of your existing or proposed connection if available.
| A9 | Connection Point Voltage Level | Please specify the voltage of your existing or proposed point of connection.
| A10 | Connection Point on the Distribution level | Please specify the name of the substation that you are connected to. Please contact DNO if unsure.
| A11 | Postcode of Connection point (if known) | Postcode of Distribution Connection, if known
| A12 | When do you expect to connect to the network (for new connections only)
Technical Capability | A13 | Existing Power Factor Setting (if applicable) | If you are currently operating at a set power factor, please let us know the setting. The power factor requirement is applied at the metered circuit breaker.
| A14 | Do you have facilities to control the Power Factor daily (if required)? | At the time where you are not providing a reactive power service, you may be asked to operate at a different power factor
| A15 | Tendered MVAr Capability | Please specify the maximum MVAr value you are tendering for. This should not be smaller than 15 MVAr. Max size depends on voltage level. See slide 23 of the tender pack for details.
| A16 | Suggested Power Factor (please state if you are flexible on the Power Factor) | Please note that the DNO will conduct an assessment to determine the optimum Power Factor for your solution. If you are not flexible on the Power Factor, the DNO will propose network reinforcements, where possible, to enable your suggested Power Factor.
| A17 | Would you like the DNO to propose reinforcements that will enable your suggested Power Factor in A16? | Y/N. Please note that you will be under no obligation to sign up to these reinforcements at this stage. If your answer to this Question is 'N' please note that your power factor of operation will be determined by the DNO.
| A18 | Generator Reactive Capability Chart | Please provide a reactive capability chart for your solution where available
| A19 | Max Mvar Absorption Capability at 0.5 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A20 | Max Mvar Absorption Capability at 0.6 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A21 | Max Mvar Absorption Capability at 0.7 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A22 | Max Mvar Absorption Capability at 0.8 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A23 | Max Mvar Absorption Capability at 0.9 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A24 | Max Mvar Absorption Capability at 0.95 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A25 | Max MVAr absorption capability at min Active Power level | Mvar capacity must be a minimum of 15MVar absorption at the point of connection
| A26 | Min Active Power level | Please state the Stable Export Limit of your generator if applicable
| A27 | What type of Loss of mains protection setting do you currently implement? E.g. RoCoF, Vector Shift | E.g. RoCoF, Vector Shift
| A28 | If applicable, do you plan to remove/ replace vector shift protection before 1 April 2022? | Y/N
| A29 | If applicable, will your RoCoF protection setting be set to a minimum of 1Hz/s before 1 April 2022? | Y/N
| A30 | Is your solution able to remain connected or stable in the event of faults causing the voltage at the Grid Entry Point or User System Entry Pont to drop to 0 pu for 140 ms? | Y/N
| A31 | Can you guarantee 24/7 availability outside of planned or unplanned outages? | Y/N
Dispatch | A32 | Can you acknowledge a dispatch instruction within 2 minutes of it being issued? | Y/N
| A33 | Is your solution dispatchable via EDL/EDT or over VPN via IEC104 server? | Y/N (Please specify dispatch mechanism)
| A34 | What is the minimum notice period that you require to enact the service? | Please note that this should be no longer than 30 mins.
Other | A35 | Comments | Please let us know if there is anything else we should be aware of when assessing this offer e.g. typical outage windows etc.
Section B - To be completed by NGESO by 07.02.2020
| B1 | Power Factor of proposed option (if no reinforcements are delivered)
| B2 | Power Factor of proposed option (if reinforcements are delivered)
| B3 | List of Reinforcements (if applicable)
| B4 | Cost of Reinforcements (if applicable)
| B5 | Earliest Date the Reinforcements can be delivered (if applicable)
| B6 | Effectiveness of solution (if no reinforcements are delivered) | NGESO will provide the effectiveness of your solution
| B7 | Effectiveness of solution (if reinforcements are delivered) | NGESO will provide the effectiveness of your solution
| B8 | Comments
Section C - To be completed by prospective providers by 28.02.2020
| C1 | Do you wish to accept the DNO network reinforcement? | Y/N- If the answer is 'N', the power factor listed B1 will apply. If the answer is 'Y', you can select a power factor which is between the values listed B1 and B2 (inclusive).
| C2 | Tendered MVAr Capability | Please confirm the MVAr capability for your commercial tender
| C3 | Tendered Power Factor | Please confirm the power factor for your commercial tender (Either B1 or between B1 and B2 depending on your answer in C1)
| C4 | Availability Fee (£/Settlement Period) | Please note that this should be inclusive of losses
| C5 | Losses calculation | Please provide details of how the losses have been calculated
| C6 | Comments

## Aggregators
Tender Proforma - Firm Contract for Aggregators
|  |  |  | Please fill in a new sheet for additional aggregated units | Each sub-unit can only be allocated to one aggregated unit |  |  |  | Please copy this column if you wish to add more sub-units
Section A- To be completed by Aggregators by 13/12/2019
|  |  |  | Aggregated Unit | Sub- Unit 1 | Sub- Unit 2 | Sub- Unit 3 | Sub- Unit 4 | Sub- Unit 5
Identifier | A1 | Power Generating Facility/ Asset Name | Name of the generator/ asset offering the service | XXX-A | XXX-1 | XXX-2 | XXX-3 | XXX-4 | XXX-5
| A2 | Company Name
| A3 | Company Contact Details | Contact Name, Address, Email, Phone Number
| A4 | Registered Capacity (MW) (if Applicable)
| A5 | Metering Point Administration Number (MPAN) (if Applicable) | 13 digit Number to include Distributor ID, Meter Point ID number and Check Digit
| A6 | Fuel Type | E.g. Biomass, Diesel, CHP, Storage etc
Location | A7 | Please select your connection status from the drop-down list. | Please select the applicable option from the dropdown list.
| A8 | Electrical Single line Diagram of your connection (if available) | Please provide an electrical layout diagram of your existing or proposed connection if available.
| A9 | Connection Voltage Level | Please specify the voltage of your existing or proposed point of connection .
| A10 | Connection Point on the Distribution level | Please specify the name of the substation that you are connected to. Please contact DNO if unsure.
| A11 | Postcode of Connection point (if known) | Postcode of Distribution Connection, if known
| A12 | When do you expect to connect to the network (for new connections only)
Technical Capability | A13 | Existing Power Factor Setting (if applicable) | If you are currently operating at a set power factor, please let us know the setting. The power factor requirement is applied at the metered circuit breaker.
| A14 | Do you have facilities to control the Power Factor daily (if required)? | At time where you are not providing a reactive power service, you may be asked to operate at a different power factor e.g. unity
| A15 | Tendered MVAr Capability | Please specify the maximum MVAr value you are tendering for. This should not be smaller than 15 MVAr. Max size depends on voltage level. See slide 23 of the tender pack for details.
| A16 | Suggested Power Factor (please state if you are flexible on the Power Factor) | Please note that the DNO will conduct an assessment to determine the optimum Power Factor for your solution. If you are not flexible on the Power Factor, the DNO will propose network reinforcements, where possible, to enable your suggested Power Factor.
| A17 | Would you like the DNO to propose reinforcements that will enable your suggested Power Factor in A16? | Y/N. Please note that you will be under no obligation to sign up to these reinforcements at this stage. If your answer to this Question is 'N' please note that your power factor of operation will be determined by the DNO.
| A18 | Generator Reactive Capability Chart | Please provide a reactive capability chart for your solution where available
| A19 | Max Mvar Absorption Capability at 0.5 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A20 | Max Mvar Absorption Capability at 0.6 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A21 | Max Mvar Absorption Capability at 0.7 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A22 | Max Mvar Absorption Capability at 0.8 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A23 | Max Mvar Absorption Capability at 0.9 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A24 | Max Mvar Absorption Capability at 0.95 leading Power Factor | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A25 | Max MVAr absorption capability at min Active Power level | Mvar capacity must be a minimum of 15MVar absorption for aggregated units. Each sub-unit must be a minimum of 5 MVAr
| A26 | Min Active Power level | Please state the Stable Export Limit of your generator if applicable
| A27 | What type of Loss of mains protection setting do you currently implement? | E.g. RoCoF, Vector Shift
| A28 | If applicable, do you plan to remove/ replace vector shift protection before 1 April 2022? | Y/N
| A29 | If applicable, will your RoCoF protection setting be set to a minimum of 1Hz/s before 1 April 2022? | Y/N
| A30 | Is your solution able to remain connected or stable in the event of faults causing the voltage at the Grid Entry Point or User System Entry Pont to drop to 0 pu for 140 ms? | Y/N
| A31 | Can you guarantee 24/7 availability outside of planned or unplanned outages? | Y/N
Dispatch | A32 | Can you acknowledge a dispatch instruction within 2 minutes of it being issued? | Y/N
| A33 | Is your solution dispatchable via EDL/EDT or over VPN via IEC104 server? | Y/N (Please specify dispatch mechanism)
| A34 | What is the minimum notice period that you require to enact the service? | Please note that this should be no longer than 30 mins.
Other | A35 | Comments | Please let us know if there is anything else we should be aware of when assessing this offer e.g. typical outage windows etc.
Section B - To be completed by NGESO by 07.02.2020
| B1 | Power Factor of proposed option (if no reinforcements are delivered)
| B2 | Power Factor of proposed option (if reinforcements are delivered)
| B3 | List of Reinforcements (if applicable)
| B4 | Cost of Reinforcements (if applicable)
| B5 | Earliest Date the Reinforcements can be delivered (if applicable)
| B6 | Effectiveness of solution (if no reinforcements are delivered) | NGESO will provide the effectiveness of your solution
| B7 | Effectiveness of solution (if reinforcements are delivered) | NGESO will provide the effectiveness of your solution
| B8 | Comments
Section C - To be completed by Aggregators by 28.02.2020
| C1 | Do you wish to accept the DNO network reinforcement? | Y/N- If the answer is 'N', the power factor listed B1 will apply. If the answer is 'Y', you can select a power factor which is between the values listed B1 and B2 (inclusive).
| C2 | Tendered MVAr Capability | Please confirm the MVAr capability for your commercial tender
| C3 | Tendered Power Factor | Please confirm the power factor for your commercial tender (Either B1 or between B1 and B2 depending on your answer in C1)
| C4 | Availability Fee (£/Settlement Period) | Please note that this should be inclusive of losses
| C5 | Losses calculation | Please provide details of how the losses have been calculated
| C6 | Comments

## Sheet1 (hidden)
New connection proposal not discussed with Network Owner
New Connection discussed with Network owner
Connection Application submitted
Connection offer issued
Connection offer accepted
Already Connected
Y
N