## Front
Dynamic Containment Performance Bound example spreadsheet
DISCLAIMER: Please note, this file is for illustrative purposes ONLY and should not be relied on, or treated as a substitute for the Service Terms.
Purpose: | To demonstrate how to calculate the upper and lower performance bounds with regards to dynamic containment performance monitoring
Sheets: | Example dataset | Dataset with general explanation on column meanings
| Using Excel formulae | The same dataset replicated with formulae
| Frequency windows | Plot of the resulting frequency windows used in the algorithm
| Bounds | Plot of both the upper and lower bounds of the performance algorithm
| Upper bound | Plot of the upper bound of the performance algorithm with and without ramp limits
| Lower bound | Plot of the lower bound of the performance algorithm with and without ramp limits
Note: | Example data shown is to demonstrate ramp limits and is not reflective of a real life scenario

## Example dataset
t | f | lfw | unr | ub | ufw | lnr | lb
0 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | NOTE: This is the dataset that was used for the example graphs in the service terms document
0.05 | 50 | 50 | 0 | 0 | 50 | 0 | 0
0.1 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | t | Time (s)
0.15 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | f | Frequency (Hz)
0.2 | 50 | 50 | 0 | 0 | 50 | 0 | 0
0.25 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | lfw | Lower frequency window (Hz) |  |  | This is a lagged rolling minimum calculation
0.3 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | unr | Upper bound without ramp limits (MW) |  |  | This is the response curve applied to the lower frequency window
0.35 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | ub | Upper bound (MW) |  |  | This is unr with the ramp limit applied to decreases
0.4 | 50 | 50 | 0 | 0 | 50 | 0 | 0
0.45 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | ufw | Upper frequency window (Hz) |  |  | This is a lagged rolling maximum calculation
0.5 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0 | lnr | Lower bound without ramp limits (MW) |  |  | This is the response curve applied to the upper frequency window
0.55 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0 | lb | Lower bound (MW) |  |  | This is lnr with the ramp limit applied to increases
0.6 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.65 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.7 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0 | This example is for 100 MW of LF and HF DC
0.75 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.8 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0 | The ramp rate limit is |  | 200 | MW / s | or | 10 | MW per 0.05 s
0.85 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.9 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.95 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
1 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0 | The upwards ramp limits are highlighted in yellow and the downwards ramp limits are highlighted in blue
1.05 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 10
1.1 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 20
1.15 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 30 | The calculation is recreated with excel formulas in the second worksheet.
1.2 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 40
1.25 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 50
1.3 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 60
1.35 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 70
1.4 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 80
1.45 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 90
1.5 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.55 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.6 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.65 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.7 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.75 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.8 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.85 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.9 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.95 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.05 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.1 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.15 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.2 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.25 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.3 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.35 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.4 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.45 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.5 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.55 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.6 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.65 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.7 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.75 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.8 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.85 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.9 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.95 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
3 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
3.05 | 50.5 | 50.5 | -100 | 90 | 50.5 | -100 | -100
3.1 | 50.5 | 50.5 | -100 | 80 | 50.5 | -100 | -100
3.15 | 50.5 | 50.5 | -100 | 70 | 50.5 | -100 | -100
3.2 | 50.5 | 50.5 | -100 | 60 | 50.5 | -100 | -100
3.25 | 50.5 | 50.5 | -100 | 50 | 50.5 | -100 | -100
3.3 | 50.5 | 50.5 | -100 | 40 | 50.5 | -100 | -100
3.35 | 50.5 | 50.5 | -100 | 30 | 50.5 | -100 | -100
3.4 | 50.5 | 50.5 | -100 | 20 | 50.5 | -100 | -100
3.45 | 50.5 | 50.5 | -100 | 10 | 50.5 | -100 | -100
3.5 | 50.5 | 50.5 | -100 | 0 | 50.5 | -100 | -100
3.55 | 50.5 | 50.5 | -100 | -10 | 50.5 | -100 | -100
3.6 | 50.5 | 50.5 | -100 | -20 | 50.5 | -100 | -100
3.65 | 50.5 | 50.5 | -100 | -30 | 50.5 | -100 | -100
3.7 | 50.5 | 50.5 | -100 | -40 | 50.5 | -100 | -100
3.75 | 50.5 | 50.5 | -100 | -50 | 50.5 | -100 | -100
3.8 | 50.5 | 50.5 | -100 | -60 | 50.5 | -100 | -100
3.85 | 50.5 | 50.5 | -100 | -70 | 50.5 | -100 | -100
3.9 | 50.5 | 50.5 | -100 | -80 | 50.5 | -100 | -100
3.95 | 50.5 | 50.5 | -100 | -90 | 50.5 | -100 | -100
4 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.05 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.1 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.15 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.2 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.25 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.3 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.35 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.4 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.45 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.5 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.55 | 50.4744 | 50.4744 | -91.8803 | -91.8803 | 50.5 | -100 | -100
4.6 | 50.4487 | 50.4487 | -83.7607 | -83.7607 | 50.5 | -100 | -100
4.65 | 50.4231 | 50.4231 | -75.641 | -75.641 | 50.5 | -100 | -100
4.7 | 50.3974 | 50.3974 | -67.5214 | -67.5214 | 50.5 | -100 | -100
4.75 | 50.3718 | 50.3718 | -59.4017 | -59.4017 | 50.5 | -100 | -100
4.8 | 50.3462 | 50.3462 | -51.2821 | -51.2821 | 50.5 | -100 | -100
4.85 | 50.3205 | 50.3205 | -43.1624 | -43.1624 | 50.5 | -100 | -100
4.9 | 50.2949 | 50.2949 | -35.0427 | -35.0427 | 50.5 | -100 | -100
4.95 | 50.2692 | 50.2692 | -26.9231 | -26.9231 | 50.5 | -100 | -100
5 | 50.2436 | 50.2436 | -18.8034 | -18.8034 | 50.5 | -100 | -100
5.05 | 50.2179 | 50.2179 | -10.6838 | -10.6838 | 50.5 | -100 | -100
5.1 | 50.1923 | 50.1923 | -4.7921 | -4.7921 | 50.4744 | -91.8803 | -91.8803
5.15 | 50.1667 | 50.1667 | -4.0991 | -4.0991 | 50.4487 | -83.7607 | -83.7607
5.2 | 50.141 | 50.141 | -3.4061 | -3.4061 | 50.4231 | -75.641 | -75.641
5.25 | 50.1154 | 50.1154 | -2.7131 | -2.7131 | 50.3974 | -67.5214 | -67.5214
5.3 | 50.0897 | 50.0897 | -2.0201 | -2.0201 | 50.3718 | -59.4017 | -59.4017
5.35 | 50.0641 | 50.0641 | -1.3271 | -1.3271 | 50.3462 | -51.2821 | -51.2821
5.4 | 50.0385 | 50.0385 | -0.6341 | -0.6341 | 50.3205 | -43.1624 | -43.1624
5.45 | 50.0128 | 50.0128 | 0 | 0 | 50.2949 | -35.0427 | -35.0427
5.5 | 49.9872 | 49.9872 | 0 | 0 | 50.2692 | -26.9231 | -26.9231
5.55 | 49.9615 | 49.9615 | 0.6341 | 0.6341 | 50.2436 | -18.8034 | -18.8034
5.6 | 49.9359 | 49.9359 | 1.3271 | 1.3271 | 50.2179 | -10.6838 | -10.6838
5.65 | 49.9103 | 49.9103 | 2.0201 | 2.0201 | 50.1923 | -4.7921 | -4.7921
5.7 | 49.8846 | 49.8846 | 2.7131 | 2.7131 | 50.1667 | -4.0991 | -4.0991
5.75 | 49.859 | 49.859 | 3.4061 | 3.4061 | 50.141 | -3.4061 | -3.4061
5.8 | 49.8333 | 49.8333 | 4.0991 | 4.0991 | 50.1154 | -2.7131 | -2.7131
5.85 | 49.8077 | 49.8077 | 4.7921 | 4.7921 | 50.0897 | -2.0201 | -2.0201
5.9 | 49.7821 | 49.7821 | 10.6838 | 10.6838 | 50.0641 | -1.3271 | -1.3271
5.95 | 49.7564 | 49.7564 | 18.8034 | 18.8034 | 50.0385 | -0.6341 | -0.6341
6 | 49.7308 | 49.7308 | 26.9231 | 26.9231 | 50.0128 | 0 | 0
6.05 | 49.7051 | 49.7051 | 35.0427 | 35.0427 | 49.9872 | 0 | 0
6.1 | 49.6795 | 49.6795 | 43.1624 | 43.1624 | 49.9615 | 0.6341 | 0.6341
6.15 | 49.6538 | 49.6538 | 51.2821 | 51.2821 | 49.9359 | 1.3271 | 1.3271
6.2 | 49.6282 | 49.6282 | 59.4017 | 59.4017 | 49.9103 | 2.0201 | 2.0201
6.25 | 49.6026 | 49.6026 | 67.5214 | 67.5214 | 49.8846 | 2.7131 | 2.7131
6.3 | 49.5769 | 49.5769 | 75.641 | 75.641 | 49.859 | 3.4061 | 3.4061
6.35 | 49.5513 | 49.5513 | 83.7607 | 83.7607 | 49.8333 | 4.0991 | 4.0991
6.4 | 49.5256 | 49.5256 | 91.8803 | 91.8803 | 49.8077 | 4.7921 | 4.7921
6.45 | 49.5 | 49.5 | 100 | 100 | 49.7821 | 10.6838 | 10.6838
6.5 | 49.5 | 49.5 | 100 | 100 | 49.7564 | 18.8034 | 18.8034
6.55 | 49.5256 | 49.5 | 100 | 100 | 49.7308 | 26.9231 | 26.9231
6.6 | 49.5513 | 49.5 | 100 | 100 | 49.7051 | 35.0427 | 35.0427
6.65 | 49.5769 | 49.5 | 100 | 100 | 49.6795 | 43.1624 | 43.1624
6.7 | 49.6026 | 49.5 | 100 | 100 | 49.6538 | 51.2821 | 51.2821
6.75 | 49.6282 | 49.5 | 100 | 100 | 49.6282 | 59.4017 | 59.4017
6.8 | 49.6538 | 49.5 | 100 | 100 | 49.6538 | 51.2821 | 51.2821
6.85 | 49.6795 | 49.5 | 100 | 100 | 49.6795 | 43.1624 | 43.1624
6.9 | 49.7051 | 49.5 | 100 | 100 | 49.7051 | 35.0427 | 35.0427
6.95 | 49.7308 | 49.5 | 100 | 100 | 49.7308 | 26.9231 | 26.9231
7 | 49.7564 | 49.5 | 100 | 100 | 49.7564 | 18.8034 | 18.8034
7.05 | 49.7821 | 49.5 | 100 | 100 | 49.7821 | 10.6838 | 10.6838
7.1 | 49.8077 | 49.5256 | 91.8803 | 91.8803 | 49.8077 | 4.7921 | 4.7921
7.15 | 49.8333 | 49.5513 | 83.7607 | 83.7607 | 49.8333 | 4.0991 | 4.0991
7.2 | 49.859 | 49.5769 | 75.641 | 75.641 | 49.859 | 3.4061 | 3.4061
7.25 | 49.8846 | 49.6026 | 67.5214 | 67.5214 | 49.8846 | 2.7131 | 2.7131
7.3 | 49.9103 | 49.6282 | 59.4017 | 59.4017 | 49.9103 | 2.0201 | 2.0201
7.35 | 49.9359 | 49.6538 | 51.2821 | 51.2821 | 49.9359 | 1.3271 | 1.3271
7.4 | 49.9615 | 49.6795 | 43.1624 | 43.1624 | 49.9615 | 0.6341 | 0.6341
7.45 | 49.9872 | 49.7051 | 35.0427 | 35.0427 | 49.9872 | 0 | 0
7.5 | 50.0128 | 49.7308 | 26.9231 | 26.9231 | 50.0128 | 0 | 0
7.55 | 50.0385 | 49.7564 | 18.8034 | 18.8034 | 50.0385 | -0.6341 | -0.6341
7.6 | 50.0641 | 49.7821 | 10.6838 | 10.6838 | 50.0641 | -1.3271 | -1.3271
7.65 | 50.0897 | 49.8077 | 4.7921 | 4.7921 | 50.0897 | -2.0201 | -2.0201
7.7 | 50.1154 | 49.8333 | 4.0991 | 4.0991 | 50.1154 | -2.7131 | -2.7131
7.75 | 50.141 | 49.859 | 3.4061 | 3.4061 | 50.141 | -3.4061 | -3.4061
7.8 | 50.1667 | 49.8846 | 2.7131 | 2.7131 | 50.1667 | -4.0991 | -4.0991
7.85 | 50.1923 | 49.9103 | 2.0201 | 2.0201 | 50.1923 | -4.7921 | -4.7921
7.9 | 50.2179 | 49.9359 | 1.3271 | 1.3271 | 50.2179 | -10.6838 | -10.6838
7.95 | 50.2436 | 49.9615 | 0.6341 | 0.6341 | 50.2436 | -18.8034 | -18.8034
8 | 50.2692 | 49.9872 | 0 | 0 | 50.2692 | -26.9231 | -26.9231
8.05 | 50.2949 | 50.0128 | 0 | 0 | 50.2949 | -35.0427 | -35.0427
8.1 | 50.3205 | 50.0385 | -0.6341 | -0.6341 | 50.3205 | -43.1624 | -43.1624
8.15 | 50.3462 | 50.0641 | -1.3271 | -1.3271 | 50.3462 | -51.2821 | -51.2821
8.2 | 50.3718 | 50.0897 | -2.0201 | -2.0201 | 50.3718 | -59.4017 | -59.4017
8.25 | 50.3974 | 50.1154 | -2.7131 | -2.7131 | 50.3974 | -67.5214 | -67.5214
8.3 | 50.4231 | 50.141 | -3.4061 | -3.4061 | 50.4231 | -75.641 | -75.641
8.35 | 50.4487 | 50.1667 | -4.0991 | -4.0991 | 50.4487 | -83.7607 | -83.7607
8.4 | 50.4744 | 50.1923 | -4.7921 | -4.7921 | 50.4744 | -91.8803 | -91.8803
8.45 | 50.5 | 50.2179 | -10.6838 | -10.6838 | 50.5 | -100 | -100
8.5 | 50.5 | 50.2436 | -18.8034 | -18.8034 | 50.5 | -100 | -100
8.55 | 50.4737 | 50.2692 | -26.9231 | -26.9231 | 50.5 | -100 | -100
8.6 | 50.4474 | 50.2949 | -35.0427 | -35.0427 | 50.5 | -100 | -100
8.65 | 50.4211 | 50.3205 | -43.1624 | -43.1624 | 50.5 | -100 | -100
8.7 | 50.3947 | 50.3462 | -51.2821 | -51.2821 | 50.5 | -100 | -100
8.75 | 50.3684 | 50.3684 | -58.3333 | -58.3333 | 50.5 | -100 | -100
8.8 | 50.3421 | 50.3421 | -50 | -50 | 50.5 | -100 | -100
8.85 | 50.3158 | 50.3158 | -41.6667 | -41.6667 | 50.5 | -100 | -100
8.9 | 50.2895 | 50.2895 | -33.3333 | -33.3333 | 50.5 | -100 | -100
8.95 | 50.2632 | 50.2632 | -25 | -25 | 50.5 | -100 | -100
9 | 50.2368 | 50.2368 | -16.6667 | -16.6667 | 50.5 | -100 | -100
9.05 | 50.2105 | 50.2105 | -8.3333 | -8.3333 | 50.5 | -100 | -100
9.1 | 50.1842 | 50.1842 | -4.5733 | -4.5733 | 50.4737 | -91.6667 | -91.6667
9.15 | 50.1579 | 50.1579 | -3.862 | -3.862 | 50.4474 | -83.3333 | -83.3333
9.2 | 50.1316 | 50.1316 | -3.1508 | -3.1508 | 50.4211 | -75 | -75
9.25 | 50.1053 | 50.1053 | -2.4395 | -2.4395 | 50.3947 | -66.6667 | -66.6667
9.3 | 50.0789 | 50.0789 | -1.7283 | -1.7283 | 50.3684 | -58.3333 | -58.3333
9.35 | 50.0526 | 50.0526 | -1.0171 | -1.0171 | 50.3421 | -50 | -50
9.4 | 50.0263 | 50.0263 | -0.30583 | -0.30583 | 50.3158 | -41.6667 | -41.6667
9.45 | 50 | 50 | 0 | 0 | 50.2895 | -33.3333 | -33.3333
9.5 | 50.0014 | 50 | 0 | 0 | 50.2632 | -25 | -25
9.55 | 50.0014 | 50 | 0 | 0 | 50.2368 | -16.6667 | -16.6667
9.6 | 49.9974 | 49.9974 | 0 | 0 | 50.2105 | -8.3333 | -8.3333
9.65 | 49.9974 | 49.9974 | 0 | 0 | 50.1842 | -4.5733 | -4.5733
9.7 | 49.9992 | 49.9974 | 0 | 0 | 50.1579 | -3.862 | -3.862
9.75 | 49.9992 | 49.9974 | 0 | 0 | 50.1316 | -3.1508 | -3.1508
9.8 | 50.0136 | 49.9974 | 0 | 0 | 50.1053 | -2.4395 | -2.4395
9.85 | 50.0136 | 49.9974 | 0 | 0 | 50.0789 | -1.7283 | -1.7283
9.9 | 49.9891 | 49.9891 | 0 | 0 | 50.0526 | -1.0171 | -1.0171
9.95 | 49.9891 | 49.9891 | 0 | 0 | 50.0263 | -0.30583 | -0.30583
10 | 49.9257 | 49.9257 | 1.6021 | 1.6021 | 50.0136 | 0 | 0
10.05 | 49.9257 | 49.9257 | 1.6021 | 1.6021 | 50.0136 | 0 | 0
10.1 | 49.9123 | 49.9123 | 1.9648 | 1.9648 | 50.0136 | 0 | 0
10.15 | 49.9123 | 49.9123 | 1.9648 | 1.9648 | 50.0136 | 0 | 0
10.2 | 49.8631 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.25 | 49.8631 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.3 | 49.8907 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.35 | 49.8907 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.4 | 49.8527 | 49.8527 | 3.5765 | 3.5765 | 50.0136 | 0 | 0
10.45 | 49.8527 | 49.8527 | 3.5765 | 3.5765 | 49.9891 | 0 | 0
10.5 | 49.853 | 49.8527 | 3.5765 | 3.5765 | 49.9891 | 0 | 0
10.55 | 49.853 | 49.8527 | 3.5765 | 3.5765 | 49.9257 | 1.6021 | 1.6021
10.6 | 49.9075 | 49.8527 | 3.5765 | 3.5765 | 49.9257 | 1.6021 | 1.6021
10.65 | 49.9075 | 49.8527 | 3.5765 | 3.5765 | 49.9123 | 1.9648 | 1.9648
10.7 | 49.9408 | 49.8527 | 3.5765 | 3.5765 | 49.9408 | 1.1955 | 1.1955
10.75 | 49.9408 | 49.8527 | 3.5765 | 3.5765 | 49.9408 | 1.1955 | 1.1955
10.8 | 49.9496 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
10.85 | 49.9496 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
10.9 | 49.9342 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
10.95 | 49.9342 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
11 | 49.9587 | 49.8527 | 3.5765 | 3.5765 | 49.9587 | 0.71194 | 0.71194
11.05 | 49.9587 | 49.853 | 3.5687 | 3.5687 | 49.9587 | 0.71194 | 0.71194
11.1 | 49.9906 | 49.853 | 3.5687 | 3.5687 | 49.9906 | 0 | 0
11.15 | 49.9906 | 49.9075 | 2.0951 | 2.0951 | 49.9906 | 0 | 0
11.2 | 49.9903 | 49.9075 | 2.0951 | 2.0951 | 49.9906 | 0 | 0
11.25 | 49.9903 | 49.9342 | 1.3741 | 1.3741 | 49.9906 | 0 | 0
11.3 | 49.9556 | 49.9342 | 1.3741 | 1.3741 | 49.9906 | 0 | 0
11.35 | 49.9556 | 49.9342 | 1.3741 | 1.3741 | 49.9906 | 0 | 0
11.4 | 50.0104 | 49.9342 | 1.3741 | 1.3741 | 50.0104 | 0 | 0
11.45 | 50.0104 | 49.9342 | 1.3741 | 1.3741 | 50.0104 | 0 | 0
11.5 | 50.0473 | 49.9342 | 1.3741 | 1.3741 | 50.0473 | -0.87176 | -0.87176
11.55 | 50.0473 | 49.9556 | 0.79433 | 0.79433 | 50.0473 | -0.87176 | -0.87176
11.6 | 49.9746 | 49.9556 | 0.79433 | 0.79433 | 50.0473 | -0.87176 | -0.87176
11.65 | 49.9746 | 49.9556 | 0.79433 | 0.79433 | 50.0473 | -0.87176 | -0.87176
11.7 | 49.9197 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.75 | 49.9197 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.8 | 49.9919 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.85 | 49.9919 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.9 | 49.9387 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.95 | 49.9387 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12 | 50.0096 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12.05 | 50.0096 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12.1 | 49.9918 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12.15 | 49.9918 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.2 | 49.9519 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.25 | 49.9519 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.3 | 49.9455 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.35 | 49.9455 | 49.9387 | 1.2516 | 1.2516 | 50.0096 | 0 | 0
12.4 | 49.9734 | 49.9387 | 1.2516 | 1.2516 | 50.0096 | 0 | 0
12.45 | 49.9734 | 49.9387 | 1.2516 | 1.2516 | 50.0096 | 0 | 0
12.5 | 49.9374 | 49.9374 | 1.2855 | 1.2855 | 50.0096 | 0 | 0
12.55 | 49.9374 | 49.9374 | 1.2855 | 1.2855 | 50.0096 | 0 | 0
12.6 | 49.8711 | 49.8711 | 3.0776 | 3.0776 | 50.0096 | 0 | 0
12.65 | 49.8711 | 49.8711 | 3.0776 | 3.0776 | 49.9918 | 0 | 0
12.7 | 49.8501 | 49.8501 | 3.6447 | 3.6447 | 49.9918 | 0 | 0
12.75 | 49.8501 | 49.8501 | 3.6447 | 3.6447 | 49.9734 | 0.31294 | 0.31294
12.8 | 49.7875 | 49.7875 | 8.9587 | 8.9587 | 49.9734 | 0.31294 | 0.31294
12.85 | 49.7875 | 49.7875 | 8.9587 | 8.9587 | 49.9734 | 0.31294 | 0.31294
12.9 | 49.7867 | 49.7867 | 9.2116 | 9.2116 | 49.9734 | 0.31294 | 0.31294
12.95 | 49.7867 | 49.7867 | 9.2116 | 9.2116 | 49.9734 | 0.31294 | 0.31294
13 | 49.8434 | 49.7867 | 9.2116 | 9.2116 | 49.9734 | 0.31294 | 0.31294
13.05 | 49.8434 | 49.7867 | 9.2116 | 9.2116 | 49.9374 | 1.2855 | 1.2855
13.1 | 49.8893 | 49.7867 | 9.2116 | 9.2116 | 49.9374 | 1.2855 | 1.2855
13.15 | 49.8893 | 49.7867 | 9.2116 | 9.2116 | 49.8893 | 2.5866 | 2.5866
13.2 | 49.8904 | 49.7867 | 9.2116 | 9.2116 | 49.8904 | 2.5568 | 2.5568
13.25 | 49.8904 | 49.7867 | 9.2116 | 9.2116 | 49.8904 | 2.5568 | 2.5568
13.3 | 49.961 | 49.7867 | 9.2116 | 9.2116 | 49.961 | 0.64754 | 0.64754
13.35 | 49.961 | 49.7867 | 9.2116 | 9.2116 | 49.961 | 0.64754 | 0.64754
13.4 | 50.0228 | 49.7867 | 9.2116 | 9.2116 | 50.0228 | -0.21089 | -0.21089
13.45 | 50.0228 | 49.7867 | 9.2116 | 9.2116 | 50.0228 | -0.21089 | -0.21089
13.5 | 50.0332 | 49.7867 | 9.2116 | 9.2116 | 50.0332 | -0.49282 | -0.49282
13.55 | 50.0332 | 49.8434 | 3.8268 | 3.8268 | 50.0332 | -0.49282 | -0.49282
13.6 | 50.0179 | 49.8434 | 3.8268 | 3.8268 | 50.0332 | -0.49282 | -0.49282
13.65 | 50.0179 | 49.8893 | 2.5866 | 2.5866 | 50.0332 | -0.49282 | -0.49282
13.7 | 50.0811 | 49.8893 | 2.5866 | 2.5866 | 50.0811 | -1.786 | -1.786
13.75 | 50.0811 | 49.8904 | 2.5568 | 2.5568 | 50.0811 | -1.786 | -1.786
13.8 | 50.0073 | 49.8904 | 2.5568 | 2.5568 | 50.0811 | -1.786 | -1.786
13.85 | 50.0073 | 49.961 | 0.64754 | 0.64754 | 50.0811 | -1.786 | -1.786
13.9 | 49.9371 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
13.95 | 49.9371 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14 | 50.0015 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.05 | 50.0015 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.1 | 49.9424 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.15 | 49.9424 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.2 | 49.9059 | 49.9059 | 2.1375 | 2.1375 | 50.0811 | -1.786 | -1.786
14.25 | 49.9059 | 49.9059 | 2.1375 | 2.1375 | 50.0811 | -1.786 | -1.786
14.3 | 49.9243 | 49.9059 | 2.1375 | 2.1375 | 50.0811 | -1.786 | -1.786
14.35 | 49.9243 | 49.9059 | 2.1375 | 2.1375 | 50.0073 | 0 | 0
14.4 | 49.8455 | 49.8455 | 3.7713 | 3.7713 | 50.0073 | 0 | 0
14.45 | 49.8455 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.5 | 49.9226 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.55 | 49.9226 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.6 | 49.952 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.65 | 49.952 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.7 | 49.9056 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.75 | 49.9056 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.8 | 49.8684 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.85 | 49.8684 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.9 | 49.8048 | 49.8048 | 4.8693 | 4.8693 | 49.952 | 0.89133 | 0.89133
14.95 | 49.8048 | 49.8048 | 4.8693 | 4.8693 | 49.952 | 0.89133 | 0.89133
15 | 49.7445 | 49.7445 | 22.5766 | 22.5766 | 49.952 | 0.89133 | 0.89133
15.05 | 49.7445 | 49.7445 | 22.5766 | 22.5766 | 49.952 | 0.89133 | 0.89133
15.1 | 49.7421 | 49.7421 | 23.33 | 23.33 | 49.952 | 0.89133 | 0.89133
15.15 | 49.7421 | 49.7421 | 23.33 | 23.33 | 49.952 | 0.89133 | 0.89133
15.2 | 49.7203 | 49.7203 | 30.2541 | 30.2541 | 49.952 | 0.89133 | 0.89133
15.25 | 49.7203 | 49.7203 | 30.2541 | 30.2541 | 49.9056 | 2.1457 | 2.1457
15.3 | 49.6661 | 49.6661 | 47.4041 | 47.4041 | 49.9056 | 2.1457 | 2.1457
15.35 | 49.6661 | 49.6661 | 47.4041 | 47.4041 | 49.8684 | 3.1514 | 3.1514
15.4 | 49.654 | 49.654 | 51.2385 | 51.2385 | 49.8684 | 3.1514 | 3.1514
15.45 | 49.654 | 49.654 | 51.2385 | 51.2385 | 49.8048 | 4.8693 | 4.8693
15.5 | 49.5869 | 49.5869 | 72.4917 | 72.4917 | 49.8048 | 4.8693 | 4.8693
15.55 | 49.5869 | 49.5869 | 72.4917 | 72.4917 | 49.7445 | 22.5766 | 14.8693
15.6 | 49.6612 | 49.5869 | 72.4917 | 72.4917 | 49.7445 | 22.5766 | 22.5766
15.65 | 49.6612 | 49.5869 | 72.4917 | 72.4917 | 49.7421 | 23.33 | 23.33
15.7 | 49.6331 | 49.5869 | 72.4917 | 72.4917 | 49.7421 | 23.33 | 23.33
15.75 | 49.6331 | 49.5869 | 72.4917 | 72.4917 | 49.7203 | 30.2541 | 30.2541
15.8 | 49.6061 | 49.5869 | 72.4917 | 72.4917 | 49.7203 | 30.2541 | 30.2541
15.85 | 49.6061 | 49.5869 | 72.4917 | 72.4917 | 49.6661 | 47.4041 | 40.2541
15.9 | 49.537 | 49.537 | 88.2919 | 88.2919 | 49.6661 | 47.4041 | 47.4041
15.95 | 49.537 | 49.537 | 88.2919 | 88.2919 | 49.6612 | 48.96 | 48.96
16 | 49.4617 | 49.4617 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.05 | 49.4617 | 49.4617 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.1 | 49.4484 | 49.4484 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.15 | 49.4484 | 49.4484 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.2 | 49.5083 | 49.4484 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.25 | 49.5083 | 49.4484 | 100 | 100 | 49.6331 | 57.8548 | 57.8548
16.3 | 49.5031 | 49.4484 | 100 | 100 | 49.6331 | 57.8548 | 57.8548
16.35 | 49.5031 | 49.4484 | 100 | 100 | 49.6061 | 66.3965 | 66.3965
16.4 | 49.541 | 49.4484 | 100 | 100 | 49.6061 | 66.3965 | 66.3965
16.45 | 49.541 | 49.4484 | 100 | 100 | 49.541 | 87.0059 | 76.3965
16.5 | 49.5937 | 49.4484 | 100 | 100 | 49.5937 | 70.3342 | 70.3342
16.55 | 49.5937 | 49.4484 | 100 | 100 | 49.5937 | 70.3342 | 70.3342
16.6 | 49.6119 | 49.4484 | 100 | 100 | 49.6119 | 64.5675 | 64.5675
16.65 | 49.6119 | 49.4484 | 100 | 100 | 49.6119 | 64.5675 | 64.5675
16.7 | 49.6111 | 49.4484 | 100 | 100 | 49.6119 | 64.5675 | 64.5675
16.75 | 49.6111 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.8 | 49.5319 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.85 | 49.5319 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.9 | 49.5385 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.95 | 49.5385 | 49.5319 | 89.8862 | 89.8862 | 49.6119 | 64.5675 | 64.5675
17 | 49.6061 | 49.5319 | 89.8862 | 89.8862 | 49.6119 | 64.5675 | 64.5675
17.05 | 49.6061 | 49.5319 | 89.8862 | 89.8862 | 49.6119 | 64.5675 | 64.5675
17.1 | 49.6607 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.15 | 49.6607 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.2 | 49.6362 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.25 | 49.6362 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.3 | 49.6911 | 49.5319 | 89.8862 | 89.8862 | 49.6911 | 39.4871 | 39.4871
17.35 | 49.6911 | 49.5319 | 89.8862 | 89.8862 | 49.6911 | 39.4871 | 39.4871
17.4 | 49.7359 | 49.5319 | 89.8862 | 89.8862 | 49.7359 | 25.3062 | 25.3062
17.45 | 49.7359 | 49.5385 | 87.8018 | 87.8018 | 49.7359 | 25.3062 | 25.3062
17.5 | 49.7763 | 49.5385 | 87.8018 | 87.8018 | 49.7763 | 12.4932 | 12.4932
17.55 | 49.7763 | 49.6061 | 66.3952 | 77.8018 | 49.7763 | 12.4932 | 12.4932
17.6 | 49.8177 | 49.6061 | 66.3952 | 67.8018 | 49.8177 | 4.521 | 4.521
17.65 | 49.8177 | 49.6362 | 56.8636 | 57.8018 | 49.8177 | 4.521 | 4.521
17.7 | 49.8641 | 49.6362 | 56.8636 | 56.8636 | 49.8641 | 3.2673 | 3.2673
17.75 | 49.8641 | 49.6362 | 56.8636 | 56.8636 | 49.8641 | 3.2673 | 3.2673
17.8 | 49.842 | 49.6362 | 56.8636 | 56.8636 | 49.8641 | 3.2673 | 3.2673
17.85 | 49.842 | 49.6911 | 39.4871 | 46.8636 | 49.8641 | 3.2673 | 3.2673
17.9 | 49.9051 | 49.6911 | 39.4871 | 39.4871 | 49.9051 | 2.1599 | 2.1599
17.95 | 49.9051 | 49.7359 | 25.3062 | 29.4871 | 49.9051 | 2.1599 | 2.1599
18 | 49.9664 | 49.7359 | 25.3062 | 25.3062 | 49.9664 | 0.50386 | 0.50386
18.05 | 49.9664 | 49.7763 | 12.4932 | 15.3062 | 49.9664 | 0.50386 | 0.50386
18.1 | 50.0333 | 49.7763 | 12.4932 | 12.4932 | 50.0333 | -0.49328 | -0.49328
18.15 | 50.0333 | 49.8177 | 4.521 | 4.521 | 50.0333 | -0.49328 | -0.49328
18.2 | 50.0527 | 49.8177 | 4.521 | 4.521 | 50.0527 | -1.0181 | -1.0181
18.25 | 50.0527 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.3 | 50.0131 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.35 | 50.0131 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.4 | 49.9457 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.45 | 49.9457 | 49.9051 | 2.1599 | 2.1599 | 50.0527 | -1.0181 | -1.0181
18.5 | 49.9917 | 49.9051 | 2.1599 | 2.1599 | 50.0527 | -1.0181 | -1.0181
18.55 | 49.9917 | 49.9457 | 1.0628 | 1.0628 | 50.0527 | -1.0181 | -1.0181
18.6 | 49.9156 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.65 | 49.9156 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.7 | 49.9748 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.75 | 49.9748 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.8 | 50.0216 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.85 | 50.0216 | 49.9156 | 1.8761 | 1.8761 | 50.0216 | -0.17836 | -0.17836
18.9 | 50.068 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
18.95 | 50.068 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
19 | 50.0569 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
19.05 | 50.0569 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
19.1 | 50.1299 | 49.9156 | 1.8761 | 1.8761 | 50.1299 | -3.1067 | -3.1067
19.15 | 50.1299 | 49.9156 | 1.8761 | 1.8761 | 50.1299 | -3.1067 | -3.1067
19.2 | 50.0921 | 49.9156 | 1.8761 | 1.8761 | 50.1299 | -3.1067 | -3.1067
19.25 | 50.0921 | 49.9748 | 0.27618 | 0.27618 | 50.1299 | -3.1067 | -3.1067
19.3 | 50.0733 | 49.9748 | 0.27618 | 0.27618 | 50.1299 | -3.1067 | -3.1067
19.35 | 50.0733 | 50.0216 | -0.17836 | -0.17836 | 50.1299 | -3.1067 | -3.1067
19.4 | 50.0669 | 50.0216 | -0.17836 | -0.17836 | 50.1299 | -3.1067 | -3.1067
19.45 | 50.0669 | 50.0569 | -1.1333 | -1.1333 | 50.1299 | -3.1067 | -3.1067
19.5 | 50.0475 | 50.0475 | -0.87881 | -0.87881 | 50.1299 | -3.1067 | -3.1067
19.55 | 50.0475 | 50.0475 | -0.87881 | -0.87881 | 50.1299 | -3.1067 | -3.1067
19.6 | 50.0071 | 50.0071 | 0 | 0 | 50.1299 | -3.1067 | -3.1067
19.65 | 50.0071 | 50.0071 | 0 | 0 | 50.1299 | -3.1067 | -3.1067
19.7 | 50.0715 | 50.0071 | 0 | 0 | 50.1299 | -3.1067 | -3.1067
19.75 | 50.0715 | 50.0071 | 0 | 0 | 50.0921 | -2.084 | -2.084
19.8 | 50.0464 | 50.0071 | 0 | 0 | 50.0921 | -2.084 | -2.084
19.85 | 50.0464 | 50.0071 | 0 | 0 | 50.0733 | -1.5761 | -1.5761
19.9 | 50.1034 | 50.0071 | 0 | 0 | 50.1034 | -2.3896 | -2.3896
19.95 | 50.1034 | 50.0071 | 0 | 0 | 50.1034 | -2.3896 | -2.3896
20 | 50.1089 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.05 | 50.1089 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.1 | 50.0635 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.15 | 50.0635 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.2 | 50.0369 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.25 | 50.0369 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.3 | 50.0668 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.35 | 50.0668 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.4 | 50.0703 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.45 | 50.0703 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.5 | 50.1113 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.55 | 50.1113 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.6 | 50.0867 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.65 | 50.0867 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.7 | 50.09 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.75 | 50.09 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.8 | 50.0213 | 50.0213 | -0.17151 | -0.17151 | 50.1113 | -2.6033 | -2.6033
20.85 | 50.0213 | 50.0213 | -0.17151 | -0.17151 | 50.1113 | -2.6033 | -2.6033
20.9 | 50.0041 | 50.0041 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
20.95 | 50.0041 | 50.0041 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21 | 50.002 | 50.002 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21.05 | 50.002 | 50.002 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21.1 | 50.0087 | 50.002 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21.15 | 50.0087 | 50.002 | 0 | 0 | 50.09 | -2.0273 | -2.0273
21.2 | 49.9728 | 49.9728 | 0.32956 | 0.32956 | 50.09 | -2.0273 | -2.0273
21.25 | 49.9728 | 49.9728 | 0.32956 | 0.32956 | 50.09 | -2.0273 | -2.0273
21.3 | 49.9723 | 49.9723 | 0.34197 | 0.34197 | 50.09 | -2.0273 | -2.0273
21.35 | 49.9723 | 49.9723 | 0.34197 | 0.34197 | 50.0213 | -0.17151 | -0.17151
21.4 | 49.93 | 49.93 | 1.4855 | 1.4855 | 50.0213 | -0.17151 | -0.17151
21.45 | 49.93 | 49.93 | 1.4855 | 1.4855 | 50.0087 | 0 | 0
21.5 | 50.0068 | 49.93 | 1.4855 | 1.4855 | 50.0087 | 0 | 0
21.55 | 50.0068 | 49.93 | 1.4855 | 1.4855 | 50.0087 | 0 | 0

## Using Excel formulae
t | f | lfw | unr | ub | ufw | lnr | lb | f | r
0 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 49.5 | 100 | DC | 100
0.05 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 49.8 | 5
0.1 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 49.985 | 0 | ramp | 10 | P*t*rrmin
0.15 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 50.015 | 0
0.2 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 50.2 | -5 | LF only | FALSE
0.25 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 50.5 | -100
0.3 | 50 | 50 | 0 | 0 | 50 | 0 | 0
0.35 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | The formulas in the unr and lnr columns are interpolating between the elbows in the response curve
0.4 | 50 | 50 | 0 | 0 | 50 | 0 | 0
0.45 | 50 | 50 | 0 | 0 | 50 | 0 | 0
0.5 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.55 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.6 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.65 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.7 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.75 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.8 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.85 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.9 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
0.95 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
1 | 49.5 | 49.5 | 100 | 100 | 50 | 0 | 0
1.05 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 10
1.1 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 20
1.15 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 30
1.2 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 40
1.25 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 50
1.3 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 60
1.35 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 70
1.4 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 80
1.45 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 90
1.5 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.55 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.6 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.65 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.7 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.75 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.8 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.85 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.9 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
1.95 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.05 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.1 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.15 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.2 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.25 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.3 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.35 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.4 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.45 | 49.5 | 49.5 | 100 | 100 | 49.5 | 100 | 100
2.5 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.55 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.6 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.65 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.7 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.75 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.8 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.85 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.9 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
2.95 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
3 | 50.5 | 49.5 | 100 | 100 | 50.5 | -100 | -100
3.05 | 50.5 | 50.5 | -100 | 90 | 50.5 | -100 | -100
3.1 | 50.5 | 50.5 | -100 | 80 | 50.5 | -100 | -100
3.15 | 50.5 | 50.5 | -100 | 70 | 50.5 | -100 | -100
3.2 | 50.5 | 50.5 | -100 | 60 | 50.5 | -100 | -100
3.25 | 50.5 | 50.5 | -100 | 50 | 50.5 | -100 | -100
3.3 | 50.5 | 50.5 | -100 | 40 | 50.5 | -100 | -100
3.35 | 50.5 | 50.5 | -100 | 30 | 50.5 | -100 | -100
3.4 | 50.5 | 50.5 | -100 | 20 | 50.5 | -100 | -100
3.45 | 50.5 | 50.5 | -100 | 10 | 50.5 | -100 | -100
3.5 | 50.5 | 50.5 | -100 | 0 | 50.5 | -100 | -100
3.55 | 50.5 | 50.5 | -100 | -10 | 50.5 | -100 | -100
3.6 | 50.5 | 50.5 | -100 | -20 | 50.5 | -100 | -100
3.65 | 50.5 | 50.5 | -100 | -30 | 50.5 | -100 | -100
3.7 | 50.5 | 50.5 | -100 | -40 | 50.5 | -100 | -100
3.75 | 50.5 | 50.5 | -100 | -50 | 50.5 | -100 | -100
3.8 | 50.5 | 50.5 | -100 | -60 | 50.5 | -100 | -100
3.85 | 50.5 | 50.5 | -100 | -70 | 50.5 | -100 | -100
3.9 | 50.5 | 50.5 | -100 | -80 | 50.5 | -100 | -100
3.95 | 50.5 | 50.5 | -100 | -90 | 50.5 | -100 | -100
4 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.05 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.1 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.15 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.2 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.25 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.3 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.35 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.4 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.45 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.5 | 50.5 | 50.5 | -100 | -100 | 50.5 | -100 | -100
4.55 | 50.4744 | 50.4744 | -91.8803 | -91.8803 | 50.5 | -100 | -100
4.6 | 50.4487 | 50.4487 | -83.7607 | -83.7607 | 50.5 | -100 | -100
4.65 | 50.4231 | 50.4231 | -75.641 | -75.641 | 50.5 | -100 | -100
4.7 | 50.3974 | 50.3974 | -67.5214 | -67.5214 | 50.5 | -100 | -100
4.75 | 50.3718 | 50.3718 | -59.4017 | -59.4017 | 50.5 | -100 | -100
4.8 | 50.3462 | 50.3462 | -51.2821 | -51.2821 | 50.5 | -100 | -100
4.85 | 50.3205 | 50.3205 | -43.1624 | -43.1624 | 50.5 | -100 | -100
4.9 | 50.2949 | 50.2949 | -35.0427 | -35.0427 | 50.5 | -100 | -100
4.95 | 50.2692 | 50.2692 | -26.9231 | -26.9231 | 50.5 | -100 | -100
5 | 50.2436 | 50.2436 | -18.8034 | -18.8034 | 50.5 | -100 | -100
5.05 | 50.2179 | 50.2179 | -10.6838 | -10.6838 | 50.5 | -100 | -100
5.1 | 50.1923 | 50.1923 | -4.7921 | -4.7921 | 50.4744 | -91.8803 | -91.8803
5.15 | 50.1667 | 50.1667 | -4.0991 | -4.0991 | 50.4487 | -83.7607 | -83.7607
5.2 | 50.141 | 50.141 | -3.4061 | -3.4061 | 50.4231 | -75.641 | -75.641
5.25 | 50.1154 | 50.1154 | -2.7131 | -2.7131 | 50.3974 | -67.5214 | -67.5214
5.3 | 50.0897 | 50.0897 | -2.0201 | -2.0201 | 50.3718 | -59.4017 | -59.4017
5.35 | 50.0641 | 50.0641 | -1.3271 | -1.3271 | 50.3462 | -51.2821 | -51.2821
5.4 | 50.0385 | 50.0385 | -0.6341 | -0.6341 | 50.3205 | -43.1624 | -43.1624
5.45 | 50.0128 | 50.0128 | 0 | 0 | 50.2949 | -35.0427 | -35.0427
5.5 | 49.9872 | 49.9872 | 0 | 0 | 50.2692 | -26.9231 | -26.9231
5.55 | 49.9615 | 49.9615 | 0.6341 | 0.6341 | 50.2436 | -18.8034 | -18.8034
5.6 | 49.9359 | 49.9359 | 1.3271 | 1.3271 | 50.2179 | -10.6838 | -10.6838
5.65 | 49.9103 | 49.9103 | 2.0201 | 2.0201 | 50.1923 | -4.7921 | -4.7921
5.7 | 49.8846 | 49.8846 | 2.7131 | 2.7131 | 50.1667 | -4.0991 | -4.0991
5.75 | 49.859 | 49.859 | 3.4061 | 3.4061 | 50.141 | -3.4061 | -3.4061
5.8 | 49.8333 | 49.8333 | 4.0991 | 4.0991 | 50.1154 | -2.7131 | -2.7131
5.85 | 49.8077 | 49.8077 | 4.7921 | 4.7921 | 50.0897 | -2.0201 | -2.0201
5.9 | 49.7821 | 49.7821 | 10.6838 | 10.6838 | 50.0641 | -1.3271 | -1.3271
5.95 | 49.7564 | 49.7564 | 18.8034 | 18.8034 | 50.0385 | -0.6341 | -0.6341
6 | 49.7308 | 49.7308 | 26.9231 | 26.9231 | 50.0128 | 0 | 0
6.05 | 49.7051 | 49.7051 | 35.0427 | 35.0427 | 49.9872 | 0 | 0
6.1 | 49.6795 | 49.6795 | 43.1624 | 43.1624 | 49.9615 | 0.6341 | 0.6341
6.15 | 49.6538 | 49.6538 | 51.2821 | 51.2821 | 49.9359 | 1.3271 | 1.3271
6.2 | 49.6282 | 49.6282 | 59.4017 | 59.4017 | 49.9103 | 2.0201 | 2.0201
6.25 | 49.6026 | 49.6026 | 67.5214 | 67.5214 | 49.8846 | 2.7131 | 2.7131
6.3 | 49.5769 | 49.5769 | 75.641 | 75.641 | 49.859 | 3.4061 | 3.4061
6.35 | 49.5513 | 49.5513 | 83.7607 | 83.7607 | 49.8333 | 4.0991 | 4.0991
6.4 | 49.5256 | 49.5256 | 91.8803 | 91.8803 | 49.8077 | 4.7921 | 4.7921
6.45 | 49.5 | 49.5 | 100 | 100 | 49.7821 | 10.6838 | 10.6838
6.5 | 49.5 | 49.5 | 100 | 100 | 49.7564 | 18.8034 | 18.8034
6.55 | 49.5256 | 49.5 | 100 | 100 | 49.7308 | 26.9231 | 26.9231
6.6 | 49.5513 | 49.5 | 100 | 100 | 49.7051 | 35.0427 | 35.0427
6.65 | 49.5769 | 49.5 | 100 | 100 | 49.6795 | 43.1624 | 43.1624
6.7 | 49.6026 | 49.5 | 100 | 100 | 49.6538 | 51.2821 | 51.2821
6.75 | 49.6282 | 49.5 | 100 | 100 | 49.6282 | 59.4017 | 59.4017
6.8 | 49.6538 | 49.5 | 100 | 100 | 49.6538 | 51.2821 | 51.2821
6.85 | 49.6795 | 49.5 | 100 | 100 | 49.6795 | 43.1624 | 43.1624
6.9 | 49.7051 | 49.5 | 100 | 100 | 49.7051 | 35.0427 | 35.0427
6.95 | 49.7308 | 49.5 | 100 | 100 | 49.7308 | 26.9231 | 26.9231
7 | 49.7564 | 49.5 | 100 | 100 | 49.7564 | 18.8034 | 18.8034
7.05 | 49.7821 | 49.5 | 100 | 100 | 49.7821 | 10.6838 | 10.6838
7.1 | 49.8077 | 49.5256 | 91.8803 | 91.8803 | 49.8077 | 4.7921 | 4.7921
7.15 | 49.8333 | 49.5513 | 83.7607 | 83.7607 | 49.8333 | 4.0991 | 4.0991
7.2 | 49.859 | 49.5769 | 75.641 | 75.641 | 49.859 | 3.4061 | 3.4061
7.25 | 49.8846 | 49.6026 | 67.5214 | 67.5214 | 49.8846 | 2.7131 | 2.7131
7.3 | 49.9103 | 49.6282 | 59.4017 | 59.4017 | 49.9103 | 2.0201 | 2.0201
7.35 | 49.9359 | 49.6538 | 51.2821 | 51.2821 | 49.9359 | 1.3271 | 1.3271
7.4 | 49.9615 | 49.6795 | 43.1624 | 43.1624 | 49.9615 | 0.6341 | 0.6341
7.45 | 49.9872 | 49.7051 | 35.0427 | 35.0427 | 49.9872 | 0 | 0
7.5 | 50.0128 | 49.7308 | 26.9231 | 26.9231 | 50.0128 | 0 | 0
7.55 | 50.0385 | 49.7564 | 18.8034 | 18.8034 | 50.0385 | -0.6341 | -0.6341
7.6 | 50.0641 | 49.7821 | 10.6838 | 10.6838 | 50.0641 | -1.3271 | -1.3271
7.65 | 50.0897 | 49.8077 | 4.7921 | 4.7921 | 50.0897 | -2.0201 | -2.0201
7.7 | 50.1154 | 49.8333 | 4.0991 | 4.0991 | 50.1154 | -2.7131 | -2.7131
7.75 | 50.141 | 49.859 | 3.4061 | 3.4061 | 50.141 | -3.4061 | -3.4061
7.8 | 50.1667 | 49.8846 | 2.7131 | 2.7131 | 50.1667 | -4.0991 | -4.0991
7.85 | 50.1923 | 49.9103 | 2.0201 | 2.0201 | 50.1923 | -4.7921 | -4.7921
7.9 | 50.2179 | 49.9359 | 1.3271 | 1.3271 | 50.2179 | -10.6838 | -10.6838
7.95 | 50.2436 | 49.9615 | 0.6341 | 0.6341 | 50.2436 | -18.8034 | -18.8034
8 | 50.2692 | 49.9872 | 0 | 0 | 50.2692 | -26.9231 | -26.9231
8.05 | 50.2949 | 50.0128 | 0 | 0 | 50.2949 | -35.0427 | -35.0427
8.1 | 50.3205 | 50.0385 | -0.6341 | -0.6341 | 50.3205 | -43.1624 | -43.1624
8.15 | 50.3462 | 50.0641 | -1.3271 | -1.3271 | 50.3462 | -51.2821 | -51.2821
8.2 | 50.3718 | 50.0897 | -2.0201 | -2.0201 | 50.3718 | -59.4017 | -59.4017
8.25 | 50.3974 | 50.1154 | -2.7131 | -2.7131 | 50.3974 | -67.5214 | -67.5214
8.3 | 50.4231 | 50.141 | -3.4061 | -3.4061 | 50.4231 | -75.641 | -75.641
8.35 | 50.4487 | 50.1667 | -4.0991 | -4.0991 | 50.4487 | -83.7607 | -83.7607
8.4 | 50.4744 | 50.1923 | -4.7921 | -4.7921 | 50.4744 | -91.8803 | -91.8803
8.45 | 50.5 | 50.2179 | -10.6838 | -10.6838 | 50.5 | -100 | -100
8.5 | 50.5 | 50.2436 | -18.8034 | -18.8034 | 50.5 | -100 | -100
8.55 | 50.4737 | 50.2692 | -26.9231 | -26.9231 | 50.5 | -100 | -100
8.6 | 50.4474 | 50.2949 | -35.0427 | -35.0427 | 50.5 | -100 | -100
8.65 | 50.4211 | 50.3205 | -43.1624 | -43.1624 | 50.5 | -100 | -100
8.7 | 50.3947 | 50.3462 | -51.2821 | -51.2821 | 50.5 | -100 | -100
8.75 | 50.3684 | 50.3684 | -58.3333 | -58.3333 | 50.5 | -100 | -100
8.8 | 50.3421 | 50.3421 | -50 | -50 | 50.5 | -100 | -100
8.85 | 50.3158 | 50.3158 | -41.6667 | -41.6667 | 50.5 | -100 | -100
8.9 | 50.2895 | 50.2895 | -33.3333 | -33.3333 | 50.5 | -100 | -100
8.95 | 50.2632 | 50.2632 | -25 | -25 | 50.5 | -100 | -100
9 | 50.2368 | 50.2368 | -16.6667 | -16.6667 | 50.5 | -100 | -100
9.05 | 50.2105 | 50.2105 | -8.3333 | -8.3333 | 50.5 | -100 | -100
9.1 | 50.1842 | 50.1842 | -4.5733 | -4.5733 | 50.4737 | -91.6667 | -91.6667
9.15 | 50.1579 | 50.1579 | -3.862 | -3.862 | 50.4474 | -83.3333 | -83.3333
9.2 | 50.1316 | 50.1316 | -3.1508 | -3.1508 | 50.4211 | -75 | -75
9.25 | 50.1053 | 50.1053 | -2.4395 | -2.4395 | 50.3947 | -66.6667 | -66.6667
9.3 | 50.0789 | 50.0789 | -1.7283 | -1.7283 | 50.3684 | -58.3333 | -58.3333
9.35 | 50.0526 | 50.0526 | -1.0171 | -1.0171 | 50.3421 | -50 | -50
9.4 | 50.0263 | 50.0263 | -0.30583 | -0.30583 | 50.3158 | -41.6667 | -41.6667
9.45 | 50 | 50 | 0 | 0 | 50.2895 | -33.3333 | -33.3333
9.5 | 50.0014 | 50 | 0 | 0 | 50.2632 | -25 | -25
9.55 | 50.0014 | 50 | 0 | 0 | 50.2368 | -16.6667 | -16.6667
9.6 | 49.9974 | 49.9974 | 0 | 0 | 50.2105 | -8.3333 | -8.3333
9.65 | 49.9974 | 49.9974 | 0 | 0 | 50.1842 | -4.5733 | -4.5733
9.7 | 49.9992 | 49.9974 | 0 | 0 | 50.1579 | -3.862 | -3.862
9.75 | 49.9992 | 49.9974 | 0 | 0 | 50.1316 | -3.1508 | -3.1508
9.8 | 50.0136 | 49.9974 | 0 | 0 | 50.1053 | -2.4395 | -2.4395
9.85 | 50.0136 | 49.9974 | 0 | 0 | 50.0789 | -1.7283 | -1.7283
9.9 | 49.9891 | 49.9891 | 0 | 0 | 50.0526 | -1.0171 | -1.0171
9.95 | 49.9891 | 49.9891 | 0 | 0 | 50.0263 | -0.30583 | -0.30583
10 | 49.9257 | 49.9257 | 1.6021 | 1.6021 | 50.0136 | 0 | 0
10.05 | 49.9257 | 49.9257 | 1.6021 | 1.6021 | 50.0136 | 0 | 0
10.1 | 49.9123 | 49.9123 | 1.9648 | 1.9648 | 50.0136 | 0 | 0
10.15 | 49.9123 | 49.9123 | 1.9648 | 1.9648 | 50.0136 | 0 | 0
10.2 | 49.8631 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.25 | 49.8631 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.3 | 49.8907 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.35 | 49.8907 | 49.8631 | 3.2941 | 3.2941 | 50.0136 | 0 | 0
10.4 | 49.8527 | 49.8527 | 3.5765 | 3.5765 | 50.0136 | 0 | 0
10.45 | 49.8527 | 49.8527 | 3.5765 | 3.5765 | 49.9891 | 0 | 0
10.5 | 49.853 | 49.8527 | 3.5765 | 3.5765 | 49.9891 | 0 | 0
10.55 | 49.853 | 49.8527 | 3.5765 | 3.5765 | 49.9257 | 1.6021 | 1.6021
10.6 | 49.9075 | 49.8527 | 3.5765 | 3.5765 | 49.9257 | 1.6021 | 1.6021
10.65 | 49.9075 | 49.8527 | 3.5765 | 3.5765 | 49.9123 | 1.9648 | 1.9648
10.7 | 49.9408 | 49.8527 | 3.5765 | 3.5765 | 49.9408 | 1.1955 | 1.1955
10.75 | 49.9408 | 49.8527 | 3.5765 | 3.5765 | 49.9408 | 1.1955 | 1.1955
10.8 | 49.9496 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
10.85 | 49.9496 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
10.9 | 49.9342 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
10.95 | 49.9342 | 49.8527 | 3.5765 | 3.5765 | 49.9496 | 0.95589 | 0.95589
11 | 49.9587 | 49.8527 | 3.5765 | 3.5765 | 49.9587 | 0.71194 | 0.71194
11.05 | 49.9587 | 49.853 | 3.5687 | 3.5687 | 49.9587 | 0.71194 | 0.71194
11.1 | 49.9906 | 49.853 | 3.5687 | 3.5687 | 49.9906 | 0 | 0
11.15 | 49.9906 | 49.9075 | 2.0951 | 2.0951 | 49.9906 | 0 | 0
11.2 | 49.9903 | 49.9075 | 2.0951 | 2.0951 | 49.9906 | 0 | 0
11.25 | 49.9903 | 49.9342 | 1.3741 | 1.3741 | 49.9906 | 0 | 0
11.3 | 49.9556 | 49.9342 | 1.3741 | 1.3741 | 49.9906 | 0 | 0
11.35 | 49.9556 | 49.9342 | 1.3741 | 1.3741 | 49.9906 | 0 | 0
11.4 | 50.0104 | 49.9342 | 1.3741 | 1.3741 | 50.0104 | 0 | 0
11.45 | 50.0104 | 49.9342 | 1.3741 | 1.3741 | 50.0104 | 0 | 0
11.5 | 50.0473 | 49.9342 | 1.3741 | 1.3741 | 50.0473 | -0.87176 | -0.87176
11.55 | 50.0473 | 49.9556 | 0.79433 | 0.79433 | 50.0473 | -0.87176 | -0.87176
11.6 | 49.9746 | 49.9556 | 0.79433 | 0.79433 | 50.0473 | -0.87176 | -0.87176
11.65 | 49.9746 | 49.9556 | 0.79433 | 0.79433 | 50.0473 | -0.87176 | -0.87176
11.7 | 49.9197 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.75 | 49.9197 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.8 | 49.9919 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.85 | 49.9919 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.9 | 49.9387 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
11.95 | 49.9387 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12 | 50.0096 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12.05 | 50.0096 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12.1 | 49.9918 | 49.9197 | 1.7636 | 1.7636 | 50.0473 | -0.87176 | -0.87176
12.15 | 49.9918 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.2 | 49.9519 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.25 | 49.9519 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.3 | 49.9455 | 49.9197 | 1.7636 | 1.7636 | 50.0096 | 0 | 0
12.35 | 49.9455 | 49.9387 | 1.2516 | 1.2516 | 50.0096 | 0 | 0
12.4 | 49.9734 | 49.9387 | 1.2516 | 1.2516 | 50.0096 | 0 | 0
12.45 | 49.9734 | 49.9387 | 1.2516 | 1.2516 | 50.0096 | 0 | 0
12.5 | 49.9374 | 49.9374 | 1.2855 | 1.2855 | 50.0096 | 0 | 0
12.55 | 49.9374 | 49.9374 | 1.2855 | 1.2855 | 50.0096 | 0 | 0
12.6 | 49.8711 | 49.8711 | 3.0776 | 3.0776 | 50.0096 | 0 | 0
12.65 | 49.8711 | 49.8711 | 3.0776 | 3.0776 | 49.9918 | 0 | 0
12.7 | 49.8501 | 49.8501 | 3.6447 | 3.6447 | 49.9918 | 0 | 0
12.75 | 49.8501 | 49.8501 | 3.6447 | 3.6447 | 49.9734 | 0.31294 | 0.31294
12.8 | 49.7875 | 49.7875 | 8.9587 | 8.9587 | 49.9734 | 0.31294 | 0.31294
12.85 | 49.7875 | 49.7875 | 8.9587 | 8.9587 | 49.9734 | 0.31294 | 0.31294
12.9 | 49.7867 | 49.7867 | 9.2116 | 9.2116 | 49.9734 | 0.31294 | 0.31294
12.95 | 49.7867 | 49.7867 | 9.2116 | 9.2116 | 49.9734 | 0.31294 | 0.31294
13 | 49.8434 | 49.7867 | 9.2116 | 9.2116 | 49.9734 | 0.31294 | 0.31294
13.05 | 49.8434 | 49.7867 | 9.2116 | 9.2116 | 49.9374 | 1.2855 | 1.2855
13.1 | 49.8893 | 49.7867 | 9.2116 | 9.2116 | 49.9374 | 1.2855 | 1.2855
13.15 | 49.8893 | 49.7867 | 9.2116 | 9.2116 | 49.8893 | 2.5866 | 2.5866
13.2 | 49.8904 | 49.7867 | 9.2116 | 9.2116 | 49.8904 | 2.5568 | 2.5568
13.25 | 49.8904 | 49.7867 | 9.2116 | 9.2116 | 49.8904 | 2.5568 | 2.5568
13.3 | 49.961 | 49.7867 | 9.2116 | 9.2116 | 49.961 | 0.64754 | 0.64754
13.35 | 49.961 | 49.7867 | 9.2116 | 9.2116 | 49.961 | 0.64754 | 0.64754
13.4 | 50.0228 | 49.7867 | 9.2116 | 9.2116 | 50.0228 | -0.21089 | -0.21089
13.45 | 50.0228 | 49.7867 | 9.2116 | 9.2116 | 50.0228 | -0.21089 | -0.21089
13.5 | 50.0332 | 49.7867 | 9.2116 | 9.2116 | 50.0332 | -0.49282 | -0.49282
13.55 | 50.0332 | 49.8434 | 3.8268 | 3.8268 | 50.0332 | -0.49282 | -0.49282
13.6 | 50.0179 | 49.8434 | 3.8268 | 3.8268 | 50.0332 | -0.49282 | -0.49282
13.65 | 50.0179 | 49.8893 | 2.5866 | 2.5866 | 50.0332 | -0.49282 | -0.49282
13.7 | 50.0811 | 49.8893 | 2.5866 | 2.5866 | 50.0811 | -1.786 | -1.786
13.75 | 50.0811 | 49.8904 | 2.5568 | 2.5568 | 50.0811 | -1.786 | -1.786
13.8 | 50.0073 | 49.8904 | 2.5568 | 2.5568 | 50.0811 | -1.786 | -1.786
13.85 | 50.0073 | 49.961 | 0.64754 | 0.64754 | 50.0811 | -1.786 | -1.786
13.9 | 49.9371 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
13.95 | 49.9371 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14 | 50.0015 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.05 | 50.0015 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.1 | 49.9424 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.15 | 49.9424 | 49.9371 | 1.2953 | 1.2953 | 50.0811 | -1.786 | -1.786
14.2 | 49.9059 | 49.9059 | 2.1375 | 2.1375 | 50.0811 | -1.786 | -1.786
14.25 | 49.9059 | 49.9059 | 2.1375 | 2.1375 | 50.0811 | -1.786 | -1.786
14.3 | 49.9243 | 49.9059 | 2.1375 | 2.1375 | 50.0811 | -1.786 | -1.786
14.35 | 49.9243 | 49.9059 | 2.1375 | 2.1375 | 50.0073 | 0 | 0
14.4 | 49.8455 | 49.8455 | 3.7713 | 3.7713 | 50.0073 | 0 | 0
14.45 | 49.8455 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.5 | 49.9226 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.55 | 49.9226 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.6 | 49.952 | 49.8455 | 3.7713 | 3.7713 | 50.0015 | 0 | 0
14.65 | 49.952 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.7 | 49.9056 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.75 | 49.9056 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.8 | 49.8684 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.85 | 49.8684 | 49.8455 | 3.7713 | 3.7713 | 49.952 | 0.89133 | 0.89133
14.9 | 49.8048 | 49.8048 | 4.8693 | 4.8693 | 49.952 | 0.89133 | 0.89133
14.95 | 49.8048 | 49.8048 | 4.8693 | 4.8693 | 49.952 | 0.89133 | 0.89133
15 | 49.7445 | 49.7445 | 22.5766 | 22.5766 | 49.952 | 0.89133 | 0.89133
15.05 | 49.7445 | 49.7445 | 22.5766 | 22.5766 | 49.952 | 0.89133 | 0.89133
15.1 | 49.7421 | 49.7421 | 23.33 | 23.33 | 49.952 | 0.89133 | 0.89133
15.15 | 49.7421 | 49.7421 | 23.33 | 23.33 | 49.952 | 0.89133 | 0.89133
15.2 | 49.7203 | 49.7203 | 30.2541 | 30.2541 | 49.952 | 0.89133 | 0.89133
15.25 | 49.7203 | 49.7203 | 30.2541 | 30.2541 | 49.9056 | 2.1457 | 2.1457
15.3 | 49.6661 | 49.6661 | 47.4041 | 47.4041 | 49.9056 | 2.1457 | 2.1457
15.35 | 49.6661 | 49.6661 | 47.4041 | 47.4041 | 49.8684 | 3.1514 | 3.1514
15.4 | 49.654 | 49.654 | 51.2385 | 51.2385 | 49.8684 | 3.1514 | 3.1514
15.45 | 49.654 | 49.654 | 51.2385 | 51.2385 | 49.8048 | 4.8693 | 4.8693
15.5 | 49.5869 | 49.5869 | 72.4917 | 72.4917 | 49.8048 | 4.8693 | 4.8693
15.55 | 49.5869 | 49.5869 | 72.4917 | 72.4917 | 49.7445 | 22.5766 | 14.8693
15.6 | 49.6612 | 49.5869 | 72.4917 | 72.4917 | 49.7445 | 22.5766 | 22.5766
15.65 | 49.6612 | 49.5869 | 72.4917 | 72.4917 | 49.7421 | 23.33 | 23.33
15.7 | 49.6331 | 49.5869 | 72.4917 | 72.4917 | 49.7421 | 23.33 | 23.33
15.75 | 49.6331 | 49.5869 | 72.4917 | 72.4917 | 49.7203 | 30.2541 | 30.2541
15.8 | 49.6061 | 49.5869 | 72.4917 | 72.4917 | 49.7203 | 30.2541 | 30.2541
15.85 | 49.6061 | 49.5869 | 72.4917 | 72.4917 | 49.6661 | 47.4041 | 40.2541
15.9 | 49.537 | 49.537 | 88.2919 | 88.2919 | 49.6661 | 47.4041 | 47.4041
15.95 | 49.537 | 49.537 | 88.2919 | 88.2919 | 49.6612 | 48.96 | 48.96
16 | 49.4617 | 49.4617 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.05 | 49.4617 | 49.4617 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.1 | 49.4484 | 49.4484 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.15 | 49.4484 | 49.4484 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.2 | 49.5083 | 49.4484 | 100 | 100 | 49.6612 | 48.96 | 48.96
16.25 | 49.5083 | 49.4484 | 100 | 100 | 49.6331 | 57.8548 | 57.8548
16.3 | 49.5031 | 49.4484 | 100 | 100 | 49.6331 | 57.8548 | 57.8548
16.35 | 49.5031 | 49.4484 | 100 | 100 | 49.6061 | 66.3965 | 66.3965
16.4 | 49.541 | 49.4484 | 100 | 100 | 49.6061 | 66.3965 | 66.3965
16.45 | 49.541 | 49.4484 | 100 | 100 | 49.541 | 87.0059 | 76.3965
16.5 | 49.5937 | 49.4484 | 100 | 100 | 49.5937 | 70.3342 | 70.3342
16.55 | 49.5937 | 49.4484 | 100 | 100 | 49.5937 | 70.3342 | 70.3342
16.6 | 49.6119 | 49.4484 | 100 | 100 | 49.6119 | 64.5675 | 64.5675
16.65 | 49.6119 | 49.4484 | 100 | 100 | 49.6119 | 64.5675 | 64.5675
16.7 | 49.6111 | 49.4484 | 100 | 100 | 49.6119 | 64.5675 | 64.5675
16.75 | 49.6111 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.8 | 49.5319 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.85 | 49.5319 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.9 | 49.5385 | 49.5031 | 99.0242 | 99.0242 | 49.6119 | 64.5675 | 64.5675
16.95 | 49.5385 | 49.5319 | 89.8862 | 89.8862 | 49.6119 | 64.5675 | 64.5675
17 | 49.6061 | 49.5319 | 89.8862 | 89.8862 | 49.6119 | 64.5675 | 64.5675
17.05 | 49.6061 | 49.5319 | 89.8862 | 89.8862 | 49.6119 | 64.5675 | 64.5675
17.1 | 49.6607 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.15 | 49.6607 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.2 | 49.6362 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.25 | 49.6362 | 49.5319 | 89.8862 | 89.8862 | 49.6607 | 49.1216 | 49.1216
17.3 | 49.6911 | 49.5319 | 89.8862 | 89.8862 | 49.6911 | 39.4871 | 39.4871
17.35 | 49.6911 | 49.5319 | 89.8862 | 89.8862 | 49.6911 | 39.4871 | 39.4871
17.4 | 49.7359 | 49.5319 | 89.8862 | 89.8862 | 49.7359 | 25.3062 | 25.3062
17.45 | 49.7359 | 49.5385 | 87.8018 | 87.8018 | 49.7359 | 25.3062 | 25.3062
17.5 | 49.7763 | 49.5385 | 87.8018 | 87.8018 | 49.7763 | 12.4932 | 12.4932
17.55 | 49.7763 | 49.6061 | 66.3952 | 77.8018 | 49.7763 | 12.4932 | 12.4932
17.6 | 49.8177 | 49.6061 | 66.3952 | 67.8018 | 49.8177 | 4.521 | 4.521
17.65 | 49.8177 | 49.6362 | 56.8636 | 57.8018 | 49.8177 | 4.521 | 4.521
17.7 | 49.8641 | 49.6362 | 56.8636 | 56.8636 | 49.8641 | 3.2673 | 3.2673
17.75 | 49.8641 | 49.6362 | 56.8636 | 56.8636 | 49.8641 | 3.2673 | 3.2673
17.8 | 49.842 | 49.6362 | 56.8636 | 56.8636 | 49.8641 | 3.2673 | 3.2673
17.85 | 49.842 | 49.6911 | 39.4871 | 46.8636 | 49.8641 | 3.2673 | 3.2673
17.9 | 49.9051 | 49.6911 | 39.4871 | 39.4871 | 49.9051 | 2.1599 | 2.1599
17.95 | 49.9051 | 49.7359 | 25.3062 | 29.4871 | 49.9051 | 2.1599 | 2.1599
18 | 49.9664 | 49.7359 | 25.3062 | 25.3062 | 49.9664 | 0.50386 | 0.50386
18.05 | 49.9664 | 49.7763 | 12.4932 | 15.3062 | 49.9664 | 0.50386 | 0.50386
18.1 | 50.0333 | 49.7763 | 12.4932 | 12.4932 | 50.0333 | -0.49328 | -0.49328
18.15 | 50.0333 | 49.8177 | 4.521 | 4.521 | 50.0333 | -0.49328 | -0.49328
18.2 | 50.0527 | 49.8177 | 4.521 | 4.521 | 50.0527 | -1.0181 | -1.0181
18.25 | 50.0527 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.3 | 50.0131 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.35 | 50.0131 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.4 | 49.9457 | 49.842 | 3.8648 | 3.8648 | 50.0527 | -1.0181 | -1.0181
18.45 | 49.9457 | 49.9051 | 2.1599 | 2.1599 | 50.0527 | -1.0181 | -1.0181
18.5 | 49.9917 | 49.9051 | 2.1599 | 2.1599 | 50.0527 | -1.0181 | -1.0181
18.55 | 49.9917 | 49.9457 | 1.0628 | 1.0628 | 50.0527 | -1.0181 | -1.0181
18.6 | 49.9156 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.65 | 49.9156 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.7 | 49.9748 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.75 | 49.9748 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.8 | 50.0216 | 49.9156 | 1.8761 | 1.8761 | 50.0527 | -1.0181 | -1.0181
18.85 | 50.0216 | 49.9156 | 1.8761 | 1.8761 | 50.0216 | -0.17836 | -0.17836
18.9 | 50.068 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
18.95 | 50.068 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
19 | 50.0569 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
19.05 | 50.0569 | 49.9156 | 1.8761 | 1.8761 | 50.068 | -1.4313 | -1.4313
19.1 | 50.1299 | 49.9156 | 1.8761 | 1.8761 | 50.1299 | -3.1067 | -3.1067
19.15 | 50.1299 | 49.9156 | 1.8761 | 1.8761 | 50.1299 | -3.1067 | -3.1067
19.2 | 50.0921 | 49.9156 | 1.8761 | 1.8761 | 50.1299 | -3.1067 | -3.1067
19.25 | 50.0921 | 49.9748 | 0.27618 | 0.27618 | 50.1299 | -3.1067 | -3.1067
19.3 | 50.0733 | 49.9748 | 0.27618 | 0.27618 | 50.1299 | -3.1067 | -3.1067
19.35 | 50.0733 | 50.0216 | -0.17836 | -0.17836 | 50.1299 | -3.1067 | -3.1067
19.4 | 50.0669 | 50.0216 | -0.17836 | -0.17836 | 50.1299 | -3.1067 | -3.1067
19.45 | 50.0669 | 50.0569 | -1.1333 | -1.1333 | 50.1299 | -3.1067 | -3.1067
19.5 | 50.0475 | 50.0475 | -0.87881 | -0.87881 | 50.1299 | -3.1067 | -3.1067
19.55 | 50.0475 | 50.0475 | -0.87881 | -0.87881 | 50.1299 | -3.1067 | -3.1067
19.6 | 50.0071 | 50.0071 | 0 | 0 | 50.1299 | -3.1067 | -3.1067
19.65 | 50.0071 | 50.0071 | 0 | 0 | 50.1299 | -3.1067 | -3.1067
19.7 | 50.0715 | 50.0071 | 0 | 0 | 50.1299 | -3.1067 | -3.1067
19.75 | 50.0715 | 50.0071 | 0 | 0 | 50.0921 | -2.084 | -2.084
19.8 | 50.0464 | 50.0071 | 0 | 0 | 50.0921 | -2.084 | -2.084
19.85 | 50.0464 | 50.0071 | 0 | 0 | 50.0733 | -1.5761 | -1.5761
19.9 | 50.1034 | 50.0071 | 0 | 0 | 50.1034 | -2.3896 | -2.3896
19.95 | 50.1034 | 50.0071 | 0 | 0 | 50.1034 | -2.3896 | -2.3896
20 | 50.1089 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.05 | 50.1089 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.1 | 50.0635 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.15 | 50.0635 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.2 | 50.0369 | 50.0071 | 0 | 0 | 50.1089 | -2.5376 | -2.5376
20.25 | 50.0369 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.3 | 50.0668 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.35 | 50.0668 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.4 | 50.0703 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.45 | 50.0703 | 50.0369 | -0.59319 | -0.59319 | 50.1089 | -2.5376 | -2.5376
20.5 | 50.1113 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.55 | 50.1113 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.6 | 50.0867 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.65 | 50.0867 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.7 | 50.09 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.75 | 50.09 | 50.0369 | -0.59319 | -0.59319 | 50.1113 | -2.6033 | -2.6033
20.8 | 50.0213 | 50.0213 | -0.17151 | -0.17151 | 50.1113 | -2.6033 | -2.6033
20.85 | 50.0213 | 50.0213 | -0.17151 | -0.17151 | 50.1113 | -2.6033 | -2.6033
20.9 | 50.0041 | 50.0041 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
20.95 | 50.0041 | 50.0041 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21 | 50.002 | 50.002 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21.05 | 50.002 | 50.002 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21.1 | 50.0087 | 50.002 | 0 | 0 | 50.1113 | -2.6033 | -2.6033
21.15 | 50.0087 | 50.002 | 0 | 0 | 50.09 | -2.0273 | -2.0273
21.2 | 49.9728 | 49.9728 | 0.32956 | 0.32956 | 50.09 | -2.0273 | -2.0273
21.25 | 49.9728 | 49.9728 | 0.32956 | 0.32956 | 50.09 | -2.0273 | -2.0273
21.3 | 49.9723 | 49.9723 | 0.34197 | 0.34197 | 50.09 | -2.0273 | -2.0273
21.35 | 49.9723 | 49.9723 | 0.34197 | 0.34197 | 50.0213 | -0.17151 | -0.17151
21.4 | 49.93 | 49.93 | 1.4855 | 1.4855 | 50.0213 | -0.17151 | -0.17151
21.45 | 49.93 | 49.93 | 1.4855 | 1.4855 | 50.0087 | 0 | 0
21.5 | 50.0068 | 49.93 | 1.4855 | 1.4855 | 50.0087 | 0 | 0
21.55 | 50.0068 | 49.93 | 1.4855 | 1.4855 | 50.0087 | 0 | 0