## Notes
What does this show?
Each row represents a different dispatch of MVAr absorption at transmission sites
We have modelled with standard reactor sizes of 100MVAr at 275kV and 200MVAr at 400kV. Other sizes are of course possible, but there are then semi-infinite combinations.
A list of all possible combinations was produced from 0MVAr at all sites to full dispatch at all sites.
The list was filtered for those that gave rise to totals of 500MVAr and 600MVAR, and these were all analysed.
Data Explanation
The scenario number in Column A is arbitrary - it is assigned in the scenario creation process and there is no meaning to it. It just helps us track.
Column B is the 'result' - see next section.
Columns C to K are the MVAr values at each transmission site for that scenario. Note the sites are 275kV except where suffixed with '4' e.g. 'STSB4'
Columns L to O summarise information about each case. Respectively: the total MVAr in that case, the MVAr inside WY1, the MVAr inside WY2, the number of sites with compensation
Column P marks counterfactual cases with 'CF'. Note the 'special' case of 20MVARs at each site in WY1 on row 57.
Pass/Fail criteria [Column B]
SQSS Planning criteria gives upper voltage limits of 1.025p.u. at 400kV [i.e. 410kV], and 1.05 for 275kV [288.75kV]
However, there is a clause that the 400kV limit [only] can be relaxed to the operational limit [1.05pu] where there is "sufficient certainty" that it can be achieved operationally.
We have determined that in this case using a limit of 1.03p.u. gives sufficient certainty
On that basis, the success criteria for combinations is no 400kV voltage > 1.03pu and no 275kV voltage > 1.05 pu
The number of violations are shown in Column C, where zero violations is an acceptable case.
Hence only cases with zero violations, marked green, would 'pass' the assessment of combinations
Data Sort
By default, data is sorted by number of violations, then by number of sites [both smallest to largest]
This is on the crude assumption that fewer sites means a cheaper outcome [i.e. same cost at all sites].
Please re-sort and filter in any way you like.

## Summary_Results
|  | Scenario dispatch data | [8 empty] | Information
Scen | Violations | KIRK | BRAW | FERR | MONF | ELLA | STAL4 | STSB4 | MACC4 | BRED | Σ MVAr | In WY1 | In WY2 | # of sites | Special
77 | 0 | 0 | 0 | -100 | 0 | 0 | -200 | -200 | 0 | 0 | -500 | -100 | -400 | 3 | CF
45 | 0 | 0 | 0 | 0 | -100 | 0 | -200 | -200 | 0 | 0 | -500 | -100 | -400 | 3 | CF
29 | 0 | 0 | 0 | 0 | 0 | -100 | -200 | -200 | 0 | 0 | -500 | -100 | -400 | 3 | CF
269 | 0 | -100 | 0 | 0 | 0 | 0 | -200 | -200 | 0 | 0 | -500 | -100 | -400 | 3 | CF
141 | 0 | 0 | -100 | 0 | 0 | 0 | -200 | -200 | 0 | 0 | -500 | -100 | -400 | 3 | CF
93 | 0 | 0 | 0 | -100 | 0 | -100 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
173 | 0 | 0 | -100 | 0 | -100 | 0 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
205 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
333 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
397 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
157 | 0 | 0 | -100 | 0 | 0 | -100 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
285 | 0 | -100 | 0 | 0 | 0 | -100 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
30 | 0 | 0 | 0 | 0 | 0 | -100 | -200 | -200 | 0 | -100 | -600 | -100 | -500 | 4
61 | 0 | 0 | 0 | 0 | -100 | -100 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
78 | 0 | 0 | 0 | -100 | 0 | 0 | -200 | -200 | 0 | -100 | -600 | -100 | -500 | 4
109 | 0 | 0 | 0 | -100 | -100 | 0 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
142 | 0 | 0 | -100 | 0 | 0 | 0 | -200 | -200 | 0 | -100 | -600 | -100 | -500 | 4
270 | 0 | -100 | 0 | 0 | 0 | 0 | -200 | -200 | 0 | -100 | -600 | -100 | -500 | 4
301 | 0 | -100 | 0 | 0 | -100 | 0 | -200 | -200 | 0 | 0 | -600 | -200 | -400 | 4
46 | 0 | 0 | 0 | 0 | -100 | 0 | -200 | -200 | 0 | -100 | -600 | -100 | -500 | 4
107 | 0 | 0 | 0 | -100 | -100 | 0 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
171 | 0 | 0 | -100 | 0 | -100 | 0 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
299 | 0 | -100 | 0 | 0 | -100 | 0 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
59 | 0 | 0 | 0 | 0 | -100 | -100 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
91 | 0 | 0 | 0 | -100 | 0 | -100 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
203 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
331 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
268 | 0 | -100 | 0 | 0 | 0 | 0 | -200 | 0 | -200 | -100 | -600 | -100 | -500 | 4
44 | 0 | 0 | 0 | 0 | -100 | 0 | -200 | 0 | -200 | -100 | -600 | -100 | -500 | 4
283 | 0 | -100 | 0 | 0 | 0 | -100 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
395 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
76 | 0 | 0 | 0 | -100 | 0 | 0 | -200 | 0 | -200 | -100 | -600 | -100 | -500 | 4
155 | 0 | 0 | -100 | 0 | 0 | -100 | -200 | 0 | -200 | 0 | -600 | -200 | -400 | 4
245 | 0 | 0 | -100 | -100 | -100 | -100 | 0 | -200 | 0 | 0 | -600 | -400 | -200 | 5
437 | 0 | -100 | -100 | 0 | -100 | -100 | 0 | -200 | 0 | 0 | -600 | -400 | -200 | 5
469 | 0 | -100 | -100 | -100 | 0 | -100 | 0 | -200 | 0 | 0 | -600 | -400 | -200 | 5
373 | 0 | -100 | 0 | -100 | -100 | -100 | 0 | -200 | 0 | 0 | -600 | -400 | -200 | 5
182 | 0 | 0 | -100 | 0 | -100 | -100 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
214 | 0 | 0 | -100 | -100 | 0 | -100 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
310 | 0 | -100 | 0 | 0 | -100 | -100 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
342 | 0 | -100 | 0 | -100 | 0 | -100 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
485 | 0 | -100 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | 0 | -600 | -400 | -200 | 5
406 | 0 | -100 | -100 | 0 | 0 | -100 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
118 | 0 | 0 | 0 | -100 | -100 | -100 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
358 | 0 | -100 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
454 | 0 | -100 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
230 | 0 | 0 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
422 | 0 | -100 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | -100 | -600 | -300 | -300 | 5
435 | 0 | -100 | -100 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | -600 | -400 | -200 | 5
467 | 0 | -100 | -100 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | -600 | -400 | -200 | 5
212 | 0 | 0 | -100 | -100 | 0 | -100 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
340 | 0 | -100 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
452 | 0 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
404 | 0 | -100 | -100 | 0 | 0 | -100 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
5_20s | 0 | -20 | -20 | -20 | -20 | -20 | -200 | -200 | 0 | 0 | -500 | -100 | -400 | 7 | CF
14 | 1 | 0 | 0 | 0 | 0 | 0 | -200 | -200 | 0 | -100 | -500 | 0 | -500 | 3
15 | 1 | 0 | 0 | 0 | 0 | 0 | -200 | -200 | -200 | 0 | -600 | 0 | -600 | 3
116 | 1 | 0 | 0 | -100 | -100 | -100 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
228 | 1 | 0 | -100 | -100 | -100 | 0 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
243 | 1 | 0 | -100 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | -600 | -400 | -200 | 5
356 | 1 | -100 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
371 | 1 | -100 | 0 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | -600 | -400 | -200 | 5
180 | 1 | 0 | -100 | 0 | -100 | -100 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
308 | 1 | -100 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
420 | 1 | -100 | -100 | 0 | -100 | 0 | 0 | 0 | -200 | -100 | -600 | -300 | -300 | 5
86 | 2 | 0 | 0 | -100 | 0 | -100 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
54 | 2 | 0 | 0 | 0 | -100 | -100 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
453 | 2 | -100 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
421 | 2 | -100 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
405 | 2 | -100 | -100 | 0 | 0 | -100 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
341 | 2 | -100 | 0 | -100 | 0 | -100 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
309 | 2 | -100 | 0 | 0 | -100 | -100 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
278 | 2 | -100 | 0 | 0 | 0 | -100 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
229 | 2 | 0 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
213 | 2 | 0 | -100 | -100 | 0 | -100 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
181 | 2 | 0 | -100 | 0 | -100 | -100 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
150 | 2 | 0 | -100 | 0 | 0 | -100 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
117 | 2 | 0 | 0 | -100 | -100 | -100 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
28 | 2 | 0 | 0 | 0 | 0 | -100 | -200 | 0 | -200 | -100 | -600 | -100 | -500 | 4
140 | 2 | 0 | -100 | 0 | 0 | 0 | -200 | 0 | -200 | -100 | -600 | -100 | -500 | 4
483 | 2 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | -600 | -400 | -200 | 5
390 | 3 | -100 | -100 | 0 | 0 | 0 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
357 | 3 | -100 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | 0 | -500 | -300 | -200 | 4
326 | 3 | -100 | 0 | -100 | 0 | 0 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
294 | 3 | -100 | 0 | 0 | -100 | 0 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
198 | 3 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
166 | 3 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
102 | 3 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | -100 | -500 | -200 | -300 | 4
339 | 4 | -100 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
279 | 4 | -100 | 0 | 0 | 0 | -100 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
451 | 5 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
419 | 5 | -100 | -100 | 0 | -100 | 0 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
355 | 5 | -100 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
307 | 5 | -100 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
227 | 5 | 0 | -100 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
211 | 5 | 0 | -100 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
179 | 5 | 0 | -100 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
115 | 5 | 0 | 0 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
151 | 5 | 0 | -100 | 0 | 0 | -100 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
87 | 5 | 0 | 0 | -100 | 0 | -100 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
391 | 5 | -100 | -100 | 0 | 0 | 0 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
55 | 5 | 0 | 0 | 0 | -100 | -100 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
295 | 5 | -100 | 0 | 0 | -100 | 0 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
327 | 5 | -100 | 0 | -100 | 0 | 0 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
167 | 5 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
199 | 5 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
103 | 5 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | -200 | 0 | -600 | -200 | -400 | 4
24 | 6 | 0 | 0 | 0 | 0 | -100 | 0 | -200 | -200 | -100 | -600 | -100 | -500 | 4
410 | 6 | -100 | -100 | 0 | 0 | -100 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
75 | 7 | 0 | 0 | -100 | 0 | 0 | -200 | 0 | -200 | 0 | -500 | -100 | -400 | 3
43 | 7 | 0 | 0 | 0 | -100 | 0 | -200 | 0 | -200 | 0 | -500 | -100 | -400 | 3
403 | 7 | -100 | -100 | 0 | 0 | -100 | 0 | 0 | -200 | 0 | -500 | -300 | -200 | 4
264 | 7 | -100 | 0 | 0 | 0 | 0 | 0 | -200 | -200 | -100 | -600 | -100 | -500 | 4
136 | 8 | 0 | -100 | 0 | 0 | 0 | 0 | -200 | -200 | -100 | -600 | -100 | -500 | 4
498 | 8 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | -100 | -600 | -500 | -100 | 6
100 | 9 | 0 | 0 | -100 | -100 | 0 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
72 | 9 | 0 | 0 | -100 | 0 | 0 | 0 | -200 | -200 | -100 | -600 | -100 | -500 | 4
40 | 9 | 0 | 0 | 0 | -100 | 0 | 0 | -200 | -200 | -100 | -600 | -100 | -500 | 4
466 | 9 | -100 | -100 | -100 | 0 | -100 | 0 | 0 | 0 | -100 | -500 | -400 | -100 | 5
434 | 9 | -100 | -100 | 0 | -100 | -100 | 0 | 0 | 0 | -100 | -500 | -400 | -100 | 5
370 | 9 | -100 | 0 | -100 | -100 | -100 | 0 | 0 | 0 | -100 | -500 | -400 | -100 | 5
242 | 9 | 0 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | -100 | -500 | -400 | -100 | 5
122 | 9 | 0 | 0 | -100 | -100 | -100 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
186 | 9 | 0 | -100 | 0 | -100 | -100 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
218 | 9 | 0 | -100 | -100 | 0 | -100 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
314 | 9 | -100 | 0 | 0 | -100 | -100 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
426 | 9 | -100 | -100 | 0 | -100 | 0 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
458 | 9 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
346 | 9 | -100 | 0 | -100 | 0 | -100 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
121 | 10 | 0 | 0 | -100 | -100 | -100 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
482 | 10 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | -100 | -500 | -400 | -100 | 5
377 | 10 | -100 | 0 | -100 | -100 | -100 | -200 | 0 | 0 | 0 | -600 | -400 | -200 | 5
249 | 10 | 0 | -100 | -100 | -100 | -100 | -200 | 0 | 0 | 0 | -600 | -400 | -200 | 5
489 | 10 | -100 | -100 | -100 | -100 | 0 | -200 | 0 | 0 | 0 | -600 | -400 | -200 | 5
441 | 10 | -100 | -100 | 0 | -100 | -100 | -200 | 0 | 0 | 0 | -600 | -400 | -200 | 5
473 | 10 | -100 | -100 | -100 | 0 | -100 | -200 | 0 | 0 | 0 | -600 | -400 | -200 | 5
234 | 10 | 0 | -100 | -100 | -100 | 0 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
362 | 10 | -100 | 0 | -100 | -100 | 0 | -200 | 0 | 0 | -100 | -600 | -300 | -300 | 5
267 | 11 | -100 | 0 | 0 | 0 | 0 | -200 | 0 | -200 | 0 | -500 | -100 | -400 | 3
457 | 11 | -100 | -100 | -100 | 0 | 0 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
425 | 11 | -100 | -100 | 0 | -100 | 0 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
361 | 11 | -100 | 0 | -100 | -100 | 0 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
345 | 11 | -100 | 0 | -100 | 0 | -100 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
313 | 11 | -100 | 0 | 0 | -100 | -100 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
233 | 11 | 0 | -100 | -100 | -100 | 0 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
217 | 11 | 0 | -100 | -100 | 0 | -100 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
185 | 11 | 0 | -100 | 0 | -100 | -100 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
148 | 11 | 0 | -100 | 0 | 0 | -100 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
497 | 11 | -100 | -100 | -100 | -100 | -100 | 0 | 0 | 0 | 0 | -500 | -500 | 0 | 5
139 | 12 | 0 | -100 | 0 | 0 | 0 | -200 | 0 | -200 | 0 | -500 | -100 | -400 | 3
276 | 12 | -100 | 0 | 0 | 0 | -100 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
164 | 12 | 0 | -100 | 0 | -100 | 0 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
106 | 12 | 0 | 0 | -100 | -100 | 0 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
27 | 13 | 0 | 0 | 0 | 0 | -100 | -200 | 0 | -200 | 0 | -500 | -100 | -400 | 3
90 | 14 | 0 | 0 | -100 | 0 | -100 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
84 | 14 | 0 | 0 | -100 | 0 | -100 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
58 | 14 | 0 | 0 | 0 | -100 | -100 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
409 | 14 | -100 | -100 | 0 | 0 | -100 | -200 | 0 | 0 | 0 | -500 | -300 | -200 | 4
330 | 14 | -100 | 0 | -100 | 0 | 0 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
324 | 14 | -100 | 0 | -100 | 0 | 0 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
292 | 14 | -100 | 0 | 0 | -100 | 0 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
298 | 14 | -100 | 0 | 0 | -100 | 0 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
202 | 14 | 0 | -100 | -100 | 0 | 0 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
196 | 14 | 0 | -100 | -100 | 0 | 0 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
170 | 14 | 0 | -100 | 0 | -100 | 0 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
52 | 15 | 0 | 0 | 0 | -100 | -100 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
388 | 15 | -100 | -100 | 0 | 0 | 0 | 0 | 0 | -200 | -100 | -500 | -200 | -300 | 4
394 | 16 | -100 | -100 | 0 | 0 | 0 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
282 | 16 | -100 | 0 | 0 | 0 | -100 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
154 | 16 | 0 | -100 | 0 | 0 | -100 | -200 | 0 | 0 | -100 | -500 | -200 | -300 | 4
12 | 17 | 0 | 0 | 0 | 0 | 0 | -200 | 0 | -200 | -100 | -500 | 0 | -500 | 3
71 | 19 | 0 | 0 | -100 | 0 | 0 | 0 | -200 | -200 | 0 | -500 | -100 | -400 | 3
39 | 19 | 0 | 0 | 0 | -100 | 0 | 0 | -200 | -200 | 0 | -500 | -100 | -400 | 3
263 | 19 | -100 | 0 | 0 | 0 | 0 | 0 | -200 | -200 | 0 | -500 | -100 | -400 | 3
23 | 20 | 0 | 0 | 0 | 0 | -100 | 0 | -200 | -200 | 0 | -500 | -100 | -400 | 3
135 | 21 | 0 | -100 | 0 | 0 | 0 | 0 | -200 | -200 | 0 | -500 | -100 | -400 | 3
8 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | -200 | -200 | -100 | -500 | 0 | -500 | 3