## Please Read First
Distributed ReStart Test Procurement Event
Appendix 3 - Mock Tender Submission Template
Please read the below information before submitting your mock tender bid.
First, please make sure you have read the Invite to Test Procurement Event and Appendix 1 - Mock Tender Requirements Document before completing this Appendix 2 - Mock Tender Submission Template. Once this template has been completed, please email your mock tender bid back to the Distributed ReStart project team, along with a completed Appendix 3 - Event Feedback Form.
The deadline for submitting your information is by Monday 6 September 09:00, please email to:
Roopkamal.Phull@nationalgrideso.com; Hannah.Rochford1@nationalgrideso.com
The purpose of this Excel document is: - to get good quality and as close to real information as possible from a variety of DER providers, for testing against our assessment criteria and testing whether the assessment works as intended - demonstrate to participants the likely questions that may be asked as part of a future distribution restoration procurement process. Please remember that this is a Test Procurement Event, no contracts will be awarded at the end of the event.
There will be an opportunity on 18 August for a ‘mid-way’ webinar to ask the Distributed ReStart project team any questions around this Test Procurement Eevent. Details to join will be emailed closer to the date. In the meantime, if you have any urgent queries, please contact us by email.
Instructions for completing this document:
1 | Save a copy of this document and complete the fields in the other three tabs. The mandatory sections will be marked with an * and we encourage you to fill in as much of the remaining sections as you can, without undertaking any detailed studies. The information you provide will be demonstrating the capability you can already provide, what changes you would need to make to meet the requirements, plus associated costs and a mock commercial bid.
2 | Complete the details requested in the Your details tab, this will enable us to understand you, your business and your plant.
Complete the requested details in the Technical submission tab, outlining your capabilities against the functional requirements and any relevant costs.
Complete the Commercial submission tab, the costs from your technical submission will be brought forward into the Commercial submission tab. Please then fill in the fields requesting information on the extra costs involved in providing a distribution restoration service.
3 | As this is a test event, we are interested in understanding your experience of completing this information. Please use Appendix 3 - Event Feedback Form to outline any comments you have around the mock tender documents and requirements.
4 | Once complete, please email copies of both forms (Appendix 2 and Appendix 3) to:
Roopkamal.Phull@nationalgrideso.com; Hannah.Rochford1@nationalgrideso.com

## Your details
Essential Details
Provider Details*:
Provider name*
Site / asset / project name*
Please provide the geographical and electrical location of any/all proposed sites/assets involved in the mock tender bid, highlight where you are connected on the network, for example at 33kV. *
Email*
Bid Application*:
Please select which services you have submitted a bid for in this mock tender. Anchor generator (AG), or one/more top-up services (TUS).
| Service |  | Select service(s) entered for this mock tender
AG - Anchor generator
TUS - Fast MW control
TUS - Inertia
TUS - Frequency control
TUS - Reactive capability (voltage control)
TUS - Short-circuit infeed
TUS - Energy (MWh)
Summary of asset(s)*:
In no more than 500 words, please provide a brief summary which includes a description of your current asset and its capability, or how planned Distributed ReStart capability could be achieved.*
Optional - Do you currently provide any services to the ESO or any DNO?
If yes, please highlight which services you provide and to which parties. We want to understand this so we can gather information on how to enable service stacking with a distribution restoration service.

## Technical submission
Technical Submission
Please read the below information before completing the technical submission.
First, make sure you have read Section 1, of Appendix 1 - Mock Tender Requirements Document, before completing this technical submission. The following technical submission template is split into two sections: anchor generator functional requirements and top-up service functional requirements.
If you are entering this mock tender as an anchor generator, please make sure to fill in the boxes against each anchor generator requirement and also each top-up service requirement. This will enable us to understand the full capabilities of assets tendering in and assess these with our assessment criteria. If you are entering as a top-up service, please fill in the boxes against the relevant requirements for the top-up service(s) you are bidding for and also the boxes against the top-service(s) resilience requirements.
Please input estimated costs into the cost column, ranges will be accepted. Costs could include: preliminary works, OEM (Original Equipment Manufacturer) inspection/upgrade costs, construction works, project costs, etc. The Commercial submision tab pulls through the estimated costs from this Technical submission - please be careful not to move around columns or rows. If you want to add extra information - please add to the right-hand side of the rows.
Example:
Requirement | Minimum level | Response format | Participant response on existing plant capability | If requirement is not currently met, but the provider could enhance their services in order to meet it, please summarise the changes required here | Estimated cost of meeting requirement, a range is acceptable | If possible, please provide a breakdown of costs, and if struggling to estimate cost, highlight what would you need to do to understand/estimate cost
Resilience of Supply, Availability to start-up | ≥ 120 hours | State in number of hours | No auxiliary units on site currently | We would propose as part of our submission to purchase and install auxiliary units. We would/would not require capital to do this. Once installed, the auxiliary units will have resilience to run continuously for 5 days. | £X - £Y (in a real tender these costs would most likely be indentified through the detailed feasibility study). | £A assessment of site £B pre-construction works £C installation of axuillary unit £D fuel costs to meet resilience requirements
Anchor Generator Functional Requirements:
Requirement | Minimum level | Response format | Participant response on existing plant capability | If requirement is not currently met, but the provider could enhance their services in order to meet it, please summarise the changes required here | Estimated cost of meeting requirement, a range is acceptable | If possible, please provide a breakdown of costs, and if struggling to estimate cost, highlight what would you need to do to understand/estimate cost
Time to Connect | ≤8h | State in number of hours.
Service Availability | ≥90% | State percentage of expected average availability.
Resilience of Supply - Availability to start-up | ≥120h | State in number of hours.
Resilience of Supply – Service Delivery | ≥72h up to 120h | State in number of hours.
Sequential Black Starts | ≥ 3 | Yes/no
Reactive Capability (Voltage Control) | Ability to provide continuous steady state control of the voltage with a set point and slope characteristic. Minimum of 0.95 leading and 0.95 lagging power factor at the point of connection. | Yes/no to voltage control and, state Mvar leading and lagging values at zero power export.
Frequency Control | A fast-acting proportional frequency control-device is required. | Yes/no
Block Loading Size | ≥ 2MW | State expected largest size of block load capability.
Short-Circuit Infeed | ≥ 1 x DER MVA rating (at t=1s) | State the maximum equivalent MVA short-circuit infeed that can be sustained at the DNO point of connection for at least one second.
Top-Up Service(s) Functional Requirements:
Technical Requirements:
Requirement | Minimum level | Response format | Participant response on existing plant capability | If requirement is not currently met, but the provider could enhance their services in order to meet it, please summarise the changes required here | Estimated cost of meeting requirement, a range is acceptable | If struggling to estimate cost, what would you need to do to understand/estimate cost
Fast MW control | <200ms provide available MW, sustained for at least 15 minutes with gradual reduction toward preferred operating position, and/or | State the maximum MW decrease that can achieved within 200ms of receiving a signal or measuring a change in frequency that would prompt such a change.
<200ms provide available MW, sustained for at least 10 seconds with gradual reduction toward preferred operating position, and/or
| Active power output reduction in response to a change in system frequency above a certain value (value and required rate of reduction to be confirmed) and/or | State the maximum MW increase that can achieved within 200ms of receiving a signal or measuring a change in frequency that would prompt such a change.
Active power output increase in response to a system frequency below a certain value (value and required rate of increase to be confirmed). This will only be required if output has been constrained below the maximum output power.
Inertia | There is no minimum requirement for individual generators/resources but the service provider should state what inertia is available. | State the inherent inertial response (without measurement or control) in MW seconds (or MJ).
Frequency Control | Provide frequency sensitive control of active power. | Yes/no
Reactive Capability (voltage control) | Ability to provide continuous steady state control of the voltage with a set point and slope characteristic. Minimum of 0.95 leading and 0.95 lagging power factor at the point of connection. | Yes/no to voltage control and, state Mvar leading and lagging values.
Short Circuit infeed | ≥ 1 x DER MVA rating (at t=1s) | State the maximum equivalent MVA short-circuit infeed that can be sustained at the DNO point of connection for at least one second.
Energy (MWh) | Generate or consume MW on instruction from an external control system, deliver within 10 seconds of request. | State the average power output that can be reliably maintained over a period of 120 hours. Express either as an average MW or the total MWh that can produced in 120 hours.
Resilience Requirements:
Requirement | Minimum level | Response format | Participant response on existing plant capability | If requirement is not currently met, but the provider could enhance their services in order to meet it, please summarise the changes required here | Estimated cost of meeting requirement, a range is acceptable | If struggling to estimate cost, what would you need to do to understand/estimate cost
Resilience of Supply - Availability of communications | ≥72h | Yes/No
Resilience of Supply - Service delivery | ≥72h up to 120h | State in number of hours.
Service Availability | ≥90% | State percentage of expected average availability.

## Commercial submission
Commercial Submission
Please read the below information before completing the commercial submission.
First, make sure you have read Section 2.2, of Appendix 1 - Mock Tender Requirements Document, before completing this commercial submission. Second, please ensure you have filled in the other two tabs, Your details & Technical submission.
The aim of this commercial submission is to understand the full costs involved, for DER, in providing a distribution restoration service. If you don't know the cost, please let us know and highlight what you would need to do to understand the cost.
| Category | Breakdown | Breakdown costs | Total category cost | Comments - please provide any comments regarding the provision of costs.
Technical submission (these costs are pulled through from the Technical submission tab - please do not overwrite). | Anchor generator requirements | Time to Connect | 0 | Due to possible ranges, we will calculate the total costs when we receive submissions.
|  | Service Availability | 0
|  | Resilience of Supply – Service Delivery | 0
|  | Resilience of Supply - Availability to start-up | 0
|  | Sequential Black Starts | 0
|  | Reactive Capability (voltage control) | 0
|  | Frequency Control | 0
|  | Block Loading Size | 0
|  | Short-circuit infeed | 0
| Top-up service requirements (technical) | Fast MW control | 0
|  | Inertia | 0
|  | Frequency Control | 0
|  | Reactive Capability (voltage control) | 0
|  | Short Circuit infeed | 0
|  | Energy (MWh) | 0
| Top-up service requirements (resilience) | Resilience of Supply - Availability of communications | 0
|  | Resilience of Supply - Service delivery | 0
|  | Service Availability | 0
Commercial submission (please fill in estimated costs here). | Availability fee (this could be paid monthly in a £/Settlement Period figure) breakdown. The proposed contract duration is 5 years but we are requesting feedback on our proposed timelines. | Potential commissioning assessment
Potential testing costs over the duration of the contract
On-going operating and maintenance costs over the duration of the contract
Service margin
Feasibility study(s) costs
Other - please specify
Other - please specify
Other - please specify
Other - please specify
Total cost |  |  |  |  | If you wish to calculate any total costs please feel free to use the free cells in this tab, and outline what you have calculated.