## Contents
Introduction
The workbook contains graphs and data from the 2021 Winter Early View publication. The Winter Early View can be downloaded from the National Grid ESO website.
Chart Contents
Section | Title
Margins | Supply margin in relation to generation capacity and demand

## System Margins
Supply margin in relation to generation capacity and demand
Key Statistics
| Summary |  | 2020/21 | 2021/22
| De-rated margin at underlying demand level (GW) |  | 4.8 GW | 4.3 GW
| De-rated margin at underlying demand level (%) |  | 8.26% | 7.299%
| Loss of Load Expectation (LOLE) |  | < 0.1 hours / year | 0.1 hours / year
| Total maximum technical capability from generation |  | 100.7 GW | 103.6 GW
| Total average cold spell (ACS) peak underlying demand (including operating reserve) |  | 58 GW | 59.5 GW
| Operating reserve |  | 1.5 GW | 1.5 GW
| Interconnectors net import flows |  | 3 GW | 4.5 GW
| Table 1 | De-rated Margin Range
|  | De-rated margin (GW) | De-rated margin (%) | Approx 3 hours LOLE
| Low case | 3141.1556 | 5.279% | 1700
| Base case | 4342.8637 | 7.299% | 1700
| High case | 5359.6837 | 9.008% | 1700
| Table 2 | Generation Capacities and Derating Factors
| Category | Type | SubType | Winter Outlook Early View Base Case De-rating Factor (%) | Winter Outlook Early View Base Case Installed capacity (MW) | Winter Outlook Early View Base Case De-rated capacity (MW)
| Renewable | Biomass / Waste | Biomass - CHP | 88.55% | 132 | 116.8804
| Renewable | Biomass / Waste | Biomass - Conversion | 88.55% | 2936 | 2599.7031
| Renewable | Biomass / Waste | Biomass - Dedicated | 88.55% | 467 | 413.5086
| Thermal | Coal | Coal | 60% | 4240 | 2544
| Thermal | Diesel | Diesel | 95.47% | 70.8 | 67.5935
| Other | Other | DSR | 78.45% | 1334.5852 | 1046.9821
| Thermal | Gas | Gas - CCGT Existing | 90.92% | 25987 | 23627.3804
| Thermal | Gas | Gas - CHP | 90.92% | 1934.68 | 1759.0111
| Thermal | Gas | Gas Recip | 95.47% | 366 | 349.4242
| Renewable | Hydro / Tidal / Wind | Hydro | 91.15% | 1350.02 | 1230.6057
| Nuclear | Nuclear | Nuclear | 75.77% | 7136 | 5406.6146
| Thermal | Gas | OCGT - GT | 95.47% | 2177.81 | 2079.1789
| Storage | Storage | Storage | 77.35% | 2959.16 | 2288.879
| Renewable | Hydro / Tidal / Wind | Tidal - Array | 22% | 14.9 | 3.278
| Renewable | Biomass / Waste | Waste | 88.55% | 36 | 31.8765
| Renewable | Hydro / Tidal / Wind | Wind - Offshore | 16.71% | 13231.3 | 2210.8805
| Renewable | Hydro / Tidal / Wind | Wind - Onshore | 16.71% | 13029.2529 | 2177.1195
| Other | Other | Other Embedded Gen |  | 26185.3835 | 11419.0848
| Total Generation |  |  |  | 103587.8915 | 59372.0008
* capacity values shown above are all transmission-connected, except for wind, DSR and 'other embedded gen'.
| Table 3 | Supply margin in relation to generation capacity and demand
| Category | Technical capability (generation) | De-rated generation capacity | ACS peak underlying demand | De-rated capacity margin (GW) | De-rated capacity margin (%)
| Nuclear | 7136 | 5406.6146
| Thermal | 34776.29 | 30426.588
| Renewable | 31196.4729 | 8783.8523
| Storage | 2959.16 | 2288.879
| Other | 27519.9686 | 12466.0669
| Interconnector Imports | 7060 | 4471
| Demand |  |  | 58000
| Operating reserve |  |  | 1500
|  | 110647.8915 | 63843.0008 | 59500 | 4343.0008 | 7.299%
| Chart label | De-rated margin of 4.3 GW (7.3%)