## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.

## Report
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; |  | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) |  | Transmission fault | Voltage Dip | Additional data
20210803-1 | Trip of LAGA-1 |  | 2021-08-03 11:05 | 20210803-1 | 50.003 | 49.875 | -0.042519 | 242 | LAGA-1 | -752
20210809-1 | Trip of SGT3 in RUGE4 |  | 2021-08-09 12:03 | [8 empty] | RUGE4 | 18.7
20210817-1 | Trip of CARR-1 |  | 2021-08-17 19:05 | 20210817-1 | 50.02 | 49.804 | -0.054223 | 220 | CARR-1 | -412
20210819-1 | Trip of HINB-7 |  | 2021-08-19 09:14 | 20210819-1 | 49.952 | 49.793 | -0.056243 | 253 | HINB-7 | -491
20210829-1 | Trip of GRAI-8 |  | 2021-08-29 17:13 | 20210829-1 | 50.027 | 49.968 | -0.007016 | 199 | GRAI-8 | -418
20210830-1 | Trip of WBURB-3 |  | 2021-08-30 08:36 | 20210830-1 | 49.975 | 49.794 | -0.049863 | 187 | WBURB-3 | -410
20210830-2 | Trip of LBAR-1 |  | 2021-08-30 17:11 | 20210830-2 | 50.022 | 49.784 | -0.018219 | 230 | LBAR-1 | -309

## Sheet2
2021-08-09 | 12:03 | 49.953
2021-08-09 | 12:03 | 49.953
2021-08-09 | 12:03 | 49.951
2021-08-09 | 12:03 | 49.948
2021-08-09 | 12:03 | 49.945
2021-08-09 | 12:03 | 49.945
2021-08-09 | 12:03 | 49.944
2021-08-09 | 12:03 | 49.941
2021-08-09 | 12:03 | 49.939
2021-08-09 | 12:03 | 49.94
2021-08-09 | 12:03 | 49.945
2021-08-09 | 12:03 | 49.949
2021-08-09 | 12:03 | 49.951
2021-08-09 | 12:03 | 49.953
2021-08-09 | 12:03 | 49.955
2021-08-09 | 12:03 | 49.957
2021-08-09 | 12:03 | 49.96
2021-08-09 | 12:03 | 49.959
2021-08-09 | 12:03 | 49.957
2021-08-09 | 12:03 | 49.958
2021-08-09 | 12:03 | 49.957
2021-08-09 | 12:03 | 49.954
2021-08-09 | 12:03 | 49.951
2021-08-09 | 12:03 | 49.949
2021-08-09 | 12:03 | 49.947
2021-08-09 | 12:03 | 49.943
2021-08-09 | 12:03 | 49.941
2021-08-09 | 12:03 | 49.937
2021-08-09 | 12:03 | 49.934
2021-08-09 | 12:03 | 49.93
2021-08-09 | 12:04 | 49.925
2021-08-09 | 12:04 | 49.923
2021-08-09 | 12:04 | 49.924
2021-08-09 | 12:04 | 49.923
2021-08-09 | 12:04 | 49.926
2021-08-09 | 12:04 | 49.93
2021-08-09 | 12:04 | 49.933
2021-08-09 | 12:04 | 49.936
2021-08-09 | 12:04 | 49.939
2021-08-09 | 12:04 | 49.941
2021-08-09 | 12:04 | 49.943
2021-08-09 | 12:04 | 49.945
2021-08-09 | 12:04 | 49.948
2021-08-09 | 12:04 | 49.953
2021-08-09 | 12:04 | 49.955
2021-08-09 | 12:04 | 49.957
2021-08-09 | 12:04 | 49.958
2021-08-09 | 12:04 | 49.96
2021-08-09 | 12:04 | 49.962
2021-08-09 | 12:04 | 49.962
2021-08-09 | 12:04 | 49.961
2021-08-09 | 12:04 | 49.96
2021-08-09 | 12:04 | 49.961
2021-08-09 | 12:04 | 49.961
2021-08-09 | 12:04 | 49.961
2021-08-09 | 12:04 | 49.961
2021-08-09 | 12:04 | 49.959
2021-08-09 | 12:04 | 49.958
2021-08-09 | 12:04 | 49.959
2021-08-09 | 12:04 | 49.959
2021-08-09 | 12:04 | 49.962
2021-08-09 | 12:04 | 49.963
2021-08-09 | 12:04 | 49.962
2021-08-09 | 12:04 | 49.96
2021-08-09 | 12:04 | 49.96
2021-08-09 | 12:04 | 49.958
2021-08-09 | 12:04 | 49.956
2021-08-09 | 12:04 | 49.955
2021-08-09 | 12:04 | 49.954
2021-08-09 | 12:04 | 49.955
2021-08-09 | 12:04 | 49.957
2021-08-09 | 12:04 | 49.959
2021-08-09 | 12:04 | 49.964
2021-08-09 | 12:04 | 49.967
2021-08-09 | 12:04 | 49.968
2021-08-09 | 12:04 | 49.971
2021-08-09 | 12:04 | 49.97
2021-08-09 | 12:04 | 49.972
2021-08-09 | 12:04 | 49.975
2021-08-09 | 12:04 | 49.979
2021-08-09 | 12:04 | 49.98
2021-08-09 | 12:04 | 49.981
2021-08-09 | 12:04 | 49.982
2021-08-09 | 12:04 | 49.982
2021-08-09 | 12:04 | 49.982
2021-08-09 | 12:04 | 49.981
2021-08-09 | 12:04 | 49.982
2021-08-09 | 12:04 | 49.982
2021-08-09 | 12:04 | 49.981
2021-08-09 | 12:04 | 49.982
2021-08-09 | 12:04 | 49.984
2021-08-09 | 12:05 | 49.983
2021-08-09 | 12:05 | 49.982
2021-08-09 | 12:05 | 49.979
2021-08-09 | 12:05 | 49.981
2021-08-09 | 12:05 | 49.982
2021-08-09 | 12:05 | 49.985
2021-08-09 | 12:05 | 49.985
2021-08-09 | 12:05 | 49.989
2021-08-09 | 12:05 | 49.992
2021-08-09 | 12:05 | 49.991
2021-08-09 | 12:05 | 49.992
2021-08-09 | 12:05 | 49.99
2021-08-09 | 12:05 | 49.991
2021-08-09 | 12:05 | 49.99
2021-08-09 | 12:05 | 49.989
2021-08-09 | 12:05 | 49.989
2021-08-09 | 12:05 | 49.988
2021-08-09 | 12:05 | 49.984
2021-08-09 | 12:05 | 49.983
2021-08-09 | 12:05 | 49.978
2021-08-09 | 12:05 | 49.975
2021-08-09 | 12:05 | 49.974
2021-08-09 | 12:05 | 49.97
2021-08-09 | 12:05 | 49.968
2021-08-09 | 12:05 | 49.966
2021-08-09 | 12:05 | 49.964
2021-08-09 | 12:05 | 49.964
2021-08-09 | 12:05 | 49.962
2021-08-09 | 12:05 | 49.964
2021-08-09 | 12:05 | 49.965
2021-08-09 | 12:05 | 49.966
2021-08-09 | 12:05 | 49.964
2021-08-09 | 12:05 | 49.966
2021-08-09 | 12:05 | 49.968
2021-08-09 | 12:05 | 49.971
2021-08-09 | 12:05 | 49.974
2021-08-09 | 12:05 | 49.979
2021-08-09 | 12:05 | 49.983
2021-08-09 | 12:05 | 49.988
2021-08-09 | 12:05 | 49.988
2021-08-09 | 12:05 | 49.988
2021-08-09 | 12:05 | 49.988
2021-08-09 | 12:05 | 49.989
2021-08-09 | 12:05 | 49.99
2021-08-09 | 12:05 | 49.991
2021-08-09 | 12:05 | 49.989
2021-08-09 | 12:05 | 49.993
2021-08-09 | 12:05 | 49.996
2021-08-09 | 12:05 | 49.998
2021-08-09 | 12:05 | 49.997
2021-08-09 | 12:05 | 50.002
2021-08-09 | 12:05 | 50.007
2021-08-09 | 12:05 | 50.011
2021-08-09 | 12:05 | 50.012
2021-08-09 | 12:05 | 50.012
2021-08-09 | 12:05 | 50.011
2021-08-09 | 12:05 | 50.012
2021-08-09 | 12:05 | 50.013
2021-08-09 | 12:05 | 50.015
2021-08-09 | 12:06 | 50.017
2021-08-09 | 12:06 | 50.02
2021-08-09 | 12:06 | 50.022
2021-08-09 | 12:06 | 50.023
2021-08-09 | 12:06 | 50.021
2021-08-09 | 12:06 | 50.017
2021-08-09 | 12:06 | 50.014
2021-08-09 | 12:06 | 50.013
2021-08-09 | 12:06 | 50.008
2021-08-09 | 12:06 | 50.009
2021-08-09 | 12:06 | 50.008
2021-08-09 | 12:06 | 50.01
2021-08-09 | 12:06 | 50.01
2021-08-09 | 12:06 | 50.012
2021-08-09 | 12:06 | 50.013
2021-08-09 | 12:06 | 50.013
2021-08-09 | 12:06 | 50.011
2021-08-09 | 12:06 | 50.011
2021-08-09 | 12:06 | 50.009
2021-08-09 | 12:06 | 50.006
2021-08-09 | 12:06 | 50.006
2021-08-09 | 12:06 | 50.005
2021-08-09 | 12:06 | 50.003
2021-08-09 | 12:06 | 50
2021-08-09 | 12:06 | 49.998
2021-08-09 | 12:06 | 49.997
2021-08-09 | 12:06 | 49.996
2021-08-09 | 12:06 | 49.998
2021-08-09 | 12:06 | 49.995
2021-08-09 | 12:06 | 49.994
2021-08-09 | 12:06 | 49.994
2021-08-09 | 12:06 | 49.993
2021-08-09 | 12:06 | 49.991
2021-08-09 | 12:06 | 49.988
2021-08-09 | 12:06 | 49.987
2021-08-09 | 12:06 | 49.986
2021-08-09 | 12:06 | 49.987
2021-08-09 | 12:06 | 49.987
2021-08-09 | 12:06 | 49.987
2021-08-09 | 12:06 | 49.985
2021-08-09 | 12:06 | 49.982
2021-08-09 | 12:06 | 49.979
2021-08-09 | 12:06 | 49.978
2021-08-09 | 12:06 | 49.981
2021-08-09 | 12:06 | 49.983
2021-08-09 | 12:06 | 49.985
2021-08-09 | 12:06 | 49.987
2021-08-09 | 12:06 | 49.985
2021-08-09 | 12:06 | 49.984
2021-08-09 | 12:06 | 49.982
2021-08-09 | 12:06 | 49.98
2021-08-09 | 12:06 | 49.977
2021-08-09 | 12:06 | 49.975
2021-08-09 | 12:06 | 49.969
2021-08-09 | 12:06 | 49.967
2021-08-09 | 12:06 | 49.962
2021-08-09 | 12:06 | 49.958
2021-08-09 | 12:06 | 49.955
2021-08-09 | 12:06 | 49.953
2021-08-09 | 12:06 | 49.955
2021-08-09 | 12:06 | 49.956
2021-08-09 | 12:07 | 49.954
2021-08-09 | 12:07 | 49.955
2021-08-09 | 12:07 | 49.955
2021-08-09 | 12:07 | 49.956
2021-08-09 | 12:07 | 49.957
2021-08-09 | 12:07 | 49.955
2021-08-09 | 12:07 | 49.95
2021-08-09 | 12:07 | 49.947
2021-08-09 | 12:07 | 49.946
2021-08-09 | 12:07 | 49.946
2021-08-09 | 12:07 | 49.948
2021-08-09 | 12:07 | 49.948
2021-08-09 | 12:07 | 49.952
2021-08-09 | 12:07 | 49.952
2021-08-09 | 12:07 | 49.952
2021-08-09 | 12:07 | 49.95
2021-08-09 | 12:07 | 49.948
2021-08-09 | 12:07 | 49.946
2021-08-09 | 12:07 | 49.943
2021-08-09 | 12:07 | 49.94
2021-08-09 | 12:07 | 49.939
2021-08-09 | 12:07 | 49.936
2021-08-09 | 12:07 | 49.935
2021-08-09 | 12:07 | 49.933
2021-08-09 | 12:07 | 49.933
2021-08-09 | 12:07 | 49.935
2021-08-09 | 12:07 | 49.935
2021-08-09 | 12:07 | 49.936
2021-08-09 | 12:07 | 49.936
2021-08-09 | 12:07 | 49.938

## 20210803-1
In GMT
Date | Time | Freq
2021-08-03 | 10:04 | 50.07
2021-08-03 | 10:04 | 50.069
2021-08-03 | 10:04 | 50.067
2021-08-03 | 10:04 | 50.068
2021-08-03 | 10:04 | 50.068
2021-08-03 | 10:04 | 50.07
2021-08-03 | 10:04 | 50.07
2021-08-03 | 10:04 | 50.071
2021-08-03 | 10:04 | 50.072
2021-08-03 | 10:04 | 50.071
2021-08-03 | 10:04 | 50.071
2021-08-03 | 10:04 | 50.071
2021-08-03 | 10:04 | 50.07
2021-08-03 | 10:04 | 50.067
2021-08-03 | 10:04 | 50.068
2021-08-03 | 10:04 | 50.069
2021-08-03 | 10:04 | 50.068
2021-08-03 | 10:04 | 50.066
2021-08-03 | 10:04 | 50.066
2021-08-03 | 10:04 | 50.062
2021-08-03 | 10:04 | 50.058
2021-08-03 | 10:04 | 50.056
2021-08-03 | 10:04 | 50.055
2021-08-03 | 10:04 | 50.055
2021-08-03 | 10:04 | 50.054
2021-08-03 | 10:04 | 50.052
2021-08-03 | 10:04 | 50.051
2021-08-03 | 10:04 | 50.051
2021-08-03 | 10:04 | 50.051
2021-08-03 | 10:04 | 50.052
2021-08-03 | 10:04 | 50.054
2021-08-03 | 10:05 | 50.054
2021-08-03 | 10:05 | 50.054
2021-08-03 | 10:05 | 50.056
2021-08-03 | 10:05 | 50.055
2021-08-03 | 10:05 | 50.056
2021-08-03 | 10:05 | 50.058
2021-08-03 | 10:05 | 50.058
2021-08-03 | 10:05 | 50.059
2021-08-03 | 10:05 | 50.058
2021-08-03 | 10:05 | 50.056
2021-08-03 | 10:05 | 50.055
2021-08-03 | 10:05 | 50.053
2021-08-03 | 10:05 | 50.053
2021-08-03 | 10:05 | 50.05
2021-08-03 | 10:05 | 50.047
2021-08-03 | 10:05 | 50.046
2021-08-03 | 10:05 | 50.041
2021-08-03 | 10:05 | 50.04
2021-08-03 | 10:05 | 50.036
2021-08-03 | 10:05 | 50.035
2021-08-03 | 10:05 | 50.032
2021-08-03 | 10:05 | 50.028
2021-08-03 | 10:05 | 50.026
2021-08-03 | 10:05 | 50.024
2021-08-03 | 10:05 | 50.023
2021-08-03 | 10:05 | 50.022
2021-08-03 | 10:05 | 50.022
2021-08-03 | 10:05 | 50.021
2021-08-03 | 10:05 | 50.019
2021-08-03 | 10:05 | 50.016
2021-08-03 | 10:05 | 50.013
2021-08-03 | 10:05 | 50.009
2021-08-03 | 10:05 | 50.005
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.002
2021-08-03 | 10:05 | 50.004
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.004
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.004
2021-08-03 | 10:05 | 50.003
2021-08-03 | 10:05 | 50.001
2021-08-03 | 10:05 | 49.999
2021-08-03 | 10:05 | 49.995
2021-08-03 | 10:05 | 49.984
2021-08-03 | 10:05 | 49.956
2021-08-03 | 10:05 | 49.931
2021-08-03 | 10:05 | 49.912
2021-08-03 | 10:05 | 49.898
2021-08-03 | 10:05 | 49.889
2021-08-03 | 10:05 | 49.882
2021-08-03 | 10:05 | 49.878
2021-08-03 | 10:05 | 49.876
2021-08-03 | 10:05 | 49.875
2021-08-03 | 10:05 | 49.878
2021-08-03 | 10:05 | 49.882
2021-08-03 | 10:06 | 49.886
2021-08-03 | 10:06 | 49.89
2021-08-03 | 10:06 | 49.893
2021-08-03 | 10:06 | 49.897
2021-08-03 | 10:06 | 49.901
2021-08-03 | 10:06 | 49.902
2021-08-03 | 10:06 | 49.903
2021-08-03 | 10:06 | 49.907
2021-08-03 | 10:06 | 49.91
2021-08-03 | 10:06 | 49.91
2021-08-03 | 10:06 | 49.911
2021-08-03 | 10:06 | 49.909
2021-08-03 | 10:06 | 49.908
2021-08-03 | 10:06 | 49.907
2021-08-03 | 10:06 | 49.906
2021-08-03 | 10:06 | 49.904
2021-08-03 | 10:06 | 49.903
2021-08-03 | 10:06 | 49.902
2021-08-03 | 10:06 | 49.898
2021-08-03 | 10:06 | 49.896
2021-08-03 | 10:06 | 49.896
2021-08-03 | 10:06 | 49.897
2021-08-03 | 10:06 | 49.899
2021-08-03 | 10:06 | 49.899
2021-08-03 | 10:06 | 49.898
2021-08-03 | 10:06 | 49.897
2021-08-03 | 10:06 | 49.894
2021-08-03 | 10:06 | 49.892
2021-08-03 | 10:06 | 49.89
2021-08-03 | 10:06 | 49.888
2021-08-03 | 10:06 | 49.884
2021-08-03 | 10:06 | 49.88
2021-08-03 | 10:06 | 49.877
2021-08-03 | 10:06 | 49.875
2021-08-03 | 10:06 | 49.876
2021-08-03 | 10:06 | 49.876
2021-08-03 | 10:06 | 49.875
2021-08-03 | 10:06 | 49.877
2021-08-03 | 10:06 | 49.875
2021-08-03 | 10:06 | 49.873
2021-08-03 | 10:06 | 49.871
2021-08-03 | 10:06 | 49.868
2021-08-03 | 10:06 | 49.864
2021-08-03 | 10:06 | 49.861
2021-08-03 | 10:06 | 49.856
2021-08-03 | 10:06 | 49.852
2021-08-03 | 10:06 | 49.851
2021-08-03 | 10:06 | 49.851
2021-08-03 | 10:06 | 49.852
2021-08-03 | 10:06 | 49.853
2021-08-03 | 10:06 | 49.853
2021-08-03 | 10:06 | 49.852
2021-08-03 | 10:06 | 49.856
2021-08-03 | 10:06 | 49.856
2021-08-03 | 10:06 | 49.861
2021-08-03 | 10:06 | 49.865
2021-08-03 | 10:06 | 49.869
2021-08-03 | 10:06 | 49.873
2021-08-03 | 10:06 | 49.875
2021-08-03 | 10:06 | 49.877
2021-08-03 | 10:06 | 49.878
2021-08-03 | 10:07 | 49.875
2021-08-03 | 10:07 | 49.875
2021-08-03 | 10:07 | 49.872
2021-08-03 | 10:07 | 49.871
2021-08-03 | 10:07 | 49.871
2021-08-03 | 10:07 | 49.871
2021-08-03 | 10:07 | 49.873
2021-08-03 | 10:07 | 49.877
2021-08-03 | 10:07 | 49.879
2021-08-03 | 10:07 | 49.883
2021-08-03 | 10:07 | 49.884
2021-08-03 | 10:07 | 49.886
2021-08-03 | 10:07 | 49.886
2021-08-03 | 10:07 | 49.885
2021-08-03 | 10:07 | 49.884
2021-08-03 | 10:07 | 49.884
2021-08-03 | 10:07 | 49.883
2021-08-03 | 10:07 | 49.885
2021-08-03 | 10:07 | 49.887
2021-08-03 | 10:07 | 49.891
2021-08-03 | 10:07 | 49.893
2021-08-03 | 10:07 | 49.897
2021-08-03 | 10:07 | 49.902
2021-08-03 | 10:07 | 49.905
2021-08-03 | 10:07 | 49.908
2021-08-03 | 10:07 | 49.909
2021-08-03 | 10:07 | 49.911
2021-08-03 | 10:07 | 49.915
2021-08-03 | 10:07 | 49.916
2021-08-03 | 10:07 | 49.918
2021-08-03 | 10:07 | 49.916
2021-08-03 | 10:07 | 49.916
2021-08-03 | 10:07 | 49.917
2021-08-03 | 10:07 | 49.916
2021-08-03 | 10:07 | 49.917
2021-08-03 | 10:07 | 49.918
2021-08-03 | 10:07 | 49.921
2021-08-03 | 10:07 | 49.923
2021-08-03 | 10:07 | 49.925
2021-08-03 | 10:07 | 49.928
2021-08-03 | 10:07 | 49.931
2021-08-03 | 10:07 | 49.936
2021-08-03 | 10:07 | 49.938
2021-08-03 | 10:07 | 49.939
2021-08-03 | 10:07 | 49.94
2021-08-03 | 10:07 | 49.942
2021-08-03 | 10:07 | 49.943
2021-08-03 | 10:07 | 49.944
2021-08-03 | 10:07 | 49.946
2021-08-03 | 10:07 | 49.947
2021-08-03 | 10:07 | 49.947
2021-08-03 | 10:07 | 49.947
2021-08-03 | 10:07 | 49.945
2021-08-03 | 10:07 | 49.942
2021-08-03 | 10:07 | 49.941
2021-08-03 | 10:07 | 49.942
2021-08-03 | 10:07 | 49.942
2021-08-03 | 10:07 | 49.944
2021-08-03 | 10:07 | 49.945
2021-08-03 | 10:08 | 49.949
2021-08-03 | 10:08 | 49.95
2021-08-03 | 10:08 | 49.954
2021-08-03 | 10:08 | 49.955
2021-08-03 | 10:08 | 49.955
2021-08-03 | 10:08 | 49.958
2021-08-03 | 10:08 | 49.959
2021-08-03 | 10:08 | 49.961
2021-08-03 | 10:08 | 49.965
2021-08-03 | 10:08 | 49.966
2021-08-03 | 10:08 | 49.967
2021-08-03 | 10:08 | 49.968
2021-08-03 | 10:08 | 49.971
2021-08-03 | 10:08 | 49.973
2021-08-03 | 10:08 | 49.974
2021-08-03 | 10:08 | 49.977
2021-08-03 | 10:08 | 49.98
2021-08-03 | 10:08 | 49.98
2021-08-03 | 10:08 | 49.979
2021-08-03 | 10:08 | 49.98
2021-08-03 | 10:08 | 49.98
2021-08-03 | 10:08 | 49.978
2021-08-03 | 10:08 | 49.977
2021-08-03 | 10:08 | 49.976
2021-08-03 | 10:08 | 49.974
2021-08-03 | 10:08 | 49.971
2021-08-03 | 10:08 | 49.971
2021-08-03 | 10:08 | 49.971
2021-08-03 | 10:08 | 49.97
2021-08-03 | 10:08 | 49.97
2021-08-03 | 10:08 | 49.97
2021-08-03 | 10:08 | 49.97
2021-08-03 | 10:08 | 49.969
2021-08-03 | 10:08 | 49.97
2021-08-03 | 10:08 | 49.973
2021-08-03 | 10:08 | 49.974
2021-08-03 | 10:08 | 49.976
2021-08-03 | 10:08 | 49.977
2021-08-03 | 10:08 | 49.981
2021-08-03 | 10:08 | 49.982
2021-08-03 | 10:08 | 49.985
2021-08-03 | 10:08 | 49.987
2021-08-03 | 10:08 | 49.989
2021-08-03 | 10:08 | 49.99
2021-08-03 | 10:08 | 49.991
2021-08-03 | 10:08 | 49.992
2021-08-03 | 10:08 | 49.989
2021-08-03 | 10:08 | 49.989
2021-08-03 | 10:08 | 49.987
2021-08-03 | 10:08 | 49.986
2021-08-03 | 10:08 | 49.986
2021-08-03 | 10:08 | 49.986
2021-08-03 | 10:08 | 49.985
2021-08-03 | 10:08 | 49.985
2021-08-03 | 10:08 | 49.988
2021-08-03 | 10:08 | 49.989
2021-08-03 | 10:08 | 49.992
2021-08-03 | 10:08 | 49.994
2021-08-03 | 10:08 | 49.996
2021-08-03 | 10:08 | 49.998
2021-08-03 | 10:09 | 49.999
2021-08-03 | 10:09 | 50
2021-08-03 | 10:09 | 50.004
2021-08-03 | 10:09 | 50.005
2021-08-03 | 10:09 | 50.006
2021-08-03 | 10:09 | 50.007
2021-08-03 | 10:09 | 50.009
2021-08-03 | 10:09 | 50.007
2021-08-03 | 10:09 | 50.007
2021-08-03 | 10:09 | 50.008
2021-08-03 | 10:09 | 50.01
2021-08-03 | 10:09 | 50.013
2021-08-03 | 10:09 | 50.015
2021-08-03 | 10:09 | 50.017
2021-08-03 | 10:09 | 50.016
2021-08-03 | 10:09 | 50.015
2021-08-03 | 10:09 | 50.014
2021-08-03 | 10:09 | 50.012
2021-08-03 | 10:09 | 50.011
2021-08-03 | 10:09 | 50.01
2021-08-03 | 10:09 | 50.011
2021-08-03 | 10:09 | 50.009
2021-08-03 | 10:09 | 50.009
2021-08-03 | 10:09 | 50.009
2021-08-03 | 10:09 | 50.007
2021-08-03 | 10:09 | 50.004
2021-08-03 | 10:09 | 50.001
2021-08-03 | 10:09 | 49.997
2021-08-03 | 10:09 | 49.995
2021-08-03 | 10:09 | 49.993

## 20210817-1
In GMT
Date | Time | Freq
2021-08-17 | 18:03 | 50.017
2021-08-17 | 18:03 | 50.015
2021-08-17 | 18:03 | 50.014
2021-08-17 | 18:03 | 50.011
2021-08-17 | 18:03 | 50.012
2021-08-17 | 18:03 | 50.011
2021-08-17 | 18:03 | 50.012
2021-08-17 | 18:03 | 50.009
2021-08-17 | 18:03 | 50.007
2021-08-17 | 18:03 | 50.007
2021-08-17 | 18:03 | 50.007
2021-08-17 | 18:03 | 50.009
2021-08-17 | 18:03 | 50.011
2021-08-17 | 18:03 | 50.013
2021-08-17 | 18:03 | 50.016
2021-08-17 | 18:03 | 50.017
2021-08-17 | 18:03 | 50.016
2021-08-17 | 18:03 | 50.014
2021-08-17 | 18:03 | 50.01
2021-08-17 | 18:03 | 50.008
2021-08-17 | 18:03 | 50.003
2021-08-17 | 18:03 | 50.001
2021-08-17 | 18:03 | 49.996
2021-08-17 | 18:03 | 49.991
2021-08-17 | 18:03 | 49.987
2021-08-17 | 18:03 | 49.986
2021-08-17 | 18:03 | 49.986
2021-08-17 | 18:03 | 49.988
2021-08-17 | 18:03 | 49.989
2021-08-17 | 18:03 | 49.991
2021-08-17 | 18:04 | 49.993
2021-08-17 | 18:04 | 49.994
2021-08-17 | 18:04 | 49.995
2021-08-17 | 18:04 | 49.996
2021-08-17 | 18:04 | 49.995
2021-08-17 | 18:04 | 49.996
2021-08-17 | 18:04 | 49.995
2021-08-17 | 18:04 | 49.994
2021-08-17 | 18:04 | 49.993
2021-08-17 | 18:04 | 49.992
2021-08-17 | 18:04 | 49.992
2021-08-17 | 18:04 | 49.994
2021-08-17 | 18:04 | 49.994
2021-08-17 | 18:04 | 49.996
2021-08-17 | 18:04 | 49.997
2021-08-17 | 18:04 | 49.998
2021-08-17 | 18:04 | 49.998
2021-08-17 | 18:04 | 50
2021-08-17 | 18:04 | 50.003
2021-08-17 | 18:04 | 50.006
2021-08-17 | 18:04 | 50.009
2021-08-17 | 18:04 | 50.011
2021-08-17 | 18:04 | 50.012
2021-08-17 | 18:04 | 50.013
2021-08-17 | 18:04 | 50.014
2021-08-17 | 18:04 | 50.015
2021-08-17 | 18:04 | 50.014
2021-08-17 | 18:04 | 50.014
2021-08-17 | 18:04 | 50.014
2021-08-17 | 18:04 | 50.01
2021-08-17 | 18:04 | 50.009
2021-08-17 | 18:04 | 50.006
2021-08-17 | 18:04 | 50.002
2021-08-17 | 18:04 | 49.996
2021-08-17 | 18:04 | 49.991
2021-08-17 | 18:04 | 49.986
2021-08-17 | 18:04 | 49.98
2021-08-17 | 18:04 | 49.979
2021-08-17 | 18:04 | 49.981
2021-08-17 | 18:04 | 49.986
2021-08-17 | 18:04 | 49.987
2021-08-17 | 18:04 | 49.988
2021-08-17 | 18:04 | 49.993
2021-08-17 | 18:04 | 49.996
2021-08-17 | 18:04 | 49.999
2021-08-17 | 18:04 | 50.001
2021-08-17 | 18:04 | 50.004
2021-08-17 | 18:04 | 50.005
2021-08-17 | 18:04 | 50.011
2021-08-17 | 18:04 | 50.018
2021-08-17 | 18:04 | 50.023
2021-08-17 | 18:04 | 50.024
2021-08-17 | 18:04 | 50.026
2021-08-17 | 18:04 | 50.027
2021-08-17 | 18:04 | 50.027
2021-08-17 | 18:04 | 50.027
2021-08-17 | 18:04 | 50.025
2021-08-17 | 18:04 | 50.024
2021-08-17 | 18:04 | 50.026
2021-08-17 | 18:04 | 50.027
2021-08-17 | 18:04 | 50.027
2021-08-17 | 18:05 | 50.027
2021-08-17 | 18:05 | 50.024
2021-08-17 | 18:05 | 50.021
2021-08-17 | 18:05 | 50.015
2021-08-17 | 18:05 | 50.01
2021-08-17 | 18:05 | 50.004
2021-08-17 | 18:05 | 49.997
2021-08-17 | 18:05 | 49.994
2021-08-17 | 18:05 | 49.992
2021-08-17 | 18:05 | 49.993
2021-08-17 | 18:05 | 49.993
2021-08-17 | 18:05 | 49.995
2021-08-17 | 18:05 | 49.996
2021-08-17 | 18:05 | 49.998
2021-08-17 | 18:05 | 50.001
2021-08-17 | 18:05 | 50.005
2021-08-17 | 18:05 | 50.01
2021-08-17 | 18:05 | 50.013
2021-08-17 | 18:05 | 50.016
2021-08-17 | 18:05 | 50.019
2021-08-17 | 18:05 | 50.019
2021-08-17 | 18:05 | 50.02
2021-08-17 | 18:05 | 50.02
2021-08-17 | 18:05 | 50.019
2021-08-17 | 18:05 | 50.019
2021-08-17 | 18:05 | 50.016
2021-08-17 | 18:05 | 49.982
2021-08-17 | 18:05 | 49.932
2021-08-17 | 18:05 | 49.891
2021-08-17 | 18:05 | 49.863
2021-08-17 | 18:05 | 49.847
2021-08-17 | 18:05 | 49.84
2021-08-17 | 18:05 | 49.838
2021-08-17 | 18:05 | 49.837
2021-08-17 | 18:05 | 49.838
2021-08-17 | 18:05 | 49.839
2021-08-17 | 18:05 | 49.843
2021-08-17 | 18:05 | 49.847
2021-08-17 | 18:05 | 49.852
2021-08-17 | 18:05 | 49.855
2021-08-17 | 18:05 | 49.856
2021-08-17 | 18:05 | 49.855
2021-08-17 | 18:05 | 49.856
2021-08-17 | 18:05 | 49.857
2021-08-17 | 18:05 | 49.854
2021-08-17 | 18:05 | 49.852
2021-08-17 | 18:05 | 49.85
2021-08-17 | 18:05 | 49.848
2021-08-17 | 18:05 | 49.842
2021-08-17 | 18:05 | 49.838
2021-08-17 | 18:05 | 49.836
2021-08-17 | 18:05 | 49.836
2021-08-17 | 18:05 | 49.838
2021-08-17 | 18:05 | 49.839
2021-08-17 | 18:05 | 49.837
2021-08-17 | 18:05 | 49.834
2021-08-17 | 18:05 | 49.833
2021-08-17 | 18:05 | 49.831
2021-08-17 | 18:05 | 49.829
2021-08-17 | 18:06 | 49.825
2021-08-17 | 18:06 | 49.82
2021-08-17 | 18:06 | 49.816
2021-08-17 | 18:06 | 49.812
2021-08-17 | 18:06 | 49.809
2021-08-17 | 18:06 | 49.808
2021-08-17 | 18:06 | 49.807
2021-08-17 | 18:06 | 49.805
2021-08-17 | 18:06 | 49.804
2021-08-17 | 18:06 | 49.804
2021-08-17 | 18:06 | 49.802
2021-08-17 | 18:06 | 49.804
2021-08-17 | 18:06 | 49.807
2021-08-17 | 18:06 | 49.807
2021-08-17 | 18:06 | 49.811
2021-08-17 | 18:06 | 49.813
2021-08-17 | 18:06 | 49.819
2021-08-17 | 18:06 | 49.824
2021-08-17 | 18:06 | 49.83
2021-08-17 | 18:06 | 49.834
2021-08-17 | 18:06 | 49.836
2021-08-17 | 18:06 | 49.836
2021-08-17 | 18:06 | 49.838
2021-08-17 | 18:06 | 49.84
2021-08-17 | 18:06 | 49.839
2021-08-17 | 18:06 | 49.838
2021-08-17 | 18:06 | 49.837
2021-08-17 | 18:06 | 49.837
2021-08-17 | 18:06 | 49.84
2021-08-17 | 18:06 | 49.838
2021-08-17 | 18:06 | 49.838
2021-08-17 | 18:06 | 49.838
2021-08-17 | 18:06 | 49.838
2021-08-17 | 18:06 | 49.841
2021-08-17 | 18:06 | 49.846
2021-08-17 | 18:06 | 49.854
2021-08-17 | 18:06 | 49.862
2021-08-17 | 18:06 | 49.869
2021-08-17 | 18:06 | 49.875
2021-08-17 | 18:06 | 49.878
2021-08-17 | 18:06 | 49.883
2021-08-17 | 18:06 | 49.89
2021-08-17 | 18:06 | 49.896
2021-08-17 | 18:06 | 49.904
2021-08-17 | 18:06 | 49.91
2021-08-17 | 18:06 | 49.914
2021-08-17 | 18:06 | 49.919
2021-08-17 | 18:06 | 49.923
2021-08-17 | 18:06 | 49.927
2021-08-17 | 18:06 | 49.93
2021-08-17 | 18:06 | 49.934
2021-08-17 | 18:06 | 49.935
2021-08-17 | 18:06 | 49.937
2021-08-17 | 18:06 | 49.939
2021-08-17 | 18:06 | 49.941
2021-08-17 | 18:06 | 49.941
2021-08-17 | 18:06 | 49.938
2021-08-17 | 18:06 | 49.937
2021-08-17 | 18:06 | 49.925
2021-08-17 | 18:06 | 49.939
2021-08-17 | 18:06 | 49.941
2021-08-17 | 18:07 | 49.941
2021-08-17 | 18:07 | 49.94
2021-08-17 | 18:07 | 49.939
2021-08-17 | 18:07 | 49.94
2021-08-17 | 18:07 | 49.937
2021-08-17 | 18:07 | 49.934
2021-08-17 | 18:07 | 49.93
2021-08-17 | 18:07 | 49.926
2021-08-17 | 18:07 | 49.924
2021-08-17 | 18:07 | 49.924
2021-08-17 | 18:07 | 49.925
2021-08-17 | 18:07 | 49.927
2021-08-17 | 18:07 | 49.924
2021-08-17 | 18:07 | 49.924
2021-08-17 | 18:07 | 49.922
2021-08-17 | 18:07 | 49.922
2021-08-17 | 18:07 | 49.919
2021-08-17 | 18:07 | 49.917
2021-08-17 | 18:07 | 49.914
2021-08-17 | 18:07 | 49.91
2021-08-17 | 18:07 | 49.905
2021-08-17 | 18:07 | 49.904
2021-08-17 | 18:07 | 49.904
2021-08-17 | 18:07 | 49.908
2021-08-17 | 18:07 | 49.914
2021-08-17 | 18:07 | 49.922
2021-08-17 | 18:07 | 49.927
2021-08-17 | 18:07 | 49.933
2021-08-17 | 18:07 | 49.937
2021-08-17 | 18:07 | 49.938
2021-08-17 | 18:07 | 49.939
2021-08-17 | 18:07 | 49.943
2021-08-17 | 18:07 | 49.948
2021-08-17 | 18:07 | 49.952
2021-08-17 | 18:07 | 49.954
2021-08-17 | 18:07 | 49.955
2021-08-17 | 18:07 | 49.952
2021-08-17 | 18:07 | 49.95
2021-08-17 | 18:07 | 49.947
2021-08-17 | 18:07 | 49.946
2021-08-17 | 18:07 | 49.942
2021-08-17 | 18:07 | 49.942
2021-08-17 | 18:07 | 49.941
2021-08-17 | 18:07 | 49.94
2021-08-17 | 18:07 | 49.942
2021-08-17 | 18:07 | 49.946
2021-08-17 | 18:07 | 49.947
2021-08-17 | 18:07 | 49.948
2021-08-17 | 18:07 | 49.95
2021-08-17 | 18:07 | 49.95
2021-08-17 | 18:07 | 49.952
2021-08-17 | 18:07 | 49.95
2021-08-17 | 18:07 | 49.95
2021-08-17 | 18:07 | 49.954
2021-08-17 | 18:07 | 49.955
2021-08-17 | 18:07 | 49.957
2021-08-17 | 18:07 | 49.959
2021-08-17 | 18:07 | 49.962
2021-08-17 | 18:07 | 49.964
2021-08-17 | 18:08 | 49.964
2021-08-17 | 18:08 | 49.964
2021-08-17 | 18:08 | 49.963
2021-08-17 | 18:08 | 49.963
2021-08-17 | 18:08 | 49.965
2021-08-17 | 18:08 | 49.968
2021-08-17 | 18:08 | 49.972
2021-08-17 | 18:08 | 49.977
2021-08-17 | 18:08 | 49.98
2021-08-17 | 18:08 | 49.985
2021-08-17 | 18:08 | 49.983
2021-08-17 | 18:08 | 49.984
2021-08-17 | 18:08 | 49.981
2021-08-17 | 18:08 | 49.98
2021-08-17 | 18:08 | 49.976
2021-08-17 | 18:08 | 49.975
2021-08-17 | 18:08 | 49.976
2021-08-17 | 18:08 | 49.976
2021-08-17 | 18:08 | 49.979
2021-08-17 | 18:08 | 49.982
2021-08-17 | 18:08 | 49.985
2021-08-17 | 18:08 | 49.988
2021-08-17 | 18:08 | 49.991
2021-08-17 | 18:08 | 49.995
2021-08-17 | 18:08 | 49.999
2021-08-17 | 18:08 | 50.005
2021-08-17 | 18:08 | 50.007
2021-08-17 | 18:08 | 50.01
2021-08-17 | 18:08 | 50.009
2021-08-17 | 18:08 | 50.008

## 20210819-1
In GMT
Date | Time | Freq
2021-08-19 | 8:13 | 49.943
2021-08-19 | 8:13 | 49.942
2021-08-19 | 8:13 | 49.942
2021-08-19 | 8:13 | 49.943
2021-08-19 | 8:13 | 49.944
2021-08-19 | 8:13 | 49.943
2021-08-19 | 8:13 | 49.943
2021-08-19 | 8:13 | 49.943
2021-08-19 | 8:13 | 49.941
2021-08-19 | 8:13 | 49.939
2021-08-19 | 8:13 | 49.937
2021-08-19 | 8:13 | 49.935
2021-08-19 | 8:13 | 49.934
2021-08-19 | 8:13 | 49.931
2021-08-19 | 8:13 | 49.933
2021-08-19 | 8:13 | 49.93
2021-08-19 | 8:13 | 49.931
2021-08-19 | 8:13 | 49.932
2021-08-19 | 8:13 | 49.932
2021-08-19 | 8:13 | 49.929
2021-08-19 | 8:13 | 49.929
2021-08-19 | 8:13 | 49.93
2021-08-19 | 8:13 | 49.928
2021-08-19 | 8:13 | 49.932
2021-08-19 | 8:13 | 49.936
2021-08-19 | 8:13 | 49.937
2021-08-19 | 8:13 | 49.937
2021-08-19 | 8:13 | 49.939
2021-08-19 | 8:13 | 49.94
2021-08-19 | 8:13 | 49.944
2021-08-19 | 8:14 | 49.946
2021-08-19 | 8:14 | 49.95
2021-08-19 | 8:14 | 49.953
2021-08-19 | 8:14 | 49.952
2021-08-19 | 8:14 | 49.952
2021-08-19 | 8:14 | 49.95
2021-08-19 | 8:14 | 49.949
2021-08-19 | 8:14 | 49.947
2021-08-19 | 8:14 | 49.947
2021-08-19 | 8:14 | 49.947
2021-08-19 | 8:14 | 49.948
2021-08-19 | 8:14 | 49.947
2021-08-19 | 8:14 | 49.945
2021-08-19 | 8:14 | 49.944
2021-08-19 | 8:14 | 49.943
2021-08-19 | 8:14 | 49.944
2021-08-19 | 8:14 | 49.946
2021-08-19 | 8:14 | 49.946
2021-08-19 | 8:14 | 49.947
2021-08-19 | 8:14 | 49.947
2021-08-19 | 8:14 | 49.949
2021-08-19 | 8:14 | 49.95
2021-08-19 | 8:14 | 49.949
2021-08-19 | 8:14 | 49.948
2021-08-19 | 8:14 | 49.943
2021-08-19 | 8:14 | 49.941
2021-08-19 | 8:14 | 49.938
2021-08-19 | 8:14 | 49.932
2021-08-19 | 8:14 | 49.929
2021-08-19 | 8:14 | 49.928
2021-08-19 | 8:14 | 49.929
2021-08-19 | 8:14 | 49.927
2021-08-19 | 8:14 | 49.928
2021-08-19 | 8:14 | 49.929
2021-08-19 | 8:14 | 49.929
2021-08-19 | 8:14 | 49.93
2021-08-19 | 8:14 | 49.928
2021-08-19 | 8:14 | 49.928
2021-08-19 | 8:14 | 49.929
2021-08-19 | 8:14 | 49.93
2021-08-19 | 8:14 | 49.933
2021-08-19 | 8:14 | 49.936
2021-08-19 | 8:14 | 49.938
2021-08-19 | 8:14 | 49.942
2021-08-19 | 8:14 | 49.946
2021-08-19 | 8:14 | 49.95
2021-08-19 | 8:14 | 49.953
2021-08-19 | 8:14 | 49.954
2021-08-19 | 8:14 | 49.957
2021-08-19 | 8:14 | 49.955
2021-08-19 | 8:14 | 49.954
2021-08-19 | 8:14 | 49.952
2021-08-19 | 8:14 | 49.949
2021-08-19 | 8:14 | 49.949
2021-08-19 | 8:14 | 49.948
2021-08-19 | 8:14 | 49.952
2021-08-19 | 8:14 | 49.952
2021-08-19 | 8:14 | 49.932
2021-08-19 | 8:14 | 49.896
2021-08-19 | 8:14 | 49.86
2021-08-19 | 8:14 | 49.832
2021-08-19 | 8:15 | 49.811
2021-08-19 | 8:15 | 49.799
2021-08-19 | 8:15 | 49.793
2021-08-19 | 8:15 | 49.794
2021-08-19 | 8:15 | 49.797
2021-08-19 | 8:15 | 49.804
2021-08-19 | 8:15 | 49.806
2021-08-19 | 8:15 | 49.811
2021-08-19 | 8:15 | 49.815
2021-08-19 | 8:15 | 49.82
2021-08-19 | 8:15 | 49.818
2021-08-19 | 8:15 | 49.817
2021-08-19 | 8:15 | 49.813
2021-08-19 | 8:15 | 49.814
2021-08-19 | 8:15 | 49.811
2021-08-19 | 8:15 | 49.814
2021-08-19 | 8:15 | 49.818
2021-08-19 | 8:15 | 49.829
2021-08-19 | 8:15 | 49.84
2021-08-19 | 8:15 | 49.856
2021-08-19 | 8:15 | 49.869
2021-08-19 | 8:15 | 49.886
2021-08-19 | 8:15 | 49.901
2021-08-19 | 8:15 | 49.917
2021-08-19 | 8:15 | 49.927
2021-08-19 | 8:15 | 49.934
2021-08-19 | 8:15 | 49.933
2021-08-19 | 8:15 | 49.934
2021-08-19 | 8:15 | 49.929
2021-08-19 | 8:15 | 49.922
2021-08-19 | 8:15 | 49.91
2021-08-19 | 8:15 | 49.895
2021-08-19 | 8:15 | 49.877
2021-08-19 | 8:15 | 49.864
2021-08-19 | 8:15 | 49.858
2021-08-19 | 8:15 | 49.857
2021-08-19 | 8:15 | 49.859
2021-08-19 | 8:15 | 49.866
2021-08-19 | 8:15 | 49.874
2021-08-19 | 8:15 | 49.878
2021-08-19 | 8:15 | 49.883
2021-08-19 | 8:15 | 49.888
2021-08-19 | 8:15 | 49.892
2021-08-19 | 8:15 | 49.892
2021-08-19 | 8:15 | 49.896
2021-08-19 | 8:15 | 49.896
2021-08-19 | 8:15 | 49.897
2021-08-19 | 8:15 | 49.897
2021-08-19 | 8:15 | 49.896
2021-08-19 | 8:15 | 49.898
2021-08-19 | 8:15 | 49.898
2021-08-19 | 8:15 | 49.901
2021-08-19 | 8:15 | 49.898
2021-08-19 | 8:15 | 49.897
2021-08-19 | 8:15 | 49.895
2021-08-19 | 8:15 | 49.894
2021-08-19 | 8:15 | 49.893
2021-08-19 | 8:15 | 49.895
2021-08-19 | 8:15 | 49.894
2021-08-19 | 8:16 | 49.898
2021-08-19 | 8:16 | 49.898
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.893
2021-08-19 | 8:16 | 49.891
2021-08-19 | 8:16 | 49.886
2021-08-19 | 8:16 | 49.887
2021-08-19 | 8:16 | 49.884
2021-08-19 | 8:16 | 49.884
2021-08-19 | 8:16 | 49.881
2021-08-19 | 8:16 | 49.879
2021-08-19 | 8:16 | 49.878
2021-08-19 | 8:16 | 49.877
2021-08-19 | 8:16 | 49.879
2021-08-19 | 8:16 | 49.881
2021-08-19 | 8:16 | 49.88
2021-08-19 | 8:16 | 49.88
2021-08-19 | 8:16 | 49.88
2021-08-19 | 8:16 | 49.883
2021-08-19 | 8:16 | 49.883
2021-08-19 | 8:16 | 49.885
2021-08-19 | 8:16 | 49.885
2021-08-19 | 8:16 | 49.888
2021-08-19 | 8:16 | 49.888
2021-08-19 | 8:16 | 49.888
2021-08-19 | 8:16 | 49.888
2021-08-19 | 8:16 | 49.887
2021-08-19 | 8:16 | 49.889
2021-08-19 | 8:16 | 49.889
2021-08-19 | 8:16 | 49.891
2021-08-19 | 8:16 | 49.893
2021-08-19 | 8:16 | 49.893
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.892
2021-08-19 | 8:16 | 49.893
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.897
2021-08-19 | 8:16 | 49.897
2021-08-19 | 8:16 | 49.895
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.891
2021-08-19 | 8:16 | 49.891
2021-08-19 | 8:16 | 49.891
2021-08-19 | 8:16 | 49.889
2021-08-19 | 8:16 | 49.89
2021-08-19 | 8:16 | 49.893
2021-08-19 | 8:16 | 49.893
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.894
2021-08-19 | 8:16 | 49.897
2021-08-19 | 8:16 | 49.9
2021-08-19 | 8:16 | 49.904
2021-08-19 | 8:16 | 49.906
2021-08-19 | 8:16 | 49.905
2021-08-19 | 8:16 | 49.903
2021-08-19 | 8:16 | 49.904
2021-08-19 | 8:16 | 49.903
2021-08-19 | 8:16 | 49.901
2021-08-19 | 8:17 | 49.904
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.905
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.913
2021-08-19 | 8:17 | 49.915
2021-08-19 | 8:17 | 49.916
2021-08-19 | 8:17 | 49.917
2021-08-19 | 8:17 | 49.918
2021-08-19 | 8:17 | 49.919
2021-08-19 | 8:17 | 49.917
2021-08-19 | 8:17 | 49.917
2021-08-19 | 8:17 | 49.917
2021-08-19 | 8:17 | 49.915
2021-08-19 | 8:17 | 49.911
2021-08-19 | 8:17 | 49.908
2021-08-19 | 8:17 | 49.908
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.908
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.905
2021-08-19 | 8:17 | 49.904
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.907
2021-08-19 | 8:17 | 49.907
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.907
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.911
2021-08-19 | 8:17 | 49.912
2021-08-19 | 8:17 | 49.913
2021-08-19 | 8:17 | 49.913
2021-08-19 | 8:17 | 49.913
2021-08-19 | 8:17 | 49.913
2021-08-19 | 8:17 | 49.912
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.909
2021-08-19 | 8:17 | 49.908
2021-08-19 | 8:17 | 49.906
2021-08-19 | 8:17 | 49.905
2021-08-19 | 8:17 | 49.908
2021-08-19 | 8:17 | 49.91
2021-08-19 | 8:17 | 49.911
2021-08-19 | 8:17 | 49.912
2021-08-19 | 8:17 | 49.912
2021-08-19 | 8:18 | 49.912
2021-08-19 | 8:18 | 49.911
2021-08-19 | 8:18 | 49.91
2021-08-19 | 8:18 | 49.905
2021-08-19 | 8:18 | 49.899
2021-08-19 | 8:18 | 49.896
2021-08-19 | 8:18 | 49.894
2021-08-19 | 8:18 | 49.892
2021-08-19 | 8:18 | 49.89
2021-08-19 | 8:18 | 49.89
2021-08-19 | 8:18 | 49.889
2021-08-19 | 8:18 | 49.892
2021-08-19 | 8:18 | 49.893
2021-08-19 | 8:18 | 49.895
2021-08-19 | 8:18 | 49.898
2021-08-19 | 8:18 | 49.901
2021-08-19 | 8:18 | 49.906
2021-08-19 | 8:18 | 49.907
2021-08-19 | 8:18 | 49.91
2021-08-19 | 8:18 | 49.911
2021-08-19 | 8:18 | 49.913
2021-08-19 | 8:18 | 49.915
2021-08-19 | 8:18 | 49.918
2021-08-19 | 8:18 | 49.916
2021-08-19 | 8:18 | 49.915
2021-08-19 | 8:18 | 49.912
2021-08-19 | 8:18 | 49.91
2021-08-19 | 8:18 | 49.91
2021-08-19 | 8:18 | 49.91
2021-08-19 | 8:18 | 49.911
2021-08-19 | 8:18 | 49.909
2021-08-19 | 8:18 | 49.907
2021-08-19 | 8:18 | 49.903
2021-08-19 | 8:18 | 49.898
2021-08-19 | 8:18 | 49.895
2021-08-19 | 8:18 | 49.893
2021-08-19 | 8:18 | 49.889
2021-08-19 | 8:18 | 49.888
2021-08-19 | 8:18 | 49.885
2021-08-19 | 8:18 | 49.882
2021-08-19 | 8:18 | 49.883
2021-08-19 | 8:18 | 49.884
2021-08-19 | 8:18 | 49.884
2021-08-19 | 8:18 | 49.885
2021-08-19 | 8:18 | 49.887
2021-08-19 | 8:18 | 49.887
2021-08-19 | 8:18 | 49.889
2021-08-19 | 8:18 | 49.888
2021-08-19 | 8:18 | 49.886
2021-08-19 | 8:18 | 49.888
2021-08-19 | 8:18 | 49.893
2021-08-19 | 8:18 | 49.895
2021-08-19 | 8:18 | 49.898
2021-08-19 | 8:18 | 49.898
2021-08-19 | 8:18 | 49.9
2021-08-19 | 8:18 | 49.902
2021-08-19 | 8:18 | 49.904
2021-08-19 | 8:18 | 49.906
2021-08-19 | 8:18 | 49.907
2021-08-19 | 8:18 | 49.911
2021-08-19 | 8:18 | 49.914
2021-08-19 | 8:19 | 49.915
2021-08-19 | 8:19 | 49.914
2021-08-19 | 8:19 | 49.916
2021-08-19 | 8:19 | 49.914
2021-08-19 | 8:19 | 49.916
2021-08-19 | 8:19 | 49.919
2021-08-19 | 8:19 | 49.92
2021-08-19 | 8:19 | 49.924
2021-08-19 | 8:19 | 49.929
2021-08-19 | 8:19 | 49.93
2021-08-19 | 8:19 | 49.93
2021-08-19 | 8:19 | 49.932
2021-08-19 | 8:19 | 49.933
2021-08-19 | 8:19 | 49.933
2021-08-19 | 8:19 | 49.93
2021-08-19 | 8:19 | 49.929
2021-08-19 | 8:19 | 49.927
2021-08-19 | 8:19 | 49.926
2021-08-19 | 8:19 | 49.921
2021-08-19 | 8:19 | 49.919
2021-08-19 | 8:19 | 49.918
2021-08-19 | 8:19 | 49.918
2021-08-19 | 8:19 | 49.92
2021-08-19 | 8:19 | 49.921
2021-08-19 | 8:19 | 49.924
2021-08-19 | 8:19 | 49.925
2021-08-19 | 8:19 | 49.924
2021-08-19 | 8:19 | 49.923
2021-08-19 | 8:19 | 49.923
2021-08-19 | 8:19 | 49.925
2021-08-19 | 8:19 | 49.922
2021-08-19 | 8:19 | 49.92
2021-08-19 | 8:19 | 49.917
2021-08-19 | 8:19 | 49.916
2021-08-19 | 8:19 | 49.915
2021-08-19 | 8:19 | 49.916
2021-08-19 | 8:19 | 49.917
2021-08-19 | 8:19 | 49.919
2021-08-19 | 8:19 | 49.922
2021-08-19 | 8:19 | 49.924
2021-08-19 | 8:19 | 49.925
2021-08-19 | 8:19 | 49.93
2021-08-19 | 8:19 | 49.936
2021-08-19 | 8:19 | 49.939
2021-08-19 | 8:19 | 49.944
2021-08-19 | 8:19 | 49.947
2021-08-19 | 8:19 | 49.95
2021-08-19 | 8:19 | 49.951
2021-08-19 | 8:19 | 49.952
2021-08-19 | 8:19 | 49.955
2021-08-19 | 8:19 | 49.955
2021-08-19 | 8:19 | 49.956
2021-08-19 | 8:19 | 49.954
2021-08-19 | 8:19 | 49.954
2021-08-19 | 8:19 | 49.954
2021-08-19 | 8:19 | 49.951
2021-08-19 | 8:19 | 49.947
2021-08-19 | 8:19 | 49.945
2021-08-19 | 8:19 | 49.941
2021-08-19 | 8:20 | 49.939
2021-08-19 | 8:20 | 49.936
2021-08-19 | 8:20 | 49.938
2021-08-19 | 8:20 | 49.941
2021-08-19 | 8:20 | 49.944
2021-08-19 | 8:20 | 49.947
2021-08-19 | 8:20 | 49.951
2021-08-19 | 8:20 | 49.953
2021-08-19 | 8:20 | 49.956
2021-08-19 | 8:20 | 49.958
2021-08-19 | 8:20 | 49.958
2021-08-19 | 8:20 | 49.96
2021-08-19 | 8:20 | 49.96
2021-08-19 | 8:20 | 49.961
2021-08-19 | 8:20 | 49.963
2021-08-19 | 8:20 | 49.963
2021-08-19 | 8:20 | 49.962
2021-08-19 | 8:20 | 49.96
2021-08-19 | 8:20 | 49.961
2021-08-19 | 8:20 | 49.963
2021-08-19 | 8:20 | 49.963
2021-08-19 | 8:20 | 49.963
2021-08-19 | 8:20 | 49.963
2021-08-19 | 8:20 | 49.957
2021-08-19 | 8:20 | 49.955
2021-08-19 | 8:20 | 49.953
2021-08-19 | 8:20 | 49.955
2021-08-19 | 8:20 | 49.955
2021-08-19 | 8:20 | 49.957
2021-08-19 | 8:20 | 49.96
2021-08-19 | 8:20 | 49.961
2021-08-19 | 8:20 | 49.959
2021-08-19 | 8:20 | 49.957
2021-08-19 | 8:20 | 49.954
2021-08-19 | 8:20 | 49.952
2021-08-19 | 8:20 | 49.95
2021-08-19 | 8:20 | 49.951
2021-08-19 | 8:20 | 49.949
2021-08-19 | 8:20 | 49.95
2021-08-19 | 8:20 | 49.949
2021-08-19 | 8:20 | 49.948
2021-08-19 | 8:20 | 49.947
2021-08-19 | 8:20 | 49.947
2021-08-19 | 8:20 | 49.947
2021-08-19 | 8:20 | 49.947
2021-08-19 | 8:20 | 49.948
2021-08-19 | 8:20 | 49.949
2021-08-19 | 8:20 | 49.948
2021-08-19 | 8:20 | 49.946
2021-08-19 | 8:20 | 49.942
2021-08-19 | 8:20 | 49.938
2021-08-19 | 8:20 | 49.937
2021-08-19 | 8:20 | 49.938
2021-08-19 | 8:20 | 49.938
2021-08-19 | 8:20 | 49.94
2021-08-19 | 8:20 | 49.941
2021-08-19 | 8:20 | 49.945
2021-08-19 | 8:20 | 49.949
2021-08-19 | 8:20 | 49.952
2021-08-19 | 8:20 | 49.95
2021-08-19 | 8:20 | 49.956
2021-08-19 | 8:21 | 49.958
2021-08-19 | 8:21 | 49.96
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.959
2021-08-19 | 8:21 | 49.96
2021-08-19 | 8:21 | 49.962
2021-08-19 | 8:21 | 49.963
2021-08-19 | 8:21 | 49.963
2021-08-19 | 8:21 | 49.964
2021-08-19 | 8:21 | 49.962
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.959
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.959
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.961
2021-08-19 | 8:21 | 49.96
2021-08-19 | 8:21 | 49.963
2021-08-19 | 8:21 | 49.964
2021-08-19 | 8:21 | 49.965
2021-08-19 | 8:21 | 49.967
2021-08-19 | 8:21 | 49.968
2021-08-19 | 8:21 | 49.969
2021-08-19 | 8:21 | 49.971
2021-08-19 | 8:21 | 49.971
2021-08-19 | 8:21 | 49.968
2021-08-19 | 8:21 | 49.964
2021-08-19 | 8:21 | 49.96
2021-08-19 | 8:21 | 49.958
2021-08-19 | 8:21 | 49.952
2021-08-19 | 8:21 | 49.947
2021-08-19 | 8:21 | 49.944
2021-08-19 | 8:21 | 49.942
2021-08-19 | 8:21 | 49.943
2021-08-19 | 8:21 | 49.942
2021-08-19 | 8:21 | 49.946
2021-08-19 | 8:21 | 49.947
2021-08-19 | 8:21 | 49.95
2021-08-19 | 8:21 | 49.951
2021-08-19 | 8:21 | 49.952
2021-08-19 | 8:21 | 49.957
2021-08-19 | 8:21 | 49.965
2021-08-19 | 8:21 | 49.972
2021-08-19 | 8:21 | 49.98
2021-08-19 | 8:21 | 49.988
2021-08-19 | 8:21 | 49.995
2021-08-19 | 8:21 | 50.005
2021-08-19 | 8:21 | 50.016
2021-08-19 | 8:21 | 50.027
2021-08-19 | 8:21 | 50.036
2021-08-19 | 8:21 | 50.045
2021-08-19 | 8:21 | 50.052
2021-08-19 | 8:21 | 50.057
2021-08-19 | 8:21 | 50.061
2021-08-19 | 8:21 | 50.066
2021-08-19 | 8:21 | 50.068
2021-08-19 | 8:21 | 50.07
2021-08-19 | 8:22 | 50.07
2021-08-19 | 8:22 | 50.07
2021-08-19 | 8:22 | 50.07
2021-08-19 | 8:22 | 50.068
2021-08-19 | 8:22 | 50.065
2021-08-19 | 8:22 | 50.063
2021-08-19 | 8:22 | 50.061
2021-08-19 | 8:22 | 50.06
2021-08-19 | 8:22 | 50.053
2021-08-19 | 8:22 | 50.048
2021-08-19 | 8:22 | 50.042
2021-08-19 | 8:22 | 50.035
2021-08-19 | 8:22 | 50.025
2021-08-19 | 8:22 | 50.018
2021-08-19 | 8:22 | 50.007
2021-08-19 | 8:22 | 49.996
2021-08-19 | 8:22 | 49.986
2021-08-19 | 8:22 | 49.974
2021-08-19 | 8:22 | 49.966
2021-08-19 | 8:22 | 49.958
2021-08-19 | 8:22 | 49.955
2021-08-19 | 8:22 | 49.954
2021-08-19 | 8:22 | 49.957
2021-08-19 | 8:22 | 49.959
2021-08-19 | 8:22 | 49.966
2021-08-19 | 8:22 | 49.973
2021-08-19 | 8:22 | 49.982
2021-08-19 | 8:22 | 49.988
2021-08-19 | 8:22 | 49.995
2021-08-19 | 8:22 | 50

## 20210829-1
In GMT
Date | Time | Freq
2021-08-29 | 16:11 | 50.038
2021-08-29 | 16:11 | 50.037
2021-08-29 | 16:11 | 50.034
2021-08-29 | 16:11 | 50.031
2021-08-29 | 16:11 | 50.03
2021-08-29 | 16:11 | 50.028
2021-08-29 | 16:11 | 50.026
2021-08-29 | 16:11 | 50.025
2021-08-29 | 16:11 | 50.026
2021-08-29 | 16:11 | 50.026
2021-08-29 | 16:11 | 50.025
2021-08-29 | 16:11 | 50.025
2021-08-29 | 16:11 | 50.025
2021-08-29 | 16:11 | 50.022
2021-08-29 | 16:11 | 50.018
2021-08-29 | 16:11 | 50.017
2021-08-29 | 16:11 | 50.015
2021-08-29 | 16:11 | 50.011
2021-08-29 | 16:11 | 50.006
2021-08-29 | 16:11 | 50.006
2021-08-29 | 16:11 | 50.009
2021-08-29 | 16:11 | 50.013
2021-08-29 | 16:11 | 50.013
2021-08-29 | 16:11 | 50.016
2021-08-29 | 16:11 | 50.018
2021-08-29 | 16:11 | 50.019
2021-08-29 | 16:11 | 50.023
2021-08-29 | 16:11 | 50.025
2021-08-29 | 16:11 | 50.024
2021-08-29 | 16:11 | 50.024
2021-08-29 | 16:12 | 50.021
2021-08-29 | 16:12 | 50.021
2021-08-29 | 16:12 | 50.019
2021-08-29 | 16:12 | 50.019
2021-08-29 | 16:12 | 50.019
2021-08-29 | 16:12 | 50.019
2021-08-29 | 16:12 | 50.02
2021-08-29 | 16:12 | 50.024
2021-08-29 | 16:12 | 50.026
2021-08-29 | 16:12 | 50.029
2021-08-29 | 16:12 | 50.03
2021-08-29 | 16:12 | 50.032
2021-08-29 | 16:12 | 50.032
2021-08-29 | 16:12 | 50.029
2021-08-29 | 16:12 | 50.028
2021-08-29 | 16:12 | 50.026
2021-08-29 | 16:12 | 50.026
2021-08-29 | 16:12 | 50.021
2021-08-29 | 16:12 | 50.02
2021-08-29 | 16:12 | 50.019
2021-08-29 | 16:12 | 50.019
2021-08-29 | 16:12 | 50.018
2021-08-29 | 16:12 | 50.017
2021-08-29 | 16:12 | 50.016
2021-08-29 | 16:12 | 50.017
2021-08-29 | 16:12 | 50.021
2021-08-29 | 16:12 | 50.026
2021-08-29 | 16:12 | 50.028
2021-08-29 | 16:12 | 50.029
2021-08-29 | 16:12 | 50.029
2021-08-29 | 16:12 | 50.033
2021-08-29 | 16:12 | 50.032
2021-08-29 | 16:12 | 50.033
2021-08-29 | 16:12 | 50.035
2021-08-29 | 16:12 | 50.034
2021-08-29 | 16:12 | 50.037
2021-08-29 | 16:12 | 50.037
2021-08-29 | 16:12 | 50.037
2021-08-29 | 16:12 | 50.035
2021-08-29 | 16:12 | 50.032
2021-08-29 | 16:12 | 50.033
2021-08-29 | 16:12 | 50.031
2021-08-29 | 16:12 | 50.027
2021-08-29 | 16:12 | 50.027
2021-08-29 | 16:12 | 50.026
2021-08-29 | 16:12 | 50.024
2021-08-29 | 16:12 | 50.021
2021-08-29 | 16:12 | 50.02
2021-08-29 | 16:12 | 50.016
2021-08-29 | 16:12 | 50.013
2021-08-29 | 16:12 | 50.012
2021-08-29 | 16:12 | 50.013
2021-08-29 | 16:12 | 50.012
2021-08-29 | 16:12 | 50.013
2021-08-29 | 16:12 | 50.012
2021-08-29 | 16:12 | 50.013
2021-08-29 | 16:12 | 50.01
2021-08-29 | 16:12 | 50.011
2021-08-29 | 16:12 | 50.009
2021-08-29 | 16:12 | 50.011
2021-08-29 | 16:12 | 50.008
2021-08-29 | 16:13 | 50.01
2021-08-29 | 16:13 | 50.014
2021-08-29 | 16:13 | 50.016
2021-08-29 | 16:13 | 50.018
2021-08-29 | 16:13 | 50.021
2021-08-29 | 16:13 | 50.024
2021-08-29 | 16:13 | 50.024
2021-08-29 | 16:13 | 50.025
2021-08-29 | 16:13 | 50.027
2021-08-29 | 16:13 | 50.025
2021-08-29 | 16:13 | 50.027
2021-08-29 | 16:13 | 50.026
2021-08-29 | 16:13 | 50.021
2021-08-29 | 16:13 | 50.017
2021-08-29 | 16:13 | 50.013
2021-08-29 | 16:13 | 50.01
2021-08-29 | 16:13 | 50.004
2021-08-29 | 16:13 | 50
2021-08-29 | 16:13 | 49.997
2021-08-29 | 16:13 | 49.993
2021-08-29 | 16:13 | 49.989
2021-08-29 | 16:13 | 49.983
2021-08-29 | 16:13 | 49.977
2021-08-29 | 16:13 | 49.973
2021-08-29 | 16:13 | 49.972
2021-08-29 | 16:13 | 49.968
2021-08-29 | 16:13 | 49.968
2021-08-29 | 16:13 | 49.967
2021-08-29 | 16:13 | 49.968
2021-08-29 | 16:13 | 49.968
2021-08-29 | 16:13 | 49.967
2021-08-29 | 16:13 | 49.971
2021-08-29 | 16:13 | 49.971
2021-08-29 | 16:13 | 49.974
2021-08-29 | 16:13 | 49.975
2021-08-29 | 16:13 | 49.978
2021-08-29 | 16:13 | 49.984
2021-08-29 | 16:13 | 49.988
2021-08-29 | 16:13 | 49.99
2021-08-29 | 16:13 | 49.99
2021-08-29 | 16:13 | 49.99
2021-08-29 | 16:13 | 49.986
2021-08-29 | 16:13 | 49.985
2021-08-29 | 16:13 | 49.978
2021-08-29 | 16:13 | 49.972
2021-08-29 | 16:13 | 49.966
2021-08-29 | 16:13 | 49.962
2021-08-29 | 16:13 | 49.959
2021-08-29 | 16:13 | 49.962
2021-08-29 | 16:13 | 49.966
2021-08-29 | 16:13 | 49.968
2021-08-29 | 16:13 | 49.969
2021-08-29 | 16:13 | 49.973
2021-08-29 | 16:13 | 49.973
2021-08-29 | 16:13 | 49.974
2021-08-29 | 16:13 | 49.973
2021-08-29 | 16:13 | 49.972
2021-08-29 | 16:13 | 49.97
2021-08-29 | 16:13 | 49.97
2021-08-29 | 16:14 | 49.97
2021-08-29 | 16:14 | 49.97
2021-08-29 | 16:14 | 49.975
2021-08-29 | 16:14 | 49.979
2021-08-29 | 16:14 | 49.98
2021-08-29 | 16:14 | 49.981
2021-08-29 | 16:14 | 49.981
2021-08-29 | 16:14 | 49.981
2021-08-29 | 16:14 | 49.982
2021-08-29 | 16:14 | 49.985
2021-08-29 | 16:14 | 49.986
2021-08-29 | 16:14 | 49.988
2021-08-29 | 16:14 | 49.985
2021-08-29 | 16:14 | 49.984
2021-08-29 | 16:14 | 49.982
2021-08-29 | 16:14 | 49.982
2021-08-29 | 16:14 | 49.98
2021-08-29 | 16:14 | 49.98
2021-08-29 | 16:14 | 49.982
2021-08-29 | 16:14 | 49.985
2021-08-29 | 16:14 | 49.987
2021-08-29 | 16:14 | 49.989
2021-08-29 | 16:14 | 49.989
2021-08-29 | 16:14 | 49.988
2021-08-29 | 16:14 | 49.988
2021-08-29 | 16:14 | 49.986
2021-08-29 | 16:14 | 49.985
2021-08-29 | 16:14 | 49.984
2021-08-29 | 16:14 | 49.986
2021-08-29 | 16:14 | 49.988
2021-08-29 | 16:14 | 49.988
2021-08-29 | 16:14 | 49.99
2021-08-29 | 16:14 | 49.994
2021-08-29 | 16:14 | 49.999
2021-08-29 | 16:14 | 50
2021-08-29 | 16:14 | 50.006
2021-08-29 | 16:14 | 50.01
2021-08-29 | 16:14 | 50.014
2021-08-29 | 16:14 | 50.016
2021-08-29 | 16:14 | 50.017
2021-08-29 | 16:14 | 50.017
2021-08-29 | 16:14 | 50.017
2021-08-29 | 16:14 | 50.016
2021-08-29 | 16:14 | 50.017
2021-08-29 | 16:14 | 50.014
2021-08-29 | 16:14 | 50.012
2021-08-29 | 16:14 | 50.013
2021-08-29 | 16:14 | 50.013
2021-08-29 | 16:14 | 50.014
2021-08-29 | 16:14 | 50.014
2021-08-29 | 16:14 | 50.018
2021-08-29 | 16:14 | 50.023
2021-08-29 | 16:14 | 50.023
2021-08-29 | 16:14 | 50.026
2021-08-29 | 16:14 | 50.027
2021-08-29 | 16:14 | 50.028
2021-08-29 | 16:14 | 50.031
2021-08-29 | 16:14 | 50.031
2021-08-29 | 16:14 | 50.029
2021-08-29 | 16:14 | 50.029
2021-08-29 | 16:14 | 50.027
2021-08-29 | 16:15 | 50.024
2021-08-29 | 16:15 | 50.018
2021-08-29 | 16:15 | 50.014
2021-08-29 | 16:15 | 50.01
2021-08-29 | 16:15 | 50.005
2021-08-29 | 16:15 | 50.002
2021-08-29 | 16:15 | 50.002
2021-08-29 | 16:15 | 50.003
2021-08-29 | 16:15 | 50.004
2021-08-29 | 16:15 | 50.007
2021-08-29 | 16:15 | 50.007
2021-08-29 | 16:15 | 50.009
2021-08-29 | 16:15 | 50.011
2021-08-29 | 16:15 | 50.014
2021-08-29 | 16:15 | 50.018
2021-08-29 | 16:15 | 50.022
2021-08-29 | 16:15 | 50.021
2021-08-29 | 16:15 | 50.022
2021-08-29 | 16:15 | 50.02
2021-08-29 | 16:15 | 50.019
2021-08-29 | 16:15 | 50.015
2021-08-29 | 16:15 | 50.009
2021-08-29 | 16:15 | 50.007
2021-08-29 | 16:15 | 50.006
2021-08-29 | 16:15 | 50.007
2021-08-29 | 16:15 | 50.005
2021-08-29 | 16:15 | 50
2021-08-29 | 16:15 | 49.998
2021-08-29 | 16:15 | 49.992

## 20210830-1
In GMT
Date | Time | Freq
2021-08-30 | 7:34 | 49.982
2021-08-30 | 7:34 | 49.979
2021-08-30 | 7:34 | 49.972
2021-08-30 | 7:34 | 49.967
2021-08-30 | 7:34 | 49.962
2021-08-30 | 7:34 | 49.96
2021-08-30 | 7:34 | 49.961
2021-08-30 | 7:34 | 49.96
2021-08-30 | 7:34 | 49.96
2021-08-30 | 7:34 | 49.958
2021-08-30 | 7:34 | 49.959
2021-08-30 | 7:34 | 49.959
2021-08-30 | 7:34 | 49.958
2021-08-30 | 7:34 | 49.958
2021-08-30 | 7:34 | 49.96
2021-08-30 | 7:34 | 49.962
2021-08-30 | 7:34 | 49.966
2021-08-30 | 7:34 | 49.97
2021-08-30 | 7:34 | 49.972
2021-08-30 | 7:34 | 49.972
2021-08-30 | 7:34 | 49.973
2021-08-30 | 7:34 | 49.972
2021-08-30 | 7:34 | 49.97
2021-08-30 | 7:34 | 49.966
2021-08-30 | 7:34 | 49.963
2021-08-30 | 7:34 | 49.961
2021-08-30 | 7:34 | 49.96
2021-08-30 | 7:34 | 49.957
2021-08-30 | 7:34 | 49.956
2021-08-30 | 7:34 | 49.954
2021-08-30 | 7:34 | 49.955
2021-08-30 | 7:35 | 49.955
2021-08-30 | 7:35 | 49.955
2021-08-30 | 7:35 | 49.955
2021-08-30 | 7:35 | 49.955
2021-08-30 | 7:35 | 49.954
2021-08-30 | 7:35 | 49.957
2021-08-30 | 7:35 | 49.96
2021-08-30 | 7:35 | 49.964
2021-08-30 | 7:35 | 49.965
2021-08-30 | 7:35 | 49.968
2021-08-30 | 7:35 | 49.971
2021-08-30 | 7:35 | 49.973
2021-08-30 | 7:35 | 49.975
2021-08-30 | 7:35 | 49.976
2021-08-30 | 7:35 | 49.977
2021-08-30 | 7:35 | 49.979
2021-08-30 | 7:35 | 49.979
2021-08-30 | 7:35 | 49.977
2021-08-30 | 7:35 | 49.972
2021-08-30 | 7:35 | 49.968
2021-08-30 | 7:35 | 49.966
2021-08-30 | 7:35 | 49.963
2021-08-30 | 7:35 | 49.963
2021-08-30 | 7:35 | 49.961
2021-08-30 | 7:35 | 49.959
2021-08-30 | 7:35 | 49.957
2021-08-30 | 7:35 | 49.956
2021-08-30 | 7:35 | 49.957
2021-08-30 | 7:35 | 49.957
2021-08-30 | 7:35 | 49.957
2021-08-30 | 7:35 | 49.959
2021-08-30 | 7:35 | 49.962
2021-08-30 | 7:35 | 49.964
2021-08-30 | 7:35 | 49.967
2021-08-30 | 7:35 | 49.97
2021-08-30 | 7:35 | 49.972
2021-08-30 | 7:35 | 49.971
2021-08-30 | 7:35 | 49.973
2021-08-30 | 7:35 | 49.976
2021-08-30 | 7:35 | 49.979
2021-08-30 | 7:35 | 49.986
2021-08-30 | 7:35 | 49.99
2021-08-30 | 7:35 | 49.99
2021-08-30 | 7:35 | 49.99
2021-08-30 | 7:35 | 49.991
2021-08-30 | 7:35 | 49.994
2021-08-30 | 7:35 | 49.996
2021-08-30 | 7:35 | 50.002
2021-08-30 | 7:35 | 50.008
2021-08-30 | 7:35 | 50.007
2021-08-30 | 7:35 | 50.006
2021-08-30 | 7:35 | 50.004
2021-08-30 | 7:35 | 50.005
2021-08-30 | 7:35 | 50.008
2021-08-30 | 7:35 | 50.007
2021-08-30 | 7:35 | 50.006
2021-08-30 | 7:35 | 50.005
2021-08-30 | 7:35 | 50.004
2021-08-30 | 7:35 | 50.003
2021-08-30 | 7:36 | 50.002
2021-08-30 | 7:36 | 50.004
2021-08-30 | 7:36 | 50.005
2021-08-30 | 7:36 | 50.007
2021-08-30 | 7:36 | 50.01
2021-08-30 | 7:36 | 50.008
2021-08-30 | 7:36 | 50.007
2021-08-30 | 7:36 | 50.004
2021-08-30 | 7:36 | 50
2021-08-30 | 7:36 | 49.996
2021-08-30 | 7:36 | 49.994
2021-08-30 | 7:36 | 49.993
2021-08-30 | 7:36 | 49.993
2021-08-30 | 7:36 | 49.992
2021-08-30 | 7:36 | 49.99
2021-08-30 | 7:36 | 49.987
2021-08-30 | 7:36 | 49.986
2021-08-30 | 7:36 | 49.981
2021-08-30 | 7:36 | 49.978
2021-08-30 | 7:36 | 49.976
2021-08-30 | 7:36 | 49.975
2021-08-30 | 7:36 | 49.973
2021-08-30 | 7:36 | 49.962
2021-08-30 | 7:36 | 49.922
2021-08-30 | 7:36 | 49.899
2021-08-30 | 7:36 | 49.891
2021-08-30 | 7:36 | 49.877
2021-08-30 | 7:36 | 49.864
2021-08-30 | 7:36 | 49.853
2021-08-30 | 7:36 | 49.844
2021-08-30 | 7:36 | 49.838
2021-08-30 | 7:36 | 49.831
2021-08-30 | 7:36 | 49.826
2021-08-30 | 7:36 | 49.818
2021-08-30 | 7:36 | 49.813
2021-08-30 | 7:36 | 49.809
2021-08-30 | 7:36 | 49.809
2021-08-30 | 7:36 | 49.808
2021-08-30 | 7:36 | 49.809
2021-08-30 | 7:36 | 49.811
2021-08-30 | 7:36 | 49.814
2021-08-30 | 7:36 | 49.816
2021-08-30 | 7:36 | 49.814
2021-08-30 | 7:36 | 49.813
2021-08-30 | 7:36 | 49.811
2021-08-30 | 7:36 | 49.811
2021-08-30 | 7:36 | 49.807
2021-08-30 | 7:36 | 49.804
2021-08-30 | 7:36 | 49.806
2021-08-30 | 7:36 | 49.806
2021-08-30 | 7:36 | 49.808
2021-08-30 | 7:36 | 49.805
2021-08-30 | 7:36 | 49.801
2021-08-30 | 7:36 | 49.799
2021-08-30 | 7:36 | 49.799
2021-08-30 | 7:36 | 49.8
2021-08-30 | 7:36 | 49.8
2021-08-30 | 7:36 | 49.798
2021-08-30 | 7:36 | 49.797
2021-08-30 | 7:36 | 49.799
2021-08-30 | 7:36 | 49.802
2021-08-30 | 7:37 | 49.805
2021-08-30 | 7:37 | 49.81
2021-08-30 | 7:37 | 49.815
2021-08-30 | 7:37 | 49.818
2021-08-30 | 7:37 | 49.821
2021-08-30 | 7:37 | 49.821
2021-08-30 | 7:37 | 49.82
2021-08-30 | 7:37 | 49.818
2021-08-30 | 7:37 | 49.818
2021-08-30 | 7:37 | 49.817
2021-08-30 | 7:37 | 49.816
2021-08-30 | 7:37 | 49.815
2021-08-30 | 7:37 | 49.813
2021-08-30 | 7:37 | 49.808
2021-08-30 | 7:37 | 49.803
2021-08-30 | 7:37 | 49.801
2021-08-30 | 7:37 | 49.8
2021-08-30 | 7:37 | 49.802
2021-08-30 | 7:37 | 49.803
2021-08-30 | 7:37 | 49.804
2021-08-30 | 7:37 | 49.806
2021-08-30 | 7:37 | 49.805
2021-08-30 | 7:37 | 49.804
2021-08-30 | 7:37 | 49.804
2021-08-30 | 7:37 | 49.803
2021-08-30 | 7:37 | 49.799
2021-08-30 | 7:37 | 49.798
2021-08-30 | 7:37 | 49.797
2021-08-30 | 7:37 | 49.795
2021-08-30 | 7:37 | 49.795
2021-08-30 | 7:37 | 49.795
2021-08-30 | 7:37 | 49.796
2021-08-30 | 7:37 | 49.798
2021-08-30 | 7:37 | 49.802
2021-08-30 | 7:37 | 49.807
2021-08-30 | 7:37 | 49.812
2021-08-30 | 7:37 | 49.817
2021-08-30 | 7:37 | 49.823
2021-08-30 | 7:37 | 49.829
2021-08-30 | 7:37 | 49.833
2021-08-30 | 7:37 | 49.838
2021-08-30 | 7:37 | 49.841
2021-08-30 | 7:37 | 49.844
2021-08-30 | 7:37 | 49.848
2021-08-30 | 7:37 | 49.852
2021-08-30 | 7:37 | 49.853
2021-08-30 | 7:37 | 49.852
2021-08-30 | 7:37 | 49.855
2021-08-30 | 7:37 | 49.859
2021-08-30 | 7:37 | 49.86
2021-08-30 | 7:37 | 49.86
2021-08-30 | 7:37 | 49.859
2021-08-30 | 7:37 | 49.858
2021-08-30 | 7:37 | 49.854
2021-08-30 | 7:37 | 49.851
2021-08-30 | 7:37 | 49.85
2021-08-30 | 7:37 | 49.85
2021-08-30 | 7:37 | 49.848
2021-08-30 | 7:37 | 49.848
2021-08-30 | 7:38 | 49.848
2021-08-30 | 7:38 | 49.85
2021-08-30 | 7:38 | 49.851
2021-08-30 | 7:38 | 49.852
2021-08-30 | 7:38 | 49.85
2021-08-30 | 7:38 | 49.853
2021-08-30 | 7:38 | 49.857
2021-08-30 | 7:38 | 49.856
2021-08-30 | 7:38 | 49.856
2021-08-30 | 7:38 | 49.856
2021-08-30 | 7:38 | 49.859
2021-08-30 | 7:38 | 49.861
2021-08-30 | 7:38 | 49.869
2021-08-30 | 7:38 | 49.877
2021-08-30 | 7:38 | 49.879
2021-08-30 | 7:38 | 49.876
2021-08-30 | 7:38 | 49.874
2021-08-30 | 7:38 | 49.874
2021-08-30 | 7:38 | 49.876
2021-08-30 | 7:38 | 49.877
2021-08-30 | 7:38 | 49.879
2021-08-30 | 7:38 | 49.881
2021-08-30 | 7:38 | 49.882
2021-08-30 | 7:38 | 49.881
2021-08-30 | 7:38 | 49.882
2021-08-30 | 7:38 | 49.882
2021-08-30 | 7:38 | 49.881
2021-08-30 | 7:38 | 49.881
2021-08-30 | 7:38 | 49.882
2021-08-30 | 7:38 | 49.884
2021-08-30 | 7:38 | 49.885
2021-08-30 | 7:38 | 49.885
2021-08-30 | 7:38 | 49.885
2021-08-30 | 7:38 | 49.883
2021-08-30 | 7:38 | 49.882
2021-08-30 | 7:38 | 49.88
2021-08-30 | 7:38 | 49.876
2021-08-30 | 7:38 | 49.874
2021-08-30 | 7:38 | 49.873
2021-08-30 | 7:38 | 49.87
2021-08-30 | 7:38 | 49.866
2021-08-30 | 7:38 | 49.863
2021-08-30 | 7:38 | 49.861
2021-08-30 | 7:38 | 49.859
2021-08-30 | 7:38 | 49.859
2021-08-30 | 7:38 | 49.863
2021-08-30 | 7:38 | 49.867
2021-08-30 | 7:38 | 49.87
2021-08-30 | 7:38 | 49.873
2021-08-30 | 7:38 | 49.877
2021-08-30 | 7:38 | 49.882
2021-08-30 | 7:38 | 49.886
2021-08-30 | 7:38 | 49.888
2021-08-30 | 7:38 | 49.89
2021-08-30 | 7:38 | 49.891
2021-08-30 | 7:38 | 49.893
2021-08-30 | 7:38 | 49.893
2021-08-30 | 7:38 | 49.895
2021-08-30 | 7:38 | 49.9
2021-08-30 | 7:38 | 49.904
2021-08-30 | 7:38 | 49.909
2021-08-30 | 7:39 | 49.911
2021-08-30 | 7:39 | 49.914
2021-08-30 | 7:39 | 49.915
2021-08-30 | 7:39 | 49.919
2021-08-30 | 7:39 | 49.922
2021-08-30 | 7:39 | 49.928
2021-08-30 | 7:39 | 49.934
2021-08-30 | 7:39 | 49.937
2021-08-30 | 7:39 | 49.94
2021-08-30 | 7:39 | 49.945
2021-08-30 | 7:39 | 49.947
2021-08-30 | 7:39 | 49.948
2021-08-30 | 7:39 | 49.947
2021-08-30 | 7:39 | 49.947
2021-08-30 | 7:39 | 49.947
2021-08-30 | 7:39 | 49.949
2021-08-30 | 7:39 | 49.95
2021-08-30 | 7:39 | 49.951
2021-08-30 | 7:39 | 49.95
2021-08-30 | 7:39 | 49.951
2021-08-30 | 7:39 | 49.951
2021-08-30 | 7:39 | 49.954
2021-08-30 | 7:39 | 49.957
2021-08-30 | 7:39 | 49.958
2021-08-30 | 7:39 | 49.957
2021-08-30 | 7:39 | 49.96
2021-08-30 | 7:39 | 49.96
2021-08-30 | 7:39 | 49.961
2021-08-30 | 7:39 | 49.959
2021-08-30 | 7:39 | 49.957
2021-08-30 | 7:39 | 49.955
2021-08-30 | 7:39 | 49.955
2021-08-30 | 7:39 | 49.956
2021-08-30 | 7:39 | 49.959
2021-08-30 | 7:39 | 49.963
2021-08-30 | 7:39 | 49.969
2021-08-30 | 7:39 | 49.971
2021-08-30 | 7:39 | 49.974
2021-08-30 | 7:39 | 49.975
2021-08-30 | 7:39 | 49.975
2021-08-30 | 7:39 | 49.974
2021-08-30 | 7:39 | 49.973
2021-08-30 | 7:39 | 49.973
2021-08-30 | 7:39 | 49.97
2021-08-30 | 7:39 | 49.966
2021-08-30 | 7:39 | 49.964
2021-08-30 | 7:39 | 49.964
2021-08-30 | 7:39 | 49.963
2021-08-30 | 7:39 | 49.964
2021-08-30 | 7:39 | 49.968
2021-08-30 | 7:39 | 49.966
2021-08-30 | 7:39 | 49.967
2021-08-30 | 7:39 | 49.968
2021-08-30 | 7:39 | 49.97
2021-08-30 | 7:39 | 49.97
2021-08-30 | 7:39 | 49.971
2021-08-30 | 7:39 | 49.972
2021-08-30 | 7:39 | 49.974
2021-08-30 | 7:39 | 49.975
2021-08-30 | 7:39 | 49.974
2021-08-30 | 7:40 | 49.972
2021-08-30 | 7:40 | 49.972
2021-08-30 | 7:40 | 49.971
2021-08-30 | 7:40 | 49.972
2021-08-30 | 7:40 | 49.973
2021-08-30 | 7:40 | 49.975
2021-08-30 | 7:40 | 49.978
2021-08-30 | 7:40 | 49.98
2021-08-30 | 7:40 | 49.978
2021-08-30 | 7:40 | 49.968
2021-08-30 | 7:40 | 49.963
2021-08-30 | 7:40 | 49.954
2021-08-30 | 7:40 | 49.947
2021-08-30 | 7:40 | 49.944
2021-08-30 | 7:40 | 49.947
2021-08-30 | 7:40 | 49.949
2021-08-30 | 7:40 | 49.947
2021-08-30 | 7:40 | 49.95
2021-08-30 | 7:40 | 49.953
2021-08-30 | 7:40 | 49.957
2021-08-30 | 7:40 | 49.962
2021-08-30 | 7:40 | 49.963
2021-08-30 | 7:40 | 49.965
2021-08-30 | 7:40 | 49.965
2021-08-30 | 7:40 | 49.962
2021-08-30 | 7:40 | 49.958
2021-08-30 | 7:40 | 49.954
2021-08-30 | 7:40 | 49.951
2021-08-30 | 7:40 | 49.947
2021-08-30 | 7:40 | 49.945
2021-08-30 | 7:40 | 49.94
2021-08-30 | 7:40 | 49.936
2021-08-30 | 7:40 | 49.93
2021-08-30 | 7:40 | 49.932
2021-08-30 | 7:40 | 49.933
2021-08-30 | 7:40 | 49.931
2021-08-30 | 7:40 | 49.929
2021-08-30 | 7:40 | 49.929
2021-08-30 | 7:40 | 49.928
2021-08-30 | 7:40 | 49.929
2021-08-30 | 7:40 | 49.93
2021-08-30 | 7:40 | 49.927
2021-08-30 | 7:40 | 49.924
2021-08-30 | 7:40 | 49.922
2021-08-30 | 7:40 | 49.921
2021-08-30 | 7:40 | 49.92
2021-08-30 | 7:40 | 49.918
2021-08-30 | 7:40 | 49.918
2021-08-30 | 7:40 | 49.916
2021-08-30 | 7:40 | 49.917
2021-08-30 | 7:40 | 49.914
2021-08-30 | 7:40 | 49.915
2021-08-30 | 7:40 | 49.913
2021-08-30 | 7:40 | 49.913
2021-08-30 | 7:40 | 49.914
2021-08-30 | 7:40 | 49.918
2021-08-30 | 7:40 | 49.922
2021-08-30 | 7:40 | 49.927
2021-08-30 | 7:40 | 49.929
2021-08-30 | 7:40 | 49.931
2021-08-30 | 7:41 | 49.934
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.938
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.937
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.934
2021-08-30 | 7:41 | 49.935
2021-08-30 | 7:41 | 49.935
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.934
2021-08-30 | 7:41 | 49.932
2021-08-30 | 7:41 | 49.93
2021-08-30 | 7:41 | 49.934
2021-08-30 | 7:41 | 49.935
2021-08-30 | 7:41 | 49.935
2021-08-30 | 7:41 | 49.932
2021-08-30 | 7:41 | 49.931
2021-08-30 | 7:41 | 49.931
2021-08-30 | 7:41 | 49.932
2021-08-30 | 7:41 | 49.933
2021-08-30 | 7:41 | 49.933
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.937
2021-08-30 | 7:41 | 49.937
2021-08-30 | 7:41 | 49.933
2021-08-30 | 7:41 | 49.931
2021-08-30 | 7:41 | 49.928
2021-08-30 | 7:41 | 49.929
2021-08-30 | 7:41 | 49.928
2021-08-30 | 7:41 | 49.93
2021-08-30 | 7:41 | 49.931
2021-08-30 | 7:41 | 49.933
2021-08-30 | 7:41 | 49.936
2021-08-30 | 7:41 | 49.939
2021-08-30 | 7:41 | 49.943
2021-08-30 | 7:41 | 49.947
2021-08-30 | 7:41 | 49.95
2021-08-30 | 7:41 | 49.952
2021-08-30 | 7:41 | 49.957
2021-08-30 | 7:41 | 49.96
2021-08-30 | 7:41 | 49.96
2021-08-30 | 7:41 | 49.96
2021-08-30 | 7:41 | 49.96
2021-08-30 | 7:41 | 49.963
2021-08-30 | 7:41 | 49.967
2021-08-30 | 7:41 | 49.968
2021-08-30 | 7:41 | 49.972
2021-08-30 | 7:41 | 49.974
2021-08-30 | 7:41 | 49.976
2021-08-30 | 7:41 | 49.978
2021-08-30 | 7:41 | 49.981
2021-08-30 | 7:41 | 49.983
2021-08-30 | 7:41 | 49.987
2021-08-30 | 7:41 | 49.986
2021-08-30 | 7:41 | 49.989
2021-08-30 | 7:42 | 49.989
2021-08-30 | 7:42 | 49.991
2021-08-30 | 7:42 | 49.992
2021-08-30 | 7:42 | 49.991
2021-08-30 | 7:42 | 49.991
2021-08-30 | 7:42 | 49.992
2021-08-30 | 7:42 | 49.992
2021-08-30 | 7:42 | 49.993
2021-08-30 | 7:42 | 49.993
2021-08-30 | 7:42 | 49.994
2021-08-30 | 7:42 | 49.993
2021-08-30 | 7:42 | 49.993
2021-08-30 | 7:42 | 49.989
2021-08-30 | 7:42 | 49.988
2021-08-30 | 7:42 | 49.987
2021-08-30 | 7:42 | 49.986
2021-08-30 | 7:42 | 49.984
2021-08-30 | 7:42 | 49.983
2021-08-30 | 7:42 | 49.979
2021-08-30 | 7:42 | 49.976
2021-08-30 | 7:42 | 49.975
2021-08-30 | 7:42 | 49.975
2021-08-30 | 7:42 | 49.977
2021-08-30 | 7:42 | 49.978
2021-08-30 | 7:42 | 49.979
2021-08-30 | 7:42 | 49.979
2021-08-30 | 7:42 | 49.979
2021-08-30 | 7:42 | 49.978
2021-08-30 | 7:42 | 49.979
2021-08-30 | 7:42 | 49.979
2021-08-30 | 7:42 | 49.977
2021-08-30 | 7:42 | 49.978
2021-08-30 | 7:42 | 49.972
2021-08-30 | 7:42 | 49.967
2021-08-30 | 7:42 | 49.964
2021-08-30 | 7:42 | 49.959
2021-08-30 | 7:42 | 49.958
2021-08-30 | 7:42 | 49.957
2021-08-30 | 7:42 | 49.959
2021-08-30 | 7:42 | 49.962
2021-08-30 | 7:42 | 49.964
2021-08-30 | 7:42 | 49.966
2021-08-30 | 7:42 | 49.969
2021-08-30 | 7:42 | 49.97
2021-08-30 | 7:42 | 49.974
2021-08-30 | 7:42 | 49.973
2021-08-30 | 7:42 | 49.972
2021-08-30 | 7:42 | 49.971
2021-08-30 | 7:42 | 49.97
2021-08-30 | 7:42 | 49.969
2021-08-30 | 7:42 | 49.967
2021-08-30 | 7:42 | 49.966
2021-08-30 | 7:42 | 49.965
2021-08-30 | 7:42 | 49.963
2021-08-30 | 7:42 | 49.966
2021-08-30 | 7:42 | 49.968
2021-08-30 | 7:42 | 49.966
2021-08-30 | 7:42 | 49.97
2021-08-30 | 7:42 | 49.971
2021-08-30 | 7:42 | 49.974
2021-08-30 | 7:43 | 49.977
2021-08-30 | 7:43 | 49.978
2021-08-30 | 7:43 | 49.978
2021-08-30 | 7:43 | 49.98
2021-08-30 | 7:43 | 49.984
2021-08-30 | 7:43 | 49.987
2021-08-30 | 7:43 | 49.99
2021-08-30 | 7:43 | 49.996
2021-08-30 | 7:43 | 49.997
2021-08-30 | 7:43 | 49.995
2021-08-30 | 7:43 | 49.997
2021-08-30 | 7:43 | 50
2021-08-30 | 7:43 | 50.004
2021-08-30 | 7:43 | 50.006
2021-08-30 | 7:43 | 50.006
2021-08-30 | 7:43 | 50.007
2021-08-30 | 7:43 | 50.006
2021-08-30 | 7:43 | 50.005
2021-08-30 | 7:43 | 50
2021-08-30 | 7:43 | 49.996
2021-08-30 | 7:43 | 49.995
2021-08-30 | 7:43 | 49.99
2021-08-30 | 7:43 | 49.989
2021-08-30 | 7:43 | 49.989
2021-08-30 | 7:43 | 49.989
2021-08-30 | 7:43 | 49.989
2021-08-30 | 7:43 | 49.99
2021-08-30 | 7:43 | 49.991
2021-08-30 | 7:43 | 49.993

## 20210830-2
In GMT
Date | Time | Freq
2021-08-30 | 16:09 | 49.986
2021-08-30 | 16:09 | 49.985
2021-08-30 | 16:09 | 49.984
2021-08-30 | 16:09 | 49.982
2021-08-30 | 16:09 | 49.981
2021-08-30 | 16:09 | 49.98
2021-08-30 | 16:09 | 49.978
2021-08-30 | 16:09 | 49.979
2021-08-30 | 16:09 | 49.981
2021-08-30 | 16:09 | 49.979
2021-08-30 | 16:09 | 49.977
2021-08-30 | 16:09 | 49.974
2021-08-30 | 16:09 | 49.97
2021-08-30 | 16:09 | 49.967
2021-08-30 | 16:09 | 49.965
2021-08-30 | 16:09 | 49.965
2021-08-30 | 16:09 | 49.965
2021-08-30 | 16:09 | 49.966
2021-08-30 | 16:09 | 49.969
2021-08-30 | 16:09 | 49.972
2021-08-30 | 16:09 | 49.975
2021-08-30 | 16:09 | 49.977
2021-08-30 | 16:09 | 49.98
2021-08-30 | 16:09 | 49.983
2021-08-30 | 16:09 | 49.988
2021-08-30 | 16:09 | 49.989
2021-08-30 | 16:09 | 49.992
2021-08-30 | 16:09 | 49.996
2021-08-30 | 16:09 | 49.997
2021-08-30 | 16:09 | 49.997
2021-08-30 | 16:10 | 49.995
2021-08-30 | 16:10 | 49.995
2021-08-30 | 16:10 | 49.993
2021-08-30 | 16:10 | 49.988
2021-08-30 | 16:10 | 49.984
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.981
2021-08-30 | 16:10 | 49.977
2021-08-30 | 16:10 | 49.975
2021-08-30 | 16:10 | 49.978
2021-08-30 | 16:10 | 49.979
2021-08-30 | 16:10 | 49.981
2021-08-30 | 16:10 | 49.982
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.983
2021-08-30 | 16:10 | 49.979
2021-08-30 | 16:10 | 49.976
2021-08-30 | 16:10 | 49.974
2021-08-30 | 16:10 | 49.972
2021-08-30 | 16:10 | 49.973
2021-08-30 | 16:10 | 49.973
2021-08-30 | 16:10 | 49.973
2021-08-30 | 16:10 | 49.972
2021-08-30 | 16:10 | 49.973
2021-08-30 | 16:10 | 49.972
2021-08-30 | 16:10 | 49.971
2021-08-30 | 16:10 | 49.97
2021-08-30 | 16:10 | 49.967
2021-08-30 | 16:10 | 49.967
2021-08-30 | 16:10 | 49.968
2021-08-30 | 16:10 | 49.97
2021-08-30 | 16:10 | 49.974
2021-08-30 | 16:10 | 49.976
2021-08-30 | 16:10 | 49.973
2021-08-30 | 16:10 | 49.969
2021-08-30 | 16:10 | 49.966
2021-08-30 | 16:10 | 49.959
2021-08-30 | 16:10 | 49.953
2021-08-30 | 16:10 | 49.944
2021-08-30 | 16:10 | 49.939
2021-08-30 | 16:10 | 49.936
2021-08-30 | 16:10 | 49.936
2021-08-30 | 16:10 | 49.935
2021-08-30 | 16:10 | 49.936
2021-08-30 | 16:10 | 49.937
2021-08-30 | 16:10 | 49.94
2021-08-30 | 16:10 | 49.944
2021-08-30 | 16:10 | 49.95
2021-08-30 | 16:10 | 49.955
2021-08-30 | 16:10 | 49.959
2021-08-30 | 16:10 | 49.965
2021-08-30 | 16:10 | 49.968
2021-08-30 | 16:10 | 49.975
2021-08-30 | 16:10 | 49.982
2021-08-30 | 16:10 | 49.987
2021-08-30 | 16:10 | 49.99
2021-08-30 | 16:10 | 49.991
2021-08-30 | 16:11 | 49.994
2021-08-30 | 16:11 | 49.995
2021-08-30 | 16:11 | 49.998
2021-08-30 | 16:11 | 50.003
2021-08-30 | 16:11 | 50.007
2021-08-30 | 16:11 | 50.01
2021-08-30 | 16:11 | 50.014
2021-08-30 | 16:11 | 50.016
2021-08-30 | 16:11 | 50.016
2021-08-30 | 16:11 | 50.017
2021-08-30 | 16:11 | 50.018
2021-08-30 | 16:11 | 50.017
2021-08-30 | 16:11 | 50.014
2021-08-30 | 16:11 | 50.011
2021-08-30 | 16:11 | 50.011
2021-08-30 | 16:11 | 50.012
2021-08-30 | 16:11 | 50.015
2021-08-30 | 16:11 | 50.018
2021-08-30 | 16:11 | 50.021
2021-08-30 | 16:11 | 50.022
2021-08-30 | 16:11 | 50.024
2021-08-30 | 16:11 | 50.025
2021-08-30 | 16:11 | 50.024
2021-08-30 | 16:11 | 50.021
2021-08-30 | 16:11 | 50.019
2021-08-30 | 16:11 | 50.019
2021-08-30 | 16:11 | 50.019
2021-08-30 | 16:11 | 50.022
2021-08-30 | 16:11 | 50.021
2021-08-30 | 16:11 | 50.016
2021-08-30 | 16:11 | 50.009
2021-08-30 | 16:11 | 49.999
2021-08-30 | 16:11 | 49.99
2021-08-30 | 16:11 | 49.98
2021-08-30 | 16:11 | 49.969
2021-08-30 | 16:11 | 49.96
2021-08-30 | 16:11 | 49.949
2021-08-30 | 16:11 | 49.944
2021-08-30 | 16:11 | 49.942
2021-08-30 | 16:11 | 49.941
2021-08-30 | 16:11 | 49.942
2021-08-30 | 16:11 | 49.94
2021-08-30 | 16:11 | 49.925
2021-08-30 | 16:11 | 49.909
2021-08-30 | 16:11 | 49.894
2021-08-30 | 16:11 | 49.88
2021-08-30 | 16:11 | 49.87
2021-08-30 | 16:11 | 49.863
2021-08-30 | 16:11 | 49.857
2021-08-30 | 16:11 | 49.853
2021-08-30 | 16:11 | 49.85
2021-08-30 | 16:11 | 49.848
2021-08-30 | 16:11 | 49.847
2021-08-30 | 16:11 | 49.849
2021-08-30 | 16:11 | 49.85
2021-08-30 | 16:11 | 49.853
2021-08-30 | 16:11 | 49.853
2021-08-30 | 16:11 | 49.854
2021-08-30 | 16:11 | 49.854
2021-08-30 | 16:12 | 49.853
2021-08-30 | 16:12 | 49.851
2021-08-30 | 16:12 | 49.85
2021-08-30 | 16:12 | 49.849
2021-08-30 | 16:12 | 49.847
2021-08-30 | 16:12 | 49.845
2021-08-30 | 16:12 | 49.845
2021-08-30 | 16:12 | 49.845
2021-08-30 | 16:12 | 49.846
2021-08-30 | 16:12 | 49.846
2021-08-30 | 16:12 | 49.844
2021-08-30 | 16:12 | 49.842
2021-08-30 | 16:12 | 49.84
2021-08-30 | 16:12 | 49.835
2021-08-30 | 16:12 | 49.829
2021-08-30 | 16:12 | 49.823
2021-08-30 | 16:12 | 49.82
2021-08-30 | 16:12 | 49.819
2021-08-30 | 16:12 | 49.821
2021-08-30 | 16:12 | 49.823
2021-08-30 | 16:12 | 49.825
2021-08-30 | 16:12 | 49.827
2021-08-30 | 16:12 | 49.826
2021-08-30 | 16:12 | 49.824
2021-08-30 | 16:12 | 49.824
2021-08-30 | 16:12 | 49.823
2021-08-30 | 16:12 | 49.822
2021-08-30 | 16:12 | 49.82
2021-08-30 | 16:12 | 49.818
2021-08-30 | 16:12 | 49.816
2021-08-30 | 16:12 | 49.812
2021-08-30 | 16:12 | 49.806
2021-08-30 | 16:12 | 49.803
2021-08-30 | 16:12 | 49.8
2021-08-30 | 16:12 | 49.797
2021-08-30 | 16:12 | 49.794
2021-08-30 | 16:12 | 49.793
2021-08-30 | 16:12 | 49.791
2021-08-30 | 16:12 | 49.79
2021-08-30 | 16:12 | 49.787
2021-08-30 | 16:12 | 49.786
2021-08-30 | 16:12 | 49.785
2021-08-30 | 16:12 | 49.786
2021-08-30 | 16:12 | 49.79
2021-08-30 | 16:12 | 49.793
2021-08-30 | 16:12 | 49.797
2021-08-30 | 16:12 | 49.797
2021-08-30 | 16:12 | 49.798
2021-08-30 | 16:12 | 49.8
2021-08-30 | 16:12 | 49.802
2021-08-30 | 16:12 | 49.803
2021-08-30 | 16:12 | 49.806
2021-08-30 | 16:12 | 49.811
2021-08-30 | 16:12 | 49.816
2021-08-30 | 16:12 | 49.819
2021-08-30 | 16:12 | 49.823
2021-08-30 | 16:12 | 49.828
2021-08-30 | 16:12 | 49.834
2021-08-30 | 16:12 | 49.838
2021-08-30 | 16:12 | 49.842
2021-08-30 | 16:12 | 49.844
2021-08-30 | 16:13 | 49.848
2021-08-30 | 16:13 | 49.852
2021-08-30 | 16:13 | 49.859
2021-08-30 | 16:13 | 49.863
2021-08-30 | 16:13 | 49.866
2021-08-30 | 16:13 | 49.868
2021-08-30 | 16:13 | 49.872
2021-08-30 | 16:13 | 49.872
2021-08-30 | 16:13 | 49.872
2021-08-30 | 16:13 | 49.87
2021-08-30 | 16:13 | 49.866
2021-08-30 | 16:13 | 49.861
2021-08-30 | 16:13 | 49.857
2021-08-30 | 16:13 | 49.853
2021-08-30 | 16:13 | 49.852
2021-08-30 | 16:13 | 49.851
2021-08-30 | 16:13 | 49.852
2021-08-30 | 16:13 | 49.853
2021-08-30 | 16:13 | 49.854
2021-08-30 | 16:13 | 49.855
2021-08-30 | 16:13 | 49.856
2021-08-30 | 16:13 | 49.857
2021-08-30 | 16:13 | 49.859
2021-08-30 | 16:13 | 49.862
2021-08-30 | 16:13 | 49.863
2021-08-30 | 16:13 | 49.867
2021-08-30 | 16:13 | 49.868
2021-08-30 | 16:13 | 49.871
2021-08-30 | 16:13 | 49.872
2021-08-30 | 16:13 | 49.875
2021-08-30 | 16:13 | 49.872
2021-08-30 | 16:13 | 49.87
2021-08-30 | 16:13 | 49.868
2021-08-30 | 16:13 | 49.867
2021-08-30 | 16:13 | 49.864
2021-08-30 | 16:13 | 49.863
2021-08-30 | 16:13 | 49.862
2021-08-30 | 16:13 | 49.863
2021-08-30 | 16:13 | 49.867
2021-08-30 | 16:13 | 49.864
2021-08-30 | 16:13 | 49.863
2021-08-30 | 16:13 | 49.867
2021-08-30 | 16:13 | 49.865
2021-08-30 | 16:13 | 49.867
2021-08-30 | 16:13 | 49.864
2021-08-30 | 16:13 | 49.866
2021-08-30 | 16:13 | 49.868
2021-08-30 | 16:13 | 49.877
2021-08-30 | 16:13 | 49.882
2021-08-30 | 16:13 | 49.887
2021-08-30 | 16:13 | 49.887
2021-08-30 | 16:13 | 49.888
2021-08-30 | 16:13 | 49.888
2021-08-30 | 16:13 | 49.892
2021-08-30 | 16:13 | 49.892
2021-08-30 | 16:13 | 49.892
2021-08-30 | 16:13 | 49.892
2021-08-30 | 16:13 | 49.891
2021-08-30 | 16:13 | 49.888
2021-08-30 | 16:14 | 49.882
2021-08-30 | 16:14 | 49.877
2021-08-30 | 16:14 | 49.872
2021-08-30 | 16:14 | 49.869
2021-08-30 | 16:14 | 49.864
2021-08-30 | 16:14 | 49.861
2021-08-30 | 16:14 | 49.862
2021-08-30 | 16:14 | 49.862
2021-08-30 | 16:14 | 49.863
2021-08-30 | 16:14 | 49.863
2021-08-30 | 16:14 | 49.868
2021-08-30 | 16:14 | 49.87
2021-08-30 | 16:14 | 49.871
2021-08-30 | 16:14 | 49.87
2021-08-30 | 16:14 | 49.869
2021-08-30 | 16:14 | 49.869
2021-08-30 | 16:14 | 49.867
2021-08-30 | 16:14 | 49.864
2021-08-30 | 16:14 | 49.859
2021-08-30 | 16:14 | 49.856
2021-08-30 | 16:14 | 49.852
2021-08-30 | 16:14 | 49.853
2021-08-30 | 16:14 | 49.855
2021-08-30 | 16:14 | 49.855
2021-08-30 | 16:14 | 49.856
2021-08-30 | 16:14 | 49.855
2021-08-30 | 16:14 | 49.852
2021-08-30 | 16:14 | 49.855
2021-08-30 | 16:14 | 49.854
2021-08-30 | 16:14 | 49.856
2021-08-30 | 16:14 | 49.853
2021-08-30 | 16:14 | 49.852
2021-08-30 | 16:14 | 49.851
2021-08-30 | 16:14 | 49.852
2021-08-30 | 16:14 | 49.851
2021-08-30 | 16:14 | 49.851
2021-08-30 | 16:14 | 49.849
2021-08-30 | 16:14 | 49.85
2021-08-30 | 16:14 | 49.848
2021-08-30 | 16:14 | 49.846
2021-08-30 | 16:14 | 49.845
2021-08-30 | 16:14 | 49.848
2021-08-30 | 16:14 | 49.846
2021-08-30 | 16:14 | 49.846
2021-08-30 | 16:14 | 49.847
2021-08-30 | 16:14 | 49.845
2021-08-30 | 16:14 | 49.843
2021-08-30 | 16:14 | 49.842
2021-08-30 | 16:14 | 49.842
2021-08-30 | 16:14 | 49.844
2021-08-30 | 16:14 | 49.842
2021-08-30 | 16:14 | 49.841
2021-08-30 | 16:14 | 49.84
2021-08-30 | 16:14 | 49.84
2021-08-30 | 16:14 | 49.843
2021-08-30 | 16:14 | 49.844
2021-08-30 | 16:14 | 49.844
2021-08-30 | 16:14 | 49.844
2021-08-30 | 16:14 | 49.842
2021-08-30 | 16:14 | 49.841
2021-08-30 | 16:14 | 49.839
2021-08-30 | 16:15 | 49.835
2021-08-30 | 16:15 | 49.833
2021-08-30 | 16:15 | 49.832
2021-08-30 | 16:15 | 49.834
2021-08-30 | 16:15 | 49.836
2021-08-30 | 16:15 | 49.84
2021-08-30 | 16:15 | 49.842
2021-08-30 | 16:15 | 49.847
2021-08-30 | 16:15 | 49.854
2021-08-30 | 16:15 | 49.862
2021-08-30 | 16:15 | 49.868
2021-08-30 | 16:15 | 49.873
2021-08-30 | 16:15 | 49.877
2021-08-30 | 16:15 | 49.882
2021-08-30 | 16:15 | 49.885
2021-08-30 | 16:15 | 49.885
2021-08-30 | 16:15 | 49.885
2021-08-30 | 16:15 | 49.886
2021-08-30 | 16:15 | 49.888
2021-08-30 | 16:15 | 49.888
2021-08-30 | 16:15 | 49.89
2021-08-30 | 16:15 | 49.892
2021-08-30 | 16:15 | 49.894
2021-08-30 | 16:15 | 49.894
2021-08-30 | 16:15 | 49.895
2021-08-30 | 16:15 | 49.894
2021-08-30 | 16:15 | 49.895
2021-08-30 | 16:15 | 49.89
2021-08-30 | 16:15 | 49.888
2021-08-30 | 16:15 | 49.884
2021-08-30 | 16:15 | 49.882
2021-08-30 | 16:15 | 49.879
2021-08-30 | 16:15 | 49.879
2021-08-30 | 16:15 | 49.878
2021-08-30 | 16:15 | 49.877
2021-08-30 | 16:15 | 49.878
2021-08-30 | 16:15 | 49.877
2021-08-30 | 16:15 | 49.876
2021-08-30 | 16:15 | 49.875
2021-08-30 | 16:15 | 49.873
2021-08-30 | 16:15 | 49.873
2021-08-30 | 16:15 | 49.87
2021-08-30 | 16:15 | 49.866
2021-08-30 | 16:15 | 49.865
2021-08-30 | 16:15 | 49.861
2021-08-30 | 16:15 | 49.859
2021-08-30 | 16:15 | 49.857
2021-08-30 | 16:15 | 49.857
2021-08-30 | 16:15 | 49.857
2021-08-30 | 16:15 | 49.858
2021-08-30 | 16:15 | 49.86
2021-08-30 | 16:15 | 49.863
2021-08-30 | 16:15 | 49.866
2021-08-30 | 16:15 | 49.867
2021-08-30 | 16:15 | 49.866
2021-08-30 | 16:15 | 49.864
2021-08-30 | 16:15 | 49.862
2021-08-30 | 16:15 | 49.862
2021-08-30 | 16:15 | 49.861
2021-08-30 | 16:16 | 49.859
2021-08-30 | 16:16 | 49.857
2021-08-30 | 16:16 | 49.856
2021-08-30 | 16:16 | 49.856
2021-08-30 | 16:16 | 49.857
2021-08-30 | 16:16 | 49.858
2021-08-30 | 16:16 | 49.859
2021-08-30 | 16:16 | 49.859
2021-08-30 | 16:16 | 49.859
2021-08-30 | 16:16 | 49.861
2021-08-30 | 16:16 | 49.861
2021-08-30 | 16:16 | 49.863
2021-08-30 | 16:16 | 49.866
2021-08-30 | 16:16 | 49.869
2021-08-30 | 16:16 | 49.868
2021-08-30 | 16:16 | 49.871
2021-08-30 | 16:16 | 49.872
2021-08-30 | 16:16 | 49.873
2021-08-30 | 16:16 | 49.873
2021-08-30 | 16:16 | 49.877
2021-08-30 | 16:16 | 49.873
2021-08-30 | 16:16 | 49.875
2021-08-30 | 16:16 | 49.871
2021-08-30 | 16:16 | 49.868
2021-08-30 | 16:16 | 49.869
2021-08-30 | 16:16 | 49.866
2021-08-30 | 16:16 | 49.862
2021-08-30 | 16:16 | 49.857
2021-08-30 | 16:16 | 49.852
2021-08-30 | 16:16 | 49.849
2021-08-30 | 16:16 | 49.848
2021-08-30 | 16:16 | 49.845
2021-08-30 | 16:16 | 49.844
2021-08-30 | 16:16 | 49.847
2021-08-30 | 16:16 | 49.849
2021-08-30 | 16:16 | 49.847
2021-08-30 | 16:16 | 49.846
2021-08-30 | 16:16 | 49.846
2021-08-30 | 16:16 | 49.846
2021-08-30 | 16:16 | 49.848
2021-08-30 | 16:16 | 49.851
2021-08-30 | 16:16 | 49.854
2021-08-30 | 16:16 | 49.859
2021-08-30 | 16:16 | 49.863
2021-08-30 | 16:16 | 49.867
2021-08-30 | 16:16 | 49.873
2021-08-30 | 16:16 | 49.88
2021-08-30 | 16:16 | 49.886
2021-08-30 | 16:16 | 49.895
2021-08-30 | 16:16 | 49.9
2021-08-30 | 16:16 | 49.909
2021-08-30 | 16:16 | 49.915
2021-08-30 | 16:16 | 49.923
2021-08-30 | 16:16 | 49.927
2021-08-30 | 16:16 | 49.927
2021-08-30 | 16:16 | 49.927
2021-08-30 | 16:16 | 49.927
2021-08-30 | 16:16 | 49.926
2021-08-30 | 16:16 | 49.923
2021-08-30 | 16:16 | 49.92
2021-08-30 | 16:16 | 49.919
2021-08-30 | 16:17 | 49.919
2021-08-30 | 16:17 | 49.919
2021-08-30 | 16:17 | 49.92
2021-08-30 | 16:17 | 49.919
2021-08-30 | 16:17 | 49.918
2021-08-30 | 16:17 | 49.916
2021-08-30 | 16:17 | 49.917
2021-08-30 | 16:17 | 49.917
2021-08-30 | 16:17 | 49.918
2021-08-30 | 16:17 | 49.921
2021-08-30 | 16:17 | 49.923
2021-08-30 | 16:17 | 49.924
2021-08-30 | 16:17 | 49.925
2021-08-30 | 16:17 | 49.924
2021-08-30 | 16:17 | 49.918
2021-08-30 | 16:17 | 49.915
2021-08-30 | 16:17 | 49.916
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.913
2021-08-30 | 16:17 | 49.915
2021-08-30 | 16:17 | 49.913
2021-08-30 | 16:17 | 49.915
2021-08-30 | 16:17 | 49.916
2021-08-30 | 16:17 | 49.918
2021-08-30 | 16:17 | 49.915
2021-08-30 | 16:17 | 49.915
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.913
2021-08-30 | 16:17 | 49.911
2021-08-30 | 16:17 | 49.908
2021-08-30 | 16:17 | 49.905
2021-08-30 | 16:17 | 49.903
2021-08-30 | 16:17 | 49.904
2021-08-30 | 16:17 | 49.906
2021-08-30 | 16:17 | 49.907
2021-08-30 | 16:17 | 49.908
2021-08-30 | 16:17 | 49.907
2021-08-30 | 16:17 | 49.907
2021-08-30 | 16:17 | 49.907
2021-08-30 | 16:17 | 49.907
2021-08-30 | 16:17 | 49.908
2021-08-30 | 16:17 | 49.909
2021-08-30 | 16:17 | 49.91
2021-08-30 | 16:17 | 49.912
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.915
2021-08-30 | 16:17 | 49.916
2021-08-30 | 16:17 | 49.916
2021-08-30 | 16:17 | 49.914
2021-08-30 | 16:17 | 49.913
2021-08-30 | 16:17 | 49.912
2021-08-30 | 16:17 | 49.913
2021-08-30 | 16:17 | 49.918
2021-08-30 | 16:17 | 49.923
2021-08-30 | 16:17 | 49.926
2021-08-30 | 16:17 | 49.927
2021-08-30 | 16:18 | 49.929
2021-08-30 | 16:18 | 49.928
2021-08-30 | 16:18 | 49.928
2021-08-30 | 16:18 | 49.927
2021-08-30 | 16:18 | 49.926
2021-08-30 | 16:18 | 49.925
2021-08-30 | 16:18 | 49.925
2021-08-30 | 16:18 | 49.927
2021-08-30 | 16:18 | 49.932
2021-08-30 | 16:18 | 49.933
2021-08-30 | 16:18 | 49.935
2021-08-30 | 16:18 | 49.939
2021-08-30 | 16:18 | 49.937
2021-08-30 | 16:18 | 49.939
2021-08-30 | 16:18 | 49.94
2021-08-30 | 16:18 | 49.941
2021-08-30 | 16:18 | 49.945
2021-08-30 | 16:18 | 49.949
2021-08-30 | 16:18 | 49.954
2021-08-30 | 16:18 | 49.958
2021-08-30 | 16:18 | 49.961
2021-08-30 | 16:18 | 49.961
2021-08-30 | 16:18 | 49.959
2021-08-30 | 16:18 | 49.954
2021-08-30 | 16:18 | 49.95
2021-08-30 | 16:18 | 49.944
2021-08-30 | 16:18 | 49.942
2021-08-30 | 16:18 | 49.941
2021-08-30 | 16:18 | 49.942
2021-08-30 | 16:18 | 49.944
2021-08-30 | 16:18 | 49.944
2021-08-30 | 16:18 | 49.943
2021-08-30 | 16:18 | 49.944
2021-08-30 | 16:18 | 49.943
2021-08-30 | 16:18 | 49.942
2021-08-30 | 16:18 | 49.94
2021-08-30 | 16:18 | 49.936
2021-08-30 | 16:18 | 49.937
2021-08-30 | 16:18 | 49.939
2021-08-30 | 16:18 | 49.941
2021-08-30 | 16:18 | 49.94
2021-08-30 | 16:18 | 49.939
2021-08-30 | 16:18 | 49.936
2021-08-30 | 16:18 | 49.934
2021-08-30 | 16:18 | 49.931
2021-08-30 | 16:18 | 49.931
2021-08-30 | 16:18 | 49.929
2021-08-30 | 16:18 | 49.928
2021-08-30 | 16:18 | 49.928
2021-08-30 | 16:18 | 49.929
2021-08-30 | 16:18 | 49.933
2021-08-30 | 16:18 | 49.934
2021-08-30 | 16:18 | 49.937
2021-08-30 | 16:18 | 49.936
2021-08-30 | 16:18 | 49.938
2021-08-30 | 16:18 | 49.938
2021-08-30 | 16:18 | 49.937
2021-08-30 | 16:18 | 49.939
2021-08-30 | 16:18 | 49.939
2021-08-30 | 16:18 | 49.933
2021-08-30 | 16:18 | 49.933
2021-08-30 | 16:19 | 49.932
2021-08-30 | 16:19 | 49.931
2021-08-30 | 16:19 | 49.93
2021-08-30 | 16:19 | 49.932
2021-08-30 | 16:19 | 49.931
2021-08-30 | 16:19 | 49.931
2021-08-30 | 16:19 | 49.933
2021-08-30 | 16:19 | 49.936
2021-08-30 | 16:19 | 49.941
2021-08-30 | 16:19 | 49.941
2021-08-30 | 16:19 | 49.943
2021-08-30 | 16:19 | 49.941
2021-08-30 | 16:19 | 49.942
2021-08-30 | 16:19 | 49.943
2021-08-30 | 16:19 | 49.945
2021-08-30 | 16:19 | 49.948
2021-08-30 | 16:19 | 49.95
2021-08-30 | 16:19 | 49.952
2021-08-30 | 16:19 | 49.952
2021-08-30 | 16:19 | 49.955
2021-08-30 | 16:19 | 49.954
2021-08-30 | 16:19 | 49.954
2021-08-30 | 16:19 | 49.953
2021-08-30 | 16:19 | 49.95
2021-08-30 | 16:19 | 49.95
2021-08-30 | 16:19 | 49.95
2021-08-30 | 16:19 | 49.948
2021-08-30 | 16:19 | 49.948
2021-08-30 | 16:19 | 49.946
2021-08-30 | 16:19 | 49.948
2021-08-30 | 16:19 | 49.949
2021-08-30 | 16:19 | 49.949
2021-08-30 | 16:19 | 49.948
2021-08-30 | 16:19 | 49.947
2021-08-30 | 16:19 | 49.944
2021-08-30 | 16:19 | 49.942
2021-08-30 | 16:19 | 49.939
2021-08-30 | 16:19 | 49.934
2021-08-30 | 16:19 | 49.931
2021-08-30 | 16:19 | 49.927
2021-08-30 | 16:19 | 49.924
2021-08-30 | 16:19 | 49.923
2021-08-30 | 16:19 | 49.923
2021-08-30 | 16:19 | 49.925
2021-08-30 | 16:19 | 49.928
2021-08-30 | 16:19 | 49.931
2021-08-30 | 16:19 | 49.936
2021-08-30 | 16:19 | 49.941
2021-08-30 | 16:19 | 49.947
2021-08-30 | 16:19 | 49.949
2021-08-30 | 16:19 | 49.949
2021-08-30 | 16:19 | 49.95
2021-08-30 | 16:19 | 49.949
2021-08-30 | 16:19 | 49.946
2021-08-30 | 16:19 | 49.944
2021-08-30 | 16:19 | 49.944
2021-08-30 | 16:19 | 49.943
2021-08-30 | 16:19 | 49.941
2021-08-30 | 16:19 | 49.937
2021-08-30 | 16:20 | 49.936
2021-08-30 | 16:20 | 49.934
2021-08-30 | 16:20 | 49.933
2021-08-30 | 16:20 | 49.931
2021-08-30 | 16:20 | 49.929
2021-08-30 | 16:20 | 49.928
2021-08-30 | 16:20 | 49.923
2021-08-30 | 16:20 | 49.921
2021-08-30 | 16:20 | 49.919
2021-08-30 | 16:20 | 49.92
2021-08-30 | 16:20 | 49.922
2021-08-30 | 16:20 | 49.926
2021-08-30 | 16:20 | 49.929
2021-08-30 | 16:20 | 49.934
2021-08-30 | 16:20 | 49.938
2021-08-30 | 16:20 | 49.945
2021-08-30 | 16:20 | 49.948
2021-08-30 | 16:20 | 49.951
2021-08-30 | 16:20 | 49.955
2021-08-30 | 16:20 | 49.957
2021-08-30 | 16:20 | 49.959
2021-08-30 | 16:20 | 49.959
2021-08-30 | 16:20 | 49.959
2021-08-30 | 16:20 | 49.965
2021-08-30 | 16:20 | 49.967
2021-08-30 | 16:20 | 49.971
2021-08-30 | 16:20 | 49.975
2021-08-30 | 16:20 | 49.976
2021-08-30 | 16:20 | 49.98
2021-08-30 | 16:20 | 49.983
2021-08-30 | 16:20 | 49.987
2021-08-30 | 16:20 | 49.987
2021-08-30 | 16:20 | 49.984
2021-08-30 | 16:20 | 49.983
2021-08-30 | 16:20 | 49.983
2021-08-30 | 16:20 | 49.983
2021-08-30 | 16:20 | 49.986
2021-08-30 | 16:20 | 49.988
2021-08-30 | 16:20 | 49.991
2021-08-30 | 16:20 | 49.997
2021-08-30 | 16:20 | 50.003
2021-08-30 | 16:20 | 50.008
2021-08-30 | 16:20 | 50.01
2021-08-30 | 16:20 | 50.011
2021-08-30 | 16:20 | 50.012
2021-08-30 | 16:20 | 50.009
2021-08-30 | 16:20 | 50.009
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:20 | 50.006
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:20 | 50.006
2021-08-30 | 16:20 | 50.006
2021-08-30 | 16:20 | 50.006
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:20 | 50.005
2021-08-30 | 16:20 | 50.005
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:20 | 50.008
2021-08-30 | 16:20 | 50.007
2021-08-30 | 16:21 | 50.008
2021-08-30 | 16:21 | 50.011
2021-08-30 | 16:21 | 50.015
2021-08-30 | 16:21 | 50.018
2021-08-30 | 16:21 | 50.023
2021-08-30 | 16:21 | 50.025
2021-08-30 | 16:21 | 50.025
2021-08-30 | 16:21 | 50.025
2021-08-30 | 16:21 | 50.023
2021-08-30 | 16:21 | 50.026
2021-08-30 | 16:21 | 50.026
2021-08-30 | 16:21 | 50.028
2021-08-30 | 16:21 | 50.027
2021-08-30 | 16:21 | 50.027
2021-08-30 | 16:21 | 50.025
2021-08-30 | 16:21 | 50.02
2021-08-30 | 16:21 | 50.015
2021-08-30 | 16:21 | 50.012
2021-08-30 | 16:21 | 50.007
2021-08-30 | 16:21 | 50.004
2021-08-30 | 16:21 | 50.003
2021-08-30 | 16:21 | 50.004
2021-08-30 | 16:21 | 50.003
2021-08-30 | 16:21 | 50.002
2021-08-30 | 16:21 | 50.002
2021-08-30 | 16:21 | 50.004
2021-08-30 | 16:21 | 50.005
2021-08-30 | 16:21 | 50.007
2021-08-30 | 16:21 | 50.01