## Menu
Electricity Ten Year Statement 2021
Appendix D - Fault Levels at Minimum
Table | Title
D1.0 | SHE Transmission Fault Levels (kA) at Minimum, Summer 2021/22
D2.0 | SPT Transmission Fault Levels (kA) at Minimum, Summer 2021/22
D3.0 | NGET Transmission Fault Levels (kA) at Minimum, Summer 2021/22

## D1.0
ETYS 21 Yr 01 - SHE Transmission Fault Levels (kA), Summer 2021/22
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABERDEEN BAY | 132 | 13.91 | 5.91 | 0.71 | 9.06 | 14.4 | 6.1 | 0.9 | 9.54
ABERNETHY | 132 | 12.31 | 6.09 | 0.03 | 8.63 | 14 | 6.62 | 0.19 | 9.56 | Menu
ABERNETHY | 33 | 23.05 | 9.56 | 0.62 | 14.14 | 2.19 | 1.52 | 0 | 2.15
A-CHRUACH | 132 | 15.52 | 6.85 | 0.43 | 10.12 | 15.99 | 6.86 | 0.85 | 10.56
AIGAS | 132 | 25.25 | 11.3 | 0.59 | 16.57 | 25.63 | 11.78 | 0.52 | 17.18
ALNESS | 132 | 26.15 | 10.12 | 4.14 | 18.46 | 31 | 12.13 | 4.37 | 21.53
ALNESS | 33 | 28.58 | 10.52 | 7.65 | 22.54 | 2.2 | 1.53 | 0 | 2.16
AN SUIDHE | 132 | 18.53 | 8.27 | 0.42 | 12.12 | 18.99 | 8.3 | 0.73 | 12.47
ARBROATH | 132 | 12 | 5.57 | 0.31 | 8.18 | 11.73 | 5.32 | 0.61 | 8.12
ARBROATH | 33 | 23.51 | 9.32 | 1.8 | 14.99 | 1.57 | 1.09 | 0 | 1.54
ARDKINGLAS | 132 | 22.82 | 10.8 | 0.17 | 15.44 | 21.63 | 10.13 | 0.43 | 14.77
ARDMORE | 132 | 1.89 | 1.07 | 0 | 1.52 | 2.62 | 1.45 | 0 | 2.05
ARDMORE | 33 | 6.16 | 3.2 | 0 | 4.53 | 1.02 | 0.71 | 0 | 1
BEAULY | 400 | 17.19 | 6.59 | 4.53 | 13.85 | 19.74 | 7.61 | 5.04 | 15.8
BEAULY | 275 | 29.83 | 11.59 | 7.35 | 23.75 | 35.56 | 13.93 | 8.18 | 27.89
BEAULY | 132 | 36.09 | 14.77 | 4.12 | 25 | 44.72 | 18.25 | 5.36 | 31.17
BEAULY | 33 | 28.26 | 10.78 | 4.28 | 19.52 | 1.47 | 1.02 | 0 | 1.44
BEINNEUN | 132 | 11.76 | 5.57 | 0.04 | 7.92 | 13.92 | 6.43 | 0.18 | 9.27
BERRY BURN | 275 | 21.55 | 8.67 | 3.52 | 15.78 | 20.18 | 8.26 | 3.02 | 14.71
BERRY BURN | 33 | 21.98 | 8.1 | 5.25 | 16.71 | 1.12 | 0.78 | 0 | 1.1
BHLARAIDH | 132 | 12.5 | 5.76 | 0.08 | 8.23 | 14.55 | 6.64 | 0.3 | 9.7
BLACKHILLOCK | 400 | 19.03 | 7.39 | 4.81 | 15.26 | 23.08 | 8.95 | 5.79 | 18.45
BLACKHILLOCK | 132 | 26.76 | 10.17 | 5.67 | 20.05 | 32.62 | 12.47 | 6.49 | 24.13
BLACKHILLOCK I | 275 | 29.15 | 11.55 | 6.4 | 22.73 | 35.93 | 14.24 | 7.81 | 27.95
BLACKHILLOCK II | 275 | 22.25 | 8.69 | 5.51 | 17.8 | 27.02 | 10.59 | 6.24 | 21.22
BOAT OF GARTEN | 132 | 9.3 | 4.29 | 0.23 | 6.3 | 10.59 | 4.77 | 0.4 | 7.15
BOAT OF GARTEN | 33 | 22.99 | 9.21 | 1.12 | 14.15 | 2.19 | 1.52 | 0 | 2.14
BRACO WEST | 275 | 26.16 | 10.24 | 5.28 | 19.76 | 24.45 | 9.71 | 4.7 | 18.43
BRACO WEST | 33 | 41.05 | 15.2 | 9.57 | 31.06 | 2.24 | 1.55 | 0 | 2.19
BRECHIN | 132 | 10.68 | 5.36 | 0.01 | 7.59 | 11.51 | 5.49 | 0.06 | 7.82
BRIDGE OF DUN | 132 | 9.1 | 4.65 | 0.01 | 6.58 | 10.11 | 4.87 | 0.07 | 6.96
BRIDGE OF DUN | 33 | 18.91 | 8.03 | 0.28 | 11.63 | 2.17 | 1.51 | 0 | 2.13
BROADFORD | 132 | 3.28 | 1.8 | 0 | 2.55 | 3.97 | 2.06 | 0.01 | 2.92
BROADFORD | 33 | 6.66 | 2.98 | 0.02 | 4.24 | 0.76 | 0.52 | 0 | 0.74
BRORA | 132 | 11.17 | 5.36 | 0.06 | 7.64 | 11.38 | 5.34 | 0.25 | 7.8
BRORA | 33 | 13.95 | 5.57 | 0.78 | 8.66 | 1.13 | 0.78 | 0 | 1.11
BURGHMUIR | 132 | 10.36 | 5.22 | 0.01 | 7.39 | 11.97 | 5.74 | 0.1 | 8.22
BURGHMUIR | 33 | 20.99 | 8.91 | 0.33 | 12.93 | 2.17 | 1.5 | 0 | 2.13
CAIRNFORD | 275 | 25.94 | 10.39 | 4.84 | 19.54 | 28.62 | 11.61 | 4.7 | 21.12
CAIRNFORD | 33 | 25.09 | 9.23 | 6.3 | 19.34 | 1.15 | 0.8 | 0 | 1.13
CARRADALE | 132 | 12.91 | 5.4 | 1.1 | 8.74 | 15.29 | 6.31 | 1.56 | 10.49
CARRADALE I | 33 | 24.1 | 9.25 | 3.72 | 16.81 | 2.22 | 1.54 | 0 | 2.17
CARRADALE II | 33 | 24.2 | 9.28 | 3.82 | 16.94 | 2.22 | 1.54 | 0 | 2.18
CASSLEY | 132 | 7.5 | 3.54 | 0.18 | 5.19 | 7.08 | 3.28 | 0.25 | 4.88
CASSLEY | 33 | 12.06 | 4.7 | 1.43 | 8.08 | 1.11 | 0.77 | 0 | 1.09
CEANNACROC | 132 | 11.38 | 5.43 | 0.04 | 7.71 | 13.31 | 6.19 | 0.15 | 8.9
CEANNACROC | 33 | 2.55 | 1.02 | 0.12 | 1.57 | 2.74 | 1.1 | 0.12 | 1.68
CHARLESTON | 132 | 28.42 | 11.93 | 2.6 | 19.48 | 33.8 | 14.32 | 3.17 | 23.42
CHARLESTON | 33 | 28.54 | 10.74 | 5.96 | 21.15 | 1.61 | 1.11 | 0 | 1.58
CLACHAN | 132 | 22.86 | 10.69 | 0.45 | 15.57 | 21.99 | 10.26 | 0.68 | 15.2
CLACHAN | 33 | 4.08 | 1.58 | 0.42 | 2.66 | 4.3 | 1.66 | 0.44 | 2.79
CLAYHILLS | 132 | 26.65 | 11.06 | 2.29 | 17.93 | 33.55 | 14.22 | 2.39 | 22.5
CLAYHILLS | 33 | 29.97 | 11.49 | 4.23 | 20.48 | 3.15 | 2.18 | 0 | 3.09
CLUNIE | 132 | 16.39 | 7.48 | 0.26 | 10.84 | 16.81 | 7.59 | 0.55 | 11.28
CONNAGILL | 275 | 13.19 | 5.21 | 3.01 | 10.38 | 15.41 | 6.12 | 3.24 | 11.9
CONNAGILL | 132 | 12.75 | 4.84 | 2.76 | 9.61 | 15.65 | 5.96 | 3.13 | 11.56
CORRIEGARTH | 132 | 8.24 | 3.36 | 0.5 | 5.25 | 9.37 | 3.78 | 0.8 | 6.15
CORRIEMOILLIE | 132 | 18.93 | 7.76 | 1.49 | 12.46 | 22.23 | 9.09 | 1.97 | 14.83
COUPAR ANGUS | 132 | 17.96 | 7.8 | 0.83 | 11.86 | 18.55 | 7.89 | 1.44 | 12.6
COUPAR ANGUS | 33 | 28.73 | 10.87 | 5.16 | 20.53 | 2.23 | 1.55 | 0 | 2.19
CRAIGIEBUCKLER | 132 | 28.31 | 11.62 | 2.73 | 19.16 | 36.34 | 15.07 | 3.06 | 24.37
CRAIGIEBUCKLER | 33 | 25.4 | 9.94 | 2.27 | 16.32 | 1.59 | 1.1 | 0 | 1.56
CROSSAIG | 132 | 18.27 | 7.74 | 1.64 | 12.59 | 22.96 | 9.65 | 2.12 | 15.76
CULLIGRAN | 132 | 14.04 | 6.88 | 0.04 | 9.77 | 14.07 | 6.73 | 0.15 | 9.66
DALCHORK | 132 | 17.24 | 7.03 | 2.39 | 12.32 | 17.49 | 7.19 | 2.18 | 12.35
DALLAS | 275 | 22 | 8.85 | 3.65 | 16.17 | 21.02 | 8.6 | 3.19 | 15.35
DALLAS | 33 | 22.35 | 8.23 | 5.35 | 17 | 1.14 | 0.79 | 0 | 1.12
DEANIE | 132 | 10.07 | 5.11 | 0.01 | 7.23 | 10.17 | 4.94 | 0.07 | 7.05
DORENELL | 132 | 10.94 | 4.67 | 0.33 | 6.93 | 12.74 | 5.3 | 0.68 | 8.17
DOUNREAY | 275 | 13.8 | 5.43 | 3.39 | 11.07 | 17.12 | 6.73 | 4.13 | 13.65
DOUNREAY | 132 | 15.2 | 5.79 | 3.31 | 11.5 | 20.47 | 7.81 | 4.29 | 15.34
DOUNREAY | 33 | 23.87 | 8.82 | 5.84 | 18.31 | 2.26 | 1.57 | 0 | 2.22
DUDHOPE | 132 | 26.62 | 11.38 | 1.82 | 17.92 | 30.59 | 13.52 | 1.64 | 20.77
DUDHOPE | 33 | 30.36 | 11.72 | 4.21 | 20.78 | 2.95 | 2.04 | 0 | 2.89
DUNBEATH | 132 | 10.44 | 4.93 | 0.09 | 7.06 | 10.3 | 4.83 | 0.23 | 7.05
DUNBEATH | 33 | 9.68 | 3.81 | 0.71 | 6.09 | 0.41 | 0.29 | 0 | 0.41
DUNMAGLASS | 132 | 9.66 | 3.85 | 0.88 | 6.32 | 11.15 | 4.41 | 1.25 | 7.49
DUNOON | 132 | 8.71 | 4.54 | 0.02 | 6.44 | 8.71 | 4.28 | 0.07 | 6.12
DUNOON | 33 | 21.59 | 9.61 | 0.1 | 13.68 | 2.13 | 1.48 | 0 | 2.09
DUNVEGAN | 132 | 2.11 | 1.19 | 0 | 1.69 | 2.97 | 1.65 | 0 | 2.33
DUNVEGAN | 33 | 6.58 | 3.37 | 0 | 4.77 | 1.04 | 0.72 | 0 | 1.02
DYCE | 132 | 17.64 | 7.52 | 0.96 | 11.6 | 18.4 | 7.84 | 1.29 | 12.38
DYCE | 33 | 30.62 | 11.68 | 4.73 | 21.24 | 2.26 | 1.57 | 0 | 2.22
EDINBANE | 132 | 2.24 | 1.26 | 0 | 1.79 | 3.13 | 1.72 | 0 | 2.44
ELGIN | 132 | 13.97 | 6 | 0.67 | 9.16 | 13.96 | 5.96 | 0.95 | 9.38
ELGIN | 33 | 25.1 | 9.68 | 3.22 | 16.91 | 1.87 | 1.29 | 0 | 1.83
ERROCHTY | 132 | 29.68 | 12.23 | 4.51 | 21.8 | 33.88 | 14.12 | 4.39 | 24.35
FARIGAIG I | 275 | 25.84 | 10.16 | 5.7 | 20.07 | 24.72 | 9.98 | 4.47 | 18.58
FARIGAIG I | 132 | 11.49 | 4.44 | 1.68 | 7.96 | 13.37 | 5.15 | 2.05 | 9.34
FARIGAIG II | 275 | 25.84 | 10.16 | 5.7 | 20.07 | 24.73 | 9.99 | 4.49 | 18.61
FARIGAIG II | 132 | 11.48 | 4.43 | 1.7 | 7.96 | 13.53 | 5.21 | 2.11 | 9.47
FARR | 132 | 17.72 | 7.67 | 0.43 | 11.27 | 18.41 | 8.05 | 0.73 | 12.1
FASNAKYLE | 275 | 24.06 | 9.33 | 5.67 | 18.86 | 24.95 | 9.81 | 5.3 | 19.17
FASNAKYLE | 33 | 50.3 | 18.56 | 11.96 | 38.21 | 2.25 | 1.56 | 0 | 2.2
FERNOCH | 132 | 9.31 | 5.03 | 0.02 | 7.13 | 11.18 | 5.68 | 0.07 | 8.1
FETTERESSO | 275 | 25.87 | 10.42 | 4.27 | 19.01 | 25.37 | 10.36 | 3.92 | 18.57
FETTERESSO | 132 | 18.66 | 7.23 | 2.71 | 12.93 | 21.93 | 8.48 | 3.26 | 15.25
FETTERESSO | 33 | 18.76 | 7.01 | 3.44 | 13.34 | 1.14 | 0.79 | 0 | 1.12
FIDDES | 132 | 10.8 | 5.47 | 0.01 | 7.75 | 12.22 | 5.82 | 0.09 | 8.32
FIDDES | 33 | 20.85 | 8.78 | 0.36 | 12.77 | 2.2 | 1.52 | 0 | 2.15
FINLARIG | 132 | 16.71 | 8.09 | 0.06 | 11.49 | 18.48 | 8.71 | 0.18 | 12.5
FORT AUGUSTUS | 400 | 15.77 | 6.04 | 4.06 | 12.6 | 18.88 | 7.25 | 4.87 | 15.12
FORT AUGUSTUS | 275 | 22.09 | 8.56 | 5.16 | 17.26 | 23.34 | 9.08 | 5.5 | 18.34
FORT AUGUSTUS | 33 | 7.17 | 2.68 | 1.38 | 5.17 | 0.73 | 0.5 | 0 | 0.71
FORT AUGUSTUS I | 132 | 33.78 | 12.81 | 7.21 | 25.32 | 43.24 | 16.47 | 8.73 | 32.02
FORT AUGUSTUS II | 132 | 27.01 | 10.17 | 6.03 | 20.42 | 34.05 | 12.96 | 6.77 | 25.1
FORT WILLIAM | 132 | 7.25 | 3.6 | 0.09 | 5.18 | 8.29 | 3.95 | 0.23 | 5.81
FORT WILLIAM | 33 | 20.91 | 8.95 | 0.24 | 12.9 | 2.2 | 1.52 | 0 | 2.15
FOYERS | 275 | 26.16 | 10.24 | 6.13 | 20.62 | 22.4 | 9.16 | 3.53 | 16.48
FRASERBURGH | 132 | 10.27 | 4.67 | 0.25 | 6.85 | 10.96 | 4.93 | 0.5 | 7.47
FRASERBURGH | 33 | 21.93 | 8.67 | 1.46 | 13.72 | 2.18 | 1.51 | 0 | 2.14
FYRISH | 275 | 19.64 | 7.73 | 4.08 | 15.01 | 20.71 | 8.25 | 4.19 | 15.86
FYRISH | 132 | 27.82 | 10.61 | 5.53 | 20.53 | 33.21 | 12.69 | 6.52 | 24.46
GLEN KYLLACHY | 132 | 22.04 | 9.35 | 0.78 | 14 | 23.88 | 10.14 | 1.16 | 15.5
GLENDOE | 132 | 29.35 | 11.64 | 3.49 | 19.95 | 35.44 | 14.42 | 3.6 | 23.99
GLENFARCLAS | 132 | 5.16 | 2.52 | 0.03 | 3.59 | 5.79 | 2.72 | 0.09 | 3.94
GLENFARCLAS | 33 | 9.5 | 3.98 | 0.21 | 5.85 | 1.1 | 0.76 | 0 | 1.08
GLENMORISTON | 132 | 13.6 | 6.26 | 0.09 | 8.94 | 15.73 | 7.14 | 0.31 | 10.41
GORDONBUSH | 275 | 13.91 | 5.52 | 2.74 | 10.54 | 15 | 6.01 | 2.9 | 11.39
GRIFFIN | 132 | 12.08 | 5.96 | 0.03 | 8.45 | 13.38 | 6.36 | 0.2 | 9.19
GRUDIE BRIDGE | 132 | 15.83 | 6.62 | 0.87 | 10.24 | 17.95 | 7.49 | 1.26 | 11.85
GRUDIE BRIDGE | 33 | 25.3 | 9.63 | 3.53 | 17.15 | 2.19 | 1.52 | 0 | 2.15
INVERARAY | 132 | 25.4 | 11.77 | 0.37 | 17.02 | 26.58 | 12.23 | 0.49 | 17.78
INVERARNAN | 132 | 40.38 | 16.73 | 4.5 | 28.15 | 45.53 | 18.88 | 4.72 | 31.42
INVERGARRY | 132 | 15.75 | 7.34 | 0.1 | 10.49 | 16.25 | 7.55 | 0.24 | 10.92
INVERNESS | 132 | 34.1 | 13.86 | 4.01 | 23.6 | 40.85 | 16.66 | 4.65 | 28.21
INVERNESS | 33 | 39.64 | 15.09 | 6.96 | 28.3 | 3.33 | 2.31 | 0 | 3.26
KEITH | 275 | 28.4 | 11.3 | 5.95 | 21.93 | 34.87 | 13.91 | 7.09 | 26.76
KEITH | 132 | 24.47 | 9.67 | 4.32 | 18 | 32.43 | 13.1 | 5.47 | 24
KEITH I | 33 | 29.73 | 11.18 | 6.43 | 22.23 | 2.2 | 1.53 | 0 | 2.16
KEITH II | 33 | 28.24 | 10.49 | 6.67 | 21.51 | 2.23 | 1.55 | 0 | 2.19
KILLIN | 132 | 18.8 | 8.97 | 0.09 | 12.77 | 21.88 | 10.11 | 0.28 | 14.57
KILLIN | 33 | 25.97 | 10.43 | 1.23 | 15.98 | 2.17 | 1.5 | 0 | 2.12
KILMORACK | 132 | 31.6 | 13.42 | 1.95 | 20.92 | 36.01 | 15.46 | 1.91 | 23.77
KINLOCHLEVEN | 132 | 4.89 | 2.46 | 0.03 | 3.5 | 5.59 | 2.66 | 0.08 | 3.85
KINLOCHLEVEN | 33 | 9.42 | 4.02 | 0.21 | 5.89 | 0.73 | 0.51 | 0 | 0.72
KINTORE | 275 | 29.49 | 11.81 | 5.64 | 22.34 | 33.72 | 13.61 | 6.13 | 25.38
KINTORE | 132 | 29.89 | 11.99 | 4.24 | 21.19 | 38.11 | 15.31 | 5.23 | 26.88
KINTORE | 33 | 39.75 | 15.16 | 6.82 | 28.26 | 3.37 | 2.32 | 0 | 3.29
KNOCKNAGAEL | 275 | 29.91 | 11.67 | 7.17 | 23.68 | 33.77 | 13.35 | 7.45 | 26.33
KNOCKNAGAEL | 132 | 36.86 | 14.75 | 5.63 | 26.49 | 44.28 | 17.67 | 6.86 | 31.85
LAIRG | 33 | 15.8 | 5.88 | 3.73 | 12.05 | 1.12 | 0.78 | 0 | 1.1
LIMEKILNS | 132 | 12.94 | 5.08 | 1.79 | 8.97 | 15.42 | 6.1 | 2.03 | 10.66
LOCH BUIDHE | 275 | 18.63 | 7.36 | 3.92 | 14.33 | 20.28 | 8.09 | 4.2 | 15.64
LOCH BUIDHE | 132 | 23.63 | 9.64 | 4.2 | 17.84 | 29.27 | 11.92 | 4.88 | 21.74
LOCHAY | 132 | 16.39 | 7.96 | 0.05 | 11.31 | 18.26 | 8.62 | 0.16 | 12.35
LUICHART | 132 | 20.5 | 8.4 | 1.66 | 13.54 | 22.66 | 9.29 | 1.96 | 15.09
LUNANHEAD | 132 | 14.73 | 6.33 | 0.81 | 9.77 | 14.52 | 6.19 | 1.31 | 10.05
LUNANHEAD | 33 | 26.41 | 10.22 | 4.03 | 18.48 | 2.2 | 1.52 | 0 | 2.16
LYNDHURST | 132 | 24.28 | 10.59 | 1.17 | 16.15 | 27.03 | 11.91 | 1.41 | 18.25
LYNDHURST | 33 | 29.49 | 11.4 | 3.7 | 19.83 | 2.98 | 2.06 | 0 | 2.92
MACDUFF | 132 | 7.82 | 3.69 | 0.11 | 5.33 | 8.5 | 3.89 | 0.27 | 5.77
MACDUFF | 33 | 23.69 | 10.09 | 0.3 | 14.57 | 2.26 | 1.57 | 0 | 2.22
MELGARVE | 400 | 14.86 | 5.69 | 3.76 | 11.81 | 17.03 | 6.57 | 4.11 | 13.39
MELGARVE | 132 | 25.86 | 9.75 | 5.68 | 19.46 | 33 | 12.51 | 6.61 | 24.3
MILLENNIUM | 132 | 13.16 | 6.1 | 0.08 | 8.71 | 15.44 | 7.05 | 0.22 | 10.2
MILLENNIUM SOUTH | 132 | 23.72 | 9.59 | 1.83 | 15.39 | 25.33 | 10.32 | 2.08 | 16.68
MILTON OF CRAIGIE | 132 | 27.96 | 11.75 | 2.67 | 19.29 | 32.72 | 14.01 | 2.84 | 22.64
MILTON OF CRAIGIE | 33 | 29 | 11.18 | 4.31 | 20.12 | 3.37 | 2.34 | 0 | 3.3
MOSSFORD | 132 | 17.37 | 7.21 | 1.1 | 11.29 | 20.16 | 8.34 | 1.52 | 13.31
MYBSTER I | 132 | 15.23 | 6.41 | 1.57 | 10.64 | 17.2 | 7.37 | 1.14 | 11.56
MYBSTER I | 33 | 25.28 | 9.4 | 5.79 | 19.08 | 2.27 | 1.57 | 0 | 2.22
MYBSTER II | 33 | 25.35 | 9.38 | 6.27 | 19.53 | 2.27 | 1.57 | 0 | 2.23
MYBSTER II | 132 | 13.53 | 5.16 | 2.97 | 10.27 | 16.74 | 6.38 | 3.7 | 12.72
MYBSTER III | 33 | 25.66 | 9.46 | 6.82 | 20.19 | 2.27 | 1.57 | 0 | 2.23
NAIRN | 132 | 13.26 | 5.8 | 0.46 | 8.66 | 12.84 | 5.54 | 0.69 | 8.52
NAIRN | 33 | 24.23 | 9.5 | 2.03 | 15.46 | 3.1 | 2.15 | 0 | 3.04
NANT | 132 | 10.03 | 5.28 | 0.06 | 7.53 | 9.78 | 4.85 | 0.17 | 7.03
NEW DEER | 275 | 23.91 | 9.58 | 4.39 | 17.93 | 23.64 | 9.68 | 3.43 | 17.12
ORRIN | 132 | 22.47 | 9.23 | 1.84 | 14.89 | 25.01 | 10.27 | 2.16 | 16.69
PERSLEY | 275 | 21.04 | 8.52 | 3.36 | 15.41 | 22.27 | 9.04 | 3.76 | 16.54
PERSLEY | 132 | 28.08 | 11.49 | 3.18 | 19.43 | 36.7 | 15.06 | 4.02 | 25.33
PERSLEY | 33 | 29.01 | 10.89 | 6.5 | 21.9 | 2.24 | 1.55 | 0 | 2.19
PETERHEAD | 275 | 22.3 | 9 | 3.74 | 16.47 | 23.84 | 9.67 | 4 | 17.68
PETERHEAD | 132 | 22.81 | 8.83 | 3.77 | 16.25 | 29.36 | 11.43 | 4.47 | 20.63
PETERHEAD GRANGE | 132 | 16.83 | 6.96 | 1.06 | 10.91 | 19.14 | 8.01 | 1.3 | 12.63
PETERHEAD GRANGE | 33 | 23.69 | 9.08 | 2.86 | 15.7 | 0.6 | 0.41 | 0 | 0.58
PORT ANN | 132 | 11.32 | 5.25 | 0.12 | 7.54 | 12.06 | 5.39 | 0.27 | 7.89
PORT ANN | 33 | 18.69 | 7.76 | 0.5 | 11.48 | 1.81 | 1.25 | 0 | 1.77
QUOICH | 132 | 10.76 | 4.77 | 0.15 | 6.9 | 10.31 | 4.5 | 0.33 | 6.7
RANNOCH | 132 | 9.98 | 4.83 | 0.24 | 7.08 | 10.23 | 4.76 | 0.55 | 7.28
RANNOCH | 33 | 23.43 | 9.49 | 1.1 | 14.52 | 2.18 | 1.51 | 0 | 2.14
REDMOSS | 132 | 25.05 | 10.61 | 1.56 | 16.57 | 30.46 | 13.28 | 1.56 | 20.34
REDMOSS | 33 | 27.69 | 10.63 | 3.9 | 18.94 | 3.11 | 2.15 | 0 | 3.05
ROTHIENORMAN | 275 | 26.68 | 10.62 | 5.37 | 20.38 | 29 | 11.71 | 5.23 | 21.79
ROTHIENORMAN | 33 | 35.9 | 13.09 | 11.24 | 29.75 | 2.29 | 1.59 | 0 | 2.24
SHIN | 132 | 19.97 | 8.72 | 0.97 | 13.3 | 20.96 | 9.14 | 1.73 | 14.65
SHIN | 33 | 26.04 | 9.97 | 3.74 | 17.84 | 2.19 | 1.52 | 0 | 2.14
SLOY | 132 | 37.24 | 16.01 | 2.17 | 24.82 | 41.53 | 17.97 | 2.52 | 27.92
SPITTAL | 132 | 17.36 | 7.01 | 3.65 | 13.57 | 22.39 | 8.97 | 4.67 | 17.36
SPITTAL | 275 | 13.38 | 5.26 | 3.53 | 10.97 | 17.03 | 6.67 | 4.51 | 13.94
ST FERGUS GAS TERMINAL | 132 | 16.59 | 6.97 | 0.81 | 10.67 | 18.53 | 7.95 | 0.81 | 12.05
ST FERGUS MOBIL | 132 | 15.92 | 6.85 | 0.49 | 10.18 | 17.51 | 7.79 | 0.48 | 11.5
ST FILLANS | 132 | 8.89 | 4.54 | 0.01 | 6.42 | 8.77 | 4.33 | 0.05 | 6.18
ST FILLANS | 33 | 4.16 | 1.58 | 0.66 | 2.9 | 1.02 | 0.7 | 0 | 1
STRATHBRORA | 275 | 14.96 | 5.93 | 2.96 | 11.35 | 16.2 | 6.48 | 3.2 | 12.36
STRATHY NORTH | 132 | 9.5 | 3.81 | 0.89 | 6.27 | 10.82 | 4.31 | 1.31 | 7.41
STRICHEN | 132 | 10.85 | 4.9 | 0.29 | 7.22 | 11.59 | 5.19 | 0.57 | 7.92
STRICHEN | 33 | 22.35 | 8.72 | 1.91 | 14.24 | 2.19 | 1.52 | 0 | 2.15
STRONELAIRG | 132 | 21.84 | 8.31 | 4.08 | 15.83 | 27.77 | 10.76 | 4.9 | 20.13
TARLAND | 132 | 7.75 | 3.78 | 0.07 | 5.41 | 7.73 | 3.6 | 0.16 | 5.25
TARLAND | 33 | 16.14 | 6.7 | 0.38 | 9.85 | 1.57 | 1.09 | 0 | 1.54
TAYNUILT | 132 | 9.28 | 4.87 | 0.12 | 7.01 | 9.62 | 4.75 | 0.35 | 7.06
TAYNUILT | 33 | 21.3 | 8.88 | 0.57 | 13.14 | 2.12 | 1.47 | 0 | 2.08
TEALING | 275 | 30.62 | 12.32 | 4.97 | 22.39 | 30.88 | 12.6 | 4.72 | 22.54
TEALING | 132 | 31.26 | 12.85 | 4.28 | 22.45 | 37.33 | 15.48 | 4.33 | 26.22
THURSO SOUTH | 275 | 12.99 | 5.11 | 3.27 | 10.5 | 15.96 | 6.27 | 3.91 | 12.78
THURSO SOUTH | 132 | 20.06 | 7.72 | 4.27 | 15.19 | 25.81 | 9.92 | 5.45 | 19.47
THURSO SOUTH | 33 | 27.55 | 10.18 | 7.64 | 22.04 | 2.26 | 1.56 | 0 | 2.21
TOMATIN | 275 | 23.15 | 9.13 | 4.74 | 17.64 | 23.99 | 9.58 | 4.81 | 18.36
TOMATIN | 132 | 28.47 | 10.87 | 5.49 | 20.87 | 34.47 | 13.24 | 6.23 | 24.96
TUMMEL | 275 | 20.69 | 8.11 | 4.3 | 15.78 | 19.78 | 7.87 | 3.98 | 15.11
TUMMEL | 132 | 24.91 | 9.88 | 4.29 | 18.27 | 27.19 | 11.18 | 3.89 | 19.71
TUMMEL BRIDGE | 132 | 27.25 | 11.49 | 2.89 | 19.14 | 29.82 | 12.78 | 2.5 | 20.57
TUMMEL BRIDGE | 33 | 5.47 | 1.97 | 1.97 | 4.76 | 1.12 | 0.78 | 0 | 1.1
WILLOWDALE | 132 | 27.47 | 11.33 | 2.66 | 18.68 | 35.41 | 14.75 | 3.09 | 23.94
WILLOWDALE | 33 | 30.5 | 11.7 | 4.31 | 20.86 | 3.13 | 2.17 | 0 | 3.07
WOODHILL | 132 | 27.25 | 11.3 | 2.39 | 18.37 | 34.89 | 14.63 | 2.74 | 23.43
WOODHILL | 33 | 28.6 | 10.82 | 5.31 | 20.61 | 4.62 | 3.2 | 0 | 4.53

## D2.0
ETYS 21 Yr 01 - SPT Transmission Fault Levels (kA), Summer 2021/22
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
AREC1- | 132 | 7.8 | 3.01 | 0.94 | 5.2 | 10.21 | 3.95 | 1.35 | 6.93
AUCH2- | 275 | 9.65 | 3.87 | 1.06 | 6.53 | 10.77 | 4.41 | 1.16 | 7.4 | Menu
AYR-3- | 33 | 37.1 | 13.29 | 9.39 | 28.19 | 5.92 | 4.1 | 0 | 5.8
BAGA0J | 25 | 15.82 | 5.8 | 3.43 | 11.63 | 0 | 0 | 0 | 0
BAGA0K | 25 | 15.82 | 5.8 | 3.42 | 11.62 | 0 | 0 | 0 | 0
BAGA3- | 33 | 26.25 | 9.45 | 3.65 | 17.01 | 4.34 | 3 | 0 | 4.25
BAIN3- | 33 | 28.31 | 10.27 | 5.93 | 20.45 | 3 | 2.08 | 0 | 2.94
BERW3- | 33 | 26.01 | 9.92 | 1.58 | 15.61 | 4.43 | 3.02 | 0 | 4.27
BLAH1- | 132 | 18.66 | 7.02 | 2.8 | 12.74 | 23.38 | 8.99 | 3.56 | 16.26
BLAH3A | 33 | 24.02 | 8.76 | 5.9 | 18.29 | 4.48 | 3.1 | 0 | 4.39
BLAH3B | 33 | 23.94 | 8.74 | 5.88 | 18.23 | 4.45 | 3.09 | 0 | 4.36
BLCW3- | 33 | 15.82 | 6.1 | 1.45 | 10.07 | 2.23 | 1.54 | 0 | 2.18
BLKS3- | 33 | 14.95 | 5.84 | 1.04 | 9.3 | 2.18 | 1.51 | 0 | 2.13
BONN0J | 25 | 17.46 | 6.32 | 5.18 | 14.12 | 0 | 0 | 0 | 0
BONN0K | 25 | 17.46 | 6.32 | 5.18 | 14.12 | 0 | 0 | 0 | 0
BONN0L | 25 | 17.46 | 6.32 | 5.18 | 14.12 | 0 | 0 | 0 | 0
BONN1- | 132 | 36.51 | 13.22 | 7.53 | 26.22 | 46.09 | 17.57 | 8.83 | 33.68
BONN3- | 33 | 28.32 | 10.18 | 7.91 | 22.3 | 4.46 | 3.09 | 0 | 4.37
BPGR3- | 33 | 48.5 | 16.67 | 10.73 | 34.31 | 5.88 | 4.07 | 0 | 5.76
BRAP1- | 132 | 25.09 | 9.72 | 3.01 | 16.76 | 29.41 | 11.89 | 3.27 | 20.09
BRAP3- | 33 | 26.94 | 9.92 | 4.64 | 18.66 | 4.42 | 3.06 | 0 | 4.33
BROX3- | 33 | 25.29 | 9.2 | 3.71 | 16.72 | 4.38 | 3.03 | 0 | 4.29
BUSB2- | 275 | 40.01 | 14.42 | 7.7 | 28.09 | 41.43 | 16.15 | 6.51 | 29.35
CAFA5- | 11 | 22.5 | 8.42 | 3.78 | 15.69 | 2.22 | 1.54 | 0 | 2.17
CATY0J | 25 | 9.84 | 3.64 | 1.69 | 6.84 | 0 | 0 | 0 | 0
CATY0K | 25 | 9.85 | 3.64 | 1.72 | 6.87 | 0 | 0 | 0 | 0
CATY3- | 33 | 25.79 | 9.46 | 4.44 | 17.82 | 2.98 | 2.06 | 0 | 2.92
CCSS3- | 33 | 25.19 | 9.15 | 6.79 | 19.73 | 3.02 | 2.1 | 0 | 2.96
CHAP1- | 132 | 23.9 | 9.64 | 1.13 | 14.76 | 26.68 | 11.2 | 1.53 | 17.36
CHAP3- | 33 | 28.17 | 10.45 | 4.07 | 18.85 | 4.58 | 3.18 | 0 | 4.49
CHAS3A | 33 | 40.14 | 14.41 | 8.93 | 29.3 | 5.9 | 4.09 | 0 | 5.79
CHAS3B | 33 | 40.14 | 14.41 | 8.93 | 29.3 | 5.9 | 4.09 | 0 | 5.79
CLYM2- | 275 | 52.99 | 18.52 | 11.33 | 37.53 | 57.42 | 21.83 | 11.26 | 42.14
CLYM3A | 33 | 36.09 | 13.93 | 6.74 | 26.44 | 5.38 | 3.72 | 0 | 5.26
CLYM3B | 33 | 36.2 | 13.96 | 6.61 | 26.36 | 5.38 | 3.72 | 0 | 5.26
CLYN2Q | 275 | 13.61 | 4.94 | 4.44 | 11.43 | 16.32 | 6.03 | 5.32 | 13.84
CLYN3A | 33 | 28.03 | 10.24 | 6.83 | 21.31 | 3.02 | 2.09 | 0 | 2.96
CLYN3B | 33 | 28.12 | 10.28 | 6.84 | 21.38 | 3.02 | 2.09 | 0 | 2.96
CLYN3C | 33 | 28 | 10.23 | 6.84 | 21.32 | 3.02 | 2.09 | 0 | 2.96
CLYN3D | 33 | 28.03 | 10.25 | 6.78 | 21.28 | 3.02 | 2.09 | 0 | 2.96
CLYS2R | 275 | 13.8 | 5.03 | 4.31 | 11.42 | 15.66 | 5.82 | 4.68 | 12.91
CLYS3A | 33 | 27.89 | 10.21 | 6.58 | 21.03 | 3.01 | 2.08 | 0 | 2.95
CLYS3B | 33 | 27.77 | 10.18 | 6.42 | 20.81 | 3.01 | 2.09 | 0 | 2.95
COAL1- | 132 | 13.15 | 4.7 | 4.28 | 10.92 | 17.84 | 6.52 | 5.3 | 14.52
COAL1A | 132 | 26.42 | 9.47 | 7.5 | 20.9 | 34.27 | 12.36 | 9.24 | 26.72
COAL4- | 400 | 38.19 | 13.86 | 6.94 | 26.55 | 38.19 | 14.91 | 6.55 | 27.63
COAT3- | 33 | 36.14 | 12.77 | 10.97 | 29.03 | 5.91 | 4.09 | 0 | 5.79
COCK2- | 275 | 46 | 16.38 | 10.66 | 33.82 | 48.22 | 18.44 | 10.05 | 36.13
COCK3- | 33 | 39.63 | 14.16 | 10.59 | 30.61 | 5.96 | 4.13 | 0 | 5.84
COYL1- | 132 | 20.32 | 7.21 | 5.41 | 15.6 | 25.44 | 9.31 | 6.94 | 20.11
COYL2- | 275 | 31.54 | 11.51 | 6.6 | 22.88 | 37.01 | 14.27 | 7.05 | 27.23
COYL3- | 33 | 29.89 | 10.65 | 5.01 | 20.07 | 3.01 | 2.08 | 0 | 2.95
CROO3J | 33 | 31.46 | 11.89 | 3.47 | 20.28 | 3 | 2.08 | 0 | 2.94
CROO3K | 33 | 26.09 | 9.71 | 3.65 | 17.38 | 2.99 | 2.07 | 0 | 2.93
CRYR1- | 132 | 11.1 | 4 | 3.78 | 9.44 | 14.72 | 5.34 | 4.83 | 12.39
CRYR1A | 132 | 11.4 | 4.09 | 4.1 | 9.89 | 15.07 | 5.46 | 5.08 | 12.81
CRYR4- | 400 | 42.44 | 15.03 | 9.75 | 31.01 | 46.58 | 17.57 | 10.31 | 35.17
CUMB3- | 33 | 26.06 | 9.48 | 4.46 | 17.86 | 4.41 | 3.06 | 0 | 4.32
CUPA3- | 33 | 23.33 | 8.98 | 1.15 | 13.85 | 4.32 | 2.99 | 0 | 4.23
CURR0J | 25 | 20.96 | 7.58 | 6.32 | 17.04 | 0 | 0 | 0 | 0
CURR0K | 25 | 20.96 | 7.58 | 6.32 | 17.04 | 0 | 0 | 0 | 0
CURR1A | 132 | 29.85 | 10.47 | 7.96 | 22.76 | 38.54 | 14.08 | 9.81 | 29.72
CURR1B | 132 | 29.85 | 10.47 | 7.96 | 22.76 | 38.54 | 14.08 | 9.81 | 29.72
CURR2- | 275 | 42.63 | 15.24 | 8.75 | 30.3 | 45.22 | 17.36 | 8.89 | 33.45
CURR5- | 11 | 33.08 | 12.19 | 5.63 | 22.86 | 4.49 | 3.11 | 0 | 4.4
DALL2- | 275 | 26.03 | 9.31 | 5.24 | 18.4 | 25.63 | 9.88 | 4.78 | 18.75
DALM1- | 132 | 22.35 | 7.92 | 6.22 | 17.42 | 27.7 | 10.11 | 7.79 | 22.08
DALM3- | 33 | 25.99 | 9.17 | 7.48 | 20.45 | 4.39 | 3.04 | 0 | 4.3
DENN2- | 275 | 49.55 | 17.17 | 10.61 | 34.89 | 50.38 | 19.16 | 10.21 | 37.3
DENN4- | 400 | 18.4 | 6.49 | 5.31 | 14.49 | 18.3 | 6.84 | 4.91 | 14.58
DESA3- | 33 | 19.75 | 7.39 | 3.08 | 13.52 | 2.27 | 1.57 | 0 | 2.22
DEVM0J | 25 | 8.21 | 2.97 | 2.52 | 6.72 | 0 | 0 | 0 | 0
DEVM0K | 25 | 8.21 | 2.97 | 2.52 | 6.72 | 0 | 0 | 0 | 0
DEVM1- | 132 | 27.75 | 10.41 | 6.29 | 21.02 | 34.61 | 13.37 | 7.45 | 26.36
DEVM3- | 33 | 32.98 | 12.39 | 4.36 | 21.88 | 3.03 | 2.1 | 0 | 2.97
DEVM4- | 400 | 25.29 | 9.14 | 5.1 | 18.02 | 24.89 | 9.69 | 4.57 | 18.27
DEVO1- | 132 | 21.14 | 8.52 | 1.16 | 13.21 | 23.01 | 9.75 | 1.72 | 15.5
DEVO3- | 33 | 25.36 | 9.28 | 3.57 | 16.7 | 4.38 | 3.03 | 0 | 4.29
DEWP3- | 33 | 46.33 | 16.52 | 11.74 | 35.09 | 7.83 | 5.42 | 0 | 7.67
DONO1- | 132 | 12.51 | 4.54 | 3.28 | 9.71 | 16.83 | 6.3 | 3.59 | 12.5
DRCR3- | 33 | 24.2 | 8.99 | 2.86 | 15.57 | 4.4 | 3.05 | 0 | 4.31
DRUM3- | 33 | 36.77 | 13.02 | 10.39 | 28.8 | 5.88 | 4.07 | 0 | 5.76
DUMF1- | 132 | 15.9 | 6.62 | 0.44 | 9.81 | 19.39 | 8.2 | 0.7 | 12.3
DUMF3A | 33 | 29.71 | 11.41 | 1.7 | 17.83 | 4.35 | 3.01 | 0 | 4.26
DUMF3B | 33 | 29.67 | 11.39 | 1.7 | 17.8 | 4.37 | 3.03 | 0 | 4.28
DUMF3I | 33 | 17.1 | 6.47 | 1.53 | 10.69 | 1.51 | 1.05 | 0 | 1.48
DUNB3A | 33 | 29.06 | 10.84 | 3.12 | 18.45 | 3.04 | 2.11 | 0 | 2.98
DUNB3B | 33 | 28.3 | 10.14 | 4.64 | 18.97 | 4.51 | 3.12 | 0 | 4.42
DUNE1- | 132 | 13.92 | 5.87 | 0.63 | 8.93 | 16 | 6.79 | 1 | 10.61
DUNE3- | 33 | 26.25 | 10.25 | 2.18 | 16.68 | 4.45 | 3.08 | 0 | 4.36
DUNF3- | 33 | 27.87 | 10.37 | 3.61 | 18.28 | 4.41 | 3.06 | 0 | 4.32
DUNH3- | 33 | 23.91 | 8.72 | 5.9 | 18.24 | 4.45 | 3.08 | 0 | 4.36
EAST5- | 11 | 16.3 | 6.32 | 1.33 | 10.27 | 1.14 | 0.79 | 0 | 1.11
ECCF0J | 25 | 15.15 | 5.84 | 1.27 | 9.53 | 0 | 0 | 0 | 0
ECCF0K | 25 | 18.58 | 6.99 | 2.55 | 12.43 | 0 | 0 | 0 | 0
ECCL1- | 132 | 25.82 | 9.35 | 8.03 | 21.25 | 33.01 | 12.35 | 9.61 | 27.07
ECCL3- | 33 | 29.51 | 11.17 | 5.55 | 21.35 | 5.09 | 3.49 | 0 | 4.93
ECCL4A | 400 | 38.37 | 13.59 | 8.96 | 28.18 | 34.91 | 13.38 | 6.93 | 25.85
ECCL4B | 400 | 38.4 | 13.6 | 8.97 | 28.2 | 35.07 | 13.43 | 6.98 | 25.98
EERH2- | 275 | 48.7 | 17.18 | 10.19 | 34.48 | 49.54 | 19.01 | 9.08 | 35.96
EERH3- | 33 | 41.83 | 14.8 | 12.53 | 33.46 | 5.97 | 4.14 | 0 | 5.85
EKIL3- | 33 | 48.45 | 17.23 | 13.38 | 37.75 | 6.02 | 4.17 | 0 | 5.9
EKIS2- | 275 | 43.37 | 15.51 | 8.82 | 30.75 | 48.8 | 18.9 | 8.5 | 35.23
EKIS3A | 33 | 25.58 | 9.12 | 6.93 | 19.82 | 5.27 | 3.64 | 0 | 5.15
EKIS3B | 33 | 25.63 | 9.13 | 7.02 | 19.93 | 5.22 | 3.6 | 0 | 5.1
ELDE3- | 33 | 34.18 | 12.73 | 4.78 | 22.79 | 2.99 | 2.08 | 0 | 2.94
ELVA0J | 25 | 19.02 | 6.73 | 7.94 | 17.47 | 0 | 0 | 0 | 0
ELVA0K | 25 | 19.02 | 6.73 | 7.94 | 17.46 | 0 | 0 | 0 | 0
ELVA2Q | 275 | 14.32 | 5.15 | 5.12 | 12.4 | 16.51 | 6.19 | 4.98 | 13.73
ELVA2R | 275 | 14.45 | 5.2 | 5.17 | 12.51 | 16.35 | 5.98 | 5.56 | 14.02
ELVA4- | 400 | 41.83 | 15.11 | 7.37 | 28.73 | 39.09 | 15.36 | 6.27 | 28
ERSK3- | 33 | 26.37 | 9.74 | 4.24 | 18.01 | 3.01 | 2.08 | 0 | 2.95
EWEH3- | 33 | 18.66 | 7.24 | 1.52 | 11.77 | 2.23 | 1.55 | 0 | 2.19
FALL4- | 400 | 37.83 | 13.53 | 8.43 | 27.55 | 38.31 | 14.68 | 7.61 | 28.37
FINN3- | 33 | 29.29 | 10.65 | 5.95 | 21.02 | 4.43 | 3.07 | 0 | 4.34
GALA1- | 132 | 16 | 6.73 | 0.3 | 9.81 | 17.5 | 7.58 | 0.69 | 11.4
GALA3- | 33 | 25.44 | 9.61 | 2.09 | 15.69 | 4.73 | 3.27 | 0 | 4.62
GAWH1Q | 132 | 20.76 | 7.77 | 3.37 | 14.36 | 26.17 | 10.16 | 3.62 | 17.98
GAWH3- | 33 | 21.32 | 7.78 | 5.25 | 16.26 | 2.26 | 1.57 | 0 | 2.22
GIFF3A | 33 | 33.49 | 12.15 | 7.32 | 24.49 | 5.38 | 3.72 | 0 | 5.27
GIFF3B | 33 | 33.61 | 12.19 | 7.37 | 24.6 | 5.38 | 3.73 | 0 | 5.27
GLGL3- | 33 | 21.97 | 8.12 | 4.26 | 15.74 | 4.39 | 3.04 | 0 | 4.3
GLLE1- | 132 | 12.13 | 5.18 | 0.26 | 7.59 | 13.45 | 5.94 | 0.33 | 8.74
GLLE5- | 11 | 17.33 | 6.53 | 2.53 | 11.76 | 2.25 | 1.56 | 0 | 2.21
GLLU3- | 33 | 16.54 | 6.93 | 0.1 | 9.9 | 3.82 | 2.64 | 0 | 3.73
GLNI1- | 132 | 33.11 | 12.38 | 4.85 | 22.35 | 40.63 | 16 | 5.46 | 28.09
GLNI3- | 33 | 27.67 | 10.14 | 5.67 | 20.01 | 4.42 | 3.06 | 0 | 4.33
GLRO2- | 275 | 30.27 | 11.15 | 4.57 | 20.34 | 28.63 | 11.33 | 4.42 | 20.44
GLRO3A | 33 | 25.75 | 9.28 | 6.27 | 19.4 | 5.25 | 3.62 | 0 | 5.12
GLRO3B | 33 | 25.8 | 9.3 | 6.28 | 19.43 | 5.25 | 3.62 | 0 | 5.12
GORG3- | 33 | 27.09 | 9.83 | 5.02 | 18.92 | 3 | 2.08 | 0 | 2.94
GOVA3- | 33 | 28.05 | 10.21 | 5.43 | 19.87 | 4.41 | 3.06 | 0 | 4.33
GRMO2- | 275 | 34.48 | 12.51 | 6.52 | 24.22 | 33.39 | 12.98 | 6.39 | 24.74
GRMO3A | 33 | 34.94 | 12.37 | 8.59 | 26.08 | 5.86 | 4.06 | 0 | 5.75
GRMO3C | 33 | 35.01 | 12.39 | 8.71 | 26.23 | 5.87 | 4.07 | 0 | 5.75
GRNA1- | 132 | 30.79 | 11.46 | 6.96 | 23.17 | 39.29 | 15.04 | 8.38 | 29.65
GRNA4- | 400 | 43.38 | 15.96 | 7.2 | 29.77 | 38.02 | 14.89 | 7.08 | 28.13
HAGR3- | 33 | 27.97 | 10.29 | 4.53 | 19.09 | 3 | 2.08 | 0 | 2.94
HAWI1- | 132 | 9.37 | 4.26 | 0.06 | 6.08 | 11.08 | 4.99 | 0.16 | 7.21
HAWI3- | 33 | 18.95 | 7.64 | 0.39 | 11.2 | 2.91 | 2.02 | 0 | 2.85
HELE1- | 132 | 16.56 | 7.73 | 0.05 | 10.98 | 17.55 | 8.15 | 0.26 | 11.78
HELE3- | 33 | 24.91 | 9.97 | 0.79 | 14.9 | 2.97 | 2.06 | 0 | 2.91
HUCS4- | 400 | 32.27 | 11.56 | 6.27 | 22.62 | 42.71 | 16.13 | 8.28 | 31.1
HUER1- | 132 | 27.53 | 9.83 | 6.74 | 20.64 | 34.43 | 12.77 | 8.56 | 26.62
HUER4- | 400 | 32.39 | 11.6 | 6.29 | 22.69 | 42.79 | 16.17 | 8.26 | 31.12
HUNE4- | 400 | 32.39 | 11.6 | 6.29 | 22.69 | 42.82 | 16.18 | 8.27 | 31.14
HUNF3- | 33 | 37.49 | 13.87 | 5.82 | 25.44 | 3.04 | 2.11 | 0 | 2.98
INKE3- | 33 | 26.83 | 10.12 | 2.31 | 16.63 | 4.4 | 3.05 | 0 | 4.31
INVR2- | 275 | 26.99 | 9.84 | 4.95 | 18.86 | 26.51 | 10.37 | 4.49 | 19.16
INWI0J | 25 | 10.9 | 3.92 | 3.34 | 8.89 | 0 | 0 | 0 | 0
INWI0K | 25 | 10.9 | 3.92 | 3.34 | 8.89 | 0 | 0 | 0 | 0
JOHN3- | 33 | 27.04 | 9.83 | 5.37 | 19.27 | 2.98 | 2.07 | 0 | 2.92
KAIM2- | 275 | 44.74 | 15.93 | 9.74 | 32.26 | 49.2 | 18.79 | 9.49 | 36.07
KAIM3- | 33 | 28.57 | 9.89 | 8.1 | 22.09 | 5.67 | 3.92 | 0 | 5.55
KEOO1- | 132 | 13.93 | 5.71 | 0.73 | 8.8 | 15.36 | 6.47 | 0.91 | 10.06
KEOO5- | 11 | 17.43 | 6.59 | 2.44 | 11.75 | 2.21 | 1.53 | 0 | 2.17
KIER3- | 33 | 29.71 | 10.82 | 5.37 | 20.67 | 4.47 | 3.09 | 0 | 4.37
KILB3- | 33 | 31.58 | 11.72 | 5.08 | 21.66 | 2.99 | 2.07 | 0 | 2.93
KILB5- | 11 | 27.08 | 10.18 | 3.97 | 18.36 | 3.04 | 2.1 | 0 | 2.98
KILG2- | 275 | 10.7 | 4.3 | 1.11 | 7.19 | 13.24 | 5.38 | 1.63 | 9.24
KILS1- | 132 | 20.8 | 7.85 | 3.97 | 15.06 | 21.66 | 8.38 | 4.89 | 16.73
KILS2- | 275 | 37.69 | 13.47 | 8.99 | 28.05 | 45.67 | 17.24 | 10.39 | 34.77
KILS3- | 33 | 36.1 | 12.94 | 9.37 | 27.67 | 5.87 | 4.07 | 0 | 5.75
KILS4- | 400 | 32.14 | 11.61 | 6.17 | 22.59 | 34.78 | 13.4 | 6.71 | 25.66
KILS4T | 400 | 31.56 | 11.43 | 6.12 | 22.29 | 33.33 | 12.86 | 6.43 | 24.62
KILT3- | 33 | 44.97 | 16.17 | 9.65 | 32.52 | 5.98 | 4.14 | 0 | 5.86
KILW1Q | 132 | 20.12 | 7.61 | 2.06 | 12.83 | 21.03 | 8.4 | 1.89 | 13.77
KILW1R | 132 | 19.95 | 7.59 | 1.9 | 12.62 | 20.64 | 8.29 | 1.75 | 13.47
KILW3- | 33 | 25.35 | 9.26 | 4.85 | 17.95 | 4.41 | 3.06 | 0 | 4.32
KINC2- | 275 | 42.72 | 15.08 | 9.65 | 30.97 | 40.06 | 15.48 | 7.33 | 29.22
LAMB2- | 275 | 43.18 | 15.24 | 8.52 | 30.08 | 41.97 | 16.27 | 7.26 | 30.28
LEVE3- | 33 | 29.59 | 11.55 | 1.15 | 17.49 | 3.01 | 2.08 | 0 | 2.95
LING3- | 33 | 26.04 | 9.09 | 3.66 | 16.51 | 4.39 | 3.04 | 0 | 4.29
LINM3- | 33 | 27.59 | 9.4 | 7.05 | 20.34 | 4.42 | 3.06 | 0 | 4.32
LOAN2- | 275 | 53 | 18.31 | 11.31 | 37.2 | 50.91 | 19.6 | 8.46 | 36.18
MAHI1- | 132 | 9.1 | 3.4 | 1.76 | 6.58 | 11.53 | 4.34 | 2.35 | 8.49
MAHI2- | 275 | 11.5 | 4.57 | 1.35 | 7.81 | 14.1 | 5.67 | 1.85 | 9.88
MAHI3- | 33 | 27.92 | 10.43 | 4.2 | 18.95 | 3.02 | 2.09 | 0 | 2.96
MARM0J | 25 | 9.59 | 3.56 | 1.79 | 6.82 | 0 | 0 | 0 | 0
MARM0K | 25 | 9.59 | 3.56 | 1.79 | 6.83 | 0 | 0 | 0 | 0
MAYB1- | 132 | 12.33 | 5.03 | 0.36 | 7.47 | 13.76 | 5.81 | 0.51 | 8.73
MAYB3- | 33 | 18.62 | 6.93 | 0.95 | 10.75 | 1.53 | 1.06 | 0 | 1.5
MEAD1- | 132 | 22.25 | 8.27 | 2.33 | 14.03 | 22.86 | 9.03 | 2.12 | 14.89
MIDM1- | 132 | 11.34 | 4.26 | 1.82 | 7.84 | 14.93 | 5.85 | 2.3 | 10.57
MOFF1- | 132 | 20.64 | 7.48 | 6.08 | 16.65 | 26.93 | 9.89 | 7.92 | 21.91
MOFF4- | 400 | 35.66 | 13.16 | 5.94 | 24.55 | 32.53 | 12.84 | 5.41 | 23.57
MOSM1A | 132 | 31.81 | 11.95 | 4.62 | 21.53 | 39.66 | 15.58 | 5.78 | 27.81
MOSM1B | 132 | 31.74 | 11.93 | 4.57 | 21.45 | 39.63 | 15.58 | 5.71 | 27.75
MOSM2- | 275 | 35.19 | 12.77 | 5.75 | 23.81 | 34 | 13.3 | 5.82 | 24.64
NEAR2Q | 275 | 40 | 14.51 | 7.51 | 28.03 | 40.18 | 15.65 | 6.88 | 29.01
NEAR3- | 33 | 46.38 | 16.67 | 9.69 | 33.27 | 5.95 | 4.12 | 0 | 5.83
NECU1- | 132 | 24.53 | 8.91 | 5.88 | 18.47 | 31.84 | 11.83 | 7.29 | 24.01
NECU1B | 132 | 26.78 | 9.89 | 6.07 | 20.07 | 33.52 | 12.65 | 7.61 | 25.5
NECU1C | 132 | 22.79 | 8.29 | 5.44 | 17.16 | 29.09 | 10.8 | 6.61 | 21.89
NECU2- | 275 | 27.23 | 10.07 | 5.36 | 19.6 | 31.82 | 12.29 | 6.46 | 23.83
NEIL1- | 132 | 35.31 | 12.77 | 8.54 | 26.6 | 45.36 | 17.05 | 10.89 | 35
NEIL2- | 275 | 47.37 | 16.66 | 10.12 | 33.68 | 54.8 | 20.68 | 11.56 | 40.81
NETS1- | 132 | 7.88 | 3.57 | 0.04 | 5.09 | 8.96 | 4.09 | 0.12 | 5.9
NETS3- | 33 | 12.62 | 5.16 | 0.54 | 7.83 | 2.95 | 2.01 | 0 | 2.85
PAIS3- | 33 | 31.18 | 11.4 | 5.79 | 21.92 | 3.01 | 2.09 | 0 | 2.95
PART3- | 33 | 33.21 | 12.42 | 4.3 | 21.86 | 3 | 2.08 | 0 | 2.94
POOB0J | 25 | 18.52 | 6.67 | 5.56 | 14.99 | 0 | 0 | 0 | 0
POOB0K | 25 | 18.52 | 6.67 | 5.56 | 14.99 | 0 | 0 | 0 | 0
POOB3- | 33 | 42.81 | 15.15 | 11.86 | 33.29 | 5.91 | 4.09 | 0 | 5.79
PORD3- | 33 | 46.19 | 16.56 | 11.25 | 34.67 | 5.97 | 4.13 | 0 | 5.85
RAVE3A | 33 | 20.59 | 7.78 | 1.74 | 12.74 | 2.95 | 2.05 | 0 | 2.89
RAVE3B | 33 | 20.89 | 8.06 | 1.57 | 12.97 | 2.94 | 2.04 | 0 | 2.88
REDH1- | 132 | 24.7 | 10.05 | 1.05 | 15.25 | 27.45 | 11.61 | 1.37 | 17.78
REDH3- | 33 | 29.02 | 10.93 | 2.91 | 18.37 | 3.7 | 2.56 | 0 | 3.62
SACO0J | 25 | 10.41 | 3.76 | 2.84 | 8.15 | 0 | 0 | 0 | 0
SACO0K | 25 | 10.38 | 3.75 | 2.77 | 8.08 | 0 | 0 | 0 | 0
SACO3J | 33 | 28.01 | 10.05 | 3.89 | 18.11 | 2.97 | 2.06 | 0 | 2.91
SACO3K | 33 | 29.34 | 10.93 | 3.67 | 19.13 | 3.02 | 2.09 | 0 | 2.96
SANX0J | 25 | 16.5 | 5.92 | 4.55 | 12.93 | 0 | 0 | 0 | 0
SANX0K | 25 | 16.49 | 5.92 | 4.5 | 12.87 | 0 | 0 | 0 | 0
SANX3- | 33 | 25.34 | 9.13 | 5.4 | 18.3 | 3 | 2.08 | 0 | 2.94
SHRU3A | 33 | 40.13 | 14.3 | 10.14 | 30.37 | 5.95 | 4.12 | 0 | 5.83
SHRU3B | 33 | 40.13 | 14.3 | 10.14 | 30.37 | 5.95 | 4.12 | 0 | 5.83
SIGH3A | 33 | 39.15 | 13.94 | 10.15 | 29.87 | 4.51 | 3.12 | 0 | 4.42
SIGH3B | 33 | 39.05 | 13.92 | 10.01 | 29.69 | 4.51 | 3.12 | 0 | 4.42
SMEA1- | 132 | 16.66 | 6.47 | 4.46 | 13.61 | 18.19 | 7.11 | 5.16 | 15.22
SMEA2- | 275 | 46.08 | 16.36 | 10.84 | 33.98 | 52.1 | 19.72 | 11.39 | 39.28
SPAV3- | 33 | 25.87 | 9.65 | 3.55 | 17.2 | 4.38 | 3.03 | 0 | 4.29
STHA2A | 275 | 47.74 | 16.88 | 10.4 | 34.28 | 54.39 | 20.57 | 11.59 | 40.68
STHA2B | 275 | 48.17 | 17.02 | 10.56 | 34.62 | 55.56 | 21.07 | 11.78 | 41.59
STHA3- | 33 | 45.66 | 16.41 | 10.67 | 33.88 | 5.96 | 4.13 | 0 | 5.84
STHA4A | 400 | 40.93 | 14.57 | 8 | 28.61 | 43.86 | 16.77 | 8.43 | 32.15
STHA4B | 400 | 38.97 | 13.97 | 7.76 | 27.52 | 41.38 | 15.87 | 8.07 | 30.51
STIR3- | 33 | 29.22 | 10.27 | 6.17 | 20.7 | 4.41 | 3.05 | 0 | 4.31
STLE0J | 25 | 10.19 | 3.73 | 2.16 | 7.44 | 0 | 0 | 0 | 0
STLE0K | 25 | 10.19 | 3.73 | 2.16 | 7.44 | 0 | 0 | 0 | 0
STLE1- | 132 | 19.73 | 8.84 | 0.17 | 12.66 | 20.5 | 9.31 | 0.52 | 13.69
STLE3S | 33 | 26.12 | 10.07 | 1.96 | 16.19 | 3.01 | 2.08 | 0 | 2.95
TELR3- | 33 | 25.9 | 9.55 | 3.71 | 17.21 | 3.01 | 2.08 | 0 | 2.95
TONG1- | 132 | 9.76 | 4.42 | 0.25 | 6.51 | 13.7 | 6.27 | 0.34 | 9.21
TONG3- | 33 | 18.88 | 7.54 | 1.03 | 11.7 | 2.92 | 2.03 | 0 | 2.87
TONG5- | 11 | 65.78 | 26.23 | 4.41 | 41.5 | 4.52 | 3.13 | 0 | 4.43
TORN1- | 132 | 26.49 | 9.46 | 7.46 | 20.84 | 32.84 | 11.99 | 9.52 | 26.48
TORN4- | 400 | 49.19 | 17.18 | 11.78 | 36.07 | 55.11 | 20.48 | 13.83 | 42.79
WESE1- | 132 | 10.98 | 3.96 | 3.61 | 9.22 | 14.52 | 5.31 | 4.38 | 11.89
WFIE1A | 132 | 25.33 | 10 | 3.94 | 18.08 | 28.11 | 11.44 | 4.95 | 21.13
WFIE1B | 132 | 29.99 | 11.46 | 4.02 | 20.24 | 33.86 | 13.63 | 5.05 | 24.32
WFIE2- | 275 | 37.54 | 13.54 | 6.18 | 25.32 | 37.11 | 14.47 | 6.38 | 26.84
WFIE3- | 33 | 29.15 | 10.53 | 6.79 | 21.68 | 3.03 | 2.1 | 0 | 2.97
WGEO3- | 33 | 46.04 | 16.58 | 9.4 | 32.85 | 5.98 | 4.14 | 0 | 5.86
WHHO3- | 33 | 39.16 | 14.04 | 9.33 | 29.19 | 5.92 | 4.1 | 0 | 5.8
WHTL3- | 33 | 25.79 | 10.14 | 0.7 | 15.04 | 2.24 | 1.55 | 0 | 2.19
WISH0J | 25 | 20.95 | 7.52 | 6.33 | 16.97 | 0 | 0 | 0 | 0
WISH0K | 25 | 20.95 | 7.52 | 6.33 | 16.97 | 0 | 0 | 0 | 0
WISH1- | 132 | 11.84 | 4.27 | 3.85 | 9.89 | 15.19 | 5.53 | 4.89 | 12.71
WISH2- | 275 | 40.93 | 14.7 | 9.21 | 30 | 47.16 | 17.84 | 10.76 | 35.98
WISH3- | 33 | 36.37 | 12.98 | 9.52 | 27.87 | 5.87 | 4.07 | 0 | 5.75
WISH4- | 400 | 38.32 | 13.73 | 7.25 | 26.67 | 40.46 | 15.53 | 7.84 | 29.8
WIYH1- | 132 | 39.25 | 14.65 | 8.57 | 29.28 | 50.04 | 19.5 | 10.85 | 38.44
WIYH2- | 275 | 44.22 | 15.5 | 9.26 | 31.18 | 48.3 | 18.32 | 10.1 | 36.01
WLEE2- | 275 | 39.11 | 14.42 | 6.1 | 26.49 | 39.05 | 16.76 | 7.6 | 31.3
WLEE3A | 33 | 35.1 | 12.78 | 8.44 | 26.5 | 3.04 | 2.11 | 0 | 2.98
WLEE3B | 33 | 35.28 | 12.84 | 8.43 | 26.6 | 3.04 | 2.11 | 0 | 2.98
WLEE3C | 33 | 34.99 | 12.74 | 8.4 | 26.42 | 3.04 | 2.11 | 0 | 2.98
WLEX2- | 275 | 32.29 | 12.33 | 3.8 | 21.25 | 30.61 | 13.29 | 6.35 | 25.15
WLEX3A | 33 | 34.73 | 12.66 | 8.12 | 26.02 | 3.04 | 2.11 | 0 | 2.98
WLEX3B | 33 | 34.69 | 12.64 | 8.12 | 26 | 3.04 | 2.11 | 0 | 2.98
WLEX3C | 33 | 34.69 | 12.64 | 8.12 | 26 | 3.04 | 2.11 | 0 | 2.98

## D3.0
ETYS 21 Yr 01 - NGET Transmission Fault Levels (kA), Summer 2021/22
Location | Voltage (kV) | Three Phase Initial Peak Current (kA) | Three Phase RMS Break Current (kA) | Three Phase DC Break Current (kA) | Three Phase Peak Break Current (kA) | Single Phase Initial Peak Current (kA) | Single Phase RMS Break Current (kA) | Single Phase DC Break Current (kA) | Single Phase Peak Break Current (kA)
ABHA4A | 400 | 26.8777 | 9.6748 | 1.2381 | 14.9203 | 27.7921 | 10.7989 | 1.2909 | 16.5628
ABHA4B | 400 | 26.873 | 9.6704 | 1.2371 | 14.9132 | 27.7906 | 10.7965 | 1.2867 | 16.5553 | Menu
ABTH1 M1 | 132 | 26.8864 | 10.0056 | 5.6881 | 19.8382 | 26.0405 | 10.2425 | 5.7826 | 20.2677
ABTH1 M2 | 132 | 24.5917 | 9.5297 | 7.1224 | 20.5994 | 21.9862 | 8.8108 | 6.3409 | 18.8013
ABTH1 R1 | 132 | 27.1246 | 10.397 | 7.1916 | 21.8952 | 30.0449 | 11.8373 | 8.3606 | 25.101
ABTH1 R2 | 132 | 27.1246 | 10.397 | 7.1916 | 21.8952 | 30.0449 | 11.8373 | 8.3606 | 25.101
ABTH2 M1 | 275 | 41.1937 | 14.992 | 6.9766 | 28.1785 | 39.4529 | 15.4788 | 6.362 | 28.2523
ABTH2 M2 | 275 | 41.1937 | 14.992 | 6.9766 | 28.1785 | 39.4529 | 15.4788 | 6.362 | 28.2523
ABTH2 M4 | 275 | 41.1937 | 14.992 | 6.9766 | 28.1785 | 39.4529 | 15.4788 | 6.362 | 28.2523
ABTH2 R | 275 | 34.5604 | 12.7399 | 3.55 | 21.567 | 31.2398 | 12.3942 | 2.6009 | 20.1289
ALDW2 MC1 | 275 | 56.1921 | 20.4765 | 8.6119 | 37.5701 | 56.9165 | 22.36 | 8.8524 | 40.4742
ALDW2 MC2 | 275 | 56.1921 | 20.4765 | 8.6119 | 37.5701 | 56.9165 | 22.36 | 8.8524 | 40.4742
ALDW2 MC3 | 275 | 56.1921 | 20.4765 | 8.6119 | 37.5701 | 56.9165 | 22.36 | 8.8524 | 40.4742
ALDW2 MC4 | 275 | 56.1921 | 20.4765 | 8.6119 | 37.5701 | 56.9165 | 22.36 | 8.8524 | 40.4742
AMEM1 M1 | 132 | 27.5165 | 9.7787 | 9.6038 | 23.433 | 33.5233 | 12.3129 | 10.8568 | 28.2699
AMEM1 M2 | 132 | 27.5165 | 9.7787 | 9.6038 | 23.433 | 33.5233 | 12.3129 | 10.8568 | 28.2699
AMEM1 R1 | 132 | 27.5165 | 9.7787 | 9.6038 | 23.433 | 33.5233 | 12.3129 | 10.8568 | 28.2699
AMEM1 R2 | 132 | 27.5165 | 9.7787 | 9.6038 | 23.433 | 33.5233 | 12.3129 | 10.8568 | 28.2699
AMEM4 M | 400 | 46.4657 | 16.4532 | 3.5466 | 26.815 | 40.1424 | 15.6957 | 2.6389 | 24.8359
AMEM4 R | 400 | 47.49 | 16.7605 | 3.6748 | 27.3777 | 40.1898 | 15.6459 | 2.6281 | 24.7547
AXMI4 MC1 | 400 | 31.0998 | 11.3265 | 5.4357 | 21.4538 | 28.9036 | 11.2587 | 4.9123 | 20.8345
AXMI4 MC2 | 400 | 31.0998 | 11.3265 | 5.4357 | 21.4538 | 28.9036 | 11.2587 | 4.9123 | 20.8345
BAGB2 M1 | 275 | 36.2644 | 13.2971 | 7.3136 | 26.1185 | 38.7289 | 14.8584 | 8.6682 | 29.6811
BAGB2 M2 | 275 | 36.2644 | 13.2971 | 7.3136 | 26.1185 | 38.7289 | 14.8584 | 8.6682 | 29.6811
BAGB2 R1 | 275 | 36.2644 | 13.2971 | 7.3136 | 26.1185 | 38.7289 | 14.8584 | 8.6682 | 29.6811
BAGB2 R2 | 275 | 36.2644 | 13.2971 | 7.3136 | 26.1185 | 38.7289 | 14.8584 | 8.6682 | 29.6811
BARK1 M5 | 132 | 43.0011 | 15.0768 | 14.3235 | 35.6453 | 50.987 | 18.6137 | 16.3031 | 42.6269
BARK1 M6 | 132 | 43.0011 | 15.0768 | 14.3235 | 35.6453 | 50.987 | 18.6137 | 16.3031 | 42.6269
BARK1 R5 | 132 | 43.0011 | 15.0768 | 14.3235 | 35.6453 | 50.987 | 18.6137 | 16.3031 | 42.6269
BARK1 R6 | 132 | 43.0011 | 15.0768 | 14.3235 | 35.6453 | 50.987 | 18.6137 | 16.3031 | 42.6269
BARK2 M1 | 275 | 26.3793 | 9.0833 | 9.5553 | 22.401 | 29.6228 | 10.6267 | 10.539 | 25.5675
BARK2 M2 | 275 | 56.8536 | 19.8231 | 13.7537 | 41.7879 | 57.8063 | 21.712 | 14.5484 | 45.2539
BARK2 R1 | 275 | 26.3793 | 9.0833 | 9.5553 | 22.401 | 29.6228 | 10.6267 | 10.539 | 25.5675
BARK2 R2 | 275 | 56.8536 | 19.8231 | 13.7537 | 41.7879 | 57.8063 | 21.712 | 14.5484 | 45.2539
BARK4 M1 | 400 | 104.2904 | 35.2144 | 29.2048 | 79.0055 | 104.765 | 39.814 | 26.1356 | 82.4412
BARK4 M2 | 400 | 104.2904 | 35.2144 | 29.2048 | 79.0055 | 104.765 | 39.814 | 26.1356 | 82.4412
BARK4 R1 | 400 | 104.2904 | 35.2144 | 29.2048 | 79.0055 | 104.765 | 39.814 | 26.1356 | 82.4412
BARK4 R2 | 400 | 104.2904 | 35.2144 | 29.2048 | 79.0055 | 104.765 | 39.814 | 26.1356 | 82.4412
BEDD2 M1/4 | 275 | 56.1283 | 19.5527 | 12.0192 | 39.6708 | 59.2415 | 22.4418 | 12.2943 | 44.0317
BEDD2 M2/3 | 275 | 72.4512 | 24.7559 | 15.0284 | 50.0386 | 75.406 | 28.4269 | 15.294 | 55.4957
BEDD2 R1 | 275 | 48.412 | 17.3719 | 10.1842 | 34.7518 | 49.14 | 18.7422 | 10.303 | 36.8084
BEDD2 R2 | 275 | 72.4512 | 24.7559 | 15.0284 | 50.0386 | 75.406 | 28.4269 | 15.294 | 55.4957
BEDD2 R3 | 275 | 72.4512 | 24.7559 | 15.0284 | 50.0386 | 75.406 | 28.4269 | 15.294 | 55.4957
BEDD2 R4 | 275 | 48.412 | 17.3719 | 10.1842 | 34.7518 | 49.14 | 18.7422 | 10.303 | 36.8084
BEDD4B | 400 | 38.7106 | 13.6736 | 2.6209 | 21.9583 | 35.0401 | 13.7567 | 3.28 | 22.7349
BESW2 MC1 | 275 | 54.8627 | 19.7069 | 9.7323 | 37.6021 | 49.1601 | 19.4128 | 7.9287 | 35.3826
BESW2 MC2 | 275 | 54.8627 | 19.7069 | 9.7323 | 37.6021 | 49.1601 | 19.4128 | 7.9287 | 35.3826
BESW2 MC3 | 275 | 54.8627 | 19.7069 | 9.7323 | 37.6021 | 49.1601 | 19.4128 | 7.9287 | 35.3826
BESW2 MC4 | 275 | 54.8627 | 19.7069 | 9.7323 | 37.6021 | 49.1601 | 19.4128 | 7.9287 | 35.3826
BICF41 M1 | 400 | 62.9763 | 22.1725 | 14.7067 | 46.0633 | 49.7586 | 19.4122 | 8.7553 | 36.2084
BICF41 M2 | 400 | 62.9763 | 22.1725 | 14.7067 | 46.0633 | 49.7586 | 19.4122 | 8.7553 | 36.2084
BICF41 R1 | 400 | 62.9763 | 22.1725 | 14.7067 | 46.0633 | 49.7586 | 19.4122 | 8.7553 | 36.2084
BICF41 R2 | 400 | 62.9763 | 22.1725 | 14.7067 | 46.0633 | 49.7586 | 19.4122 | 8.7553 | 36.2084
BIRK1 M1 | 132 | 36.4533 | 12.6041 | 10.851 | 28.6759 | 45.576 | 16.6318 | 12.842 | 36.363
BIRK1 M2 | 132 | 36.4533 | 12.6041 | 10.851 | 28.6759 | 45.576 | 16.6318 | 12.842 | 36.363
BIRK1 R1 | 132 | 36.4533 | 12.6041 | 10.851 | 28.6759 | 45.576 | 16.6318 | 12.842 | 36.363
BIRK1 R2 | 132 | 36.4533 | 12.6041 | 10.851 | 28.6759 | 45.576 | 16.6318 | 12.842 | 36.363
BIRK2 MC1 | 275 | 44.9095 | 15.9552 | 10.2836 | 32.8476 | 46.8488 | 17.7577 | 9.9727 | 35.0858
BIRK2 MC2 | 275 | 44.9095 | 15.9552 | 10.2836 | 32.8476 | 46.8488 | 17.7577 | 9.9727 | 35.0858
BIRK2 MC3 | 275 | 44.9095 | 15.9552 | 10.2836 | 32.8476 | 46.8488 | 17.7577 | 9.9727 | 35.0858
BIRK2 MC4 | 275 | 44.9095 | 15.9552 | 10.2836 | 32.8476 | 46.8488 | 17.7577 | 9.9727 | 35.0858
BISW2 MC1 | 275 | 61.1945 | 21.9244 | 11.0047 | 42.0104 | 57.4073 | 22.425 | 9.1855 | 40.8992
BISW2 MC2 | 275 | 61.1945 | 21.9244 | 11.0047 | 42.0104 | 57.4073 | 22.425 | 9.1855 | 40.8992
BISW2 MC3 | 275 | 61.1945 | 21.9244 | 11.0047 | 42.0104 | 57.4073 | 22.425 | 9.1855 | 40.8992
BISW2 MC4 | 275 | 61.1945 | 21.9244 | 11.0047 | 42.0104 | 57.4073 | 22.425 | 9.1855 | 40.8992
BLYT1A | 132 | 23.3671 | 8.4201 | 3.9074 | 15.8153 | 26.1868 | 9.8728 | 4.4733 | 18.4356
BLYT1B | 132 | 23.3093 | 8.4095 | 3.9056 | 15.7984 | 26.1386 | 9.8591 | 4.4727 | 18.4155
BLYT2 M1 | 275 | 79.8114 | 28.2259 | 24.6533 | 64.5708 | 74.2302 | 28.3941 | 21.3262 | 61.4814
BLYT2 M2 | 275 | 79.8114 | 28.2259 | 24.6533 | 64.5708 | 74.2302 | 28.3941 | 21.3262 | 61.4814
BLYT2 R1 | 275 | 79.8114 | 28.2259 | 24.6533 | 64.5708 | 74.2302 | 28.3941 | 21.3262 | 61.4814
BLYT2 R2 | 275 | 79.8114 | 28.2259 | 24.6533 | 64.5708 | 74.2302 | 28.3941 | 21.3262 | 61.4814
BLYT4 M1 | 400 | 62.583 | 19.9386 | 7.2517 | 35.4491 | 47.6217 | 17.7516 | 5.4886 | 30.5932
BLYT4 M2 | 400 | 62.583 | 19.9386 | 7.2517 | 35.4491 | 47.6217 | 17.7516 | 5.4886 | 30.5932
BLYT4 R1 | 400 | 62.583 | 19.9386 | 7.2517 | 35.4491 | 47.6217 | 17.7516 | 5.4886 | 30.5932
BLYT4 R2 | 400 | 62.583 | 19.9386 | 7.2517 | 35.4491 | 47.6217 | 17.7516 | 5.4886 | 30.5932
BODE4 M1 | 400 | 63.4056 | 22.2191 | 14.0253 | 45.4479 | 52.3076 | 20.4021 | 8.3495 | 37.2024
BODE4 R1 | 400 | 63.4056 | 22.2191 | 14.0253 | 45.4479 | 52.3076 | 20.4021 | 8.3495 | 37.2024
BOLN4 M1 | 400 | 57.6785 | 20.8422 | 16.127 | 45.6022 | 51.2374 | 19.7199 | 14.6356 | 42.5238
BOLN4 M2 | 400 | 57.6785 | 20.8422 | 16.127 | 45.6022 | 51.2374 | 19.7199 | 14.6356 | 42.5238
BOLN4 R1 | 400 | 57.6785 | 20.8422 | 16.127 | 45.6022 | 51.2374 | 19.7199 | 14.6356 | 42.5238
BOLN4 R2 | 400 | 57.6785 | 20.8422 | 16.127 | 45.6022 | 51.2374 | 19.7199 | 14.6356 | 42.5238
BOTW4 MC1 | 400 | 60.0248 | 20.7685 | 10.787 | 40.158 | 54.4586 | 20.8977 | 9.0947 | 38.6485
BOTW4 MC2 | 400 | 60.0248 | 20.7685 | 10.787 | 40.158 | 54.4586 | 20.8977 | 9.0947 | 38.6485
BRAI4A | 400 | 57.5592 | 20.33 | 12.2172 | 40.9682 | 45.1154 | 17.487 | 8.3292 | 33.0595
BRAI4A BRFO | 400 | 57.5592 | 20.33 | 12.2172 | 40.9682 | 45.1154 | 17.487 | 8.3292 | 33.0595
BRAI4A RAYL | 400 | 57.5592 | 20.33 | 12.2172 | 40.9682 | 45.1154 | 17.487 | 8.3292 | 33.0595
BRAI4B | 400 | 54.8003 | 19.3178 | 11.1773 | 38.4969 | 42.9184 | 16.568 | 7.8402 | 31.2709
BRAI4B PELH | 400 | 54.8003 | 19.3178 | 11.1773 | 38.4969 | 42.9184 | 16.568 | 7.8402 | 31.2709
BRAI4B RAYL | 400 | 54.8003 | 19.3178 | 11.1773 | 38.4969 | 42.9184 | 16.568 | 7.8402 | 31.2709
BRAW2 MC1 | 275 | 61.3791 | 21.6655 | 13.3856 | 44.0252 | 63.5382 | 24.2092 | 13.0314 | 47.2684
BRAW2 MC2 | 275 | 61.3791 | 21.6655 | 13.3856 | 44.0252 | 63.5382 | 24.2092 | 13.0314 | 47.2684
BRAW2 MC3 | 275 | 61.3791 | 21.6655 | 13.3856 | 44.0252 | 63.5382 | 24.2092 | 13.0314 | 47.2684
BRAW2 MC4 | 275 | 61.3791 | 21.6655 | 13.3856 | 44.0252 | 63.5382 | 24.2092 | 13.0314 | 47.2684
BRAW4A | 400 | 33.6738 | 11.9899 | 3.9992 | 20.9555 | 30.2258 | 11.4089 | 4.0036 | 20.1382
BRED2 MC1 | 275 | 72.55 | 25.9585 | 13.7045 | 50.4154 | 71.5794 | 27.811 | 11.9061 | 51.2368
BRED2 MC2 | 275 | 72.55 | 25.9585 | 13.7045 | 50.4154 | 71.5794 | 27.811 | 11.9061 | 51.2368
BRED2 MC3 | 275 | 72.55 | 25.9585 | 13.7045 | 50.4154 | 71.5794 | 27.811 | 11.9061 | 51.2368
BRED2 MC4 | 275 | 72.55 | 25.9585 | 13.7045 | 50.4154 | 71.5794 | 27.811 | 11.9061 | 51.2368
BRFO4 M5 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO4 M6 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO4 R5 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO4 R6 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO41 M3 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO41 M7 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO41 R3 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRFO41 R7 | 400 | 78.6439 | 28.1656 | 24.6378 | 64.47 | 72.2828 | 27.7089 | 20.8163 | 60.0025
BRIM1 M1 | 132 | 38.4582 | 12.8458 | 13.1343 | 31.3011 | 51.0666 | 18.2436 | 16.9196 | 42.72
BRIM1 M2 | 132 | 38.4582 | 12.8458 | 13.1343 | 31.3011 | 51.0666 | 18.2436 | 16.9196 | 42.72
BRIM1 R1 | 132 | 38.4582 | 12.8458 | 13.1343 | 31.3011 | 51.0666 | 18.2436 | 16.9196 | 42.72
BRIM1 R2 | 132 | 38.4582 | 12.8458 | 13.1343 | 31.3011 | 51.0666 | 18.2436 | 16.9196 | 42.72
BRIN2 M1 | 275 | 56.3865 | 20.3463 | 10.7448 | 39.5188 | 60.4105 | 23.51 | 10.8913 | 44.1395
BRIN2 M2 | 275 | 60.8458 | 21.8319 | 13.9447 | 44.8197 | 65.4428 | 25.0685 | 14.2123 | 49.6645
BRIN2 R1 | 275 | 56.3865 | 20.3463 | 10.7448 | 39.5188 | 60.4105 | 23.51 | 10.8913 | 44.1395
BRIN2 R2 | 275 | 60.8458 | 21.8319 | 13.9447 | 44.8197 | 65.4428 | 25.0685 | 14.2123 | 49.6645
BRIN4 MC1 | 400 | 57.7777 | 20.6495 | 11.9865 | 41.1893 | 48.8084 | 18.9303 | 9.5275 | 36.2991
BRIN4 MC4 | 400 | 57.7777 | 20.6495 | 11.9865 | 41.1893 | 48.8084 | 18.9303 | 9.5275 | 36.2991
BRLE4 M1 | 400 | 92.969 | 31.576 | 16.0997 | 60.7549 | 87.3263 | 33.2116 | 16.3281 | 63.2964
BRLE4 M2 | 400 | 92.969 | 31.576 | 16.0997 | 60.7549 | 87.3263 | 33.2116 | 16.3281 | 63.2964
BRLE4 R1 | 400 | 92.969 | 31.576 | 16.0997 | 60.7549 | 87.3263 | 33.2116 | 16.3281 | 63.2964
BRLE4 R2 | 400 | 92.969 | 31.576 | 16.0997 | 60.7549 | 87.3263 | 33.2116 | 16.3281 | 63.2964
BULL4 MC1 | 400 | 61.3127 | 21.4789 | 12.507 | 42.8828 | 47.6647 | 18.5267 | 8.0111 | 34.2118
BULL4 MC2 | 400 | 61.3127 | 21.4789 | 12.507 | 42.8828 | 47.6647 | 18.5267 | 8.0111 | 34.2118
BURW4 MC1 | 400 | 74.8841 | 26.0434 | 16.2221 | 53.0531 | 55.3005 | 21.7282 | 9.6643 | 40.3926
BURW4 MC2 | 400 | 74.8841 | 26.0434 | 16.2221 | 53.0531 | 55.3005 | 21.7282 | 9.6643 | 40.3926
BURW4 MC3 | 400 | 74.8841 | 26.0434 | 16.2221 | 53.0531 | 55.3005 | 21.7282 | 9.6643 | 40.3926
BURW4 MC4 | 400 | 74.8841 | 26.0434 | 16.2221 | 53.0531 | 55.3005 | 21.7282 | 9.6643 | 40.3926
BUSH2 MC1 | 275 | 52.8251 | 18.9993 | 10.35 | 37.219 | 53.2422 | 20.6298 | 9.798 | 38.973
BUSH2 MC2 | 275 | 52.8251 | 18.9993 | 10.35 | 37.219 | 53.2422 | 20.6298 | 9.798 | 38.973
BUSH2 MC3 | 275 | 52.8251 | 18.9993 | 10.35 | 37.219 | 53.2422 | 20.6298 | 9.798 | 38.973
BUSH2 MC4 | 275 | 52.8251 | 18.9993 | 10.35 | 37.219 | 53.2422 | 20.6298 | 9.798 | 38.973
BUST2 M1 | 275 | 51.9211 | 18.5205 | 12.6019 | 38.7939 | 55.4971 | 21.1967 | 12.7329 | 42.7097
BUST2 M2 | 275 | 51.9211 | 18.5205 | 12.6019 | 38.7939 | 55.4971 | 21.1967 | 12.7329 | 42.7097
BUST2 R1 | 275 | 51.9211 | 18.5205 | 12.6019 | 38.7939 | 55.4971 | 21.1967 | 12.7329 | 42.7097
BUST2 R2 | 275 | 51.9211 | 18.5205 | 12.6019 | 38.7939 | 55.4971 | 21.1967 | 12.7329 | 42.7097
CANT4 MC1 | 400 | 71.1172 | 24.7846 | 13.0018 | 48.0526 | 60.1104 | 23.2489 | 10.1293 | 43.0082
CANT4 MC2 | 400 | 71.1172 | 24.7846 | 13.0018 | 48.0526 | 60.1104 | 23.2489 | 10.1293 | 43.0082
CANT4 MC3 | 400 | 71.1172 | 24.7846 | 13.0018 | 48.0526 | 60.1104 | 23.2489 | 10.1293 | 43.0082
CANT4 MC4 | 400 | 71.1172 | 24.7846 | 13.0018 | 48.0526 | 60.1104 | 23.2489 | 10.1293 | 43.0082
CAPE2 M1 | 275 | 58.9841 | 20.3893 | 17.0248 | 45.8597 | 68.4905 | 25.0173 | 19.2946 | 54.6744
CAPE2 M2 | 275 | 58.9841 | 20.3893 | 17.0248 | 45.8597 | 68.4905 | 25.0173 | 19.2946 | 54.6744
CAPE2 R1 | 275 | 58.9841 | 20.3893 | 17.0248 | 45.8597 | 68.4905 | 25.0173 | 19.2946 | 54.6744
CAPE2 R2 | 275 | 58.9841 | 20.3893 | 17.0248 | 45.8597 | 68.4905 | 25.0173 | 19.2946 | 54.6744
CAPE4A | 400 | 70.4352 | 24.4261 | 15.6601 | 50.2038 | 71.2347 | 26.8173 | 14.8828 | 52.8081
CAPE4B | 400 | 70.4315 | 24.4252 | 15.6579 | 50.2003 | 71.7335 | 26.9996 | 14.9473 | 53.1306
CARE2 MC1 | 275 | 39.2944 | 14.4171 | 6.2441 | 26.6329 | 35.3414 | 13.934 | 5.9313 | 25.6369
CARE2 MC2 | 275 | 39.2944 | 14.4171 | 6.2441 | 26.6329 | 35.3414 | 13.934 | 5.9313 | 25.6369
CARR1 M1 | 132 | 33.1293 | 12.1575 | 9.3873 | 26.5805 | 39.3831 | 14.959 | 11.3051 | 32.4604
CARR1 M2 | 132 | 33.1293 | 12.1575 | 9.3873 | 26.5805 | 39.3831 | 14.959 | 11.3051 | 32.4604
CARR1 M3 | 132 | 33.1293 | 12.1575 | 9.3873 | 26.5805 | 39.3831 | 14.959 | 11.3051 | 32.4604
CARR1 M4 | 132 | 41.3724 | 14.4637 | 13.4967 | 33.9514 | 53.3292 | 19.5269 | 16.9372 | 44.5524
CARR1 R1 | 132 | 33.1293 | 12.1575 | 9.3873 | 26.5805 | 39.3831 | 14.959 | 11.3051 | 32.4604
CARR1 R2 | 132 | 33.1293 | 12.1575 | 9.3873 | 26.5805 | 39.3831 | 14.959 | 11.3051 | 32.4604
CARR1 R3 | 132 | 41.3724 | 14.4637 | 13.4967 | 33.9514 | 53.3292 | 19.5269 | 16.9372 | 44.5524
CARR1 R4 | 132 | 41.3724 | 14.4637 | 13.4967 | 33.9514 | 53.3292 | 19.5269 | 16.9372 | 44.5524
CARR1B | 132 | 40.594 | 13.996 | 7.4818 | 27.2751 | 50.4533 | 18.9814 | 6.6121 | 33.4559
CARR1C | 132 | 40.4268 | 13.9802 | 7.0994 | 26.8704 | 50.0074 | 18.9344 | 5.2287 | 32.006
CARR1D | 132 | 40.7025 | 14.0143 | 7.6992 | 27.5184 | 50.83 | 19.0304 | 6.9537 | 33.8667
CARR2 M1 | 275 | 74.3905 | 26.223 | 18.3504 | 55.4353 | 82.2326 | 30.7474 | 21.009 | 64.4924
CARR2 M2 | 275 | 74.3905 | 26.223 | 18.3504 | 55.4353 | 82.2326 | 30.7474 | 21.009 | 64.4924
CARR2 R1 | 275 | 74.3905 | 26.223 | 18.3504 | 55.4353 | 82.2326 | 30.7474 | 21.009 | 64.4924
CARR2 R2 | 275 | 74.3905 | 26.223 | 18.3504 | 55.4353 | 82.2326 | 30.7474 | 21.009 | 64.4924
CARR4 M1 | 400 | 97.5463 | 35.0223 | 26.7585 | 76.2876 | 93.7943 | 36.1341 | 25.8706 | 76.9719
CARR4 M2/4 | 400 | 97.5463 | 35.0223 | 26.7585 | 76.2876 | 93.7943 | 36.1341 | 25.8706 | 76.9719
CARR4 R1 | 400 | 97.5463 | 35.0223 | 26.7585 | 76.2876 | 93.7943 | 36.1341 | 25.8706 | 76.9719
CARR4 R1/2 | 400 | 97.5463 | 35.0223 | 26.7585 | 76.2876 | 93.7943 | 36.1341 | 25.8706 | 76.9719
CARR4 R2 | 400 | 97.5463 | 35.0223 | 26.7585 | 76.2876 | 93.7943 | 36.1341 | 25.8706 | 76.9719
CARR4 R4 | 400 | 97.5463 | 35.0223 | 26.7585 | 76.2876 | 93.7943 | 36.1341 | 25.8706 | 76.9719
CARR4A | 400 | 85.0211 | 28.6675 | 6.1047 | 46.6467 | 75.8524 | 28.8934 | 6.7835 | 47.6449
CARR4B | 400 | 86.0913 | 28.9632 | 6.1872 | 47.1473 | 77.8306 | 29.6366 | 6.7563 | 48.6688
CASK1 M1 | 132 | 47.4941 | 15.6954 | 11.6473 | 33.844 | 53.4052 | 18.7441 | 14.4989 | 41.0071
CELL1 M1 | 132 | 45.3303 | 16.7723 | 14.1178 | 37.8374 | 56.1957 | 22.0862 | 16.631 | 47.8656
CELL1 M2 | 132 | 43.4831 | 16.0014 | 11.8929 | 34.5223 | 48.261 | 18.5987 | 12.8453 | 39.1477
CELL1 R1 | 132 | 45.3303 | 16.7723 | 14.1178 | 37.8374 | 56.1957 | 22.0862 | 16.631 | 47.8656
CELL1 R2 | 132 | 43.4831 | 16.0014 | 11.8929 | 34.5223 | 48.261 | 18.5987 | 12.8453 | 39.1477
CELL1A | 132 | 37.6547 | 13.3974 | 6.7486 | 25.6954 | 46.4387 | 18.5487 | 8.1379 | 34.3697
CELL4 M1 | 400 | 81.1451 | 28.7688 | 13.5252 | 54.2104 | 70.526 | 27.5203 | 12.6092 | 51.5288
CELL4 M2 | 400 | 81.1451 | 28.7688 | 13.5252 | 54.2104 | 70.526 | 27.5203 | 12.6092 | 51.5288
CELL4 R1 | 400 | 81.1451 | 28.7688 | 13.5252 | 54.2104 | 70.526 | 27.5203 | 12.6092 | 51.5288
CELL4 R2 | 400 | 81.1451 | 28.7688 | 13.5252 | 54.2104 | 70.526 | 27.5203 | 12.6092 | 51.5288
CHIC4 MB1 | 400 | 16.1025 | 6.0795 | 4.5618 | 13.1595 | 16.1159 | 6.237 | 4.6786 | 13.499
CHIC4 MB2 | 400 | 16.1025 | 6.0795 | 4.5618 | 13.1595 | 16.1159 | 6.237 | 4.6786 | 13.499
CHIC4 R1/2 | 400 | 31.5139 | 11.7161 | 8.7238 | 25.2929 | 26.9939 | 10.5892 | 7.0376 | 22.0131
CHIC4A | 400 | 31.5139 | 11.7161 | 8.7238 | 25.2929 | 26.9939 | 10.5892 | 7.0376 | 22.0131
CHIL41 M1 | 400 | 58.3602 | 20.9966 | 15.6957 | 45.3894 | 53.521 | 20.7282 | 13.9403 | 43.2543
CHIL41 MB 1 | 400 | 58.3602 | 20.9966 | 15.6957 | 45.3894 | 53.521 | 20.7282 | 13.9403 | 43.2543
CHSI2 MC1 | 275 | 78.4433 | 26.9706 | 15.7034 | 53.8456 | 69.9207 | 27.1089 | 11.445 | 49.7827
CHSI2 MC2 | 275 | 78.4433 | 26.9706 | 15.7034 | 53.8456 | 69.9207 | 27.1089 | 11.445 | 49.7827
CHSI2 MC3 | 275 | 78.4433 | 26.9706 | 15.7034 | 53.8456 | 69.9207 | 27.1089 | 11.445 | 49.7827
CHSI2 MC4 | 275 | 78.4433 | 26.9706 | 15.7034 | 53.8456 | 69.9207 | 27.1089 | 11.445 | 49.7827
CHTE2 MC1 | 275 | 61.507 | 21.761 | 13.4852 | 44.2599 | 54.733 | 21.5173 | 9.8625 | 40.2925
CHTE2 MC2 | 275 | 61.507 | 21.761 | 13.4852 | 44.2599 | 54.733 | 21.5173 | 9.8625 | 40.2925
CHTE2 MC3 | 275 | 61.507 | 21.761 | 13.4852 | 44.2599 | 54.733 | 21.5173 | 9.8625 | 40.2925
CHTE2 MC4 | 275 | 61.507 | 21.761 | 13.4852 | 44.2599 | 54.733 | 21.5173 | 9.8625 | 40.2925
CHUE4A | 400 | 96.4977 | 29.1348 | 7.4448 | 48.6477 | 93.9023 | 34.3473 | 5.9802 | 54.5547
CILF4 M1 | 400 | 56.7937 | 20.0181 | 10.7233 | 39.0332 | 55.1658 | 21.106 | 9.9226 | 39.771
CILF4 M2 | 400 | 56.7937 | 20.0181 | 10.7233 | 39.0332 | 55.1658 | 21.106 | 9.9226 | 39.771
CILF4 R1 | 400 | 56.7937 | 20.0181 | 10.7233 | 39.0332 | 55.1658 | 21.106 | 9.9226 | 39.771
CILF4 R2 | 400 | 56.7937 | 20.0181 | 10.7233 | 39.0332 | 55.1658 | 21.106 | 9.9226 | 39.771
CITR4 M5 | 400 | 91.0192 | 28.9605 | 18.7507 | 59.707 | 102.0969 | 37.994 | 17.7915 | 71.5232
CITR4 M6 | 400 | 91.0192 | 28.9605 | 18.7507 | 59.707 | 102.0969 | 37.994 | 17.7915 | 71.5232
CITR4 MC1 | 400 | 90.9573 | 28.9442 | 18.7346 | 59.6679 | 101.9898 | 37.965 | 17.7748 | 71.4654
CITR4 MC2 | 400 | 90.9573 | 28.9442 | 18.7346 | 59.6679 | 101.9898 | 37.965 | 17.7748 | 71.4654
CITR4 MC3 | 400 | 90.9573 | 28.9442 | 18.7346 | 59.6679 | 101.9898 | 37.965 | 17.7748 | 71.4654
CITR4 MC4 | 400 | 90.9573 | 28.9442 | 18.7346 | 59.6679 | 101.9898 | 37.965 | 17.7748 | 71.4654
CITR4 R5 | 400 | 91.0192 | 28.9605 | 18.7507 | 59.707 | 102.0969 | 37.994 | 17.7915 | 71.5232
CITR4 R6 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLEH4 M1 | 400 | 63.0505 | 22.0412 | 12.004 | 43.175 | 52.5631 | 20.4175 | 7.9651 | 36.8398
CLEH4 R1 | 400 | 63.0505 | 22.0412 | 12.004 | 43.175 | 52.5631 | 20.4175 | 7.9651 | 36.8398
CONQ4 M1 | 400 | 87.4644 | 29.9209 | 18.7547 | 61.0693 | 98.4894 | 36.474 | 23.054 | 74.6361
CONQ4 M2 | 400 | 87.4644 | 29.9209 | 18.7547 | 61.0693 | 98.4894 | 36.474 | 23.054 | 74.6361
CONQ4 M3 | 400 | 87.4644 | 29.9209 | 18.7547 | 61.0693 | 98.4894 | 36.474 | 23.054 | 74.6361
CONQ4 M4 | 400 | 87.4644 | 29.9209 | 18.7547 | 61.0693 | 98.4894 | 36.474 | 23.054 | 74.6361
CONQ4 R1/3 | 400 | 87.4644 | 29.9209 | 18.7547 | 61.0693 | 98.4894 | 36.474 | 23.054 | 74.6361
CONQ4 R2/4 | 400 | 87.4644 | 29.9209 | 18.7547 | 61.0693 | 98.4894 | 36.474 | 23.054 | 74.6361
COSO4 M | 400 | 77.947 | 26.3558 | 14.2877 | 51.5605 | 73.7775 | 27.8345 | 14.7204 | 54.0843
COSO4 R | 400 | 77.947 | 26.3558 | 14.2877 | 51.5605 | 73.7775 | 27.8345 | 14.7204 | 54.0843
COTT4 M1 | 400 | 80.746 | 28.6756 | 16.4694 | 57.0229 | 76.3073 | 29.2682 | 14.1887 | 55.5801
COTT4 M2 | 400 | 80.746 | 28.6756 | 16.4694 | 57.0229 | 76.3073 | 29.2682 | 14.1887 | 55.5801
COTT4 M3 | 400 | 74.6659 | 27.3307 | 21.3846 | 60.036 | 69.1751 | 26.7888 | 19.3154 | 57.2005
COTT4 M4 | 400 | 74.6659 | 27.3307 | 21.3846 | 60.036 | 69.1751 | 26.7888 | 19.3154 | 57.2005
COTT4 R1/2 | 400 | 74.6659 | 27.3307 | 21.3846 | 60.036 | 69.1751 | 26.7888 | 19.3154 | 57.2005
COTT4 R3/4 | 400 | 74.6659 | 27.3307 | 21.3846 | 60.036 | 69.1751 | 26.7888 | 19.3154 | 57.2005
COVE2 MC1 | 275 | 56.3244 | 20.0353 | 10.949 | 39.2831 | 54.5935 | 21.0255 | 10.8078 | 40.5424
COVE2 MC2 | 275 | 56.3244 | 20.0353 | 10.949 | 39.2831 | 54.5935 | 21.0255 | 10.8078 | 40.5424
COVE2 MC3 | 275 | 56.3244 | 20.0353 | 10.949 | 39.2831 | 54.5935 | 21.0255 | 10.8078 | 40.5424
COVE2 MC4 | 275 | 56.3244 | 20.0353 | 10.949 | 39.2831 | 54.5935 | 21.0255 | 10.8078 | 40.5424
COWL4 M1 | 400 | 87.4986 | 31.4734 | 24.2016 | 68.7116 | 83.4381 | 32.2284 | 22.1025 | 67.6804
COWL4 M2 | 400 | 87.4986 | 31.4734 | 24.2016 | 68.7116 | 83.4381 | 32.2284 | 22.1025 | 67.6804
COWL4 R1 | 400 | 87.4986 | 31.4734 | 24.2016 | 68.7116 | 83.4381 | 32.2284 | 22.1025 | 67.6804
COWL4 R2 | 400 | 87.4986 | 31.4734 | 24.2016 | 68.7116 | 83.4381 | 32.2284 | 22.1025 | 67.6804
CREB2A | 275 | 54.9605 | 19.3183 | 10.6312 | 37.9515 | 57.3941 | 21.2518 | 9.6798 | 39.7344
CREB2B | 275 | 54.9646 | 19.3183 | 10.6299 | 37.9502 | 57.8789 | 21.4271 | 9.7573 | 40.0598
CREB4 MB1 | 400 | 83.8692 | 29.2669 | 19.2214 | 60.611 | 77.3524 | 29.4157 | 16.5189 | 58.119
CREB4 MB2 | 400 | 83.8692 | 29.2669 | 19.2214 | 60.611 | 77.3524 | 29.4157 | 16.5189 | 58.119
CREB4 RB1 | 400 | 83.8692 | 29.2669 | 19.2214 | 60.611 | 77.3524 | 29.4157 | 16.5189 | 58.119
CREB4 RB2 | 400 | 83.8692 | 29.2669 | 19.2214 | 60.611 | 77.3524 | 29.4157 | 16.5189 | 58.119
DAIN4 M1 | 400 | 92.324 | 32.0996 | 17.0418 | 62.4375 | 86.0486 | 32.9605 | 16.1146 | 62.7277
DAIN4 M2 | 400 | 92.324 | 32.0996 | 17.0418 | 62.4375 | 86.0486 | 32.9605 | 16.1146 | 62.7277
DAIN4 R1 | 400 | 93.8845 | 32.5613 | 17.4077 | 63.4563 | 86.8857 | 33.2936 | 16.3225 | 63.4067
DAIN4 R2 | 400 | 93.8845 | 32.5613 | 17.4077 | 63.4563 | 86.8857 | 33.2936 | 16.3225 | 63.4067
DIDC4 M1 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 M2 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 M3 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 M4 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 M5 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 M6 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 R1/2 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 R3/4 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 R5 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DIDC4 R6 | 400 | 80.5265 | 28.1153 | 15.0856 | 54.8467 | 85.3681 | 32.0159 | 18.3129 | 63.5902
DINO41 1 | 400 | 49.0718 | 17.2409 | 11.8353 | 36.2176 | 56.9737 | 21.0622 | 14.9505 | 44.7369
DINO41 2 | 400 | 49.0718 | 17.2409 | 11.8353 | 36.2176 | 56.9737 | 21.0622 | 14.9505 | 44.7369
DINO41 3 | 400 | 49.0718 | 17.2409 | 11.8353 | 36.2176 | 56.9737 | 21.0622 | 14.9505 | 44.7369
DRAK1 M1 | 132 | 31.3316 | 11.1845 | 12.5025 | 28.3198 | 38.6368 | 14.2523 | 15.5206 | 35.6764
DRAK1 M2 | 132 | 31.3316 | 11.1845 | 12.5025 | 28.3198 | 38.6368 | 14.2523 | 15.5206 | 35.6764
DRAK1 R1 | 132 | 31.3316 | 11.1845 | 12.5025 | 28.3198 | 38.6368 | 14.2523 | 15.5206 | 35.6764
DRAK1 R2 | 132 | 31.3316 | 11.1845 | 12.5025 | 28.3198 | 38.6368 | 14.2523 | 15.5206 | 35.6764
DRAK4 M1 | 400 | 102.0008 | 35.2195 | 16.8729 | 66.6808 | 96.4169 | 37.2873 | 15.1716 | 67.9038
DRAK4 M2 | 400 | 102.0008 | 35.2195 | 16.8729 | 66.6808 | 96.4169 | 37.2873 | 15.1716 | 67.9038
DRAK4 M3 | 400 | 102.0008 | 35.2195 | 16.8729 | 66.6808 | 96.4169 | 37.2873 | 15.1716 | 67.9038
DRAK4 R1/3 | 400 | 102.0008 | 35.2195 | 16.8729 | 66.6808 | 96.4169 | 37.2873 | 15.1716 | 67.9038
DRAK4 R2 | 400 | 102.0008 | 35.2195 | 16.8729 | 66.6808 | 96.4169 | 37.2873 | 15.1716 | 67.9038
DRAX1 M1 | 132 | 37.0811 | 11.089 | 10.5332 | 26.2155 | 46.6608 | 15.7833 | 13.4323 | 35.7533
DRAX1 M2 | 132 | 37.0811 | 11.089 | 10.5332 | 26.2155 | 46.6608 | 15.7833 | 13.4323 | 35.7533
DRAX1 R1 | 132 | 37.0811 | 11.089 | 10.5332 | 26.2155 | 46.6608 | 15.7833 | 13.4323 | 35.7533
DRAX1 R2 | 132 | 37.0811 | 11.089 | 10.5332 | 26.2155 | 46.6608 | 15.7833 | 13.4323 | 35.7533
DRAX4 M1 | 400 | 87.0838 | 29.9845 | 18.9866 | 61.3911 | 98.5588 | 36.3928 | 23.0176 | 74.4848
DRAX4 M2 | 400 | 87.0838 | 29.9845 | 18.9866 | 61.3911 | 98.5588 | 36.3928 | 23.0176 | 74.4848
DRAX4 M3 | 400 | 87.0838 | 29.9845 | 18.9866 | 61.3911 | 98.5588 | 36.3928 | 23.0176 | 74.4848
DRAX4 M4 | 400 | 74.3175 | 25.9738 | 17.6007 | 54.3332 | 78.6544 | 29.2372 | 19.5895 | 60.9372
DRAX4 M5 | 400 | 74.3175 | 25.9738 | 17.6007 | 54.3332 | 78.6544 | 29.2372 | 19.5895 | 60.9372
DRAX4 M6 | 400 | 74.3175 | 25.9738 | 17.6007 | 54.3332 | 78.6544 | 29.2372 | 19.5895 | 60.9372
DRAX4 R1/2/3 | 400 | 87.0838 | 29.9845 | 18.9866 | 61.3911 | 98.5588 | 36.3928 | 23.0176 | 74.4848
DRAX4 R4/5/6 | 400 | 74.3175 | 25.9738 | 17.6007 | 54.3332 | 78.6544 | 29.2372 | 19.5895 | 60.9372
DUNG2 M1 | 275 | 40.0486 | 14.1739 | 11.562 | 31.6069 | 42.3267 | 15.6088 | 12.5411 | 34.6153
DUNG2 M2 | 275 | 40.0486 | 14.1739 | 11.562 | 31.6069 | 42.3267 | 15.6088 | 12.5411 | 34.6153
DUNG2 R1 | 275 | 40.0486 | 14.1739 | 11.562 | 31.6069 | 42.3267 | 15.6088 | 12.5411 | 34.6153
DUNG2 R2 | 275 | 40.0486 | 14.1739 | 11.562 | 31.6069 | 42.3267 | 15.6088 | 12.5411 | 34.6153
DUNG4 M1 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
DUNG4 M2 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
DUNG4 M3 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
DUNG4 M4 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
DUNG4 M5 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
DUNG4 R1/2 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
DUNG4 R4/5 | 400 | 58.1511 | 20.2045 | 6.72 | 35.2935 | 58.8928 | 22.1289 | 8.5577 | 39.8526
EALI2 MC1 | 275 | 53.4362 | 18.14 | 10.7408 | 36.3946 | 58.1279 | 22.5013 | 6.8677 | 38.6894
EALI2 MC2 | 275 | 53.4362 | 18.14 | 10.7408 | 36.3946 | 58.1279 | 22.5013 | 6.8677 | 38.6894
EALI2 MC3 | 275 | 53.4362 | 18.14 | 10.7408 | 36.3946 | 58.1279 | 22.5013 | 6.8677 | 38.6894
EALI2 MC4 | 275 | 53.4362 | 18.14 | 10.7408 | 36.3946 | 58.1279 | 22.5013 | 6.8677 | 38.6894
EASO4 M1 | 400 | 68.2228 | 24.0376 | 13.4831 | 47.4775 | 66.7059 | 25.0492 | 15.8619 | 51.2868
EASO4 M2 | 400 | 68.2228 | 24.0376 | 13.4831 | 47.4775 | 66.7059 | 25.0492 | 15.8619 | 51.2868
EASO4 R1 | 400 | 68.2228 | 24.0376 | 13.4831 | 47.4775 | 66.7059 | 25.0492 | 15.8619 | 51.2868
EASO4 R2 | 400 | 68.2228 | 24.0376 | 13.4831 | 47.4775 | 66.7059 | 25.0492 | 15.8619 | 51.2868
EASO4A | 400 | 68.2228 | 24.0376 | 13.4831 | 47.4775 | 66.7059 | 25.0492 | 15.8619 | 51.2868
EASO4B | 400 | 68.2228 | 24.0376 | 13.4831 | 47.4775 | 66.7059 | 25.0492 | 15.8619 | 51.2868
ECLA1 M1 | 132 | 45.8353 | 16.9837 | 13.0929 | 37.1115 | 48.6609 | 18.8629 | 14.4437 | 41.1199
ECLA1 M2 | 132 | 45.8353 | 16.9837 | 13.0929 | 37.1115 | 48.6609 | 18.8629 | 14.4437 | 41.1199
ECLA1 R1 | 132 | 45.133 | 16.7849 | 12.466 | 36.2034 | 53.9105 | 20.8389 | 15.1565 | 44.6272
ECLA1 R2 | 132 | 45.133 | 16.7849 | 12.466 | 36.2034 | 53.9105 | 20.8389 | 15.1565 | 44.6272
ECLA4 M1 | 400 | 94.8343 | 32.624 | 17.6067 | 63.7439 | 82.1396 | 31.6324 | 14.6591 | 59.3941
ECLA4 M2 | 400 | 94.8343 | 32.624 | 17.6067 | 63.7439 | 82.1396 | 31.6324 | 14.6591 | 59.3941
ECLA4 R1 | 400 | 94.8343 | 32.624 | 17.6067 | 63.7439 | 82.1396 | 31.6324 | 14.6591 | 59.3941
ECLA4 R2 | 400 | 94.8343 | 32.624 | 17.6067 | 63.7439 | 82.1396 | 31.6324 | 14.6591 | 59.3941
EGGB4 M1 | 400 | 80.2251 | 27.9171 | 17.0902 | 56.5709 | 79.9759 | 30.2028 | 15.8621 | 58.5754
EGGB4 M2 | 400 | 80.2251 | 27.9171 | 17.0902 | 56.5709 | 79.9759 | 30.2028 | 15.8621 | 58.5754
EGGB4 R1 | 400 | 67.6436 | 23.7906 | 15.6799 | 49.3248 | 66.2263 | 24.9903 | 14.2631 | 49.6047
EGGB4 R2 | 400 | 67.6436 | 23.7906 | 15.6799 | 49.3248 | 66.2263 | 24.9903 | 14.2631 | 49.6047
ELLA2 MC1 | 275 | 60.5134 | 21.3086 | 7.3311 | 37.466 | 62.249 | 23.7829 | 7.3339 | 40.968
ELLA2 MC2 | 275 | 60.5134 | 21.3086 | 7.3311 | 37.466 | 62.249 | 23.7829 | 7.3339 | 40.968
ELLA2 MC3 | 275 | 60.5134 | 21.3086 | 7.3311 | 37.466 | 62.249 | 23.7829 | 7.3339 | 40.968
ELLA2 MC4 | 275 | 60.5134 | 21.3086 | 7.3311 | 37.466 | 62.249 | 23.7829 | 7.3339 | 40.968
ELST1 M1 | 132 | 30.6142 | 11.0313 | 9.5768 | 25.1774 | 37.5811 | 14.0296 | 11.5876 | 31.4284
ELST1 M2 | 132 | 44.384 | 15.5197 | 12.8961 | 34.8442 | 55.4655 | 20.9323 | 15.1894 | 44.7921
ELST1 M3 | 132 | 38.5138 | 14.0943 | 9.44 | 29.3723 | 44.6539 | 17.0131 | 11.3121 | 35.3722
ELST1 R1 | 132 | 30.6142 | 11.0313 | 9.5768 | 25.1774 | 37.5811 | 14.0296 | 11.5876 | 31.4284
ELST1 R2 | 132 | 44.384 | 15.5197 | 12.8961 | 34.8442 | 55.4655 | 20.9323 | 15.1894 | 44.7921
ELST1 R3 | 132 | 38.5138 | 14.0943 | 9.44 | 29.3723 | 44.6539 | 17.0131 | 11.3121 | 35.3722
ELST2 M1 | 275 | 60.314 | 21.0349 | 14.5451 | 44.293 | 66.7385 | 24.8424 | 16.4918 | 51.6243
ELST2 M2 | 275 | 62.3281 | 21.8796 | 13.0017 | 43.9442 | 69.1199 | 26.2135 | 14.0426 | 51.1142
ELST2 R1 | 275 | 60.314 | 21.0349 | 14.5451 | 44.293 | 66.7385 | 24.8424 | 16.4918 | 51.6243
ELST2 R2 | 275 | 62.3281 | 21.8796 | 13.0017 | 43.9442 | 69.1199 | 26.2135 | 14.0426 | 51.1142
ELST4 M1 | 400 | 79.5821 | 27.4821 | 23.0651 | 61.9308 | 95.8368 | 35.7464 | 27.3188 | 77.8719
ELST4 R1 | 400 | 79.5821 | 27.4821 | 23.0651 | 61.9308 | 95.8368 | 35.7464 | 27.3188 | 77.8719
ELST4A | 400 | 52.2988 | 18.0895 | 5.9833 | 31.5657 | 50.9192 | 19.0181 | 7.1332 | 34.0289
ENDE4 MC1 | 400 | 77.0113 | 27.3622 | 12.8924 | 51.5885 | 57.0916 | 22.4881 | 9.1588 | 40.9618
ENDE4 MC2 | 400 | 77.0113 | 27.3622 | 12.8924 | 51.5885 | 57.0916 | 22.4881 | 9.1588 | 40.9618
ENDE4 MC3 | 400 | 77.0113 | 27.3622 | 12.8924 | 51.5885 | 57.0916 | 22.4881 | 9.1588 | 40.9618
ENDE4 MC4 | 400 | 77.0113 | 27.3622 | 12.8924 | 51.5885 | 57.0916 | 22.4881 | 9.1588 | 40.9618
EXET4 M1 | 400 | 35.6706 | 12.9251 | 5.643 | 23.9219 | 39.0273 | 15.0615 | 6.7478 | 28.0479
EXET4 M2 | 400 | 35.6706 | 12.9251 | 5.643 | 23.9219 | 39.0273 | 15.0615 | 6.7478 | 28.0479
EXET4 R1 | 400 | 35.6706 | 12.9251 | 5.643 | 23.9219 | 39.0273 | 15.0615 | 6.7478 | 28.0479
EXET4 R2 | 400 | 35.6706 | 12.9251 | 5.643 | 23.9219 | 39.0273 | 15.0615 | 6.7478 | 28.0479
FAWL1 M1 | 132 | 41.9305 | 14.5894 | 15.1701 | 35.8026 | 54.1408 | 20.2797 | 18.3706 | 47.0505
FAWL1 M2 | 132 | 41.9305 | 14.5894 | 15.1701 | 35.8026 | 54.1408 | 20.2797 | 18.3706 | 47.0505
FAWL1 R1 | 132 | 41.9305 | 14.5894 | 15.1701 | 35.8026 | 54.1408 | 20.2797 | 18.3706 | 47.0505
FAWL1 R2 | 132 | 41.9305 | 14.5894 | 15.1701 | 35.8026 | 54.1408 | 20.2797 | 18.3706 | 47.0505
FAWL4 M1/3 | 400 | 58.2197 | 19.6758 | 6.5221 | 34.3478 | 53.5735 | 20.3042 | 5.9692 | 34.6837
FAWL4 M1/3(1) | 400 | 58.2197 | 19.6758 | 6.5221 | 34.3478 | 53.5735 | 20.3042 | 5.9692 | 34.6837
FAWL4 M2/4(2) | 400 | 58.2197 | 19.6758 | 6.5221 | 34.3478 | 53.5735 | 20.3042 | 5.9692 | 34.6837
FAWL4 M2/4(3) | 400 | 58.2197 | 19.6758 | 6.5221 | 34.3478 | 53.5735 | 20.3042 | 5.9692 | 34.6837
FAWL4 R1/3 | 400 | 58.2197 | 19.6758 | 6.5221 | 34.3478 | 53.5735 | 20.3042 | 5.9692 | 34.6837
FAWL4 R2/4 | 400 | 58.2197 | 19.6758 | 6.5221 | 34.3478 | 53.5735 | 20.3042 | 5.9692 | 34.6837
FECK2 M1 | 275 | 59.4761 | 21.3797 | 12.8847 | 43.1202 | 59.5797 | 22.8074 | 12.9901 | 45.2446
FECK2 M2 | 275 | 59.4761 | 21.3797 | 12.8847 | 43.1202 | 59.5797 | 22.8074 | 12.9901 | 45.2446
FECK2 R | 275 | 59.4761 | 21.3797 | 12.8847 | 43.1202 | 59.5797 | 22.8074 | 12.9901 | 45.2446
FECK4 M1 | 400 | 70.9431 | 25.5321 | 11.4309 | 47.5387 | 62.09 | 24.2481 | 11.3047 | 45.5967
FECK4 M2 | 400 | 70.9431 | 25.5321 | 11.4309 | 47.5387 | 62.09 | 24.2481 | 11.3047 | 45.5967
FECK4 R1 | 400 | 70.9431 | 25.5321 | 11.4309 | 47.5387 | 62.09 | 24.2481 | 11.3047 | 45.5967
FECK4 R2 | 400 | 70.9431 | 25.5321 | 11.4309 | 47.5387 | 62.09 | 24.2481 | 11.3047 | 45.5967
FENW4A | 400 | 83.4433 | 28.1211 | 7.8175 | 47.5868 | 78.6383 | 29.6622 | 5.3883 | 47.337
FERR2 M1 | 275 | 53.5711 | 18.9455 | 9.5307 | 36.3237 | 55.8266 | 20.9734 | 10.0986 | 39.7595
FERR2 M2 | 275 | 52.4645 | 18.5496 | 12.3683 | 38.6014 | 57.383 | 21.3986 | 12.2898 | 42.5519
FERR2 R1 | 275 | 57.3188 | 20.1868 | 9.9513 | 38.4998 | 58.4604 | 22.1187 | 9.0035 | 40.2841
FERR2 R2 | 275 | 57.3188 | 20.1868 | 9.9513 | 38.4998 | 58.4604 | 22.1187 | 9.0035 | 40.2841
FERR2A | 275 | 52.4885 | 18.4112 | 9.8798 | 35.9172 | 57.2464 | 21.2856 | 9.7627 | 39.865
FERR2B | 275 | 53.123 | 18.5962 | 7.4145 | 33.7135 | 55.1161 | 20.6836 | 7.6515 | 36.9025
FERR4A | 400 | 62.6804 | 21.5352 | 6.3945 | 36.8499 | 58.578 | 22.0173 | 6.3225 | 37.4597
FFES2 Term205 | 275 | 32.6191 | 11.9992 | 2.4853 | 19.4548 | 32.3002 | 12.5981 | 2.2187 | 20.0352
FFES2 Term210 | 275 | 32.5723 | 12.0001 | 2.4688 | 19.4394 | 32.7349 | 12.7645 | 2.2406 | 20.2923
FIDF2 M1 | 275 | 43.482 | 15.4113 | 12.5811 | 34.376 | 45.2799 | 16.8152 | 12.2166 | 35.9969
FIDF2 M2 | 275 | 42.8113 | 15.1492 | 12.422 | 33.8462 | 43.7218 | 16.2373 | 11.6233 | 34.5863
FIDF2 M3 | 275 | 47.0333 | 16.6107 | 12.374 | 35.8651 | 47.4519 | 17.741 | 11.5544 | 36.6439
FIDF2 M4 | 275 | 47.4401 | 16.7505 | 12.4823 | 36.1712 | 48.7492 | 18.2032 | 12.0085 | 37.7518
FIDF2 R1 | 275 | 43.482 | 15.4113 | 12.5811 | 34.376 | 45.2799 | 16.8152 | 12.2166 | 35.9969
FIDF2 R2 | 275 | 47.4401 | 16.7505 | 12.4823 | 36.1712 | 48.7492 | 18.2032 | 12.0085 | 37.7518
FLEE4 MC1 | 400 | 82.9111 | 28.3147 | 14.3439 | 54.387 | 73.184 | 28.1107 | 12.8456 | 52.6001
FLEE4 MC2 | 400 | 82.9111 | 28.3147 | 14.3439 | 54.387 | 73.184 | 28.1107 | 12.8456 | 52.6001
FLEE4 MC3 | 400 | 82.9111 | 28.3147 | 14.3439 | 54.387 | 73.184 | 28.1107 | 12.8456 | 52.6001
FLEE4 MC4 | 400 | 82.9111 | 28.3147 | 14.3439 | 54.387 | 73.184 | 28.1107 | 12.8456 | 52.6001
FLIB4 M1 | 400 | 82.8508 | 28.4694 | 17.9524 | 58.2142 | 93.3377 | 34.8439 | 20.519 | 69.7958
FLIB4 M2 | 400 | 82.8508 | 28.4694 | 17.9524 | 58.2142 | 93.3377 | 34.8439 | 20.519 | 69.7958
FOUR2 MC1 | 275 | 37.5743 | 14.4193 | 4.9351 | 25.3271 | 31.2821 | 12.7651 | 3.8673 | 21.9199
FOUR2 MC2 | 275 | 37.5743 | 14.4193 | 4.9351 | 25.3271 | 31.2821 | 12.7651 | 3.8673 | 21.9199
FROD2 MC1 | 275 | 44.1405 | 15.5963 | 13.3571 | 35.4136 | 48.7046 | 17.8471 | 15.0633 | 40.3029
FROD2 MC3 | 275 | 44.0576 | 15.2717 | 8.1818 | 29.7793 | 48.1065 | 17.5451 | 8.7966 | 33.6092
FROD4 M1 | 400 | 66.5388 | 23.8476 | 20.2752 | 54.0008 | 68.6872 | 25.8814 | 21.4146 | 58.0164
FROD4 R1 | 400 | 66.5388 | 23.8476 | 20.2752 | 54.0008 | 68.6872 | 25.8814 | 21.4146 | 58.0164
GART4A | 400 | 72.2933 | 24.5717 | 9.243 | 43.9926 | 64.7912 | 24.4815 | 5.5227 | 40.1448
GART4B | 400 | 77.8533 | 26.4503 | 9.2848 | 46.6911 | 72.4316 | 27.3557 | 6.2248 | 44.9117
GRAI4 M1 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 M2 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 M3 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 M4 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 M5 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 M6 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 M7 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 R1/2 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 R3 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 R4 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 R4/5 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRAI4 R5 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 R6 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GRAI4 R7 | 400 | 97.9922 | 33.5943 | 27.095 | 74.6045 | 99.0258 | 37.0039 | 28.6193 | 80.9508
GREN1 M1 | 132 | 39.3045 | 14.1756 | 10.9044 | 30.9517 | 45.5585 | 17.8029 | 11.2678 | 36.4449
GREN1 M2 | 132 | 39.4551 | 14.4114 | 11.1723 | 31.5532 | 40.5563 | 15.8388 | 10.3356 | 32.735
GREN1 R1 | 132 | 39.3045 | 14.1756 | 10.9044 | 30.9517 | 45.5585 | 17.8029 | 11.2678 | 36.4449
GREN1 R2 | 132 | 39.4551 | 14.4114 | 11.1723 | 31.5532 | 40.5563 | 15.8388 | 10.3356 | 32.735
GREN4 M1 | 400 | 70.8708 | 25.3853 | 11.1116 | 47.0119 | 51.0941 | 20.448 | 8.272 | 37.1898
GREN4 M2 | 400 | 70.8708 | 25.3853 | 11.1116 | 47.0119 | 51.0941 | 20.448 | 8.272 | 37.1898
GREN4 R1 | 400 | 70.8708 | 25.3853 | 11.1116 | 47.0119 | 51.0941 | 20.448 | 8.272 | 37.1898
GREN4 R2 | 400 | 70.8708 | 25.3853 | 11.1116 | 47.0119 | 51.0941 | 20.448 | 8.272 | 37.1898
GRIW4 MC1 | 400 | 54.521 | 19.3075 | 13.525 | 40.8299 | 50.2449 | 19.2151 | 9.9283 | 37.1026
GRIW4 MC2 | 400 | 54.521 | 19.3075 | 13.525 | 40.8299 | 50.2449 | 19.2151 | 9.9283 | 37.1026
GRSA2 M1 | 275 | 47.5316 | 16.8659 | 13.3822 | 37.2342 | 51.3783 | 19.0721 | 13.6787 | 40.6507
GRSA2 M2 | 275 | 47.5316 | 16.8659 | 13.3822 | 37.2342 | 51.3783 | 19.0721 | 13.6787 | 40.6507
GRSA2 R1 | 275 | 47.5316 | 16.8659 | 13.3822 | 37.2342 | 51.3783 | 19.0721 | 13.6787 | 40.6507
GRSA2 R2 | 275 | 47.5316 | 16.8659 | 13.3822 | 37.2342 | 51.3783 | 19.0721 | 13.6787 | 40.6507
GRSB2 M3 | 275 | 47.7897 | 16.9461 | 13.5115 | 37.4769 | 52.1303 | 19.3032 | 14.2117 | 41.5105
GRSB2 M4 | 275 | 47.7897 | 16.9461 | 13.5115 | 37.4769 | 52.1303 | 19.3032 | 14.2117 | 41.5105
GRSB2 R3 | 275 | 47.7897 | 16.9461 | 13.5115 | 37.4769 | 52.1303 | 19.3032 | 14.2117 | 41.5105
GRSB2 R4 | 275 | 47.7897 | 16.9461 | 13.5115 | 37.4769 | 52.1303 | 19.3032 | 14.2117 | 41.5105
HACK2A | 275 | 66.9172 | 22.4421 | 9.3017 | 41.0396 | 70.6134 | 26.0163 | 10.1181 | 46.9107
HACK2B | 275 | 71.0261 | 23.5522 | 9.3994 | 42.7073 | 74.5821 | 27.4312 | 10.1499 | 48.9435
HACK4 M1 | 400 | 99.2183 | 31.2742 | 20.3847 | 64.6131 | 116.3237 | 41.8989 | 22.5509 | 81.8049
HACK4 M2 | 400 | 99.2183 | 31.2742 | 20.3847 | 64.6131 | 116.3237 | 41.8989 | 22.5509 | 81.8049
HACK4 R1 | 400 | 99.2183 | 31.2742 | 20.3847 | 64.6131 | 116.3237 | 41.8989 | 22.5509 | 81.8049
HACK4 R2 | 400 | 99.2183 | 31.2742 | 20.3847 | 64.6131 | 116.3237 | 41.8989 | 22.5509 | 81.8049
HAMB4A | 400 | 65.4007 | 22.3091 | 9.2784 | 40.8282 | 56.2903 | 21.4983 | 4.8496 | 35.2528
HAMB4A_HEYS | 400 | 65.4007 | 22.3091 | 9.2784 | 40.8282 | 56.2903 | 21.4983 | 4.8496 | 35.2528
HAMB4A_PEWO | 400 | 65.4007 | 22.3091 | 9.2784 | 40.8282 | 56.2903 | 21.4983 | 4.8496 | 35.2528
HAMB4B | 400 | 65.3842 | 22.3045 | 9.2846 | 40.8279 | 55.8627 | 21.3369 | 4.8566 | 35.0315
HAMB4B_HEYS | 400 | 65.3842 | 22.3045 | 9.2846 | 40.8279 | 55.8627 | 21.3369 | 4.8566 | 35.0315
HAMB4B_PEWO | 400 | 65.3842 | 22.3045 | 9.2846 | 40.8279 | 55.8627 | 21.3369 | 4.8566 | 35.0315
HAMH1B | 132 | 48.0195 | 16.4291 | 9.1331 | 32.3674 | 57.1325 | 21.5273 | 5.7024 | 36.1467
HAMH1C | 132 | 46.9611 | 16.1916 | 7.8958 | 30.7942 | 55.234 | 20.4886 | 7.3487 | 36.3239
HAMH4 M1 | 400 | 68.7191 | 24.6161 | 11.2769 | 46.0894 | 66.7288 | 25.7562 | 12.129 | 48.5538
HAMH4 M2 | 400 | 68.7191 | 24.6161 | 11.2769 | 46.0894 | 66.7288 | 25.7562 | 12.129 | 48.5538
HAMH4 R1 | 400 | 68.7191 | 24.6161 | 11.2769 | 46.0894 | 66.7288 | 25.7562 | 12.129 | 48.5538
HAMH4 R2 | 400 | 68.7191 | 24.6161 | 11.2769 | 46.0894 | 66.7288 | 25.7562 | 12.129 | 48.5538
HARK1 M1 | 132 | 23.5131 | 8.8329 | 5.99 | 18.4816 | 28.6069 | 11.1585 | 6.79 | 22.5705
HARK1 M2 | 132 | 23.5131 | 8.8329 | 5.99 | 18.4816 | 28.6069 | 11.1585 | 6.79 | 22.5705
HARK1 R1 | 132 | 24.1705 | 9.7027 | 6.615 | 20.3367 | 28.1617 | 11.5091 | 7.8071 | 24.0835
HARK1 R2 | 132 | 25.9415 | 9.917 | 6.6198 | 20.6446 | 31.4486 | 12.4862 | 7.9422 | 25.6003
HARK1 R3 | 132 | 25.9415 | 9.917 | 6.6198 | 20.6446 | 31.4486 | 12.4862 | 7.9422 | 25.6003
HARK2 MC1 | 275 | 34.483 | 12.8445 | 7.8681 | 26.033 | 39.3111 | 15.0882 | 9.5604 | 30.8982
HARK2 MC11 | 275 | 34.4802 | 13.0628 | 10.1298 | 28.6034 | 39.3072 | 15.188 | 12.0601 | 33.5392
HARK2 MC12 | 275 | 34.4802 | 13.0628 | 10.1298 | 28.6034 | 39.3072 | 15.188 | 12.0601 | 33.5392
HARK2 MC13 | 275 | 34.4802 | 13.0628 | 10.1298 | 28.6034 | 39.3072 | 15.188 | 12.0601 | 33.5392
HARK2 MC2 | 275 | 34.483 | 12.8445 | 7.8681 | 26.033 | 39.3111 | 15.0882 | 9.5604 | 30.8982
HARK2 MC3 | 275 | 34.483 | 12.8445 | 7.8681 | 26.033 | 39.3111 | 15.0882 | 9.5604 | 30.8982
HARK2 MC4 | 275 | 34.483 | 12.8445 | 7.8681 | 26.033 | 39.3111 | 15.0882 | 9.5604 | 30.8982
HARK2 MC6 | 275 | 34.483 | 12.8445 | 7.8681 | 26.033 | 39.3111 | 15.0882 | 9.5604 | 30.8982
HARK2 MC8 | 275 | 34.4802 | 13.0628 | 10.1298 | 28.6034 | 39.3072 | 15.188 | 12.0601 | 33.5392
HARK2 MC9 | 275 | 34.4802 | 13.0628 | 10.1298 | 28.6034 | 39.3072 | 15.188 | 12.0601 | 33.5392
HARK4 M1 | 400 | 56.6301 | 20.5176 | 10.2343 | 39.2506 | 49.3998 | 19.1169 | 10.1877 | 37.2231
HARK4 M2 | 400 | 56.6301 | 20.5176 | 10.2343 | 39.2506 | 49.3998 | 19.1169 | 10.1877 | 37.2231
HARK4 R1 | 400 | 56.6301 | 20.5176 | 10.2343 | 39.2506 | 49.3998 | 19.1169 | 10.1877 | 37.2231
HARK4 R2 | 400 | 56.6301 | 20.5176 | 10.2343 | 39.2506 | 49.3998 | 19.1169 | 10.1877 | 37.2231
HARM2 MC1 | 275 | 62.8064 | 21.9485 | 14.1801 | 45.2199 | 55.2631 | 21.3343 | 9.4694 | 39.6407
HARM2 MC2 | 275 | 62.8064 | 21.9485 | 14.1801 | 45.2199 | 55.2631 | 21.3343 | 9.4694 | 39.6407
HARM2 MC3 | 275 | 62.8064 | 21.9485 | 14.1801 | 45.2199 | 55.2631 | 21.3343 | 9.4694 | 39.6407
HARM2 MC4 | 275 | 62.8064 | 21.9485 | 14.1801 | 45.2199 | 55.2631 | 21.3343 | 9.4694 | 39.6407
HATL2 M1 | 275 | 84.9469 | 28.5257 | 23.1209 | 63.4623 | 88.6774 | 32.403 | 24.6601 | 70.4848
HATL2 M2 | 275 | 84.9469 | 28.5257 | 23.1209 | 63.4623 | 88.6774 | 32.403 | 24.6601 | 70.4848
HATL2 R1 | 275 | 84.9469 | 28.5257 | 23.1209 | 63.4623 | 88.6774 | 32.403 | 24.6601 | 70.4848
HATL2 R2 | 275 | 84.9469 | 28.5257 | 23.1209 | 63.4623 | 88.6774 | 32.403 | 24.6601 | 70.4848
HAWP2 MC1 | 275 | 83.2081 | 28.2199 | 20.2519 | 60.1609 | 74.3637 | 28.4099 | 13.6346 | 53.8124
HAWP2 MC2 | 275 | 83.2081 | 28.2199 | 20.2519 | 60.1609 | 74.3637 | 28.4099 | 13.6346 | 53.8124
HAWP2 MC3 | 275 | 83.2081 | 28.2199 | 20.2519 | 60.1609 | 74.3637 | 28.4099 | 13.6346 | 53.8124
HAWP2 MC4 | 275 | 83.2081 | 28.2199 | 20.2519 | 60.1609 | 74.3637 | 28.4099 | 13.6346 | 53.8124
HEDO2 M1 | 275 | 47.3711 | 17.2294 | 11.9347 | 36.3006 | 52.4626 | 19.7257 | 13.7119 | 41.6082
HEDO2 M2 | 275 | 47.3711 | 17.2294 | 11.9347 | 36.3006 | 52.4626 | 19.7257 | 13.7119 | 41.6082
HEDO2 R1 | 275 | 47.3711 | 17.2294 | 11.9347 | 36.3006 | 52.4626 | 19.7257 | 13.7119 | 41.6082
HEDO2 R2 | 275 | 47.3711 | 17.2294 | 11.9347 | 36.3006 | 52.4626 | 19.7257 | 13.7119 | 41.6082
HEYS1 M1 | 132 | 31.5594 | 10.5218 | 11.2353 | 26.1154 | 37.5335 | 13.3795 | 12.7445 | 31.6659
HEYS1 M2 | 132 | 31.5594 | 10.5218 | 11.2353 | 26.1154 | 37.5335 | 13.3795 | 12.7445 | 31.6659
HEYS1 R1 | 132 | 31.5594 | 10.5218 | 11.2353 | 26.1154 | 37.5335 | 13.3795 | 12.7445 | 31.6659
HEYS1 R2 | 132 | 31.5594 | 10.5218 | 11.2353 | 26.1154 | 37.5335 | 13.3795 | 12.7445 | 31.6659
HEYS4 M1 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 M2 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 M3 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 M4 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 M5 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 R1/2 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 R3/4 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HEYS4 R5 | 400 | 90.2571 | 31.5626 | 31.1881 | 75.8243 | 96.5635 | 35.6345 | 33.9106 | 84.3055
HIBU4 M1 | 400 | 97.485 | 30.7322 | 20.1969 | 63.6588 | 115.3097 | 41.4101 | 22.9922 | 81.5548
HIBU4 M2 | 400 | 97.485 | 30.7322 | 20.1969 | 63.6588 | 115.3097 | 41.4101 | 22.9922 | 81.5548
HIBU4 R1 | 400 | 97.485 | 30.7322 | 20.1969 | 63.6588 | 115.3097 | 41.4101 | 22.9922 | 81.5548
HIBU4 R2 | 400 | 97.485 | 30.7322 | 20.1969 | 63.6588 | 115.3097 | 41.4101 | 22.9922 | 81.5548
HIGM2 M1 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM2 M2 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM2 M3 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM2 R1 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM2 R4 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM2 R5 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM2 R6 | 275 | 55.1099 | 20.0286 | 13.5288 | 41.8535 | 52.7948 | 20.6909 | 10.7914 | 40.0527
HIGM4 MC1 | 400 | 57.881 | 20.805 | 12.6511 | 42.0739 | 52.7422 | 20.4089 | 9.4251 | 38.2876
HIGM4 MC2 | 400 | 57.881 | 20.805 | 12.6511 | 42.0739 | 52.7422 | 20.4089 | 9.4251 | 38.2876
HIGM4A | 400 | 51.1821 | 18.1286 | 6.238 | 31.8757 | 46.4963 | 17.8 | 4.0398 | 29.2128
HINP2 M1 | 275 | 20.4383 | 7.2933 | 5.8516 | 16.1659 | 21.6239 | 8.0654 | 5.7406 | 17.1467
HINP2 M2 | 275 | 20.7202 | 7.4006 | 5.8648 | 16.3309 | 23.5828 | 8.8454 | 5.8331 | 18.3423
HINP4 M1 | 400 | 41.4592 | 15.0151 | 6.3703 | 27.6049 | 36.6213 | 14.4584 | 5.5861 | 26.0333
HINP4 M2 | 400 | 41.4592 | 15.0151 | 6.3703 | 27.6049 | 36.6213 | 14.4584 | 5.5861 | 26.0333
HINP4 M3 | 400 | 41.4592 | 15.0151 | 6.3703 | 27.6049 | 36.6213 | 14.4584 | 5.5861 | 26.0333
HINP4 M4 | 400 | 41.4592 | 15.0151 | 6.3703 | 27.6049 | 36.6213 | 14.4584 | 5.5861 | 26.0333
HINP4 R1/2 | 400 | 41.4592 | 15.0151 | 6.3703 | 27.6049 | 36.6213 | 14.4584 | 5.5861 | 26.0333
HINP4 R3/4 | 400 | 41.4592 | 15.0151 | 6.3703 | 27.6049 | 36.6213 | 14.4584 | 5.5861 | 26.0333
HUMR4 M1 | 400 | 72.7341 | 25.0257 | 18.6255 | 54.0172 | 74.3926 | 27.6073 | 18.4574 | 57.5001
HUMR4 M2 | 400 | 72.7341 | 25.0257 | 18.6255 | 54.0172 | 74.3926 | 27.6073 | 18.4574 | 57.5001
HUMR4 R1 | 400 | 72.7341 | 25.0257 | 18.6255 | 54.0172 | 74.3926 | 27.6073 | 18.4574 | 57.5001
HUMR4 R2 | 400 | 72.7341 | 25.0257 | 18.6255 | 54.0172 | 74.3926 | 27.6073 | 18.4574 | 57.5001
HURS2 MC1 | 275 | 63.1021 | 21.3728 | 15.7044 | 45.9301 | 67.1087 | 26.0063 | 14.3062 | 51.0846
HURS2 MC2 | 275 | 63.1021 | 21.3728 | 15.7044 | 45.9301 | 67.1087 | 26.0063 | 14.3062 | 51.0846
HURS2 MC3 | 275 | 63.1021 | 21.3728 | 15.7044 | 45.9301 | 67.1087 | 26.0063 | 14.3062 | 51.0846
HURS2 MC4 | 275 | 63.1021 | 21.3728 | 15.7044 | 45.9301 | 67.1087 | 26.0063 | 14.3062 | 51.0846
HUTT4 MC1 | 400 | 65.3048 | 23.8899 | 19.3901 | 53.1754 | 46.4161 | 18.5983 | 11.0382 | 37.3402
HUTT4 MC2 | 400 | 65.3048 | 23.8899 | 19.3901 | 53.1754 | 46.4161 | 18.5983 | 11.0382 | 37.3402
HUTT4 MC3 | 400 | 65.3048 | 23.8899 | 19.3901 | 53.1754 | 46.4161 | 18.5983 | 11.0382 | 37.3402
HUTT4 MC4 | 400 | 65.3048 | 23.8899 | 19.3901 | 53.1754 | 46.4161 | 18.5983 | 11.0382 | 37.3402
IMPP4 MC1 | 400 | 43.7494 | 15.7812 | 8.2894 | 30.6074 | 40.2662 | 15.4772 | 7.6154 | 29.5034
IMPP4 MC2 | 400 | 43.7494 | 15.7812 | 8.2894 | 30.6074 | 40.2662 | 15.4772 | 7.6154 | 29.5034
INDQ4 MC1 | 400 | 27.9107 | 10.3428 | 3.8765 | 18.5034 | 31.4365 | 12.2005 | 5.1884 | 22.4425
INDQ4 MC2 | 400 | 27.9107 | 10.3428 | 3.8765 | 18.5034 | 31.4365 | 12.2005 | 5.1884 | 22.4425
INDQ4 MC3 | 400 | 27.9107 | 10.3428 | 3.8765 | 18.5034 | 31.4365 | 12.2005 | 5.1884 | 22.4425
INDQ4 MC4 | 400 | 27.9107 | 10.3428 | 3.8765 | 18.5034 | 31.4365 | 12.2005 | 5.1884 | 22.4425
IROA1 M1 | 132 | 39.7768 | 14.171 | 9.7517 | 29.7925 | 49.0844 | 18.3993 | 11.8915 | 37.912
IROA1 M2 | 132 | 39.7768 | 14.171 | 9.7517 | 29.7925 | 49.0844 | 18.3993 | 11.8915 | 37.912
IROA1 R1 | 132 | 42.3961 | 15.0574 | 10.2043 | 31.4988 | 51.5641 | 19.3885 | 11.917 | 39.3365
IROA1 R2 | 132 | 28.2436 | 10.113 | 8.3507 | 22.6526 | 34.9349 | 12.9989 | 9.6815 | 28.0647
IROA2 MC1 | 275 | 52.6857 | 18.85 | 9.2966 | 35.9545 | 52.4276 | 20.171 | 9.9839 | 38.5101
IROA2 MC2 | 275 | 52.6857 | 18.85 | 9.2966 | 35.9545 | 52.4276 | 20.171 | 9.9839 | 38.5101
IROA2 MC3 | 275 | 52.6857 | 18.85 | 9.2966 | 35.9545 | 52.4276 | 20.171 | 9.9839 | 38.5101
IROA2 MC4 | 275 | 52.6857 | 18.85 | 9.2966 | 35.9545 | 52.4276 | 20.171 | 9.9839 | 38.5101
IROA2 MC5 | 275 | 52.6857 | 18.85 | 9.2966 | 35.9545 | 52.4276 | 20.171 | 9.9839 | 38.5101
IRON1 M1 | 132 | 26.7245 | 10.3065 | 8.8454 | 23.4209 | 30.7666 | 12.0441 | 10.0805 | 27.1134
IRON1 M2 | 132 | 26.6004 | 10.2621 | 8.7494 | 23.2622 | 30.4766 | 11.945 | 9.9063 | 26.7991
IRON1 R1 | 132 | 17.946 | 6.5118 | 6.2703 | 15.4793 | 20.4665 | 7.4806 | 7.2805 | 17.8597
IRON1 R2 | 132 | 17.946 | 6.5118 | 6.2703 | 15.4793 | 20.4665 | 7.4806 | 7.2805 | 17.8597
IRON4 M1 | 400 | 65.1484 | 23.364 | 11.3791 | 44.4208 | 57.5233 | 22.4742 | 10.0643 | 41.8476
IRON4 M2 | 400 | 65.1484 | 23.364 | 11.3791 | 44.4208 | 57.5233 | 22.4742 | 10.0643 | 41.8476
IRON4 R1 | 400 | 65.1484 | 23.364 | 11.3791 | 44.4208 | 57.5233 | 22.4742 | 10.0643 | 41.8476
IRON4 R2 | 400 | 65.1484 | 23.364 | 11.3791 | 44.4208 | 57.5233 | 22.4742 | 10.0643 | 41.8476
IVER2 M1 | 275 | 61.6802 | 21.7377 | 14.5127 | 45.2545 | 67.1247 | 25.281 | 15.3702 | 51.1229
IVER2 M2 | 275 | 61.6802 | 21.7377 | 14.5127 | 45.2545 | 67.1247 | 25.281 | 15.3702 | 51.1229
IVER2 R1 | 275 | 61.6802 | 21.7377 | 14.5127 | 45.2545 | 67.1247 | 25.281 | 15.3702 | 51.1229
IVER2 R2 | 275 | 63.6757 | 22.2997 | 13.7699 | 45.3065 | 64.805 | 24.7071 | 13.0808 | 48.022
IVER4A | 400 | 43.5064 | 15.2311 | 4.8516 | 26.3917 | 42.0151 | 15.8685 | 5.2968 | 27.7382
IVER4B | 400 | 41.7059 | 14.6991 | 4.427 | 25.2146 | 39.7355 | 15.2359 | 4.5093 | 26.0561
JORD2 MC1 | 275 | 43.6017 | 16.2236 | 6.9601 | 29.9038 | 45.0025 | 18.4274 | 6.3733 | 32.4336
JORD2 MC2 | 275 | 43.6017 | 16.2236 | 6.9601 | 29.9038 | 45.0025 | 18.4274 | 6.3733 | 32.4336
KEAD4 M2 | 400 | 77.4133 | 27.1747 | 17.8456 | 56.2765 | 75.54 | 28.5736 | 16.4596 | 56.8688
KEAD4 M3 | 400 | 71.6603 | 25.087 | 17.3714 | 52.8498 | 66.2488 | 25.0944 | 14.1574 | 49.6462
KEAD4 R2 | 400 | 77.4133 | 27.1747 | 17.8456 | 56.2765 | 75.54 | 28.5736 | 16.4596 | 56.8688
KEAD4 R3 | 400 | 75.5644 | 26.8372 | 15.4398 | 53.3933 | 66.3823 | 25.5661 | 13.1199 | 49.2757
KEAR2 M1 | 275 | 69.7267 | 24.4926 | 16.7007 | 51.3384 | 76.5686 | 28.7498 | 17.9288 | 58.5871
KEAR2 M2 | 275 | 69.7267 | 24.4926 | 16.7007 | 51.3384 | 76.5686 | 28.7498 | 17.9288 | 58.5871
KEAR2 R1 | 275 | 69.7267 | 24.4926 | 16.7007 | 51.3384 | 76.5686 | 28.7498 | 17.9288 | 58.5871
KEAR2 R2 | 275 | 69.7267 | 24.4926 | 16.7007 | 51.3384 | 76.5686 | 28.7498 | 17.9288 | 58.5871
KEMS4 M1 | 400 | 96.0288 | 31.3399 | 17.8245 | 62.1458 | 88.2966 | 33.1514 | 15.1004 | 61.9836
KEMS4 M2 | 400 | 96.0288 | 31.3399 | 17.8245 | 62.1458 | 88.2966 | 33.1514 | 15.1004 | 61.9836
KEMS4 R1 | 400 | 96.0288 | 31.3399 | 17.8245 | 62.1458 | 88.2966 | 33.1514 | 15.1004 | 61.9836
KEMS4 R2 | 400 | 96.0288 | 31.3399 | 17.8245 | 62.1458 | 88.2966 | 33.1514 | 15.1004 | 61.9836
KENG4 M1 | 400 | 93.7268 | 29.6395 | 19.6838 | 61.6004 | 111.1135 | 40.0563 | 22.2677 | 78.9158
KENG4 M2 | 400 | 93.7268 | 29.6395 | 19.6838 | 61.6004 | 111.1135 | 40.0563 | 22.2677 | 78.9158
KENG4 R1 | 400 | 93.7268 | 29.6395 | 19.6838 | 61.6004 | 111.1135 | 40.0563 | 22.2677 | 78.9158
KENG4 R2 | 400 | 93.7268 | 29.6395 | 19.6838 | 61.6004 | 111.1135 | 40.0563 | 22.2677 | 78.9158
KIBY2 M1 | 275 | 42.9861 | 15.1976 | 10.2347 | 31.7274 | 46.4141 | 17.8918 | 9.9425 | 35.2454
KIBY2 M2 | 275 | 42.9861 | 15.1976 | 10.2347 | 31.7274 | 46.4141 | 17.8918 | 9.9425 | 35.2454
KIBY2 R1 | 275 | 50.9478 | 18.0147 | 12.7077 | 38.1842 | 49.5417 | 18.7325 | 11.1001 | 37.5918
KIBY2 R2 | 275 | 50.9478 | 18.0147 | 12.7077 | 38.1842 | 49.5417 | 18.7325 | 11.1001 | 37.5918
KILL4 M1 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 M2 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 M3 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 M4 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 M5 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 R1/2 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 R3/4 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL4 R5 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL41 M9 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KILL41 R9 | 400 | 77.3008 | 27.2113 | 25.8379 | 64.3205 | 80.1124 | 29.9503 | 25.7611 | 68.1172
KINO1 M1 | 132 | 29.6303 | 10.3613 | 10.2087 | 24.8619 | 35.9544 | 13.2714 | 12.3237 | 31.0922
KINO1 M2 | 132 | 29.6303 | 10.3613 | 10.2087 | 24.8619 | 35.9544 | 13.2714 | 12.3237 | 31.0922
KINO1 R1 | 132 | 29.6303 | 10.3613 | 10.2087 | 24.8619 | 35.9544 | 13.2714 | 12.3237 | 31.0922
KINO1 R2 | 132 | 29.6303 | 10.3613 | 10.2087 | 24.8619 | 35.9544 | 13.2714 | 12.3237 | 31.0922
KINO1A | 132 | 29.2648 | 10.1222 | 5.9198 | 20.2347 | 35.419 | 13.0929 | 7.0607 | 25.5768
KINO1B | 132 | 24.2432 | 8.9752 | 1.383 | 14.0759 | 25.7635 | 10.405 | 0.77997 | 15.4949
KINO4 M1 | 400 | 92.8114 | 31.9438 | 25.8739 | 71.0493 | 93.6387 | 35.2529 | 26.0839 | 75.939
KINO4 M2 | 400 | 92.8114 | 31.9438 | 25.8739 | 71.0493 | 93.6387 | 35.2529 | 26.0839 | 75.939
KINO4 M3 | 400 | 92.8114 | 31.9438 | 25.8739 | 71.0493 | 93.6387 | 35.2529 | 26.0839 | 75.939
KINO4 M4 | 400 | 92.8114 | 31.9438 | 25.8739 | 71.0493 | 93.6387 | 35.2529 | 26.0839 | 75.939
KINO4 R1/2 | 400 | 92.8114 | 31.9438 | 25.8739 | 71.0493 | 93.6387 | 35.2529 | 26.0839 | 75.939
KINO4 R3/4 | 400 | 92.8114 | 31.9438 | 25.8739 | 71.0493 | 93.6387 | 35.2529 | 26.0839 | 75.939
KIRK2 MC1 | 275 | 51.0858 | 18.28 | 10.943 | 36.7949 | 52.8126 | 20.2372 | 11.9272 | 40.5469
KIRK2 MC2 | 275 | 51.0858 | 18.28 | 10.943 | 36.7949 | 52.8126 | 20.2372 | 11.9272 | 40.5469
KIRK2 MC3 | 275 | 51.0858 | 18.28 | 10.943 | 36.7949 | 52.8126 | 20.2372 | 11.9272 | 40.5469
KIRK2 MC4 | 275 | 51.0858 | 18.28 | 10.943 | 36.7949 | 52.8126 | 20.2372 | 11.9272 | 40.5469
KIRK2A | 275 | 50.1051 | 17.3721 | 5.4731 | 30.0409 | 49.0099 | 19.0194 | 7.0698 | 33.9673
KITW2 MC1 | 275 | 58.5051 | 20.876 | 10.955 | 40.4781 | 58.2879 | 22.5994 | 9.9159 | 41.8763
KITW2 MC2 | 275 | 58.5051 | 20.876 | 10.955 | 40.4781 | 58.2879 | 22.5994 | 9.9159 | 41.8763
KITW2 MC3 | 275 | 58.5051 | 20.876 | 10.955 | 40.4781 | 58.2879 | 22.5994 | 9.9159 | 41.8763
KITW2 MC4 | 275 | 58.5051 | 20.876 | 10.955 | 40.4781 | 58.2879 | 22.5994 | 9.9159 | 41.8763
KNAR2 MC1 | 275 | 28.0296 | 11.1432 | 2.3684 | 18.1273 | 26.2215 | 10.7903 | 3.4121 | 18.672
KNAR2 MC2 | 275 | 28.0296 | 11.1432 | 2.3684 | 18.1273 | 26.2215 | 10.7903 | 3.4121 | 18.672
LACK2 M1 | 275 | 54.3427 | 18.6231 | 13.6602 | 39.9973 | 59.9341 | 22.0115 | 15.8411 | 46.97
LACK2 M2 | 275 | 54.3427 | 18.6231 | 13.6602 | 39.9973 | 59.9341 | 22.0115 | 15.8411 | 46.97
LACK2 R1 | 275 | 54.3427 | 18.6231 | 13.6602 | 39.9973 | 59.9341 | 22.0115 | 15.8411 | 46.97
LACK2 R2 | 275 | 54.3427 | 18.6231 | 13.6602 | 39.9973 | 59.9341 | 22.0115 | 15.8411 | 46.97
LACK4 M1 | 400 | 58.0209 | 20.9672 | 17.5821 | 47.2342 | 57.0182 | 21.6129 | 17.6421 | 48.2074
LACK4 M2 | 400 | 58.0209 | 20.9672 | 17.5821 | 47.2342 | 57.0182 | 21.6129 | 17.6421 | 48.2074
LACK4 R1 | 400 | 58.0209 | 20.9672 | 17.5821 | 47.2342 | 57.0182 | 21.6129 | 17.6421 | 48.2074
LACK4 R2 | 400 | 58.0209 | 20.9672 | 17.5821 | 47.2342 | 57.0182 | 21.6129 | 17.6421 | 48.2074
LAGA4 M1 | 400 | 29.2653 | 10.746 | 4.3482 | 19.5454 | 34.2511 | 13.1891 | 6.0226 | 24.6747
LAGA4 M2 | 400 | 29.2653 | 10.746 | 4.3482 | 19.5454 | 34.2511 | 13.1891 | 6.0226 | 24.6747
LAGA4 R1 | 400 | 29.2653 | 10.746 | 4.3482 | 19.5454 | 34.2511 | 13.1891 | 6.0226 | 24.6747
LAGA4 R2 | 400 | 29.2653 | 10.746 | 4.3482 | 19.5454 | 34.2511 | 13.1891 | 6.0226 | 24.6747
LALE2 MC1 | 275 | 55.8398 | 19.3625 | 14.1744 | 41.5571 | 60.7174 | 23.3131 | 14.1968 | 47.1665
LALE2 MC2 | 275 | 55.8398 | 19.3625 | 14.1744 | 41.5571 | 60.7174 | 23.3131 | 14.1968 | 47.1665
LALE2 MC3 | 275 | 55.8398 | 19.3625 | 14.1744 | 41.5571 | 60.7174 | 23.3131 | 14.1968 | 47.1665
LALE2 MC4 | 275 | 55.8398 | 19.3625 | 14.1744 | 41.5571 | 60.7174 | 23.3131 | 14.1968 | 47.1665
LAND4 MC1 | 400 | 25.7237 | 9.5381 | 3.7752 | 17.264 | 27.8751 | 10.8987 | 4.2251 | 19.6382
LAND4 MC2 | 400 | 25.7237 | 9.5381 | 3.7752 | 17.264 | 27.8751 | 10.8987 | 4.2251 | 19.6382
LEGA4 M1 | 400 | 71.3949 | 25.1112 | 14.3619 | 49.8746 | 61.3935 | 23.9549 | 10.777 | 44.6544
LEGA4 M2 | 400 | 71.3949 | 25.1112 | 14.3619 | 49.8746 | 61.3935 | 23.9549 | 10.777 | 44.6544
LEGA4 R1 | 400 | 71.3949 | 25.1112 | 14.3619 | 49.8746 | 61.3935 | 23.9549 | 10.777 | 44.6544
LEGA4 R2 | 400 | 71.3949 | 25.1112 | 14.3619 | 49.8746 | 61.3935 | 23.9549 | 10.777 | 44.6544
LEIS1 M1 | 132 | 52.9583 | 18.9449 | 18.9133 | 45.7054 | 61.5701 | 22.3953 | 21.8324 | 53.5041
LEIS1 M2 | 132 | 52.9583 | 18.9449 | 18.9133 | 45.7054 | 61.5701 | 22.3953 | 21.8324 | 53.5041
LEIS1 R1 | 132 | 52.9583 | 18.9449 | 18.9133 | 45.7054 | 61.5701 | 22.3953 | 21.8324 | 53.5041
LEIS1 R2 | 132 | 52.9583 | 18.9449 | 18.9133 | 45.7054 | 61.5701 | 22.3953 | 21.8324 | 53.5041
LEMR1 M1 | 132 | 50.1574 | 17.2112 | 13.5582 | 37.8986 | 61.7633 | 22.4946 | 15.9109 | 47.7231
LEMR1 M2 | 132 | 50.1574 | 17.2112 | 13.5582 | 37.8986 | 61.7633 | 22.4946 | 15.9109 | 47.7231
LEMR1 R1 | 132 | 50.1574 | 17.2112 | 13.5582 | 37.8986 | 61.7633 | 22.4946 | 15.9109 | 47.7231
LEMR1 R2 | 132 | 50.1574 | 17.2112 | 13.5582 | 37.8986 | 61.7633 | 22.4946 | 15.9109 | 47.7231
LISD2 M1 | 275 | 41.5242 | 14.6836 | 9.7438 | 30.5096 | 45.9587 | 17.4909 | 10.367 | 35.1029
LISD2 M2 | 275 | 41.5242 | 14.6836 | 9.7438 | 30.5096 | 45.9587 | 17.4909 | 10.367 | 35.1029
LISD2 R1 | 275 | 41.5242 | 14.6836 | 9.7438 | 30.5096 | 45.9587 | 17.4909 | 10.367 | 35.1029
LISD2 R2 | 275 | 41.5242 | 14.6836 | 9.7438 | 30.5096 | 45.9587 | 17.4909 | 10.367 | 35.1029
LITT1 M3 | 132 | 41.5855 | 14.3329 | 12.7023 | 32.9721 | 50.1679 | 18.0338 | 14.6944 | 40.1981
LITT1 M4 | 132 | 41.5855 | 14.3329 | 12.7023 | 32.9721 | 50.1679 | 18.0338 | 14.6944 | 40.1981
LITT1 R3 | 132 | 41.5855 | 14.3329 | 12.7023 | 32.9721 | 50.1679 | 18.0338 | 14.6944 | 40.1981
LITT1 R4 | 132 | 41.5855 | 14.3329 | 12.7023 | 32.9721 | 50.1679 | 18.0338 | 14.6944 | 40.1981
LITT4 M1 | 400 | 98.9132 | 31.8377 | 18.7121 | 63.7373 | 96.4529 | 35.9456 | 17.82 | 68.6548
LITT4 M2 | 400 | 98.9132 | 31.8377 | 18.7121 | 63.7373 | 96.4529 | 35.9456 | 17.82 | 68.6548
LITT4 M3 | 400 | 98.9132 | 31.8377 | 18.7121 | 63.7373 | 96.4529 | 35.9456 | 17.82 | 68.6548
LITT4 R1 | 400 | 98.9132 | 31.8377 | 18.7121 | 63.7373 | 96.4529 | 35.9456 | 17.82 | 68.6548
LITT4 R2 | 400 | 98.9132 | 31.8377 | 18.7121 | 63.7373 | 96.4529 | 35.9456 | 17.82 | 68.6548
LITT4 R3 | 400 | 98.9132 | 31.8377 | 18.7121 | 63.7373 | 96.4529 | 35.9456 | 17.82 | 68.6548
LOFI4A | 400 | 80.1463 | 25.1801 | 5.7652 | 41.3753 | 71.064 | 26.6923 | 3.5762 | 41.3248
LOFI4A_KEMS | 400 | 80.1463 | 25.1801 | 5.7652 | 41.3753 | 71.064 | 26.6923 | 3.5762 | 41.3248
LOFI4A_LITT | 400 | 80.1463 | 25.1801 | 5.7652 | 41.3753 | 71.064 | 26.6923 | 3.5762 | 41.3248
LOFI4A_ROWD | 400 | 80.1463 | 25.1801 | 5.7652 | 41.3753 | 71.064 | 26.6923 | 3.5762 | 41.3248
LOFI4B | 400 | 79.2864 | 25.0028 | 5.6506 | 41.0099 | 71.6845 | 26.9313 | 3.5803 | 41.667
LOFI4B_KEMS | 400 | 79.2864 | 25.0028 | 5.6506 | 41.0099 | 71.6845 | 26.9313 | 3.5803 | 41.667
LOFI4B_LITT | 400 | 79.2864 | 25.0028 | 5.6506 | 41.0099 | 71.6845 | 26.9313 | 3.5803 | 41.667
LOFI4B_ROWD | 400 | 79.2864 | 25.0028 | 5.6506 | 41.0099 | 71.6845 | 26.9313 | 3.5803 | 41.667
LONO4B | 400 | 63.0505 | 22.0412 | 12.004 | 43.175 | 52.5631 | 20.4175 | 7.9651 | 36.8398
LOVE4 M1 | 400 | 74.9322 | 25.5969 | 12.7921 | 48.9915 | 71.2618 | 27.1157 | 12.4772 | 50.8246
LOVE4 M2 | 400 | 74.9322 | 25.5969 | 12.7921 | 48.9915 | 71.2618 | 27.1157 | 12.4772 | 50.8246
LOVE4 R1 | 400 | 74.9322 | 25.5969 | 12.7921 | 48.9915 | 71.2618 | 27.1157 | 12.4772 | 50.8246
LOVE4 R2 | 400 | 74.9322 | 25.5969 | 12.7921 | 48.9915 | 71.2618 | 27.1157 | 12.4772 | 50.8246
MACC2 MC1 | 275 | 52.4922 | 19.021 | 12.1401 | 39.0398 | 50.5675 | 19.4115 | 10.9355 | 38.3875
MACC2 MC2 | 275 | 52.4922 | 19.021 | 12.1401 | 39.0398 | 50.5675 | 19.4115 | 10.9355 | 38.3875
MACC4 MC1 | 400 | 73.3678 | 26.9516 | 19.6008 | 57.7161 | 60.5885 | 24.0337 | 14.6599 | 48.6487
MACC4 MC2 | 400 | 73.3678 | 26.9516 | 19.6008 | 57.7161 | 60.5885 | 24.0337 | 14.6599 | 48.6487
MACC4 MC3 | 400 | 73.3678 | 26.9516 | 19.6008 | 57.7161 | 60.5885 | 24.0337 | 14.6599 | 48.6487
MACC4 MC4 | 400 | 73.3678 | 26.9516 | 19.6008 | 57.7161 | 60.5885 | 24.0337 | 14.6599 | 48.6487
MAGA2 MC1 | 275 | 40.4801 | 14.7903 | 7.4055 | 28.3221 | 38.779 | 15.2714 | 6.5523 | 28.1493
MAGA2 MC2 | 275 | 40.4801 | 14.7903 | 7.4055 | 28.3221 | 38.779 | 15.2714 | 6.5523 | 28.1493
MANN4 M5 | 400 | 44.0982 | 15.5812 | 7.8532 | 29.8883 | 44.2617 | 16.7799 | 8.8734 | 32.6038
MANN4 MC1 | 400 | 44.0982 | 15.5812 | 7.8532 | 29.8883 | 44.2617 | 16.7799 | 8.8734 | 32.6038
MANN4 MC2 | 400 | 44.0982 | 15.5812 | 7.8532 | 29.8883 | 44.2617 | 16.7799 | 8.8734 | 32.6038
MANN4 MC3 | 400 | 44.0982 | 15.5812 | 7.8532 | 29.8883 | 44.2617 | 16.7799 | 8.8734 | 32.6038
MANN4 MC4 | 400 | 44.0982 | 15.5812 | 7.8532 | 29.8883 | 44.2617 | 16.7799 | 8.8734 | 32.6038
MANN4 R5 | 400 | 44.0982 | 15.5812 | 7.8532 | 29.8883 | 44.2617 | 16.7799 | 8.8734 | 32.6038
MAWO4 M | 400 | 49.6639 | 17.4347 | 8.837 | 33.4934 | 51.2353 | 19.2728 | 10.7185 | 37.9744
MAWO4 R | 400 | 49.6639 | 17.4347 | 8.837 | 33.4934 | 51.2353 | 19.2728 | 10.7185 | 37.9744
MEDW4 Term500 | 400 | 85.7967 | 28.4163 | 15.2212 | 55.4079 | 84.4092 | 31.3999 | 16.2965 | 60.7027
MELK1 M1 | 132 | 43.7239 | 15.2046 | 14.393 | 35.8955 | 53.824 | 19.736 | 16.9002 | 44.8111
MELK1 M2 | 132 | 43.7239 | 15.2046 | 14.393 | 35.8955 | 53.824 | 19.736 | 16.9002 | 44.8111
MELK1 R1 | 132 | 43.7239 | 15.2046 | 14.393 | 35.8955 | 53.824 | 19.736 | 16.9002 | 44.8111
MELK1 R2 | 132 | 43.7239 | 15.2046 | 14.393 | 35.8955 | 53.824 | 19.736 | 16.9002 | 44.8111
MELK4 M1 | 400 | 75.7989 | 26.617 | 11.731 | 49.3731 | 71.1765 | 27.6303 | 10.8662 | 49.9413
MELK4 M2 | 400 | 75.7989 | 26.617 | 11.731 | 49.3731 | 71.1765 | 27.6303 | 10.8662 | 49.9413
MELK4 M3 | 400 | 75.7989 | 26.617 | 11.731 | 49.3731 | 71.1765 | 27.6303 | 10.8662 | 49.9413
MELK4 R1 | 400 | 75.7989 | 26.617 | 11.731 | 49.3731 | 71.1765 | 27.6303 | 10.8662 | 49.9413
MELK4 R2 | 400 | 75.7989 | 26.617 | 11.731 | 49.3731 | 71.1765 | 27.6303 | 10.8662 | 49.9413
MELK4 R3 | 400 | 75.7989 | 26.617 | 11.731 | 49.3731 | 71.1765 | 27.6303 | 10.8662 | 49.9413
MIDL41 M1 | 400 | 88.2457 | 29.915 | 24.9269 | 67.2331 | 92.1546 | 33.7829 | 25.6792 | 73.4554
MIDL41 R1 | 400 | 88.2457 | 29.915 | 24.9269 | 67.2331 | 92.1546 | 33.7829 | 25.6792 | 73.4554
MILH1 M1 | 132 | 39.5302 | 14.3246 | 8.7732 | 29.0312 | 45.9098 | 18.544 | 8.9074 | 35.1326
MILH1 M2 | 132 | 39.5302 | 14.3246 | 8.7732 | 29.0312 | 45.9098 | 18.544 | 8.9074 | 35.1326
MILH1 R1 | 132 | 39.5222 | 14.322 | 8.7735 | 29.0279 | 45.9006 | 18.5403 | 8.9237 | 35.1437
MILH1 R2 | 132 | 39.5222 | 14.322 | 8.7735 | 29.0279 | 45.9006 | 18.5403 | 8.9237 | 35.1437
MITY4 MC1 | 400 | 58.135 | 21.7366 | 13.9732 | 44.7134 | 48.6475 | 19.4939 | 11.0749 | 38.6435
MITY4 MC2 | 400 | 58.135 | 21.7366 | 13.9732 | 44.7134 | 48.6475 | 19.4939 | 11.0749 | 38.6435
MITY4 MC3 | 400 | 58.135 | 21.7366 | 13.9732 | 44.7134 | 48.6475 | 19.4939 | 11.0749 | 38.6435
MITY4 MC4 | 400 | 58.135 | 21.7366 | 13.9732 | 44.7134 | 48.6475 | 19.4939 | 11.0749 | 38.6435
MONF2 M1 | 275 | 60.2607 | 21.4618 | 14.9009 | 45.2525 | 62.4777 | 23.6656 | 14.3673 | 47.8354
MONF2 M2 | 275 | 60.2607 | 21.4618 | 14.9009 | 45.2525 | 62.4777 | 23.6656 | 14.3673 | 47.8354
MONF2 R1 | 275 | 52.3007 | 18.7184 | 15.3908 | 41.8626 | 56.3786 | 21.1264 | 15.5341 | 45.4113
MONF2 R2 | 275 | 52.3007 | 18.7184 | 15.3908 | 41.8626 | 56.3786 | 21.1264 | 15.5341 | 45.4113
MONF4 MC2 | 400 | 66.6426 | 23.5932 | 14.1481 | 47.514 | 62.8607 | 23.9003 | 13.0961 | 46.8962
MONF4 MC3 | 400 | 66.6426 | 23.5932 | 14.1481 | 47.514 | 62.8607 | 23.9003 | 13.0961 | 46.8962
NECH2 MC1 | 275 | 57.9224 | 20.4551 | 14.08 | 43.0079 | 60.225 | 22.9932 | 13.0077 | 45.5249
NECH2 MC2 | 275 | 57.9224 | 20.4551 | 14.08 | 43.0079 | 60.225 | 22.9932 | 13.0077 | 45.5249
NECH2 MC3 | 275 | 57.9224 | 20.4551 | 14.08 | 43.0079 | 60.225 | 22.9932 | 13.0077 | 45.5249
NECH2 MC4 | 275 | 57.9224 | 20.4551 | 14.08 | 43.0079 | 60.225 | 22.9932 | 13.0077 | 45.5249
NECT4 M1 | 400 | 60.4232 | 21.5852 | 13.004 | 43.5301 | 42.0459 | 16.9023 | 5.4147 | 29.3181
NECT4 R1 | 400 | 60.4232 | 21.5852 | 13.004 | 43.5301 | 42.0459 | 16.9023 | 5.4147 | 29.3181
NEEP2 M1 | 275 | 43.9595 | 16.16 | 9.3654 | 32.2191 | 44.9323 | 17.8912 | 9.482 | 34.7841
NEEP2 M2 | 275 | 43.9595 | 16.16 | 9.3654 | 32.2191 | 44.9323 | 17.8912 | 9.482 | 34.7841
NEEP2 R1/R2 | 275 | 43.9595 | 16.16 | 9.3654 | 32.2191 | 44.9323 | 17.8912 | 9.482 | 34.7841
NEWX21 M5 | 275 | 67.0706 | 22.6229 | 15.6082 | 47.6018 | 72.9123 | 28.4366 | 14.6888 | 54.9043
NEWX21 M6 | 275 | 67.0706 | 22.6229 | 15.6082 | 47.6018 | 72.9123 | 28.4366 | 14.6888 | 54.9043
NEWX21 R5 | 275 | 67.0706 | 22.6229 | 15.6082 | 47.6018 | 72.9123 | 28.4366 | 14.6888 | 54.9043
NEWX21 R6 | 275 | 67.0706 | 22.6229 | 15.6082 | 47.6018 | 72.9123 | 28.4366 | 14.6888 | 54.9043
NFLE4 M1 | 400 | 84.9063 | 27.907 | 15.6451 | 55.1116 | 74.191 | 28.3046 | 12.1138 | 52.1425
NFLE4 M2 | 400 | 84.9063 | 27.907 | 15.6451 | 55.1116 | 74.191 | 28.3046 | 12.1138 | 52.1425
NFLE4 R1 | 400 | 84.9063 | 27.907 | 15.6451 | 55.1116 | 74.191 | 28.3046 | 12.1138 | 52.1425
NFLE4 R2 | 400 | 84.9063 | 27.907 | 15.6451 | 55.1116 | 74.191 | 28.3046 | 12.1138 | 52.1425
NHYD2A | 275 | 43.722 | 15.9707 | 2.3695 | 24.9555 | 38.2369 | 17.78 | 0.43418 | 25.5789
NHYD2B | 275 | 44.6548 | 16.1705 | 2.1293 | 24.9979 | 38.825 | 17.5678 | 1.0022 | 25.8468
NHYD2C | 275 | 44.6548 | 16.1705 | 2.1293 | 24.9979 | 38.825 | 17.5678 | 1.0022 | 25.8468
NINF4 M1 | 400 | 54.4964 | 19.2074 | 10.2049 | 37.3683 | 49.79 | 19.0485 | 9.9141 | 36.8527
NINF4 M2 | 400 | 54.4964 | 19.2074 | 10.2049 | 37.3683 | 49.79 | 19.0485 | 9.9141 | 36.8527
NINF4 R1 | 400 | 54.4964 | 19.2074 | 10.2049 | 37.3683 | 49.79 | 19.0485 | 9.9141 | 36.8527
NINF4 R2 | 400 | 54.4964 | 19.2074 | 10.2049 | 37.3683 | 49.79 | 19.0485 | 9.9141 | 36.8527
NORL2A | 275 | 45.6702 | 16.3587 | 3.7448 | 26.8795 | 46.2376 | 18.4723 | 2.2425 | 28.3663
NORL2B | 275 | 44.0302 | 15.956 | 2.3786 | 24.9439 | 45.1546 | 18.5999 | 1.6746 | 27.9789
NORM4 M1 | 400 | 59.4606 | 21.3499 | 12.3004 | 42.4937 | 46.6792 | 18.2917 | 9.4331 | 35.3014
NORM4 M2 | 400 | 59.4606 | 21.3499 | 12.3004 | 42.4937 | 46.6792 | 18.2917 | 9.4331 | 35.3014
NORM4 R1 | 400 | 59.4606 | 21.3499 | 12.3004 | 42.4937 | 46.6792 | 18.2917 | 9.4331 | 35.3014
NORM4 R2 | 400 | 59.4606 | 21.3499 | 12.3004 | 42.4937 | 46.6792 | 18.2917 | 9.4331 | 35.3014
NORT2 M1 | 275 | 79.9898 | 27.1323 | 21.6368 | 60.0077 | 81.0665 | 30.2197 | 18.5668 | 61.3038
NORT2 M2 | 275 | 79.9898 | 27.1323 | 21.6368 | 60.0077 | 81.0665 | 30.2197 | 18.5668 | 61.3038
NORT2 R1 | 275 | 79.9898 | 27.1323 | 21.6368 | 60.0077 | 81.0665 | 30.2197 | 18.5668 | 61.3038
NORT2 R2 | 275 | 79.9898 | 27.1323 | 21.6368 | 60.0077 | 81.0665 | 30.2197 | 18.5668 | 61.3038
NORT4 M1 | 400 | 80.7096 | 28.3122 | 25.6698 | 65.7093 | 70.7663 | 26.9873 | 20.3496 | 58.5153
NORT4 M2 | 400 | 80.7096 | 28.3122 | 25.6698 | 65.7093 | 70.7663 | 26.9873 | 20.3496 | 58.5153
NORT4 R1 | 400 | 80.7096 | 28.3122 | 25.6698 | 65.7093 | 70.7663 | 26.9873 | 20.3496 | 58.5153
NORT4 R2 | 400 | 80.7096 | 28.3122 | 25.6698 | 65.7093 | 70.7663 | 26.9873 | 20.3496 | 58.5153
NURS4 MC1 | 400 | 48.9242 | 16.8552 | 5.5761 | 29.4129 | 49.568 | 18.5754 | 6.5125 | 32.7821
NURS4 MC2 | 400 | 48.9242 | 16.8552 | 5.5761 | 29.4129 | 49.568 | 18.5754 | 6.5125 | 32.7821
NURS4A | 400 | 44.2661 | 15.7106 | 8.1941 | 30.4122 | 43.9356 | 16.6429 | 8.9455 | 32.4822
OCKH1 M1 | 132 | 24.4044 | 8.6866 | 8.2877 | 20.5724 | 32.9034 | 12.0213 | 10.9905 | 27.9912
OCKH1 M2 | 132 | 24.4044 | 8.6866 | 8.2877 | 20.5724 | 32.9034 | 12.0213 | 10.9905 | 27.9912
OCKH1 R1 | 132 | 24.4044 | 8.6866 | 8.2877 | 20.5724 | 32.9034 | 12.0213 | 10.9905 | 27.9912
OCKH1 R2 | 132 | 24.4044 | 8.6866 | 8.2877 | 20.5724 | 32.9034 | 12.0213 | 10.9905 | 27.9912
OCKH2 MC1 | 275 | 52.7019 | 18.9421 | 9.802 | 36.5902 | 55.4293 | 21.4834 | 10.289 | 40.6711
OCKH2 MC2 | 275 | 52.7019 | 18.9421 | 9.802 | 36.5902 | 55.4293 | 21.4834 | 10.289 | 40.6711
OCKH2 MC3 | 275 | 52.7019 | 18.9421 | 9.802 | 36.5902 | 55.4293 | 21.4834 | 10.289 | 40.6711
OCKH2 MC4 | 275 | 52.7019 | 18.9421 | 9.802 | 36.5902 | 55.4293 | 21.4834 | 10.289 | 40.6711
OCKH2A | 275 | 46.6844 | 16.4055 | 3.8865 | 27.0873 | 47.4051 | 18.1579 | 4.4553 | 30.1345
OFFE2 MC1 | 275 | 66.9532 | 23.3766 | 13.8264 | 46.8859 | 58.7142 | 23.059 | 8.5707 | 41.181
OFFE2 MC2 | 275 | 66.9532 | 23.3766 | 13.8264 | 46.8859 | 58.7142 | 23.059 | 8.5707 | 41.181
OLDB2 MC1 | 275 | 50.6353 | 18.3064 | 9.8243 | 35.7135 | 52.804 | 20.318 | 10.2365 | 38.9704
OLDB2 MC2 | 275 | 50.6353 | 18.3064 | 9.8243 | 35.7135 | 52.804 | 20.318 | 10.2365 | 38.9704
OLDS1 M2 | 132 | 32.2293 | 11.6583 | 3.7501 | 20.2375 | 29.365 | 11.7271 | 1.7413 | 18.3258
OSBA4 MC1 | 400 | 49.688 | 17.8931 | 10.8866 | 36.1913 | 46.6256 | 17.6801 | 10.9222 | 35.9257
OSBA4 MC2 | 400 | 49.688 | 17.8931 | 10.8866 | 36.1913 | 46.6256 | 17.6801 | 10.9222 | 35.9257
OSBA4 MC3/4 | 400 | 45.7628 | 16.595 | 10.2575 | 33.7264 | 38.1798 | 14.6733 | 8.196 | 28.9472
PADI1 M1 | 132 | 31.6326 | 11.0758 | 10.9555 | 26.619 | 39.1214 | 14.2926 | 13.2166 | 33.4294
PADI1 M2 | 132 | 31.6326 | 11.0758 | 10.9555 | 26.619 | 39.1214 | 14.2926 | 13.2166 | 33.4294
PADI1 R1 | 132 | 31.6326 | 11.0758 | 10.9555 | 26.619 | 39.1214 | 14.2926 | 13.2166 | 33.4294
PADI1 R2 | 132 | 31.6326 | 11.0758 | 10.9555 | 26.619 | 39.1214 | 14.2926 | 13.2166 | 33.4294
PADI4 MC1 | 400 | 68.2598 | 24.1932 | 13.9885 | 48.2028 | 54.2096 | 21.2104 | 9.1477 | 39.1438
PADI4 MC2 | 400 | 68.2598 | 24.1932 | 13.9885 | 48.2028 | 54.2096 | 21.2104 | 9.1477 | 39.1438
PADI4 MC3 | 400 | 68.2598 | 24.1932 | 13.9885 | 48.2028 | 54.2096 | 21.2104 | 9.1477 | 39.1438
PADI4 MC4 | 400 | 68.2598 | 24.1932 | 13.9885 | 48.2028 | 54.2096 | 21.2104 | 9.1477 | 39.1438
PELH4 M1 | 400 | 108.622 | 36.3333 | 22.2734 | 73.6565 | 96.9387 | 36.7574 | 17.4885 | 69.4713
PELH4 M2 | 400 | 108.622 | 36.3333 | 22.2734 | 73.6565 | 96.9387 | 36.7574 | 17.4885 | 69.4713
PELH4 R1 | 400 | 108.622 | 36.3333 | 22.2734 | 73.6565 | 96.9387 | 36.7574 | 17.4885 | 69.4713
PELH4 R2 | 400 | 108.622 | 36.3333 | 22.2734 | 73.6565 | 96.9387 | 36.7574 | 17.4885 | 69.4713
PEMB1 M1 | 132 | 27.2625 | 9.9971 | 9.7524 | 23.8904 | 34.6657 | 13.1285 | 12.2093 | 30.7758
PEMB1 M2 | 132 | 27.2625 | 9.9971 | 9.7524 | 23.8904 | 34.6657 | 13.1285 | 12.2093 | 30.7758
PEMB1 R1 | 132 | 27.2625 | 9.9971 | 9.7524 | 23.8904 | 34.6657 | 13.1285 | 12.2093 | 30.7758
PEMB1 R2 | 132 | 27.2625 | 9.9971 | 9.7524 | 23.8904 | 34.6657 | 13.1285 | 12.2093 | 30.7758
PEMB4 M1 | 400 | 29.3707 | 10.5796 | 6.9508 | 21.9127 | 36.3084 | 13.535 | 9.2889 | 28.4303
PEMB4 M2 | 400 | 29.3707 | 10.5796 | 6.9508 | 21.9127 | 36.3084 | 13.535 | 9.2889 | 28.4303
PEMB4 M3 | 400 | 29.3707 | 10.5796 | 6.9508 | 21.9127 | 36.3084 | 13.535 | 9.2889 | 28.4303
PEMB4 M4 | 400 | 29.3707 | 10.5796 | 6.9508 | 21.9127 | 36.3084 | 13.535 | 9.2889 | 28.4303
PEMB4 R1/2 | 400 | 29.3707 | 10.5796 | 6.9508 | 21.9127 | 36.3084 | 13.535 | 9.2889 | 28.4303
PEMB4 R3/4 | 400 | 29.3707 | 10.5796 | 6.9508 | 21.9127 | 36.3084 | 13.535 | 9.2889 | 28.4303
PENN2 MC1 | 275 | 62.497 | 22.2623 | 12.605 | 44.0887 | 66.6342 | 25.376 | 13.6737 | 49.5608
PENN2 MC2 | 275 | 62.497 | 22.2623 | 12.605 | 44.0887 | 66.6342 | 25.376 | 13.6737 | 49.5608
PENN2 MC3 | 275 | 62.497 | 22.2623 | 12.605 | 44.0887 | 66.6342 | 25.376 | 13.6737 | 49.5608
PENN2 MC4 | 275 | 62.497 | 22.2623 | 12.605 | 44.0887 | 66.6342 | 25.376 | 13.6737 | 49.5608
PENT4 M1 | 400 | 51.9425 | 18.2222 | 12.3409 | 38.111 | 58.5447 | 21.8168 | 14.0685 | 44.9222
PENT4 M2 | 400 | 51.9425 | 18.2222 | 12.3409 | 38.111 | 58.5447 | 21.8168 | 14.0685 | 44.9222
PENT4 R1 | 400 | 51.9425 | 18.2222 | 12.3409 | 38.111 | 58.5447 | 21.8168 | 14.0685 | 44.9222
PENT4 R2 | 400 | 51.9425 | 18.2222 | 12.3409 | 38.111 | 58.5447 | 21.8168 | 14.0685 | 44.9222
PEWO2A | 275 | 62.7186 | 21.9961 | 19.0618 | 50.169 | 65.9404 | 24.3796 | 18.8811 | 53.3591
PEWO2B | 275 | 60.3021 | 21.4814 | 22.3772 | 52.7564 | 64.0313 | 23.7723 | 23.0588 | 56.6779
PEWO4 M1 | 400 | 91.0592 | 32.2058 | 29.0695 | 74.6155 | 86.3773 | 32.9681 | 25.5695 | 72.1935
PEWO4 M2 | 400 | 91.0592 | 32.2058 | 29.0695 | 74.6155 | 86.3773 | 32.9681 | 25.5695 | 72.1935
PEWO4 M3 | 400 | 91.0592 | 32.2058 | 29.0695 | 74.6155 | 86.3773 | 32.9681 | 25.5695 | 72.1935
PEWO4 M4 | 400 | 91.0592 | 32.2058 | 29.0695 | 74.6155 | 86.3773 | 32.9681 | 25.5695 | 72.1935
PEWO4 R1/2 | 400 | 91.0592 | 32.2058 | 29.0695 | 74.6155 | 86.3773 | 32.9681 | 25.5695 | 72.1935
PEWO4 R3/4 | 400 | 91.0592 | 32.2058 | 29.0695 | 74.6155 | 86.3773 | 32.9681 | 25.5695 | 72.1935
PITS2 MC1 | 275 | 50.0053 | 18.0264 | 5.323 | 30.8161 | 53.1498 | 21.1821 | 5.3086 | 35.2646
PITS2 MC2 | 275 | 50.0053 | 18.0264 | 5.323 | 30.8161 | 53.1498 | 21.1821 | 5.3086 | 35.2646
PITS2 MC3 | 275 | 50.0053 | 18.0264 | 5.323 | 30.8161 | 53.1498 | 21.1821 | 5.3086 | 35.2646
PITS2 MC4 | 275 | 50.0053 | 18.0264 | 5.323 | 30.8161 | 53.1498 | 21.1821 | 5.3086 | 35.2646
POPP2 MC1 | 275 | 26.338 | 10.4035 | 2.7485 | 17.4612 | 22.6418 | 9.3011 | 3.0158 | 16.1696
POPP2 MC2 | 275 | 26.338 | 10.4035 | 2.7485 | 17.4612 | 22.6418 | 9.3011 | 3.0158 | 16.1696
PUDM4 MC1 | 400 | 83.6949 | 27.0264 | 17.4051 | 55.6263 | 89.4943 | 34.1261 | 15.97 | 64.2316
PUDM4 MC2 | 400 | 83.6949 | 27.0264 | 17.4051 | 55.6263 | 89.4943 | 34.1261 | 15.97 | 64.2316
PYLE2 MC1 | 275 | 43.082 | 15.7485 | 7.4902 | 29.7619 | 41.274 | 16.2384 | 7.1013 | 30.0659
PYLE2 MC2 | 275 | 43.1106 | 15.7583 | 7.4956 | 29.7812 | 41.3041 | 16.2489 | 7.1116 | 30.091
QUER4A | 400 | 77.1694 | 25.8366 | 12.4473 | 48.9858 | 69.1191 | 26.0998 | 5.8907 | 42.8014
QUER4A_HEYS | 400 | 77.1694 | 25.8366 | 12.4473 | 48.9858 | 69.1191 | 26.0998 | 5.8907 | 42.8014
QUER4A_HUTT | 400 | 77.1694 | 25.8366 | 12.4473 | 48.9858 | 69.1191 | 26.0998 | 5.8907 | 42.8014
QUER4A_PEWO | 400 | 77.1694 | 25.8366 | 12.4473 | 48.9858 | 69.1191 | 26.0998 | 5.8907 | 42.8014
QUER4B | 400 | 77.978 | 26.0595 | 12.7509 | 49.6045 | 71.1493 | 26.7523 | 6.5479 | 44.3814
QUER4B_HEYS | 400 | 77.978 | 26.0595 | 12.7509 | 49.6045 | 71.1493 | 26.7523 | 6.5479 | 44.3814
QUER4B_HUTT | 400 | 77.978 | 26.0595 | 12.7509 | 49.6045 | 71.1493 | 26.7523 | 6.5479 | 44.3814
QUER4B_PEWO | 400 | 77.978 | 26.0595 | 12.7509 | 49.6045 | 71.1493 | 26.7523 | 6.5479 | 44.3814
RAIN2 MC1 | 275 | 52.4811 | 18.3481 | 13.7716 | 39.7197 | 54.3848 | 20.3053 | 12.7908 | 41.5068
RAIN2 MC2 | 275 | 52.4811 | 18.3481 | 13.7716 | 39.7197 | 54.3848 | 20.3053 | 12.7908 | 41.5068
RAIN2 MC3 | 275 | 52.4811 | 18.3481 | 13.7716 | 39.7197 | 54.3848 | 20.3053 | 12.7908 | 41.5068
RAIN2 MC4 | 275 | 52.4811 | 18.3481 | 13.7716 | 39.7197 | 54.3848 | 20.3053 | 12.7908 | 41.5068
RASS4 M1 | 400 | 44.0662 | 16.2676 | 12.3947 | 35.4006 | 38.2203 | 14.9575 | 9.8931 | 31.0461
RASS4 M2 | 400 | 44.0662 | 16.2676 | 12.3947 | 35.4006 | 38.2203 | 14.9575 | 9.8931 | 31.0461
RATS1 M1 | 132 | 43.2218 | 15.1353 | 13.681 | 35.0855 | 48.9944 | 18.1051 | 16.3816 | 41.9861
RATS1 M2 | 132 | 43.2218 | 15.1353 | 13.681 | 35.0855 | 48.9944 | 18.1051 | 16.3816 | 41.9861
RATS1 R1 | 132 | 39.7778 | 14.0374 | 12.429 | 32.2808 | 44.932 | 16.7521 | 13.5758 | 37.2668
RATS1 R2 | 132 | 39.7778 | 14.0374 | 12.429 | 32.2808 | 44.932 | 16.7521 | 13.5758 | 37.2668
RATS2A | 275 | 40.9932 | 14.5085 | 8.2254 | 28.7436 | 44.3495 | 15.9689 | 17.161 | 39.7444
RATS4 M1 | 400 | 102.6242 | 35.436 | 17.4065 | 67.5205 | 110.9019 | 41.7601 | 22.4168 | 81.4745
RATS4 M2 | 400 | 102.6242 | 35.436 | 17.4065 | 67.5205 | 110.9019 | 41.7601 | 22.4168 | 81.4745
RATS4 M3 | 400 | 102.6242 | 35.436 | 17.4065 | 67.5205 | 110.9019 | 41.7601 | 22.4168 | 81.4745
RATS4 M4 | 400 | 102.6242 | 35.436 | 17.4065 | 67.5205 | 110.9019 | 41.7601 | 22.4168 | 81.4745
RATS4 R1/2 | 400 | 102.6242 | 35.436 | 17.4065 | 67.5205 | 110.9019 | 41.7601 | 22.4168 | 81.4745
RATS4 R3/4 | 400 | 102.6242 | 35.436 | 17.4065 | 67.5205 | 110.9019 | 41.7601 | 22.4168 | 81.4745
RAYL4 M1 | 400 | 84.335 | 29.7177 | 23.3161 | 65.3432 | 70.8396 | 27.5304 | 18.1683 | 57.1021
RAYL4 M2 | 400 | 84.335 | 29.7177 | 23.3161 | 65.3432 | 70.8396 | 27.5304 | 18.1683 | 57.1021
RAYL4 R1 | 400 | 84.335 | 29.7177 | 23.3161 | 65.3432 | 70.8396 | 27.5304 | 18.1683 | 57.1021
RAYL4 R2 | 400 | 84.335 | 29.7177 | 23.3161 | 65.3432 | 70.8396 | 27.5304 | 18.1683 | 57.1021
REBR2 MC1 | 275 | 21.5666 | 7.7105 | 8.1378 | 19.0421 | 22.6513 | 8.4128 | 8.0482 | 19.9457
REBR2 MC2 | 275 | 69.4007 | 24.7164 | 21.5226 | 56.4768 | 67.9301 | 26.5734 | 17.1328 | 54.7133
REBR2 MC3 | 275 | 69.4007 | 24.7164 | 21.5226 | 56.4768 | 67.9301 | 26.5734 | 17.1328 | 54.7133
REBR2 MC4 | 275 | 21.5666 | 7.7105 | 8.1378 | 19.0421 | 22.6513 | 8.4128 | 8.0482 | 19.9457
RHIG4 M1 | 400 | 41.5848 | 14.9575 | 8.1759 | 29.3289 | 37.7626 | 14.6146 | 6.4194 | 27.0875
RHIG4 R1 | 400 | 41.5848 | 14.9575 | 8.1759 | 29.3289 | 37.7626 | 14.6146 | 6.4194 | 27.0875
RICH41 M1 | 400 | 52.0059 | 18.892 | 8.9834 | 35.7007 | 41.4241 | 16.1583 | 8.6063 | 31.4576
RICH41 R1 | 400 | 52.0059 | 18.892 | 8.9834 | 35.7007 | 41.4241 | 16.1583 | 8.6063 | 31.4576
ROCH2 MC1 | 275 | 67.191 | 23.6541 | 8.6094 | 42.0613 | 65.5735 | 25.1729 | 8.6664 | 44.2663
ROCH2 MC2 | 275 | 67.191 | 23.6541 | 8.6094 | 42.0613 | 65.5735 | 25.1729 | 8.6664 | 44.2663
ROCH2 MC3 | 275 | 67.191 | 23.6541 | 8.6094 | 42.0613 | 65.5735 | 25.1729 | 8.6664 | 44.2663
ROCH2 MC4 | 275 | 67.191 | 23.6541 | 8.6094 | 42.0613 | 65.5735 | 25.1729 | 8.6664 | 44.2663
ROCK1A | 132 | 45.6673 | 15.6839 | 15.5471 | 37.7275 | 48.3521 | 17.4706 | 15.577 | 40.2841
ROCK4 Term900 | 400 | 63.9014 | 22.3105 | 13.9164 | 45.4682 | 66.137 | 24.6853 | 15.5858 | 50.4961
RUGE4 M1 | 400 | 59.2932 | 21.6248 | 8.8794 | 39.4615 | 48.1423 | 19.2534 | 6.5167 | 33.7451
RUGE4 M2 | 400 | 59.2932 | 21.6248 | 8.8794 | 39.4615 | 48.1423 | 19.2534 | 6.5167 | 33.7451
RUGE4 R1 | 400 | 59.2932 | 21.6248 | 8.8794 | 39.4615 | 48.1423 | 19.2534 | 6.5167 | 33.7451
RUGE4 R2 | 400 | 59.2932 | 21.6248 | 8.8794 | 39.4615 | 48.1423 | 19.2534 | 6.5167 | 33.7451
RYEH4 M1 | 400 | 63.4075 | 21.9953 | 14.1512 | 45.2572 | 67.9819 | 25.2067 | 16.4262 | 52.0738
RYEH4 R1 | 400 | 63.4075 | 21.9953 | 14.1512 | 45.2572 | 67.9819 | 25.2067 | 16.4262 | 52.0738
RYHA4 MC1 | 400 | 39.7019 | 14.5875 | 8.0607 | 28.6905 | 27.4195 | 10.8795 | 3.8404 | 19.2263
SAEN2 MC1 | 275 | 47.4049 | 17.2394 | 11.9394 | 36.3196 | 52.8404 | 19.8546 | 13.9031 | 41.9818
SAEN2 MC2 | 275 | 47.4049 | 17.2394 | 11.9394 | 36.3196 | 52.8404 | 19.8546 | 13.9031 | 41.9818
SAES2 M | 275 | 47.4256 | 17.2473 | 11.9443 | 36.3357 | 53.2117 | 19.9609 | 14.2954 | 42.5244
SAES2 R | 275 | 47.4256 | 17.2473 | 11.9443 | 36.3357 | 53.2117 | 19.9609 | 14.2954 | 42.5244
SAFO1 M1 | 132 | 13.4419 | 4.8794 | 4.7399 | 11.6405 | 15.2911 | 5.613 | 5.1599 | 13.0979
SAFO1 M2 | 132 | 13.4419 | 4.8794 | 4.7399 | 11.6405 | 15.2911 | 5.613 | 5.1599 | 13.0979
SAFO1 R1 | 132 | 13.4419 | 4.8794 | 4.7399 | 11.6405 | 15.2911 | 5.613 | 5.1599 | 13.0979
SAFO1 R2 | 132 | 13.4419 | 4.8794 | 4.7399 | 11.6405 | 15.2911 | 5.613 | 5.1599 | 13.0979
SAFO4 M1 | 400 | 33.9081 | 12.7967 | 8.6028 | 26.7001 | 26.8444 | 10.8058 | 6.2646 | 21.5464
SAFO4 M2 | 400 | 33.9081 | 12.7967 | 8.6028 | 26.7001 | 26.8444 | 10.8058 | 6.2646 | 21.5464
SALH2 MC1 | 275 | 72.7953 | 25.0968 | 17.5875 | 53.0797 | 71.9353 | 27.036 | 15.0303 | 53.265
SALH2 MC2 | 275 | 72.7953 | 25.0968 | 17.5875 | 53.0797 | 71.9353 | 27.036 | 15.0303 | 53.265
SEAB4 M1 | 400 | 43.5152 | 15.9916 | 12.0681 | 34.6837 | 50.8859 | 19.3383 | 15.0979 | 42.4464
SEAB4 M2 | 400 | 43.5152 | 15.9916 | 12.0681 | 34.6837 | 50.8859 | 19.3383 | 15.0979 | 42.4464
SEAB4 R1 | 400 | 43.5152 | 15.9916 | 12.0681 | 34.6837 | 50.8859 | 19.3383 | 15.0979 | 42.4464
SEAB4 R2 | 400 | 43.5152 | 15.9916 | 12.0681 | 34.6837 | 50.8859 | 19.3383 | 15.0979 | 42.4464
SELL4 M1 | 400 | 65.4006 | 23.0576 | 11.5876 | 44.1961 | 60.8114 | 23.1609 | 12.4023 | 45.1568
SELL4 M2 | 400 | 65.4006 | 23.0576 | 11.5876 | 44.1961 | 60.8114 | 23.1609 | 12.4023 | 45.1568
SELL4 R1 | 400 | 65.4006 | 23.0576 | 11.5876 | 44.1961 | 60.8114 | 23.1609 | 12.4023 | 45.1568
SELL4 R2 | 400 | 65.4006 | 23.0576 | 11.5876 | 44.1961 | 60.8114 | 23.1609 | 12.4023 | 45.1568
SELL4C | 400 | 65.3571 | 22.1697 | 4.2538 | 35.6066 | 60.7643 | 22.874 | 5.839 | 38.1877
SELL4C | 400 | 65.3571 | 22.1697 | 4.2538 | 35.6066 | 60.7643 | 22.874 | 5.839 | 38.1877
SELL4D | 400 | 65.3569 | 22.1697 | 4.2538 | 35.6065 | 60.7642 | 22.8739 | 5.839 | 38.1876
SELL4D | 400 | 65.3569 | 22.1697 | 4.2538 | 35.6065 | 60.7642 | 22.8739 | 5.839 | 38.1876
SELL4E | 400 | 65.2766 | 22.1465 | 4.2455 | 35.5654 | 60.708 | 22.8559 | 5.8187 | 38.1418
SELL4E | 400 | 65.2766 | 22.1465 | 4.2455 | 35.5654 | 60.708 | 22.8559 | 5.8187 | 38.1418
SELL4F | 400 | 65.2766 | 22.1465 | 4.2455 | 35.5653 | 60.7079 | 22.8559 | 5.8187 | 38.1418
SELL4F | 400 | 65.2766 | 22.1465 | 4.2455 | 35.5653 | 60.7079 | 22.8559 | 5.8187 | 38.1418
SELW4 M3 | 400 | 65.2958 | 23.0245 | 11.5662 | 44.1279 | 60.5193 | 23.0641 | 12.2659 | 44.8835
SELW4 M4 | 400 | 65.2958 | 23.0245 | 11.5662 | 44.1279 | 60.5193 | 23.0641 | 12.2659 | 44.8835
SELW4 R3 | 400 | 65.2958 | 23.0245 | 11.5662 | 44.1279 | 60.5193 | 23.0641 | 12.2659 | 44.8835
SELW4 R4 | 400 | 65.2958 | 23.0245 | 11.5662 | 44.1279 | 60.5193 | 23.0641 | 12.2659 | 44.8835
SGT 5 HV | 400 | 86.9364 | 25.9736 | 8.4742 | 45.2064 | 102.4728 | 36.451 | 7.9911 | 59.5405
SGT6_HV | 400 | 86.8307 | 25.9487 | 8.4638 | 45.1607 | 102.3389 | 36.4132 | 7.9629 | 59.4589
SHBA4 M1 | 400 | 60.6526 | 21.7177 | 20.2396 | 50.953 | 63.3649 | 23.7791 | 20.8197 | 54.4485
SHBA4 M2 | 400 | 60.6526 | 21.7177 | 20.2396 | 50.953 | 63.3649 | 23.7791 | 20.8197 | 54.4485
SHBA4 R1 | 400 | 60.6526 | 21.7177 | 20.2396 | 50.953 | 63.3649 | 23.7791 | 20.8197 | 54.4485
SHBA4 R2 | 400 | 60.6526 | 21.7177 | 20.2396 | 50.953 | 63.3649 | 23.7791 | 20.8197 | 54.4485
SHEC2 MC1 | 275 | 44.7659 | 16.4584 | 8.9353 | 32.211 | 45.6128 | 18.3473 | 6.9837 | 32.9307
SHEC2 MC2 | 275 | 44.7659 | 16.4584 | 8.9353 | 32.211 | 45.6128 | 18.3473 | 6.9837 | 32.9307
SHRE4B | 400 | 51.5054 | 18.7745 | 9.2132 | 35.7643 | 42.4639 | 16.7762 | 6.8049 | 30.5301
SHUR4 M1 | 400 | 40.7548 | 14.7771 | 6.262 | 27.1599 | 35.7579 | 14.1356 | 5.3857 | 25.3764
SHUR4 M2 | 400 | 14.2783 | 5.0415 | 4.8593 | 11.989 | 13.4643 | 4.9392 | 4.3636 | 11.3486
SHUR4 M3 | 400 | 40.7548 | 14.7771 | 6.262 | 27.1599 | 35.7579 | 14.1356 | 5.3857 | 25.3764
SHUR4 M4 | 400 | 14.2783 | 5.0415 | 4.8593 | 11.989 | 13.4643 | 4.9392 | 4.3636 | 11.3486
SHUR4 R1/3 | 400 | 40.7548 | 14.7771 | 6.262 | 27.1599 | 35.7579 | 14.1356 | 5.3857 | 25.3764
SHUR4 R2/4 | 400 | 14.2783 | 5.0415 | 4.8593 | 11.989 | 13.4643 | 4.9392 | 4.3636 | 11.3486
SING4 MC1 | 400 | 77.0524 | 25.6919 | 14.3124 | 50.6463 | 67.3095 | 25.7388 | 10.5762 | 46.9765
SING4 MC2 | 400 | 77.0524 | 25.6919 | 14.3124 | 50.6463 | 67.3095 | 25.7388 | 10.5762 | 46.9765
SIZE4 M1 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 M2 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 M3 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 M4 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 R1 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 R2 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 R3 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SIZE4 R4 | 400 | 65.4485 | 22.8501 | 16.8605 | 49.1755 | 70.3758 | 25.9069 | 19.9923 | 56.6301
SJOW2 MC1 | 275 | 24.6871 | 8.4954 | 9.2901 | 21.3044 | 29.2796 | 10.4555 | 10.8568 | 25.643
SJOW2 MC2 | 275 | 24.6871 | 8.4954 | 9.2901 | 21.3044 | 29.2796 | 10.4555 | 10.8568 | 25.643
SJOW2 MC3 | 275 | 24.6871 | 8.4954 | 9.2901 | 21.3044 | 29.2796 | 10.4555 | 10.8568 | 25.643
SJOW2 MC4 | 275 | 24.6871 | 8.4954 | 9.2901 | 21.3044 | 29.2796 | 10.4555 | 10.8568 | 25.643
SJOW4 M1 | 400 | 98.18 | 30.8456 | 20.4714 | 64.0936 | 116.6783 | 41.6945 | 24.462 | 83.4269
SJOW4 M2 | 400 | 98.18 | 30.8456 | 20.4714 | 64.0936 | 116.6783 | 41.6945 | 24.462 | 83.4269
SJOW4 M3 | 400 | 98.18 | 30.8456 | 20.4714 | 64.0936 | 116.6783 | 41.6945 | 24.462 | 83.4269
SJOW4 M4 | 400 | 98.18 | 30.8456 | 20.4714 | 64.0936 | 116.6783 | 41.6945 | 24.462 | 83.4269
SJOW4 R1/2 | 400 | 98.18 | 30.8456 | 20.4714 | 64.0936 | 116.6783 | 41.6945 | 24.462 | 83.4269
SJOW4 R3/4 | 400 | 98.18 | 30.8456 | 20.4714 | 64.0936 | 116.6783 | 41.6945 | 24.462 | 83.4269
SKLG2 MC1 | 275 | 54.6804 | 20.0158 | 16.0531 | 44.3597 | 53.8113 | 20.9089 | 14.9063 | 44.476
SKLG2 MC2 | 275 | 54.6804 | 20.0158 | 16.0531 | 44.3597 | 53.8113 | 20.9089 | 14.9063 | 44.476
SKLG2 MC3 | 275 | 54.6804 | 20.0158 | 16.0531 | 44.3597 | 53.8113 | 20.9089 | 14.9063 | 44.476
SKLG2 MC4 | 275 | 54.6804 | 20.0158 | 16.0531 | 44.3597 | 53.8113 | 20.9089 | 14.9063 | 44.476
SMAN2 MC1 | 275 | 70.0202 | 25.6706 | 20.4144 | 56.7181 | 70.7772 | 27.5213 | 19.2885 | 58.2095
SMAN2 MC2 | 275 | 70.0202 | 25.6706 | 20.4144 | 56.7181 | 70.7772 | 27.5213 | 19.2885 | 58.2095
SMAN2 MC3 | 275 | 70.0202 | 25.6706 | 20.4144 | 56.7181 | 70.7772 | 27.5213 | 19.2885 | 58.2095
SMAN2 MC4 | 275 | 70.0202 | 25.6706 | 20.4144 | 56.7181 | 70.7772 | 27.5213 | 19.2885 | 58.2095
SPEN4 MC1 | 400 | 57.8135 | 20.1709 | 12.9003 | 41.4262 | 47.4659 | 18.1779 | 9.1702 | 34.8776
SPEN4 MC2 | 400 | 57.8135 | 20.1709 | 12.9003 | 41.4262 | 47.4659 | 18.1779 | 9.1702 | 34.8776
SPLN4 M1 | 400 | 54.3132 | 19.3764 | 12.423 | 39.8253 | 52.0956 | 19.7824 | 12.2989 | 40.2755
SPLN4 R1 | 400 | 54.3132 | 19.3764 | 12.423 | 39.8253 | 52.0956 | 19.7824 | 12.2989 | 40.2755
SSHI2 MC1 | 275 | 64.9534 | 22.8097 | 12.554 | 44.8118 | 57.8862 | 22.5932 | 9.6719 | 41.6235
SSHI2 MC2 | 275 | 64.9534 | 22.8097 | 12.554 | 44.8118 | 57.8862 | 22.5932 | 9.6719 | 41.6235
STAL2 M1 | 275 | 79.0915 | 28.1364 | 15.4483 | 55.2391 | 75.6988 | 29.095 | 15.8521 | 56.9987
STAL2 M2 | 275 | 79.0915 | 28.1364 | 15.4483 | 55.2391 | 75.6988 | 29.095 | 15.8521 | 56.9987
STAL2 R1 | 275 | 79.0915 | 28.1364 | 15.4483 | 55.2391 | 75.6988 | 29.095 | 15.8521 | 56.9987
STAL2 R2 | 275 | 79.0915 | 28.1364 | 15.4483 | 55.2391 | 75.6988 | 29.095 | 15.8521 | 56.9987
STAL4 MC1 | 400 | 56.5483 | 20.3788 | 11.3306 | 40.1506 | 48.574 | 19.035 | 8.8874 | 35.807
STAL4 MC2 | 400 | 56.5483 | 20.3788 | 11.3306 | 40.1506 | 48.574 | 19.035 | 8.8874 | 35.807
STAY4 M1 | 400 | 81.0148 | 28.893 | 14.8155 | 55.6764 | 85.4743 | 32.4618 | 18.0065 | 63.9145
STAY4 M2 | 400 | 81.0148 | 28.893 | 14.8155 | 55.6764 | 85.4743 | 32.4618 | 18.0065 | 63.9145
STAY4 R1 | 400 | 81.0148 | 28.893 | 14.8155 | 55.6764 | 85.4743 | 32.4618 | 18.0065 | 63.9145
STAY4 R2 | 400 | 81.0148 | 28.893 | 14.8155 | 55.6764 | 85.4743 | 32.4618 | 18.0065 | 63.9145
STAY4A | 400 | 62.7968 | 22.5328 | 13.9522 | 45.8184 | 61.0451 | 23.0777 | 15.1801 | 47.8168
STEN1 M1 | 132 | 53.7533 | 18.6996 | 18.9627 | 45.408 | 65.8561 | 24.1195 | 22.4659 | 56.576
STEN1 M2 | 132 | 53.7533 | 18.6996 | 18.9627 | 45.408 | 65.8561 | 24.1195 | 22.4659 | 56.576
STEN1 R1 | 132 | 53.7533 | 18.6996 | 18.9627 | 45.408 | 65.8561 | 24.1195 | 22.4659 | 56.576
STEN1 R2 | 132 | 53.7533 | 18.6996 | 18.9627 | 45.408 | 65.8561 | 24.1195 | 22.4659 | 56.576
STES1 M1 | 132 | 54.0019 | 18.1976 | 15.1637 | 40.899 | 65.8726 | 23.81 | 17.2993 | 50.9718
STES1 M2 | 132 | 54.0019 | 18.1976 | 15.1637 | 40.899 | 65.8726 | 23.81 | 17.2993 | 50.9718
STES1 R1 | 132 | 54.0019 | 18.1976 | 15.1637 | 40.899 | 65.8726 | 23.81 | 17.2993 | 50.9718
STES1 R2 | 132 | 54.0019 | 18.1976 | 15.1637 | 40.899 | 65.8726 | 23.81 | 17.2993 | 50.9718
STEW2 M1 | 275 | 77.4642 | 27.5881 | 24.2479 | 63.2634 | 75.2016 | 28.5617 | 22.8292 | 63.2216
STEW2 M2 | 275 | 77.4642 | 27.5881 | 24.2479 | 63.2634 | 75.2016 | 28.5617 | 22.8292 | 63.2216
STEW2 R1 | 275 | 77.4642 | 27.5881 | 24.2479 | 63.2634 | 75.2016 | 28.5617 | 22.8292 | 63.2216
STEW2 R2 | 275 | 77.4642 | 27.5881 | 24.2479 | 63.2634 | 75.2016 | 28.5617 | 22.8292 | 63.2216
STEW4 M1 | 400 | 74.0242 | 25.7929 | 23.5792 | 60.0559 | 59.1871 | 22.636 | 17.3 | 49.3122
STEW4 M2 | 400 | 74.0242 | 25.7929 | 23.5792 | 60.0559 | 59.1871 | 22.636 | 17.3 | 49.3122
STEW4 R1 | 400 | 74.0242 | 25.7929 | 23.5792 | 60.0559 | 59.1871 | 22.636 | 17.3 | 49.3122
STEW4 R2a | 400 | 74.0242 | 25.7929 | 23.5792 | 60.0559 | 59.1871 | 22.636 | 17.3 | 49.3122
STOB4 M1 | 400 | 55.6908 | 20.3841 | 9.439 | 38.2665 | 48.3789 | 19.1978 | 7.1867 | 34.3365
STOB4 R1 | 400 | 55.6908 | 20.3841 | 9.439 | 38.2665 | 48.3789 | 19.1978 | 7.1867 | 34.3365
STSB4 MC1 | 400 | 53.1547 | 19.114 | 10.9951 | 38.0263 | 43.9438 | 17.2853 | 7.2588 | 31.7038
STSB4 MC2 | 400 | 53.1547 | 19.114 | 10.9951 | 38.0263 | 43.9438 | 17.2853 | 7.2588 | 31.7038
STSB4A | 400 | 51.2806 | 18.0239 | 4.9014 | 30.391 | 41.638 | 16.2531 | 2.995 | 25.9804
SUND4 M1 | 400 | 94.8732 | 32.4573 | 18.2293 | 64.1308 | 84.3694 | 32.1482 | 15.3725 | 60.837
SUND4 M2 | 400 | 76.8919 | 26.8503 | 14.8742 | 52.8463 | 68.4868 | 26.1472 | 12.9489 | 49.9267
SUND4 R1 | 400 | 94.8732 | 32.4573 | 18.2293 | 64.1308 | 84.3694 | 32.1482 | 15.3725 | 60.837
SUND4 R2 | 400 | 76.8919 | 26.8503 | 14.8742 | 52.8463 | 68.4868 | 26.1472 | 12.9489 | 49.9267
SUTB4A | 400 | 63.7127 | 22.7411 | 12.8693 | 45.03 | 60.4918 | 23.1805 | 12.9523 | 45.7345
SWAN2 MC3 | 275 | 16.6041 | 6.0571 | 4.7244 | 13.2904 | 18.8599 | 7.0328 | 5.3312 | 15.277
SWAN2 MC4 | 275 | 16.6041 | 6.0571 | 4.7244 | 13.2904 | 18.8599 | 7.0328 | 5.3312 | 15.277
SWAN4 M1 | 400 | 15.2444 | 5.6324 | 3.5843 | 11.5496 | 15.4887 | 5.8696 | 3.7949 | 12.0957
SWAN4 M2 | 400 | 15.2444 | 5.6324 | 3.5843 | 11.5496 | 15.4887 | 5.8696 | 3.7949 | 12.0957
SWAN4 M3 | 400 | 42.9419 | 15.3507 | 8.6911 | 30.4003 | 44.0858 | 16.7766 | 9.0604 | 32.786
SWAN4 M4 | 400 | 42.9419 | 15.3507 | 8.6911 | 30.4003 | 44.0858 | 16.7766 | 9.0604 | 32.786
SWAN4 R3 | 400 | 42.9419 | 15.3507 | 8.6911 | 30.4003 | 44.0858 | 16.7766 | 9.0604 | 32.786
SWAN4 R4 | 400 | 42.9419 | 15.3507 | 8.6911 | 30.4003 | 44.0858 | 16.7766 | 9.0604 | 32.786
TAUN4 M1 | 400 | 29.1674 | 10.8253 | 4.437 | 19.7463 | 27.6169 | 10.8643 | 4.3907 | 19.7552
TAUN4 M2 | 400 | 36.1163 | 13.1828 | 5.5134 | 24.1567 | 34.4549 | 13.5522 | 5.1941 | 24.3598
TEMP2 MC1 | 275 | 51.5317 | 18.786 | 9.3089 | 35.8764 | 53.903 | 21.2263 | 9.2301 | 39.2485
TEMP2 MC2 | 275 | 51.5317 | 18.786 | 9.3089 | 35.8764 | 53.903 | 21.2263 | 9.2301 | 39.2485
TEMP2 MC3 | 275 | 51.6291 | 18.8161 | 9.3371 | 35.947 | 54.5205 | 21.4527 | 9.3647 | 39.7034
THOM2 M1 | 275 | 58.9148 | 21.1773 | 14.9091 | 44.8583 | 62.9395 | 23.7342 | 15.812 | 49.3772
THOM2 R1 | 275 | 58.9148 | 21.1773 | 14.9091 | 44.8583 | 62.9395 | 23.7342 | 15.812 | 49.3772
THOM4 MC1 | 400 | 66.0412 | 23.3575 | 14.2586 | 47.2911 | 64.2636 | 24.4072 | 13.2732 | 47.7903
THOM4 MC2 | 400 | 66.0412 | 23.3575 | 14.2586 | 47.2911 | 64.2636 | 24.4072 | 13.2732 | 47.7903
THOM4 MC3 | 400 | 66.0412 | 23.3575 | 14.2586 | 47.2911 | 64.2636 | 24.4072 | 13.2732 | 47.7903
THOM4 MC4 | 400 | 66.0412 | 23.3575 | 14.2586 | 47.2911 | 64.2636 | 24.4072 | 13.2732 | 47.7903
THOM42 M5 | 400 | 71.0333 | 25.2479 | 13.6866 | 49.3925 | 66.2575 | 25.4272 | 12.2616 | 48.2211
THOM42 R2(2) | 400 | 71.0333 | 25.2479 | 13.6866 | 49.3925 | 66.2575 | 25.4272 | 12.2616 | 48.2211
THOM42 R2(3) | 400 | 71.0333 | 25.2479 | 13.6866 | 49.3925 | 66.2575 | 25.4272 | 12.2616 | 48.2211
THOM42 R5 | 400 | 71.0333 | 25.2479 | 13.6866 | 49.3925 | 66.2575 | 25.4272 | 12.2616 | 48.2211
THTO4 M1 | 400 | 72.4746 | 25.5348 | 16.8131 | 52.9247 | 62.8771 | 24.1175 | 11.9185 | 46.0258
THTO4 M2 | 400 | 50.8686 | 18.334 | 11.6949 | 37.623 | 43.304 | 16.607 | 8.7959 | 32.2817
THTO4 M3 | 400 | 50.8686 | 18.334 | 11.6949 | 37.623 | 43.304 | 16.607 | 8.7959 | 32.2817
THTO4 M4 | 400 | 72.4746 | 25.5348 | 16.8131 | 52.9247 | 62.8771 | 24.1175 | 11.9185 | 46.0258
THTO4 R1/2 | 400 | 57.3027 | 20.4142 | 12.8025 | 41.6725 | 52.1122 | 19.8405 | 10.5524 | 38.6112
THTO4 R3/4 | 400 | 57.3027 | 20.4142 | 12.8025 | 41.6725 | 52.1122 | 19.8405 | 10.5524 | 38.6112
THUR2 MC1 | 275 | 57.8839 | 21.2914 | 9.1041 | 39.2147 | 60.4588 | 23.7564 | 9.7547 | 43.3513
THUR2 MC2 | 275 | 57.8839 | 21.2914 | 9.1041 | 39.2147 | 60.4588 | 23.7564 | 9.7547 | 43.3513
THUR2 MC3 | 275 | 57.8839 | 21.2914 | 9.1041 | 39.2147 | 60.4588 | 23.7564 | 9.7547 | 43.3513
THUR2 MC4 | 275 | 57.8839 | 21.2914 | 9.1041 | 39.2147 | 60.4588 | 23.7564 | 9.7547 | 43.3513
TILB2 M1 | 275 | 65.7788 | 22.6546 | 17.5127 | 49.5511 | 71.0223 | 26.1919 | 18.7819 | 55.8229
TILB2 M2 | 275 | 65.7788 | 22.6546 | 17.5127 | 49.5511 | 71.0223 | 26.1919 | 18.7819 | 55.8229
TILB2 R1 | 275 | 65.7788 | 22.6546 | 17.5127 | 49.5511 | 71.0223 | 26.1919 | 18.7819 | 55.8229
TILB2 R2 | 275 | 65.7788 | 22.6546 | 17.5127 | 49.5511 | 71.0223 | 26.1919 | 18.7819 | 55.8229
TILB4 M2 | 400 | 104.9129 | 35.8173 | 29.0342 | 79.6875 | 102.0991 | 38.716 | 26.8299 | 81.5827
TILB4 M3 | 400 | 104.9129 | 35.8173 | 29.0342 | 79.6875 | 102.0991 | 38.716 | 26.8299 | 81.5827
TILB4 R2 | 400 | 104.9129 | 35.8173 | 29.0342 | 79.6875 | 102.0991 | 38.716 | 26.8299 | 81.5827
TILB4 R3 | 400 | 104.9129 | 35.8173 | 29.0342 | 79.6875 | 102.0991 | 38.716 | 26.8299 | 81.5827
TINP2 M1 | 275 | 52.6375 | 18.6663 | 5.5157 | 31.9137 | 52.6267 | 20.2876 | 4.7336 | 33.4246
TINP2 M2 | 275 | 52.7781 | 18.6726 | 5.5293 | 31.9364 | 53.4102 | 20.5641 | 4.7996 | 33.8817
TODP2 MC1 | 275 | 56.3704 | 19.396 | 13.2406 | 40.6707 | 53.661 | 20.3676 | 10.4813 | 39.2854
TODP2 MC2 | 275 | 56.3704 | 19.396 | 13.2406 | 40.6707 | 53.661 | 20.3676 | 10.4813 | 39.2854
TOTE2A | 275 | 83.1548 | 29.221 | 26.1358 | 67.4606 | 88.0985 | 33.3312 | 25.5557 | 72.6932
TOTE2B | 275 | 75.467 | 26.8558 | 23.3166 | 61.2964 | 78.9939 | 30.0414 | 22.8006 | 65.2855
TOTT2 MC1 | 275 | 75.467 | 26.8558 | 23.3166 | 61.2964 | 78.9939 | 30.0414 | 22.8006 | 65.2855
TOTT2 MC2A | 275 | 83.1548 | 29.221 | 26.1358 | 67.4606 | 88.0985 | 33.3312 | 25.5557 | 72.6932
TOTT2 MC2B | 275 | 75.467 | 26.8558 | 23.3166 | 61.2964 | 78.9939 | 30.0414 | 22.8006 | 65.2855
TOTT2 MC3 | 275 | 83.1548 | 29.221 | 26.1358 | 67.4606 | 88.0985 | 33.3312 | 25.5557 | 72.6932
TOTT2 MC4A | 275 | 75.467 | 26.8558 | 23.3166 | 61.2964 | 78.9939 | 30.0414 | 22.8006 | 65.2855
TOTT2 MC4B | 275 | 83.1548 | 29.221 | 26.1358 | 67.4606 | 88.0985 | 33.3312 | 25.5557 | 72.6932
TOTT2 MC5 | 275 | 75.467 | 26.8558 | 23.3166 | 61.2964 | 78.9939 | 30.0414 | 22.8006 | 65.2855
TOTT2 MC6 | 275 | 75.467 | 26.8558 | 23.3166 | 61.2964 | 78.9939 | 30.0414 | 22.8006 | 65.2855
TOTT2 MC7 | 275 | 83.1548 | 29.221 | 26.1358 | 67.4606 | 88.0985 | 33.3312 | 25.5557 | 72.6932
TOTT2 MC8 | 275 | 83.1548 | 29.221 | 26.1358 | 67.4606 | 88.0985 | 33.3312 | 25.5557 | 72.6932
TRAW2 M1 | 275 | 40.5143 | 14.4192 | 11.7134 | 32.1052 | 43.4585 | 16.2183 | 11.3257 | 34.2618
TRAW2 M2 | 275 | 40.5143 | 14.4192 | 11.7134 | 32.1052 | 43.4585 | 16.2183 | 11.3257 | 34.2618
TRAW2 R1 | 275 | 40.5143 | 14.4192 | 11.7134 | 32.1052 | 43.4585 | 16.2183 | 11.3257 | 34.2618
TRAW2 R2 | 275 | 40.5143 | 14.4192 | 11.7134 | 32.1052 | 43.4585 | 16.2183 | 11.3257 | 34.2618
TRAW4 MC1 | 400 | 48.1652 | 17.7195 | 14.1827 | 39.2419 | 42.0544 | 16.5412 | 10.9881 | 34.3809
TRAW4 MC2 | 400 | 48.1652 | 17.7195 | 14.1827 | 39.2419 | 42.0544 | 16.5412 | 10.9881 | 34.3809
TRAW4 MC3 | 400 | 48.1652 | 17.7195 | 14.1827 | 39.2419 | 42.0544 | 16.5412 | 10.9881 | 34.3809
TRAW4 MC4 | 400 | 48.1652 | 17.7195 | 14.1827 | 39.2419 | 42.0544 | 16.5412 | 10.9881 | 34.3809
TREM2 MC1 | 275 | 39.3639 | 13.9391 | 1.8685 | 21.5814 | 36.3878 | 14.2725 | 1.9144 | 22.0988
TREM2 MC2 | 275 | 39.3639 | 13.9391 | 1.8685 | 21.5814 | 36.3878 | 14.2725 | 1.9144 | 22.0988
TREU4A | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.5313 | 24.3831 | 3.8419 | 38.3248
TREU4A_DEES1 | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.5313 | 24.3831 | 3.8419 | 38.3248
TREU4A_LEGA1 | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.5313 | 24.3831 | 3.8419 | 38.3248
TREU4A_TRAW1 | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.5313 | 24.3831 | 3.8419 | 38.3248
TREU4B | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.6555 | 24.4286 | 3.8494 | 38.3967
TREU4B_DEES2 | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.6555 | 24.4286 | 3.8494 | 38.3967
TREU4B_LEGA2 | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.6555 | 24.4286 | 3.8494 | 38.3967
TREU4B_TRAW2 | 400 | 69.4329 | 23.6257 | 6.169 | 39.5809 | 63.6555 | 24.4286 | 3.8494 | 38.3967
TYNE2 MC1 | 275 | 60.6076 | 21.4577 | 11.3807 | 41.7264 | 53.7976 | 20.927 | 9.4139 | 39.0092
TYNE2 MC2 | 275 | 60.6076 | 21.4577 | 11.3807 | 41.7264 | 53.7976 | 20.927 | 9.4139 | 39.0092
TYNE2A | 275 | 59.9065 | 20.6516 | 4.2965 | 33.5022 | 50.7573 | 19.7846 | 2.9176 | 30.8972
UPPB2 MC1 | 275 | 34.5856 | 12.6817 | 7.8334 | 25.7681 | 35.2113 | 13.5144 | 8.0249 | 27.1372
UPPB2 MC2 | 275 | 36.7299 | 13.4155 | 8.0782 | 27.0506 | 36.7013 | 14.1203 | 7.7972 | 27.7663
UPPB2 MC3 | 275 | 36.7299 | 13.4155 | 8.0782 | 27.0506 | 36.7013 | 14.1203 | 7.7972 | 27.7663
UPPB2 MC4 | 275 | 34.5856 | 12.6817 | 7.8334 | 25.7681 | 35.2113 | 13.5144 | 8.0249 | 27.1372
USKM1 M1 | 132 | 47.4121 | 16.692 | 17.783 | 41.3891 | 63.2224 | 23.2849 | 22.9797 | 55.9095
USKM1 M2 | 132 | 47.4121 | 16.2645 | 14.9278 | 37.9293 | 63.2224 | 23.0068 | 19.0449 | 51.5814
USKM1 M4 | 132 | 47.4121 | 16.2645 | 14.9278 | 37.9293 | 63.2224 | 23.0068 | 19.0449 | 51.5814
USKM1 R1 | 132 | 47.4121 | 16.692 | 17.783 | 41.3891 | 63.2224 | 23.2849 | 22.9797 | 55.9095
USKM1 R2 | 132 | 47.4121 | 16.2645 | 14.9278 | 37.9293 | 63.2224 | 23.0068 | 19.0449 | 51.5814
USKM1 R4 | 132 | 47.4121 | 16.2645 | 14.9278 | 37.9293 | 63.2224 | 23.0068 | 19.0449 | 51.5814
USKM2 M1 | 275 | 57.2214 | 20.0547 | 11.233 | 39.5947 | 63.2758 | 23.9616 | 12.6699 | 46.5568
USKM2 M2 | 275 | 57.2214 | 20.0547 | 11.233 | 39.5947 | 63.2758 | 23.9616 | 12.6699 | 46.5568
USKM2 R1 | 275 | 57.2214 | 20.0547 | 11.233 | 39.5947 | 63.2758 | 23.9616 | 12.6699 | 46.5568
USKM2 R2 | 275 | 57.2214 | 20.0547 | 11.233 | 39.5947 | 63.2758 | 23.9616 | 12.6699 | 46.5568
USKM2A | 275 | 56.0705 | 18.9253 | 4.9927 | 31.7571 | 61.1429 | 22.8985 | 5.4049 | 37.7883
WALH4 MC1 | 400 | 53.4709 | 19.3357 | 9.4619 | 36.8068 | 47.4065 | 18.4148 | 9.2636 | 35.306
WALH4 MC2 | 400 | 53.4709 | 19.3357 | 9.4619 | 36.8068 | 47.4065 | 18.4148 | 9.2636 | 35.306
WALH4 MC3 | 400 | 53.4709 | 19.3357 | 9.4619 | 36.8068 | 47.4065 | 18.4148 | 9.2636 | 35.306
WALH4 MC4 | 400 | 53.4709 | 19.3357 | 9.4619 | 36.8068 | 47.4065 | 18.4148 | 9.2636 | 35.306
WALP R4 | 132 | 59.4543 | 20.9951 | 16.972 | 46.6636 | 72.3816 | 27.778 | 19.2468 | 58.5309
WALP1 M4 | 132 | 59.4543 | 20.9951 | 16.972 | 46.6636 | 72.3816 | 27.778 | 19.2468 | 58.5309
WALP4 M1 | 400 | 73.9984 | 25.9181 | 16.2057 | 52.8595 | 70.4241 | 26.7511 | 15.613 | 53.4448
WALP4 M2 | 400 | 73.9984 | 25.9181 | 16.2057 | 52.8595 | 70.4241 | 26.7511 | 15.613 | 53.4448
WALP4 R1 | 400 | 73.9984 | 25.9181 | 16.2057 | 52.8595 | 70.4241 | 26.7511 | 15.613 | 53.4448
WALP4 R2 | 400 | 73.9984 | 25.9181 | 16.2057 | 52.8595 | 70.4241 | 26.7511 | 15.613 | 53.4448
WALPM3 | 132 | 59.4543 | 20.9951 | 16.972 | 46.6636 | 72.3816 | 27.778 | 19.2468 | 58.5309
WALPR3 | 132 | 59.4543 | 20.9951 | 16.972 | 46.6636 | 72.3816 | 27.778 | 19.2468 | 58.5309
WALX2 M1 | 275 | 80.3904 | 26.9902 | 13.5557 | 51.7257 | 81.8768 | 30.3179 | 13.678 | 56.554
WALX2 M2 | 275 | 80.2726 | 26.9152 | 13.5925 | 51.6563 | 85.465 | 31.5168 | 14.2257 | 58.7972
WALX2 R1 | 275 | 80.3904 | 26.9902 | 13.5557 | 51.7257 | 81.8768 | 30.3179 | 13.678 | 56.554
WALX2 R2 | 275 | 80.2726 | 26.9152 | 13.5925 | 51.6563 | 85.465 | 31.5168 | 14.2257 | 58.7972
WALX4A | 400 | 59.8816 | 20.089 | 6.9978 | 35.4079 | 62.4774 | 22.9458 | 7.846 | 40.2963
WALX4B | 400 | 59.8239 | 20.1127 | 7.0122 | 35.4559 | 57.5038 | 21.2279 | 7.394 | 37.4148
WARL2 MC1 | 275 | 60.4357 | 21.1705 | 13.2787 | 43.2182 | 57.3744 | 22.0399 | 10.2963 | 41.4654
WARL2 MC2 | 275 | 60.4357 | 21.1705 | 13.2787 | 43.2182 | 57.3744 | 22.0399 | 10.2963 | 41.4654
WARL2 MC3 | 275 | 60.4357 | 21.1705 | 13.2787 | 43.2182 | 57.3744 | 22.0399 | 10.2963 | 41.4654
WARL2 MC4 | 275 | 60.4357 | 21.1705 | 13.2787 | 43.2182 | 57.3744 | 22.0399 | 10.2963 | 41.4654
WASF2A | 275 | 49.1586 | 17.2566 | 5.4292 | 29.8337 | 43.5932 | 16.7718 | 3.2207 | 26.9396
WASF2B | 275 | 43.8387 | 15.3073 | 4.8161 | 26.464 | 42.4941 | 16.4195 | 3.3162 | 26.5369
WBOL2 MC1 | 275 | 73.3206 | 25.2861 | 15.2702 | 51.0301 | 64.3698 | 24.9868 | 10.979 | 46.3156
WBOL2 MC2 | 275 | 73.3206 | 25.2861 | 15.2702 | 51.0301 | 64.3698 | 24.9868 | 10.979 | 46.3156
WBOL2 MC3 | 275 | 73.3206 | 25.2861 | 15.2702 | 51.0301 | 64.3698 | 24.9868 | 10.979 | 46.3156
WBOL2 MC4 | 275 | 73.3206 | 25.2861 | 15.2702 | 51.0301 | 64.3698 | 24.9868 | 10.979 | 46.3156
WBUR1 M1 | 132 | 21.0984 | 7.484 | 6.4547 | 17.0387 | 24.7137 | 9.143 | 7.8012 | 20.7313
WBUR1 M2 | 132 | 21.0984 | 7.484 | 6.4547 | 17.0387 | 24.7137 | 9.143 | 7.8012 | 20.7313
WBUR1 R1 | 132 | 21.0984 | 7.484 | 6.4547 | 17.0387 | 24.7137 | 9.143 | 7.8012 | 20.7313
WBUR1 R2 | 132 | 20.6939 | 7.3666 | 6.207 | 16.6249 | 24.3232 | 9.0085 | 7.5429 | 20.2829
WBUR4 M1 | 400 | 63.5377 | 22.511 | 15.5178 | 47.3531 | 65.6459 | 24.5448 | 16.8382 | 51.5498
WBUR4 M2 | 400 | 63.5377 | 22.511 | 15.5178 | 47.3531 | 65.6459 | 24.5448 | 16.8382 | 51.5498
WBUR4 M3 | 400 | 63.5377 | 22.511 | 15.5178 | 47.3531 | 65.6459 | 24.5448 | 16.8382 | 51.5498
WBUR4 M4 | 400 | 63.5377 | 22.511 | 15.5178 | 47.3531 | 65.6459 | 24.5448 | 16.8382 | 51.5498
WBUR4 R1/2 | 400 | 85.5102 | 30.0991 | 18.5747 | 61.1413 | 89.0681 | 33.41 | 21.0808 | 68.3297
WBUR4 R3/4 | 400 | 85.5102 | 30.0991 | 18.5747 | 61.1413 | 89.0681 | 33.41 | 21.0808 | 68.3297
WHAM4 M1 | 400 | 101.0728 | 33.9805 | 28.8787 | 76.9344 | 116.1197 | 43.3817 | 30.902 | 92.253
WHAM4 M2 | 400 | 101.0728 | 33.9805 | 28.8787 | 76.9344 | 116.1197 | 43.3817 | 30.902 | 92.253
WHAM4 R1 | 400 | 101.0728 | 33.9805 | 28.8787 | 76.9344 | 116.1197 | 43.3817 | 30.902 | 92.253
WHAM4 R2 | 400 | 101.0728 | 33.9805 | 28.8787 | 76.9344 | 116.1197 | 43.3817 | 30.902 | 92.253
WHAM4A | 400 | 82.3025 | 24.9656 | 8.7506 | 44.0574 | 87.8108 | 32.3869 | 11.2724 | 57.0743
WHAM4B | 400 | 82.3859 | 24.9858 | 8.7485 | 44.0837 | 87.9229 | 32.4283 | 11.2723 | 57.1329
WHSO2 M1 | 275 | 52.3783 | 18.5798 | 9.53 | 35.8058 | 57.433 | 21.8851 | 10.8468 | 41.7969
WHSO2 M2 | 275 | 52.3783 | 18.5798 | 9.53 | 35.8058 | 57.433 | 21.8851 | 10.8468 | 41.7969
WHSO2 R1 | 275 | 56.4754 | 19.8407 | 11.6263 | 39.6853 | 63.0384 | 23.7733 | 13.4868 | 47.1074
WHSO2 R2 | 275 | 56.4754 | 19.8407 | 11.6263 | 39.6853 | 63.0384 | 23.7733 | 13.4868 | 47.1074
WIBA2 MC1 | 275 | 50.1089 | 18.3594 | 8.6438 | 34.6079 | 52.8911 | 21.247 | 8.3664 | 38.4142
WIBA2 MC2 | 275 | 50.1089 | 18.3594 | 8.6438 | 34.6079 | 52.8911 | 21.247 | 8.3664 | 38.4142
WILE4 M1 | 400 | 88.8011 | 32.374 | 22.3787 | 68.1624 | 82.1802 | 32.3776 | 20.0925 | 65.8813
WILE4 M2 | 400 | 88.8011 | 32.374 | 22.3787 | 68.1624 | 82.1802 | 32.3776 | 20.0925 | 65.8813
WILE4 R1 | 400 | 88.8011 | 32.374 | 22.3787 | 68.1624 | 82.1802 | 32.3776 | 20.0925 | 65.8813
WILE4 R2 | 400 | 88.8011 | 32.374 | 22.3787 | 68.1624 | 82.1802 | 32.3776 | 20.0925 | 65.8813
WILL1 M1 | 132 | 50.3615 | 17.4953 | 15.4783 | 40.2204 | 57.7965 | 21.7701 | 17.9975 | 48.7851
WILL1 M2 | 132 | 50.3615 | 17.4953 | 15.4783 | 40.2204 | 57.7965 | 21.7701 | 17.9975 | 48.7851
WILL1 R1 | 132 | 34.5863 | 12.7575 | 10.342 | 28.3838 | 38.5733 | 14.839 | 11.9539 | 32.9394
WILL1 R2 | 132 | 50.3615 | 17.4953 | 15.4783 | 40.2204 | 57.7965 | 21.7701 | 17.9975 | 48.7851
WILL2 M2 | 275 | 22.8226 | 8.1041 | 8.1711 | 19.6321 | 24.6785 | 8.9898 | 8.6942 | 21.4077
WILT2A | 275 | 47.1217 | 16.4298 | 7.6486 | 30.8839 | 50.9101 | 18.7664 | 7.6232 | 34.1628
WILT2B | 275 | 47.1217 | 16.4298 | 7.6486 | 30.8839 | 50.9101 | 18.7664 | 7.6232 | 34.1628
WILT2C | 275 | 47.3752 | 16.5058 | 7.7527 | 31.0953 | 51.6549 | 18.9924 | 8.1135 | 34.9728
WILT2D | 275 | 47.375 | 16.5058 | 7.7525 | 31.0952 | 51.6522 | 18.9916 | 8.1123 | 34.9705
WIMB2 MC1 | 275 | 75.5592 | 25.3311 | 17.5235 | 53.3471 | 82.7938 | 31.3197 | 18.8949 | 63.1876
WIMB2 MC2 | 275 | 75.5592 | 25.3311 | 17.5235 | 53.3471 | 82.7938 | 31.3197 | 18.8949 | 63.1876
WIMB2 MC3 | 275 | 75.5592 | 25.3311 | 17.5235 | 53.3471 | 82.7938 | 31.3197 | 18.8949 | 63.1876
WIMB2 MC4 | 275 | 75.5592 | 25.3311 | 17.5235 | 53.3471 | 82.7938 | 31.3197 | 18.8949 | 63.1876
WIMB2A | 275 | 75.5592 | 25.3311 | 17.5235 | 53.3471 | 82.7938 | 31.3197 | 18.8949 | 63.1876
WIMB4 MB2 | 400 | 72.6533 | 23.7199 | 15.9467 | 49.4917 | 85.206 | 31.8021 | 15.6526 | 60.6276
WIMB4 RB2 | 400 | 72.6533 | 23.7199 | 15.9467 | 49.4917 | 85.206 | 31.8021 | 15.6526 | 60.6276
WISD2 M1 | 275 | 63.562 | 21.2708 | 18.5822 | 48.6636 | 74.5413 | 27.1548 | 21.3727 | 59.7754
WISD2 M2 | 275 | 63.562 | 21.2708 | 18.5822 | 48.6636 | 74.5413 | 27.1548 | 21.3727 | 59.7754
WISD2 R1 | 275 | 63.562 | 21.2708 | 18.5822 | 48.6636 | 74.5413 | 27.1548 | 21.3727 | 59.7754
WISD2 R2 | 275 | 63.562 | 21.2708 | 18.5822 | 48.6636 | 74.5413 | 27.1548 | 21.3727 | 59.7754
WISD2A | 275 | 53.7189 | 17.8836 | 9.8321 | 35.1234 | 58.9464 | 22.0848 | 11.3968 | 42.6295
WMEL2 MC1 | 275 | 68.2429 | 24.4335 | 11.8503 | 46.4046 | 67.8711 | 26.5262 | 10.6067 | 48.1204
WMEL2 MC2 | 275 | 68.2429 | 24.4335 | 11.8503 | 46.4046 | 67.8711 | 26.5262 | 10.6067 | 48.1204
WMEL2 MC3 | 275 | 68.2429 | 24.4335 | 11.8503 | 46.4046 | 67.8711 | 26.5262 | 10.6067 | 48.1204
WMEL2 MC4 | 275 | 68.2429 | 24.4335 | 11.8503 | 46.4046 | 67.8711 | 26.5262 | 10.6067 | 48.1204
WTHU4A | 400 | 77.1708 | 24.3211 | 5.1624 | 39.5577 | 66.3843 | 25.1321 | 3.7149 | 39.2571
WTHU4B | 400 | 77.1708 | 24.3211 | 5.1624 | 39.5577 | 67.7192 | 25.6 | 3.7896 | 39.9935
WWEY2 M1 | 275 | 66.7603 | 23.2812 | 15.316 | 48.2405 | 66.9771 | 25.2465 | 14.994 | 50.6979
WWEY2 M2 | 275 | 66.7603 | 23.2812 | 15.316 | 48.2405 | 66.9771 | 25.2465 | 14.994 | 50.6979
WWEY2 R1 | 275 | 68.1779 | 23.872 | 14.2666 | 48.0267 | 69.3736 | 26.2329 | 14.9403 | 52.0391
WWEY2 R2 | 275 | 68.1779 | 23.872 | 14.2666 | 48.0267 | 69.3736 | 26.2329 | 14.9403 | 52.0391
WWEY4A | 400 | 46.0565 | 15.9064 | 5.0798 | 27.5748 | 42.4477 | 16.0173 | 5.3544 | 28.0063
WWEY4B | 400 | 46.324 | 16.0024 | 5.1058 | 27.7366 | 42.1677 | 15.9822 | 5.468 | 28.0703
WYLF1 M1 | 132 | 17.837 | 5.5465 | 6.4525 | 14.2965 | 20.1408 | 6.9603 | 6.7619 | 16.6053
WYLF1 M2 | 132 | 17.837 | 5.5465 | 6.4525 | 14.2965 | 20.1408 | 6.9603 | 6.7619 | 16.6053
WYLF1 R1 | 132 | 17.837 | 5.5465 | 6.4525 | 14.2965 | 20.1408 | 6.9603 | 6.7619 | 16.6053
WYLF1 R2 | 132 | 17.837 | 5.5465 | 6.4525 | 14.2965 | 20.1408 | 6.9603 | 6.7619 | 16.6053
WYLF4 M1 | 400 | 37.549 | 13.4258 | 8.5891 | 27.576 | 31.3491 | 12.1581 | 5.8998 | 23.0939
WYLF4 M2 | 400 | 37.549 | 13.4258 | 8.5891 | 27.576 | 31.3491 | 12.1581 | 5.8998 | 23.0939
WYLF4 R1 | 400 | 37.549 | 13.4258 | 8.5891 | 27.576 | 31.3491 | 12.1581 | 5.8998 | 23.0939
WYLF4 R2 | 400 | 37.549 | 13.4258 | 8.5891 | 27.576 | 31.3491 | 12.1581 | 5.8998 | 23.0939
WYMO4 M1 | 400 | 91.0967 | 31.3025 | 17.8555 | 62.124 | 83.6171 | 31.7546 | 15.5389 | 60.4467
WYMO4 M2 | 400 | 91.0967 | 31.3025 | 17.8555 | 62.124 | 83.6171 | 31.7546 | 15.5389 | 60.4467
WYMO4 R1 | 400 | 91.0967 | 31.3025 | 17.8555 | 62.124 | 83.6171 | 31.7546 | 15.5389 | 60.4467
WYMO4 R2 | 400 | 91.0967 | 31.3025 | 17.8555 | 62.124 | 83.6171 | 31.7546 | 15.5389 | 60.4467