## Q&A
Publication date | Question source | Topic | Question number | Question | Answer
10.11.21 | Response & Reserve webinar (4/11) | Baselines | 1 | How far ahead will nomination baselines have to be given? | Operational baselines will become final 60 minutes before the start of the 30-minute settlement period. This aligns with the existing arrangements for DC.
10.11.21 | Response & Reserve webinar (4/11) | Launch dates | 2 | What is the target date for the Day 1 MVP Go-Live? | Late March for DR and April for DM
10.11.21 | Response & Reserve webinar (4/11) | Procurement | 3 | Can you enter 1 EFA for DC and another for DM? | Yes, you can be contracted for different services in different EFA blocks providing all service parameters can be satisfied at all times. For the avoidance of doubt, the same unit can't deliver more than one service (DM, DR, DC) simultaneously per EFA block although high and low versions of the same service can be delivered in the same EFA block.
10.11.21 | Response & Reserve webinar (4/11) | Baselines | 4 | When will the method/solution for submitting baselines for units not in the BM be ready? | At present, we are not able to specify exactly when the non-BM solution for submitting baselines will be ready. However, this is an important item in our product backlog so will be delivered as soon as possible.
10.11.21 | Response & Reserve webinar (4/11) | Procurement | 5 | Is there going to be one unique Auction Sell Sheet for DC/DM/DR? Or it's going to be separate? Same question for the file with auction results - is the DM/DR file going to be different than the DC one, or it's going to be one file with all results? | This is still to be confirmed but the plan is to have one sell order for DC, DM and DR and similarly one auction results file for all three services.
10.11.21 | Response & Reserve webinar (4/11) | Performance monitoring | 6 | Is there going to be any Performance Monitoring for DM/DR? (ie. similar to DC) | Yes, performance monitoring for DM and DR will follow similar approach as DC. More information can be found in the consultation documentation.
10.11.21 | Response & Reserve webinar (4/11) | Duration of energy limited assets | 7 | How should we interpret the duration of energy limited assets ? Does it mean it should contain at least 30/60min of energy as long as frequency deviation < 0.2 Hz (and not recovering) ? | Yes, units must be able to provide a service in line with the energy-limited asset duration.
10.11.21 | Response & Reserve webinar (4/11) | Volume | 8 | Does the 100MW procurement mean 50MW low and 50MW high? | No, 100MW of DRL (or DML) and 100MW of DRH (or DMH).
10.11.21 | Response & Reserve webinar (4/11) | Volume | 9 | 100 MW volume seems a little low? Currently BMUs in FFR receive an instruction to provide FFR and non BMUs don't. What are the ESO's plans ref this? Thanks | Implementing new services requires a period of transition as we review how the new products perform on the system and interact with the control room's toolkit, as well as reviewing providers' ability to deliver the services. This test and refine approach will be conducted over a period of time, during which the procurement of the legacy services will be slowly reduced as the volumes of the new services increase, and system improvements will be developed and implemented.
10.11.21 | Response & Reserve webinar (4/11) | Volume | 10 | DR Unit Cap - 50 MW. Is this 50MW High and 50MW Low? Is 50MW the frequency holding for a given frequency deviation e.g. 50MW for a 0.2Hz deviation? | The unit cap of 50MW applies to each of the unbundled services separately. If a unit can provide 50MW of Low and 50 MW of High at the same time without compromising provision of either service then they would qualify as a 50MW DRL and a 50MW DRH unit. When referring to unit cap we mean maximum MW of DR (or DM) response provided at the 0.2Hz deviation level.
10.11.21 | Response & Reserve webinar (4/11) | Procurement | 11 | Please could you repeat the bidding rules across DC/DM/DR for the same EFA periods? | All services (DC, DM, and DR) will be cleared simultaneously in an auction at 14:30 each day. Providers will have to choose in advance which of the three services to offer in each period and should not bid in such a way that means they can not deliver on their awarded capacity.
10.11.21 | Response & Reserve webinar (4/11) | Oscillations | 12 | Are the ESO over worrying about oscillations, - if all the response was in Scotland and HINP C tripped maybe it is an issue but is that realistic? | We are undertaking a series of studies to establish the magnitude of the problem of localised frequency oscillations and assess the level of risk. We will share our findings with industry.
10.11.21 | Response & Reserve webinar (4/11) | Minimum participation threshold | 13 | Is the minimum unit size still 1MW for DM/DR? | Yes the minimum participation threshold to bid into DM and DR is 1.0MW.
10.11.21 | Response & Reserve webinar (4/11) | Baselines | 14 | Can you submit an operational baseline that is a non integer? This is important for smaller assets (e.g 1MW) | Currently we accept integers above 1MW and we are exploring when and how we can accept non-integers.
10.11.21 | Response & Reserve webinar (4/11) | Co-optimisation of auctions | 15 | Is there an intention to co-optimise eventually? (It seems rather old-fashioned and wasteful not to.) | Yes, our end state is to develop co-optimisation through the Enduring Auction Capability project. We recognise the efficiencies which could be explored.
10.11.21 | Response & Reserve webinar (4/11) | Interaction between DM/DR and other services | 16 | On longer term, how will you interplay between DR (DM) requirements and MFR ? | As the impact of procuring DM and DR becomes more established against our expectation, the aim is to offset requirement for MFR. We share our requirements and reasoning behind these requirements in the Market Information Reports, which are published monthly on the ESO Data Portal.
10.11.21 | Response & Reserve webinar (4/11) | Volume | 17 | How long do you expect to keep the cap at 100MW for analysis? and is the end goal to increase this if system risk proves minimal? | We will be steadily reducing the volume of FFR procured as we increase the volume of our new services. We intend to share a product backlog with industry, which will show further development plans to the services, including timelines. We expect the volume cap to be increased once we have completed an initial review of the services; how they interact with the control room's toolkit, and how providers' assets respond.
10.11.21 | Response & Reserve webinar (4/11) | Stacking | 18 | Can high and low bids be stacked? | Yes, bids can be looped, similar to the way DC works currently.
10.11.21 | Response & Reserve webinar (4/11) | Metering data | 19 | For aggregated assets delivering DR (e.g. domestic 3.68kW aggregated to 1MW) will Operational and Performance metering data only be required at overall aggregated level (i.e. 1MW level), or are you actually looking for this data for each asset? | Operational and Performance metering is required at Unit level. Where a Unit may consist of a number of aggregated Assets.
10.11.21 | Response & Reserve webinar (4/11) | Procurement | 20 | Are the auction results for DC/DM/DR going to be in the same file? | Pending final confirmation, yes it will be one file.
30.11.21 | Markets Roadmap webinar (18/11) | Stacking | 21 | To what extent will DC, DR and DM be stackable? | Stacking with the BM and stacking low frequency and high frequency products within the same service are allowed for “day one”. Stacking across different services (DC, DM and DR) will not be permitted for "day one". Detailed examples of the different bidding options can be found in the slides of the consultation overview webinar which have been published on the DM and DR pages on the ESO website.
30.11.21 | Markets Roadmap webinar (18/11) | Stacking | 22 | Can you please explain why we are unable to stack, for example DCL and DMH? They are responses in different directions. | For the "day one" launch, we are focusing on embedding the services to allow us to test the performance of the product alongsidethe rest of the control room's toolkit in a safe, controlled manner. We’re introducing new services onto the system, as a prudent system operator we want to ensure that the performance of the service as designed is delivered by participants and operates as expected, hence starting without stacking across different services. Our auction capability is being developed under our RIIO-2 business plan and we will be exploring optimisation through that.
30.11.21 | Markets Roadmap webinar (18/11) | Aggregated distributed resources | 23 | Will aggregated distributed resources be able to take part? | If they pass testing and are within the GSP group regarding aggregation, and they are above the 1MW threshold. The technical details of the service can be found in the consultation documents on the DM and DR pages on the ESO website.
1.12.21 | Consultation overview webinar (23/11) | SMP vs EPEX | 24 | Can you describe what aspects of the service will be on the Single Markets Platform, versus procurement on the EPEX CTS platform. | Initially, the Single Market Platform (SMP) will just be used for onboarding, with EPEX being used for tenders and the Data Portal for publishing the results. We will eventually transition all activities on to the SMP. We don’t have any timeframes to share on this yet.
1.12.21 | Consultation overview webinar (23/11) | EPEX | 25 | Interesting that you have gone for EPEX for this service but not others? | We took the decision to move the new response services onto the EPEX platform because we were already procuring PSH via the weekly auction. We knew we could quickly move response services onto this platform and use the EPEX auction platform as an interim procurement solution for response whilst the enduring auction capability is being developed. The technical design of STOR and the method of procurement is different to that of response, hence having two interim procurement platforms. Both of these interim platforms enable automated day ahead procurement, which is a key deliverable under our RIIO-2 business plan.
1.12.21 | Consultation overview webinar (23/11) | Price cap | 26 | Will DM & DR Day 1 have a price cap similar to that of DCL, the cost of alternative action? | Yes. DM and DR will use a forecast of the alternative costs as a basis for the price cap. We will calculate how much PSH, DM and DR offset and then forecast the cost of procuring the equivalent from mandatory response. For day 1, as with DC, the price cap will likely be longer-term average forecasts. As the services mature, we expect this price cap to become more sophisticated ultimately with specific day ahead forecasts for each EFA block.
1.12.21 | Consultation overview webinar (23/11) | Disarming instruction | 27 | So, is it assumed that if you win a tender you deliver without an arming instruction, but you might send an instruction to disarm us for a period of time? | Yes. If you are awarded a contract via the auction you should deliver it unless/until you receive a dis-arming instruction.
1.12.21 | Consultation overview webinar (23/11) | Disarming instruction | 28 | When will you provide the technical information explaining how disarming functionality will be delivered? | We are still working on this but will hopefully be able to provide more information on this soon.
1.12.21 | Consultation overview webinar (23/11) | Disarming instruction | 29 | If you win two consecutive periods, and in the first are sent a disarming instruction, are we meant to rearm ourselves at the beginning of second delivery period? | No, the unit should remain disarmed until a re-arming instruction is sent by ENCC.
1.12.21 | Consultation overview webinar (23/11) | Downward regulation | 30 | What is the difference between downward regulation and dynamic regulation? What are the factors that affect the total volume required for downward regulation? | Downward regulation is another name for negative reserve. It means having access to generation that can turn down or demand that can turn up. It is a reserve service that is instructed manually to manage imbalance. Dynamic Regulation is a response service activated automatically by reference to system frequency. It has both high and low frequency variants that both aim to control frequency around the 50Hz target.
1.12.21 | Consultation overview webinar (23/11) | FFR | 31 | What is your updated plan for phasing out FFR, now that we know DR and DM auctions are planned to start late March and late April 22? | The plan is to run FFR concurrently with DR and DM for a period of time whilst the new services are bedding in. Once the services become fully BAU, we will cease to procure FFR.
1.12.21 | Consultation overview webinar (23/11) | Disarming instruction | 32 | How will the disarming and rearming instructions be sent? | In the consultation, we have stated this will be done by electronic means, we are still identifying how this will exactly be done. We are considering for BM that this will be done by reason codes but this still needs to be finalised.
1.12.21 | Consultation overview webinar (23/11) | Onboarding | 33 | When switching assets between aggregators, onboarding can be painful - NGs DB only updates once per week - can this be streamlined? | Once the full SMP solution is in place then this process for switching assets will have shorter timelines. Whilst we will look for process improvements, it is foreseen that the current process will remain for the short to mid-term.
1.12.21 | Consultation overview webinar (23/11) | Testing | 34 | Do you need to qualify/ complete testing for each service or if you are suitable for the faster services does that qualify you for the lower services? | Yes, testing needs to be completed for all services as each service has different delivery profiles, speed and duration and are tested accordingly.
1.12.21 | Consultation overview webinar (23/11) | CSV template | 35 | We currently have specific availability fields for DC HF and DC LF within the Operational Metering and Performance monitoring data. Do you have details of how this will change when DM is introduced? Would we have additional fields for DM HF and DM LF as well, or would the fields combine to just be Dynamic availability overall? | Yes, an updated CSV with extended availability flags will be published.
1.12.21 | Consultation overview webinar (23/11) | Thermal/ pumped storage | 36 | On initial inspection, DR looks too tight for large thermal or pumped storage plant, i.e. they will not be able to follow the line as closely as ESO would like. For a service that we thought was going to be ideal for such plant, we are surprised and do not consider such tight tolerances required? | Tolerances in performance monitoring should cater for this but we will investigate this further.
1.12.21 | Consultation overview webinar (23/11) | Energy limited | 37 | Is the intention to classify all four of the pumped storage sites as energy limited? If not, you might need to rewrite the definition of Energy Limited | Energy Limited is a defined term in the Glossary. Pumped storage will be classified as Energy Limited
1.12.21 | Consultation overview webinar (23/11) | Procurement | 38 | What was the rationale behind clearing all three services simultaneously at 14:30? | The Helena assessment algorithm, which is currently used for DC will also be used to clear the DM and DR auctions therefore as per the platform requirements we will be clearing all the 3 services simultaneously at 14:30.
1.12.21 | Consultation overview webinar (23/11) | MFR | 39 | Is the intention to segregate the MFR and DR markets i.e. batteries only do DR and all conventional power stations do MFR? This might explain the very strict k factor tolerance method proposed. Or is there a lack of understanding of the technical capability of conventional power stations? | Tolerances in performance monitoring should cater for this but we will investigate this further.
1.12.21 | Consultation overview webinar (23/11) | Stacking | 40 | Can you review Clause 12.5 to ensure this does not prevent stacking BM actions | Thanks for this feedback, we will take a look at 12.5.
1.12.21 | Consultation overview webinar (23/11) | Testing | 41 | Will assets that are already qualified in DC or FFR will have to redo testing for DM and DR in order to prequalify? Or will there be some allowance for DC, FFR assets to be automatically qualified for the new services? | All assets will need to be tested to enter the DM and DR services as the delivery profile is different to DC and FFR.
1.12.21 | Consultation overview webinar (23/11) | Integers | 42 | 6.2 states "each Operational Baseline may be either an integer or a value with 4 dp". There seems to be some confusion on whether this means baselines need always be integers, but you could state them in the ops/perf data as either "1" or "1.0000", or does it mean you can also have baselines that are not integers e.g. 0.1234 MW, 1.1234 MW etc? | Operational Baselines can be either integers or have up to 4dp. It depends on the route taken. BM system have some limitations that mean Ops Baselines (Physical Notifications) may be limited to integers. Non-BM systems do not have this limitation meaning that decimals may be allowed. The clause is written in this way to allow flexibility to providers depending on their route.
1.12.21 | Consultation overview webinar (23/11) | Stacking | 43 | Could you stack high and low services in the same EFA, e.g. DCL and DMH? | You can only stack high and low services of the same product in the same EFA block. For example, you can stack DML and DMH within the same EFA block. You cannot stack DCL and DMH in the same EFA, but you can stack these products across different EFA periods. Slides 25 and 26 in the consultation overview webinar slides shows examples of what can and cannot be done in relation to stacking and looping bids.
1.12.21 | Consultation overview webinar (23/11) | Stacking | 44 | Can you bid across different services for the same EFA block, and resultantly only win a single contract for the same unit? | If you bid across the same service, i.e. DCL and DCH, then you could win a single contract. If you bid across different products, i.e. DCL and DML then neither of these will be awarded a contract.
1.12.21 | Consultation overview webinar (23/11) | Procurement | 45 | Will the output for the auctions have the same fields as DC? Will the auction results API, be the same API end point as DC? | Yes, with the addition of 2 additional fields - location and generation type. We will give providers notice of these changes.
1.12.21 | Consultation overview webinar (23/11) | Pay as Bid/Clear | 46 | In line with the Auction Trial using the pay as clear mechanism, we witness uneconomical DC bids with clearing price as low as 1£/MW/h. Will NG consider Pay As Bid or any other approach to avoid the new markets becoming uneconomical markets / avoid destructive competition? | We outlined the desire to move markets to pay as clear in our RIIO-2 submission. The recent low prices in DC are a result of provider behaviour (the submission of price taker offers rather than genuine marginal cost) and the volatility in required volumes essentially creating some very liquid EFA blocks. DM and DR will have much more stable volume requirements at launch and we don’t expect to see the same behaviour occurring as in DC.
1.12.21 | Consultation overview webinar (23/11) | 2Hz/1Hz | 47 | What is the rationale behind the transitional period of 1Hz for DR and then going to 2Hz? | To provide a grace period and flexibility for assets needing more time to transition from a current 1Hz meter to 2Hz.
1.12.21 | Consultation overview webinar (23/11) | Procurement | 48 | If you bid across DC, DM and DR, and only win one of them, is there a ranking of priority of which service procurement target is filled first? i.e. Do you fill your boots with DC before looking at DM / DR? | If you bid across DC, DM or DR within the same EFA period then none of the bids will be accepted as you cannot stack or loop different services within the same EFA period. You can only bid for different services across different EFA periods.
1.12.21 | Consultation overview webinar (23/11) | Pay as Bid/Clear | 49 | Should you not start with pay as bid in line with your document that said you needed competition and perfect knowledge? You can't have either at the start of a new market. | The DM and DR services are enhanced versions of existing PSH, it is therefore relatively straightforward to understand the alternative costs based on how much PSH would be offset from the mandatory market. The volume requirements are also stable in the medium term. We feel this represents sufficient knowledge, if not perfect knowledge. Whilst the market may not be fully competitive at the start, with the relatively low volumes required, we feel it is better to launch with the end state in mind rather than having to change the market design further down the line.
10.12.21 | General queries | Disarming instruction | 50 | Will dis-arming and re-arming span EFAs where a participant does not have a contract e.g. contract for EFA 4 and 6 but not 5. | Yes the disarming instruction would still span across the scenario mentioned. You would only re-arm once notified.
10.12.21 | General queries | Onboarding | 51 | What do you need to do in terms of onboarding for existing assets? | If your assets are already registered, Forms A, B and C will continue to cover them. However, you will need to register on the new Single Market Platform (SMP) once it is available in February. Once registered on SMP, you will just need to register the assets i.e. you won't need to submit Forms A, B and C each time.
10.12.21 | General queries | Operational metering | 52 | What do you need to do in terms of operational metering for existing assets? | There are no additional requirements for existing assets which already provide DC. Such assets would already have operational metering and performance metering in place.
10.12.21 | General queries | State of Energy | 53 | We must enter the EFA block with sufficient energy to deliver the service and the rules for recovery are to set a baseline and eventually recover over several SPs. What happens if we follow these rules but have not yet fully recovered as we enter a new EFA block and remain in contract? | If you follow the rules and show reasonable intention to restore SoE as per rules/guidance, then there will be no penalty. E.g. a 10MW contract in EFA 1 followed by a 20MW contract in EFA 2, the energy requirement will obviously be different (2x as much in EFA 2). You should be anticipating the increase in energy requirement and submitting baselines while in EFA 1 to increase stored energy ready for the start of EFA 2.
10.12.21 | General queries | Freqeuncy Measurement specification | 54 | What does industry best practice for ‘Frequency Measurement Specification’ look like? Why has this been introduced? | We will be looking to define 'best practice' with industry in 2022. Any changes to the FMS will be consulted on in the normal way. The reason we have introduced the FMS is to help both ESO and providers reach a common understanding of how to measure frequency.
10.12.21 | General queries | Disarming instruction | 55 | What are the interface requirements for dis-arming and re-arming of DM and DR? | ESO will send providers an instruction via electronic means to turn off and providers will only resume once ESO send a re-arming instruction even if that is across multiple EFA blocks. We are still working through the technical aspects of this and will let providers know more information on the functionality as soon as possible.
10.12.21 | General queries | Usage | 56 | What is the expected usage of DM and DR? | DR quantity will probably remain fairly static over the year, DM will be more variable as we look to use it to manage periods with significant ramping changes.
10.12.21 | General queries | Participation | 57 | For DR H can a 1-hour battery participate by being fully charged? | It’s not possible to give a simple yes/no to a question like this. All the SoE rules are explained in the ST and the Participation Guidance.
10.12.21 | General queries | Performance monitoring | 58 | If we need to resubmit performance monitoring data I understand that we have another 24 hours where we can submit via the same communication method. What should we do after this time? Can we submit in the same way or should we email? | In case an erroneous file is submitted with any of the error categories, the provider has until 5th of the next month at 00:00:00 UTC to upload correct or amended data before it is considered final to over-write the incorrect data. Beyond this window the system would block any old data resubmitted. We do not receive Performance Data over email.
10.12.21 | General queries | 2Hz/10Hz | 59 | For the testing of DR, why is it necessary to provide 2hz testing if you provide 10hz? Can we test at 10hz? | Testing can be done 10Hz.
10.12.21 | Technical consultation webinar (30/11) | State of Energy | 60 | Are you considering the possibility of potentially delivering 2x the power for discharging (as this gives some space for services on the other side) (10 MW assets, power charge setpoint at -5MW, you can provide 15 MW of discharge) | Yes this is allowed. But the capacity must be available for the whole 4hr EFA block. In the example, the battery would be continously charging at 5MW for 4hrs. Provided the energy capacity and delivery duration requirements can be met, this is a suitable configuration.
10.12.21 | Technical consultation webinar (30/11) | State of Energy | 61 | Energy recovery management may be challenging, the 5%/min ramp requirements only make this more difficult - can you not remove these? | Can you please elaborate on why precisely you find this challenging - that way we can understand if any compromise may be suitable. The ramp-rate limits are there to mitigate the risk of herding behaviour.
10.12.21 | Technical consultation webinar (30/11) | Testing | 62 | Any indication on value for DR (and DM?) Is this comparable to FFR? | DR is more comparable to FFR-PSH. But all these new services are in response to significant changes in operation & risk in last ~5yrs - so direct comparison is not easy. We are obliged to keep frequency in statutory & operational range - and any period where there is greater uncertainty or possibility for error/imbalance in supply-demand creates a need for frequency regulation provided by DM & DR. There will always be a 'base' requirement but expect periods where we seek additional supply.
10.12.21 | Technical consultation webinar (30/11) | Performance Monitoring | 63 | Can performance monitoring data be resubmitted on the API rather than sharepoint? | Data should be resubmitted through the API and not through SharePoint. In the event of delayed or incorrect data, you have until 5th of the next month at 00:00:00 UTC to upload correct or amended data before it is considered final.
10.12.21 | Technical consultation webinar (30/11) | LFSM | 64 | Are DR provider still expected to provide LFSM in accordance with the Grid Code? | Yes.
10.12.21 | Technical consultation webinar (30/11) | Pumped storage | 65 | The inclusion of pumped storage assets as time limited seems odd, yes they are energy limited but over a far, far longer timeframe compared to batteries. | We will take another look at this. It is not easy to determine where energy limited begins/ends.
10.12.21 | Technical consultation webinar (30/11) | Duration for energy limited assets | 66 | Why has NGESO decided on 60 minutes delivery duration - an extreme duration compared with the 30 minutes required for FFR. That will eliminate a lot of possible energy limited participants from the market which is not good for NGESO or the cost to customers. | We've seen high/low frequency for periods of hours over the past two years, this has informed our requirement for 60min duration from energy limited assets. Our new suite of reserve services will help to reduce the duration and frequency of these events - once these are launched (specifically Quick Reserve) we may be able to revisit the duration requirements from energy limited providers.
10.12.21 | Technical consultation webinar (30/11) | State of Energy | 67 | Is availability an on/off logic or could a unit declare availability in the range 0%-100% of contracted capacity as SOC recovers? | It is an on/off logic, partial available is not considered at the moment, i.e. declare available at 100% SoC.
10.12.21 | Technical consultation webinar (30/11) | State of Energy | 68 | How would an energy recovery baseline for LF (i.e. to recharge) affect required delivery of simultaneous HF (i.e. a proportional charging service)? | If you need to submit an charging baseline it should not erode any provision of HF. This is explained with an example in the Participation Guidance document.
10.12.21 | Technical consultation webinar (30/11) | State of Energy | 69 | Is DR "response Energy" in slide 19 really 50MWh on a 50MW 1h duration? that implies permanent 100% SoE? | The full response energy volume is expected at the beginning of the contacted EFA block. This energy will gradually be exhausted through a settlement period, but the provider should be using baselines to restore and manage that energy. An example in the Participation Guidance explains this.
10.12.21 | Technical consultation webinar (30/11) | Performance Monitoring | 70 | How will performance assessment manage the case of delivering response while ramping for SOC management? | Any ramping for SoC will be achieved by submitting and following a baseline. This baseline is then used as the datum/reference for performance monitoring. Therefore it is very important to be able to follow accurately a baseline AND also deliver response accurately from any position on a baseline.
15.12.21 | Technical consultation webinar (30/11) | Testing | 71 | If there are any identical or more stringent tests an asset has already passed (for DC or FFR for example) do those individual tests still have to be redone? | All assets will need to be tested to enter the DM and DR services as the delivery profile is different to DC and FFR.
15.12.22 | General queries | Operational metering | 72 | Will there be additional fields added for the Operational metering communication, as was the case for DC H? | We will be adding two more binary inputs for DM and DR availability signals. The rest of the ops metering is staying unchanged. An updated CSV with extended availability flags has been published for performance monitoring.
15.12.21 | General queries | Performance Monitoring | 73 | The performance tolerance is very tight, particularly for DR and also when compared to FFR. We recommend it would be more appropriate to use a range of 5-10%. Ideally this should also be applied to DM and DC. | Tolerances in performance monitoring should cater for this, particularly in the error calculation where rolling minimum/mean windows are applied. We will consider your feedback for further investigation.
15.12.21 | General queries | State of Energy | 74 | Assuming a 10MW asset with 1h duration, can the asset provide continuously 10MW of Low and High service or shall it reduce its contracted amount to allow SOC management though baseline and to which level | SoE is described in the Participation Guidance with examples given. We cannot give specific direction as all assets are different and it is up to providers to ensure they manage this. It does state some volume should be held back for this which will mean there cannot be symmetrical delivery.
15.12.21 | General queries | Stacking | 75 | Whilst we understand we can’t stack across services, is it possible to split an asset to have volume in different services for the same EFA block? | This option won't be available for the launch, this is something that will be included as part of the development of the service. Different Unit IDs and separate metering would be required.
15.12.21 | General queries | Penalties | 76 | How will the penalties work? Will they start from the launch of the services? | Penalties will be issued from the launch of the services.